## Slide 1: Existing Building Commissioning Workshop Series 16, Session 2
Introduction to System Diagrams

## Slide 2: Resources for Details Behind this Content
Search for “System Diagrams: …”
You can also filter for them with the drop-down menu
Developing a System Diagram: Getting Started and the next few posts walk you through the process using the PEC ice storage system as an example
www.Av8rdas.Wordpress.com

## Slide 3: Resources for Details Behind this Content
PowerPoint based tool and symbol library
AutoCAD symbol library
Examples in AutoCAD and PowerPoint
https://www.av8rdas.com/system-diagram-symbols.html

## Slide 4: Resources for Details Behind this Content
Full day workshop content
Multiple examples in multiple formats
https://www.av8rdas.com/pacific-energy-center-design-performance-and-commissioning-issues-classes.html#System

## Slide 5: Its Not Just a Heat Exchanger … …It’s a Hot Water System

## Slide 6: Its Not Just a Heat Exchanger … …It’s a Hot Water System

## Slide 7: Its Not Just an Air Handling Unit … …It’s an Air Handling System

## Slide 8: Its Not Just an Air Handling Unit … …It’s an Air Handling System

## Slide 9: Physically Complex, Schematically Simple

## Slide 10: “Like a Ladder on its Side” Chuck McClure

## Slide 11: Tee’s are Important
For both the physical system and the system diagram:
  Divergence or convergence of flow
  An opportunity to introduce a problem if the order of connection is not correct
For the physical system, they represent a pressure drop
  Significant
  Highly variable with configuration

## Slide 12: Elbows; Not So Much Maybe
From the perspective of the system diagram:
  Just a bent piece of straight pipe
  Water in = Water out
One way to think of elbow resistance is to consider it as composed of:
    Resistance due to interaction with the pipe wall

## Slide 13: Elbows; Not So Much Maybe
From the perspective of the system diagram:
  Just a bent piece of straight pipe
  Water in = Water out
One way to think of elbow resistance is to consider it as composed of:
    Resistance due to interaction with the pipe wall
    + Resistance due to a change in direction

## Slide 14: Elbows; Not So Much Maybe
From the perspective of the system diagram:
  Just a bent piece of straight pipe
  Water in = Water out
One way to think of elbow resistance is to consider it as composed of:
    Resistance due to interaction with the pipe wall
    + Resistance due to a change in direction
    _______________________________________________________________
    Total Resistance for the Elbow

## Slide 15: Order of Connection Matters

## Slide 16: System Diagram Rules for Elbows and Tees
Show all tees
  Verify order of connection
  Order of connection “trumps” drawing organization
  Drawing organization “trumps” matching branch and main configuration in the field
Don’t show elbows
  Turns on the system diagram should be made for drawing organization purposes, not to reflect real elbows

## Slide 17: Getting Started
Find something you can identify
  Nameplate data
  Labels
  Past experience

## Slide 18: Getting Started
Find something you can identify
  Nameplate data
  Labels
  Past experience
Start following the system of interest
  Your first effort will likely not be your last effort

## Slide 19: Getting Started
Find something you can identify
  Nameplate data
  Labels
  Past experience
Start following the system of interest
  Your first effort will likely not be your last effort
  “Follow your nose”
  Make decisions at tees

## Slide 20: Getting Started
Find something you can identify
  Nameplate data
  Labels
  Past experience
Start following the system of interest
  Your first effort will likely not be your last effort
  “Follow your nose”
  Make decisions at tees

## Slide 21: Sometimes Rules are Made to be Broken
Elbows that form traps or inverted traps in open systems
Pipes that run above basin level in open systems
Pipe runs with an relatively excessive number of elbows
Tees where the pressure drop created by the installed configuration could cause an operational issue

## Slide 23: So Far, Our Focus Has Been Hydronic Systems; What About Air Systems?

## Slide 24: Can You Identify the HVAC/Air Handling System Elements in this Picture?

## Slide 25: Air Handling Systems and System Diagrams
The same general rules apply
Significant differences from piping systems
  Envelope is a part of the system
  Mass (air and water vapor) are actively moved across the system boundary by the operation of the system
  The water vapor can change state in the system
  People move around inside the systems
  Building processes occur inside the system

## Slide 26: Envelope Integrity = HVAC Duct Integrity

## Slide 27: The Envelope is Significant(ly Complex)
Atriums interconnect floors

## Slide 28: The Envelope is Significantly Complex
Atriums interconnect floors
Stair and elevator shafts act like chimneys

## Slide 29: The Envelope is Significantly Complex
Atriums interconnect floors
Stair and elevator shafts act like chimneys
Smoke shafts act like chimneys and interconnect floors

## Slide 30: The Envelope is Significantly Complex
Atriums interconnect floors
Stair and elevator shafts act like chimneys
Smoke shafts act like chimneys and interconnect floors
Return and relief plenums interconnect floors and shafts

## Slide 31: The Envelope as the Framework for the Air Handling System Diagnostics
AHU1
AHU3
AHU2
AHU4
AHU 8
Flow Arrow Color Codes
  AHU1
  AHU2
  AHU3
  AHU4
  AHU8 (Note AHU7 is not shown but serves a similar area and function for the other half of the building)
  Return air (all systems)
  Transferred air
  Outdoor air infiltration
  Garage exhaust

## Slide 32: The Envelope as the Framework for the Air Handling System Diagnostics
AHU1
AHU3
AHU2
AHU4
AHU 8

## Slide 33: Air Handling System Diagram Characteristics

## Slide 34: Reflect the Building Physical Arrangement

## Slide 35: Include Examples of Each Zone Type

## Slide 36: Include the Impacts of Other Systems

## Slide 37: Document Conservation of Mass and Energy

## Slide 38: Let’s Review By Getting Started with the Hijend Hotel CHW Plant Diagram