## Slide 1: VAV Systems
Design, Performance and Commissioning Issues
Terminal Unit Basics
David Sellers
Senior Engineer
Facility Dynamics Engineering
March 7, 2018

## Slide 2: What’s In This Module
Your basic box:
  Pressure dependent
  Pressure independent
  Fan powered boxes
  Double duct boxes

## Slide 3: Your Basic Box
Enclosure
Damper
Duct to Zone
Duct from System
Actuator
Crank Arm
Linkage and Swivel Joints

## Slide 4: Your Basic Box
Enclosure
Damper
Centerline Drive Actuator
Duct to Zone
Duct from System
with set screws

## Slide 5: Your Basic Box
T

## Slide 6: Your Basic Box
T

## Slide 7: Your Basic Box
T
Flow through the box is a function of damper position and pressure difference …
…thus it is called pressure dependent

## Slide 8: Your Basic Box
T
T
P
Time
L
T
Time
T
Time
L
T

## Slide 9: Your Basic Box
T
T
P
Time
T
Time
L
L
T
Time

## Slide 10: Your Basic Box
T
T
L
T
Time
T
Time
L
P
Time

## Slide 11: Your Basic Box
T
T
T
Time
L
T
Time
L
P
Time

## Slide 12: Becoming Pressure Independent
Temperature
Flow
T
F
CFlow
Minimum
Maximum
Volume regulation can also be accomplished mechanically (both fixed and variable)

## Slide 13: The Relationship Between Flow and Velocity

## Slide 14: The Relationship Between Velocity and Velocity Pressure

## Slide 15: Pneumatic vs. DDC Terminal Unit Controllers
DDC Terminal Units
Newer technology
No moving parts
Maintenance on condition
Can provide important diagnostics
  Leaving air temperature
  Current flow rate
Can provide data useful for system optimization strategies
Set points can be adjusted and verified from the OWS
Performance can be verified from the OWS
Pneumatic Terminal Units
Been around for a long time
A lot of moving parts
Don’t know the condition
They are low first cost
They are low first cost
They are low first cost
They are low first cost

## Slide 16: The Relationship Between Velocity and Velocity Pressure
12 inch VAV Box
    Maximum flow
      2,000 cfm
      VP = .2494 in.w.c.
    Minimum flow
      325 cfm
      VP = .0066 in.w.c.

## Slide 17: The Relationship Between Velocity and Velocity Pressure
12 inch VAV Box
    Maximum flow
      2,000 cfm
      VP = 0.2494 in.w.c.
      Force = 0.0465 lb
      Force = 0.74 oz
    Minimum flow
      325 cfm
      VP = 0.0066 in.w.c.
      Force = 0.0017 lb
      Force = 0.03 oz
Frame of reference; a letter in an envelop weighs about 1 oz.
Notes: 0.0465 lb 0.74 oz 0.0017 lb 0.03 oz

## Slide 18: Pneumatic Terminal Failure Modes
Flow set points drift up
Recent experience
  Sample 10 of 45 pneumatic zones
  Three years since last service effort
Many of the controllers worked
Many thermostats were out of calibration
0 (zero) zones were regulating at the required flow
Many zones were wide open
Some reheat valves were leaking through

## Slide 19: Pneumatic Zones = Opportunity
Troubleshooting a Pneumatic Terminal
Troubleshooting a DDC Terminal

## Slide 20: The Regulator (PG13)
http://tinyurl.com/3kebw3s
Notes: http://tinyurl.com/3kebw3s

## Slide 21: VAV Reheat
Temperature
Flow
T
F
CFlow
Minimum
Maximum
Reheat coil
Control valve

## Slide 22: A Typical VAV Reheat Box

## Slide 23: Overview

## Slide 24: The Damper

## Slide 25: The Flow Sensor

## Slide 26: The Reheat Coil

## Slide 27: The DDC Controller with Built In Actuator

## Slide 28: A Pneumatic DDC Controller and Actuator

## Slide 29: Recovering Heat to Reheat Series Fan Powered Box
T
F
CFlow

## Slide 30: Recovering Heat to Reheat Series Fan Powered Box
Filter
Return Connection
Fan runs continuously when the zone is occupied
  Tends to be constant volume
Reduction in primary flow (cooling air) is compensated for by increased return flow
  First stage of reheat
  Coil provides second stage
T
F
CFlow
Fan

## Slide 31: Recovering Heat to Reheat Series Fan Powered Box
Filter
Return Connection
T
F
CFlow
Fan

## Slide 32: Recovering Heat to Reheat Parallel Fan Powered Box
Filter
Return Connection
Fan runs intermittently when the zone is occupied
  Tends to be constant volume when the fan runs
Zone sees some reduction in flow until the fan starts
  First stage of reheat
  Coil provides second stage
T
F
CFlow
Fan

## Slide 33: A Typical Fan Powered Box

## Slide 34: A Typical Fan Powered Box Filter

## Slide 35: A Typical Optimized Inlet Condition

## Slide 36: The In Series Fan

## Slide 37: The In Series Fan

## Slide 38: Double Duct Boxes = Reheat with Hot Air
Twice the components = twice the “fun”
Often separate fan systems for each deck
Ventilation air typically provided by the cold deck
  Always minimum cold deck flow
  Hot deck goes to 0 cfm
T
F
CFlow
F
Cold duct or “deck”
Hot duct or “deck”
Mixed air to the zone

## Slide 39: A Single Path Double Duct Unit

## Slide 40: A Single Path Double Duct Unit

## Slide 41: A Single Path Double Duct Unit

## Slide 43: A Dual Path Double Duct Unit

## Slide 44: A Dual Path Double Duct Unit

## Slide 45: A Constant Volume to VAV Conversion

## Slide 46: A Double Duct Box

## Slide 47: Bottom Lines
The basic box is pretty simple
Making it bullet proof makes it a bit more complex
Making it energy efficient makes it more complex
Making it cost effective makes persistent complexity challenging