## Slide 1: Pumps and Piping; Design, Performance and Commissioning Issues
Open and Closed Systems
David Sellers
Senior Engineer, Facility Dynamics Engineering
Presented By:

## Slide 2: Central Plants Typically Have Open and Closed Systems Associated with Them
Piping Network
Piping Network
Piping Network
Load
Chilled Water Pump
Expansion tank and make up water
Make-up, Blow-down, and Water Treatment
Evaporator
Condenser
Expansion Device
Compressor
Water Chiller
Condenser Water Pump
Cooling Tower
Typically an open system
  More than one interface with the atmosphere or a compressible gas
Typically a closed system
  Only one interface with atmosphere or a compressible gas

## Slide 3
Chillers, pumps, and chilled water make up connection here
Piping mains run up and down this chase
Air handling units are here
Cooling towers and make up connections are here

## Slide 4
Approximately 475 ft. from the lowest point in the CHW system to the highest point in the CHW system

## Slide 5
Approximately 455 ft. from the lowest point in the CW system to the cold basins of the cooling towers
Approximately 15 ft. from the cold basin to the hot basin of the cooling towers

## Slide 6
Closed Chilled Water System
Open Condenser Water System

## Slide 7
Closed Chilled Water System
Open Condenser Water System
The closed chilled water system could be completely filled from a connection at the high point in the system
The open condenser water system could only be filled to the rim of the open basin from a connection at the high point in the system

## Slide 8: A Couple of Questions
What pressure should be used as a fill pressure for the chilled water system and why?
Notes: Electric rate = $0.0480 $ per kWh
Natural gas rate = $0.7700 $ per therm
Over-all boiler plant efficiency = 69% Basis - Energy Star Performance Ratings Methodology for Incorporating Source Energy Use
Net Cost for Steam = $11.16 per MMBtu
Boiler plant emmissions = 116.3 lbs CO2/MMBtu
Electrical plant emmissions = 1.8440 lbs CO2/kWh
Chiller plant over-all efficiency = 0.90 kW/ton

## Slide 9: A Couple of Questions
What pressure should be used as a fill pressure for the chilled water system and why?
If the evaporator pumps serving the chillers are rated to produce 30 ft.w.c. of head at design conditions, what would an appropriate range be for the pressure gauges on the pump?
Notes: Electric rate = $0.0480 $ per kWh
Natural gas rate = $0.7700 $ per therm
Over-all boiler plant efficiency = 69% Basis - Energy Star Performance Ratings Methodology for Incorporating Source Energy Use
Net Cost for Steam = $11.16 per MMBtu
Boiler plant emmissions = 116.3 lbs CO2/MMBtu
Electrical plant emmissions = 1.8440 lbs CO2/kWh
Chiller plant over-all efficiency = 0.90 kW/ton

## Slide 10: Some More Questions
How much head needs to be included in the condenser water pump selection to lift water through an elevation change?
Assuming the condenser pump is at the lowest point in the system, what would the gauge on its suction connection read when the system was not operating?
Would this reading change when you started the pump?
Notes: Electric rate = $0.0480 $ per kWh
Natural gas rate = $0.7700 $ per therm
Over-all boiler plant efficiency = 69% Basis - Energy Star Performance Ratings Methodology for Incorporating Source Energy Use
Net Cost for Steam = $11.16 per MMBtu
Boiler plant emmissions = 116.3 lbs CO2/MMBtu
Electrical plant emmissions = 1.8440 lbs CO2/kWh
Chiller plant over-all efficiency = 0.90 kW/ton

## Slide 11: Closed Systems
Piping Network
Load
Pump
Expansion tank and make up water
Evaporator
Condenser
Expansion Device
Compressor
Water Chiller
  Interface is at the expansion tank
    Open or diaphragm type
      Different sizing issues
      Different piping issues
  Pressure tends to hold constant at the expansion tank
  Expansion tank typically at the distribution pump suction connection
  Air separation may or may not be at the expansion tank
  Fill pressure needs to be sufficient to vent air at high points
  Make up typically connected at the expansion tank
    Very little required once filled
    Limited water treatment
    Monitor volume and pressure

## Slide 12: Non-Diaphragm Expansion Tank

## Slide 13: Diaphragm Expansion Tank

## Slide 14: Air Separators

## Slide 15: Makeup Connections

## Slide 16: Water Treatment via Shot Feeder

## Slide 17: Back Flow Preventer Isolating Treated Water from Potable (Drinking) Water

## Slide 18: Back Flow Preventer Isolating Treated Water from Potable (Drinking) Water

## Slide 19: Open Systems
Make-up, Blow-down, and Water Treatment
Evaporator
Condenser
Expansion Device
Compressor
Water Chiller
Pump
Piping Network
Piping Network
Cooling Tower
  Interfaces are at the cooling tower return and supply points
    Cold water typically connected to a sump or cold basin
    Hot water distributed by spray nozzles or orifices in a “hot basin”
  Pump head must lift the water between the basins
  Make-up requirements more significant
    Evaporation
    Blow-down
  Water treatment requirements more significant
  Chilled and hot water systems can be open systems

## Slide 20: Water Treatment

## Slide 21: Side Stream Filtration

## Slide 22: Cooling Tower Make-up Piping and Meter

## Slide 23: Cooling Tower Blow-down Piping and Meter

## Slide 24: Cooling Tower Opportunity http://youtu.be/EVtO-y_NKN8
Notes: http://youtu.be/EVtO-y_NKN8

## Slide 25
Chillers, pumps, and chilled water make up connection here
Piping mains run up and down this chase
Air handling units are here
Cooling towers and make up connections are here

## Slide 26
Approximately 475 ft. from the lowest point in the CHW system to the highest point in the CHW system

## Slide 27
Approximately 455 ft. from the lowest point in the CW system to the cold basins of the cooling towers
Approximately 15 ft. from the cold basin to the hot basin of the cooling towers