## 1510 6G 1150rpm
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2015-03-29
Project Name: | Duct Friction Spreadsheet
Project Number: | None
Engineer: | David
Assumptions
1 | This information was digitized by Dawn using plot digitizer.
2 | The source files are in the following folders.
3 | The original source of the data
4 | ????
5 | ????
6 | ????
7 | ????

## Impeller 6G 1150
10 Inch |  | 10.5 Inch |  | 11 Inch |  | 11.5 Inch |  | 12 Inch |  | 12.5 Inch |  | 13 Inch |  | 13.5 Inch
File 10 Inch.csv |  | File 10.5 Inch.csv |  | File 11 Inch.csv |  | File 11.5 Inch.csv |  | File 12 Inch.csv |  | File 12.5 Inch.csv |  | File 13 Inch.csv |  | File 13.5 Inch.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
0 | 41.2281 | 0 | 46.5887 | 0 | 51.7544 | 0 | 57.5049 | 0 | 63.9376 | 0 | 70.078 | 0 | 76.8031 | 0 | 83.5283
102.422 | 41.3255 | 102.422 | 46.5887 | 101.038 | 51.7544 | 99.654 | 57.5049 | 101.038 | 63.8402 | 102.422 | 70.1 | 101.038 | 76.7057 | 101.038 | 83.6257
202.076 | 41.423 | 200.692 | 46.4912 | 202.076 | 51.462 | 200.692 | 57.4074 | 202.076 | 63.6452 | 202.076 | 69.9805 | 203.46 | 76.6082 | 202.076 | 83.5283
300.346 | 41.2281 | 301.73 | 46.1988 | 303.114 | 51.1696 | 300.346 | 57.2125 | 303.114 | 63.5478 | 301.73 | 69.7856 | 301.73 | 76.5107 | 301.73 | 83.4308
402.768 | 40.85 | 402.768 | 45.7115 | 402.768 | 50.7797 | 397.232 | 56.9201 | 400 | 63.2554 | 400 | 69.4932 | 402.768 | 76.4133 | 401.384 | 83.2359
502.422 | 40.4 | 517.647 | 45.2 | 517.647 | 50.3899 | 501.038 | 56.4327 | 502.422 | 62.8655 | 501.038 | 69.1 | 501.038 | 76.0234 | 502.422 | 82.846
600.692 | 39.5 | 610.381 | 44.5 | 613.149 | 49.9025 | 600.692 | 56.0429 | 602.076 | 62.3782 | 599.308 | 68.6 | 602.076 | 75.5 | 602.076 | 82.4561
701.73 | 38.5965 | 703.114 | 43.7622 | 705.882 | 49.3177 | 701.73 | 55.5556 | 700.346 | 61.8908 | 698.962 | 68.1287 | 701.73 | 74.9513 | 703.114 | 82.0663
801.384 | 37.037 | 802.768 | 42.4951 | 798.616 | 48.538 | 800 | 54.6784 | 777.855 | 61.2 | 798.616 | 67.5439 | 798.616 | 74.269 | 801.384 | 81.6764
899.654 | 34.9903 | 898.27 | 40.8382 | 901.038 | 47.271 | 898.27 | 53.7037 | 822.145 | 60.9 | 901.038 | 66.6667 | 901.038 | 73.4893 | 903.806 | 80.9941
1002.08 | 31.7739 | 1002.08 | 38.4016 | 997.924 | 45.2242 | 1000.69 | 51.5595 | 865.052 | 60.4288 | 1003.46 | 65.1072 | 999.308 | 72.2222 | 999.308 | 80.0195
1100.35 | 27.9727 | 1100.35 | 35.0877 | 1100.35 | 42.2027 | 1100.35 | 48.9279 | 913.495 | 59.7466 | 1098.96 | 63.2554 | 1098.96 | 70.9 | 1101.73 | 78.3626
1202.77 | 23.3918 | 1202.77 | 30.9942 | 1200 | 38.3041 | 1200 | 45.4191 | 956.401 | 59.0643 | 1201.38 | 60.5263 | 1201.38 | 69.0059 | 1201.38 | 76.4133
1259.52 | 20.2729 | 1281.66 | 27.0955 | 1301.04 | 33.8207 | 1299.65 | 41.5205 | 997.924 | 58.2846 | 1255.36 | 58.9669 | 1301.04 | 66.7641 | 1302.42 | 74.0741
|  | 1364.71 | 22.2222 | 1402.08 | 28.8499 | 1367.47 | 38.1092 | 1062.98 | 57.0175 | 1299.65 | 57.6023 | 1356.4 | 64.8148 | 1402.08 | 71.54
|  |  |  | 1478.2 | 24.3665 | 1431.14 | 34.6004 | 1147.4 | 54.8733 | 1345.33 | 56.1404 | 1407.61 | 62.963 | 1501.73 | 68.5185
[6 empty] | 1500.35 | 30.117 | 1224.91 | 52.5341 | 1397.92 | 54.0936 | 1460.21 | 60.8187 | 1600 | 64.6199
[6 empty] | 1555.71 | 26.0234 | 1292.73 | 50.0975 | 1457.44 | 51.6569 | 1518.34 | 58.4795 | 1647.06 | 62.4756
[8 empty] | 1349.48 | 47.6608 | 1512.8 | 49.0253 | 1577.85 | 55.7505 | 1699.65 | 60.039
402.768 | 40.7407 | [6 empty] | 1422.84 | 44.2495 | 1555.71 | 46.7836 | 1627.68 | 53.2164 | 1791 | 55.1657
502.422 | 40.0585 | [6 empty] | 1490.66 | 40.7407 | 1600 | 44.2495 | 1681.66 | 50.2924 | 1847.75 | 51.3645
600.692 | 39.0838 | [6 empty] | 1564.01 | 36.3548 | 1642.91 | 41.7154 | 1731.49 | 47.3684 | 1903.11 | 47.3684
[8 empty] | 1676.12 | 29.3372 | 1685.81 | 39.0838 | 1781.31 | 44.152 | 1948.79 | 43.8596
[10 empty] | 1731.49 | 36.2573 | 1826.99 | 41.0331 | 2013.84 | 38.4016
|  | 0 | 46.5887 | [6 empty] | 1788.24 | 31.9688 | 1904.5 | 35.3801
|  | 102.422 | 46.5887
|  | 200.692 | 46.4912
|  | 301.73 | 46.1988 | [8 empty] | 602.076 | 75.3411
|  | 402.768 | 45.7115 | [8 empty] | 701.73 | 74.9513
|  | 517.647 | 44.9318 | [8 empty] | 798.616 | 74.269
|  | 610.381 | 44.347 | [8 empty] | 901.038 | 73.4893
|  | 703.114 | 43.7622 | [8 empty] | 999.308 | 72.2222
|  | 802.768 | 42.4951 | [8 empty] | 1098.96 | 70.468
[10 empty] | 0 | 70.078
[10 empty] | 102.422 | 70.1754
[10 empty] | 202.076 | 69.9805
[10 empty] | 301.73 | 69.7856
[10 empty] | 400 | 69.4932
[10 empty] | 501.038 | 68.9084
[10 empty] | 599.308 | 68.4211
[10 empty] | 698.962 | 68.1287
[10 empty] | 798.616 | 67.5439
[10 empty] | 901.038 | 66.6667
[8 empty] | 0 | 63.9376
[8 empty] | 101.038 | 63.8402
[8 empty] | 202.076 | 63.6452
[8 empty] | 303.114 | 63.5478
[8 empty] | 400 | 63.2554
[8 empty] | 502.422 | 62.8655
[8 empty] | 602.076 | 62.3782
[8 empty] | 700.346 | 61.8908
[8 empty] | 777.855 | 61.501
[8 empty] | 822.145 | 61.0136
[8 empty] | 865.052 | 60.4288

## Efficiency 6G 1150
60% |  | 70% |  | 75% |  | 80% |  | 83% |  | 86% |  | 87%
File 60%.csv |  | File 70%.csv |  | File 75%.csv |  | File 80%.csv |  | File 83%.csv |  | File 86%.csv |  | File 87%.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
451.385 | 83.0949 | 620.308 | 82.3147 | 711.692 | 82.0221 | 850.154 | 81.4369 | 995.538 | 79.974 | 1154.77 | 77.4382 | 1236.46 | 75.9753
438.923 | 80.3641 | 596.769 | 78.0234 | 692.308 | 78.6086 | 841.846 | 78.6086 | 976.154 | 76.1703 | 1142.31 | 73.9272 | 1236.46 | 74.6099
430.615 | 76.7555 | 574.615 | 72.5618 | 671.538 | 75 | 829.385 | 75.0975 | 948.462 | 71.0013 | 1129.85 | 69.9285 | 1253.08 | 73.2445
419.538 | 72.5618 | 558 | 68.4655 | 656.308 | 71.2939 | 818.308 | 71.9766 | 926.308 | 65.8323 | 1121.54 | 66.2224 | 1275.23 | 71.5865
412.615 | 68.4655 | 544.154 | 63.9792 | 639.692 | 65.8323 | 808.615 | 68.4655 | 911.077 | 61.4434 | 1110.46 | 61.736 | 1297.38 | 70.8062
402.923 | 63.2965 | 531.692 | 58.7126 | 624.462 | 59.4928 | 793.385 | 64.857 | 906.923 | 56.4694 | 1110.46 | 58.7126 | 1325.08 | 70.3186
397.385 | 59.0052 | 523.385 | 52.8609 | 614.769 | 53.446 | 783.692 | 61.541 | 915.231 | 52.2757 | 1121.54 | 56.9571 | 1361.08 | 70.7087
394.615 | 55.3966 | 516.462 | 47.5943 | 607.846 | 47.2042 | 776.769 | 57.9324 | 931.846 | 48.6671 | 1135.38 | 55.2991 | 1394.31 | 71.4889
390.462 | 51.8856 | 512.308 | 40.0845 | 603.692 | 42.1326 | 769.846 | 52.9584 | 951.231 | 45.9363 | 1156.15 | 54.5189
390.462 | 48.1795 | 1140.92 | 26.3329 | 605.077 | 39.1092 | 765.692 | 48.5696 | 984.462 | 43.8882 | 1185.23 | 54.1287
391.846 | 43.4005 | 1200.46 | 27.3082 | 1048.15 | 29.9415 | 764.308 | 44.6684 | 1027.38 | 42.3277 | 1221.23 | 54.3238
389.077 | 40.8648 | 1278 | 28.9662 | 1085.54 | 30.6242 | 767.077 | 40.0845 | 1074.46 | 42.1326 | 1253.08 | 55.104
1248.92 | 20.6762 | 1355.54 | 31.0143 | 1136.77 | 31.4044 | 774 | 37.5488 | 1121.54 | 43.0104 | 1301.54 | 56.6645
1302.92 | 21.749 | 1449.69 | 33.1599 | 1188 | 32.6723 | 931.846 | 34.1352 | 1175.54 | 44.3758 | 1345.85 | 58.3225
1363.85 | 22.6268 | 1548 | 35.7932 | 1246.15 | 33.9402 | 995.538 | 35.1105 | 1239.23 | 46.3264 | 1395.69 | 60.8583
1458 | 24.6749 | 1629.69 | 38.329 | 1302.92 | 35.4031 | 1067.54 | 36.2809 | 1304.31 | 48.3745 | 1442.77 | 63.2965
1542.46 | 26.8205 | 1725.23 | 41.4499 | 1350 | 36.4759 | 1134 | 37.6463 | 1372.15 | 50.7152 | 1518.92 | 67.7828
1640.77 | 29.2588 | 1815.23 | 44.5709 | 1408.15 | 38.1339 | 1203.23 | 39.3043 | 1433.08 | 52.9584
1733.54 | 31.7945 | 1899.69 | 47.3017 | 1452.46 | 39.4994 | 1261.38 | 40.8648 | 1494 | 55.5917
1833.23 | 34.3303 |  |  | 1507.85 | 41.2549 | 1340.31 | 43.2055 | 1561.85 | 58.5176
1914.92 | 36.5735 |  |  | 1556.31 | 42.9129 | 1401.23 | 45.156 | 1644.92 | 62.5163
2003.54 | 39.0117 |  |  | 1621.38 | 44.8635 | 1460.77 | 47.3017
|  |  |  | 1665.69 | 46.3264 | 1530 | 49.8375
|  |  |  | 1714.15 | 48.1795 | 1585.38 | 51.8856
|  |  |  | 1772.31 | 50.4226 | 1654.62 | 54.6164
|  |  |  | 1830.46 | 52.6658 | 1737.69 | 58.1274

## Brake Horsepower 6G 1150
10HP |  | 15HP |  | 20HP |  | 25HP |  | 30HP |  | 40HP
File 10HP.csv |  | File 15HP.csv |  | File 20HP.csv |  | File 25HP.csv |  | File 30HP.csv |  | File 40HP.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
398.616 | 58.8694 | 441.522 | 79.7271 | 728.028 | 82.0663 | 1060.21 | 79.0448 | 1494.81 | 68.8109 | 2022.15 | 57.0175
438.754 | 56.5302 | 483.045 | 77.5828 | 775.086 | 79.2398 | 1082.35 | 77.5828 | 1528.03 | 66.6667 | 2059.52 | 53.7037
481.661 | 54.5809 | 534.256 | 74.4639 | 833.218 | 76.1209 | 1115.57 | 75.731 | 1564.01 | 64.5224 | 2102.42 | 49.9025
524.567 | 52.729 | 575.779 | 72.2222 | 877.509 | 73.5867 | 1152.94 | 73.8791 | 1598.62 | 62.5731 | 2130.1 | 47.1735
573.01 | 50.4873 | 615.917 | 70.1754 | 920.415 | 71.1501 | 1200 | 71.345 | 1637.37 | 60.3314 | 2179.93 | 41.8129
626.99 | 48.0507 | 656.055 | 67.7388 | 981.315 | 68.1287 | 1259.52 | 68.1287 | 1684.43 | 56.9201
680.969 | 45.614 | 693.426 | 65.692 | 1031.14 | 65.4971 | 1316.26 | 65.3996 | 1728.72 | 53.5088
721.107 | 43.6647 | 740.484 | 63.0604 | 1083.74 | 62.5731 | 1371.63 | 62.4756 | 1771.63 | 50.3899
762.63 | 41.7154 | 786.159 | 60.8187 | 1130.8 | 60.1365 | 1413.15 | 59.8441 | 1809 | 47.7583
804.152 | 39.8635 | 837.37 | 58.3821 | 1180.62 | 57.6023 | 1453.29 | 57.6998 | 1868.51 | 43.5673
842.907 | 38.1092 | 888.581 | 55.9454 | 1235.99 | 54.9708 | 1501.73 | 54.7758 | 1908.65 | 40.4483
896.886 | 35.3801 | 941.176 | 52.924 | 1281.66 | 52.5341 | 1540.48 | 52.0468 | 1969.55 | 35.4776
930.104 | 33.7882 | 997.924 | 50.4873 | 1327.34 | 49.8051 | 1591.7 | 48.9279
964.245 | 32.0988 | 1051.9 | 47.9532 | 1378.55 | 46.8811 | 1641.52 | 45.614
999.308 | 30.3444 | 1104.5 | 45.2242 | 1421.45 | 44.152 | 1683.04 | 42.5926
1038.06 | 28.3301 | 1151.56 | 42.6901 | 1467.13 | 41.3255 | 1739.79 | 38.7914
1097.12 | 25.2112 | 1200 | 40.3509 | 1515.57 | 38.3041 | 1781.31 | 35.6725
|  | 1252.6 | 37.4269 | 1562.63 | 35.2826 | 1838.06 | 31.6764
|  | 1292.73 | 35.0877 | 1602.77 | 32.4561
|  | 1321.8 | 33.2359 | 1674.74 | 27.3879
|  | 1343.94 | 31.7739
|  | 1371.63 | 30.3119
|  | 1399.31 | 28.46
|  | 1438.06 | 26.3158
|  | 1493.43 | 22.9045

## Design Point System Curve
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-04-06 06:32
Project Name: | Chiller Plant Model
Project Number:
Engineer: | David
Assumptions
1 | Known flow = | 1100 | gpm (design parameter)
2 | Head or static at known flow = | 40 | ft.w.c. (design parameter)
3 | Fixed static or open system lift = | 0 | Note 1
4 | System Curve Exponent = | 2 | Note 2
5 | Efficiency = | 82.5% | (From the curve)
6 | Bhp = | 13.468 | Bhp (calculated)
7 | Largest impeller = | 13.5 | inches
8 | Closest known impeller size = | 11 | inches (enter the known impeller size closes to the design operating point)
9 | Smallest impeller = | 10 | inches
10 | DP set point = | N/A | ft.w.c. (at the remote load at discharge header)
11 | Published curve speed = | 1150 | rpm (from the published curve)
Note 1 - For closed systems that control for a fixed pressure, enter it here in ft.w.c., otherwise use 0.
Note 2 - The typical value for this is 2, but ASHRAE research indicates that generally, 1.85 - 1.89 may be more appropriate for systems were there are some portions with out fully developed turbulent flow.
| System Curve Points |  |  |  | Click here to go to the data used to plot the digital pump curve set
| Condition | Flow | Static |  | Click here to go to the design condition tabs
| 140% of known flow | 1540 | 78.4 |  | Click here to go to the 75% load condition tabs
| 120% of known flow | 1320 | 57.6 |  | Click here to go to the 50% load condition tabs
| Known | 1100 | 40 |  | Click here to go to the 25% load condition tabs
| 80% of known flow | 880 | 25.6 |  | Click here to go to the 12.5% load condition tabs
| 60% of known flow | 660 | 14.4 |  | Click here to go to the summary tab
| 40% of known flow | 440 | 6.4
| 30% of known flow | 330 | 3.6
| 20% of known flow | 220 | 1.6
| 18% of known flow | 198 | 1.296
| 16% of known flow | 176 | 1.024
| 14% of known flow | 154 | 0.784
| 12% of known flow | 132 | 0.576
| 10% of known flow | 110 | 0.4
| 8% of known flow | 88 | 0.256
| 6% of known flow | 66 | 0.144
| 4% of known flow | 26.4 | 0.02304
| 2% of known flow | 13.2 | 0.00576
| No Flow | 0 | 0
Design Conditions
| Head Line | 2500 | 40 | Set the flow values in the yellow cells to match the range of the X axis
|  | 0 | 40
| Flow Line | 1100 | 90 | Set the head values in the orange cells to match the range of the Y axis
|  | 1100 | 0
Point on a Known Impeller Line
| Head Line | 2500 | 41.5 | Set the head value in the orange cell to the head value where the design system curve crosses the known impeller size line
|  | 0 | 41.5
| Flow Line | 1120 | 90 | Set the flow value in the yellow cell to the flow value where the design system curve crosses the known impeller size line
|  | 1120 | 0
Motor Speed Calculation
| Rated speed from nameplate - | 1150 | rpm
| Rated hp from the nameplate - | 15 | hp
| Rated slip - | 50 | rpm (1,200 rpm basis)
| Measured speed with the tach - | 1155.1066 | rpm
| Measured slip - | 44.8934 | rpm (1,200 rpm basis)
| Approximate load based on the tach reading - | 13.468 | hp

## Impeller Size Projection
Step 1 - Estimate the new impeller size
Basis for Estimating the new impeller size
Desired Flow - | 1100 | gpm - Enter the flow you are trying to predict the impeller size for here
Known flow - | 1120 | gpm - Enter the flow at a known point on a known impeller line here
Known impeller size - | 11 | inches - Enter the known impeller size here
Impeller size tweak - | 0 | The affinity laws assume geometric similarity, which is not perfectly true for an impeller trim. For example an impeller trim reduces the impeller diameter but not the diameter of the eye of the impeller. So you should make your projection from the closest known impeller size., but you may have to tweak the predicted value to get it he new impeller line to go through the target point. The further your projected line is from the known size, the bigger the tweak will need to be.
Desired impeller size - | 10.8036 | inches (calculated from the other metrics)
Lable generator - | 10 3/4 inch at 1,150 rpm
Step 2 - For each point on the known impeller line, calculate the flow for the different impeller size
Basis for Estimating the Design Impeller Line Flow
Known impeller size - | 11 | inches
Desired impeller size - | 10.8036 | inches (calculated above)
| 11.000 Impeller Flow, gpm (Known value from digitized curve) | 10.804 Impeller Flow, gpm (Calculated with the affinity law)
Adjust the number of rows here to match the number of rows in the impeller curve line you are using as a reference and then adjust the formula in column B to point to the flow data for the impeller you are using as a reference except for the zero value. You need to make the zero value a really small number to avoid a division by 0 error in the next step. | 1e-09 | 9.8214e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 99.2338
| 202.076 | 198.4675
| 303.114 | 297.7013
| 402.768 | 395.5757
| 517.647 | 508.4033
| 613.149 | 602.1999
| 705.882 | 693.277
| 798.616 | 784.355
| 901.038 | 884.948
| 997.924 | 980.1039
| 1100.35 | 1080.7009
| 1200 | 1178.5714
| 1301.04 | 1277.8071
| 1402.08 | 1377.0429
| 1478.2 | 1451.8036
Step 3 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 11.000 inch Impeller Flow, gpm (Known value from digitized curve) | 10.804 inch Impeller Flow, gpm (Calculated above) | 11.000 inch Impeller Head, ft.w.c. (Known value from digitized curve) | 10.804 inch Impeller Head, ft.w.c. (From square law)
Adjust the number of rows here to match the number of rows in the impeller curve line you are using as a reference and then adjust the formula in column D to point to the head data for the impeller you are using as a reference. | 1e-09 | 9.8214e-10 | 51.7544 | 49.9225
| 101.038 | 99.2338 | 51.7544 | 49.9225
| 202.076 | 198.4675 | 51.462 | 49.6405
| 303.114 | 297.7013 | 51.1696 | 49.3584
| 402.768 | 395.5757 | 50.7797 | 48.9823
| 517.647 | 508.4033 | 50.3899 | 48.6063
| 613.149 | 602.1999 | 49.9025 | 48.1362
| 705.882 | 693.277 | 49.3177 | 47.5721
| 798.616 | 784.355 | 48.538 | 46.82
| 901.038 | 884.948 | 47.271 | 45.5978
| 997.924 | 980.1039 | 45.2242 | 43.6235
| 1100.35 | 1080.7009 | 42.2027 | 40.7089
| 1200 | 1178.5714 | 38.3041 | 36.9483
| 1301.04 | 1277.8071 | 33.8207 | 32.6236
| 1402.08 | 1377.0429 | 28.8499 | 27.8287
| 1478.2 | 1451.8036 | 24.3665 | 23.504
Step 4 - Plot the results (the cells highlighted in yellow above) on the pump curve