## Instructions
Control System Object Name Structure and Convention Overview
This spreadsheet is intended to support the control system design process starting during schematic design and design development when the points required by the system are initially selected. This information can be used to build a per point cost based budget and also to build the formal point list for the project. The drop down menus in the working portion of the spreadsheet reference the abbreviations contained in the tabs that define the drop-down lists to allow the user to build the point names using the Owners specific naming convention. This specific point list has been set up based on FDE's Object naming standard as outlined in the Siemens Master Specification for the City of Seattle that was developed by Scooter in May of 2018 (Note 1). The details of that convention are documented at the top of the Point Nam Builder tab and set up the point names on that basis. The general convention used for point naming via this tool has its roots in the Kraftwerk-Kennzeichen-System (KKS) convention. This, in turn appears to be associated with an international technical association for generation and storage of power and heat named VGB PowerTech e.V. There are also some similarities to the ISA convention associated with the ISA-5.1 standard.
Click here to go to more information about the KKS convention
Click here to go to more information about ISA 5.1.
The general format for the point names created by this tool is a string of all caps abbreviations with seperator characters (underlines, periods, etc.) between them to make the resulting point name less cryptic. This could also be accomplished without seperators by using upper and lower case letters. However, some control systems will not support upper and lower case letters, so the conservative approach is to use all capitals and seperators, even though the seperators take up a space in the total character count that could otherwise be used to provide a less cryptic point name. The total character count is a hard limit that can not be exceeded and is typically set by the specific requirements of the control system vendor and their point data base convention. The target character counts for each segment are soft limits. The intent is to allow flexibility in terms of trading shorter abbreviations for the location, system, and subsystem segments for more detail in the device descriptor segment on a point by point basis, but also allow flexibility going the other way if more length is required for the other segments. Most of the time, the number of characters targeted for a given segment represent a trade-off between how cryptic and specific the location segments will be vs. the level of detail you can provide in the other segments. For instance, if you needed to reference a department as well as a building name along with a floor level and room in the location segment because the person monitoring the facility from a central location is also monitoring 10's if not 100's of other facilities and needs the point name to convey that information in addition to the point specifics, then it would likely take more characters for the location segment than if you had a situation were you only needed to reference a floor or room because there was only one building and one operating group involved. For example, if you needed to reference the second floor mechanical space in the Public Works Department's Street Maintenance Division's South Operations Center the location segment might end up looking like PW_SM_SOC_02_M for Public Works Street Maintenance South Operations Center Level 2 Mechancial Room. That would use up about half of the available characters and as a result, the rest of the point name would need to be much more cryptic. But if you only needed the point name to reference the floor and room, for instance 02_M for Level 2 Mechanical Room, then you would have much more flexibiltiy for the remaining segments in terms of describing the point completely. Ultimately, having a consistent, flexible standard in place for a given facility and operating group will have long term benefits and also long term implications for and facility expansions or additions that come up in the future. Thus, spending some time developing the initial standard can be time well spent. One of the benefits of this point list tool is that it allows you to "play" with different combinations of abbreviations to visualize how different naming strategies will look once implemented.

## Point Name Builder
Control System Object Name Structure General Conventions
The table below is used to set up the general structure for object names. Once these conventions are set, they will be the same for each system in the project and are referenced by the next table, which will be specific to each system on the project.
Jump to the System Specific Object Name Structure (the working point name generator)
Number of segments for a complete point name |  |  | 4 | ◄ Note 2
Maximum number of characters |  |  | 30 | 30 | ◄ Note 3, 11
Segment functions |  |  |  | Location Segment | System Segment | Subsystem/Component Segment | Device Descriptor Segment
Target character count for the segment, including the seperator character(s) |  |  |  | 7 | 7 | 8 | 8 | ◄ Note 2, 11, 13
Acceptable characters |  |  |  | LETTER, Number, Seperator | LETTER, Number, Seperator | LETTER, Number, Seperator | LETTER, Number, Seperator
Segment functions |  |  | Segment Function | This segment is intended to designate the location of a control system object. For example the Coad Engineering Research Center might be called COAD_ER | This segment is intended to designate the system containing the object associated with the name. For example, a building might have a chilled water system, an air handling system, a hot water system, an electrical system, etc. | This segment specifies the subsystem or component associated with the object. For instance, a hot water system might have pumps, heat exchantgers, control valves, boilers, etc. | This segment designates the specific device associated with the object. For instance, the pump serving a hot water system might have a start/stop point, a proof of operation point, a speed command point, and a speed feedback point.
Applicable notes |  |  |  | 4, 8, 9, 10, 12, 13 | 8, 9, 10, 12, 13 | 5, 6, 8, 9, 10, 12, 13 | 6, 7, 8, 9, 10, 12, 13
Notes:
1 | This red text should be replaced with a project specific description.
2 | If you want to have a different number of segments, in the current version of the tool, you would need to edit the spreadsheet to create them. Similarly, if you wanted to be able to use more than two descriptors to build the location segment, more than two descriptors and a letter or number to build the subsystem/component segment, or more than four descriptors and a letter o number to build the descriptor segment, then you would need to edit the spreadsheet to create them.
3 | The desired maximum character count is manually entered in the white cell with the red boarder and is referenced by the various formulas in the spreadsheet that count characters in a given point name. The number in the adjacent cell reflects the total for target character counts per segment entered below. The color will change from green to orange as the total approaches the character limit you enter. It will turn to red if the target counts you have entered exceed the limit.
4 | This segment can include two location descriptors strung together as needed to fully describe the object with-in the constraints of the maximum character count allowed. Each descriptor needs to be followed by a seperator character.
5 | This segment can include two location descriptors and a letter or number strung together as needed to fully describe the object with-in the constraints of the maximum character count allowed. Each descriptor needs to be followed by a seperator character.
6 | The letter/number field provide some flexibility in terms of making a custom descriptor using something that is not included in the standard dropdown selections.
7 | This segment can include four location descriptors and a letter or number strung together as needed to fully describe the object with-in the constraints of the maximum character count allowed. Each descriptor other than the last one needs to be followed by a seperator character.
8 | Avoid using upper case "O" (the letter O) to avoid confusion with "0" (the number zero).
9 | Avoid using upper case "I" (the letter I) to avoid confusion with 1 (the number one).
10 | Use leading zeros for numbered items with similar prefixes to ensure they sort in numerical order. No leading zero is required if you only anticipate 10 or fewer objects with a similar prefix. If you anticpate fewer than 100 objects with a similar prefix use one leading zero. If you anticipate fewer than 1,000 objects with a similar prefix, use two leading zeros. For example in a facility with 12 air handling units use AHU01, AHU02, ... AHU10, AHU11, AHU12 instead of AHU1, AHU2, ... AHU 10, AHU11, AHU12.
11 | Names may use less than the maximum number of allowable characters for a given segment. In addition the number of characters in a segment can exceed the target for the segment as long as the total character count is less than the maximum allowable character count.
12 | Use an appostrophe ahead of any numeric values so they are interpreted as text and allow the other formulas to work; i.e. enter'01 vs. 01
13 | The formulas that build the point names place a seperator after each descriptor. That means that for segments built from two or more descriptors, there will be two or more seperators included in the character count. Note that the final descriptor in the Device Descriptor segment does not have a seperator after it. This should be reflected in the target character count for that segment.
System Specific Control System Object Name Structure
The table below is used to set up the structure for object names for the system associated with this tab in the spreadsheet. Each system should have its own tab and the values will be different for each system.
The full object name is the composed of the building and system segments which are set up in the table below plus the subsystem and device descriptor segments associated with each point in the system, which are set up in the subsequent table. The maximum character count is 30 characters. Both tables contain a cell that indicates the current character count, which automatically totals up the characters associated with your selection and goes from green to orange as you approach the limite. It turns red if you exceed the limit. The limit that matters the most is the limit indicated for each point name since you can trade longer location and system segments for shorter subsystem/component and descriptor segments as long as the hard maximum character segment total is not exceeded.
Jump to the General Object Name Structure
Jump to the "Instructions" tab
|  | System Name - | Roof Level |  | Assembled from selections |  |  |  | Target Characters | Actual Characters
|  | Object Name - Location and System Segments - | RF_ |  | Assembled from selections | Abbreviation | Description | Links to Lists | 14 | 3
|  | Seperator Character - | Underline |  | From drop down menu | _ | Underline | Seperator List | 1 | 1
|  | Building/Location Segment Part 1 Selection - | Roof Level |  | From drop down menu; both reference the same list | RF | Roof Level | Location List | 7 | 3
|  | Building/Location Segment Part 2 Selection - | Top of list
|  | System Segment Selection - | Top of list |  | From drop down menu | 0 | 0 | System List | 7 | 2
|  | System Number - |  |  | Manual Entry
Point Name Generator
The table below is used to set up the specific point name structure for each point on the point list. Filling it out also starts to populate the project point list and the project budget point list (to the right).
Character Count | Subsystem/Component Segment (Select at least one) |  |  | Descriptor Segment (Select at least one) |  |  |  |  | Full point object names and descriptive name
| Subsystem/Component List |  |  | Descriptor List
Target ► | Target total = 8 with seperators |  |  | Target total = 8 with seperators
Total for the point with all segments and seperators (red means the maximum count is exceeded) ▼ | System | System | Number (Optional) | Descriptor 1 | Descriptor 2 | Descriptor 3 | Descriptor 4 | Number (Optional)
| Select using the drop down list for each point | Select using the drop down list for each point | Manually enter a number or text. Use an appostrophe ahead of the entry so it is interpreted as text and allow the other formulas to work; i.e. enter'01 vs. 01 | Select using the drop down list for each point | Select using the drop down list for each point | Select using the drop down list for each point | Select using the drop down list for each point | 1
32 | BACnet - York BACnet | Coil - Direct Expansion |  | Supply | Air | Temperature | Top of list | 1
[8 empty] | Point Object Name - | RF_YKBACNET_DXCOIL_SUP_AIR_TEMP1
[8 empty] | Point Descriptor - | Roof Level York RTU BACnet Direct Expansion Coil Supply Air Temperature 1
EXAMPLES
[7 empty] | Point Object Name |  | Point Descriptor
0

## Seperators
Seperator Selections
Top of list
Underline | _ | (Underline)
Bottom of list
Note
Insert or delete rows between the highlighted rows to have them show up automatically
Revision History
| Created | 2018-04-20 18:01
| Rev 1 | 2018-04-20 18:01
| Rev 2 | 3/26/2020 - Edited to UCOP Standard

## Location Seg 1 and 2
Selection Text and Description Text | Abbreviation
Target Character Count
Seperator
Top of list
01 - 1st Floor | 1ST | 1st Floor
02 - 2nd Floor | 2ND | 2nd Floor
03 - 3rd Floor | 3RD | 3rd Floor
04 - 4th Floor | 4TH | 4th Floor
BACnet | BACNET | BACnet
BACnet - York BACnet | YkBACnet | York RTU BACnet
Blank
Building -UCPath Center | PC | UCPath Center
Central | CNT | Central
Central Plant - CPLT | CPLT | Central Plant
Central Plant - CPLNT | CPLNT | Central Plant
Central Plant - CNPLNT | CNPLNT | Central Plant
Central Plant - CNTPLNT | CNTPLNT | Central Plant
Chilled Water | CHW | Chilled Water
Chilled Water Plant | CHWP | Chilled Water Plant
Column Line .5A-1 | A.5-1 | Column Line A.5-1
Column Line .5A-10 | A.5-10 | Column Line A.5-10
Column Line .5A-11 | A.5-11 | Column Line A.5-11
Column Line .5A-12 | A.5-12 | Column Line A.5-12
Column Line .5A-13 | A.5-13 | Column Line A.5-13
Column Line .5A-14 | A.5-14 | Column Line A.5-14
Column Line .5A-15 | A.5-15 | Column Line A.5-15
Column Line .5A-16 | A.5-16 | Column Line A.5-16
Column Line .5A-2 | A.5-2 | Column Line A.5-2
Column Line .5A-3 | A.5-3 | Column Line A.5-3
Column Line .5A-4 | A.5-4 | Column Line A.5-4
Column Line .5A-5 | A.5-5 | Column Line A.5-5
Column Line .5A-6 | A.5-6 | Column Line A.5-6
Column Line .5A-7 | A.5-7 | Column Line A.5-7
Column Line .5A-8 | A.5-8 | Column Line A.5-8
Column Line .5A-9 | A.5-9 | Column Line A.5-9
Column Line A-1 | A-1 | Column Line A-1
Column Line A-10 | A-10 | Column Line A-10
Column Line A-11 | A-11 | Column Line A-11
Column Line A-12 | A-12 | Column Line A-12
Column Line A-13 | A-13 | Column Line A-13
Column Line A-14 | A-14 | Column Line A-14
Column Line A-15 | A-15 | Column Line A-15
Column Line A-16 | A-16 | Column Line A-16
Column Line A-2 | A-2 | Column Line A-2
Column Line A-3 | A-3 | Column Line A-3
Column Line A-4 | A-4 | Column Line A-4
Column Line A-5 | A-5 | Column Line A-5
Column Line A-6 | A-6 | Column Line A-6
Column Line A-7 | A-7 | Column Line A-7
Column Line A-8 | A-8 | Column Line A-8
Column Line A-9 | A-9 | Column Line A-9
Column Line B-1 | B-1 | Column Line B-1
Column Line B-10 | B-10 | Column Line B-10
Column Line B-11 | B-11 | Column Line B-11
Column Line B-12 | B-12 | Column Line B-12
Column Line B-13 | B-13 | Column Line B-13
Column Line B-14 | B-14 | Column Line B-14
Column Line B-15 | B-15 | Column Line B-15
Column Line B-16 | B-16 | Column Line B-16
Column Line B-2 | B-2 | Column Line B-2
Column Line B-3 | B-3 | Column Line B-3
Column Line B-4 | B-4 | Column Line B-4
Column Line B-5 | B-5 | Column Line B-5
Column Line B-6 | B-6 | Column Line B-6
Column Line B-7 | B-7 | Column Line B-7
Column Line B-8 | B-8 | Column Line B-8
Column Line B-9 | B-9 | Column Line B-9
Column Line C-1 | C-1 | Column Line C-1
Column Line C-10 | C-10 | Column Line C-10
Column Line C-11 | C-11 | Column Line C-11
Column Line C-12 | C-12 | Column Line C-12
Column Line C-13 | C-13 | Column Line C-13
Column Line C-14 | C-14 | Column Line C-14
Column Line C-15 | C-15 | Column Line C-15
Column Line C-16 | C-16 | Column Line C-16
Column Line C-2 | C-2 | Column Line C-2
Column Line C-3 | C-3 | Column Line C-3
Column Line C-4 | C-4 | Column Line C-4
Column Line C-5 | C-5 | Column Line C-5
Column Line C-6 | C-6 | Column Line C-6
Column Line C-7 | C-7 | Column Line C-7
Column Line C-8 | C-8 | Column Line C-8
Column Line C-9 | C-9 | Column Line C-9
Column Line D-1 | D-1 | Column Line D-1
Column Line D-10 | D-10 | Column Line D-10
Column Line D-11 | D-11 | Column Line D-11
Column Line D-12 | D-12 | Column Line D-12
Column Line D-13 | D-13 | Column Line D-13
Column Line D-14 | D-14 | Column Line D-14
Column Line D-15 | D-15 | Column Line D-15
Column Line D-16 | D-16 | Column Line D-16
Column Line D-2 | D-2 | Column Line D-2
Column Line D-3 | D-3 | Column Line D-3
Column Line D-4 | D-4 | Column Line D-4
Column Line D-5 | D-5 | Column Line D-5
Column Line D-6 | D-6 | Column Line D-6
Column Line D-7 | D-7 | Column Line D-7
Column Line D-8 | D-8 | Column Line D-8
Column Line D-9 | D-9 | Column Line D-9
Column Line E-1 | E-1 | Column Line E-1
Column Line E-10 | E-10 | Column Line E-10
Column Line E-11 | E-11 | Column Line E-11
Column Line E-12 | E-12 | Column Line E-12
Column Line E-13 | E-13 | Column Line E-13
Column Line E-14 | E-14 | Column Line E-14
Column Line E-15 | E-15 | Column Line E-15
Column Line E-16 | E-16 | Column Line E-16
Column Line E-2 | E-2 | Column Line E-2
Column Line E-3 | E-3 | Column Line E-3
Column Line E-4 | E-4 | Column Line E-4
Column Line E-5 | E-5 | Column Line E-5
Column Line E-6 | E-6 | Column Line E-6
Column Line E-7 | E-7 | Column Line E-7
Column Line E-8 | E-8 | Column Line E-8
Column Line E-9 | E-9 | Column Line E-9
Column Line F-1 | F-1 | Column Line F-1
Column Line F-10 | F-10 | Column Line F-10
Column Line F-11 | F-11 | Column Line F-11
Column Line F-12 | F-12 | Column Line F-12
Column Line F-13 | F-13 | Column Line F-13
Column Line F-14 | F-14 | Column Line F-14
Column Line F-15 | F-15 | Column Line F-15
Column Line F-16 | F-16 | Column Line F-16
Column Line F-2 | F-2 | Column Line F-2
Column Line F-3 | F-3 | Column Line F-3
Column Line F-4 | F-4 | Column Line F-4
Column Line F-5 | F-5 | Column Line F-5
Column Line F-6 | F-6 | Column Line F-6
Column Line F-7 | F-7 | Column Line F-7
Column Line F-8 | F-8 | Column Line F-8
Column Line F-9 | F-9 | Column Line F-9
Column Line .5G-1 | G.5-1 | Column Line G.5-1
Column Line .5G-10 | G.5-10 | Column Line G.5-10
Column Line .5G-11 | G.5-11 | Column Line G.5-11
Column Line .5G-12 | G.5-12 | Column Line G.5-12
Column Line .5G-13 | G.5-13 | Column Line G.5-13
Column Line .5G-14 | G.5-14 | Column Line G.5-14
Column Line .5G-15 | G.5-15 | Column Line G.5-15
Column Line .5G-16 | G.5-16 | Column Line G.5-16
Column Line .5G-2 | G.5-2 | Column Line G.5-2
Column Line .5G-3 | G.5-3 | Column Line G.5-3
Column Line .5G-4 | G.5-4 | Column Line G.5-4
Column Line .5G-5 | G.5-5 | Column Line G.5-5
Column Line .5G-6 | G.5-6 | Column Line G.5-6
Column Line .5G-7 | G.5-7 | Column Line G.5-7
Column Line .5G-8 | G.5-8 | Column Line G.5-8
Column Line .5G-9 | G.5-9 | Column Line G.5-9
Column Line G-1 | G-1 | Column Line G-1
Column Line G-10 | G-10 | Column Line G-10
Column Line G-11 | G-11 | Column Line G-11
Column Line G-12 | G-12 | Column Line G-12
Column Line G-13 | G-13 | Column Line G-13
Column Line G-14 | G-14 | Column Line G-14
Column Line G-15 | G-15 | Column Line G-15
Column Line G-16 | G-16 | Column Line G-16
Column Line G-2 | G-2 | Column Line G-2
Column Line G-3 | G-3 | Column Line G-3
Column Line G-4 | G-4 | Column Line G-4
Column Line G-5 | G-5 | Column Line G-5
Column Line G-6 | G-6 | Column Line G-6
Column Line G-7 | G-7 | Column Line G-7
Column Line G-8 | G-8 | Column Line G-8
Column Line G-9 | G-9 | Column Line G-9
Column Line H-1 | H-1 | Column Line H-1
Column Line H-10 | H-10 | Column Line H-10
Column Line H-11 | H-11 | Column Line H-11
Column Line H-12 | H-12 | Column Line H-12
Column Line H-13 | H-13 | Column Line H-13
Column Line H-14 | H-14 | Column Line H-14
Column Line H-15 | H-15 | Column Line H-15
Column Line H-16 | H-16 | Column Line H-16
Column Line H-2 | H-2 | Column Line H-2
Column Line H-3 | H-3 | Column Line H-3
Column Line H-4 | H-4 | Column Line H-4
Column Line H-5 | H-5 | Column Line H-5
Column Line H-6 | H-6 | Column Line H-6
Column Line H-7 | H-7 | Column Line H-7
Column Line H-8 | H-8 | Column Line H-8
Column Line H-9 | H-9 | Column Line H-9
Electrical (E) | E | Electrical
Electrical (EL) | EL | Electrical
Electrical (ELEC) | ELEC | Electrical
Emergency | EM | Emergency Generator Room
Exterior | EXT | Exterior
Generator | GEN | Emergency Generator Room
Hot Water | HW | Hot Water Plant
Hot Water Plant | HWP | Hot Water Plant
Interior | INT | Interior
Landscape (LS) | LS | Landscape
Lobby | LOB | Lobby
Mechanical (M) | M | Mechanical Room
Mezzanine | MEZ | Mezzanine
Outside | OUTSD | Outside
Parking Lot (PKLT) | PKLT | Parking Lot
Roof Level | RF | Roof Level
Room | RM | Room
Site (SITE) | SITE | Site
Switch Gear | SG | Switch Gear Room
Bottom of list
Revision History
| Created | 2018-04-20 18:01
| Rev 1 | 2018-04-20 18:01
| Rev 2 | 3/26/2020 - Edited to UCOP Standard

## System Level List
Jump to Revision History
Selection Text | Abbreviation | Description Text
Top of list
Air | AIR | Air | Insert or Delete Rows to Add or Delete Systems by Inserting Them Between the Higlighted Rows
Air Handling - Air Handling Unit | AHU | Air Handling Unit
Air Handling - Roof Top Unit | RTU | Roof Top Unit
Air Side | RTU_A | Roof Top Unit Air Side
Building System | BLD | Building System
Building Wide | BLD-WD | Building Wide
Cabinet Unit Heater | CUH | Cabinet Unit Heater
Computer Room Unit | CRU | Computer Room Unit
Condensate | CND | Condensate
Control | CTR | Control
Control - Field Panel Resident Objects | PNL | Field Panel
Control - Floor Level Network | FLN | Floor Level Network
Cooling | CLG | Cooling
Direct Expansion | DX | Direct Expansion
Domestic Cold Water | DCW | Domestic Cold Water
Domestic Hot Water | DHW | Domestic Hot Water
Dx System | RTU_R | Roof Top Unit Refrigeration System
Electrical | ELEC | Electrical System
Emergency Power | EPWR | Emergency Power System
Exhaust System | EXH | Exhaust System
External Shades | EXTSHD | External Shades
Fan System | FAN | Fan System
Fire Alarm System | FA | Fire Alarm System
Furnace | FRNC | Furnace
Heating System | HTGSYS | Heating System
Lighting System | LT | Lighting System
Make-up Air System | MAU | Make-up Air System
Master | MSTR | Master
Metering System | MTR | Metering System
Natural Gas System | GAS | Natural Gas System
Remote Control | REMOTE | Remote Control
Room | ROOM | Room
Security Systems | SEC | Security Systems
Site Wide Applicable Data | SITE | Site Wide
Split System | SPS | Split System
Sprinkler System | SPR | Sprinkler System
Sump Pump System | SMP | Sump Pump System
Tennant Loads | TEN | Tennant
Variable Flow Refrigeration System | VRF | Variable Flow Refrigeration System
Variable Flow Refrigeration System Indoor Unit | VRFIDU | VRF Indoor Unit
Variable Flow Refrigeration System Outdoor Unit | VRFODU | VRF Outdoor Unit
Water Side | RTU_W | Roof Top Unit Water Side
Bottom of list
| Revision History | Back to Top
| Created | 2018-01-01 13:14
| Rev 1 | 2018-04-20 18:01
| Rev 2 | 3/26/2020 - Edited to UCOP Standard

## Component Lvl List
Jump to Revision History
Selection Text | Abbreviation | Description Text
Top of list
Air | AIR | Air | Insert or Delete Rows to Add or Delete Subsystems by Inserting Them Between the Higlighted Rows
Alarm | ALRM | Alarm
Back Flow Preventer | BFP | Back Flow Preventer
BACnet | BACNET | BACnet
BACnet - York BACnet | YKBACNET | York RTU BACnet
Building | BLDG | Building
Building System | BLD | Building System
Building Wide | BLD-WD | Building Wide
Bypass | BYPAS | Bypass
Cabinet Unit Heater | CUH | Cabinet Unit Heater
Coil - Direct Expansion | DXCOIL | Direct Expansion Coil
Coil - Reheat | RHCOIL | Reheat Coil
Compressor | CMP | Compressor
Condenser | CND | Condenser
Condenser - Air Cooled | ACCOND | Air Cooled Condenser
Condensing Unit - Air Cooled | ACCDU | Air Cooled Condensing Unit
Cooling | CLG | Cooling
Crankcase | CRKCS | Crankcase
Crankcase Heater | CCHTR | Crankcase Heater
Diagnostic | DIAG | Diagnostic
Direction - 01 - Left | LFT | Left
Direction - 02 - Right | RT | Right
Direction - 03 - Upper | UPR | Upper
Direction - 04 - Lower | LWR | Lower
Direction - 05 - Upper Middle | UPRMDL | Upper Middle
Direction - 05 - Upper Right | UPRRT | Upper Right
Direction - 07 - Upper Left | UPRLFT | Upper Left
Direction - 08 - Lower Right | LWRRT | Lower Right
Direction - 09 - Lower Middle | LWRMDL | Lower Middle
Direction - 10 - Lower Left | LWRLFT | Lower Left
Direction - 11 - Middle | MDL | Middle
Direction - 12 - North | N | North
Direction - 12 - Upper Middle | UPRMDL | Upper Middle
Direction - 13 - Middle, Center | CNTR | Center
Direction - 13 North East | NE | North East
Direction - 14 - East | E | East
Direction - 14 - Lower Middle | LWRMDL | Lower Middle
Direction - 15 - South East | SE | South East
Direction - 16 - South | S | South
Direction - 17 - South West | SW | South West
Direction - 18 - West | W | West
Direction - 19 - North West | NW | North West
Discharge | DSCHG | Discharge
Distribution | DST | Distribution
Duct | DUCT | Duct |  | Dschg
Economizer | ECON | Economizer
Electric Duct Heater | EDH | Electric Duct Heater
Electrical System | KW | Electrical System
Emergency Generator | EMGEN | Emergency Generator
Entering | ENT | Entering
Exhaust | EXH | Exhaust
Exhaust - Exhaust Side | EXHSD | Exhaust Side
Fan | FAN | Fan
Filter | FLTR | Filter
Filter - Final | FNFLT | Final Filter
Filter - Prefilter | PRFLT | Prefilter
Fire Alarm | FIRALM | Fire Alarm
Flame | FLM | Flame
Flexsys | FLEX | York Flexsys
Floor Level Network | FLN | Floor Level Network
Freeze Protection | FZPR | Freeze Protection
Furnace - Gas | GSFRNC | Gas Furnace
Generator | GEN | Generator
Header | HDR | Header
Heater | HTR | Heater
Heating | HTG | Heating
Indoor Unit | IDU | Indoor Unit
Inlet | INLET | Inlet
Leaving | LVG | Leaving
Lighting | LGHT | Lighting
Lighting Panel | LGTPN | Lighting Panel
Lock-out | LKOT | Lock-out
Make-up | MKUP | Make-up
Metering System | MTR | Metering System
Mixed | MIX | Mixed
Outdoor | OUTDR | Outdoor
Outdoor Unit | ODU | Outdoor Unit
Override | OVR | Override
Pump | PMP | Pump
Pump - Domestic Hot Water | DHPMP | Domestic Hot Water Pump
Pump - Sump | SMPPMP | Sump Pump
Pump - Vacuum Condensate Type | VACPMP | Vacuum Condensate Pump
Recirculation | RECIR | Recirculation
Refrigeration | REF | Refrigeration
Relief | REL | Relief
Return | RTRN | Return
Reverse Cycle | REV | Reverse Cycle
Room | ROOM | Room
Security | SEC | Security
Siemens Field Panel Resident Objects | PNL | Siemens Field Panel Object
Site | SITE | Site
Sprinkler | SPR | Sprinkler
Supply | SUP | Supply
Supply - Supply Side | SUPSD | Supply Side
System | SYSTM | System
Tank | TNK | Tank
Terminal Unit - Terminal Equipment Controller | TEC | Terminal Unit - Terminal Equipment Controller
Terminal Unit - Under Floor FTU | UFT | Under Floor Fan Terminal
Terminal Unit - Variable Air Volume Floor Diffusser | VAVFD | Variable Air Volume Floor Diffusser
Trigger | TRGR | Trigger
Under Floor Air Distribution | UFLR | Under Floor Air Distribution
Unit | UNIT | Unit
Unit Heater | UH | Unit Heater
Variable Speed Drive | VSD | Variable Speed Drive
Vent Stack | VNTSTK | Vent Stack
Ventilation | VNT | Ventilation
Water | WTR | Water
York RTU | YORK | York RTU
Zone | ZN | Zone
Bottom of list
Revision History
| Created | 2018-04-20 18:01
| Rev 1 | 2018-04-20 18:01
| Rev 2 | 3/26/2020 - Edited to UCOP Standard

## Device Descriptor List
Jump to Revision History
Selection Text | Abbreviation | Description Text
Top of list
Adjustment | ADJ | Adjustment | Insert or Delete Rows to Add or Delete Subsystems by Inserting Them Between the Higlighted Rows
Air | AIR | Air
Air Flow Measuring Station | AFM | Air Flow Measuring Station
Alarm | ALM | Alarm
Automation Level Network | ALN | Automation Level Network
Average | AVG | Average
Back Flow Preventer | BFP | Back Flow Preventer
BACnet | BACNET | BACnet
BACnet - York BACnet | YkBACnet | York RTU BACnet
Blow-down | BLODWN | Blow-down
British Thermal Unit | BTU | BTU
Building | BLDG | Building
Building Level Network | BLN | Building Level Network
Building System | BLD | Building System
Building Wide | BLD-WD | Building Wide
Burner | BRNR | Burner
Bypass | BYPAS | Bypass
Close | CLS | Close
Coil - Direct Expansion | DXCOIL | Direct Expansion Coil
Coil - Reheat | RHCOIL | Reheat Coil
Cold | COLD | Cold
Combustion | COMB | Combustion
Command | CMND | Command
Compressor | CMP | Compressor
Condenser | CND | Condenser
Condenser - Air Cooled | ACCOND | Air Cooled Condenser
Condensing Unit - Air Cooled | ACCDU | Air Cooled Condensing Unit
Controller | CNTRL | Controller
Cooling | CLG | Cooling
Counter | CNTR | Counter
Counter - Pulse Accumulator | PLSCNTR | Pulse Counter
Counter - Run Time Accumulator | RUNTM | Run Time Accumulator
Crankcase | CRKCS | Crankcase
Cubic Feet per Minute | CFM | CFM
Cycle | CYCLE | Cycle
Damper | DMPR | Damper
Deviation | DEV | Deviation
Dew Point | DEWPT | Dew Point Temperature
Diagnostic | DIAG | Diagnostic
Differential | DIFF | Differential
Diffuser | DIFF | Diffuser
Direction - 01 - Left | LFT | Left
Direction - 02 - Center | CENTR | Center
Direction - 03 - Right | RT | Right
Direction - 04 - Upper | UPR | Upper
Direction - 05 - Middle | MDL | Middle
Direction - 06 - Lower | LWR | Lower
Direction - 12 - North | N | North
Direction - 13 North East | NE | North East
Direction - 14 - East | E | East
Direction - 15 - South East | SE | South East
Direction - 16 - South | S | South
Direction - 17 - South West | SW | South West
Direction - 18 - West | W | West
Direction - 19 - North West | NW | North West
Direction - 20 - Up | UP | Up
Direction - 21 - Down | DN | Down
Disable | DISABLE | Disable
Discharge | DSCHG | Discharge
Distribution | DST | Distribution
Diverting | DIV | Diverting
Domestic Hot Water | DHW | Domestic Hot Water
Downstream | DNSTRM | Downstream
Drain | DRN | Drain
Duct | DUCT | Duct
Duration | DUR | Duration
Duty Cycle | CYCL | Duty Cycle
Economizer | ECON | Economizer
Electric Duct Heater | EDH | Electric Duct Heater
Electrical - A Phase | APH | A Phase
Electrical - B Phase | BPH | B Phase
Electrical - Battery | BAT | Battery
Electrical - C Phase | CPH | C Phase
Electrical - Current | CUR | Current
Electrical - Ground | GND | Ground
Electrical - Inverter | INVTR | Inverter
Electrical - kW | KW | kW
Electrical - kWh | KWH | kWh
Electrical - Neutral | NEU | Neutral
Electrical - Phase Angle | PHANG | Phase Angle
Electrical - Photovoltaic | PV | Photovoltaic
Electrical - Voltage | VLT | Voltage
Electrical System | KW | Electrical System
Emergency Generator | EMGEN | Emergency Generator
Enable | ENABLE | Enable
Entering | ENT | Entering
Enthalpy | ENTH | Enthalpy
Evaporator | EVAP | Evaporator
Exhaust | EXH | Exhaust
Exhaust | EXH | Exhaust
Exhaust - Exhaust Side | EXHSD | Exhaust Side
Exhaust - Exhaust Side | EXHSD | Exhaust Side
External | EXT | External
Face | FACE | Face
Fan | FAN | Fan
Fault | FAULT | Fault
Feedback | FBK | Feedback
Fill | FILL | Fill
Filter | FLTR | Filter
Filter - Final | FNFLT | Final Filter
Filter - Prefilter | PRFLT | Prefilter
Fire | FIRe | Fire
Fire Alarm | FIRALM | Fire Alarm
Flame | FLM | Flame
Flexsys | FLEX | York Flexsys
Floor Level Network | FLN | Floor Level Network
Flow (Water or Air) | FLW | Flow
Flue | FLU | Flue
Freeze Protection | FRZPRT | Freeze Protection
Frequency | FRQ | Frequency
Furnace - Gas | GSFRNC | Gas Furnace
Gain - Derivative | DG | Derivative Gain
Gain - Integral | IG | Integral Gain
Gain - Loop Off Value | OFF | Loop Off Value
Gain - Proportional | PG | Proportional Gain
Gallons per Minute | GPM | GPM
Gas - Carbon Dioxide | CO2 | Carbon Dioxide
Gas - Carbon Monoxide | CO | Carbon Monoxide
Gas - Natural Gas | NG | Natural Gas
General | GENRL | General
Generator | GEN | Generator
Head | HD | Head
Header | HDR | Header
Heater | HTR | Heater
Heating | HTG | Heating
High | HIGH | High
Hot | HOT | Hot
Hot Gas | HOTGAS | Hot Gas
Humidity | HUM | Humidity
Indication | IND | Indication
Indoor Unit | IDU | Indoor Unit
Inlet | INLET | Inlet
Internal | INT | Internal
Irradiance | IRRDNC | Irradiance
Isolation | ISO | Isolation
Latch Off | LCHOFF | Latch Off
Latch On | LCHON | Latch On
Leaving | LVNG | Leaving
Level | LVL | Level
Level Switch | LVLSW | Level Switch
Light | LGHT | Light
Lighting | LGHT | Lighting
Lighting Panel | LGTPN | Lighting Panel
Lights | LGHT | Lights
Limit - High Limit | HILMT | High Limit
Limit - Low Limit | LOLMT | Low Limit
Lock-out | LKOUT | Lock-out
Loop - Control Loop | CTRLLP | Control Loop
Loop - Off state value | OFFVLU | Loop Off State Value
Loop - P Only | PLP | P Only Loop
Loop - PI | PILP | P+I Loop
Loop - PID | PIDLP | PID Loop
Low | LOW | Low
Magnetic Door Lock | DOORLK | Magnetic Door Lock
Make-up | MKUP | Make-up
Manual | MAN | Manual
Manual Reset | MR | Manual Reset
Maximum | MAX | Maximum
Meter | MTR | Meter
Minimum | MIN | Minimum
Mixed | MIX | Mix
Modulation | MOD | Modulation
Motor | MTR | Motor
Network | NTWK | Network
Network - Internet Access | IPNTWK | Internet Access
Occupied | OCC | Occupied
Off | OFF | Off
Oil | OIL | Oil
On | ON | On
On Power Return Point (Changes state when power returns) | ONPWRT | Power Failure Recovery Trigger
On/Off | ON/OFF | On/Off
Open | OPN | Open
Outdoor | OUTDR | Outdoor
Overload | OL | Motor Overload
Overload (Manual Reset) | OL_MR | Overload (Manual Reset)
Override | OVR | Override
Override - 01 - Down | OVRDN | Override Up
Override - 02 - Up | OVRUP | Override Down
Override - 03 - On | OVRON | Override On
Override - 04 - Off | OVROFF | Override Off
Parts per Million | PPM | PPM
Placeholder | PLHLDR | Placeholder
Point | PNT | Point
Power | PWR | Power
Power Failure | PWRFAIL | Power Failure
Pressure | PRESS | Pressure
Proof | PRF | Proof
Pump | PMP | Pump
Recirculation | RECIR | Recirculation
Refrigerant | REF | Refrigerant
Refrigeration | REF | Refrigeration
Relay | RLY | Relay
Relief | RELF | Relief
Request | RQST | Request
Reset | RSET | Reset
Reset - Input Lower Limit | RSETILO | Reset Lo Lmt.
Reset - Input Upper Limit | RSETIHI | Reset Hi Lmt.
Reset - Output - Lower Limit | RSETOLO | Reset Lo Lmt.
Reset - Output - Upper Limit | RSETOHI | Reset Hi Lmt.
Reset - Remote | RMRSET | Remote Reset
Return | RTRN | Return
Reverse | REV | Reverse
Room | ROOM | Room
Security | SEC | Security
Sensor | SNSR | Sensor
Sensor - Field Installed Factory Control Sensor | FLDSNSR | Field Installed Factory Control Sensor
Separator | SEP | Separator
Set Point | SP | Set Point
Siemens Field Panel Resident Objects | PNL | Siemens Field Panel Object
Silicon Controlled Rectifier | SCR | Silicon Controlled Rectifier
Site | SITE | Site
Smoke | SMK | Smoke
Smoke and Fire | SMKFIRE | Smoke and Fire
Smoke Detector | SMKDT | Smoke Detector
Solar - 01 - Azimuth | SOLAZ | Azimuth
Solar - 02 - Declination | SOLDEC | Declination
Solar - 03 - Elevation | SOLELV | Elevation
Solar - 04 - Equation of Time | SOLEOT | Equation of Time
Solar - 05 - Latitude | SOLLAT | Latitude
Solar - 06 - Longitude | SOLLNG | Longitude
Solar - 07 - Time Zone | TMZN | Time Zone
Space | SPC | Space
Speed | SPD | Speed
Sprinkler | SPR | Sprinkler
Stage - 01 | STG01 | First Stage
Stage - 02 | STG02 | Second Stage
Stage - 03 | STG03 | Third Stage
Stage - 04 | STG04 | Fourth Stage
Stage - 05 | STG05 | Fifth Stage
Stage - 06 | STG06 | Sixth Stage
Stage - 07 | STG07 | Seventh Stage
Stage - 08 | STG08 | Eighth Stage
Stage - 09 | STG09 | Ninth Stage
Stage - 10 | STG10 | Tenth Stage
Start | STR | Start
Start/Stop | S/S | Start/Stop
Static | STAT | Static
Status | STAT | Status
Status - Boiler Firing Controller | FLMFL | Flame Failure Status
Status - Cooling System Status | CLSTAT | Cooling System Status
Status - Free Cooling Status | FCSTAT | Free Cooling Status
Status - Heating System Status | HSSTAT | Heating System Status
Status - HOA | HOASTAT | HOA Switch Status
Status - Proof of Operation | PRF | Proof of Operation
Stop | STP | Stop
Strainer | STR | Strainer
Strobe | STRB | Strobe Light
Suction | SUC | Suction
Suction | SUC | Suction
Sump | SUMP | Sump
Supply | SUP | Supply
Switch | SW | Switch
Switch - Differential Pressure | DPSW | Differential Pressure Switch
Switch - Emergency Machine Off | EMO | Emergency Machine Off
Switch - Emergency Stop | EMS | Emergency Stop
Switch - End Switch | ENDSW | End Switch
Switch - Filter Differential Pressure | FLTSW | Filter Differential Pressure Switch
Switch - Flow (Water or Air) | FLOWSW | Flow Switch
Switch - High Head Pressure Limit Switch - Manual Reset | HPLSW | Head Pressure Limit Switch
Switch - High Head Pressure Switch | HHPSW | High Head Pressure Switch
Switch - High Static Pressure | HSPSW | High Static Pressure Switch
Switch - High Static Pressure Limit - Manual Reset | HSPLIM | High Static Pressure Limit Switch
Switch - High Temperature | HITMP | Firestat
Switch - High Temperature Limit - Manual Reset | FIRST | Firestat
Switch - Lead/Lag | LDLG | Lead Lag Switch
Switch - Level - High | HLVSW | High Level Switch
Switch - Level - Low | HLVSW | High Level Switch
Switch - Limit Switch | LMSW | Limit Switch
Switch - Low Static Pressure | LSPSW | Low Static Pressure Switch
Switch - Low Static Pressure Limit - Manual Reset | LSPLIM | Low Static Pressure Limit Switch
Switch - Low Suction Pressure | LSPSW | Low Suction Pressure Switch
Switch - Low Temperature Limit | SWLOLM | Low Temperature Limit Switch
Switch - Low Temperature Limit - Manual Reset | FRZST | Freezestat
Switch - Moisture | MOISTSW | Moisture Switch
Switch - Motion | MOTNSW | Motion Switch
Switch - Occupancy | OCCSW | Occupancy Switch
Switch - Photocell | PHOSW | Photo Switch
Switch - Roll-out | ROLLOUT | Roll-out Switch
Switch - Suction Pressure Limit Switch - Manual Reset | SPLSW | Suction Pressure Limit Switch
Switch - Vibration - Manual Reset | MRVIBSW | Manual Reset Vibration Switch
System | SYSTM | System
Tank | TNK | Tank
Temperature | TEMP | Temperature
Terminal Unit - Series Fan Powered Terminal Unit | SERFT | Series Fan Powered Terminal Unit
Terminal Unit - Terminal Equipment Controller | TEC | Terminal Unit - Terminal Equipment Controller
Terminal Unit - Variable Air Volume Floor Diffusser | VAVFD | Variable Air Volume Floor Diffusser
Time | TIME | Time
Time - Days | DYS | Days
Time - Hours | HRS | Hours
Time - Minutes | MINS | Minutes
Time - Months | MNTHS | Months
Time - Run Time | RUNTM | Run Time
Time - Seconds | SEC | Seconds
Time - Totalizer | TOTAL | Totalizer
Time - Weeks | WKS | Weeks
Time - Years | YRS | Years
Time Delay | TMDLY | Time Delay
Timer | TMR | Timer
Timer - Acceleration Timer | ACCEL | Acceleration Timer
Timer - Deceleration Timer | DECEL | Deceleration Timer
Timer - Interval Timer | INTTMR | Interval Timer
Timer - Off Delay | OFFDLY | Off Delay
Timer - On Delay | ONDLY | On Delay
Timer - One-Shot Delay | ONSHT | One Shot Delay
Timer - Ramp Down | RMPDN | Ramp Down Timer
Timer - Ramp Up | RMPUP | Ramp Up Timer
Timer - Time Clock | TMCLK | Time Clock
Total | TOTAL
Trigger | TRGR | Trigger
Under Floor Air Distribution | UFLR | Under Floor Air Distribution
Unit | UNIT | Unit
Unit Heater | UH | Unit Heater
Unoccupied | UNOCC | Unoccupied
Valve | VLV | Valve
Variable Frequency Drive | VFD | Variable Frequency Drive
Variable Speed Drive | VSD | Variable Speed Drive
Velocity | VEL | Velocity
Velocity | VEL | Velocity
Ventilation | VENT | Ventilation
Vibration | VIB | Vibration
VRF BACnet - Air Direction Set | AIRDRSET | Set Airflow Direction
VRF BACnet - Air Direction State | AIRDRFDBK | Airflow Direction Feedback
VRF BACnet - Alarm Signal | ALARM | General Alarm
VRF BACnet - Error Code | ERRCD | General Error
VRF BACnet - Fan Speed Set-up | FNSPSET | Set Fan Speed
VRF BACnet - Fan Speed State | FNSPFDBK | Fan Speed Feedback
VRF BACnet - Filter Sign | FTRSGN | Change Filter Indication
VRF BACnet - Filter Sign Reset | FTRRSET | Change Filter Indication Reset
VRF BACnet - MNet Communication State | MNETST | MNet Error Indication
VRF BACnet - On/Off Set-up | ONOFSET | Indoor Unit Start/Stop
VRF BACnet - On/Off State | ONOFFDBK | Indoor Unit Operating State
VRF BACnet - Operating Mode Set-up | OPMDSET | Operating Mode Setting
VRF BACnet - Operating Mode State | OPMDFDBK | Operating Mode Feedback
VRF BACnet - Prohibit Filter Sign Reset | PRFLRRSET | Prohibit Remt. Filter Change Ind. Reset
VRF BACnet - Prohibit Mode | PRMODE | Prohibit Remote Operating Mode Override
VRF BACnet - Prohibit On/Off | PRONOF | Prohibit Remote On-Off Override
VRF BACnet - Prohibit Set Temperature | PRSETTMP | Prohibit Remote Set Point Adjustment
VRF BACnet - Room Temperature | RMTMP | Space Temperature Indication
VRF BACnet - Set High Limit Set Back Temp | SETHSBTMP | Set Unoccupied Cycle High Limit Set Point
VRF BACnet - Set Low Limit Set Back Temp | SETLSBTMP | Set Unoccupied Cycle Low Limit Set Point
VRF BACnet - Set Temp Auto | SETTAUTO | Set Temporary Auto Mode Set Point
VRF BACnet - Set Temp Cool | SETTCOOL | Set Temporary Cooling Set Point
VRF BACnet - Set Temp Heat | SETTHEAT | Set Temporary Heating Set Point
VRF BACnet - Set Temperature | SETRMTMP | Set Space Temperature Set Point
VRF BACnet - System Force Off | FRCOFF | Force Indoor Unit Off
Warm-up | WRMUP | Warm-up
Warning | WRN | Warning
Water | WTR | Water
Wet Bulb | WTBLB | Wet Bulb
Wind Direction | WNDDIR | Wind Direction
Wind Speed | WNDSPD | Wind Speed
York BACnet - ACT_SAT_SP | ACT_SAT_SP | Derived Supply Air Temperature Set Point
York BACnet - EL_AIR_TMP-H | EL_AIR_TMP-H | Flexsys Supply Air Temperature High Set Point
York BACnet - EL_AIR_TMP-L | EL_AIR_TMP-L | Flexsys Supply Air Temperature Low Set Point
York BACnet - EVAP_AIR_TMP | EVAP_AIR_TMP | Flexsys Evaporator Coil Leaving Air Temperature
York BACnet - MORN_WUP_RAT | MORN_WUP_RAT | RAT Set Point That Switches The Unit To Heating Mode
York BACnet - OA_ENTH_LIMT | OA_ENTH_LIMT | OA Enthalpy Economizer Limit Set Point
York BACnet - OA_ENTHALPY | OA_ENTHALPY | Outooor Air Enthalpy
York BACnet - OA_REL_HUMD | OA_REL_HUMD | OA Relative Humidity
York BACnet - OA_TEMP | OA_TEMP | OA Temperature
York BACnet - RAT_COOL_SP | RAT_COOL_SP | RAT Set Point That Switches The Unit To Cooling Mode
York BACnet - RET_AIR_BY_S | RET_AIR_BY_S | Derived Return Air Bypass Damper Set Point
York BACnet - RET_AIR_ENTH | RET_AIR_ENTH | Return Air Enthalpy
York BACnet - RET_AIR_HUMD | RET_AIR_HUMD | Return Air Humidity
York BACnet - RET_AIR_TEMP | RET_AIR_TEMP | Return Air Temperature
York BACnet - SAT_HIGH_LIM | SAT_HIGH_LIM | Supply Temperature Set Point Upper Limit
York BACnet - SAT_LOW_LIM | SAT_LOW_LIM | Supply Temperature Set Point Lower Limit
York BACnet - SAT-RST-BAS | SAT-RST-BAS | Hardwired BAS Reset Signal Value
York BACnet - SUP_AIR_TEMP | SUP_AIR_TEMP | Supply Air Temperature
York BACnet - SUP_AIR_TRST | SUP_AIR_TRST | Supply Air Temperature Reset
York RTU | YORK | York RTU
Zone | ZN | Zone
Bottom of list
Revision History
| Created | 2018-04-20 18:01
| Rev 1 | 2018-04-20 18:01
| Rev 2 | 3/26/2020 - Edited to UCOP Standard

## Sheet3
#NAME?