## Slide 1: 2020 RCx Academy Scope of Work Exercise
27 January 2021

## Slide 2: A Resource https://www.screencast.com/t/VIaNTeGfkCH

## Slide 3: Let’s Replace a Boiler
Background
Existing boilers are at the end of useful life
Existing boilers are conventional non-condensing boilers, nominal 84% efficiency
Existing system serves warm-up coils, finned tube radiation and reheat coils with the LWT reset from 160°F – 180°F
Capacity has not been an issue
The building tends to overheat in mild weather
The building operating team likes the existing boiler vendor

## Slide 4: EBCx Project Results
An expanded reset schedule has the potential to improve comfort by better managing FTR capacity
Reheat loads could be served with 110°F water
Reset savings = $2,000 per year in parasitic losses

## Slide 5: A Few Acronyms and Definitions (AFA2D)
Definitions
  Heating
    A process that adds energy. For a space, this is often accomplished by circulating air through it at a temperature above the required set point. For an airstream, this is often accomplished by passing it over a surface that is above the required supply temperature.

## Slide 6: AFA2D
Definitions
  Freezing
    A condition that occurs when water is cooled to the point where it changes phase from a solid to a liquid.

## Slide 7: AFA2D
Definitions
  Water Damage
    A condition that occurs after frozen water contained in a HVAC coil changes back to the liquid phase.

## Slide 8: AFA2D
Definitions
  Expletive
    A generic reference to the field terminology used to describe and discuss water damage when it occurs.

## Slide 9: AFA2D
Definitions
  Preheat
    A process that heats a fluid stream to prepare it for a subsequent HVAC process. In air handling systems, this process is used to raise subfreezing air above freezing to protect water filled elements down stream from damage due to freezing.
    See the Functional Testing Guide (www.peci.org/ftguide) Air Handling System Reference Guide Chapter 5 – Preheat, Table 5.1 to contrast preheat, reheat and heating applications

## Slide 10: AFA2D
Definitions
  Reheat
    A process that uses heat to warm air being delivered to a zone to prevent over cooling. The temperature of the air was set by the need to hit a dehumidification target or by the requirements of another zone, so it can not be raised at the central system. The volume can not be reduced because it has been set to assure proper ventilation (contaminant control). In the limit, reheat will raise the supply temperature to the zone temperature but not above it.

## Slide 11: EBCx Project Results
An expanded reset schedule has the potential to improve comfort by better managing FTR capacity
Reheat loads could be served with 110°F water
Reset savings = $2,000 per year in parasitic losses

## Slide 12: EBCx Project Results
An expanded reset schedule has the potential to improve comfort by better managing FTR capacity
Reheat loads could be served with 110°F water
Reset savings = $2,000 per year in parasitic losses

## Slide 13: EBCx Project Results
An expanded reset schedule has the potential to improve comfort by better managing FTR capacity
Reheat loads could be served with 110°F water
Reset savings = $2,000 per year in parasitic losses

## Slide 14: EBCx Project Results
An expanded reset schedule has the potential to improve comfort by better managing FTR capacity
Reheat loads could be served with 110°F water
Reset savings = $2,000 per year in parasitic losses

## Slide 15: EBCx Project Results
An expanded reset schedule has the potential to improve comfort by better managing FTR capacity
Reheat loads could be served with 110°F water
Expanding the reset schedule yields savings of $2,000 per year in parasitic losses

## Slide 16: EBCx Project Results
An expanded reset schedule has the potential to improve comfort by better managing FTR capacity
Reheat loads could be served with 110°F water
Reset savings = $2,000 per year in parasitic losses

## Slide 17
TT
DP
Pump 1
Bell and Gossett 2.5BB
240 gpm at 45.6 ft.w.c.
71.15% Efficiency
1,750 rpm, 3.9 Bhp, 5hp motor
(Typical for each pump)
DP
1st Floor Finned Tube Radiation
TT
Typical of 4 circuits
Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single tier, 18" mounting height, 816 Btu/hr/ft;
243 feet of active element in four circuits of 7.2 gpm each, 28.8 total gpm, 14°F ∆t, 170°F average water temperature, 156°F return
Normally Open
FTR and Rheat Typical for 5 Floors
TT
Reheat Coil (Typical of 5)
Normally Open to the Coil
Capacity – Varies
Air Side
Flow rate = Varies, 500 fpm maximum face velocity
Entering air temperature – 53.0°F
Leaving air temperature – 82 °F
Pressure drop – 0.1 in.w.c. maximum
Water Side
Flow rate = Varies
Entering water temperature – 180.0°F
Leaving water temperature – 140.0°F
Pressure drop – 5 ft.w.c. maximum.
1st Floor Reheat Loads; Nominal gpm for the floor = 36.5 gpm
Pump 2
TT
DP
Boiler 1
TT
TT
DP
Boiler 2
TT
TT
Boiler/Pump (Typical)
Laars Mighty Therm
Input – 1,670,000 Btu/hr
Output – 1,396,000 Btu/hr
Flow – 120 gpm
Pressure drop – 1.5 ft.w.c.
EWT – 157°F
LWT – 180°F
15 amp 1 ph 120 vac
Bell and Gossett
656S ECM
120 gpm at 3.3 ft.w.c.
1.12 bhp
1725 rpm
TT
Warm-up Coil
Normally Open to the Coil
Capacity – 586,200 Btu/hr
6 ft. high x 8 ft. wide
Air Side
Flow rate = 22,306 cfm
Entering air temperature – 62.0°F
Leaving air temperature – 86.3°F
Pressure drop – 0.09 in.w.c.
Water Side
Flow rate = 29.8 gpm
Entering water temperature – 180.0°F
Leaving water temperature – 140.0°F
Pressure drop – 4.4 ft.w.c.
Typical for 2 AHUs (East and West)
PT
Cold water make-up from a back flow preventer
Diaphragm type expansion tank
BIMCOM
Supreme Command Facility
Alternative Shape Analysis Command
Ames Research Facility
Heating Hot Water System
Butterfly valve
Two way control valve
Balance valve
Check valve
Ball valve
Pressure reducing valve
Pressure relief valve
Three way control valve
Steam trap
Thermometer with well
Pressure gauge with isolation valve
PT
Pressure Transmitter
TT
Temperature transmitter with well
DP
Differential pressure transmitter with isolation valves
Notes: Bell and Gossett 2AD-es Flow - 87.4 Head - 45.6 Speed - 1,750 Bhp - 1.3 Efficiency - 75.9% Motor hp - 2

## Slide 18: Facility Operations Request
Prepare and RFP to replace the existing boiler with the current model rated for the same capacity
If possible, capture the savings identified by the EBCx project

## Slide 19: Boiler Break-out Session 1
Given
The preceding information
The local climate (next slide and TMY file)
Annual gas cost of $25,200
Field data suggests existing boiler efficiency has degraded to 70-75%
A requirement to secure a minimum of three bids
A requirement to go with the low bidder
A requirement for an open equipment specification (not flat specs; the “Or Equal” clause is mandated)
Do you think a like for like replacement is the best option?
  If no, what other options should be considered?
No matter what boiler is selected, what items should the RFP address and/or include to ensure:
  Efficiency optimization is maximized
  The Facility Operation team’s needs are met
  Key installation and performance issues are addressed
  All bidders “see” the project the same way

## Slide 20: Climate Data
For security reasons, we can not disclose where the facility is.
But if we were allowed, we would tell you it was near Ames, Iowa.
Unfortunately, we can not say that, so you are on your own.
Probably not the actual location

## Slide 21: Variable Flow Connection that Keeps the Boilers Hot While the Loop Does “What-Ever”
Non-condensing boilers piped in a constant volume loop and operate at a constant flow at a safe (non-condensing) temperature (typically 140°F)
Variable flow distribution loop sees flow that varies with load
Three way valve mixes water from the boiler loop with water returning from the loads to provide supply temperatures at or below the boiler loop temperature

## Slide 22: Boiler Piping

## Slide 24: Boiler Break-out Session 2
Given
The basis of design boiler information
Basis of design requirements
  System diagram that follows
  Ability to reset supply LWT to 110°F is the design target/incentive basis
    EWT range of 90 - 101°F under that condition
  Cx process hopes to get to a 95°F LWT temperature under some conditions
    EWT range of 75 - 86°F under that condition
The proposed “equal” substitution by the contractor
Is the proposed substitution equivalent to the basis of design boiler?
If not, what could you do about it?

## Slide 25
TT
DP
Pump 1
DP
1st Floor Finned Tube Radiation
TT
Warm-up Coil
Normally Open to the Coil
TT
Typical of 4 circuits
Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single tier, 18" mounting height, 816 Btu/hr/ft;
243 feet of active element in four circuits of 7.2 gpm each, 28.8 total gpm, 14°F ∆t, 170°F supply, 156°F return
Normally Open
TT
Reheat Coil (Typical of 5)
Normally Open to the Coil
Capacity – Varies
Air Side
Flow rate = Varies, 500 fpm maximum face velocity
Entering air temperature – 53.0°F
Leaving air temperature – 82 °F
Pressure drop – 0.1 in.w.c. maximum
Water Side
Flow rate = Varies
Entering water temperature – 170.0°F
Leaving water temperature – 150.0°F
Pressure drop – 5 ft.w.c. maximum.
See also Note 1 on sheet 2
1st Floor Reheat Loads; Nominal gpm for the floor = 36.5 gpm
Pump 2
TT
DP
Boiler 1
TT
TT
DP
Boiler 2
TT
TT
Boiler/Pump (Typical)
Aerco Benchmark 1.5
Input – 1,500,000 Btu/hr
Output – 1,395,000 Btu/hr
Flow – 43.7 gpm
Pressure drop – 6.5 ft.w.c.
EWT – 157°F
LWT – 180°F
Turn down ratio – 14:1
13 fla at 120 vac 1 phase
Bell and Gossett
611
120 gpm at 11 ft.w.c.
.84 bhp, 1hp motor
1750 rpm
PT
Cold water make-up from a back flow preventer
Diaphragm type expansion tank
Butterfly valve
Two way control valve
Balance valve
Check valve
Ball valve
Pressure reducing valve
Pressure relief valve
Three way control valve
Steam trap
Thermometer with well
Pressure gauge with isolation valve
PT
Pressure Transmitter
TT
Temperature transmitter with well
DP
Differential pressure transmitter with isolation valves
Capacity – 586,200 Btu/hr
6 ft. high x 8 ft. wide
Air Side
Flow rate = 22,306 cfm
Entering air temperature – 62.0°F
Leaving air temperature – 86.3°F
Pressure drop – 0.09 in.w.c.
Water Side
Flow rate = 29.8 gpm
Entering water temperature – 180.0°F
Leaving water temperature – 140.0°F
Pressure drop – 4.4 ft.w.c.
Typical for 2 AHUs (East and West)
Bell and Gossett 2.5BB
240 gpm at 45.6 ft.w.c.
71.15% Efficiency
1,750 rpm, 3.9 Bhp, 5hp motor
(Typical for each pump)
FTR and Rheat Typical for 5 Floors
BIMCOM
Supreme Command Facility
Alternative Shape Analysis Command
Ames Research Facility
Heating Hot Water System
Notes: Bell and Gossett 2AD-es Flow - 87.4 Head - 45.6 Speed - 1,750 Bhp - 1.3 Efficiency - 75.9% Motor hp - 2