## Slide 1: Existing Building Commissioning Series Workshop
Sessions 3 and 4
David Sellers
Senior Engineer, Facility Dynamics Engineering

## Slide 2: Air Side Economizers are Often EBCx Opportunities
Industry metrics indicate 70% or more of them have an issue
  Poor minimum outdoor air regulation
  Poor damper sizing
  Damper seal leakage
  Poor mixing
  Improper or non-functioning high limit control strategy
  Nuisance freezestat trips
  Coil freeze-ups

## Slide 3: Resources for Further Study
Economizer Evaluation Checklist
https://www.av8rdas.com/economizer-evaluation-checklist.html
Economizer Stratification Video
https://www.av8rdas.com/economizer-stratification.html
Economizer Stratification Blog Post
https://av8rdas.wordpress.com/2013/01/17/retrocommissioning-findings-economizer-mixed-air-plenum-stratificationoverview/
Pacific Energy Center Economizers; Design, Performance and Commissioning Issues Class Materials
https://www.av8rdas.com/pacific-energy-center-design-performance-and-commissioning-issues-classes.html#Economizers

## Slide 4: Our Initial Focus
Poor minimum outdoor air regulation
Poor damper sizing
Damper seal leakage
Poor mixing

## Slide 5: An Important Monitoring Plan Target
Improper or non-functioning high limit control strategy
https://tinyurl.com/PerfectEconomizer

## Slide 6: The Economizer Evaluation Checklist

## Slide 7: The Economizer Evaluation Checklist
Economize evaluation guidance for all phases of a project
Included with the functional testing guide
  https://tinyurl.com/BallRoomAHU2020

## Slide 8: Break Out 01
Given
The first section of the checklist
The images of the Ball Room AHU that follow
The drawings provided
Assess the minimum outdoor air (MOA) flow regulation capability of the Ball Room AHU economizer
How well is it regulated?
What are some of the assumptions behind the strategy?
Can you estimate the MOA% required from the documents?
Are their other things that you observe that would be items that should be added to your findings list?

## Slide 9: Economizer/Mixed Air Section Plan View

## Slide 10: Equipment Overview

## Slide 11: Equipment Overview

## Slide 12: Equipment Overview

## Slide 13: Filter Bank

## Slide 14: Filter Detail

## Slide 15: Mixed Air Plenum Overview

## Slide 16: Mixed Air Plenum Overview – Heating Coil Hidden

## Slide 17: Outdoor Air Temperature Sensor

## Slide 18: Return Air Temperature Sensor

## Slide 19: Return Air Temperature Sensor

## Slide 20: Dampers Viewed from Actuator Side

## Slide 21: Outdoor Air Damper from Inside the OA Duct

## Slide 22: Outdoor Air Damper Blade Close-up

## Slide 23: Return Air Damper Blade Close-up

## Slide 24: Relief Dampers - Overview

## Slide 25: Relief Dampers – Close-up

## Slide 26: Relief Dampers – Actuator and Blade Close-up

## Slide 27: Return Air Damper Measurements - Overview

## Slide 28: Return Air Damper Measurements - Height

## Slide 29: Return Air Damper Measurements - Width

## Slide 30: Outdoor Air Damper Measurements - Overview

## Slide 31: Outdoor Air Damper Measurements - Height

## Slide 32: Outdoor Air Damper Measurements - Width

## Slide 33: Relief Dampers – Measurements Overview

## Slide 34: Relief Dampers – Measurements - Width

## Slide 35: Relief Dampers – Measurements - Height

## Slide 36: Mixed Air Plenum Looking in the Direction of Airflow, Filters Hidden

## Slide 37: Control Device

## Slide 38: Hot Water Coil Leaving Air Temperature

## Slide 39: Hot Water Coil Pipe Temperatures

## Slide 40: Supply Air Temperature

## Slide 42: Break Out 02
Given
The second section of the checklist
Previous information
Damper curves that follow
Assess the economizer damper sizing and arrangement
How well sized are they?
How well are they arranged to promote mixing?
Are their improvements you would recommend?
Would your recommendations vary with the climate the system was in?
What monitoring and testing would you want to do based on what you observe?

## Slide 43: Damper Characteristic Curves