## New Plant kW per Ton Summary
The spreadsheet assumes that if more than one chiller is running, then they all run at the same % load
Design Tons
CH-1 | 300
CH-2 and 3 | 1000
Load | System ∆t. °F | CHW Flow, gpm | Chiller Status |  |  | Condenser Pump Status |  |  | Chilled Water Pump Status |  |  | Cooling Tower Cell Status |  |  |  | System % of Full Load | Online Tonnage |  |  |  | Chiller Percent Load |  |  | Chiller Tons (Green Total Text means Tonnage Cross-checks) |  |  |  | Chiller kW per Ton |  |  | Chiller kW |  |  |  |  | Condenser Pump kW |  |  |  |  | Cooling Tower Fan kW |  | Chilled Water Pump kW |  |  |  |  | Total kW | Total kW/Ton
|  |  | CH-1 | CH-2 | CH-3 | P14-4 | P14-5 | P14-6 | P14-1 | P14-2 | P14-3 | CT-1A | CT-1B | CT-2A | CT-2B |  | CH-1 | CH-2 | CH-3 | Total | CH-1 | CH-2 | CH-3 | CH-1 | CH-2 | CH-3 | Total | CH-1 | CH-2 | CH-3 | CH-1 | CH-2 | CH-3 | Total | Average kW/ton | P14-4 | P14-5 | P14-6 | Total | kW/ton | Total | kW/ton | P14-1 | P14-2 | P14-3 | Total | kW/ton
50 | 16 | 75 | On | Off | Off | On | Off | Off | On | Off | Off | On | Off | Off | Off | 2.174% | 300 | 0 | 0 | 300 | 16.67% | 0% | 0% | 50 | 0 | 0 | 50 | 0.25709 | N/A | N/A | 12.8543 | 0 | 0 | 12.8543 | 0.25709 | 8.2923 | 0 | 0 | 8.2923 | 0.16585 | 1.5131 | 0.030261 | 2.926 | 0 | 0 | 2.926 | 0.058521 | 25.5857 | 0.51171
100 | 16 | 150 | On | Off | Off | On | Off | Off | On | Off | Off | On | Off | Off | Off | 4.348% | 300 | 0 | 0 | 300 | 33.33% | 0% | 0% | 100 | 0 | 0 | 100 | 0.24846 | N/A | N/A | 24.8461 | 0 | 0 | 24.8461 | 0.24846 | 8.2923 | 0 | 0 | 8.2923 | 0.082923 | 1.3274 | 0.013274 | 3.8817 | 0 | 0 | 3.8817 | 0.038817 | 38.3475 | 0.38348
150 | 16 | 225 | On | Off | Off | On | Off | Off | On | Off | Off | On | Off | Off | Off | 6.522% | 300 | 0 | 0 | 300 | 50% | 0% | 0% | 150 | 0 | 0 | 150 | 0.31641 | N/A | N/A | 47.4618 | 0 | 0 | 47.4618 | 0.31641 | 8.2923 | 0 | 0 | 8.2923 | 0.055282 | 1.7941 | 0.01196 | 4.4641 | 0 | 0 | 4.4641 | 0.029761 | 62.0123 | 0.41342
200 | 16 | 300 | On | Off | Off | On | Off | Off | On | Off | Off | On | Off | Off | Off | 8.696% | 300 | 0 | 0 | 300 | 66.67% | 0% | 0% | 200 | 0 | 0 | 200 | 0.41073 | N/A | N/A | 82.1461 | 0 | 0 | 82.1461 | 0.41073 | 8.2923 | 0 | 0 | 8.2923 | 0.041461 | 2.601 | 0.013005 | 4.8489 | 0 | 0 | 4.8489 | 0.024244 | 97.8883 | 0.48944
250 | 16 | 375 | On | Off | Off | On | Off | Off | On | Off | Off | On | Off | Off | Off | 10.87% | 300 | 0 | 0 | 300 | 83.33% | 0% | 0% | 250 | 0 | 0 | 250 | 0.50694 | N/A | N/A | 126.7339 | 0 | 0 | 126.7339 | 0.50694 | 8.2923 | 0 | 0 | 8.2923 | 0.033169 | 3.3495 | 0.013398 | 5.8433 | 0 | 0 | 5.8433 | 0.023373 | 144.2189 | 0.57688
300 | 16 | 450 | Off | On | Off | Off | On | Off | Off | On | Off | On | On | Off | Off | 13.04% | 0 | 1000 | 0 | 1000 | 0% | 30% | 0% | 0 | 300 | 0 | 300 | N/A | 0.242 | N/A | 0 | 72.6003 | 0 | 72.6003 | 0.242 | 0 | 32.4129 | 0 | 32.4129 | 0.10804 | 3.5881 | 0.01196 | 0 | 10.643 | 0 | 10.643 | 0.035477 | 119.2443 | 0.39748
350 | 16 | 525 | Off | On | Off | Off | On | Off | Off | On | Off | On | On | Off | Off | 15.22% | 0 | 1000 | 0 | 1000 | 0% | 35% | 0% | 0 | 350 | 0 | 350 | N/A | 0.25284 | N/A | 0 | 88.4942 | 0 | 88.4942 | 0.25284 | 0 | 32.4129 | 0 | 32.4129 | 0.092608 | 3.2454 | 0.0092726 | 0 | 11.2073 | 0 | 11.2073 | 0.032021 | 135.3598 | 0.38674
400 | 16 | 600 | Off | On | Off | Off | On | Off | Off | On | Off | On | On | Off | Off | 17.39% | 0 | 1000 | 0 | 1000 | 0% | 40% | 0% | 0 | 400 | 0 | 400 | N/A | 0.26984 | N/A | 0 | 107.9362 | 0 | 107.9362 | 0.26984 | 0 | 32.4129 | 0 | 32.4129 | 0.081032 | 4.0482 | 0.01012 | 0 | 11.6839 | 0 | 11.6839 | 0.02921 | 156.0812 | 0.3902
450 | 16 | 675 | Off | On | Off | Off | On | Off | Off | On | Off | On | On | Off | Off | 19.57% | 0 | 1000 | 0 | 1000 | 0% | 45% | 0% | 0 | 450 | 0 | 450 | N/A | 0.29147 | N/A | 0 | 131.1621 | 0 | 131.1621 | 0.29147 | 0 | 32.4129 | 0 | 32.4129 | 0.072029 | 4.9447 | 0.010988 | 0 | 12.0902 | 0 | 12.0902 | 0.026867 | 180.6098 | 0.40136
500 | 16 | 750 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 21.74% | 0 | 1000 | 1000 | 2000 | 0% | 25% | 25% | 0 | 250 | 250 | 500 | N/A | 0.23906 | 0.23906 | 0 | 59.7648 | 59.7648 | 119.5296 | 0.23906 | 0 | 41.236 | 41.236 | 82.472 | 0.16494 | 4.0402 | 0.0080804 | 0 | 13.302 | 0 | 13.302 | 0.026604 | 219.3437 | 0.43869
550 | 16 | 825 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 23.91% | 0 | 1000 | 1000 | 2000 | 0% | 27.5% | 27.5% | 0 | 275 | 275 | 550 | N/A | 0.23943 | 0.23943 | 0 | 65.8422 | 65.8422 | 131.6844 | 0.23943 | 0 | 41.236 | 41.236 | 82.472 | 0.14995 | 4.5302 | 0.0082367 | 0 | 14.5185 | 0 | 14.5185 | 0.026397 | 233.2051 | 0.42401
600 | 16 | 900 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 26.09% | 0 | 1000 | 1000 | 2000 | 0% | 30% | 30% | 0 | 300 | 300 | 600 | N/A | 0.242 | 0.242 | 0 | 72.6003 | 72.6003 | 145.2006 | 0.242 | 0 | 41.236 | 41.236 | 82.472 | 0.13745 | 3.2787 | 0.0054645 | 0 | 15.7748 | 0 | 15.7748 | 0.026291 | 246.7261 | 0.41121
650 | 16 | 975 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 28.26% | 0 | 1000 | 1000 | 2000 | 0% | 32.5% | 32.5% | 0 | 325 | 325 | 650 | N/A | 0.24655 | 0.24655 | 0 | 80.1278 | 80.1278 | 160.2556 | 0.24655 | 0 | 41.236 | 41.236 | 82.472 | 0.12688 | 4.0683 | 0.006259 | 0 | 17.0838 | 0 | 17.0838 | 0.026283 | 263.8797 | 0.40597
700 | 16 | 1050 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 30.43% | 0 | 1000 | 1000 | 2000 | 0% | 35% | 35% | 0 | 350 | 350 | 700 | N/A | 0.25284 | 0.25284 | 0 | 88.4942 | 88.4942 | 176.9885 | 0.25284 | 0 | 41.236 | 41.236 | 82.472 | 0.11782 | 4.9447 | 0.0070638 | 0 | 18.4591 | 0 | 18.4591 | 0.02637 | 282.8642 | 0.40409
750 | 16 | 1125 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 32.61% | 0 | 1000 | 1000 | 2000 | 0% | 37.5% | 37.5% | 0 | 375 | 375 | 750 | N/A | 0.26067 | 0.26067 | 0 | 97.7516 | 97.7516 | 195.5033 | 0.26067 | 0 | 41.236 | 41.236 | 82.472 | 0.10996 | 5.9022 | 0.0078696 | 0 | 19.9146 | 0 | 19.9146 | 0.026553 | 303.792 | 0.40506
800 | 16 | 1200 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 34.78% | 0 | 1000 | 1000 | 2000 | 0% | 40% | 40% | 0 | 400 | 400 | 800 | N/A | 0.26984 | 0.26984 | 0 | 107.9362 | 107.9362 | 215.8724 | 0.26984 | 0 | 41.236 | 41.236 | 82.472 | 0.10309 | 6.9345 | 0.0086681 | 0 | 21.4643 | 0 | 21.4643 | 0.02683 | 326.7432 | 0.40843
850 | 16 | 1275 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 36.96% | 0 | 1000 | 1000 | 2000 | 0% | 42.5% | 42.5% | 0 | 425 | 425 | 850 | N/A | 0.28016 | 0.28016 | 0 | 119.0699 | 119.0699 | 238.1398 | 0.28016 | 0 | 41.236 | 41.236 | 82.472 | 0.097026 | 8.0351 | 0.0094531 | 0 | 23.1231 | 0 | 23.1231 | 0.027204 | 351.7699 | 0.41385
900 | 16 | 1350 | Off | On | On | Off | On | On | Off | On | Off | On | On | On | On | 39.13% | 0 | 1000 | 1000 | 2000 | 0% | 45% | 45% | 0 | 450 | 450 | 900 | N/A | 0.29147 | 0.29147 | 0 | 131.1621 | 131.1621 | 262.3241 | 0.29147 | 0 | 41.236 | 41.236 | 82.472 | 0.091636 | 9.1981 | 0.01022 | 0 | 24.9054 | 0 | 24.9054 | 0.027673 | 378.8996 | 0.421
950 | 16 | 1425 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 41.3% | 0 | 1000 | 1000 | 2000 | 0% | 47.5% | 47.5% | 0 | 475 | 475 | 950 | N/A | 0.3036 | 0.3036 | 0 | 144.2111 | 144.2111 | 288.4222 | 0.3036 | 0 | 41.236 | 41.236 | 82.472 | 0.086813 | 10.4188 | 0.010967 | 0 | 15.0141 | 15.0141 | 30.0282 | 0.031609 | 411.3412 | 0.43299
1000 | 16 | 1500 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 43.48% | 0 | 1000 | 1000 | 2000 | 0% | 50% | 50% | 0 | 500 | 500 | 1000 | N/A | 0.31641 | 0.31641 | 0 | 158.206 | 158.206 | 316.4121 | 0.31641 | 0 | 41.236 | 41.236 | 82.472 | 0.082472 | 11.6947 | 0.011695 | 0 | 15.9677 | 15.9677 | 31.9354 | 0.031935 | 442.5141 | 0.44251
1050 | 16 | 1575 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 45.65% | 0 | 1000 | 1000 | 2000 | 0% | 52.5% | 52.5% | 0 | 525 | 525 | 1050 | N/A | 0.32977 | 0.32977 | 0 | 173.1282 | 173.1282 | 346.2563 | 0.32977 | 0 | 41.236 | 41.236 | 82.472 | 0.078545 | 13.0255 | 0.012405 | 0 | 16.9687 | 16.9687 | 33.9374 | 0.032321 | 475.6912 | 0.45304
1100 | 16 | 1650 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 47.83% | 0 | 1000 | 1000 | 2000 | 0% | 55% | 55% | 0 | 550 | 550 | 1100 | N/A | 0.34355 | 0.34355 | 0 | 188.9527 | 188.9527 | 377.9055 | 0.34355 | 0 | 41.236 | 41.236 | 82.472 | 0.074975 | 14.4138 | 0.013103 | 0 | 18.0232 | 18.0232 | 36.0464 | 0.032769 | 510.8376 | 0.4644
1150 | 16 | 1725 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 50% | 0 | 1000 | 1000 | 2000 | 0% | 57.5% | 57.5% | 0 | 575 | 575 | 1150 | N/A | 0.35765 | 0.35765 | 0 | 205.6505 | 205.6505 | 411.3009 | 0.35765 | 0 | 41.236 | 41.236 | 82.472 | 0.071715 | 15.8654 | 0.013796 | 0 | 19.1379 | 19.1379 | 38.2757 | 0.033283 | 547.914 | 0.47645
1200 | 16 | 1800 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 52.17% | 0 | 1000 | 1000 | 2000 | 0% | 60% | 60% | 0 | 600 | 600 | 1200 | N/A | 0.37198 | 0.37198 | 0 | 223.1893 | 223.1893 | 446.3786 | 0.37198 | 0 | 41.236 | 41.236 | 82.472 | 0.068727 | 17.3893 | 0.014491 | 0 | 20.3197 | 20.3197 | 40.6394 | 0.033866 | 586.8793 | 0.48907
1250 | 16 | 1875 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 54.35% | 0 | 1000 | 1000 | 2000 | 0% | 62.5% | 62.5% | 0 | 625 | 625 | 1250 | N/A | 0.38646 | 0.38646 | 0 | 241.536 | 241.536 | 483.072 | 0.38646 | 0 | 41.236 | 41.236 | 82.472 | 0.065978 | 18.998 | 0.015198 | 0 | 21.5762 | 21.5762 | 43.1523 | 0.034522 | 627.6943 | 0.50216
1300 | 16 | 1950 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 56.52% | 0 | 1000 | 1000 | 2000 | 0% | 65% | 65% | 0 | 650 | 650 | 1300 | N/A | 0.40101 | 0.40101 | 0 | 260.6576 | 260.6576 | 521.3152 | 0.40101 | 0 | 41.236 | 41.236 | 82.472 | 0.06344 | 20.7073 | 0.015929 | 0 | 22.9151 | 22.9151 | 45.8303 | 0.035254 | 670.3247 | 0.51563
1350 | 16 | 2025 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 58.7% | 0 | 1000 | 1000 | 2000 | 0% | 67.5% | 67.5% | 0 | 675 | 675 | 1350 | N/A | 0.41559 | 0.41559 | 0 | 280.5233 | 280.5233 | 561.0466 | 0.41559 | 0 | 41.236 | 41.236 | 82.472 | 0.06109 | 22.5359 | 0.016693 | 0 | 24.3446 | 24.3446 | 48.6892 | 0.036066 | 714.7437 | 0.52944
1400 | 16 | 2100 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 60.87% | 0 | 1000 | 1000 | 2000 | 0% | 70% | 70% | 0 | 700 | 700 | 1400 | N/A | 0.43015 | 0.43015 | 0 | 301.106 | 301.106 | 602.212 | 0.43015 | 0 | 41.236 | 41.236 | 82.472 | 0.058909 | 24.5058 | 0.017504 | 0 | 25.8726 | 25.8726 | 51.7452 | 0.036961 | 760.9351 | 0.54353
1450 | 16 | 2175 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 63.04% | 0 | 1000 | 1000 | 2000 | 0% | 72.5% | 72.5% | 0 | 725 | 725 | 1450 | N/A | 0.44467 | 0.44467 | 0 | 322.3839 | 322.3839 | 644.7677 | 0.44467 | 0 | 41.236 | 41.236 | 82.472 | 0.056877 | 26.6415 | 0.018373 | 0 | 27.5068 | 27.5068 | 55.0137 | 0.03794 | 808.8948 | 0.55786
1500 | 16 | 2250 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 65.22% | 0 | 1000 | 1000 | 2000 | 0% | 75% | 75% | 0 | 750 | 750 | 1500 | N/A | 0.45912 | 0.45912 | 0 | 344.3419 | 344.3419 | 688.6839 | 0.45912 | 0 | 41.236 | 41.236 | 82.472 | 0.054981 | 28.969 | 0.019313 | 0 | 29.2544 | 29.2544 | 58.5088 | 0.039006 | 858.6336 | 0.57242
1550 | 16 | 2325 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 67.39% | 0 | 1000 | 1000 | 2000 | 0% | 77.5% | 77.5% | 0 | 775 | 775 | 1550 | N/A | 0.47351 | 0.47351 | 0 | 366.9739 | 366.9739 | 733.9477 | 0.47351 | 0 | 41.236 | 41.236 | 82.472 | 0.053208 | 31.5154 | 0.020333 | 0 | 31.1213 | 31.1213 | 62.2426 | 0.040157 | 910.1778 | 0.58721
1600 | 16 | 2400 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 69.57% | 0 | 1000 | 1000 | 2000 | 0% | 80% | 80% | 0 | 800 | 800 | 1600 | N/A | 0.48785 | 0.48785 | 0 | 390.2835 | 390.2835 | 780.567 | 0.48785 | 0 | 41.236 | 41.236 | 82.472 | 0.051545 | 34.307 | 0.021442 | 0 | 33.1119 | 33.1119 | 66.2238 | 0.04139 | 963.5698 | 0.60223
1650 | 16 | 2475 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 71.74% | 0 | 1000 | 1000 | 2000 | 0% | 82.5% | 82.5% | 0 | 825 | 825 | 1650 | N/A | 0.50217 | 0.50217 | 0 | 414.2865 | 414.2865 | 828.573 | 0.50217 | 0 | 41.236 | 41.236 | 82.472 | 0.049983 | 37.3671 | 0.022647 | 0 | 35.2282 | 35.2282 | 70.4564 | 0.042701 | 1018.8685 | 0.6175
1700 | 16 | 2550 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 73.91% | 0 | 1000 | 1000 | 2000 | 0% | 85% | 85% | 0 | 850 | 850 | 1700 | N/A | 0.51648 | 0.51648 | 0 | 439.012 | 439.012 | 878.024 | 0.51648 | 0 | 41.236 | 41.236 | 82.472 | 0.048513 | 40.7129 | 0.023949 | 0 | 37.4694 | 37.4694 | 74.9388 | 0.044082 | 1076.1477 | 0.63303
1750 | 16 | 2625 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 76.09% | 0 | 1000 | 1000 | 2000 | 0% | 87.5% | 87.5% | 0 | 875 | 875 | 1750 | N/A | 0.53086 | 0.53086 | 0 | 464.5041 | 464.5041 | 929.0081 | 0.53086 | 0 | 41.236 | 41.236 | 82.472 | 0.047127 | 44.3522 | 0.025344 | 0 | 39.831 | 39.831 | 79.662 | 0.045521 | 1135.4943 | 0.64885
1800 | 16 | 2700 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 78.26% | 0 | 1000 | 1000 | 2000 | 0% | 90% | 90% | 0 | 900 | 900 | 1800 | N/A | 0.54536 | 0.54536 | 0 | 490.8236 | 490.8236 | 981.6472 | 0.54536 | 0 | 41.236 | 41.236 | 82.472 | 0.045818 | 48.279 | 0.026822 | 0 | 42.3044 | 42.3044 | 84.6088 | 0.047005 | 1197.007 | 0.665
1850 | 16 | 2775 | Off | On | On | Off | On | On | Off | On | On | On | On | On | On | 80.43% | 0 | 1000 | 1000 | 2000 | 0% | 92.5% | 92.5% | 0 | 925 | 925 | 1850 | N/A | 0.56005 | 0.56005 | 0 | 518.0498 | 518.0498 | 1036.0997 | 0.56005 | 0 | 41.236 | 41.236 | 82.472 | 0.044579 | 52.4696 | 0.028362 | 0 | 44.8768 | 44.8768 | 89.7536 | 0.048515 | 1260.7948 | 0.68151
1900 | 16 | 2850 | Off | On | On | Off | On | On | On | On | On | On | On | On | On | 82.61% | 0 | 1000 | 1000 | 2000 | 0% | 95% | 95% | 0 | 950 | 950 | 1900 | N/A | 0.57503 | 0.57503 | 0 | 546.2819 | 546.2819 | 1092.5638 | 0.57503 | 0 | 41.236 | 41.236 | 82.472 | 0.043406 | 56.8811 | 0.029937 | 13.261 | 41.2887 | 41.2887 | 95.8385 | 0.050441 | 1327.7553 | 0.69882
1950 | 16 | 2925 | On | On | On | On | On | On | On | On | On | On | On | On | On | 84.78% | 300 | 1000 | 1000 | 2300 | 84.78% | 84.78% | 84.78% | 254.3478 | 847.8261 | 847.8261 | 1950 | 0.51524 | 0.51524 | 0.51524 | 131.0497 | 436.8323 | 436.8323 | 1004.7142 | 0.51524 | 15.9148 | 46.9428 | 46.9428 | 109.8004 | 0.056308 | 61.4529 | 0.031514 | 14.0057 | 43.7329 | 43.7329 | 101.4715 | 0.052037 | 1277.439 | 0.6551
2000 | 16 | 3000 | On | On | On | On | On | On | On | On | On | On | On | On | On | 86.96% | 300 | 1000 | 1000 | 2300 | 86.96% | 86.96% | 86.96% | 260.8696 | 869.5652 | 869.5652 | 2000 | 0.52773 | 0.52773 | 0.52773 | 137.6683 | 458.8943 | 458.8943 | 1055.4569 | 0.52773 | 15.9148 | 46.9428 | 46.9428 | 109.8004 | 0.0549 | 66.1152 | 0.033058 | 14.7922 | 46.2606 | 46.2606 | 107.3134 | 0.053657 | 1338.6858 | 0.66934
2050 | 16 | 3075 | On | On | On | On | On | On | On | On | On | On | On | On | On | 89.13% | 300 | 1000 | 1000 | 2300 | 89.13% | 89.13% | 89.13% | 267.3913 | 891.3043 | 891.3043 | 2050 | 0.5403 | 0.5403 | 0.5403 | 144.4712 | 481.5706 | 481.5706 | 1107.6124 | 0.5403 | 15.9148 | 46.9428 | 46.9428 | 109.8004 | 0.053561 | 70.8069 | 0.03454 | 15.6206 | 48.8552 | 48.8552 | 113.331 | 0.055283 | 1401.5506 | 0.68368
2100 | 16 | 3150 | On | On | On | On | On | On | On | On | On | On | On | On | On | 91.3% | 300 | 1000 | 1000 | 2300 | 91.3% | 91.3% | 91.3% | 273.913 | 913.0435 | 913.0435 | 2100 | 0.553 | 0.553 | 0.553 | 151.4729 | 504.9097 | 504.9097 | 1161.2923 | 0.553 | 15.9148 | 46.9428 | 46.9428 | 109.8004 | 0.052286 | 75.504 | 0.035954 | 16.4901 | 51.4987 | 51.4987 | 119.4875 | 0.056899 | 1466.0842 | 0.69814
2150 | 16 | 3225 | On | On | On | On | On | On | On | On | On | On | On | On | On | 93.48% | 300 | 1000 | 1000 | 2300 | 93.48% | 93.48% | 93.48% | 280.4348 | 934.7826 | 934.7826 | 2150 | 0.56588 | 0.56588 | 0.56588 | 158.6914 | 528.9712 | 528.9712 | 1216.6338 | 0.56588 | 15.9148 | 46.9428 | 46.9428 | 109.8004 | 0.05107 | 80.2621 | 0.037331 | 17.3989 | 54.1745 | 54.1745 | 125.7478 | 0.058487 | 1532.4441 | 0.71276
2200 | 16 | 3300 | On | On | On | On | On | On | On | On | On | On | On | On | On | 95.65% | 300 | 1000 | 1000 | 2300 | 95.65% | 95.65% | 95.65% | 286.9565 | 956.5217 | 956.5217 | 2200 | 0.579 | 0.579 | 0.579 | 166.148 | 553.8266 | 553.8266 | 1273.8012 | 0.579 | 15.9148 | 46.9428 | 46.9428 | 109.8004 | 0.049909 | 85.2748 | 0.038761 | 18.344 | 56.8708 | 56.8708 | 132.0856 | 0.060039 | 1600.9621 | 0.72771
2250 | 16 | 3375 | On | On | On | On | On | On | On | On | On | On | On | On | On | 97.83% | 300 | 1000 | 1000 | 2300 | 97.83% | 97.83% | 97.83% | 293.4783 | 978.2609 | 978.2609 | 2250 | 0.59244 | 0.59244 | 0.59244 | 173.8681 | 579.5602 | 579.5602 | 1332.9884 | 0.59244 | 15.9148 | 46.9428 | 46.9428 | 109.8004 | 0.0488 | 90.9615 | 0.040427 | 19.3216 | 59.5865 | 59.5865 | 138.4947 | 0.061553 | 1672.245 | 0.74322
2300 | 16 | 3450 | On | On | On | On | On | On | On | On | On | On | On | On | On | 100% | 300 | 1000 | 1000 | 2300 | 100% | 100% | 100% | 300 | 1000 | 1000 | 2300 | 0.60627 | 0.60627 | 0.60627 | 181.8809 | 606.2695 | 606.2695 | 1394.42 | 0.60627 | 15.9148 | 46.9428 | 46.9428 | 109.8004 | 0.047739 | 98.1234 | 0.042662 | 20.327 | 62.3381 | 62.3381 | 145.0033 | 0.063045 | 1747.3471 | 0.75972

## New Plant Chillers+CW Pmp
|  | Source for kW/ton Profile - | ..\Equipment Information\Plant Replacement\Smardt Chillers\SMARDT WC CATALOGUE TD-0080B.pdf
This initial profile is based on the generic data presented in the Smardt catalog. It will be updated once we get project specfic information.
Chiller 1, 44°F LWT |  | Rated Capacity - | 300 | tons
% Load | Tons | Chiller 1 Compressor kW/ton | kW | All Pumps |  | Chiller 1 Running with All Chillers kW/ton with CW Pumps | One Large and One Small Pump |  | Chiller 1 Running with Chiller 2 or 3 kW/ton with CW Pumps | Small Pump Only |  | Chiller 1 Running Alone kW/ton with CW Pump
|  |  |  | Pump kW | Total kW |  | Pump kW | Total kW |  | Pump kW | Total kW
10% | 30 | 0.29651 | 8.8954 | 15.9148 | 24.8102 | 0.82701 | 11.1072 | 20.0026 | 0.66675 | 8.2923 | 17.1876 | 0.57292
20% | 60 | 0.25 | 15 | 15.9148 | 30.9148 | 0.51525 | 11.1072 | 26.1072 | 0.43512 | 8.2923 | 23.2923 | 0.3882
30% | 90 | 0.24186 | 21.7674 | 15.9148 | 37.6822 | 0.41869 | 11.1072 | 32.8746 | 0.36527 | 8.2923 | 30.0597 | 0.334
40% | 120 | 0.26395 | 31.6744 | 15.9148 | 47.5892 | 0.39658 | 11.1072 | 42.7816 | 0.35651 | 8.2923 | 39.9666 | 0.33306
50% | 150 | 0.31861 | 47.7908 | 15.9148 | 63.7056 | 0.4247 | 11.1072 | 58.898 | 0.39265 | 8.2923 | 56.083 | 0.37389
60% | 180 | 0.37442 | 67.3954 | 15.9148 | 83.3102 | 0.46283 | 11.1072 | 78.5027 | 0.43613 | 8.2923 | 75.6877 | 0.42049
70% | 210 | 0.43023 | 90.3489 | 15.9148 | 106.2637 | 0.50602 | 11.1072 | 101.4562 | 0.48312 | 8.2923 | 98.6412 | 0.46972
80% | 240 | 0.48721 | 116.9302 | 15.9148 | 132.845 | 0.55352 | 11.1072 | 128.0374 | 0.53349 | 8.2923 | 125.2224 | 0.52176
90% | 270 | 0.54419 | 146.9302 | 15.9148 | 162.845 | 0.60313 | 11.1072 | 158.0375 | 0.58532 | 8.2923 | 155.2225 | 0.5749
100% | 300 | 0.60698 | 182.0931 | 15.9148 | 198.0079 | 0.66003 | 11.1072 | 193.2003 | 0.644 | 8.2923 | 190.3854 | 0.63462
Chiller 2 & 3, 44°F LWT |  | Rated Capacity - | 1000 | tons
% Load | Tons | Chiller 2 or 3 Compressor kW/ton | kW | All Pumps |  | Chiller 2 or 3 Running with All Chillers kW/ton with CW Pumps | One Large and One Small Pump |  | Chiller 2 or 3 Running with Chiller 1 kW/ton with CW Pumps | Two Large Pumps |  | Chiller 2 Running with Chiller 3 kW/ton with CW Pumps | Large Pump Only |  | Chiller 2 or 3 Running Alone kW/ton with CW Pump
|  |  |  | Pump kW | Total kW |  | Pump kW | Total kW |  | Pump kW | Total kW |  | Pump kW | Total kW
10% | 100 | 0.29651 | 29.6512 | 46.9428 | 76.594 | 0.76594 | 32.7487 | 62.3999 | 0.624 | 41.236 | 70.8872 | 0.70887 | 32.4129 | 62.0641 | 0.62064
20% | 200 | 0.25 | 50 | 46.9428 | 96.9428 | 0.48471 | 32.7487 | 82.7487 | 0.41374 | 41.236 | 91.236 | 0.45618 | 32.4129 | 82.4129 | 0.41206
30% | 300 | 0.24186 | 72.558 | 46.9428 | 119.5008 | 0.39834 | 32.7487 | 105.3067 | 0.35102 | 41.236 | 113.794 | 0.37931 | 32.4129 | 104.9709 | 0.3499
40% | 400 | 0.26395 | 105.5812 | 46.9428 | 152.524 | 0.38131 | 32.7487 | 138.3299 | 0.34582 | 41.236 | 146.8172 | 0.36704 | 32.4129 | 137.9941 | 0.34499
50% | 500 | 0.31861 | 159.3025 | 46.9428 | 206.2453 | 0.41249 | 32.7487 | 192.0512 | 0.3841 | 41.236 | 200.5385 | 0.40108 | 32.4129 | 191.7154 | 0.38343
60% | 600 | 0.37442 | 224.6514 | 46.9428 | 271.5942 | 0.45266 | 32.7487 | 257.4001 | 0.429 | 41.236 | 265.8874 | 0.44315 | 32.4129 | 257.0643 | 0.42844
70% | 700 | 0.43023 | 301.1631 | 46.9428 | 348.1059 | 0.49729 | 32.7487 | 333.9118 | 0.47702 | 41.236 | 342.3991 | 0.48914 | 32.4129 | 333.576 | 0.47654
80% | 800 | 0.48721 | 389.7672 | 46.9428 | 436.71 | 0.54589 | 32.7487 | 422.5159 | 0.52814 | 41.236 | 431.0032 | 0.53875 | 32.4129 | 422.1801 | 0.52773
90% | 900 | 0.54419 | 489.7674 | 46.9428 | 536.7102 | 0.59634 | 32.7487 | 522.5161 | 0.58057 | 41.236 | 531.0034 | 0.59 | 32.4129 | 522.1803 | 0.5802
100% | 1000 | 0.60698 | 606.977 | 46.9428 | 653.9198 | 0.65392 | 32.7487 | 639.7257 | 0.63973 | 41.236 | 648.213 | 0.64821 | 32.4129 | 639.3899 | 0.63939
1,000 Tons
Part Load, Proportional Split, Chiller 2 and 3 Running |  |  |  | Non-uniform Load Split, Chiller 2 and 3 Running
Total load | 1000 | tons |  | Total load | 1000 | tons | [9 empty] | Digitized Curve Data
CH-2 Load | 500 | tons |  | CH-2 Load | 300 | tons (best efficiency point)
CH-3 Load | 500 | tons |  | CH-3 Load | 700 | tons | [9 empty] | 44°F |  |  | 46°F |  | 48°F |  | 50°F
| Compressor | Compressor plus Pump |  |  | Compressor | Compressor plus Pump | [8 empty] | % Chiller Load | % Chiller Load | kW/Ton | Calculated | % Chiller Load | kW/Ton | % Chiller Load | kW/Ton | % Chiller Load | kW/Ton
Chiller 2 kW/ton | 0.31861 | 0.40108 |  | Chiller 2 kW/ton | 0.24186 | 0.37931 | [8 empty] | 10.1362 | 10 | 0.29651 | 0.297 | 10.1362 | 0.28721 | 10.1362 | 0.27442 | 10.1362 | 0.26163
Chiller 3 kW/ton | 0.31861 | 0.40108 |  | Chiller 3 kW/ton | 0.43023 | 0.48914 | [8 empty] | 10.1362 | 10 | 0.29651 | 0.297 | 10.1362 | 0.28721 | 10.1362 | 0.27442 | 10.1362 | 0.26163
Chiller 2 kW | 159.3025 | 200.5385 |  | Chiller 2 kW | 72.558 | 113.794 | [8 empty] | 20.0545 | 20 | 0.25 | 0.24583 | 20.0545 | 0.22558 | 20.0545 | 0.20349 | 19.9455 | 0.18954
Chiller 3 kW | 159.3025 | 200.5385 |  | Chiller 3 kW | 301.1631 | 342.3991 | [8 empty] | 30.1907 | 30 | 0.24186 | 0.24228 | 30.0817 | 0.21628 | 30.1907 | 0.19535 | 30.1907 | 0.17907
TOTAL kW | 318.605 | 401.077 |  | TOTAL kW | 373.7211 | 456.1931 | [8 empty] | 40 | 40 | 0.26395 | 0.26984 | 40.109 | 0.23605 | 40.109 | 0.21977 | 40.109 | 0.19419
500 Tons | [14 empty] | 50.2452 | 50 | 0.31861 | 0.3177 | 50.2452 | 0.29186 | 50.2452 | 0.26628 | 50.3542 | 0.24419
Part Load, Proportional Split, Chiller 2 and 3 Running, Low Load |  |  |  | Non-uniform Load Split, Chiller 2 and 3 Running, Low Load | [10 empty] | 60.0545 | 60 | 0.37442 | 0.3723 | 60.1635 | 0.35 | 60.0545 | 0.32442 | 60.1635 | 0.29767
Total load | 500 | tons |  | Total load | 500 | tons | [8 empty] | 70.1907 | 70 | 0.43023 | 0.43126 | 70.1907 | 0.40698 | 70.1907 | 0.38139 | 70.2997 | 0.35698
CH-2 Load | 250 | tons |  | CH-2 Load | 300 | tons (best efficiency point) | [8 empty] | 80.109 | 80 | 0.48721 | 0.48848 | 80.109 | 0.46279 | 80.109 | 0.43837 | 80 | 0.41628
CH-3 Load | 250 | tons |  | CH-3 Load | 200 | tons | [8 empty] | 90.2452 | 90 | 0.54419 | 0.54679 | 90.2452 | 0.52093 | 90.2452 | 0.49535 | 90.1362 | 0.47442
| Compressor | Compressor plus Pump |  |  | Compressor | Compressor plus Pump | [8 empty] | 100.272 | 100 | 0.60698 | 0.60803 | 100.163 | 0.58023 | 100.163 | 0.55465 | 100.163 | 0.53139
Chiller 2 kW/ton | 0.24593 | 0.41775 |  | Chiller 2 kW/ton | 0.24186 | 0.37931 | [8 empty] | This column is the actual digitized data. The 44°F % column is rounded to an even percentage
Chiller 3 kW/ton | 0.24593 | 0.41775 |  | Chiller 3 kW/ton | 0.25 | 0.45618
Chiller 2 kW | 61.4825 | 104.4366 |  | Chiller 2 kW | 72.558 | 113.794
Chiller 3 kW | 61.4825 | 104.4366 |  | Chiller 3 kW | 50 | 91.236
TOTAL kW | 122.965 | 208.8733 |  | TOTAL kW | 122.558 | 205.03
1,600 Tons
Part Load, Proportional Split, Chiller 2 and 3 Running, High Load |  |  |  | Non-uniform Load Split, Chiller 2 and 3 Running, High Load
Total load | 1600 | tons |  | Total load | 1600 | tons
CH-2 Load | 800 | tons |  | CH-2 Load | 600 | tons
CH-3 Load | 800 | tons |  | CH-3 Load | 1000 | tons
| Compressor | Compressor plus Pump |  |  | Compressor | Compressor plus Pump
Chiller 2 kW/ton | 0.48721 | 0.53875 |  | Chiller 2 kW/ton | 0.37442 | 0.44315
Chiller 3 kW/ton | 0.48721 | 0.53875 |  | Chiller 3 kW/ton | 0.60698 | 0.64821
Chiller 2 kW | 389.7672 | 431.0032 |  | Chiller 2 kW | 224.6514 | 265.8874
Chiller 3 kW | 389.7672 | 431.0032 |  | Chiller 3 kW | 606.977 | 648.213
TOTAL kW | 779.5344 | 862.0064 |  | TOTAL kW | 831.6284 | 914.1004
1,300 Tons
Part Load, Proportional Split, Chiller 2 and 3 Running, Moderate Load |  |  |  | Non-uniform Load Split, Chiller 2 and 3 Running, Moderate Load
Total load | 1300 | tons |  | Total load | 1300 | tons
CH-2 Load | 650 | tons |  | CH-2 Load | 300 | tons (best efficiency)
CH-3 Load | 650 | tons |  | CH-3 Load | 1000 | tons
| Compressor | Compressor plus Pump |  |  | Compressor | Compressor plus Pump
Chiller 2 kW/ton | 0.40233 | 0.46614 |  | Chiller 2 kW/ton | 0.24186 | 0.37931
Chiller 3 kW/ton | 0.40233 | 0.46614 |  | Chiller 3 kW/ton | 0.60698 | 0.64821
Chiller 2 kW | 261.5119 | 302.9933 |  | Chiller 2 kW | 72.558 | 113.794
Chiller 3 kW | 261.5119 | 302.9933 |  | Chiller 3 kW | 606.977 | 648.213
TOTAL kW | 523.0238 | 605.9867 |  | TOTAL kW | 679.535 | 762.007
1,100 Tons
Part Load, Proportional Split, Chiller 2 and 3 Running, Moderate Load |  |  |  | Non-uniform Load Split, Chiller 2 and 3 Running, Moderate Load
Total load | 1100 | tons |  | Total load | 1100 | tons
CH-2 Load | 550 | tons |  | CH-2 Load | 300 | tons (best efficiency)
CH-3 Load | 550 | tons |  | CH-3 Load | 800 | tons
| Compressor | Compressor plus Pump |  |  | Compressor | Compressor plus Pump
Chiller 2 kW/ton | 0.34651 | 0.42211 |  | Chiller 2 kW/ton | 0.24186 | 0.37931
Chiller 3 kW/ton | 0.34651 | 0.42211 |  | Chiller 3 kW/ton | 0.48721 | 0.53875
Chiller 2 kW | 190.5816 | 232.1612 |  | Chiller 2 kW | 72.558 | 113.794
Chiller 3 kW | 190.5816 | 232.1612 |  | Chiller 3 kW | 389.7672 | 431.0032
TOTAL kW | 381.1632 | 464.3224 |  | TOTAL kW | 462.3252 | 544.7972

## CW Pumps
This analysis assumes that there is programing in place to keep the flow for any operating pump at the design flow rate. It also assumes that the pump runs stead state at that flow any time its chiller runs, irrespective of the load on the chiller. It also uses the scheduled chiller flow vs. the scheduled pump flow. The value scheduled for the tower is closer to this than the sheduled pump values, but none of them agree so we need to figure that out (see below). I have included a comment asking about the intent in my review and can modify this once I know the answer.
Scheduled CW Flow Values
Sum of scheduled pump flows | 7900 | gpm | 1975 | gpm per cell | 3950 | gpm, 2 cells | 5925 | gpm, 3 cells
Sum of scheduled chiller CW flows - | 6450 | gpm | 1612.5 | gpm per cell | 3225 | gpm, 2 cells | 4837.5 | gpm, 3 cells
Sum of scheduled tower flows - | 6900 | gpm | 1725 | gpm per cell | 3450 | gpm, 2 cells | 5175 | gpm, 3 cells
Installed tons in the plant - | 2300 | tons
Tons per tower cell - | 575 | tons
Tower cells and flows for different operating conditions
Assumed total condenser water flow - | 6450 | gpm | 1.9545 | gpm/ton | 27.5 | tons/hp | Original Plant - | 9.6917 | tons/hp
Chillers Running | Small Chiller Only | Large Chiller Only | Large Chiller Only | Small Chiller + 1 Large Chiller | Two Large Chillers | All Chillers
Total CW Flow | 850 | 2800 | 2800 | 3650 | 5600 | 6450
Number of cells active (from control sequence) | 1 | 2 | 3 | 3 | 4 | 4
Flow per cell | 850 | 1400 | 933.3333 | 1216.6667 | 1400 | 1612.5
Tons per tower cell | 300 | 500 | 333.3333 | 433.3333 | 500 | 575
% of cell full load rating | 52.17% | 86.96% | 57.97% | 75.36% | 86.96% | 100%
Green cell sequence is a suggestion; if one cell can handle the small chiller with good flow distribution, then it should be able to handle the flow associated with 1 large chiller split over three cells with the associated fan power reduction.
Blue cell sequence is also a suggestion but not currently in the staging sequence. Given what I think the load profile looks like, it could deliver some energy savings relative to running two larger chillers under some load conditions.
Note that the operating mode with the small chiller and one large chiller is currently not part of the sequence
Chiller 1 Pump Head at Different Operating Conditions
| All Pumps | One Large and One Small Pump | Small Pump Only
Design flow, gpm - | 850 | 850 | 850
Head, ft.w.c | 60 | 41.2363 | 30.6817
Pump efficiency - | 67% | 67% | 67%
Pump bhp - | 19.2221 | 13.2108 | 9.8294
Motor hp - | 25 | 25 | 25
% Load - | 76.89% | 52.84% | 39.32%
Motor efficiency - | 93.56% | 93.86% | 93.53%
VFD efficiency - | 96.3% | 94.53% | 94.55%
Pump kW - | 15.9148 | 11.1072 | 8.2923
Chiller 2 or 3 Condenser Water Pump Head at Different Operating Conditions
| All Pumps | One Large and One Small Pump | Two Large Pumps | Large Pump Only
Design flow, gpm - | 2800 | 2800 | 2800 | 2800
Head, ft.w.c | 60 | 41.2363 | 52.1216 | 40.8146
Pump efficiency - | 74% | 74% | 74% | 74%
Pump bhp - | 57.3301 | 39.4013 | 49.8023 | 38.9984
Motor hp - | 75 | 75 | 75 | 75
% Load - | 76.44% | 52.54% | 66.4% | 52%
Motor efficiency - | 94.66% | 94.95% | 94.7% | 94.95%
VFD efficiency - | 96.25% | 94.53% | 95.14% | 94.53%
Pump kW - | 46.9428 | 32.7487 | 41.236 | 32.4129
Pump head components at Design Conditions
This assumes the design head that is scheduled is the correct number. I have commented on that in my reivew because it seems high and can change these metrics if that turns out to be true.
| Chiller |  | Flow - | 6450 | gpm |  | Tower Cell Rating - | 1612.5 | gpm
Condenser | 16 | ft.w.c. | Since the chillers are in parallel, I have used the higher condenser pressure rop
Tower lift | 12 | ft.w.c.
Spray nozzle | 12 | ft.w.c. | Flow - | 1612.5 | gpm per cell; see table above
Piping network | 20 | ft.w.c.
TOTAL | 60 | ft.w.c.
Pump head with the small chiller and one large chiller running |  |  | Flow - | 3650 | gpm
Chiller | 16 | ft.w.c.
Tower Lift | 12 | ft.w.c.
Spray nozzle | 6.8316 | ft.w.c. | Flow - | 1216.6667 | gpm per cell; see table above
Piping network | 6.4047 | ft.w.c.
TOTAL | 41.2363 | ft.w.c.
Pump head with just the small chiller running |  |  | Flow - | 850
Chiller | 15 | ft.w.c.
Tower Lift | 12 | ft.w.c.
Spray nozzle | 3.3344 | ft.w.c. | Flow - | 850 | gpm per cell; see table above
Piping network | 0.34733 | ft.w.c.
TOTAL | 30.6817 | ft.w.c.
Pump head with two large chillers running |  |  | Flow - | 5600
Chiller | 16 | ft.w.c.
Tower Lift | 12 | ft.w.c.
Spray nozzle | 9.0456 | ft.w.c. | Flow - | 1400 | gpm per cell; see table above
Piping network | 15.076 | ft.w.c.
TOTAL | 52.1216 | ft.w.c.
Pump head with one large chiller running |  |  | Flow - | 2800
Chiller | 16 | ft.w.c.
Tower Lift | 12 | ft.w.c.
Spray nozzle | 9.0456 | ft.w.c. | Flow - | 1400 | gpm per cell; see table above
Piping network | 3.769 | ft.w.c.
TOTAL | 40.8146 | ft.w.c.

## CHW Pumps
|  |  |  | Design Tons | Design Flow, gpm | Minimum Flow, gpm | Design ∆t°F | Evaporator Head, ft.w.c |  |  |  | Chilller Staging | Low Trigger, tons | High Triger, tons | Minimum Flow, gpm
|  |  | CH-1 | 300 | 450 | 112.5 | 16 | 11 |  |  |  | Stage 1 | 0 | 280 | 112.5 | CH-1 On, CH-2 and CH-3 Off
|  |  | CH-2 and 3 | 1000 | 1500 | 375 | 16 | 18 |  |  |  | Stage 2 | 280 | 450 | 375 | CH-2 On, CH-1 and CH-3 Off |  |  | 0.43478
|  |  | Rated Pump Head | [8 empty] | Stage 3 | 450 | 1900 | 750 | CH-2 and CH-3 On, CH-1 Off |  |  | 32.6087
|  |  |  | P14-1 | 120 | ft.w.c. (from schedule) | [5 empty] | Stage 4 | 1900 |  | 862.5 | All Chillers On
|  |  |  | P14-2, P14-3 | 160 | ft.w.c. (from schedule)
|  |  |  | Load Head - | 34.25 | ft.w.c. | Source - | ..\Calculations\CHW Distribution System v3.xlsx |  |  |  | Pump Staging | Low Trigger, gpm | High Triger, gpm
|  |  |  | Design Distribution System Head - | 107.75 | ft.w.c. | [5 empty] | Stage 1 | 0 | 450 | P14-1 Enabled, P14-2 And P14-3 Off.
More Pump Ratings |  |  |  |  | Efficiency | Motor HP | [5 empty] | Stage 2 | 450 | 1400 | Lead Pump {P14-2 Or P14-3) Enabled, P14-1 And Lag Pump Off
|  |  |  | P14-1 | 75% | 40 | [5 empty] | Stage 3 | 1400 | 2850 | P14-2 And P14-3 Enabled, P14-1 Off.
|  |  |  | P14-2, P14-3 | 79% | 100 | [5 empty] | Stage 4 | 2850 |  | All Pumps Enabled.
Load, tons | Active Chiller |  |  | System ∆t with No Bypass Flow, °F | Total CHW Flow, gpm |  |  | Plant ∆t with Bypass Flow, °F | CHW Pump Status |  |  | CHW Pump Head |  |  |  | CHW Pump Flow |  |  | CHW Pump Efficiency (Scheduled Value) |  |  | CHW Pump bhp |  |  | CHW Pump Motor % Load |  |  | CHW Pump Motor Efficiency |  |  | CHW Pump Drive Efficiency |  |  | CHW Pump kW (see formula to the right)
[5 empty] | Theoretical Flow, gpm | Current Min. Flow Requirement, gpm | System Flow, gpm |  | P14-1 | P14-2 | P14-3 | Head Calculation
| CH-1 | CH-2 | CH-3 | [8 empty] | Evaporator, ft.w.c. | Distribution, ft.w.c. | Load, ft.w.c. | Total, ft.w.c. | P14-1 | P14-2 | P14-3 | P14-1 | P14-2 | P14-3 | P14-1 | P14-2 | P14-3 | P14-1 | P14-2 | P14-3 | P14-1 | P14-2 | P14-3 | P14-1 | P14-2 | P14-3 | P14-1 | P14-2 | P14-3
50 | On | Off | Off | 16 | 75 | 112.5 | 75 | 16 | On | Off | Off | 11 | 0.050922 | 34.25 | 45.3009 | 75 | 0 | 0 | 75% | 79% | 79% | 1.144 | 0 | 0 | 2.86% | 0% | 0% | 56.62% | N/A | N/A | 51.51% | N/A | N/A | 2.926 | 0 | 0
100 | On | Off | Off | 16 | 150 | 112.5 | 150 | 16 | On | Off | Off | 11 | 0.20369 | 34.25 | 45.4537 | 150 | 0 | 0 | 75% | 79% | 79% | 2.2956 | 0 | 0 | 5.739% | 0% | 0% | 71.35% | N/A | N/A | 61.83% | N/A | N/A | 3.8817 | 0 | 0
150 | On | Off | Off | 16 | 225 | 112.5 | 225 | 16 | On | Off | Off | 11 | 0.45829 | 34.25 | 45.7083 | 225 | 0 | 0 | 75% | 79% | 79% | 3.4627 | 0 | 0 | 8.657% | 0% | 0% | 80.05% | N/A | N/A | 72.29% | N/A | N/A | 4.4641 | 0 | 0
200 | On | Off | Off | 16 | 300 | 112.5 | 300 | 16 | On | Off | Off | 11 | 0.81474 | 34.25 | 46.0647 | 300 | 0 | 0 | 75% | 79% | 79% | 4.653 | 0 | 0 | 11.63% | 0% | 0% | 86.3% | N/A | N/A | 82.95% | N/A | N/A | 4.8489 | 0 | 0
250 | On | Off | Off | 16 | 375 | 112.5 | 375 | 16 | On | Off | Off | 11 | 1.273 | 34.25 | 46.523 | 375 | 0 | 0 | 75% | 79% | 79% | 5.8741 | 0 | 0 | 14.69% | 0% | 0% | 85.43% | N/A | N/A | 87.78% | N/A | N/A | 5.8433 | 0 | 0
300 | Off | On | Off | 16 | 450 | 375 | 450 | 16 | Off | On | Off | 18 | 1.8332 | 34.25 | 54.0832 | 0 | 450 | 0 | 75% | 79% | 79% | 0 | 7.7795 | 0 | 0% | 7.78% | 0% | N/A | 78.86% | N/A | N/A | 69.14% | N/A | 0 | 10.643 | 0
350 | Off | On | Off | 16 | 525 | 375 | 525 | 16 | Off | On | Off | 18 | 2.4952 | 34.25 | 54.7452 | 0 | 525 | 0 | 75% | 79% | 79% | 0 | 9.1872 | 0 | 0% | 9.187% | 0% | N/A | 82.43% | N/A | N/A | 74.19% | N/A | 0 | 11.2073 | 0
400 | Off | On | Off | 16 | 600 | 375 | 600 | 16 | Off | On | Off | 18 | 3.259 | 34.25 | 55.509 | 0 | 600 | 0 | 75% | 79% | 79% | 0 | 10.6461 | 0 | 0% | 10.65% | 0% | N/A | 85.59% | N/A | N/A | 79.42% | N/A | 0 | 11.6839 | 0
450 | Off | On | Off | 16 | 675 | 750 | 675 | 16 | Off | On | Off | 18 | 4.1246 | 34.25 | 56.3746 | 0 | 675 | 0 | 75% | 79% | 79% | 0 | 12.1637 | 0 | 0% | 12.16% | 0% | N/A | 88.45% | N/A | N/A | 84.85% | N/A | 0 | 12.0902 | 0
500 | Off | On | On | 16 | 750 | 750 | 750 | 16 | Off | On | Off | 18 | 5.0922 | 34.25 | 57.3422 | 0 | 750 | 0 | 75% | 79% | 79% | 0 | 13.7472 | 0 | 0% | 13.75% | 0% | N/A | 88.54% | N/A | N/A | 87.08% | N/A | 0 | 13.302 | 0
550 | Off | On | On | 16 | 825 | 750 | 825 | 16 | Off | On | Off | 18 | 6.1615 | 34.25 | 58.4115 | 0 | 825 | 0 | 75% | 79% | 79% | 0 | 15.4039 | 0 | 0% | 15.4% | 0% | N/A | 89.65% | N/A | N/A | 88.29% | N/A | 0 | 14.5185 | 0
600 | Off | On | On | 16 | 900 | 750 | 900 | 16 | Off | On | Off | 18 | 7.3327 | 34.25 | 59.5827 | 0 | 900 | 0 | 75% | 79% | 79% | 0 | 17.1412 | 0 | 0% | 17.14% | 0% | N/A | 90.67% | N/A | N/A | 89.4% | N/A | 0 | 15.7748 | 0
650 | Off | On | On | 16 | 975 | 750 | 975 | 16 | Off | On | Off | 18 | 8.6057 | 34.25 | 60.8557 | 0 | 975 | 0 | 75% | 79% | 79% | 0 | 18.9664 | 0 | 0% | 18.97% | 0% | N/A | 91.6% | N/A | N/A | 90.42% | N/A | 0 | 17.0838 | 0
700 | Off | On | On | 16 | 1050 | 750 | 1050 | 16 | Off | On | Off | 18 | 9.9806 | 34.25 | 62.2306 | 0 | 1050 | 0 | 75% | 79% | 79% | 0 | 20.8868 | 0 | 0% | 20.89% | 0% | N/A | 92.43% | N/A | N/A | 91.32% | N/A | 0 | 18.4591 | 0
750 | Off | On | On | 16 | 1125 | 750 | 1125 | 16 | Off | On | Off | 18 | 11.4573 | 34.25 | 63.7073 | 0 | 1125 | 0 | 75% | 79% | 79% | 0 | 22.9097 | 0 | 0% | 22.91% | 0% | N/A | 93.17% | N/A | N/A | 92.11% | N/A | 0 | 19.9146 | 0
800 | Off | On | On | 16 | 1200 | 750 | 1200 | 16 | Off | On | Off | 18 | 13.0359 | 34.25 | 65.2859 | 0 | 1200 | 0 | 75% | 79% | 79% | 0 | 25.0425 | 0 | 0% | 25.04% | 0% | N/A | 93.8% | N/A | N/A | 92.79% | N/A | 0 | 21.4643 | 0
850 | Off | On | On | 16 | 1275 | 750 | 1275 | 16 | Off | On | Off | 18 | 14.7163 | 34.25 | 66.9663 | 0 | 1275 | 0 | 75% | 79% | 79% | 0 | 27.2926 | 0 | 0% | 27.29% | 0% | N/A | 94.32% | N/A | N/A | 93.35% | N/A | 0 | 23.1231 | 0
900 | Off | On | On | 16 | 1350 | 750 | 1350 | 16 | Off | On | Off | 18 | 16.4986 | 34.25 | 68.7486 | 0 | 1350 | 0 | 75% | 79% | 79% | 0 | 29.6671 | 0 | 0% | 29.67% | 0% | N/A | 94.74% | N/A | N/A | 93.8% | N/A | 0 | 24.9054 | 0
950 | Off | On | On | 16 | 1425 | 750 | 1425 | 16 | Off | On | On | 18 | 18.3827 | 34.25 | 70.6327 | 0 | 712.5 | 712.5 | 75% | 79% | 79% | 0 | 16.0867 | 16.0867 | 0% | 16.09% | 16.09% | N/A | 90.07% | 90.07% | N/A | 88.75% | 88.75% | 0 | 15.0141 | 15.0141
1000 | Off | On | On | 16 | 1500 | 750 | 1500 | 16 | Off | On | On | 18 | 20.3686 | 34.25 | 72.6186 | 0 | 750 | 750 | 75% | 79% | 79% | 0 | 17.4095 | 17.4095 | 0% | 17.41% | 17.41% | N/A | 90.82% | 90.82% | N/A | 89.56% | 89.56% | 0 | 15.9677 | 15.9677
1050 | Off | On | On | 16 | 1575 | 750 | 1575 | 16 | Off | On | On | 18 | 22.4564 | 34.25 | 74.7064 | 0 | 787.5 | 787.5 | 75% | 79% | 79% | 0 | 18.8056 | 18.8056 | 0% | 18.81% | 18.81% | N/A | 91.52% | 91.52% | N/A | 90.33% | 90.33% | 0 | 16.9687 | 16.9687
1100 | Off | On | On | 16 | 1650 | 750 | 1650 | 16 | Off | On | On | 18 | 24.646 | 34.25 | 76.896 | 0 | 825 | 825 | 75% | 79% | 79% | 0 | 20.2785 | 20.2785 | 0% | 20.28% | 20.28% | N/A | 92.18% | 92.18% | N/A | 91.05% | 91.05% | 0 | 18.0232 | 18.0232
1150 | Off | On | On | 16 | 1725 | 750 | 1725 | 16 | Off | On | On | 18 | 26.9375 | 34.25 | 79.1875 | 0 | 862.5 | 862.5 | 75% | 79% | 79% | 0 | 21.832 | 21.832 | 0% | 21.83% | 21.83% | N/A | 92.79% | 92.79% | N/A | 91.71% | 91.71% | 0 | 19.1379 | 19.1379
1200 | Off | On | On | 16 | 1800 | 750 | 1800 | 16 | Off | On | On | 18 | 29.3308 | 34.25 | 81.5808 | 0 | 900 | 900 | 75% | 79% | 79% | 0 | 23.4697 | 23.4697 | 0% | 23.47% | 23.47% | N/A | 93.35% | 93.35% | N/A | 92.31% | 92.31% | 0 | 20.3197 | 20.3197
1250 | Off | On | On | 16 | 1875 | 750 | 1875 | 16 | Off | On | On | 18 | 31.826 | 34.25 | 84.076 | 0 | 937.5 | 937.5 | 75% | 79% | 79% | 0 | 25.1954 | 25.1954 | 0% | 25.2% | 25.2% | N/A | 93.84% | 93.84% | N/A | 92.83% | 92.83% | 0 | 21.5762 | 21.5762
1300 | Off | On | On | 16 | 1950 | 750 | 1950 | 16 | Off | On | On | 18 | 34.423 | 34.25 | 86.673 | 0 | 975 | 975 | 75% | 79% | 79% | 0 | 27.0126 | 27.0126 | 0% | 27.01% | 27.01% | N/A | 94.26% | 94.26% | N/A | 93.29% | 93.29% | 0 | 22.9151 | 22.9151
1350 | Off | On | On | 16 | 2025 | 750 | 2025 | 16 | Off | On | On | 18 | 37.1218 | 34.25 | 89.3718 | 0 | 1012.5 | 1012.5 | 75% | 79% | 79% | 0 | 28.925 | 28.925 | 0% | 28.92% | 28.92% | N/A | 94.62% | 94.62% | N/A | 93.67% | 93.67% | 0 | 24.3446 | 24.3446
1400 | Off | On | On | 16 | 2100 | 750 | 2100 | 16 | Off | On | On | 18 | 39.9225 | 34.25 | 92.1725 | 0 | 1050 | 1050 | 75% | 79% | 79% | 0 | 30.9363 | 30.9363 | 0% | 30.94% | 30.94% | N/A | 94.91% | 94.91% | N/A | 93.98% | 93.98% | 0 | 25.8726 | 25.8726
1450 | Off | On | On | 16 | 2175 | 750 | 2175 | 16 | Off | On | On | 18 | 42.825 | 34.25 | 95.075 | 0 | 1087.5 | 1087.5 | 75% | 79% | 79% | 0 | 33.0501 | 33.0501 | 0% | 33.05% | 33.05% | N/A | 95.13% | 95.13% | N/A | 94.22% | 94.22% | 0 | 27.5068 | 27.5068
1500 | Off | On | On | 16 | 2250 | 750 | 2250 | 16 | Off | On | On | 18 | 45.8294 | 34.25 | 98.0794 | 0 | 1125 | 1125 | 75% | 79% | 79% | 0 | 35.2702 | 35.2702 | 0% | 35.27% | 35.27% | N/A | 95.28% | 95.28% | N/A | 94.39% | 94.39% | 0 | 29.2544 | 29.2544
1550 | Off | On | On | 16 | 2325 | 750 | 2325 | 16 | Off | On | On | 18 | 48.9356 | 34.25 | 101.1856 | 0 | 1162.5 | 1162.5 | 75% | 79% | 79% | 0 | 37.6001 | 37.6001 | 0% | 37.6% | 37.6% | N/A | 95.37% | 95.37% | N/A | 94.5% | 94.5% | 0 | 31.1213 | 31.1213
1600 | Off | On | On | 16 | 2400 | 750 | 2400 | 16 | Off | On | On | 18 | 52.1437 | 34.25 | 104.3937 | 0 | 1200 | 1200 | 75% | 79% | 79% | 0 | 40.0436 | 40.0436 | 0% | 40.04% | 40.04% | N/A | 95.41% | 95.41% | N/A | 94.56% | 94.56% | 0 | 33.1119 | 33.1119
1650 | Off | On | On | 16 | 2475 | 750 | 2475 | 16 | Off | On | On | 18 | 55.4536 | 34.25 | 107.7036 | 0 | 1237.5 | 1237.5 | 75% | 79% | 79% | 0 | 42.6043 | 42.6043 | 0% | 42.6% | 42.6% | N/A | 95.4% | 95.4% | N/A | 94.57% | 94.57% | 0 | 35.2282 | 35.2282
1700 | Off | On | On | 16 | 2550 | 750 | 2550 | 16 | Off | On | On | 18 | 58.8653 | 34.25 | 111.1153 | 0 | 1275 | 1275 | 75% | 79% | 79% | 0 | 45.2858 | 45.2858 | 0% | 45.29% | 45.29% | N/A | 95.35% | 95.35% | N/A | 94.56% | 94.56% | 0 | 37.4694 | 37.4694
1750 | Off | On | On | 16 | 2625 | 750 | 2625 | 16 | Off | On | On | 18 | 62.3789 | 34.25 | 114.6289 | 0 | 1312.5 | 1312.5 | 75% | 79% | 79% | 0 | 48.0918 | 48.0918 | 0% | 48.09% | 48.09% | N/A | 95.27% | 95.27% | N/A | 94.54% | 94.54% | 0 | 39.831 | 39.831
1800 | Off | On | On | 16 | 2700 | 750 | 2700 | 16 | Off | On | On | 18 | 65.9943 | 34.25 | 118.2443 | 0 | 1350 | 1350 | 75% | 79% | 79% | 0 | 51.026 | 51.026 | 0% | 51.03% | 51.03% | N/A | 95.19% | 95.19% | N/A | 94.53% | 94.53% | 0 | 42.3044 | 42.3044
1850 | Off | On | On | 16 | 2775 | 750 | 2775 | 16 | Off | On | On | 18 | 69.7116 | 34.25 | 121.9616 | 0 | 1387.5 | 1387.5 | 75% | 79% | 79% | 0 | 54.0921 | 54.0921 | 0% | 54.09% | 54.09% | N/A | 95.11% | 95.11% | N/A | 94.55% | 94.55% | 0 | 44.8768 | 44.8768
1900 | Off | On | On | 16 | 2850 | 862.5 | 2850 | 16 | On | On | On | 18 | 73.5307 | 34.25 | 125.7807 | 371.7391 | 1239.1304 | 1239.1304 | 75% | 79% | 79% | 15.7433 | 49.8206 | 49.8206 | 39.36% | 49.82% | 49.82% | 93.67% | 95.22% | 95.22% | 94.55% | 94.53% | 94.53% | 13.261 | 41.2887 | 41.2887
1950 | On | On | On | 16 | 2925 | 862.5 | 2925 | 16 | On | On | On | 18 | 77.4517 | 34.25 | 129.7017 | 381.5217 | 1271.7391 | 1271.7391 | 75% | 79% | 79% | 16.6613 | 52.7256 | 52.7256 | 41.65% | 52.73% | 52.73% | 93.84% | 95.14% | 95.14% | 94.57% | 94.53% | 94.53% | 14.0057 | 43.7329 | 43.7329
2000 | On | On | On | 16 | 3000 | 862.5 | 3000 | 16 | On | On | On | 18 | 81.4745 | 34.25 | 133.7245 | 391.3043 | 1304.3478 | 1304.3478 | 75% | 79% | 79% | 17.6185 | 55.7548 | 55.7548 | 44.05% | 55.75% | 55.75% | 93.96% | 95.07% | 95.07% | 94.57% | 94.57% | 94.57% | 14.7922 | 46.2606 | 46.2606
2050 | On | On | On | 16 | 3075 | 862.5 | 3075 | 16 | On | On | On | 18 | 85.5991 | 34.25 | 137.8491 | 401.087 | 1336.9565 | 1336.9565 | 75% | 79% | 79% | 18.616 | 58.9114 | 58.9114 | 46.54% | 58.91% | 58.91% | 94.03% | 95.02% | 95.02% | 94.55% | 94.67% | 94.67% | 15.6206 | 48.8552 | 48.8552
2100 | On | On | On | 16 | 3150 | 862.5 | 3150 | 16 | On | On | On | 18 | 89.8256 | 34.25 | 142.0756 | 410.8696 | 1369.5652 | 1369.5652 | 75% | 79% | 79% | 19.6547 | 62.1985 | 62.1985 | 49.14% | 62.2% | 62.2% | 94.06% | 95.01% | 95.01% | 94.53% | 94.83% | 94.83% | 16.4901 | 51.4987 | 51.4987
2150 | On | On | On | 16 | 3225 | 862.5 | 3225 | 16 | On | On | On | 18 | 94.1539 | 34.25 | 146.4039 | 420.6522 | 1402.1739 | 1402.1739 | 75% | 79% | 79% | 20.7357 | 65.6194 | 65.6194 | 51.84% | 65.62% | 65.62% | 94.05% | 95.04% | 95.04% | 94.53% | 95.07% | 95.07% | 17.3989 | 54.1745 | 54.1745
2200 | On | On | On | 16 | 3300 | 862.5 | 3300 | 16 | On | On | On | 18 | 98.5841 | 34.25 | 150.8341 | 430.4348 | 1434.7826 | 1434.7826 | 75% | 79% | 79% | 21.86 | 69.1773 | 69.1773 | 54.65% | 69.18% | 69.18% | 94.02% | 95.12% | 95.12% | 94.55% | 95.4% | 95.4% | 18.344 | 56.8708 | 56.8708
2250 | On | On | On | 16 | 3375 | 862.5 | 3375 | 16 | On | On | On | 18 | 103.1161 | 34.25 | 155.3661 | 440.2174 | 1467.3913 | 1467.3913 | 75% | 79% | 79% | 23.0286 | 72.8752 | 72.8752 | 57.57% | 72.88% | 72.88% | 93.97% | 95.23% | 95.23% | 94.62% | 95.81% | 95.81% | 19.3216 | 59.5865 | 59.5865
2300 | On | On | On | 16 | 3450 | 862.5 | 3450 | 16 | On | On | On | 18 | 107.75 | 34.25 | 160 | 450 | 1500 | 1500 | 75% | 79% | 79% | 24.2424 | 76.7165 | 76.7165 | 60.61% | 76.72% | 76.72% | 93.91% | 95.35% | 95.35% | 94.74% | 96.28% | 96.28% | 20.327 | 62.3381 | 62.3381

## Tower Fans
Assumed total condenser water flow - | 6450 | gpm | 1.9545 | gpm/ton | 27.5 | tons/hp
Chillers Running | Small Chiller Only | Large Chiller Only | Large Chiller Only | Small Chiller + 1 Large Chiller | Two Large Chillers | All Chillers
Total CW Flow | 850 | 2800 | 2800 | 3650 | 5600 | 6450
Number of cells active (from control sequence) | 1 | 2 | 3 | 3 | 4 | 4
Flow per cell | 850 | 1400 | 933.3333 | 1216.6667 | 1400 | 1612.5
Tons per tower cell | 300 | 500 | 333.3333 | 433.3333 | 500 | 575
% of cell full load rating | 52.17% | 86.96% | 57.97% | 75.36% | 86.96% | 100%
Green cell sequence is a suggestion; if one cell can handle the small chiller with good flow distribution, then it should be able to handle the flow associated with 1 large chiller split over three cells with the associated fan power reduction. | 0 | 0 | 0 | 0 | 0 | 0
Blue cell sequence is also a suggestion but not currently in the staging sequence. Given what I think the load profile looks like, it could deliver some energy savings relative to running two larger chillers under some load conditions. | 0 | 0 | 0 | 0 | 0 | 0
Tower full load bhp per cell - | 30 | I have assumed the motor hp for now until I get bhp information
| 22.38 | kW
The spreadsheet assumes tower capacity is linear with tower air flow and fan speed and that fan power varies as the cube of airflow.
Minimum fan speed, % of maximum - | 20%
Full load fan bhp - | 120
Full load fan kW - | 89.52
Full load tower fan kW/ton - | 0.038922
Load, tons | Active Chiller |  |  | Active Tower Cell |  |  |  | Online Tower Capacity, tons | Online Tower bhp | Actual Load as a % of Online Capacity | Minimum Fan Speed, % | Fan Speed, % of Maximum | Fan Duty Cycle | Fan bhp per Hour at a Duty Cycle of 1 | Average Fan bhp per hour | Fan bhp per Online Tower Cell | Motor % Full Load | Motor Efficiency | VFD Efficiency | Average Fan kW
| CH-1 | CH-2 | CH-3 | CT-1A | CT-1B | CT-2A | CT-2B
50 | On | Off | Off | 1 | 0 | 0 | 0 | 575 | 30 | 8.696% | 20% | 20% | 43.48% | 0.24 | 0.10435 | 0.10435 | 0.3478% | 12.04% | 42.73% | 1.5131
100 | On | Off | Off | 1 | 0 | 0 | 0 | 575 | 30 | 17.39% | 20% | 20% | 86.96% | 0.24 | 0.2087 | 0.2087 | 0.6957% | 26.71% | 43.92% | 1.3274
150 | On | Off | Off | 1 | 0 | 0 | 0 | 575 | 30 | 26.09% | 20% | 26.09% | 100% | 0.53259 | 0.53259 | 0.53259 | 1.775% | 46.53% | 47.6% | 1.7941
200 | On | Off | Off | 1 | 0 | 0 | 0 | 575 | 30 | 34.78% | 20% | 34.78% | 100% | 1.2624 | 1.2624 | 1.2624 | 4.208% | 64.79% | 55.89% | 2.601
250 | On | Off | Off | 1 | 0 | 0 | 0 | 575 | 30 | 43.48% | 20% | 43.48% | 100% | 2.4657 | 2.4657 | 2.4657 | 8.219% | 78.95% | 69.56% | 3.3495
300 | Off | On | Off | 1 | 1 | 0 | 0 | 1150 | 60 | 26.09% | 20% | 26.09% | 100% | 1.0652 | 1.0652 | 0.53259 | 1.775% | 46.53% | 47.6% | 3.5881
350 | Off | On | Off | 1 | 1 | 0 | 0 | 1150 | 60 | 30.43% | 20% | 30.43% | 100% | 1.6915 | 1.6915 | 0.84573 | 2.819% | 56.31% | 69.04% | 3.2454
400 | Off | On | Off | 1 | 1 | 0 | 0 | 1150 | 60 | 34.78% | 20% | 34.78% | 100% | 2.5249 | 2.5249 | 1.2624 | 4.208% | 64.79% | 71.82% | 4.0482
450 | Off | On | Off | 1 | 1 | 0 | 0 | 1150 | 60 | 39.13% | 20% | 39.13% | 100% | 3.595 | 3.595 | 1.7975 | 5.992% | 72.26% | 75.05% | 4.9447
500 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 21.74% | 20% | 21.74% | 100% | 1.2328 | 1.2328 | 0.30821 | 1.027% | 34.95% | 65.12% | 4.0402
550 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 23.91% | 20% | 23.91% | 100% | 1.6409 | 1.6409 | 0.41023 | 1.367% | 41% | 65.9% | 4.5302
600 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 26.09% | 20% | 26.09% | 100% | 2.1304 | 2.1304 | 0.53259 | 1.775% | 72.55% | 66.81% | 3.2787
650 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 28.26% | 20% | 28.26% | 100% | 2.7086 | 2.7086 | 0.67714 | 2.257% | 73.19% | 67.86% | 4.0683
700 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 30.43% | 20% | 30.43% | 100% | 3.3829 | 3.3829 | 0.84573 | 2.819% | 73.92% | 69.04% | 4.9447
750 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 32.61% | 20% | 32.61% | 100% | 4.1608 | 4.1608 | 1.0402 | 3.467% | 74.74% | 70.37% | 5.9022
800 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 34.78% | 20% | 34.78% | 100% | 5.0497 | 5.0497 | 1.2624 | 4.208% | 75.64% | 71.82% | 6.9345
850 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 36.96% | 20% | 36.96% | 100% | 6.057 | 6.057 | 1.5142 | 5.047% | 76.63% | 73.38% | 8.0351
900 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 39.13% | 20% | 39.13% | 100% | 7.1899 | 7.1899 | 1.7975 | 5.992% | 77.7% | 75.05% | 9.1981
950 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 41.3% | 20% | 41.3% | 100% | 8.4561 | 8.4561 | 2.114 | 7.047% | 78.83% | 76.81% | 10.4188
1000 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 43.48% | 20% | 43.48% | 100% | 9.8627 | 9.8627 | 2.4657 | 8.219% | 80.02% | 78.62% | 11.6947
1050 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 45.65% | 20% | 45.65% | 100% | 11.4174 | 11.4174 | 2.8543 | 9.514% | 81.26% | 80.47% | 13.0255
1100 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 47.83% | 20% | 47.83% | 100% | 13.1273 | 13.1273 | 3.2818 | 10.94% | 82.53% | 82.33% | 14.4138
1150 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 50% | 20% | 50% | 100% | 15 | 15 | 3.75 | 12.5% | 83.81% | 84.15% | 15.8654
1200 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 52.17% | 20% | 52.17% | 100% | 17.0428 | 17.0428 | 4.2607 | 14.2% | 85.09% | 85.92% | 17.3893
1250 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 54.35% | 20% | 54.35% | 100% | 19.2632 | 19.2632 | 4.8158 | 16.05% | 86.35% | 87.6% | 18.998
1300 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 56.52% | 20% | 56.52% | 100% | 21.6684 | 21.6684 | 5.4171 | 18.06% | 87.57% | 89.15% | 20.7073
1350 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 58.7% | 20% | 58.7% | 100% | 24.266 | 24.266 | 6.0665 | 20.22% | 88.72% | 90.54% | 22.5359
1400 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 60.87% | 20% | 60.87% | 100% | 27.0634 | 27.0634 | 6.7658 | 22.55% | 89.79% | 91.75% | 24.5058
1450 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 63.04% | 20% | 63.04% | 100% | 30.0678 | 30.0678 | 7.517 | 25.06% | 90.77% | 92.76% | 26.6415
1500 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 65.22% | 20% | 65.22% | 100% | 33.2868 | 33.2868 | 8.3217 | 27.74% | 91.63% | 93.55% | 28.969
1550 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 67.39% | 20% | 67.39% | 100% | 36.7276 | 36.7276 | 9.1819 | 30.61% | 92.36% | 94.13% | 31.5154
1600 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 69.57% | 20% | 69.57% | 100% | 40.3978 | 40.3978 | 10.0994 | 33.66% | 92.96% | 94.49% | 34.307
1650 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 71.74% | 20% | 71.74% | 100% | 44.3047 | 44.3047 | 11.0762 | 36.92% | 93.43% | 94.67% | 37.3671
1700 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 73.91% | 20% | 73.91% | 100% | 48.4557 | 48.4557 | 12.1139 | 40.38% | 93.75% | 94.7% | 40.7129
1750 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 76.09% | 20% | 76.09% | 100% | 52.8581 | 52.8581 | 13.2145 | 44.05% | 93.96% | 94.63% | 44.3522
1800 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 78.26% | 20% | 78.26% | 100% | 57.5195 | 57.5195 | 14.3799 | 47.93% | 94.05% | 94.5% | 48.279
1850 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 80.43% | 20% | 80.43% | 100% | 62.4472 | 62.4472 | 15.6118 | 52.04% | 94.05% | 94.4% | 52.4696
1900 | Off | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 82.61% | 20% | 82.61% | 100% | 67.6486 | 67.6486 | 16.9121 | 56.37% | 93.99% | 94.39% | 56.8811
1950 | On | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 84.78% | 20% | 84.78% | 100% | 73.131 | 73.131 | 18.2828 | 60.94% | 93.9% | 94.54% | 61.4529
2000 | On | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 86.96% | 20% | 86.96% | 100% | 78.9019 | 78.9019 | 19.7255 | 65.75% | 93.81% | 94.9% | 66.1152
2050 | On | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 89.13% | 20% | 89.13% | 100% | 84.9688 | 84.9688 | 21.2422 | 70.81% | 93.76% | 95.48% | 70.8069
2100 | On | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 91.3% | 20% | 91.3% | 100% | 91.3389 | 91.3389 | 22.8347 | 76.12% | 93.76% | 96.25% | 75.504
2150 | On | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 93.48% | 20% | 93.48% | 100% | 98.0196 | 98.0196 | 24.5049 | 81.68% | 93.83% | 97.1% | 80.2621
2200 | On | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 95.65% | 20% | 95.65% | 100% | 105.0185 | 105.0185 | 26.2546 | 87.52% | 93.94% | 97.8% | 85.2748
2250 | On | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 97.83% | 20% | 97.83% | 100% | 112.3428 | 112.3428 | 28.0857 | 93.62% | 94.05% | 97.96% | 90.9615
2300 | On | On | On | 1 | 1 | 1 | 1 | 2300 | 120 | 100% | 20% | 100% | 100% | 120 | 120 | 30 | 100% | 94.06% | 96.99% | 98.1234

## Motor Eff Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2016-07-29 14:51
Project Name: | None
Project Number: | None
Engineer: | David
Assumptions
1 | This spreadsheet uses efficiency data for a US Motors 25 hp motor to generate efficiency curves for other motor sizes based on an assumption that the the curve shapes are similar and proportional to the nameplate motor efficiency
2 | Nameplate efficiency from MotorMaster for NEMA Premium Efficiency Motor
3 | ????
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????
Plot Digitizer Data
| Horsepower | Efficiency - Plot Digitizer | Curve From 25 hp Efficiency Equations | 30 hp Motor Load | Projected 30 hp NEMA Premium Efficiency Curve | Curve From 30 hp Efficiency Equations | 40 hp Motor Load | Projected 40 hp NEMA Premium Efficiency Curve | Curve From 40 hp Efficiency Equations | 75 hp Motor Load | Projected 75 hp NEMA Premium Efficiency Curve | Curve From 75 hp Efficiency Equations | 100 hp Motor Load | Projected 100 hp NEMA Premium Efficiency Curve | Curve From 100 hp Efficiency Equations
|  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation
| 0.1255 | 20.09% | 19.77% | 0.1506 | 19.8% | 19.8% | 0.2008 | 19.8% | 19.8% | 0.37651 | 19.99% | 19.99% | 0.50201 | 20.08% | 20.08%
| 0.31376 | 38.43% | 39.12% | 0.37651 | 39.19% | 39.19% | 0.50201 | 39.19% | 39.19% | 0.94127 | 39.56% | 39.56% | 1.255 | 39.73% | 39.73%
| 0.53338 | 49.54% | 50.32% | 0.64006 | 50.42% | 50.42% | 0.85341 | 50.42% | 50.42% | 1.6002 | 50.9% | 50.9% | 2.1335 | 51.11% | 51.11%
| 0.87851 | 61.76% | 60.86% | 1.0542 | 60.97% | 60.97% | 1.4056 | 60.97% | 60.97% | 2.6355 | 61.56% | 61.56% | 3.5141 | 61.82% | 61.82%
| 1.3178 | 70.65% | 69.42% | 1.5813 | 69.55% | 69.55% | 2.1084 | 69.55% | 69.55% | 3.9533 | 70.22% | 70.22% | 5.2711 | 70.51% | 70.51%
| 1.757 | 75.65% | 75.5% | 2.1084 | 75.64% | 75.64% | 2.8112 | 75.64% | 75.64% | 5.2711 | 76.36% | 76.36% | 7.0281 | 76.69% | 76.69%
| 2.259 | 79.68% | 80.8% | 2.7108 | 80.96% | 80.96% | 3.6145 | 80.96% | 80.96% | 6.7771 | 81.73% | 81.73% | 9.0362 | 82.08% | 82.08%
| 3.0748 | 83.7% | 83.36% | 3.6898 | 83.51% | 83.65% | 4.9197 | 83.51% | 83.65% | 9.2244 | 84.31% | 84.45% | 12.2992 | 84.67% | 87.46%
| 3.8592 | 86.34% | 85.71% | 4.631 | 85.87% | 85.95% | 6.1747 | 85.87% | 85.95% | 11.5776 | 86.69% | 86.77% | 15.4368 | 87.06% | 89.67%
| 5.1142 | 89.12% | 88.66% | 6.1371 | 88.83% | 88.84% | 8.1827 | 88.83% | 88.84% | 15.3426 | 89.68% | 89.69% | 20.4568 | 90.05% | 92.26%
| 6.432 | 90.65% | 90.86% | 7.7184 | 91.03% | 91% | 10.2912 | 91.03% | 91% | 19.2959 | 91.9% | 91.87% | 25.7279 | 92.29% | 93.97%
| 7.8125 | 92.04% | 92.38% | 9.375 | 92.55% | 92.5% | 12.5 | 92.55% | 92.5% | 23.4375 | 93.43% | 93.39% | 31.25 | 93.83% | 94.95%
| 10.0088 | 93.15% | 93.59% | 12.0106 | 93.76% | 93.73% | 16.0141 | 93.76% | 93.73% | 30.0264 | 94.66% | 94.62% | 40.0352 | 95.06% | 95.41%
| 13.8052 | 93.84% | 93.82% | 16.5662 | 94% | 94.01% | 22.0883 | 94% | 94.01% | 41.4156 | 94.89% | 94.91% | 55.2208 | 95.29% | 95.08%
| 16.5663 | 93.98% | 93.59% | 19.8796 | 93.77% | 93.81% | 26.5061 | 93.77% | 93.81% | 49.6989 | 94.67% | 94.7% | 66.2652 | 95.07% | 95.05%
| 21.1471 | 93.84% | 93.69% | 25.3765 | 93.87% | 93.88% | 33.8354 | 93.87% | 93.88% | 63.4413 | 94.77% | 94.78% | 84.5884 | 95.17% | 95.49%
| 24.6298 | 93.56% | 93.93% | 29.5558 | 94.11% | 94.08% | 39.4077 | 94.11% | 94.08% | 73.8894 | 95.01% | 94.98% | 98.5192 | 95.41% | 94.04%
| 28.6772 | 92.73% | 92.61% | 34.4126 | 92.78% | 92.8% | 45.8835 | 92.78% | 92.8% | 86.0316 | 93.67% | 93.68% | 114.7088 | 94.07% | 85.01%
|  | Nameplate Horsepower - | 25 |  | 30 |  |  | 40 |  |  | 75 |  |  | 100
|  | Namplate Efficiency - | 93.92% |  | 94.1% |  |  | 94.1% |  |  | 95% |  |  | 95.4%
| 25 hp Motor Equations | y = 0.2111824658028150ln(x) + 0.6359480527478800
| Back to Top | y = -0.00000272882243596700x4 + 0.00020012279554159800x3 - 0.00530280440572924000x2 + 0.05994807399403190000x + 0.69380575105737600000
| 30 hp Motor Equations | y = 0.2115810603234930ln(x) + 0.5985725790998000
| Back to Top | y = -0.00000125333486590551x4 + 0.00011071157367939200x3 - 0.00354093526504893000x2 + 0.04842508461609080000x + 0.70072077798516200000
| 40 hp Motor Equations | y = 0.2115810603234930ln(x) + 0.5377045011743920
| Back to Top | y = -0.00000039656298491363x4 + 0.00004670644514582700x3 - 0.00199177608658508000x2 + 0.03631881346200920000x + 0.70072077798588600000
| 75 hp Motor Equations | y = 0.2136046836422090ln(x) + 0.4085735109043710
| Back to Top | y = -0.00000003239224648108x4 + 0.00000715330890507886x3 - 0.00057196828935814500x2 + 0.01955529453145500000x + 0.70742267703065800000
| 100 hp Motor Equations | y = 0.2145040717838600ln(x) + 0.3485848445038420
| Back to Top | y = -0.00000001977357647103x4 + 0.00000490324034986658x3 - 0.00043734117790208300x2 + 0.01655560495725840000x + 0.72842425147362200000

## VFD Data >= 20 hp
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2016-07-29 14:51
Project Name: | None
Project Number: | None
Engineer: | David
Assumptions
1 | This spreadsheet uses efficiency data for a Safetronics 20 hp VFD to generate efficiency curves for other VFD sizes based on an assumption that the the curve shapes are similar and proportional to the nameplate VFD efficiency. It produces fairly accurate results relative to the DOE data for mpst sizes above 20 hp. In fact, for most sizes about 20 hp, the efficiencis are vitrually identical above about 42% rated load. For less than 20 hp, use the tab for 10 hp and less. The projections are off the most at the 1.6% and 12.5% load conditions,understating efficiency by3% and 1.9% respectsively for the 40 hp projection. Most of the time, minimum speed restrictions will prevent HVAC system operation at these conditons.
2 | Nameplate efficiency from Safetronics Data published in the referenced DOE tip sheet on VFD efficiency
3
4
5
6
7
8
| Horsepower | Efficiency - Safetronics Data | Curve From 20 hp Efficiency Equations | 25 hp VFD Load | Projected 25 hp VFD Efficiency Curve | Curve From 25 hp Efficiency Equations | 30 hp VFD Load | Projected 30 hp VFD Efficiency Curve | Curve From 30 hp Efficiency Equations | 40 hp VFD Load | Projected 40 hp VFD Efficiency Curve | Curve From 40 hp Efficiency Equations | 75 hp VFD Load | Projected 75 hp VFD Efficiency Curve | Curve From 75 hp Efficiency Equations | 100 hp VFD Load | Projected 100 hp VFD Efficiency Curve | Curve From 100 hp Efficiency Equations
|  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation
| 0.32 | 47% | 47% | 0.4 | 47% | 47% | 0.48 | 47% | 47% | 0.64 | 47% | 47% | 1.2 | 47% | 47% | 1.6 | 47% | 47%
| 2.5 | 86% | 86.06% | 3.125 | 86.06% | 84.14% | 3.75 | 84.14% | 84.15% | 5 | 86.06% | 86.06% | 9.375 | 86.06% | 86.06% | 12.5 | 86.06% | 86.06%
| 5 | 93% | 92.78% | 6.25 | 92.78% | 92.78% | 7.5 | 92.78% | 92.74% | 10 | 92.78% | 92.78% | 18.75 | 92.78% | 92.78% | 25 | 92.78% | 92.78%
| 8.4 | 94% | 94.57% | 10.5 | 94.57% | 94.57% | 12.6 | 94.57% | 94.68% | 16.8 | 94.57% | 94.57% | 31.5 | 94.57% | 94.57% | 42 | 94.57% | 94.57%
| 10 | 95% | 94.53% | 12.5 | 94.53% | 94.53% | 15 | 94.53% | 94.44% | 20 | 94.53% | 94.53% | 37.5 | 94.53% | 94.53% | 50 | 94.53% | 94.53%
| 15 | 96% | 96.07% | 18.75 | 96.07% | 96.07% | 22.5 | 96.07% | 96.08% | 30 | 96.07% | 96.07% | 56.25 | 96.07% | 96.07% | 75 | 96.07% | 96.07%
| 20 | 97% | 96.99% | 25 | 96.99% | 96.99% | 30 | 96.99% | 96.99% | 40 | 96.99% | 96.99% | 75 | 96.99% | 96.99% | 100 | 96.99% | 96.99%
|  | Rated Horsepower - | 20 |  | 25 |  |  | 30 |  |  | 40 |  |  | 75 |  |  | 100
|  | Rated Efficiency - | 97% |  | 97% |  |  | 97% |  |  | 97% |  |  | 97% |  |  | 97%
| 20 hp VFD Equations | y = 0.1788990825688070x + 0.4127522935779820
| Back to Top | y = -0.00001436037018445750x4 + 0.00071268036973309900x3 - 0.01244805814563230000x2 + 0.09243085290103550000x + 0.69673004683703800000
| 25 hp VFD Equations | y = 0.1433326585307060x + 0.4126669365877180
| Back to Top | y = -0.00000588200762753621x4 + 0.00036489234930193300x3 - 0.00796675721317327000x2 + 0.07394468232088740000x + 0.69673004683416500000
| 30 hp VFD Equations | y = 0.1135902151463750x + 0.4154766967297400
| Back to Top | y = -0.00000380965434349997x4 + 0.00028312423935715800x3 - 0.00738946953923258000x2 + 0.08116549615999030000x + 0.62691382111474400000
| 40 hp VFD Equations | y = 0.0895829115816913x + 0.4126669365877180
| Back to Top | y = -0.00000089752313652599x4 + 0.00008908504621630770x3 - 0.00311201453639731000x2 + 0.04621542645027710000x + 0.69673004683940300000
| 75 hp VFD Equations | y = 0.0477775528435687x + 0.4126669365877180
| Back to Top | y = -0.00000007261737811830x4 + 0.00001351453145572600x3 - 0.00088519524591471800x2 + 0.02464822744039140000x + 0.69673004683638800000
| 100 hp VFD Equations | y = 0.0358331646326765x + 0.4126669365877180
| Back to Top | y = -0.00000002297659229506x4 + 0.00000570144295784271x3 - 0.00049792232582333000x2 + 0.01848617058022180000x + 0.69673004683416500000
| Safetronics Data | DOE Drive Efficiencyh Tip Sheet
Load | 1.6% | 12.5% | 25% | 42% | 50% | 75% |  |  |  | 100%
hp | 0.32 | 2.5 | 5 | 8.4 | 10 | 15 |  |  |  | 20
20 | 47% | 86% | 93% | 94% | 95% | 96% |  |  |  | 97%

## Hours at tonages
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2016-07-10 14:14
Project Name: | Seattle Muni Tower
Project Number:
Engineer: | David
Assumptions
1 | Date Range Lable |  | Thursday 09/24/15 12:00 AM thorugh Monday 12/07/15 11:59 PM
2 | ????
3 | ????
4 | ????
5 | ????
6 | ???? | [13 empty] | 1
7 | ????
8 | ????
From data to date
|  | 1 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 2500
| Minutes at less than or equal to the given tonnage | 366 | 8448 | 10440 | 12146 | 12701 | 13163 | 13535 | 14015 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184 | 14184
|  | <1 | 1 - 100 | 100 - 200 | 200 - 300 | 300 - 400 | 400 - 500 | 500 - 600 | 600 - 700 | 700 - 800 | 800 - 900 | 900 - 1,000 | 1,000 - 1,100 | 1,100 - 1,200 | 1,200 - 1,300 | 1,300 - 1,400 | 1,400 - 1,500 | 1,500 - 1,600 | 1,600 - 1,700 | 1,700 - 1,800 | 1,800 - 1,900 | 1,900 - 2,000 | 2,000 - 2,100 | 2,100 - 2,200 | 2,200 - 2,300 | 2,300 - 2,400 | 2,400 - 2,500
| Minutes at less than or equal to the given tonnage | 366 | 8082 | 1992 | 1706 | 555 | 462 | 372 | 480 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hours at less than or equal to the given tonnage | 6.1 | 134.7 | 33.2 | 28.4333 | 9.25 | 7.7 | 6.2 | 8 | 2.8167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
From Regression based on data to date
|  | 1 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 1900 | 2000 | 2100 | 2200 | 2300 | 2400 | 2500
| Hours at less than or equal to the given tonnage | 5988 | 7393 | 8034 | 8203 | 8366 | 8484 | 8533 | 8576 | 8612 | 8627 | 8648 | 8670 | 8670 | 8695 | 8709 | 8709 | 8720 | 8736 | 8736 | 8742 | 8742 | 8748 | 8748 | 8749 | 8749 | 8760
|  | <1 | <100 | 100 - 200 | 200 - 300 | 300 - 400 | 400 - 500 | 500 - 600 | 600 - 700 | 700 - 800 | 800 - 900 | 900 - 1,000 | 1,000 - 1,100 | 1,100 - 1,200 | 1,200 - 1,300 | 1,300 - 1,400 | 1,400 - 1,500 | 1,500 - 1,600 | 1,600 - 1,700 | 1,700 - 1,800 | 1,800 - 1,900 | 1,900 - 2,000 | 2,000 - 2,100 | 2,100 - 2,200 | 2,200 - 2,300 | 2,300 - 2,400 | 2,400 - 2,500
| Hours at less than or equal to the given tonnage | 5988 | 1405 | 641 | 169 | 163 | 118 | 49 | 43 | 36 | 15 | 21 | 22 | 0 | 25 | 14 | 0 | 11 | 16 | 0 | 6 | 0 | 6 | 0 | 1 | 0 | 11 | 2772
|  |  | 50 | 150 | 250 | 350 | 450 | 550 | 650 | 750 | 850 | 950 | 1050 | 1150 | 1250 | 1350 | 1450 | 1550 | 1650 | 1750 | 1850 | 1950 | 2050 | 2150 | 2250 | 2350 | 2450