## Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2009-08-05
Project Name: | UCB MBCx LeConte Hall AHU-2 Existing Condition
Project Number: | NUMBER?
Engineer: | David
Assumptions |  |  |  |  | Number | Filter Cost | Labor Cost | Waste, cu. Yd | Disposal Cost | Make | Model
1 | Prefilters - |  |  |  | 20 | 4.4 | 2 | 0.024691 | 0 | Camfil Farr | 24" x 24" x 2" (Cost based on recent pricing for similar)
2 | Final Filters - |  |  |  | 20 | 27.16 | 5 | 0.22222 | 0 | Camfil Farr | S Flow 65/24/24/22/8 (Cost based on recent pricing for similar)
3 | Loading assumptions:
4 |  | Number of intervals with linear match to DMV Data -
5 | Initial pressure drop from calculations done for 06 AHU2 Zn Lvl Schedule - Savings v1.xls.
6 | ???? | [28 empty] | 771.2
7 | ????
8 | ????
| Interval | [6 empty] | Filter | [11 empty] | Fan Power and Energy | [9 empty] | Filter Operating Cost $ per Average Day |  |  | Filter Operating Cost for Proposed Option, $ per Average Day | Accumulated Savings
| Number | Start Date | End Date | Weeks | Median Date | Hours of Operation per Week | Hours of Operation for the Interval | Filter First Cost | [5 empty] | Cost per average day through this interval | Pressure drop, in.w.c. |  |  |  | Flow rate, cfm | Fan efficiency | Fan bhp for filter pressure drop | Motor efficiency | Drive efficiency | Motor kW for filter pressure drop | Electric rate - $ per kWh | kWh |  | $ |  | Filter Cost | Fan Energy | Total
[8 empty] | Prefilter | Final Filter | Installation Labor | Disposal |  | Total Filter Cost |  | Start | Increase | End | Median | [7 empty] | Total for the interval | Per average day | Total | Per average day |  |  |  |  | Cost for the interval
[11 empty] | Cubic Yards | Cost | [21 empty] | Existing Approach | Proposed Approach | Savings | Accumulated Savings
| 1 | 2009-09-01 | 2009-09-29 | 4 | 2009-09-15 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 27.5429 | 0.38 | 0.039979 | 0.41998 | 0.39999 | 32000 | 72% | 2.7969 | 93% | 95% | 2.3616 | 0.1 | 1587.0253 | 56.6795 | 158.7025 | 5.6679 | 27.5429 | 5.6679 | 33.2108 | 0 | 929.9025 | 0 | 929.9025 | 929.9025
| 2 | 2009-09-29 | 2009-10-27 | 4 | 2009-10-13 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 13.7714 | 0.41998 | 0.039979 | 0.45996 | 0.43997 | 32000 | 72% | 3.0765 | 93% | 95% | 2.5977 | 0.1 | 1745.6494 | 62.3446 | 174.5649 | 6.2345 | 13.7714 | 6.2345 | 20.0059 | Total | 174.5649 | $ | 174.5649 | 1104.4675
| 3 | 2009-10-27 | 2009-11-24 | 4 | 2009-11-10 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 9.181 | 0.45996 | 0.039979 | 0.49994 | 0.47995 | 32000 | 72% | 3.356 | 93% | 95% | 2.8337 | 0.1 | 1904.2735 | 68.0098 | 190.4274 | 6.801 | 9.181 | 6.801 | 15.9819 | 0 | 190.4274 | Total | 190.4274 | 1294.8948
| 4 | 2009-11-24 | 2009-12-22 | 4 | 2009-12-08 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 6.8857 | 0.49994 | 0.039979 | 0.53992 | 0.51993 | 32000 | 72% | 3.6356 | 93% | 95% | 3.0698 | 0.1 | 2062.8977 | 73.6749 | 206.2898 | 7.3675 | 6.8857 | 7.3675 | 14.2532 | 0 | 206.2898 | 0 | 206.2898 | 1501.1846
| 5 | 2009-12-22 | 2010-01-19 | 4 | 2010-01-05 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 5.5086 | 0.53992 | 0.039979 | 0.5799 | 0.55991 | 32000 | 72% | 3.9152 | 93% | 95% | 3.3058 | 0.1 | 2221.5218 | 79.3401 | 222.1522 | 7.934 | 5.5086 | 7.934 | 13.4426 | 71.6009 | 222.1522 | 44.8243 | 177.3279 | 1678.5125
| 6 | 2010-01-19 | 2010-02-16 | 4 | 2010-02-02 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 4.5905 | 0.5799 | 0.039979 | 0.61988 | 0.59989 | 32000 | 72% | 4.1947 | 93% | 95% | 3.5419 | 0.1 | 2380.1459 | 85.0052 | 238.0146 | 8.5005 | 4.5905 | 8.5005 | 13.091 | 36.6852 | 238.0146 | 47.1843 | 190.8303 | 1869.3428
| 7 | 2010-02-16 | 2010-03-16 | 4 | 2010-03-02 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 3.9347 | 0.61988 | 0.039979 | 0.65985 | 0.63986 | 32000 | 72% | 4.4743 | 93% | 95% | 3.7779 | 0.1 | 2538.7701 | 90.6704 | 253.877 | 9.067 | 3.9347 | 9.067 | 13.0017 | 25.1028 | 253.877 | 49.5442 | 204.3328 | 2073.6756
| 8 | 2010-03-16 | 2010-04-13 | 4 | 2010-03-30 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 3.4429 | 0.65985 | 0.039979 | 0.69983 | 0.67984 | 32000 | 72% | 4.7538 | 93% | 95% | 4.014 | 0.1 | 2697.3942 | 96.3355 | 269.7394 | 9.6336 | 3.4429 | 9.6336 | 13.0764 | 19.3537 | 269.7394 | 51.9042 | 217.8353 | 2291.5108
| 9 | 2010-04-13 | 2010-05-11 | 4 | 2010-04-27 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 3.0603 | 0.69983 | 0.039979 | 0.73981 | 0.71982 | 32000 | 72% | 5.0334 | 93% | 95% | 4.25 | 0.1 | 2856.0184 | 102.0007 | 285.6018 | 10.2001 | 3.0603 | 10.2001 | 13.2604 | 15.938 | 285.6018 | 54.2641 | 231.3377 | 2522.8486
| 10 | 2010-05-11 | 2010-06-08 | 4 | 2010-05-25 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 2.7543 | 0.73981 | 0.039979 | 0.77979 | 0.7598 | 32000 | 72% | 5.3129 | 93% | 95% | 4.4861 | 0.1 | 3014.6425 | 107.6658 | 301.4642 | 10.7666 | 2.7543 | 10.7666 | 13.5209 | 13.689 | 301.4642 | 56.6241 | 244.8402 | 2767.6887
| 11 | 2010-06-08 | 2010-07-06 | 4 | 2010-06-22 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 2.5039 | 0.77979 | 0.039979 | 0.81977 | 0.79978 | 32000 | 72% | 5.5925 | 93% | 95% | 4.7221 | 0.1 | 3173.2666 | 113.331 | 317.3267 | 11.3331 | 2.5039 | 11.3331 | 13.837 | 12.1066 | 317.3267 | 58.984 | 258.3426 | 3026.0314
| 12 | 2010-07-06 | 2010-08-03 | 4 | 2010-07-20 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 2.2952 | 0.81977 | 0.039979 | 0.85975 | 0.83976 | 32000 | 72% | 5.872 | 93% | 95% | 4.9582 | 0.1 | 3331.8908 | 118.9961 | 333.1891 | 11.8996 | 2.2952 | 11.8996 | 14.1948 | 10.9409 | 333.1891 | 61.344 | 271.8451 | 3297.8765
| 13 | 2010-08-03 | 2010-08-31 | 4 | 2010-08-17 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 2.1187 | 0.85975 | 0.039979 | 0.89973 | 0.87974 | 32000 | 72% | 6.1516 | 93% | 95% | 5.1942 | 0.1 | 3490.5149 | 124.6612 | 349.0515 | 12.4661 | 2.1187 | 12.4661 | 14.5848 | 10.0529 | 349.0515 | 63.7039 | 285.3476 | 3583.224
| 14 | 2010-08-31 | 2010-09-28 | 4 | 2010-09-14 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.9673 | 0.89973 | 0.039979 | 0.93971 | 0.91972 | 32000 | 72% | 6.4312 | 93% | 95% | 5.4303 | 0.1 | 3649.139 | 130.3264 | 364.9139 | 13.0326 | 1.9673 | 13.0326 | 15 | 9.3594 | 364.9139 | 66.0639 | 298.85 | 3882.074
| 15 | 2010-09-28 | 2010-10-26 | 4 | 2010-10-12 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.8362 | 0.93971 | 0.039979 | 0.97969 | 0.9597 | 32000 | 72% | 6.7107 | 93% | 95% | 5.6663 | 0.1 | 3807.7632 | 135.9915 | 380.7763 | 13.5992 | 1.8362 | 13.5992 | 15.4353 | 8.8073 | 380.7763 | 68.4238 | 312.3525 | 4194.4265
| 16 | 2010-10-26 | 2010-11-23 | 4 | 2010-11-09 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.7214 | 0.97969 | 0.039979 | 1.0197 | 0.99968 | 32000 | 72% | 6.9903 | 93% | 95% | 5.9024 | 0.1 | 3966.3873 | 141.6567 | 396.6387 | 14.1657 | 1.7214 | 14.1657 | 15.8871 | 8.3613 | 396.6387 | 70.7838 | 325.8549 | 4520.2814
| 17 | 2010-11-23 | 2010-12-21 | 4 | 2010-12-07 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.6202 | 1.0197 | 0.039979 | 1.0596 | 1.0397 | 32000 | 72% | 7.2698 | 93% | 95% | 6.1384 | 0.1 | 4125.0114 | 147.3218 | 412.5011 | 14.7322 | 1.6202 | 14.7322 | 16.3524 | 7.9969 | 412.5011 | 73.1438 | 339.3574 | 4859.6388
| 18 | 2010-12-21 | 2011-01-18 | 4 | 2011-01-04 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.5302 | 1.0596 | 0.039979 | 1.0996 | 1.0796 | 32000 | 72% | 7.5494 | 93% | 95% | 6.3745 | 0.1 | 4283.6356 | 152.987 | 428.3636 | 15.2987 | 1.5302 | 15.2987 | 16.8289 | 7.6966 | 428.3636 | 75.5037 | 352.8599 | 5212.4987
| 19 | 2011-01-18 | 2011-02-15 | 4 | 2011-02-01 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.4496 | 1.0996 | 0.039979 | 1.1396 | 1.1196 | 32000 | 72% | 7.8289 | 93% | 95% | 6.6105 | 0.1 | 4442.2597 | 158.6521 | 444.226 | 15.8652 | 1.4496 | 15.8652 | 17.3148 | 7.4475 | 444.226 | 77.8637 | 366.3623 | 5578.861
| 20 | 2011-02-15 | 2011-03-15 | 4 | 2011-03-01 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.3771 | 1.1396 | 0.039979 | 1.1796 | 1.1596 | 32000 | 72% | 8.1085 | 93% | 95% | 6.8466 | 0.1 | 4600.8838 | 164.3173 | 460.0884 | 16.4317 | 1.3771 | 16.4317 | 17.8089 | 7.2401 | 460.0884 | 80.2236 | 379.8648 | 5958.7258
| 21 | 2011-03-15 | 2011-04-12 | 4 | 2011-03-29 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.3116 | 1.1796 | 0.039979 | 1.2196 | 1.1996 | 32000 | 72% | 8.388 | 93% | 95% | 7.0826 | 0.1 | 4759.508 | 169.9824 | 475.9508 | 16.9982 | 1.3116 | 16.9982 | 18.3098 | 7.0671 | 475.9508 | 82.5836 | 393.3672 | 6352.093
| 22 | 2011-04-12 | 2011-05-10 | 4 | 2011-04-26 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.2519 | 1.2196 | 0.039979 | 1.2595 | 1.2396 | 32000 | 72% | 8.6676 | 93% | 95% | 7.3186 | 0.1 | 4918.1321 | 175.6476 | 491.8132 | 17.5648 | 1.2519 | 17.5648 | 18.8167 | 6.9226 | 491.8132 | 84.9435 | 406.8697 | 6758.9627
| 23 | 2011-05-10 | 2011-06-07 | 4 | 2011-05-24 | 168 | 672 | 88 | 543.2 | 140 | 4.9383 | 0 | 771.2 | 1.1975 | 1.2595 | 0.039979 | 1.2995 | 1.2795 | 32000 | 72% | 8.9472 | 93% | 95% | 7.5547 | 0.1 | 5076.7563 | 181.3127 | 507.6756 | 18.1313 | 1.1975 | 18.1313 | 19.3288 | 6.8022 | 1278.8756 | 87.3035 | 1191.5721 | 7950.5348
| 24 | 2011-06-07 | 2011-07-05 | 4 | 2011-06-21 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 2.2952 | 0.38 | 0.039979 | 0.41998 | 0.39999 | 32000 | 72% | 2.7969 | 93% | 95% | 2.3616 | 0.1 | 1587.0253 | 56.6795 | 158.7025 | 5.6679 | 2.2952 | 5.6679 | 7.9632 | 6.7023 | 158.7025 | 89.6634 | 69.0391 | 8019.5739
| 25 | 2011-07-05 | 2011-08-02 | 4 | 2011-07-19 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 2.2034 | 0.41998 | 0.039979 | 0.45996 | 0.43997 | 32000 | 72% | 3.0765 | 93% | 95% | 2.5977 | 0.1 | 1745.6494 | 62.3446 | 174.5649 | 6.2345 | 2.2034 | 6.2345 | 8.4379 | 6.6199 | 174.5649 | 92.0234 | 82.5416 | 8102.1155
| 26 | 2011-08-02 | 2011-08-30 | 4 | 2011-08-16 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 2.1187 | 0.45996 | 0.039979 | 0.49994 | 0.47995 | 32000 | 72% | 3.356 | 93% | 95% | 2.8337 | 0.1 | 1904.2735 | 68.0098 | 190.4274 | 6.801 | 2.1187 | 6.801 | 8.9197 | 6.5527 | 190.4274 | 94.3833 | 96.044 | 8198.1595
| 27 | 2011-08-30 | 2011-09-27 | 4 | 2011-09-13 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 2.0402 | 0.49994 | 0.039979 | 0.53992 | 0.51993 | 32000 | 72% | 3.6356 | 93% | 95% | 3.0698 | 0.1 | 2062.8977 | 73.6749 | 206.2898 | 7.3675 | 2.0402 | 7.3675 | 9.4077 | 6.4986 | 206.2898 | 96.7433 | 109.5465 | 8307.706
| 28 | 2011-09-27 | 2011-10-25 | 4 | 2011-10-11 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.9673 | 0.53992 | 0.039979 | 0.5799 | 0.55991 | 32000 | 72% | 3.9152 | 93% | 95% | 3.3058 | 0.1 | 2221.5218 | 79.3401 | 222.1522 | 7.934 | 1.9673 | 7.934 | 9.9014 | 6.4561 | 222.1522 | 99.1032 | 123.0489 | 8430.7549
| 29 | 2011-10-25 | 2011-11-22 | 4 | 2011-11-08 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.8995 | 0.5799 | 0.039979 | 0.61988 | 0.59989 | 32000 | 72% | 4.1947 | 93% | 95% | 3.5419 | 0.1 | 2380.1459 | 85.0052 | 238.0146 | 8.5005 | 1.8995 | 8.5005 | 10.4 | 6.4237 | 238.0146 | 101.4632 | 136.5514 | 8567.3063
| 30 | 2011-11-22 | 2011-12-20 | 4 | 2011-12-06 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.8362 | 0.61988 | 0.039979 | 0.65985 | 0.63986 | 32000 | 72% | 4.4743 | 93% | 95% | 3.7779 | 0.1 | 2538.7701 | 90.6704 | 253.877 | 9.067 | 1.8362 | 9.067 | 10.9032 | 6.4003 | 253.877 | 103.8232 | 150.0539 | 8717.3602
| 31 | 2011-12-20 | 2012-01-17 | 4 | 2012-01-03 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.777 | 0.65985 | 0.039979 | 0.69983 | 0.67984 | 32000 | 72% | 4.7538 | 93% | 95% | 4.014 | 0.1 | 2697.3942 | 96.3355 | 269.7394 | 9.6336 | 1.777 | 9.6336 | 11.4105 | 6.3848 | 269.7394 | 106.1831 | 163.5563 | 8880.9165
| 32 | 2012-01-17 | 2012-02-14 | 4 | 2012-01-31 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.7214 | 0.69983 | 0.039979 | 0.73981 | 0.71982 | 32000 | 72% | 5.0334 | 93% | 95% | 4.25 | 0.1 | 2856.0184 | 102.0007 | 285.6018 | 10.2001 | 1.7214 | 10.2001 | 11.9215 | 6.3765 | 285.6018 | 108.5431 | 177.0588 | 9057.9752
| 33 | 2012-02-14 | 2012-03-13 | 4 | 2012-02-28 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.6693 | 0.73981 | 0.039979 | 0.77979 | 0.7598 | 32000 | 72% | 5.3129 | 93% | 95% | 4.4861 | 0.1 | 3014.6425 | 107.6658 | 301.4642 | 10.7666 | 1.6693 | 10.7666 | 12.4358 | 6.3746 | 301.4642 | 110.903 | 190.5612 | 9248.5365
| 34 | 2012-03-13 | 2012-04-10 | 4 | 2012-03-27 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.6202 | 0.77979 | 0.039979 | 0.81977 | 0.79978 | 32000 | 72% | 5.5925 | 93% | 95% | 4.7221 | 0.1 | 3173.2666 | 113.331 | 317.3267 | 11.3331 | 1.6202 | 11.3331 | 12.9533 | 6.3784 | 317.3267 | 113.263 | 204.0637 | 9452.6002
| 35 | 2012-04-10 | 2012-05-08 | 4 | 2012-04-24 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.5739 | 0.81977 | 0.039979 | 0.85975 | 0.83976 | 32000 | 72% | 5.872 | 93% | 95% | 4.9582 | 0.1 | 3331.8908 | 118.9961 | 333.1891 | 11.8996 | 1.5739 | 11.8996 | 13.4735 | 6.3875 | 333.1891 | 115.6229 | 217.5662 | 9670.1663
| 36 | 2012-05-08 | 2012-06-05 | 4 | 2012-05-22 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.5302 | 0.85975 | 0.039979 | 0.89973 | 0.87974 | 32000 | 72% | 6.1516 | 93% | 95% | 5.1942 | 0.1 | 3490.5149 | 124.6612 | 349.0515 | 12.4661 | 1.5302 | 12.4661 | 13.9963 | 6.4012 | 349.0515 | 117.9829 | 231.0686 | 9901.2349
| 37 | 2012-06-05 | 2012-07-03 | 4 | 2012-06-19 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.4888 | 0.89973 | 0.039979 | 0.93971 | 0.91972 | 32000 | 72% | 6.4312 | 93% | 95% | 5.4303 | 0.1 | 3649.139 | 130.3264 | 364.9139 | 13.0326 | 1.4888 | 13.0326 | 14.5214 | 6.4192 | 364.9139 | 120.3428 | 244.5711 | 10145.806
| 38 | 2012-07-03 | 2012-07-31 | 4 | 2012-07-17 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.4496 | 0.93971 | 0.039979 | 0.97969 | 0.9597 | 32000 | 72% | 6.7107 | 93% | 95% | 5.6663 | 0.1 | 3807.7632 | 135.9915 | 380.7763 | 13.5992 | 1.4496 | 13.5992 | 15.0488 | 6.4411 | 380.7763 | 122.7028 | 258.0735 | 10403.8796
| 39 | 2012-07-31 | 2012-08-28 | 4 | 2012-08-14 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.4125 | 0.97969 | 0.039979 | 1.0197 | 0.99968 | 32000 | 72% | 6.9903 | 93% | 95% | 5.9024 | 0.1 | 3966.3873 | 141.6567 | 396.6387 | 14.1657 | 1.4125 | 14.1657 | 15.5781 | 6.4665 | 396.6387 | 125.0627 | 271.576 | 10675.4555
| 40 | 2012-08-28 | 2012-09-25 | 4 | 2012-09-11 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.3771 | 1.0197 | 0.039979 | 1.0596 | 1.0397 | 32000 | 72% | 7.2698 | 93% | 95% | 6.1384 | 0.1 | 4125.0114 | 147.3218 | 412.5011 | 14.7322 | 1.3771 | 14.7322 | 16.1093 | 6.4953 | 412.5011 | 127.4227 | 285.0785 | 10960.534
| 41 | 2012-09-25 | 2012-10-23 | 4 | 2012-10-09 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.3436 | 1.0596 | 0.039979 | 1.0996 | 1.0796 | 32000 | 72% | 7.5494 | 93% | 95% | 6.3745 | 0.1 | 4283.6356 | 152.987 | 428.3636 | 15.2987 | 1.3436 | 15.2987 | 16.6423 | 6.527 | 428.3636 | 129.7826 | 298.5809 | 11259.1149
| 42 | 2012-10-23 | 2012-11-20 | 4 | 2012-11-06 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.3116 | 1.0996 | 0.039979 | 1.1396 | 1.1196 | 32000 | 72% | 7.8289 | 93% | 95% | 6.6105 | 0.1 | 4442.2597 | 158.6521 | 444.226 | 15.8652 | 1.3116 | 15.8652 | 17.1768 | 6.5615 | 444.226 | 132.1426 | 312.0834 | 11571.1983
| 43 | 2012-11-20 | 2012-12-18 | 4 | 2012-12-04 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.2811 | 1.1396 | 0.039979 | 1.1796 | 1.1596 | 32000 | 72% | 8.1085 | 93% | 95% | 6.8466 | 0.1 | 4600.8838 | 164.3173 | 460.0884 | 16.4317 | 1.2811 | 16.4317 | 17.7128 | 6.5985 | 460.0884 | 134.5026 | 325.5858 | 11896.7841
| 44 | 2012-12-18 | 2013-01-15 | 4 | 2013-01-01 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.2519 | 1.1796 | 0.039979 | 1.2196 | 1.1996 | 32000 | 72% | 8.388 | 93% | 95% | 7.0826 | 0.1 | 4759.508 | 169.9824 | 475.9508 | 16.9982 | 1.2519 | 16.9982 | 18.2502 | 6.6379 | 475.9508 | 136.8625 | 339.0883 | 12235.8724
| 45 | 2013-01-15 | 2013-02-12 | 4 | 2013-01-29 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.2241 | 1.2196 | 0.039979 | 1.2595 | 1.2396 | 32000 | 72% | 8.6676 | 93% | 95% | 7.3186 | 0.1 | 4918.1321 | 175.6476 | 491.8132 | 17.5648 | 1.2241 | 17.5648 | 18.7889 | 6.6795 | 491.8132 | 139.2225 | 352.5908 | 12588.4632
| 46 | 2013-02-12 | 2013-03-12 | 4 | 2013-02-26 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.1975 | 1.2595 | 0.039979 | 1.2995 | 1.2795 | 32000 | 72% | 8.9472 | 93% | 95% | 7.5547 | 0.1 | 5076.7563 | 181.3127 | 507.6756 | 18.1313 | 1.1975 | 18.1313 | 19.3288 | 6.7232 | 507.6756 | 141.5824 | 366.0932 | 12954.5564
| 47 | 2013-03-12 | 2013-04-09 | 4 | 2013-03-26 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.172 | 1.2995 | 0.039979 | 1.3395 | 1.3195 | 32000 | 72% | 9.2267 | 93% | 95% | 7.7907 | 0.1 | 5235.3804 | 186.9779 | 523.538 | 18.6978 | 1.172 | 18.6978 | 19.8698 | 6.7687 | 523.538 | 143.9424 | 379.5957 | 13334.152
| 48 | 2013-04-09 | 2013-05-07 | 4 | 2013-04-23 | 168 | 672 | 176 | 1086.4 | 280 | 9.8765 | 0 | 1542.4 | 1.1476 | 1.3395 | 0.039979 | 1.3795 | 1.3595 | 32000 | 72% | 9.5063 | 93% | 95% | 8.0268 | 0.1 | 5394.0045 | 192.643 | 539.4005 | 19.2643 | 1.1476 | 19.2643 | 20.4119 | 6.816 | 539.4005 | 146.3023 | 393.0981 | 13727.2502
[26 empty] | 163896.3599 |  | 16389.636
Formulas:
End Date = ([Weeks]*7)+[Start Date]
Number = ([Start Date]+[End Date])/2
Start Date = [End Date, row above]

## Initial pressure drop
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2008-04-02 07:58
Project Name: | CA DGA DMV
Project Number: | NUMBER?
Engineer: | David
Assumptions
1 | ????
2 | ????
3 | ????
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????
Projected clean pressure drops based on manufacturer's rating data
AHU-C
Prefilter
Filtration Group Series 400, 2"
Velocity, fpm
|  | 375 | 500
| Rated pressure drop | 0.18 | 0.28
| Linear relationship | 0.18 | 0.24
| Square law | 0.18 | 0.32
| Average face velocity, AHU-C | 407.5208
| Projected clean pressure drop, linear interpolation | 0.19561
Final filter
Filtration Group Series 6 pocket MERV 11, 22" deep
Velocity, fpm
|  | 375 | 500 | 625
| Rated pressure drop | 0.2 | 0.25 | 0.37
| Linear relationship | 0.2 | 0.26667 | 0.33333
| Square law | 0.2 | 0.35556 | 0.55556
| Average face velocity, AHU-C | 407.5208
| Projected clean pressure drop, linear interpolation | 0.21734
| Total initial clean pressure drop, AHU-C | 0.41295
AHU-A
Freudenberg Viledon MV4 24 x 24 x 12 MERV 14
| Average face velocity, AHU-A | 338.8542
| Average cfm per filter, AHU-A | 1129.5139
| Projected clean pressure drop, linear interpolation | 0.18072
Pressure drop vs. time graph
| AHU-A operating hours per day | 10 | Normally, but it ran round the clock from the time the VFDs were installed until mid January when the controls were in place for scheduling
| Number of days AHU-A ran round the clock | 62 | Approximate, based on discussions with field staff.
| AHU-C operating hours per day | 24
| Date | Pressure drop, in.w.c. |  | Operating hours |  | Rate of Change, in.w.c. per 1,000 hours
|  | AHU-A | AHU-C | AHU-A | AHU-C | AHU-A | AHU-C
| 2007-10-21 | 0.18072 | 0.41295 | 0 | 0
| 2008-02-29 | 0.2 | 0.6 | 2178 | 3144 | 0.0088511 | 0.059493

## Summary
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2009-08-05 13:02
Project Name: | UCB MBCx LeConte Hall
Project Number: | 09084
Engineer: | David Sellers
Finding: | 03 AHU1 Filter Upgrade
Assumptions
1 | ????
2 | ????
3 | ????
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????
EXTENDED SURFACE AREA FILTER SAVINGS
Savings Summary
Savings Summary - First Year Basis
|  | Fan Energy |  | Filter Cost |  |  | Total Cost | Waste
|  | $ | kWh | Filters | Labor | Total
| Existing Approach | 2951.3496 | 29513.4962 | 631.2 | 140 | 771.2 | 3722.5496 | 4.9383
| Proposed Approach | 424.6732 | 4246.7316 | 1860 | 100 | 1960 | 2384.6732 | 4.4444
| Savings | 2526.6765 | 25266.7646 | -1228.8 | 40 | -1188.8 | 1337.8765 | 0.49383
Savings Summary - 48 Month Cycle Basis
|  | Fan Energy |  | Filter Cost |  |  | Total Cost | Waste
|  | $ | kWh | Filters | Labor | Total
| Existing Approach | 16389.636 | 163896.3599 | 1262.4 | 280 | 1542.4 | 17932.036 | 9.8765
| Proposed Approach | 148.6623 | 1486.6228 | 1860 | 100 | 1960 | 2108.6623 | 4.4444
| Savings | 16240.9737 | 162409.7371 | -597.6 | 180 | -417.6 | 15823.3737 | 5.4321
EXTENDED SURFACE AREA FILTER SIMPLE PAYBACK, ENERGY ONLY
First year of operation basis
| First year energy savings - | 2526.6765 | (25,267 kWh)
| First year cost premium - | 1228.8 | (more expensive filters)
| Simple payback - | 5.836 | months, energy only
| First year total savings - | 2566.6765 | (25,267 kWh plus $40 in filter installation labor)
| First year cost premium - | 1228.8 | (more expensive filters)
| Simple payback - | 5.745 | months all inclusive
Extended Surface Area Filter Life Cycle Basis
| Life cycle energy savings - | 16240.9737 | ( 162,410 kWh)
| Life cycle cost premium - | 597.6 | (more expensive filters)
| Simple payback - | 0.036796 | life cycles, energy only
| Simple payback - | 1.7662 | months, energy only
| Life cycle total savings - | 16420.9737 | (162,410 kWh plus $180 in filter installation labor)
| Life cycle cost premium - | 597.6 | (more expensive filters)
| Simple payback - | 0.036392 | life cycles, energy only
| Simple payback - | 1.7468 | months all inclusive
FORMATED TABLE FOR REPORTS AND GRAPHS
Savings Summary - First Year Basis
[10 empty] | Electricity |  | Filters | Total | Waste
[10 empty] | kWh | $ | $ | $ | cubic yards
[9 empty] | Existing Approach | 29513.4962 | 2951.3496 | 631.2 | 3582.5496 | 4.9383
[9 empty] | Proposed Approach | 4246.7316 | 424.6732 | 1860 | 2284.6732 | 4.4444
[9 empty] | Savings | 25266.7646 | 2526.6765 | -1228.8 | 1297.8765 | 0.49383
[9 empty] | Simple Payback | 0.48633 | years (energy only)
Savings Summary - 48 Month Cycle Basis
[10 empty] | Electricity |  | Filters | Total | Waste
[10 empty] | kWh | $ | $ | $ | cubic yards
[9 empty] | Existing Approach | 163896.3599 | 16389.636 | 1262.4 | 17652.036 | 9.8765
[9 empty] | Proposed Approach | 1486.6228 | 148.6623 | 1860 | 2008.6623 | 4.4444
[9 empty] | Savings | 162409.7371 | 16240.9737 | -597.6 | 15643.3737 | 5.4321
[9 empty] | Simple Payback | 1.7662 | months (energy only)
Savings Summary - First Year Basis
[10 empty] | Electricity |  | Filters | Total | Waste
[10 empty] | kWh | $ | $ | $ | cu. yd.
[9 empty] | Existing Approach | 29513.4962 | 2951.3496 | 631.2 | 3582.5496 | 4.9383
[9 empty] | Proposed Approach | 4246.7316 | 424.6732 | 1860 | 2284.6732 | 4.4444
[9 empty] | Savings | 25266.7646 | 2526.6765 | -1228.8 | 1297.8765 | 0.49383
[9 empty] | Simple Payback | 0.48633 | years (energy only) | 0 | 0 | 0
[9 empty] | Savings Summary - 48 Month Cycle Basis | 0 | 0 | 0 | 0 | 0
[9 empty] | Existing Approach | 163896.3599 | 16389.636 | 1262.4 | 17652.036 | 9.8765
[9 empty] | Proposed Approach | 1486.6228 | 148.6623 | 1860 | 2008.6623 | 4.4444
[9 empty] | Savings | 162409.7371 | 16240.9737 | -597.6 | 15643.3737 | 5.4321
[9 empty] | Simple Payback | 1.7662 | months (energy only) | 0 | 0 | 0

## Summary - Scheduled
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2009-08-05 13:02
Project Name: | NAME?
Project Number: | NUMBER? |  |  |  |  | y
Engineer: | ENGINEER?
Assumptions
1 | Current hours of operation - | 8760 | per year (Current 24/7 operation)
2 | Proposed hours of operation - | 2483.2857 | per year (Average proposed from 06 AHU2 Zn Lvl Schedule - Savings v1.xls)
3 | Ratio - | 0.28348
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????
EXTENDED SURFACE AREA FILTER SAVINGS
Savings Summary - 24 7 savings adjusted by proposed operating hours ratio
Savings Summary - First Year Basis
|  | Fan Energy |  | Filter Cost |  |  | Total Cost | Waste
|  | $ | kWh | Filters | Labor | Total
| Existing Approach | 836.6489 | 8366.489 | 631.2 | 140 | 771.2 | 1607.8489 | 4.9383
| Proposed Approach | 120.3864 | 1203.8639 | 1860 | 100 | 1960 | 2080.3864 | 4.4444
| Savings | 716.2625 | 7162.6251 | -1228.8 | 40 | -1188.8 | -472.5375 | 0.49383
Savings Summary - 48 Month Cycle Basis
|  | Fan Energy |  | Filter Cost |  |  | Total Cost | Waste
|  | $ | kWh | Filters | Labor | Total
| Existing Approach | 4646.1357 | 46461.3572 | 1262.4 | 280 | 1542.4 | 6188.5357 | 9.8765
| Proposed Approach | 42.1428 | 421.428 | 1860 | 100 | 1960 | 2002.1428 | 4.4444
| Savings | 4603.9929 | 46039.9292 | -597.6 | 180 | -417.6 | 4186.3929 | 5.4321
EXTENDED SURFACE AREA FILTER SIMPLE PAYBACK, ENERGY ONLY
First year of operation basis
| First year energy savings - | 716.2625 | (7,163 kWh)
| First year cost premium - | 1228.8 | (more expensive filters)
| Simple payback - | 1.7156 | years, energy only
| First year total savings - | 756.2625 | (7,163 kWh plus $40 in filter installation labor)
| First year cost premium - | 1228.8 | (more expensive filters)
| Simple payback - | 1.6248 | years, all inclusive
Extended Surface Area Filter Life Cycle Basis
| Life cycle energy savings - | 4603.9929 | ( 46,040 kWh)
| Life cycle cost premium - | 597.6 | (more expensive filters)
| Simple payback - | 0.1298 | life cycles, energy only
| Simple payback - | 6.2304 | months, energy only
| Life cycle total savings - | 4783.9929 | ((more expensive filters) kWh plus $ in filter installation labor)
| Life cycle cost premium - | 597.6 | (more expensive filters)
| Simple payback - | 0.12492 | life cycles, energy only
| Simple payback - | 5.996 | months, energy only
FORMATED TABLE FOR REPORTS AND GRAPHS
Savings Summary - First Year Basis
[10 empty] | Electricity |  | Filters | Total | Waste
[10 empty] | kWh | $ | $ | $ | cubic yards
[9 empty] | Existing Approach | 8366.489 | 836.6489 | 631.2 | 1467.8489 | 4.9383
[9 empty] | Proposed Approach | 1203.8639 | 120.3864 | 1860 | 1980.3864 | 4.4444
[9 empty] | Savings | 7162.6251 | 716.2625 | -1228.8 | -512.5375 | 0.49383
[9 empty] | Simple Payback | 1.7156 | years (energy only)
Savings Summary - 48 Month Cycle Basis
[10 empty] | Electricity |  | Filters | Total | Waste
[10 empty] | kWh | $ | $ | $ | cubic yards
[9 empty] | Existing Approach | 46461.3572 | 4646.1357 | 1262.4 | 5908.5357 | 9.8765
[9 empty] | Proposed Approach | 421.428 | 42.1428 | 1860 | 1902.1428 | 4.4444
[9 empty] | Savings | 46039.9292 | 4603.9929 | -597.6 | 4006.3929 | 5.4321
[9 empty] | Simple Payback | 6.2304 | months (energy only)
Savings Summary - First Year Basis
[10 empty] | Electricity |  | Filters | Total | Waste
[10 empty] | kWh | $ | $ | $ | cu. yd.
[9 empty] | Existing Approach | 8366.489 | 836.6489 | 631.2 | 1467.8489 | 4.9383
[9 empty] | Proposed Approach | 1203.8639 | 120.3864 | 1860 | 1980.3864 | 4.4444
[9 empty] | Savings | 7162.6251 | 716.2625 | -1228.8 | -512.5375 | 0.49383
[9 empty] | Simple Payback | 1.7156 | years (energy only) | 0 | 0 | 0
[9 empty] | Savings Summary - 48 Month Cycle Basis | 0 | 0 | 0 | 0 | 0
[9 empty] | Existing Approach | 46461.3572 | 4646.1357 | 1262.4 | 5908.5357 | 9.8765
[9 empty] | Proposed Approach | 421.428 | 42.1428 | 1860 | 1902.1428 | 4.4444
[9 empty] | Savings | 46039.9292 | 4603.9929 | -597.6 | 4006.3929 | 5.4321
[9 empty] | Simple Payback | 6.2304 | months (energy only) | 0 | 0 | 0