## Class Lines
Intial State
| X | Y
Pressure Line | -50 | 9e-07
| 1550 | 9e-07
Enthalpy Line | 1600 | 0.1
| 1600 | 10000

## Lines Example 1
Intial State
| X | Y
Pressure Line | -50 | 134.7
| 1193 | 134.7
Enthalpy Line | 1193 | 26.7
| 1193 | 134.7
Enthalpy Line 2 | 1193 | 14.7
| 1193 | 0.1
Leaving the PRV, Entering the Control Valve
| X | Y
Pressure Line | -50 | 26.7
| 1193 | 26.7
Enthalpy Line | 1193 | 26.7
| 1193 | 14.7
Enthalpy Line 2 | 1193 | 14.7
| 1193 | 0
Reduced Pressure in Heat Exchanger
| X | Y
Pressure Line | 1193 | 14.7
| 181 | 14.7
Enthalpy Line | 1193 | 0.1
| 1193 | 10000
Pressure Line 2 | 181 | 14.7
| -50 | 14.7
Condensate |  |  | Delta | 1012
| X | Y | Rule of thumb | 970
Pressure Line | -50 | 14.7 | Difference | 42 | 4.15%
| 1550 | 14.7 | EnergyStar | 1194
Enthalpy Line | 181 | 0.1 | Difference | -182 | -15.24%
| 181 | 14.7

## Lines Example 2
Intial State
| X | Y
Pressure Line | -50 | 134.7
| 1193 | 134.7
Enthalpy Line | 1193 | 26.7
| 1193 | 134.7
Enthalpy Line 2 | 1193 | 3.05
| 1193 | 0.1
Leaving the PRV, Entering the Control Valve
| X | Y
Pressure Line | -50 | 26.7
| 1193 | 26.7
Enthalpy Line | 1193 | 26.7
| 1193 | 3.05
Enthalpy Line 2 | 1193 | 3.05
| 1193 | 0
Reduced Pressure in Heat Exchanger
| X | Y
Pressure Line | 1193 | 3.05
| 109 | 3.05
Enthalpy Line | 1193 | 0.1
| 1193 | 10000
Pressure Line 2 | 109 | 3.05
| -50 | 3.05
Condensate |  |  | Delta | 1084
| X | Y | Rule of thumb | 970
Pressure Line | -50 | 3.05 | Difference | 114 | 10.52%
| 1550 | 3.05 | EnergyStar | 1194
Enthalpy Line | 109 | 0.1 | Difference | -110 | -9.213%
| 109 | 3.05

## Lines Example 3
Intial State
| X | Y
Pressure Line | -50 | 134.7
| 1193 | 134.7
Enthalpy Line | 1193 | 26.7
| 1193 | 134.7
Enthalpy Line 2 | 1193 | 14.7
| 1193 | 0.1
Leaving the PRV, Entering the Control Valve
| X | Y
Pressure Line | -50 | 26.7
| 1193 | 26.7
Enthalpy Line | 1193 | 26.7
| 1193 | 14.7
Enthalpy Line 2 | 1193 | 14.7
| 1193 | 0
Reduced Pressure in Heat Exchanger
| X | Y
Pressure Line | 1193 | 14.7
| 180.3 | 14.7
Enthalpy Line | 1193 | 0.1
| 1193 | 10000
Pressure Line 2 | 180.3 | 14.7
| -50 | 14.7
Condensate |  |  | Delta | 1064
| X | Y | Rule of thumb | 970
Pressure Line | -50 | 14.7 | Difference | 94 | 8.835%
| 1550 | 14.7 | EnergyStar | 1194
Enthalpy Line | 180.3 | 0.1 | Difference | -130 | -10.89%
| 180.3 | 14.7
Subcoolng
| X | Y
Pressure Line | 180.3 | 14.7
| 150 | 8
| 130 | 5
| 129 | 5
Enthalpy Line | 129 | 0.1
| 129 | 5

## Lines Example 4
30 psig Saturated Condensate
| X | Y
Pressure Line | -50 | 44.7
| 242.93 | 44.7
Enthalpy Line | 242.93 | 14.7
| 242.93 | 44.7
Enthalpy Line 2 | 242.93 | 14.7
| 242.93 | 0.1
Flash Steam Condition
| X | Y
Pressure Line | 1151.1 | 14.7
| 242.93 | 14.7
Enthalpy Line | 242.93 | 14.7
| 242.93 | 14.7
Enthalpy Line 2 | 1151.1 | 14.7
| 1151.1 | 0.1
Enthalpy Line 3 | 1151.1 | 14.7
| 1151.1 | 0.1
Reduced Pressure in Heat Exchanger
| X | Y
Pressure Line | 242.93 | 14.7
| 180.3 | 14.7
Enthalpy Line | 1151.1 | 0.1
| 1151.1 | 10000
Pressure Line 2 | 242.93 | 14.7
| -50 | 14.7
0 psig Saturated Condensate |  |  | Delta | #REF!
| X | Y | Rule of thumb | 970
Pressure Line | -50 | 14.7 | Difference | #REF! | #REF!
| #REF! | 14.7 | EnergyStar | 1194
Enthalpy Line | 180.3 | 0.1 | Difference | #REF! | #REF!
| 180.3 | 14.7

## Heat Exchanger and Pipe Calcs
Heating Load Estimate - 400 Montgomery Avenue, San Francisco, CA
Square footage - | 85011 | sq.ft. | https://harvestproperties.com/investments/400-montgomery/
Average load - | 30 | Btu/hr/sq.ft. | HVAC Equations and Rules of Thumb
Peak load - | 2550330 | Btu/hr/sq.ft.
Assumed steam pressure in the heat exchanger at design flow - | 0 | psig (saturation temperature of 212°F)
Design Condition Selection |  |  |  | Design load, 110°F Water
Im pact of a longer 4 inch steam header with thermal losses and a pressure drop
Average temperaure for the run - | 300 | °F
Insulation thickness - | 3 | inches
Loss from 3EPlus - | 40.51 | Btu/hr/ft.
Design flow rate - | 2607 | lb/hr
Enthalpy leaving the PRV - | 1193 | Btu/lb
Heat loss for 100 feet of pipe - | 4051 | Btu/hr
| 1.5539 | Btu/lb
Assumed pressure loss for 100 feet of pipe - | 1 | psi
Enthalpy entering the control valve - | 1191.4461
Pressure entering the control valve - | 11 | psig

## Saturation Table
Properties of Water at Saturation Data generated with REFPROP 9.1 | [10 empty] | Example Calculations and Interpolators |  |  |  | Tables for Presentations
Temperature. °F | Pressure |  | Liquid Density, lbm/ft3 | Vapor Density, lbm/ft3 | Liquid Enthalpy, Btu/lbm | Latent Heat of Vaporization, Btu/lbm | Vapor Enthalpy, Btu/lbm | Liquid Entropy, Btu/lbm-°R | Vapor Entropy, Btu/lbm-°R | Temperature. °F
| psia | psig
32.375 | 0.09 | -14.619 | 62.416 | 0.00030724 | 0.36037 | 1075.7396 | 1076.1 | 0.00073212 | 2.1869 | 32.375 | Volume change - liquid to vapor at atmospheric pressure |  |  |  | Flashing 1 pound of condensate at 80 psia to 14.7 psia |  |  | Volume Change - Liquid at 55°F vs. 200°F
35.005 | 0.1 | -14.609 | 62.421 | 0.00033957 | 3.011 | 1074.189 | 1077.2 | 0.0061046 | 2.1777 | 35.005 | Item | Saturated Liquid | Saturated Vapor |  | Liquid enthalpy at 80 psia - | 282.32 | Btu/lb | Temperature | Saturated Liquid Specific Volume
37.411 | 0.11 | -14.599 | 62.423 | 0.00037174 | 5.4339 | 1072.8661 | 1078.3 | 0.010991 | 2.1693 | 37.411 |  |  |  |  | Liquid enthalpy at 14.7 psia - | 180.33 | Btu/lb |  | lb/ft3 | lb/gallons | ft3/lb | in.3/lb
39.632 | 0.12 | -14.589 | 62.423 | 0.00040374 | 7.6673 | 1071.6327 | 1079.3 | 0.015474 | 2.1616 | 39.632 | lb/ft3 | 59.828 | 0.037343 |  | Enthalpy change - | 101.99 | Btu/lb | 55°F | 62.39 | 8.3409 | 0.016028 | 27.6967
41.694 | 0.13 | -14.579 | 62.422 | 0.0004356 | 9.7403 | 1070.4597 | 1080.2 | 0.019617 | 2.1546 | 41.694 | ft3/lb | 0.016715 | 26.7788 |  | Latent heat of vaporization at 14.7 psia - | 970.77 | Btu/lb | 200°F | 60.12 | 8.0374 | 0.016633 | 28.7425
43.62 | 0.14 | -14.569 | 62.42 | 0.00046733 | 11.676 | 1069.324 | 1081 | 0.02347 | 2.1481 | 43.62 | Change factor, liquid to vapor - |  | 1602.1209 |  | Enthalpy change for 1 pound of condensate - | 101.99 | Btu | Change | -2.27 | -0.30348 | 0.00060519 | 1.0458
45.429 | 0.15 | -14.559 | 62.418 | 0.00049894 | 13.492 | 1068.308 | 1081.8 | 0.027072 | 2.1421 | 45.429 |  |  |  |  | Pounds of condensate flashed to steam - | 0.10506 | lb |  |  | Volume change for 13,000 gallons - | 65.6219 | 113394.6012
47.134 | 0.16 | -14.549 | 62.414 | 0.00053043 | 15.203 | 1067.297 | 1082.5 | 0.030454 | 2.1365 | 47.134 | [5 empty] | 10.51% |  | Approximate system volume - |  |  | 13000
48.748 | 0.17 | -14.539 | 62.41 | 0.00056181 | 16.822 | 1066.378 | 1083.2 | 0.033643 | 2.1312 | 48.748 |  | Flashing 1 pound of condensate at 80 psia to 14.7 psia
50.28 | 0.18 | -14.529 | 62.406 | 0.00059309 | 18.359 | 1065.541 | 1083.9 | 0.036661 | 2.1262 | 50.28 |  | Liquid enthalpy at 80 psia - | 282.32 | Btu/lb | Flashing 1 pound of condensate at 44.7 psia to 14.7 psia |  |  | Volume Change - Liquid at 140°F vs. 200°F
51.739 | 0.19 | -14.519 | 62.401 | 0.00062427 | 19.821 | 1064.679 | 1084.5 | 0.039525 | 2.1215 | 51.739 |  | Liquid enthalpy at 14.7 psia - | 180.33 | Btu/lb | Liquid enthalpy at 44.7 psia - | 242.93 | Btu/lb | Temperature | Saturated Liquid Specific Volume
53.132 | 0.2 | -14.509 | 62.396 | 0.00065536 | 21.217 | 1063.983 | 1085.2 | 0.042251 | 2.117 | 53.132 |  | Enthalpy change - | 101.99 | Btu/lb | Liquid enthalpy at 14.7 psia - | 180.33 | Btu/lb |  | lb/ft3 | lb/gallons | ft3/lb | in.3/lb
54.464 | 0.21 | -14.499 | 62.39 | 0.00068637 | 22.553 | 1063.147 | 1085.7 | 0.044852 | 2.1128 | 54.464 |  | Latent heat of vaporization at 14.7 psia - | 970.77 | Btu/lb | Enthalpy change - | 62.6 | Btu/lb | 140°F | 61.373 | 8.2049 | 0.016294 | 28.1557
55.742 | 0.22 | -14.489 | 62.385 | 0.00071729 | 23.833 | 1062.467 | 1086.3 | 0.047339 | 2.1087 | 55.742 |  | Enthalpy change for 1 pound of condensate - | 101.99 | Btu | Latent heat of vaporization at 14.7 psia - | 970.77 | Btu/lb | 200°F | 60.12 | 8.0374 | 0.016633 | 28.7425
56.97 | 0.23 | -14.479 | 62.379 | 0.00074814 | 25.063 | 1061.737 | 1086.8 | 0.049722 | 2.1049 | 56.97 |  | Pounds of condensate flashed to steam - | 0.10506 | lb | Enthalpy change for 1 pound of condensate - | 62.6 | Btu | Change | -1.253 | -0.16751 | 0.00033959 | 0.58681
58.152 | 0.24 | -14.469 | 62.373 | 0.0007789 | 26.247 | 1061.053 | 1087.3 | 0.052011 | 2.1012 | 58.152 |  |  | 10.51% |  | Pounds of condensate flashed to steam - | 0.064485 | lb |  |  | Volume change for 13,000 gallons - | 36.2221 | 62591.8217
59.292 | 0.25 | -14.459 | 62.368 | 0.0008096 | 27.387 | 1060.413 | 1087.8 | 0.054211 | 2.0976 | 59.292 | [5 empty] | 6.448% |  | Approximate system volume - |  |  | 13000
60.392 | 0.26 | -14.449 | 62.362 | 0.00084023 | 28.489 | 1059.811 | 1088.3 | 0.056331 | 2.0942 | 60.392 |  | Flashing 1 pound of condensate at 170 psia to 14.7 psia
61.456 | 0.27 | -14.439 | 62.356 | 0.00087079 | 29.553 | 1059.247 | 1088.8 | 0.058376 | 2.091 | 61.456 |  | Enthalpy at 170 psia - | 341.42
62.485 | 0.28 | -14.429 | 62.349 | 0.00090128 | 30.584 | 1058.616 | 1089.2 | 0.060351 | 2.0878 | 62.485 |  | Enthalpy at 14.7 psia - | 180.33
63.483 | 0.29 | -14.419 | 62.343 | 0.00093171 | 31.582 | 1058.118 | 1089.7 | 0.062261 | 2.0848 | 63.483 |  | Difference - | 161.09 |  |  | 1151.1
64.451 | 0.3 | -14.409 | 62.337 | 0.00096209 | 32.551 | 1057.549 | 1090.1 | 0.064111 | 2.0818 | 64.451 |  | hfg - | 855.78
65.391 | 0.31 | -14.399 | 62.331 | 0.0009924 | 33.491 | 1057.009 | 1090.5 | 0.065904 | 2.079 | 65.391 |  | Pounds of atmospheric pressure steam generated by flashing 170 psig steam to atmospheric pressure - | 0.18824
66.305 | 0.32 | -14.389 | 62.325 | 0.0010227 | 34.406 | 1056.494 | 1090.9 | 0.067644 | 2.0763 | 66.305
67.195 | 0.33 | -14.379 | 62.319 | 0.0010529 | 35.295 | 1056.005 | 1091.3 | 0.069334 | 2.0736 | 67.195 | Temperature Interpolator |  | psig | psia
68.061 | 0.34 | -14.369 | 62.313 | 0.001083 | 36.162 | 1055.538 | 1091.7 | 0.070976 | 2.071 | 68.061 |  | Saturation pressure 1 - | 54.709 | 40
68.905 | 0.35 | -14.359 | 62.307 | 0.0011131 | 37.006 | 1054.994 | 1092 | 0.072575 | 2.0685 | 68.905 |  | Saturation temperature 1 - | 267.22
69.728 | 0.36 | -14.349 | 62.301 | 0.0011432 | 37.829 | 1054.571 | 1092.4 | 0.074131 | 2.0661 | 69.728 |  | Saturation pressure 2 - | 64.709 | 50
70.532 | 0.37 | -14.339 | 62.294 | 0.0011732 | 38.632 | 1054.068 | 1092.7 | 0.075647 | 2.0638 | 70.532 |  | Saturation temperture 2 - | 280.99
71.316 | 0.38 | -14.329 | 62.288 | 0.0012031 | 39.417 | 1053.683 | 1093.1 | 0.077126 | 2.0615 | 71.316 |  | Selected pressure - | 30 | 44.709
72.083 | 0.39 | -14.319 | 62.282 | 0.001233 | 40.184 | 1053.216 | 1093.4 | 0.078569 | 2.0592 | 72.083 |  | Interpolated temperature at selected pressure - | 273.7043
72.833 | 0.4 | -14.309 | 62.276 | 0.0012629 | 40.933 | 1052.767 | 1093.7 | 0.079977 | 2.057 | 72.833
73.567 | 0.41 | -14.299 | 62.27 | 0.0012927 | 41.667 | 1052.333 | 1094 | 0.081354 | 2.0549 | 73.567 | Liquid Enthalpy Interpolator |  | psig | psia
74.285 | 0.42 | -14.289 | 62.264 | 0.0013225 | 42.385 | 1052.015 | 1094.4 | 0.082699 | 2.0529 | 74.285 |  | Saturation pressure 1 - | 29.418 | 14.709
74.988 | 0.43 | -14.279 | 62.258 | 0.0013522 | 43.088 | 1051.612 | 1094.7 | 0.084015 | 2.0508 | 74.988 |  | Liquid enthalpy 1 - | 180.33
75.677 | 0.44 | -14.269 | 62.252 | 0.0013819 | 43.777 | 1051.223 | 1095 | 0.085303 | 2.0489 | 75.677 |  | Saturation pressure 2 - | 100 | 50
76.353 | 0.45 | -14.259 | 62.247 | 0.0014116 | 44.452 | 1050.848 | 1095.3 | 0.086563 | 2.0469 | 76.353 |  | Liquid enthlapy 2 - | 250.38
77.016 | 0.46 | -14.249 | 62.241 | 0.0014412 | 45.114 | 1050.386 | 1095.5 | 0.087798 | 2.045 | 77.016 |  | Selected pressure - | 0 | 14.709
77.666 | 0.47 | -14.239 | 62.235 | 0.0014708 | 45.764 | 1050.036 | 1095.8 | 0.089009 | 2.0432 | 77.666 |  | Interpolated enthalpy at selected pressure - | 180.33
78.304 | 0.48 | -14.229 | 62.229 | 0.0015004 | 46.402 | 1049.698 | 1096.1 | 0.090195 | 2.0414 | 78.304
78.931 | 0.49 | -14.219 | 62.223 | 0.0015299 | 47.029 | 1049.371 | 1096.4 | 0.091359 | 2.0396 | 78.931
79.547 | 0.5 | -14.209 | 62.218 | 0.0015593 | 47.644 | 1048.956 | 1096.6 | 0.092501 | 2.0379 | 79.547
80.152 | 0.51 | -14.199 | 62.212 | 0.0015888 | 48.249 | 1048.651 | 1096.9 | 0.093622 | 2.0362 | 80.152
80.747 | 0.52 | -14.189 | 62.206 | 0.0016182 | 48.843 | 1048.357 | 1097.2 | 0.094722 | 2.0345 | 80.747
81.332 | 0.53 | -14.179 | 62.201 | 0.0016475 | 49.428 | 1047.972 | 1097.4 | 0.095803 | 2.0329 | 81.332
81.908 | 0.54 | -14.169 | 62.195 | 0.0016769 | 50.003 | 1047.697 | 1097.7 | 0.096866 | 2.0313 | 81.908
82.474 | 0.55 | -14.159 | 62.19 | 0.0017062 | 50.569 | 1047.331 | 1097.9 | 0.09791 | 2.0297 | 82.474
83.031 | 0.56 | -14.149 | 62.184 | 0.0017355 | 51.126 | 1046.974 | 1098.1 | 0.098937 | 2.0282 | 83.031
83.58 | 0.57 | -14.139 | 62.179 | 0.0017647 | 51.674 | 1046.726 | 1098.4 | 0.099946 | 2.0267 | 83.58
84.121 | 0.58 | -14.129 | 62.173 | 0.0017939 | 52.214 | 1046.386 | 1098.6 | 0.10094 | 2.0252 | 84.121
84.653 | 0.59 | -14.119 | 62.168 | 0.0018231 | 52.746 | 1046.054 | 1098.8 | 0.10192 | 2.0237 | 84.653
85.178 | 0.6 | -14.109 | 62.162 | 0.0018523 | 53.27 | 1045.83 | 1099.1 | 0.10288 | 2.0223 | 85.178
85.695 | 0.61 | -14.099 | 62.157 | 0.0018814 | 53.787 | 1045.513 | 1099.3 | 0.10383 | 2.0209 | 85.695
86.205 | 0.62 | -14.089 | 62.152 | 0.0019105 | 54.296 | 1045.204 | 1099.5 | 0.10476 | 2.0195 | 86.205
86.707 | 0.63 | -14.079 | 62.146 | 0.0019395 | 54.799 | 1044.901 | 1099.7 | 0.10568 | 2.0181 | 86.707
87.203 | 0.64 | -14.069 | 62.141 | 0.0019686 | 55.294 | 1044.606 | 1099.9 | 0.10659 | 2.0168 | 87.203
87.692 | 0.65 | -14.059 | 62.136 | 0.0019976 | 55.783 | 1044.417 | 1100.2 | 0.10748 | 2.0155 | 87.692
88.175 | 0.66 | -14.049 | 62.131 | 0.0020266 | 56.265 | 1044.135 | 1100.4 | 0.10836 | 2.0142 | 88.175
88.651 | 0.67 | -14.039 | 62.125 | 0.0020555 | 56.741 | 1043.859 | 1100.6 | 0.10923 | 2.0129 | 88.651
89.121 | 0.68 | -14.029 | 62.12 | 0.0020845 | 57.21 | 1043.59 | 1100.8 | 0.11008 | 2.0116 | 89.121
89.585 | 0.69 | -14.019 | 62.115 | 0.0021134 | 57.674 | 1043.326 | 1101 | 0.11093 | 2.0104 | 89.585
90.044 | 0.7 | -14.009 | 62.11 | 0.0021423 | 58.132 | 1043.068 | 1101.2 | 0.11176 | 2.0092 | 90.044
90.496 | 0.71 | -13.999 | 62.105 | 0.0021711 | 58.584 | 1042.816 | 1101.4 | 0.11259 | 2.008 | 90.496
90.944 | 0.72 | -13.989 | 62.1 | 0.0022 | 59.031 | 1042.569 | 1101.6 | 0.1134 | 2.0068 | 90.944
91.386 | 0.73 | -13.979 | 62.095 | 0.0022288 | 59.473 | 1042.227 | 1101.7 | 0.1142 | 2.0056 | 91.386
91.822 | 0.74 | -13.969 | 62.09 | 0.0022576 | 59.909 | 1041.991 | 1101.9 | 0.11499 | 2.0044 | 91.822
92.254 | 0.75 | -13.959 | 62.085 | 0.0022863 | 60.34 | 1041.76 | 1102.1 | 0.11577 | 2.0033 | 92.254
92.68 | 0.76 | -13.949 | 62.08 | 0.0023151 | 60.766 | 1041.534 | 1102.3 | 0.11654 | 2.0022 | 92.68
93.102 | 0.77 | -13.939 | 62.075 | 0.0023438 | 61.188 | 1041.312 | 1102.5 | 0.11731 | 2.0011 | 93.102
93.519 | 0.78 | -13.929 | 62.07 | 0.0023725 | 61.604 | 1041.096 | 1102.7 | 0.11806 | 2 | 93.519
93.932 | 0.79 | -13.919 | 62.065 | 0.0024011 | 62.016 | 1040.784 | 1102.8 | 0.1188 | 1.9989 | 93.932
94.34 | 0.8 | -13.909 | 62.061 | 0.0024298 | 62.424 | 1040.576 | 1103 | 0.11954 | 1.9978 | 94.34
94.743 | 0.81 | -13.899 | 62.056 | 0.0024584 | 62.827 | 1040.373 | 1103.2 | 0.12027 | 1.9968 | 94.743
95.142 | 0.82 | -13.889 | 62.051 | 0.002487 | 63.226 | 1040.174 | 1103.4 | 0.12099 | 1.9957 | 95.142
95.538 | 0.83 | -13.879 | 62.046 | 0.0025156 | 63.62 | 1039.88 | 1103.5 | 0.1217 | 1.9947 | 95.538
95.928 | 0.84 | -13.869 | 62.042 | 0.0025442 | 64.011 | 1039.689 | 1103.7 | 0.1224 | 1.9937 | 95.928
96.315 | 0.85 | -13.859 | 62.037 | 0.0025727 | 64.397 | 1039.503 | 1103.9 | 0.1231 | 1.9927 | 96.315
96.698 | 0.86 | -13.849 | 62.032 | 0.0026012 | 64.78 | 1039.22 | 1104 | 0.12378 | 1.9917 | 96.698
97.078 | 0.87 | -13.839 | 62.028 | 0.0026297 | 65.159 | 1039.041 | 1104.2 | 0.12446 | 1.9907 | 97.078
97.453 | 0.88 | -13.829 | 62.023 | 0.0026582 | 65.534 | 1038.766 | 1104.3 | 0.12514 | 1.9897 | 97.453
97.825 | 0.89 | -13.819 | 62.019 | 0.0026867 | 65.905 | 1038.595 | 1104.5 | 0.1258 | 1.9888 | 97.825
98.193 | 0.9 | -13.809 | 62.014 | 0.0027151 | 66.273 | 1038.427 | 1104.7 | 0.12646 | 1.9878 | 98.193
98.558 | 0.91 | -13.799 | 62.009 | 0.0027436 | 66.637 | 1038.163 | 1104.8 | 0.12712 | 1.9869 | 98.558
98.919 | 0.92 | -13.789 | 62.005 | 0.002772 | 66.998 | 1038.002 | 1105 | 0.12776 | 1.986 | 98.919
99.277 | 0.93 | -13.779 | 62 | 0.0028003 | 67.356 | 1037.744 | 1105.1 | 0.1284 | 1.9851 | 99.277
99.631 | 0.94 | -13.769 | 61.996 | 0.0028287 | 67.71 | 1037.59 | 1105.3 | 0.12903 | 1.9842 | 99.631
99.982 | 0.95 | -13.759 | 61.992 | 0.0028571 | 68.061 | 1037.339 | 1105.4 | 0.12966 | 1.9833 | 99.982
100.33 | 0.96 | -13.749 | 61.987 | 0.0028854 | 68.408 | 1037.192 | 1105.6 | 0.13028 | 1.9824 | 100.33
100.68 | 0.97 | -13.739 | 61.983 | 0.0029137 | 68.753 | 1036.947 | 1105.7 | 0.1309 | 1.9815 | 100.68
101.02 | 0.98 | -13.729 | 61.978 | 0.002942 | 69.095 | 1036.805 | 1105.9 | 0.13151 | 1.9806 | 101.02
101.36 | 0.99 | -13.719 | 61.974 | 0.0029703 | 69.433 | 1036.567 | 1106 | 0.13211 | 1.9798 | 101.36
101.69 | 1 | -13.709 | 61.97 | 0.0029985 | 69.769 | 1036.431 | 1106.2 | 0.13271 | 1.9789 | 101.69
102.03 | 1.01 | -13.699 | 61.965 | 0.0030268 | 70.101 | 1036.199 | 1106.3 | 0.1333 | 1.9781 | 102.03
105.21 | 1.11 | -13.599 | 61.923 | 0.0033083 | 73.281 | 1034.419 | 1107.7 | 0.13895 | 1.9701 | 105.21
108.15 | 1.21 | -13.499 | 61.883 | 0.0035882 | 76.222 | 1032.678 | 1108.9 | 0.14414 | 1.9628 | 108.15
110.89 | 1.31 | -13.399 | 61.845 | 0.0038667 | 78.961 | 1031.139 | 1110.1 | 0.14895 | 1.9562 | 110.89
113.46 | 1.41 | -13.299 | 61.808 | 0.0041439 | 81.526 | 1029.674 | 1111.2 | 0.15343 | 1.95 | 113.46
115.87 | 1.51 | -13.199 | 61.772 | 0.0044198 | 83.938 | 1028.262 | 1112.2 | 0.15763 | 1.9442 | 115.87
118.15 | 1.61 | -13.099 | 61.738 | 0.0046946 | 86.218 | 1026.982 | 1113.2 | 0.16159 | 1.9389 | 118.15
120.32 | 1.71 | -12.999 | 61.705 | 0.0049684 | 88.379 | 1025.721 | 1114.1 | 0.16532 | 1.9338 | 120.32
122.37 | 1.81 | -12.899 | 61.673 | 0.0052411 | 90.434 | 1024.566 | 1115 | 0.16885 | 1.9291 | 122.37
124.33 | 1.91 | -12.799 | 61.642 | 0.0055128 | 92.394 | 1023.406 | 1115.8 | 0.17222 | 1.9246 | 124.33
126.21 | 2.01 | -12.699 | 61.611 | 0.0057837 | 94.268 | 1022.332 | 1116.6 | 0.17542 | 1.9203 | 126.21
128.01 | 2.11 | -12.599 | 61.582 | 0.0060537 | 96.065 | 1021.235 | 1117.3 | 0.17848 | 1.9163 | 128.01
129.73 | 2.21 | -12.499 | 61.554 | 0.0063229 | 97.79 | 1020.31 | 1118.1 | 0.18141 | 1.9124 | 129.73
131.39 | 2.31 | -12.399 | 61.526 | 0.0065913 | 99.45 | 1019.35 | 1118.8 | 0.18422 | 1.9088 | 131.39
132.99 | 2.41 | -12.299 | 61.499 | 0.0068589 | 101.05 | 1018.35 | 1119.4 | 0.18693 | 1.9052 | 132.99
134.53 | 2.51 | -12.199 | 61.472 | 0.0071259 | 102.59 | 1017.51 | 1120.1 | 0.18953 | 1.9019 | 134.53
136.03 | 2.61 | -12.099 | 61.447 | 0.0073922 | 104.09 | 1016.61 | 1120.7 | 0.19204 | 1.8986 | 136.03
137.47 | 2.71 | -11.999 | 61.421 | 0.0076578 | 105.53 | 1015.77 | 1121.3 | 0.19446 | 1.8955 | 137.47
138.87 | 2.81 | -11.899 | 61.397 | 0.0079227 | 106.93 | 1014.97 | 1121.9 | 0.1968 | 1.8925 | 138.87
140.23 | 2.91 | -11.799 | 61.373 | 0.0081871 | 108.29 | 1014.11 | 1122.4 | 0.19906 | 1.8896 | 140.23
141.55 | 3.01 | -11.699 | 61.349 | 0.0084509 | 109.61 | 1013.39 | 1123 | 0.20126 | 1.8868 | 141.55
142.83 | 3.11 | -11.599 | 61.326 | 0.0087141 | 110.89 | 1012.61 | 1123.5 | 0.20339 | 1.8841 | 142.83
144.08 | 3.21 | -11.499 | 61.303 | 0.0089768 | 112.14 | 1011.86 | 1124 | 0.20546 | 1.8815 | 144.08
145.29 | 3.31 | -11.399 | 61.281 | 0.0092389 | 113.35 | 1011.15 | 1124.5 | 0.20747 | 1.879 | 145.29
146.47 | 3.41 | -11.299 | 61.259 | 0.0095005 | 114.54 | 1010.46 | 1125 | 0.20943 | 1.8765 | 146.47
147.63 | 3.51 | -11.199 | 61.237 | 0.0097617 | 115.69 | 1009.81 | 1125.5 | 0.21133 | 1.8741 | 147.63
148.76 | 3.61 | -11.099 | 61.216 | 0.010022 | 116.82 | 1009.18 | 1126 | 0.21319 | 1.8718 | 148.76
149.86 | 3.71 | -10.999 | 61.196 | 0.010282 | 117.92 | 1008.48 | 1126.4 | 0.215 | 1.8696 | 149.86
150.93 | 3.81 | -10.899 | 61.175 | 0.010542 | 119 | 1007.9 | 1126.9 | 0.21676 | 1.8674 | 150.93
151.99 | 3.91 | -10.799 | 61.155 | 0.010801 | 120.06 | 1007.24 | 1127.3 | 0.21848 | 1.8652 | 151.99
153.01 | 4.01 | -10.699 | 61.135 | 0.01106 | 121.09 | 1006.61 | 1127.7 | 0.22017 | 1.8632 | 153.01
154.02 | 4.11 | -10.599 | 61.116 | 0.011319 | 122.1 | 1006 | 1128.1 | 0.22181 | 1.8611 | 154.02
155.01 | 4.21 | -10.499 | 61.097 | 0.011577 | 123.09 | 1005.51 | 1128.6 | 0.22342 | 1.8592 | 155.01
155.98 | 4.31 | -10.399 | 61.078 | 0.011834 | 124.05 | 1004.85 | 1128.9 | 0.225 | 1.8572 | 155.98
156.93 | 4.41 | -10.299 | 61.059 | 0.012092 | 125.01 | 1004.29 | 1129.3 | 0.22654 | 1.8554 | 156.93
157.86 | 4.51 | -10.199 | 61.041 | 0.012348 | 125.94 | 1003.76 | 1129.7 | 0.22805 | 1.8535 | 157.86
158.77 | 4.61 | -10.099 | 61.023 | 0.012605 | 126.85 | 1003.25 | 1130.1 | 0.22953 | 1.8517 | 158.77
159.67 | 4.71 | -9.999 | 61.005 | 0.012861 | 127.75 | 1002.75 | 1130.5 | 0.23099 | 1.85 | 159.67
160.55 | 4.81 | -9.899 | 60.987 | 0.013117 | 128.64 | 1002.16 | 1130.8 | 0.23241 | 1.8483 | 160.55
161.42 | 4.91 | -9.799 | 60.97 | 0.013372 | 129.5 | 1001.7 | 1131.2 | 0.23381 | 1.8466 | 161.42
162.27 | 5.01 | -9.699 | 60.953 | 0.013627 | 130.36 | 1001.14 | 1131.5 | 0.23518 | 1.8449 | 162.27
163.11 | 5.11 | -9.599 | 60.936 | 0.013882 | 131.2 | 1000.7 | 1131.9 | 0.23653 | 1.8433 | 163.11
163.93 | 5.21 | -9.499 | 60.919 | 0.014136 | 132.02 | 1000.18 | 1132.2 | 0.23785 | 1.8417 | 163.93
164.74 | 5.31 | -9.399 | 60.902 | 0.01439 | 132.83 | 999.67 | 1132.5 | 0.23915 | 1.8402 | 164.74
165.54 | 5.41 | -9.299 | 60.886 | 0.014644 | 133.63 | 999.17 | 1132.8 | 0.24043 | 1.8386 | 165.54
166.32 | 5.51 | -9.199 | 60.87 | 0.014897 | 134.42 | 998.78 | 1133.2 | 0.24169 | 1.8371 | 166.32
167.09 | 5.61 | -9.099 | 60.854 | 0.01515 | 135.19 | 998.31 | 1133.5 | 0.24292 | 1.8357 | 167.09
167.86 | 5.71 | -8.999 | 60.838 | 0.015403 | 135.96 | 997.84 | 1133.8 | 0.24414 | 1.8342 | 167.86
168.61 | 5.81 | -8.899 | 60.822 | 0.015656 | 136.71 | 997.39 | 1134.1 | 0.24534 | 1.8328 | 168.61
169.35 | 5.91 | -8.799 | 60.807 | 0.015908 | 137.45 | 996.95 | 1134.4 | 0.24652 | 1.8314 | 169.35
170.07 | 6.01 | -8.699 | 60.792 | 0.01616 | 138.18 | 996.52 | 1134.7 | 0.24768 | 1.8301 | 170.07
170.79 | 6.11 | -8.599 | 60.776 | 0.016412 | 138.9 | 996.1 | 1135 | 0.24882 | 1.8287 | 170.79
171.5 | 6.21 | -8.499 | 60.761 | 0.016663 | 139.61 | 995.59 | 1135.2 | 0.24995 | 1.8274 | 171.5
172.2 | 6.31 | -8.399 | 60.747 | 0.016914 | 140.32 | 995.18 | 1135.5 | 0.25106 | 1.8261 | 172.2
172.89 | 6.41 | -8.299 | 60.732 | 0.017165 | 141.01 | 994.79 | 1135.8 | 0.25215 | 1.8248 | 172.89
173.57 | 6.51 | -8.199 | 60.717 | 0.017416 | 141.69 | 994.41 | 1136.1 | 0.25323 | 1.8235 | 173.57
174.25 | 6.61 | -8.099 | 60.703 | 0.017666 | 142.37 | 994.03 | 1136.4 | 0.2543 | 1.8223 | 174.25
174.91 | 6.71 | -7.999 | 60.689 | 0.017916 | 143.03 | 993.57 | 1136.6 | 0.25535 | 1.8211 | 174.91
175.57 | 6.81 | -7.899 | 60.675 | 0.018166 | 143.69 | 993.21 | 1136.9 | 0.25638 | 1.8199 | 175.57
176.21 | 6.91 | -7.799 | 60.661 | 0.018416 | 144.34 | 992.76 | 1137.1 | 0.25741 | 1.8187 | 176.21
176.85 | 7.01 | -7.699 | 60.647 | 0.018665 | 144.98 | 992.42 | 1137.4 | 0.25842 | 1.8175 | 176.85
177.49 | 7.11 | -7.599 | 60.633 | 0.018915 | 145.62 | 991.98 | 1137.6 | 0.25941 | 1.8164 | 177.49
178.11 | 7.21 | -7.499 | 60.62 | 0.019164 | 146.24 | 991.66 | 1137.9 | 0.26039 | 1.8152 | 178.11
178.73 | 7.31 | -7.399 | 60.606 | 0.019412 | 146.86 | 991.24 | 1138.1 | 0.26137 | 1.8141 | 178.73
179.34 | 7.41 | -7.299 | 60.593 | 0.019661 | 147.48 | 990.92 | 1138.4 | 0.26233 | 1.813 | 179.34
179.94 | 7.51 | -7.199 | 60.58 | 0.019909 | 148.08 | 990.52 | 1138.6 | 0.26327 | 1.8119 | 179.94
180.54 | 7.61 | -7.099 | 60.566 | 0.020157 | 148.68 | 990.22 | 1138.9 | 0.26421 | 1.8109 | 180.54
181.13 | 7.71 | -6.999 | 60.553 | 0.020405 | 149.28 | 989.82 | 1139.1 | 0.26513 | 1.8098 | 181.13
181.71 | 7.81 | -6.899 | 60.54 | 0.020653 | 149.86 | 989.44 | 1139.3 | 0.26605 | 1.8088 | 181.71
182.29 | 7.91 | -6.799 | 60.528 | 0.0209 | 150.44 | 989.16 | 1139.6 | 0.26695 | 1.8077 | 182.29
182.86 | 8.01 | -6.699 | 60.515 | 0.021147 | 151.02 | 988.78 | 1139.8 | 0.26785 | 1.8067 | 182.86
183.43 | 8.11 | -6.599 | 60.502 | 0.021394 | 151.58 | 988.42 | 1140 | 0.26873 | 1.8057 | 183.43
183.99 | 8.21 | -6.499 | 60.49 | 0.021641 | 152.15 | 988.05 | 1140.2 | 0.2696 | 1.8047 | 183.99
184.54 | 8.31 | -6.399 | 60.477 | 0.021888 | 152.7 | 987.7 | 1140.4 | 0.27047 | 1.8037 | 184.54
185.09 | 8.41 | -6.299 | 60.465 | 0.022134 | 153.26 | 987.44 | 1140.7 | 0.27132 | 1.8028 | 185.09
185.64 | 8.51 | -6.199 | 60.453 | 0.02238 | 153.8 | 987.1 | 1140.9 | 0.27217 | 1.8018 | 185.64
186.17 | 8.61 | -6.099 | 60.441 | 0.022626 | 154.34 | 986.76 | 1141.1 | 0.273 | 1.8008 | 186.17
186.71 | 8.71 | -5.999 | 60.429 | 0.022872 | 154.88 | 986.42 | 1141.3 | 0.27383 | 1.7999 | 186.71
187.24 | 8.81 | -5.899 | 60.417 | 0.023118 | 155.41 | 986.09 | 1141.5 | 0.27465 | 1.799 | 187.24
187.76 | 8.91 | -5.799 | 60.405 | 0.023363 | 155.93 | 985.77 | 1141.7 | 0.27546 | 1.7981 | 187.76
188.28 | 9.01 | -5.699 | 60.393 | 0.023608 | 156.45 | 985.45 | 1141.9 | 0.27627 | 1.7972 | 188.28
188.79 | 9.11 | -5.599 | 60.381 | 0.023854 | 156.97 | 985.13 | 1142.1 | 0.27706 | 1.7963 | 188.79
189.3 | 9.21 | -5.499 | 60.37 | 0.024098 | 157.48 | 984.82 | 1142.3 | 0.27785 | 1.7954 | 189.3
189.8 | 9.31 | -5.399 | 60.358 | 0.024343 | 157.99 | 984.51 | 1142.5 | 0.27863 | 1.7945 | 189.8
190.3 | 9.41 | -5.299 | 60.347 | 0.024588 | 158.49 | 984.21 | 1142.7 | 0.2794 | 1.7937 | 190.3
190.8 | 9.51 | -5.199 | 60.336 | 0.024832 | 158.99 | 983.91 | 1142.9 | 0.28016 | 1.7928 | 190.8
191.29 | 9.61 | -5.099 | 60.324 | 0.025076 | 159.48 | 983.62 | 1143.1 | 0.28092 | 1.792 | 191.29
191.77 | 9.71 | -4.999 | 60.313 | 0.025321 | 159.97 | 983.33 | 1143.3 | 0.28167 | 1.7911 | 191.77
192.26 | 9.81 | -4.899 | 60.302 | 0.025564 | 160.45 | 983.05 | 1143.5 | 0.28242 | 1.7903 | 192.26
192.73 | 9.91 | -4.799 | 60.291 | 0.025808 | 160.93 | 982.77 | 1143.7 | 0.28315 | 1.7895 | 192.73
193.16 | 10 | -4.709 | 60.281 | 0.026027 | 161.36 | 982.44 | 1143.8 | 0.28381 | 1.7887 | 193.16
200 | 11.538 | -3.171 | 60.12 | 0.029754 | 168.24 | 978.26 | 1146.5 | 0.29429 | 1.7772 | 200
201 | 11.778 | -2.931 | 60.096 | 0.030333 | 169.25 | 977.65 | 1146.9 | 0.29581 | 1.7755 | 201
202 | 12.023 | -2.686 | 60.072 | 0.030922 | 170.26 | 977.04 | 1147.3 | 0.29733 | 1.7739 | 202
203 | 12.271 | -2.438 | 60.048 | 0.03152 | 171.26 | 976.34 | 1147.6 | 0.29885 | 1.7722 | 203
204 | 12.524 | -2.185 | 60.024 | 0.032128 | 172.27 | 975.73 | 1148 | 0.30037 | 1.7706 | 204
205 | 12.782 | -1.927 | 60 | 0.032745 | 173.28 | 975.12 | 1148.4 | 0.30188 | 1.769 | 205
206 | 13.044 | -1.665 | 59.976 | 0.033372 | 174.28 | 974.52 | 1148.8 | 0.3034 | 1.7673 | 206
207 | 13.31 | -1.399 | 59.951 | 0.034009 | 175.29 | 973.91 | 1149.2 | 0.30491 | 1.7657 | 207
208 | 13.581 | -1.128 | 59.927 | 0.034655 | 176.3 | 973.2 | 1149.5 | 0.30642 | 1.7641 | 208
209 | 13.856 | -0.853 | 59.902 | 0.035312 | 177.31 | 972.59 | 1149.9 | 0.30792 | 1.7625 | 209
210 | 14.136 | -0.573 | 59.877 | 0.035978 | 178.31 | 971.99 | 1150.3 | 0.30943 | 1.7609 | 210
211 | 14.42 | -0.289 | 59.853 | 0.036655 | 179.32 | 971.38 | 1150.7 | 0.31093 | 1.7593 | 211
212 | 14.709 | 0 | 59.828 | 0.037343 | 180.33 | 970.77 | 1151.1 | 0.31243 | 1.7577 | 212
213 | 15.003 | 0.294 | 59.803 | 0.03804 | 181.34 | 970.06 | 1151.4 | 0.31393 | 1.7561 | 213
214 | 15.302 | 0.593 | 59.778 | 0.038749 | 182.35 | 969.45 | 1151.8 | 0.31543 | 1.7545 | 214
215 | 15.606 | 0.897 | 59.753 | 0.039468 | 183.36 | 968.84 | 1152.2 | 0.31692 | 1.7529 | 215
216 | 15.915 | 1.206 | 59.728 | 0.040197 | 184.36 | 968.24 | 1152.6 | 0.31841 | 1.7514 | 216
217 | 16.229 | 1.52 | 59.702 | 0.040938 | 185.37 | 967.53 | 1152.9 | 0.3199 | 1.7498 | 217
218 | 16.548 | 1.839 | 59.677 | 0.04169 | 186.38 | 966.92 | 1153.3 | 0.32139 | 1.7482 | 218
219 | 16.872 | 2.163 | 59.651 | 0.042453 | 187.39 | 966.31 | 1153.7 | 0.32288 | 1.7467 | 219
220 | 17.201 | 2.492 | 59.626 | 0.043228 | 188.4 | 965.7 | 1154.1 | 0.32436 | 1.7451 | 220
227.92 | 20 | 5.291 | 59.421 | 0.049774 | 196.4 | 960.6 | 1157 | 0.33605 | 1.7331 | 227.92
250.3 | 30 | 15.291 | 58.812 | 0.072741 | 219.08 | 945.82 | 1164.9 | 0.36847 | 1.7007 | 250.3
267.22 | 40 | 25.291 | 58.324 | 0.095239 | 236.3 | 934.3 | 1170.6 | 0.3924 | 1.6777 | 267.22
280.99 | 50 | 35.291 | 57.909 | 0.11741 | 250.38 | 924.62 | 1175 | 0.41153 | 1.6599 | 280.99
292.68 | 60 | 45.291 | 57.545 | 0.13935 | 262.38 | 916.22 | 1178.6 | 0.42757 | 1.6454 | 292.68
302.91 | 70 | 55.291 | 57.217 | 0.16111 | 272.91 | 908.69 | 1181.6 | 0.44143 | 1.633 | 302.91
312.02 | 80 | 65.291 | 56.918 | 0.18271 | 282.32 | 901.78 | 1184.1 | 0.45366 | 1.6223 | 312.02
320.26 | 90 | 75.291 | 56.641 | 0.20421 | 290.87 | 895.43 | 1186.3 | 0.46463 | 1.6128 | 320.26
327.81 | 100 | 85.291 | 56.383 | 0.2256 | 298.71 | 889.59 | 1188.3 | 0.4746 | 1.6043 | 327.81
334.77 | 110 | 95.291 | 56.14 | 0.24692 | 305.98 | 884.02 | 1190 | 0.48375 | 1.5965 | 334.77
341.25 | 120 | 105.291 | 55.91 | 0.26818 | 312.76 | 878.74 | 1191.5 | 0.49221 | 1.5894 | 341.25
347.32 | 130 | 115.291 | 55.692 | 0.28938 | 319.13 | 873.77 | 1192.9 | 0.50008 | 1.5829 | 347.32
353.03 | 140 | 125.291 | 55.483 | 0.31055 | 325.14 | 869.06 | 1194.2 | 0.50746 | 1.5768 | 353.03 | 1193.55
358.42 | 150 | 135.291 | 55.284 | 0.33167 | 330.83 | 864.47 | 1195.3 | 0.5144 | 1.5711 | 358.42
363.54 | 160 | 145.291 | 55.092 | 0.35278 | 336.25 | 860.05 | 1196.3 | 0.52097 | 1.5657 | 363.54
368.41 | 170 | 155.291 | 54.906 | 0.37386 | 341.42 | 855.78 | 1197.2 | 0.52719 | 1.5607 | 368.41 | 1196.75 | 0.2674%
373.07 | 180 | 165.291 | 54.728 | 0.39492 | 346.37 | 851.73 | 1198.1 | 0.53311 | 1.5559 | 373.07
377.52 | 190 | 175.291 | 54.555 | 0.41598 | 351.13 | 847.77 | 1198.9 | 0.53876 | 1.5514 | 377.52
381.8 | 200 | 185.291 | 54.387 | 0.43703 | 355.7 | 843.9 | 1199.6 | 0.54417 | 1.547 | 381.8
385.91 | 210 | 195.291 | 54.224 | 0.45807 | 360.11 | 840.09 | 1200.2 | 0.54936 | 1.5429 | 385.91
389.87 | 220 | 205.291 | 54.065 | 0.47912 | 364.36 | 836.44 | 1200.8 | 0.55434 | 1.539 | 389.87
393.7 | 230 | 215.291 | 53.91 | 0.50017 | 368.48 | 832.92 | 1201.4 | 0.55914 | 1.5352 | 393.7
397.39 | 240 | 225.291 | 53.759 | 0.52123 | 372.48 | 829.42 | 1201.9 | 0.56376 | 1.5315 | 397.39
400.97 | 250 | 235.291 | 53.612 | 0.5423 | 376.35 | 826.05 | 1202.4 | 0.56824 | 1.528 | 400.97
404.44 | 260 | 245.291 | 53.467 | 0.56338 | 380.11 | 822.69 | 1202.8 | 0.57256 | 1.5246 | 404.44
407.8 | 270 | 255.291 | 53.326 | 0.58448 | 383.78 | 819.42 | 1203.2 | 0.57675 | 1.5213 | 407.8
411.07 | 280 | 265.291 | 53.188 | 0.60559 | 387.34 | 816.16 | 1203.5 | 0.58081 | 1.5182 | 411.07
414.26 | 290 | 275.291 | 53.052 | 0.62672 | 390.82 | 813.08 | 1203.9 | 0.58476 | 1.5151 | 414.26
417.35 | 300 | 285.291 | 52.919 | 0.64787 | 394.21 | 809.89 | 1204.1 | 0.58859 | 1.5121 | 417.35
420.37 | 310 | 295.291 | 52.788 | 0.66905 | 397.53 | 806.87 | 1204.4 | 0.59233 | 1.5092 | 420.37
423.31 | 320 | 305.291 | 52.66 | 0.69025 | 400.77 | 803.93 | 1204.7 | 0.59596 | 1.5064 | 423.31
426.19 | 330 | 315.291 | 52.533 | 0.71147 | 403.94 | 800.96 | 1204.9 | 0.59951 | 1.5036 | 426.19
429 | 340 | 325.291 | 52.409 | 0.73272 | 407.04 | 798.06 | 1205.1 | 0.60296 | 1.501 | 429
431.74 | 350 | 335.291 | 52.286 | 0.754 | 410.08 | 795.12 | 1205.2 | 0.60634 | 1.4984 | 431.74
434.42 | 360 | 345.291 | 52.166 | 0.77531 | 413.06 | 792.34 | 1205.4 | 0.60964 | 1.4958 | 434.42
437.05 | 370 | 355.291 | 52.047 | 0.79665 | 415.98 | 789.52 | 1205.5 | 0.61286 | 1.4933 | 437.05
439.62 | 380 | 365.291 | 51.93 | 0.81803 | 418.85 | 786.75 | 1205.6 | 0.61602 | 1.4909 | 439.62
442.14 | 390 | 375.291 | 51.814 | 0.83943 | 421.67 | 784.03 | 1205.7 | 0.61911 | 1.4885 | 442.14
444.62 | 400 | 385.291 | 51.7 | 0.86087 | 424.44 | 781.36 | 1205.8 | 0.62213 | 1.4862 | 444.62
447.04 | 410 | 395.291 | 51.587 | 0.88235 | 427.16 | 778.74 | 1205.9 | 0.6251 | 1.4839 | 447.04
449.42 | 420 | 405.291 | 51.475 | 0.90387 | 429.84 | 776.06 | 1205.9 | 0.62801 | 1.4817 | 449.42
451.76 | 430 | 415.291 | 51.365 | 0.92542 | 432.47 | 773.43 | 1205.9 | 0.63086 | 1.4795 | 451.76
454.05 | 440 | 425.291 | 51.257 | 0.94701 | 435.06 | 770.94 | 1206 | 0.63366 | 1.4773 | 454.05
456.31 | 450 | 435.291 | 51.149 | 0.96864 | 437.62 | 768.38 | 1206 | 0.63642 | 1.4752 | 456.31
458.52 | 460 | 445.291 | 51.042 | 0.99031 | 440.13 | 765.77 | 1205.9 | 0.63912 | 1.4732 | 458.52
460.7 | 470 | 455.291 | 50.937 | 1.012 | 442.61 | 763.29 | 1205.9 | 0.64177 | 1.4711 | 460.7
462.85 | 480 | 465.291 | 50.833 | 1.0338 | 445.05 | 760.85 | 1205.9 | 0.64439 | 1.4691 | 462.85
464.96 | 490 | 475.291 | 50.73 | 1.0556 | 447.46 | 758.34 | 1205.8 | 0.64696 | 1.4671 | 464.96
467.04 | 500 | 485.291 | 50.628 | 1.0774 | 449.84 | 755.96 | 1205.8 | 0.64949 | 1.4652 | 467.04
469.09 | 510 | 495.291 | 50.526 | 1.0993 | 452.19 | 753.51 | 1205.7 | 0.65198 | 1.4633 | 469.09
471.1 | 520 | 505.291 | 50.426 | 1.1212 | 454.5 | 751.1 | 1205.6 | 0.65443 | 1.4614 | 471.1
473.09 | 530 | 515.291 | 50.327 | 1.1432 | 456.79 | 748.71 | 1205.5 | 0.65684 | 1.4596 | 473.09
475.05 | 540 | 525.291 | 50.228 | 1.1652 | 459.05 | 746.35 | 1205.4 | 0.65922 | 1.4577 | 475.05
476.98 | 550 | 535.291 | 50.13 | 1.1873 | 461.28 | 744.02 | 1205.3 | 0.66157 | 1.4559 | 476.98
478.88 | 560 | 545.291 | 50.033 | 1.2094 | 463.48 | 741.72 | 1205.2 | 0.66388 | 1.4542 | 478.88
480.76 | 570 | 555.291 | 49.937 | 1.2316 | 465.66 | 739.44 | 1205.1 | 0.66616 | 1.4524 | 480.76
482.61 | 580 | 565.291 | 49.842 | 1.2538 | 467.82 | 737.08 | 1204.9 | 0.66841 | 1.4507 | 482.61
484.44 | 590 | 575.291 | 49.747 | 1.2761 | 469.95 | 734.85 | 1204.8 | 0.67063 | 1.449 | 484.44
486.24 | 600 | 585.291 | 49.653 | 1.2984 | 472.06 | 732.54 | 1204.6 | 0.67282 | 1.4473 | 486.24
488.02 | 610 | 595.291 | 49.56 | 1.3208 | 474.14 | 730.36 | 1204.5 | 0.67498 | 1.4456 | 488.02
489.78 | 620 | 605.291 | 49.468 | 1.3433 | 476.21 | 728.09 | 1204.3 | 0.67712 | 1.444 | 489.78
491.52 | 630 | 615.291 | 49.376 | 1.3657 | 478.25 | 725.85 | 1204.1 | 0.67923 | 1.4424 | 491.52
493.24 | 640 | 625.291 | 49.284 | 1.3883 | 480.27 | 723.73 | 1204 | 0.68131 | 1.4408 | 493.24
494.94 | 650 | 635.291 | 49.194 | 1.4109 | 482.27 | 721.53 | 1203.8 | 0.68337 | 1.4392 | 494.94
496.61 | 660 | 645.291 | 49.104 | 1.4335 | 484.25 | 719.35 | 1203.6 | 0.68541 | 1.4376 | 496.61
498.27 | 670 | 655.291 | 49.014 | 1.4562 | 486.22 | 717.18 | 1203.4 | 0.68742 | 1.436 | 498.27
499.91 | 680 | 665.291 | 48.925 | 1.479 | 488.16 | 714.94 | 1203.1 | 0.68941 | 1.4345 | 499.91
501.53 | 690 | 675.291 | 48.837 | 1.5018 | 490.09 | 712.81 | 1202.9 | 0.69138 | 1.433 | 501.53
503.13 | 700 | 685.291 | 48.749 | 1.5247 | 492 | 710.7 | 1202.7 | 0.69332 | 1.4315 | 503.13
504.72 | 710 | 695.291 | 48.661 | 1.5477 | 493.89 | 708.61 | 1202.5 | 0.69525 | 1.43 | 504.72
506.29 | 720 | 705.291 | 48.574 | 1.5707 | 495.77 | 706.43 | 1202.2 | 0.69715 | 1.4285 | 506.29
507.84 | 730 | 715.291 | 48.488 | 1.5937 | 497.63 | 704.37 | 1202 | 0.69904 | 1.427 | 507.84
509.37 | 740 | 725.291 | 48.402 | 1.6169 | 499.48 | 702.22 | 1201.7 | 0.70091 | 1.4256 | 509.37
510.89 | 750 | 735.291 | 48.317 | 1.64 | 501.31 | 700.19 | 1201.5 | 0.70275 | 1.4242 | 510.89
512.4 | 760 | 745.291 | 48.232 | 1.6633 | 503.12 | 698.08 | 1201.2 | 0.70458 | 1.4227 | 512.4
513.89 | 770 | 755.291 | 48.147 | 1.6866 | 504.92 | 695.98 | 1200.9 | 0.70639 | 1.4213 | 513.89
515.36 | 780 | 765.291 | 48.063 | 1.71 | 506.71 | 693.99 | 1200.7 | 0.70819 | 1.4199 | 515.36
516.82 | 790 | 775.291 | 47.979 | 1.7334 | 508.48 | 691.92 | 1200.4 | 0.70996 | 1.4185 | 516.82
518.27 | 800 | 785.291 | 47.896 | 1.7569 | 510.24 | 689.86 | 1200.1 | 0.71173 | 1.4171 | 518.27
519.7 | 810 | 795.291 | 47.813 | 1.7805 | 511.99 | 687.81 | 1199.8 | 0.71347 | 1.4158 | 519.7
521.12 | 820 | 805.291 | 47.73 | 1.8042 | 513.72 | 685.78 | 1199.5 | 0.7152 | 1.4144 | 521.12
522.53 | 830 | 815.291 | 47.648 | 1.8279 | 515.44 | 683.76 | 1199.2 | 0.71691 | 1.4131 | 522.53
523.92 | 840 | 825.291 | 47.566 | 1.8516 | 517.15 | 681.75 | 1198.9 | 0.71861 | 1.4117 | 523.92
525.3 | 850 | 835.291 | 47.484 | 1.8755 | 518.85 | 679.75 | 1198.6 | 0.7203 | 1.4104 | 525.3
526.67 | 860 | 845.291 | 47.403 | 1.8994 | 520.53 | 677.77 | 1198.3 | 0.72196 | 1.4091 | 526.67
528.02 | 870 | 855.291 | 47.322 | 1.9234 | 522.2 | 675.8 | 1198 | 0.72362 | 1.4078 | 528.02
529.37 | 880 | 865.291 | 47.242 | 1.9474 | 523.87 | 673.73 | 1197.6 | 0.72526 | 1.4065 | 529.37
530.7 | 890 | 875.291 | 47.161 | 1.9716 | 525.52 | 671.78 | 1197.3 | 0.72689 | 1.4052 | 530.7
532.02 | 900 | 885.291 | 47.081 | 1.9958 | 527.16 | 669.84 | 1197 | 0.72851 | 1.4039 | 532.02
533.33 | 910 | 895.291 | 47.002 | 2.0201 | 528.79 | 667.81 | 1196.6 | 0.73011 | 1.4027 | 533.33
534.63 | 920 | 905.291 | 46.922 | 2.0444 | 530.41 | 665.89 | 1196.3 | 0.7317 | 1.4014 | 534.63
535.92 | 930 | 915.291 | 46.843 | 2.0688 | 532.02 | 663.88 | 1195.9 | 0.73328 | 1.4002 | 535.92
537.19 | 940 | 925.291 | 46.764 | 2.0933 | 533.62 | 661.98 | 1195.6 | 0.73484 | 1.3989 | 537.19
538.46 | 950 | 935.291 | 46.686 | 2.1179 | 535.21 | 659.99 | 1195.2 | 0.7364 | 1.3977 | 538.46
539.72 | 960 | 945.291 | 46.608 | 2.1425 | 536.79 | 658.11 | 1194.9 | 0.73794 | 1.3964 | 539.72
540.97 | 970 | 955.291 | 46.53 | 2.1673 | 538.36 | 656.14 | 1194.5 | 0.73947 | 1.3952 | 540.97
542.2 | 980 | 965.291 | 46.452 | 2.1921 | 539.92 | 654.18 | 1194.1 | 0.74099 | 1.394 | 542.2
543.43 | 990 | 975.291 | 46.374 | 2.217 | 541.47 | 652.33 | 1193.8 | 0.7425 | 1.3928 | 543.43
544.65 | 1000 | 985.291 | 46.297 | 2.2419 | 543.02 | 650.38 | 1193.4 | 0.744 | 1.3916 | 544.65
545.86 | 1010 | 995.291 | 46.22 | 2.267 | 544.55 | 648.45 | 1193 | 0.74549 | 1.3904 | 545.86
547.06 | 1020 | 1005.291 | 46.143 | 2.2921 | 546.08 | 646.52 | 1192.6 | 0.74697 | 1.3892 | 547.06
548.25 | 1030 | 1015.291 | 46.066 | 2.3173 | 547.6 | 644.6 | 1192.2 | 0.74844 | 1.388 | 548.25
549.43 | 1040 | 1025.291 | 45.99 | 2.3426 | 549.11 | 642.69 | 1191.8 | 0.7499 | 1.3868 | 549.43
550.61 | 1050 | 1035.291 | 45.914 | 2.368 | 550.62 | 640.88 | 1191.5 | 0.75135 | 1.3857 | 550.61
551.77 | 1060 | 1045.291 | 45.838 | 2.3934 | 552.11 | 638.89 | 1191 | 0.75279 | 1.3845 | 551.77
552.93 | 1070 | 1055.291 | 45.762 | 2.419 | 553.6 | 637 | 1190.6 | 0.75422 | 1.3833 | 552.93
554.08 | 1080 | 1065.291 | 45.686 | 2.4446 | 555.08 | 635.12 | 1190.2 | 0.75564 | 1.3822 | 554.08
555.22 | 1090 | 1075.291 | 45.611 | 2.4703 | 556.56 | 633.24 | 1189.8 | 0.75705 | 1.381 | 555.22
556.35 | 1100 | 1085.291 | 45.536 | 2.4961 | 558.02 | 631.38 | 1189.4 | 0.75846 | 1.3799 | 556.35
557.47 | 1110 | 1095.291 | 45.461 | 2.522 | 559.48 | 629.52 | 1189 | 0.75985 | 1.3787 | 557.47
558.59 | 1120 | 1105.291 | 45.386 | 2.548 | 560.93 | 627.67 | 1188.6 | 0.76124 | 1.3776 | 558.59
559.7 | 1130 | 1115.291 | 45.311 | 2.5741 | 562.38 | 625.72 | 1188.1 | 0.76262 | 1.3765 | 559.7
560.8 | 1140 | 1125.291 | 45.236 | 2.6002 | 563.82 | 623.88 | 1187.7 | 0.76399 | 1.3754 | 560.8
561.89 | 1150 | 1135.291 | 45.162 | 2.6265 | 565.25 | 622.05 | 1187.3 | 0.76535 | 1.3742 | 561.89
562.98 | 1160 | 1145.291 | 45.087 | 2.6528 | 566.68 | 620.12 | 1186.8 | 0.76671 | 1.3731 | 562.98
564.06 | 1170 | 1155.291 | 45.013 | 2.6793 | 568.1 | 618.3 | 1186.4 | 0.76805 | 1.372 | 564.06
565.13 | 1180 | 1165.291 | 44.939 | 2.7058 | 569.51 | 616.39 | 1185.9 | 0.76939 | 1.3709 | 565.13
566.2 | 1190 | 1175.291 | 44.865 | 2.7324 | 570.92 | 614.58 | 1185.5 | 0.77073 | 1.3698 | 566.2
567.26 | 1200 | 1185.291 | 44.792 | 2.7591 | 572.32 | 612.68 | 1185 | 0.77205 | 1.3687 | 567.26
568.31 | 1210 | 1195.291 | 44.718 | 2.786 | 573.72 | 610.88 | 1184.6 | 0.77337 | 1.3676 | 568.31
569.36 | 1220 | 1205.291 | 44.645 | 2.8129 | 575.11 | 608.99 | 1184.1 | 0.77468 | 1.3665 | 569.36
570.4 | 1230 | 1215.291 | 44.571 | 2.8399 | 576.49 | 607.21 | 1183.7 | 0.77599 | 1.3654 | 570.4
571.43 | 1240 | 1225.291 | 44.498 | 2.867 | 577.87 | 605.33 | 1183.2 | 0.77728 | 1.3643 | 571.43
572.45 | 1250 | 1235.291 | 44.425 | 2.8942 | 579.24 | 603.46 | 1182.7 | 0.77857 | 1.3633 | 572.45
573.47 | 1260 | 1245.291 | 44.352 | 2.9216 | 580.61 | 601.59 | 1182.2 | 0.77986 | 1.3622 | 573.47
574.49 | 1270 | 1255.291 | 44.279 | 2.949 | 581.98 | 599.82 | 1181.8 | 0.78114 | 1.3611 | 574.49
575.49 | 1280 | 1265.291 | 44.206 | 2.9765 | 583.33 | 597.97 | 1181.3 | 0.78241 | 1.36 | 575.49
576.5 | 1290 | 1275.291 | 44.133 | 3.0041 | 584.69 | 596.11 | 1180.8 | 0.78368 | 1.359 | 576.5
577.49 | 1300 | 1285.291 | 44.061 | 3.0319 | 586.03 | 594.27 | 1180.3 | 0.78493 | 1.3579 | 577.49
578.48 | 1310 | 1295.291 | 43.988 | 3.0597 | 587.38 | 592.42 | 1179.8 | 0.78619 | 1.3569 | 578.48
579.47 | 1320 | 1305.291 | 43.916 | 3.0877 | 588.72 | 590.58 | 1179.3 | 0.78744 | 1.3558 | 579.47
580.44 | 1330 | 1315.291 | 43.843 | 3.1157 | 590.05 | 588.75 | 1178.8 | 0.78868 | 1.3547 | 580.44
581.42 | 1340 | 1325.291 | 43.771 | 3.1439 | 591.38 | 586.92 | 1178.3 | 0.78992 | 1.3537 | 581.42
582.38 | 1350 | 1335.291 | 43.699 | 3.1722 | 592.7 | 585.1 | 1177.8 | 0.79115 | 1.3526 | 582.38
583.34 | 1360 | 1345.291 | 43.626 | 3.2006 | 594.02 | 583.28 | 1177.3 | 0.79237 | 1.3516 | 583.34
584.3 | 1370 | 1355.291 | 43.554 | 3.2291 | 595.34 | 581.46 | 1176.8 | 0.79359 | 1.3505 | 584.3
585.25 | 1380 | 1365.291 | 43.482 | 3.2577 | 596.65 | 579.65 | 1176.3 | 0.79481 | 1.3495 | 585.25
586.2 | 1390 | 1375.291 | 43.41 | 3.2864 | 597.96 | 577.74 | 1175.7 | 0.79602 | 1.3485 | 586.2
587.14 | 1400 | 1385.291 | 43.338 | 3.3153 | 599.26 | 575.94 | 1175.2 | 0.79722 | 1.3474 | 587.14
588.07 | 1410 | 1395.291 | 43.267 | 3.3443 | 600.56 | 574.14 | 1174.7 | 0.79842 | 1.3464 | 588.07
589 | 1420 | 1405.291 | 43.195 | 3.3733 | 601.85 | 572.35 | 1174.2 | 0.79961 | 1.3454 | 589
589.93 | 1430 | 1415.291 | 43.123 | 3.4026 | 603.14 | 570.46 | 1173.6 | 0.8008 | 1.3443 | 589.93
590.85 | 1440 | 1425.291 | 43.051 | 3.4319 | 604.43 | 568.67 | 1173.1 | 0.80199 | 1.3433 | 590.85
591.76 | 1450 | 1435.291 | 42.98 | 3.4613 | 605.72 | 566.88 | 1172.6 | 0.80317 | 1.3423 | 591.76
592.67 | 1460 | 1445.291 | 42.908 | 3.4909 | 607 | 565 | 1172 | 0.80435 | 1.3413 | 592.67
593.58 | 1470 | 1455.291 | 42.836 | 3.5206 | 608.27 | 563.23 | 1171.5 | 0.80552 | 1.3402 | 593.58
594.48 | 1480 | 1465.291 | 42.765 | 3.5504 | 609.54 | 561.36 | 1170.9 | 0.80668 | 1.3392 | 594.48
595.37 | 1490 | 1475.291 | 42.693 | 3.5804 | 610.81 | 559.59 | 1170.4 | 0.80785 | 1.3382 | 595.37
596.26 | 1500 | 1485.291 | 42.622 | 3.6105 | 612.08 | 557.72 | 1169.8 | 0.809 | 1.3372 | 596.26
597.15 | 1510 | 1495.291 | 42.55 | 3.6407 | 613.34 | 555.86 | 1169.2 | 0.81016 | 1.3362 | 597.15
598.03 | 1520 | 1505.291 | 42.479 | 3.671 | 614.6 | 554.1 | 1168.7 | 0.81131 | 1.3352 | 598.03
598.91 | 1530 | 1515.291 | 42.407 | 3.7015 | 615.86 | 552.24 | 1168.1 | 0.81245 | 1.3341 | 598.91
599.78 | 1540 | 1525.291 | 42.336 | 3.7321 | 617.11 | 550.39 | 1167.5 | 0.81359 | 1.3331 | 599.78
600.65 | 1550 | 1535.291 | 42.264 | 3.7629 | 618.36 | 548.64 | 1167 | 0.81473 | 1.3321 | 600.65
601.51 | 1560 | 1545.291 | 42.193 | 3.7938 | 619.6 | 546.8 | 1166.4 | 0.81587 | 1.3311 | 601.51
602.37 | 1570 | 1555.291 | 42.122 | 3.8248 | 620.85 | 544.95 | 1165.8 | 0.817 | 1.3301 | 602.37
603.23 | 1580 | 1565.291 | 42.05 | 3.856 | 622.09 | 543.11 | 1165.2 | 0.81812 | 1.3291 | 603.23
604.08 | 1590 | 1575.291 | 41.979 | 3.8873 | 623.33 | 541.27 | 1164.6 | 0.81924 | 1.3281 | 604.08
604.93 | 1600 | 1585.291 | 41.907 | 3.9187 | 624.56 | 539.44 | 1164 | 0.82036 | 1.3271 | 604.93
605.77 | 1610 | 1595.291 | 41.836 | 3.9503 | 625.79 | 537.61 | 1163.4 | 0.82148 | 1.3261 | 605.77
606.61 | 1620 | 1605.291 | 41.764 | 3.9821 | 627.02 | 535.78 | 1162.8 | 0.82259 | 1.3251 | 606.61
607.45 | 1630 | 1615.291 | 41.693 | 4.014 | 628.25 | 533.95 | 1162.2 | 0.8237 | 1.3241 | 607.45
608.28 | 1640 | 1625.291 | 41.621 | 4.046 | 629.47 | 532.13 | 1161.6 | 0.8248 | 1.3231 | 608.28
609.11 | 1650 | 1635.291 | 41.55 | 4.0782 | 630.7 | 530.3 | 1161 | 0.82591 | 1.3221 | 609.11
609.93 | 1660 | 1645.291 | 41.478 | 4.1105 | 631.91 | 528.49 | 1160.4 | 0.827 | 1.3211 | 609.93
610.75 | 1670 | 1655.291 | 41.407 | 4.143 | 633.13 | 526.67 | 1159.8 | 0.8281 | 1.3201 | 610.75
611.56 | 1680 | 1665.291 | 41.335 | 4.1757 | 634.35 | 524.75 | 1159.1 | 0.82919 | 1.3191 | 611.56
612.38 | 1690 | 1675.291 | 41.264 | 4.2085 | 635.56 | 522.94 | 1158.5 | 0.83028 | 1.3181 | 612.38
613.18 | 1700 | 1685.291 | 41.192 | 4.2415 | 636.77 | 521.13 | 1157.9 | 0.83137 | 1.3171 | 613.18
613.99 | 1710 | 1695.291 | 41.12 | 4.2746 | 637.98 | 519.32 | 1157.3 | 0.83245 | 1.3161 | 613.99
614.79 | 1720 | 1705.291 | 41.048 | 4.3079 | 639.18 | 517.42 | 1156.6 | 0.83353 | 1.3151 | 614.79
615.59 | 1730 | 1715.291 | 40.977 | 4.3414 | 640.39 | 515.61 | 1156 | 0.83461 | 1.3141 | 615.59
616.38 | 1740 | 1725.291 | 40.905 | 4.375 | 641.59 | 513.71 | 1155.3 | 0.83568 | 1.3131 | 616.38
617.17 | 1750 | 1735.291 | 40.833 | 4.4088 | 642.79 | 511.91 | 1154.7 | 0.83676 | 1.3121 | 617.17
617.96 | 1760 | 1745.291 | 40.761 | 4.4428 | 643.98 | 510.02 | 1154 | 0.83783 | 1.3111 | 617.96
618.74 | 1770 | 1755.291 | 40.689 | 4.477 | 645.18 | 508.22 | 1153.4 | 0.83889 | 1.3101 | 618.74
619.52 | 1780 | 1765.291 | 40.617 | 4.5113 | 646.37 | 506.33 | 1152.7 | 0.83996 | 1.3091 | 619.52
620.29 | 1790 | 1775.291 | 40.545 | 4.5458 | 647.57 | 504.53 | 1152.1 | 0.84102 | 1.3082 | 620.29
621.07 | 1800 | 1785.291 | 40.473 | 4.5805 | 648.76 | 502.64 | 1151.4 | 0.84208 | 1.3072 | 621.07
621.84 | 1810 | 1795.291 | 40.4 | 4.6153 | 649.95 | 500.75 | 1150.7 | 0.84314 | 1.3062 | 621.84
622.6 | 1820 | 1805.291 | 40.328 | 4.6504 | 651.13 | 498.87 | 1150 | 0.84419 | 1.3052 | 622.6
623.36 | 1830 | 1815.291 | 40.256 | 4.6856 | 652.32 | 497.08 | 1149.4 | 0.84524 | 1.3042 | 623.36
624.12 | 1840 | 1825.291 | 40.183 | 4.721 | 653.5 | 495.2 | 1148.7 | 0.8463 | 1.3032 | 624.12
624.88 | 1850 | 1835.291 | 40.11 | 4.7567 | 654.68 | 493.32 | 1148 | 0.84734 | 1.3022 | 624.88
625.63 | 1860 | 1845.291 | 40.038 | 4.7925 | 655.87 | 491.43 | 1147.3 | 0.84839 | 1.3012 | 625.63
626.38 | 1870 | 1855.291 | 39.965 | 4.8285 | 657.05 | 489.55 | 1146.6 | 0.84943 | 1.3002 | 626.38
627.13 | 1880 | 1865.291 | 39.892 | 4.8647 | 658.22 | 487.68 | 1145.9 | 0.85048 | 1.2992 | 627.13
627.87 | 1890 | 1875.291 | 39.819 | 4.9011 | 659.4 | 485.8 | 1145.2 | 0.85152 | 1.2982 | 627.87
628.61 | 1900 | 1885.291 | 39.746 | 4.9377 | 660.58 | 483.92 | 1144.5 | 0.85255 | 1.2972 | 628.61
629.35 | 1910 | 1895.291 | 39.673 | 4.9745 | 661.75 | 482.05 | 1143.8 | 0.85359 | 1.2962 | 629.35
630.08 | 1920 | 1905.291 | 39.6 | 5.0115 | 662.93 | 480.17 | 1143.1 | 0.85463 | 1.2952 | 630.08
630.81 | 1930 | 1915.291 | 39.526 | 5.0488 | 664.1 | 478.2 | 1142.3 | 0.85566 | 1.2942 | 630.81
631.54 | 1940 | 1925.291 | 39.453 | 5.0862 | 665.27 | 476.33 | 1141.6 | 0.85669 | 1.2932 | 631.54
632.27 | 1950 | 1935.291 | 39.379 | 5.1239 | 666.44 | 474.46 | 1140.9 | 0.85772 | 1.2922 | 632.27
632.99 | 1960 | 1945.291 | 39.305 | 5.1618 | 667.61 | 472.49 | 1140.1 | 0.85875 | 1.2912 | 632.99
633.71 | 1970 | 1955.291 | 39.232 | 5.1999 | 668.78 | 470.62 | 1139.4 | 0.85977 | 1.2902 | 633.71
634.42 | 1980 | 1965.291 | 39.158 | 5.2382 | 669.95 | 468.75 | 1138.7 | 0.8608 | 1.2892 | 634.42
635.14 | 1990 | 1975.291 | 39.083 | 5.2768 | 671.12 | 466.78 | 1137.9 | 0.86182 | 1.2882 | 635.14
635.85 | 2000 | 1985.291 | 39.009 | 5.3156 | 672.28 | 464.92 | 1137.2 | 0.86284 | 1.2872 | 635.85
636.56 | 2010 | 1995.291 | 38.935 | 5.3546 | 673.45 | 462.95 | 1136.4 | 0.86387 | 1.2862 | 636.56
637.26 | 2020 | 2005.291 | 38.86 | 5.3939 | 674.62 | 460.98 | 1135.6 | 0.86489 | 1.2852 | 637.26
637.96 | 2030 | 2015.291 | 38.785 | 5.4334 | 675.78 | 459.12 | 1134.9 | 0.8659 | 1.2842 | 637.96
638.66 | 2040 | 2025.291 | 38.71 | 5.4732 | 676.95 | 457.15 | 1134.1 | 0.86692 | 1.2831 | 638.66
639.36 | 2050 | 2035.291 | 38.635 | 5.5132 | 678.11 | 455.19 | 1133.3 | 0.86794 | 1.2821 | 639.36
640.05 | 2060 | 2045.291 | 38.56 | 5.5535 | 679.27 | 453.23 | 1132.5 | 0.86895 | 1.2811 | 640.05
640.74 | 2070 | 2055.291 | 38.485 | 5.594 | 680.44 | 451.36 | 1131.8 | 0.86997 | 1.2801 | 640.74
641.43 | 2080 | 2065.291 | 38.409 | 5.6348 | 681.6 | 449.4 | 1131 | 0.87098 | 1.2791 | 641.43
642.12 | 2090 | 2075.291 | 38.333 | 5.6758 | 682.77 | 447.43 | 1130.2 | 0.87199 | 1.2781 | 642.12
642.8 | 2100 | 2085.291 | 38.257 | 5.7172 | 683.93 | 445.47 | 1129.4 | 0.873 | 1.277 | 642.8
643.48 | 2110 | 2095.291 | 38.181 | 5.7587 | 685.09 | 443.51 | 1128.6 | 0.87402 | 1.276 | 643.48
644.16 | 2120 | 2105.291 | 38.105 | 5.8006 | 686.26 | 441.54 | 1127.8 | 0.87503 | 1.275 | 644.16
644.83 | 2130 | 2115.291 | 38.028 | 5.8428 | 687.42 | 439.48 | 1126.9 | 0.87604 | 1.274 | 644.83
645.51 | 2140 | 2125.291 | 37.951 | 5.8852 | 688.58 | 437.52 | 1126.1 | 0.87704 | 1.2729 | 645.51
646.18 | 2150 | 2135.291 | 37.874 | 5.9279 | 689.75 | 435.55 | 1125.3 | 0.87805 | 1.2719 | 646.18
646.85 | 2160 | 2145.291 | 37.797 | 5.9709 | 690.91 | 433.59 | 1124.5 | 0.87906 | 1.2709 | 646.85
647.51 | 2170 | 2155.291 | 37.72 | 6.0142 | 692.08 | 431.52 | 1123.6 | 0.88007 | 1.2698 | 647.51
648.17 | 2180 | 2165.291 | 37.642 | 6.0579 | 693.24 | 429.56 | 1122.8 | 0.88108 | 1.2688 | 648.17
648.83 | 2190 | 2175.291 | 37.564 | 6.1018 | 694.41 | 427.49 | 1121.9 | 0.88208 | 1.2678 | 648.83
649.49 | 2200 | 2185.291 | 37.486 | 6.146 | 695.57 | 425.53 | 1121.1 | 0.88309 | 1.2667 | 649.49
650.15 | 2210 | 2195.291 | 37.407 | 6.1906 | 696.74 | 423.46 | 1120.2 | 0.8841 | 1.2657 | 650.15
650.8 | 2220 | 2205.291 | 37.329 | 6.2355 | 697.91 | 421.39 | 1119.3 | 0.88511 | 1.2646 | 650.8
651.45 | 2230 | 2215.291 | 37.249 | 6.2807 | 699.08 | 419.42 | 1118.5 | 0.88611 | 1.2636 | 651.45
652.1 | 2240 | 2225.291 | 37.17 | 6.3262 | 700.25 | 417.35 | 1117.6 | 0.88712 | 1.2625 | 652.1
652.74 | 2250 | 2235.291 | 37.091 | 6.3721 | 701.42 | 415.28 | 1116.7 | 0.88813 | 1.2615 | 652.74
653.39 | 2260 | 2245.291 | 37.011 | 6.4183 | 702.59 | 413.21 | 1115.8 | 0.88914 | 1.2604 | 653.39
654.03 | 2270 | 2255.291 | 36.93 | 6.4649 | 703.76 | 411.14 | 1114.9 | 0.89014 | 1.2593 | 654.03
654.67 | 2280 | 2265.291 | 36.85 | 6.5119 | 704.93 | 409.07 | 1114 | 0.89115 | 1.2583 | 654.67
655.3 | 2290 | 2275.291 | 36.769 | 6.5592 | 706.11 | 406.99 | 1113.1 | 0.89216 | 1.2572 | 655.3
655.94 | 2300 | 2285.291 | 36.688 | 6.6069 | 707.28 | 404.92 | 1112.2 | 0.89317 | 1.2561 | 655.94
656.57 | 2310 | 2295.291 | 36.606 | 6.6549 | 708.46 | 402.84 | 1111.3 | 0.89418 | 1.255 | 656.57
657.2 | 2320 | 2305.291 | 36.525 | 6.7034 | 709.64 | 400.66 | 1110.3 | 0.89519 | 1.254 | 657.2
657.83 | 2330 | 2315.291 | 36.442 | 6.7522 | 710.82 | 398.58 | 1109.4 | 0.8962 | 1.2529 | 657.83
658.45 | 2340 | 2325.291 | 36.36 | 6.8014 | 712.01 | 396.49 | 1108.5 | 0.89722 | 1.2518 | 658.45
659.08 | 2350 | 2335.291 | 36.277 | 6.8511 | 713.19 | 394.31 | 1107.5 | 0.89823 | 1.2507 | 659.08
659.7 | 2360 | 2345.291 | 36.193 | 6.9012 | 714.38 | 392.12 | 1106.5 | 0.89925 | 1.2496 | 659.7
660.32 | 2370 | 2355.291 | 36.109 | 6.9516 | 715.57 | 390.03 | 1105.6 | 0.90026 | 1.2485 | 660.32
660.93 | 2380 | 2365.291 | 36.025 | 7.0026 | 716.76 | 387.84 | 1104.6 | 0.90128 | 1.2474 | 660.93
661.55 | 2390 | 2375.291 | 35.941 | 7.0539 | 717.95 | 385.65 | 1103.6 | 0.9023 | 1.2463 | 661.55
662.16 | 2400 | 2385.291 | 35.855 | 7.1057 | 719.15 | 383.45 | 1102.6 | 0.90332 | 1.2452 | 662.16
662.77 | 2410 | 2395.291 | 35.77 | 7.158 | 720.35 | 381.25 | 1101.6 | 0.90434 | 1.244 | 662.77
663.38 | 2420 | 2405.291 | 35.684 | 7.2107 | 721.55 | 379.05 | 1100.6 | 0.90536 | 1.2429 | 663.38
663.98 | 2430 | 2415.291 | 35.597 | 7.264 | 722.75 | 376.85 | 1099.6 | 0.90639 | 1.2418 | 663.98
664.59 | 2440 | 2425.291 | 35.51 | 7.3177 | 723.96 | 374.64 | 1098.6 | 0.90742 | 1.2407 | 664.59
665.19 | 2450 | 2435.291 | 35.423 | 7.3719 | 725.17 | 372.43 | 1097.6 | 0.90845 | 1.2395 | 665.19
665.79 | 2460 | 2445.291 | 35.335 | 7.4266 | 726.38 | 370.12 | 1096.5 | 0.90948 | 1.2384 | 665.79
666.39 | 2470 | 2455.291 | 35.246 | 7.4818 | 727.6 | 367.9 | 1095.5 | 0.91051 | 1.2372 | 666.39
666.98 | 2480 | 2465.291 | 35.157 | 7.5376 | 728.82 | 365.58 | 1094.4 | 0.91155 | 1.2361 | 666.98
667.58 | 2490 | 2475.291 | 35.067 | 7.5939 | 730.04 | 363.36 | 1093.4 | 0.91259 | 1.2349 | 667.58
668.17 | 2500 | 2485.291 | 34.977 | 7.6508 | 731.27 | 361.03 | 1092.3 | 0.91363 | 1.2338 | 668.17
668.76 | 2510 | 2495.291 | 34.886 | 7.7082 | 732.5 | 358.7 | 1091.2 | 0.91467 | 1.2326 | 668.76
669.35 | 2520 | 2505.291 | 34.794 | 7.7663 | 733.74 | 356.36 | 1090.1 | 0.91572 | 1.2314 | 669.35
669.93 | 2530 | 2515.291 | 34.702 | 7.8249 | 734.98 | 354.02 | 1089 | 0.91677 | 1.2302 | 669.93
670.52 | 2540 | 2525.291 | 34.609 | 7.8842 | 736.22 | 351.68 | 1087.9 | 0.91783 | 1.229 | 670.52
671.1 | 2550 | 2535.291 | 34.516 | 7.944 | 737.47 | 349.33 | 1086.8 | 0.91888 | 1.2278 | 671.1
671.68 | 2560 | 2545.291 | 34.421 | 8.0046 | 738.72 | 346.98 | 1085.7 | 0.91995 | 1.2266 | 671.68
672.25 | 2570 | 2555.291 | 34.326 | 8.0657 | 739.98 | 344.52 | 1084.5 | 0.92101 | 1.2254 | 672.25
672.83 | 2580 | 2565.291 | 34.231 | 8.1276 | 741.25 | 342.15 | 1083.4 | 0.92208 | 1.2242 | 672.83
673.41 | 2590 | 2575.291 | 34.134 | 8.1902 | 742.52 | 339.68 | 1082.2 | 0.92315 | 1.2229 | 673.41
673.98 | 2600 | 2585.291 | 34.037 | 8.2534 | 743.79 | 337.21 | 1081 | 0.92423 | 1.2217 | 673.98
674.55 | 2610 | 2595.291 | 33.939 | 8.3175 | 745.07 | 334.73 | 1079.8 | 0.92531 | 1.2205 | 674.55
675.12 | 2620 | 2605.291 | 33.84 | 8.3822 | 746.36 | 332.24 | 1078.6 | 0.9264 | 1.2192 | 675.12
675.68 | 2630 | 2615.291 | 33.74 | 8.4478 | 747.65 | 329.75 | 1077.4 | 0.92749 | 1.2179 | 675.68
676.25 | 2640 | 2625.291 | 33.639 | 8.5141 | 748.95 | 327.25 | 1076.2 | 0.92859 | 1.2167 | 676.25
676.81 | 2650 | 2635.291 | 33.537 | 8.5813 | 750.26 | 324.64 | 1074.9 | 0.92969 | 1.2154 | 676.81
677.37 | 2660 | 2645.291 | 33.435 | 8.6493 | 751.57 | 322.13 | 1073.7 | 0.93079 | 1.2141 | 677.37
677.93 | 2670 | 2655.291 | 33.331 | 8.7182 | 752.9 | 319.5 | 1072.4 | 0.93191 | 1.2128 | 677.93
678.49 | 2680 | 2665.291 | 33.227 | 8.788 | 754.22 | 316.88 | 1071.1 | 0.93303 | 1.2115 | 678.49
679.04 | 2690 | 2675.291 | 33.121 | 8.8588 | 755.56 | 314.24 | 1069.8 | 0.93415 | 1.2101 | 679.04
679.6 | 2700 | 2685.291 | 33.015 | 8.9305 | 756.9 | 311.6 | 1068.5 | 0.93528 | 1.2088 | 679.6
680.15 | 2710 | 2695.291 | 32.907 | 9.0032 | 758.26 | 308.94 | 1067.2 | 0.93642 | 1.2075 | 680.15
680.7 | 2720 | 2705.291 | 32.798 | 9.0769 | 759.62 | 306.28 | 1065.9 | 0.93756 | 1.2061 | 680.7
681.25 | 2730 | 2715.291 | 32.688 | 9.1517 | 760.99 | 303.51 | 1064.5 | 0.93871 | 1.2047 | 681.25
681.8 | 2740 | 2725.291 | 32.577 | 9.2276 | 762.36 | 300.74 | 1063.1 | 0.93987 | 1.2033 | 681.8
682.34 | 2750 | 2735.291 | 32.465 | 9.3047 | 763.75 | 297.95 | 1061.7 | 0.94104 | 1.2019 | 682.34
682.88 | 2760 | 2745.291 | 32.352 | 9.3829 | 765.15 | 295.15 | 1060.3 | 0.94221 | 1.2005 | 682.88
683.43 | 2770 | 2755.291 | 32.237 | 9.4624 | 766.56 | 292.34 | 1058.9 | 0.94339 | 1.1991 | 683.43
683.97 | 2780 | 2765.291 | 32.121 | 9.5432 | 767.98 | 289.42 | 1057.4 | 0.94458 | 1.1977 | 683.97
684.5 | 2790 | 2775.291 | 32.003 | 9.6253 | 769.4 | 286.5 | 1055.9 | 0.94578 | 1.1962 | 684.5
685.04 | 2800 | 2785.291 | 31.885 | 9.7088 | 770.85 | 283.55 | 1054.4 | 0.94699 | 1.1947 | 685.04
685.57 | 2810 | 2795.291 | 31.764 | 9.7937 | 772.3 | 280.6 | 1052.9 | 0.94821 | 1.1932 | 685.57
686.11 | 2820 | 2805.291 | 31.643 | 9.8802 | 773.76 | 277.54 | 1051.3 | 0.94943 | 1.1917 | 686.11
686.64 | 2830 | 2815.291 | 31.52 | 9.9682 | 775.24 | 274.56 | 1049.8 | 0.95067 | 1.1902 | 686.64
687.17 | 2840 | 2825.291 | 31.395 | 10.058 | 776.73 | 271.47 | 1048.2 | 0.95192 | 1.1886 | 687.17
687.7 | 2850 | 2835.291 | 31.269 | 10.149 | 778.23 | 268.27 | 1046.5 | 0.95318 | 1.187 | 687.7
688.22 | 2860 | 2845.291 | 31.141 | 10.243 | 779.74 | 265.16 | 1044.9 | 0.95445 | 1.1854 | 688.22
688.75 | 2870 | 2855.291 | 31.011 | 10.338 | 781.28 | 261.92 | 1043.2 | 0.95573 | 1.1838 | 688.75
689.27 | 2880 | 2865.291 | 30.88 | 10.435 | 782.82 | 258.68 | 1041.5 | 0.95702 | 1.1822 | 689.27
689.79 | 2890 | 2875.291 | 30.747 | 10.534 | 784.39 | 255.31 | 1039.7 | 0.95833 | 1.1805 | 689.79
690.31 | 2900 | 2885.291 | 30.612 | 10.636 | 785.97 | 252.03 | 1038 | 0.95965 | 1.1788 | 690.31
690.83 | 2910 | 2895.291 | 30.475 | 10.74 | 787.56 | 248.54 | 1036.1 | 0.96099 | 1.177 | 690.83
691.34 | 2920 | 2905.291 | 30.335 | 10.846 | 789.18 | 245.12 | 1034.3 | 0.96234 | 1.1753 | 691.34
691.86 | 2930 | 2915.291 | 30.193 | 10.956 | 790.82 | 241.58 | 1032.4 | 0.96371 | 1.1735 | 691.86
692.37 | 2940 | 2925.291 | 30.049 | 11.068 | 792.48 | 237.92 | 1030.4 | 0.9651 | 1.1716 | 692.37
692.88 | 2950 | 2935.291 | 29.903 | 11.183 | 794.16 | 234.24 | 1028.4 | 0.96651 | 1.1698 | 692.88
693.39 | 2960 | 2945.291 | 29.753 | 11.301 | 795.87 | 230.53 | 1026.4 | 0.96794 | 1.1678 | 693.39
693.9 | 2970 | 2955.291 | 29.6 | 11.423 | 797.61 | 226.69 | 1024.3 | 0.96939 | 1.1659 | 693.9
694.4 | 2980 | 2965.291 | 29.444 | 11.549 | 799.38 | 222.72 | 1022.1 | 0.97087 | 1.1639 | 694.4
694.91 | 2990 | 2975.291 | 29.285 | 11.678 | 801.18 | 218.72 | 1019.9 | 0.97237 | 1.1618 | 694.91
695.41 | 3000 | 2985.291 | 29.121 | 11.812 | 803.02 | 214.58 | 1017.6 | 0.97391 | 1.1597 | 695.41
695.91 | 3010 | 2995.291 | 28.953 | 11.951 | 804.9 | 210.3 | 1015.2 | 0.97548 | 1.1575 | 695.91
696.41 | 3020 | 3005.291 | 28.78 | 12.096 | 806.83 | 205.97 | 1012.8 | 0.97709 | 1.1553 | 696.41
696.91 | 3030 | 3015.291 | 28.601 | 12.245 | 808.8 | 201.5 | 1010.3 | 0.97875 | 1.1529 | 696.91
697.4 | 3040 | 3025.291 | 28.416 | 12.402 | 810.84 | 196.86 | 1007.7 | 0.98045 | 1.1505 | 697.4
697.9 | 3050 | 3035.291 | 28.223 | 12.565 | 812.94 | 191.96 | 1004.9 | 0.98221 | 1.1481 | 697.9
698.39 | 3060 | 3045.291 | 28.022 | 12.736 | 815.12 | 186.98 | 1002.1 | 0.98403 | 1.1455 | 698.39
698.88 | 3070 | 3055.291 | 27.812 | 12.916 | 817.38 | 181.72 | 999.1 | 0.98593 | 1.1428 | 698.88
699.37 | 3080 | 3065.291 | 27.591 | 13.106 | 819.75 | 176.22 | 995.97 | 0.98792 | 1.14 | 699.37
699.85 | 3090 | 3075.291 | 27.356 | 13.307 | 822.23 | 170.45 | 992.68 | 0.99 | 1.137 | 699.85
700.34 | 3100 | 3085.291 | 27.107 | 13.521 | 824.85 | 164.35 | 989.2 | 0.9922 | 1.1339 | 700.34
700.82 | 3110 | 3095.291 | 26.839 | 13.751 | 827.64 | 157.85 | 985.49 | 0.99454 | 1.1306 | 700.82
701.31 | 3120 | 3105.291 | 26.55 | 13.999 | 830.62 | 150.91 | 981.53 | 0.99705 | 1.127 | 701.31
701.79 | 3130 | 3115.291 | 26.236 | 14.268 | 833.84 | 143.42 | 977.26 | 0.99976 | 1.1232 | 701.79
702.26 | 3140 | 3125.291 | 25.89 | 14.564 | 837.35 | 135.26 | 972.61 | 1.0027 | 1.1191 | 702.26
702.74 | 3150 | 3135.291 | 25.506 | 14.895 | 841.21 | 126.28 | 967.49 | 1.006 | 1.1146 | 702.74
703.22 | 3160 | 3145.291 | 25.073 | 15.271 | 845.54 | 116.2 | 961.74 | 1.0096 | 1.1096 | 703.22
703.69 | 3170 | 3155.291 | 24.575 | 15.713 | 850.5 | 104.6 | 955.1 | 1.0138 | 1.1038 | 703.69
704.16 | 3180 | 3165.291 | 23.976 | 16.262 | 856.44 | 90.6 | 947.04 | 1.0189 | 1.0967 | 704.16
704.63 | 3190 | 3175.291 | 23.17 | 17.031 | 864.44 | 71.62 | 936.06 | 1.0257 | 1.0872 | 704.63
705.1 | 3200 | 3185.291 | 20.634 | 19.561 | 890.67 | 12.35 | 903.02 | 1.0481 | 1.0587 | 705.1
705.1 | 3200.1 | 3185.391 | 21.758 | 21.758 | 878.83 | 0 | 878.83 | 1.038 | 1.038 | 705.1