## Cost Benefit
For Hijend Hotel Ball Room Branch Duct to Reheat Coils
[6 empty] | V Groove | Fabricated Airfoil | Extruded Airfoil
[5 empty] | Flow - | 10000 | 10000 | 10000 | cfm | Flow = Velocity x Area
[5 empty] | Duct Area - | 6.8611 | 6.8611 | 6.8611 | sq.ft.
[5 empty] | Velocity - | 1457.4899 | 1457.4899 | 1457.4899 | fpm
[5 empty] | Static - | 0.15591 | 0.10962 | 0.058418 | in.w.c.
[5 empty] | Motor efficiency - | 92.4% | 92.4% | 92.4%
[5 empty] | Belt efficiency - | 97% | 97% | 97%
[5 empty] | VSD efficiency - | 97% | 97% | 97%
[5 empty] | kW - | 0.21048 | 0.148 | 0.078865
[5 empty] | Operating Hours - | 5000 | 5000 | 5000
[5 empty] | kWh - | 1052.4145 | 739.9761 | 394.3241
[5 empty] | Savings - | Base Case | 312.4384 | 658.0904
[5 empty] | Cost of electricity - | 0.19 | 0.19 | 0.19
[7 empty] | 59.3633 | 125.0372
[5 empty] | Damper cost - | 1026.4222 |  | 1213.0444
[5 empty] | Difference - |  |  | 186.6222
[5 empty] | Simple payback - |  |  | 1.4925 | years
At a Higher Velocity
[6 empty] | V Groove | Fabricated Airfoil | Extruded Airfoil
[5 empty] | Flow - | 10000 | 10000 | 10000 | cfm
[5 empty] | Duct Area - | 5 | 5 | 5 | sq.ft.
[5 empty] | Velocity - | 2000 | 2000 | 2000 | fpm
[5 empty] | Static - | 0.29074 | 0.21321 | 0.11 | in.w.c.
[5 empty] | Motor efficiency - | 92.4% | 92.4% | 92.4%
[5 empty] | Belt efficiency - | 97% | 97% | 97%
[5 empty] | VSD efficiency - | 97% | 97% | 97%
[5 empty] | kW - | 0.39251 | 0.28784 | 0.1485
[5 empty] | Operating Hours - | 5000 | 5000 | 5000
[5 empty] | kWh - | 1962.5272 | 1439.1953 | 742.5098
[5 empty] | Savings - | Base Case | 523.3318 | 1220.0174
[5 empty] | Cost of electricity - | 0.19 | 0.19 | 0.19
[7 empty] | 99.433 | 231.8033
[5 empty] | Damper cost - | 748 |  | 884
[5 empty] | Difference - |  |  | 136
[5 empty] | Simple payback - |  |  | 0.5867 | years
24/7 Operation
| V Groove | Extruded Airfoil |  |  |  | V Groove | Fabricated Airfoil | Extruded Airfoil
Damper cost based on 24 x 24 damper - | 149.6 | 176.8 | $/sq.ft. |  | Flow - | 10000 | 10000 | 10000 | cfm
Data Source - | ..\..\..\..\..\Technical Library\Costs\Airfoil Blade vs. Conventional Blade.txt |  |  |  | Duct Area - | 5 | 5 | 5 | sq.ft.
| https://www.bls.gov/data/inflation_calculator.htm |  |  |  | Velocity - | 2000 | 2000 | 2000 | fpm
[5 empty] | Static - | 0.29074 | 0.21321 | 0.11 | in.w.c.
[5 empty] | Motor efficiency - | 92.4% | 92.4% | 92.4%
[5 empty] | Belt efficiency - | 97% | 97% | 97%
[5 empty] | VSD efficiency - | 97% | 97% | 97%
[5 empty] | kW - | 0.39251 | 0.28784 | 0.1485
[5 empty] | Operating Hours - | 8760 | 8760 | 8760
[5 empty] | kWh - | 3438.3476 | 2521.4702 | 1300.8772
[5 empty] | Savings - | Base Case | 916.8774 | 2137.4704
[5 empty] | Cost of electricity - | 0.19 | 0.19 | 0.19
[7 empty] | 174.2067 | 406.1194
[5 empty] | Damper cost - | 748 |  | 884
[5 empty] | Difference - |  |  | 136
[5 empty] | Simple payback - |  |  | 0.33488 | years

## Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2011-10-23 10:25
Project Name: | None
Project Number: | None
Engineer: | David
Assumptions
1 | Based on Gfeenheck Catalog Data
2 | ????
3 | ????
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????
|  | Velocity, fpm | Static Loss |  |  | Static Loss - Square Law Basis |  |  | % Improvement Relative to SMD-203
|  |  | SMD-203 (V groove blade) | SMD-301 (fabricated airfoil) | SMD-401 (extruded aluminum airfoil) | SMD-203 (V groove blade) | SMD-301 (fabricated airfoil) | SMD-401 (extruded aluminum airfoil) | SMD-203 (V groove blade) | SMD-301 (fabricated airfoil) | SMD-401 (extruded aluminum airfoil)
|  | 500 | 0.02 | 0.01 | 0.006875 | 0.018125 | 0.013594 | 0.006875 | Baseline | 50% | 65.62%
|  | 1000 | 0.07 | 0.06 | 0.0275 | 0.0725 | 0.054375 | 0.0275 |  | 14.29% | 60.71%
|  | 1500 | 0.16 | 0.12 | 0.061875 | 0.16312 | 0.12234 | 0.061875 |  | 25% | 61.33%
|  | 2000 | 0.29 | 0.22 | 0.11 | 0.29 | 0.2175 | 0.11 |  | 24.14% | 62.07%
|  | 2500 | 0.45 | 0.34 | 0.17188 | 0.45312 | 0.33984 | 0.17188 |  | 24.44% | 61.81%
|  | 3000 | 0.65 | 0.49 | 0.2475 | 0.6525 | 0.48938 | 0.2475 |  | 24.62% | 61.92%
|  | 3500 | 0.89 | 0.67 | 0.33687 | 0.88812 | 0.66609 | 0.33687 |  | 24.72% | 62.15%
|  | 4000 | 1.16 | 0.87 | 0.44 | 1.16 | 0.87 | 0.44 |  | 25% | 62.07%
|  | Velocity, fpm | Static Loss
|  |  | SMD-401 with a plenum in and out | SMD-401 with open discharge | SMD-401 at full duct size
|  | 500 | 0.039062 | 0.017188 | 0.006875
|  | 1000 | 0.15625 | 0.06875 | 0.0275
|  | 1500 | 0.35156 | 0.15469 | 0.061875
|  | 2000 | 0.625 | 0.275 | 0.11
|  | 2500 | 0.97656 | 0.42969 | 0.17188
|  | 3000 | 1.4062 | 0.61875 | 0.2475
|  | 3500 | 1.9141 | 0.84219 | 0.33687
|  | 4000 | 2.5 | 1.1 | 0.44