## Slide 1: The Simplified Design Intent System Diagram
Ch2
Pm
Ch1
Pm
Pm
Pm
VF1
AHU8
AHU9
AHU10
AHU1
AHU7
South FC Riser 1A
South FC Riser 8A
North FC Riser 8D
North FC Riser 1D
AHU5
AHU6
AHU2
AHU3
AHU4
A
B
C
D
MATCH LINE
See Below
A
B
C
D
MATCH LINE
See Above
See Sheet 11
See Sheets 7 - 10
See Sheets 3 - 6
See Sheet 2
See Sheet 1

## Slide 2: Design Intent System Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 1
Fixed Spd
SD
TDV
Chiller 2
VFD & HG
SD
TDV
SD
TDV
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1
Central Plant portion
NC