## Working Table
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Date: | 2017-11-17 15:30
Project Name: | PEC EBCx Series 13 - Byers Hall Site Visit
Project Number:
Engineer: | David
Assumptions
1 |  | Electric rate = | 0.11893 | $ per kWh |  | Source -
2 |  | Gas rate = | 0.77551 | $ per therm |  | Source -
3 |  | Steam rate = |  | $ per therm
4 |  | Water rate = | 0.011581 | $ per gallon |  | Source -
5 |  | Steam thermal content = | 1000 | btu/pound
6 |  | Electrical incentive = | 0 | per kWh
7 |  | Thermal incentive = | 0 | per therm
Working Table | Enter data in to the columns with a yellow header for each finding as it is developed and the rest of the columns should calculate accordingly
| Number | Brief Description | Total Savings $ |  | Incentive, $ |  | Implementation Cost Projections, $ |  | Implementation Cost After Incentives, $ |  | Simple Payback Range After Incentives, Years |  | Electricity | [5 empty] | Gas |  |  |  | Other Savings | [5 empty] | Notes | NOTES
[13 empty] | kWh savings |  |  |  | kW savings |  | Therm Savings | [10 empty] | 1
[13 empty] | Low end |  | High end |  | Low End | High End | Low end |  | High end |  | Low end |  |  | High end |  |  |  | 2
|  |  | Low End | High End | Low End | High End | Low End | High End | Low End | High End | Low End | High End | kWh | $ | kWh | $ |  |  | Therm | $ | Therms | $ | Amount | Units | $ | Amount | Units | $
| 1 | The chiller seemed to have 200-300 tons of load on it on a cool day in a building with near 100% OA AHUs; Is there that much load that can not be served by OA? | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 2 | The condenser water pumps are slighlty throttled. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0 |  | 3
| 3 | The chillers share a common CW header and could see a significant change in head depending on how many machines are on. As a result running only one machine and pump may be producing more CW flow than required. A field assessment of the potential head change indicates this is possible. The delta t and heat balance on the machine suggest 200-300 gpm more than design with one machine. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 4 | The chillers appear to have constant flow valves installed, probably in an effort to mitigate item 3. But removing the valve and using a VFD to address the problem will likely save pump energy. If the head indicated on the equipment schedule is correct and the flow was near design when we were there, then the flow control valve could have about as much pressure drop through it as the condenser based on the delta p sensor, which is piped across both of them. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 5 | Related to item 1, once the true base load is identified, there may be a viable payback in a capital project that provided a low load chiller tailored to the base load in terms of compressor efficiency and auxilliary energy using a modular chiller approach. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 6 | Make sure that the packaged unit serving the elevator machine room has an econmoizer and that it works and that the set points are coordinated with the actual elevator machine requirements. They can often work just fine with temperatures in the 80°F range (vs. the upper 60's°F) | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 7 | There seemed to be a difference between the HHW set point the control system indicated it was looking for (160°F) and the temperature the boilers seemed to fire to (200°F plus). That could indicate a number of problems including something wrong with the interface between the control system and the boiler, improper adjustment of the boiler firing controls, or a failure of some portion of the boiler control system (i.e. it may be running on a limit control vs. an operating control because the operating control has failed). | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0 |  | 4
| 8 | Related to item 7, the boilers seem to be purging as much as they are firing productively (i.e. they are short cycling). In watching a couple of cycles, it looked like the boilers simply went to high fire and sat there until they cut out. That could mean there is a problem with the part of the process that is supposed to modulate the boiler to match the load. Or it could mean that the load is so low relative to the boiler size that the boiler can not fire long enough to allow the burner to adjust to match the load. So this should be part of what is checked when addressing item 7. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 9 | Related to items 7 and 8, if the boiler is short cycling simply because it can not operate long enough to begin to match the load, then there may be a financial case for a capital project that provided for a low load boiler. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0 |  | 5
| 10 | It is likely that you could operate the hot water system at much lower temperatures than | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 11 | Related to item 5, there appears to be a chilled water connection to a central plant. This could provide another option for serving the base load more efficiently. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0 |  | 4
| 12 | Related to item 9, the drawings show a high pressure steam and condensate return line from what I suspect is a central plant. If that is true, then adding steam heat exchangers to serve the building load may be attractive rather than some sort of low load boiler. The steam heat exchangers would also open the door to reseting water temperatures much lower than you could with the existing boilers due to condensation issues. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 13 | Given the laboratory application, the filtration requirements in the facility are significant and make it a good candidate for looking at life cycle cost based filter operaiton. I know that they were looking at this in other USCF facilities, so there may already be a plan in place or a pilot running. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0 |  | 5
| 14 | The flow distribution over the cooling towers was dynamically non-uniform as we observed in class. My current theory on how pipes connected to the tee inside the tower with no valves in them could experience flow on one side and not the other is that there is air trapped in the inverted trap the piping creates. I am working on an annimation to explain this and will follow up with that when I get it done. As we discussed in class, there are other implications to this problem aside from energy efficinecy related to ruining the fill/reducing its life. Those implications could actualy be more significant than the fan energy implication and would need to be considered in assessing this finding. This finding is also interactive with the findings related to condenser water flow, which would also need to be considered. | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 15 | There appears to be some zone level scheduling going on in the air handling system. But it is possible that there are additional opportunities for areas like conference rooms where some sort of occupancy based scheduling technique would be used vs. time of day. And, as Ryan observed, it may also be possible to further optimize the time schedules based on how people really use the facility vs. how the imagine they might use the facility | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| 16 |  | To Be Determined | To Be Determined | None Offered | None Offered |  |  | 0 | 0 | To Be Determined | To Be Determined | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | None | N/A | 0 | None | N/A | 0
| TOTALS |  | To Be Determined | To Be Determined | None Offered | None Offered | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined | To Be Determined |  |  | To Be Determined |  |  | To Be Determined
0
0

## Initial Cost-Benefit Assessment
MBCx/EBCx Project Cost Benefit Assessment from Scoping Phase Data and Industry Metrics | [7 empty] | Steam conversion
Second Version - October | [7 empty] | Meter reading - | 3111520 | lb of steam for 2012 (from Obvious)
This spreadsheet projects what an acceptable budget might be for an MBCx/EBCx project based on the anticipated savings and incentives. The anticipated savings are derived from current utility data and the metrics contained in the LBNL Commissioning Cost/Benefit Studies. Links to the studies are provided below. | [7 empty] | Btu/lb | 1000 | Btu/lb (campus conversion standard)
LBNL Report | Summary |  |  |  | Full Report |  |  | Plant efficiency | 80% | (Campus over-all plant efficiency standard)
The Cost-Effectiveness of Commercial-Buildings Commissioning (Original December 15, 2004 Assessment) | http://cx.lbl.gov/2004-assessment.html |  |  |  | http://evanmills.lbl.gov/pubs/pdf/cx-costs-benefits.pdf |  |  | Btu/therm | 100000 | Btu/therm
Building Commissioning; A Golden Opportunity for Reducing Energy Costs and Greenhouse Gas Emissions (July 21, 2009 Update) | http://cx.lbl.gov/2009-assessment.html |  |  |  | http://cx.lbl.gov/documents/2009-assessment/lbnl-cx-cost-benefit.pdf |  |  | Therms | 38894 | Therms
Monitoring-Based Commissioning: Benchmarking Analysis of 24 UC/CSU/IOU Projects (Focus on MBCx only projects) | http://cx.lbl.gov/mbcx.html |  |  |  | http://evanmills.lbl.gov/pubs/pdf/MBCx-LBNL.pdf
The other tabs in this spreadsheet are the tables we have been using on UC Berkeley and other projects to develop findings lists. This tab references them for some of its information, which is why they are part of the workbook. However, you could extract this tab and use it independently if you supplied the findings list data from some other source. The blue highlighted cells discuss this further where appropriate.
The Cost Benefit Discussion tab contains images showing how we endeavored to use this information in a proposal for a UC Berkeley project to frame our fee in the context of the Owner's payback metrics and project goals.
Cells with the light yellow highlighting are cells that you would need to fill in with project specific information to get meaningful results. Some can ro should be linked as noted
Cells with the light green highlighting are cells that you might want to modify depending on the specifics of your project, the incentive program, if any, your building type, etc.
Cells with the light blue highlighting contain information regarding what the other shaded cells are used for and/or what they mean and how you might go about filling them in.
Cells with the yellow highlighting and the red boarders are the "answers"
Remember that the results you get are only as good as the inputs and event then are an approximation at best. Before you use them, do a quick sanity check somehow to make sure they make sense, especially if you have edited anything because that might affect the formulas.
Project Energy Metrics - Source as indicated
Electric rate - | 0.11893 | $/kWh - Link to the cell with the correct metric in the working table - Just needs to be reasonable and representative of current rates
Thermal energy rate - | 0.77551 | $ per therm - Ditto above
Electrical incentive - | 0 | $ per kWh - Ditto above; Non-utility program driven projects will not have this.
Thermal incentive - | 0 | $ per therm - Ditto above; Non-utility program driven projects will not have this.
Building square footage - | 660000 | Hyperlink to Source
Site energy electrical energy conversion factor - | 3413 | Btu/kWh
Source energy electrical energy conversion factor - | 11484.745 | Btu/Kwh |  |  |  | Source = | EnergyStart Portfolio Manager Source Energy Technical Reference
Source energy thermal energy conversion factor - | 1.05 | Therms at the well head per therm delivered |  |  |  | Source = | EnergyStart Portfolio Manager Source Energy Technical Reference
Annual Consumption - From a baseline report, utility bills, utility meters, etc.
| Energy | $
Electricity - kWh/$ per year |  | 0 | Source = | Hyperlink to Source
Thermal at the Central Plant - Therms/$ per year |  | 0 | Source = | Hyperlink to Source
TOTAL |  | 0 | $ per year
|  | 0 | $ per square foot per year
EUI Factors | Site Energy | Source Energy
Electrical Energy | 0 | 0 | kBtu/sq.ft./yr. | Cross-check this with any other EUI you might have calculated. The should agree
Thermal Energy | 0 | 0 | kBtu/sq.ft./yr. | Cross-check this with any other EUI you might have calculated. The should agree
Total | 0 | 0 | kBtu/sq.ft./yr. | Cross-check this with any other EUI you might have calculated. The should agree
Savings Projection Based on the LBNL Cost Benefit Study
LBNL Cx Cost Benefit Median Energy Savings (2009 update) - | 16% | of Whole Building Energy Consumption. |  |  | This is the median value reported for existing building commissioning in the 2009 update to the original report. If you look at the report that focuses on MBCx only projects, the savings range was quite broad; 2 to 25%. So I used this number because it is in the middle of that range, it is citable, and it is consistent with my personal experience over the years. Generally, it should be a good default. But it could also be set based on past experience with other projects, especially other projects at a certain location or with a certain client. Or it could be tuned to a specific building type from data in the LBNL reports.
| Low End | High End
Potential savings range for the purposes of our discussion - | 10% | 16% | High end set from metric above, low end set at 62.5% of the high end to create a range; either could be set manually instead.
Potential annual savings - | 0 | 0 | $ per year
Percentage of the annual savings to be allocated electricity - | #DIV/0!
Percentage of the annual savings to be allocated to thermal - | #DIV/0!
Potential electrical savings - | #DIV/0! | #DIV/0! | kWh per year
| #DIV/0! | #DIV/0! | $ per year
Potential thermal savings - | #DIV/0! | #DIV/0! | Therms per year
| #DIV/0! | #DIV/0!
Projected EUIs Post Implementation
| Low End |  | High End
| Site Energy | Source Energy | Site Energy | Source Energy
Electrical Energy | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | kBtu/sq.ft./yr.
Thermal Energy | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | kBtu/sq.ft./yr.
Total | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | kBtu/sq.ft./yr.
Potential electrical savings already identified - | #DIV/0! | #DIV/0! | Average kWh per year from the findings list |  |  | Source = | ..\..\..\..\..\ComIT\Project Data\UCB_MinorAddtn\Rons Report\Minor Addition ECM Implementation Recommendation Report (October 9, 2013).pdf
| #DIV/0! |  | Average $ per year from the findings list
% of potential electrical savings - | #DIV/0! | #DIV/0!
Potential thermal savings already identified - | #DIV/0! | #DIV/0! | Average therms per year from the findings list |  |  | Source = | ..\..\..\..\..\ComIT\Project Data\UCB_MinorAddtn\Rons Report\Minor Addition ECM Implementation Recommendation Report (October 9, 2013).pdf
| #DIV/0! |  | Average $ per year from the findings list
% of potential thermal savings - | #DIV/0! | #DIV/0!
Potential non-energy savings already identified - | 0 | 0 | Average $ per year from the findings list | [5 empty] | 0.80001
Total savings already identified - | #DIV/0! | 0 | Average $ per year from the findings list
| #DIV/0! | #DIV/0! | % of LBNL based projection
Potential electrical incentive - | #DIV/0! | #DIV/0! | $ | These figures are calculated from other parameters in the spreadsheet. For programs that have no utility incentives, they will be zero.
Potential thermal incentive - | #DIV/0! | #DIV/0! | $
Expenditure Justified by Anticipated Savings
Simple payback time frame - | 5 | years | 10 | years | This is where you enter the simple payback range that is acceptable to the Owner
Savings range - | Low End | High End | Low End | High End | These figures are calculated from other parameters in the spreadsheet. In general terms, they reverse engineer a budget based on the Owner's acceptable simple payback parameters. If there are utility incentives, they are added to the energy savings based budget, meaning the simple payback will be achieved after the incentives are subtracted from the over-all project costs.
Energy savings after the indicated interval, 2013 $ - | 0 | 0 | 0 | 0
Incentive, 2013 $ - | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Total, 2013 $ - | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Project Budget based on Past Project Metrics
Item | 5 Year Simple Payback, Average Savings | [5 empty] | The budget dollars and $/sq.ft. parameters here are calculated based on other parameters in the spreadsheet. The percentages used to prorate the budget and the categories shown are based on two projects where I had access to the full budget information (I kind of wasn't supposed to so we should not exactly advertise that). They are representative of our experience with the UCB MBCx program and probably are not a bad way to assess other similar programs. For other projects and clients, you may need to add different budget components or change the percentages allocated to various items. If you do that, be aware that some of the percentages are calculated from others based on what was known and what was unknown for the UCB work. Specifically, the non-highlighted cells are calculated from the highlighted cells. So, if you make changes, be sure that everything adds up. That is the purpose of the check row. The numbers there should match the bottom line in the table. Of course, your edits could affect that to so verify your formulas if you start editing.
| Contractor Intensive (Le Conte ECM Basis) |  |  | Non-Contractor Intensive (Le Conte MBCx Basis)
| % of Total | $ | $/sq.ft. | % of Total | $ | $/sq.ft.
Project Technical Support
FDE Scoping | 2% | #DIV/0! | #DIV/0! | 9% | #DIV/0! | #DIV/0!
FDE Implementation | 24% | #DIV/0! | #DIV/0! | 29% | #DIV/0! | #DIV/0!
FDE TOTAL | 26% | #DIV/0! | #DIV/0! | 38% | #DIV/0! | #DIV/0!
Capital Projects | 3% | #DIV/0! | #DIV/0! | 12% | #DIV/0! | #DIV/0!
Physical Plant | 1% | #DIV/0! | #DIV/0! | 1% | #DIV/0! | #DIV/0!
TOTAL - Project Technical Support | 30% | #DIV/0! | #DIV/0! | 51% | #DIV/0! | #DIV/0!
Metering | 0% | #DIV/0! | #DIV/0! | 0% | #DIV/0! | #DIV/0!
Construction/Contractors | 68% | #DIV/0! | #DIV/0! | 44% | #DIV/0! | #DIV/0!
Contingency | 2% | #DIV/0! | #DIV/0! | 5% | #DIV/0! | #DIV/0!
TOTAL | 100% | #DIV/0! | #DIV/0! | 100% | #DIV/0! | #DIV/0!
Check | 100% | #DIV/0! |  | 100% | #DIV/0!
Item | 10 Year Simple Payback, Average Savings
| Contractor Intensive (Le Conte ECM Basis) |  |  | Non-Contractor Intensive (Le Conte MBCx Basis)
| % of Total | $ | $/sq.ft. | % of Total | $ | $/sq.ft.
Project Technical Support
FDE Scoping | 2% | #DIV/0! | #DIV/0! | 9% | #DIV/0! | #DIV/0!
FDE Implementation | 24% | #DIV/0! | #DIV/0! | 29% | #DIV/0! | #DIV/0!
FDE TOTAL | 26% | #DIV/0! | #DIV/0! | 38% | #DIV/0! | #DIV/0!
Capital Projects | 3% | #DIV/0! | #DIV/0! | 12% | #DIV/0! | #DIV/0!
Physical Plant | 1% | #DIV/0! | #DIV/0! | 1% | #DIV/0! | #DIV/0!
TOTAL - Project Technical Support | 30% | #DIV/0! | #DIV/0! | 51% | #DIV/0! | #DIV/0!
Metering | 10% | #DIV/0! | #DIV/0! | 10% | #DIV/0! | #DIV/0!
Construction/Contractors | 58% | #DIV/0! | #DIV/0! | 34% | #DIV/0! | #DIV/0!
Contingency | 2% | #DIV/0! | #DIV/0! | 5% | #DIV/0! | #DIV/0!
TOTAL | 100% | #DIV/0! | #DIV/0! | 100% | #DIV/0! | #DIV/0!
Check | 100% | #DIV/0! |  | 100% | #DIV/0!

## Throttled Valves
Rough estimate of the throttled valve savings potential