## Slide 1: EBCx Workshop Series 18
Session 1
David Sellers, Facility Dynamics Engineering
Senior Engineer

## Slide 2: Are Your Ready to Use SketchUp
https://tinyurl.com/EBCxWS0101SketchUpReady

## Slide 3: Self Study Goals

## Slide 4: What You Should be Doing
Identify a Project Building
Begin to fill out the building information form Ryan will provide
Benchmark the building
  EnergyStar
  DOE Building Performance Database
Start a Utility Consumption Analysis
Make a site visit to scope it and start a findings list

## Slide 5: Steps for Your Self-Study Effort
Collect your merit badges
https://tinyurl.com/SSBenchmarkUCAScoping
https://tinyurl.com/SSLoadsAndPsych
https://tinyurl.com/SSSystemDgmIntro

## Slide 6: Next Steps for Your Self-Study Effort
Reach Out to Ryan if You Have Questions or Need Some Help
r2s2@pge.com

## Slide 7: Navigating In SketchUp

## Slide 10: The Technical Guide

## Slide 11: An EBCx Resource
https://tinyurl.com/EBCxGuideAndChecklist

## Slide 12: Situational Awareness
A Psych Chart Refresher

## Slide 13: A Psych Chart Refresher
Constant Dry Bulb
Constant Dew Point
Constant Humidity Ratio
Constant SHR
Constant Wet Bulb
Constant RH
Constant Enthalpy
Identify the different lines on a psych chart
Constant dry bulb
Constant wet bulb
Constant dew point
Constant humidity ratio
Constant relative humidity
Specific heat ratio

## Slide 14
Constant Dry Bulb
Constant Dew Point
Constant Humidity Ratio
Constant SHR
Constant Wet Bulb
Constant RH
Constant Enthalpy

## Slide 16
Constant Dry Bulb
Constant Dew Point
Constant Humidity Ratio
Constant SHR
Constant Wet Bulb
Constant RH
Constant Enthalpy

## Slide 17: Situational Awareness
The Ball Room Design Conditions

## Slide 18: Current Conditions

## Slide 19: Current Conditions
Foggy
Furnace running at home when you left
Low 50’s °F through early afternoon, then clearing and sunny with a high of 68-70°F anticipated
Hotel at 84% occupancy
Major conference happening
  Main ball room in use
  Meeting rooms and Junior Ball Room in use
  Spaces under control at design target of 72°F/50% RH
  Ballroom MOA settings recently verified

## Slide 20: Ball Room Design Conditions
Plot the design point on the chart
75°F
50% RH
Constant Dew Point

## Slide 21: Ball Room Design Conditions
Plot the design point on the chart
75°F
75°F
50% RH
Constant Dew Point

## Slide 22: Ball Room Design Conditions
Plot the design point on the chart
75°F
50% RH
75°F
50% RH
Constant Dew Point
Ball Room Design Condition

## Slide 23: Ball Room Design Conditions
Plot the design point on the chart
75°F
50% RH
Read other parameters
75°F
50% RH
Dew Point = 55.1°F
Ball Room Design Condition

## Slide 24: Situational Awareness
Break Out Session

## Slide 25: How to Draw a Straight Line in PowerPoint

## Slide 26: How to Draw a Curved Line in PowerPoint

## Slide 27: Given
Outdoor temperature = 52.2°F
Foggy
The Ball Room design condition target
AHUs with integrated economizer cycles
Should the economizer equipped AHUs be on minimum outdoor air?
Ball Room Design Condition

## Slide 29: Given
Outdoor temperature = 52.2°F
Foggy
The Ball Room design condition target
AHUs with integrated economizer cycles
Should the economizer equipped AHUs be on minimum outdoor air?
No because the OA enthalpy is lower than the Ball Room Enthalpy
Ball Room Design Condition
Ball Room h = 28.1 Btu/lb
52.2°F
OA h = 21.6 Btu/lb
Fog (100% RH)

## Slide 30: Facilitating Your Analysis
A free electronic psych chart
https://tinyurl.com/FreePsychChart

## Slide 31: Facilitating Your Analysis
A free electronic psych chart
https://tinyurl.com/FreePsychChart

## Slide 32: Facilitating Your Analysis
A free electronic psych chart
https://tinyurl.com/FreePsychChart

## Slide 33: Facilitating Your Analysis
A free electronic psych chart
https://tinyurl.com/FreePsychChart

## Slide 34: No Pro Version? No Problem! https://tinyurl.com/NOWData

## Slide 35: Finding Those Days https://tinyurl.com/NOWData

## Slide 36: Another Climate Data Resource https://tinyurl.com/TMIAboutTMY

## Slide 37: Doing Math with Psychrometrics
KW Engineering’s Get Psyched Excel Plug-in
https://tinyurl.com/kWEngineeringGetPsyched

## Slide 38: Situational Awareness
Break Out Session

## Slide 39: Given:
Information so far
Chilled water plant equipment schedule
A bit more information about the Hijend Hotel:
  Occupancy runs 80-95%
  Conference facility
What outdoor design cooling conditions were used by the design team?
On the day in question, would you anticipate a large load on the CWH plant and why or why not?

## Slide 41: Given:
Information so far
Chilled water plant equipment schedule
A bit more information about the Hijend Hotel:
  Occupancy runs 80-95%
  Conference facility
What outdoor design cooling conditions were used by the design team?
On the day in question, would you anticipate a large load on the CWH plant and why or why not?

## Slide 42: Given:
What outdoor design cooling conditions were used by the design team?
Cooling design conditions = 90.3tdb/67.6twb Based on 100% OA AHU entering air condition
On the day in question, would you anticipate a large load on the CWH plant and why or why not?

## Slide 43: Given:
What outdoor design cooling conditions were used by the design team?
Cooling design conditions = 90.3tdb/67.6twb Based on 100% OA AHU entering air condition
On the day in question, would you anticipate a large load on the CWH plant and why or why not?
Very little load because the OAT is at or below the design AHU Leaving Air Temperatures (LATs). And the OAT is also below the balance point for a perimeter space

## Slide 44: Getting Ready for the Field

## Slide 45: We Already Have Some Clues
Utility data insights based on the EUI and average daily consumption patterns
Building documents
  Provide insights regarding the building and equipment
  Allow preliminary system diagrams to be developed
Operating conditions on the day of our visit frame up expectations

## Slide 46: The EUI Relationship
The EUI relationship

## Slide 47: Adding Things Up

## Slide 48: Adding Things Up

## Slide 49: Projecting Savings

## Slide 50: Projecting Savings

## Slide 53: Think About It It Will Come Up as We Work With the Hijend Hotel

## Slide 54: Start Your Findings List the Day You Start Your Project
https://tinyurl.com/EBCxCostBenefitSpreadsheet

## Slide 55: A (Potentially) Informative Relationship
This relationship tells us that the power used by a pump is directly related to the flow and head it produces and inversely related to the pump, motor and drive system efficiency

## Slide 56: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time

## Slide 57: Power vs. Energy
Power
Instantaneous rate of energy use
Thermal energy is similar
Energy
Power used over a period of time

## Slide 58: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time
Can be established by a test
Variations in flow and head will shift the operating point and cause variations in power
Shifting the operating point can cause pump efficiency to vary, also affecting power
Variations in power will cause variations in motor and drive efficiency

## Slide 59: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time
For a constant flow system:
Nothing varies
Only one test point is required

## Slide 60: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time
For a variable flow system:
Everything can vary
Multiple test points are required

## Slide 61: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time
For a variable flow system:
Establishing the load or flow profile for your energy calculations is critical

## Slide 62: Establishing Load and Flow Profiles
Calculated
Potentially time consuming
May require complex mathematics or software
Only as good as the assumptions
Measured
No assumptions!
  Reflects the current state of affairs
May require complex mathematics or software
  But typically, you can handle it with Excel
Requires some time to establish
  Using regressions can compress the timeline
  Need to start gathering data early
Start thinking about it while you are scoping and look for ways you could do it

## Slide 63: Pumps are Common EBCx Targets
The Hijend Hotel chilled water plant seems to have a number of them
Here ‘s a question for you https://tinyurl.com/EBCxWS0102PumpOpt

## Slide 64: Pumps are Common EBCx Targets
The Hijend Hotel chilled water plant seems to have a number of them
Here ‘s a question for you https://tinyurl.com/EBCxWS0102PumpOpt

## Slide 65: Assessing the Plant Load Condition
Break Out Session

## Slide 66: Assessing the Plant Load Condition
Let’s get oriented

## Slide 67: Given:
The central plant model
The drawings you have for the plant
The work we have done up to this point

## Slide 68: Assignment:
Estimate the current load condition on the central plant
Look for ways that you could develop a load profile
  There could be more than one
  Some will be better than others
  What are the pro’s and con’s for your list?

## Slide 69: Scoping the Ball Room AHU
Break Out Session

## Slide 70: Scoping the Ball Room AHU
The Ball Room AHU is one of the components of the current load on the central plant

## Slide 71: Given:
The Ball Room AHU model
Previous observations

## Slide 72: Assignment:
Scope the Ball Room AHU and expand the findings list
Are you finding things that may be contributors to the load condition you observed at the central plant?
If so, why?