## Slide 1: EBCx Workshop Series 18
Session 2
David Sellers, Facility Dynamics Engineering
Senior Engineer

## Slide 2: Self Study Goals

## Slide 3: What You Should be Doing
Identify a Project Building
Begin to fill out the building information form Ryan will provide
Benchmark the building
  EnergyStar
  DOE Building Performance Database
Start a Utility Consumption Analysis
Make a site visit to scope it and start a findings list

## Slide 4: Steps for Your Self-Study Effort
Collect your merit badges
https://tinyurl.com/SSBenchmarkUCAScoping
https://tinyurl.com/SSLoadsAndPsych
https://tinyurl.com/SSSystemDgmIntro

## Slide 5: Steps for Your Self-Study Effort
Continue to Develop your System Diagram Skills
Developing the Hijend Hotel CHW Distribution Loop Diagram
https://tinyurl.com/HijendDistLoop
Add the Evaporator Loop to the Diagram
https://tinyurl.com/HijendEvapLoopFlyThru
Field Verify Joe DeNugy’s Central Plant Diagram
https://tinyurl.com/HijendCHWFieldVerify

## Slide 6: Next Steps for Your Self-Study Effort
Reach Out to Ryan if You Have Questions or Need Some Help
r2s2@pge.com

## Slide 7: Situational Awareness
A Psych Chart Refresher

## Slide 8: A Psych Chart Refresher
Constant Dry Bulb
Constant Dew Point
Constant Humidity Ratio
Constant SHR
Constant Wet Bulb
Constant RH
Constant Enthalpy
Identify the different lines on a psych chart
Constant dry bulb
Constant wet bulb
Constant dew point
Constant humidity ratio
Constant relative humidity
Specific heat ratio

## Slide 9
Constant Dry Bulb
Constant Dew Point
Constant Humidity Ratio
Constant SHR
Constant Wet Bulb
Constant RH
Constant Enthalpy

## Slide 10: Let’s Go to the Breakout Rooms

## Slide 11
Constant Dry Bulb
Constant Dew Point
Constant Humidity Ratio
Constant SHR
Constant Wet Bulb
Constant RH
Constant Enthalpy

## Slide 12: Situational Awareness
The Ball Room Design Conditions

## Slide 13: Current Conditions

## Slide 14: Current Conditions
Foggy
Furnace running at home when you left
Low 50’s °F through early afternoon, then clearing and sunny with a high of 68-70°F anticipated
Let’s see what you have learned
https://tinyurl.com/EBCxWS0201SitAware
Hotel at 84% occupancy
Major conference happening
  Main ball room in use
  Meeting rooms and Junior Ball Room in use
  Spaces under control at design target of 72°F/50% RH
  Ballroom MOA settings recently verified

## Slide 16: Getting Ready for the Field

## Slide 17: We Already Have Some Clues
Utility data insights based on the EUI and average daily consumption patterns
Building documents
  Provide insights regarding the building and equipment
  Allow preliminary system diagrams to be developed
Operating conditions on the day of our visit frame up expectations

## Slide 18: The EUI Relationship
The EUI relationship

## Slide 19: Adding Things Up

## Slide 20: Adding Things Up

## Slide 21: Projecting Savings

## Slide 22: Projecting Savings

## Slide 25: Think About It It Will Come Up as We Work With the Hijend Hotel

## Slide 26: Start Your Findings List the Day You Start Your Project
https://tinyurl.com/EBCxCostBenefitSpreadsheet

## Slide 27: A (Potentially) Informative Relationship
This relationship tells us that the power used by a pump is directly related to the flow and head it produces and inversely related to the pump, motor and drive system efficiency

## Slide 28: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time

## Slide 29: Power vs. Energy
Power
Instantaneous rate of energy use
Thermal energy is similar
Energy
Power used over a period of time

## Slide 30: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time
Can be established by a test
Variations in flow and head will shift the operating point and cause variations in power
Shifting the operating point can cause pump efficiency to vary, also affecting power
Variations in power will cause variations in motor and drive efficiency

## Slide 31: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time
For a constant flow system:
Nothing varies
Only one test point is required

## Slide 32: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time
For a variable flow system:
Everything can vary
Multiple test points are required

## Slide 33: Power vs. Energy
Power
Instantaneous rate of energy use
Energy
Power used over a period of time
For a variable flow system:
Establishing the load or flow profile for your energy calculations is critical

## Slide 34: Establishing Load and Flow Profiles
Calculated
Potentially time consuming
May require complex mathematics or software
Only as good as the assumptions
Measured
No assumptions!
  Reflects the current state of affairs
May require complex mathematics or software
  But typically, you can handle it with Excel
Requires some time to establish
  Using regressions can compress the timeline
  Need to start gathering data early
Start thinking about it while you are scoping and look for ways you could do it

## Slide 35: Pumps are Common EBCx Targets
The Hijend Hotel chilled water plant seems to have a number of them
Here ‘s a question for you https://tinyurl.com/EBCxWS0102PumpOpt

## Slide 36: Pumps are Common EBCx Targets
The Hijend Hotel chilled water plant seems to have a number of them
Here ‘s a question for you https://tinyurl.com/EBCxWS0102PumpOpt

## Slide 37: Assessing the Plant Load Condition
Break Out Session

## Slide 38: Assessing the Plant Load Condition
Let’s get oriented

## Slide 39: Given:
The central plant model
The drawings you have for the plant
The work we have done up to this point

## Slide 40: Assignment:
Estimate the current load condition on the central plant
Look for ways that you could develop a load profile
  There could be more than one
  Some will be better than others
  What are the pro’s and con’s for your list?

## Slide 41: Let’s Go to the Breakout Rooms

## Slide 42: Scoping the Ball Room AHU
Break Out Session

## Slide 43: Scoping the Ball Room AHU
The Ball Room AHU is one of the components of the current load on the central plant

## Slide 44: Scoping the Ball Room AHU
Let’s Get Oriented

## Slide 45: Given:
The Ball Room AHU model
The documents you have for the equipment room and ball room
Previous observations

## Slide 46: Assignment:
Scope the Ball Room AHU and expand the findings list
Are you finding things that may be contributors to the load condition you observed at the central plant?
If so, why?

## Slide 47: Let’s Go to the Breakout Rooms

## Slide 48: An HVAC Relationship and Few Handy Rules of Thumb for Assessing an Economizer in the Field

## Slide 49: An HVAC Relationship and Few Handy Rules of Thumb for Assessing an Economizer in the Field

## Slide 50: An HVAC Relationship and Few Handy Rules of Thumb for Assessing an Economizer in the Field

## Slide 51: An HVAC Relationship and Few Handy Rules of Thumb for Assessing an Economizer in the Field

## Slide 52: An HVAC Relationship and Few Handy Rules of Thumb for Assessing an Economizer in the Field

## Slide 53: Given:
The Ball Room AHU Economizer (Scenes 10 and 11 will be handy)
The documents you have for the equipment room and ball room
The relationships we just discussed

## Slide 54: Assignment
Evaluate the Ball Room AHU Economizer dampers
Do you think the dampers will have a linear characteristic
Do you think mixing will be thorough?
What are some of the implications of your observations?

## Slide 55: Let’s Go to the Breakout Rooms

## Slide 56: Developing a System Diagram in the Field

## Slide 58: The Distribution Loop

## Slide 59: Given:
The distribution loop sketch
The Hijend Hotel chilled water plant model

## Slide 60: Assignment:
Add the evaporator loops to the sketch (hint: they will plug in between points C and D)

## Slide 61: Let’s Go to the Breakout Rooms

## Slide 62: A System Diagram Development “Plan B”
Develop a first draft diagram from the project documents
Field verify it

## Slide 63: The Simplified Design Intent System Diagram
Ch2
Pm
Ch1
Pm
Pm
Pm
VF1
AHU8
AHU9
AHU10
AHU1
AHU7
South FC Riser 1A
South FC Riser 8A
North FC Riser 8D
North FC Riser 1D
AHU5
AHU6
AHU2
AHU3
AHU4
A
B
C
D
MATCH LINE
See Below
A
B
C
D
MATCH LINE
See Above
See Sheet 11
See Sheets 7 - 10
See Sheets 3 - 6
See Sheet 2
See Sheet 1

## Slide 64: The Detailed Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 1
Fixed Spd
SD
TDV
Chiller 2
VFD & HG
SD
TDV
SD
TDV
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1
Developed from the mechanical drawings and submittals
Needs to be field verified

## Slide 65: The Detailed Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 1
Fixed Spd
SD
TDV
Chiller 2
VFD & HG
SD
TDV
SD
TDV
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1

## Slide 66
Match Line – See Sheet 1
A
B
Match Line – See Sheet 3
C
D
73.7 gpm from 42.0°F to 54°F, 9.3 ft.w.c. Δ p, 36.9 tons
157.2 gpm from 42.0°F to 54°F, 9.6 ft.w.c. Δ p, 78.6 tons
43.9 gpm from 42.0°F to 54°F, 7.8 ft.w.c. Δ p, 21.9 tons; bypass balanced for 5 gpm in full bypass.
AHU8 Cafe
AHU9 Rest/Lng
AHU10 Kitchen
141 gpm from 42.0°F to 54°F, 8.6 ft.w.c. Δ p, 42.2 tons
57.9 gpm from 42.0°F to 54°F, 3.1 ft.w.c. Δ p, 29 tons
AHU1 Admin/Lby
AHU7 Laundry
Hijend Hotel CHW System Diagram
Sheet 2

## Slide 67
Match Line – See Sheet 2
C
D
1st Floor (Typical through Floor 23)
Fan Coil Riser 1.5 A, North Face
62 gpm at 42°EWT, LWT varies, 19.1 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
West FCU
24th Floor
West FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 2.5 A, North Face
125.4 gpm at 42°EWT, LWT varies, 34.9 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 4
E
H
G
F
Hijend Hotel CHW System Diagram
Sheet 3

## Slide 68
Match Line – See Sheet 3
1st Floor (Typical through Floor 24)
Fan Coil Riser 3.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 4.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 5
I
L
K
J
E
H
G
F
Hijend Hotel CHW System Diagram
Sheet 4

## Slide 69
Match Line – See Sheet 4
1st Floor (Typical through Floor 24)
Fan Coil Riser 5.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; ; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 6.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 6
M
P
O
N
I
L
K
J
Hijend Hotel CHW System Diagram
Sheet 5

## Slide 70
Match Line – See Sheet 5
1st Floor (Typical through Floor 24)
Fan Coil Riser 7.5 A, North Face
125.4 gpm at 42°EWT, LWT varies, 34.9 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
1st Floor (Typical through Floor 23)
Fan Coil Riser 8.5 A, North Face
121.5 gpm at 42°EWT, LWT varies, 35.5 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
East FCU
Match Line – See Sheet 7
Q
T
S
R
M
P
O
N
Hijend Hotel CHW System Diagram
Sheet 6

## Slide 71
Match Line – See Sheet 6
1st Floor (Typical through Floor 23)
Fan Coil Riser 8.5 D, South Face
90.6 gpm at 42°EWT, LWT varies, 30.6 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 7.5 D, South Face
187.6 gpm at 42°EWT, LWT varies, 63.4 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 8
U
X
W
V
Q
T
S
R
Hijend Hotel CHW System Diagram
Sheet 7

## Slide 72
Match Line – See Sheet 7
1st Floor (Typical through Floor 24)
Fan Coil Riser 6.5 D, South Face
189.5 gpm at 42°EWT, LWT varies, 64.0 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 5.5 D, South Face
94.7 gpm at 42°EWT, LWT varies, 32 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
25th Floor
East FCU
Match Line – See Sheet 9
Y
B
A
Z
U
X
W
V
Hijend Hotel CHW System Diagram
Sheet 8

## Slide 73
Match Line – See Sheet 8
1st Floor (Typical through Floor 24)
Fan Coil Riser 4.5 D, South Face
189.5 gpm at 42°EWT, LWT varies, 64.0 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 10
Y
B
A
Z
U
X
W
V
1st Floor (Typical through Floor 24)
Fan Coil Riser 3.5 D, South Face
185.4 gpm at 42°EWT, LWT varies, 62.6 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
East FCU
Hijend Hotel CHW System Diagram
Sheet 9

## Slide 74
Fan Coil Riser 1.5 D, South Face
467.4 gpm at 42°EWT, LWT varies, 218.3 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
Match Line – See Sheet 9
1st Floor (Typical through Floor 23)
Fan Coil Riser 2.5 D, South Face
181.2 gpm at 42°EWT, LWT varies, 61.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
East FCU
Match Line – See Sheet 11
Y
Z
U
X
W
V
1st Floor
West FCU (Typical through 24th floor)
25th Floor
West FCU
186.3 gpm from 42.0°F to 54°F, 6.9 ft.w.c. Δ p, 91.2 tons (Typical of each MAU)
AHU5 Corr. MAU
AHU6 Corr.MAU
Roof Level
Hijend Hotel CHW System Diagram
Sheet 10

## Slide 75
Match Line – See Sheet 10
Y
Z
88.7 gpm from 42.0°F to 54°F, 9.2 ft.w.c. Δ p, 44.3 tons
120.1 gpm from 42.0°F to 54°F, 9.1 ft.w.c. Δ p, 60.1 tons; bypass balanced for 5 gpm in full bypass.
148.7 gpm from 42.0°F to 54°F, 11 ft.w.c. Δ p, 74.4 tons
AHU4 Mtg. Rooms
AHU3 Jr. Ball Room
AHU2 Ball Room
Hijend Hotel CHW System Diagram
Sheet 11

## Slide 76: Fan Coil Unit Riser Schedule

## Slide 77: Cooling Coil Schedule

## Slide 78: System Volume Projection

## Slide 79: Given:
The “Plan B” concept
The Hijend Hotel chilled water plant model
Joe DeNuguy’s system diagram developed from the project documents before going on site

## Slide 80: Assignment:
Field verify the central plant portion of Joe DeNuguy’s system diagram
Was the system installed as intended based on the project documents?

## Slide 81: Let’s Go to the Breakout Rooms