## Slide 1: Field Verifying a Chilled Water System Diagram

## Slide 2: Field Verifying a System Diagram (Continued)
The slide that follows contains the central plant portion of a system diagram that Joe DeNuguy developed for the Hijend Hotel based on the project documents he was given. Now it needs to be field verified and that is where you come in.
Take Joe’s drawing along with the screenshots from the plant that follow it and see if what he captured from the documents matches what was actually installed in the plant. You can edit the PowerPoint slide to show any differences, either directly in the slide or by printing out a copy and marking it up as needed.
This link/QR code will take you to a web page where you can download copies of the central plant portion of the design intent system diagram as a PowerPoint slide or .pdf file in white or black background to work with if you prefer.
https://tinyurl.com/HijendCHWDI
The resources provided at this link/QR code may also be helpful (video fly-thru and SketchUp model)
https://tinyurl.com/HijendEvapLoop

## Slide 3: Field Verifying a System Diagram (Continued)
Once you have finished your verification process, the link/QR code below will take you to a MS Form based quiz where the correct answer is revealed. Then, you are given a few questions to answer that will reveal how the field verified diagram can be applied to understand how the system works and reveal potential opportunities associated with any differences that might exist from the design intent configuration.
https://tinyurl.com/SystemDgmFieldVerifySelfStudy

## Slide 4: The Detailed Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 1
Fixed Spd
SD
TDV
Chiller 2
VFD & HG
SD
TDV
SD
TDV
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1
Developed from the mechanical drawings and submittals
Needs to be field verified

## Slide 28: Complete Design Intent System Diagram
The slides that follow illustrate the complete design intent system diagram for those who are interested. You don’t really need them to do the exercise.

## Slide 29: Field Verifying a Chilled Water System Diagram

## Slide 30: Field Verifying a Chilled Water System

## Slide 31: Field Verifying a Chilled Water System

## Slide 32: The Simplified System Diagram
Ch2
Pm
Ch1
Pm
Pm
Pm
VF1
AHU8
AHU9
AHU10
AHU1
AHU7
South FC Riser 1A
South FC Riser 8A
North FC Riser 8D
North FC Riser 1D
AHU5
AHU6
AHU2
AHU3
AHU4
A
B
C
D
MATCH LINE
See Below
A
B
C
D
MATCH LINE
See Above
See Sheet 11
See Sheets 7 - 10
See Sheets 3 - 6
See Sheet 2
See Sheet 1

## Slide 33: The Detailed Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 1
Fixed Spd
SD
TDV
Chiller 2
VFD & HG
SD
TDV
SD
TDV
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1
Developed from the mechanical drawings and submittals
Needs to be field verified

## Slide 34
Match Line – See Sheet 1
A
B
Match Line – See Sheet 3
C
D
73.7 gpm from 42.0°F to 54°F, 9.3 ft.w.c. Δ p, 36.9 tons
157.2 gpm from 42.0°F to 54°F, 9.6 ft.w.c. Δ p, 78.6 tons
43.9 gpm from 42.0°F to 54°F, 7.8 ft.w.c. Δ p, 21.9 tons; bypass balanced for 5 gpm in full bypass.
AHU8 Cafe
AHU9 Rest/Lng
AHU10 Kitchen
141 gpm from 42.0°F to 54°F, 8.6 ft.w.c. Δ p, 42.2 tons
57.9 gpm from 42.0°F to 54°F, 3.1 ft.w.c. Δ p, 29 tons
AHU1 Admin/Lby
AHU7 Laundry
Hijend Hotel CHW System Diagram
Sheet 2

## Slide 35
Match Line – See Sheet 2
C
D
1st Floor (Typical through Floor 23)
Fan Coil Riser 1.5 A, North Face
62 gpm at 42°EWT, LWT varies, 19.1 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
West FCU
24th Floor
West FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 2.5 A, North Face
125.4 gpm at 42°EWT, LWT varies, 34.9 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 4
E
H
G
F
Hijend Hotel CHW System Diagram
Sheet 3

## Slide 36
Match Line – See Sheet 3
1st Floor (Typical through Floor 24)
Fan Coil Riser 3.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 4.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 5
I
L
K
J
E
H
G
F
Hijend Hotel CHW System Diagram
Sheet 4

## Slide 37
Match Line – See Sheet 4
1st Floor (Typical through Floor 24)
Fan Coil Riser 5.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; ; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 6.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 6
M
P
O
N
I
L
K
J
Hijend Hotel CHW System Diagram
Sheet 5

## Slide 38
Match Line – See Sheet 5
1st Floor (Typical through Floor 24)
Fan Coil Riser 7.5 A, North Face
125.4 gpm at 42°EWT, LWT varies, 34.9 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
1st Floor (Typical through Floor 23)
Fan Coil Riser 8.5 A, North Face
121.5 gpm at 42°EWT, LWT varies, 35.5 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
East FCU
Match Line – See Sheet 7
Q
T
S
R
M
P
O
N
Hijend Hotel CHW System Diagram
Sheet 6

## Slide 39
Match Line – See Sheet 6
1st Floor (Typical through Floor 23)
Fan Coil Riser 8.5 D, South Face
90.6 gpm at 42°EWT, LWT varies, 30.6 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 7.5 D, South Face
187.6 gpm at 42°EWT, LWT varies, 63.4 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 8
U
X
W
V
Q
T
S
R
Hijend Hotel CHW System Diagram
Sheet 7

## Slide 40
Match Line – See Sheet 7
1st Floor (Typical through Floor 24)
Fan Coil Riser 6.5 D, South Face
189.5 gpm at 42°EWT, LWT varies, 64.0 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 5.5 D, South Face
94.7 gpm at 42°EWT, LWT varies, 32 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
25th Floor
East FCU
Match Line – See Sheet 9
Y
B
A
Z
U
X
W
V
Hijend Hotel CHW System Diagram
Sheet 8

## Slide 41
Match Line – See Sheet 8
1st Floor (Typical through Floor 24)
Fan Coil Riser 4.5 D, South Face
189.5 gpm at 42°EWT, LWT varies, 64.0 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 10
Y
B
A
Z
U
X
W
V
1st Floor (Typical through Floor 24)
Fan Coil Riser 3.5 D, South Face
185.4 gpm at 42°EWT, LWT varies, 62.6 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
East FCU
Hijend Hotel CHW System Diagram
Sheet 9

## Slide 42
Fan Coil Riser 1.5 D, South Face
467.4 gpm at 42°EWT, LWT varies, 218.3 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
Match Line – See Sheet 9
1st Floor (Typical through Floor 23)
Fan Coil Riser 2.5 D, South Face
181.2 gpm at 42°EWT, LWT varies, 61.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
East FCU
Match Line – See Sheet 11
Y
Z
U
X
W
V
1st Floor
West FCU (Typical through 24th floor)
25th Floor
West FCU
186.3 gpm from 42.0°F to 54°F, 6.9 ft.w.c. Δ p, 91.2 tons (Typical of each MAU)
AHU5 Corr. MAU
AHU6 Corr.MAU
Roof Level
Hijend Hotel CHW System Diagram
Sheet 10

## Slide 43
Match Line – See Sheet 10
Y
Z
88.7 gpm from 42.0°F to 54°F, 9.2 ft.w.c. Δ p, 44.3 tons
120.1 gpm from 42.0°F to 54°F, 9.1 ft.w.c. Δ p, 60.1 tons; bypass balanced for 5 gpm in full bypass.
148.7 gpm from 42.0°F to 54°F, 11 ft.w.c. Δ p, 74.4 tons
AHU4 Mtg. Rooms
AHU3 Jr. Ball Room
AHU2 Ball Room
Hijend Hotel CHW System Diagram
Sheet 11

## Slide 44: Fan Coil Unit Riser Schedule

## Slide 45: Cooling Coil Schedule

## Slide 46: System Volume Projection