## Instructions
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2021-09-28 11:59
Project Name: | NAME?
Project Number: | NUMBER?
Engineer: | ENGINEER?
Assumptions
1 | ????
2 | ????
3 | ????
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????

## Filter Data
Filter Procurement and Disposal Costs
Note that there are some vendors that sell "clean air". In other words, their quote includes not just the filters sitting on your loading dock but also the cost of distributing them to the AHU, removing the old filters and disposing of them, cleaning and inspecting the frames and making minor repairs, and installing the new filters. It is very important to fully specify what you expect when you write an RFP for filters and to fully understand what is included in a quote you recieve in response. Enter data in this form appropriately on that basis to allow a true comparison of different options to be made.
Cells with an orange shading are the cells that need data entered to drive the model. |  |  | Database Reference (if used) - | Filter Loading Rates v4.xlsx Tab 1
Item |  | Prefilter | Final Filter | Project Specific Assumptions and Notes | Comment
| Make - | Flanders Pre Pleat 40 | Camfil Farr | User Note 1 | Note 15
| Model - | 24x24x2 High Capacity | S Flow 65/24/24/22/8
| Filter Height - inches - | 24 | 24
| Filter Width - inches - | 24 | 24
| Filter Depth - inches - | 2 | 22
| Filter Bank Cross-sectional Area - sq.ft. - | 80 | 80
| Quantity - | 20 | 20
| Filter Unit Cost - | 4.4 | 27.16 |  | Note 1
| Total Filter Cost - | 88 | 543.2
| Istallation Labor - Hours per Filter - | 0.083333 | 0.20833 |  | Note 2
| Installation Labor - Total - | 1.6667 | 4.1667
| Labor Rate - $ per hour - | 30 | 30
| Installation Labor Cost - | 50 | 125
| Waste - cubic yards - | 0.012346 | 0.1358 | I assumed a 50% compression from the value in the database | Note 12
| Disposal - Fixed Cost - | 0 | 0 |  | Note 3
| Disposal Labor - Hours - | 0 | 0 |  | Note 4
| Labor Rate - $ per hour - | 0 | 0
| Disposal Labor Cost - | 0 | 0
| Total Cost per Filter Change - | 138 | 668.2
| Filter Operating Strategy - | Time In Service | Time In Service |  | Note 11
| Filter Operating Cycle - Hours - | 17520 | 17520 |  | Notes 5, 6, 7, 8, 9
| Maximum allowable filter pressure drop, in.w.c. - | 1 | 1 |  | Note 10
| Maximum allowable fan power pressure drop, in.w.c. - | 0.48232 | 0.54485 | User Note 3
| Clean Pressure Drop Relationship - pressure drop in in.w.c. as a function of face velocity in fpm - | y = 0.0000005371x2 + 0.0002768571x + 0.0032142857 | y = 0.0000003336x2 + 0.0004309575x + 0.0000509915 | y = calculated filter pressure drop, in.w.c. based on face velocity x in fpm | Note 13
| System Design Flow Rate - cfm - | 32000 | 32000
| Clean filter pressure drop at design flow - in.w.c. - | 0.19989 | 0.22581
| Loading Profile Relationship - pressure drop increase above the clean pressure drop as a fuction of millions of cubic feet of air handled per square foot of filter bank cross section - | y = 0.0019923581x + 0.0000000000 |  | This is the curve fit derived from the field data for the combined prefilter and final filter bank. y = calculated pressure drop increase over the clean filter value. x = millions of cubic feet of air handled per square foot of filter bank cross sectional area | Note 14
Notes
1 | Cost of the filters delivered to the site.
2 | This typically includes the cost of receiving the filters, distributing them to the AHU location, removing the old filters and transporting them to the dumpster/disposal location, inspecting, cleanung and minor repairs to the filter frames as needed, and installing the new filters. For filter banks that must be verified in terms of performance (for example final filters serving a clean room), the cost of the validation testing should also be included here. Typcial allowances for labor are in the range of 5-10 minutes per filter. Things that can cause this value to be deviated from include: - Difficult access, either due to obstructions or systems located in the upper levels of a high-rise facility. - A large site with many systems distributed over it and a central recieving location from which the filters need to be dispersed. - Very high efficinecy filters that require special procedures to ensure they are sealed to their holding frames and validiation of installed performance. - Owner or municiple requirements to seperate recyclable content like metal frames from non-recyclable content prior to disposal. - Filters that have filtered hazardous air streams and require special handling and disposal practices.
3 | Includes any disposal costs like having to rent an extra dumpster and/or fees associated with disposing of filters that have been used to capture a hazardous waste like bag-in/bag-out filters on process and lab exhaust systems.
4 | Includes all labor to dispose of the filters including any labor used to recover recyclable content, which may be required by some municipalities. Some entities include this labor in the filter installation labor. But sometimes, this labor is provided by a different crew with a different labor rate and these fields allow it to be accounted for seperately.
5 | For situations where the filters are operated based on time in service, this is the number of calendar days - converted to hours - between replacement cycles. For instance, if the filters were changed every 2 years, you would enter 2 x24x365 = 17,520 hours. The model tracks calendar days and will initiate a filter change when this point in time is reached regardless of the amount of air that has been filtered and the projected filter differential pressure or the number of actual operating hours.
6 | If the filters are changed based on operating hours in service the number of operating hours should be entered. The model tracks operating hours for systems running on a schedule and will initiate a filter change when this point in time is reached regardless of the amount of air that has been filtered and the projected filter differential pressure.
7 | For systems that are operating based on the filters reaching a maximum allowable pressure drop (which will approach a best life cycle cost based approach in terms of cost/benefit), this value should be based on historicaly values. Or it can be estimated and then fine tuned by iteration based on the results of the model prediction.
8 | For systems that are being modeled to assess the benefit of a best life cycle cost based approach, this value should be set based on an initial estimate based on past experience and then fine tuned via iteration based on the model results. Generally speaking, experience to date indicates that it is not unusual for the best life cycle point to be in the 42 - 60 month range for systems that operate 12-24 hours per day in typical climates/environments.
9 | Note that it is no unusual for filter banks that are operated based on time in service or maximum allowable pressuer drop to have a different number of days associated with the change-out interval. For instance, the prefilters might be changed every 6 months and the final filters are changed every 24 months.
10 | This should be set to the manufacturers maximum recommended pressure drop or the maximum pressure drop allowed by the design documents. If this value is reached before the best life cycle cost filter change point, the model will flag it and initiate a filter change on that basis. For systems that are being operate based on hitting a maximum allowable pressure drop, the model will use this as the trigger to initiate a filter change.
11 | The selection made here sets the trigger used by the model to initiate a filter change. The difference between " Maximum Fan Pressure Capability" and "Maximum Filter Pressure Drop" is as follows: Operating for "Maximum Fan Pressure Capability" means the filters will be changed when the fan static pressure capability is not longer sufficient to deliver design flow with the filters loaded. Operating for "Maximum Filter Pressure Drop" runs the filters until the maxium allowable pressure drop recommended by the manufacturer (basically a structural limit) is reached, even if operating at this pressure drop results in a system curve that does not allow design flow to be delivered.
12 | This can be based on the filter dimensions. For rigid filters, the volume is probably just about equal to the filter dimensions unless they are compacted somehow. But for bag flexible bag filters, it is likely less and a compression factor should be applied based on engineering judgement.
13 | This can be read directly from the manufacturer's curves, but for variable flow systems it is desirable to develop a curve fit from the manufacturer's data to allow the pressure drop for a given flow to be calculated. The filter data base includes this information for the filters it contains. Note that you need to edit the formulas in the calculation spreadsheet to reflect this when you change this form to reflect a different filter.
14 | This relationship is key to the analysis. Pardoxically, it is also the most ellusive piece of information to find because it is dependent on the details of the filter design and the local environment. Most manufacturers can no provide this data because it is so location and application specific. The filter rating data can provide some insight, but it is not really a good solution because the real "dust" in a given climate will likley be significantly different from the actual "dust". Ideally, you will base this relationship on a curve fit dervied from logged data for the filters you are using and/or considering as an option. Logged data for the existing filter arrangement is not too challening to come by. Even if it is only operator logs on rounds, a reasonable fit can be established given several months of data. The challenge is in understanding how an untried, engineered filter with a low initial pressure drop and a flat loading characteristic will perform. Thus far, experience to date indicates that using the logged data for the high performance filter documented in Tab 3 of the filter data base will yield conservative results (i.e. systems that were modeled on this basis exceeded the projected filter life cycle and pressure drop vs. time curve assoicated with the filter). Note that you need to edit the formulas in the calculation spreadsheet to reflect this when you change this form to reflect a different filter.

## Calculation Notes
Back to Calculation Page
Back to Filter Data Tab
Calculation Notes
1 | "New" = The first hour operating with new filters.
"In Service " = The filters are somewhere in there operating cycle.
"Change" = The filter change trigger has been reached.
When the "Change" trigger is reached, the model assumes new filters are in place for the next hour and starts a new cycle. Obvoiusly, the change will not happen that quickly. But as long as the change happens with in a couple of weeks on either side of the change trigger (either anticipating it and having filters on hand or reacting to it in a timely fashion), the results predicted by the model should be reliable assuming good data and assumptions.
2 | This is an important driver for the model because it affects not only the fan power but also the amount of air that goes thorugh the filter and thus the amount of dust it is exposed to.
| a. | Measured values are better than design values read from project documents.
| b. | For constant volume systems, the flow rate will vary as the filters load unless there is a mechanism in place to hold the flow constant. Thus it is desirable to have a flow measurement for the system with clean filters and another for the system with dirty filters. However, there are fan curve analysis techniques that can be used to estimate where the system will move as the filters load or unload based on a single measurement and some assumptions about how the filter static will change.
| c. | For variable flow systems, this becomes more challenging. Different techniques for developing a flow profile for a system are discussed on the Affinity Laws page of FDE's commissioning resources website.
https://www.av8rdas.com/affinity-laws.html
https://www.av8rdas.com/affinity-laws.html#Profile
A future revision of this spreadsheet will include a tool that will allow you to generate a flow profile based on the system's design parameters and some assumptions about the nature of the load and how much of it is driven by internal gains vs. perimeter gains and losses.
3 | The spreadsheet calculates the fan energy used to move air through the filter using the fan power relationship below.
4 | Because the filters are pushing the fan around on its curve as they load and unload, the fan efficincy is actually changing a bit. This will be true regardless of if the system is a fixed speed system or if the system uses a VFD because each incramental change in the filter pressure drop creates a different system curve. The shallowest curve is associated with clean filters and the steepest curve is associated with dirty filters.
It would be possible to accommodate this in the spreadsheet by using a fan curve to understand how the efficiency is impacted and then doing a curve fit that correlated fan efficiency with flow rate and using a forumula in this cell to calculate the efficiency for every hour. However, if the variation is not huge, satisfactory results will likely be obtained by using an representative value such as the average, based on engineering judgement.
5 | The motor efficiency should be based on the fan brake horsepower, not just the brake horsepower associated with moving air thorugh the filters. This can be assessed using the relationship above but using the system static pressure vs. the filter static pressure drop.
This will be a more complex problem for systems with a large variation in flow and or static than for systems with fairly constant flow with the only pressure variations associated with the filter loading and unloading. Generally speaking, if the motor load varies from full load to 30-40% of full load, then assuming the motor nameplate efficiency as a constant will only introduce an error in the range of 1-1.5% due to the general shape of the typical motor efficiency curve.
If the motor operates at load conditions below 30-40% of full load, then adjusting the motor efficiency as the load varies will be more important, espeially if there are a lot of hours at the low load condition. There are a number of ways to accomplish this using look-up tables or a curve fit developed for a motor efficiency curve.
6 | For direct drive systems use an efficiency of 100% here.
7 | For systems with no variable speed drive (VSD), use 100% here. Otherwise, considerations/adjusments similar to those described for motor efficiency above should be considered.
8 | Since the calculation interval is one hour, this also represents a kWh value (kW times one hour).
9 | The formulas in these columns will need to be adjusted based on the specifics of a given installation. For instance, if the loading rate being used is for the combined filters (pre filter plus final filter) because there is not independent pressure drop data available, then the total pressure drop will be calculated from the curve fit to the data. Pre and final filter pressure drops will need to be allocated based on engineering judgement. Evidence to date suggests that allocating the total pressure drop based on the ratio of clean pressure drops is reasonable. The reason pressure drops need to be allocated to each filter element is that it allows the spreadsheet to project exceeding the maximum allowable pressure drop for either the pre or final filter. However, if the prefilter is face loading (which is common) but the final filter is depth loading, it is likely that the prefilter will load faster than the final filter, so allocating more of the pressure drop increase to it may merit consideration. Similarly, if the contaminates are items that will tend to load the prefilter (lint for instance) faster than the final filter, then allocating more of the pressure drop increase to the prefilter may merit consideration. Ultimately, having a loading profile relationship for each filter is the most desirable approach.

## User Notes
Back to Calculation Tab
Back to Filter Data Tab
User, Project Specific Notes
Use this tab to document the assumptions you make while using the spreadsheet tool for a specific project.
1 | Since I am using this copy of the tool to compare it with the results the first generation tool generated for the LeConte Annex AHU2 system, I am using the same assumptions that I used for that calculation to the extent possible. See the spreadsheet referenced below for additoinal information.
AHU 2 Filters - Existing and Summary r1.xls
2 | For this installation, we only had the pressure drop of the combined filters to work with. We believe that both filters are more incline to face load than depth load, so we allocated the total pressure drop - which was calculated based on the observed loading rate for the combined filters - based on the ratio of clean pressure drops.
3 | The total avilable fan static was estimated from the documents (see the "Misc. Calculations" tab) and then allocated based on the ratio of clean filter pressure drops.

## Shedule and Load Factor
Operating Schedule | [24 empty] | Occupancy Driven Load
The table below is referenced by the operating cost calculation to determine if the system is in operation based on time of day and day of week. Place a 1 in the cells representing the hours of each day when the system is running. The example (lower table, not used by the calculation) illustrates what a building that operated from 6 am - 6 pm on the weekdays, 8 am - noon on Saturday would look like. The top table is the one actually used by the calculation. The spreadsheet addresses holidays by referencing the holiday list tab. | [24 empty] | The table below is referenced by the operating cost calculation to determine the percentage of occupancy driven base load based on time of day and day of week. The second table uses the information in the first table to determin the % of base load occupancy for each hour of each day. In the first table, place a % in the cells for each hour and day to represent the occupancy level. The maximum percentage is automatically filled in from data in the load profile generator tab. The second table is calculated using the data in the first table and is the one referenced by the calculation. For non-base load conditions, the energy and operating cost calculation handles occupancy driven load in a different manner. The example (the lower two tables; not used by the calculation) illustrates what a building that was occupied from 6 am - 6 pm on the weekdays, 8 am - noon on Saturday, with occupancy that varied from 10% at a minimum to 100% would look like. The top two tables are the ones actually used by the calculation. The spreadsheet addresses holidays by referencing the holiday list tab.
Day of Week (1 = Sunday, 8 = Holiday) | Scheduled Operationfor Each Hour of the Day - Supports Calculation | [23 empty] | Day of Week (1 = Sunday, 8 = Holiday) | % of Full Occupancy for Each Hour of the Day - Supports the Second Table
[26 empty] | Occupancy Driven Load Factor = | [9 empty] | 75% | 100% means that there is no influence on the peak load from the envelope
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 0% | 0% | 0% | 0% | 0% | 10% | 20% | 45% | 90% | 95% | 95% | 75% | 95% | 95% | 95% | 65% | 60% | 20% | 0% | 0% | 0% | 0% | 0% | 0%
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 0% | 0% | 0% | 0% | 0% | 10% | 25% | 50% | 100% | 100% | 100% | 85% | 100% | 100% | 100% | 75% | 75% | 25% | 0% | 0% | 0% | 0% | 0% | 0%
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 0% | 0% | 0% | 0% | 0% | 10% | 25% | 50% | 100% | 100% | 100% | 85% | 100% | 100% | 100% | 75% | 75% | 25% | 0% | 0% | 0% | 0% | 0% | 0%
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 0% | 0% | 0% | 0% | 0% | 10% | 25% | 50% | 100% | 100% | 100% | 85% | 100% | 100% | 100% | 75% | 75% | 25% | 0% | 0% | 0% | 0% | 0% | 0%
6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 0% | 0% | 0% | 0% | 0% | 10% | 20% | 45% | 90% | 95% | 95% | 75% | 95% | 95% | 95% | 65% | 60% | 20% | 0% | 0% | 0% | 0% | 0% | 0%
7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 10% | 15% | 12% | 5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Day of Week (1 = Sunday, 8 = Holiday) | Scheduled Operationfor Each Hour of the Day- Example | [23 empty] | Day of Week (1 = Sunday, 8 = Holiday) | % of Occupancy Driven Base Load for Each Hour of the Day - Used by Calculation
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0% | 0% | 0% | 0% | 0% | 7.5% | 15% | 33.75% | 67.5% | 71.25% | 71.25% | 56.25% | 71.25% | 71.25% | 71.25% | 48.75% | 45% | 15% | 0% | 0% | 0% | 0% | 0% | 0%
3 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0% | 0% | 0% | 0% | 0% | 7.5% | 18.75% | 37.5% | 75% | 75% | 75% | 63.75% | 75% | 75% | 75% | 56.25% | 56.25% | 18.75% | 0% | 0% | 0% | 0% | 0% | 0%
4 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0% | 0% | 0% | 0% | 0% | 7.5% | 18.75% | 37.5% | 75% | 75% | 75% | 63.75% | 75% | 75% | 75% | 56.25% | 56.25% | 18.75% | 0% | 0% | 0% | 0% | 0% | 0%
5 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0% | 0% | 0% | 0% | 0% | 7.5% | 18.75% | 37.5% | 75% | 75% | 75% | 63.75% | 75% | 75% | 75% | 56.25% | 56.25% | 18.75% | 0% | 0% | 0% | 0% | 0% | 0%
6 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0% | 0% | 0% | 0% | 0% | 7.5% | 15% | 33.75% | 67.5% | 71.25% | 71.25% | 56.25% | 71.25% | 71.25% | 71.25% | 48.75% | 45% | 15% | 0% | 0% | 0% | 0% | 0% | 0%
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.75% | 7.5% | 11.25% | 9% | 3.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | Day of Week (1 = Sunday, 8 = Holiday) | % of Full Occupancy for Each Hour of the Day - Example - Supporting the Fourth Table
[26 empty] | % of Base Load that is Occupancy Driven = | [7 empty] | 0%
[26 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 | bar: % of Base Load that is Occupancy Driven = 1 to 0% 24
[25 empty] | 2 | 0% | 0% | 0% | 0% | 0% | 10% | 25% | 50% | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 75% | 75% | 25% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 3 | 0% | 0% | 0% | 0% | 0% | 10% | 25% | 50% | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 75% | 75% | 25% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 4 | 0% | 0% | 0% | 0% | 0% | 10% | 25% | 50% | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 75% | 75% | 25% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 5 | 0% | 0% | 0% | 0% | 0% | 10% | 25% | 50% | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 75% | 75% | 25% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 6 | 0% | 0% | 0% | 0% | 0% | 10% | 25% | 50% | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 75% | 75% | 25% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 7 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 10% | 10% | 10% | 5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | Day of Week (1 = Sunday, 8 = Holiday) | % of Base Load that is Occupancy Driven = 1: % of Occupancy Driven Base Load for Each Hour of the Day - Example
[26 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 | bar: % of Occupancy Driven Base Load for Each Hour of the Day - Example 1 to % of Occupancy Driven Base Load for Each Hour of the Day - Example 24
[25 empty] | 2 | 0% | 0% | 0% | 0% | 0% | 7.5% | 18.75% | 37.5% | 75% | 75% | 75% | 37.5% | 75% | 75% | 75% | 56.25% | 56.25% | 18.75% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 3 | 0% | 0% | 0% | 0% | 0% | 7.5% | 18.75% | 37.5% | 75% | 75% | 75% | 37.5% | 75% | 75% | 75% | 56.25% | 56.25% | 18.75% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 4 | 0% | 0% | 0% | 0% | 0% | 7.5% | 18.75% | 37.5% | 75% | 75% | 75% | 37.5% | 75% | 75% | 75% | 56.25% | 56.25% | 18.75% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 5 | 0% | 0% | 0% | 0% | 0% | 7.5% | 18.75% | 37.5% | 75% | 75% | 75% | 37.5% | 75% | 75% | 75% | 56.25% | 56.25% | 18.75% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 6 | 0% | 0% | 0% | 0% | 0% | 7.5% | 18.75% | 37.5% | 75% | 75% | 75% | 37.5% | 75% | 75% | 75% | 56.25% | 56.25% | 18.75% | 0% | 0% | 0% | 0% | 0% | 0%
[25 empty] | 7 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.75% | 7.5% | 7.5% | 7.5% | 3.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%

## Holiday List Y1
The dates below are public, federal holidays in the United States and are used by the energy calculation to determine if the cooling tower is in operation or not. The spreadsheet uses the assumed year from the energy calculation for the year here (see the yellow notes and yellow column in the "WeatherDataFile tab.) The rows labeled "Additional Holiday" can be used to add more days when the system would be offline, for instance if a facilty was closed for the week between Christmas and New Years. For the spreadsheet to see these dates, they need to be entered inside the array higlighted in yellow. That means that if you need more lines, you need to insert rows ahead of the last row, which should cause the array reference in the energy spreadsheet to shift. Inserting them after the last row will result in those dates not being seen by the energy calculation.
Year used by the energy calculation | 2022 | Linked to the date you set for the first filter change | [7 empty] | Holiday List
Excel date value for January 1, 2022 | 44562 | (Used to calculate "third Monday in January type holidays |  |  |  | Date | Month (1 = January) | Day of Month | Month and Day | Holiday | Comment | Supporting Calc | Supporting Calc
Month Data |  | (Used to calculate "third Monday in January type holidays |  |  |  | 2022-01-01 | 1 | 1 | 01/01 | New Years Day
Month | Number of Days | Day of week for the first day of the month for the referenced year |  |  |  | 2022-01-02 | 1 | 2 | 01/02 | New Years Day Holiday
|  | Day (1 is Sunday) | Excel Time Value | Formatted Excel Date and Time | First Monday of the Month | 2022-01-17 | 1 | 17 | 01/17 | Martin Luther King Day | Third Monday in January
January | 31 | 7 | 44562 | 2022-01-01 | 2022-01-03 | 2022-02-21 | 2 | 21 | 02/21 | President's Day | Third Monday in February
February | 28 | 3 | 44593 | 2022-02-01 | 2022-02-07 | 2022-04-15 | 4 | 15 | 04/15 | Emancipation Day | Weekday closest to April 16 | 2022-04-16
March | 31 | 3 | 44621 | 2022-03-01 | 2022-03-07 | 2022-05-31 | 5 | 31 | 05/31 | Memorial Day | Last Monday in May
April | 30 | 6 | 44652 | 2022-04-01 | 2022-04-04 | 2022-07-04 | 7 | 4 | 07/04 | Independence Day
May | 31 | 1 | 44682 | 2022-05-01 | 2022-05-02 | 2022-09-05 | 9 | 5 | 09/05 | Labor Day | First Monday in September
June | 30 | 4 | 44713 | 2022-06-01 | 2022-06-06 | 2022-10-10 | 10 | 10 | 10/10 | Columbus Day | Second Monday in October
July | 31 | 6 | 44743 | 2022-07-01 | 2022-07-04 | 2022-10-01 | 10 | 1 | 10/01 | Veterans Day (Observed) | Note 1
August | 31 | 2 | 44774 | 2022-08-01 | 2022-08-01 | 2022-11-24 | 11 | 24 | 11/24 | Thanksgiving | 4th Thursday in November
September | 30 | 5 | 44805 | 2022-09-01 | 2022-09-05 | 2022-11-25 | 11 | 25 | 11/25 | Day After Thanksgiving
October | 31 | 7 | 44835 | 2022-10-01 | 2022-10-03 | 2022-12-25 | 12 | 25 | 12/25 | Christmas Day
November | 30 | 3 | 44866 | 2022-11-01 | 2022-11-07 |  | 20 | 0 | 20/0 | Other Holiday
December | 31 | 5 | 44896 | 2022-12-01 | 2022-12-05 |  | 20 | 0 | 20/0 | Other Holiday
Total | 365 | [5 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
Note 1 - The spreadsheet assumes that if Veterans Day (November 11) falls on a Saturday, then it will be observed on the Friday before and if it falls on a Sunday, it will be observed the Monday after.

## Holiday List Y2
The dates below are public, federal holidays in the United States and are used by the energy calculation to determine if the cooling tower is in operation or not. The spreadsheet uses the assumed year from the energy calculation for the year here (see the yellow notes and yellow column in the "WeatherDataFile tab.) The rows labeled "Additional Holiday" can be used to add more days when the system would be offline, for instance if a facilty was closed for the week between Christmas and New Years. For the spreadsheet to see these dates, they need to be entered inside the array higlighted in yellow. That means that if you need more lines, you need to insert rows ahead of the last row, which should cause the array reference in the energy spreadsheet to shift. Inserting them after the last row will result in those dates not being seen by the energy calculation.
Year used by the energy calculation | 2023 | Created from the date the new filters were installed and the days in Holiday List Y1 | [7 empty] | Holiday List
Excel date value for January 1, 2023 | 44927 | (Used to calculate "third Monday in January type holidays |  |  |  | Date | Month (1 = January) | Day of Month | Month and Day | Holiday | Comment | Supporting Calc | Supporting Calc
Month Data |  | (Used to calculate "third Monday in January type holidays |  |  |  | 2023-01-01 | 1 | 1 | 01/01 | New Years Day
Month | Number of Days | Day of week for the first day of the month for the referenced year |  |  |  | 2023-01-02 | 1 | 2 | 01/02 | New Years Day Holiday
|  | Day (1 is Sunday) | Excel Time Value | Formatted Excel Date and Time | First Monday of the Month | 2023-01-16 | 1 | 16 | 01/16 | Martin Luther King Day | Third Monday in January
January | 31 | 1 | 44927 | 2023-01-01 | 2023-01-02 | 2023-02-20 | 2 | 20 | 02/20 | President's Day | Third Monday in February
February | 28 | 4 | 44958 | 2023-02-01 | 2023-02-06 | 2023-04-17 | 4 | 17 | 04/17 | Emancipation Day | Weekday closest to April 16 | 2023-04-16
March | 31 | 4 | 44986 | 2023-03-01 | 2023-03-06 | 2023-05-31 | 5 | 31 | 05/31 | Memorial Day | Last Monday in May
April | 30 | 7 | 45017 | 2023-04-01 | 2023-04-03 | 2023-07-04 | 7 | 4 | 07/04 | Independence Day
May | 31 | 2 | 45047 | 2023-05-01 | 2023-05-01 | 2023-09-04 | 9 | 4 | 09/04 | Labor Day | First Monday in September
June | 30 | 5 | 45078 | 2023-06-01 | 2023-06-05 | 2023-10-09 | 10 | 9 | 10/09 | Columbus Day | Second Monday in October
July | 31 | 7 | 45108 | 2023-07-01 | 2023-07-03 | 2023-10-01 | 10 | 1 | 10/01 | Veterans Day (Observed) | Note 1
August | 31 | 3 | 45139 | 2023-08-01 | 2023-08-07 | 2023-11-23 | 11 | 23 | 11/23 | Thanksgiving | 4th Thursday in November
September | 30 | 6 | 45170 | 2023-09-01 | 2023-09-04 | 2023-11-24 | 11 | 24 | 11/24 | Day After Thanksgiving
October | 31 | 1 | 45200 | 2023-10-01 | 2023-10-02 | 2023-12-25 | 12 | 25 | 12/25 | Christmas Day
November | 30 | 4 | 45231 | 2023-11-01 | 2023-11-06 |  | 20 | 0 | 20/0 | Other Holiday
December | 31 | 6 | 45261 | 2023-12-01 | 2023-12-04 |  | 20 | 0 | 20/0 | Other Holiday
Total | 365 | [5 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
Note 1 - The spreadsheet assumes that if Veterans Day (November 11) falls on a Saturday, then it will be observed on the Friday before and if it falls on a Sunday, it will be observed the Monday after.

## Holiday List Y3
The dates below are public, federal holidays in the United States and are used by the energy calculation to determine if the cooling tower is in operation or not. The spreadsheet uses the assumed year from the energy calculation for the year here (see the yellow notes and yellow column in the "WeatherDataFile tab.) The rows labeled "Additional Holiday" can be used to add more days when the system would be offline, for instance if a facilty was closed for the week between Christmas and New Years. For the spreadsheet to see these dates, they need to be entered inside the array higlighted in yellow. That means that if you need more lines, you need to insert rows ahead of the last row, which should cause the array reference in the energy spreadsheet to shift. Inserting them after the last row will result in those dates not being seen by the energy calculation.
Year used by the energy calculation | 2024 | Created from the date the new filters were installed and the days in Holiday List Y1 | [7 empty] | Holiday List
Excel date value for January 1, 2024 | 45292 | (Used to calculate "third Monday in January type holidays |  |  |  | Date | Month (1 = January) | Day of Month | Month and Day | Holiday | Comment | Supporting Calc | Supporting Calc
Month Data |  | (Used to calculate "third Monday in January type holidays |  |  |  | 2024-01-01 | 1 | 1 | 01/01 | New Years Day
Month | Number of Days | Day of week for the first day of the month for the referenced year |  |  |  | 2024-01-02 | 1 | 2 | 01/02 | New Years Day Holiday
|  | Day (1 is Sunday) | Excel Time Value | Formatted Excel Date and Time | First Monday of the Month | 2024-01-15 | 1 | 15 | 01/15 | Martin Luther King Day | Third Monday in January
January | 31 | 2 | 45292 | 2024-01-01 | 2024-01-01 | 2024-02-19 | 2 | 19 | 02/19 | President's Day | Third Monday in February
February | 29 | 5 | 45323 | 2024-02-01 | 2024-02-05 | 2024-04-16 | 4 | 16 | 04/16 | Emancipation Day | Weekday closest to April 16 | 2024-04-16
March | 31 | 6 | 45352 | 2024-03-01 | 2024-03-04 | 2024-05-31 | 5 | 31 | 05/31 | Memorial Day | Last Monday in May
April | 30 | 2 | 45383 | 2024-04-01 | 2024-04-01 | 2024-07-04 | 7 | 4 | 07/04 | Independence Day
May | 31 | 4 | 45413 | 2024-05-01 | 2024-05-06 | 2024-09-02 | 9 | 2 | 09/02 | Labor Day | First Monday in September
June | 30 | 7 | 45444 | 2024-06-01 | 2024-06-03 | 2024-10-14 | 10 | 14 | 10/14 | Columbus Day | Second Monday in October
July | 31 | 2 | 45474 | 2024-07-01 | 2024-07-01 | 2024-10-01 | 10 | 1 | 10/01 | Veterans Day (Observed) | Note 1
August | 31 | 5 | 45505 | 2024-08-01 | 2024-08-05 | 2024-11-28 | 11 | 28 | 11/28 | Thanksgiving | 4th Thursday in November
September | 30 | 1 | 45536 | 2024-09-01 | 2024-09-02 | 2024-11-29 | 11 | 29 | 11/29 | Day After Thanksgiving
October | 31 | 3 | 45566 | 2024-10-01 | 2024-10-07 | 2024-12-25 | 12 | 25 | 12/25 | Christmas Day
November | 30 | 6 | 45597 | 2024-11-01 | 2024-11-04 |  | 20 | 0 | 20/0 | Other Holiday
December | 31 | 1 | 45627 | 2024-12-01 | 2024-12-02 |  | 20 | 0 | 20/0 | Other Holiday
Total | 366 | [5 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
Note 1 - The spreadsheet assumes that if Veterans Day (November 11) falls on a Saturday, then it will be observed on the Friday before and if it falls on a Sunday, it will be observed the Monday after.

## Holiday List Y4
The dates below are public, federal holidays in the United States and are used by the energy calculation to determine if the cooling tower is in operation or not. The spreadsheet uses the assumed year from the energy calculation for the year here (see the yellow notes and yellow column in the "WeatherDataFile tab.) The rows labeled "Additional Holiday" can be used to add more days when the system would be offline, for instance if a facilty was closed for the week between Christmas and New Years. For the spreadsheet to see these dates, they need to be entered inside the array higlighted in yellow. That means that if you need more lines, you need to insert rows ahead of the last row, which should cause the array reference in the energy spreadsheet to shift. Inserting them after the last row will result in those dates not being seen by the energy calculation.
Year used by the energy calculation | 2025 | (copied from the value you used in your weather data on the WeatherDataFile tab) | [7 empty] | Holiday List
Excel date value for January 1, 2025 | 45658 | (Used to calculate "third Monday in January type holidays |  |  |  | Date | Month (1 = January) | Day of Month | Month and Day | Holiday | Comment | Supporting Calc | Supporting Calc
Month Data |  | (Used to calculate "third Monday in January type holidays |  |  |  | 2025-01-01 | 1 | 1 | 01/01 | New Years Day
Month | Number of Days | Day of week for the first day of the month for the referenced year |  |  |  | 2025-01-02 | 1 | 2 | 01/02 | New Years Day Holiday
|  | Day (1 is Sunday) | Excel Time Value | Formatted Excel Date and Time | First Monday of the Month | 2025-01-20 | 1 | 20 | 01/20 | Martin Luther King Day | Third Monday in January
January | 31 | 4 | 45658 | 2025-01-01 | 2025-01-06 | 2025-02-17 | 2 | 17 | 02/17 | President's Day | Third Monday in February
February | 28 | 7 | 45689 | 2025-02-01 | 2025-02-03 | 2025-04-16 | 4 | 16 | 04/16 | Emancipation Day | Weekday closest to April 16 | 2025-04-16
March | 31 | 7 | 45717 | 2025-03-01 | 2025-03-03 | 2025-05-31 | 5 | 31 | 05/31 | Memorial Day | Last Monday in May
April | 30 | 3 | 45748 | 2025-04-01 | 2025-04-07 | 2025-07-04 | 7 | 4 | 07/04 | Independence Day
May | 31 | 5 | 45778 | 2025-05-01 | 2025-05-05 | 2025-09-01 | 9 | 1 | 09/01 | Labor Day | First Monday in September
June | 30 | 1 | 45809 | 2025-06-01 | 2025-06-02 | 2025-10-13 | 10 | 13 | 10/13 | Columbus Day | Second Monday in October
July | 31 | 3 | 45839 | 2025-07-01 | 2025-07-07 | 2025-10-01 | 10 | 1 | 10/01 | Veterans Day (Observed) | Note 1
August | 31 | 6 | 45870 | 2025-08-01 | 2025-08-04 | 2025-11-27 | 11 | 27 | 11/27 | Thanksgiving | 4th Thursday in November
September | 30 | 2 | 45901 | 2025-09-01 | 2025-09-01 | 2025-11-28 | 11 | 28 | 11/28 | Day After Thanksgiving
October | 31 | 4 | 45931 | 2025-10-01 | 2025-10-06 | 2025-12-25 | 12 | 25 | 12/25 | Christmas Day
November | 30 | 7 | 45962 | 2025-11-01 | 2025-11-03 |  | 20 | 0 | 20/0 | Other Holiday
December | 31 | 2 | 45992 | 2025-12-01 | 2025-12-01 |  | 20 | 0 | 20/0 | Other Holiday
Total | 365 | [5 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
Note 1 - The spreadsheet assumes that if Veterans Day (November 11) falls on a Saturday, then it will be observed on the Friday before and if it falls on a Sunday, it will be observed the Monday after.

## Holiday List Y5
The dates below are public, federal holidays in the United States and are used by the energy calculation to determine if the cooling tower is in operation or not. The spreadsheet uses the assumed year from the energy calculation for the year here (see the yellow notes and yellow column in the "WeatherDataFile tab.) The rows labeled "Additional Holiday" can be used to add more days when the system would be offline, for instance if a facilty was closed for the week between Christmas and New Years. For the spreadsheet to see these dates, they need to be entered inside the array higlighted in yellow. That means that if you need more lines, you need to insert rows ahead of the last row, which should cause the array reference in the energy spreadsheet to shift. Inserting them after the last row will result in those dates not being seen by the energy calculation.
Year used by the energy calculation | 2026 | (copied from the value you used in your weather data on the WeatherDataFile tab) | [7 empty] | Holiday List
Excel date value for January 1, 2026 | 46023 | (Used to calculate "third Monday in January type holidays |  |  |  | Date | Month (1 = January) | Day of Month | Month and Day | Holiday | Comment | Supporting Calc | Supporting Calc
Month Data |  | (Used to calculate "third Monday in January type holidays |  |  |  | 2026-01-01 | 1 | 1 | 01/01 | New Years Day
Month | Number of Days | Day of week for the first day of the month for the referenced year |  |  |  | 2026-01-02 | 1 | 2 | 01/02 | New Years Day Holiday
|  | Day (1 is Sunday) | Excel Time Value | Formatted Excel Date and Time | First Monday of the Month | 2026-01-19 | 1 | 19 | 01/19 | Martin Luther King Day | Third Monday in January
January | 31 | 5 | 46023 | 2026-01-01 | 2026-01-05 | 2026-02-16 | 2 | 16 | 02/16 | President's Day | Third Monday in February
February | 28 | 1 | 46054 | 2026-02-01 | 2026-02-02 | 2026-04-16 | 4 | 16 | 04/16 | Emancipation Day | Weekday closest to April 16 | 2026-04-16
March | 31 | 1 | 46082 | 2026-03-01 | 2026-03-02 | 2026-05-31 | 5 | 31 | 05/31 | Memorial Day | Last Monday in May
April | 30 | 4 | 46113 | 2026-04-01 | 2026-04-06 | 2026-07-04 | 7 | 4 | 07/04 | Independence Day
May | 31 | 6 | 46143 | 2026-05-01 | 2026-05-04 | 2026-09-07 | 9 | 7 | 09/07 | Labor Day | First Monday in September
June | 30 | 2 | 46174 | 2026-06-01 | 2026-06-01 | 2026-10-12 | 10 | 12 | 10/12 | Columbus Day | Second Monday in October
July | 31 | 4 | 46204 | 2026-07-01 | 2026-07-06 | 2026-10-09 | 10 | 9 | 10/09 | Veterans Day (Observed) | Note 1
August | 31 | 7 | 46235 | 2026-08-01 | 2026-08-03 | 2026-11-26 | 11 | 26 | 11/26 | Thanksgiving | 4th Thursday in November
September | 30 | 3 | 46266 | 2026-09-01 | 2026-09-07 | 2026-11-27 | 11 | 27 | 11/27 | Day After Thanksgiving
October | 31 | 5 | 46296 | 2026-10-01 | 2026-10-05 | 2026-12-25 | 12 | 25 | 12/25 | Christmas Day
November | 30 | 1 | 46327 | 2026-11-01 | 2026-11-02 |  | 20 | 0 | 20/0 | Other Holiday
December | 31 | 3 | 46357 | 2026-12-01 | 2026-12-07 |  | 20 | 0 | 20/0 | Other Holiday
Total | 365 | [5 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
[7 empty] | 20 | 0 | 20/0 | Other Holiday
Note 1 - The spreadsheet assumes that if Veterans Day (November 11) falls on a Saturday, then it will be observed on the Friday before and if it falls on a Sunday, it will be observed the Monday after.

## Fan Cap for Filter Loading
Fan static available to support filter loading if the supply fan motor is allowed to fully load
Assumptions:
1 | The analysis is done for the design point system curve. Most systems will operating on a range of system curves, For constant volume systems, the range of curves is created by the filters loading. In the limit, each incramental increase in filter pressure drop creates a new system curve. How the system reacts to it will depend on if it is actively being controlled to maintain the design flow or if it is simply operating at a fixed speed that provides the design flow with the filters in a specific state. In the latter case, the filters loading will push the fan up its curve. Many balancing specs require the system be balanced with clean filters. As a result, if there is no active flow control system, the filters loading will actually shift the flow rate away from the design point. This phenomenon comes into play with Variable Air Volume systems (VAV systems) but by design, these systems typically have some mechanism in place to try to regulate the fan speed as needed to maintain the required flow. The design point typically will represent the diversified maximum flow rate and the static pressure required to deliver it.
2 |  | Design bhp - | 28.39 | hp | Source - | Contract documents
3 |  | Motor hp - | 40 | hp | Source - | Contract documents
4 |  | Design flow rate - | 32000 | cfm | Source - | Contract documents
5 |  | Design total static pressure - | 4 | in.w.c. | Source - | Contract documents
Full motor hp flow rate based on the affinity law (relationship to the right)
|  | Full load motor flow rate - | 35874.141
Full motor hp flow rate static based on the square law (relationship to right)
|  | Static with motor at full load - | 5.0272 | in.w.c.
|  | Static available to support filter loading - | 1.0272 | in.w.c.

## Support
Filter Operating Strategy Drop Down
Best Life Cycle Cost
Maximum Fan Pressure Capability
Maximum Filter Pressure Drop
Time - Calendar Days
Time - Operating Hours