## Index
Tab | Project/Source | Filter and Project Information
|  | Product | Model | Style | MERV | ASHRAE Dust Spot Efficiency | Height. inches | Width, inches | Depth, inches | Media Area, sq.ft. | Duct Holding Capactiy, grams | Filter Bank Design Face Velocity, fpm | Loading Rate, in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
1 | UC Berkeley LeConte Annex AHU 1 and 2 Original Filter Arrangement | Pre Filter
|  | Flanders Pre Pleat 40 | 24x24x2 High Capacity | Pleated | 8 | 30-35% | 24 | 24 | 2 | 17.6 | Not Published | 415.4 | 0.0019924
Final Filter
|  | Camfil Farr | S Flow 65/24/24/22/8 | Flexible Bag | 11 | 65% | 24 | 24 | 22 | 58 | Not Published | 415.4
Description and Comments
This was one of the projects where we piloted the use of the first generation of this spreadsheet. Ongoing monitoring revealed that the spreadsheet conservatively projected the improved filter life cycle and performance.
2 | Caifornia Department of General Services AHU C | Pre Filter
|  | Filtration Group Series 400 | 10389 (standard capacity) | Pleated | 8 | 25-30% | 20 | 24 | 2 | 10.6 | Not Published | 407.5188 | 0.0023415
Final Filter
|  | Filtration Group | 18365 | Flexible Bag | 12 | 65% | 20 | 24 | 22 | 46 | Not Published | 407.5188
Description and Comments
This is another one of the projects where we piloted the use of the first generation of this spreadsheet. Because we were running two similar systems in the same climate with the two different filtration options and had more exact data, the loading rates we developed on this project because our defaults for modeling a conventional approach with the best live cycle cost approach lacking any better data. More specifically, this system became the baseline for an approach using a prefilter in combination with some sort of flexible bag final filter. AHU A (Tab 3) was the system running the alternative approach.
3 | Caifornia Department of General Services AHU A | Pre Filter
No prefilter used
Final Filter
|  | Viledon | Win Air MVP 85 V Style | V Pleat | 14 | 82% | 20 | 24 | 12.5 | 85 | 3.5 | 338.8562 | 0.00045165
Description and Comments
This is another one of the projects where we piloted the use of the first generation of this spreadsheet. Because we were running two similar systems in the same climate with the two different filtration options and had more exact data, the loading rates we developed on this project because our defaults for modeling a conventional approach with the best live cycle cost approach lacking any better data. More specifically, this system became the baseline for an approach using a low initial pressure drop, high dust holding capacity engineered filter with no prefilter. AHU C (Tab 2) was the system running the conventional approach. Note that this filter delivered a higher MERV rating but at a better life cycle cost than the conventional approach
4 | UC Berkeley LeConte Annex AHU 1 and 2 Modified Filter Arrangement | Pre Filter
No Prefilter Used
Final Filter
Description and Comments
Cell Formating Template Below; Copy and paste above this line to add filter types
Pre Filter
Final Filter
Description and Comments
Pre Filter
Final Filter
Description and Comments

## Tab 1
Filter Loading Data Form | [7 empty] | Click here to go back to the index
Instructions
Enter the the data indicated in the cells with a yellow highlight, including links to appropriate data sheets. Insert lines if needed to add additional links or data. Edit the trendline equation for the filter pressure drop curve as needed to obtain a good fit, including revealing enough decimal places in the equation to ensure the curve fit check matches the trend line and filter performance data. Edit the curve fit cells higlighted in orange to reflect the trend line equation for the filter.
Data Source Description
Project Name - |  |  | UC Berkeley LeConte MRCx
Project Location - |  |  |  | Berkeley, CA, USA
System Name - |  |  | AHU 2 (AHU 1 Similar)
ASHRAE Climate Zone - |  |  |  | 3C
Project Time Frame - |  |  |  | 2009 - 2011
This data was obtained from one of the early projects where we implemented best life cycle cost filter operation and used the first generation filter life cycle cost spreadsheet to model it. This project gave me some confidence in the validity of the modeling technique because it predicted a pressure drop of about 1.26 to 1.30 in.w.c. for the existing arrangement at the 24 month change-out point and we were observing 1.25 in.w.c. in the field.
We did not have individual pressure drop data for the pre filters and final filters so this loading rate is based on the combination of the two.
Prefilter Information
|  | Description - |  | Pleated MERV8 Filter - Media: 100% Non-woven synthetic media manufactured from recycled material - Media Support: Diamond-shaped expanded metal - Pleat Design: V-Pleat - Frame: Moisture-resistant clay coated frame made with recycled material
|  | Data Sheet - |  | Flanders Pre Pleat 40 Data Sheet
|  |  |  | Quantity - | 20
|  |  |  | Filter Cost - | 4.4
|  |  |  | Labor Cost - | 2 | (Note 1)
|  |  |  | Waste - | 0.024691 | cubic yards (Note 5)
|  |  |  | Disposal Cost - | 0 | (Note 2, 3)
|  |  |  | Make - | Flanders Pre Pleat 40
|  |  |  | Model - | 24x24x2 High Capacity
|  |  |  | Height - | 24 | inches
|  |  |  | Width - | 24 | inches
|  |  |  | Depth - | 2 | inches
|  |  |  | Filter bank area - | 80 | sq.ft.
|  |  |  | System design flow rate - | 33232 | cfm (Note 4)
|  |  |  | Filter design flow face velocity - | 415.4 | fpm
|  |  |  | Efficiency - ASHRAE Dust Spot Basis - | 30-35%
|  |  |  | Efficiency - MERV Basis - | 8
|  |  |  | Media Area - | 17.6 | sq.ft.
|  |  |  | Weight - | 1.8 | lb.
|  |  |  | Dust Holding Capacity - | Not Published | grams
|  |  |  | Clean Pressure Drop | Manufacturers Data |  |  | Projections
|  |  |  | Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Velocity, fpm | cfm | in.w.c. | square law, in.w.c. | Straight Line |  | Curve Fit Check, in..w.c.
[9 empty] | in.w.c. | cfm
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0.0032143
[5 empty] | 125 | 500 | 0.05 | 0.016875 |  |  | 0.046214
[5 empty] | 250 | 1000 | 0.11 | 0.0675 |  |  | 0.106
[5 empty] | 375 | 1500 | 0.18 | 0.15188 |  |  | 0.18257
[5 empty] | 500 | 2000 | 0.27 | 0.27 | 0.27 | 2000 | 0.27592
[5 empty] | 625 | 2500 | 0.39 | 0.42188 |  |  | 0.38605
|  |  |  | Maximum rated pressure drop - | 1 | in.w.c.
Notes
| 1 | This is the labor rate Doug Potter of Air Filters North West used for this type of filter. Doug sold clean air; i.e. not just the filters, but the installed filters including clean up of the frames, removal of the old filters, installation of the new filters, and minor repairs to the frames as needed. At the time, this dollar value represented about 5 minutes per filter.
| 2 | The labor associated with removing the filters is included with the installation labor. This field is used for any extra costs like an extra dumpster rental for the old filters or labor required to break down filters that had recyclable content in them and recover it, like the metal enclosure on FAR Rigiflow Filters. Another example of a cost that would go here is the cost associated with disposing of a bag-in/bag-out type filter that takes extra labor to remove and is a hazardous waste due to what it is filtering out of the exhaust stream.
| 3 | For this project, the University staff could use a dumpster they already had available and did not require any breakdown of the filters, they just put everything in the dumpster.
| 4 | Logged data demonstrated that there was a slight variation in flow depending on if the sytem was on minimum outdoor air vs. 100% outdoor air during the economizer cycle. The flow rate used here is the typical flow rate we documented via a field test and is assumed to be constant for all hours of operation.
| 5 | This is purely based on the filter dimensions. If the filters will be compressed/compacted, it probably would be wise to apply a multiplier to this to reflect a smaller volume based on observation or engineering judgement.
Final Filter Information
|  | Description - |  | 8 Pocket Bag Filter - Media: Electrostatically enhanced synthetic biologically inert microfibers - Media Support: Lightweight scrim fabric - Pleat Design: Stiched pockets crimped to header - Frame: Galvanized steel
|  | Data Sheet - |  | Camfil Farr S-flow Flow vs. Pressure Drop
Camfil Farr S-flow Submittal
Camfil Farr Sflow Data Sheet
|  |  |  | Quantity - | 20
|  |  |  | Filter Cost - | 27.16
|  |  |  | Labor Cost - | 5 | (Note 1)
|  |  |  | Waste - | 0.2716 | cubic yards (Note 4)
|  |  |  | Disposal Cost - | 0 | (Note 2, 3)
|  |  |  | Make - | Camfil Farr
|  |  |  | Model - | S Flow 65/24/24/22/8
|  |  |  | Height - | 24 | inches
|  |  |  | Width - | 24 | inches
|  |  |  | Depth - | 22 | inches
|  |  |  | Filter bank area - | 80 | sq.ft.
|  |  |  | System design flow rate - | 33232 | cfm
|  |  |  | Filter design flow face velocity - | 415.4 | fpm
|  |  |  | Efficiency - ASHRAE Dust Spot Basis - | 65%
|  |  |  | Efficiency - MERV Basis - | 11
|  |  |  | Media Area - | 58 | sq.ft.
|  |  |  | Weight - | Not Published | lb.
|  |  |  | Dust Holding Capacity - | Not Published | grams
|  |  |  | Clean Pressure Drop Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Manufacturers Data |  |  | Projections
|  |  |  | Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Velocity, fpm | cfm | in.w.c. | square law, in.w.c. | Straight Line |  | Curve Fit Check, in..w.c.
[9 empty] | in.w.c. | cfm
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 5.0992e-05
[5 empty] | 125 | 500 |  | 0.01875 |  |  | 0.059133
[5 empty] | 250 | 1000 |  | 0.075 |  |  | 0.12864
[5 empty] | 375 | 1500 | 0.21 | 0.16875 |  |  | 0.20857
[5 empty] | 437.5 | 1750 | 0.25 | 0.22969 |  |  | 0.25245
[5 empty] | 500 | 2000 | 0.3 | 0.3 | 0.3 | 2000 | 0.29893
[5 empty] | 625 | 2500 |  | 0.46875 |  |  | 0.39971
|  |  |  | Maximum rated pressure drop - | 1 | in.w.c.
Notes
| 1 | This is the labor rate Doug Potter of Air Filters North West used for this type of filter. Doug sold clean air; i.e. not just the filters, but the installed filters including clean up of the frames, removal of the old filters, installation of the new filters, and minor repairs to the frames as needed. At the time, this dollar value represented about 15-20 minutes per filter.
| 2 | The labor associated with removing the filters is included with the installation labor. This field is used for any extra costs like an extra dumpster rental for the old filters or labor required to break down filters that had recyclable content in them and recover it, like the metal enclosure on FAR Rigiflow Filters. Another example of a cost that would go here is the cost associated with disposing of a bag-in/bag-out type filter that takes extra labor to remove and is a hazardous waste due to what it is filtering out of the exhaust stream.
| 3 | For this project, the University staff could use a dumpster they already had available and did not require any breakdown of the filters, they just put everything in the dumpster.
| 4 | This is purely based on the filter dimensions. If the filters will be compressed/compacted, it probably would be wise to apply a multiplier to this to reflect a smaller volume based on observation or engineering judgement.
Filter Loading Rate Information
Comments/Description
The filter loading information is based on field data for the final condition and number of hours in service and the manufacturers data for the clean (initial) pressure drops. There was only data avaiable for the combined pre and final filter banks so the loading rate is the composite rate for both filters. The California Department of General Services system AHU-C had very similar filters and the loading data we logged for them over a much shorter interval of time agreed very closely with the loading rate we came up with here which is based only on two data points, the projected clean pressure drop and the observed final pressure drop. Therefore we think the loading profile we document here for this filter combination is a believable and usable profile for modeling similar arrangements.
|  |  |  | System flow rate - | 33232 | cfm (Note 1)
[5 empty] | 1993920 | cubic feet per hour
[5 empty] | 1.9939 | million cubic feet per hour
|  |  |  | System type (constant or variable volume) - | Constant volume | Note 1
|  |  |  | Hours of operation between clean and dirty data points - | 17520 | Note 2
|  |  |  | Millions of cubic feet of air handled - | 34933.4784 | million cubic feet of air
[5 empty] | 436.6685 | million cubic feet of air per square foot of filter bank
Initial clean pressure drop
|  |  |  | Prefilter - | 0.18 | in.w.c. (from vendor data)
|  |  |  | Final filter - | 0.2 | in.w.c. (from vendor data)
|  |  |  | Total - | 0.38 | in.w.c. (from vendor data)
|  |  |  | Final dirty pressure drop - Total - | 1.25 | in.w.c. (Note 3)
|  |  |  | Change in pressure drop - | 0.87 | in.w.c.
[5 empty] | 0.0019924 | in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
|  |  |  | . | 0.0019924 | in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
|  | Chart Data |  | We only had two data points so this chart assumes a linear loading characteristic over time. Based on what we know, this is reasoanble up to the point where the filters saturate and the pressure drop starts to climb exponentially relative to the trend up to that point. Our visual observation indiated that the prefilters probably were approaching saturation if not at that point, but the final filters, which were the predominate part of the pressure drop from what we could tell, had not.
[5 empty] | Hours of operation | Millions of Cubic Feet of Air Handled per Square Foot of Filter Bank Cross Section (Note 4) | Change in Pressure drop, in.w.c. | Curve Fit Check
[5 empty] | 0 | 0 | 0 | 0
[5 empty] | 17520 | 436.6685 | 0.87 | 0.87
Notes
| 1 | Logged data demonstrated that there was a slight variation in flow depending on if the sytem was on minimum outdoor air vs. 100% outdoor air during the economizer cycle. The flow rate used here is the typical flow rate we documented via a field test and is assumed to be constant for all hours of operation.
| 2 | The filters were changed every 2 years nominally. Since we were at that point in the operating cycle (approximately 2 years from when the clean filters were installed) we assumed 2 years of operation, round the clock.
| 3 | Individual filter pressure drop data was not avaialble so this model is based on the total observed pressure drop for the combined filter bank (pre and final filters).
| 4 | To clarify, this number multiplied by 1,000,000 represents the total amount of air handled at the point in time associated with the data point. So, for the second data point, the system had handled 437,000,000 cubic feet of air at that point in time.

## Tab 2
Filter Loading Data Form | [7 empty] | Click here to go back to the index
Instructions
Enter the the data indicated in the cells with a yellow highlight, including links to appropriate data sheets. Insert lines if needed to add additional links or data. Edit the trendline equation for the filter pressure drop curve as needed to obtain a good fit, including revealing enough decimal places in the equation to ensure the curve fit check matches the trend line and filter performance data. Edit the curve fit cells higlighted in orange to reflect the trend line equation for the filter.
Data Source Description
Project Name - |  |  | California Department of General Services AHU A
Project Location - |  |  |  | Sacramento, CA, USA
System Name - |  |  | AHU C
ASHRAE Climate Zone - |  |  |  | 3B
Project Time Frame - |  |  |  | 2007 - 2009
This data was obtained from one of the early projects where we implemented best life cycle cost filter operation and used the first generation filter life cycle cost spreadsheet to model it. Our long term involvement as not as long as some of the other projects, in particular, the UC Berkeley projects. But, we were able to run two similar systems side by side, one with a common approach for filtration (pleated prefilters plus a flexible bag final filter) and one with the filter type we were using to optimize the filter life cycle cost (no prefilter with a high performance, high capacity rigid bag filter with a very low initial pressure drop and a very flat loading profile).
This allowed us to generate field data based loading curves for the two different approaches, which then allowed us to project how the strategy might work in other applications and facilities. We did not have logged data to work with, just spot readings taken over a period of time. However, subsequent applications of the loading curves yeilded conservative results that generall matched what we observed on those projects. Thus we feel these two loading profiles are useful for comparing the two approaches on other applications if more project, site, and filter specific data is not avaialble.
This is the data for the common approach (pleated prefilter with a bag final filter). We did not have individual pressure drop data for the pre filters and final filters so this loading rate is based on the combination of the two.
Prefilter Information
|  | Description - |  | Pleated MERV8 Filter - Media: 100% Non-woven synthetic media manufactured from recycled material - Media Support: Diamond-shaped expanded metal - Pleat Design: V-Pleat - Frame: Moisture-resistant clay coated frame made with recycled material
|  | Data Sheet - |  | Filtration Group Series 400 Data Sheet
|  |  |  | Quantity - | 48
|  |  |  | Filter Cost - | 4.4
|  |  |  | Labor Cost - | 2 | (Note 1)
|  |  |  | Waste - | 0.02 | cubic yards (Note 5)
|  |  |  | Disposal Cost - | 0 | (Note 2, 3)
|  |  |  | Make - | Filtration Group Series 400
|  |  |  | Model - | 10389 (standard capacity)
|  |  |  | Height - | 20 | inches
|  |  |  | Width - | 24 | inches
|  |  |  | Depth - | 2 | inches
|  |  |  | Filter bank area - | 160 | sq.ft.
|  |  |  | System design flow rate - | 65203 | cfm (Note 4)
|  |  |  | Filter design flow face velocity - | 407.5188 | fpm
|  |  |  | Efficiency - ASHRAE Dust Spot Basis - | 25-30%
|  |  |  | Efficiency - MERV Basis - | 8
|  |  |  | Media Area - | 10.6 | sq.ft.
|  |  |  | Weight - | Not Published | lb.
|  |  |  | Dust Holding Capacity - | Not Published | grams
|  |  |  | Clean Pressure Drop | Manufacturers Data |  |  | Projections
|  |  |  | Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Velocity, fpm | cfm | in.w.c. | square law, in.w.c. | Straight Line |  | Curve Fit Check, in..w.c.
[9 empty] | in.w.c. | cfm
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 125 | 416.6667 |  | 0.0175 |  |  | 0.04
[5 empty] | 250 | 833.3333 |  | 0.07 |  |  | 0.1
[5 empty] | 375 | 1250 | 0.18 | 0.1575 |  |  | 0.18
[5 empty] | 500 | 1666.6667 | 0.28 | 0.28 | 0.28 | 1666.6667 | 0.28
[5 empty] | 625 | 2083.3333 |  | 0.4375 |  |  | 0.4
|  |  |  | Maximum rated pressure drop - | 1 | in.w.c.
Notes
| 1 | This is the labor rate Doug Potter of Air Filters North West used for this type of filter. Doug sold clean air; i.e. not just the filters, but the installed filters including clean up of the frames, removal of the old filters, installation of the new filters, and minor repairs to the frames as needed. At the time, this dollar value represented about 5 minutes per filter.
| 2 | The labor associated with removing the filters is included with the installation labor. This field is used for any extra costs like an extra dumpster rental for the old filters or labor required to break down filters that had recyclable content in them and recover it, like the metal enclosure on FAR Rigiflow Filters. Another example of a cost that would go here is the cost associated with disposing of a bag-in/bag-out type filter that takes extra labor to remove and is a hazardous waste due to what it is filtering out of the exhaust stream.
| 3 | For this project, the DMV staff could use a dumpster they already had available and did not require any breakdown of the filters, they just put everything in the dumpster.
| 4 | This was measured by doing a traverse of the filter bank using a rotating vane anemometer taking one reading in the center of each filter.
| 5 | This is purely based on the filter dimensions. If the filters will be compressed/compacted, it probably would be wise to apply a multiplier to this to reflect a smaller volume based on observation or engineering judgement.
Final Filter Information
|  | Description - |  | 6 Pocket Bag Filter - Media: Moisture resistant ultrasonically welded synthetic - Media Support: Metal header with vertial seperators - Pleat Design: Polyproppylene fibers and backing - Frame: Galvanized steel
|  | Data Sheet - |  | Filtration Group Pocket Filter Data Sheet
Filtration Group Pocket Filter Submittal
|  |  |  | Quantity - | 48
|  |  |  | Filter Cost - | 27
|  |  |  | Labor Cost - | 5 | (Note 1)
|  |  |  | Waste - | 0.22 | cubic yards (Note 5)
|  |  |  | Disposal Cost - | 0 | (Note 2, 3)
|  |  |  | Make - | Filtration Group
|  |  |  | Model - | 18365
|  |  |  | Height - | 20 | inches
|  |  |  | Width - | 24 | inches
|  |  |  | Depth - | 22 | inches
|  |  |  | Filter bank area - | 160 | sq.ft.
|  |  |  | System design flow rate - | 65203 | cfm
|  |  |  | Filter design flow face velocity - | 407.5188 | fpm
|  |  |  | Efficiency - ASHRAE Dust Spot Basis - | 65%
|  |  |  | Efficiency - MERV Basis - | 12
|  |  |  | Media Area - | 46 | sq.ft.
|  |  |  | Weight - | Not Published | lb.
|  |  |  | Dust Holding Capacity - | Not Published | grams
|  |  |  | Clean Pressure Drop Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Manufacturers Data |  |  | Projections
|  |  |  | Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Velocity, fpm | cfm | in.w.c. | square law, in.w.c. | Straight Line |  | Curve Fit Check, in..w.c.
[9 empty] | in.w.c. | cfm
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 8.2873e-05
[5 empty] | 125 | 416.6667 |  | 0.020625 |  |  | 0.067935
[5 empty] | 250 | 833.3333 |  | 0.0825 |  |  | 0.14546
[5 empty] | 300 | 1000 | 0.18 | 0.1188 |  |  | 0.17917
[5 empty] | 400 | 1333.3333 | 0.25 | 0.2112 |  |  | 0.25124
[5 empty] | 500 | 1666.6667 | 0.33 | 0.33 | 0.33 | 1666.6667 | 0.3295
[5 empty] | 625 | 2083.3333 |  | 0.51562 |  |  | 0.43603
|  |  |  | Maximum rated pressure drop - | 1 | in.w.c.
Notes
| 1 | This is the labor rate Doug Potter of Air Filters North West used for this type of filter. Doug sold clean air; i.e. not just the filters, but the installed filters including clean up of the frames, removal of the old filters, installation of the new filters, and minor repairs to the frames as needed. At the time, this dollar value represented about 10-15 minutes per filter.
| 2 | The labor associated with removing the filters is included with the installation labor. This field is used for any extra costs like an extra dumpster rental for the old filters or labor required to break down filters that had recyclable content in them and recover it, like the metal enclosure on FAR Rigiflow Filters. Another example of a cost that would go here is the cost associated with disposing of a bag-in/bag-out type filter that takes extra labor to remove and is a hazardous waste due to what it is filtering out of the exhaust stream.
| 3 | For this project, the DGS staff could use a dumpster they already had available and did not require any breakdown of the filters, they just put everything in the dumpster.
| 4 | The submittal included test data for an 8 pocket filter and no test data for the 6 pocket filter showing how initial pressure drop varied with flow rate with a clean filter. We assumed the 6 pocket curve was parallel to the 8 pocket curve, offset by the difference between the published pressure drop at 500 fpm for both filters.
| 5 | This is purely based on the filter dimensions. If the filters will be compressed/compacted, it probably would be wise to apply a multiplier to this to reflect a smaller volume based on observation or engineering judgement.
Filter Loading Rate Information
Comments/Description
The filter loading information is based on field data for the final condition and number of hours in service and the manufacturers data for the clean (initial) pressure drops. There was only data avaiable for the combined pre and final filter banks so the loading rate is the composite rate for both filters. Therefore we think the loading profile we document here for this filter combination is a believable and usable profile for modeling similar arrangements.
|  |  |  | System flow rate - | 65203 | cfm (Note 1)
[5 empty] | 3912180 | cubic feet per hour
[5 empty] | 3.9122 | million cubic feet per hour
|  |  |  | System type (constant or variable volume) - | Constant volume
|  |  |  | Hours of operation between clean and dirty data points - | 3144 | Note 1
|  |  |  | Millions of cubic feet of air handled - | 12299.8939 | million cubic feet of air
[5 empty] | 76.8743 | million cubic feet of air per square foot of filter bank
Initial clean pressure drop
|  |  |  | Prefilter - | 0.2 | in.w.c. (from vendor data)
|  |  |  | Final filter - | 0.22 | in.w.c. (from vendor data)
|  |  |  | Total - | 0.42 | in.w.c. (from vendor data)
|  |  |  | Final dirty pressure drop - Total - | 0.6 | in.w.c. (Note 3)
|  |  |  | Change in pressure drop - | 0.18 | in.w.c.
[5 empty] | 0.0023415 | in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
[5 empty] | 0.0023415 | in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
|  | Chart Data |  | We only had two data points so this chart assumes a linear loading characteristic over time. Based on what we know, this is reasoanble up to the point where the filters saturate and the pressure drop starts to climb exponentially relative to the trend up to that point. Our visual observation indiated that the prefilters probably were approaching saturation if not at that point, but the final filters, which were the predominate part of the pressure drop from what we could tell, had not.
[5 empty] | Hours of operation | Millions of Cubic Feet of Air Handled per Square Foot of Filter Bank Cross Section (Note 3) | Change in Pressure drop, in.w.c. | Curve Fit Check
[5 empty] | 0 | 0 | 0 | 0
[5 empty] | 3144 | 76.8743 | 0.18 | 0.18
Notes
| 1 | The test was started on Sunday, October 21, 2007 and ended on Friday, February 29, 2008 and the dirty pressure drop value is the reading across both sets of filters on the end date.
| 2 | Individual filter pressure drop data was not avaialble so this model is based on the total observed pressure drop for the combined filter bank (pre and final filters).
| 3 | To clarify, this number multiplied by 1,000,000 represents the total amount of air handled at the point in time associated with the data point. So, for the second data point, the system had handled 77,000,000 cubic feet of air at that point in time.

## Tab 3
Filter Loading Data Form | [7 empty] | Click here to go back to the index
Instructions
Enter the the data indicated in the cells with a yellow highlight, including links to appropriate data sheets. Insert lines if needed to add additional links or data. Edit the trendline equation for the filter pressure drop curve as needed to obtain a good fit, including revealing enough decimal places in the equation to ensure the curve fit check matches the trend line and filter performance data. Edit the curve fit cells higlighted in orange to reflect the trend line equation for the filter.
Data Source Description
Project Name - |  |  | California Department of General Services AHU A
Project Location - |  |  |  | Sacramento, CA, USA
System Name - |  |  | AHU A
ASHRAE Climate Zone - |  |  |  | 3B
Project Time Frame - |  |  |  | 2007 - 2009
This data was obtained from one of the early projects where we implemented best life cycle cost filter operation and used the first generation filter life cycle cost spreadsheet to model it. Our long term involvement as not as long as some of the other projects, in particular, the UC Berkeley projects. But, we were able to run two similar systems side by side, one with a common approach for filtration (pleated prefilters plus a flexible bag final filter) and one with the filter type we were using to optimize the filter life cycle cost (no prefilter with a high performance, high capacity rigid bag filter with a very low initial pressure drop and a very flat loading profile).
This allowed us to generate field data based loading curves for the two different approaches, which then allowed us to project how the strategy might work in other applications and facilities. We did not have logged data to work with, just spot readings taken over a period of time. However, subsequent applications of the loading curves yeilded conservative results that generall matched what we observed on those projects. Thus we feel these two loading profiles are useful for comparing the two approaches on other applications if more project, site, and filter specific data is not avaialble.
This is the data for the common approach (pleated prefilter with a bag final filter). We did not have individual pressure drop data for the pre filters and final filters so this loading rate is based on the combination of the two.
Prefilter Information
|  | Description - |  | This system was used to demonstrate an approach were we used a filter with engineered media that provided a very low initial pressure drop, a very flat loading curve, and high dust holding capacity and ran it with out a prefilter.
|  | Data Sheet - |  | None
|  |  |  | Quantity - | 0
|  |  |  | Filter Cost - | 0
|  |  |  | Labor Cost - | 0
|  |  |  | Waste - | 0
|  |  |  | Disposal Cost - | 0
|  |  |  | Make - | No prefilter used
|  |  |  | Model - | No prefilter used
|  |  |  | Height - | No prefilter used | inches
|  |  |  | Width - | No prefilter used | inches
|  |  |  | Depth - | No prefilter used | inches
|  |  |  | Filter bank area - | No prefilter used | sq.ft.
|  |  |  | System design flow rate - | 54217 | cfm (Note 1)
|  |  |  | Filter design flow face velocity - | No prefilter used | fpm
|  |  |  | Efficiency - ASHRAE Dust Spot Basis - | No prefilter used
|  |  |  | Efficiency - MERV Basis - | No prefilter used
|  |  |  | Media Area - | No prefilter used | sq.ft.
|  |  |  | Weight - | No prefilter used | lb.
|  |  |  | Dust Holding Capacity - | No prefilter used | grams
|  |  |  | Clean Pressure Drop | Manufacturers Data |  |  | Projections
|  |  |  | Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Velocity, fpm | cfm | in.w.c. | square law, in.w.c. | Straight Line |  | Curve Fit Check, in..w.c.
[9 empty] | in.w.c. | cfm
[5 empty] | 0 | N/A | 0 | N/A | N/A | N/A | N/A
[5 empty] | 125 | N/A |  | N/A |  |  | N/A
[5 empty] | 250 | N/A |  | N/A |  |  | N/A
[5 empty] | 375 | N/A | 0 | N/A |  |  | N/A
[5 empty] | 500 | N/A | 0 | N/A | N/A | N/A | N/A
[5 empty] | 625 | N/A |  | N/A |  |  | N/A
|  |  |  | Maximum rated pressure drop - | No prefilter used | in.w.c.
Notes
| 1 | This was measured by doing a traverse of the filter bank using a rotating vane anemometer taking one reading in the center of each filter.
Final Filter Information
|  | Description - |  | Ridged V Bank V Pleat - Media: Organic, synthetic, progressively structured, thermally bonded - Media Support: Potted to frame - Frame: Plastic with media potted into the frame
|  | Data Sheet - |  | Viledon Submittal Information
|  |  |  | Quantity - | 48
|  |  |  | Filter Cost - | 93
|  |  |  | Labor Cost - | 5 | (Note 1)
|  |  |  | Waste - | 0.22 | cubic yards (Note 4)
|  |  |  | Disposal Cost - | 0 | (Note 2, 3)
|  |  |  | Make - | Viledon
|  |  |  | Model - | Win Air MVP 85 V Style
|  |  |  | Height - | 20 | inches
|  |  |  | Width - | 24 | inches
|  |  |  | Depth - | 12.5 | inches
|  |  |  | Filter bank area - | 160 | sq.ft.
|  |  |  | System design flow rate - | 54217 | cfm
|  |  |  | Filter design flow face velocity - | 338.8562 | fpm
|  |  |  | Efficiency - ASHRAE Dust Spot Basis - | 82%
|  |  |  | Efficiency - MERV Basis - | 14
|  |  |  | Media Area - | 85 | sq.ft.
|  |  |  | Weight - | 3.5 | lb.
|  |  |  | Dust Holding Capacity - | 300 | grams
|  |  |  | Clean Pressure Drop Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Manufacturers Data |  |  | Projections
|  |  |  | Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Velocity, fpm | cfm | in.w.c. | square law, in.w.c. | Straight Line |  | Curve Fit Check, in..w.c.
[9 empty] | in.w.c. | cfm
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | -0.0028571
[5 empty] | 123 | 410 | 0.07 | 0.0225 |  |  | 0.074857
[5 empty] | 246 | 820 | 0.16 | 0.09 |  |  | 0.16114
[5 empty] | 369 | 1230 | 0.26 | 0.2025 |  |  | 0.256
[5 empty] | 492 | 1640 | 0.36 | 0.36 | 0.36 | 1640 | 0.35943
[5 empty] | 615 | 2050 | 0.47 | 0.5625 |  |  | 0.47144
|  |  |  | Maximum rated pressure drop - | 1.5 | in.w.c.
Notes
| 1 | This is the labor rate Doug Potter of Air Filters North West used for this type of filter. Doug sold clean air; i.e. not just the filters, but the installed filters including clean up of the frames, removal of the old filters, installation of the new filters, and minor repairs to the frames as needed. At the time, this dollar value represented about 10-15 minutes per filter.
| 2 | The labor associated with removing the filters is included with the installation labor. This field is used for any extra costs like an extra dumpster rental for the old filters or labor required to break down filters that had recyclable content in them and recover it, like the metal enclosure on FAR Rigiflow Filters. Another example of a cost that would go here is the cost associated with disposing of a bag-in/bag-out type filter that takes extra labor to remove and is a hazardous waste due to what it is filtering out of the exhaust stream.
| 3 | For this project, the DGS staff could use a dumpster they already had available and did not require any breakdown of the filters, they just put everything in the dumpster.
| 4 | This is purely based on the filter dimensions. If the filters will be compressed/compacted, it probably would be wise to apply a multiplier to this to reflect a smaller volume based on observation or engineering judgement.
Filter Loading Rate Information
Comments/Description
The filter loading information is based on field data for the final condition and number of hours in service and the manufacturers data for the clean (initial) pressure drops. There was only data avaiable for the combined pre and final filter banks so the loading rate is the composite rate for both filters. Therefore we think the loading profile we document here for this filter combination is a believable and usable profile for modeling similar arrangements.
|  |  |  | System flow rate - | 54217 | cfm (Note 1)
[5 empty] | 3253020 | cubic feet per hour
[5 empty] | 3.253 | million cubic feet per hour
|  |  |  | System type (constant or variable volume) - | Constant volume
|  |  |  | Hours of operation between clean and dirty data points - | 2178 | Note 1
|  |  |  | Millions of cubic feet of air handled - | 7085.0776 | million cubic feet of air
[5 empty] | 44.2817 | million cubic feet of air per square foot of filter bank
Initial clean pressure drop
|  |  |  | Prefilter - | 0 | in.w.c. (None used)
|  |  |  | Final filter - | 0.18 | in.w.c. (from vendor data)
|  |  |  | Total - | 0.18 | in.w.c. (from vendor data)
|  |  |  | Final dirty pressure drop - Total - | 0.2 | in.w.c.
|  |  |  | Change in pressure drop - | 0.02 | in.w.c.
[5 empty] | 0.00045165 | in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
[5 empty] | 0.00045165 | in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
|  | Chart Data |  | We only had two data points so this chart assumes a linear loading characteristic over time. Based on what we know, this is reasoanble up to the point where the filters saturate and the pressure drop starts to climb exponentially relative to the trend up to that point. Our visual observation indiated that the prefilters probably were approaching saturation if not at that point, but the final filters, which were the predominate part of the pressure drop from what we could tell, had not.
[5 empty] | Hours of operation | Millions of Cubic Feet of Air Handled per Square Foot of Filter Bank Cross Section (Note 3) | Change in Pressure drop, in.w.c. | Curve Fit Check
[5 empty] | 0 | 0 | 0 | 0
[5 empty] | 2178 | 44.2817 | 0.02 | 0.02
Notes
| 1 | The test was started on Sunday, October 21, 2007 and ended on Friday, February 29, 2008 and the dirty pressure drop value is the reading across both sets of filters on the end date.
| 2 | To clarify, this number multiplied by 1,000,000 represents the total amount of air handled at the point in time associated with the data point. So, for the second data point, the system had handled 44,000,000 cubic feet of air at that point in time.

## Tab 4
Filter Loading Data Form | [7 empty] | Click here to go back to the index
Instructions
Enter the the data indicated in the cells with a yellow highlight, including links to appropriate data sheets. Insert lines if needed to add additional links or data. Edit the trendline equation for the filter pressure drop curve as needed to obtain a good fit, including revealing enough decimal places in the equation to ensure the curve fit check matches the trend line and filter performance data. Edit the curve fit cells higlighted in orange to reflect the trend line equation for the filter.
Data Source Description
Project Name - |  |  | UC Berkeley LeConte MRCx
Project Location - |  |  |  | Berkeley, CA, USA
System Name - |  |  | AHU 2 (AHU 1 Similar)
ASHRAE Climate Zone - |  |  |  | 3C
Project Time Frame - |  |  |  | 2009 - 2011
This is one of the original projects where we applied the first version of this spreadsheet to predict the results of switching to a higher performance filter, eliminating the prefilter, and using a best life cycle cost based apparoch to changing the filters. The model was based on using a filter with similar performance to what we had tried at CADGS (Tab 2). The successful vendor proposed a rigid bag filter vs. the V-pleat filter that we used at CADGS, but it was depth loading and had as much or more media area and dust holding capability as the CADGS filter and a similar but lower clean initial pressure drop. Given that there was no loading profile data avaiable. we accepted the proposed filter.
The information on this tab is that filter with a loading profile similar to the CADGS filter assumed. A sepereate tab will document the performance we obserbed, which exceeded what we projected. We believe that some of that was related to the filter design itself. But some of it was related to other changes we made in the system, including implementing a schedule, zone level scheduling, and switching the operation to a quasi-single zone VAV strategy similar to Federspiel but with out using their proprietary algorithm or hardware.
Prefilter Information
|  | Description - |  | We leveraged the high dust holding capacity of the proposed filter along with its higher pressure drop capabiltiy to eliminate the prefilter in the modified operating strategy.
|  | Data Sheet - |  | None
|  |  |  | Quantity - | 0
|  |  |  | Filter Cost - | 0
|  |  |  | Labor Cost - | 0
|  |  |  | Waste - | 0
|  |  |  | Disposal Cost - | 0
|  |  |  | Make - | No prefilter used
|  |  |  | Model - | No prefilter used
|  |  |  | Height - | No prefilter used | inches
|  |  |  | Width - | No prefilter used | inches
|  |  |  | Depth - | No prefilter used | inches
|  |  |  | Filter bank area - | No prefilter used | sq.ft.
|  |  |  | System design flow rate - | 33232 | cfm (Note 1)
|  |  |  | Filter design flow face velocity - | No prefilter used | fpm
|  |  |  | Efficiency - ASHRAE Dust Spot Basis - | No prefilter used
|  |  |  | Efficiency - MERV Basis - | No prefilter used
|  |  |  | Media Area - | No prefilter used | sq.ft.
|  |  |  | Weight - | No prefilter used | lb.
|  |  |  | Dust Holding Capacity - | No prefilter used | grams
|  |  |  | Clean Pressure Drop | Manufacturers Data |  |  | Projections
|  |  |  | Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Velocity, fpm | cfm | in.w.c. | square law, in.w.c. | Straight Line |  | Curve Fit Check, in..w.c.
[9 empty] | in.w.c. | cfm
[5 empty] | 0 | N/A | 0 | N/A | N/A | N/A | N/A
[5 empty] | 125 | N/A |  | N/A |  |  | N/A
[5 empty] | 250 | N/A |  | N/A |  |  | N/A
[5 empty] | 375 | N/A | 0 | N/A |  |  | N/A
[5 empty] | 500 | N/A | 0 | N/A | N/A | N/A | N/A
[5 empty] | 625 | N/A |  | N/A |  |  | N/A
|  |  |  | Maximum rated pressure drop - | No prefilter used | in.w.c.
Notes
| 1 | Logged data demonstrated that there was a slight variation in flow depending on if the sytem was on minimum outdoor air vs. 100% outdoor air during the economizer cycle. The flow rate used here is the typical flow rate we documented via a field test and is assumed to be constant for all hours of operation.
Final Filter Information
|  | Description - |  | 8 Pocket Hybrid Media Rigid Bag Filter - Media: Hybrid blend of synthetic fibers adheared to a non-woven support backing, adhesive sealed span stich - Media Support: Mechanically secured to the frame and adjacent pockets - Frame: Galvanized 26 gauge metal header
|  | Data Sheet - |  | Filtrair PLT Data Sheet
Filtrair PLT Specification
Filtrair PLT ASHRAE Test
Filtrair PLT Submittal Drawing
Filtrair Pricing Document
|  |  |  | Quantity - | 20
|  |  |  | Filter Cost - | 124
|  |  |  | Labor Cost - | 5 | (Note 1)
|  |  |  | Waste - | 0.2963 | cubic yards (Note 4)
|  |  |  | Disposal Cost - | 0 | (Note 2, 3)
|  |  |  | Make - | Filtrair
|  |  |  | Model - | PTL 1/1
|  |  |  | Height - | 24 | inches
|  |  |  | Width - | 24 | inches
|  |  |  | Depth - | 24 | inches
|  |  |  | Filter bank area - | 80 | sq.ft.
|  |  |  | System design flow rate - | 33232 | cfm
|  |  |  | Filter design flow face velocity - | 415.4 | fpm
|  |  |  | Efficiency - ASHRAE Dust Spot Basis - | 63%
|  |  |  | Efficiency - MERV Basis - | 11
|  |  |  | Media Area - | 60.2779 | sq.ft.
|  |  |  | Weight - | 7.2753 | lb.
|  |  |  | Dust Holding Capacity - | 3000 | grams
|  |  |  | Clean Pressure Drop Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Manufacturers Data |  |  | Projections
|  |  |  | Enter manufacturer's data into the cells higlighted in yellow. Edit rows as needed to cover the velocities that the manufacturer rates the filters at. If inserting or deleting rows, do it between the rows with the red boarders to preserve the chart data references. | Velocity, fpm | cfm | in.w.c. | square law, in.w.c. | Straight Line |  | Curve Fit Check, in..w.c.
[9 empty] | in.w.c. | cfm
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | -0.0028571
[5 empty] | 123 | 492 | 0.07 | 0.0225 |  |  | 0.074857
[5 empty] | 246 | 984 | 0.16 | 0.09 |  |  | 0.16114
[5 empty] | 369 | 1476 | 0.26 | 0.2025 |  |  | 0.256
[5 empty] | 492 | 1968 | 0.36 | 0.36 | 0.36 | 1968 | 0.35943
[5 empty] | 615 | 2460 | 0.47 | 0.5625 |  |  | 0.47144
|  |  |  | Maximum rated pressure drop - | 1.5 | in.w.c.
Notes
| 1 | This is the labor rate Doug Potter of Air Filters North West used for this type of filter. Doug sold clean air; i.e. not just the filters, but the installed filters including clean up of the frames, removal of the old filters, installation of the new filters, and minor repairs to the frames as needed. At the time, this dollar value represented about 10-15 minutes per filter.
| 2 | The labor associated with removing the filters is included with the installation labor. This field is used for any extra costs like an extra dumpster rental for the old filters or labor required to break down filters that had recyclable content in them and recover it, like the metal enclosure on FAR Rigiflow Filters. Another example of a cost that would go here is the cost associated with disposing of a bag-in/bag-out type filter that takes extra labor to remove and is a hazardous waste due to what it is filtering out of the exhaust stream.
| 3 | For this project, the DGS staff could use a dumpster they already had available and did not require any breakdown of the filters, they just put everything in the dumpster.
| 4 | This is purely based on the filter dimensions. If the filters will be compressed/compacted, it probably would be wise to apply a multiplier to this to reflect a smaller volume based on observation or engineering judgement.
Filter Loading Rate Information
Comments/Description
The filter loading information is based on field data for the final condition and number of hours in service and the manufacturers data for the clean (initial) pressure drops. There was only data avaiable for the combined pre and final filter banks so the loading rate is the composite rate for both filters. Therefore we think the loading profile we document here for this filter combination is a believable and usable profile for modeling similar arrangements.
|  |  |  | System flow rate - | 54217 | cfm (Note 1)
[5 empty] | 3253020 | cubic feet per hour
[5 empty] | 3.253 | million cubic feet per hour
|  |  |  | System type (constant or variable volume) - | Constant volume
|  |  |  | Hours of operation between clean and dirty data points - | 2178 | Note 1
|  |  |  | Millions of cubic feet of air handled - | 7085.0776 | million cubic feet of air
[5 empty] | 88.5635 | million cubic feet of air per square foot of filter bank
Initial clean pressure drop
|  |  |  | Prefilter - | 0 | in.w.c. (None used)
|  |  |  | Final filter - | 0.18 | in.w.c. (from vendor data)
|  |  |  | Total - | 0.18 | in.w.c. (from vendor data)
|  |  |  | Final dirty pressure drop - Total - | 0.2 | in.w.c.
|  |  |  | Change in pressure drop - | 0.02 | in.w.c.
[5 empty] | 0.00022583 | in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
[5 empty] | 0.00022583 | in.w.c. per million cubic feet of air handled per square foot of filter bank cross section
|  | Chart Data |  | We only had two data points so this chart assumes a linear loading characteristic over time. Based on what we know, this is reasoanble up to the point where the filters saturate and the pressure drop starts to climb exponentially relative to the trend up to that point. Our visual observation indiated that the prefilters probably were approaching saturation if not at that point, but the final filters, which were the predominate part of the pressure drop from what we could tell, had not.
[5 empty] | Hours of operation | Millions of Cubic Feet of Air Handled per Square Foot of Filter Bank Cross Section (Note 3) | Change in Pressure drop, in.w.c. | Curve Fit Check
[5 empty] | 0 | 0 | 0 | 0
[5 empty] | 2178 | 88.5635 | 0.02 | 0.04
Notes
| 1 | The test was started on Sunday, October 21, 2007 and ended on Friday, February 29, 2008 and the dirty pressure drop value is the reading across both sets of filters on the end date.
| 2 | To clarify, this number multiplied by 1,000,000 represents the total amount of air handled at the point in time associated with the data point. So, for the second data point, the system had handled 44,000,000 cubic feet of air at that point in time.

## Support
Filter Style Drop-down
Extended Surface Area
Flexible Bag
Pleated
Rigid Bag
Supported Media Box
V Pleat

## CADGS DMV
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2008-04-02 07:58
Project Name: | CA DGA DMV
Project Number: | NUMBER?
Engineer: | David
Assumptions
1 | Original spreadsheet - | Filter Loading Model AHU-A v1.xls
Projected clean pressure drops based on manufacturer's rating data
AHU-C
Prefilter
Filtration Group Series 400, 2"
Velocity, fpm
|  | 375 | 500
| Rated pressure drop | 0.18 | 0.28
| Linear relationship | 0.18 | 0.24
| Square law | 0.18 | 0.32
| Average face velocity, AHU-C | 407.5208
| Projected clean pressure drop, linear interpolation | 0.19561
Final filter
Filtration Group Series 6 pocket MERV 11, 22" deep
Velocity, fpm
|  | 375 | 500 | 625
| Rated pressure drop | 0.2 | 0.25 | 0.37
| Linear relationship | 0.2 | 0.26667 | 0.33333
| Square law | 0.2 | 0.35556 | 0.55556
| Average face velocity, AHU-C | 407.5208
| Projected clean pressure drop, linear interpolation | 0.21734
| Total initial clean pressure drop, AHU-C | 0.41295
AHU-A
Freudenberg Viledon MV4 24 x 24 x 12 MERV 14
| Average face velocity, AHU-A | 338.8542
| Average cfm per filter, AHU-A | 1129.5139
| Projected clean pressure drop, linear interpolation | 0.18072
Pressure drop vs. time graph
| AHU-A operating hours per day | 10 | Normally, but it ran round the clock from the time the VFDs were installed until mid January when the controls were in place for scheduling
| Number of days AHU-A ran round the clock | 62 | Approximate, based on discussions with field staff.
| AHU-C operating hours per day | 24
| Date | Pressure drop, in.w.c. |  | Operating hours |  | Rate of Change, in.w.c. per 1,000 hours
|  | AHU-A | AHU-C | AHU-A | AHU-C | AHU-A | AHU-C
| 2007-10-21 | 0.18072 | 0.41295 | 0 | 0
| 2008-02-29 | 0.2 | 0.6 | 2178 | 3144 | 0.0088511 | 0.059493
Pressure drop vs. air handled per square foot of filter area (Revised modeling concept)
| AHU-A operating hours per day | 10 | Normally, but it ran round the clock from the time the VFDs were installed until mid January when the controls were in place for scheduling
| Number of days AHU-A ran round the clock | 62 | Approximate, based on discussions with field staff.
| AHU-C operating hours per day | 24
| AHU-A constant volume flow rate | 54216.6667 | cfm | Source - | AHU-A and C filter bank flow and temperature v2.xls
| AHU-C constant volume flow rate | 65203.3333 | cfm | Source - | AHU-A and C filter bank flow and temperature v2.xls
| Date | Pressure drop, in.w.c. |  | Operating hours |  | Millions of cfm Handled |  | Filter Bank Area, square feet |  | Millions of cfm Handled per sq.ft. of filter area |  | Rate of Change, in.w.c. per million cfm handled per square foot of filter area |  | Filter Face Velocity, ft. per minute
|  | AHU-A | AHU-C | AHU-A | AHU-C | AHU-A | AHU-C | AHU-A | AHU-C | AHU-A | AHU-C | AHU-A | AHU-C | AHU-A | AHU-C
| 2007-10-21 | 0.18072 | 0.41295 | 0 | 0 | 0 | 0 |  |  | 0 | 0
| 2008-02-29 | 0.2 | 0.6 | 2178 | 3144 | 7085.034 | 12299.9568 | 160 | 160 | 44.2815 | 76.8747 | 0.00043535 | 0.0024331 | 338.8542 | 407.5208
131