## Vulcan LV4-S
Everything Standard
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft. | Straight Line
1880 | 90 | 0.11 | 1 | 1 | 1 | 206.8 | 90 | 56.8
1880 | 100 | 0.15 | 1 | 1 | 1 | 282 | 240 | 2200
1880 | 110 | 0.2 | 1 | 1 | 1 | 376 | Offset | 150
1880 | 120 | 0.26 | 1 | 1 | 1 | 488.8
1880 | 130 | 0.33 | 1 | 1 | 1 | 620.4
1880 | 140 | 0.4 | 1 | 1 | 1 | 752
1880 | 150 | 0.45 | 1 | 1 | 1 | 846
1880 | 160 | 0.53 | 1 | 1 | 1 | 996.4
1880 | 170 | 0.61 | 1 | 1 | 1 | 1146.8
1880 | 180 | 0.69 | 1 | 1 | 1 | 1297.2
1880 | 190 | 0.78 | 1 | 1 | 1 | 1466.4
1880 | 200 | 0.86 | 1 | 1 | 1 | 1616.8
1880 | 210 | 0.95 | 1 | 1 | 1 | 1786
1880 | 215 | 1 | 1 | 1 | 1 | 1880
1880 | 220 | 1.05 | 1 | 1 | 1 | 1974
1880 | 230 | 1.14 | 1 | 1 | 1 | 2143.2
1880 | 240 | 1.25 | 1 | 1 | 1 | 2350
Warmer Entering Air
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 70°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1540 | 90 | 0.11 | 0.54545 | 1 | 1 | 92.4
1540 | 100 | 0.15 | 0.73333 | 1 | 1 | 169.4
1540 | 110 | 0.2 | 0.8 | 1 | 1 | 246.4
1540 | 120 | 0.26 | 0.80769 | 1 | 1 | 323.4
1540 | 130 | 0.33 | 0.84848 | 1 | 1 | 431.2
1540 | 140 | 0.4 | 0.85 | 1 | 1 | 523.6
1540 | 150 | 0.45 | 0.91111 | 1 | 1 | 631.4
1540 | 160 | 0.53 | 0.92453 | 1 | 1 | 754.6
1540 | 170 | 0.61 | 0.93443 | 1 | 1 | 877.8
1540 | 180 | 0.69 | 0.94203 | 1 | 1 | 1001
1540 | 190 | 0.78 | 0.9359 | 1 | 1 | 1124.2
1540 | 200 | 0.86 | 0.95349 | 1 | 1 | 1262.8
1540 | 210 | 0.95 | 0.95789 | 1 | 1 | 1401.4
1540 | 215 | 1 | 0.95 | 1 | 1 | 1463
1540 | 220 | 1.05 | 0.95238 | 1 | 1 | 1540
1540 | 230 | 1.14 | 0.95614 | 1 | 1 | 1678.6
1540 | 240 | 1.25 | 0.952 | 1 | 1 | 1832.6
Colder Entering Air
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 55°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1880 | 90 | 0.11 | 1.1818 | 1 | 1 | 244.4
1880 | 100 | 0.15 | 1.2667 | 1 | 1 | 357.2
1880 | 110 | 0.2 | 1.25 | 1 | 1 | 470
1880 | 120 | 0.26 | 1.1923 | 1 | 1 | 582.8
1880 | 130 | 0.33 | 1.1515 | 1 | 1 | 714.4
1880 | 140 | 0.4 | 1.125 | 1 | 1 | 846
1880 | 150 | 0.45 | 1.1778 | 1 | 1 | 996.4
1880 | 160 | 0.53 | 1.1509 | 1 | 1 | 1146.8
1880 | 170 | 0.61 | 1.1311 | 1 | 1 | 1297.2
1880 | 180 | 0.69 | 1.1159 | 1 | 1 | 1447.6
1880 | 190 | 0.78 | 1.1026 | 1 | 1 | 1616.8
1880 | 200 | 0.86 | 1.1047 | 1 | 1 | 1786
1880 | 210 | 0.95 | 1.1053 | 1 | 1 | 1974
1880 | 215 | 1 | 1.09 | 1 | 1 | 2049.2
1880 | 220 | 1.05 | 1.0857 | 1 | 1 | 2143.2
1880 | 230 | 1.14 | 1.0877 | 1 | 1 | 2331.2
1880 | 240 | 1.25 | 1.072 | 1 | 1 | 2519.2
50% Flow Reduction
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1880 | 90 | 0.11 | 1 | 0.973 | 1 | 201.2164
1880 | 100 | 0.15 | 1 | 0.973 | 1 | 274.386
1880 | 110 | 0.2 | 1 | 0.973 | 1 | 365.848
1880 | 120 | 0.26 | 1 | 0.973 | 1 | 475.6024
1880 | 130 | 0.33 | 1 | 0.973 | 1 | 603.6492
1880 | 140 | 0.4 | 1 | 0.973 | 1 | 731.696
1880 | 150 | 0.45 | 1 | 0.973 | 1 | 823.158
1880 | 160 | 0.53 | 1 | 0.973 | 1 | 969.4972
1880 | 170 | 0.61 | 1 | 0.973 | 1 | 1115.8364
1880 | 180 | 0.69 | 1 | 0.973 | 1 | 1262.1756
1880 | 190 | 0.78 | 1 | 0.973 | 1 | 1426.8072
1880 | 200 | 0.86 | 1 | 0.973 | 1 | 1573.1464
1880 | 210 | 0.95 | 1 | 0.973 | 1 | 1737.778
1880 | 215 | 1 | 1 | 0.973 | 1 | 1829.24
1880 | 220 | 1.05 | 1 | 0.973 | 1 | 1920.702
1880 | 230 | 1.14 | 1 | 0.973 | 1 | 2085.3336
1880 | 240 | 1.25 | 1 | 0.973 | 1 | 2286.55
50% Flow Reduction
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1880 | 90 | 0.11 | 1 | 0.973 | 1 | 201.2164
1880 | 100 | 0.15 | 1 | 0.973 | 1 | 274.386
1880 | 110 | 0.2 | 1 | 0.973 | 1 | 365.848
1880 | 120 | 0.26 | 1 | 0.973 | 1 | 475.6024
1880 | 130 | 0.33 | 1 | 0.973 | 1 | 603.6492
1880 | 140 | 0.4 | 1 | 0.973 | 1 | 731.696
1880 | 150 | 0.45 | 1 | 0.973 | 1 | 823.158
1880 | 160 | 0.53 | 1 | 0.973 | 1 | 969.4972
1880 | 170 | 0.61 | 1 | 0.973 | 1 | 1115.8364
1880 | 180 | 0.69 | 1 | 0.973 | 1 | 1262.1756
1880 | 190 | 0.78 | 1 | 0.973 | 1 | 1426.8072
1880 | 200 | 0.86 | 1 | 0.973 | 1 | 1573.1464
1880 | 210 | 0.95 | 1 | 0.973 | 1 | 1737.778
1880 | 215 | 1 | 1 | 0.973 | 1 | 1829.24
1880 | 220 | 1.05 | 1 | 0.973 | 1 | 1920.702
1880 | 230 | 1.14 | 1 | 0.973 | 1 | 2085.3336
1880 | 240 | 1.25 | 1 | 0.973 | 1 | 2286.55

## Lines
Design Condition HW Temperature Line
OAT, °F | Btu/hr/ft | Average FTR HW, °F
7.4 | 2100 | 160
7.4 | 0 | 160
Design Condition Capacity Line
OAT, °F | Btu/hr/ft | HW Set Point, °F
7.4 | 996 | 80
7.4 | 996 | 250

## Unit Length Load
Reset Schedule Design Point
Design Average Water Temperature - | 160 | °F (From Manufacturer's Data)
Design Btu/hr/ft - | 996.4 | Btu/hr/ft
Design Outdoor Temperature - | 7.4 | °F
Design Indoor Temperature - | 72 | °F
Btu/hr/ft/°ΔtIndoor/Outdoor - | 15.4241 | Btu/hr/ft/°ΔtIndoor/Outdoor