## RPM Curves
Manufacturer | Greenheck
Model | 40-AFDW-41
Static Pressure, in.w.c.(Flow, cfm), created by Plot Digitizer, 2.6.6
Date: 11/26/15, 2:31:59 PM | [5 empty] | Design Flow - |  |  | Minimum Flow - |  |  | Minimum Flow - |  |  | Minimum Flow - |  |  | Minimum Flow -
Original Digitial Information |  |  |  |  | 276 rpm | Design Fan Static - |  |  | Fan Static at Minimum Flow - |  |  | Fan Static at Minimum Flow - |  |  | Fan Static at Minimum Flow - |  |  | Fan Static at Minimum Flow -
Maximum Speed Curve |  | Label | Minimum Speed Curve |  | Label | Design (Dirty Filters) |  | Label | Clean Filters |  | Label | 75% Flow |  | Label | 50% Flow |  | Label | 25% Flow |  | Label
996 | rpm (Max. Class I) | 996 rpm (Max. Class I) | 276 | rpm (Minimum charted speed) | 276 rpm (Minimum charted speed) | 900 | rpm | 900 rpm | 836 | rpm | 836 rpm | 648 | rpm | 648 rpm | 476 | rpm | 476 rpm | 334 | rpm | 334 rpm
Flow, cfm | Static pressure, in. w.c. |  | Flow, cfm | Static pressure, in. w.c. |  | Flow, cfm | Static pressure, in. w.c. |  | Flow, cfm | Static pressure, in. w.c. |  | Flow, cfm | Static pressure, in. w.c. |  | Flow, cfm | Static pressure, in. w.c. |  | Flow, cfm | Static pressure, in. w.c.
1e-07 | 5.8008 |  | 2.7711e-08 | 0.44544 |  | 9.0361e-08 | 4.7364 |  | 8.3936e-08 | 4.0868 |  | 6.506e-08 | 2.4554 |  | 4.7791e-08 | 1.3249 |  | 3.3534e-08 | 0.65232
15038.1 | 5.8926 |  | 4167.1843 | 0.45249 |  | 13588.6446 | 4.8114 |  | 12622.341 | 4.1514 |  | 9783.8241 | 2.4942 |  | 7186.8831 | 1.3459 |  | 5042.897 | 0.66264
20164.6 | 5.9154 |  | 5587.7807 | 0.45424 |  | 18221.0241 | 4.8301 |  | 16925.3068 | 4.1676 |  | 13119.1373 | 2.5039 |  | 9636.8972 | 1.3511 |  | 6762.0245 | 0.66521
23833 | 5.9106 |  | 6604.3253 | 0.45387 |  | 21535.8434 | 4.8261 |  | 20004.4056 | 4.1641 |  | 15505.8072 | 2.5019 |  | 11390.0683 | 1.35 |  | 7992.1908 | 0.66467
27924.5 | 5.8733 |  | 7738.1145 | 0.451 |  | 25232.9819 | 4.7957 |  | 23438.6365 | 4.1379 |  | 18167.747 | 2.4861 |  | 13345.4438 | 1.3415 |  | 9364.24 | 0.66047
32250.6 | 5.7433 |  | 8936.9133 | 0.44102 |  | 29142.1084 | 4.6895 |  | 27069.7807 | 4.0463 |  | 20982.3181 | 2.431 |  | 15412.9373 | 1.3118 |  | 10814.9602 | 0.64586
36904.6 | 5.3956 |  | 10226.5759 | 0.41432 |  | 33347.5301 | 4.4056 |  | 30976.1502 | 3.8013 |  | 24010.2217 | 2.2838 |  | 17637.1382 | 1.2323 |  | 12375.639 | 0.60675
43578.6 | 4.6446 |  | 12075.9976 | 0.35665 |  | 39378.253 | 3.7924 |  | 36578.0217 | 3.2722 |  | 28352.3422 | 1.966 |  | 20826.7205 | 1.0608 |  | 14613.7072 | 0.5223
49311.7 | 3.8659 |  | 13664.688 | 0.29686 |  | 44558.7651 | 3.1566 |  | 41390.1418 | 2.7236 |  | 32082.3108 | 1.6364 |  | 23566.6357 | 0.88296 |  | 16536.2528 | 0.43473
54949.9 | 2.9296 |  | 15227.0807 | 0.22496 |  | 49653.5241 | 2.3921 |  | 46122.6068 | 2.064 |  | 35750.5373 | 1.2401 |  | 26261.1972 | 0.66913 |  | 18426.9745 | 0.32945
61715.1 | 1.7107 |  | 17101.7747 | 0.13136 |  | 55766.6566 | 1.3968 |  | 51801.0277 | 1.2052 |  | 40151.9928 | 0.72412 |  | 29494.3651 | 0.39073 |  | 20695.6259 | 0.19238
66647.7 | 0.75599 |  | 18468.6398 | 0.058051 |  | 60223.8253 | 0.61728 |  | 55941.2422 | 0.53261 |  | 43361.1542 | 0.32 |  | 31851.712 | 0.17267 |  | 22349.7307 | 0.085014
69560.2 | 0.1813 |  | 19275.7181 | 0.013922 |  | 62855.6024 | 0.14803 |  | 58385.8707 | 0.12773 |  | 45256.0337 | 0.076741 |  | 33243.6297 | 0.041409 |  | 23326.4124 | 0.020388
Projected curves assume the affinity laws. |  |  |  | Horizontal line for taking readings on the static pressure axis
Flow is projected from the following relationship |  |  |  | Set x values to minimum and maximum x axis values
Set y value to cross the point on the curve you are trying to read
Set y to zero to make the line go away
|  |  |  | X | Primary Y
|  |  |  | 0 | 0
|  |  |  | 80000 | 0
Horizontal line for taking readings on the bhp axis
Set x values to minimum and maximum x axis values
Set y value to cross the point on the curve you are trying to read
Set y to zero to make the line go away
|  |  |  | X | Secondary Y
|  |  |  | 0 | 0
Static is projected from the following relationship |  |  |  | 80000 | 0
Vertical line for taking readings on the flow axis
Set y values to minimum and maximum static pressure axis values
Set x value to cross the point on the curve you are trying to read
Set y to zero to make the line go away
|  |  |  | X | Secondary Y
|  |  |  | 0 | 0
|  |  |  | 0 | 6

## HP Curves
Static Pressure, in.w.c.(Flow, cfm), created by Plot Digitizer, 2.6.6
Date: 11/26/15, 2:31:59 PM
Original Digitial Information
Maximum Speed Curve |  | Label | Minimum Speed Curve |  | Label | Design (Dirty Filters) |  | Label | Clean Filters |  | Label | 75% Flow |  | Label | 50% Flow |  | Label | 25% Flow |  | Label
996 | rpm hp | 996 rpm hp | 276 | rpm hp | 276 rpm hp | 900 | rpm hp | 900 rpm hp | 836 | rpm hp | 836 rpm hp | 648 | rpm hp | 648 rpm hp | 476 | rpm hp | 476 rpm hp | 334 | rpm hp | 334 rpm hp
Drive losses - | 3%
Flow, cfm | bhp | hp | Flow, cfm | hp |  | Flow, cfm | bhp |  | Flow, cfm | bhp |  | Flow, cfm | bhp |  | Flow, cfm | bhp |  | Flow, cfm | bhp
0.0001 | 17.2978 | 17.8328 | 2.7711e-05 | 0.36808 |  | 9.0361e-05 | 12.7626 |  | 8.3936e-05 | 10.229 |  | 6.506e-05 | 4.7636 |  | 4.7791e-05 | 1.8881 |  | 3.3534e-05 | 0.65231
5280.34 | 20.9437 | 21.5914 | 1463.2267 | 0.44566 |  | 4771.3916 | 15.4526 |  | 4432.0926 | 12.3849 |  | 3435.4019 | 5.7677 |  | 2523.536 | 2.2861 |  | 1770.7164 | 0.78979
9044.61 | 23.8245 | 24.5613 | 2506.3377 | 0.50696 |  | 8172.8404 | 17.5781 |  | 7591.6606 | 14.0885 |  | 5884.4451 | 6.561 |  | 4322.5245 | 2.6006 |  | 3033.0319 | 0.89843
15208.4 | 28.1905 | 29.0624 | 4214.3759 | 0.59986 |  | 13742.5301 | 20.7995 |  | 12765.2835 | 16.6703 |  | 9894.6217 | 7.7634 |  | 7268.2715 | 3.0771 |  | 5100.0056 | 1.0631
29181.8 | 36.6514 | 37.7849 | 8086.5229 | 0.7799 |  | 26369.0964 | 27.042 |  | 24493.9606 | 21.6736 |  | 18985.7494 | 10.0934 |  | 13946.3221 | 4.0007 |  | 9785.8647 | 1.3821
34262.6 | 38.9459 | 40.1504 | 9494.4554 | 0.82873 |  | 30960.1807 | 28.735 |  | 28758.5679 | 23.0305 |  | 22291.3301 | 10.7253 |  | 16374.4956 | 4.2511 |  | 11489.6671 | 1.4687
38543.4 | 40.4751 | 41.7269 | 10680.7012 | 0.86127 |  | 34828.3735 | 29.8633 |  | 32351.6892 | 23.9347 |  | 25076.4289 | 11.1464 |  | 18420.3398 | 4.4181 |  | 12925.1964 | 1.5263
42306.6 | 41.6892 | 42.9786 | 11723.5157 | 0.8871 |  | 38228.8554 | 30.7591 |  | 35510.359 | 24.6527 |  | 27524.7759 | 11.4808 |  | 20218.8169 | 4.5506 |  | 14187.153 | 1.5721
46022.7 | 42.7682 | 44.0909 | 12753.2783 | 0.91006 |  | 41586.7771 | 31.5551 |  | 38629.4952 | 25.2907 |  | 29942.4795 | 11.7779 |  | 21994.7843 | 4.6684 |  | 15433.3151 | 1.6128
49315.2 | 43.2168 | 44.5534 | 13665.6578 | 0.91961 |  | 44561.9277 | 31.8862 |  | 41393.0795 | 25.556 |  | 32084.588 | 11.9014 |  | 23568.3084 | 4.7173 |  | 16537.4265 | 1.6297
52654.3 | 43.0798 | 44.4122 | 14590.9506 | 0.91669 |  | 47579.1867 | 31.7851 |  | 44195.7779 | 25.475 |  | 34257.0145 | 11.8637 |  | 25164.1032 | 4.7024 |  | 17657.1649 | 1.6246
58156.5 | 42.3109 | 43.6195 | 16115.6566 | 0.90033 |  | 52551.0542 | 31.2178 |  | 48814.0904 | 25.0203 |  | 37836.759 | 11.652 |  | 27793.6687 | 4.6184 |  | 19502.2801 | 1.5956
63423.1 | 40.9566 | 42.2233 | 17575.0759 | 0.87151 |  | 57310.0301 | 30.2185 |  | 53234.6502 | 24.2195 |  | 41263.2217 | 11.279 |  | 30310.6382 | 4.4706 |  | 21268.389 | 1.5445
70429 | 37.9796 | 39.1542 | 19516.4699 | 0.80816 |  | 63640.6627 | 28.022 |  | 59115.1044 | 22.459 |  | 45821.2771 | 10.4592 |  | 33658.8394 | 4.1457 |  | 23617.757 | 1.4322
Projected curves assume the affinity laws.
Flow is projected from the following relationship
Static is projected from the following relationship

## BHP vs RPM
Condition | Flow, cfm | Static, in.w.c. | Fan Speed, rpm | Bhp
Design Flow, Clean Filters | 37500 | 3.17 | 836 | 25
75% Flow, 1 of 4 Zones at 0 cfm | 28125 | 2.0019 | 648 | 11.5
50% Flow, 2 of 4 Zones at 0 cfm | 18750 | 1.1675 | 476 | 4.4
25% Flow, 3 of 4 Zones at 0 cfm | 9375 | 0.66687 | 334 | 1.32

## Surge Line
The surge line is projected as a system curve through a point selected from the original fan curve
Maximum Flow - | 35000
Minimum Flow - | 0
Point on Surge Line - | 32450 | 5.75
% Maximum | Flow | Static
100% | 35000 | 6.6892
80% | 28000 | 4.2811
60% | 21000 | 2.4081
40% | 14000 | 1.0703
30% | 10500 | 0.60203
20% | 7000 | 0.26757
15% | 5250 | 0.15051
10% | 3500 | 0.066892
5% | 1750 | 0.016723
2.5% | 875 | 0.0041808
0% | 0 | 0

## Best Efficiency Point
This projects a system curve through the best efficiency point, which is entered manually from the fan curve
Maximum Flow - | 40000
Minimum Flow - | 0
| Flow | Static
Operating condition - | Best Efficiency
Best static efficiency point - | 27500 | 2.925
% Maximum | Flow | Static
100% | 40000 | 6.1884
80% | 32000 | 3.9606
60% | 24000 | 2.2278
40% | 16000 | 0.99015
30% | 12000 | 0.55696
20% | 8000 | 0.24754
15% | 6000 | 0.13924
10% | 4000 | 0.061884
5% | 2000 | 0.015471
2.5% | 1000 | 0.0038678
0% | 0 | 0
Label - | Best Efficiency Operating Point; 27,500 cfm at 2.93 in.w.c.

## Static Pressure
Design Flow - | 37500 | cfm |  |  |  |  | 75% Flow - | 28125 | cfm | 50% Flow - | 18750 | cfm | 25% Flow - | 9375 | cfm | Design Flow - | 37500 | cfm
Design Static - | 4 | in.w.c. |  |  |  |  | Clean Filters, 1 of 4 Zones at 0 cfm | 2.0019 | in.w.c. | Clean Filters, 2 of 4 Zones at 0 | 1.1675 | in.w.c. | Clean Filters, 3 of 4 Zones at 0 | 0.66687 | in.w.c. | Clean Filters | 3.17 | in.w.c.
Static Components | Loss, in. w.c. | Comment |  |  |  |  | Static Components | Loss, in. w.c. | Comment | Static Components | Loss, in. w.c. | Comment | Static Components | Loss, in. w.c. | Comment | Static Components | Loss, in. w.c. | Comment
Intake louver | 0.05 | [5 empty] | Intake louver | 0.028125 |  | Intake louver | 0.0125 |  | Intake louver | 0.003125 |  | Intake louver | 0.05
Intake duct | 0.1 | 100 | eq.ft. at | 0.1 | in.w.c. per 100 ft. |  | Intake duct | 0.05625 |  | Intake duct | 0.025 |  | Intake duct | 0.00625 |  | Intake duct | 0.1
Economizer dampers | 0.22 | [5 empty] | Economizer dampers | 0.12375 |  | Economizer dampers | 0.055 |  | Economizer dampers | 0.01375 |  | Economizer dampers | 0.22
Prefilters | 0.5 | Dirty | 0.15 | Clean | Loading ∆ P - | 0.35 | Prefilters | 0.084375 | Clean | Prefilters | 0.0375 | Clean | Prefilters | 0.009375 | Clean | Prefilters | 0.15 | Clean
Final filters | 0.65 | Dirty | 0.17 | Clean | Loading ∆ P - | 0.48 | Final filters | 0.095625 | Clean | Final filters | 0.0425 | Clean | Final filters | 0.010625 | Clean | Final filters | 0.17 | Clean
Preheat coil | 0.08 | [5 empty] | Preheat coil | 0.045 |  | Preheat coil | 0.02 |  | Preheat coil | 0.005 |  | Preheat coil | 0.08
Cooling coil | 0.85 | [5 empty] | Cooling coil | 0.47812 |  | Cooling coil | 0.2125 |  | Cooling coil | 0.053125 |  | Cooling coil | 0.85
Casing losses | 0.05 | [5 empty] | Casing losses | 0.028125 |  | Casing losses | 0.0125 |  | Casing losses | 0.003125 |  | Casing losses | 0.05
System effect | 0.1 | [5 empty] | System effect | 0.05625 |  | System effect | 0.025 |  | System effect | 0.00625 |  | System effect | 0.1
Discharge duct to discharge sensor location | 0.05 | 50 | eq.ft. at | 0.1 | in.w.c. per 100 ft. |  | Discharge duct to discharge sensor location | 0.028125 |  | Discharge duct to discharge sensor location | 0.0125 |  | Discharge duct to discharge sensor location | 0.003125 |  | Discharge duct to discharge sensor location | 0.05
Duct system to remote sensor location | 0.85 | 850 | eq.ft. at | 0.1 | in.w.c. per 100 ft. | Includes intake and supply system | Duct system to remote sensor location | 0.47813 |  | Duct system to remote sensor location | 0.2125 |  | Duct system to remote sensor location | 0.053125 |  | Duct system to remote sensor location | 0.85
Wide open VAV Box | 0.37 | [5 empty] | Wide open VAV Box | 0.37 | The three active zones are still at design flow and pressure drop | Wide open VAV Box | 0.37 | The two active zones are still at design flow and pressure drop | Wide open VAV Box | 0.37 | The one active zones is still at design flow and pressure drop | Wide open VAV Box | 0.37
Reheat Coil | 0.08 | [5 empty] | Reheat Coil | 0.08 |  | Reheat Coil | 0.08 |  | Reheat Coil | 0.08 |  | Reheat Coil | 0.08
Terminal duct work and diffusser | 0.05 | [5 empty] | Terminal duct work and diffusser | 0.05 |  | Terminal duct work and diffusser | 0.05 |  | Terminal duct work and diffusser | 0.05 |  | Terminal duct work and diffusser | 0.05
Total | 4 | With dirty filters - | 3.17 | With clean filters |  |  | Total | 2.0019 |  | Total | 1.1675 |  | Total | 0.66687 |  | Total | 3.17
Fixed control static (box loss at design flow) | 0.5 | Equals the pressure required from the inlet of the VAV to the zone under design conditions |  |  |  |  | Control static | 0 | Pressure added by the requirement to control at a fixed pressure | Control static | 0 | Pressure added by the requirement to control at a fixed pressure | Control static | 0 | Pressure added by the requirement to control at a fixed pressure | Control static | 0 | Pressure added by the requirement to control at a fixed pressure
Subtotal for the zone equipment - | 0.5 | in.w.c |  |  |  |  | Subtotal for the zone equipment - | 0.5 | in.w.c | Subtotal for the zone equipment - | 0.5 | in.w.c | Subtotal for the zone equipment - | 0.5 | in.w.c | Subtotal for the zone equipment - | 0.5 | in.w.c

## Duct Leakage Estimate
The analysis in this spreadsheet assumes that the mimimum flow point on a system curve for a VAV system will likely be the duct leakage that occurs with all of the terminal units shut off (0 cfm delivered flow to the zone) at the static pressure that is used to control the system. To try to understand what flow rate that might imply, I used the requirements from the International Energy Conservation Code (copy to the right) along with an assumption that the system flow rate is in the range of 1/2 cfm to 1 cfm per square foot of building area. In other words, I use the design flow rate to estimate the building square footage and then the building square footage to estimate what the duct leakage would be on an IECC basis at the IECC test condition. I then adjust that based on the minimum duct static pressure using the square law and that becomes the first point on my system curve.
Design flow rate - | 37500 | cfm
| Low end (1 cfm per square foot) | High end (0.5 cfm per square foot)
Implied square footage of the area served - | 37500 | 75000 | sq.ft.
IECC leakage rate (2012 basis) - | 4 | 4 | cfm per 100 sq.ft.
Duct leakage - | 1500 | 3000 | cfm at 0.1 in.w.c.
IECC test pressure - | 0.1 | 0.1 | in. w.c.
Fixed control pressure - | 0.5 | 0.5 | in.w.c.
Anticipated leakage at zero cfm delivered to the zone - | 3354.102 | 6708.2039 | cfm at 0.5 in.w.c.
Duct leakage as a percentage of the design flow - | 8.944% | 17.89%

## Design System Curve
Design Flow, Dirty Filters
This projects a system curve through a point selected from the original fan curve.
The system curve origin is adjusted to go through the fixed control pressure at the duct leakage rate as shown below and discussed/developed on the "Duct Leakage Estimate" tab.
It is assumed that at the design flow rate, the damper in the terminal VAV box is wide open; i.e. there is no throttling pressure drop at the VAV damper, just the wide open loss.
It is assumed that the flow that generates pressure drop in the duct system is the flow delivered to the zone via the terminal equipment. This is set as being equal to the design flow minus the leakage.
The pressure drop due to flow is calculated based on the delivered flow.
Once the pressure drop due to flow is established via the square law, the fixed control pressure is added to it to offset the system curve from 0 in.w.c. at the leakage flow rate.
The flow rate is adjusted from the delivered flow rate by adding the leakage flow to it.
| Flow, cfm | Static, in.w.c.
Maximum - | 50000 | 6 | These numbers set up the end points used for projecting curves
Minimum - | 3354.102 | 0
Change in flow - | 46645.898
Remote static control set point at design - | 0 | 0.5
Discharge static control set point at design - | 0 | 0.85
Operating condition - | Design Flow, Dirty Filters
| Flow, cfm | Static, in.w.c.
|  | Duct System to Discharge Sensor, in.w.c. | Discharge Sensor to Remote Sensor, in.w.c. | Terminal System, in.w.c. | Total
Design Operating Point - | 37500 | 2.65 | 0.85 | 0.5 | 4
Assumed leakage flow rate - | 3354.102
Flow delivered to the zone based on the assumed leakage - | 34145.898
| Labels | Design Flow, Dirty Filters System Curve | Design Flow, Dirty Filters Operating Curve with a Discharge Sensor | Design Flow, Dirty Filters Operating Curve with a Remote Sensor
% Maximum | Flow, cfm | System Curve Static Pressure, in.w.c. | Operating Curve with Discharge Sensor | Operating Curve with Remote Sensor
133.3% | 50000 | 7.1111 | 7.1111 | 7.1111
122.2% | 45833.3333 | 5.9753 | 5.9753 | 5.9753
111.1% | 41666.6667 | 4.9383 | 4.9383 | 4.9383
Design Flow, Dirty Filters flow rate | 37500 | 4 | 4 | 4
86.99% | 32622.0146 | 3.027 | 3.3554 | 3.1487
73.98% | 27744.0291 | 2.1895 | 2.8005 | 2.4158
60.98% | 22866.0437 | 1.4872 | 2.3353 | 1.8013
47.97% | 17988.0583 | 0.92038 | 1.9598 | 1.3053
34.96% | 13110.0728 | 0.48889 | 1.6739 | 0.92778
21.95% | 8232.0874 | 0.19276 | 1.4777 | 0.66867
8.944% | 3354.102 | 0.032 | 1.3712 | 0.528
Label - | Design Flow, Dirty Filters Operating Point; 37,500 cfm at 4. in.w.c. and 30.7 bhp
Design Point Flow and Static | Design Flow, Dirty Filters Operating Point
| 37500 | 4
Design Point Flow and Bhp | Design Flow | Design Flow, Dirty Filters bhp | Design Flow, Dirty Filters rpm
| 37500 | 30.7 | 900
Design Point Lines | Design Flow |  | Maximum Flow | Design Static | Maximum Flow | Design Bhp
| 37500 | 4 | 37500 | 4 | 80000 | 30.7
| 37500 | 0 | 0 | 4 | 37500 | 30.7

## Clean Filter System Curve
Design Flow, Clean Filters
This projects a system curve through a point selected from the original fan curve.
The system curve origin is adjusted to go through the fixed control pressure at the duct leakage rate as shown below and discussed/developed on the "Duct Leakage Estimate" tab.
It is assumed that at the design flow rate, the damper in the terminal VAV box is wide open; i.e. there is no throttling pressure drop at the VAV damper, just the wide open loss.
It is assumed that the flow that generates pressure drop in the duct system is the flow delivered to the zone via the terminal equipment. This is set as being equal to the design flow minus the leakage.
The pressure drop due to flow is calculated based on the delivered flow.
Once the pressure drop due to flow is established via the square law, the fixed control pressure is added to it to offset the system curve from 0 in.w.c. at the leakage flow rate.
The flow rate is adjusted from the delivered flow rate by adding the leakage flow to it.
| Flow, cfm | Static, in.w.c.
Maximum - | 54000 | 6 | These numbers set up the end points used for projecting curves
Minimum - | 3354.102 | 0
Change in flow - | 50645.898
Remote static control set point at design - | 0 | 0.5
Discharge static control set point at design - | 0 | 0.85
Operating condition - | Design Flow, Clean Filters
| Flow, cfm | Static, in.w.c.
|  | Duct System to Discharge Sensor, in.w.c. | Discharge Sensor to Remote Sensor, in.w.c. | Terminal System, in.w.c. | Total
Design Operating Point - | 37500 | 1.82 | 0.85 | 0.5 | 3.17
Assumed leakage flow rate - | 3354.102
Flow delivered to the zone based on the assumed leakage - | 34145.898
| Labels | Design Flow, Clean Filters System Curve | Design Flow, Clean Filters Operating Curve with a Discharge Sensor | Design Flow, Clean Filters Operating Curve with a Remote Sensor | System Curve through 0
% Maximum | Flow, cfm | System Curve Static Pressure, in.w.c. | Operating Curve with Discharge Sensor | Operating Curve with Remote Sensor | Flow, cfm | Fan Static Pressure, in.w.c.
144% | 54000 | 6.5733 | 6.5733 | 6.5733 | 54000 | 6.5733
129.3% | 48500 | 5.3025 | 5.3025 | 5.3025 | 48500 | 5.3025
114.7% | 43000 | 4.1681 | 4.1681 | 4.1681 | 43000 | 4.1681
Design Flow, Clean Filters flow rate | 37500 | 3.17 | 3.17 | 3.17 | 37500 | 3.17
86.99% | 32622.0146 | 2.3989 | 2.7273 | 2.5206 | 32622.0146 | 2.3989
73.98% | 27744.0291 | 1.7351 | 2.3462 | 1.9615 | 27744.0291 | 1.7351
60.98% | 22866.0437 | 1.1786 | 2.0267 | 1.4927 | 22866.0437 | 1.1786
47.97% | 17988.0583 | 0.7294 | 1.7688 | 1.1144 | 17988.0583 | 0.7294
34.96% | 13110.0728 | 0.38744 | 1.5724 | 0.82633 | 13110.0728 | 0.38744
21.95% | 8232.0874 | 0.15276 | 1.4377 | 0.62867 | 8232.0874 | 0.15276
8.944% | 3354.102 | 0.02536 | 1.3646 | 0.52136 | 3354.102 | 0.02536
Label - | Design Flow, Clean Filters Operating Point; 37,500 cfm at 3.17 in.w.c. and 25. bhp |  |  |  | 0 | 0
Design Point Flow and Static | Design Flow, Clean Filters Operating Point
| 37500 | 3.17
Design Point Flow and Bhp | Design Flow | Design Flow, Clean Filters bhp | Design Flow, Clean Filters rpm
| 37500 | 25 | 836
Design Point Lines | Design Flow, Clean Filters Flow |  | Maximum Flow | Design Flow, Clean Filters Static | Maximum Flow | Design Flow, Clean Filters Bhp
| 37500 | 3.17 | 37500 | 3.17 | 80000 | 25
| 37500 | 0 | 0 | 3.17 | 37500 | 25

## 75% Flow
75% Flow, 1 of 4 Zones at 0 cfm
This projects a system curve through a point selected from the original fan curve.
The system curve origin is adjusted to go through the fixed control pressure at the duct leakage rate as shown below and discussed/developed on the "Duct Leakage Estimate" tab.
It is assumed that at the design flow rate, the damper in the terminal VAV box is wide open; i.e. there is no throttling pressure drop at the VAV damper, just the wide open loss.
It is assumed that the flow that generates pressure drop in the duct system is the flow delivered to the zone via the terminal equipment. This is set as being equal to the design flow minus the leakage.
The pressure drop due to flow is calculated based on the delivered flow.
Once the pressure drop due to flow is established via the square law, the fixed control pressure is added to it to offset the system curve from 0 in.w.c. at the leakage flow rate.
The flow rate is adjusted from the delivered flow rate by adding the leakage flow to it.
| Flow, cfm | Static, in.w.c.
Maximum - | 50000 | 6 | These numbers set up the end points used for projecting curves
Minimum - | 3354.102 | 0
Change in flow - | 46645.898
Remote static control set point at design - | 0 | 0.5
Discharge static control set point at design - | 0 | 0.47813
Operating condition - | 75% Flow, 1 of 4 Zones at 0 cfm
| Flow, cfm | Static, in.w.c.
|  | Duct System to Discharge Sensor, in.w.c. | Discharge Sensor to Remote Sensor, in.w.c. | Terminal System, in.w.c. | Total
Design Operating Point - | 28125 | 1.0237 | 0.47813 | 0.5 | 2.0019
Assumed leakage flow rate - | 3354.102
Flow delivered to the zone based on the assumed leakage - | 24770.898
| Labels | 75% Flow, 1 of 4 Zones at 0 cfm System Curve | 75% Flow, 1 of 4 Zones at 0 cfm Operating Curve with a Discharge Sensor | 75% Flow, 1 of 4 Zones at 0 cfm Operating Curve with a Remote Sensor
% Maximum | Flow, cfm | System Curve Static Pressure, in.w.c. | Operating Curve with Discharge Sensor | Operating Curve with Remote Sensor
177.8% | 50000 | 6.3269 | 6.3269 | 6.3269
151.9% | 42708.3333 | 4.6161 | 4.6161 | 4.6161
125.9% | 35416.6667 | 3.1744 | 3.1744 | 3.1744
75% Flow, 1 of 4 Zones at 0 cfm flow rate | 28125 | 2.0019 | 2.0019 | 2.0019
93.71% | 26355.6501 | 1.7579 | 1.8771 | 1.8189
74.84% | 21047.6006 | 1.1211 | 1.5515 | 1.3411
62.25% | 17508.9008 | 0.77584 | 1.3749 | 1.0821
49.67% | 13970.2011 | 0.49392 | 1.2307 | 0.87056
37.09% | 10431.5014 | 0.27539 | 1.119 | 0.70661
24.51% | 6892.8017 | 0.12024 | 1.0396 | 0.59021
11.93% | 3354.102 | 0.028471 | 0.99269 | 0.52136
Label - | 75% Flow, 1 of 4 Zones at 0 cfm Operating Point; 28,125 cfm at 2. in.w.c. and 11.5 bhp
Design Point Flow and Static | 75% Flow, 1 of 4 Zones at 0 cfm Operating Point
| 28125 | 2.0019
Design Point Flow and Bhp | Design Flow | 75% Flow, 1 of 4 Zones at 0 cfm bhp | 75% Flow, 1 of 4 Zones at 0 cfm rpm
| 28125 | 11.5 | 648
Design Point Lines | 75% Flow, 1 of 4 Zones at 0 cfm Flow |  | Maximum Flow | 75% Flow, 1 of 4 Zones at 0 cfm Static | Maximum Flow | 75% Flow, 1 of 4 Zones at 0 cfm Bhp
| 28125 | 2.0019 | 28125 | 2.0019 | 80000 | 11.5
| 28125 | 0 | 0 | 2.0019 | 28125 | 11.5

## 50% Flow
50% Flow, 2 of 4 Zones at 0 cfm
This projects a system curve through a point selected from the original fan curve.
The system curve origin is adjusted to go through the fixed control pressure at the duct leakage rate as shown below and discussed/developed on the "Duct Leakage Estimate" tab.
It is assumed that at the design flow rate, the damper in the terminal VAV box is wide open; i.e. there is no throttling pressure drop at the VAV damper, just the wide open loss.
It is assumed that the flow that generates pressure drop in the duct system is the flow delivered to the zone via the terminal equipment. This is set as being equal to the design flow minus the leakage.
The pressure drop due to flow is calculated based on the delivered flow.
Once the pressure drop due to flow is established via the square law, the fixed control pressure is added to it to offset the system curve from 0 in.w.c. at the leakage flow rate.
The flow rate is adjusted from the delivered flow rate by adding the leakage flow to it.
| Flow, cfm | Static, in.w.c.
Maximum - | 44000 | 6 | These numbers set up the end points used for projecting curves
Minimum - | 3354.102 | 0
Change in flow - | 40645.898
Remote static control set point at design - | 0 | 0.5
Discharge static control set point at design - | 0 | 0.2125
Operating condition - | 50% Flow, 2 of 4 Zones at 0 cfm
| Flow, cfm | Static, in.w.c.
|  | Duct System to Discharge Sensor, in.w.c. | Discharge Sensor to Remote Sensor, in.w.c. | Terminal System, in.w.c. | Total
Design Operating Point - | 18750 | 0.455 | 0.2125 | 0.5 | 1.1675
Assumed leakage flow rate - | 3354.102
Flow delivered to the zone based on the assumed leakage - | 15395.898
| Labels | 50% Flow, 2 of 4 Zones at 0 cfm System Curve | 50% Flow, 2 of 4 Zones at 0 cfm Operating Curve with a Discharge Sensor | 50% Flow, 2 of 4 Zones at 0 cfm Operating Curve with a Remote Sensor
% Maximum | Flow, cfm | System Curve Static Pressure, in.w.c. | Operating Curve with Discharge Sensor | Operating Curve with Remote Sensor
234.7% | 44000 | 6.4292 | 6.4292 | 6.4292
189.8% | 35583.3333 | 4.2048 | 4.2048 | 4.2048
144.9% | 27166.6667 | 2.4509 | 2.4509 | 2.4509
50% Flow, 2 of 4 Zones at 0 cfm flow rate | 18750 | 1.1675 | 1.1675 | 1.1675
94.13% | 17650.293 | 1.0346 | 1.1157 | 1.0915
76.54% | 14351.172 | 0.68396 | 0.97905 | 0.89104
64.81% | 12151.758 | 0.49038 | 0.90361 | 0.78037
53.08% | 9952.344 | 0.32893 | 0.84069 | 0.68806
41.35% | 7752.93 | 0.19961 | 0.79029 | 0.61412
29.62% | 5553.516 | 0.10242 | 0.75242 | 0.55856
17.89% | 3354.102 | 0.03736 | 0.72706 | 0.52136
Label - | 50% Flow, 2 of 4 Zones at 0 cfm Operating Point; 18,750 cfm at 1.17 in.w.c. and 4.4 bhp
Design Point Flow and Static | 50% Flow, 2 of 4 Zones at 0 cfm Operating Point
| 18750 | 1.1675
Design Point Flow and Bhp | Design Flow | 50% Flow, 2 of 4 Zones at 0 cfm bhp | 50% Flow, 2 of 4 Zones at 0 cfm rpm
| 18750 | 4.4 | 476
Design Point Lines | 50% Flow, 2 of 4 Zones at 0 cfm Flow |  | Maximum Flow | 50% Flow, 2 of 4 Zones at 0 cfm Static | Maximum Flow | 50% Flow, 2 of 4 Zones at 0 cfm Bhp
| 18750 | 1.1675 | 18750 | 1.1675 | 80000 | 4.4
| 18750 | 0 | 0 | 1.1675 | 18750 | 4.4

## 25% Flow
25% Flow, 3 of 4 Zones at 0 cfm
This projects a system curve through a point selected from the original fan curve.
The system curve origin is adjusted to go through the fixed control pressure at the duct leakage rate as shown below and discussed/developed on the "Duct Leakage Estimate" tab.
It is assumed that at the design flow rate, the damper in the terminal VAV box is wide open; i.e. there is no throttling pressure drop at the VAV damper, just the wide open loss.
It is assumed that the flow that generates pressure drop in the duct system is the flow delivered to the zone via the terminal equipment. This is set as being equal to the design flow minus the leakage.
The pressure drop due to flow is calculated based on the delivered flow.
Once the pressure drop due to flow is established via the square law, the fixed control pressure is added to it to offset the system curve from 0 in.w.c. at the leakage flow rate.
The flow rate is adjusted from the delivered flow rate by adding the leakage flow to it.
| Flow, cfm | Static, in.w.c.
Maximum - | 30000 | 6 | These numbers set up the end points used for projecting curves
Minimum - | 3354.102 | 0
Change in flow - | 26645.898
Remote static control set point at design - | 0 | 0.5
Discharge static control set point at design - | 0 | 0.053125
Operating condition - | 25% Flow, 3 of 4 Zones at 0 cfm
| Flow, cfm | Static, in.w.c.
|  | Duct System to Discharge Sensor, in.w.c. | Discharge Sensor to Remote Sensor, in.w.c. | Terminal System, in.w.c. | Total
Design Operating Point - | 9375 | 0.11375 | 0.053125 | 0.5 | 0.66687
Assumed leakage flow rate - | 3354.102
Flow delivered to the zone based on the assumed leakage - | 6020.898
| Labels | 25% Flow, 3 of 4 Zones at 0 cfm System Curve | 25% Flow, 3 of 4 Zones at 0 cfm Operating Curve with a Discharge Sensor | 25% Flow, 3 of 4 Zones at 0 cfm Operating Curve with a Remote Sensor
% Maximum | Flow, cfm | System Curve Static Pressure, in.w.c. | Operating Curve with Discharge Sensor | Operating Curve with Remote Sensor
320% | 30000 | 6.8288 | 6.8288 | 6.8288
246.7% | 23125 | 4.0576 | 4.0576 | 4.0576
173.3% | 16250 | 2.0036 | 2.0036 | 2.0036
25% Flow, 3 of 4 Zones at 0 cfm flow rate | 9375 | 0.66687 | 0.66687 | 0.66687
95.41% | 8944.9359 | 0.60709 | 0.65668 | 0.65192
81.65% | 7654.7434 | 0.44459 | 0.62896 | 0.61125
72.48% | 6794.6151 | 0.35029 | 0.61288 | 0.58766
63.3% | 5934.4868 | 0.26722 | 0.59871 | 0.56687
54.13% | 5074.3585 | 0.19537 | 0.58645 | 0.54889
44.95% | 4214.2303 | 0.13475 | 0.57611 | 0.53372
35.78% | 3354.102 | 0.08536 | 0.56768 | 0.52136
Label - | 25% Flow, 3 of 4 Zones at 0 cfm Operating Point; 9,375 cfm at .67 in.w.c. and 1.3 bhp
Design Point Flow and Static | 25% Flow, 3 of 4 Zones at 0 cfm Operating Point
| 9375 | 0.66687
Design Point Flow and Bhp | Design Flow | 25% Flow, 3 of 4 Zones at 0 cfm bhp | 25% Flow, 3 of 4 Zones at 0 cfm rpm
| 9375 | 1.32 | 334
Design Point Lines | 25% Flow, 3 of 4 Zones at 0 cfm Flow |  | Maximum Flow | 25% Flow, 3 of 4 Zones at 0 cfm Static | Maximum Flow | 25% Flow, 3 of 4 Zones at 0 cfm Bhp
| 9375 | 0.66687 | 9375 | 0.66687 | 80000 | 1.32
| 9375 | 0 | 0 | 0.66687 | 9375 | 1.32

## 996 rpm
Fan Static Pressure, in.w.c.(Flow, cfm), created by Plot Digitizer, 2.6.6
Date: 11/27/15, 10:47:14 AM
13
Flow | cfm | Fan Static Pressure | in.w.c.
175.71 | 5.8008
15038.1 | 5.8926
20164.6 | 5.9154
23833 | 5.9106
27924.5 | 5.8733
32250.6 | 5.7433
36904.6 | 5.3956
43578.6 | 4.6446
49311.7 | 3.8659
54949.9 | 2.9296
61715.1 | 1.7107
66647.7 | 0.75599
69560.2 | 0.1813

## 996 rpm hp
HP(Flow, cfm), created by Plot Digitizer, 2.6.6
Date: 11/27/15, 10:53:20 AM
14
Flow | cfm | HP
104.68 | 17.8328
5280.34 | 21.5914
9044.61 | 24.5613
15208.4 | 29.0624
29181.8 | 37.7849
34262.6 | 40.1504
38543.4 | 41.7269
42306.6 | 42.9786
46022.7 | 44.0909
49315.2 | 44.5534
52654.3 | 44.4122
58156.5 | 43.6195
63423.1 | 42.2233
70429 | 39.1542