## Mixed Air Temp Ctrl
Ball Room Air Handling Unit 2 Discharge Air Temperature Control Process
.
Notes
|  | 1 |  | Coordinate address during submittal review the the project specific hardware requirements and network architecture.
|  | 2 | 2 | Tune during the Cx process for stable operation under all operating conditions.
|  | 3 | 2 | The design intent is that this loop be a proportional only loop. Thus the integral and derivative gain should be set to 0 unless directed otherwise by the control system designer or commissioning provider during commissioning
|  | 4 | 2 | The recommended set point for this loop is 40°F. It is only intended to over-ride the discharge temperature control loop during start-up on a cold day to keep the mixed air plenum above freezing while the system stabilizes.
|  | 5 | 2 | The design set point for this system is 52°F
© 2017 Faciltiy Dynamics Engineering - All Rights Reserved
SupFn.Proof
Address
DI
Econ.OADpr
Note 1
AO
NC
4-20 ma
Econ.RetDpr
Note 1
AO
NO
4-20 ma
BA.Bld.OA.Temp
Note 1
AI
68
OA.HiLmtTemp
COA
IF
I
Greater Than
O
SP
°F
MxAirTmp
Note 1
AI
P
I
D
SP
O
I
Go
KP
KI
KD
0-100%
IGOff
DA
CHWCoil.Vlv
Note 1
AO
NC
4-20 ma
HWCoil.Vlv
Note 1
AO
NO
4-20 ma
Mixed Air Low Limit Set Point, Note 4
Adjust
Discharge Temap. Set Point, Note 5
Adjust
DischargeTmp
Note 1
AI
5.5 ma
Min OA
C
Note 3
Mixed Air DGain
C
Note 3
Mixed Air IGain
C
Note 2
Mixed Air PGain
C
0%
Mixed Air Off
C
Note 3
Discharge Temp. DGain
C
Note 3
Discharge Temp. IGain
C
Note 2
Discharge Temp. PGain
C
0%
Discharge Temp. Off
C
4 ma
HW Coil Opn Out
C
20 ma
HW Coil Cls Out
C
30%
HW Coil Cos In
C
0%
HW Coil Opn In
C
RATIO - DA
IHi
ILo
OIHi
OILo
I
O
OIHi
OILo
ILo
IHi
4 ma
CHW Coil Opn Out
C
20 ma
CHW Coil Cls Out
C
100%
CHW Coil Cls In
C
67%
CHW Coil Opn In
C
4 ma
OA Cls/RA Opn Out
C
20 ma
OA Opn/RA Cls Out
C
63%
OA Opn/RA Cls In
C
33%
OA Cls/RA Opn In
C
L
O
W
I1
O
I2
RATIO - DA
IHi
ILo
OIHi
OILo
I
O
OIHi
OILo
ILo
IHi
RATIO - DA
IHi
ILo
OIHi
OILo
I
O
OIHi
OILo
ILo
IHi
P
I
D
SP
O
I
Go
KP
KI
KD
0-100%
IGOff
DA
H
I
G
H
I1
O
I2
4 ma
OA/RA Off
C
20 ma
CHWCoil.VlvOff
C
SW
INO
INC
Pilot
O
SW
INO
INC
Pilot
O
5 ma
HWCoil.VlvOff
C
SW
INO
INC
Pilot
O
SW
INO
INC
Pilot
O