## Slide 1: Existing Building Commissioning Workshop: Series 16, Session 4
A Field Introduction to Hot Gas Bypass and the Vapor Compression Cycle
David Sellers
Senior Engineer, Facility Dynamics Engineering
Presented By:

## Slide 2: Get Connected with My Poll Everywhere
Via text messaging
Step 1
Text DAVIDSELLERS022 to 22333 (the hyphen gets inserted automatically on some phones)

## Slide 3: Get Connected with My Poll Everywhere
Via text messaging
Step 2
Receive confirmation that you have joined the session

## Slide 4: Get Connected with My Poll Everywhere
Via web browser
Step 1
Go to pollev.com/davidsellers022

## Slide 5: Get Connected with My Poll Everywhere
Via web browser
Step 1
Go to pollev.com/davidsellers022

## Slide 6: Get Connected with My Poll Everywhere
Via web browser or text messaging
Step 3
Wait for a poll question to come up

## Slide 7
Notes: Poll Title: What's the weather like where you are at? https://www.polleverywhere.com/free_text_polls/2dxl0d5Yb3aqmsBKVPYWy

## Slide 8: Vapor Compression Refrigeration Machines
An application of saturated system and phase change principles and concepts
https://av8rdas.wordpress.com/2013/07/15/saturated-multi-phase-systems-and-proof-that-a-watched-pot-does-actually-boil/

## Slide 9
Evaporation
Compression
Condensation
Expansion

## Slide 10: An Air-Cooled Vapor Compression Cycle Chiller

## Slide 12
Hot Gas Line
Compressor

## Slide 13
Liquid Line
Liquid Line Solenoid Valve
Condenser
Receiver

## Slide 14
Expansion Valve

## Slide 15
Evaporator
Suction Line

## Slide 16
Evaporator
Suction Line
Liquid Line
Liquid Line Solenoid Valve
Hot Gas Line
Condenser
Compressor
Receiver
Expansion Valve
An Air-Cooled Vapor Compression Cycle Chiller

## Slide 17
Notes: Poll Title: Click on the characteristic(s) of the suction line (more than one might apply) https://www.polleverywhere.com/clickable_images/tkixDbA1h12unfLsdlIxK

## Slide 18
Notes: Poll Title: Click on the characteristic(s) of the liquid line (more than one might apply) https://www.polleverywhere.com/clickable_images/1GTfhK08hKMt6frkU3SrU

## Slide 19
Notes: Poll Title: Click on the characteristic(s) of the hot gas line (more than one might apply) https://www.polleverywhere.com/clickable_images/TtyTkijOHsNyOn61tRi2u

## Slide 20: Which Pipe is Which
Suction Line
Liquid Line
Hot gas line
Largest, coldest and insulated
Smallest, warm, usually not insulated
Size between suction and liquid line size, hot, typically not insulated

## Slide 21
Notes: Poll Title: Click on the item of equipment that you think is the air cooled chiller. https://www.polleverywhere.com/clickable_images/Ef4D78wBZ4FsmJqPCBWMM

## Slide 22: An Air Cooled Vapor Compression Cycle Chiller

## Slide 23
Notes: Poll Title: Click on the area on the chiller where you think the condensing coils are located. https://www.polleverywhere.com/clickable_images/p7iPdry9rFof1WTJ2pM1t

## Slide 24
Condenser

## Slide 25
Evaporator
Filter Dryer (Not shown on diagram)
Service Valves (Not shown on diagram
Service Bypass to Allow Filter Dryer to be Serviced (Not shown on diagram

## Slide 26
Chilled Water Pipes
Liquid Line Solenoid Valve
Liquid Lines
Suction Line

## Slide 27
Compressor
Compressor
Suction Line
Hot Gas Lines

## Slide 28
Compressor
Suction Line

## Slide 29
Unloaders

## Slide 30
Crank Case Heater

## Slide 31
Crank Case Heater

## Slide 32
Notes: Poll Title: When should the crankcase heaters be energized? https://www.polleverywhere.com/multiple_choice_polls/ZJNJcLfHkZjFrfVSNMMq6

## Slide 33
Oil Sight Glass

## Slide 34
Notes: Poll Title: The oil level in the sight glass will not change much over the course of an operating cycle. https://www.polleverywhere.com/multiple_choice_polls/RY8qZuXtDMBLeed6XVXA9

## Slide 35: Hand Pump for Adding Oil

## Slide 36
Notes: Poll Title: Refrigerant oil is specific to the refrigerant that is used in a refrigeration system. https://www.polleverywhere.com/multiple_choice_polls/EPll2Xm0gTo8JuqIAri3U

## Slide 37: Vacuum Pump Evacuating the System in Preparation for Charging
Vacuum Pump

## Slide 39
Liquid Line Solenoid Valve
Expansion Valve
Liquid Lines
Suction Line

## Slide 40: Electronic Expansion Valve Controllers

## Slide 41: A Refrigerant Sight Glass

## Slide 42
Notes: Poll Title: The green dots in the refrigerant sight glass will alternate between green and red during the Christmas holidays. https://www.polleverywhere.com/multiple_choice_polls/MVnMOf6dKOkRA9F5CgD13

## Slide 43: https://www.av8rdas.com/ebcx-workshop-series-16.html#EBCx16-4

## Slide 44: Typical Control Switches

## Slide 45: Adding Hot Gas Bypass
Hot Gas Solenoid
Hot Gas Regulator

## Slide 46
Hot Gas Bypass Lines
Hot Gas Solenoid Valve
Service Valve
Hot Gas Regulator

## Slide 47
Hot Gas Connections to the Evaporator