## Mixed Air Temp Calcs
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Notice: Facility Dynamics Engineering has provided this spreadsheet for educational purposes. We are fine with you using it as a starting point for your own spreadsheet performing a similar analysis or even using it as is. But you are using it at your own risk and FDE can not be responsible for the results you generate with it and the decisions you make as a result. Please check your work and use your head.
Click here to jump to the assumptions used in this spreadsheet and the instructions.
Click here to go to the equation behind the mathematics in the spreadsheet
Click here to jump to calculate the outdoor percentage based on outdoor air, return air, and supply air temperature
Click here to calculate the outdoor air temperature that results in a 32°F mixed air temperature
Click here to calculate the outdoor air temperature that results in a specific mixed air temperature of interest
Click here to calculate the mixed air temperature created by a known outdoor air percentage, a known outdoor air temperature, and a known return air temperature
Assumptions
1 | Enter appropriate data in the yellow cells in consistent units of measure …
… and read the results in the blue cells.
Note that the Supply Air Flow is the flow out of the mixed air plenum.
2 | These equations are derived from the steady flow energy equation, conservation of mass, the assumption that for an HVAC system, air can be treated as an ideal gas, and the assumption that for an HVAC system, the constant pressure specific heat of air can be assumed to be constant . See this blog post for more info.
Av8rDAS.Wordpress.Com - Economizers - The Physics of a Mixed Air Plenum
3 | Supply air temperature and mixed air temperature are used interchangably; the supply air temperature is the temperature leaving the mixing process.
4 | Any calculation involving mixed air/supply air temperature assumes complete mixing of the two air streams feeding into the process.
5 | Even though these equations were developed in the context of mixed air plenum, they actually could be applied to any node in an HVAC or HVAC utility system where two streams mix. The only constraint is that the units need to be consistent; if one flow is a percentage, then they all need to be a percentage; if one flow is in cubic meters per hour, then they all need to be in cubic meters per hour; if one temperature is in degrees celsius, then they all need to be in degrees celsius. For example, they could be used on a double duct box in which case the hot deck and cold deck would take the place of the return air and outdoor air and the blended stream coming out of the box would be the mixed air or supply air. Or they could be used to understand a fan powered box where the out door air would represent the primary air from the central system, the return air would be the return air entering the terminal unit, and the supply air/mixed air would be the blended air stream. On the water side of things, they could be used to predict what is going on where the bypass line in a variable flow primary secondary plant tees into the return line. If the flow was reversed in the bypass (chiller discharge water recirculating and blending with the plant return) the return air temperature would be analogous to the return water temperature, the outdoor air temperature would be analogous to the return water from the plant, and the supply air/mixed air woudl be analogous to the blended water temperature leaving the tee.
Back to Top
Steady Flow Energy Equation
On a Rate Basis, Given the Assumptions Listed in 2 Above, the Steady Flow Energy Equation can be Reduced to this Relationship
Back to Top
Outdoor percentage based on outdoor air, return air, and supply air temperature
|  | Mixed air temperature (MAT) = | 40 | °F | (This is the blended fluid stream leaving the node.)
|  | Return air temperature (RAT) = | 68 | °F | (This is the warm fluid stream entering the node.)
|  | Outdoor air temperature (OAT)= | -3 | °F | (This is the cold fluid stream entering the node.)
|  | Supply flow (SAF) = | 100000 | cfm | (This is the blended fluid stream leaving the node.)
|  | Outdoor air flow (OA Flow) = | 39436.6197 | cfm | (This is the cold fluid stream entering the node.)
|  | Outdoor air percentage = | 39.44% |  | (This is the cold fluid stream entering the node.)
|  | Return air flow (RA Flow) = | 60563.3803 | cfm | (This is the warm fluid stream entering the node.)
Back to Top
Outdoor air temperature that results in a 32°F mixed air temperature
This is simply a special case with the mixed air temperature set to 32°F
|  | Mixed air temperature (MAT) = | 32 | °F | (This is the blended fluid stream leaving the node.)
|  | Return air temperature (RAT) = | 68 | °F | (This is the warm fluid stream entering the node.)
|  | Supply flow (SAF) = | 100000 | cfm | (This is the blended fluid stream leaving the node.)
|  | Outdoor air flow (OA Flow) = | 25000 | cfm | (This is the cold fluid stream entering the node.)
|  | Outdoor air percentage = | 25% |  | (This is the cold fluid stream entering the node.)
|  | Return air flow (RA Flow) = | 75000 | cfm | (This is the warm fluid stream entering the node.)
|  | Outdoor air temperature (OAT)= | -76 | °F | (This is the cold fluid stream entering the node.)
Back to Top
Outdoor air temperature that results in a specific mixed air temperature of interest
This is simply a more general case of the preceeding equation
|  | Design mixed air temperature (MAT) = | 50 | °F | (This is the blended fluid stream leaving the node.)
|  | Return air temperature (RAT) = | 68 | °F | (This is the warm fluid stream entering the node.)
|  | Supply flow (SAF) = | 100000 | cfm | (This is the blended fluid stream leaving the node.)
|  | Outdoor air flow (OA Flow) = | 25000 | cfm | (This is the cold fluid stream entering the node.)
|  | Outdoor air percentage = | 25% |  | (This is the cold fluid stream entering the node.)
|  | Return air flow (RA Flow) = | 75000 | cfm | (This is the warm fluid stream entering the node.)
|  | Outdoor air temperature (OAT)= | -4 | °F | (This is the cold fluid stream entering the node.)
Back to Top
Mixed air temperature created by a known outdoor air percentage, a known outdoor air temperature, and a known return air temperature
|  | Return air temperature (RAT) = | 75 | °F | (This is the warm fluid stream entering the node.)
|  | Outdoor air temperature (OAT)= | 35 | °F | (This is the cold fluid stream entering the node.)
|  | Supply flow (SAF) = | 20000 | cfm | (This is the blended fluid stream leaving the node.)
|  | Outdoor air flow (OA Flow) = | 10000 | cfm | (This is the cold fluid stream entering the node.)
|  | Outdoor air percentage = | 50% |  | (This is the cold fluid stream entering the node.)
|  | Return air flow (RA Flow) = | 10000 | cfm | (This is the warm fluid stream entering the node.)
|  | Mixed air temperature (MAT) = | 55 | °F | (This is the blended fluid stream leaving the node.)
Back to Top