## Operating Point
Notice: Facility Dynamics Engineering has provided this spreadsheet for educational purposes. We are fine with you using it as a starting point for your own spreadsheet performing a similar analysis or even using it as is. But you are using it at your own risk and FDE can not be responsible for the results you generate with it and the decisions you make as a result. Please check your work and use your head.
Instructions for Generating an Operating Point Line on the Chart |  |  |  | Comments and Other Information
Step 1 | Set the friction rate in the orange cell to 30 to create a vertical flow line that extends from the bottom to the top of the chart. |  |  | The chart is for schedule 40 steel pipe specifically and would get you in the ball park for other types of pipe until: • You get into smaller line sizes (below 1”) where the dimensions of copper for a nominal pipe size make the velocities higher and thus the friction rates higher in terms of ft.w.c. per 100 ft. of pipe. • Steel will tend to be high relative to PVC and CPVC because it is rougher and because of the dimensions of plastic pipe relative to steel pipe for a given nominal pipe size.
Step 2 | Set the flow rate in the yellow cell to the flow you are interested in |  |  |  | You get into smaller line sizes (below 1”) where the dimensions of copper for a nominal pipe size make the velocities higher and thus the friction rates higher in terms of ft.w.c. per 100 ft. of pipe.
Step 3 | Using the Schedule 40 Standard Steel Chart on the green tab, "eyeball" estimate the friction rate required to get the red, dashed, horizontal friction rate line to cross the red, dashed, vertical flow line for the pipe size you are interested in (the colored diagnal lines with sizes on them). Manually tweak the friction rate value in the orange cell until the friction rate line crosses the line for the pipe size you are targeting at the point where the flow line crosses it to read the exact friction rate associated with the flow rate and line size you are interested in. |  |  |  | You change materials; steel will tend to be high relative to PVC and CPVC because it is rougher and because of the dimensions of plastic pipe relative to steel pipe for a given nominal pipe size.
The first time you open the chart, it is set to show the friction rate for an 8 inch pipe (the purple diagonal line on the chart) with 1,100 gpm flowing in it (the value in the yellow cell below). The friction rate is 1.8 ft.w.c. per 100 feet of pipe (the value in the orange cell below). |  |  |  | The link below will take you to a free download of the Bell and Gossett Syzer tool. This is another way to get the numbers (basically an electronic version of the plastic circular slide rule us older folks have in our desk drawer from back in the olden days). The reason I use the friction chart is that it gives a quicker visual of where you are relative to the other possibilities. The sizer tool is probably faster in terms of giving you a number. And it certainly is more flexible because of the number of parameters you can adjust, including the type of pipe, the fluid, its temperature, etc. and because it gives you a lot of other metrics like relative roughness, Reynolds number, etc.
To make the operating point lines and lables disappear, set the orange and yellow cells to 0
Note that the value in cell 8A needs to be bigger than 0 because of the log scales to get this to work
The lable and dot generator cells are just formulas that make the lables and lines on the chart and you should not need to do anything with them to get this to work.
Vertical Flow Rate Line Generator |  | Horizontal Friction Rate Line Generator |  | Note that if you page down on the web page, there is also a version of the Syzer tool that you can download as a smart phone app at the location this link takes you to.
Friction Rate, ft.w.c. per 100 linear feet of pipe | Design Flow Rate, gpm | Friction Rate Read from the Chart at the Design Flow Rate, ft.w.c. per 100 linear feet of pipe | Flow Rate, gpm
0.1 | 635 | 2.5 | 0.1
2.5 | 635 | 2.5 | 635
Lable Generator - | 635 gpm
Lable Generator - | 2.5 ft.w.c./100 ft.
Lable Generator - | Use the orange Operating Point tab to add a flow rate and friction rate line to this chart. The currently selected point is 635 gpm at 2.5 ft.w.c./100 ft.
Dot Generator
Friction Rate, ft.w.c. per 100 linear feet of pipe | Design Flow Rate, gpm
2.5 | 635
2.5 | 635

## Log Scale Guide
All that “logarithmic scale” really means is that the distance between one grid line and the next is a function of an exponent in contrast with a linear scale, where the distance between each grid line is an equal division relative to the others. So for instance, in the pipe friction chart x and y axis, the distance between 1 and 10 is divided into 9, non-equal intervals with each interval being proportional to a power of 10, as illustrated in the tables below.
This link will take you to a blog post that includes a more detailed discussion of logarithmic scales.
Log Scale Guide
| X from 1 to 10 | Expontent that 10 needs to be raised to to give you the number in the X column (log X) | X from 1 to 2 | Expontent that 10 needs to be raised to to give you the number in the X column (log X)
| 10 | 1 | 2 | 0.30103
| 9 | 0.95424 | 1.9 | 0.27875
| 8 | 0.90309 | 1.8 | 0.25527
| 7 | 0.8451 | 1.7 | 0.23045
| 6 | 0.77815 | 1.6 | 0.20412
| 5 | 0.69897 | 1.5 | 0.17609
| 4 | 0.60206 | 1.4 | 0.14613
| 3 | 0.47712 | 1.2 | 0.079181
| 2 | 0.30103 | 1.1 | 0.041393
| 1 | 0 | 1 | 0
For example:
| 101.000 = | 10 | 100.3010 = | 2
| 100.6990 = | 5 | 100.1761 = | 1.5
| 100.3010 = | 2 | 100.0414 = | 1.1
Log Scale Guide
| X | Percentage of the distance to X (Log X) | Percentage of the distance from 1 to 2
| 10 | 100%
| 9 | 95.42%
| 8 | 90.31%
| 7 | 84.51%
| 6 | 77.82%
| 5 | 69.9%
| 4 | 60.21%
| 3 | 47.71%
| 2 | 30.1% | 100%
| 1.9 | 27.88% | 92.6%
| 1.8 | 25.53% | 84.8%
| 1.7 | 23.04% | 76.55%
| 1.6 | 20.41% | 67.81%
| 1.5 | 17.61% | 58.5%
| 1.4 | 14.61% | 48.54%
| 1.3 | 11.39% | 37.85%
| 1.2 | 7.918% | 26.3%
| 1.1 | 4.139% | 13.75%
| 1 | 0% | 0%

## Steel Pipe - Flow vs. Loss
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2013-07-03 11:56
Project Name: | Pipe Friction Chart from ASHRAE Data
Project Number: | None
Engineer: | David
Assumptions
1 | I origianlly started to use data taken from the pipe friction chart published in the ASHRAE 2013 Handbook of Fundamentals, Chapter 22
But it was going to get labor intensive and did not lend itself to plotting a few points and then using the square law. You got dlose but not perfect, probably because of renolds number variations, etc.
So, was going to run the numbers manually using the Darcey Weisbach equation, etc. but found a software package that had all of that built in, so it paid for itself in the time it saved.
2 | Date for my charts was generated with PipeFlow Wizard
| 1/2" Schedule 40 |  |  | 10" Schedule 40 |  |  | 3/4" Schedule 40 |  |  | 1" Schedule 40 |  |  | 1-1/4" Schedule 40 |  |  | 1-1/2" Schedule 40 |  |  | 2" Shedule 40 |  |  | 2-1/2" Schedule 40 |  |  | 3" Schedule 40 |  |  | 4" Schedule 40 |  |  | 5" Shedule 40 |  |  | 6" Shedule 40 |  |  | 8" Shedule 40 |  |  | 12" Schedule 40 |  |  | 14" Shedule 40 |  |  | 16" Schedule 40 |  |  | 18" Schedule 40 |  |  | 20" Schedule 40 |  |  | 24" Shedule 40
| Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec
Point 1 | 0.57 | 0.502 | 0.602 | 1015 | 0.501 | 4.13 | 1.23 | 0.501 | 0.74 | 2.39 | 0.501 | 0.887 | 5.05 | 0.5 | 1.083 | 7.68 | 0.501 | 1.21 | 15.1 | 0.501 | 1.444 | 24.35 | 0.5 | 1.632 | 43.7 | 0.501 | 1.897 | 90 | 0.497 | 2.268 | 165 | 0.501 | 2.646 | 269 | 0.502 | 2.987 | 556 | 0.501 | 3.566 | 1610 | 0.501 | 4.615 | 2065 | 0.5 | 4.898 | 2935 | 0.501 | 5.329 | 4000 | 0.501 | 5.737 | 5325 | 0.502 | 6.147 | 8625 | 0.5 | 6.884
Point 2 | 1.2 | 1.86 | 1.267 | 1800 | 1.492 | 7.324 | 2.4 | 1.624 | 1.444 | 5 | 1.868 | 1.856 | 10 | 1.713 | 2.145 | 16 | 1.896 | 2.521 | 30 | 1.757 | 2.868 | 50 | 1.879 | 3.351 | 80 | 1.534 | 3.472 | 180 | 1.814 | 4.536 | 300 | 1.537 | 4.811 | 500 | 1.613 | 5.553 | 1000 | 1.522 | 6.413 | 3000 | 1.646 | 8.599 | 3600 | 1.449 | 8.538 | 4800 | 1.285 | 8.715 | 6800 | 1.388 | 9.753 | 9000 | 1.377 | 10.389 | 14000 | 1.274 | 11.173
Point 3 | 1.8 | 3.833 | 1.901 | 2700 | 3.26 | 10.985 | 3.6 | 3.371 | 2.166 | 7.5 | 3.916 | 2.784 | 15 | 3.613 | 3.218 | 24 | 4.02 | 3.782 | 45 | 3.744 | 4.303 | 75 | 4.024 | 5.026 | 120 | 3.29 | 5.208 | 270 | 3.919 | 6.805 | 450 | 3.327 | 7.217 | 750 | 3.503 | 8.329 | 1500 | 3.317 | 9.62 | 4500 | 3.608 | 12.898 | 5400 | 3.177 | 12.807 | 7200 | 2.818 | 13.072 | 10200 | 3.049 | 14.63 | 13500 | 3.03 | 15.583 | 21000 | 2.806 | 16.76
Point 4 | 2.4 | 6.456 | 2.534 | 3600 | 5.702 | 14.647 | 4.8 | 5.705 | 2.888 | 10 | 6.671 | 3.712 | 20 | 6.179 | 4.29 | 32 | 6.901 | 5.043 | 60 | 6.447 | 5.737 | 100 | 6.95 | 6.701 | 160 | 5.688 | 6.944 | 360 | 6.806 | 9.073 | 600 | 5.785 | 9.622 | 1000 | 6.105 | 11.105 | 2000 | 5.792 | 12.826 | 6000 | 6.323 | 17.198 | 7200 | 5.567 | 17.076 | 9600 | 4.939 | 17.429 | 13600 | 5.351 | 19.507 | 18000 | 5.321 | 20.777 | 28000 | 4.93 | 22.346
Point 5 | 3 | 9.72 | 3.168 | 4500 | 8.818 | 18.309 | 6 | 8.618 | 3.61 | 12.5 | 10.127 | 4.64 | 25 | 9.406 | 5.363 | 40 | 10.533 | 6.304 | 75 | 9.861 | 7.171 | 125 | 10.653 | 8.376 | 200 | 8.725 | 8.68 | 450 | 10.475 | 11.341 | 750 | 8.909 | 12.028 | 1250 | 9.416 | 13.882 | 2500 | 8.946 | 16.033 | 7500 | 9.789 | 21.497 | 9000 | 8.619 | 21.345 | 12000 | 7.648 | 21.787 | 17000 | 8.292 | 24.384 | 22500 | 8.249 | 25.972 | 35000 | 7.647 | 27.933
Point 6 | 3.6 | 13.62 | 3.801 | 5400 | 12.606 | 21.971 | 7.2 | 12.106 | 4.332 | 15 | 14.279 | 5.568 | 30 | 13.291 | 6.435 | 48 | 14.914 | 7.564 | 90 | 13.985 | 8.605 | 150 | 15.134 | 10.052 | 240 | 12.4 | 10.416 | 540 | 14.923 | 13.609 | 900 | 12.7 | 14.433 | 1500 | 13.437 | 16.658 | 3000 | 12.779 | 19.24 | 9000 | 14.008 | 25.797 | 10800 | 12.333 | 25.614 | 14400 | 10.945 | 26.144 | 20400 | 11.872 | 29.26 | 27000 | 11.815 | 31.166 | 42000 | 10.956 | 33.52
Point 7 | 4.2 | 18.153 | 4.435 | 6300 | 17.067 | 25.633 | 8.4 | 16.168 | 5.054 | 17.5 | 19.127 | 6.496 | 35 | 17.834 | 7.508 | 56 | 20.044 | 8.825 | 105 | 18.817 | 10.039 | 175 | 20.39 | 11.727 | 280 | 16.712 | 12.152 | 630 | 20.151 | 15.878 | 1050 | 17.155 | 16.839 | 1750 | 18.166 | 19.434 | 3500 | 17.29 | 22.446 | 10500 | 18.978 | 30.096 | 12600 | 16.708 | 29.883 | 16800 | 14.829 | 30.501 | 23800 | 16.092 | 34.137 | 31500 | 16.018 | 36.361 | 49000 | 14.858 | 39.106
Point 8 | 4.8 | 23.317 | 5.068 | 7200 | 22.201 | 29.295 | 9.6 | 20.801 | 5.776 | 20 | 24.669 | 7.425 | 40 | 23.032 | 8.58 | 64 | 25.92 | 10.086 | 120 | 24.358 | 11.473 | 200 | 26.422 | 13.402 | 320 | 21.662 | 13.888 | 720 | 26.157 | 18.146 | 1200 | 22.276 | 19.244 | 2000 | 23.604 | 22.21 | 4000 | 22.48 | 25.653 | 12000 | 24.699 | 34.396 | 14400 | 21.745 | 34.152 | 19200 | 19.301 | 34.858 | 27200 | 20.952 | 39.014 | 36000 | 20.859 | 41.555 | 56000 | 19.351 | 44.693
Point 9 | 5.4 | 29.11 | 5.702 | 8100 | 28.008 | 32.956 | 10.8 | 26.004 | 6.498 | 22.5 | 30.905 | 8.353 | 45 | 28.887 | 9.653 | 72 | 32.543 | 11.347 | 135 | 30.607 | 12.908 | 225 | 33.228 | 15.078 | 360 | 27.248 | 15.624 | 810 | 32.943 | 20.414 | 1350 | 28.062 | 21.65 | 2250 | 29.751 | 24.987 | 4500 | 28.348 | 28.859 | 13500 | 31.172 | 38.695 | 16200 | 27.443 | 38.421 | 21600 | 24.36 | 39.216 | 30600 | 26.451 | 43.891 | 40500 | 26.337 | 46.749 | 63000 | 24.437 | 50.28
Point 10 | 6 | 35.533 | 6.335 | 9000 | 34.486 | 36.618 | 12 | 31.778 | 7.22 | 25 | 37.833 | 9.281 | 50 | 35.396 | 10.725 | 80 | 39.912 | 12.607 | 150 | 37.564 | 14.342 | 250 | 40.81 | 16.753 | 400 | 33.471 | 17.36 | 900 | 40.508 | 22.682 | 1500 | 34.514 | 24.055 | 2500 | 36.607 | 27.763 | 5000 | 34.894 | 32.066 | 15000 | 38.397 | 42.995 | 18000 | 33.802 | 42.69 | 24000 | 30.007 | 43.573 | 34000 | 32.589 | 48.767 | 45000 | 32.452 | 51.944 | 70000 | 30.114 | 55.866
PipeFlow Calcualtion Results
Point 1 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 0.57 | gpm-USA | Flow | 1015 | gpm-USA | Flow | 1.23 | gpm-USA | Flow | 2.39 | gpm-USA | Flow | 5.05 | gpm-USA | Flow | 7.68 | gpm-USA | Flow | 15.1 | gpm-USA | Flow | 24.35 | gpm-USA | Flow | 43.7 | gpm-USA | Flow | 90 | gpm-USA | Flow | 165 | gpm-USA | Flow | 269 | gpm-USA | Flow | 556 | gpm-USA | Flow | 1610 | gpm-USA | Flow | 2065 | gpm-USA | Flow | 2935 | gpm-USA | Flow | 4000 | gpm-USA | Flow | 5325 | gpm-USA | Flow | 8625 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Critical |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 2887 |  | Reynold's number | 319082 |  | Reynold's number | 4702 |  | Reynold's number | 7177 |  | Reynold's number | 11527 |  | Reynold's number | 15026 |  | Reynold's number | 23011 |  | Reynold's number | 31066 |  | Reynold's number | 44867 |  | Reynold's number | 70416 |  | Reynold's number | 102981 |  | Reynold's number | 139710 |  | Reynold's number | 219443 |  | Reynold's number | 424814 |  | Reynold's number | 495631 |  | Reynold's number | 616342 |  | Reynold's number | 746612 |  | Reynold's number | 891639 |  | Reynold's number | 1200865
| Friction factor | 0.046 |  | Friction factor | 0.016 |  | Friction factor | 0.04 |  | Friction factor | 0.036 |  | Friction factor | 0.032 |  | Friction factor | 0.03 |  | Friction factor | 0.027 |  | Friction factor | 0.025 |  | Friction factor | 0.023 |  | Friction factor | 0.021 |  | Friction factor | 0.019 |  | Friction factor | 0.018 |  | Friction factor | 0.017 |  | Friction factor | 0.015 |  | Friction factor | 0.015 |  | Friction factor | 0.014 |  | Friction factor | 0.014 |  | Friction factor | 0.013 |  | Friction factor | 0.013
| Fluid velocity | 0.602 | ft/s | Fluid velocity | 4.13 | ft/s | Fluid velocity | 0.74 | ft/s | Fluid velocity | 0.887 | ft/s | Fluid velocity | 1.083 | ft/s | Fluid velocity | 1.21 | ft/s | Fluid velocity | 1.444 | ft/s | Fluid velocity | 1.632 | ft/s | Fluid velocity | 1.897 | ft/s | Fluid velocity | 2.268 | ft/s | Fluid velocity | 2.646 | ft/s | Fluid velocity | 2.987 | ft/s | Fluid velocity | 3.566 | ft/s | Fluid velocity | 4.615 | ft/s | Fluid velocity | 4.898 | ft/s | Fluid velocity | 5.329 | ft/s | Fluid velocity | 5.737 | ft/s | Fluid velocity | 6.147 | ft/s | Fluid velocity | 6.884 | ft/s
| Pressure drop | 0.502 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.5 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.5 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.497 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.502 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.5 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.501 | ft hd | Pressure drop | 0.502 | ft hd | Pressure drop | 0.5 | ft hd
Point 2 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 1.2 | gpm-USA | Flow | 1800 | gpm-USA | Flow | 2.4 | gpm-USA | Flow | 5 | gpm-USA | Flow | 10 | gpm-USA | Flow | 16 | gpm-USA | Flow | 30 | gpm-USA | Flow | 50 | gpm-USA | Flow | 80 | gpm-USA | Flow | 180 | gpm-USA | Flow | 300 | gpm-USA | Flow | 500 | gpm-USA | Flow | 1000 | gpm-USA | Flow | 3000 | gpm-USA | Flow | 3600 | gpm-USA | Flow | 4800 | gpm-USA | Flow | 6800 | gpm-USA | Flow | 9000 | gpm-USA | Flow | 14000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 6077 |  | Reynold's number | 565860 |  | Reynold's number | 9175 |  | Reynold's number | 15014 |  | Reynold's number | 22826 |  | Reynold's number | 31304 |  | Reynold's number | 45718 |  | Reynold's number | 63790 |  | Reynold's number | 82137 |  | Reynold's number | 140833 |  | Reynold's number | 187237 |  | Reynold's number | 259683 |  | Reynold's number | 394682 |  | Reynold's number | 791579 |  | Reynold's number | 864054 |  | Reynold's number | 1007986 |  | Reynold's number | 1269241 |  | Reynold's number | 1506996 |  | Reynold's number | 1949231
| Friction factor | 0.039 |  | Friction factor | 0.015 |  | Friction factor | 0.034 |  | Friction factor | 0.031 |  | Friction factor | 0.028 |  | Friction factor | 0.026 |  | Friction factor | 0.024 |  | Friction factor | 0.022 |  | Friction factor | 0.021 |  | Friction factor | 0.019 |  | Friction factor | 0.018 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.014 |  | Friction factor | 0.014 |  | Friction factor | 0.014 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012
| Fluid velocity | 1.267 | ft/s | Fluid velocity | 7.324 | ft/s | Fluid velocity | 1.444 | ft/s | Fluid velocity | 1.856 | ft/s | Fluid velocity | 2.145 | ft/s | Fluid velocity | 2.521 | ft/s | Fluid velocity | 2.868 | ft/s | Fluid velocity | 3.351 | ft/s | Fluid velocity | 3.472 | ft/s | Fluid velocity | 4.536 | ft/s | Fluid velocity | 4.811 | ft/s | Fluid velocity | 5.553 | ft/s | Fluid velocity | 6.413 | ft/s | Fluid velocity | 8.599 | ft/s | Fluid velocity | 8.538 | ft/s | Fluid velocity | 8.715 | ft/s | Fluid velocity | 9.753 | ft/s | Fluid velocity | 10.389 | ft/s | Fluid velocity | 11.173 | ft/s
| Pressure drop | 1.86 | ft hd | Pressure drop | 1.492 | ft hd | Pressure drop | 1.624 | ft hd | Pressure drop | 1.868 | ft hd | Pressure drop | 1.713 | ft hd | Pressure drop | 1.896 | ft hd | Pressure drop | 1.757 | ft hd | Pressure drop | 1.879 | ft hd | Pressure drop | 1.534 | ft hd | Pressure drop | 1.814 | ft hd | Pressure drop | 1.537 | ft hd | Pressure drop | 1.613 | ft hd | Pressure drop | 1.522 | ft hd | Pressure drop | 1.646 | ft hd | Pressure drop | 1.449 | ft hd | Pressure drop | 1.285 | ft hd | Pressure drop | 1.388 | ft hd | Pressure drop | 1.377 | ft hd | Pressure drop | 1.274 | ft hd
Point 3 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 1.8 | gpm-USA | Flow | 2700 | gpm-USA | Flow | 3.6 | gpm-USA | Flow | 7.5 | gpm-USA | Flow | 15 | gpm-USA | Flow | 24 | gpm-USA | Flow | 45 | gpm-USA | Flow | 75 | gpm-USA | Flow | 120 | gpm-USA | Flow | 270 | gpm-USA | Flow | 450 | gpm-USA | Flow | 750 | gpm-USA | Flow | 1500 | gpm-USA | Flow | 4500 | gpm-USA | Flow | 5400 | gpm-USA | Flow | 7200 | gpm-USA | Flow | 10200 | gpm-USA | Flow | 13500 | gpm-USA | Flow | 21000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 9116 |  | Reynold's number | 848791 |  | Reynold's number | 13762 |  | Reynold's number | 22521 |  | Reynold's number | 34239 |  | Reynold's number | 46956 |  | Reynold's number | 68577 |  | Reynold's number | 95685 |  | Reynold's number | 123206 |  | Reynold's number | 211249 |  | Reynold's number | 280856 |  | Reynold's number | 389525 |  | Reynold's number | 592023 |  | Reynold's number | 1187368 |  | Reynold's number | 1296081 |  | Reynold's number | 1511979 |  | Reynold's number | 1903861 |  | Reynold's number | 2260494 |  | Reynold's number | 2923846
| Friction factor | 0.035 |  | Friction factor | 0.015 |  | Friction factor | 0.032 |  | Friction factor | 0.028 |  | Friction factor | 0.026 |  | Friction factor | 0.024 |  | Friction factor | 0.022 |  | Friction factor | 0.021 |  | Friction factor | 0.02 |  | Friction factor | 0.018 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.015 |  | Friction factor | 0.014 |  | Friction factor | 0.014 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012
| Fluid velocity | 1.901 | ft/s | Fluid velocity | 10.985 | ft/s | Fluid velocity | 2.166 | ft/s | Fluid velocity | 2.784 | ft/s | Fluid velocity | 3.218 | ft/s | Fluid velocity | 3.782 | ft/s | Fluid velocity | 4.303 | ft/s | Fluid velocity | 5.026 | ft/s | Fluid velocity | 5.208 | ft/s | Fluid velocity | 6.805 | ft/s | Fluid velocity | 7.217 | ft/s | Fluid velocity | 8.329 | ft/s | Fluid velocity | 9.62 | ft/s | Fluid velocity | 12.898 | ft/s | Fluid velocity | 12.807 | ft/s | Fluid velocity | 13.072 | ft/s | Fluid velocity | 14.63 | ft/s | Fluid velocity | 15.583 | ft/s | Fluid velocity | 16.76 | ft/s
| Pressure drop | 3.833 | ft hd | Pressure drop | 3.26 | ft hd | Pressure drop | 3.371 | ft hd | Pressure drop | 3.916 | ft hd | Pressure drop | 3.613 | ft hd | Pressure drop | 4.02 | ft hd | Pressure drop | 3.744 | ft hd | Pressure drop | 4.024 | ft hd | Pressure drop | 3.29 | ft hd | Pressure drop | 3.919 | ft hd | Pressure drop | 3.327 | ft hd | Pressure drop | 3.503 | ft hd | Pressure drop | 3.317 | ft hd | Pressure drop | 3.608 | ft hd | Pressure drop | 3.177 | ft hd | Pressure drop | 2.818 | ft hd | Pressure drop | 3.049 | ft hd | Pressure drop | 3.03 | ft hd | Pressure drop | 2.806 | ft hd
Point 4 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 2.4 | gpm-USA | Flow | 3600 | gpm-USA | Flow | 4.8 | gpm-USA | Flow | 10 | gpm-USA | Flow | 20 | gpm-USA | Flow | 32 | gpm-USA | Flow | 60 | gpm-USA | Flow | 100 | gpm-USA | Flow | 160 | gpm-USA | Flow | 360 | gpm-USA | Flow | 600 | gpm-USA | Flow | 1000 | gpm-USA | Flow | 2000 | gpm-USA | Flow | 6000 | gpm-USA | Flow | 7200 | gpm-USA | Flow | 9600 | gpm-USA | Flow | 13600 | gpm-USA | Flow | 18000 | gpm-USA | Flow | 28000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 12154 |  | Reynold's number | 1131721 |  | Reynold's number | 18349 |  | Reynold's number | 30028 |  | Reynold's number | 45652 |  | Reynold's number | 62608 |  | Reynold's number | 91436 |  | Reynold's number | 127580 |  | Reynold's number | 164274 |  | Reynold's number | 281665 |  | Reynold's number | 374475 |  | Reynold's number | 519366 |  | Reynold's number | 789364 |  | Reynold's number | 1583158 |  | Reynold's number | 1728108 |  | Reynold's number | 2015972 |  | Reynold's number | 2538481 |  | Reynold's number | 3013992 |  | Reynold's number | 3898461
| Friction factor | 0.034 |  | Friction factor | 0.014 |  | Friction factor | 0.03 |  | Friction factor | 0.027 |  | Friction factor | 0.025 |  | Friction factor | 0.023 |  | Friction factor | 0.022 |  | Friction factor | 0.02 |  | Friction factor | 0.019 |  | Friction factor | 0.018 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.015 |  | Friction factor | 0.014 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012 |  | Friction factor | 0.012
| Fluid velocity | 2.534 | ft/s | Fluid velocity | 14.647 | ft/s | Fluid velocity | 2.888 | ft/s | Fluid velocity | 3.712 | ft/s | Fluid velocity | 4.29 | ft/s | Fluid velocity | 5.043 | ft/s | Fluid velocity | 5.737 | ft/s | Fluid velocity | 6.701 | ft/s | Fluid velocity | 6.944 | ft/s | Fluid velocity | 9.073 | ft/s | Fluid velocity | 9.622 | ft/s | Fluid velocity | 11.105 | ft/s | Fluid velocity | 12.826 | ft/s | Fluid velocity | 17.198 | ft/s | Fluid velocity | 17.076 | ft/s | Fluid velocity | 17.429 | ft/s | Fluid velocity | 19.507 | ft/s | Fluid velocity | 20.777 | ft/s | Fluid velocity | 22.346 | ft/s
| Pressure drop | 6.456 | ft hd | Pressure drop | 5.702 | ft hd | Pressure drop | 5.705 | ft hd | Pressure drop | 6.671 | ft hd | Pressure drop | 6.179 | ft hd | Pressure drop | 6.901 | ft hd | Pressure drop | 6.447 | ft hd | Pressure drop | 6.95 | ft hd | Pressure drop | 5.688 | ft hd | Pressure drop | 6.806 | ft hd | Pressure drop | 5.785 | ft hd | Pressure drop | 6.105 | ft hd | Pressure drop | 5.792 | ft hd | Pressure drop | 6.323 | ft hd | Pressure drop | 5.567 | ft hd | Pressure drop | 4.939 | ft hd | Pressure drop | 5.351 | ft hd | Pressure drop | 5.321 | ft hd | Pressure drop | 4.93 | ft hd
Point 5 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 3 | gpm-USA | Flow | 4500 | gpm-USA | Flow | 6 | gpm-USA | Flow | 12.5 | gpm-USA | Flow | 25 | gpm-USA | Flow | 40 | gpm-USA | Flow | 75 | gpm-USA | Flow | 125 | gpm-USA | Flow | 200 | gpm-USA | Flow | 450 | gpm-USA | Flow | 750 | gpm-USA | Flow | 1250 | gpm-USA | Flow | 2500 | gpm-USA | Flow | 7500 | gpm-USA | Flow | 9000 | gpm-USA | Flow | 12000 | gpm-USA | Flow | 17000 | gpm-USA | Flow | 22500 | gpm-USA | Flow | 35000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 15193 |  | Reynold's number | 1414651 |  | Reynold's number | 22937 |  | Reynold's number | 37535 |  | Reynold's number | 57064 |  | Reynold's number | 78260 |  | Reynold's number | 114295 |  | Reynold's number | 159475 |  | Reynold's number | 205343 |  | Reynold's number | 352082 |  | Reynold's number | 468093 |  | Reynold's number | 649208 |  | Reynold's number | 986705 |  | Reynold's number | 1978947 |  | Reynold's number | 2160135 |  | Reynold's number | 2519965 |  | Reynold's number | 3173102 |  | Reynold's number | 3767490 |  | Reynold's number | 4873076
| Friction factor | 0.032 |  | Friction factor | 0.014 |  | Friction factor | 0.029 |  | Friction factor | 0.026 |  | Friction factor | 0.024 |  | Friction factor | 0.023 |  | Friction factor | 0.021 |  | Friction factor | 0.02 |  | Friction factor | 0.019 |  | Friction factor | 0.018 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.015 |  | Friction factor | 0.014 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012 |  | Friction factor | 0.012
| Fluid velocity | 3.168 | ft/s | Fluid velocity | 18.309 | ft/s | Fluid velocity | 3.61 | ft/s | Fluid velocity | 4.64 | ft/s | Fluid velocity | 5.363 | ft/s | Fluid velocity | 6.304 | ft/s | Fluid velocity | 7.171 | ft/s | Fluid velocity | 8.376 | ft/s | Fluid velocity | 8.68 | ft/s | Fluid velocity | 11.341 | ft/s | Fluid velocity | 12.028 | ft/s | Fluid velocity | 13.882 | ft/s | Fluid velocity | 16.033 | ft/s | Fluid velocity | 21.497 | ft/s | Fluid velocity | 21.345 | ft/s | Fluid velocity | 21.787 | ft/s | Fluid velocity | 24.384 | ft/s | Fluid velocity | 25.972 | ft/s | Fluid velocity | 27.933 | ft/s
| Pressure drop | 9.72 | ft hd | Pressure drop | 8.818 | ft hd | Pressure drop | 8.618 | ft hd | Pressure drop | 10.127 | ft hd | Pressure drop | 9.406 | ft hd | Pressure drop | 10.533 | ft hd | Pressure drop | 9.861 | ft hd | Pressure drop | 10.653 | ft hd | Pressure drop | 8.725 | ft hd | Pressure drop | 10.475 | ft hd | Pressure drop | 8.909 | ft hd | Pressure drop | 9.416 | ft hd | Pressure drop | 8.946 | ft hd | Pressure drop | 9.789 | ft hd | Pressure drop | 8.619 | ft hd | Pressure drop | 7.648 | ft hd | Pressure drop | 8.292 | ft hd | Pressure drop | 8.249 | ft hd | Pressure drop | 7.647 | ft hd
Point 6 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 3.6 | gpm-USA | Flow | 5400 | gpm-USA | Flow | 7.2 | gpm-USA | Flow | 15 | gpm-USA | Flow | 30 | gpm-USA | Flow | 48 | gpm-USA | Flow | 90 | gpm-USA | Flow | 150 | gpm-USA | Flow | 240 | gpm-USA | Flow | 540 | gpm-USA | Flow | 900 | gpm-USA | Flow | 1500 | gpm-USA | Flow | 3000 | gpm-USA | Flow | 9000 | gpm-USA | Flow | 10800 | gpm-USA | Flow | 14400 | gpm-USA | Flow | 20400 | gpm-USA | Flow | 27000 | gpm-USA | Flow | 42000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 18231 |  | Reynold's number | 1697581 |  | Reynold's number | 27524 |  | Reynold's number | 45042 |  | Reynold's number | 68477 |  | Reynold's number | 93912 |  | Reynold's number | 137153 |  | Reynold's number | 191370 |  | Reynold's number | 246411 |  | Reynold's number | 422498 |  | Reynold's number | 561712 |  | Reynold's number | 779049 |  | Reynold's number | 1184046 |  | Reynold's number | 2374737 |  | Reynold's number | 2592162 |  | Reynold's number | 3023958 |  | Reynold's number | 3807722 |  | Reynold's number | 4520988 |  | Reynold's number | 5847692
| Friction factor | 0.031 |  | Friction factor | 0.014 |  | Friction factor | 0.029 |  | Friction factor | 0.026 |  | Friction factor | 0.024 |  | Friction factor | 0.023 |  | Friction factor | 0.021 |  | Friction factor | 0.02 |  | Friction factor | 0.019 |  | Friction factor | 0.017 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.015 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012 |  | Friction factor | 0.012
| Fluid velocity | 3.801 | ft/s | Fluid velocity | 21.971 | ft/s | Fluid velocity | 4.332 | ft/s | Fluid velocity | 5.568 | ft/s | Fluid velocity | 6.435 | ft/s | Fluid velocity | 7.564 | ft/s | Fluid velocity | 8.605 | ft/s | Fluid velocity | 10.052 | ft/s | Fluid velocity | 10.416 | ft/s | Fluid velocity | 13.609 | ft/s | Fluid velocity | 14.433 | ft/s | Fluid velocity | 16.658 | ft/s | Fluid velocity | 19.24 | ft/s | Fluid velocity | 25.797 | ft/s | Fluid velocity | 25.614 | ft/s | Fluid velocity | 26.144 | ft/s | Fluid velocity | 29.26 | ft/s | Fluid velocity | 31.166 | ft/s | Fluid velocity | 33.52 | ft/s
| Pressure drop | 13.62 | ft hd | Pressure drop | 12.606 | ft hd | Pressure drop | 12.106 | ft hd | Pressure drop | 14.279 | ft hd | Pressure drop | 13.291 | ft hd | Pressure drop | 14.914 | ft hd | Pressure drop | 13.985 | ft hd | Pressure drop | 15.134 | ft hd | Pressure drop | 12.4 | ft hd | Pressure drop | 14.923 | ft hd | Pressure drop | 12.7 | ft hd | Pressure drop | 13.437 | ft hd | Pressure drop | 12.779 | ft hd | Pressure drop | 14.008 | ft hd | Pressure drop | 12.333 | ft hd | Pressure drop | 10.945 | ft hd | Pressure drop | 11.872 | ft hd | Pressure drop | 11.815 | ft hd | Pressure drop | 10.956 | ft hd
Point 7 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 4.2 | gpm-USA | Flow | 6300 | gpm-USA | Flow | 8.4 | gpm-USA | Flow | 17.5 | gpm-USA | Flow | 35 | gpm-USA | Flow | 56 | gpm-USA | Flow | 105 | gpm-USA | Flow | 175 | gpm-USA | Flow | 280 | gpm-USA | Flow | 630 | gpm-USA | Flow | 1050 | gpm-USA | Flow | 1750 | gpm-USA | Flow | 3500 | gpm-USA | Flow | 10500 | gpm-USA | Flow | 12600 | gpm-USA | Flow | 16800 | gpm-USA | Flow | 23800 | gpm-USA | Flow | 31500 | gpm-USA | Flow | 49000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 21270 |  | Reynold's number | 1980512 |  | Reynold's number | 32111 |  | Reynold's number | 52549 |  | Reynold's number | 79890 |  | Reynold's number | 109564 |  | Reynold's number | 160012 |  | Reynold's number | 223265 |  | Reynold's number | 287480 |  | Reynold's number | 492914 |  | Reynold's number | 655331 |  | Reynold's number | 908891 |  | Reynold's number | 1381387 |  | Reynold's number | 2770526 |  | Reynold's number | 3024189 |  | Reynold's number | 3527951 |  | Reynold's number | 4442342 |  | Reynold's number | 5274486 |  | Reynold's number | 6822307
| Friction factor | 0.031 |  | Friction factor | 0.014 |  | Friction factor | 0.028 |  | Friction factor | 0.026 |  | Friction factor | 0.023 |  | Friction factor | 0.022 |  | Friction factor | 0.021 |  | Friction factor | 0.02 |  | Friction factor | 0.019 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.016 |  | Friction factor | 0.015 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012 |  | Friction factor | 0.012
| Fluid velocity | 4.435 | ft/s | Fluid velocity | 25.633 | ft/s | Fluid velocity | 5.054 | ft/s | Fluid velocity | 6.496 | ft/s | Fluid velocity | 7.508 | ft/s | Fluid velocity | 8.825 | ft/s | Fluid velocity | 10.039 | ft/s | Fluid velocity | 11.727 | ft/s | Fluid velocity | 12.152 | ft/s | Fluid velocity | 15.878 | ft/s | Fluid velocity | 16.839 | ft/s | Fluid velocity | 19.434 | ft/s | Fluid velocity | 22.446 | ft/s | Fluid velocity | 30.096 | ft/s | Fluid velocity | 29.883 | ft/s | Fluid velocity | 30.501 | ft/s | Fluid velocity | 34.137 | ft/s | Fluid velocity | 36.361 | ft/s | Fluid velocity | 39.106 | ft/s
| Pressure drop | 18.153 | ft hd | Pressure drop | 17.067 | ft hd | Pressure drop | 16.168 | ft hd | Pressure drop | 19.127 | ft hd | Pressure drop | 17.834 | ft hd | Pressure drop | 20.044 | ft hd | Pressure drop | 18.817 | ft hd | Pressure drop | 20.39 | ft hd | Pressure drop | 16.712 | ft hd | Pressure drop | 20.151 | ft hd | Pressure drop | 17.155 | ft hd | Pressure drop | 18.166 | ft hd | Pressure drop | 17.29 | ft hd | Pressure drop | 18.978 | ft hd | Pressure drop | 16.708 | ft hd | Pressure drop | 14.829 | ft hd | Pressure drop | 16.092 | ft hd | Pressure drop | 16.018 | ft hd | Pressure drop | 14.858 | ft hd
Point 8 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 4.8 | gpm-USA | Flow | 7200 | gpm-USA | Flow | 9.6 | gpm-USA | Flow | 20 | gpm-USA | Flow | 40 | gpm-USA | Flow | 64 | gpm-USA | Flow | 120 | gpm-USA | Flow | 200 | gpm-USA | Flow | 320 | gpm-USA | Flow | 720 | gpm-USA | Flow | 1200 | gpm-USA | Flow | 2000 | gpm-USA | Flow | 4000 | gpm-USA | Flow | 12000 | gpm-USA | Flow | 14400 | gpm-USA | Flow | 19200 | gpm-USA | Flow | 27200 | gpm-USA | Flow | 36000 | gpm-USA | Flow | 56000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 24308 |  | Reynold's number | 2263442 |  | Reynold's number | 36699 |  | Reynold's number | 60056 |  | Reynold's number | 91303 |  | Reynold's number | 125216 |  | Reynold's number | 182871 |  | Reynold's number | 255161 |  | Reynold's number | 328548 |  | Reynold's number | 563331 |  | Reynold's number | 748949 |  | Reynold's number | 1038733 |  | Reynold's number | 1578728 |  | Reynold's number | 3166316 |  | Reynold's number | 3456216 |  | Reynold's number | 4031944 |  | Reynold's number | 5076963 |  | Reynold's number | 6027984 |  | Reynold's number | 7796922
| Friction factor | 0.03 |  | Friction factor | 0.014 |  | Friction factor | 0.028 |  | Friction factor | 0.025 |  | Friction factor | 0.023 |  | Friction factor | 0.022 |  | Friction factor | 0.021 |  | Friction factor | 0.019 |  | Friction factor | 0.018 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.016 |  | Friction factor | 0.015 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012 |  | Friction factor | 0.012 |  | Friction factor | 0.012
| Fluid velocity | 5.068 | ft/s | Fluid velocity | 29.295 | ft/s | Fluid velocity | 5.776 | ft/s | Fluid velocity | 7.425 | ft/s | Fluid velocity | 8.58 | ft/s | Fluid velocity | 10.086 | ft/s | Fluid velocity | 11.473 | ft/s | Fluid velocity | 13.402 | ft/s | Fluid velocity | 13.888 | ft/s | Fluid velocity | 18.146 | ft/s | Fluid velocity | 19.244 | ft/s | Fluid velocity | 22.21 | ft/s | Fluid velocity | 25.653 | ft/s | Fluid velocity | 34.396 | ft/s | Fluid velocity | 34.152 | ft/s | Fluid velocity | 34.858 | ft/s | Fluid velocity | 39.014 | ft/s | Fluid velocity | 41.555 | ft/s | Fluid velocity | 44.693 | ft/s
| Pressure drop | 23.317 | ft hd | Pressure drop | 22.201 | ft hd | Pressure drop | 20.801 | ft hd | Pressure drop | 24.669 | ft hd | Pressure drop | 23.032 | ft hd | Pressure drop | 25.92 | ft hd | Pressure drop | 24.358 | ft hd | Pressure drop | 26.422 | ft hd | Pressure drop | 21.662 | ft hd | Pressure drop | 26.157 | ft hd | Pressure drop | 22.276 | ft hd | Pressure drop | 23.604 | ft hd | Pressure drop | 22.48 | ft hd | Pressure drop | 24.699 | ft hd | Pressure drop | 21.745 | ft hd | Pressure drop | 19.301 | ft hd | Pressure drop | 20.952 | ft hd | Pressure drop | 20.859 | ft hd | Pressure drop | 19.351 | ft hd
Point 9 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 5.4 | gpm-USA | Flow | 8100 | gpm-USA | Flow | 10.8 | gpm-USA | Flow | 22.5 | gpm-USA | Flow | 45 | gpm-USA | Flow | 72 | gpm-USA | Flow | 135 | gpm-USA | Flow | 225 | gpm-USA | Flow | 360 | gpm-USA | Flow | 810 | gpm-USA | Flow | 1350 | gpm-USA | Flow | 2250 | gpm-USA | Flow | 4500 | gpm-USA | Flow | 13500 | gpm-USA | Flow | 16200 | gpm-USA | Flow | 21600 | gpm-USA | Flow | 30600 | gpm-USA | Flow | 40500 | gpm-USA | Flow | 63000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 27347 |  | Reynold's number | 2546372 |  | Reynold's number | 41286 |  | Reynold's number | 67563 |  | Reynold's number | 102716 |  | Reynold's number | 140868 |  | Reynold's number | 205730 |  | Reynold's number | 287056 |  | Reynold's number | 369617 |  | Reynold's number | 633747 |  | Reynold's number | 842568 |  | Reynold's number | 1168574 |  | Reynold's number | 1776069 |  | Reynold's number | 3562105 |  | Reynold's number | 3888243 |  | Reynold's number | 4535937 |  | Reynold's number | 5711583 |  | Reynold's number | 6781482 |  | Reynold's number | 8771538
| Friction factor | 0.03 |  | Friction factor | 0.014 |  | Friction factor | 0.027 |  | Friction factor | 0.025 |  | Friction factor | 0.023 |  | Friction factor | 0.022 |  | Friction factor | 0.02 |  | Friction factor | 0.019 |  | Friction factor | 0.018 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.016 |  | Friction factor | 0.015 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012 |  | Friction factor | 0.012 |  | Friction factor | 0.012
| Fluid velocity | 5.702 | ft/s | Fluid velocity | 32.956 | ft/s | Fluid velocity | 6.498 | ft/s | Fluid velocity | 8.353 | ft/s | Fluid velocity | 9.653 | ft/s | Fluid velocity | 11.347 | ft/s | Fluid velocity | 12.908 | ft/s | Fluid velocity | 15.078 | ft/s | Fluid velocity | 15.624 | ft/s | Fluid velocity | 20.414 | ft/s | Fluid velocity | 21.65 | ft/s | Fluid velocity | 24.987 | ft/s | Fluid velocity | 28.859 | ft/s | Fluid velocity | 38.695 | ft/s | Fluid velocity | 38.421 | ft/s | Fluid velocity | 39.216 | ft/s | Fluid velocity | 43.891 | ft/s | Fluid velocity | 46.749 | ft/s | Fluid velocity | 50.28 | ft/s
| Pressure drop | 29.11 | ft hd | Pressure drop | 28.008 | ft hd | Pressure drop | 26.004 | ft hd | Pressure drop | 30.905 | ft hd | Pressure drop | 28.887 | ft hd | Pressure drop | 32.543 | ft hd | Pressure drop | 30.607 | ft hd | Pressure drop | 33.228 | ft hd | Pressure drop | 27.248 | ft hd | Pressure drop | 32.943 | ft hd | Pressure drop | 28.062 | ft hd | Pressure drop | 29.751 | ft hd | Pressure drop | 28.348 | ft hd | Pressure drop | 31.172 | ft hd | Pressure drop | 27.443 | ft hd | Pressure drop | 24.36 | ft hd | Pressure drop | 26.451 | ft hd | Pressure drop | 26.337 | ft hd | Pressure drop | 24.437 | ft hd
Point 10 | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D. |  |  | Find P.D.
| Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel |  | Pipe material | steel
| Internal diameter | 0.622 | inch | Internal diameter | 10.02 | inch | Internal diameter | 0.824 | inch | Internal diameter | 1.049 | inch | Internal diameter | 1.38 | inch | Internal diameter | 1.61 | inch | Internal diameter | 2.067 | inch | Internal diameter | 2.469 | inch | Internal diameter | 3.068 | inch | Internal diameter | 4.026 | inch | Internal diameter | 5.047 | inch | Internal diameter | 6.065 | inch | Internal diameter | 7.981 | inch | Internal diameter | 11.938 | inch | Internal diameter | 13.124 | inch | Internal diameter | 15 | inch | Internal diameter | 16.876 | inch | Internal diameter | 18.812 | inch | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch | Internal roughness | 0.001811 | inch
| Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft | Length | 100 | ft
| Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none |  | Pipe fittings | none
| Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise | Elevation change | 0 | ft Rise
| Flow | 6 | gpm-USA | Flow | 9000 | gpm-USA | Flow | 12 | gpm-USA | Flow | 25 | gpm-USA | Flow | 50 | gpm-USA | Flow | 80 | gpm-USA | Flow | 150 | gpm-USA | Flow | 250 | gpm-USA | Flow | 400 | gpm-USA | Flow | 900 | gpm-USA | Flow | 1500 | gpm-USA | Flow | 2500 | gpm-USA | Flow | 5000 | gpm-USA | Flow | 15000 | gpm-USA | Flow | 18000 | gpm-USA | Flow | 24000 | gpm-USA | Flow | 34000 | gpm-USA | Flow | 45000 | gpm-USA | Flow | 70000 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F) |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent |  | Flow type | Turbulent
| Reynold's number | 30385 |  | Reynold's number | 2829302 |  | Reynold's number | 45873 |  | Reynold's number | 75070 |  | Reynold's number | 114129 |  | Reynold's number | 156520 |  | Reynold's number | 228589 |  | Reynold's number | 318951 |  | Reynold's number | 410685 |  | Reynold's number | 704163 |  | Reynold's number | 936187 |  | Reynold's number | 1298416 |  | Reynold's number | 1973410 |  | Reynold's number | 3957895 |  | Reynold's number | 4320270 |  | Reynold's number | 5039931 |  | Reynold's number | 6346203 |  | Reynold's number | 7534980 |  | Reynold's number | 9746153
| Friction factor | 0.03 |  | Friction factor | 0.014 |  | Friction factor | 0.027 |  | Friction factor | 0.025 |  | Friction factor | 0.023 |  | Friction factor | 0.022 |  | Friction factor | 0.02 |  | Friction factor | 0.019 |  | Friction factor | 0.018 |  | Friction factor | 0.017 |  | Friction factor | 0.016 |  | Friction factor | 0.015 |  | Friction factor | 0.015 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.013 |  | Friction factor | 0.012 |  | Friction factor | 0.012 |  | Friction factor | 0.012
| Fluid velocity | 6.335 | ft/s | Fluid velocity | 36.618 | ft/s | Fluid velocity | 7.22 | ft/s | Fluid velocity | 9.281 | ft/s | Fluid velocity | 10.725 | ft/s | Fluid velocity | 12.607 | ft/s | Fluid velocity | 14.342 | ft/s | Fluid velocity | 16.753 | ft/s | Fluid velocity | 17.36 | ft/s | Fluid velocity | 22.682 | ft/s | Fluid velocity | 24.055 | ft/s | Fluid velocity | 27.763 | ft/s | Fluid velocity | 32.066 | ft/s | Fluid velocity | 42.995 | ft/s | Fluid velocity | 42.69 | ft/s | Fluid velocity | 43.573 | ft/s | Fluid velocity | 48.767 | ft/s | Fluid velocity | 51.944 | ft/s | Fluid velocity | 55.866 | ft/s
| Pressure drop | 35.533 | ft hd | Pressure drop | 34.486 | ft hd | Pressure drop | 31.778 | ft hd | Pressure drop | 37.833 | ft hd | Pressure drop | 35.396 | ft hd | Pressure drop | 39.912 | ft hd | Pressure drop | 37.564 | ft hd | Pressure drop | 40.81 | ft hd | Pressure drop | 33.471 | ft hd | Pressure drop | 40.508 | ft hd | Pressure drop | 34.514 | ft hd | Pressure drop | 36.607 | ft hd | Pressure drop | 34.894 | ft hd | Pressure drop | 38.397 | ft hd | Pressure drop | 33.802 | ft hd | Pressure drop | 30.007 | ft hd | Pressure drop | 32.589 | ft hd | Pressure drop | 32.452 | ft hd | Pressure drop | 30.114 | ft hd

## Steel Pipe - Constant Lines
Design Cut-off
gpm | Pressure loss, ft.w.c per 100 linear feet of pipe
0.1 | 4
100000 | 4
Velocity = 1 fpm
Flowcu.ft./min = | Velocityft/min x Areasq.ft.
Areasq.ft. = | Flowcu.ft./min/Velocityft/min
Areasq.ft. = | Flowcu.ft./sec/Velocityft/sec
7.48 | gallons/cu.ft.
| Velocity = | 1 | ft/sec. |  | Velocity = | 2 | ft/sec.
| Flow rate, gpm |  |  | Cross-sectional Area, sq.ft. | Flow rate, gpm |  |  | Cross-sectional Area, sq.ft. |  |  |  | Cross-sectional Area, sq.ft. |  |  |  | Cross-sectional Area, sq.ft. |  |  |  | Cross-sectional Area, sq.ft. |  |  |  | Cross-sectional Area, sq.ft. |  |  |  | Cross-sectional Area, sq.ft. |  |  |  | Cross-sectional Area, sq.ft.
| gallons/minute | gallons/second | cu.ft./sec |  | gallons/minute | gallons/second | cu.ft./sec
| 1 | 0.016667 | 0.0022282 | 0.0022282 | 1 | 0.016667 | 0.0022282 | 0.0011141 |  |  |  | 0 |  |  |  | #REF! |  |  |  | 0.0011141 |  |  |  | 0.0011141 |  |  |  | 0 |  |  |  | 0
| 10 | 0.16667 | 0.022282 | 0.022282 | 10 | 0.16667 | 0.022282 | 0.011141 |  |  |  | 0 |  |  |  | #REF! |  |  |  | 0.011141 |  |  |  | 0.011141 |  |  |  | 0 |  |  |  | 0
| 100 | 1.6667 | 0.22282 | 0.22282 | 100 | 1.6667 | 0.22282 | 0.11141 |  |  |  | 0 |  |  |  | #REF! |  |  |  | 0.11141 |  |  |  | 0.11141 |  |  |  | 0 |  |  |  | 0
| 1000 | 16.6667 | 2.2282 | 2.2282 | 1000 | 16.6667 | 2.2282 | 1.1141 |  |  |  | 0 |  |  |  | #REF! |  |  |  | 1.1141 |  |  |  | 1.1141 |  |  |  | 0 |  |  |  | 0
| 10000 | 166.6667 | 22.2816 | 22.2816 | 10000 | 166.6667 | 22.2816 | 11.1408 |  |  |  | 0 |  |  |  | #REF! |  |  |  | 11.1408 |  |  |  | 11.1408 |  |  |  | 0 |  |  |  | 0
| \ | #VALUE! | #VALUE! | #VALUE! | 100000 | 1666.6667 | 222.8164 | 111.4082 |  |  |  | 0 |  |  |  | #REF! |  |  |  | #VALUE! |  |  |  | 111.4082 |  |  |  | 0 |  |  |  | 0
Size | 1 fps |  |  | Size | 2 fps |  |  | Size | 3 fps |  |  | Size | 4 fps |  |  | Size | 6 fps |  |  | Size | 8 fps |  |  | Size | 10 fps |  |  | Size | 15 fps |  |  | Size | 20 fps
| Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec |  | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec |  | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec |  | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec |  | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec |  | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec |  | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec |  | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec |  | Flow, gpm | Friction Rate, ft.w.c. per 100 ft. of pipe | Velocity, ft./sec
1/4" Schedule 40 Steel | 0.325 | 2.25 | 1.002 | 1/4" Schedule 40 Steel | 0.649 | 8.515 | 2.001 | 1/4" Schedule 40 Steel | 0.973 | 17.725 | 3 | 1/4" Schedule 40 Steel | 1.2975 | 30.116 | 4 | 1/2" Schedule 40 Steel | 5.683 | 32.061 | 6 | 1" Schedule 40 Steel | 21.55 | 28.454 | 8 | 1-1/4" Schedule 40 Steel | 46.62 | 30.924 | 10 | 2-1/2" Schedule 40 Steel | 223.85 | 32.898 | 15 | 4" Schedule 40 Steel | 793.58 | 31.647 | 20
1/2" Schedule 40 Steel | 0.949 | 1.232 | 1.002 | 3/4" Schedule 40 Steel | 3.326 | 2.92 | 2.001 | 1" Schedule 40 Steel | 8.08 | 4.493 | 3 | 2" Schedule 40 Steel | 41.84 | 3.266 | 4 | 2" Schedule 40 Steel | 62.75 | 7.02 | 6 | 2" Schedule 40 Steel | 83.67 | 12.158 | 8 | 2-1/2" Schedule 40 Steel | 149.23 | 14.984 | 10 | 4" Schedule 40 Steel | 587.5 | 18.178 | 15 | 8" Schedule 40 Steel | 3118.5 | 13.787 | 20
3/4" Schedule 40 Steel | 1.665 | 0.85 | 1.002 | 1" Schedule 40 Steel | 5.39 | 2.141 | 2.001 | 2" Schedule 40 Steel | 31.38 | 1.91 | 3 | 4" Schedule 40 Steel | 158.73 | 1.431 | 4 | 4" Schedule 40 Steel | 238.08 | 3.083 | 6 | 4" Schedule 40 Steel | 317.43 | 5.343 | 8 | 4" Schedule 40 Steel | 396.8 | 8.212 | 10 | 6" Schedule 40 Steel | 1350.7 | 10.95 | 15 | 12" Schedule 40 Steel | 6977.5 | 8.497 | 20
1" Schedule 40 Steel | 2.7 | 0.621 | 1.002 | 2" Schedule 40 Steel | 20.925 | 0.906 | 2.001 | 4" Schedule 40 Steel | 119.05 | 0.836 | 3 | 6" Schedule 40 Steel | 360.2 | 0.867 | 4 | 8" Schedule 40 Steel | 935.5 | 1.34 | 6 | 8" Schedule 40 Steel | 1247.5 | 2.326 | 8 | 8" Schedule 40 Steel | 1559.3 | 3.575 | 10 | 8" Schedule 40 Steel | 2339 | 7.856 | 15 | 14" Schedule 40 Steel | 8433 | 7.586 | 20
1-1/4" Schedule 40 Steel | 4.67 | 0.436 | 1.002 | 3" Schedule 40 Steel | 46.1 | 0.553 | 2.001 | 6" Schedule 40 Steel | 270.1 | 0.506 | 3 | 8" Schedule 40 Steel | 623.7 | 0.621 | 4 | 14" Schedule 40 Steel | 2530 | 0.737 | 6 | 14" Schedule 40 Steel | 3373 | 1.278 | 8 | 14" Schedule 40 Steel | 4216.5 | 1.966 | 10 | 14" Schedule 40 Steel | 6324.5 | 4.322 | 15 | 18" Schedule 40 Steel | 13944 | 5.619 | 20
1-1/2" Schedule 40 Steel | 6.35 | 0.357 | 1.001 | 4" Schedule 40 Steel | 79.41 | 0.395 | 2.001 | 8" Schedule 40 Steel | 467.8 | 0.362 | 3 | 12" Schedule 40 Steel | 1395.5 | 0.382 | 4 | 24" Schedule 40 Steel | 7518 | 0.385 | 6 | 24" Schedule 40 Steel | 10024 | 0.668 | 8 | 24" Schedule 40 Steel | 12530 | 1.028 | 10 | 24" Schedule 40 Steel | 18795 | 2.259 | 15 | 24" Schedule 40 Steel | 25060 | 3.966 | 20
1/4" Schedule 40 Steel | Find P.D. |  |  | 1/4" Schedule 40 Steel | Find P.D. |  |  | 1/4" Schedule 40 Steel | Find P.D. |  |  | 1/4" Schedule 40 Steel | Find P.D. |  |  | 1/2" Schedule 40 Steel | Find P.D. |  |  | 1" Schedule 40 Steel | Find P.D. |  |  | 1-1/4" Schedule 40 Steel | Find P.D. |  |  | 2-1/2" Schedule 40 Steel | Find P.D. |  |  | 4" Schedule 40 Steel | Find P.D.
| Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel
| Internal diameter | 0.364 | inch |  | Internal diameter | 0.364 | inch |  | Internal diameter | 0.364 | inch |  | Internal diameter | 0.364 | inch |  | Internal diameter | 0.622 | inch |  | Internal diameter | 1.049 | inch |  | Internal diameter | 1.38 | inch |  | Internal diameter | 2.469 | inch |  | Internal diameter | 4.026 | inch
| Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch
| Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft
| Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none
| Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise
| Flow | 0.325 | gpm-USA |  | Flow | 0.649 | gpm-USA |  | Flow | 0.973 | gpm-USA |  | Flow | 1.2975 | gpm-USA |  | Flow | 5.683 | gpm-USA |  | Flow | 21.55 | gpm-USA |  | Flow | 46.62 | gpm-USA |  | Flow | 223.85 | gpm-USA |  | Flow | 793.58 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F)
| Flow type | Critical |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent
| Reynold's number | 2812 |  |  | Reynold's number | 5616 |  |  | Reynold's number | 8420 |  |  | Reynold's number | 11228 |  |  | Reynold's number | 28780 |  |  | Reynold's number | 64711 |  |  | Reynold's number | 106414 |  |  | Reynold's number | 285588 |  |  | Reynold's number | 620900
| Friction factor | 0.044 |  |  | Friction factor | 0.042 |  |  | Friction factor | 0.038 |  |  | Friction factor | 0.037 |  |  | Friction factor | 0.03 |  |  | Friction factor | 0.025 |  |  | Friction factor | 0.023 |  |  | Friction factor | 0.019 |  |  | Friction factor | 0.017
| Fluid velocity | 1.002 | ft/s |  | Fluid velocity | 2.001 | ft/s |  | Fluid velocity | 3 | ft/s |  | Fluid velocity | 4 | ft/s |  | Fluid velocity | 6 | ft/s |  | Fluid velocity | 8 | ft/s |  | Fluid velocity | 10 | ft/s |  | Fluid velocity | 15 | ft/s |  | Fluid velocity | 20 | ft/s
| Pressure drop | 2.25 | ft hd |  | Pressure drop | 8.515 | ft hd |  | Pressure drop | 17.725 | ft hd |  | Pressure drop | 30.116 | ft hd |  | Pressure drop | 32.061 | ft hd |  | Pressure drop | 28.454 | ft hd |  | Pressure drop | 30.924 | ft hd |  | Pressure drop | 32.898 | ft hd |  | Pressure drop | 31.647 | ft hd
1/2" Schedule 40 Steel | Find P.D. |  |  | 3/4" Schedule 40 Steel | Find P.D. |  |  | 1" Schedule 40 Steel | Find P.D. |  |  | 2" Schedule 40 Steel | Find P.D. |  |  | 2" Schedule 40 Steel | Find P.D. |  |  | 2" Schedule 40 Steel | Find P.D. |  |  | 2-1/2" Schedule 40 Steel | Find P.D. |  |  | 4" Schedule 40 Steel | Find P.D. |  |  | 8" Schedule 40 Steel | Find P.D.
| Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel
| Internal diameter | 0.622 | inch |  | Internal diameter | 0.824 | inch |  | Internal diameter | 1.049 | inch |  | Internal diameter | 2.067 | inch |  | Internal diameter | 2.067 | inch |  | Internal diameter | 2.067 | inch |  | Internal diameter | 2.469 | inch |  | Internal diameter | 4 | inch |  | Internal diameter | 7.981 | inch
| Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch
| Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft
| Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none
| Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise
| Flow | 0.949 | gpm-USA |  | Flow | 3.326 | gpm-USA |  | Flow | 8.08 | gpm-USA |  | Flow | 41.84 | gpm-USA |  | Flow | 62.75 | gpm-USA |  | Flow | 83.67 | gpm-USA |  | Flow | 149.23 | gpm-USA |  | Flow | 587.5 | gpm-USA |  | Flow | 3118.5 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent
| Reynold's number | 4806 |  |  | Reynold's number | 12715 |  |  | Reynold's number | 24263 |  |  | Reynold's number | 63761 |  |  | Reynold's number | 95626 |  |  | Reynold's number | 127507 |  |  | Reynold's number | 190388 |  |  | Reynold's number | 462650 |  |  | Reynold's number | 1230816
| Friction factor | 0.041 |  |  | Friction factor | 0.032 |  |  | Friction factor | 0.028 |  |  | Friction factor | 0.023 |  |  | Friction factor | 0.022 |  |  | Friction factor | 0.021 |  |  | Friction factor | 0.02 |  |  | Friction factor | 0.017 |  |  | Friction factor | 0.015
| Fluid velocity | 1.002 | ft/s |  | Fluid velocity | 2.001 | ft/s |  | Fluid velocity | 3 | ft/s |  | Fluid velocity | 4 | ft/s |  | Fluid velocity | 6 | ft/s |  | Fluid velocity | 8 | ft/s |  | Fluid velocity | 10 | ft/s |  | Fluid velocity | 15 | ft/s |  | Fluid velocity | 20 | ft/s
| Pressure drop | 1.232 | ft hd |  | Pressure drop | 2.92 | ft hd |  | Pressure drop | 4.493 | ft hd |  | Pressure drop | 3.266 | ft hd |  | Pressure drop | 7.02 | ft hd |  | Pressure drop | 12.158 | ft hd |  | Pressure drop | 14.984 | ft hd |  | Pressure drop | 18.178 | ft hd |  | Pressure drop | 13.787 | ft hd
3/4" Schedule 40 Steel | Find P.D. |  |  | 1" Schedule 40 Steel | Find P.D. |  |  | 2" Schedule 40 Steel | Find P.D. |  |  | 4" Schedule 40 Steel | Find P.D. |  |  | 4" Schedule 40 Steel | Find P.D. |  |  | 4" Schedule 40 Steel | Find P.D. |  |  | 4" Schedule 40 Steel | Find P.D. |  |  | 6" Schedule 40 Steel | Find P.D. |  |  | 12" Schedule 40 Steel | Find P.D.
| Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel
| Internal diameter | 0.824 | inch |  | Internal diameter | 1.049 | inch |  | Internal diameter | 2.067 | inch |  | Internal diameter | 4.026 | inch |  | Internal diameter | 4.026 | inch |  | Internal diameter | 4.026 | inch |  | Internal diameter | 4.026 | inch |  | Internal diameter | 6.065 | inch |  | Internal diameter | 11.938 | inch
| Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch
| Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft
| Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none
| Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise
| Flow | 1.665 | gpm-USA |  | Flow | 5.39 | gpm-USA |  | Flow | 31.38 | gpm-USA |  | Flow | 158.73 | gpm-USA |  | Flow | 238.08 | gpm-USA |  | Flow | 317.43 | gpm-USA |  | Flow | 396.8 | gpm-USA |  | Flow | 1350.7 | gpm-USA |  | Flow | 6977.5 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent
| Reynold's number | 6365 |  |  | Reynold's number | 16185 |  |  | Reynold's number | 47821 |  |  | Reynold's number | 124191 |  |  | Reynold's number | 186275 |  |  | Reynold's number | 248358 |  |  | Reynold's number | 310458 |  |  | Reynold's number | 701508 |  |  | Reynold's number | 1841081
| Friction factor | 0.037 |  |  | Friction factor | 0.03 |  |  | Friction factor | 0.024 |  |  | Friction factor | 0.019 |  |  | Friction factor | 0.018 |  |  | Friction factor | 0.018 |  |  | Friction factor | 0.018 |  |  | Friction factor | 0.016 |  |  | Friction factor | 0.014
| Fluid velocity | 1.002 | ft/s |  | Fluid velocity | 2.001 | ft/s |  | Fluid velocity | 3 | ft/s |  | Fluid velocity | 4 | ft/s |  | Fluid velocity | 6 | ft/s |  | Fluid velocity | 8 | ft/s |  | Fluid velocity | 10 | ft/s |  | Fluid velocity | 15 | ft/s |  | Fluid velocity | 20 | ft/s
| Pressure drop | 0.85 | ft hd |  | Pressure drop | 2.141 | ft hd |  | Pressure drop | 1.91 | ft hd |  | Pressure drop | 1.431 | ft hd |  | Pressure drop | 3.083 | ft hd |  | Pressure drop | 5.343 | ft hd |  | Pressure drop | 8.212 | ft hd |  | Pressure drop | 10.95 | ft hd |  | Pressure drop | 8.497 | ft hd
1" Schedule 40 Steel | Find P.D. |  |  | 2" Schedule 40 Steel | Find P.D. |  |  | 4" Schedule 40 Steel | Find P.D. |  |  | 6" Schedule 40 Steel | Find P.D. |  |  | 8" Schedule 40 Steel | Find P.D. |  |  | 8" Schedule 40 Steel | Find P.D. |  |  | 8" Schedule 40 Steel | Find P.D. |  |  | 8" Schedule 40 Steel | Find P.D. |  |  | 14" Schedule 40 Steel | Find P.D.
| Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel
| Internal diameter | 1.049 | inch |  | Internal diameter | 2.067 | inch |  | Internal diameter | 4.026 | inch |  | Internal diameter | 6.065 | inch |  | Internal diameter | 7.981 | inch |  | Internal diameter | 7.981 | inch |  | Internal diameter | 7.981 | inch |  | Internal diameter | 7.981 | inch |  | Internal diameter | 13.124 | inch
| Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch
| Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft
| Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none
| Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise
| Flow | 2.7 | gpm-USA |  | Flow | 20.925 | gpm-USA |  | Flow | 119.05 | gpm-USA |  | Flow | 360.2 | gpm-USA |  | Flow | 935.5 | gpm-USA |  | Flow | 1247.5 | gpm-USA |  | Flow | 1559.3 | gpm-USA |  | Flow | 2339 | gpm-USA |  | Flow | 8433 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent
| Reynold's number | 8108 |  |  | Reynold's number | 31888 |  |  | Reynold's number | 93145 |  |  | Reynold's number | 187076 |  |  | Reynold's number | 369225 |  |  | Reynold's number | 492366 |  |  | Reynold's number | 615428 |  |  | Reynold's number | 923161 |  |  | Reynold's number | 2024046
| Friction factor | 0.035 |  |  | Friction factor | 0.025 |  |  | Friction factor | 0.02 |  |  | Friction factor | 0.018 |  |  | Friction factor | 0.016 |  |  | Friction factor | 0.016 |  |  | Friction factor | 0.015 |  |  | Friction factor | 0.015 |  |  | Friction factor | 0.013
| Fluid velocity | 1.002 | ft/s |  | Fluid velocity | 2.001 | ft/s |  | Fluid velocity | 3 | ft/s |  | Fluid velocity | 4 | ft/s |  | Fluid velocity | 6 | ft/s |  | Fluid velocity | 8 | ft/s |  | Fluid velocity | 10 | ft/s |  | Fluid velocity | 15 | ft/s |  | Fluid velocity | 20 | ft/s
| Pressure drop | 0.621 | ft hd |  | Pressure drop | 0.906 | ft hd |  | Pressure drop | 0.836 | ft hd |  | Pressure drop | 0.867 | ft hd |  | Pressure drop | 1.34 | ft hd |  | Pressure drop | 2.326 | ft hd |  | Pressure drop | 3.575 | ft hd |  | Pressure drop | 7.856 | ft hd |  | Pressure drop | 7.586 | ft hd
1-1/4" Schedule 40 Steel | Find P.D. |  |  | 3" Schedule 40 Steel | Find P.D. |  |  | 6" Schedule 40 Steel | Find P.D. |  |  | 8" Schedule 40 Steel | Find P.D. |  |  | 14" Schedule 40 Steel | Find P.D. |  |  | 14" Schedule 40 Steel | Find P.D. |  |  | 14" Schedule 40 Steel | Find P.D. |  |  | 14" Schedule 40 Steel | Find P.D. |  |  | 18" Schedule 40 Steel | Find P.D.
| Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel
| Internal diameter | 1.38 | inch |  | Internal diameter | 3.068 | inch |  | Internal diameter | 6.065 | inch |  | Internal diameter | 7.981 | inch |  | Internal diameter | 13.124 | inch |  | Internal diameter | 13.124 | inch |  | Internal diameter | 13.124 | inch |  | Internal diameter | 13.124 | inch |  | Internal diameter | 16.876 | inch
| Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch
| Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft
| Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none
| Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise
| Flow | 4.67 | gpm-USA |  | Flow | 46.1 | gpm-USA |  | Flow | 270.1 | gpm-USA |  | Flow | 623.7 | gpm-USA |  | Flow | 2530 | gpm-USA |  | Flow | 3373 | gpm-USA |  | Flow | 4216.5 | gpm-USA |  | Flow | 6324.5 | gpm-USA |  | Flow | 13944 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent
| Reynold's number | 10660 |  |  | Reynold's number | 47331 |  |  | Reynold's number | 140281 |  |  | Reynold's number | 246163 |  |  | Reynold's number | 607238 |  |  | Reynold's number | 809571 |  |  | Reynold's number | 1012023 |  |  | Reynold's number | 1517975 |  |  | Reynold's number | 2602690
| Friction factor | 0.032 |  |  | Friction factor | 0.023 |  |  | Friction factor | 0.018 |  |  | Friction factor | 0.017 |  |  | Friction factor | 0.014 |  |  | Friction factor | 0.014 |  |  | Friction factor | 0.014 |  |  | Friction factor | 0.014 |  |  | Friction factor | 0.013
| Fluid velocity | 1.002 | ft/s |  | Fluid velocity | 2.001 | ft/s |  | Fluid velocity | 3 | ft/s |  | Fluid velocity | 4 | ft/s |  | Fluid velocity | 6 | ft/s |  | Fluid velocity | 8 | ft/s |  | Fluid velocity | 10 | ft/s |  | Fluid velocity | 15 | ft/s |  | Fluid velocity | 20 | ft/s
| Pressure drop | 0.436 | ft hd |  | Pressure drop | 0.553 | ft hd |  | Pressure drop | 0.506 | ft hd |  | Pressure drop | 0.621 | ft hd |  | Pressure drop | 0.737 | ft hd |  | Pressure drop | 1.278 | ft hd |  | Pressure drop | 1.966 | ft hd |  | Pressure drop | 4.322 | ft hd |  | Pressure drop | 5.619 | ft hd
1-1/2" Schedule 40 Steel | Find P.D. |  |  | 4" Schedule 40 Steel | Find P.D. |  |  | 8" Schedule 40 Steel | Find P.D. |  |  | 12" Schedule 40 Steel | Find P.D. |  |  | 24" Schedule 40 Steel | Find P.D. |  |  | 24" Schedule 40 Steel | Find P.D. |  |  | 24" Schedule 40 Steel | Find P.D. |  |  | 24" Schedule 40 Steel | Find P.D. |  |  | 24" Schedule 40 Steel | Find P.D.
| Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel |  |  | Pipe material | steel
| Internal diameter | 1.61 | inch |  | Internal diameter | 4.026 | inch |  | Internal diameter | 7.981 | inch |  | Internal diameter | 11.938 | inch |  | Internal diameter | 22.624 | inch |  | Internal diameter | 22.624 | inch |  | Internal diameter | 22.624 | inch |  | Internal diameter | 22.624 | inch |  | Internal diameter | 22.624 | inch
| Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch |  | Internal roughness | 0.001811 | inch
| Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft |  | Length | 100 | ft
| Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none |  |  | Pipe fittings | none
| Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise |  | Elevation change | 0 | ft Rise
| Flow | 6.35 | gpm-USA |  | Flow | 79.41 | gpm-USA |  | Flow | 467.8 | gpm-USA |  | Flow | 1395.5 | gpm-USA |  | Flow | 7518 | gpm-USA |  | Flow | 10024 | gpm-USA |  | Flow | 12530 | gpm-USA |  | Flow | 18795 | gpm-USA |  | Flow | 25060 | gpm-USA
| Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F) |  |  | Fluid | Water @ 20°C (68°F)
| Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent |  |  | Flow type | Turbulent
| Reynold's number | 12424 |  |  | Reynold's number | 62131 |  |  | Reynold's number | 184632 |  |  | Reynold's number | 368216 |  |  | Reynold's number | 1046737 |  |  | Reynold's number | 1395649 |  |  | Reynold's number | 1744561 |  |  | Reynold's number | 2616842 |  |  | Reynold's number | 3489123
| Friction factor | 0.031 |  |  | Friction factor | 0.021 |  |  | Friction factor | 0.017 |  |  | Friction factor | 0.015 |  |  | Friction factor | 0.013 |  |  | Friction factor | 0.013 |  |  | Friction factor | 0.012 |  |  | Friction factor | 0.012 |  |  | Friction factor | 0.012
| Fluid velocity | 1.001 | ft/s |  | Fluid velocity | 2.001 | ft/s |  | Fluid velocity | 3 | ft/s |  | Fluid velocity | 4 | ft/s |  | Fluid velocity | 6 | ft/s |  | Fluid velocity | 8 | ft/s |  | Fluid velocity | 10 | ft/s |  | Fluid velocity | 15 | ft/s |  | Fluid velocity | 20 | ft/s
| Pressure drop | 0.357 | ft hd |  | Pressure drop | 0.395 | ft hd |  | Pressure drop | 0.362 | ft hd |  | Pressure drop | 0.382 | ft hd |  | Pressure drop | 0.385 | ft hd |  | Pressure drop | 0.668 | ft hd |  | Pressure drop | 1.028 | ft hd |  | Pressure drop | 2.259 | ft hd |  | Pressure drop | 3.966 | ft hd