## Introduction v1.5
EDR Guidelines CoolTools
Pipe Size Optimization Tool v1.6
Introduction
Traditionally, most designers size piping using rules of thumb, such as limiting friction rate (e.g., 4 feet per 100 feet of pipe), water velocity (e.g., 10 feet per second), or a combination of the two. These methods are expedient and reproducible, but they seldom result in an optimum design on either a first-cost or life-cycle cost basis. The optimum pipe size for a given design flow rate is a function of:
- Location of pipe in the system (whether or not it is in the critical circuit (1));
- First costs of installed piping;
- Pump energy costs, which in turn will depend on pump and motor efficiency, distribution system type (constant or variable flow), annual flow profile through the system as well as the pipe in question, type of pump control (variable speed or riding pump curve), etc.;
- Erosion considerations (high velocities can contribute to hastening of pipe wall deterioration);
- Noise considerations, such as velocity limits to minimize noise caused by turbulence and the proximity of the pipe to noise-sensitive areas;
- Physical constraints; and
- Budget constraints.
The CoolTools Pipe Size Optimization Tool incorporates the above design and cost factors, allowing the designer to find the lowest cost piping system design.
1. The critical circuit is the circuit within the system with the highest pressure loss that determines pump head. This is often the longest run in the system, but not always. The pressure loss in this circuit, and only this circuit, drives annual energy consumption.
System Assumptions Tab
System Type and Average Water Temperature
System options include chilled water, hot water, and condenser water. Choice of system type impacts the annual energy calculation. For chilled water, pump heat is added to total annual energy, for hot water, pump heat is subtracted, and for condenser water, pump heat is ignored.
System type will also select a default average water temperature, which will appear in the cell below. Default temperatures for the three system types can be adjusted on the Constants tab.
Is this circuit the critical circuit?
The Tool optimizes pipe sizes for one circuit at a time. If CRITICAL is selected, the Tool will treat the circuit as the critical circuit in the system, taking into account energy cost when determining the least expensive alternative. If NON-CRITICAL is selected, the Tool will treat the circuit as a non-critical circuit (2) , and will not take energy cost into account for sizing. Non-critical circuits will be sized according to the selected noise and erosion criteria. When NON-CRITICAL is selected, the Lifecycle Energy Cost output will read "-" because it is not possible to calculate energy consumption from the non-critical circuit.
Note: If NON-CRITICAL is selected and noise and erosion velocity limits are turned off, then the optimized pipe size will be the smallest available pipe size.
System operation
Select Contstant Flow/ Constant Speed (CFCS), Variable Flow/ Constant Speed (VFCS), Variable Flow/ Variable Speed with Fixed Set Point (VFVSFSP), or Variable Flow/ Variable Speed with Reset Set Point (VFVSRSP). This selection will impact annual energy consumption. Variable flow selections will reduce annual energy consumption according to the factors specified on the Constants tab.
Hours per year of operation
Enter total annual estimated hours of operation.
Pipe insulation thickness
Select desired pipe insulation thickness or none. The Title 24 option will automatically select the code-required insulation thickness for the specified water temperature and pipe diameter.
This input is one of three that can be applied to override user inputs for individual pipe segments on the Piping Circuit tab. Once a selection is made, the Apply button next to the input must be clicked. This will overwrite all inputs in the Insulation Wall Thickness column on the Piping Circuit page. After clicking Apply, further modifications to the insulation thickness for individual segments may be made. However, these modifications will be overwritten if the Apply button is clicked again.
Fluid speed limit for noise sensitivity?
If noise is a concern, velocities may be limited to minimize noise caused by turbulence. If YES is selected and pipe size is chosen as AUTO, then the automated pipe sizing function will not allow the noise velocity limit to be exceeded. If YES is selected and pipe size is chosen manually, then a red-flagged cell will indicate when the maximum noise velocity is exceeded for a particular pipe segment. These limits (starting at 3 fps for ¾" pipe and increasing linearly to 20 fps for 30" pipe (3) ) are given on the Constants tab and can be edited there.
Fluid speed limit for erosion control?
If pipe wall erosion is a concern, velocities may be limited to reduce the risk of erosion. If YES is selected and pipe size is chosen as AUTO, then the automated pipe sizing function will not allow the erosion velocity limit to be exceeded. If YES is selected and pipe size is chosen manually, then a red-flagged cell will indicate when the maximium erosion velocity is exceeded. Velocity limits are given on the Constants tab. While these and similar maximum velocity guidelines have been around for years, they have never been corroborated by research. In fact, most of the research on this issue has indicated that unless there are particles or air bubbles in the water, there is little erosion of piping regardless of velocity, within the normal velocity ranges found in commercial systems.
This input is one of three that can be applied to override user inputs for individual pipe segments on the Piping Circuit tab. Once a selection is made, the Apply button next to the input must be clicked. This will overwrite all inputs in the Flow Speed Limit to Prevent Erosion? column on the Piping Circuit page. After clicking Apply, further modifications to this column for individual segments may be made. However, these modifications will be overwritten if the Apply button is clicked again.
2. Care must be taken when sizing a non-critical circuit. Energy consumption is independent of pressure loss in a non-critical circuit as long as the total pressure loss is not greater than that of the critical circuit. If pressure loss in a non-critical circuit exceeds pressure loss in the critical circuit, then that becomes the new critical circuit. Pressure loss for a circuit can be obtained from the spreadsheet’s Total Head (Feet) output at the bottom of the Piping Circuit sheet.
3. Wilson, George. 1988. Wilson Ihrig Associates, Oakland, Calif. Unpublished information from an ASHRAE Golden Gate Chapter seminar.
Piping Circuit Tab
The Piping Circuit tab contains inputs for each pipe segment and system element within the piping circuit. For each segment, complete all yellow fields with appropriate physical data. All white fields are locked and may not be edited.
Sheet Management Functions
When starting a new pipe circuit, always clear sheet and reset formulas with the Clear and Apply User Settings button at the top left corner of the sheet. Note: This will clear ALL user inputs and will apply the selections from the three Settings inputs (insulation thickness, erosion velocity limit, and noise velocity limit) to all piping segments. This can not be undone.
In order to preserve the structure of the spreadsheet (formulas and conditional formatting), do not copy and paste cells or rows, and do not manually add or delete rows using Excel functions. When adding or deleting piping segments, always use the Add a Row and Delete a Row buttons. Two rows is the minimum number of rows allowed.
Troubleshooting: If the function buttons (Add a Row, Optimize Pipe Size, etc.) will not work, hit Esc or Return to finish editing cells. Function buttons will not work while cells are in edit mode.
Pipe Size Selection/ Automated Sizing
If automatic pipe sizing is desired for a segment, select AUTO in the pull-down menu under Select Pipe Size or AUTO. Segments not containing AUTO in this field will be ignored during the optimization routine.
If a fixed pipe size is desired for a segment, select the size from the options in the pull-down menu.
Regardless of pipe sizing choice (AUTO or fixed size), the pipe size used in the spreadsheet will be displayed in the adjacent column, under Pipe Size.
Segment Auto-grouping
All segments must be assigned to a segment group when using the auto-size feature. If it is desired that all segments containing the same flow rate be grouped together and optimized to a single size, click the Auto Group button below the Segment Grouping heading. This will automatically create a group number for each distinct flow rate within the system and assign the appropriate group number to each segment. Only segments that are selected for auto-sizing will be assigned a group number. These group assignments may be edited manually, but all changes will be overwritten if Auto Group is clicked again.
Total system flow
Enter the flow rate, in gallons per minute, for the entire system. Note, this is not the flow for the current circuit being modeled, but for all circuits in the system.
The default value for this cell is the maximum flow rate of all listed pipe segments. This can be overwritten by the user, however the formula can only be restored by clicking Clear and Apply User Settings.
Insulation Thickness
If the insulation thickness has been set using the Apply button on the Settings tab (see Pipe Insulation Thickness under Settings Tab: Piping above), the insulation thickness setting for all segments will match the input on the Settings tab. If Title 24 has been selected, the spreadsheet will determine the code-required insulation thickness based on water temperature and pipe size and this thickness will be displayed in the adjacent column, under Insulation Thickness. If a fixed thickness has been selected, it will be displayed in the Insulation Thickness column.
Optimize Pipe Size
Once pipe segment setup is complete, pipe sizes may be optimized by clicking the Auto-select Optimized Pipe Size button at the top left corner. The tool will iterate through pipe size options for each segment selected for auto sizing until the lowest possible combination of first cost and life-cycle cost is found. Auto-sized segments with the same segment grouping number will be treated as a single pipe size and iterated to give the group of segments the lowest combined cost.
All lifecycle parameters may be adjusted on the Settings page. Lifecycle cost is calculated annually for the system lifetime specified and then discounted back to the present using the specified discount rate. Energy escalation and/or inflation rates may be applied to the lifecycle cost. These rates are additive: a 1.0% energy escalation rate and a 1.8% inflation rate will result in an annual energy rate increase of 2.8%.
Occasionally, selected valves are not available in the optimized pipe size. In this case, an error message will appear and the problem valves will be tagged in red.
The Auto-select Optimized Pipe Size button will grey out after optimization is completed, showing that the button is disabled. When a change is made to any of the inputs, the button will become enabled again.
Economic Assumptions
Life-cycle cost for the pipe segment is calculated by taking the net present value of electricity expenditures over the specified lifetime of the piping system. An inflation rate and/or an energy escalation rate can be applied to the annual energy expenditures and a discount rate is specified to discount the expenditures back to present value.
City cost index multipliers
Most pricing data come from RS Means Mechanical Cost Data, 2008. The location adjustment factors for materials and labor are provided for seven California cities. Average national factors are also provided. These adjustment factors can be edited on the Constants tab. New markets may be added either by entering the new market data in the last row, titled "NEW MARKET" or by overwriting one of the existing markets.
Electricity cost/ Gas cost
Enter local electricity and gas prices. Gas price will be used only when the HW system type is selected
Apply an inflation rate
Inflation rate and energy escalation rate, if both are used, will be applied additively. For example, an inflation rate of 1.8% and an energy escalation rate of 1.0% will result in an overall annual energy rate increase of 2.8%. If no inflation rate is desired, enter 0.
Apply an energy escalation rate
Inflation rate and energy escalation rate, if both are used will be applied additively. For example, an inflation rate of 1.8% and an energy escalation rate of 1.0% will result in an overall annual energy rate increase of 2.8%. If no energy escalation rate is desired, enter 0.
Discount rate
This rate is used to discount the annual electricity expenditures over the projected lifetime of the system back to the present. If an inflation rate is applied (see above), then this should be the nominal discount rate. If an inflation rate is not applied, then this should be the real discount rate.
Lifetime of system
Enter the projected lifetime of the system. Input must be less than or equal to 40 years.
Constants Tab
The Constants tab contains all physical and cost parameters for the piping components and system. Notes at the top of each column indicate data source. All fields may be edited.
Additional Information
If you have any questions or want to report a bug, please contact:
Molly McGuire, Senior Mechanical Engineer
Taylor Engineering
510-749-9135
mmcguire@taylor-engineering.com
DISCLAIMER
This pipe sizing applet was prepared for Pacific Gas and Electric Company by Taylor Engineering and Architectural Energy Corporation and funded by California utility customers under the auspices of the California Public Utilities Commission. Neither Pacific Gas and Electric Company nor any of its employees and agents:
1. Makes any written or oral warranty, expressed or implied, regarding this report, including, but not limited to those concerning merchantability or fitness for a particular purpose.
2. Assumes any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, apparatus, product, process, method, or policy contained herein.
3. Represents that use of the report would not infringe any privately owned rights,including, but not limited to, patents, trademarks or copyrights.

## System Assumptions
Project Name | My Project
System Name | CHW
System Parameters
System type | CHW |  | CHW | HW | CW
Average Water temperature | 50 | °F
System operation | VFVSFSP |  | CFCS | VFCS | VFVSFSP | VFVSRSP
Multiplier for constant/variable system | 0.3
Hours per year of operation | 2000 | hours
Pipe insulation thickness (in inches) | Title 24 | (must click "Apply" for change to take effect) | Title 24 | 0.5 | 1 | 1.5 | 2 | None
Fluid speed limit for noise sensitivity? | ON | (must click "Apply" for change to take effect) | ON | OFF
Fluid speed limit for erosion control? | ON | (must click "Apply" for change to take effect) | ON | OFF
Default safety factor: greater of | 5 | %
OR | 5 | ft W.C.
Note on C8: Default temperatures for CHW, HW, and CW may be changed on the 'Constants' tab.
Note on C9: CFCS: Contstant Flow/ Constant Speed VFCS: Variable Flow/ Constant Speed VFVSFSP: Variable Flow/ Variable Speed with Fixed Set Point VFVSRSP: Variable Flow/ Variable Speed with Reset Set Point Variable flow selections will reduce annual energy consumption according to the factors specified on the 'Constants' tab.
Note on C12: Applying changes for this field will overwrite all existing insulation choices. User will have the option to adjust this input for individual circuit segments. Choosing "Title 24" option will automatically select the insulation thickness required by Title 24 code based on water temperature and pipe diameter.
Note on C13: If noise is a concern, velocities may be limited to minimize noise caused by turbulence. If YES is selected and pipe size is chosen as AUTO, then the automated pipe sizing function will not allow the noise velocity limit to be exceeded. If YES is selected and pipe size is chosen manually, then a red-flagged cell will indicate when the maximum noise velocity is exceeded for a particular pipe segment. These limits (starting at 3 fps for ¾” pipe and increasing linearly to 20 fps for 30” pipe ) are given on the Constants tab and can be edited there. Once a selection is made, the Apply button next to the input must be clicked. This will overwrite all inputs in the Flow Speed Limit to Prevent Noise? column on the Piping Circuit page. After clicking Apply, further modifications to this column for individual segments may be made. However, these modifications will be overwritten if the Apply button is clicked again.
Note on C14: If pipe wall erosion is a concern, velocities may be limited to reduce the risk of erosion. If YES is selected and pipe size is chosen as AUTO, then the automated pipe sizing function will not allow the erosion velocity limit to be exceeded. If YES is selected and pipe size is chosen manually, then a red-flagged cell will indicate when the maximium erosion velocity is exceeded. Velocity limits are given on the Constants tab. While these and similar maximum velocity guidelines have been around for years, they have never been corroborated by research. In fact, most of the research on this issue has indicated that unless there are particles or air bubbles in the water, there is little erosion of piping regardless of velocity, within the normal velocity ranges found in commercial systems. Once a selection is made, the Apply button next to the input must be clicked. This will overwrite all inputs in the Flow Speed Limit to Prevent Erosion? column on the Piping Circuit page. After clicking Apply, further modifications to this column for individual segments may be made. However, these modifications will be overwritten if the Apply button is clicked again.

## Economic Assumptions
Economic Assumptions
City cost index multipliers
Market | Oakland, CA
Materials | 110.2
Labor | 127.3
Contractor mark-up
HVAC | 25%
General | 3%
Current year | 2011
Means Mechanical Cost Data year | 2008
Average annual first cost escalation | 9.5%
Taxes | 8%
Electricity cost | 0.15 | $/kWh
Gas cost (used only for HW system type) | 1 | $/therm
Inflation rate | 0%
Energy escalation rate | 1%
Discount rate | 5%
Lifetime of system (<=40 years) | 30 | years
Oakland, CA
Los Angeles, CA
Fresno, CA
San Francisco, CA
San Jose, CA
Riverside, CA
Sacramento, CA
Average National
Note on C5: This index adjusts the materials and labor costs to account for local market conditions.
Note on C12: Molly McGuire: Cost data are taken from R.S. Means Mechanical Cost Data. Input the current year (or year of the project) here to allow labor and materials costs to be escalated to present values. Input must be greater than or equal to the input in Means Mechanical Cost Data year (below).
Note on C14: Molly McGuire: This is the average percentage increase of first costs per year between the year input in Means Mechanical Cost Data year and the year input in Current year.This value is used only if Current year is greater than Means Mechanical Cost Data year.
Note on C20: This rate is used in the calculation of the present value of energy rates
Note on C21: This time period is used to calculate total energy cost over the lifetime of the system

## Piping Circuit
[32 empty] | Inputs | [33 empty] | Outputs
Total system flow | 0 |  | GPM |  |  |  | CRITICAL | [10 empty] | CRITICAL | NON-CRITICAL | [5 empty] | 100
Add or delete a row above current cursor position | Segment Grouping |  | Flow rate |  | Select Pipe Size or "AUTO" | Auto- Optimized Nominal Pipe Size | Pipe Size | Previous Size | Annual Hours of Oper. | Flow Speed Limit to Prevent Noise? | [5 empty] | Flow Speed Limit to Prevent Erosion? |  | TYPE COPPER=0, STEEL =1 | Rough- ness | I.D. ["] | RE3 | RE2 | RE* E-4 | Reynolds Number | Relative Roughness, e/D | D/E Threshold for turbulent flow | Fmin | A | B | f | Flow regime | Desired Insulation Wall Thickness | Insulation Thickness | Straight Pipe Length | Number of Elbows |  | Tees with flow through: |  | Number of Valves | [21 empty] | Control Valve DP |  | Other: Chiller/ Boiler/ Coil/ HX/ etc. |  |  | Segment Head |  | Velocity | Friction Rate | Water volume in pipe | Const/ Variable multiplier | BHP | Pump Motor Power | + Pump Heat to Chiller | - Pump Heat to Boiler | Total Power |  | Energy Cnsmp per Year |  | ELLS K FACTOR |  | TEES K FACTOR |  | Total K Factor | VALVES Cv FACTOR | [5 empty] | P drop | Calc P drop from fittings (feet) | Calc P drop from valves (psi) | MATERIALS COST: MOTOR | MATERIALS COST: VFD | MATERIALS COST: PIPING |  | MATERIALS COST: ELLS |  | MATERIALS COST: TEES | MATERIALS COST: VALVES | [6 empty] | LABOR COST: PIPING |  | LABOR COST: ELLS |  | LABOR COST: TEES | LABOR COST: VALVES | [6 empty] | LABOR COST: MOTOR | LABOR COST: VFD | First Cost |  |  |  |  | Lifecycle Cost | Lifecycle + First Cost | Annl Energy Costs
Pipe Segment Description |  | calc'ed? | GPM | rounded GPM | Inches | Inches | Inches |  | h/yr |  | Too fast? | T^3 (F) | T^2 (F) | T (F) | viscosity |  | Too fast? | [14 empty] | Inches |  | Feet | 90º | 45º | Straight | Branch | Circuit Setter | Value in Range? |  | Silent Check | Value in Range? |  | Swing Check | Value in Range? |  | Ball or Butterfly | Value in Range? |  | Use Ball or Butterfly? Ball = 0, Butterfly = 1 | Wye-Strainer | Value in Range? |  | Suction Diffuser | Value in Range? |  | Flow Limiting | Value in Range? |  | Psi |  | Feet |  |  | Feet | psi | Feet/ sec | Feet/ 100 ft | Gal |  | HP | kW | kW | therms/ hr | kW | therms /hr | kWh | therms | 90 | 45 | LINE | BRANCH |  | Circuit Setter | Silent Check | Swing Check | Ball/ Butterfly | Wye-Strainer | Suction Diffuser | Flow Limiting Valve (feet) |  |  |  |  | piping | insulation | 90 | 45 | LINE | Circuit Setter | Silent Check | Swing Check | Ball/ Butterfly | Wye-Strainer | Suction Diffuser | Flow Limiting Valve | piping | insulation | 90 | 45 | LINE | Circuit Setter | Silent Check | Swing Check | Ball/ Butterfly | Wye-Strainer | Suction Diffuser | Flow Limiting Valve |  |  | Materials | Taxes | Labor | Contractor Markup | Total |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
| 1 | TRUE |  | 0 | AUTO | 6 | 6 | AUTO | 2000 | ON | NO | 125000 | 2500 | 50 | 1.425e-05 | ON | NO | 1 | 0.00015 | 6.065 | 0 | 0 | 0 | 0 | 0.00029678 | 34.9634 | 0.028581 | #DIV/0! | #DIV/0! | #DIV/0! | Laminar | Title 24 | 1 | [6 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 1 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0.3 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0.29 | 0.17 | 0.12 | 0.62 | 0 | 650 | 625 | 1440 | 1613 | 597 | 520 | 7.4 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | TRUE |  | 0 | AUTO | 6 | 6 | AUTO | 2000 | ON | NO | 125000 | 2500 | 50 | 1.425e-05 | ON | NO | 1 | 0.00015 | 6.065 | 0 | 0 | 0 | 0 | 0.00029678 | 34.9634 | 0.028581 | #DIV/0! | #DIV/0! | #DIV/0! | Laminar | Title 24 | 1 | [6 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 1 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0.3 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | 0 | 0.29 | 0.17 | 0.12 | 0.62 | 0 | 650 | 625 | 1440 | 1613 | 597 | 520 | 7.4 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | Totals |  |  | #DIV/0! | #DIV/0! |  |  | 0 |  | #DIV/0! |  |  |  | without Safety Factor | [17 empty] | #DIV/0! | #DIV/0! | [24 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[65 empty] | + | #DIV/0! |  | Safety factor |  |  |  | #DIV/0! |  |  |  | with Safety Factor
Output Summary: |  | Previous Cost | [63 empty] | #DIV/0!
Total Head (Feet) | #DIV/0!
Total Head w S.F. (Feet) | #DIV/0!
Total Cost | #DIV/0!
Lifecycle Energy Cost | #DIV/0! | 183.86
First Cost | #DIV/0!
Scalar Ratio | #DIV/0!
Notes:
Enter user notes here.
[5 empty] | AUTO |  |  |  |  | ON | [5 empty] | ON | [15 empty] | Title 24
[5 empty] | 0.5 |  |  |  |  | OFF | [5 empty] | OFF | [15 empty] | 0.5
[5 empty] | 0.75 | [26 empty] | 1
[5 empty] | 1 | [26 empty] | 1.5
[5 empty] | 1.25 | [26 empty] | 2
[5 empty] | 1.5 | [26 empty] | None
2
2.5
3
4
5
6
8
10
12
14
16
18
20
24
26
30
Note on A3: Default value is maximum GPM listed below. User may override.
Note on H3: The critical circuit is the circuit in the system with the highest pressure drop, and is the circuit that determines the pump head. When "NON-CRITICAL" is selected, the spreadsheet will optimize pipe size based only on first cost and will not take into account lifecycle (energy) cost. If "NON-CRITICAL" is selected, pipe size will be reduced to the smallest size possible without violating specified noise and erosion limits. If no noise or erosion limits are indicated, then optimized pipe size will be the smallest available pipe size (1/2"). Note that if the total head of a non-critical circuit exceeds the total head of the critical circuit, it then becomes the critical circuit. So care must be taken when sizing non-critical circuits to ensure their head is below the critical circuit head.
Note on B5: This function allows pipes with similar flows to be optimized together so that pipes with similar flows will have the same size. Click the "Auto Group" button for Excel to create groups for all entered segments. Excel will place pipes with the same flow rates into the same group. To overwrite the auto grouping, simply type a new group number into the cell. For pipes with the same group number to be optimized as a group, each segment must have the "AUTO" pipe size selection option selected. Note: The "Auto Group" button will overwrite all existing groupings.
Note on F5: Selecting "AUTO" in this column will allow this pipe segment to be optimized when the "Optimize Pipe Size" button is clicked. Selecting a pipe size manually will lock in that pipe size, and that segment will not be affected when "Optimize Pipe Size" is clicked.
Note on G5: This is the auto-generated pipe size, optimized for first and lifecycle costs
Note on K5: Turning this function on will limit flow speed in order to prevent noise. A change to the speed limit for noise input on the "Settings" sheet will override all inputs in this column
Note on Q5: Turning this function on will limit flow speed in order to prevent erosion. A change to the speed limit for erosion input on the "Settings" sheet will override all inputs in this column
Note on AE5: Molly McGuire: This equation and those for "A" and "B" in the preceeding columns are taken from AHSRAE Fundamentals 2.7
Note on AG5: Selecting "Title 24" will default to the thickness specified by Title 24 for the indicated water temperature and pipe diameter
Note on AN5: Molly McGuire: If cell to right of input is red, then this is not a valid fitting selection for this pipe size. Either remove fitting selection or change pipe size.
Note on BJ5: Typically 2 psi for small coils like reheat VAVs, 5 psi for large coils
Note on BL5: Obtain from Manufacturer This field can also be used to add a safety factor to the head calculation.
Note on BS5: Water volume is provided as a convenience only--not used in lifecycle cost calculation. Includes only volume in pipe length, not in coil or equipment.
Note on BW5: Molly McGuire: For CHW, pump heat is added to the load that the chiller will see. For HW, pump heat is subracted from the load that the boiler will see. For CW, pump heat is ignored.
Note on BX5: Molly McGuire: For CHW, pump heat is added to the load that the chiller will see. For HW, pump heat is subracted from the load that the boiler will see. For CW, pump heat is ignored.
Note on AN6: Molly McGuire: Acceptable size range: 1/2" to 12"
Note on AQ6: Molly McGuire: Acceptable size range: ALL SIZES
Note on AT6: Molly McGuire: Acceptable size range: ALL SIZES
Note on AW6: Molly McGuire: Insert # of Ball or Butterfly valves. Based on pipe size, spreadsheet will automatically choose type of valve based on the cutoff size selected on the "Constants" sheet. Ball valves are usedfor pipes smaller than the selected size and Butterfly valves are used for pipes greater than or equal to the selected size. Acceptable size range: ANY SIZE
Note on BA6: Molly McGuire: Acceptable size range: 1/2" - 12"
Note on BD6: Molly McGuire: Acceptable size range: 2" - 10"
Note on BG6: Molly McGuire: Acceptable size range: 1/2" - 24"
Note on DZ9: Molly McGuire: Motor and VFD cost are added in here
Note on A20: Present value of lifecycle energy cost / Year 0 energy cost This is a function of the entered discount rate, inflation rate, and energy escalation rate.

## Constants
Grey cells indicate components or elements that do not exist; values are set to 999999999
Pink cells indicate extrapolations for data points that were unavailable
| Red | Red font indicates updated pricing values
Flow Parameters
| K VALUES COPPER | [6 empty] | VALVES | [11 empty] | PIPE INNER DIAMETERS |  |  |  | Threshold for fully turbulent rough flow
| SIZE | ELLS |  | TEES |  |  |  | SIZE | Cv | [6 empty] | dP (feet) |  |  |  | O.D " | I.D. " |  |  | Re3 | Re2 | Reynolds Number* 10-4 | Relative Roughness, D/E
|  | 90 | 45 | Straight | Branch |  |  |  | Circuit Setter | Silent Check | Swing Check | Ball | Butterfly | Wye-Strainer | Suction Diffuser | Flow Limiting Valve |  |  |  |  | Type L COPPER | SCH 40 or STD WT STEEL |  | 27 | 9 | 3 | 20
| 0.5 | 0.47 | 0.25 | 0.29 | 1.1 |  |  | 0.5 | 1.7 | 6.86 | 4.8 | 5 | 999999999 | 25.8977 | 999999999 | 7.4 |  |  |  | 0.5 | 0.545 | 0.622 |  | 0.85737 | 0.9025 | 0.95 | 66.6667
| 0.75 | 0.45 | 0.24 | 0.28 | 1.05 |  |  | 0.75 | 2.7 | 16.3 | 14.3 | 12 | 999999999 | 32.7926 | 999999999 | 7.4 |  |  |  | 0.75 | 0.785 | 0.824 |  | 474552 | 6084 | 78 | 500
| 1 | 0.43 | 0.22 | 0.26 | 1 |  |  | 1 | 5.8 | 30 | 24 | 22 | 999999999 | 40.814 | 999999999 | 7.4 |  |  |  | 1 | 1.025 | 1.049 |  | 85184000 | 193600 | 440 | 2500
| 1.25 | 0.41 | 0.22 | 0.25 | 0.95 |  |  | 1.25 | 11 | 49 | 43 | 35 | 999999999 | 50.0472 | 999999999 | 7.4 |  |  |  | 1.25 | 1.265 | 1.38 |  | 9261000000 | 4410000 | 2100 | 10000
| 1.5 | 0.4 | 0.21 | 0.23 | 0.9 |  |  | 1.5 | 20 | 72 | 60 | 52 | 999999999 | 60.5774 | 999999999 | 7.4 |  |  |  | 1.5 | 1.505 | 1.61 |  | 97336000000 | 21160000 | 4600 | 20000
| 2 | 0.38 | 0.2 | 0.2 | 0.84 |  |  | 2 | 40 | 130 | 102 | 95 | 166 | 72 | 55 | 7.4 |  |  |  | 2 | 1.985 | 2.067
| 2.5 | 0.35 | 0.19 | 0.18 | 0.79 |  |  | 2.5 | 62 | 110 | 221 | 999999999 | 247 | 111 | 90 | 7.4 |  |  |  | 2.5 | 2.465 | 2.469
| 3 | 0.34 | 0.18 | 0.17 | 0.76 |  |  | 3 | 110 | 155 | 327 | 999999999 | 340 | 164 | 110 | 7.4 |  |  |  | 3 | 2.945 | 3.068
| 4 | 0.31 | 0.18 | 0.15 | 0.7 |  |  | 4 | 220 | 278 | 605 | 999999999 | 660 | 285 | 200 | 7.4 |  |  |  | 4 | 3.905 | 4.026
[8 empty] | 5 | 420 | 431 | 975 | 999999999 | 1080 | 410 | 350 | 7.4 |  |  |  | 5 | 4.875 | 5.047
| K VALUES STEEL | [6 empty] | 6 | 650 | 625 | 1440 | 999999999 | 1613 | 597 | 520 | 7.4 |  |  |  | 6 | 5.845 | 6.065
| SIZE | ELLS |  | TEES |  |  |  | 8 | 875 | 1115 | 2670 | 999999999 | 3759 | 1000 | 760 | 7.4 |  |  |  | 8 | 7.725 | 7.981
|  | 90 | 45 | Straight | BRANCH |  |  | 10 | 1200 | 1770 | 4300 | 999999999 | 5300 | 1800 | 1000 | 7.4 |  |  |  | 10 | 9.625 | 10.02
| 1 | 0.43 | 0.22 | 0.26 | 1 |  |  | 12 | 2250 | 2500 | 6350 | 999999999 | 7969 | 2800 | 999999999 | 7.4 |  |  |  | 12 | 11.565 | 12
| 1.25 | 0.41 | 0.22 | 0.25 | 0.95 |  |  | 14 | 999999999 | 3400 | 8600 | 999999999 | 11917 | 4120 | 999999999 | 7.4 |  |  |  | 14 |  | 13.25
| 1.5 | 0.4 | 0.21 | 0.23 | 0.9 |  |  | 16 | 999999999 | 4400 | 11400 | 999999999 | 16383 | 5810 | 999999999 | 7.4 |  |  |  | 16 |  | 15.25
| 2 | 0.38 | 0.2 | 0.2 | 0.84 |  |  | 18 | 999999999 | 5600 | 14700 | 999999999 | 21705 | 7900 | 999999999 | 7.4 |  |  |  | 18 |  | 17.25
| 2.5 | 0.35 | 0.19 | 0.18 | 0.79 |  |  | 20 | 999999999 | 6900 | 18100 | 999999999 | 27908 | 10430 | 999999999 | 7.4 |  |  |  | 20 |  | 19.25
| 3 | 0.34 | 0.18 | 0.17 | 0.76 |  |  | 24 | 999999999 | 10000 | 26800 | 999999999 | 43116 | 17020 | 999999999 | 7.4 |  |  |  | 24 |  | 23.25
| 4 | 0.31 | 0.18 | 0.15 | 0.7 |  |  | 26 | 999999999 | 15400 | 31000 | 999999999 | 60922 | 21170 | 999999999 | 999999999 |  |  |  | 26 |  | 25.25
| 5 | 0.3 | 0.17 | 0.13 | 0.66 |  |  | 30 | 999999999 | 22400 | 42000 | 999999999 | 86375 | 31370 | 999999999 | 999999999 |  |  |  | 30 |  | 29.25
| 6 | 0.29 | 0.17 | 0.12 | 0.62 | [14 empty] | Roughness | 5e-06 | 0.00015 | inches
| 8 | 0.27 | 0.17 | 0.1 | 0.58 |  | Property at T= | 32°F | 77°F | 212°F
| 10 | 0.25 | 0.16 | 0.09 | 0.53 |  | c (Btu/lbm-°F) | 1.007 | 0.998 | 1.007
| 12 | 0.24 | 0.16 | 0.09 | 0.5 |  | u (ft3/lbm) | 0.016 | 0.0161 | 0.0167
| 14 | 0.23 | 0.15 | 0.08 | 0.5
| 16 | 0.23 | 0.15 | 0.08 | 0.47 |  | T-cubed | T-squared | Temperature | Viscosity
| 18 | 0.22 | 0.14 | 0.07 | 0.44 |  | 64000 | 1600 | 40 | 1.66e-05
| 20 | 0.22 | 0.14 | 0.07 | 0.42 |  | 125000 | 2500 | 50 | 1.41e-05
| 24 | 0.21 | 0.13 | 0.06 | 0.41 |  | 343000 | 4900 | 70 | 1.06e-05
| 26 | 0.21 | 0.13 | 0.06 | 0.4 |  | 729000 | 8100 | 90 | 8.26e-06
| 30 | 0.2 | 0.12 | 0.05 | 0.39 |  | 1331000 | 12100 | 110 | 6.67e-06
[7 empty] | 2197000 | 16900 | 130 | 5.58e-06
[7 empty] | 3375000 | 22500 | 150 | 4.76e-06
[7 empty] | 4913000 | 28900 | 170 | 4.13e-06
[7 empty] | 6859000 | 36100 | 190 | 3.62e-06
[7 empty] | 9528128 | 44944 | 212 | 3.19e-06
Piping Component Pricing
column for vlookup | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| Use copper piping for sizes less than or equal to: |  |  |  | 2.5 | inches
| Use butterfly valve for sizes greater than or equal to: |  |  |  | 3 | inches
Copper pipe pricing (type L)
|  | piping |  | 90 ell |  | 45 ell |  | tee |  | Circuit Setter |  | Silent Check |  | Swing Check |  | Ball |  | Butterfly |  | Wye-Strainer |  | Suction Diffuser |  | Flow Limiting Valve
| Size | Mat ($/LF) | Inst ($/LF) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea)
| 0.5 | 2.26 | 4.61 | 0.92 | 18.7 | 1.67 | 18.7 | 1.56 | 28.5 | 40 | 17.15 | 93.7662 | 17.15 | 23.5 | 15.55 | 10.3 | 17 | 999999999 | 999999999 | 19.2 | 18.85 | 999999999 | 999999999 | 120.98 | 17.15
| 0.75 | 3.51 | 4.92 | 2.04 | 19.65 | 2.93 | 19.65 | 3.75 | 31 | 44 | 18.85 | 148.1582 | 18.85 | 30 | 18.7 | 16.95 | 18.7 | 999999999 | 999999999 | 21.5 | 19.85 | 999999999 | 999999999 | 131.12 | 18.85
| 1 | 5.1 | 5.5 | 5 | 23.5 | 7.35 | 23.5 | 11.6 | 37.5 | 54 | 21 | 260 | 26.5 | 42 | 19.65 | 21.5 | 19.65 | 999999999 | 999999999 | 23 | 22 | 999999999 | 999999999 | 142.72 | 21
| 1.25 | 7.05 | 6.45 | 7.6 | 25 | 10.45 | 25 | 16.7 | 41.5 | 78 | 25 | 271 | 31 | 54.5 | 25 | 32.5 | 25 | 999999999 | 999999999 | 51.5 | 25 | 999999999 | 999999999 | 263.7 | 25
| 1.5 | 9.05 | 7.2 | 11.8 | 28.5 | 12.6 | 28.5 | 25.5 | 46.5 | 91 | 31.5 | 325 | 34 | 72 | 28.5 | 42.5 | 28.5 | 999999999 | 999999999 | 365 | 34.5 | 999999999 | 999999999 | 263.7 | 31.5
| 2 | 14.05 | 8.9 | 21.5 | 34 | 21 | 34 | 40 | 53.5 | 130 | 37.5 | 440 | 41.5 | 109 | 34 | 51.5 | 34 | 227 | 26.5 | 440 | 47 | 250 | 63 | 394.1 | 37.5
| 2.5 | 21.5 | 10.85 | 45.5 | 51.5 | 45 | 51.5 | 95 | 84 | 370 | 45 | 495 | 74.5 | 258 | 45 | 172 | 41.5 | 228 | 74.5 | 650 | 136 | 279 | 104 | 587.54 | 45
| 3 | 29.5 | 12 | 60.5 | 61 | 66.5 | 51.5 | 124 | 96 | 562 | 170 | 550 | 84 | 345 | 51.5 | 261 | 46.5 | 240 | 84 | 805 | 151 | 279 | 104 | 587.54 | 170
| 4 | 50 | 17.25 | 156 | 74.5 | 142 | 74.5 | 299 | 135 | 867 | 226 | 810 | 135 | 1100 | 224 | 999999999 | 999999999 | 271 | 135 | 1225 | 226 | 550 | 194 | 1514.78 | 226
| 5 | 107 | 19.8 | 650 | 112 | 550 | 112 | 980 | 168 | 1308 | 205.1776 | 1050 | 174 | 1400 | 287 | 999999999 | 999999999 | 335 | 209 | 1225 | 310 | 725 | 278 | 1514.78 | 205.1776
| 6 | 149 | 26 | 865 | 116 | 865 | 116 | 1325 | 174 | 1763 | 251.5566 | 1375 | 209 | 1700 | 350 | 999999999 | 999999999 | 375 | 209 | 2325 | 350 | 755 | 320 | 1514.78 | 251.5566
| 8 | 208 | 29 | 3200 | 131 | 2950 | 131 | 5150 | 209 | 3313 | 344.3145 | 2225 | 232 | 2800 | 420 | 999999999 | 999999999 | 485 | 232 | 2550 | 405 | 1025 | 390 | 2338.04 | 344.3145
Steel pipe pricing
|  | piping |  | 90 ell |  | 45 ell |  | tee |  | Circuit Setter |  | Silent Check |  | Swing Check |  | Ball |  | Butterfly |  | Wye-Strainer |  | Suction Diffuser |  | Flow Limiting Valve
| Size | Mat ($/LF) | Inst ($/LF) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea) | Mat ($/ea) | Inst ($/ea)
| 0.5 | 2.18 | 5.95 | 27 | 45.51 | 37.5 | 45.51 | 68 | 73.1 | 40 | 17.15 | 93.7662 | 17.15 | 280.1429 | 17.15 | 62.5 | 38.46 | 999999999 | 999999999 | 7.75 | 18.85 | 999999999 | 999999999 | 120.98 | 17.15
| 0.75 | 2.58 | 6.1 | 27 | 45.51 | 37.5 | 45.51 | 68 | 73.1 | 44 | 18.85 | 148.1582 | 18.85 | 335.7857 | 18.85 | 83 | 38.46 | 999999999 | 999999999 | 9.45 | 21 | 999999999 | 999999999 | 131.12 | 18.85
| 1 | 3.7 | 7.85 | 13.1 | 45.51 | 13.45 | 45.51 | 34.5 | 73.1 | 54 | 21 | 340 | 26.5 | 510 | 37.5 | 103 | 48.74 | 999999999 | 999999999 | 12.9 | 23.5 | 999999999 | 999999999 | 142.72 | 21
| 1.25 | 4.93 | 8.67 | 13.1 | 52.01 | 13.45 | 52.01 | 42 | 80.75 | 78 | 25 | 375 | 31 | 447.0714 | 25 | 138 | 55.82 | 999999999 | 999999999 | 17.2 | 25 | 999999999 | 999999999 | 263.7 | 25
| 1.5 | 5.65 | 9.59 | 13.1 | 55.42 | 13.45 | 55.82 | 42 | 91 | 91 | 31.5 | 410 | 34 | 502.7143 | 31.5 | 180 | 66.1 | 999999999 | 999999999 | 101 | 34.5 | 999999999 | 999999999 | 263.7 | 31.5
| 2 | 7.4 | 11.92 | 14.1 | 73.1 | 13.45 | 73.1 | 34 | 121.35 | 130 | 37.5 | 495 | 41.5 | 645 | 46.5 | 255 | 85.6 | 227 | 26.5 | 106 | 47 | 250 | 63 | 394.1 | 37.5
| 2.5 | 9.8 | 15.49 | 16.95 | 91 | 15.7 | 91 | 46.5 | 146.25 | 370 | 45 | 595 | 74.5 | 745 | 135 | 999999999 | 999999999 | 228 | 74.5 | 128 | 136 | 279 | 104 | 587.54 | 45
| 3 | 12.5 | 16.96 | 21 | 104 | 16.95 | 104 | 51.5 | 182.05 | 562 | 170 | 695 | 84 | 745 | 149 | 999999999 | 999999999 | 240 | 84 | 142 | 151 | 279 | 104 | 587.54 | 170
| 4 | 16.5 | 19.72 | 34 | 146.25 | 30 | 146.25 | 72.5 | 242.7 | 867 | 226 | 945 | 135 | 1100 | 224 | 999999999 | 999999999 | 271 | 135 | 181 | 226 | 550 | 194 | 1514.78 | 226
| 5 | 24 | 22.76 | 71 | 182.05 | 46 | 182.05 | 120 | 291.5 | 1308 | 205.1776 | 1175 | 174 | 1400 | 287 | 999999999 | 999999999 | 335 | 209 | 283 | 310 | 725 | 278 | 1514.78 | 205.1776
| 6 | 30 | 30.56 | 74 | 220.25 | 60 | 220.25 | 124 | 368.7 | 1763 | 251.5566 | 1525 | 209 | 1700 | 350 | 999999999 | 999999999 | 375 | 209 | 283 | 350 | 755 | 320 | 1514.78 | 251.5566
| 8 | 47 | 37.94 | 140 | 294 | 100 | 279.15 | 219 | 442.5 | 3313 | 344.3145 | 2225 | 232 | 2800 | 420 | 999999999 | 999999999 | 485 | 232 | 580 | 420 | 1025 | 390 | 2338.04 | 344.3145
| 10 | 60 | 45.84 | 282 | 368.7 | 200 | 368.7 | 435 | 553 | 4650 | 437.0724 | 3125 | 261 | 4150 | 475 | 999999999 | 999999999 | 620 | 261 | 1100 | 530 | 2475 | 440 | 2654.16 | 437.0724
| 12 | 75 | 57.96 | 420 | 442.5 | 282 | 442.5 | 605 | 690 | 10133 | 529.8303 | 4825 | 350 | 5900 | 615 | 999999999 | 999999999 | 925 | 350 | 1675 | 620 | 3475 | 585 | 3401.69 | 529.8303
| 14 | 85 | 73.24 | 430 | 553 | 380 | 553 | 985 | 848 | 999999999 | 999999999 | 7300 | 455 | 8525 | 805 | 999999999 | 999999999 | 1225 | 455 | 3075 | 810 | 5075 | 705 | 4445.58 | 626.9782
| 16 | 114 | 84.82 | 790 | 732.5 | 670 | 732.5 | 1200 | 1106 | 999999999 | 999999999 | 10200 | 600 | 8550 | 1050 | 999999999 | 999999999 | 1600 | 600 | 4350 | 1050 | 999999999 | 999999999 | 6191.38 | 719.6532
| 18 | 120 | 100.1 | 1050 | 880 | 955 | 880 | 1875 | 1370 | 999999999 | 999999999 | 10700 | 695 | 10400 | 805 | 999999999 | 999999999 | 2075 | 695 | 5564.892 | 1073.3732 | 999999999 | 999999999 | 8922.05 | 812.3282
| 20 | 146 | 122.25 | 1500 | 959 | 990 | 959 | 2900 | 1475 | 999999999 | 999999999 | 13387.5 | 820 | 12946.91 | 1102.5 | 999999999 | 999999999 | 2550 | 1050 | 7139.48 | 1197.0751 | 999999999 | 999999999 | 11209.68 | 905.0032
| 24 | 186 | 138 | 2000 | 1080 | 1500 | 1048.5 | 3750 | 1580 | 999999999 | 999999999 | 17492.5 | 1056 | 19700 | 1400 | 999999999 | 999999999 | 3575 | 1400 | 10877.328 | 1444.479 | 999999999 | 999999999 | 13497.32 | 1090.3532
| 26 | 345 | 146.5 | 2500 | 1200 | 1650 | 1291 | 4125 | 2002 | 999999999 | 999999999 | 19545 | 1174 | 27280.0316 | 1375.2978 | 999999999 | 999999999 | 4256.5824 | 1634.5428 | 13040.588 | 1568.181 | 999999999 | 999999999 | 999999999 | 999999999
| 30 | 375 | 183.35 | 3000 | 1350 | 1825 | 2450 | 4550 | 3662 | 999999999 | 999999999 | 23650 | 1410 | 41213.61 | 1589.623 | 999999999 | 999999999 | 5705.58 | 2186.43 | 17955.78 | 1815.5849 | 999999999 | 999999999 | 999999999 | 999999999
| Insulation Pricing: Materials | [6 empty] | Insulation Pricing: Installation | [6 empty] | Insulation thickness per T24 | [6 empty] | Motor and VFD drive cost | [6 empty] | Motor and VFD drive cost per HP
| Insul. Thickness | 0.5 | 1 | 1.5 | 2 |  |  | Insul. Thickness | 0.5 | 1 | 1.5 | 2 |  |  | Pipe diameter is less than: (in inches) | [6 empty] | HP | Pump |  |  | VFD |  |  | HP | Pump |  | VFD
| Pipe size | 2 | 3 | 4 | 5 |  |  | Pipe size | 2 | 3 | 4 | 5 | [9 empty] | Greater than | Materials | Installation | Total | Materials | Installation | Total |  | Materials | Installation | Materials | Installation
| 0.375 | 0.73126 | 0.85909 | 1.5796 | 2.5456 |  |  | 0.375 | 2.4903 | 2.5951 | 2.704 | 2.827 |  |  | 0 | 1 | 2 | 4 | 6 | 8 |  | 0 | 272 | 112 | 384 | 828.7712 | 355 | 1183.7712
| 0.5 | 0.73 | 0.89 | 1.67 | 2.6 |  |  | 0.5 | 2.48 | 2.59 | 2.7 | 2.82 |  | Temp is less than °F | 2 | 3 | 4 | 5 | 6 | 7 |  | 0.083333 | 455 | 112 | 567 | 828.7712 | 355 | 1183.7712 | 0.083333 | 5460 | 1344 | 9945.2547 | 4260
| 0.75 | 0.83 | 0.97 | 1.68 | 2.68 |  |  | 0.75 | 2.59 | 2.7 | 2.82 | 2.96 |  | 0 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 |  | 0.125 | 555 | 135 | 690 | 828.7712 | 355 | 1183.7712 | 0.125 | 4440 | 1080 | 6630.1698 | 2840
| 1 | 0.86 | 1.04 | 1.8 | 2.86 |  |  | 1 | 2.7 | 2.82 | 2.96 | 3.1 |  | 40 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 |  | 0.16667 | 705 | 135 | 840 | 828.7712 | 355 | 1183.7712 | 0.16667 | 4230 | 810 | 4972.6274 | 2130
| 1.25 | 0.91 | 1.12 | 1.96 | 3.02 |  |  | 1.25 | 2.82 | 2.96 | 3.1 | 3.27 |  | 60 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.25 | 980 | 168 | 1148 | 828.7712 | 355 | 1183.7712 | 0.25 | 3920 | 672 | 3315.0849 | 1420
| 1.5 | 1.05 | 1.21 | 2.05 | 3.14 |  |  | 1.5 | 2.82 | 2.96 | 3.1 | 3.27 |  | 105 | 1 | 1 | 1 | 1 | 1.5 | 1.5 |  | 0.33333 | 1025 | 168 | 1193 | 828.7712 | 355 | 1183.7712 | 0.33333 | 3075 | 504 | 2486.3137 | 1065
| 2 | 1.12 | 1.31 | 2.26 | 3.32 |  |  | 2 | 2.96 | 3.1 | 3.27 | 3.45 |  | 140 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | 0.5 | 1175 | 168 | 1343 | 828.7712 | 355 | 1183.7712 | 0.5 | 2350 | 336 | 1657.5425 | 710
| 2.5 | 1.17 | 1.49 | 2.42 | 3.57 |  |  | 2.5 | 3.1 | 3.27 | 3.45 | 3.65 |  | 200 | 1.5 | 1.5 | 1.5 | 2 | 2 | 3.5 |  | 0.75 | 1700 | 168 | 1868 | 868.3816 | 355 | 1223.3816 | 0.75 | 2266.6667 | 224 | 1157.8422 | 473.3333
| 3 | 1.3235 | 1.59 | 2.54 | 3.79 |  |  | 3 | 3.2684 | 3.45 | 3.65 | 3.88 |  | 250 | 2 | 2 | 2.5 | 2.5 | 3.5 | 3.5 |  | 1 | 1550 | 224 | 1774 | 1465.5844 | 355 | 1820.5844 | 1 | 1550 | 224 | 1465.5844 | 355
| 4 | 1.5492 | 2.11 | 2.88 | 4.42 |  |  | 4 | 3.5648 | 4.14 | 4.43 | 4.78 |  | 350 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3.5 |  | 1.5 | 1825 | 224 | 2049 | 1465.5844 | 355 | 1820.5844 | 1.5 | 1216.6667 | 149.3333 | 977.0563 | 236.6667
| 5 | 1.7748 | 2.38 | 3.23 | 5.05 |  |  | 5 | 3.8612 | 4.43 | 4.78 | 5.15 | [9 empty] | 2 | 1900 | 292 | 2192 | 1525 | 455 | 1980 | 2 | 950 | 146 | 762.5 | 227.5
| 6 | 2.0004 | 2.52 | 3.41 | 5.2 |  |  | 6 | 4.1576 | 5.15 | 5.65 | 6.2 | [9 empty] | 3 | 2350 | 375 | 2725 | 1675 | 455 | 2130 | 3 | 783.3333 | 125 | 558.3333 | 151.6667
| 8 | 2.4517 | 4.12 | 4.78 | 6.35 |  |  | 8 | 4.7504 | 6.2 | 6.9 | 7.75 | [9 empty] | 5 | 2925 | 395 | 3320 | 1975 | 545 | 2520 | 5 | 585 | 79 | 395 | 109
| 10 | 2.9029 | 4.37 | 5.15 | 7.6 |  |  | 10 | 5.3432 | 6.9 | 7.75 | 8.85 | [9 empty] | 7.5 | 5800 | 515 | 6315 | 1975 | 545 | 2520 | 7.5 | 773.3333 | 68.6667 | 263.3333 | 72.6667
| 12 | 3.3542 | 4.76 | 5.85 | 8.5 |  |  | 12 | 5.936 | 7.75 | 8.3 | 9.55 | [9 empty] | 15 | 7025 | 655 | 7680 | 3375 | 820 | 4195 | 15 | 468.3333 | 43.6667 | 225 | 54.6667
| 14 | 3.8054 | 5.5 | 6.7 | 10.55 |  |  | 14 | 6.5289 | 7.75 | 8.85 | 10.35 | [9 empty] | 20 | 7250 | 680 | 7930 | 3925 | 1100 | 5025 | 20 | 362.5 | 34 | 196.25 | 55
| 16 | 4.2567 | 7 | 8.75 | 11.6 |  |  | 16 | 7.1217 | 8.85 | 9.55 | 11.3 | [9 empty] | 25 | 9475 | 870 | 10345 | 4775 | 1100 | 5875 | 25 | 379 | 34.8 | 191 | 44
| 18 | 4.708 | 7.75 | 9.85 | 12.95 |  |  | 18 | 7.7145 | 8.85 | 10.35 | 12.4 | [9 empty] | 40 | 11900 | 1000 | 12900 | 7650 | 1375 | 9025 | 40 | 297.5 | 25 | 191.25 | 34.375
| 20 | 5.1592 | 8.65 | 10.05 | 14.65 |  |  | 20 | 8.3073 | 10.35 | 11.3 | 13.8 | [9 empty] | 50 | 16200 | 1250 | 17450 | 8375 | 1600 | 9975 | 50 | 324 | 25 | 167.5 | 32
| 24 | 6.0617 | 10.55 | 12.3 | 15.75 |  |  | 24 | 9.4929 | 10.35 | 12.4 | 15.5 | [9 empty] | 75 | 18000 | 1475 | 19475 | 11700 | 1800 | 13500 | 75 | 240 | 19.6667 | 156 | 24
| 26 | 6.513 | 10.9153 | 12.7982 | 17.3479 |  |  | 26 | 10.0857 | 10.0857 | 13.9463 | 17.0416 | [9 empty] | 100 | 22300 | 1650 | 23950 | 12900 | 1800 | 14700 | 100 | 223 | 16.5 | 129 | 18
| 30 | 7.4155 | 12.5183 | 14.5844 | 19.6934 |  |  | 30 | 11.2714 | 11.2714 | 15.6842 | 19.2682 | [9 empty] | 150 | 33100 | 2150 | 35250 | 20500 | 2125 | 22625 | 150 | 220.6667 | 14.3333 | 136.6667 | 14.1667
[22 empty] | 200 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 200 | 220.6667 | 14.3333 | 136.6667 | 14.1667
Noise/Erosion Sensitivity
| Noise Sensitivity |  |  |  |  | Noise sensitivity eqn |  |  |  |  | Erosion Max Velocity
| Pipe OD | Pipe ID | Max fps |  |  | Max V for size: | 3 | 6 | fps |  | Hours/yr operation | Max v [fps]
| 0.5 | 0.545 | 2.5424 |  |  | Max V for size: | 10 | 11 | fps |  | 0 | 15
| 0.75 | 0.785 | 3.0551 | [7 empty] | 2000 | 14
| 1 | 1.025 | 3.4942 |  |  | log(fps) =m* log(Pipe OD) + b |  |  |  |  | 3000 | 13
| 1.25 | 1.265 | 3.8846 |  |  | m | 0.50345 |  |  |  | 4000 | 12
| 1.5 | 1.505 | 4.2396 |  |  | b | 0.53795 |  |  |  | 6000 | 10
| 2 | 1.985 | 4.8736
| 2.5 | 2.469 | 5.4395 |  |  | fps = 10^0.5379*10^(0.5034*log(Pipe ID))
| 3 | 3.068 | 6.0681
| 4 | 4.026 | 6.9577
| 5 | 5.047 | 7.7963
| 6 | 6.065 | 8.5518
| 8 | 7.981 | 9.8194
| 10 | 10.02 | 11.0111
| 12 | 12 | 12.0575
| 14 | 13.25 | 12.6742
| 16 | 15.25 | 13.6038
| 18 | 17.25 | 14.4745
| 20 | 19.25 | 15.2964
| 24 | 23.25 | 16.8216
| 26 | 25.25 | 17.5352
| 30 | 29.25 | 18.8826
System and Location Defaults
Default Water Temperatures
| CHW | 50 | °F
| HW | 160 | °F
| CW | 80 | °F
Variable Flow/Variable Speed Diversity Factor
| CFCS | VFCS | VFVSFSP | VFVSRSP
| 1 | 0.6 | 0.3 | 0.2
| CFCS | Contstant Flow/ Constant Speed
| VFCS | Variable Flow/ Constant Speed
| VFVSFSP | Variable Flow/ Variable Speed with Fixed Set Point
| VFVSRSP | Variable Flow/ Variable Speed with Reset Set Point
Market Lookup
|  | Materials | Labor
| Oakland, CA | 110.2 | 127.3
| Los Angeles, CA | 103.3 | 115.1
| Fresno, CA | 103.9 | 112.3
| San Francisco, CA | 112.4 | 137.5
| San Jose, CA | 107 | 130.4
| Riverside, CA | 102.1 | 112.5
| Sacramento, CA | 106 | 113.6
| Average National | 100 | 100
ADD MARKET
Efficiencies
| Pump |  |  | Current value, based on input system gpm
| GPM |  |  | Pump | 54.85%
| Greater than | Efficiency
| 0 | 54.85%
| 60 | 57.55%
| 100 | 66.05% |  |  | Pump Efficiency eqn
| 500 | 69.71%
| 1000 | 71.85% |  |  | eff = m * ln(gpm) + b
| 1500 | 73.37% |  |  | m | 0.0587
| 2000 | 74.55% |  |  | b | 36.91%
| 2500 | 75.52%
| 3000 | 76.33%
| 3500 | 77.04%
| 4000 | 77.66%
| 4500 | 78.22%
| 5000 | 78.72%
5500
| Motor (premium) |  |  | Current value, based on calculated HP
| HP |  |  | Motor | #DIV/0!
| Greater than | Efficiency
| 0 | 89.5%
| 5 | 91%
| 10 | 92.4%
| 15 | 92.4%
| 20 | 93.6%
| 30 | 94.1%
| 40 | 94.1%
| 60 | 95%
| 75 | 95.4%
| 100 | 95.4%
| 125 | 95.8%
| 150 | 95.8%
| 200 | 95.8%
| Chiller | 0.6 | kW/ton
| Boiler | 75%
| VS Drive | 97%
Note on B8: Molly McGuire: ASHRAE HOF, flanged welded pipe fittings (factors for soldered fittings not available)
Note on C10: Molly McGuire: standard elbow
Note on D10: Molly McGuire: standard elbow
Note on J10: B&G Circuit Setter Performance Charts
Note on K10: Nibco S/T-480 up to 2", F-910 for sizes greater than 2"
Note on L10: Nibco S/T up to 2", T/F up to 12", no data for sizes > 12"
Note on M10: Nibco T-560-BR/CS/S6
Note on N10: Nibco LD/WD
Note on O10: Mueller Steam Specialty model 758
Note on P10: Taco, SD Inlet size: pipe dia Outlet size: pipe dia - 1 size
Note on Q10: Griswold Class 150 Automatic Flow Control Valve
Note on W10: Molly McGuire: From Glover Pocket Ref
Note on W11: Standard wt = Sch 40
Note on W12: Standard wt = Sch 40
Note on W13: Standard wt = Sch 40
Note on W14: Standard wt = Sch 40
Note on W15: Standard wt = Sch 40
Note on W16: Standard wt = Sch 40
Note on W17: Standard wt = Sch 40
Note on W18: Standard wt = Sch 40
Note on W19: Standard wt = Sch 40
Note on W20: Standard wt = Sch 40
Note on B21: Molly McGuire: ASHRAE HOF, welded fittings
Note on W21: Standard wt = Sch 40
Note on W22: Standard wt = Sch 40
Note on C23: Molly McGuire: standard elbow
Note on D23: Molly McGuire: Long-radius elbow
Note on W23: Standard wt = Sch 40
Note on W24: Standard wt
Note on W25: Standard wt = Sch 30
Note on W26: Standard wt = Sch 30
Note on W27: Standard wt
Note on W28: Standard wt = sch 20
Note on W29: Standard wt = sch 20
Note on W30: Standard wt
Note on W31: Standard wt
Note on U32: Molly McGuire: Steve's previous values, can be corrorborated at EngineeringToolbox.com.
Note on B53: Molly McGuire: Use ball valve for all sizes smaller than the input size.
Note on C55: Molly McGuire: 2008 RS Means Mechanical Cost Data Type L tubing, couplings & hangers 10' O.C.
Note on E55: Molly McGuire: 2008 RS Means Mechanical Cost Data solder joints, copper x copper
Note on G55: Molly McGuire: 2008 RS Means Mechanical Cost Data solder joints, copper x copper
Note on I55: Molly McGuire: 2008 RS Means Mechanical Cost Data, solder joints, copper x copper
Note on M55: Molly Mcguire: 2008 RS Means Mechanical Cost Data, Silent check, bronze trim, full flange wafer type, 150#, up to 6", size 8" references steel piping below
Note on O55: Molly McGuire: 2008 RS Means Mechanical Cost Data, Bronze, check swing, 300#, sweat, up to 3", sizes 4" and up reference steel pricing
Note on Q55: Molly McGuire: 2008 RSMeans Mechanical Cost Data, Bronze, ball, 150 psi, threaded
Note on S55: Molly McGuire: 2008 RSMeans Mechanical Cost Data, references steel pricing below
Note on U55: Molly McGuire: 2008 RSMeans Mechanical Cost Data bronze, screwed <1-1/2", flanged >=1-1/2"
Note on W55: Molly McGuire: 2008 RSMeans Mechanical Cost Data Cast Iron body with integral straightening vanes, strainer, flanged Inlet size: pipe dia Outlet size: pipe dia - 1 size
Note on K56: Molly McGuire: California Hydronics, prices as of 10/08 <=2": Bell & Gossett model: CB Circuit Setter, bronze FPT body with sweat ends >2": Bell & Bossett model CB-F, 125" flanged cast iron valves
Note on L56: Molly McGuire: 2008 RSMeans Mechanical Cost Data
Note on Y56: Molly McGuire: California Hydronics, prices as of 10/08 for Griswold valves
Note on Z56: Molly McGuire: circuit setter install costs used here, from 2002 RSMeans Mechanical Cost Data
Note on C71: Molly McGuire: 2008 RS Means Mechanical Cost Data Schedule 40, threaded up to 3/4"; welded for 1" and up Std wt pricing for sizes larger than 12" not available
Note on E71: Molly McGuire: 2008 RS Means Mechanical Cost Data Standard weight, weld joint, butt, carbon steel, long radius
Note on G71: Molly McGuire: 2008 RS Means Mechanical Cost Data Standard weight, weld joint, butt, carbon steel, long radius
Note on I71: Molly McGuire: 2008 RS Means Mechanical Cost Data Standard weight, weld joint, butt, carbon steel
Note on M71: Molly Mcguire: 2008 RS Means Mechanical Cost Data, Cast steel, silent check, 316 S.S. trim, full flange type, 150# sizes 1" to 10", sizes 12" and up are globe type, 150#, sizes 1/2" and 3/4" reference copper pricing above
Note on O71: Molly McGuire: 2008 RS Means Mechanical Cost Data, check valve, cast steel, swing type, 150#, flanged
Note on Q71: Molly McGuire: 2008 RSMeans Mechanical Cost Data, Steel, forged, ball valve, 800#, socket weld
Note on S71: Molly McGuire: 2008 RSMeans Mechanical Cost Data, Iron body, butterfly, lug type, gear operated, 200/150#
Note on U71: Molly McGuire: 2008 RSMeans Mechanical Cost Data iron body, screwed < 1 1/2", flanged >=1 1/2"
Note on W71: Molly McGuire: 2008 RSMeans Mechanical Cost Data Cast Iron body with integral straightening vanes, strainer, flanged Inlet size: pipe dia Outlet size: pipe dia - 1 size
Note on D72: Molly McGuire: labor + equip
Note on K72: Molly McGuire: California Hydronics, prices as of 10/08 <=2": Bell & Gossett model: CB Circuit Setter, bronze FPT body with sweat ends >2": Bell & Bossett model CB-F, 125" flanged cast iron valves
Note on L72: Molly McGuire: 2008 RSMeans Mechanical Cost Data
Note on Y72: Molly McGuire: California Hydronics, prices as of 10/08 for Griswold valves
Note on Z72: Molly McGuire: 2008 RSMeans Mechanical Cost Data, circuit setter costs used here
Note on C85: Molly McGuire: Prices for 10" and 12" steel pipe are typos in Means.
Note on B95: Molly McGuire: RS Means 2008 Fiberglass, with all service jacket
Note on I95: Molly McGuire: RS Means 2008 Fiberglass, with all service jacket
Note on AE95: Cost per HP, based on table to left
Note on X96: Molly McGuire: RS Means Mechanical Cost Data 2008 <= 1 HP: In-line centrifugal, cast iron, flange connection > 1 HP, <=20 HP: In-line centrifugal, cast iron, flange connection, Close coupled, end suction, bronze impeller > 25 HP: Centrifugal, end suction, base mounted, horizontal split case, drip proof motor, single stage, rated at 100' head
Note on AA96: Molly McGuire: Contractor cost from Dave Eisenberg, 10/07
Note on W120: Molly McGuire: Greater than 200 HP, use $/HP for each, see formula for calc
Note on X120: Molly McGuire: Greater than 200 HP, use $/HP for each, see formula for calc
Note on Y120: Molly McGuire: Greater than 200 HP, use $/HP for each, see formula for calc
Note on Z120: Molly McGuire: Greater than 200 HP, use $/HP for each, see formula for calc
Note on AA120: Molly McGuire: Greater than 200 HP, use $/HP for each, see formula for calc
Note on AB120: Molly McGuire: Greater than 200 HP, use $/HP for each, see formula for calc
Note on AC120: Molly McGuire: Greater than 200 HP, use $/HP for each, see formula for calc
Note on B125: Molly McGuire Noise-sensitive piping is limited to the following velocities. Limits are based on a linear interpolation between 3 fps for a 3/4" pipe and 20 fps for a 30" pipe.
Note on G125: Molly McGuire: From Wilson
Note on L126: Molly McGuire: If hours value is greater than or equal to this number (but less than the subsequent value in the table) use the corresponding fps limit.
Note on D165: Molly McGuire: From RS Means Mechanical Cost Data 2008
Note on F185: Molly McGuire: Based on Bell & Gossett selections for models 1531, 1510, and VSC. Table values to the left reflect a 10% reduction from calculated values, as the calculated values are the maximum efficiency at that point.

## Versions (hidden)
Version | Update | Requested by | Date Completed
1.1 | Added cost escalation feature to bring 2002 Means costs to present.
1.1 | Changed display of system head, with and without safety factor.
1.2 | Delete the two pull downs that ask if escalation and inflation apply. If people want no inflation they can enter a zero. | Steve | 2008-05-20
1.2 | We need to figure out some way of detecting whether the Optimize button needs to be repressed. Perhaps after you press the button, the button grays out and the LCC cost gets copied to a hidden cell. Then if the LCC in cell B18 ever differs from the hidden cell value, you know that an input was changed so you can un-gray out the button, indicating that it must be repressed. | Steve | 2008-05-21
| Add buttons for 189.1 and 90.1 compliance | Steve
1.4 | Updated to Excel 2007
1.5 | Unlocked input cells on "System Assumptions" | Steve | 2010-05-13
| Remove "optimize" button de-activation macro so that the undo command works | Steve | 2010-05-13
1.6 | Updated changeover from ball to butterfly valve from 2.5" to 3". Now all pipes 3" and larger will have butterfly valves, all pipes 2.5" and smaller will have ball valves. Also added a pull-down menu to the "Constants" sheet to change this in the future. Current year updated to 2011. | Steve | 2011-01-07