## Point List
Point List
Point |  |  | System and Service | Sensor |  | Features | [10 empty] | Notes
Name |  | Number |  | Type | Accuracy | Alarms |  |  |  | Trending
[6 empty] | Limit |  | Warning |  | Samples1 | Commissioning5 |  |  | Operating5
[6 empty] | Hi | Lo | Hi | Lo |  | Time2 | Local3 | Archive4 | Time2 | Local3 | Archive4
Analog Inputs
| System Supply Tempeature |  | Control
| Cooling LWT |  | Monitoring, could also control cooling tower fan speed
| System DP - Remote Point |  | Optimize pump speed
| System DP - Local Point |  | Control pump speed
Analog Outputs
VFD SCommand
Digital Inputs
Digital Outputs
VFD Start/Stop
Safety Interlocks (Hardwired to shut down the system. Safeties shall funciton no matter what position the equipments Hand-Off-Auto, Inverter-Bypass, or other selector switches are in)
Network Points
Virtual Points
Notes:
1 | Samples indicates the minimum number of data samples that must be held in the local controller if it is trending the point.
2 | Time indicates the required sampling time for the trending function.
3 | A check in the local column indicates that the trending only needs to be running in the local controller and the most recent value can write over the last value when the trend buffer fills up.
4 | A check in the archive column indicates that the trend data must be archived to the system hard disc when trend buffer fills up so that a continuous trend record is maintained.
5 | Commissioning trending requirements only need to be implemented during the start-up and warranty year. After the start-up and warranty process, the control contractor should set the trending parameters to the operating requirements listed if they differ from the commissioning requirements.
6
7
8
9
10
11
12
Formatted Blank Rows