## Current Revision Summary
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com | [24 empty] | Integration Cost Summary
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com | [24 empty] | Layer 1 integration (Makes the data from 24 indoor units visible in the Siemens system) | 0
Engineering Calculation | [24 empty] | Layer 2 integration (Makes the data from 1 outdoor unit visible in the Siemens system) | 0
Date: | 2017-12-26 15:46 | [23 empty] | Layer 3 integration (Makes the Mitsubishi maintenance tool remotely accessible) | 0
Project Name: | Bureacratic Affairs Building | [23 empty] | Total | 0
Project Number: | None
Engineer: | David
Assumptions
1 | Per point costs are from Darrens FS-32 estimate for physical points, which had some roots in our other work and hit very close to Siemens estimate. I adjusted his per point costs for network points and virtual points to reflect how I take those off.
2 | Physical Points - | 1000 | Expensive analog points and "typical" points
|  | 750 | Low Cost analog points (allows you to discount points you know will not be expensive)
3 | Virtual Points - | 75
4 | Hardwired Interlock - | 300
5 | Packaged System Network Points - | 12
6 | Complex System Network Points - | 150
7 | Assumed labor rate - | 150
8 | The lump sum column allows you to "goose" points like ultrasonic flow meters that could be really expensive and higher than the "typical" point.
9 | The take-off in this spreadsheet is based on this set of documents -
| The cells in these columns need to be populated manually or by linking them to the system take-offs in the other tabs | [11 empty] | The cells in these columns will calcuate based on the inputs from yellow headers
| System | Number of Similar Systems | Per System Point Count | [9 empty] | Total for All Similar Systems | [9 empty] | Cost per typical unit/system | Cost per unit/system type
| Manually enter data in these cells or link them up with point take-offs on the other tabs. Cells to link are color coded. If you need to add rows copy a blank row and insert it as many times as you need somewhere before the last row and after the first row. |  | High Cost AI | Low Cost AI | AO | DI | DO | Hardwired | Virtual | Packaged System Network Point | Complex System Network Point | Lump Sum | High Cost AI | Low Cost AI | AO | DI | DO | Hardwired | Virtual | Packaged System Network Point | Complex System Network Point | Lump Sum
| Central Chilled Water Plant.Chilled Water System-? (Typical of 1) | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 6 | 0 | 0 | 1200 | 0 | 1 | 0 | 0 | 1 | 1 | 6 | 0 | 0 | 1200 | 3700 | 3700
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTALS | [11 empty] | 0 | 1 | 0 | 0 | 1 | 1 | 6 | 0 | 0 | 1200 |  | Cross-check
| Physical Point Cost - | 1750 |  | Calculated
| Virtual Point Cost - | 450 |  | Calculated
| Hardwired Point Cost - | 300 |  | Calculated
| Lump Sum Cost - | 1200 |  | Calculated
| Packaged System Network Points - | 0 |  | Calculated
| Complex System Network Points - | 0 |  | Calculated
| Subtotal - | 3700 |  | Cross-check (Calculated) | [19 empty] | 3700
| Contingency factor - | 15% |  | Manual Entry
| Contingency - | 555 |  | Calculated
| TOTAL - | 4255 |  | Calculated
0
3700
370
4070

## Evaporator Pump Addition
[6 empty] | The full object name is the composed of the building and system segments below plus the subsystem and device descriptor segments associated with each point in the system. The maximum character count is 30 characters. Enter segment character count targets in the colored cells with red outlines in row 8 columns B, D, and row 5 and 6, column X. The target sum automatically totals up and turns red if you exceed the limit. The spreadsheet 2018-04-20 Point Name Structure v1.xlsx describes the naming convention in detail, as does the Standard Object Naming section of the specification.) | [13 empty] | Character Count; "Actual" goes from green to red as limit is approached
[7 empty] | System Name - | Central Chilled Water Plant.Chilled Water System-? | Assembled from selections | [10 empty] | Segments |  | Entire Name Maximum with Periods
[7 empty] | Object Name - Building and System Segments - | CentPl.CHW-? | Assembled from selections | Abbreviation | Description | [5 empty] | Links to Lists |  |  | Tgt. | Act. |  |  |  | Central Chilled Water Plant.Chilled Water System-? (Typical of 1)
[7 empty] | Building Segment Selection - | Central Chilled Water Plant | From drop down menu | CentPl | Central Chilled Water Plant | [5 empty] | Building List |  |  | 7 | 7 | 30 | Desired Total |  | General Comments: (Manual Entry) | None
Character Count | Subsystem Segment |  | Descriptor Segment |  |  |  | System Segment Selection - | Chilled Water System | From drop down menu | CHW | Chilled Water System | [5 empty] | System Level List |  |  | 7 | 4 | 30 | Target Sum
[7 empty] | System Number - | ? | Manual Entry | ? | ? | [13 empty] | Point Description | Point Type | [9 empty] | Cost Estimate Notes
Target ► | 8 |  | 8 |  |  |  | Number of similar Systems - | 1 | Manual Entry | [16 empty] | High Cost AI | Low Cost AI | AO | DI | DO | Hardwired | Virtual | Packaged System Network Point | Complex System Network Point | Lump Sum (enter $ value, not X)
Total for the point with all segments (red means the maximum count is exceeded) ▼ | System | Number (Optional) | Descriptor 1 | Descriptor 2 | Number (Optional) | The data in these columns should be manually entered as the control system design evolves. This data will automatically populate the budget estimate point list to the right other than the lump sum value, general comments and cost estimate notes, which must be manually entered.
| Select using the drop down list for each point | Manually enter a number or text. Use an appostrophe ahead of the entry so it is interpreted as text and allow the other formulas to work; i.e. enter'01 vs. 01 | Select using the drop down list for each point | Select using the drop down list for each point | Manually enter a number or text. Use an appostrophe ahead of the entry so it is interpreted as text and allow the other formulas to work; i.e. enter'01 vs. 01 | The heading for the point list will be autmatically generated from the information entered above. |  |  | Click here to jump to a column that contains the full object name including all segments
Entering "Existing" into the "Sensor Type" column will prevent any cost from being tabulated for the point in the cost estimate point list.
[6 empty] | These columns are automatically generated using the point name tool in columns A-F |  |  | Use the drop down in this column to pick the appropriate sensor | These columns are filled in based on the sensor selection |  | These columns are filled in manually based on project requirements
Central Chilled Water Plant.Chilled Water System-? (Typical of 1)
[6 empty] | Point |  |  | Sensor |  |  | Features | [10 empty] | Notes
[6 empty] | Name (Note 6) |  | Description and Service | Type | Reference Spec Paragraph | Accuracy | Alarms |  |  |  | Trending
[12 empty] | Limit |  | Warning |  | Samples1 | Commissioning5 |  |  | Operating5
[12 empty] | Hi | Lo | Hi | Lo |  | Time2 | Local3 | Archive4 | Time2 | Local3 | Archive4
Analog Inputs | [5 empty] | Analog Inputs | [17 empty] | Full point object names | Analog Inputs (These cells will automatically fill in from the main point list) | [9 empty] | Manual Entry
High Cost -- HIDE THIS ROW AND "Not Used" ROWS BEFORE PRINTING
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
[6 empty] | Low Cost -- HIDE THIS ROW AND "Not Used" ROWS BEFORE PRINTING | [17 empty] | CentPl.CHW-?.
24 | Pump - Chilled Water | -06 | Electrical - Current | Top of list |  |  | CHWPmp-06.Cur | Chilled Water Pump-06 Current | Current Transformer | 25 35 00 | +/-2% full scale | N/A | N/A | Note 8 |  | 60 | 1 min | X | X | 1 min | X | X | Note 7 | CentPl.CHW-?.CHWPmp-06.Cur | CHWPmp-06.Cur |  | X
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Analog Outputs (All analog outputs to include local override capability and status indication at the controller) | [5 empty] | Analog Outputs (All analog outputs to include local override capability and status indication at the controller) | [17 empty] | CentPl.CHW-?. | Analog Outputs (All analog outputs to include local override capability and status indication at the controller)
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Digital Inputs | [5 empty] | Digital Inputs | [17 empty] | CentPl.CHW-?. | Digital Inputs
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Digital Outputs (All digital outputs to include local override capability and status indication at the controller) | [5 empty] | Digital Outputs (All digital outputs to include local override capability and status indication at the controller) | [17 empty] | CentPl.CHW-?. | Digital Outputs (All digital outputs to include local override capability and status indication at the controller)
27 | Pump - Chilled Water | -06 | Command - Start/Stop | Top of list |  |  | CHWPmp-06.StrStp | Chilled Water Pump-06 Start/Stop Command | Relay Output | 25 35 13 | N/A | N/A | N/A | Note 9 |  | 10 | COV | X | X | COV | X | X |  | CentPl.CHW-?.CHWPmp-06.StrStp | CHWPmp-06.StrStp |  |  |  |  | X |  |  |  |  | 1200 |  | Lump sum is provided to create budget for adapting the existing plant staging software to the new pump and verfifying it.
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Safety Interlocks (Hardwired to shut down or otherwise manipulate the system. Safeties shall function no matter what position the equipment's Hand-Off-Auto, Inverter-Bypass, or other selector switches are in) | [5 empty] | Safety Interlocks (Hardwired to shut down or otherwise manipulate the system. Safeties shall function no matter what position the equipment's Hand-Off-Auto, Inverter-Bypass, or other selector switches are in) | [17 empty] | CentPl.CHW-?. | Safety Interlocks (Hardwired to shut down or otherwise manipulate the system. Safeties shall function no matter what position the equipment's Hand-Off-Auto, Inverter-Bypass, or other selector switches are in)
26 | Pump - Chilled Water | -06 | Switch - Motor Overload - Manual Reset | Top of list |  |  | CHWPmp-06.MtrOL | Chilled Water Pump-06 Motor Overload | Hard Wired | 25 35 00 | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A |  | CentPl.CHW-?.CHWPmp-06.MtrOL | CHWPmp-06.MtrOL | [5 empty] | X
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Virtual Points | [5 empty] | Virtual Points | [17 empty] | CentPl.CHW-?. | Virtual Points
24 | Pump - Chilled Water | -06 | Status - Proof of Operation | Top of list |  |  | CHWPmp-06.PRF | Chilled Water Pump-06 Proof of Operation | N/A | 25 35 00 | N/A | N/A | N/A | N/A | N/A | 10 | COV | X | X | COV | X | X | Note 7, 8 | CentPl.CHW-?.CHWPmp-06.PRF | CHWPmp-06.PRF | [6 empty] | X
29 | Pump - Chilled Water | -06 | Time - Hours | Time - Totalizer |  |  | CHWPmp-06.HrsTotal | Chilled Water Pump-06 Hours Totalizer | N/A | 25 35 00 | N/A | N/A | N/A | N/A | N/A | 24 | 1 hr | X | X | 1 hr | X | X | Note 11 | CentPl.CHW-?.CHWPmp-06.HrsTotal | CHWPmp-06.HrsTotal | [6 empty] | X
20 | Electrical System |  | Average | Electrical - Voltage |  |  | kW.AvgVlt | Electrical System Average Voltage | N/A | 25 35 00 | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | Note 12 | CentPl.CHW-?.kW.AvgVlt | kW.AvgVlt | [6 empty] | X
22 | Electrical System |  | Average | Electrical - Phase Angle |  |  | kW.AvgPhAng | Electrical System Average Phase Angle | N/A | 25 35 00 | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | Note 7 | CentPl.CHW-?.kW.AvgPhAng | kW.AvgPhAng | [6 empty] | X
23 | Pump - Chilled Water | -06 | Electrical - kW | Top of list |  |  | CHWPmp-06.kW | Chilled Water Pump-06 kW | N/A | 25 35 00 | N/A | N/A | N/A | N/A | N/A | 60 | 1 min | X | X | 15 min | X | X | Note 7 | CentPl.CHW-?.CHWPmp-06.kW | CHWPmp-06.kW | [6 empty] | X
29 | Pump - Chilled Water | -06 | Electrical - kWh | Time - Totalizer |  |  | CHWPmp-06.kWhTotal | Chilled Water Pump-06 kWh Totalizer | N/A | 25 35 00 | N/A | N/A | N/A | N/A | N/A | 24 | 1 hr | X | X | 1 hr | X | X | Note 7 | CentPl.CHW-?.CHWPmp-06.kWhTotal | CHWPmp-06.kWhTotal | [6 empty] | X
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Network Points | [5 empty] | Network Points | [17 empty] | CentPl.CHW-?. | Network Points
[6 empty] | Packaged System Network Point -- HIDE THIS ROW AND "Not Used" ROWS BEFORE PRINTING | [17 empty] | CentPl.CHW-?.
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
[6 empty] | Complex System Network Point -- HIDE THIS ROW AND "Not Used" ROWS BEFORE PRINTING | [17 empty] | CentPl.CHW-?.
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
[6 empty] | Notes: | [18 empty] | Totals | 0 | 1 | 0 | 0 | 1 | 1 | 6 | 0 | 0 | 1200
[6 empty] | 1 | Samples indicates the minimum number of data samples that must be held in the local controller if it is trending the point. | [17 empty] | Notes:
[6 empty] | 2 | Time indicates the required sampling time for the trending function. COV indicates a sample should be taken on a Change Of Value. | [17 empty] | 1. (Placeholder)
[6 empty] | 3 | A check in the local column indicates that the trending only needs to be running in the local controller and the most recent value can write over the last value when the trend buffer fills up.
[6 empty] | 4 | A check in the archive column indicates that the trend data must be archived to the system hard disc when trend buffer fills up so that a continuous trend record is maintained.
[6 empty] | 5 | Commissioning trending requirements only need to be implemented during the start-up and warranty year. After the start-up and warranty process, the control contractor should set the trending parameters to the operating requirements listed if they differ from the commissioning requirements. | [17 empty] | Cost Assumptions
[6 empty] | 6 | Point numbers are based on the Owner's point naming convention which is included in the specification. Point names will be verified during the submittal process in the control system integration and coordination meeting. | [24 empty] | Physical Points - | 1000
[6 empty] | 7 | Monitor amps to provide a proof of operation in put and create a virtual meter to track energy use using voltage and power factor constants determined during commissioning. Accumulate and display current demand level, kWh for the day, and kWh for the previous day, calendar month, and calendar year. Archive data to the data to the dedicated archival data storage drive in the Hotel's Data Center. | [25 empty] | 750
[6 empty] | 8 | Provide a warning alarm when the motor current reaches the service factor rating or motor starter overload rating, which ever is lower; coordinate the setting in the field with the electrician. | [24 empty] | Virtual Points - | 75
[6 empty] | 9 | Issue an alarm if the pump is commanded on and there is no proof of operation with-in 10 seconds. Issue and alarm if the pump is commanded off and the proof of operation point still is active after 1 minute (adjustable). | [24 empty] | Hardwired Interlock - | 300
[6 empty] | 10 | This point is furnished by the electrician in their starter and is only listed here to provide a complete list of the points that could affect the operation of CHWP-5. | [24 empty] | Packaged System Network Points - | 12
[6 empty] | 11 | Create a virtual meter to accumuluate hours of operation. Accumulate and display hours for for the day, and hours for the previous day, calendar month, and calendar year. Archive data to the data to the dedicated archival data storage drive in the Hotel's Data Center. | [24 empty] | Complex System Network Points - | 150
[6 empty] | 12 | [25 empty] | Assumed labor rate - | 150
13
14
15
16
17
18
19
20
21
22

## Building List
Selection Text and Description Text | Abbreviation
Top of list
Central Chilled Water Plant | CentPl
Cooling Tower Yard | CTYard
Condenser Water Pump Room | CWPump
North Level 1 Mechanical Room | L1NAHU
Future 03 | Fut03
Future 04 | Fut04
Future o5 | Fut05
Future 06 | Fut06 | test
Future 07 | Fut07
Future 08 | Fut08
Future 09 | Fut09
Future 10 | Fut10
Future 11 | Fut11
Future 12 | Fut12
Future 13 | Fut13
Future 14 | Fut14
Bottom of list

## System Level List
Jump to Revision History
Selection Text | Abbreviation | Description Text |  | For specification section (Sorted by Descriptive Text)
Top of list
Air Handling - Air Handling Unit | AHU | Air Handling Unit | Insert or Delete Rows to Add or Delete Systems by Inserting Them Between the Higlighted Rows | Air Handling Unit | AHU
Air Handling - Dedicated Outdoor Air System | DOAS | Dedicated Outdoor Air System |  | Alarm | Alrm
Air Handling - Heat Recovery Ventilator | HRV | Heat Recovery Ventilator |  | Automation Level Network | ALN
Air Handling - Roof Top Unit | RTU | Roof Top Unit |  | Boiler Systems | Blr
Alarm | Alrm | Alarm |  | Building Level Network | BLN
Automation Level Network | ALN | Automation Level Network |  | Building System | Bld
Boiler Systems | Blr | Boiler Systems |  | Building Wide | BldWd
Building Level Network | BLN | Building Level Network |  | Cabinet Unit Heater | CUH
Building System | Bld | Building System |  | Chemical Treatment System | Chm
Building Wide | BldWd | Building Wide |  | Chilled Water System | CHW
Cabinet Unit Heater | CUH | Cabinet Unit Heater |  | Compressed Air | CA
Chemical Treatment System | Chm | Chemical Treatment System |  | Computer Room Unit | CRU
Chilled Water System | CHW | Chilled Water System |  | Condensate System | Cnd
Chilled Water System - Laboratory Loads | CHWLb | Lab Loads Chilled Water System |  | Condenser Water System | CW
Chilled Water System - Research Loads | CHWRs | Research Loads Chilled Water System |  | Control Air System | CtA
Chilled Water System - Tennant Loads | CHWTn | Tennant Loads Chilled Water System |  | Cooling System | ClgSys
Compressed Air System | CA | Compressed Air |  | Cooling Tower System | CT
Compressed Air System - Control Air | CtA | Control Air System |  | Dedicated Outdoor Air System | DOAS
Compressed Air System - Laboratory Air | LA | Laboratory Air |  | Direct Expansion System | DX
Compressed Air System - Medical Compressed Air | MCA | Medical Compressed Air |  | Domestic Cold Water System | DCW
Compressed Air System - Process Air | PA | Process Air |  | Domestic Hot Water System | DHW
Computer Room Unit | CRU | Computer Room Unit |  | Electrical System | KW
Condensate System | Cnd | Condensate System |  | Emergency Power System | kW
Condenser Water System | CW | Condenser Water System |  | Exhaust System | Exh
Condenser Water System - Laboratory Loads | CWLb | Lab Loads Condenser Water System |  | Field Panel | Pnl
Condenser Water System - Process Loads | CWPr | Process Loads Condenser Water System |  | Fire Alarm System | FA
Condenser Water System - Research Loads | CWRs | Research Loads Condenser Water System |  | Floor Heating System | FlH
Condenser Water System - Tennant Loads | CWTn | Tennant Loads Condenser Water System |  | Floor Level Network | FLN
Cooling System | ClgSys | Cooling System |  | Furnace | Frnc
Cooling Tower System | CT | Cooling Tower System |  | Heat Pump Loop | HtPmp
Direct Expansion System | DX | Direct Expansion System |  | Heat Recovery System | HRc
Domestic Cold Water System | DCW | Domestic Cold Water System |  | Heat Recovery Ventilator | HRV
Domestic Hot Water System | DHW | Domestic Hot Water System |  | Heating System | HtgSys
Electrical System | KW | Electrical System |  | Hot Water System | HWS
Emergency Power System | kW | Emergency Power System |  | Industrial Cold Water | ICW
Exhaust System | Exh | Exhaust System |  | iPhone MobiLinc Application | iPhn
Field Panel Resident Objects ( is the panel number, all panels shall have a number) | Pnl | Field Panel |  | Lab Loads Chilled Water System | CHWLb
Fire Alarm System | FA | Fire Alarm System |  | Lab Loads Condenser Water System | CWLb
Floor Heating System | FlH | Floor Heating System |  | Laboratory Air | LA
Floor Level Network | FLN | Floor Level Network |  | Laboratory Vacuum | LVa
Furnace | Frnc | Furnace |  | Lighting System | LT
Heating System | HtgSys | Heating System |  | Make-up Air System | MAU
Heat Pump Water | HtPmp | Heat Pump Loop |  | Master | Mstr
Heat Recovery System | HRc | Heat Recovery System |  | Mechanical Equipment Room System | MER
Hot Water System | HWS | Hot Water System |  | Medical Compressed Air | MCA
Industrial Cold Water | ICW | Industrial Cold Water |  | Medical Vacuum | MVa
iPhone MobiLinc Application | iPhn | iPhone MobiLinc Application |  | Metering System | Mtr
Lighting System | LT | Lighting System |  | Natural Gas System | Gas
Make-up Air System | MAU | Make-up Air System |  | Process Air | PA
Master | Mstr | Master |  | Process Loads Condenser Water System | CWPr
Mechanical Equipment Room System | MER | Mechanical Equipment Room System |  | Process Vacuum | PVa
Metering System | Mtr | Metering System |  | Remote Control | Remote
Miscellaneous and General Purpose Fan System | Fan | Utility Fan System |  | Research Loads Chilled Water System | CHWRs
Natural Gas System | Gas | Natural Gas System |  | Research Loads Condenser Water System | CWRs
Remote Control | Remote | Remote Control |  | Roof Top Unit | RTU
Room Object | Rm | Room |  | Room | Rm
Security Systems | Sec | Security Systems |  | Security Systems | Sec
Site Wide Applicable Data | Site | Site Wide |  | Site Wide | Site
Split System | SpS | Split System |  | Split System | SpS
Sprinkler System | Spr | Sprinkler System |  | Sprinkler System | Spr
Steam System | Stm | Steam System |  | Steam System | Stm
Sump Pump System | Smp | Sump Pump System |  | Sump Pump System | Smp
Vacuum System | VAC | Vacuum |  | Tennant Loads Chilled Water System | CHWTn
Vacuum System - Laboratory Vacuum | LVa | Laboratory Vacuum |  | Tennant Loads Condenser Water System | CWTn
Vacuum System - Medical Vacuum | MVa | Medical Vacuum |  | Utility Fan System | Fan
Vacuum System - Process Vacuum | PVa | Process Vacuum |  | Vacuum | VAC
Variable Flow Refrigeration System | VRF | Variable Flow Refrigeration System |  | Variable Flow Refrigeration System | VRF
Bottom of list
| Revision History | Back to Top
| Created | 2018-01-01 13:14
| Rev 1 | 2018-04-20 18:01

## Component Lvl List
Jump to Revision History
Selection Text | Abbreviation | Description Text
Top of list
Air - Exhaust Air | ExA | Exhaust Air
Air - Mixed Air | MA | Mixed Air
Air - Outdoor Air | OA | Outdoor Air
Air - Return Air | RA | Return Air
Air - Supply Air | SA | Supply Air
Alarm | Alrm | Alarm | Insert or Delete Rows to Add or Delete Subsystems by Inserting Them Between the Higlighted Rows
Back Flow Preventer | BFP | Back Flow Preventer
Back Flow Preventer - Reduced Pressure Principle | RPBFP | Reduced Pressure Principle Back Flow Preventer
Bypass | Bypas | Bypass
Cabinet Unit Heater | CUH | Cabinet Unit Heater
Chiller - Absorption | AbChl | Absorption Chiller
Chiller - Centrifugal | CnChl | Centrifugal Chiller
Chiller - Reciprocating | ReChl | Reciprocating Chiller
Chiller - Screw | ScwChl | Screw Chiller
Chiller - Scroll | SclChl | Scroll Chiller
Coil - Cooling | ClCoil | Cooling Coil
Coil - Direct Expansion | DXCoil | Direct Expansion Coil
Coil - Hot Gas Reclaim | HGRCoil | Hot Gas Reclaim Coil
Coil - Preheat | PHCoil | Preheat Coil
Coil - Reheat | RHCoil | Reheat Coil
Coil - Warm-up | WUCoil | Warmup Coil
Compressor | Cm[ | Compressor
Compressor - Refrigeration | RefCmp | Refrigeration Compressor
Compressor - Air | AirCmp | Air Compressor
Condenser | Cnd | Condenser
Condenser - Air Cooled | ACCond | Air Cooled Condenser
Condenser - Water Cooled | WCCnd | Water Cooled Condenser
Condensing Unit - Air Cooled | ACCdU | Air Cooled Condensing Unit
Cooling | Clg | Cooling
Cooling Tower - Forced Draft | FrDCT | Forced Draft Cooling Tower
Cooling Tower - Induced Draft | InDCT | Induced Draft Cooling Tower
Crankcase | CrkCs | Crankcase
Crankcase Heater | CcHtr | Crankcase Heater
Diagnostic | Diag | Diagnostic
Discharge | Dschg | Discharge
Duct | Duct | Duct
Economizer | Econ | Economizer
Electric Duct Heater | EDH | Electric Duct Heater
Electrical System | kW | Electrical System
Emergency Generator | EmGen | Emergency Generator
Entering | Ent | Entering
Evaporator | Evap | Evaporator
Exhaust | Exh | Exhaust
Exhaust - Exhaust Side | ExhSd | Exhaust Side
Fan | Fan | Fan
Fan - Condenser | CndFn | Condenser Fan
Fan - Exhaust | ExhFn | Exhaust Fan
Fan - Relief | RelFn | Relief Fan
Fan - Return | RetFn | Return Fan
Fan - Supply | SupFn | Supply Fan
Fan - Induction | IndFn | Induction Fan
Fan Coil Unit - Direct Expansion Coil | FnCDx | Direct Expansion Fan Coil Unit
Fan Coil Unit- Water Coil | FnCWt | Chilled Water Fan Coil Unit
Flame | Flm | Flame
Filter | Fltr | Filter
Filter - Chemical | ChFlt | Chemical Filter
Filter - Final | FnFlt | Final Filter
Filter - HEPA | HPFlt | HEPA Filter
Filter - Prefilter | PrFlt | Prefilter
Finned Tube Radiation | FTR | Finned Tube Radiation
Fire Alarm | FirAlm | Fire Alarm
Floor Heating System | FlHt | Radiant Floor Heating System
Floor Level Network | FLN | Floor Level Network
Furnace | Frnc | Furnace
Furnace - Gas | GsFrnc | Gas Furnace
Generator | Gen | Generator
Heating | Htg | Heating
Heat Exchanger | Hx | Heat Exchanger
Heat Exchanger - Plate and Frame | PFHx | Plate and Frame Heat Exchanger
Heat Exchanger - Shell and Tube | STHx | Shell and Tube Heat Exchanger
Heat Recovery System | HtRec | Heat Recovery System
Heat Recovery System - Air to Air Plate Heat Exchanger | PltHx | Air to Air Plate Heat Exchanger
Heat Recovery System - Energy Wheel | NrgWhl | Energy Wheel
Heat Recovery System - Enthalpy Wheel | EnthWhl | Enthalpy Wheel
Heat Recovery System - Hot Gas Reclaim Reheat | HGRH | Hot Gas Reheat
Heater | Htr | Heater
Humidifier - Primary | PrHum | Primary Humidifier
Humidifier - Secondary | ZnHum | Secondary Humidifier
Indoor Unit | IDU | Indoor Unit
Inlet | Inlet | Inlet
Leaving | Lvg | Leaving
Lighting | Lght | Lighting
Lighting Panel | LgtPn | Lighting Panel
Lock-out | LkOt | Lock-out
Make-up Air Systems | MAU | Make-up Air System
Metering System | Mtr | Metering System
Oil | Oil | Oil
Outdoor Air Condition | OA | Outdoor Air
Outdoor Unit | ODU | Outdoor Unit
Pump | Pmp | Pump
Pump - Boiler Circulation | BlrPmp | Boiler Circulation Pump
Pump - Booster | BstPmp | Booster Pump
Pump - Chilled Water | CHWPmp | Chilled Water Pump
Pump - Coil Circulator | CirPmp | Coil Circulation Pump
Pump - Condensate | CndPmp | Condensate Pump
Pump - Condenser Water | CWPmp | Condenser Water Pump
Pump - Distribution | DistPmp | Distribution Pump
Pump - Domestic Hot Water | DHPmp | Domestic Hot Water Pump
Pump - Evaporator | EvpPmp | Evaporator Pump
Pump - Feedwater | FdWPmp | Feedwater Pump
Pump - Hot Water | HWPmp | Hot Water Pump
Pump - Sand Filter | SndPmp | Sand Filter Pump
Pump - Sump | SmpPmp | Sump Pump
Pump - Vacuum Condensate Type | VacPmp | Vacuum Condensate Pump
Recirculation | Recir | Recirculation
Relief | Rel | Relief
Return | Ret | Return
Return - Return Side | RetSd | Return Side
Room Objects (Where is the room number) | Rm | Room
Security | Sec | Security
Siemens Field Panel Resident Objects ( is the panel number, all panels shall have a number) | PNL | Siemens Field Panel Object
Sprinkler | Spr | Sprinkler
Steam | Stm | Steam
Supply | Sup | Supply
Supply - Supply Side | SupSd | Supply Side
System | Systm | System
Tank | Tnk | Tank
Terminal Unit - Terminal Equipment Controller | TEC | Terminal Unit - Terminal Equipment Controller
Terminal Unit - Parallel Fan Powered Terminal Unit | ParFT | Parallel Fan Powered Terminal Unit
Terminal Unit - Constant Air Volume Reheat Terminal Unit | CAVRh | Constant Air Volume Reheat Unit
Terminal Unit - Constant Air Volume Terminal Unit | CAV | Constant Air Volume Unit
Terminal Unit - Series Fan Powered Terminal Unit | SerFT | Series Fan Powered Terminal Unit
Terminal Unit - Terminal Equipment Controller Update Trigger (used with Field Panel system name) | TECUp | TEC Update Trigger
Terminal Unit - Variable Air Volume Reheat Terminal Unit | VAVRh | Variable Air Volume Reheat Unit
Terminal Unit - Variable Air Volume Terminal Unit | VAV | Variable Air Volume Unit
Trigger | Trgr | Trigger
Unit | Unit | Unit
Unit Heater | UH | Unit Heater
Variable Speed Drive | VSD | Variable Speed Drive
Vent | Vnt | Vent
Vent Stack | VntStk | Vent Stack
Zone | Zn | Zone
Bottom of list
| Revision History | Back to Top
| Created | 2018-01-01 13:14
| Rev 1 | 2018-04-20 17:59

## Device Descriptor List
Jump to Revision History
Selection Text | Abbreviation | Description Text
Top of list
Accumulator | Accum | Accumulator
Adjustment | Adj | Adjustment
Air | Air | Air
Air - Mixed Air | MA | Mixed Air
Air - Outdoor Air | OA | Outdoor Air
Air - Return Air | RA | Return Air
Air - Supply Air | SA | Supply Air
Air Flow Measuring Devices | AFM | Air Flow Measuring Station
Air Temperature - Bypass Deck Temperature | BDkT | Bypass Deck Temperature
Air Temperature - Cold Deck Temperature | CDkT | Cold Deck Temperature
Air Temperature - Entering Air Temperature | EAT | Entering Air Temperature
Air Temperature - Hot Deck Temperature | HDkT | Hot Deck Temperature
Air Temperature - Leaving Air Temperature | LAT | Leaving Air Temperature
Air Temperature - Mixed Air | MAT | Mixed Air Temperature
Air Temperature - Neutral Deck Temperature | NDkT | Neutral Deck Temperature
Air Temperature - Outdoor Air Temperature | OAT | Outdoor Air Temperature
Air Temperature - Return Air Temperature | RAT | Return Air Temperature
Air Temperature - Space Temperature | SpTmp | Space Temperature
Air Temperature - Supply Air | SAT | Supply Air Temperature
Air Temperature - Zone Temperature | ZnTmp | Zone Temperature
Alarm | Alm | Alarm
Automation Level Network | ALN | Automation Level Network
Average | Avg | Average
British Thermal Unit | BTU | BTU
Building Level Network | BLN | Building Level Network
Burner | Brnr | Burner
Chilled Water | CHW | Chilled Water
Close | Cls | Close
Command | Cmd | Command
Command - Disable | Disabl | Disable Command
Command - Enable | Ena | Enable Command
Command - High/Low Speed Command | HiLoCmd | High/Low Speed Command
Command - Latch Off | LchOff | Latch Off Command
Command - Latch On | LchOn | Latch On Command
Command - Modulation | ModCmd | Modulation Command
Command - Off | Off | Off Command
Command - On | On | On Command
Command - On/Off | OnOff | On/Off Command
Command - Reset | Rst | Reset Command
Command - Speed | SpdCmd | Speed Command
Command - Start | Str | Start Command
Command - Start/Stop | StrStp | Start/Stop Command
Command - Stop | Stop | Stop Command
Counter | Cntr | Counter
Counter - Pulse Accumulator | PlsCntr | Pulse Counter
Counter - Run Time Accumulator | RTAcc | Run Time Accumulator
Crankcase | CrkCs | Crankcase
Crankcase Heater | CcHtr | Crankcase Heater
Cubic Feet per Minute | CFM | CFM
Damper | Dpr | Damper
Damper - Bypass | BypDpr | Bypass Damper
Damper - Cold Deck | CDkDpr | Cold Deck Damper
Damper - Combustion Air | CArDpr | Combustion Air Damper
Damper - Exhaust | ExhDpr | Exhaust Damper
Damper - Face and Bypass | FBDpr | Face and Bypass Damper
Damper - Fire | FirDpr | Fire Damper
Damper - Hot Deck | HDkDpr | Hot Deck Damper
Damper - Hot Deck | HDkDpr | Hot Deck Damper
Damper - Inlet Guide Vanes | IGV | Inlet Guide Vanes
Damper - Integral Face and Bypass | IFBDpr | Integral Face and Bypass Damper
Damper - Isolation | IsoDpr | Isolation Damper
Damper - Maximum Outdoor Air | MxOADpr | Maximum Outdoor Air Damper
Damper - Minimum Outdoor Air | MnOADpr | Minimum Outdoor Air Damper
Damper - Mixed Air | MADpr | Mixed Air Damper
Damper - Neutral Deck | NDkDpr | Neutral Deck Damper
Damper - Outdoor Air | OADpr | Outdoor Air Damper
Damper - Relief | RelDpr | Relief Damper
Damper - Return Air | RetDpr | Return Air Damper
Damper - Smoke | SmkDpr | Smoke Damper
Damper - Smoke and Fire | SmFrDpr | Smoke and Fire Damper
Direction - 01 - Left | Lft | Left
Direction - 02 - Right | Rt | Right
Direction - 03 - Upper | Upr | Upper
Direction - 04 - Lower | Lwr | Lower
Direction - 05 - Upper Right | UprRt | Upper Right
Direction - 05 - Upper Middle | UprMdl | Upper Middle
Direction - 07 - Upper Left | UprLft | Upper Left
Direction - 08 - Lower Right | LwrRt | Lower Right
Direction - 09 - Lower Middle | LwrMdl | Lower Middle
Direction - 10 - Lower Left | LwrLft | Lower Left
Direction - 11 - Middle | Mdl | Middle
Direction - 12 - Upper Middle | UprMdl | Upper Middle
Direction - 13 - Middle, Center | Cntr | Center
Direction - 14 - Lower Middle | LwrMdl | Lower Middle
Direction - 12 - North | N | North
Direction - 13 North East | NE | North East
Direction - 14 - East | E | East
Direction - 15 - South East | SE | South East
Direction - 16 - South | S | South
Direction - 17 - South West | SW | South West
Direction - 18 - West | W | West
Direction - 19 - North West | NW | North West
Diffuser | Diff | Diffuser
Discharge | Dschg | Discharge
Electrical - A Phase | APh | A Phase
Electrical - B Phase | BPh | B Phase
Electrical - Battery | Bat | Battery
Electrical - C Phase | CPh | C Phase
Electrical - Current | Cur | Current
Electrical - Ground | Gnd | Ground
Electrical - Inverter | Invtr | Inverter
Electrical - kW | kW | kW
Electrical - kWh | kWh | kWh
Electrical - Neutral | Neu | Neutral
Electrical - Phase Angle | PhAng | Phase Angle
Electrical - Photovoltaic | PV | Photovoltaic
Electrical - Voltage | Vlt | Voltage
Enthalpy | Enth | Enthalpy
Enthalpy - Outdoor Enthalpy | OAEn | Outdoor Enthalpy
Enthalpy - Return Enthalpy | RAEn | Return Enthalpy
Enthalpy - Space Enthalpy | SpEn | Space Enthalpy
Enthalpy - Zone Enthalpy | ZnEn | Zone Enthalpy
Exhaust | Exh | Exhaust
Exhaust - Exhaust Side | ExhSd | Exhaust Side
Fault | Fault | Fault
Filter | Fltr | Filter
Filter - Chemical | ChFlt | Chemical Filter
Filter - Final | FnFlt | Final Filter
Filter - HEPA | HPFlt | HEPA Filter
Filter - Prefilter | PrFlt | Prefilter
Fire Alarm | FirAlm | Fire Alarm
Floor Level Network | FLN | Floor Level Network
Flow (Water or Air) | Flow | Flow Switch
Gain - Derivative | DGain | Derivative Gain
Gain - Integral | IGain | Integral Gain
Gain - Proportional | PGain | Proportional Gain
Gallons per Minute | GPM | GPM
Gas - Carbon Dioxide | CO2 | Carbon Dioxide
Gas - Carbon Monoxide | CO | Carbon Monoxide
Gas - Hydrogen | H2 | Hydrogen
Gas - Medical | MG | Medical Gas
Gas - Natural Gas | NG | Natural Gas
Gas - Nitrogen (N2) | N2 | Nitrogen
Gas - Oxygen | O2 | Oxygen
Generator | Gen | Generator
Heater | Htr | Heater
High | High | High
Humidity | Hum | Humidity
Humidity - Outdoor Humidity | OAHum | Outdoor Humidity
Humidity - Return Humidity | RAHum | Return Humidity
Humidity - Room Humidity | RmHum | Room Humidity
Humidity - Space Humidity | SpHum | Space Humidity
Humidity - Supply Air | SAHum | Supply Air Humidity
Humidity - Zone Humidity | ZnHum | Zone Humidity
Humidity - Zone Humidity | ZnHum | Zone Humidity
Indication | Ind | Indication
Inlet | Inlet | Inlet
Isolation | Iso | Isolation
Leaving | Lvng | Leaving
Leaving - Supply Air | LSA | Leaving Supply Air
Leaving - Supply Water | LSW | Leaving Supply Water
Level Indicator | Lvl | Level Indicator
Level Switch | LvlSw | Level Switch
Light | Lght | Light
Lights | Lght | Lights
Limit - High Limit | HiLmt | High Limit
Limit - Low Limit | LoLmt | Low Limit
Lock-out | LkOut | Lock-out
Loop - Control Loop | CtrlLp | Control Loop
Loop - Off state value | OffVlu | Loop Off State Value
Loop - P Only | PLp | Proportional Control Loop
Loop - PI | PILp | Proportional Plus Integral Control Loop
Loop - PID | PIDLp | Proportional Plus Integral Plus Derivative Control Loop
Low | Low | Low
Magnetic Door Lock | DoorLk | Magnetic Door Lock
Maximum | Max | Maximum
Minimum | Min | Minimum
Motor | Mot | Motor
Network | Nwk | Network
Network - Internet Access | IPNwk | Internet Access
On Power Return Point (Changes state when power returns) | OnPwrRt | Power Recovery Trigger
Open | Opn | Open
Parts per Million | PPM | PPM
Placeholder | PlHldr | Placeholder
Power | Pwr | Power
Power Failure | PwrFail | Power Failure
Pressure - Building Static | BldgSP | Building Static Pressure
Pressure - Condenser | CdPr | Condenser Pressure
Pressure - Differential | DiffPr | Differential Pressure
Pressure - Discharge | DisPr | Discharge Pressure
Pressure - Downstream Duct Pressure | DnStPr | Downstream Duct Pressure
Pressure - Evaporator | EvPr | Evaporator Pressure
Pressure - Head | HdPr | Head Pressure
Pressure - Oil | OilPr | Oil Pressure
Pressure - Room Static Pressure | RmPr | Room Pressure
Pressure - Static | StPr | Static Pressure
Pressure - Suction | SucPr | Suction Pressure
Pressure - Supply Pressure | SupPr | Supply Pressure
Pressure - System Fill Pressure | FillPr | Fill Pressure
Pressure - Total | TotPr | Total Pressure
Pressure - Velocity | VelPr | Velocity Pressure
Pressure - Zone Static Pressure | ZnPr | Zone Pressure
Proof of Operation | Prf | Proof of Operation
Refrigerant | Ref | Refrigerant
Refrigeration | Ref | Refrigeration
Relay | Rly | Relay
Relay - Low Fire | LFrRy | Low Fire Relay
Relief | Rel | Relief
Request | Rqst | Request
Reset | Rst | Reset
Reset - Input Lower Limit | RstILo | Reset Schedule Input Parameter Lower Limit
Reset - Input Upper Limit | RstIHi | Reset Schedule Input Parameter Upper Limit
Reset - Output - Lower Limit | RstOLo | Reset Schedule Output Parameter Lower Limit
Reset - Output - Upper Limit | RstOHi | Reset Schedule Output Parameter Upper Limit
Return | Ret | Return
Return - Return Side | RetSd | Return Side
Sensor | Snsr | Sensor
Sensor - Field Installed Factory Control Sensor | FldSnsr | Field Installed Factory Control Sensor
Set Point | SetPnt | Set Point
Silicon Controlled Rectifier | SCR | Silicon Controlled Rectifier
Smoke Detector | SmkDt | Smoke Detector
Speed | Spd | Speed
Stage - 01 | Stg01 | First Stage
Stage - 02 | Stg02 | Second Stage
Stage - 03 | Stg03 | Third Stage
Stage - 04 | Stg04 | Fourth Stage
Stage - 05 | Stg05 | Fifth Stage
Stage - 06 | Stg06 | Sixth Stage
Stage - 07 | Stg07 | Seventh Stage
Stage - 08 | Stg08 | Eighth Stage
Stage - 09 | Stg09 | Ninth Stage
Stage - 10 | Stg10 | Tenth Stage
Status | Stat | Status
Status - Boiler Firing Controller | FlmFl | Flame Failure Status
Status - Cooling System Status | ClStat | Cooling System Status
Status - Free Cooling Status | FCStat | Free Cooling Status
Status - Heating System Status | HSStat | Heating System Status
Status - HOA | HOAStat | HOA Switch Status
Status - Proof of Operation | PRF | Proof of Operation
Status - Speed Feedback | SpdFbk | Speed Feedback
Strobe | Strb | Strobe Light
Supply | Sup | Supply
Supply - Supply Side | SupSd | Supply Side
Switch | Sw | Switch
Switch - Differential Pressure | DPSw | Differential Pressure Switch
Switch - Emergency Machine Off | EMO | Emergency Machine Off
Switch - Emergency Power Off | EPO | Emergency Power Off Switch
Switch - Emergency Stop | EMS | Emergency Stop
Switch - End Switch | EndSw | End Switch
Switch - Filter Differential Pressure | FltSw | Filter Differential Pressure Switch
Switch - Flow (Water or Air) | FlowSw | Flow Switch
Switch - High Head Pressure Limit Switch - Manual Reset | HPLSw | Head Pressure Limit Switch
Switch - High Head Pressure Switch | HHPSw | High Head Pressure Switch
Switch - High Static Pressure | HSPSw | High Static Pressure Switch
Switch - High Static Pressure Limit - Manual Reset | HSPLim | High Static Pressure Limit Switch
Switch - High Temperature | HiTmp | Firestat
Switch - High Temperature Limit - Manual Reset | FirSt | Firestat
Switch - Lead/Lag | LdLg | Lead Lag Switch
Switch - Level - High | HLvSw | High Level Switch
Switch - Level - Low | HLvSw | High Level Switch
Switch - Limit Switch | LmSw | Limit Switch
Switch - Low Static Pressure | LSPSw | Low Static Pressure Switch
Switch - Low Static Pressure Limit - Manual Reset | LSPLim | Low Static Pressure Limit Switch
Switch - Low Suction Pressure | LSPSw | Low Suction Pressure Switch
Switch - Low Temperature Limit | SwLoLm | Low Temperature Limit Switch
Switch - Low Temperature Limit - Manual Reset | FrzSt | Freezestat
Switch - Moisture | MoistSw | Moisture Switch
Switch - Motion | MotnSw | Motion Switch
Switch - Motor Overload - Manual Reset | MtrOL | Motor Overload
Switch - Occupancy | OccSw | Occupancy Switch
Switch - Photocell | PhoSw | Photo Switch
Switch - Roll-out | RollOut | Roll-out Switch
Switch - Suction Pressure Limit Switch - Manual Reset | SPLSw | Suction Pressure Limit Switch
Temperature | Temp | Temperature
Temperature - Average | AvgTmp | Average Temperature
Temperature - Condenser | CdTmp | Condenser Temperature
Temperature - Crankcase | CrCTmp | Crankcase Temperature
Temperature - Dew Point | DewPt | Dew Point Temperature
Temperature - Discharge | DisTmp | Discharge Temperature
Temperature - Duct | DctTmp | Duct Temperature
Temperature - Evaporator | EvTmp | Evaporator Temperature
Temperature - Floor Slab | SlbTmp | Slab Temperature
Temperature - Flue Gas | FluTmp | Flue Gas Temperature
Temperature - Hot Gas Line | HGTmp | Hot Gas Line Temperature
Temperature - Jacket Water | JWTmp | Jacket Water Temperature
Temperature - Pan | PnTmp | Pan Temperature
Temperature - Room | RmTmp | Room Temperature
Temperature - Suction | SucTmp | Suction Temperature
Temperature - Wet Bulb | WtBlb | Wet Bulb Temperature
Temperature - Zone | ZnTmp | Zone Temperature
Terminal Unit - Constant Air Volume | CAV | Constant Volume Terminal Unit
Time | Time | Time
Time - Days | Dys | Days
Time - Hours | Hrs | Hours
Time - Minutes | Mins | Minutes
Time - Months | Mnths | Months
Time - Run Time | RunTm | Run Time
Time - Seconds | Sec | Seconds
Time - Totalizer | Total | Totalizer
Time - Weeks | Wks | Weeks
Time - Years | Yrs | Years
Time Delay | TmDly | Time Delay
Timer - Acceleration Timer | Accel | Acceleration Timer
Timer - Deceleration Timer | Decel | Deceleration Timer
Timer - Interval Timer | IntTmr | Interval Timer
Timer - Off Delay | OffDly | Off Delay
Timer - On Delay | OnDly | On Delay
Timer - One-Shot Delay | OnSht | One Shot Delay
Timer - Ramp Down | RmpDn | Ramp Down Timer
Timer - Ramp Up | RmpUp | Ramp Up Timer
Timer - Time Clock | TmClk | Time Clock
Trigger | Trgr | Trigger
Valve | Vlv | Valve
Valve - Bypass | BpsVlv | Bypass Valve
Valve - Chilled Water | CHWVlv | Chilled Water Valve
Valve - Control | CtrVlv | Control Valve
Valve - Cooling Coil | CCVlv | Cooling Coil Valve
Valve - Diverting | DivVlv | Diverting Valve
Valve - Diverting | DivVlv | Diverting Valve
Valve - Flow Control | FCVlv | Flow Control Valve
Valve - Heating Coil | HCVlv | Heating Coil Valve
Valve - Hot Water | HWVLV | Hot Water Valve
Valve - Humidifier | HumVlv | Humidifier Valve
Valve - Isolation | IsoVlv | Isolation Valve
Valve - Mixing | MixVlv | Mixing Valve
Valve - Mixing | MixVlv | Mixing Valve
Valve - Preheat Coil | PHVlv | Preheat Coil Valve
Valve - Reheat Coil | RHVlv | Reheat Coil Valve
Valve - Reversing | RevVlv | Reversing Valve
Valve - Steam | StmVlv | Steam Valve
Variable Frequency Drive | VFD | Variable Frequency Drive
Variable Speed Drive | VSD | Variable Speed Drive
VRF BACnet - Air Direction Set | ArDrSe | BACnet - Set Airflow Direction
VRF BACnet - Air Direction State | ArDrSt | BACnet - Airflow Direction Feedback
VRF BACnet - Alarm Signal | Alm | BACnet - General Alarm
VRF BACnet - Error Code | ErrCd | BACnet - General Error
VRF BACnet - Fan Speed Set-up | FnSpSe | BACnet - Set Fan Speed
VRF BACnet - Fan Speed State | FnSpSt | BACnet - Fan Speed Feedback
VRF BACnet - Filter Sign | FtrSgn | BACnet - Change Filter Indication
VRF BACnet - Filter Sign Reset | FtrRst | BACnet - Change Filter Indication Reset
VRF BACnet - MNet Communication State | MNetSt | BACnet - MNet Error Indication
VRF BACnet - On/Off Set-up | OnOfSe | BACnet - Indoor Unit Start/Stop
VRF BACnet - On/Off State | OnOfSt | BACnet - Indoor Unit Operating State
VRF BACnet - Operating Mode Set-up | OpMdSe | BACnet - Operating Mode Setting
VRF BACnet - Operating Mode State | OpMdSt | BACnet - Operating Mode Feedback
VRF BACnet - Prohibit Filter Sign Reset | PrFlr | BACnet - Prohibit Remote Filter Change Indication Reset
VRF BACnet - Prohibit Mode | PrMd | BACnet - Prohibit Remote Operating Mode Override
VRF BACnet - Prohibit On/Off | PrOnOf | BACnet - Prohibit Remote On-Off Override
VRF BACnet - Prohibit Set Temperature | PrSTmp | BACnet - Prohibit Remote Set Point Adjustment
VRF BACnet - Room Temperature | RmTmp | BACnet - Space Temperature Indication
VRF BACnet - Set High Limit Set Back Temp | SetHSB | BACnet - Set Unoccupied Cycle High Limit Set Point
VRF BACnet - Set Low Limit Set Back Temp | SetLSB | BACnet - Set Unoccupied Cycle Low Limit Set Point
VRF BACnet - Set Temp Auto | SetTAu | BACnet - Set Temporary Auto Mode Set Point
VRF BACnet - Set Temp Cool | SetTCl | BACnet - Set Temporary Cooling Set Point
VRF BACnet - Set Temp Heat | SetTHt | BACnet - Set Temporary Heating Set Point
VRF BACnet - Set Temperature | SetTmp | BACnet - Set Space Temperature Set Point
VRF BACnet - System Force Off | FrcOff | BACnet - Force Indoor Unit Off
Water | Wtr | Water
Water Temperature - Entering Water Temperature | EWT | Entering Water Temperature
Water Temperature - Leaving Water Temperature | LWT; | Leaving Water Temperature
Water Temperature - Mixed Water | MWT | Mixed Water Temperature
Water Temperature - Return Water Temperature | RWT | Return Water Temperature
Water Temperature - Supply Water | SWT | Supply Water Temperature
Zone | Zn | Zone
Bottom of list
| Revision History | Back to Top
| Created | 2018-01-01 13:14
| Rev 1 | 2018-04-20 17:57

## Inputs Devices
Jump to Revision History
Selection Text | Spec Section Reference | Accuracy
Top of List
0-(-1) in.w.c. input, 4-20 ma output transmitter, Dwyer MS-121 | 25 35 00 | +/-1% full scale
0-(-2) in.w.c. input, 4-20 ma output transmitter, Dwyer MS-121 | 25 35 00 | +/-1% full scale
0-1 in.w.c. input, 4-20 ma output transmitter, Dwyer MS-121 | 25 35 00 | +/-1% full scale
0-10 in.w.c. input, 4-20 ma output transmitter, Dwyer MS-121 | 25 35 00 | +/-1% full scale
0-2 in.w.c. input, 4-20 ma output transmitter, Dwyer MS-121 | 25 35 00 | +/-1% full scale
0-30 psig Ashcroft A2 pressure transmitter, 4-20 ma output | 25 35 00 | 0.25% Accuracy Class
0-300 psig Ashcroft A2 pressure transmitter, 4-20 ma output | 25 35 00 | 0.25% Accuracy Class
0-500 psig Ashcroft A2 pressure transmitter, 4-20 ma output | 25 35 00 | 0.25% Accuracy Class
4-20 ma CO2 sensor, 4-20 ma output | 25 35 00 | +/- 50 ppm
4-20 ma Programmable VFD Output | 25 35 00 | N/A
Current Transformer | 25 35 00 | +/-2% full scale
Factory furnished sensor, field installed and wired | 25 35 00 | N/A
Flexible averaging 1,000 Ω Pt RTD with close coupled transmitter | 25 35 00 | 0.75% of span for sensor + transmitter
Hard Wired | 25 35 00 | N/A
N/A | 25 35 00 | N/A
Single point 1,000 Ω Pt RTD with close coupled transmitter | 25 35 00 | 0.75% of span for sensor + transmitter
Surface mounted 1,000 Ω Pt RTD with close coupled transmitter | 25 35 00 | 0.75% of span for sensor + transmitter
Thermocouple with 4-20 ma transmitter | 25 35 00 | +/- 3°F
Vendor Furnished Isolated Dry Contact | 25 35 00 | N/A
Bottom of List
| Revision History | Back to Top
| Created | 2018-04-20 18:05

## Output Devices
Jump to Revision History
Selection Text | Spec Section Reference | Accuracy
Top of List
4-20 ma command | 25 35 13 | N/A
2-10 vdc actuator | 25 35 13 | N/A
3-15 psi pneumatic signal convertor | 25 35 13 | N/A
Relay Output | 25 35 13 | N/A
Bottom of List
| Revision History | Back to Top
| Created | 2018-04-20 18:05

## Template
[6 empty] | The full object name is the composed of the building and system segments below plus the subsystem and device descriptor segments associated with each point in the system. The maximum character count is 30 characters. Enter segment character count targets in the colored cells with red outlines in row 8 columns B, D, and row 5 and 6, column X. The target sum automatically totals up and turns red if you exceed the limit. The spreadsheet 2018-04-20 Point Name Structure v1.xlsx describes the naming convention in detail, as does the Standard Object Naming section of the specification.) | [13 empty] | Character Count; "Actual" goes from green to red as limit is approached
[7 empty] | System Name - | .0-? | Assembled from selections | [10 empty] | Segments |  | Entire Name Maximum with Periods
[7 empty] | Object Name - Building and System Segments - | 0.0-? | Assembled from selections | Abbreviation | Description | [5 empty] | Links to Lists |  |  | Tgt. | Act. |  |  |  | .0-? (Typical of ?)
[7 empty] | Building Segment Selection - | Top of list | From drop down menu | 0 | [6 empty] | Building List |  |  | 7 | 2 | 30 | Desired Total |  | General Comments: (Manual Entry) | None
Character Count | Subsystem Segment |  | Descriptor Segment |  |  |  | System Segment Selection - | Top of list | From drop down menu | 0 | 0 | [5 empty] | System Level List |  |  | 7 | 2 | 30 | Target Sum
[7 empty] | System Number - | ? | Manual Entry | ? | ? | [13 empty] | Point Description | Point Type | [9 empty] | Cost Estimate Notes
Target ► | 8 |  | 8 |  |  |  | Number of similar Systems - | ? | Manual Entry | [16 empty] | High Cost AI | Low Cost AI | AO | DI | DO | Hardwired | Virtual | Packaged System Network Point | Complex System Network Point | Lump Sum (enter $ value, not X)
Total for the point with all segments (red means the maximum count is exceeded) ▼ | System | Number (Optional) | Descriptor 1 | Descriptor 2 | Number (Optional) | The data in these columns should be manually entered as the control system design evolves. This data will automatically populate the budget estimate point list to the right other than the lump sum value, general comments and cost estimate notes, which must be manually entered.
| Select using the drop down list for each point | Manually enter a number or text. Use an appostrophe ahead of the entry so it is interpreted as text and allow the other formulas to work; i.e. enter'01 vs. 01 | Select using the drop down list for each point | Select using the drop down list for each point | Manually enter a number or text. Use an appostrophe ahead of the entry so it is interpreted as text and allow the other formulas to work; i.e. enter'01 vs. 01 | The heading for the point list will be autmatically generated from the information entered above. |  |  | Click here to jump to a column that contains the full object name including all segments
Entering "Existing" into the "Sensor Type" column will prevent any cost from being tabulated for the point in the cost estimate point list.
[6 empty] | These columns are automatically generated using the point name tool in columns A-F |  |  | Use the drop down in this column to pick the appropriate sensor | These columns are filled in based on the sensor selection |  | These columns are filled in manually based on project requirements
.0-? (Typical of ?)
[6 empty] | Point |  |  | Sensor |  |  | Features | [10 empty] | Notes
[6 empty] | Name (Note 6) |  | Description and Service | Type | Reference Spec Paragraph | Accuracy | Alarms |  |  |  | Trending
[12 empty] | Limit |  | Warning |  | Samples1 | Commissioning5 |  |  | Operating5
[12 empty] | Hi | Lo | Hi | Lo |  | Time2 | Local3 | Archive4 | Time2 | Local3 | Archive4
Analog Inputs | [5 empty] | Analog Inputs | [17 empty] | Full point object names | Analog Inputs (These cells will automatically fill in from the main point list) | [9 empty] | Manual Entry
High Cost -- HIDE THIS ROW AND "Not Used" ROWS BEFORE PRINTING
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
[6 empty] | Low Cost -- HIDE THIS ROW AND "Not Used" ROWS BEFORE PRINTING | [17 empty] | 0.0-?.
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Analog Outputs (All analog outputs to include local override capability and status indication at the controller) | [5 empty] | Analog Outputs (All analog outputs to include local override capability and status indication at the controller) | [17 empty] | 0.0-?. | Analog Outputs (All analog outputs to include local override capability and status indication at the controller)
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Digital Inputs | [5 empty] | Digital Inputs | [17 empty] | 0.0-?. | Digital Inputs
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Digital Outputs (All digital outputs to include local override capability and status indication at the controller) | [5 empty] | Digital Outputs (All digital outputs to include local override capability and status indication at the controller) | [17 empty] | 0.0-?. | Digital Outputs (All digital outputs to include local override capability and status indication at the controller)
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Safety Interlocks (Hardwired to shut down or otherwise manipulate the system. Safeties shall function no matter what position the equipment's Hand-Off-Auto, Inverter-Bypass, or other selector switches are in) | [5 empty] | Safety Interlocks (Hardwired to shut down or otherwise manipulate the system. Safeties shall function no matter what position the equipment's Hand-Off-Auto, Inverter-Bypass, or other selector switches are in) | [17 empty] | 0.0-?. | Safety Interlocks (Hardwired to shut down or otherwise manipulate the system. Safeties shall function no matter what position the equipment's Hand-Off-Auto, Inverter-Bypass, or other selector switches are in)
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Virtual Points | [5 empty] | Virtual Points | [17 empty] | 0.0-?. | Virtual Points
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
Network Points | [5 empty] | Network Points | [17 empty] | 0.0-?. | Network Points
[6 empty] | Packaged System Network Point -- HIDE THIS ROW AND "Not Used" ROWS BEFORE PRINTING | [17 empty] | 0.0-?.
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
[6 empty] | Complex System Network Point -- HIDE THIS ROW AND "Not Used" ROWS BEFORE PRINTING | [17 empty] | 0.0-?.
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
0 | Top of list |  | Top of list | Top of list |  |  | (NOT USED) |  | Top of List
[6 empty] | Notes: | [18 empty] | Totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 1 | Samples indicates the minimum number of data samples that must be held in the local controller if it is trending the point. | [17 empty] | Notes:
[6 empty] | 2 | Time indicates the required sampling time for the trending function. | [17 empty] | 1. (Placeholder)
[6 empty] | 3 | A check in the local column indicates that the trending only needs to be running in the local controller and the most recent value can write over the last value when the trend buffer fills up.
[6 empty] | 4 | A check in the archive column indicates that the trend data must be archived to the system hard disc when trend buffer fills up so that a continuous trend record is maintained.
[6 empty] | 5 | Commissioning trending requirements only need to be implemented during the start-up and warranty year. After the start-up and warranty process, the control contractor should set the trending parameters to the operating requirements listed if they differ from the commissioning requirements. | [17 empty] | Cost Assumptions
[6 empty] | 6 | Point numbers are based on the Owner's point naming convention which is included in the specification. Point names will be verified during the submittal process in the control system integration and coordination meeting. | [24 empty] | Physical Points - | 1000
[6 empty] | 7 | Monitor amps to provide a proof of operation in put and create a virtual meter to track energy use using voltage and power factor constants determined during commissioning. Accumulate and display current demand level, kWh for the day, and kWh for the previous day, calendar month, and calendar year. Archive data to the data to the dedicated archival data storage drive in the City's Data Center. See Network Diagram. | [25 empty] | 750
[6 empty] | 8 | 0.75% of span for sensor plus transmitter combined. | [24 empty] | Virtual Points - | 75
[6 empty] | 9 | 2 feet of element for every 4 sq.ft. of duct or AHU cross-sectional area, 6 ft. minimum length. | [24 empty] | Hardwired Interlock - | 300
[6 empty] | 10 | Use flow and pressure drop to trend filter life cycle cost and trigger filter changes based on life cycle cost. See control logic and narrative for additional information. | [24 empty] | Packaged System Network Points - | 12
[6 empty] | 11 | Install a tee with two service valves on the existing pressure connection. Install a service fitting on the branch of the tee and connect the pressure transmitter to the other side of the tee. Coordinate with Mitsubishi as required to verify and prove the integrity of the piping connections when they charge the system. | [24 empty] | Complex System Network Points - | 150
[6 empty] | 12 | Used as a proof of operation input and also as a loss of efficiency alarm. Also use the proof of operation input to create a virtual meter to track energy use. | [24 empty] | Assumed labor rate - | 150
[6 empty] | 13 | Command the actuator to provide two position operation. An analog actuator is provided for flexibility.
[6 empty] | 14 | Perform a relative calibration of this point relative to the other temperature points in the same air stream using the outdoor air temperature sensor as a reference. Adjust the zero of the other sensors so all sensors agree when immersed in a well stirred bucket of ice water. Adjust the span of the other sensors so the all agree when subject to an air stream at the same temperature (heat wheel off, electric heat off).
[6 empty] | 15 | Coordinate with the Architect, mechanical designer, commissioning provider, control designer, and operating team to select a location for the outdoor air conditions sensor in the field during construction. Anticipate a wiring run with-in 25 feet of the sensor location shown on the drawings.
[6 empty] | 16 | Analog actuators are provbided for a two position function to provide future flexibility.
[6 empty] | 17 | Furnish and install a load resistor terminal in the DOAS control panel to convert the 4-20 ma signal to 2-10 vdc for use by the DOAS control system.
[6 empty] | 18 | Mount limit swith on unistrut per detail to provide adjustablity. Set the switch so that the damper has to be fully open before it triggers.
[6 empty] | 19 | Coordinate with the fire alarm vendor to provide a contact that closes if there is any sort of fire alarm in the building. This input will be used to trigger a software based courtesy fire alarm shut down of the building HVAC systems in the event of an alarm.
[6 empty] | 20 | Accumulate run hours based on the status of the proof of operation input. Archive daily, monthly, annual and total run hours.
[6 empty] | 21 | Accumulate starts based on the stauts of the proof of opeation point. Archive daily, monthly, annual, and total starts.
[6 empty] | 22 | Coordinate with the DOAS vendor to obtain a PICS for the network interface. Coordinate with the Owner to determin with objects they want to have mapped across the interface. For bidding purposes, assume all objects will be mapped across the interface.

## Typical VRF with Network
Variable Flow Refrigeration - Indoor Unit Point List (Typical of 24 Units) | [17 empty] | Variable Flow Refrigeration - Indoor Unit Point List (Typical of 24 Units) | Typical of how many: | [9 empty] | 24
Point |  |  | System and Service | Sensor |  | Features | [10 empty] | Notes | General Comments: | (none)
Name |  | Number [BACnet Object ID], Note 7 |  | Type | Accuracy | Alarms |  |  |  | Trending
[6 empty] | Limit |  | Warning |  | Samples1 | Commissioning5 |  |  | Operating5 |  |  |  |  | Point Type
[6 empty] | Hi | Lo | Hi | Lo |  | Time2 | Local3 | Archive4 | Time2 | Local3 | Archive4 |  | Point Description | High Cost AI | Low Cost AI | AO | DI | DO | Hardwired | Virtual | Packaged System Network Point | Complex System Network Point | Lump Sum (enter $ value, not X) | Notes
Analog Inputs | [17 empty] | Analog Inputs
High Cost -- HIDE THIS ROW BEFORE PRINTING
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
Low Cost -- HIDE THIS ROW BEFORE PRINTING
| Discharge air temperature |  | FC-xx Discharge air temperature | Rigid averaging 1,000 Ω Pt RTD with close coupled transmitter | Note 8 |  |  |  |  | 60 | 1 min. | X | X | 5 min. | X | X | Note 18 | Discharge air temperature | X | [10 empty] | Had a CO sensor in for FS bunk rooms. Deleted for this project
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
Analog Outputs | [17 empty] | Analog Outputs
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
Digital Inputs | [17 empty] | Digital Inputs
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
Digital Outputs (All digital outputs to include local override capability and indication) | [17 empty] | Digital Outputs (All digital outputs to include local override capability and indication)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
Hardwired Points | [17 empty] | Hardwired Points
| Multi-function controller |  | FC-xx Multi-function controller | Proprietary Controller; Type to be determined | N/A |  |  |  |  | N/A | N/A | X | X | N/A | X | X | Note 17 | Multi-function controller | [5 empty] | X
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
(NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
Virtual Points | [17 empty] | Virtual Points
| Diagnostic 1 |  | FC-xx Diagnostic 1 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 1 | [6 empty] | X
| Diagnostic 2 |  | FC-xx Diagnostic 2 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 2 | [6 empty] | X
| Diagnostic 3 |  | FC-xx Diagnostic 3 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 3 | [6 empty] | X
| Diagnostic 4 |  | FC-xx Diagnostic 4 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 4 | [6 empty] | X
| Diagnostic 5 |  | FC-xx Diagnostic 5 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 5 | [6 empty] | X
| Diagnostic 6 |  | FC-xx Diagnostic 6 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 6 | [6 empty] | X
| Diagnostic 7 |  | FC-xx Diagnostic 7 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 7 | [6 empty] | X
| Diagnostic 8 |  | FC-xx Diagnostic 8 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 8 | [6 empty] | X
| Diagnostic 9 |  | FC-xx Diagnostic 9 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 9 | [6 empty] | X
| Diagnostic 10 |  | FC-xx Diagnostic 10 | Logic generated based on data from multiple points | N/A |  |  |  |  | 5 | COV | X | X | COV | X | X | Note 9 | Diagnostic 10 | [6 empty] | X
BACnet Points | [17 empty] | BACnet Points
Packaged System Network Point -- HIDE THIS ROW BEFORE PRINTING
| On/Off Set-up | [BO_01xx01} | Start/stop fan coil unit | Binary Output Network Point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | On/Off Set-up | [7 empty] | X
| On/Off State | [BI_01xx02] | Operating status feedback | Binary Input Network Point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | On/Off State | [7 empty] | X
| Alarm Signal | [BI_01xx03] | Alarm signal | Binary Input Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Alarm Signal | [7 empty] | X
| Error Code | [MI_01xx04] | General indication of an error, Note 13 | Multistate Input Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Error Code | [7 empty] | X
| Operating Mode Set-up | [MO_01xx05 | Sets the unit into 1 of 6 operating states, Note 14, 15 | Multistate Output Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Operating Mode Set-up | [7 empty] | X
| Operating Mode State | [MI_01xx06] | Operating status feedback; Note 14, 15 | Multistate Input Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Operating Mode State | [7 empty] | X
| Fan Speed Set-up | [MO_01xx07] | Allows fan speed to be set; Note 15 | Multistate Output Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Fan Speed Set-up | [7 empty] | X
| Fan Speed State | [MI_01xx08] | Fan speed status feedback | Multistate Input Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Fan Speed State | [7 empty] | X
| Room Temperature | [AI_01xx09] | Space temperature indication | Analog Input Network point | N/A |  |  |  |  | 60 | 1 min | X | X | 1 min | X | X | Notes 11, 12 | Room Temperature | [7 empty] | X
| Set Temperature | [AV_01xx10] | Space temperature set point adjustment | Analog Command or Value Network point | N/A |  |  |  |  | 60 | 1 min | X | X | 1 min | X | X | Notes 11, 12 | Set Temperature | [7 empty] | X
| Filter Sign | [BI_01xx11] | Change filter indication | Binary Input Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Filter Sign | [7 empty] | X
| Filter Sign Reset | [BV_401xx12] | Change filter indication reset | Binary Value Network Point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Filter Sign Reset | [7 empty] | X
| Prohibit On/Off | [BV_01xx13] | Prohibits a remote control over ride of On/Off state | Binary Value Network Point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Prohibit On/Off | [7 empty] | X
| Prohibit Mode | [BV_01xx14] | Prohibits a remote control over ride of operating mode | Binary Value Network Point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Prohibit Mode | [7 empty] | X
| Prohibit Filter Sign Reset | [BV_01xx15] | Prohibits a remote control reset of filter alarm | Binary Value Network Point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Prohibit Filter Sign Reset | [7 empty] | X
| Prohibit Set Temperature | [BV_01xx16] | Prohibits a remote control from adjusting set point | Binary Value Network Point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Prohibit Set Temperature | [7 empty] | X
| MNet Communication State | [BI_01xx20] | Indicates if there is an MNet error | Binary Input Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | MNet Communication State | [7 empty] | X
| System Force Off | [BV_01xx21] | Forces the unit to the off state | Binary Value Network Point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | System Force Off | [7 empty] | X
| Air Direction Set | [MO_0xx22} | Sets air flow direction; Note 16 | Multistate Output Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Air Direction Set | [7 empty] | X
| Air Direction State | [MI_01xx23] | Flow direction feedback, Note 16 | Multistate Input Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Air Direction State | [7 empty] | X
| Set Temp Cool | [AV_01xx24] | Sets a temporary cooling set point | Analog Command or Value Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Set Temp Cool | [7 empty] | X
| Set Temp Heat | [AV_01xx25] | Sets a temporary heating set point | Analog Command or Value Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Set Temp Heat | [7 empty] | X
| Set Temp Auto | [AV_01xx26] | Sets a temporary set point for Auto mode | Analog Command or Value Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Set Temp Auto | [7 empty] | X
| Set High Limit Set Back Temp | [AV_01xx27] | Sets the high limit during the unoccupied cycle | Analog Command or Value Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Set High Limit Set Back Temp | [7 empty] | X
| Set Low Limit Set Back Temp | [AV_01xx28] | Set the low limit during the unoccupied cycle | Analog Command or Value Network point | N/A |  |  |  |  | 20 | COV | X | X | COV | X | X | Notes 11, 12 | Set Low Limit Set Back Temp | [7 empty] | X
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
Complex System Network Point -- HIDE THIS ROW BEFORE PRINTING
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
| (NOT USED) |  | FC-xx (NOT USED)
Notes: | [17 empty] | Totals | 1 | 0 | 0 | 0 | 0 | 1 | 10 | 25 | 0 | 0
1 | Samples indicates the minimum number of data samples that must be held in the local controller if it is trending the point. | [16 empty] | Notes:
2 | Time indicates the required sampling time for the trending function. | [16 empty] | 1. (Placeholder)
3 | A check in the local column indicates that the trending only needs to be running in the local controller and the most recent value can write over the last value when the trend buffer fills up.
4 | A check in the archive column indicates that the trend data must be archived to the system hard disc when trend buffer fills up so that a continuous trend record is maintained.
5 | Commissioning trending requirements only need to be implemented during the start-up and warranty year. After the start-up and warranty process, the control contractor should set the trending parameters to the operating requirements listed if they differ from the commissioning requirements. | [16 empty] | Cost Assumptions
6 | 0.12% of reading for the RTD, .012% of span for the transmitter. | [23 empty] | Physical Points - | 1000
7 | Unused | [24 empty] | 750
8 | 0.75% of span for sensor plus transmitter combined. | [23 empty] | Virtual Points - | 75
9 | See narrative sequence and logic diagrams for diagnostic definition. | [23 empty] | Hardwired Interlock - | 300
10 | Unused | [23 empty] | Packaged System Network Points - | 12
11 | Point numbers will be determined once the Owner's point naming standard is finalized. And this list will be updated at that time. For BACnet points, "xx" refers to the equipment's "group number". For the purposes of this project, each indoor unit will be considered to be a group. | [23 empty] | Complex System Network Points - | 150
12 | The VRF system works on a "Last Command Wins" methodology. Meaning that the last command that a remote unit receive, be it from the DDC system via BACnet or via the remote control unit will be the command that is executed. So, if the DDC system refreshes its commands ever minute, an occupant who is, for instance, trying to adjust the set point, will not be able to get their adjustment to "stick" longer than one minute. | [23 empty] | Assumed labor rate - | 150
13 | This error code indicates an error in a certain category has occurred with the text parameter indicating the category as follows: 01 = Normal; 02 = Other error; 03 = Refrigeration system fault; 05; 06 = Electronic system error; 07 = Sensor fault; 08 = Communication error; 09 = System error; Log into the maintenance tool for additional information.
14 | Possible states are 01 = Cooling, 02 = Heating, 03 - Fan only, 04 = Auto fan control, 05 = Dry, and 06 = Setback. Note that the Dry feature must be enabled by selecting the "Use" option. | [16 empty] | Cost Per Typical | [7 empty] | 2350
15 | Dry mode provides additional dehumidification by reducing the fan speed. As a result, all other things being equal, the air comes off the evaporator coil at a lower dry bulb and dew point temperature, which will tend to dehumidify the space (due to the lower leaving air temperature) with out over-cooling it (due to the reduced flow rate). | [16 empty] | Total Cost | [7 empty] | 56400
16 | Applies only to units with movable vanes. Possible states are Horizontal, Down blow 60°. Down blow 80°, Down blow 100°, and swing
13 | Possible states are 01 = Cooling, 02 = Heating, 03 - Fan only, 04 = Auto fan control, 05 = Dry, and 06 = Setback. Note that the Dry feature must be enabled by selecting the "Use" option.
14 | Dry mode provides additional dehumidification by reducing the fan speed. As a result, all other things being equal, the air comes off the evaporator coil at a lower dry bulb and dew point temperature, which will tend to dehumidify the space (due to the lower leaving air temperature) with out over-cooling it (due to the reduced flow rate). | [16 empty] | Lump Sum Number
15 | Possible states are 01 = Low, 02 = High, 03 - Mid 2, and 05 = Mid 1. Note that the Mid1 and Mid2 settings must be enabled by selecting the "Use" option. | [16 empty] | Mapping the first unit across the BACNet interface and general set-up | [7 empty] | 4000
16 | Possible states are Horizontal, Down blow 60°. Down blow 80°, Down blow 100°, and swing | [16 empty] | BACnet module (by MRF Vendor and in the Mechancal contract) | [7 empty] | 0
17 | Two wire remote controller wired directly to the fan coil unit controller board. | [16 empty] | Control panel for BACnet module and Central Controller (Assumes no enclosure requried for the PC and the others are in a Siemens panel) | [7 empty] | 0
18 | Sensor length to be long enough to travers the longest dimension of the duct. | [16 empty] | PC and Remote Desktop software for Mitsubishi OWS (does not include annual subscription costs) | [7 empty] | 800
[18 empty] | Power wiring to Control panel (All ready provided with the Siemens panel; see above) | [7 empty] | 0
[18 empty] | TOTAL | [7 empty] | 4800