## Data and Calculator
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Notice: Facility Dynamics Engineering has provided this spreadsheet for educational purposes. We are fine with you using it as a starting point for your own spreadsheet performing a similar analysis or even using it as is. But you are using it at your own risk and FDE can not be responsible for the results you generate with it and the decisions you make as a result. Please check your work and use your head.
Engineering Calculation
Assumptions
1 | Standard atmosphere calculator - | http://www.digitaldutch.com/atmoscalc/
2 | Table Data Source - | http://www.avs.org/AVS/files/c7/c7edaedb-95b2-438f-adfb-36de54f87b9e.pdf
3 | Click here to jump to the correction factor tool
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????
|  |  | Standard Atmosphere | [9 empty] | Formula cross-check to table, psia |  | Formula cross-check to table, kPa
|  |  | Altitude Above Sea Level |  |  | Temperature |  | Barometric Pressure |  | Atmospheric Pressure |  |  | Formula psia | Difference from Table | Formula kPa | Difference from Table | Click here to go back to the top of the assumptions
|  |  | Feet | Miles | Meters | F | C | In. Hg. Abs. | mm Hg. Abs. | psia | Kg/sq.cm. | kPa A
|  |  | 0 |  | 0 | 59 | 15 | 29.92 | 760 | 14.696 | 1.0333 | 101.33 | 14.696 | -2.388e-05 | 101.2886 | 0.041434 | Correction factor relative to sea level pressure in psia and altitude in feet
|  |  | 500 |  | 153 | 57 | 14 | 29.38 | 746.3 | 14.43 | 1.015 | 99.49 | 14.4333 | -0.0033088 | 99.472 | 0.018046 | Enter your altitude in feet in the cell with the red outline and read the standard pressure at that altitude in the blue cell and the correction factor in the yellow cell.
|  |  | 1000 |  | 305 | 55 | 13 | 28.86 | 733 | 14.16 | 0.956 | 97.63 | 14.1743 | -0.014325 | 97.6928 | -0.062837
|  |  | 1500 |  | 458 | 54 | 12 | 28.33 | 719.6 | 13.91 | 0.978 | 95.91 | 13.919 | -0.009036 | 95.9276 | -0.017552
|  |  | 2000 |  | 610 | 52 | 11 | 27.82 | 706.6 | 13.66 | 0.96 | 94.19 | 13.6674 | -0.0074053 | 94.1989 | -0.0089258 |  | Altitude in feet - | 5280 | ft.
|  |  | 2500 |  | 763 | 50 | 10 | 27.32 | 693.9 | 13.41 | 0.943 | 92.46 | 13.4194 | -0.0093968 | 92.484 | -0.023962 |  | Standard pressure at altitude, psia - | 12.1049 | psia
|  |  | 3000 |  | 915 | 48 | 9 | 26.82 | 681.2 | 13.17 | 0.926 | 90.81 | 13.175 | -0.0049745 | 90.8048 | 0.0051668 |  | Correction factor - | 0.82369 | Multiply by this to make a correction
|  |  | 3500 |  | 1068 | 47 | 8 | 26.33 | 668.8 | 12.93 | 0.909 | 89.15 | 12.9341 | -0.0041025 | 89.1392 | 0.010804 |  | Equation - | y = 1.21250592E-19x4 - 4.91012316E-14x3 + 7.53603419E-09x2 - 5.29185935E-04x + 1.46902388E+01
|  |  | 4000 |  | 1220 | 45 | 7 | 25.84 | 656.3 | 12.69 | 0.892 | 87.49 | 12.6967 | -0.0067452 | 87.5086 | -0.018581
|  |  | 4500 |  | 1373 | 43 | 6 | 25.37 | 644.4 | 12.46 | 0.876 | 85.91 | 12.4629 | -0.0028672 | 85.8913 | 0.018714 | Correction factor relative to sea level pressure in kPa and altitude in meters
|  |  | 5000 | 0.95 | 1526 | 41 | 5 | 24.9 | 632.5 | 12.23 | 0.86 | 84.33 | 12.2324 | -0.0024332 | 84.2979 | 0.032127 | Enter your altitude in feet in the cell with the red outline and read the standard pressure at that altitude in the blue cell and the correction factor in the yellow cell.
|  |  | 6000 | 1.1 | 1831 | 38 | 3 | 23.99 | 609.3 | 11.78 | 0.828 | 81.22 | 11.7818 | -0.0017568 | 81.1918 | 0.028249
|  |  | 7000 | 1.3 | 2136 | 34 | 1 | 23.1 | 586.7 | 11.34 | 0.797 | 78.19 | 11.3444 | -0.0044374 | 78.1776 | 0.012352
|  |  | 8000 | 1.5 | 2441 | 31 | -1 | 22.23 | 564.6 | 10.91 | 0.767 | 75.22 | 10.9202 | -0.010199 | 75.2537 | -0.033666 |  | Altitude in meters - | 2042 | meters
|  |  | 9000 | 1.7 | 2746 | 27 | -3 | 21.39 | 543.3 | 10.5 | 0.738 | 72.4 | 10.5088 | -0.00877 | 72.4179 | -0.017926 |  | Standard pressure at altitude, kPa - | 79.0969 | kiloPascals
|  |  | 10000 | 1.9 | 3050 | 23 | -5 | 20.58 | 522.7 | 10.1 | 0.71 | 69.64 | 10.1099 | -0.0098792 | 69.6774 | -0.037444 |  | Correction factor - | 0.78059 | Multiply by this to make a correction
|  |  | 15000 | 2.8 | 4577 | 6 | -14 | 16.89 | 429 | 8.29 | 0.583 | 57.16 | 8.2943 | -0.0042642 | 57.1464 | 0.013649 |  | Equation - | y = 9.64211029E-17x4 - 1.19160079E-11x3 + 5.58098266E-07x2 - 1.19583889E-02x + 1.01288566E+02
|  |  | 20000 | 3.8 | 6102 | -12 | -24 | 13.76 | 349.5 | 6.76 | 0.475 | 46.61 | 6.7533 | 0.0066909 | 46.5252 | 0.084757
|  |  | 25000 | 4.7 | 7628 | -30 | -34 | 11.12 | 282.4 | 5.46 | 0.384 | 37.65 | 5.4566 | 0.0034464 | 37.5813 | 0.068725
|  |  | 30000 | 5.7 | 9153 | -48 | -44 | 8.903 | 226.1 | 4.37 | 0.307 | 30.13 | 4.3754 | -0.0053563 | 30.1288 | 0.0011636
|  |  | 35000 | 6.6 | 10679 | -66 | -54 | 7.06 | 179.3 | 3.47 | 0.244 | 23.93 | 3.4829 | -0.012894 | 23.9732 | -0.043187
|  |  | 40000 | 7.6 | 12204 | -70 | -57 | 5.558 | 141.2 | 2.73 | 0.192 | 18.82 | 2.7542 | -0.024164 | 18.9501 | -0.13012
|  |  | 45000 | 8.5 | 13730 | -70 | -57 | 4.375 | 111.1 | 2.15 | 0.151 | 14.82 | 2.166 | -0.01598 | 14.8931 | -0.073147
|  |  | 50000 | 9.5 | 15255 | -70 | -57 | 3.444 | 87.5 | 1.69 | 0.119 | 11.65 | 1.697 | -0.0069749 | 11.6604 | -0.010369
|  |  | 55000 | 10.4 | 16781 | -70 | -57 | 2.712 | 68.9 | 1.33 | 0.0935 | 9.17 | 1.3276 | 0.0023978 | 9.1127 | 0.057271
|  |  | 60000 | 11.4 | 18306 | -70 | -57 | 2.135 | 54.2 | 1.05 | 0.0738 | 7.24 | 1.0401 | 0.0098675 | 7.1314 | 0.10861
|  |  | 70000 | 13.3 | 21357 | -67 | -55 | 1.325 | 33.7 | 0.651 | 0.651 | 4.49 | 0.64908 | 0.0019198 | 4.4355 | 0.054486
|  |  | 80000 | 15.2 | 24408 | -62 | -52 | 0.8273 | 21 | 0.406 | 0.406 | 2.8 | 0.41836 | -0.012362 | 2.8456 | -0.045563
|  |  | 90000 | 17.1 | 27459 | -57 | -59 | 0.52 | 13.2 | 0.255 | 0.255 | 1.76 | 0.27162 | -0.01662 | 1.8349 | -0.074896
|  |  | 100000 | 18.9 | 30510 | -51 | -46 | 0.329 | 8.36 | 0.162 | 0.162 | 1.12 | 0.1616 | 0.00040012 | 1.0774 | 0.042614

## 1.08 cfm delta T
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-03-30 15:46
Project Name: | NAME?
Project Number: | NUMBER?
Engineer: | ENGINEER?
Assumptions
1 | ????
2 | ????
3 | ????
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????
|  | 1.08 Units Conversion Factor (Uses density of dry air at 70°F, specific heat valid for -80 to 129°F) | [17 empty] | Specific Heat and Density of Dry and Moist Air vs. Temperature (From HVAC Equations, Data, and Rules of Thumb)
[20 empty] | Temperature Range, °F |  |  | Specific Heat, btu/lb.°F | Density, lb/ cubic ft. |  | Temperature, °F | Density, lb/ cubic ft.
|  | 1 | btu | = | 1 | cubic ft. | x | 60 | minutes | x | 0.074912 | pounds | x | 0.24 | btu |  | x | 1 | °F | Low End | High End | Average |  | Dry Air | Saturated Air |  | Dry Air | Saturated Air
|  |  | hour |  |  | minute |  |  | hour |  |  | cubic ft. |  |  | pound | °F |  |  |  | -80 | 129 | 24.5 | 0.24 | 0.081887 | 0.081533 | -80 | 0.10468 | 0.10468
[20 empty] | 130 | 215 | 172.5 | 0.241 | 0.062692 | 0.035271 | -50 | 0.096965 | 0.096956
|  | 1 | btu | = | 1.0787 | cubic ft. | x | ∆t, °F | [11 empty] | 216 | 280 | 248 | 0.242 |  |  | 0 | 0.086363 | 0.086252
|  |  | hour |  |  | minute | [13 empty] | 281 | 330 | 305.5 | 0.243 |  |  | 50 | 0.077857 | 0.076917
[20 empty] | 331 | 370 | 350.5 | 0.244 |  |  | 100 | 0.070887 | 0.066295
|  | For saturated air at 0°F | [17 empty] | 371 | 400 | 385.5 | 0.245 |  |  | 150 | 0.065062 | 0.048579
|  | 1 | btu | = | 1 | cubic ft. | x | 60 | minutes | x | 0.086363 | pounds | x | 0.24 | btu |  | x | 1 | °F | 401 | 440 | 420.5 | 0.246 |  |  | 200 | 0.060013 | 0.01291
|  |  | hour |  |  | minute |  |  | hour |  |  | cubic ft. |  |  | pound | °F |  |  |  | 441 | 460 | 450.5 | 0.247
[20 empty] | 461 | 470 | 465.5 | 0.248 |  |  |  | 0.0069706 | 0.010622
|  | 1 | btu | = | 1.2436 | cubic ft. | x | ∆t, °F | [11 empty] | 471 | 500 | 485.5 | 0.249 |  |  | 75 | 0.074372 | 0.071606
|  |  | hour |  |  | minute
For dry air at 0°F
|  | 1 | btu | = | 1 | cubic ft. | x | 60 | minutes | x | 0.086363 | pounds | x | 0.24 | btu |  | x | 1 | °F
|  |  | hour |  |  | minute |  |  | hour |  |  | cubic ft. |  |  | pound | °F
|  | 1 | btu | = | 1.2436 | cubic ft. | x | ∆t, °F
|  |  | hour |  |  | minute
For saturated air at 200°F
|  | 1 | btu | = | 1 | cubic ft. | x | 60 | minutes | x | 0.01291 | pounds | x | 0.241 | btu |  | x | 1 | °F
|  |  | hour |  |  | minute |  |  | hour |  |  | cubic ft. |  |  | pound | °F
|  | 1 | btu | = | 0.18667 | cubic ft. | x | ∆t, °F
|  |  | hour |  |  | minute
For dry air at 200°F
|  | 1 | btu | = | 1 | cubic ft. | x | 60 | minutes | x | 0.060013 | pounds | x | 0.241 | btu |  | x | 1 | °F
|  |  | hour |  |  | minute |  |  | hour |  |  | cubic ft. |  |  | pound | °F
|  | 1 | btu | = | 0.86779 | cubic ft. | x | ∆t, °F
|  |  | hour |  |  | minute
1.08 Units Conversion Factor (Uses density of dry air at 70°F, specific heat valid for -80 to 129°F)
|  | 1 | btu | = | 1 | cubic ft. | x | 60 | minutes | x | 0.074912 | pounds | x | 0.24 | btu |  | x | 1 | °F
|  |  | hour |  |  | minute |  |  | hour |  |  | cubic ft. |  |  | pound | °F
|  | 1 | btu | = | 1.0787 | cubic ft. | x | ∆t, °F
|  |  | hour |  |  | minute
1.1 Units Conversion Factor (Uses density of dry air at 60°F, specific heat valid for -80 to 129°F)
|  | 1 | btu | = | 1 | cubic ft. | x | 60 | minutes | x | 0.076359 | pounds | x | 0.24 | btu |  | x | 1 | °F
|  |  | hour |  |  | minute |  |  | hour |  |  | cubic ft. |  |  | pound | °F
|  | 1 | btu | = | 1.0996 | cubic ft. | x | ∆t, °F
|  |  | hour |  |  | minute
514.6392

## Composition of Air
Composition of Dry Air
Element |  | Symbol | % of Total, Note 1
Nitrogen |  | N | 78.08%
Oxygen |  | O | 20.95%
Argon |  | Ar | 0.934%
Carbon Dioxide |  | CO2 | 0.0314%
Neon |  | Ne | 0.001818%
Methane |  | CH | 0.0002%
Helium |  | He | 0.000524%
Krypton |  | Kr | 0.000114%
Hydrogen |  | H | 5e-05%
Xenon |  | Xe | 8.7e-06%
Ozone |  | O | 7e-06%
Nitrogen Dioxide |  | NO | 2e-06%
Iodine |  | I | 1e-06%
Carbon Monoxide |  | CO | Trace
Ammonia |  | NH | Trace
Notes
1 | These are perectages by volume at sea level pressure and 59°F
2 | From the CRC Handbook of Chemistry and Physics, 1997
3 | Air can contain as much as 5% water vapor (more typically, 1-3%). At 1-5%, it becomes the third most common constituent of air, which changes the other percentages accordingly.