## Slide 1: Existing Building Commissioning Workshop: Series 16, Session 4
A Field Introduction to Steam and Condensate Pumps
David Sellers
Senior Engineer, Facility Dynamics Engineering
Presented By:

## Slide 2: Logging Hot Gas Bypass

## Slide 3: Adding Hot Gas Bypass
Condenser
Evaporator
Metering Orifices
CW Supply and Return
CHW Supply and Return
Economizer
Hot Gas Bypass Valve
3 Stage Centrifugal Compressor

## Slide 4
Compressor
Hot gas valve and piping
Traditional condenser
Suction elbow

## Slide 5: Logging a Centrifugal Chiller’s Inlet Vanes and Hot Gas Bypass

## Slide 10: Steam and Condensate Resources
https://av8rdas.wordpress.com/2017/07/10/a-steam-heating-resources/
https://av8rdas.wordpress.com/2020/10/17/what-is-the-energy-content-of-a-pound-of-condensed-steam-part-1/
https://www.av8rdas.com/thermodynamic-diagrams-spreadsheet.html
https://www.av8rdas.com/magazine-articles.html#SteamValves

## Slide 11: Gordon’s Question
How do you convert pounds of steam to Btus?
My Answer
It depends ….

## Slide 12: It Depends on the Units of Measure
Invoice – 301.3 Mlbs of steam
So, M probably means mega, like megabyte, so the invoice is for 301,300,000 pounds of stream
But:
In the Roman Numeral System, M = 1,000, so the invoice could be for 301,300 pounds of steam

## Slide 13: Gordon’s Next Question (to the Utility)
Can you clarify what the “M” stands for in the invoice ?
The Answer
It stands for “K”, the SI prefix for 1,000
(which is “M” in the Roman Numeral System)

## Slide 14: Incidentally:
For a boiler burning gas to make steam, the bill could be:
MCF, for 1,000 (Roman M) cubic (volume, not the roman numeral for 100) feet, where a cubic foot is nominally 1,000 Btus, so about 1,000,000 Btu
Or it could be
Therms, which is exactly 100,000 Btu
Or it could be
Dth, the metric prefix Deka for 10, which is exactly 1,000,000 Btu
And the boiler itself could be rated in MMBtu, which are Roman “M”s so a thousand thousand Btus, i.e. a million Btus or a SI MBtus

## Slide 15: Confused Yet?

## Slide 16: Gordon’s Next Question
How do you convert pounds of steam to Btus?

## Slide 17: How Does Steam Deliver Energy

## Slide 25: Our Condensate Pump
Field Notes:
Condensate receiver dimensions
  38” high
  38” wide
Level change per cycle – 3-5/8”
Typical cycle time – 13 seconds
The Technique:
https://av8rdas.wordpress.com/2009/12/23/assessing-steam-consumption-with-an-alarm-clock/