## Slide 1: Central Plants
Tab 18-1
Pump Interactions and the Affinity Laws

## Slide 2: Parallel Pumps
Increasing Flow
Increasing Head
If both pumps are operating at the same speed and one fails, the operating point shifts down the system curve to the point where the single pump curve crosses it; typically more than 50% of the original flow but at less head
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 3
Assume the pumps are 100% redundant
    What should the logic be, specifically, to operate the pumps on a lead/lag basis?

## Slide 4
Assume the pumps are 100% redundant
    Is there any problem with running one pump and starting the other pump if a failure is detected?

## Slide 5
Assume the pumps are 100% redundant
    Will running two pumps at reduced speed save energy relative to running one pump at full speed?

## Slide 6: One Pump Operating Point
Single Pump Operating Point
2,000 gpm
55 ft.w.c.
12.5 inch impeller
1,150 rpm
84% efficiency
33.1 bhp

## Slide 7: Two Pumps Doing What One Could Do Each Pump Moves Half the Flow at the Design Head
Single Pump Operating Point
1,000 gpm
55 ft.w.c.
12.5 inch impeller
1,070 rpm
70% efficiency
19.8 bhp

## Slide 8: Two Pumps Doing What One Could Do Each Pump Moves Half the Flow at the Design Head
Both Pumps Operating Together
2,000 gpm
55 ft.w.c.
12.5 inch impeller
1,070 rpm
70% efficiency
39.6 bhp

## Slide 9: Two Pumps Doing What One Could Do Each Pump Moves Half the Flow at the Design Head
Both Pumps Operating Together
2,000 gpm
55 ft.w.c.
12.5 inch impeller
1,070 rpm
70% efficiency
39.6 bhp (vs. 33.1)

## Slide 10: The Motor Efficiency Changed
33.1 bhp
19.8 bhp

## Slide 11: The Drive Efficiency Changed

## Slide 12: The Fluid Mechanics Changed
One Pump

## Slide 13: The Fluid Mechanics Changed
One Pump

## Slide 14: The Bottom Line You’re Still Doing the Same Amount of Work
But probably not as efficiently

## Slide 15: What About Running Two Tower Fans at Half Speed vs. One at Full Speed?

## Slide 16: Same Question for These Towers?

## Slide 17: Same Question for These Towers?

## Slide 18: Different Size Parallel Pumps
System Dynamics can be Complex as Pumps Interact
The combined curve for different pumps in parallel can have an odd shape

## Slide 19: Different Size Parallel Pumps
System Dynamics can be Complex as Pumps Interact
Odd shapes can lead to odd events
The absorber and centrifugal pumps can “dead head” the modular chiller pump in some operating modes

## Slide 20: Multi Pump Constant Volume CW System
600 ton Absorption Chiller (Heat Sink for Cogen Plant)

## Slide 21: Multi Pump Constant Volume CW System
600 ton Centrifugal Chiller (Runs when no Heat Sink Needed

## Slide 22: Multi Pump Constant Volume CW System
60 Ton Modular Chiller Runs Year Round

## Slide 23: Multi Pump Constant Volume CW System
60 Ton Modular Chiller Runs Year Round
Mission critical load

## Slide 24: Multi Pump Constant Volume CW System
All Pumps in Parallel Through Their Loads
Mission critical load

## Slide 25: Multi Pump Constant Volume CW System
Mission critical load
Operating Mode for 4,380 hours per year

## Slide 26: Multi Pump Constant Volume CW System
Transitional Operating Mode