## Slide 1: Existing Building Commissioning Workshop: Series 16, Session 5
Testing the PEC Chilled Glycol System
David Sellers
Senior Engineer, Facility Dynamics Engineering
Presented By:

## Slide 2: Design Intent vs. Our Intent
What the designer anticipated
  106 gpm at 110 ft.w.c
  Both pumps run
  53 gpm at 110 ft.w.c from each pump
What we anticipate
  106 gpm at 42 – 69 ft.w.c.
  See the article on right sizing pumps at the link below for the details of how we made this field estimate
What our functional testing told us
  To be seen!
https://www.av8rdas.com/magazine-articles.html#RightSize

## Slide 3: Why Did We Need to Test the PEC Chilled Glycol System?
What the designer anticipated
  106 gpm at 110 ft.w.c
  Both pumps run
  53 gpm at 110 ft.w.c from each pump
What we anticipate
  106 gpm at 42 – 69 ft.w.c.
  See the article on right sizing pumps at the link below for the details of how we made this field estimate
What our functional testing told us
  To be seen!
https://www.av8rdas.com/magazine-articles.html#RightSize

## Slide 4: Why Did We Need to Test the PEC Chilled Glycol System?
Trending shows evidence of flow variation and instability in a constant flow system

## Slide 5: Flow Instability Appears to Trigger Temperature Control Instability

## Slide 6: What Could Cause Flow Variation in a Constant Volume System?
Three-way valve
Bypass with no balance valve
Three-way valve
Bypass with no balance valve

## Slide 7: What Could Cause Flow Variation in a Constant Volume System?
Supply piping
Header
Tubes; 1 per row
A
B
A
B

## Slide 8: What Could Cause Flow Variation in a Constant Volume System?
Multi-pass serpentine path through the coil fins

## Slide 9: What Could Cause Flow Variation in a Constant Volume System?
A
B
A
B
No cooling and Ice Making

## Slide 10: What Could Cause Flow Variation in a Constant Volume System?
A
B
A
B
Full Cooling

## Slide 11: What Could Cause Flow Variation in a Constant Volume System?
A
B
Modulating
A
B

## Slide 12: Assessing System Performance
Functional testing can help us assess these issues
…have pump, will test flow!
  Wide open test and shut off test establish pump performance point and impeller size
  Wide open test in different system configurations assesses the impact of configuration changes on flow

## Slide 13: Our Test Procedure

## Slide 14: What Operating Modes Should We Test?

## Slide 15: What Operating Modes Should We Test?
Closed

## Slide 16: What Operating Modes Should We Test?
Closed
50% Closed

## Slide 17: What Operating Modes Should We Test?
Closed

## Slide 18: What Operating Modes Should We Test?
Closed
50% Closed

## Slide 19: What Operating Modes Should We Test?
Closed

## Slide 20: What Operating Modes Should We Test?
Closed
50% Open

## Slide 21: What Operating Modes Should We Test?
Closed

## Slide 22: What Operating Modes Should We Test?

## Slide 23: Performing the Test https://www.av8rdas.com/testing-a-pump.html

## Slide 24: Plotting Our Pump Test Results
Test data
  Shut off test
    0 gpm
    106.4 ft. w.c.
  One pump, wide open
    ? gpm
    93.9 ft. w.c.

## Slide 25
Our test point is one point on the system curve

## Slide 26
Projecting the required flow up to our system curve tells us the actual head required by the system at that flow rate
Sketching an impeller curve through the intersection of our system curve and the design point shows we could get what we need with a 7-5/8” or so impeller

## Slide 27
The pump affinity laws tell us we could also get what we need by a speed change:
Speed New = Speed Old x (FlowNew/FlowOld)
Speed New = 1,344 rpm

## Slide 28
We could also get what we need by throttling to design with the existing impeller, which would generate a new system curve through that operating point
Notes: Head - ft.w.c. Flow Rate - gpm
0.00 0
0.92 10
8.25 30
22.92 50
91.67 100
103.00 106

## Slide 29: Our Options
Throttling ssss sss
Reduce speed with a motor change
Reduce speed with a VFD SSSSSSSsssss SSSSSSS
Trim the impeller
Quick, saves energy right away, but not as much as other options
Not possible ssssssss
Preserves pump efficiency, adds drive losses, adds complexity, adds cost
Reduces pump efficiency, very persistent, lower cost, less complex

## Slide 30: The Modification Process
Taking the pump apart
Rear access
Motor shaft coupling hub

## Slide 31: The Modification Process
The untrimmed impeller and empty casing

## Slide 32: The Modification Process
The trimmed impeller ready for re-installation along with a new seal
Before trimming
After trimming
The mechanical seal

## Slide 33: The Modification Process
The re-assembled pump with the base grouted and motor aligned

## Slide 34: Plotting Our Pump Test Results
Data from the modified pump
  Shut off test
    0 gpm
    70.2 ft. w.c.
    1 kW
  One pump, wide open
    ? gpm
    58.7 ft. w.c.
    2.1 kW

## Slide 35
Shut off test forces a known flow condition of 0 gpm
The head produced matches a 7-3/4” impeller curve

## Slide 36
“Eye-ball” the new impeller curve through the shut-off head test point

## Slide 37
With the pump running wide open, we read about 59 ft.w.c. of head
Projecting our measured head over to the impeller curve we have, and then projecting down from that point indicates about 105 – 110 gpm of flow and 2.6 – 2.7 bhp. At .746 kW/hp this equates to 1.9 – 2.0 kW vs. the 2.1kW we read.
Our target = 106 gpm

## Slide 38: Another Interesting Result

## Slide 39: Another Interesting Result
The system curve was unchanged by the impeller trim
With a smaller impeller, P2 can contribute nothing to the system flow until the head required drops below about 70 ft.w.c.
With P2 running alone, we get the performance targeted by the modification
If P1 is started, the operating point shifts to the point where the system curve intersects the combined pump operating curve. The head at this point is above the shut-off head for P2, so it produces no flow, even though it is operating

## Slide 40: Component Interactions

## Slide 41
Thanks For Attending!
The End