## Slide 1: Vapor Compression Refrigeration
Leveraging Phase Changes in Saturated Systems to Provide Cooling
David Sellers
Senior Engineer, Facility Dynamics Engineering

## Slide 2: Phase Changes and Saturated Systems

## Slide 3: Phase Changes and Saturated Systems

## Slide 4: Phase Changes and Saturated Systems

## Slide 5: Phase Changes and Saturated Systems

## Slide 6: Phase Changes and Saturated Systems

## Slide 7: Phase Changes and Saturated Systems

## Slide 8: Phase Changes and Saturated Systems
At saturation:
  The substance exists in both a liquid and vapor state
  At a constant pressure, the temperature of the substance will not change until:
    It is fully converted to a liquid (removing energy), or
    It is fully converted to a vapor (adding energy)
Notes: Water
Temp Pressure Density Enthalpy Entropy
Liquid Vapor Liquid Vapor Liquid Vapor
°F psia lbm/cu ft lbm/cu ft Btu/lbm Btu/lbm Btu/lbm °R Btu/lbm °R
211.80 14.650 59.833 0.037201 180.12 1151.0 0.31212 1.7580

## Slide 9: Phase Changes and Saturated Systems
Phase changes absorb a lot of energy
  Melting ice – 144 Btu/lb
  Heating water – 1Btu/lb-°F
  Converting water to steam – 971 Btu/lb
  Superheating steam – 0.5 Btu/lb
(all parameters are at atmospheric pressure)
Notes: Water
Temp Pressure Density Enthalpy Entropy
Liquid Vapor Liquid Vapor Liquid Vapor
°F psia lbm/cu ft lbm/cu ft Btu/lbm Btu/lbm Btu/lbm °R Btu/lbm °R
211.80 14.650 59.833 0.037201 180.12 1151.0 0.31212 1.7580

## Slide 10: Phase Changes and Saturated Systems
Phase changes absorb a lot of energy
  Melting ice – 144 Btu/lb
  Heating liquid R134 – .325 Btu/lb-°F
  Converting liquid R134 to vapor – 83.025 Btu/lb
  Superheating R134 vapor – .136 Btu/lb
(all parameters are at 40, psig, 45°F)
Notes: Water
Temp Pressure Density Enthalpy Entropy
Liquid Vapor Liquid Vapor Liquid Vapor
°F psia lbm/cu ft lbm/cu ft Btu/lbm Btu/lbm Btu/lbm °R Btu/lbm °R
211.80 14.650 59.833 0.037201 180.12 1151.0 0.31212 1.7580

## Slide 11: Ideal Refrigerant Properties
1928
Low condensing pressure
Evaporating pressure near atmospheric pressure
Condensing pressure not much higher than evaporating pressure
Low latent heat of vaporization for small machines to ensure controllability
Low vapor specific volume
Compatible with lubricating oil
Non-corrosive
Stable/does not decompose with age
Does not form non-condensable gasses upon contact with moisture
Does not form explosive compounds upon contact with lubricant
Non-explosive and non-inflammable
Low cost and easy to obtain
Non-poisonous and no discomfort if it leaks into air
Leaks easy to detect with simple methods
Compatible with gaskets and packing materials
Now
Nontoxic
Nonflammable
Zero ozone depletion potential (ODP)
Zero global warming potential (GWP)
Short atmospheric lifetime
High latent heat of vaporization
Low power consumption
Low vapor specific volume
Compressor discharge temperature below 260°F
Evaporating pressure above atmospheric pressure
Condensing pressure below the critical pressure

## Slide 12: Refrigerant Properties Comparison for Typical HVAC Application Conditions

## Slide 13: Refrigerant Properties Comparison for Typical Refrigeration Application Conditions

## Slide 14: Refrigerant Properties Comparison for Typical Freezer Application Conditions

## Slide 15: Refrigerant Environmental Properties

## Slide 16: Refrigerant Environmental Properties

## Slide 17: Refrigerant Environmental Properties

## Slide 18: Refrigerant Environmental Properties

## Slide 19: Refrigerant Environmental Properties

## Slide 20: Refrigerant Environmental Properties

## Slide 21: Refrigerant Environmental Properties

## Slide 22: Refrigerant Environmental Properties

## Slide 23: Refrigerant Environmental Properties

## Slide 24: A Few Words about Refrigerant Blends

## Slide 25: Azeotrope
A mixture made up of two or more refrigerants with similar boiling points that act as a single fluid. The components of azeotropic mixtures will not separate under normal operating conditions and can be charged as a vapor or liquid
Definitions from the National Refrigerants web site; http://www.refrigerants.com/frame.htm
Notes: http://www.refrigerants.com/frame.htm

## Slide 26: Near Azeotrope
A mixture made up of two or more refrigerants with different boiling points that, when in a totally liquid or vapor state, act as one component. However, when changing from vapor to liquid or liquid to vapor, the individual refrigerants evaporate or condense at different temperatures. Near-azeotropic mixtures have a temperature glide of less than 10° F and should be charged in the liquid state to assure proper mixture (non-azeotropic) composition
Definitions from the National Refrigerants web site; http://www.refrigerants.com/frame.htm
Notes: http://www.refrigerants.com/frame.htm

## Slide 27: Zeotrope
A mixture made up of two or more refrigerants with different boiling points. Zeotropic mixtures are similar to near-azeotropic mixtures with the exception of having a temperature glide greater than 10° F. Zeotropic mixtures should be charged in the liquid state
Definitions from the National Refrigerants web site; http://www.refrigerants.com/frame.htm
Notes: http://www.refrigerants.com/frame.htm

## Slide 28: Phase Changes and Saturated Systems An Experiment
Heat water in a low pressure boiler
Monitor:
  Water temperature
  Vapor temperature over the water surface
  Power
Plot the results

## Slide 29: Phase Changes and Saturated Systems An Experiment
Monitoring temperature
Liquid sensor
Vapor sensor
Thermocouple

## Slide 30: Phase Changes and Saturated Systems An Experiment
Monitoring power

## Slide 31: Phase Changes and Saturated Systems An Experiment
Monitoring power

## Slide 37: For More Information
https://av8rdas.wordpress.com/2013/07/15/saturated-multi-phase-systems-and-proof-that-a-watched-pot-does-actually-boil/

## Slide 38: Vapor Compression Refrigeration Machines
An application of saturated system and phase change principles and concepts

## Slide 39
Evaporation
Compression
Condensation
Expansion

## Slide 40: Refrigeration Compressor Performance
Basis for Example
Trane RAU air cooled condensing unit
  Contains compressors, and condenser coil
  Connects to a remote coil or evaporator
40 tons, 2 circuits,
Four 10 ton compressors
R410a
https://www.trane.com/commercial/north-america/us/en.html

## Slide 43: Evaporator Performance
Basis for Example
Greenheck Direct Expansion (Dx) Coil
  8,750 cfm
  500 fpm face velocity
  4 row
  10 fins per Inch
  Intertwined
Courtesy https://www.capitalcoil.com/

## Slide 45
Compressor and Evaporator Interactions

## Slide 46
Compressor and Evaporator Interactions

## Slide 47
Compressor and Evaporator Interactions

## Slide 48
Compressor and Evaporator Interactions

## Slide 49
Compressor and Evaporator Interactions

## Slide 50: An Air Cooled Vapor Compression Cycle Chiller

## Slide 52: An Air Cooled Vapor Compression Cycle Chiller

## Slide 53
Evaporator
Suction Line
Liquid Line
Liquid Line Solenoid Valve
Hot Gas Line

## Slide 54: Which Pipe is Which
Suction Line
Liquid Line
Hot gas line
Largest, coldest and insulated
Smallest, warm, usually not insulated
Size between suction and liquid line size, hot, typically not insulated

## Slide 55
Evaporator
Filter Dryer (Not shown on diagram)
Service Valves (Not shown on diagram
Service Bypass to Allow Filter Dryer to be Serviced (Not shown on diagram

## Slide 56
Chilled Water Pipes
Liquid Line Solenoid Valve
Liquid Lines
Suction Line

## Slide 57
Evaporator
Compressor
Liquid Line
Hot Gas Line
Suction Line

## Slide 58
Compressor
Compressor
Suction Line
Hot Gas Lines

## Slide 59
Compressor
Suction Line

## Slide 60
Unloaders

## Slide 61
Crank Case Heater

## Slide 62
Crank Case Heater

## Slide 63
Oil Sight Glass

## Slide 64: Hand Pump for Adding Oil

## Slide 65: Refrigerant Oil
R22 systems use mineral oil as a lubricant
R410A systems use either ether oil or alkylbenzene
    Using the wrong oil can cause sludge and other problems leading to failure
    Tools use on R22 systems can be “contaminated” with mineral oil and should not be used on R410A systems
    Contamination can lead to sludge and other problems
    R410 oil is an order of magnitude more hygroscopic than R22 oil

## Slide 66: Oil Management is Crucial
Oil Seperators
  Piped into the discharge line
  Keep it from leaving the compressor

## Slide 67: Oil Management is Crucial
Oil Seperators
  Piped into the discharge line
  Keep it from leaving the compressor

## Slide 68: Oil Management is Crucial
Oil Seperators
  Piped into the discharge line
  Keep it from leaving the compressor

## Slide 69: Oil Management is Crucial
Oil Seperators
  Piped into the discharge line
  Keep it from leaving the compressor

## Slide 70: Oil Management is Crucial
Design the Piping to Bring it Back
Pitch towards the compressor
Maintain velocities that will carry the oil back
Use double suction risers to change elevation

## Slide 71: Vacuum Pump Evacuating the System in Preparation for Charging
Vacuum Pump

## Slide 73: Installation Practices
Refrigerant piping installation practice critical to short and long term system integrity
  General requirements no different from those employed with any built up refrigeration system
  Details associated with R410 systems may vary from standard practice in the field at this point in time

## Slide 74: Installation Practices
Refrigerant piping installation practice critical to short and long term system integrity
  General requirements no different from those employed with any built up refrigeration system
  Details associated with R410 systems may vary from standard practice in the field at this point in time

## Slide 75: Cleanliness Is Essential
Cleaned to an ASTM established limit for residue
Purged with dry nitrogen
Sealed with rubber plugs with positive nitrogen pressure inside the tuber
Cleaned and Capped
Used to be Cleaned and Capped

## Slide 76: Cleanliness Is Essential
  Moisture and refrigerant don’t work well together
  Corrosion
  Ice
  Refrigerant oil problems
  Motor problems
Cleaned and Capped
Used to be Cleaned and Capped

## Slide 77: Cleanliness Is Essential
  Dirt and precision machinery don’t work well together
  Moving parts in compressors
  Small orifices in metering and control valves and lubrication system
  Chemical reactions with oil and refrigerant
Cleaned and Capped
Used to be Cleaned and Capped

## Slide 78: Nitrogen Purge is Essential While Brazing
Courtesy http://www.hvactrainingsolutions.net
Courtesy http://www.reflok.pl
Notes: http://www.reflok.pl

## Slide 79: Field Joints
Field joints can be made using a frustum of right circular cone
Image courtesy Mitsubishi PRUY Service Instruction; Used with Permission

## Slide 80: Field Joints
Field joints can be made using a 45°SAE Flare joint
Image courtesy Mitsubishi PRUY Service Instruction; Used with Permission
Operating Pressures
Refrigerant Low Side High Side
R22 55-70 psig 180 - 260 psig
R410 95 - 135 psig 305 - 410 psig

## Slide 81: Field Joints
Field joints are made using a 45°SAE Flare joint
Image courtesy Mitsubishi PRUY Service Instruction; Used with Permission
Operating Pressures
Refrigerant Low Side High Side
R22 55-70 psig 180 - 260 psig
R410 95 - 135 psig 305 - 410 psig

## Slide 82: Field Joints

## Slide 83: Field Joints

## Slide 84: Flaring Tools; They’re Not All Created Equal
Conventional flaring tools “press” the flare onto the end of the tube
Recommended flaring tool rolls the flare onto the end of the tube
Images courtesy www.ridgid.com/; Used with Permission
Either way:
  Metal to metal sealing mechanism
  Lubricate flare before tightening
Notes: http://www.ridgid.com/Tools/458R-Ratchet-Flaring-Tool/index.htm
www.snapon.com

## Slide 85: Tightening the Connection
Lubricate with a refrigerant compatible oil
Use two wrenches
Use specified torque values

## Slide 86: Torque Wrenches, Flare Nut Wrench and Crow’s Foot

## Slide 87: Tightening the Connection
Easier accomplished on the bench than in the air
Factory line sets minimize field flares

## Slide 88: Vibration and Stress Relief
Flare
Flare
Branch controller support per vendor requirements
Rigid support nominally with-in 20” per vendpr requirements

## Slide 89: Vibration and Stress Relief
Relative motion still possible with out sway bracing

## Slide 90
Condenser
Compressor
Receiver

## Slide 91
Condenser

## Slide 92: Failed Condenser Fan

## Slide 96
Condenser
Receiver
Liquid Line Solenoid Valve
Expansion Valve
Evaporator
Compressor

## Slide 97
Liquid Line Solenoid Valve
Expansion Valve
Liquid Lines
Suction Line

## Slide 98: Electronic Expansion Valve Controllers

## Slide 99: A Refrigerant Sight Glass

## Slide 101: Typical Control Switches

## Slide 102: Adding Hot Gas Bypass
Hot Gas Solenoid
Hot Gas Regulator

## Slide 103
Hot Gas Bypass Lines
Hot Gas Solenoid Valve
Service Valve
Hot Gas Regulator

## Slide 104
Hot Gas Connections to the Evaporator

## Slide 105: Let’s Review

## Slide 106: Name the Parts in the Diagram on the Next Slide

## Slide 107
A
B
C
D
E
F
G

## Slide 108: Name the Parts in the Diagram on the Next Slide
Air Cooled Condenser
Reciever
Liquid Line Solenoid Valve
Expansion Valve
Evaporator
Compressor
Hot Gas Solenoid Valve (Right) and Hot Gas Regulator (Left)

## Slide 109: A Water Cooled Centrifugal Chiller

## Slide 110: Same Cycle, Larger, Centrifugal vs. Screw Compressor, Water vs. Air Cooled

## Slide 111: A Typical Water Cooled Vapor Compression Cycle Chiller
Condenser
Evaporator
Metering Orifices
3 Stage Centrifugal Compressor
CW Supply and Return
CHW Supply and Return
Economizer

## Slide 112: Try Your Hand At Identifying the Parts (Answers Follow)

## Slide 113: A Water Cooled Centrifugal Chiller
7 ?
9 ?
8 ?
2 ?
1 ?
6 ?
5 ?
3 ?
4 ?

## Slide 114: A Water Cooled Centrifugal Chiller
Condenser
Evaporator
Economizer
Three Stage Centrifugal Compressor
Motor
Purge Pump
Suction Elbow
Controls
Lubrication System

## Slide 115: Inside the Condenser
Water Box; Marine Head Type
Tube Sheet
Tubes
Temperature Sensor
Baffle Plate

## Slide 116: Inside the Evaporator
Eliminators
Oil Sump and Pump

## Slide 117: Inside the 3 Stage Compressor

## Slide 118
Impeller (One per Stage)
Diffuser (One per Stage)
Inlet Vane Linkage System
Refrigerant Flow Through a Typical Compressor Stage

## Slide 119: Inlet Vanes and Suction Elbow

## Slide 120: Adding Hot Gas Bypass
Condenser
Evaporator
Metering Orifices
CW Supply and Return
CHW Supply and Return
Economizer
Hot Gas Bypass Valve
3 Stage Centrifugal Compressor

## Slide 121
Compressor
Hot gas valve and piping
Traditional condenser
Suction elbow

## Slide 122: Logging a Centrifugal Chiller’s Inlet Vanes and Hot Gas Bypass

## Slide 127: Free Cooling Cycles
Are they really free?

## Slide 128: Just Because It’s Free Doesn’t Mean You Should Use It

## Slide 129: Plate and Frame Heat Exchangers

## Slide 135: Plate and Frame vs. Shell and Tube

## Slide 136: Plate and Frame vs. Shell and Tube

## Slide 137: Plate and Frame vs. Shell and Tube

## Slide 138: Plate and Frame vs. Shell and Tube

## Slide 139: An Innovative Approach to Free Cooling

## Slide 140
UC Santa Cruz
Pre-Wet Economizer System
2016-01-29
Drawn By : DS
The Control System Graphic

## Slide 141
UC Santa Cruz
Pre-Wet Economizer System
2016-01-29
Drawn By : DS
Physical Sciences Building Loads
Science Library Building Loads
Natural Science Building Loads
Thimann Building Loads
Sinsheimer Labs Building Loads
Chiller 4
Chiller 6
Chiller 3
The Untangled System Diagram

## Slide 142
UC Santa Cruz
Pre-Wet Economizer System
2016-01-29
Drawn By : DS
Physical Sciences Building Loads
Science Library Building Loads
Natural Science Building Loads
Thimann Building Loads
Sinsheimer Labs Building Loads
Chiller 4
Chiller 6
Chiller 3
The Original Plant Configuration
These loads are 100% outdoor air loads trying to deliver air in the low to mid 50’s°F
These loads are economizer equipped loads trying to deliver air in the upper 50’s to low 60’s°F

## Slide 143
UC Santa Cruz
Pre-Wet Economizer System
2016-01-29
Drawn By : DS
Physical Sciences Building Loads
Science Library Building Loads
Natural Science Building Loads
Thimann Building Loads
Sinsheimer Labs Building Loads
Chiller 4
Chiller 6
Chiller 3
The Original Plant Configuration
These loads are 100% outdoor air loads trying to deliver air in the 50-60°F range
These loads are economizer equipped loads trying to deliver air in the upper 50’s to low 60’s°F

## Slide 144
There Are A Lot of Hours When 100% Outdoor Air Systems Delivering 50-60°F Air will Need Preheat

## Slide 145
UC Santa Cruz
Pre-Wet Economizer System
2016-01-29
Drawn By : DS
Physical Sciences Building Loads
Science Library Building Loads
Chiller 4
Chiller 6
Chiller 3
The Original Plant Configuration
If you pumped water that was warmer than the outdoor air through the chilled water coils in these units, you would cool the water and warm the air
Thimann Building Loads
Sinsheimer Labs Building Loads
Natural Science Building Loads

## Slide 146
UC Santa Cruz
Pre-Wet Economizer System
2016-01-29
Drawn By : DS
Physical Sciences Building Loads
Chiller 4
Chiller 6
Chiller 3
The Original Plant Configuration
If you shut down the economizers, these loads would require cooling
If you pumped water that was colder than the mix of return air and minimum outdoor air through the chilled water coils in these units, you would provide the cooling and warm the water
Thimann Building Loads
Sinsheimer Labs Building Loads
Natural Science Building Loads
Science Library Building Loads

## Slide 147
Physical Sciences Building Loads
Chiller 4
Chiller 6
Chiller 3
UC Santa Cruz
Wet Economizer System
2016-01-29
Drawn By : DS
The Modification to Make the Wet Economizer
A strategically located valve and piping connection will allow water returning from the loads requiring preheat (a source of cool water) to be circulated to the loads requiring cooling (a source of warm water) and then back to the loads requiring preheat
Science Library Building Loads
Thimann Building Loads
Sinsheimer Labs Building Loads
Natural Science Building Loads

## Slide 148
Physical Sciences Building Loads
Chiller 4
Chiller 6
Chiller 3
UC Santa Cruz
Wet Economizer System
2016-01-29
Drawn By : DS
The Wet Economizer in Operation
A strategically located valve and piping connection will allow water returning from the loads requiring preheat (a source of cool water) to be circulated to the loads requiring cooling (a source of warm water) and then back to the loads requiring preheat
Science Library Building Loads
Thimann Building Loads
Sinsheimer Labs Building Loads
Natural Science Building Loads
≈ 62°F
≈ 55°F
≈ 61°F
≈ 58°F
≈ 62°F
Outdoor Air ≈ 53°F

## Slide 149: Chiller Based Free Cooling Cycle

## Slide 150: Adding “Free Cooling”
Condenser
CW Supply and Return
CHW Supply and Return
Evaporator
Economizer
2 Position Valve (Typical of 2; Open for Free Cooling)
Hot Gas Bypass Valve
3 Stage Centrifugal Compressor

## Slide 151: “Free Cooling” Operation
Condenser
CW Supply and Return
CHW Supply and Return
Evaporator
Economizer
2 Position Valve Opens
Compressor locked out
2 Position Valve Opens

## Slide 152: “Free Cooling” Operation
Condenser
CW Supply and Return
CHW Supply and Return
Evaporator
Economizer
2 Position Valve Opens
Compressor locked out
2 Position Valve Opens

## Slide 153: “Free Cooling” Operation
Condenser
CW Supply and Return
CHW Supply and Return
Evaporator
Economizer
2 Position Valve Opens
Compressor locked out
2 Position Valve Opens

## Slide 154: “Free Cooling” Operation
Condenser
CW Supply and Return
CHW Supply and Return
Evaporator
Economizer
2 Position Valve Opens
Compressor locked out
2 Position Valve Opens

## Slide 155: A Heat Recovery Centrifugal Chiller
The chiller in the following slide has a second condenser tube bundle that is piped to the heating hot water system. This allows the hot gas off of the compressor to be used to generate hot water for reheat loads prior to having its heat rejected to the cooling tower via the traditional condenser.

## Slide 158
Hot gas valve and piping
Compressor
Evaporator
Traditional condenser
Heat recovery condenser
Suction elbow