## Slide 1
DP
Pump 1
PT
Cold water make-up from a back flow preventer
Diaphragm type expansion tank
Bell and Gossett 2AD-es
87.4 gpm at 45.6 ft.w.c.
75.9% Efficiency
1,750 rpm, 1.3 Bhp, 2 hp motor
(Typical for each pump)
DP
TT
TT
1st Floor Finned Tube Radiation
Butterfly valve
Bureaucratic Affairs
Heating Hot Water System
Page 1
2016-11-24
Drawn By – DAS
Click Here to Return to the Exercise Description
Two way control valve
Balance valve
Check valve
Ball valve
Pressure reducing valve
Pressure relief valve
Three way control valve
Steam trap
Thermometer with well
Pressure gauge with isolation valve
PT
Pressure Transmitter
TT
Temperature transmitter with well
DP
Differential pressure transmitter with isolation valves
TT
Warm-up Coil
Normally Open to the Coil
Capacity – 586,200 Btu/hr
6 ft. high x 8 ft. wide
Air Side
Flow rate = 22,306 cfm
Entering air temperature – 62.0°F
Leaving air temperature – 86.3°F
Pressure drop – 0.09 in.w.c.
Water Side
Flow rate = 29.8 gpm
Entering water temperature – 170.0°F
Leaving water temperature – 130.0°F
Pressure drop – 4.4 ft.w.c.
TT
Typical of 4 circuits
Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single tier, 18" mounting height, 816 Btu/hr/ft;
243 feet of active element in four circuits of 7.2 gpm each, 28.8 total gpm, 14°F ∆t, 170°F supply, 156°F return
Normally Open
Match Line – See Sheet 2
A
B
Reheat Coil (Typical of 5)
Normally Open to the Coil
Capacity – Varies
Air Side
Flow rate = Varies, 500 fpm maximum face velocity
Entering air temperature – 53.0°F
Leaving air temperature – 82 °F
Pressure drop – 0.1 in.w.c. maximum
Water Side
Flow rate = Varies
Entering water temperature – 170.0°F
Leaving water temperature – 150.0°F
Pressure drop – 5 ft.w.c. maximum.
1st Floor Reheat Loads; Nominal gpm for the floor = 36.5 gpm
Pump 2
Normally Open
Heat Exchanger
Bell and Gossett SU-67-2
Shell Side
Flow - 85.5 gpm
Entering water – 147°F
Leaving water – 170°F
Pressure drop – 2.11 ft.w.c.
Tube Side
1,019 lb/hr
5 psig steam
LPS
LPR
Heat Exchanger 1
Note 1
Notes: Bell and Gossett 2AD-es Flow - 87.4 Head - 45.6 Speed - 1,750 Bhp - 1.3 Efficiency - 75.9% Motor hp - 2

## Slide 2
Bureaucratic Affairs
Heating Hot Water System
Page 2
2016-11-24
Drawn By – DAS
Click Here to Return to the Exercise De
scription
TT
Normally Open
Typical of 4 circuits
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single tier, 18" mounting height,996 Btu/hr/ft;
270 feet of active element in four circuits of 7.2 gpm each, 28.8 total gpm, 19°F ∆t, 170°F supply, 151°F return
2nd Floor Finned Tube Radiation
Match Line – See Sheet 1
A
B
TT
Reheat Coil (Typical of 7)
Normally Open to the Coil
Capacity – Varies
Air Side
Flow rate = Varies, 500 fpm maximum face velocity
Entering air temperature – 53.0°F
Leaving air temperature – 82.7 °F
Pressure drop – 0.1 in.w.c. maximum
Water Side
Flow rate = Varies
Entering water temperature – 170.0°F
Leaving water temperature – 150.0°F
Pressure drop – 5 ft.w.c. maximum
2nd Floor Reheat Loads; Nominal gpm for the floor = 36.5 gpm
Note 1
Set for 1 gpm to maintain minimum flow in the circuit for the floor. The 1st floor valve to be located across the mains near column A2. The 2nd floor valve to be located across the mains near column B2
Note 1
Notes: Bell and Gossett 2AD-es Flow - 87.4 Head - 45.6 Speed - 1,750 Bhp - 1.3 Efficiency - 75.9% Motor hp - 2