## Slide 1: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes

## Slide 2: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
A Historical Perspective and A Look at Pneumatic Controls

## Slide 3: A 1950/60’s Vintage Analog Controller

## Slide 4: A 1950/60’s Vintage Analog Controller

## Slide 5: A 1950/60’s Vintage Analog Controller

## Slide 6: A 1950/60’s Vintage Analog Controller

## Slide 7: A 1950/60’s Vintage Analog Controller

## Slide 8: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
Pneumatic Controllers in Action

## Slide 9: A Typical One Pipe Pneumatic Control System
M
Actuator
Air Supply (“Main” Air)
Nozzle
Restrictor T
Controller
“Flapper”
Filter
Gauge
Restrictor
Diaphragm
Piston
Spring

## Slide 10: A Typical One Pipe Pneumatic Control System
M
A wide open flapper causes more of a pressure drop due to flow at the orifice in the restrictor tee than a flapper that has moved closer to the nozzle. As a result, the pressure down stream of the orifice is relatively low and the actuator retracts

## Slide 11: A Typical One Pipe Pneumatic Control System
M
As the flapper closes, the flow and pressure drop due to flow through the restrictor tee orifice is reduced. As a result, the pressure down stream of the orifice builds and the actuator extends

## Slide 12: A Typical One Pipe Pneumatic Control System
M
As the flapper closes, the flow and pressure drop due to flow through the restrictor tee orifice is reduced. As a result, the pressure down stream of the orifice builds and the actuator extends

## Slide 13: A Typical One Pipe Pneumatic Control System
M
As the flapper closes, the flow and pressure drop due to flow through the restrictor tee orifice is reduced. As a result, the pressure down stream of the orifice builds and the actuator extends

## Slide 14: A Typical One Pipe Pneumatic Control System
M
Flapper motion in the opposite direction increases the airflow through the restrictor tee orifice, the pressure downstream of the orifice drops again, and the actuator retracts

## Slide 15: A Typical One Pipe Pneumatic Control System
M
Flapper motion in the opposite direction increases the airflow through the restrictor tee orifice, the pressure downstream of the orifice drops again, and the actuator retracts

## Slide 16: A Typical One Pipe Pneumatic Control System
M
Flapper motion in the opposite direction increases the airflow through the restrictor tee orifice, the pressure downstream of the orifice drops again, and the actuator retracts

## Slide 17: A Typical Two Pipe Pneumatic Control System
M
“Main Air” chamber
“Branch” pressure chamber
Pilot pressure chamber
Exhaust chamber
Flapper (moved by controlled parameter)
Orifice

## Slide 18: A Typical Two Pipe Pneumatic Control System
M
Main air supply valve and spring
Motion

## Slide 19: A Typical Two Pipe Pneumatic Control System
M
Exhaust valve and spring
Motion

## Slide 20: A Typical Two Pipe Pneumatic Control System
M
Diaphragms

## Slide 21: A Typical Two Pipe Pneumatic Control System
M
A wide open flapper bleeds enough air from the pilot chamber to cause a significant pressure drop at the orifice and the chamber pressure approaches atmospheric pressure

## Slide 22: A Typical Two Pipe Pneumatic Control System
M
A process up-set causes the flapper to move and restrict flow out of the pilot chamber, reducing the pressure drop at the orifice.

## Slide 23: A Typical Two Pipe Pneumatic Control System
M
Pilot chamber pressure increases, moving the exhaust valve, which moves the supply valve and feeds main air into the branch line, causing the branch pressure to increase and the actuator to extend

## Slide 24: A Typical Two Pipe Pneumatic Control System
The increasing pressure in the branch chamber pushes back on the exhaust valve, moving it back towards the pilot chamber. As the forces come into balance, the movement of the exhaust valve allows the supply valve to close.
M

## Slide 25: A Typical Two Pipe Pneumatic Control System
A process upset the other way moves the flapper away from the nozzle and causes the pilot chamber pressure to drop. As a result, the exhaust valve moves away from the supply valve and vents the branch chamber to atmosphere.
M

## Slide 26: A Typical Two Pipe Pneumatic Control System
M
As the branch chamber pressure drops, the forces acting on the exhaust valve and diaphragms come back into balance and the exhaust valve closes.

## Slide 27: One Pipe vs. Two Pipe Pneumatic Thermostats
One Pipe Thermostats
Inexpensive and simple
High air consumption
Sensitive to leaks
Restrictor tees that can:
  Plug
  Require periodic replacement
  Are difficult to find
Branch line length to the sensor can impact accuracy
Branch line length impacts lags
Mechanical devices
Operate on very small force differentials
Pivot points, linkages and diaphragms that can wear
Two Pipe Thermostats
More expensive and complex
Lower air consumption
Tolerate leaks
No restrictor tees
  Plug
  Require periodic replacement
  A re difficult to find
Branch line length has no accuracy impact
Branch line length does not impacts lags
Mechanical devices
Operate on very small force differentials
Pivot points, linkages and diaphragms that can wear

## Slide 28: Pneumatic Controls vs. Pneumatic Actuation
Pneumatic Controls
Complex
Operate on very small force differentials
Potentially slow reaction times due to orifices
Pivot points, linkages and diaphragms that can wear
Consume air continuously due to pilot valves and bleed orifices
Dirty air leads to system wide failures
Mechanical devices
Pneumatic Actuation
Simple
Can generate large forces
Can move very quickly
Very few moving parts and moving parts are simple
Only consume air (energy) when they move
Tolerate dirty air
Mechanical devices
Require a separate air system and signal convertors when applied when with DDC technology

## Slide 29: Electric Actuators vs. Pneumatic Actuators
Electric Actuation
Complex
Use small, low power motors to allow wiring without conduit
Slow because of gear trains required by small motors
Many moving parts; gears, clutches end switches etc.
Consume power continuously if they are holding against a spring
Mechanical devices
No air system required (but power distribution panels required for zones to comply with NEC article 725 requirements for the energy limited required for wiring with out conduit
Pneumatic Actuation
Simple
Can generate large forces
Can move very quickly
Very few moving parts and moving parts are simple
Only consume air (energy) when they move
Mechanical devices
Require a separate air system and signal convertors when applied when with DDC technology
No air system required (but power distribution panels required for zones to comply with NEC article 725 requirements for the energy limited required for wiring with out conduit

## Slide 30: Pneumatic Control Resources
Blog posts on www.Av8rDAS.Wordpress.com
Pneumatic Controls Resources
Pneumatic Controls, First Cost Advantages, and Retrocommissioning Opportunities
Retrocommissioning Findings: Make Up Air Handling System Simultaneous Heating and Cooling – The Clues – #2 – The Controls May be Pneumatic
Resources for the Resourceful: The Honeywell "Gray Manual’
Control Technology; A Glimpse Backward and Some Thoughts on the Future

## Slide 31: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
Moving to DDC (Direct Digital Control or Distributed Digital Control)

## Slide 32: A 1970’s Vintage Control and Automation System

## Slide 33: A 1970’s Vintage Control and Automation System

## Slide 34: Current Technology Control and Automation System – The Controller

## Slide 35: Not Being Able to See or Get Your Hands on What’s Going On
… a down side to DDC
Black Box
Black Box

## Slide 36: Even Though You Can’t See Them …
Black Box
… the inner workings and controlling software of a DDC controller are critical to success

## Slide 37: Even Though You Can’t See Them …
Output
Multiplexer
Amplifier
Sample/Hold
A to D Conversion
Communications Controller
Micro-processor/ Controller
Power Supply
Amplifier
D to A Conversion
Output
Output
Output
Input
Input
Input
Input
De-multiplexer
Network Interface
Memory
Accuracy Impact
Accuracy Impact
Accuracy Impact
Accuracy Impact
… the inner workings and controlling software of a DDC controller are critical to success

## Slide 38: Even Though You Can’t See Them …
Output
Multiplexer
Amplifier
Sample/Hold
A to D Conversion
Communications Controller
Micro-processor/ Controller
Power Supply
Amplifier
D to A Conversion
Output
Output
Output
Input
Input
Input
Input
De-multiplexer
Network Interface
Memory
… the inner workings and controlling software of a DDC controller are critical to success
Impact What Happens
Impact What Happens
Impact What Happens
Impact What Happens

## Slide 39: Even Though You Can’t See Them …
Output
Multiplexer
Amplifier
Sample/Hold
A to D Conversion
Communications Controller
Micro-processor/ Controller
Power Supply
Amplifier
D to A Conversion
Output
Output
Output
Input
Input
Input
Input
De-multiplexer
Network Interface
Memory
… the inner workings and controlling software of a DDC controller are critical to success
Speed Impact
Speed Impact
Speed Impact
Speed Impact

## Slide 40: Step Outside the Black Box and its Still and Analog World
Black Box
Black Box

## Slide 41: Generally, there’s Good News and Bad News
Good News
No moving parts in the controller
More information
Fast response
Precision
Modifications made by typing things in stead of wiring or piping things
Infinitely flexible
Cost effective
Out of this world capabilities
Bad News
The controller is a black box
The information may not be correct
Capable of doing dumb things very quickly
Capable of doing dumb things very precisely
Not everyone took the high school typing elective
Can implement misapplication of fundamentals
Flexibility sacrificed by poorly defined designs in competitive bid environments
Still have to deal with the real world

## Slide 42: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
Digital Control Processes

## Slide 43: A Simple Digital Control Process

## Slide 44
A Simple Digital Controller

## Slide 45
Coil Circuit Connections
Common Contact Connection
Normally Open Contact Connection
Normally Closed Contact Connection
Normally Open Contact
Normally Closed Contact
Coil
Armature and Common Contact
Pivot
Spring
Manual Test Mechanism
Mechanical Indication Mechanism
LED Indicator
A Simple Digital Controller

## Slide 46
For More on Relays, see Learning about Relay Logic; What’s a Relay? at www.Av8rDAS.Wordpress.com

## Slide 47: A Fun Digital Control Process

## Slide 48: Multiple Relays Allow You to Perform Logic

## Slide 49: Multiple Relays Allow You to Perform Logic

## Slide 50: Multiple Relays Allow You to Perform Logic
For more about how to make your own Jeopardy game, see Learning about Relay Logic; Build Your Very Own Jeopardy Game and Making a Jeopardy Game Board in PowerPoint to Supplement Your Light and Buzzer System (and Learning a Bit About PowerPoint Templates)

## Slide 51: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
Floating and Proportional Control

## Slide 52: A Simple Analog Proportional Control System
Sensor
Set Point and Throttling Range Adjustments
Final Control Element
Feedback Mechanism

## Slide 53: A Simple Control System
The make up valve is the device to be controlled; a.k.a. the Controlled Variable
Notes: Development 2

## Slide 54: A Simple Control System
Ideally, the make up valve would open as the level drops and close as it rises
Notes: Development 2

## Slide 55: A Simple Control System
Because the tank acts as a flywheel in the system, it would be possible to serve the load by:
Adding water when the level drops to a certain point
Adding water at a rate that matches how quickly it is being used
Notes: Development 2

## Slide 56: A Simple Control System
Monitoring the tank water level will allow us to gauge how much make up we need to add as demand picks up
Notes: Development 2

## Slide 57: A Simple Control System
The tank water level is the Process Variable
Set Point
The desired level becomes the Set Point
Notes: Development 2

## Slide 58: A Simple Control System
Hi Limit
Low Limit
It may be possible to achieve satisfactory control by simply keeping the tank level between two limits
Notes: 4 - Figure out how to make the process variable interact appropriately with the controlled variable

## Slide 59: A Simple Control System
Hi Limit
Low Limit
Notes: 4 - Figure out how to make the process variable interact appropriately with the controlled variable

## Slide 60: A Simple Floating Control System
Cl
Op
Ta Da!
Hi Limit
Low Limit
-
+
Com
Notes: Development 2

## Slide 61: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
The distance between the contacts sets the difference between the limits
Notes: Development 2

## Slide 62: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
The contacts are far enough apart that it is possible for neither one to be connected to the power supply
Notes: Development 2

## Slide 63: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
63
If the water level drops far enough, the float will drop far enough to connect the “open” circuit, driving the valve open
Notes: Development 2

## Slide 64: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
64
If demand is reduced, then, unless the valve moves, the water level will rise, causing the float to rise
Notes: Development 2

## Slide 65: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
65
Initially, this only stops trying to open the valve, so the level continues to rise, and eventually, connects the “close” circuit, causing the valve to start to close
Notes: Development 2

## Slide 66: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
66
If the closing valve reduces the flow more than the demand, the float drops again, breaking the open circuit and the valve stays partially open
Notes: Development 2

## Slide 67: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
67
Key Points:
If the process is between the limits, the valve does nothing and the level is allowed to Float between the limits
Notes: Development 2

## Slide 68: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
68
Key Points:
If the process is between the limits, the valve does nothing and the level is allowed to Float between the limits
Notes: Development 2

## Slide 69: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
69
Key Points:
As long as the ripples are smaller than the difference in level between the limits, they will not have an impact
Notes: Development 2

## Slide 70: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
Key Points:
The valve response speed needs to be slow relative to the rate at which the process can change …
Notes: Development 2

## Slide 71: A Simple Floating Control System
Cl
Op
Hi Limit
Low Limit
-
+
Com
71
Key Points:
… but not so slow that the process can overshoot the limits significantly
I think I see another way to do this!
Notes: Development 2

## Slide 72: A Simple Proportional Control System
Set Point
Cl
Op
-
+
Com
Notes: 4 - Figure out how to make the process variable interact appropriately with the controlled variable

## Slide 73: A Simple Proportional Control System
Ta Da!
Set Point
Notes: Development 2

## Slide 74: A Simple Control Requirement
The make up valve is the device to be controlled; a.k.a. the Controlled Variable or Final Control Element
Notes: Development 2

## Slide 75: A Simple Control Requirement
The tank water level is the Process Variable
Set Point
The desired level becomes the Set Point
Notes: Development 2

## Slide 76: A Simple Proportional Control System
The float is the Sensor
Set Point
The valve handle and linkage is the Actuation System
The lever arms and the pivot point are the controller
Notes: Development 2

## Slide 77: A Simple Proportional Control System
The linkage system makes the water level proportional to the amount the control valve is opened
Set Point
Notes: Development 2

## Slide 78: A Simple Proportional Control System
The ratio of the lever arms on each side of the fulcrum sets the proportional band and gain the of the control system
Set Point
Notes: Development 2

## Slide 79: A Simple Proportional Control System
As long as the demand does not exceed the capacity of the delivery system (i.e. steady state can be achieved inside the proportional band) the system will be under control
Control Point
Set Point
The proportional band is the change in the process variable that causes the controlled variable to go through its full range
Notes: Development 2

## Slide 80: A Simple Proportional Control System
Set Point
By its nature, a proportional control system will always have a difference or “error” between the set point and the control point except at one specific condition
Control Point
Error
Notes: Development 2

## Slide 81: A Simple Proportional Control System
Set Point
We could reduce the error by increasing the gain of the controller (making it more sensitive to a level change in this case) …
Control Point
Notes: Development 2

## Slide 82: A Simple Proportional Control System
Set Point
… but at some point, feedback from the process would interact with the control loop in a way that would make it unstable
Control Point
Notes: Development 2

## Slide 83: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
The Impact of Narrowing the Throttling Range in a Proportional Control Process

## Slide 84: The Impact of Narrowing Throttling Range
Proportional band =400% and set point changed to 80% (black line)
Set point changed to 80%
Significant error between the control point and set point

## Slide 85: The Impact of Narrowing Throttling Range
Proportional band =400% (black line)
Proportional band =300% and set point changed to 80% (red line)
Set point changed to 80%
Error between the control point and set point is reduced

## Slide 86: The Impact of Narrowing Throttling Range
Proportional band =400% (black line)
Proportional band =300% (red line)
Proportional band =200% and set point changed to 80% (blue line)
Set point changed to 80%
Error between the control point and set point is further reduced
Signs of instability and hunting emerge

## Slide 87: The Impact of Narrowing Throttling Range
Proportional band =400% (black line)
Proportional band =300% (red line)
Proportional band =200% (blue line)
Proportional band =150% and set point changed to 80% (gray line)
Set point changed to 80%
The system begins to resonate at it’s natural frequency (hunting begins)

## Slide 88: The Impact of Narrowing Throttling Range
Proportional band =400% (black line)
Proportional band =300% (red line)
Proportional band =200% (blue line)
Proportional band =150% ((gray line)
Proportional band =100% and set point changed to 80% (second black line)
Set point changed to 80%
The system becomes dynamically unstable

## Slide 89: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
Proportional plus Integral plus Derivation (PID) Control Processes

## Slide 90: Bottom Lines On Proportional Control
All proportional control processes will show a difference between set point and control point (a.k.a. error) under all operating conditions other than one very specific condition
The error can be reduced by narrowing down the throttling range
There is a limit to how much you can narrow the throttling range with out hunting
The limit is a function of the physics of the control system; things like lags, play in the linkage system, the nature of the process, etc.

## Slide 91: Then a Miracle Occurs
Image from http://www.sciencecartoonsplus.com/pages/gallery.php
Notes: http://www.sciencecartoonsplus.com/pages/gallery.php

## Slide 92: Proportional plus Integral plus Derivative Control (PID)
PID is the Miracle that can:
  Eliminate error
  Reduce the magnitude of a spike when a system is upset
  Reduce the settling time after an upset

## Slide 93: A Simple Proportional Control System; Adding Integral Control
Set Point
Control Point
If the system has capacity beyond the current operating requirement, and the error had persisted for a while, the operator could adjust the float to eliminate the error at the current load condition
Notes: Development 2

## Slide 94: A Simple Proportional Control System; Adding Integral Control
Set Point
Control Point
If the system has capacity beyond the current operating requirement, and the error had persisted for a while, the operator could adjust the float to eliminate the error at the current load condition
Notes: Development 2

## Slide 95: A Simple Proportional Control System; Adding Integral Control
By monitoring the error over time, the operator could adjust the float setting so that it always maintained the desired set point
Set Point =
Control Point
Notes: Development 2

## Slide 96: A Simple Proportional Control System; Adding Integral Control
This is what the Integral function in a Proportional plus Integral plus Derivative control loop does
Set Point =
Control Point
Notes: Development 2

## Slide 97: A Simple Proportional Control System; Adding Derivative Control
Similarly, the operator could monitor the process and if he or she saw the error start to rapidly change relative to time, they could quickly push the float up or down to minimize the deviation from set point
Set Point =
Control Point
Notes: Development 2

## Slide 98: A Simple Proportional Control System; Adding Derivative Control
Once the sudden change is over the operator could reset the float to match the current load condition and maintain the required set point
Set Point =
Control Point
Notes: Development 2

## Slide 99: A Simple Proportional Control System; Adding Derivative Control
This is what the Derivative function in a Proportional plus Integral plus Derivative control loop does
Set Point =
Control Point
Notes: Development 2

## Slide 100: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
The Impact of Adding Integral and Derivative Gain to a Proportional Control Process

## Slide 101: The Impact of Adding Integral Gain
Set point changed to 80%
Proportional only response; 250% proportional band
Note error between the control point and set point

## Slide 102: The Impact of Adding Integral Gain
Set point changed to 80%
Proportional only response; 250% proportional band
Proportional + Integral response; 250% proportional band, Integral time = 2 minutes
Error eliminated!

## Slide 103: The Impact of Adding Integral Gain
Set point changed to 80%
Proportional only response; 250% proportional band
Proportional + Integral response; 250% proportional band, Integral time = 2 minutes
Proportional + Integral response; 250% proportional band, Integral time = 0.75 minutes
Signs of instability and hunting emerge

## Slide 104: The Impact of Adding Derivative Gain
Set point changed to 80%
Proportional + Integral + Derivative response; 250% proportional band, Integral time = 0.75 minutes, Derivative time = 0.1 minutes
Properly applied, derivative reduces the spike at upset and shortens the settling time

## Slide 105: PID; Its Been Around for a While
Image courtesy Control Engineering Magazine
Notes: Started to show up in the HVAC industry in the late 1970’s
Technology actually developed in the late 1930’s.
Ziegler-Nichols tuning techniques developed in the 1940’s.

## Slide 106: PID Good News and Bad News
Good News
Eliminate offset
  Save energy
  Improve precision
Minimize process swings at start-up
Bad News
Not well understood by the HVAC industry
  More difficult to tune and adjust
  More difficult to maintain
Algorithm used varies with the manufacturer
  Tuning solution specifics are not portable
  Auto-tuning is not a panacea
Difficult to apply correctly
Often misapplied

## Slide 107: PID; The Math Perspective

## Slide 108: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
Integral and Derivative Gain Units of Measure

## Slide 109: Integral Gain; Minutes per Repeat or Repeats per Minute
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
Proportional only response to the upset
P only response
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 110: Integral Gain; Minutes per Repeat or Repeats per Minute
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
P only response
PI response
Integral response to the upset
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 111: Integral Gain; Minutes per Repeat or Repeats per Minute
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
P only response
PI response
Integral gain of 1 repeat per minute will increases the output by an amount equal to the P only response after one minute
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 112: Potential Problems when Adding Integral Action
Loop instability unless a commensurate reduction in proportional gain is made
Tuning and maintenance become more complex, time consuming and difficult
“Wind-up” can occur
  During HVAC system overload conditions.
  During HVAC shut down if not handled appropriately

## Slide 113: Derivative Gain is in Minutes
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
Proportional only response to the upset
P only response
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 114: Derivative Gain is in Minutes
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
P only response
PD response
Derivative response to the upset
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 115: Derivative Gain is in Minutes
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
P only response
PI response
A derivative gain of 1 minute will immediately increases the output by an amount equal to the Integral response after one minute
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 116: Derivative Action Is Difficult to Apply
Provides no benefit if there is not enough
Too much can cause many more problems than it is worth
Typically not necessary for HVAC applications
Use it with CAUTION!

## Slide 117: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
Response to an Upset and PID Tuning Methods

## Slide 118: The Quarter Decay Ratio; Signature of a Well Tuned PID Loop
Increasing Time
Minutes
Increasing Process Variable
1
2
3
Process upset occurs
Set Point
Process Variable
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 119: The Quarter Decay Ratio; Signature of a Well Tuned PID Loop
Increasing Time
Minutes
Increasing Process Variable
1
2
3
Process upset occurs
Set Point
Process Variable
This …
… is about 4 times as big as this
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 120: Closed Loop Tuning Method
With the system under automatic control, determine the Natural Period
  Proportional gain = ¼ to ½ of the ultimate gain producing the Natural Period
  Integral time in minutes per repeat = 1.2 times the Natural Period
  Derivative time in minutes = 1/8 of the Natural Period
Natural Period

## Slide 121: Open Loop Tuning Method
Also useful for troubleshooting
With the system under manual control, insert a step change and observe the response curve. Set the controller as follows:
  Proportional gain = 1/(RL) to 1/(2 RL)
  Integral time in minutes per repeat = 5 times the apparent dead time
  Derivative time in minutes = ½ the apparent dead time.
Point in time when the step change was initiated
Apparent dead time (Lag; L)
Slope of the response curve after a stable rate of change is established (Rate of change; R)
Some processes are self regulating and will level off. Others won’t.

## Slide 122: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
The Impact of Lags

## Slide 123: The Quarter Decay Ratio; Signature of a Well Tuned PID Loop
Increasing Time
Minutes
Increasing Process Variable
1
2
3
Process upset occurs
Set Point
Process Variable
This spike needs to be small enough to not break something
This settling time needs to be reasonable in the context of the load served by the process
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 124: It All Depends on the Lags David W. St. Clair

## Slide 125: Lags and the Response to a Set Point Change
The controller has to react to the change
A volume of air needs to move through the line and fill the actuator
The actuator linkage has to move through any “play” that exists
The valve plug needs to move
Steam needs to flow into the heat exchanger
The thermal mass of the heat exchanger and water needs to change temperature
The warmer water needs to move to the sensor location
The mass of the sensor and well needs to change temperature
Notes: The warmer water needs to move to the sensor location

## Slide 126: Some Observations
Red to Black is the control system response with increasing gains applied to the controller until the natural period is identified

## Slide 127: Some Observations
Apparent dead time (Lag; L)
Natural period PN

## Slide 128: Some Observations
1
2
3
4
The Natural Period is about 4 times the Apparent Dead Time

## Slide 129: Some Observations
The deviation from set point upon an upset with tightly tuned control loop (gray line) is about the same as a totally un-tuned loop (red line) at a point in time equal to about half the natural period

## Slide 130: Some Observations
A tightly tuned control loop (gray line) will take about twice the natural period to re-stabilize after an upset

## Slide 131: Lags; The Bottom Line
Increasing Time
Minutes
Increasing Process Variable
1
2
3
Process upset occurs
Set Point
Process Variable
If this breaks something, or …
… if this is too long, and …
… if this is less than twice the apparent dead time …
… then you won’t be able to solve the problem with loop tuning until you get rid of some lags
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 132: Getting Rid of Lags; Sometimes It’s Easier than Others
Easier
Add positioning relays to valve and damper actuators
Install faster actuators (particularly applicable to electric actuators)
Reduce the thermal lag associated with wells by not using them
Use tighter linkages to minimize hysteresis
Use ramps instead of acceleration and deceleration times in VFDs
Harder
Reducing transportation times
Reducing the thermal lags associated with the size of the machinery (mass of coils, fans, duct, pipe, etc.)

## Slide 133: A Bit More About Ramps
Acceleration and Deceleration times
Apply all of the time, any time there is a change in the process
  An acceleration setting of, for example, 1hz/second will always apply regardless of if the difference between set point and control point was because of a start-up or step change in set point vs. minor variations in the control point relative to set point
  This introduces a permanent lag into the control process with the associated implications for tuning the process
Ramps
Only apply when the set point is outside some window relative to the control point
  Ramps will only apply if the difference between the set point and control point is large (outside of some predefined window)
  If the set point and control point are inside the window, then the lag associated with the ramp drops out of the picture
  As a result, the response to a minor variation in set point is much faster than the response to a step change (start up or set point change

## Slide 134: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
Rules for Tuning Control Loops (and Performing Functional Tests)

## Slide 135: General Rules for Tuning Control Loops
The Natural Period will be about 4 times the apparent dead time
Periodic disturbances can significantly impact a loop’s ability to control
  Disturbance faster than the Natural Period – Control will not help
  Disturbance at or near the Natural Period – Resonance
For optimum performance, be just on the stable side of the ultimate gain point
The ultimate gain of the system will change as the characteristics of the system change
  Seasonal effects
  Aging and wear
Notes: The natural period and apparent dead time of a control loop are important and related. As a general rule, the natural period will be about 4 times the apparent dead time.
If the control loop is subject to a periodic disturbance then the frequency of the disturbance might have a very significant impact on the loops ability to control.
  Disturbance faster – Control will not help
  Disturbance at or near the natural period – Resonance
In general, for optimum performance, you want to be just on the stable side of the ultimate gain point.
The ultimate gain of the system will change as the characteristics of the system change.

## Slide 136: General Rules for Tuning Control Loops
Be a little conservative
  HVAC systems see many variations in operating conditions
  First year is critical
Have an idea of what you expect to happen
  What you hope happens
  What you fear could happen
Know and agree about how far you will let things go
  How will you shut down the test in an emergency?
  Who will do what?
  Rehearse failure for critical systems
Notes: Given the variable performance criteria seen by HVAC systems, you may want to be a little conservative in your tuning parameter settings, especially during the first year of operation.
Before tuning, you should have an idea of what you expect to happen and what your desired outcome is as well as what the given system can be expected to do.
You, and everyone else involved with the tuning process should know and agree about how far you will let things go before you abort the test and shut down or otherwise take over control of the system.

## Slide 137: General Rules for Tuning Control Loops
Test and set all safety systems first
  Protect equipment
  Protect people
Schedule your testing
  Protect the load served from unnecessary disturbance
  Protect the load served from a crisis
Be available later
Document everything
Proceed slowly
Notes: You should have tested all safety systems and interlocks and they should be set at the appropriate levels required to protect systems, people and equipment.
You should schedule your testing at a time when the system and the loads it serves can tolerate some disturbance and a shutdown down of the system would not create a crisis.
Plan on being readily available for some time after you make your adjustments in case problems show up.
Document everything.
Proceed slowly.

## Slide 138: Related Considerations
Non-linearity can influence ease of tuning.
  Input side
    Thermistors
    Differential pressure based flow sensors.
  Output side
    Linkage arrangements
    Velocity limiting
Loop interactions
  Very common in HVAC
Hysteresis and dead band effects
Auto tuning
  Not a panacea
  Not all algorithms will work the same

## Slide 139: Just because you CAN do PID doesn’t mean you SHOULD do PID
Use proportional only control in situations where high precision is not required or warranted by operational or economic concerns
  Space temperature control
  Limit functions
  Cascaded or highly interactive loops
Add integral action in situations where precision is required
Add integral action in situations where the proportional offset associated with a proportional only loop will result in significant energy waste
Think hard before adding derivative action to a control loop

## Slide 140: Control Systems: Design, Performance and Commissioning Issues
David Sellers
Senior Engineer
Facility Dynamics Engineering
Control Processes
PID and Loop Tuning Resources

## Slide 141: Tuning Resources
Controller Tuning and Control Loop Performance by David W. St. Clair
  Judy St. Clair Straight Line Control, LLC 6326 4th Avenue South Richfield, MN 55423 USA Phone:612-869-6814 Fax: 612-869-2761 jastclair@pro-ns.net http://www.straightlinecontrol.com
Notes: To order a copy of "Reference Guide to PID Tuning" visit www.controleng.com/info and request number 367 from the August 1998 North American issue of Control Engineering.
Judy St. Clair Straight Line Control, LLC 6326 4th Avenue South Richfield, MN 55423 USA Phone:612-869-6814 Fax: 612-869-2761 jastclair@pro-ns.net http://www.straightlinecontrol.com

## Slide 142: Tuning Resources
Reference Guide to PID Tuning
  Available from the publishers of Control Engineering
  See A Field Perspective on Engineering Blog Post for Links
Notes: To order a copy of "Reference Guide to PID Tuning" visit www.controleng.com/info and request number 367 from the August 1998 North American issue of Control Engineering.
Judy St. Clair Straight Line Control, LLC 6326 4th Avenue South Richfield, MN 55423 USA Phone:612-869-6814 Fax: 612-869-2761 jastclair@pro-ns.net http://www.straightlinecontrol.com

## Slide 143: Tuning Resources
See An Overview of Proportional plus Integral plus Derivative Control and Suggestions for Its Successful Application and Implementation from the proceedings of the 2001 International Conference on Enhanced Building Operations