## Design Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2016-12-01 15:52
Project Name: | Eikon Logic Diagram Exercise HHW System
Project Number:
Engineer: | David
Assumptions
Basic Data and Assumptions
This spreadsheet develops some basic load metrics for the HHW system in the Eikon logic diagram exercise so they can become "clues" for answering some questions that will come up when you are developing the logic
| Assumed heating load - | 32.5 | Btu/hr/sqft |  | Source - | Average of the range for an average building from HVAC Equations, Data, and Rules of Thumb
| Building size - | 20000 | sq.ft.
| Number of floors - | 2 | both above grade, both the same size
| Building length - | 200 | ft. (North-South)
| Building width - | 50 | ft. (East-West)
| Perimeter zone depth - | 12 | ft.
| Perimeter area - | 12000 | sq.ft. (total for both floors)
| Core area - | 8000
| Heating system - | Finned tube radiation with a warm-up coil in the AHU
| Cooling and Ventilation System - | VAV reheat AHU with economizer, warm-up coil, and DX cooling
First floor mechanical room for the AHU, heat exchanger and pumps
Air cooled condenser located on grade next to the parking lot
Steam from a district steam system reduced to 5 psi at the building service entrance in the mechanical room
1979 rennovation replaced the original constant volume reheat AHU with a VAV reheat system
2015 rennovation upgraded the controls to DDC
Trends show:
HHW system locks out above 65°F
HHW system controls for a constant 170°F supply temperature
AHU runs 24/7 to maintain conditions in the server room
Economizer is non-integrated
Occupant interviews indicate:
People are more comfortable during extreme conditions than during milder conditions and swing seasons
Confernce spaces and core areas are really cold in the summer
Tendency to over-heat and see temperature swings in milder weather until cooling system comes on line
FTR zone thermostat locations set the conditions for other areas and sometimes not everyone is comortable, even if the person with the zone stat is
| Building use - | Office
| Square feet per person - | 115 | sq,ft, per person |  | Source - | Average of the range for an office building from HVAC Equations, Data, and Rules of Thumb
| Number of people - | 173.913 | people
| People in the periemter area - | 104.3478 | peope
| People in the core area - | 69.5652 | people
| Ventilation rate - | 15 | cfm/person
| Minimum outdoor air requirement - | 2608.6957 | cfm total
|  | 1565.2174 | cfm for the perimeter zones
|  | 1043.4783 | cfm for the core zones
| Building location - | St. Louis, MO
| Building HVAC Zones |  |  | Square Feet (from floor plan) | Number of Occupants | Minimum OA Flow, cfm | Minimum Flow, cfm | Maximum flow, cfm | Reheat gpm | Titus Terminal Unit Size. Inches
| 1st Floor FTR - | North perimeter
East perimeter
South perimeter
|  | West perimeter | [9 empty] | Notes
| 1st Floor VAV Reheat - | North East perimeter |  | 825 | 3 | 45 | 384.7854 | 1046.3555 | 3.4204 | 12 |  | 1. Occupants based on room function.
|  | North West perimeter |  | 825 | 3 | 45 | 384.7854 | 1046.3555 | 3.4204 | 12 |  |  | Design occupant count - | 173.913 | people
|  | East perimeter |  | 825 | 3 | 45 | 384.7854 | 1046.3555 | 3.4204 | 12 |  | 2. Minimum flow proated on occupant basis
|  | South East perimeter |  | 775 | 3 | 45 | 384.7854 | 982.94 | 3.2131 | 12 |  |  | Design MOA - | 2608.6957 | cfm
|  | South West perimeter |  | 975 | 4 | 60 | 513.0471 | 1236.602 | 4.0423 | 12 |  |  | MOA % - | 11.69%
|  | West perimeter |  | 750 | 2 | 30 | 256.5236 | 951.2323 | 3.1095 | 12 |  |  | Conference room cfm/occ. - | 15
|  | Conference Room |  | 287.5 | 25 | 375 | 3206.5446 | 364.639 | 1.192 | 12 |  |  | 1st Fl. Conf Rm. Occ. - | 20
| 1st Floor VAV Cooling Only - | East core |  | 1675 | 19.0341 | 285.5114 | 2441.3465 | 2124.4188 | 6.9444 | 14 |  |  | 2nd Fl. Conf Rm. Occ. - | 30
|  | West core |  | 1650 | 18.75 | 281.25 | 2404.9085 | 2092.711 | 6.8408 | 14 |  | 3. Maximum flow prorated a conditioned square foot basis.
| 2nd Floor FTR - | North perimeter | [10 empty] | Total square feet - | 17587.5 | sq.ft.
|  | East perimeter | [10 empty] | Conditioned square feet - | 20000 | sq.ft.
|  | South perimeter | [10 empty] | Design flow rate - | 22306.3973 | cfm
|  | West perimeter | [9 empty] | 4. Reheat gpm prorated on a conditioned square foot basis.
| 2nd Floor VAV Reheat - | North East perimeter |  | 1025 | 3 | 45 | 384.7854 | 1300.0175 | 4.2496 | 12 |  |  | Total reheat flow rate - | 72.9167 | gpm
|  | North West perimeter |  | 900 | 3 | 45 | 384.7854 | 1141.4788 | 3.7313 | 12 |  | 5. Open office cubicle size -
|  | East perimeter |  | 1125 | 2 | 30 | 256.5236 | 1426.8484 | 4.6642 | 12 |  |  | Length - | 8 | ft.
|  | South East perimeter |  | 1175 | 5 | 75 | 641.3089 | 1490.2639 | 4.8715 | 12 |  |  | Width - | 8 | ft.
|  | South West perimeter |  | 1050 | 10.3829 | 155.743 | 1331.7252 | 1331.7252 | 4.3532 | 12 |  |  | Walkway per cubicle - | 24 | sq.ft.
|  | West perimeter |  | 750 | 8.5227 | 127.8409 | 1093.1402 | 951.2323 | 3.1095 | 12
|  | Conference Room |  | 600 | 35 | 525 | 4489.1625 | 760.9858 | 2.4876 | 16
|  | East core |  | 1275 | 14.4886 | 217.3295 | 1858.3384 | 1617.0949 | 5.2861 | 12
|  | West core |  | 1100 | 12.5 | 187.5 | 1603.2723 | 1395.1407 | 4.5605 | 12
| Unconditioned - | Mechanical Room |  | 750 | 0 | 0 |  | 0 | 0
|  | Entry |  | 62.5 | 0 | 0 |  | 0 | 0
|  | 1st Floor RR |  | 400 | 0 | 0 |  | 0 | 0
|  | Stairs (2nd Fl) |  | 300 | 0 | 0 |  | 0 | 0
|  | 1st Fl. Elev. |  | 200 | 0 | 0 |  | 0 | 0
|  | 2nd Fl. Elev. |  | 100 | 0 | 0 |  | 0 | 0
|  | 2nd Floor RR |  | 600 | 0 | 0 |  | 0 | 0
|  | Check |  | 20000 | 174.6783 | 2620.1748 |  | 22306.3973 | 72.9167 |  | 0
Cooling Load Estimate
| Assumed cooling load - Room Sensible - | 26.5 | Btu/hr/sqft |  | Source - | Average of the range for an office building from HVAC Equations, Data, and Rules of Thumb
|  | 530000 | Btu/hr for the building
|  | 44.1667 | Tons for the building
| SHR - | 0.85 |  |  | Source - | Past experience
| Assumed cooling load - Room Latent - | 3.975 | Btu/hr/sqft |  | Source - | Assumed SHR and room sensible load
|  | 79500 | Btu/hr for the building
|  | 6.625 | Tons for the building
| Assumed cooling load - Room Total - | 30.475 | Btu/hr/sqft
|  | 609500 | Btu/hr for the building
|  | 50.7917 | Tons for the building
| Space condition - | 75 | °F
|  | 50% | RH
|  | 28.15 | Btu/lb
| Design cooling coil LAT - | 53 | °F |  | Source - | Psych chart to the right
| AHU design flow rate - | 22306.3973 | cfm, Sensible heat equation using space temperature cooling coil LAT and total space load
|  | 1.1153 | cfm per square foot
| Asummed turndown ratio - | 33.33% | Estmiate based on past experience
| Minimum flow rate at mimimum load - | 7435.4658 | cfm
| 2% outdoor cooling design conditions - | 90.7 | °Ftdb
|  | 75 | °Ftwb
|  | 36.4 | Btu/lb
| Ventilation total load - | 96847.8261 | Btu/hr for the building
|  | 8.0707 | Tons for the building
|  | 4.8424 | Btu/hr/sqft
| Total cooling load - | 706347.8261 | Btu/hr
|  | 58.8623 | Tons
Preheat Requirement Assessment
| 99% outdoor heating design condition | 10.2 | °F
|  | 50% | RH
| Return duct temperature drop, design heating day - | 3 | °F
| Outdoor temperature where preheat would be required - | -33.9554 | °F; from conservation of mass and energy; see the Mixed Air Temp Calcs tab; Preheat not required
Warm-up Requirement Assessment
| Warm-up leaving air temperature - | 85 | °F |  | Source - | Assumption
| Building set back temperature - | 65 | °F |  | Source - | Assumption based on past experience
| Warm-up entering air temperature (no OA) - | 62 | °F
| Warm-up load - | 554090.9091 | Btu/hr from the sensible load equation
Total Peak Heating Load
| Ventilation load - | 182566.9565 | Btu/hr, from the sensible load equation and design conditions and MOA flow
|  | 9.1283 | Btu/hr/sqft
| Space load - | 23.3717 | Btu/hr, from assumptions about total heating load and ventilation load
|  | 467433.0435 | Btu/hr
| Building perimeter per floor - | 500 | ft.
| Total perimeter, heated area - | 1000
| Roof load - | 70114.9565 | Btu/hr | 15% | = percent of space load assumed to be roof load
| Total perimeter heating load - | 397318.087 | Btu/hr
| Perimeter heating load per floor - | 198659.0435
| First floor perimeter heating load - | 198659.0435
| Second floor heating load (with roof load ) - | 268774
| Total spoce heating load - | 467433.0435 | Btu/hr (should match number above)
| Btu/foot of heated space, first floor - | 397.3181 | Btu/ft | Size the first floor FTR for this load
| Btu/foot of heated space, second floor - | 537.548 | Bti/ft | Size the second floor FTR for this load
| Percent of perimeter with an active FTR element - | 50%
| Btu/foot of heated space, 50% of the perimeter is FTR element, first floor - | 794.6362 | Btu/ft | Size the first floor FTR for this load
| Btu/foot of heated space, 50% of the perimeter is FTR element, second floor - | 1075.096 | Bti/ft | Size the seconf floor FTR for this load
Reheat Load Requirement Assessment
Assume on a design heating day the core is still at design cooling load with full people count
| Core total flow rate - | 8922.5589 | cfm
| Core MOA flow rate - | 1043.4783 | cfm
| Core % MOA - | 11.69%
| Assume on a design heating day, the perimeter only needs the MOA flow as neutral air |  |  |  | Iteration | Perimeter flow | MOA Percent | Total Flow
| Perimeter MOA flow rate - | 1565.2174 | cfm |  | 1 | 6292.6658 | 24.87% | 10487.7763
| Perimeter % MOA - | 100% |  |  | 2 | 9129.1348 | 17.15% | 15215.2247
| Total system flow rate - | 10487.7763 | cfm |  | 3 | 10831.0162 | 14.45% | 18051.6937
| Total system MOA flow rate - | 2608.6957 | cfm |  | 4 | 11852.1451 | 13.21% | 19753.5752
| % MOA - | 24.87% |  |  | 5 | 12464.8224 | 12.56% | 20774.704
| Perimeter minimum flow rate with 25% outdoor air - | 6292.6658 | cfm
Second Iteration
| Total minimum flow rate with 25% outdoor air - | 15215.2247 | cfm
| Total system MOA flow rate - | 2608.6957 | cfm
| % MOA - | 17.15%
| Perimeter minimum flow rate with 17% outdoor air - | 9129.1348 | cfm
Third Iteration
| Total minimum flow rate with 17% outdoor air - | 18051.6937 | cfm
| Total system MOA flow rate - | 2608.6957 | cfm
| % MOA - | 14.45%
| Perimeter minimum flow rate with 14% outdoor air - | 10831.0162 | cfm
Fourth Iteration
| Total minimum flow rate with 14% outdoor air - | 19753.5752 | cfm
| Total system MOA flow rate - | 2608.6957 | cfm
| % MOA - | 13.21%
| Perimeter minimum flow rate with 13% outdoor air - | 11852.1451 | cfm
Fifth Iteration
| Total minimum flow rate with 13% outdoor air - | 20774.704 | cfm
| Total system MOA flow rate - | 2608.6957 | cfm
| % MOA - | 12.56%
| Perimeter minimum flow rate with 13% outdoor air - | 12464.8224 | cfm; Assume this is the perimeter minimum flow rate on the design heating day
MOA % on design and extreme days
| MOA % on a design day required to deliver design supply temperature - | 30.74%
| MOA % on an extreme day required to deliver design supply temperature - | 23.26%
| Assume the lowest MOA% that will be seen is - | 23.26%
Basis of Design
| Assumed perimeter minimum flow rate on a design day - | 6730.4348 | cfm
| Perimeter minimum flow entering air temperature - | 53 | °F
| Perimeter minimum flow leaving air temperature (neutral air) - | 75 | °F
| Reheat load - | 159915.1304 | Btu/hr (from the sensible heat equation)
| Typical flow rate (based on a long side perimeter zone) - | 2355.5556 | cfm
| Nominal size - | 4.7111 | sq.ft. at 500 fpm
| Entering water temperature - Design day - | 170 | °F
| Typical leaving water temperature - Design day - |  | °F (from coil model)
| System flow rate - | 15652.9937 | cfm
| MOA - | 3640.2311 | cfm
| Mixed air temperature - | 53 | °F
| Temperature where preheat would be required - | -9.7 | °F
Total Heating Load
Load components
| Space heating load - | 467433.0435 | Btu/hr
| Warm-up load - | 554090.9091 | Btu/hr (non-concurrent with the space load and reheat load)
| Reheat load - | 159915.1304 | Btu/hr
| Space heating plus peak reheat load - | 627348.1739 | Btu/hr
| Space heating plus warm-up load - | 1021523.9526 | Btu/hr | Size the heating system for this load
Heating Load Summary (see First Floor FTR and Second Floor FTR tabs for details on the finned tube radiation)
|  | Load, Btu/hr | Btu/hr/ft | Feet of Active Element | Supply Temp., °F | Circuits | gpm per circuit | Total gpm | ∆t, °F | Return Temp, °F
| First Floor - | 198659.0435 | 816.2 | 243.3951 | 170 | 4 | 7.2 | 28.8 | 13.7958 | 156.2042
| Second Floor - | 268774 | 996.4 | 269.7451 | 170 | 4 | 7.2 | 28.8 | 18.6649 | 151.3351
| Warm-up Coil - | 554090.9091 | N/A | N/A | 170 | N/A | N/A | 29.8 | 37.1873 | 132.8127
| Total Building - | 1021523.9526 |  | 513.1401 | 170 | 8 |  | 87.4 | 23.3758 | 146.6242

## Mixed Air Temp Calcs
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2012-04-24 13:41
Project Name: | None
Project Number: | None
Engineer: | David Sellers
Assumptions
1 | Enter appropriate data in the yellow cells in consistent units of measure …
… and read the results in the blue cells.
Note that the Supply Air Flow is the flow out of the mixed air plenum.
2 | These equations are derived from the steady flow energy equation, conservation of mass, the assumption that
for an HVAC system, air can be treated as an ideal gas, and the assumption that for an HVAC system, the constant
| pressure specific heat of air can be assumed to be constant . See this blog post for more info. |  |  |  | Av8rDAS.Wordpress.Com - Economizers - The Physics of a Mixed Air Plenum
3 | Supply air temperature and mixed air temperature are used interchangably; the supply air temperature is the temperature leaving the mixing process.
4 | Any calculation involving mixed air/supply air temperature assumes complete mixing of the two air streams feeding into the process.
Steady Flow Energy Equation
On a Rate Basis, Given the Assumptions Listed in 2 Above, the Steady Flow Energy Equation can be Reduced to this Relationship
Outdoor percentage based on outdoor air, return air, and supply air temperature - Reheat Analysis - Exterme Day
|  | Mixed air temperature (MAT) = | 53 | °F
|  | Return air temperature (RAT) = | 72 | °F
|  | Outdoor air temperature (OAT)= | -9.7 | °F
|  | Supply flow (SAF) = | 10487.7763 | cfm
|  | Outdoor air flow (OA Flow) = | 2439.0177 | cfm
|  | Outdoor air percentage = | 23.26%
|  | RA Flow = | 8048.7586 | cfm
Outdoor percentage based on outdoor air, return air, and supply air temperature - Reheat Analysis - Design Day
|  | Mixed air temperature (MAT) = | 53 | °F
|  | Return air temperature (RAT) = | 72 | °F
|  | Outdoor air temperature (OAT)= | 10.2 | °F
|  | Supply flow (SAF) = | 10487.7763 | cfm
|  | Outdoor air flow (OA Flow) = | 3224.3972 | cfm
|  | Outdoor air percentage = | 30.74%
|  | RA Flow = | 7263.3791 | cfm
Outdoor air temperature that results in a 32°F mixed air temperature
This is simply a special case with the mixed air temperature set to 32°F
|  | Mixed air temperature (MAT) = | 32 | °F
|  | Return air temperature (RAT) = | 72 | °F
|  | Supply flow (SAF) = | 22306.3973 | cfm
|  | Outdoor air flow (OA Flow) = | 2608.6957 | cfm
|  | Outdoor air percentage = | 11.69%
|  | RA Flow = | 19697.7017 | cfm
|  | Outdoor air temperature (OAT)= | -270.0314 | °F
Outdoor air temperature that results in a specific mixed air temperature of interest - Preheat Analyisis
This is simply a more general case of the preceeding equation
|  | Design mixed air temperature (MAT) = | 53 | °F
|  | Return air temperature (RAT) = | 72 | °F
|  | Supply flow (SAF) = | 22306.3973 | cfm
|  | Outdoor air flow (OA Flow) = | 4000 | cfm
|  | Outdoor air percentage = | 17.93%
|  | RA Flow = | 18306.3973 | cfm
|  | Outdoor air temperature (OAT)= | -33.9554 | °F
Outdoor air temperature that results in a specific mixed air temperature of interest - Reheat Analysis
This is simply a more general case of the preceeding equation
|  | Design mixed air temperature (MAT) = | 53 | °F
|  | Return air temperature (RAT) = | 72 | °F
|  | Supply flow (SAF) = | 15652.9937 | cfm
|  | Outdoor air flow (OA Flow) = | 3640.2311 | cfm
|  | Outdoor air percentage = | 23.26%
|  | RA Flow = | 12012.7626 | cfm
|  | Outdoor air temperature (OAT)= | -9.7 | °F
Mixed air temperature created by a known outdoor air percentage, a known outdoor air temperature, and a known return air temperature - Reheat Analysis
|  | Return air temperature (RAT) = | 72 | °F
|  | Outdoor air temperature (OAT)= | -9.7 | °F
|  | Supply flow (SAF) = | 15652.9937 | cfm
|  | Outdoor air flow (OA Flow) = | 3640.2311 | cfm
|  | Outdoor air percentage = | 23.26%
|  | RA Flow = | 12012.7626 | cfm
|  | Mixed air temperature (MAT) = | 53 | °F

## First Floor FTR
|  |  | Load - | 198659.0435 | Btu/hr
|  |  | Target Btu/ft - | 794.6362 | Btu/hr/ft
|  |  | Design average water temperature - | 160 | °F
|  |  | Actual capacity with 160 °F average water temperature - | 816.2 | Btu/hr/ft
|  |  | Feet of active element required - | 243.3951 | ft
Everything Standard
Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft. | Straight Line
1540 | 90 | 0.11 | 1 | 1 | 1 | 169.4 | 90 | 19.4
1540 | 100 | 0.15 | 1 | 1 | 1 | 231 | 240 | 1775
1540 | 110 | 0.2 | 1 | 1 | 1 | 308 | Offset | 150 | Selection and Circuiting Options
1540 | 120 | 0.26 | 1 | 1 | 1 | 400.4 |  |  | Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height
1540 | 130 | 0.33 | 1 | 1 | 1 | 508.2 |  |  |  | gpm at 3 ft/sec velocity - | 7.2 | gpm
1540 | 140 | 0.4 | 1 | 1 | 1 | 616 |  |  |  | target ∆t, °F - | 10 | °F
1540 | 150 | 0.45 | 1 | 1 | 1 | 693 |  |  |  | gpm to handle the load at a 10 °F ∆t - | 39.7318 | gpm
1540 | 160 | 0.53 | 1 | 1 | 1 | 816.2 |  |  |  | Number of circuits required to hold 3 ft/sec - | 5.5183
1540 | 170 | 0.61 | 1 | 1 | 1 | 939.4 |  |  |  | Target circuit count - | 6
1540 | 180 | 0.69 | 1 | 1 | 1 | 1062.6 |  |  |  | ∆t with 6 circuits - | 9.1972 | °F
1540 | 190 | 0.78 | 1 | 1 | 1 | 1201.2 |  |  |  | Design supply temperature - | 164.5986 | °F
1540 | 200 | 0.86 | 1 | 1 | 1 | 1324.4 |  |  |  | Design return temperature - | 155.4014 | °F
1540 | 210 | 0.95 | 1 | 1 | 1 | 1463 |  |  | Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height
1540 | 215 | 1 | 1 | 1 | 1 | 1540 |  |  |  | gpm at 3 ft/sec velocity - | 7.2 | gpm
1540 | 220 | 1.05 | 1 | 1 | 1 | 1617 |  |  |  | target ∆t, °F - | 20 | °F
1540 | 230 | 1.14 | 1 | 1 | 1 | 1755.6 |  |  |  | gpm to handle the load at a 20 °F ∆t - | 19.8659 | gpm
1540 | 240 | 1.25 | 1 | 1 | 1 | 1925 |  |  |  | Number of circuits required to hold 3 ft/sec - | 2.7592
Warmer Entering Air | [9 empty] | Target circuit count - | 4
Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 70°F entering air | [9 empty] | ∆t with 4 circuits - | 13.7958 | °F
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft. |  |  |  | Design supply temperature - | 166.8979 | °F
1540 | 90 | 0.11 | 0.54545 | 1 | 1 | 92.4 |  |  |  | Design return temperature - | 153.1021 | °F
1540 | 100 | 0.15 | 0.73333 | 1 | 1 | 169.4
1540 | 110 | 0.2 | 0.8 | 1 | 1 | 246.4
1540 | 120 | 0.26 | 0.80769 | 1 | 1 | 323.4
1540 | 130 | 0.33 | 0.84848 | 1 | 1 | 431.2
1540 | 140 | 0.4 | 0.85 | 1 | 1 | 523.6
1540 | 150 | 0.45 | 0.91111 | 1 | 1 | 631.4
1540 | 160 | 0.53 | 0.92453 | 1 | 1 | 754.6
1540 | 170 | 0.61 | 0.93443 | 1 | 1 | 877.8
1540 | 180 | 0.69 | 0.94203 | 1 | 1 | 1001
1540 | 190 | 0.78 | 0.9359 | 1 | 1 | 1124.2
1540 | 200 | 0.86 | 0.95349 | 1 | 1 | 1262.8
1540 | 210 | 0.95 | 0.95789 | 1 | 1 | 1401.4
1540 | 215 | 1 | 0.95 | 1 | 1 | 1463
1540 | 220 | 1.05 | 0.95238 | 1 | 1 | 1540
1540 | 230 | 1.14 | 0.95614 | 1 | 1 | 1678.6
1540 | 240 | 1.25 | 0.952 | 1 | 1 | 1832.6
Colder Entering Air
Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 55°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1540 | 90 | 0.11 | 1.1818 | 1 | 1 | 200.2
1540 | 100 | 0.15 | 1.2667 | 1 | 1 | 292.6
1540 | 110 | 0.2 | 1.25 | 1 | 1 | 385
1540 | 120 | 0.26 | 1.1923 | 1 | 1 | 477.4
1540 | 130 | 0.33 | 1.1515 | 1 | 1 | 585.2
1540 | 140 | 0.4 | 1.125 | 1 | 1 | 693
1540 | 150 | 0.45 | 1.1778 | 1 | 1 | 816.2
1540 | 160 | 0.53 | 1.1509 | 1 | 1 | 939.4
1540 | 170 | 0.61 | 1.1311 | 1 | 1 | 1062.6
1540 | 180 | 0.69 | 1.1159 | 1 | 1 | 1185.8
1540 | 190 | 0.78 | 1.1026 | 1 | 1 | 1324.4
1540 | 200 | 0.86 | 1.1047 | 1 | 1 | 1463
1540 | 210 | 0.95 | 1.1053 | 1 | 1 | 1617
1540 | 215 | 1 | 1.09 | 1 | 1 | 1678.6
1540 | 220 | 1.05 | 1.0857 | 1 | 1 | 1755.6
1540 | 230 | 1.14 | 1.0877 | 1 | 1 | 1909.6
1540 | 240 | 1.25 | 1.072 | 1 | 1 | 2063.6
50% Flow Reduction
Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1540 | 90 | 0.11 | 1 | 0.973 | 1 | 164.8262
1540 | 100 | 0.15 | 1 | 0.973 | 1 | 224.763
1540 | 110 | 0.2 | 1 | 0.973 | 1 | 299.684
1540 | 120 | 0.26 | 1 | 0.973 | 1 | 389.5892
1540 | 130 | 0.33 | 1 | 0.973 | 1 | 494.4786
1540 | 140 | 0.4 | 1 | 0.973 | 1 | 599.368
1540 | 150 | 0.45 | 1 | 0.973 | 1 | 674.289
1540 | 160 | 0.53 | 1 | 0.973 | 1 | 794.1626
1540 | 170 | 0.61 | 1 | 0.973 | 1 | 914.0362
1540 | 180 | 0.69 | 1 | 0.973 | 1 | 1033.9098
1540 | 190 | 0.78 | 1 | 0.973 | 1 | 1168.7676
1540 | 200 | 0.86 | 1 | 0.973 | 1 | 1288.6412
1540 | 210 | 0.95 | 1 | 0.973 | 1 | 1423.499
1540 | 215 | 1 | 1 | 0.973 | 1 | 1498.42
1540 | 220 | 1.05 | 1 | 0.973 | 1 | 1573.341
1540 | 230 | 1.14 | 1 | 0.973 | 1 | 1708.1988
1540 | 240 | 1.25 | 1 | 0.973 | 1 | 1873.025
50% Flow Reduction
Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1540 | 90 | 0.11 | 1 | 0.973 | 1 | 164.8262
1540 | 100 | 0.15 | 1 | 0.973 | 1 | 224.763
1540 | 110 | 0.2 | 1 | 0.973 | 1 | 299.684
1540 | 120 | 0.26 | 1 | 0.973 | 1 | 389.5892
1540 | 130 | 0.33 | 1 | 0.973 | 1 | 494.4786
1540 | 140 | 0.4 | 1 | 0.973 | 1 | 599.368
1540 | 150 | 0.45 | 1 | 0.973 | 1 | 674.289
1540 | 160 | 0.53 | 1 | 0.973 | 1 | 794.1626
1540 | 170 | 0.61 | 1 | 0.973 | 1 | 914.0362
1540 | 180 | 0.69 | 1 | 0.973 | 1 | 1033.9098
1540 | 190 | 0.78 | 1 | 0.973 | 1 | 1168.7676
1540 | 200 | 0.86 | 1 | 0.973 | 1 | 1288.6412
1540 | 210 | 0.95 | 1 | 0.973 | 1 | 1423.499
1540 | 215 | 1 | 1 | 0.973 | 1 | 1498.42
1540 | 220 | 1.05 | 1 | 0.973 | 1 | 1573.341
1540 | 230 | 1.14 | 1 | 0.973 | 1 | 1708.1988
1540 | 240 | 1.25 | 1 | 0.973 | 1 | 1873.025

## Second Floor FTR
|  |  | Load - | 268774 | Btu/hr
|  |  | Target Btu/ft - | 1075.096 | Btu/hr/ft
|  |  | Design average water temperature - | 160 | Btu/hr/ft
|  |  | Actual capacity with 160 °F average water temperature - | 996.4 | Btu/hr/ft
|  |  | Feet of active element required - | 269.7451 | ft
Everything Standard
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft. | Straight Line
1880 | 90 | 0.11 | 1 | 1 | 1 | 206.8 | 90 | 56.8
1880 | 100 | 0.15 | 1 | 1 | 1 | 282 | 240 | 2200
1880 | 110 | 0.2 | 1 | 1 | 1 | 376 | Offset | 150 | Selection and Circuiting Options
1880 | 120 | 0.26 | 1 | 1 | 1 | 488.8 |  |  | Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height
1880 | 130 | 0.33 | 1 | 1 | 1 | 620.4 |  |  |  | gpm at 3 ft/sec velocity - | 7.2 | gpm
1880 | 140 | 0.4 | 1 | 1 | 1 | 752 |  |  |  | target ∆t, °F - | 10 | °F
1880 | 150 | 0.45 | 1 | 1 | 1 | 846 |  |  |  | gpm to handle the load at a 10 °F ∆t - | 53.7548 | gpm
1880 | 160 | 0.53 | 1 | 1 | 1 | 996.4 |  |  |  | Number of circuits required to hold 3 ft/sec - | 7.4659
1880 | 170 | 0.61 | 1 | 1 | 1 | 1146.8 |  |  |  | Target circuit count - | 8
1880 | 180 | 0.69 | 1 | 1 | 1 | 1297.2 |  |  |  | ∆t with 8 circuits - | 9.3324 | °F
1880 | 190 | 0.78 | 1 | 1 | 1 | 1466.4 |  |  |  | Design supply temperature - | 164.6662 | °F
1880 | 200 | 0.86 | 1 | 1 | 1 | 1616.8 |  |  |  | Design return temperature - | 155.3338 | °F
1880 | 210 | 0.95 | 1 | 1 | 1 | 1786 |  |  | Vulcan LV4-S, VC433, 1" line size, 4-1/4" x 3-5/8" fins, 32 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height
1880 | 215 | 1 | 1 | 1 | 1 | 1880 |  |  |  | gpm at 3 ft/sec velocity - | 7.2 | gpm
1880 | 220 | 1.05 | 1 | 1 | 1 | 1974 |  |  |  | target ∆t, °F - | 20 | °F
1880 | 230 | 1.14 | 1 | 1 | 1 | 2143.2 |  |  |  | gpm to handle the load at a 20 °F ∆t - | 26.8774 | gpm
1880 | 240 | 1.25 | 1 | 1 | 1 | 2350 |  |  |  | Number of circuits required to hold 3 ft/sec - | 3.733
Warmer Entering Air | [9 empty] | Target circuit count - | 4
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 70°F entering air | [9 empty] | ∆t with 4 circuits - | 18.6649 | °F
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft. |  |  |  | Design supply temperature - | 169.3324 | °F
1540 | 90 | 0.11 | 0.54545 | 1 | 1 | 92.4 |  |  |  | Design return temperature - | 150.6676 | °F
1540 | 100 | 0.15 | 0.73333 | 1 | 1 | 169.4 |  |  | Pressure drop analysis
1540 | 110 | 0.2 | 0.8 | 1 | 1 | 246.4 |  |  |  | gpm - | 7.2 | °F
1540 | 120 | 0.26 | 0.80769 | 1 | 1 | 323.4 |  |  |  | Maximum circuit length - | 200 | ft
1540 | 130 | 0.33 | 0.84848 | 1 | 1 | 431.2 |  |  |  | Friction rate - | 3.75 | ft.w.c/100 ft. of pipe
1540 | 140 | 0.4 | 0.85 | 1 | 1 | 523.6 |  |  |  | Pipe and FTR element pressure drop - | 7.5 | ft.w.c
1540 | 150 | 0.45 | 0.91111 | 1 | 1 | 631.4 |  |  |  | Fitting pressure drop - | 7.5 | ft.w.c.
1540 | 160 | 0.53 | 0.92453 | 1 | 1 | 754.6 |  |  |  | Control valve pressure drop - | 7.5 | ft.w.c.
1540 | 170 | 0.61 | 0.93443 | 1 | 1 | 877.8 |  |  |  | Total circuit pressure drop - | 22.5 | ft.w.c.
1540 | 180 | 0.69 | 0.94203 | 1 | 1 | 1001
1540 | 190 | 0.78 | 0.9359 | 1 | 1 | 1124.2
1540 | 200 | 0.86 | 0.95349 | 1 | 1 | 1262.8
1540 | 210 | 0.95 | 0.95789 | 1 | 1 | 1401.4
1540 | 215 | 1 | 0.95 | 1 | 1 | 1463
1540 | 220 | 1.05 | 0.95238 | 1 | 1 | 1540
1540 | 230 | 1.14 | 0.95614 | 1 | 1 | 1678.6
1540 | 240 | 1.25 | 0.952 | 1 | 1 | 1832.6
Colder Entering Air
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 55°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1880 | 90 | 0.11 | 1.1818 | 1 | 1 | 244.4
1880 | 100 | 0.15 | 1.2667 | 1 | 1 | 357.2
1880 | 110 | 0.2 | 1.25 | 1 | 1 | 470
1880 | 120 | 0.26 | 1.1923 | 1 | 1 | 582.8
1880 | 130 | 0.33 | 1.1515 | 1 | 1 | 714.4
1880 | 140 | 0.4 | 1.125 | 1 | 1 | 846
1880 | 150 | 0.45 | 1.1778 | 1 | 1 | 996.4
1880 | 160 | 0.53 | 1.1509 | 1 | 1 | 1146.8
1880 | 170 | 0.61 | 1.1311 | 1 | 1 | 1297.2
1880 | 180 | 0.69 | 1.1159 | 1 | 1 | 1447.6
1880 | 190 | 0.78 | 1.1026 | 1 | 1 | 1616.8
1880 | 200 | 0.86 | 1.1047 | 1 | 1 | 1786
1880 | 210 | 0.95 | 1.1053 | 1 | 1 | 1974
1880 | 215 | 1 | 1.09 | 1 | 1 | 2049.2
1880 | 220 | 1.05 | 1.0857 | 1 | 1 | 2143.2
1880 | 230 | 1.14 | 1.0877 | 1 | 1 | 2331.2
1880 | 240 | 1.25 | 1.072 | 1 | 1 | 2519.2
50% Flow Reduction
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1880 | 90 | 0.11 | 1 | 0.973 | 1 | 201.2164
1880 | 100 | 0.15 | 1 | 0.973 | 1 | 274.386
1880 | 110 | 0.2 | 1 | 0.973 | 1 | 365.848
1880 | 120 | 0.26 | 1 | 0.973 | 1 | 475.6024
1880 | 130 | 0.33 | 1 | 0.973 | 1 | 603.6492
1880 | 140 | 0.4 | 1 | 0.973 | 1 | 731.696
1880 | 150 | 0.45 | 1 | 0.973 | 1 | 823.158
1880 | 160 | 0.53 | 1 | 0.973 | 1 | 969.4972
1880 | 170 | 0.61 | 1 | 0.973 | 1 | 1115.8364
1880 | 180 | 0.69 | 1 | 0.973 | 1 | 1262.1756
1880 | 190 | 0.78 | 1 | 0.973 | 1 | 1426.8072
1880 | 200 | 0.86 | 1 | 0.973 | 1 | 1573.1464
1880 | 210 | 0.95 | 1 | 0.973 | 1 | 1737.778
1880 | 215 | 1 | 1 | 0.973 | 1 | 1829.24
1880 | 220 | 1.05 | 1 | 0.973 | 1 | 1920.702
1880 | 230 | 1.14 | 1 | 0.973 | 1 | 2085.3336
1880 | 240 | 1.25 | 1 | 0.973 | 1 | 2286.55
50% Flow Reduction
Vulcan LV4-S, VC44, 1" line size, 4-1/4" x 4-1/4" fins, 40 fins per foot, 0.20 thick fins, 14" enclosure, single teir, 18" mounting height, 65°F entering air
Catalog Rating, Btu/hr./ft. | Average Water Temperature. °F | Water Temperature Correction | Entering Air Temperature Correction | Flow Correction | Mounting Height Correction | Corrected Rating, Btu/hr./ft.
1880 | 90 | 0.11 | 1 | 0.973 | 1 | 201.2164
1880 | 100 | 0.15 | 1 | 0.973 | 1 | 274.386
1880 | 110 | 0.2 | 1 | 0.973 | 1 | 365.848
1880 | 120 | 0.26 | 1 | 0.973 | 1 | 475.6024
1880 | 130 | 0.33 | 1 | 0.973 | 1 | 603.6492
1880 | 140 | 0.4 | 1 | 0.973 | 1 | 731.696
1880 | 150 | 0.45 | 1 | 0.973 | 1 | 823.158
1880 | 160 | 0.53 | 1 | 0.973 | 1 | 969.4972
1880 | 170 | 0.61 | 1 | 0.973 | 1 | 1115.8364
1880 | 180 | 0.69 | 1 | 0.973 | 1 | 1262.1756
1880 | 190 | 0.78 | 1 | 0.973 | 1 | 1426.8072
1880 | 200 | 0.86 | 1 | 0.973 | 1 | 1573.1464
1880 | 210 | 0.95 | 1 | 0.973 | 1 | 1737.778
1880 | 215 | 1 | 1 | 0.973 | 1 | 1829.24
1880 | 220 | 1.05 | 1 | 0.973 | 1 | 1920.702
1880 | 230 | 1.14 | 1 | 0.973 | 1 | 2085.3336
1880 | 240 | 1.25 | 1 | 0.973 | 1 | 2286.55

## Warm-up Coil
Flow rate - | 22306.3973 | cfm during warm-up
Maximum face velocity - | 500 | fpm
Minimum coils face area - | 44.6128 | sq.ft.
Coil height - | 6 | ft | 72 | in
Minimum coil width - | 7.4355 | ft | 89.2256 | in
Coil width - | 8 | ft | 96 | in
Entering Air Temperature - | 62 | °F
Target leaving Air Temperature - | 85 | °F
Target Capacity - | 554090.9091 | Btu/hr
Target Water Flow Rate - | 27.7045 | gpm
Entering Water Temperature - | 170 | °F
Target Leaving Water Temperature - | 130 | °F
Actual Capacity - | 586200 | Btu/hr
Actual Flow rate - | 29.8 | gpm
Actual Leaving Water Temperature - | 130 | °F
Actual Leaving Air Temperature - | 86.3 | °F

## Typical Reheat Coil
Based on a long perimeter zone
Design heating day
| Flow rate - | 2355.5556 | cfm
| Entering air temperature - | 53 | °F
| Leaving air temperature - | 82 | °F
| Nominal face velocity - | 500 | fpm at maximum flow
| Nominal zone squarefootage - | 2112 | sq.ft.
| Nominal sq.ft. per person - | 115 | sq.ft. per person
| Nominal number of people in the zone - | 18.3652 | people
| Nominal ventilation rate - | 15 | cfm per person
| MOA % - | 23.26%
| Ventilation requirement - | 275.4783 | cfm
| Minimum flow - | 1184.5565 | cfm
| Height - | 18 | inches
| Width - | 37.6889 | inches
| Entering water temperature - | 170 | °F
| gpm from selection program - | 7.7 | gpm
| gpm per square foot - | 0.0036458 | gpm/sq.ft
| Floor area - | 10000 | sq.ft.
| Nominal gpm per floor - | 36.4583 | gpm
Design day, Maximum flow |  |  |  | Summer day, reheat only, 90°F EWT, Maximum flow |  |  | Summer day, reheat only, 110°F EWT, Maximum flow | Summer day, reheat only, 130°F EWT Maximum flow | Summer day, reheat only, 150°F EWT Maximum flow
Design day, Minimum flow |  |  |  | Summer day, reheat only, 90°F EWT, Minimum flow |  |  | Summer day, reheat only, 110°F EWT, Minimum flow | Summer day, reheat only, 130°F EWT Minimum flow | Summer day, reheat only, 150°F EWT Minimum flow
|  |  |  | EWT,°F | LAT,°F at Maximum Flow | LAT,°F at Minimum Flow
|  |  |  | 90 | 62.1 | 65.4
|  |  |  | 110 | 67.2 | 72.3
|  |  |  | 130 | 72.4 | 79.2
|  |  |  | 150 | 77.5 | 86.1
|  |  |  | 170 | 82.7 | 93

## Pumps
Distribution Mains
Design flow rate - | 87.4 | gpm
Pump Head Estimate
Typical FTR Circuit - | 22.5 | ft.w.c.
Distribution mains to and from FTR Circuits - | 9.3 | ft.w.c. | 500 | ft. | 1.86 | ft.w.c./100 ft. | 3" lines the length of the building and back plus the width of the building and back
Fittings - | 4.65 | ft.w.c.
Heat Exchanger - | 5 | ft.w.c.
Safety factor - | 4.145 | ft.w.c.
Total - | 45.595 | ft.w.c.
Selection
Bell and Gossett 2AD-es
Flow - | 87.4
Head - | 45.595
Speed - | 1750
Bhp - | 1.33
Efficiency - | 75.85%
Motor hp - | 2
Boiler Pumps - Non-condensing Boilers
Boiler - | 1.5 | ft.w.c
Pipe - | 0.7325 | ft.w.c. | 25 | ft. | 2.93 | ft.w.c./100 ft.
Fittings - | 0.7325 | ft.w.c.
Safety Factor - | 0.2965 | ft.w.c.
Total - | 3.2615 | ft.w.c.
Boiler Pumps - Condensing Boilers
Boiler - | 6.5 | ft.w.c
Pipe - | 0.7325 | ft.w.c. | 25 | ft. | 2.93 | ft.w.c./100 ft.
Fittings - | 0.7325 | ft.w.c.
Safety Factor - | 0.7965 | ft.w.c.
Total - | 8.7615 | ft.w.c.

## Heat Exchanger
Water Side
pounds per hour - | 42788
pounds per minute - | 713.1333
pounds per cubic foot - | 62.4
gallons per cubic foot - | 7.48
gallons per minute - | 85.4846

## Non-condensing Boiler
Total load - | 1021523.9526 | Btu/hr
Per boiler - | 510761.9763 | Btu/hr
Total gpm - | 87.4 | gpm
Gpm per boiler - | 43.7 | gpm
Laars model - | 715
Input rating - | 715000 | Btu/hr
Output rating - | 586000 | Btu/hr
Efficiency - | 81.96%
Flow rate - | 43.7 | gpm
Pressure drop - | 1.5224 | ft.w.c.
Leaving water temperature - | 170 | °F
Entering water temperature - | 143.1808 | °F
Temperature rise - | 26.8192 | °F (23°F required at design conditions)
Burner motor - | 0.33 | hp
Phase - | 1
Voltage - | 120 | vac

## Condensing Boiler
Total load - | 1021523.9526 | Btu/hr
Per boiler - | 510761.9763 | Btu/hr
Total gpm - | 87.4 | gpm
Gpm per boiler - | 43.7 | gpm
Aerco Multiflex model number - | MLX EXT 600
Input rating - | 642000 | Btu/hr
Output rating - | 609000 | Btu/hr
Efficiency - | 94.86% | (Varies with firing rate and return water temperature)
Flow rate - | 43.7 | gpm
Pressure drop - | 6.4585 | ft.w.c.
Leaving water temperature - | 170 | °F (Design OAT; reset; minimum is 90°F for summer time operation)
Entering water temperature - | 142.1281 | °F
Temperature rise - | 27.8719 | °F (23°F required at design conditions)
Turn-down - | 14:1
Amperage - | 3.6 | FLA
Phase - | 1
Voltage - | 120 | vac

## General Arrangement
= approximately 5 feet by 5 feet
|  |  | Slab to slab height - | 12 | feet finshed floor to finished floor
|  |  | Slab thickness - | 6 | inches
200 feet
| 50 feet | Assistant Division Chief |  |  |  | Deputy Assistant Planner |  |  | Deputy Assistant Planning |  |  | Assistant Deputy Planner |  | Mechancial/Electrical |  |  |  | Tel/Com | Stairs Up |  |  | Mount Engineering |  |  | Signage Shop |  |  |  |  | Geometric Shape Development | Chief Political Correctness Officer
[18 empty] | Elv. Mach. | Elev.
|  | Office Admin. |  |  | Open Office Cubicles - Division of Departmental Planning and Compartmentalization | [7 empty] | Copy Room | [10 empty] | Open Office - Signage Planning and Development
[18 empty] | Lobby and Reception | [12 empty] | Office of Non-offensive References
Division Chief
[20 empty] | Men's Room |  | Lady's Room
[5 empty] | Resource Manager | [7 empty] | Office of Bureacratic Mischief |  | Conference Room | [8 empty] | Font Management Officer |  |  | Font Development Officer |  | Director of Fonts and Other Things that Matter
Kitchenette/Break Area
Covered Entry
First Floor
North
200 feet
| 50 feet | Assistant Chief Bureaucrat |  |  |  | Executive Assistant to the Assistant Chief Bureaucrat |  |  |  | Associate Assistant to the Executive Assistant … |  |  | Director of Minions |  | Chief Minion | Minion |  |  | Stairs Down |  |  | Storage |  |  | Open Office Cubicals | [5 empty] | Director of Bureacratic Nightmares
Elev.
[11 empty] | Open Office Cubicals - Department of Upper Echelons | [19 empty] | Director of Bureacratic Nightmare Resolution
|  | Chief Bureaucrat |  |  |  |  | Executive Assistant to the Chief Bureaucrat
[16 empty] | Main Conference Room |  |  |  | Men's Room |  |  | Lady's Room |  |  | Office of Essential Planning and Development |  | Conflict Resultion Officer |  | Office of Non-essential Planning and Development
[11 empty] | Kitchenette/Break Area |  |  |  | Copy Room
Second Floor
+

## FTR Zones
= approximately 5 feet by 5 feet
|  |  | Slab to slab height - | 12 | feet finshed floor to finished floor
|  |  | Slab thickness - | 6 | inches
200 feet
| 50 feet | Assistant Division Chief |  |  |  | Deputy Assistant Planner |  |  | Deputy Assistant Planning |  |  | Assistant Deputy Planner |  | Mechancial/Electrical |  |  |  | Tel/Com | Stairs Up |  |  | Mount Engineering |  |  | Signage Shop |  |  |  |  | Geometric Shape Development | Chief Political Correctness Officer
[18 empty] | Elv. Mach. | Elev.
|  | Office Admin. |  |  | Open Office Cubicles - Division of Departmental Planning and Compartmentalization | [7 empty] | Copy Room | [10 empty] | Open Office - Signage Planning and Development
[18 empty] | Lobby and Reception | [12 empty] | Office of Non-offensive References
Division Chief
[20 empty] | Men's Room |  | Lady's Room
[5 empty] | Resource Manager | [7 empty] | Office of Bureacratic Mischief |  | Conference Room | [8 empty] | Font Management Officer |  |  | Font Development Officer |  | Director of Fonts and Other Things that Matter
Kitchenette/Break Area
Covered Entry
|  | First Floor |  |  |  |  | Thermostat Location
First Floor - North FTR Zone
|  | North |  |  |  |  | First Floor - East FTR Zone
First Floor - South FTR Zone
First Floor - West FTR Zone
200 feet
| 50 feet | Assistant Chief Bureaucrat |  |  |  | Executive Assistant to the Assistant Chief Bureaucrat |  |  |  | Associate Assistant to the Executive Assistant … |  |  | Director of Minions |  | Chief Minion | Minion |  |  | Stairs Down |  |  | Storage |  |  | Open Office Cubicals - Department of Middle Management | [5 empty] | Director of Bureacratic Nightmares
Elev.
[11 empty] | Open Office Cubicals - Department of Upper Echelons | [19 empty] | Director of Bureacratic Nightmare Resolution
|  | Chief Bureaucrat |  |  |  |  | Executive Assistant to the Chief Bureaucrat
[16 empty] | Main Conference Room |  |  |  | Men's Room |  |  | Lady's Room |  |  | Office of Essential Planning and Development |  | Conflict Resultion Officer |  | Office of Non-essential Planning and Development
Copy Room
Kitchenette/Break Area
|  | Second Floor |  |  |  |  | Thermostat Location
Second Floor - North FTR Zone
Second Floor - East FTR Zone
Second Floor - South FTR Zone
[7 empty] | Second Floor - West FTR Zone | [13 empty] | +
T
T
T
T
T
T
T
T
T
T

## FTR and VAV Zones
= approximately 5 feet by 5 feet
|  |  | Slab to slab height - | 12 | feet finshed floor to finished floor
|  |  | Slab thickness - | 6 | inches
200 feet
| 50 feet | Assistant Division Chief |  |  |  | Deputy Assistant Planner |  |  | Deputy Assistant Planning |  |  | Assistant Deputy Planner |  | Mechancial/Electrical |  |  |  |  | Tel/Com | Stairs Up |  |  | Mount Engineering |  |  | Signage Shop | [5 empty] | Geometric Shape Development | Chief Political Correctness Officer
[19 empty] | Elv. Mach. | Elev.
|  | Office Admin. |  |  | Open Office Cubicles - Division of Departmental Planning and Compartmentalization | [7 empty] | Copy Room | [11 empty] | Open Office - Signage Planning and Development
[19 empty] | Lobby and Reception | [13 empty] | Office of Non-offensive References
Division Chief
[21 empty] | Men's Room |  | Lady's Room
[5 empty] | Resource Manager | [7 empty] | Office of Bureacratic Mischief |  | Conference Room | [9 empty] | Font Management Officer |  |  | Font Development Officer |  | Director of Fonts and Other Things that Matter
Kitchenette/Break Area
Covered Entry
|  | First Floor |  |  |  |  | Thermostat Location
[7 empty] | First Floor - North FTR Zone | [7 empty] | First Floor North East | [6 empty] | First Floor North West | [7 empty] | Served by transfer air
|  | North |  |  |  |  | First Floor - East FTR Zone | [7 empty] | First Floor East | [6 empty] | First Floor West | [7 empty] | Conference Room
[7 empty] | First Floor - South FTR Zone | [7 empty] | First Floor South East | [6 empty] | First Floor South West
[7 empty] | First Floor - West FTR Zone | [7 empty] | First Floor East Core | [6 empty] | First Floor Core West
200 feet
| 50 feet | Assistant Chief Bureaucrat |  |  |  | Executive Assistant to the Assistant Chief Bureaucrat |  |  |  | Associate Assistant to the Executive Assistant … |  |  | Director of Minions |  | Chief Minion |  | Minion |  |  | Stairs Down |  |  | Storage |  |  | Open Office Cubicals - Department of Middle Management | [6 empty] | Director of Bureacratic Nightmares
Elev.
[11 empty] | Open Office Cubicals - Department of Upper Echelons | [21 empty] | Director of Bureacratic Nightmare Resolution
|  | Chief Bureaucrat |  |  |  |  | Executive Assistant to the Chief Bureaucrat
[17 empty] | Main Conference Room |  |  |  | Men's Room |  |  | Lady's Room |  |  | Office of Essential Planning and Development |  | Conflict Resultion Officer |  |  | Office of Non-essential Planning and Development
Copy Room
Kitchenette/Break Area
|  | Second Floor |  |  |  |  | Thermostat Location
[7 empty] | Second Floor - North FTR Zone | [8 empty] | Second Floor North East | [6 empty] | Second Floor North West | [7 empty] | Served by transfer air
[7 empty] | Second Floor - East FTR Zone | [8 empty] | Second Floor East | [6 empty] | Second Floor West | [7 empty] | Conference Room
[7 empty] | Second Floor - South FTR Zone | [8 empty] | Second Floor South East | [6 empty] | Second Floor South West
[7 empty] | Second Floor - West FTR Zone | [8 empty] | Second Floor East Core | [6 empty] | Second Floor Core West
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T
T

## Pipe Insulation Losses
Data generated using 3EPlus
| Line size - | 3 | inches
| Ambient Temperature - | 75 | °F
Insulation thickness | 70°F Water |  | 90°F Water |  | 110°F Water |  | 130°F Water |  | 150°F Water |  | 170°F Water |  | 190°F Water |  | 210°F Water |  | 280°F Steam |  | 350°F Steam
| Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft | Surface Temperature, °F | Heat Loss, Btu/hr/ft
0 | 70 | 5.97 | 90 | 20.78 | 110 | 55.34 | 129.9 | 94.75 | 149.9 | 138.2 | 169.9 | 185.3 | 189.9 | 235.9 | 209.8 | 289.9 | 279.7 | 506.6 | 349.5 | 768.8
0.5 | 73.7 | 1.89 | 78.7 | 5.89 | 83.2 | 14.28 | 87.6 | 23.18 | 92 | 32.56 | 96.5 | 42.45 | 101 | 52.88 | 105.6 | 63.87 | 122.4 | 107.2 | 140.9 | 159.1
1 | 74.3 | 1.17 | 76.9 | 3.62 | 79.3 | 8.69 | 81.7 | 14.01 | 84.1 | 19.61 | 86.5 | 25.49 | 88.9 | 31.66 | 91.4 | 38.16 | 100.7 | 63.65 | 110.9 | 94.07
1.5 | 74.6 | 0.89 | 76.3 | 2.74 | 77.9 | 6.56 | 79.5 | 10.57 | 81 | 14.77 | 82.7 | 19.17 | 84.3 | 23.8 | 86 | 28.66 | 92.3 | 47.7 | 99.3 | 70.38
2 | 74.7 | 0.75 | 76 | 2.29 | 77.1 | 5.48 | 78.3 | 8.82 | 79.5 | 12.31 | 80.8 | 15.98 | 82 | 19.82 | 83.3 | 23.86 | 88 | 39.67 | 93.4 | 58.49
2.5 | 74.7 | 0.65 | 75.7 | 2 | 76.7 | 4.79 | 77.6 | 7.7 | 78.6 | 10.74 | 79.6 | 13.93 | 80.5 | 17.28 | 81.6 | 20.8 | 85.4 | 34.56 | 89.6 | 50.94
3 | 74.8 | 0.59 | 75.6 | 1.8 | 76.4 | 4.3 | 77.2 | 6.91 | 77.9 | 9.64 | 78.7 | 12.51 | 79.6 | 15.51 | 80.4 | 18.67 | 83.6 | 31.01 | 87.1 | 45.68
3.5 | 74.8 | 0.53 | 75.5 | 1.63 | 76.1 | 3.9 | 76.8 | 6.26 | 77.4 | 8.74 | 78.1 | 11.33 | 78.8 | 14.05 | 79.5 | 16.91 | 82.1 | 28.07 | 85.1 | 41.35
4 | 74.9 | 0.5 | 75.4 | 1.52 | 76 | 3.63 | 76.5 | 5.82 | 77.1 | 8.13 | 77.7 | 10.54 | 78.3 | 13.07 | 78.9 | 15.72 | 81.2 | 26.1 | 83.7 | 38.43
4.5 | 74.9 | 0.47 | 75.4 | 1.43 | 75.9 | 3.41 | 76.4 | 5.47 | 76.8 | 7.63 | 77.3 | 9.9 | 77.9 | 12.27 | 78.4 | 14.76 | 80.4 | 24.51 | 82.7 | 36.09
5 | 74.9 | 0.44 | 75.3 | 1.34 | 75.7 | 3.19 | 76.2 | 5.12 | 76.6 | 7.14 | 77 | 9.26 | 77.5 | 11.47 | 77.9 | 13.8 | 79.7 | 22.91 | 81.7 | 33.73
5.5 | 74.9 | 0.42 | 75.3 | 1.28 | 75.7 | 3.04 | 76 | 4.88 | 76.4 | 6.81 | 76.8 | 8.83 | 77.2 | 10.95 | 77.6 | 13.17 | 79.2 | 21.86 | 81 | 32.18
6 | 74.9 | 0.4 | 75.3 | 1.22 | 75.6 | 2.92 | 75.9 | 4.68 | 76.3 | 6.53 | 76.7 | 8.47 | 77 | 10.5 | 77.4 | 12.63 | 78.8 | 20.95 | 80.5 | 30.85
6.5 | 74.9 | 0.38 | 75.2 | 1.18 | 75.6 | 2.81 | 75.9 | 4.51 | 76.2 | 6.29 | 76.5 | 8.15 | 76.8 | 10.11 | 77.2 | 12.16 | 78.5 | 20.17 | 80 | 29.69
7 | 74.9 | 0.37 | 75.2 | 1.14 | 75.5 | 2.71 | 75.8 | 4.36 | 76.1 | 6.08 | 76.4 | 7.88 | 76.7 | 9.76 | 77 | 11.74 | 78.2 | 19.49 | 79.6 | 28.68
7.5 | 74.9 | 0.36 | 75.2 | 1.1 | 75.5 | 2.63 | 75.7 | 4.22 | 76 | 5.89 | 76.3 | 7.63 | 76.6 | 9.46 | 76.9 | 11.38 | 78 | 18.88 | 79.3 | 27.79
8 | 74.9 | 0.35 | 75.2 | 1.07 | 75.4 | 2.55 | 75.7 | 4.1 | 75.9 | 5.72 | 76.2 | 7.41 | 76.5 | 9.19 | 76.7 | 11.05 | 77.8 | 18.33 | 79 | 26.99
8.5 | 74.9 | 0.34 | 75.2 | 1.04 | 75.4 | 2.49 | 75.6 | 3.99 | 75.9 | 5.57 | 76.1 | 7.21 | 76.4 | 8.94 | 76.6 | 10.76 | 77.6 | 17.85 | 78.7 | 26.27
9 | 74.9 | 0.33 | 75.2 | 1.02 | 75.4 | 2.42 | 75.6 | 3.89 | 75.8 | 5.43 | 76 | 7.04 | 76.3 | 8.72 | 76.5 | 10.49 | 77.4 | 17.4 | 78.5 | 25.61
9.5 | 74.9 | 0.32 | 75.2 | 0.99 | 75.4 | 2.37 | 75.6 | 3.8 | 75.8 | 5.3 | 76 | 6.87 | 76.2 | 8.52 | 76.4 | 10.25 | 77.3 | 17 | 78.3 | 25.02
10 | 75 | 0.32 | 75.1 | 0.97 | 75.3 | 2.32 | 75.5 | 3.72 | 75.7 | 5.19 | 75.9 | 6.72 | 76.1 | 8.34 | 76.3 | 10.02 | 77.1 | 16.63 | 78.1 | 24.48