## Butterfly with Check
1400 SW 5th Ave, Suite 700, Portland, Oregon 97201 (503) 248-4636 FAX: (503) 295-0820 E-Mail: peci@peci.org Web Site: www.peci.org
Engineering Calculation
| Date: | 2006-09-06 16:33 |  |  | Revised - | 2019-03-22 16:47
| Project Name: | ????
| Project Number: | ????
| Engineer: | ????
Assumptions
| 1 |  |  |  |  | Inflation rate for revised pricing for 2006 data - | 1.19 | Source - | http://www.bls.gov/data/inflation_calculator.htm
| 2 |  |  |  |  | RS Means wage adjustments for San Francisco - | 1.75 | Mechanial
| 3 | ???? |  |  |  |  | 1.59 | Electrical
| 4 | ???? |  |  |  |  | 1.26 | General
| 5 | ????
| 6 | ????
| 7 | ????
| 8 | ????
Cost Projection for Adding a Redundant Pump - Butterfly with Wafer Check Approach
No. | Description | Quant. | Units | Material |  | Outside Contractor Labor
|  |  |  | Unit Cost, $ | Total Cost, $ | Rate, $ per hour | Unit Hours | Total Hours | Total Cost, $
| Pump | 1 | ea | 10600 | 10600 | 96.25 | 48 | 48 | 4620
| 8" suction Diffusser | 1 | ea | 2112.25 | 2112.25 | 96.25 | 9.6 | 9.6 | 924
| 8" butterfly valve | 3 | ea | 380.8 | 1142.4 | 96.25 | 5.333 | 15.999 | 1539.9037
| Butterfly valve operator | 3 | ea | With valve |  | With valve |  | 0 | 0
| 8" Wafer Check | 2 | ea | 1130.5 | 2261 | 96.25 | 5.333 | 10.666 | 1026.6025
| 8" flex connector | 2 | ea | 368.9 | 737.8 | 96.25 | 2 | 4 | 385
| 8" pipe flanges | 18 | ea | 110.075 | 1981.35 | 96.25 | 3.429 | 61.722 | 5940.7425
| 8" elbow | 4 | ea | 210.63 | 842.52 | 96.25 | 3.429 | 13.716 | 1320.165
| 8" tee | 3 | ea | 809.2 | 2427.6 | 96.25 | 3.429 | 10.287 | 990.1237
| Flange gaskets and bolt sets | 18 | ea | 19.278 | 347.004 | 96.25 | 1.6 | 28.8 | 2772
| 8" pipe | 14 | ft | 68.5 | 959 | 96.25 | 0.828 | 11.592 | 1115.73
| 10" butterfly valve | 1 | ea | 476 | 476 | 96.25 | 5.333 | 5.333 | 513.3012
| Butterfly valve operator | 1 | ea | With valve |  | With valve |  | 0 | 0
| 10" x 8" reducing tee | 1 | ea | 850 | 850 | 96.25 | 12 | 12 | 1155
| 10" pipe | 3 | ft | 89.5 | 268.5 | 96.25 | 1 | 3 | 288.75
| 10" pipe flange | 2 | ea | 283 | 566 | 96.25 | 6 | 12 | 1155
| 10" flange cap | 1 | ea | 283 | 283 | 96.25 | 6 | 6 | 577.5
| Flange gaskets and bolt sets | 2 | ea | 0 | 0 | 96.25 | 1.6 | 3.2 | 308
| Gauge valves (1/4" ball valves) | 2 | ea | 12.257 | 24.514 | 96.25 | 0.333 | 0.666 | 64.1025
| Vent and drain (3/4" ball valves) | 2 | ea | 20.1705 | 40.341 | 96.25 | 0.4 | 0.8 | 77
| Pressure gauge | 2 | ea | 198.73 | 397.46 | 96.25 | 0.25 | 0.5 | 48.125
| 8" Pipe insulation | 14 | ft | 3.85 | 53.9 | 85.2775 | 0.16 | 2.24 | 191.0216
| Pump/suction diffusser insulation | 20 | sq.ft | 4.24 | 84.8 | 85.2775 | 0.168 | 3.36 | 286.5324
| Fitting insulation - flanges | 18 | ea | 15.4 | 277.2 | 85.2775 | 0.64 | 11.52 | 982.3968
| Fitting insulation - special fittings | 8 | ea | 15.4 | 123.2 | 85.2775 | 0.64 | 5.12 | 436.6208
| Fitting insulation - 8" elbow | 3 | ea | 11.55 | 34.65 | 85.2775 | 0.48 | 1.44 | 122.7996
| Fitting insulation - 10" tee | 1 | ea | 15.45 | 15.45 | 85.2775 | 0.6 | 0.6 | 51.1665
| 10" Pipe insulation | 2 | ft | 4.09 | 8.18 | 85.2775 | 0.178 | 0.356 | 30.3588
| Pipe hanger | 3 | ea | 100 | 300 | 96.25 | 4 | 12 | 1155
| Drain, Fill and Vent System | 1 | lot | 0 | 0 | 96.25 | 4 | 4 | 385
| 1" conduit | 50 | ft | 3.66 | 183 | 86.655 | 0.123 | 6.15 | 532.9283
| #8 gauge wire | 200 | ft | 0.48195 | 96.39 | 86.655 | 0.01 | 2 | 173.31
| Pull box | 2 | ea | 30.94 | 61.88 | 86.655 | 1.445 | 2.89 | 250.433
| Conduit hanger | 5 | ea | 100 | 500 | 86.655 | 4 | 20 | 1733.1
| Starter (15 hp Combination, Fused) | 1 | ea | 1143 | 1143 | 86.655 | 8 | 8 | 693.24
| Panel board switch | 1 | ea | 1309 | 1309 | 86.655 | 2 | 2 | 173.31
| Pad | 1 | ea | 150 | 150 | 47.6437 | 4 | 4 | 190.575
| Painting | 1 | lot | 100 | 100 | 47.6437 | 8 | 8 | 381.15
| Labeling | 1 | lot | 100 | 100 | 47.6437 | 1 | 1 | 47.6437
| Grouting | 1 | ea | 75 | 75 | 47.6437 | 4 | 4 | 190.575
| Alignment | 1 | ea | 25 | 25 | 96.25 | 2 | 2 | 192.5
| Start stop point | 1 | ea | 1000 | 1000 | With material |  | 0 | 0
| Proof of operation point | 1 | ea | 1000 | 1000 | With material |  | 0 | 0
| Control Program Modification | 1 | ea | 0 | 0 | 150 | 24 | 24 | 3600
| Impeller trim | 1 | ea | 150 | 150 | 96.25 | 8 | 8 | 770
| Seals | 1 | ea | 100 | 100 | With trim |  | 0 | 0
| Verification checks and start-up | 1 | lot | 0 | 0 | 165 | 2 | 2 | 330
| Commissioning | 1 | lot | 0 | 0 | 165 | 4 | 4 | 660
[5 empty] | 0 |  |  | 0 | 0
TOTALS |  |  |  |  | 33207.389 |  |  | 396.557 | 38380.7077
TOTAL - All Cost Components |  |  |  |  | 71588.0967
TAX |  | 5% |  |  | 1660.3695
TOTAL DIRECT COST |  |  |  |  | 73248.4661
CONTINGENCIES
| Design | 0% |  |  | 0
| Construction | 3% |  |  | 2197.454
CONTRACTOR'S MARK-UPS
| Overhead | 10% |  |  | 7544.592
| Profit | 5% |  |  | 4149.5256
Net Mark-up with contingencies |  | 121.7%
GRAND TOTAL |  |  |  |  | 87140.0377
Notes
1