## 1510 6G 1150rpm
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2015-03-29
Project Name: | Impeller Diameter Affinity Law Example
Project Number: | None
Engineer: | David
Notice: We have provided this spreadsheet for educational purposes. We are fine with you using it as a starting point for your own spreadsheet performing a similar analysis or even using it as is. But you are using it at your own risk and neither FDE nor I can not be responsible for the results you generate with it and the decisions you make as a result. Please check your work and use your head.
Assumptions

## Impeller 6G 1150
10 Inch |  | 10.5 Inch |  | 11 Inch |  | 11.5 Inch |  | 12 Inch |  | 12.5 Inch |  | 13 Inch |  | 13.5 Inch
File 10 Inch.csv |  | File 10.5 Inch.csv |  | File 11 Inch.csv |  | File 11.5 Inch.csv |  | File 12 Inch.csv |  | File 12.5 Inch.csv |  | File 13 Inch.csv |  | File 13.5 Inch.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
0 | 41.2281 | 0 | 46.5887 | 0 | 51.7544 | 0 | 57.5049 | 0 | 63.9376 | 0 | 70.078 | 0 | 76.8031 | 0 | 83.5283
102.422 | 41.3255 | 102.422 | 46.5887 | 101.038 | 51.7544 | 99.654 | 57.5049 | 101.038 | 63.8402 | 102.422 | 70.1 | 101.038 | 76.7057 | 101.038 | 83.6257
202.076 | 41.423 | 200.692 | 46.4912 | 202.076 | 51.462 | 200.692 | 57.4074 | 202.076 | 63.6452 | 202.076 | 69.9805 | 203.46 | 76.6082 | 202.076 | 83.5283
300.346 | 41.2281 | 301.73 | 46.1988 | 303.114 | 51.1696 | 300.346 | 57.2125 | 303.114 | 63.5478 | 301.73 | 69.7856 | 301.73 | 76.5107 | 301.73 | 83.4308
402.768 | 40.85 | 402.768 | 45.7115 | 402.768 | 50.7797 | 397.232 | 56.9201 | 400 | 63.2554 | 400 | 69.4932 | 402.768 | 76.4133 | 401.384 | 83.2359
502.422 | 40.4 | 517.647 | 45.2 | 517.647 | 50.3899 | 501.038 | 56.4327 | 502.422 | 62.8655 | 501.038 | 69.1 | 501.038 | 76.0234 | 502.422 | 82.846
600.692 | 39.5 | 610.381 | 44.5 | 613.149 | 49.9025 | 600.692 | 56.0429 | 602.076 | 62.3782 | 599.308 | 68.6 | 602.076 | 75.5 | 602.076 | 82.4561
701.73 | 38.5965 | 703.114 | 43.7622 | 705.882 | 49.3177 | 701.73 | 55.5556 | 700.346 | 61.8908 | 698.962 | 68.1287 | 701.73 | 74.9513 | 703.114 | 82.0663
801.384 | 37.037 | 802.768 | 42.4951 | 798.616 | 48.538 | 800 | 54.6784 | 777.855 | 61.2 | 798.616 | 67.5439 | 798.616 | 74.269 | 801.384 | 81.6764
899.654 | 34.9903 | 898.27 | 40.8382 | 901.038 | 47.271 | 898.27 | 53.7037 | 822.145 | 60.9 | 901.038 | 66.6667 | 901.038 | 73.4893 | 903.806 | 80.9941
1002.08 | 31.7739 | 1002.08 | 38.4016 | 997.924 | 45.2242 | 1000.69 | 51.5595 | 865.052 | 60.4288 | 1003.46 | 65.1072 | 999.308 | 72.2222 | 999.308 | 80.0195
1100.35 | 27.9727 | 1100.35 | 35.0877 | 1100.35 | 42.2027 | 1100.35 | 48.9279 | 913.495 | 59.7466 | 1098.96 | 63.2554 | 1098.96 | 70.9 | 1101.73 | 78.3626
1202.77 | 23.3918 | 1202.77 | 30.9942 | 1200 | 38.3041 | 1200 | 45.4191 | 956.401 | 59.0643 | 1201.38 | 60.5263 | 1201.38 | 69.0059 | 1201.38 | 76.4133
1259.52 | 20.2729 | 1281.66 | 27.0955 | 1301.04 | 33.8207 | 1299.65 | 41.5205 | 997.924 | 58.2846 | 1255.36 | 58.9669 | 1301.04 | 66.7641 | 1302.42 | 74.0741
|  | 1364.71 | 22.2222 | 1402.08 | 28.8499 | 1367.47 | 38.1092 | 1062.98 | 57.0175 | 1299.65 | 57.6023 | 1356.4 | 64.8148 | 1402.08 | 71.54
|  |  |  | 1478.2 | 24.3665 | 1431.14 | 34.6004 | 1147.4 | 54.8733 | 1345.33 | 56.1404 | 1407.61 | 62.963 | 1501.73 | 68.5185
[6 empty] | 1500.35 | 30.117 | 1224.91 | 52.5341 | 1397.92 | 54.0936 | 1460.21 | 60.8187 | 1600 | 64.6199
[6 empty] | 1555.71 | 26.0234 | 1292.73 | 50.0975 | 1457.44 | 51.6569 | 1518.34 | 58.4795 | 1647.06 | 62.4756
[8 empty] | 1349.48 | 47.6608 | 1512.8 | 49.0253 | 1577.85 | 55.7505 | 1699.65 | 60.039
402.768 | 40.7407 | [6 empty] | 1422.84 | 44.2495 | 1555.71 | 46.7836 | 1627.68 | 53.2164 | 1791 | 55.1657
502.422 | 40.0585 | [6 empty] | 1490.66 | 40.7407 | 1600 | 44.2495 | 1681.66 | 50.2924 | 1847.75 | 51.3645
600.692 | 39.0838 | [6 empty] | 1564.01 | 36.3548 | 1642.91 | 41.7154 | 1731.49 | 47.3684 | 1903.11 | 47.3684
[8 empty] | 1676.12 | 29.3372 | 1685.81 | 39.0838 | 1781.31 | 44.152 | 1948.79 | 43.8596
[10 empty] | 1731.49 | 36.2573 | 1826.99 | 41.0331 | 2013.84 | 38.4016
|  | 0 | 46.5887 | [6 empty] | 1788.24 | 31.9688 | 1904.5 | 35.3801
|  | 102.422 | 46.5887
|  | 200.692 | 46.4912
|  | 301.73 | 46.1988 | [8 empty] | 602.076 | 75.3411
|  | 402.768 | 45.7115 | [8 empty] | 701.73 | 74.9513
|  | 517.647 | 44.9318 | [8 empty] | 798.616 | 74.269
|  | 610.381 | 44.347 | [8 empty] | 901.038 | 73.4893
|  | 703.114 | 43.7622 | [8 empty] | 999.308 | 72.2222
|  | 802.768 | 42.4951 | [8 empty] | 1098.96 | 70.468
[10 empty] | 0 | 70.078
[10 empty] | 102.422 | 70.1754
[10 empty] | 202.076 | 69.9805
[10 empty] | 301.73 | 69.7856
[10 empty] | 400 | 69.4932
[10 empty] | 501.038 | 68.9084
[10 empty] | 599.308 | 68.4211
[10 empty] | 698.962 | 68.1287
[10 empty] | 798.616 | 67.5439
[10 empty] | 901.038 | 66.6667
[8 empty] | 0 | 63.9376
[8 empty] | 101.038 | 63.8402
[8 empty] | 202.076 | 63.6452
[8 empty] | 303.114 | 63.5478
[8 empty] | 400 | 63.2554
[8 empty] | 502.422 | 62.8655
[8 empty] | 602.076 | 62.3782
[8 empty] | 700.346 | 61.8908
[8 empty] | 777.855 | 61.501
[8 empty] | 822.145 | 61.0136
[8 empty] | 865.052 | 60.4288

## Efficiency 6G 1150
60% |  | 70% |  | 75% |  | 80% |  | 83% |  | 86% |  | 87%
File 60%.csv |  | File 70%.csv |  | File 75%.csv |  | File 80%.csv |  | File 83%.csv |  | File 86%.csv |  | File 87%.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
451.385 | 83.0949 | 620.308 | 82.3147 | 711.692 | 82.0221 | 850.154 | 81.4369 | 995.538 | 79.974 | 1154.77 | 77.4382 | 1236.46 | 75.9753
438.923 | 80.3641 | 596.769 | 78.0234 | 692.308 | 78.6086 | 841.846 | 78.6086 | 976.154 | 76.1703 | 1142.31 | 73.9272 | 1236.46 | 74.6099
430.615 | 76.7555 | 574.615 | 72.5618 | 671.538 | 75 | 829.385 | 75.0975 | 948.462 | 71.0013 | 1129.85 | 69.9285 | 1253.08 | 73.2445
419.538 | 72.5618 | 558 | 68.4655 | 656.308 | 71.2939 | 818.308 | 71.9766 | 926.308 | 65.8323 | 1121.54 | 66.2224 | 1275.23 | 71.5865
412.615 | 68.4655 | 544.154 | 63.9792 | 639.692 | 65.8323 | 808.615 | 68.4655 | 911.077 | 61.4434 | 1110.46 | 61.736 | 1297.38 | 70.8062
402.923 | 63.2965 | 531.692 | 58.7126 | 624.462 | 59.4928 | 793.385 | 64.857 | 906.923 | 56.4694 | 1110.46 | 58.7126 | 1325.08 | 70.3186
397.385 | 59.0052 | 523.385 | 52.8609 | 614.769 | 53.446 | 783.692 | 61.541 | 915.231 | 52.2757 | 1121.54 | 56.9571 | 1361.08 | 70.7087
394.615 | 55.3966 | 516.462 | 47.5943 | 607.846 | 47.2042 | 776.769 | 57.9324 | 931.846 | 48.6671 | 1135.38 | 55.2991 | 1394.31 | 71.4889
390.462 | 51.8856 | 512.308 | 40.0845 | 603.692 | 42.1326 | 769.846 | 52.9584 | 951.231 | 45.9363 | 1156.15 | 54.5189
390.462 | 48.1795 | 1140.92 | 26.3329 | 605.077 | 39.1092 | 765.692 | 48.5696 | 984.462 | 43.8882 | 1185.23 | 54.1287
391.846 | 43.4005 | 1200.46 | 27.3082 | 1048.15 | 29.9415 | 764.308 | 44.6684 | 1027.38 | 42.3277 | 1221.23 | 54.3238
389.077 | 40.8648 | 1278 | 28.9662 | 1085.54 | 30.6242 | 767.077 | 40.0845 | 1074.46 | 42.1326 | 1253.08 | 55.104
1248.92 | 20.6762 | 1355.54 | 31.0143 | 1136.77 | 31.4044 | 774 | 37.5488 | 1121.54 | 43.0104 | 1301.54 | 56.6645
1302.92 | 21.749 | 1449.69 | 33.1599 | 1188 | 32.6723 | 931.846 | 34.1352 | 1175.54 | 44.3758 | 1345.85 | 58.3225
1363.85 | 22.6268 | 1548 | 35.7932 | 1246.15 | 33.9402 | 995.538 | 35.1105 | 1239.23 | 46.3264 | 1395.69 | 60.8583
1458 | 24.6749 | 1629.69 | 38.329 | 1302.92 | 35.4031 | 1067.54 | 36.2809 | 1304.31 | 48.3745 | 1442.77 | 63.2965
1542.46 | 26.8205 | 1725.23 | 41.4499 | 1350 | 36.4759 | 1134 | 37.6463 | 1372.15 | 50.7152 | 1518.92 | 67.7828
1640.77 | 29.2588 | 1815.23 | 44.5709 | 1408.15 | 38.1339 | 1203.23 | 39.3043 | 1433.08 | 52.9584
1733.54 | 31.7945 | 1899.69 | 47.3017 | 1452.46 | 39.4994 | 1261.38 | 40.8648 | 1494 | 55.5917
1833.23 | 34.3303 |  |  | 1507.85 | 41.2549 | 1340.31 | 43.2055 | 1561.85 | 58.5176
1914.92 | 36.5735 |  |  | 1556.31 | 42.9129 | 1401.23 | 45.156 | 1644.92 | 62.5163
2003.54 | 39.0117 |  |  | 1621.38 | 44.8635 | 1460.77 | 47.3017
|  |  |  | 1665.69 | 46.3264 | 1530 | 49.8375
|  |  |  | 1714.15 | 48.1795 | 1585.38 | 51.8856
|  |  |  | 1772.31 | 50.4226 | 1654.62 | 54.6164
|  |  |  | 1830.46 | 52.6658 | 1737.69 | 58.1274

## Brake Horsepower 6G 1150
10HP |  | 15HP |  | 20HP |  | 25HP |  | 30HP |  | 40HP
File 10HP.csv |  | File 15HP.csv |  | File 20HP.csv |  | File 25HP.csv |  | File 30HP.csv |  | File 40HP.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
398.616 | 58.8694 | 441.522 | 79.7271 | 728.028 | 82.0663 | 1060.21 | 79.0448 | 1494.81 | 68.8109 | 2022.15 | 57.0175
438.754 | 56.5302 | 483.045 | 77.5828 | 775.086 | 79.2398 | 1082.35 | 77.5828 | 1528.03 | 66.6667 | 2059.52 | 53.7037
481.661 | 54.5809 | 534.256 | 74.4639 | 833.218 | 76.1209 | 1115.57 | 75.731 | 1564.01 | 64.5224 | 2102.42 | 49.9025
524.567 | 52.729 | 575.779 | 72.2222 | 877.509 | 73.5867 | 1152.94 | 73.8791 | 1598.62 | 62.5731 | 2130.1 | 47.1735
573.01 | 50.4873 | 615.917 | 70.1754 | 920.415 | 71.1501 | 1200 | 71.345 | 1637.37 | 60.3314 | 2179.93 | 41.8129
626.99 | 48.0507 | 656.055 | 67.7388 | 981.315 | 68.1287 | 1259.52 | 68.1287 | 1684.43 | 56.9201
680.969 | 45.614 | 693.426 | 65.692 | 1031.14 | 65.4971 | 1316.26 | 65.3996 | 1728.72 | 53.5088
721.107 | 43.6647 | 740.484 | 63.0604 | 1083.74 | 62.5731 | 1371.63 | 62.4756 | 1771.63 | 50.3899
762.63 | 41.7154 | 786.159 | 60.8187 | 1130.8 | 60.1365 | 1413.15 | 59.8441 | 1809 | 47.7583
804.152 | 39.8635 | 837.37 | 58.3821 | 1180.62 | 57.6023 | 1453.29 | 57.6998 | 1868.51 | 43.5673
842.907 | 38.1092 | 888.581 | 55.9454 | 1235.99 | 54.9708 | 1501.73 | 54.7758 | 1908.65 | 40.4483
896.886 | 35.3801 | 941.176 | 52.924 | 1281.66 | 52.5341 | 1540.48 | 52.0468 | 1969.55 | 35.4776
930.104 | 33.7882 | 997.924 | 50.4873 | 1327.34 | 49.8051 | 1591.7 | 48.9279
964.245 | 32.0988 | 1051.9 | 47.9532 | 1378.55 | 46.8811 | 1641.52 | 45.614
999.308 | 30.3444 | 1104.5 | 45.2242 | 1421.45 | 44.152 | 1683.04 | 42.5926
1038.06 | 28.3301 | 1151.56 | 42.6901 | 1467.13 | 41.3255 | 1739.79 | 38.7914
1097.12 | 25.2112 | 1200 | 40.3509 | 1515.57 | 38.3041 | 1781.31 | 35.6725
|  | 1252.6 | 37.4269 | 1562.63 | 35.2826 | 1838.06 | 31.6764
|  | 1292.73 | 35.0877 | 1602.77 | 32.4561
|  | 1321.8 | 33.2359 | 1674.74 | 27.3879
|  | 1343.94 | 31.7739
|  | 1371.63 | 30.3119
|  | 1399.31 | 28.46
|  | 1438.06 | 26.3158
|  | 1493.43 | 22.9045

## Design Point System Curve
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-04-06 06:32
Project Name: | Chiller Plant Model
Project Number:
Engineer: | David
Assumptions
1 | Known flow = | 1300 | gpm
2 | Head or static at known flow = | 70 | ft.w.c.
3 | Fixed static or open system lift = | 0 | For closed systems enter pressure control set point
If there is no pressure control, enter 0
4 | Efficiency = | 86.9% | (From the curve)
5 | Bhp = | 26.444 | Bhp (calculated)
6 | Largest impeller = | 13.5 | inches
7 | Smallest impeller = | 10 | inches
System Curve Points
| Condition | Flow | Static
| 140% of known flow | 1820 | 137.2
| 120% of known flow | 1560 | 100.8
| Known | 1300 | 70
| 80% of known flow | 1040 | 44.8
| 60% of known flow | 780 | 25.2
| 40% of known flow | 520 | 11.2
| 30% of known flow | 390 | 6.3
| 20% of known flow | 260 | 2.8
| 18% of known flow | 234 | 2.268
| 16% of known flow | 208 | 1.792
| 14% of known flow | 182 | 1.372
| 12% of known flow | 156 | 1.008
| 10% of known flow | 130 | 0.7
| 8% of known flow | 104 | 0.448
| 6% of known flow | 78 | 0.252
| 4% of known flow | 31.2 | 0.04032
| 2% of known flow | 15.6 | 0.01008
| No Flow | 0 | 0
Design Conditions
| Head Line | 2500 | 70
|  | 0 | 70
| Flow Line | 1300 | 90
|  | 1300 | 0
System Curve and Largest Impeller
| Head Line | 2500 | 73.5
|  | 0 | 73.5
| Flow Line | 1330 | 90
|  | 1330 | 0

## Design Impeller from Largest
Step 1 - Estimate the new impeller size
Basis for Estimating the new impeller size
Desired Flow - | 1300 | gpm
Known flow - | 1330 | gpm (from where the design system curve crosses the known impeller size curve)
Known impeller size - | 13.5 | inches
Desired impeller size - | 13.1955 | inches
Step 2 - For each point on the known impeller line, calculate the flow for the different impeller size
Basis for Estimating the Design Impeller Line Flow
Known impeller size - | 13.5 | inches
Desired impeller size - | 13.1955 | inches (calculated above)
| 13.500 Impeller Flow, gpm (Known value from digitized curve) | 13.195 Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 9.7744e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 98.7589
| 202.076 | 197.5179
| 301.73 | 294.9241
| 401.384 | 392.3302
| 502.422 | 491.0892
| 602.076 | 588.4953
| 703.114 | 687.2543
| 801.384 | 783.3077
| 903.806 | 883.4194
| 999.308 | 976.7672
| 1101.73 | 1076.8789
| 1201.38 | 1174.2812
| 1302.42 | 1273.0421
| 1402.08 | 1370.4541
| 1501.73 | 1467.8564
| 1600 | 1563.9098
| 1647.06 | 1609.9083
| 1699.65 | 1661.312
| 1791 | 1750.6015
| 1847.75 | 1806.0714
| 1903.11 | 1860.1827
| 1948.79 | 1904.8323
| 2013.84 | 1968.415
Step 3 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 13.500 inch Impeller Flow, gpm (Known value from digitized curve) | 13.195 inch Impeller Flow, gpm (Calculated above) | 13.500 inch Impeller Head, ft.w.c. (Known value from digitized curve) | 13.195 inch Impeller Head, ft.w.c. (From square law)
| 1e-09 | 9.7744e-10 | 83.5283 | 79.8026
| 101.038 | 98.7589 | 83.6257 | 79.8957
| 202.076 | 197.5179 | 83.5283 | 79.8026
| 301.73 | 294.9241 | 83.4308 | 79.7095
| 401.384 | 392.3302 | 83.2359 | 79.5232
| 502.422 | 491.0892 | 82.846 | 79.1507
| 602.076 | 588.4953 | 82.4561 | 78.7782
| 703.114 | 687.2543 | 82.0663 | 78.4058
| 801.384 | 783.3077 | 81.6764 | 78.0333
| 903.806 | 883.4194 | 80.9941 | 77.3814
| 999.308 | 976.7672 | 80.0195 | 76.4503
| 1101.73 | 1076.8789 | 78.3626 | 74.8673
| 1201.38 | 1174.2812 | 76.4133 | 73.005
| 1302.42 | 1273.0421 | 74.0741 | 70.7701
| 1402.08 | 1370.4541 | 71.54 | 68.349
| 1501.73 | 1467.8564 | 68.5185 | 65.4623
| 1600 | 1563.9098 | 64.6199 | 61.7376
| 1647.06 | 1609.9083 | 62.4756 | 59.6889
| 1699.65 | 1661.312 | 60.039 | 57.361
| 1791 | 1750.6015 | 55.1657 | 52.7051
| 1847.75 | 1806.0714 | 51.3645 | 49.0734
| 1903.11 | 1860.1827 | 47.3684 | 45.2556
| 1948.79 | 1904.8323 | 43.8596 | 41.9033
| 2013.84 | 1968.415 | 38.4016 | 36.6887
Step 4 - Plot the results (the cells highlighted in yellow above) on the pump curve
| First Point System Curve Points |  |  | Flow Line, gpm
| Condition | Flow | Static | X | Y
| 140% of known flow | 2728.306 | 85.9648 | 1904.8323 | 41.9033
| 120% of known flow | 2338.548 | 63.1578 | 1904.8323 | 0
| Known | 1904.8323 | 41.9033
| 80% of known flow | 1559.032 | 28.0701 | Head Line, ft.w.c.
| 60% of known flow | 1169.274 | 15.7895 | X | Y
| 40% of known flow | 779.516 | 7.0175 | 1904.8323 | 41.9033
| 30% of known flow | 584.637 | 3.9474 | 0 | 41.9033
| 20% of known flow | 389.758 | 1.7544
| 18% of known flow | 350.7822 | 1.4211
| 16% of known flow | 311.8064 | 1.1228
| 14% of known flow | 272.8306 | 0.85965
| 12% of known flow | 233.8548 | 0.63158
| 10% of known flow | 194.879 | 0.4386
| 8% of known flow | 155.9032 | 0.2807
| 6% of known flow | 116.9274 | 0.15789
| 4% of known flow | 77.9516 | 0.070175
| 2% of known flow | 38.9758 | 0.017544
| No Flow | 0 | 0
Table for illustration
| Column A | Column B | Column C | Column D
| 13.500 inch Impeller Flow, gpm (Known value from digitized curve) | 13.195 inch Impeller Flow, gpm (Calculatedfrom the affinity law) | 13.500 inch Impeller Head, ft.w.c. (Known value from digitized curve) | 13.195 inch Impeller Head, ft.w.c. (From square law)
| 1e-09 | 9.7744e-10 | 83.5283 | 79.8026
| 101.038 | 98.7589 | 83.6257 | 79.8957
| 202.076 | 197.5179 | 83.5283 | 79.8026
| 301.73 | 294.9241 | 83.4308 | 79.7095
| 401.384 | 392.3302 | 83.2359 | 79.5232
| 502.422 | 491.0892 | 82.846 | 79.1507
| 602.076 | 588.4953 | 82.4561 | 78.7782
| 703.114 | 687.2543 | 82.0663 | 78.4058
| 801.384 | 783.3077 | 81.6764 | 78.0333
| 903.806 | 883.4194 | 80.9941 | 77.3814
| 999.308 | 976.7672 | 80.0195 | 76.4503
| 1101.73 | 1076.8789 | 78.3626 | 74.8673
| 1201.38 | 1174.2812 | 76.4133 | 73.005
| 1302.42 | 1273.0421 | 74.0741 | 70.7701
| 1402.08 | 1370.4541 | 71.54 | 68.349
| 1501.73 | 1467.8564 | 68.5185 | 65.4623
| 1600 | 1563.9098 | 64.6199 | 61.7376
| 1647.06 | 1609.9083 | 62.4756 | 59.6889
| 1699.65 | 1661.312 | 60.039 | 57.361
| 1791 | 1750.6015 | 55.1657 | 52.7051
| 1847.75 | 1806.0714 | 51.3645 | 49.0734
| 1903.11 | 1860.1827 | 47.3684 | 45.2556
| 1948.79 | 1904.8323 | 43.8596 | 41.9033
| 2013.84 | 1968.415 | 38.4016 | 36.6887

## Smallest Impeller from Largest
Step 1 - For each point on the known impeller line, calculate the flow for the different impeller size
Basis for Estimating the Design Impeller Line Flow
Known impeller size - | 13.5 | inches
Desired impeller size - | 10 | inches (Set equal to the smallest tested size)
| 13.500 Impeller Flow, gpm (Known value from digitized curve) | 10.000 Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 7.4074e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 74.843
| 202.076 | 149.6859
| 301.73 | 223.5037
| 401.384 | 297.3215
| 502.422 | 372.1644
| 602.076 | 445.9822
| 703.114 | 520.8252
| 801.384 | 593.6178
| 903.806 | 669.4859
| 999.308 | 740.2281
| 1101.73 | 816.0963
| 1201.38 | 889.9111
| 1302.42 | 964.7556
| 1402.08 | 1038.5778
| 1501.73 | 1112.3926
| 1600 | 1185.1852
| 1647.06 | 1220.0444
| 1699.65 | 1259
| 1791 | 1326.6667
| 1847.75 | 1368.7037
| 1903.11 | 1409.7111
| 1948.79 | 1443.5481
| 2013.84 | 1491.7333
Step 2 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 13.500 inch Impeller Flow, gpm (Known value from digitized curve) | 10.000 inch Impeller Flow, gpm (Calculated above) | 13.500 inch Impeller Head, ft.w.c. (Known value from digitized curve) | 10.000 inch Impeller Head, ft.w.c. (From square law)
| 1e-09 | 7.4074e-10 | 83.5283 | 45.8317
| 101.038 | 74.843 | 83.6257 | 45.8852
| 202.076 | 149.6859 | 83.5283 | 45.8317
| 301.73 | 223.5037 | 83.4308 | 45.7782
| 401.384 | 297.3215 | 83.2359 | 45.6713
| 502.422 | 372.1644 | 82.846 | 45.4573
| 602.076 | 445.9822 | 82.4561 | 45.2434
| 703.114 | 520.8252 | 82.0663 | 45.0295
| 801.384 | 593.6178 | 81.6764 | 44.8156
| 903.806 | 669.4859 | 80.9941 | 44.4412
| 999.308 | 740.2281 | 80.0195 | 43.9064
| 1101.73 | 816.0963 | 78.3626 | 42.9973
| 1201.38 | 889.9111 | 76.4133 | 41.9277
| 1302.42 | 964.7556 | 74.0741 | 40.6442
| 1402.08 | 1038.5778 | 71.54 | 39.2538
| 1501.73 | 1112.3926 | 68.5185 | 37.5959
| 1600 | 1185.1852 | 64.6199 | 35.4567
| 1647.06 | 1220.0444 | 62.4756 | 34.2802
| 1699.65 | 1259 | 60.039 | 32.9432
| 1791 | 1326.6667 | 55.1657 | 30.2692
| 1847.75 | 1368.7037 | 51.3645 | 28.1835
| 1903.11 | 1409.7111 | 47.3684 | 25.9909
| 1948.79 | 1443.5481 | 43.8596 | 24.0656
| 2013.84 | 1491.7333 | 38.4016 | 21.0708
Step 3 - Plot the results (the cells highlighted in yellow above) on the pump curve

## 10.5 from 13.5
Step 1 - For each point on the known impeller line, calculate the flow for the different impeller size
Basis for Estimating the Design Impeller Line Flow
Known impeller size - | 13.5 | inches
Desired impeller size - | 10.5 | inches (Set equal to the smallest tested size)
| 13.500 Impeller Flow, gpm (Known value from digitized curve) | 10.500 Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 7.7778e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 78.5851
| 202.076 | 157.1702
| 301.73 | 234.6789
| 401.384 | 312.1876
| 502.422 | 390.7727
| 602.076 | 468.2813
| 703.114 | 546.8664
| 801.384 | 623.2987
| 903.806 | 702.9602
| 999.308 | 777.2396
| 1101.73 | 856.9011
| 1201.38 | 934.4067
| 1302.42 | 1012.9933
| 1402.08 | 1090.5067
| 1501.73 | 1168.0122
| 1600 | 1244.4444
| 1647.06 | 1281.0467
| 1699.65 | 1321.95
| 1791 | 1393
| 1847.75 | 1437.1389
| 1903.11 | 1480.1967
| 1948.79 | 1515.7256
| 2013.84 | 1566.32
Step 2 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 13.500 inch Impeller Flow, gpm (Known value from digitized curve) | 10.500 inch Impeller Flow, gpm (Calculated above) | 13.500 inch Impeller Head, ft.w.c. (Known value from digitized curve) | 10.500 inch Impeller Head, ft.w.c. (From square law)
| 1e-09 | 7.7778e-10 | 83.5283 | 50.5295
| 101.038 | 78.5851 | 83.6257 | 50.5884
| 202.076 | 157.1702 | 83.5283 | 50.5295
| 301.73 | 234.6789 | 83.4308 | 50.4705
| 401.384 | 312.1876 | 83.2359 | 50.3526
| 502.422 | 390.7727 | 82.846 | 50.1167
| 602.076 | 468.2813 | 82.4561 | 49.8809
| 703.114 | 546.8664 | 82.0663 | 49.645
| 801.384 | 623.2987 | 81.6764 | 49.4092
| 903.806 | 702.9602 | 80.9941 | 48.9964
| 999.308 | 777.2396 | 80.0195 | 48.4069
| 1101.73 | 856.9011 | 78.3626 | 47.4045
| 1201.38 | 934.4067 | 76.4133 | 46.2253
| 1302.42 | 1012.9933 | 74.0741 | 44.8103
| 1402.08 | 1090.5067 | 71.54 | 43.2773
| 1501.73 | 1168.0122 | 68.5185 | 41.4495
| 1600 | 1244.4444 | 64.6199 | 39.0911
| 1647.06 | 1281.0467 | 62.4756 | 37.7939
| 1699.65 | 1321.95 | 60.039 | 36.3199
| 1791 | 1393 | 55.1657 | 33.3718
| 1847.75 | 1437.1389 | 51.3645 | 31.0724
| 1903.11 | 1480.1967 | 47.3684 | 28.655
| 1948.79 | 1515.7256 | 43.8596 | 26.5324
| 2013.84 | 1566.32 | 38.4016 | 23.2306
Step 3 - Plot the results (the cells highlighted in yellow above) on the pump curve

## 10.5 from 10
Step 1 - For each point on the known impeller line, calculate the flow for the different impeller size
Basis for Estimating the Design Impeller Line Flow
Known impeller size - | 10 | inches
Desired impeller size - | 10.5 | inches (Set equal to the smallest tested size)
| 10.000 Impeller Flow, gpm (Known value from digitized curve) | 10.500 Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 1.05e-09 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 102.422 | 107.5431
| 202.076 | 212.1798
| 300.346 | 315.3633
| 402.768 | 422.9064
| 502.422 | 527.5431
| 600.692 | 630.7266
| 701.73 | 736.8165
| 801.384 | 841.4532
| 899.654 | 944.6367
| 1002.08 | 1052.184
| 1100.35 | 1155.3675
| 1202.77 | 1262.9085
| 1259.52 | 1322.496
Step 2 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 10.000 inch Impeller Flow, gpm (Known value from digitized curve) | 10.500 inch Impeller Flow, gpm (Calculated above) | 10.000 inch Impeller Head, ft.w.c. (Known value from digitized curve) | 10.500 inch Impeller Head, ft.w.c. (From square law)
| 1e-09 | 1.05e-09 | 41.2281 | 45.454
| 102.422 | 107.5431 | 41.3255 | 45.5614
| 202.076 | 212.1798 | 41.423 | 45.6689
| 300.346 | 315.3633 | 41.2281 | 45.454
| 402.768 | 422.9064 | 40.85 | 45.0371
| 502.422 | 527.5431 | 40.4 | 44.541
| 600.692 | 630.7266 | 39.5 | 43.5487
| 701.73 | 736.8165 | 38.5965 | 42.5526
| 801.384 | 841.4532 | 37.037 | 40.8333
| 899.654 | 944.6367 | 34.9903 | 38.5768
| 1002.08 | 1052.184 | 31.7739 | 35.0307
| 1100.35 | 1155.3675 | 27.9727 | 30.8399
| 1202.77 | 1262.9085 | 23.3918 | 25.7895
| 1259.52 | 1322.496 | 20.2729 | 22.3509
Step 3 - Plot the results (the cells highlighted in yellow above) on the pump curve