## 1510 6G 1150rpm
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2015-03-29
Project Name: | Duct Friction Spreadsheet
Project Number: | None
Engineer: | David
Click here to go to the data used to plot the digital pump curve set
Click here to go to the design condition tabs
Click here to go to the 75% load condition tabs
Click here to go to the 50% load condition tabs
Click here to go to the 25% load condition tabs
Click here to go to the 12.5% load condition tabs
Click here to go to the summary tab

## Impeller 6G 1150
10 Inch |  | 10.5 Inch |  | 11 Inch |  | 11.5 Inch |  | 12 Inch |  | 12.5 Inch |  | 13 Inch |  | 13.5 Inch
File 10 Inch.csv |  | File 10.5 Inch.csv |  | File 11 Inch.csv |  | File 11.5 Inch.csv |  | File 12 Inch.csv |  | File 12.5 Inch.csv |  | File 13 Inch.csv |  | File 13.5 Inch.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
0 | 41.2281 | 0 | 46.5887 | 0 | 51.7544 | 0 | 57.5049 | 0 | 63.9376 | 0 | 70.078 | 0 | 76.8031 | 0 | 83.5283
102.422 | 41.3255 | 102.422 | 46.5887 | 101.038 | 51.7544 | 99.654 | 57.5049 | 101.038 | 63.8402 | 102.422 | 70.1 | 101.038 | 76.7057 | 101.038 | 83.6257
202.076 | 41.423 | 200.692 | 46.4912 | 202.076 | 51.462 | 200.692 | 57.4074 | 202.076 | 63.6452 | 202.076 | 69.9805 | 203.46 | 76.6082 | 202.076 | 83.5283
300.346 | 41.2281 | 301.73 | 46.1988 | 303.114 | 51.1696 | 300.346 | 57.2125 | 303.114 | 63.5478 | 301.73 | 69.7856 | 301.73 | 76.5107 | 301.73 | 83.4308
402.768 | 40.85 | 402.768 | 45.7115 | 402.768 | 50.7797 | 397.232 | 56.9201 | 400 | 63.2554 | 400 | 69.4932 | 402.768 | 76.4133 | 401.384 | 83.2359
502.422 | 40.4 | 517.647 | 45.2 | 517.647 | 50.3899 | 501.038 | 56.4327 | 502.422 | 62.8655 | 501.038 | 69.1 | 501.038 | 76.0234 | 502.422 | 82.846
600.692 | 39.5 | 610.381 | 44.5 | 613.149 | 49.9025 | 600.692 | 56.0429 | 602.076 | 62.3782 | 599.308 | 68.6 | 602.076 | 75.5 | 602.076 | 82.4561
701.73 | 38.5965 | 703.114 | 43.7622 | 705.882 | 49.3177 | 701.73 | 55.5556 | 700.346 | 61.8908 | 698.962 | 68.1287 | 701.73 | 74.9513 | 703.114 | 82.0663
801.384 | 37.037 | 802.768 | 42.4951 | 798.616 | 48.538 | 800 | 54.6784 | 777.855 | 61.2 | 798.616 | 67.5439 | 798.616 | 74.269 | 801.384 | 81.6764
899.654 | 34.9903 | 898.27 | 40.8382 | 901.038 | 47.271 | 898.27 | 53.7037 | 822.145 | 60.9 | 901.038 | 66.6667 | 901.038 | 73.4893 | 903.806 | 80.9941
1002.08 | 31.7739 | 1002.08 | 38.4016 | 997.924 | 45.2242 | 1000.69 | 51.5595 | 865.052 | 60.4288 | 1003.46 | 65.1072 | 999.308 | 72.2222 | 999.308 | 80.0195
1100.35 | 27.9727 | 1100.35 | 35.0877 | 1100.35 | 42.2027 | 1100.35 | 48.9279 | 913.495 | 59.7466 | 1098.96 | 63.2554 | 1098.96 | 70.9 | 1101.73 | 78.3626
1202.77 | 23.3918 | 1202.77 | 30.9942 | 1200 | 38.3041 | 1200 | 45.4191 | 956.401 | 59.0643 | 1201.38 | 60.5263 | 1201.38 | 69.0059 | 1201.38 | 76.4133
1259.52 | 20.2729 | 1281.66 | 27.0955 | 1301.04 | 33.8207 | 1299.65 | 41.5205 | 997.924 | 58.2846 | 1255.36 | 58.9669 | 1301.04 | 66.7641 | 1302.42 | 74.0741
|  | 1364.71 | 22.2222 | 1402.08 | 28.8499 | 1367.47 | 38.1092 | 1062.98 | 57.0175 | 1299.65 | 57.6023 | 1356.4 | 64.8148 | 1402.08 | 71.54
|  |  |  | 1478.2 | 24.3665 | 1431.14 | 34.6004 | 1147.4 | 54.8733 | 1345.33 | 56.1404 | 1407.61 | 62.963 | 1501.73 | 68.5185
[6 empty] | 1500.35 | 30.117 | 1224.91 | 52.5341 | 1397.92 | 54.0936 | 1460.21 | 60.8187 | 1600 | 64.6199
[6 empty] | 1555.71 | 26.0234 | 1292.73 | 50.0975 | 1457.44 | 51.6569 | 1518.34 | 58.4795 | 1647.06 | 62.4756
[8 empty] | 1349.48 | 47.6608 | 1512.8 | 49.0253 | 1577.85 | 55.7505 | 1699.65 | 60.039
402.768 | 40.7407 | [6 empty] | 1422.84 | 44.2495 | 1555.71 | 46.7836 | 1627.68 | 53.2164 | 1791 | 55.1657
502.422 | 40.0585 | [6 empty] | 1490.66 | 40.7407 | 1600 | 44.2495 | 1681.66 | 50.2924 | 1847.75 | 51.3645
600.692 | 39.0838 | [6 empty] | 1564.01 | 36.3548 | 1642.91 | 41.7154 | 1731.49 | 47.3684 | 1903.11 | 47.3684
[8 empty] | 1676.12 | 29.3372 | 1685.81 | 39.0838 | 1781.31 | 44.152 | 1948.79 | 43.8596
[10 empty] | 1731.49 | 36.2573 | 1826.99 | 41.0331 | 2013.84 | 38.4016
|  | 0 | 46.5887 | [6 empty] | 1788.24 | 31.9688 | 1904.5 | 35.3801
|  | 102.422 | 46.5887
|  | 200.692 | 46.4912
|  | 301.73 | 46.1988 | [8 empty] | 602.076 | 75.3411
|  | 402.768 | 45.7115 | [8 empty] | 701.73 | 74.9513
|  | 517.647 | 44.9318 | [8 empty] | 798.616 | 74.269
|  | 610.381 | 44.347 | [8 empty] | 901.038 | 73.4893
|  | 703.114 | 43.7622 | [8 empty] | 999.308 | 72.2222
|  | 802.768 | 42.4951 | [8 empty] | 1098.96 | 70.468
[10 empty] | 0 | 70.078
[10 empty] | 102.422 | 70.1754
[10 empty] | 202.076 | 69.9805
[10 empty] | 301.73 | 69.7856
[10 empty] | 400 | 69.4932
[10 empty] | 501.038 | 68.9084
[10 empty] | 599.308 | 68.4211
[10 empty] | 698.962 | 68.1287
[10 empty] | 798.616 | 67.5439
[10 empty] | 901.038 | 66.6667
[8 empty] | 0 | 63.9376
[8 empty] | 101.038 | 63.8402
[8 empty] | 202.076 | 63.6452
[8 empty] | 303.114 | 63.5478
[8 empty] | 400 | 63.2554
[8 empty] | 502.422 | 62.8655
[8 empty] | 602.076 | 62.3782
[8 empty] | 700.346 | 61.8908
[8 empty] | 777.855 | 61.501
[8 empty] | 822.145 | 61.0136
[8 empty] | 865.052 | 60.4288

## Efficiency 6G 1150
60% |  | 70% |  | 75% |  | 80% |  | 83% |  | 86% |  | 87%
File 60%.csv |  | File 70%.csv |  | File 75%.csv |  | File 80%.csv |  | File 83%.csv |  | File 86%.csv |  | File 87%.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
451.385 | 83.0949 | 620.308 | 82.3147 | 711.692 | 82.0221 | 850.154 | 81.4369 | 995.538 | 79.974 | 1154.77 | 77.4382 | 1236.46 | 75.9753
438.923 | 80.3641 | 596.769 | 78.0234 | 692.308 | 78.6086 | 841.846 | 78.6086 | 976.154 | 76.1703 | 1142.31 | 73.9272 | 1236.46 | 74.6099
430.615 | 76.7555 | 574.615 | 72.5618 | 671.538 | 75 | 829.385 | 75.0975 | 948.462 | 71.0013 | 1129.85 | 69.9285 | 1253.08 | 73.2445
419.538 | 72.5618 | 558 | 68.4655 | 656.308 | 71.2939 | 818.308 | 71.9766 | 926.308 | 65.8323 | 1121.54 | 66.2224 | 1275.23 | 71.5865
412.615 | 68.4655 | 544.154 | 63.9792 | 639.692 | 65.8323 | 808.615 | 68.4655 | 911.077 | 61.4434 | 1110.46 | 61.736 | 1297.38 | 70.8062
402.923 | 63.2965 | 531.692 | 58.7126 | 624.462 | 59.4928 | 793.385 | 64.857 | 906.923 | 56.4694 | 1110.46 | 58.7126 | 1325.08 | 70.3186
397.385 | 59.0052 | 523.385 | 52.8609 | 614.769 | 53.446 | 783.692 | 61.541 | 915.231 | 52.2757 | 1121.54 | 56.9571 | 1361.08 | 70.7087
394.615 | 55.3966 | 516.462 | 47.5943 | 607.846 | 47.2042 | 776.769 | 57.9324 | 931.846 | 48.6671 | 1135.38 | 55.2991 | 1394.31 | 71.4889
390.462 | 51.8856 | 512.308 | 40.0845 | 603.692 | 42.1326 | 769.846 | 52.9584 | 951.231 | 45.9363 | 1156.15 | 54.5189
390.462 | 48.1795 | 1140.92 | 26.3329 | 605.077 | 39.1092 | 765.692 | 48.5696 | 984.462 | 43.8882 | 1185.23 | 54.1287
391.846 | 43.4005 | 1200.46 | 27.3082 | 1048.15 | 29.9415 | 764.308 | 44.6684 | 1027.38 | 42.3277 | 1221.23 | 54.3238
389.077 | 40.8648 | 1278 | 28.9662 | 1085.54 | 30.6242 | 767.077 | 40.0845 | 1074.46 | 42.1326 | 1253.08 | 55.104
1248.92 | 20.6762 | 1355.54 | 31.0143 | 1136.77 | 31.4044 | 774 | 37.5488 | 1121.54 | 43.0104 | 1301.54 | 56.6645
1302.92 | 21.749 | 1449.69 | 33.1599 | 1188 | 32.6723 | 931.846 | 34.1352 | 1175.54 | 44.3758 | 1345.85 | 58.3225
1363.85 | 22.6268 | 1548 | 35.7932 | 1246.15 | 33.9402 | 995.538 | 35.1105 | 1239.23 | 46.3264 | 1395.69 | 60.8583
1458 | 24.6749 | 1629.69 | 38.329 | 1302.92 | 35.4031 | 1067.54 | 36.2809 | 1304.31 | 48.3745 | 1442.77 | 63.2965
1542.46 | 26.8205 | 1725.23 | 41.4499 | 1350 | 36.4759 | 1134 | 37.6463 | 1372.15 | 50.7152 | 1518.92 | 67.7828
1640.77 | 29.2588 | 1815.23 | 44.5709 | 1408.15 | 38.1339 | 1203.23 | 39.3043 | 1433.08 | 52.9584
1733.54 | 31.7945 | 1899.69 | 47.3017 | 1452.46 | 39.4994 | 1261.38 | 40.8648 | 1494 | 55.5917
1833.23 | 34.3303 |  |  | 1507.85 | 41.2549 | 1340.31 | 43.2055 | 1561.85 | 58.5176
1914.92 | 36.5735 |  |  | 1556.31 | 42.9129 | 1401.23 | 45.156 | 1644.92 | 62.5163
2003.54 | 39.0117 |  |  | 1621.38 | 44.8635 | 1460.77 | 47.3017
|  |  |  | 1665.69 | 46.3264 | 1530 | 49.8375
|  |  |  | 1714.15 | 48.1795 | 1585.38 | 51.8856
|  |  |  | 1772.31 | 50.4226 | 1654.62 | 54.6164
|  |  |  | 1830.46 | 52.6658 | 1737.69 | 58.1274

## Brake Horsepower 6G 1150
10HP |  | 15HP |  | 20HP |  | 25HP |  | 30HP |  | 40HP
File 10HP.csv |  | File 15HP.csv |  | File 20HP.csv |  | File 25HP.csv |  | File 30HP.csv |  | File 40HP.csv
Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT) | Capacity (GPM) | Total Head (FT)
398.616 | 58.8694 | 441.522 | 79.7271 | 728.028 | 82.0663 | 1060.21 | 79.0448 | 1494.81 | 68.8109 | 2022.15 | 57.0175
438.754 | 56.5302 | 483.045 | 77.5828 | 775.086 | 79.2398 | 1082.35 | 77.5828 | 1528.03 | 66.6667 | 2059.52 | 53.7037
481.661 | 54.5809 | 534.256 | 74.4639 | 833.218 | 76.1209 | 1115.57 | 75.731 | 1564.01 | 64.5224 | 2102.42 | 49.9025
524.567 | 52.729 | 575.779 | 72.2222 | 877.509 | 73.5867 | 1152.94 | 73.8791 | 1598.62 | 62.5731 | 2130.1 | 47.1735
573.01 | 50.4873 | 615.917 | 70.1754 | 920.415 | 71.1501 | 1200 | 71.345 | 1637.37 | 60.3314 | 2179.93 | 41.8129
626.99 | 48.0507 | 656.055 | 67.7388 | 981.315 | 68.1287 | 1259.52 | 68.1287 | 1684.43 | 56.9201
680.969 | 45.614 | 693.426 | 65.692 | 1031.14 | 65.4971 | 1316.26 | 65.3996 | 1728.72 | 53.5088
721.107 | 43.6647 | 740.484 | 63.0604 | 1083.74 | 62.5731 | 1371.63 | 62.4756 | 1771.63 | 50.3899
762.63 | 41.7154 | 786.159 | 60.8187 | 1130.8 | 60.1365 | 1413.15 | 59.8441 | 1809 | 47.7583
804.152 | 39.8635 | 837.37 | 58.3821 | 1180.62 | 57.6023 | 1453.29 | 57.6998 | 1868.51 | 43.5673
842.907 | 38.1092 | 888.581 | 55.9454 | 1235.99 | 54.9708 | 1501.73 | 54.7758 | 1908.65 | 40.4483
896.886 | 35.3801 | 941.176 | 52.924 | 1281.66 | 52.5341 | 1540.48 | 52.0468 | 1969.55 | 35.4776
930.104 | 33.7882 | 997.924 | 50.4873 | 1327.34 | 49.8051 | 1591.7 | 48.9279
964.245 | 32.0988 | 1051.9 | 47.9532 | 1378.55 | 46.8811 | 1641.52 | 45.614
999.308 | 30.3444 | 1104.5 | 45.2242 | 1421.45 | 44.152 | 1683.04 | 42.5926
1038.06 | 28.3301 | 1151.56 | 42.6901 | 1467.13 | 41.3255 | 1739.79 | 38.7914
1097.12 | 25.2112 | 1200 | 40.3509 | 1515.57 | 38.3041 | 1781.31 | 35.6725
|  | 1252.6 | 37.4269 | 1562.63 | 35.2826 | 1838.06 | 31.6764
|  | 1292.73 | 35.0877 | 1602.77 | 32.4561
|  | 1321.8 | 33.2359 | 1674.74 | 27.3879
|  | 1343.94 | 31.7739
|  | 1371.63 | 30.3119
|  | 1399.31 | 28.46
|  | 1438.06 | 26.3158
|  | 1493.43 | 22.9045

## Design Point System Curve
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-04-06 06:32
Project Name: | Chiller Plant Model
Project Number:
Engineer: | David
Assumptions
1 | Known flow = | 1300 | gpm (design parameter)
2 | Head or static at known flow = | 70 | ft.w.c. (design parameter)
3 | Fixed static or open system lift = | 0 | Note 1
4 | System Curve Exponent = | 2 | Note 2
5 | Efficiency = | 86.9% | (From the curve)
6 | Bhp = | 26.444 | Bhp (calculated)
7 | Largest impeller = | 13.5 | inches
8 | Closest known impeller size = | 13.5 | inches (enter the known impeller size closes to the design operating point)
9 | Smallest impeller = | 10 | inches
10 | Published curve speed = | 1150 | rpm (from the published curve)
Note 1 - For closed systems that control for a fixed pressure, enter it here in ft.w.c., otherwise use 0.
Note 2 - The typical value for this is 2, but ASHRAE research indicates that generally, 1.85 - 1.89 may be more appropriate for systems were there are some portions with out fully developed turbulent flow.
| System Curve Points |  |  |  | Click here to go to the data used to plot the digital pump curve set
| Condition | Flow | Pressure |  | Click here to go to the design condition tabs
| 140% of known flow | 1820 | 137.2 |  | Click here to go to the 75% load condition tabs
| 120% of known flow | 1560 | 100.8 |  | Click here to go to the 50% load condition tabs
| Known | 1300 | 70 |  | Click here to go to the 25% load condition tabs
| 80% of known flow | 1040 | 44.8 |  | Click here to go to the 12.5% load condition tabs
| 60% of known flow | 780 | 25.2 |  | Click here to go to the summary tab
| 40% of known flow | 520 | 11.2
| 30% of known flow | 390 | 6.3
| 20% of known flow | 260 | 2.8
| 18% of known flow | 234 | 2.268
| 16% of known flow | 208 | 1.792
| 14% of known flow | 182 | 1.372
| 12% of known flow | 156 | 1.008
| 10% of known flow | 130 | 0.7
| 8% of known flow | 104 | 0.448
| 6% of known flow | 78 | 0.252
| 4% of known flow | 31.2 | 0.04032
| 2% of known flow | 15.6 | 0.01008
| No Flow | 0 | 0
Design Conditions
| Head Line | 2500 | 70 | Set the flow values in the yellow cells to match the range of the X axis
|  | 0 | 70
| Flow Line | 1300 | 90 | Set the head values in the orange cells to match the range of the Y axis
|  | 1300 | 0
System Curve and Largest Impeller
| Head Line | 2500 | 73.5 | Set the head value in the orange cell to the head value where the design system curve crosses the known impeller size line
|  | 0 | 73.5
| Flow Line | 1330 | 90 | Set the flow value in the yellow cell to the flow value where the design system curve crosses the known impeller size line
|  | 1330 | 0

## Design Impeller from Largest
Step 1 - Estimate the new impeller size
Basis for Estimating the new impeller size
Desired Flow - | 1300 | gpm (design parameter from the design system curve tab inputs)
Known flow - | 1330 | gpm (from where the design system curve crosses the known impeller size curve)
Known impeller size - | 13.5 | inches (from the design system curve tab inputs)
Desired impeller size - | 13.1955 | inches (calculated from the other metrics)
Lable generator - | 13.195 inch at 1,150 rpm
Step 2 - For each point on the known impeller line, calculate the flow for the different impeller size
Basis for Estimating the Design Impeller Line Flow
Known impeller size - | 13.5 | inches
Desired impeller size - | 13.1955 | inches (calculated above)
| 13.500 Impeller Flow, gpm (Known value from digitized curve) | 13.195 Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 9.7744e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 98.7589
| 202.076 | 197.5179
| 301.73 | 294.9241
| 401.384 | 392.3302
| 502.422 | 491.0892
| 602.076 | 588.4953
| 703.114 | 687.2543
| 801.384 | 783.3077
| 903.806 | 883.4194
| 999.308 | 976.7672
| 1101.73 | 1076.8789
| 1201.38 | 1174.2812
| 1302.42 | 1273.0421
| 1402.08 | 1370.4541
| 1501.73 | 1467.8564
| 1600 | 1563.9098
| 1647.06 | 1609.9083
| 1699.65 | 1661.312
| 1791 | 1750.6015
| 1847.75 | 1806.0714
| 1903.11 | 1860.1827
| 1948.79 | 1904.8323
| 2013.84 | 1968.415
Step 3 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 13.500 inch Impeller Flow, gpm (Known value from digitized curve) | 13.195 inch Impeller Flow, gpm (Calculated above) | 13.500 inch Impeller Head, ft.w.c. (Known value from digitized curve) | 13.195 inch Impeller Head, ft.w.c. (From square law)
| 1e-09 | 9.7744e-10 | 83.5283 | 79.8026
| 101.038 | 98.7589 | 83.6257 | 79.8957
| 202.076 | 197.5179 | 83.5283 | 79.8026
| 301.73 | 294.9241 | 83.4308 | 79.7095
| 401.384 | 392.3302 | 83.2359 | 79.5232
| 502.422 | 491.0892 | 82.846 | 79.1507
| 602.076 | 588.4953 | 82.4561 | 78.7782
| 703.114 | 687.2543 | 82.0663 | 78.4058
| 801.384 | 783.3077 | 81.6764 | 78.0333
| 903.806 | 883.4194 | 80.9941 | 77.3814
| 999.308 | 976.7672 | 80.0195 | 76.4503
| 1101.73 | 1076.8789 | 78.3626 | 74.8673
| 1201.38 | 1174.2812 | 76.4133 | 73.005
| 1302.42 | 1273.0421 | 74.0741 | 70.7701
| 1402.08 | 1370.4541 | 71.54 | 68.349
| 1501.73 | 1467.8564 | 68.5185 | 65.4623
| 1600 | 1563.9098 | 64.6199 | 61.7376
| 1647.06 | 1609.9083 | 62.4756 | 59.6889
| 1699.65 | 1661.312 | 60.039 | 57.361
| 1791 | 1750.6015 | 55.1657 | 52.7051
| 1847.75 | 1806.0714 | 51.3645 | 49.0734
| 1903.11 | 1860.1827 | 47.3684 | 45.2556
| 1948.79 | 1904.8323 | 43.8596 | 41.9033
| 2013.84 | 1968.415 | 38.4016 | 36.6887
Step 4 - Plot the results (the cells highlighted in yellow above) on the pump curve

## 75 Pct
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-04-06 06:32
Project Name: | Chiller Plant Model
Project Number:
Engineer: | David
Assumptions
1 | Known flow = | 975 | gpm (manual selection for the desired condition to analyze)
2 | Head or static at known flow = | 70 | ft.w.c. (from square law and design requirements)
3 | Fixed static or open system lift = | 0 | Note 1
4 | System Curve Exponent = | 2 | Note 2
5 | Efficiency = | 83.5% | (From where the system curve intersects the design impeller curve)
6 | Bhp = | 20.6405 | Bhp (calculated)
7 | Largest impeller = | 13.5 | inches
8 | Smallest impeller = | 10 | inches
Note 1 - For closed systems that control for a fixed pressure, enter it here in ft.w.c., otherwise use 0.
Note 2 - The typical value for this is 2, but ASHRAE research indicates that generally, 1.85 - 1.89 may be more appropriate for systems were there are some portions with out fully developed turbulent flow.
| System Curve Points |  |  |  | Click here to go to the data used to plot the digital pump curve set
| Condition | Flow | Pressure |  | Click here to go to the design condition tabs
| 160% of known flow | 1560 | 179.2 |  | Click here to go to the 75% load condition tabs
| 120% of known flow | 1170 | 100.8 |  | Click here to go to the 50% load condition tabs
| Known | 975 | 70 |  | Click here to go to the 25% load condition tabs
| 80% of known flow | 780 | 44.8 |  | Click here to go to the 12.5% load condition tabs
| 60% of known flow | 585 | 25.2 |  | Click here to go to the summary tab
| 40% of known flow | 390 | 11.2
| 30% of known flow | 292.5 | 6.3
| 20% of known flow | 195 | 2.8
| 18% of known flow | 175.5 | 2.268
| 16% of known flow | 156 | 1.792
| 14% of known flow | 136.5 | 1.372
| 12% of known flow | 117 | 1.008
| 10% of known flow | 97.5 | 0.7
| 8% of known flow | 78 | 0.448
| 6% of known flow | 58.5 | 0.252
| 4% of known flow | 23.4 | 0.04032
| 2% of known flow | 11.7 | 0.01008
| No Flow | 0 | 0
New Point
| Head Line | 2500 | 70 | Set the flow values in the yellow cells to match the range of the X axis
|  | 0 | 70
| Flow Line | 975 | 90 | Set the head values in the orange cells to match the range of the Y axis
|  | 975 | 0
System Curve and New Point
| Head Line | 2500 | 75.8 | Read the head value manually from the pump curve where the new system curve intersects the design impeller line and enter it in the orange cell
|  | 0 | 75.8
| Flow Line | 1015 | 90 | Read the flow value manually from the pump curve where the new system curve intersects the design impeller line and enter it manually in the yellow cell
|  | 1015 | 0

## 75 Pct Speed Estimate
Step 1 - Estimate the new impeller speed
Basis for Estimating the new impeller size
Desired Flow - | 975 | gpm (given, from system curve tab)
Known flow - | 1015 | gpm (where the new system curve crosses the full speed impeller line)
Known impeller speed - | 1150 | rpm (Manually entered from manufacturer's pump curve)
"Tweak" value - | 0 | rpm (Manually adjusted to make the speed line intersect the new operating point)
Desired impeller speed - | 1104.6798 | rpm (tweaked from affinity law estimate to intersect the known operating point)
Lable generator - | 13.195 inch impeller at 1,105 rpm from the affinity law
Step 2 - For each point on the known impeller speed line, calculate the flow for the different impeller speed
Basis for Estimating the Design Impeller Line Flow
Known impeller speed - | 1150 | rpm (from manufacturer's pump curve)
Desired impeller speed - | 1104.6798 | rpm (calculated above)
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,105 rpm Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 9.6059e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 97.0562
| 202.076 | 194.1124
| 301.73 | 289.8392
| 401.384 | 385.5659
| 502.422 | 482.6221
| 602.076 | 578.3489
| 703.114 | 675.4051
| 801.384 | 769.8024
| 903.806 | 868.188
| 999.308 | 959.9264
| 1101.73 | 1058.3121
| 1201.38 | 1154.035
| 1302.42 | 1251.0931
| 1402.08 | 1346.8256
| 1501.73 | 1442.5485
| 1600 | 1536.9458
| 1647.06 | 1582.1512
| 1699.65 | 1632.6687
| 1791 | 1720.4187
| 1847.75 | 1774.9323
| 1903.11 | 1828.1106
| 1948.79 | 1871.9904
| 2013.84 | 1934.4768
Step 3 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,105 rpm Impeller Flow, gpm (Calculated above) | 1,150 rpm Impeller Head, ft.w.c. (Known value from previous calculation) | 1,105 rpm Impeller Head, ft.w.c. (From square law)
| 1e-09 | 9.6059e-10 | 83.5283 | 77.0745
| 101.038 | 97.0562 | 83.6257 | 77.1644
| 202.076 | 194.1124 | 83.5283 | 77.0745
| 301.73 | 289.8392 | 83.4308 | 76.9845
| 401.384 | 385.5659 | 83.2359 | 76.8047
| 502.422 | 482.6221 | 82.846 | 76.4449
| 602.076 | 578.3489 | 82.4561 | 76.0852
| 703.114 | 675.4051 | 82.0663 | 75.7255
| 801.384 | 769.8024 | 81.6764 | 75.3657
| 903.806 | 868.188 | 80.9941 | 74.7361
| 999.308 | 959.9264 | 80.0195 | 73.8368
| 1101.73 | 1058.3121 | 78.3626 | 72.3079
| 1201.38 | 1154.035 | 76.4133 | 70.5093
| 1302.42 | 1251.0931 | 74.0741 | 68.3508
| 1402.08 | 1346.8256 | 71.54 | 66.0125
| 1501.73 | 1442.5485 | 68.5185 | 63.2244
| 1600 | 1536.9458 | 64.6199 | 59.6271
| 1647.06 | 1582.1512 | 62.4756 | 57.6484
| 1699.65 | 1632.6687 | 60.039 | 55.4001
| 1791 | 1720.4187 | 55.1657 | 50.9033
| 1847.75 | 1774.9323 | 51.3645 | 47.3958
| 1903.11 | 1828.1106 | 47.3684 | 43.7085
| 1948.79 | 1871.9904 | 43.8596 | 40.4708
| 2013.84 | 1934.4768 | 38.4016 | 35.4345
Step 4 - Plot the results (the cells highlighted in yellow above) on the pump curve

## 75 Pct Speed Estimate Tweak
Step 1 - Estimate the new impeller speed
Basis for Estimating the new impeller size
Desired Flow - | 975 | gpm (given, from system curve tab)
Known flow - | 1015 | gpm (where the new system curve crosses the full speed impeller line)
Known impeller speed - | 1150 | rpm (Manually entered from manufacturer's pump curve)
"Tweak" value - | -24 | rpm (Manually adjusted to make the speed line intersect the new operating point)
Desired impeller speed - | 1080.6798 | rpm (tweaked from affinity law estimate to intersect the known operating point)
Lable generator - | 13.195 inch impeller at 1,081 rpm from the affinity law, adjusted to go through the operating point
Step 2 - For each point on the known impeller speed line, calculate the flow for the different impeller speed
Basis for Estimating the Design Impeller Line Flow
Known impeller speed - | 1150 | rpm (from manufacturer's pump curve)
Desired impeller speed - | 1080.6798 | rpm (calculated above)
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,081 rpm Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 9.3972e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 94.9476
| 202.076 | 189.8952
| 301.73 | 283.5422
| 401.384 | 377.1892
| 502.422 | 472.1368
| 602.076 | 565.7838
| 703.114 | 660.7314
| 801.384 | 753.0778
| 903.806 | 849.326
| 999.308 | 939.0713
| 1101.73 | 1035.3194
| 1201.38 | 1128.9627
| 1302.42 | 1223.9122
| 1402.08 | 1317.5648
| 1501.73 | 1411.2081
| 1600 | 1503.5545
| 1647.06 | 1547.7778
| 1699.65 | 1597.1978
| 1791 | 1683.0413
| 1847.75 | 1736.3705
| 1903.11 | 1788.3935
| 1948.79 | 1831.32
| 2013.84 | 1892.4489
Step 3 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,081 rpm Impeller Flow, gpm (Calculated above) | 1,150 rpm Impeller Head, ft.w.c. (Known value from previous calculation) | 1,081 rpm Impeller Head, ft.w.c. (From square law)
| 1e-09 | 9.3972e-10 | 83.5283 | 73.7619
| 101.038 | 94.9476 | 83.6257 | 73.8479
| 202.076 | 189.8952 | 83.5283 | 73.7619
| 301.73 | 283.5422 | 83.4308 | 73.6758
| 401.384 | 377.1892 | 83.2359 | 73.5037
| 502.422 | 472.1368 | 82.846 | 73.1594
| 602.076 | 565.7838 | 82.4561 | 72.8151
| 703.114 | 660.7314 | 82.0663 | 72.4708
| 801.384 | 753.0778 | 81.6764 | 72.1265
| 903.806 | 849.326 | 80.9941 | 71.524
| 999.308 | 939.0713 | 80.0195 | 70.6633
| 1101.73 | 1035.3194 | 78.3626 | 69.2002
| 1201.38 | 1128.9627 | 76.4133 | 67.4788
| 1302.42 | 1223.9122 | 74.0741 | 65.4131
| 1402.08 | 1317.5648 | 71.54 | 63.1753
| 1501.73 | 1411.2081 | 68.5185 | 60.5071
| 1600 | 1503.5545 | 64.6199 | 57.0643
| 1647.06 | 1547.7778 | 62.4756 | 55.1707
| 1699.65 | 1597.1978 | 60.039 | 53.019
| 1791 | 1683.0413 | 55.1657 | 48.7155
| 1847.75 | 1736.3705 | 51.3645 | 45.3588
| 1903.11 | 1788.3935 | 47.3684 | 41.8299
| 1948.79 | 1831.32 | 43.8596 | 38.7314
| 2013.84 | 1892.4489 | 38.4016 | 33.9116
Step 4 - Plot the results (the cells highlighted in yellow above) on the pump curve

## 50 Pct
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-04-06 06:32
Project Name: | Chiller Plant Model
Project Number:
Engineer: | David
Assumptions
1 | Known flow = | 650 | gpm (manual selection for the desired condition to analyze)
2 | Head or static at known flow = | 70 | ft.w.c. (from square law and design requirements)
3 | Fixed static or open system lift = | 0 | Note 1
4 | System Curve Exponent = | 2 | Note 2
5 | Efficiency = | 72% | (From where the system curve intersects the design impeller curve)
6 | Bhp = | 15.9582 | Bhp (calculated)
7 | Largest impeller = | 13.5 | inches
8 | Smallest impeller = | 10 | inches
Note 1 - For closed systems that control for a fixed pressure, enter it here in ft.w.c., otherwise use 0.
Note 2 - The typical value for this is 2, but ASHRAE research indicates that generally, 1.85 - 1.89 may be more appropriate for systems were there are some portions with out fully developed turbulent flow.
| System Curve Points |  |  |  | Click here to go to the data used to plot the digital pump curve set
| Condition | Flow | Pressure |  | Click here to go to the design condition tabs
| 160% of known flow | 1040 | 179.2 |  | Click here to go to the 75% load condition tabs
| 120% of known flow | 780 | 100.8 |  | Click here to go to the 50% load condition tabs
| Known | 650 | 70 |  | Click here to go to the 25% load condition tabs
| 80% of known flow | 520 | 44.8 |  | Click here to go to the 12.5% load condition tabs
| 60% of known flow | 390 | 25.2 |  | Click here to go to the summary tab
| 40% of known flow | 260 | 11.2
| 30% of known flow | 195 | 6.3
| 20% of known flow | 130 | 2.8
| 18% of known flow | 117 | 2.268
| 16% of known flow | 104 | 1.792
| 14% of known flow | 91 | 1.372
| 12% of known flow | 78 | 1.008
| 10% of known flow | 65 | 0.7
| 8% of known flow | 52 | 0.448
| 6% of known flow | 39 | 0.252
| 4% of known flow | 15.6 | 0.04032
| 2% of known flow | 7.8 | 0.01008
| No Flow | 0 | 0
New Point
| Head Line | 2500 | 70 | Set the flow values in the yellow cells to match the range of the X axis
|  | 0 | 70
| Flow Line | 650 | 90 | Set the head values in the orange cells to match the range of the Y axis
|  | 650 | 0
System Curve and New Point
| Head Line | 2500 | 78 | Read the head value manually from the pump curve where the new system curve intersects the design impeller line and enter it in the orange cell
|  | 0 | 78
| Flow Line | 687 | 90 | Read the flow value manually from the pump curve where the new system curve intersects the design impeller line and enter it manually in the yellow cell
|  | 687 | 0

## 50 Pct Speed Estimate Tweak
Step 1 - Estimate the new impeller speed
Basis for Estimating the new impeller size
Desired Flow - | 650 | gpm (given, from system curve tab)
Known flow - | 687 | gpm (where the new system curve crosses the full speed impeller line)
Known impeller speed - | 1150 | rpm (Manually entered from manufacturer's pump curve)
"Tweak" value - | -25 | rpm (Manually adjusted to make the speed line intersect the new operating point)
Desired impeller speed - | 1063.064 | rpm (tweaked from affinity law estimate to intersect the known operating point)
Lable generator - | 13.195 inch impeller at 1,063 rpm from the affinity law, adjusted to go through the operating point
Step 2 - For each point on the known impeller speed line, calculate the flow for the different impeller speed
Basis for Estimating the Design Impeller Line Flow
Known impeller speed - | 1150 | rpm (from manufacturer's pump curve)
Desired impeller speed - | 1063.064 | rpm (calculated above)
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,063 rpm Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 9.244e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 93.3999
| 202.076 | 186.7998
| 301.73 | 278.9203
| 401.384 | 371.0408
| 502.422 | 464.4407
| 602.076 | 556.5612
| 703.114 | 649.9611
| 801.384 | 740.8022
| 903.806 | 835.4814
| 999.308 | 923.7638
| 1101.73 | 1018.4431
| 1201.38 | 1110.5599
| 1302.42 | 1203.9616
| 1402.08 | 1296.0877
| 1501.73 | 1388.2045
| 1600 | 1479.0456
| 1647.06 | 1522.5481
| 1699.65 | 1571.1624
| 1791 | 1655.6067
| 1847.75 | 1708.0666
| 1903.11 | 1759.2416
| 1948.79 | 1801.4683
| 2013.84 | 1861.6008
Step 3 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,063 rpm Impeller Flow, gpm (Calculated above) | 1,150 rpm Impeller Head, ft.w.c. (Known value from previous calculation) | 1,063 rpm Impeller Head, ft.w.c. (From square law)
| 1e-09 | 9.244e-10 | 83.5283 | 71.3768
| 101.038 | 93.3999 | 83.6257 | 71.46
| 202.076 | 186.7998 | 83.5283 | 71.3768
| 301.73 | 278.9203 | 83.4308 | 71.2934
| 401.384 | 371.0408 | 83.2359 | 71.1269
| 502.422 | 464.4407 | 82.846 | 70.7937
| 602.076 | 556.5612 | 82.4561 | 70.4605
| 703.114 | 649.9611 | 82.0663 | 70.1274
| 801.384 | 740.8022 | 81.6764 | 69.7943
| 903.806 | 835.4814 | 80.9941 | 69.2112
| 999.308 | 923.7638 | 80.0195 | 68.3784
| 1101.73 | 1018.4431 | 78.3626 | 66.9626
| 1201.38 | 1110.5599 | 76.4133 | 65.2968
| 1302.42 | 1203.9616 | 74.0741 | 63.2979
| 1402.08 | 1296.0877 | 71.54 | 61.1325
| 1501.73 | 1388.2045 | 68.5185 | 58.5506
| 1600 | 1479.0456 | 64.6199 | 55.2191
| 1647.06 | 1522.5481 | 62.4756 | 53.3868
| 1699.65 | 1571.1624 | 60.039 | 51.3046
| 1791 | 1655.6067 | 55.1657 | 47.1403
| 1847.75 | 1708.0666 | 51.3645 | 43.8921
| 1903.11 | 1759.2416 | 47.3684 | 40.4773
| 1948.79 | 1801.4683 | 43.8596 | 37.479
| 2013.84 | 1861.6008 | 38.4016 | 32.815
Step 4 - Plot the results (the cells highlighted in yellow above) on the pump curve

## 25 Pct
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-04-06 06:32
Project Name: | Chiller Plant Model
Project Number:
Engineer: | David
Assumptions
1 | Known flow = | 325 | gpm (manual selection for the desired condition to analyze)
2 | Head or static at known flow = | 70 | ft.w.c. (from square law and design requirements)
3 | Fixed static or open system lift = | 0 | Note 1
4 | System Curve Exponent = | 2 | Note 2
5 | Efficiency = | 50% | (From where the system curve intersects the design impeller curve)
6 | Bhp = | 11.4899 | Bhp (calculated)
7 | Largest impeller = | 13.5 | inches
8 | Smallest impeller = | 10 | inches
Note 1 - For closed systems that control for a fixed pressure, enter it here in ft.w.c., otherwise use 0.
Note 2 - The typical value for this is 2, but ASHRAE research indicates that generally, 1.85 - 1.89 may be more appropriate for systems were there are some portions with out fully developed turbulent flow.
| System Curve Points |  |  |  | Click here to go to the data used to plot the digital pump curve set
| Condition | Flow | Pressure |  | Click here to go to the design condition tabs
| 160% of known flow | 520 | 179.2 |  | Click here to go to the 75% load condition tabs
| 120% of known flow | 390 | 100.8 |  | Click here to go to the 50% load condition tabs
| Known | 325 | 70 |  | Click here to go to the 25% load condition tabs
| 80% of known flow | 260 | 44.8 |  | Click here to go to the 12.5% load condition tabs
| 60% of known flow | 195 | 25.2 |  | Click here to go to the summary tab
| 40% of known flow | 130 | 11.2
| 30% of known flow | 97.5 | 6.3
| 20% of known flow | 65 | 2.8
| 18% of known flow | 58.5 | 2.268
| 16% of known flow | 52 | 1.792
| 14% of known flow | 45.5 | 1.372
| 12% of known flow | 39 | 1.008
| 10% of known flow | 32.5 | 0.7
| 8% of known flow | 26 | 0.448
| 6% of known flow | 19.5 | 0.252
| 4% of known flow | 7.8 | 0.04032
| 2% of known flow | 3.9 | 0.01008
| No Flow | 0 | 0
New Point
| Head Line | 2500 | 70 | Set the flow values in the yellow cells to match the range of the X axis
|  | 0 | 70
| Flow Line | 325 | 90 | Set the head values in the orange cells to match the range of the Y axis
|  | 325 | 0
System Curve and New Point
| Head Line | 2500 | 79.6 | Read the head value manually from the pump curve where the new system curve intersects the design impeller line and enter it in the orange cell
|  | 0 | 79.6
| Flow Line | 350 | 90 | Read the flow value manually from the pump curve where the new system curve intersects the design impeller line and enter it manually in the yellow cell
|  | 350 | 0

## 25 Pct Speed Estimate Tweak
Step 1 - Estimate the new impeller speed
Basis for Estimating the new impeller size
Desired Flow - | 325 | gpm (given, from system curve tab)
Known flow - | 350 | gpm (where the new system curve crosses the full speed impeller line)
Known impeller speed - | 1150 | rpm (Manually entered from manufacturer's pump curve)
"Tweak" value - | -13 | rpm (Manually adjusted to make the speed line intersect the new operating point)
Desired impeller speed - | 1054.8571 | rpm (tweaked from affinity law estimate to intersect the known operating point)
Lable generator - | 13.195 inch impeller at 1,055 rpm from the affinity law, adjusted to go through the operating point
Step 2 - For each point on the known impeller speed line, calculate the flow for the different impeller speed
Basis for Estimating the Design Impeller Line Flow
Known impeller speed - | 1150 | rpm (from manufacturer's pump curve)
Desired impeller speed - | 1054.8571 | rpm (calculated above)
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,055 rpm Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 9.1727e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 92.6788
| 202.076 | 185.3577
| 301.73 | 276.767
| 401.384 | 368.1763
| 502.422 | 460.8552
| 602.076 | 552.2645
| 703.114 | 644.9433
| 801.384 | 735.0832
| 903.806 | 829.0315
| 999.308 | 916.6323
| 1101.73 | 1010.5807
| 1201.38 | 1101.9863
| 1302.42 | 1194.667
| 1402.08 | 1286.0818
| 1501.73 | 1377.4875
| 1600 | 1467.6273
| 1647.06 | 1510.7939
| 1699.65 | 1559.033
| 1791 | 1642.8253
| 1847.75 | 1694.8802
| 1903.11 | 1745.6602
| 1948.79 | 1787.5609
| 2013.84 | 1847.2291
Step 3 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,055 rpm Impeller Flow, gpm (Calculated above) | 1,150 rpm Impeller Head, ft.w.c. (Known value from previous calculation) | 1,055 rpm Impeller Head, ft.w.c. (From square law)
| 1e-09 | 9.1727e-10 | 83.5283 | 70.2789
| 101.038 | 92.6788 | 83.6257 | 70.3609
| 202.076 | 185.3577 | 83.5283 | 70.2789
| 301.73 | 276.767 | 83.4308 | 70.1969
| 401.384 | 368.1763 | 83.2359 | 70.0329
| 502.422 | 460.8552 | 82.846 | 69.7049
| 602.076 | 552.2645 | 82.4561 | 69.3768
| 703.114 | 644.9433 | 82.0663 | 69.0489
| 801.384 | 735.0832 | 81.6764 | 68.7208
| 903.806 | 829.0315 | 80.9941 | 68.1467
| 999.308 | 916.6323 | 80.0195 | 67.3267
| 1101.73 | 1010.5807 | 78.3626 | 65.9326
| 1201.38 | 1101.9863 | 76.4133 | 64.2925
| 1302.42 | 1194.667 | 74.0741 | 62.3244
| 1402.08 | 1286.0818 | 71.54 | 60.1922
| 1501.73 | 1377.4875 | 68.5185 | 57.65
| 1600 | 1467.6273 | 64.6199 | 54.3698
| 1647.06 | 1510.7939 | 62.4756 | 52.5657
| 1699.65 | 1559.033 | 60.039 | 50.5155
| 1791 | 1642.8253 | 55.1657 | 46.4153
| 1847.75 | 1694.8802 | 51.3645 | 43.217
| 1903.11 | 1745.6602 | 47.3684 | 39.8548
| 1948.79 | 1787.5609 | 43.8596 | 36.9025
| 2013.84 | 1847.2291 | 38.4016 | 32.3103
Step 4 - Plot the results (the cells highlighted in yellow above) on the pump curve

## 12.5 Pct
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-04-06 06:32
Project Name: | Chiller Plant Model
Project Number:
Engineer: | David
Assumptions
1 | Known flow = | 162.5 | gpm (manual selection for the desired condition to analyze)
2 | Head or static at known flow = | 70 | ft.w.c. (from square law and design requirements)
3 | Fixed static or open system lift = | 0 | Note 1
4 | System Curve Exponent = | 2 | Note 2
5 | Efficiency = | 30% | (From where the system curve intersects the design impeller curve)
6 | Bhp = | 9.5749 | Bhp (calculated)
7 | Largest impeller = | 13.5 | inches
8 | Smallest impeller = | 10 | inches
Note 1 - For closed systems that control for a fixed pressure, enter it here in ft.w.c., otherwise use 0.
Note 2 - The typical value for this is 2, but ASHRAE research indicates that generally, 1.85 - 1.89 may be more appropriate for systems were there are some portions with out fully developed turbulent flow.
| System Curve Points |  |  |  | Click here to go to the data used to plot the digital pump curve set
| Condition | Flow | Pressure |  | Click here to go to the design condition tabs
| 200% of known flow | 325 | 280 |  | Click here to go to the 75% load condition tabs
| 120% of known flow | 195 | 100.8 |  | Click here to go to the 50% load condition tabs
| Known | 162.5 | 70 |  | Click here to go to the 25% load condition tabs
| 80% of known flow | 130 | 44.8 |  | Click here to go to the 12.5% load condition tabs
| 60% of known flow | 97.5 | 25.2 |  | Click here to go to the summary tab
| 40% of known flow | 65 | 11.2
| 30% of known flow | 48.75 | 6.3
| 20% of known flow | 32.5 | 2.8
| 18% of known flow | 29.25 | 2.268
| 16% of known flow | 26 | 1.792
| 14% of known flow | 22.75 | 1.372
| 12% of known flow | 19.5 | 1.008
| 10% of known flow | 16.25 | 0.7
| 8% of known flow | 13 | 0.448
| 6% of known flow | 9.75 | 0.252
| 4% of known flow | 3.9 | 0.04032
| 2% of known flow | 1.95 | 0.01008
| No Flow | 0 | 0
New Point
| Head Line | 2500 | 70 | Set the flow values in the yellow cells to match the range of the X axis
|  | 0 | 70
| Flow Line | 162.5 | 90 | Set the head values in the orange cells to match the range of the Y axis
|  | 162.5 | 0
System Curve and New Point
| Head Line | 2500 | 79.925 | Read the head value manually from the pump curve where the new system curve intersects the design impeller line and enter it in the orange cell
|  | 0 | 79.925
| Flow Line | 175 | 90 | Read the flow value manually from the pump curve where the new system curve intersects the design impeller line and enter it manually in the yellow cell
|  | 175 | 0

## 12.5 Pct Speed Estimate Tweak
Step 1 - Estimate the new impeller speed
Basis for Estimating the new impeller size
Desired Flow - | 162.5 | gpm (given, from system curve tab)
Known flow - | 175 | gpm (where the new system curve crosses the full speed impeller line)
Known impeller speed - | 1150 | rpm (Manually entered from manufacturer's pump curve)
"Tweak" value - | -14 | rpm (Manually adjusted to make the speed line intersect the new operating point)
Desired impeller speed - | 1053.8571 | rpm (tweaked from affinity law estimate to intersect the known operating point)
Lable generator - | 13.195 inch impeller at 1,054 rpm from the affinity law, adjusted to go through the operating point
Step 2 - For each point on the known impeller speed line, calculate the flow for the different impeller speed
Basis for Estimating the Design Impeller Line Flow
Known impeller speed - | 1150 | rpm (from manufacturer's pump curve)
Desired impeller speed - | 1053.8571 | rpm (calculated above)
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,054 rpm Impeller Flow, gpm (Calculated with the affinity law)
| 1e-09 | 9.164e-10 | Make the "0" a really small number to get rid of the "#DIV/0!" error that will otherwise come up in the next step
| 101.038 | 92.591
| 202.076 | 185.1819
| 301.73 | 276.5046
| 401.384 | 367.8273
| 502.422 | 460.4183
| 602.076 | 551.741
| 703.114 | 644.3319
| 801.384 | 734.3863
| 903.806 | 828.2456
| 999.308 | 915.7634
| 1101.73 | 1009.6226
| 1201.38 | 1100.9416
| 1302.42 | 1193.5345
| 1402.08 | 1284.8626
| 1501.73 | 1376.1816
| 1600 | 1466.236
| 1647.06 | 1509.3617
| 1699.65 | 1557.555
| 1791 | 1641.268
| 1847.75 | 1693.2735
| 1903.11 | 1744.0053
| 1948.79 | 1785.8663
| 2013.84 | 1845.478
Step 3 - For each of the new flow rates, calculate the head associated with it using the affinity laws
Basis for Estimating the Design Impeller Line Head
| 1,150 rpm Impeller Flow, gpm (Known value from previous calculation) | 1,054 rpm Impeller Flow, gpm (Calculated above) | 1,150 rpm Impeller Head, ft.w.c. (Known value from previous calculation) | 1,054 rpm Impeller Head, ft.w.c. (From square law)
| 1e-09 | 9.164e-10 | 83.5283 | 70.1458
| 101.038 | 92.591 | 83.6257 | 70.2276
| 202.076 | 185.1819 | 83.5283 | 70.1458
| 301.73 | 276.5046 | 83.4308 | 70.0639
| 401.384 | 367.8273 | 83.2359 | 69.9002
| 502.422 | 460.4183 | 82.846 | 69.5728
| 602.076 | 551.741 | 82.4561 | 69.2453
| 703.114 | 644.3319 | 82.0663 | 68.918
| 801.384 | 734.3863 | 81.6764 | 68.5906
| 903.806 | 828.2456 | 80.9941 | 68.0176
| 999.308 | 915.7634 | 80.0195 | 67.1991
| 1101.73 | 1009.6226 | 78.3626 | 65.8077
| 1201.38 | 1100.9416 | 76.4133 | 64.1707
| 1302.42 | 1193.5345 | 74.0741 | 62.2063
| 1402.08 | 1284.8626 | 71.54 | 60.0782
| 1501.73 | 1376.1816 | 68.5185 | 57.5408
| 1600 | 1466.236 | 64.6199 | 54.2668
| 1647.06 | 1509.3617 | 62.4756 | 52.466
| 1699.65 | 1557.555 | 60.039 | 50.4198
| 1791 | 1641.268 | 55.1657 | 46.3273
| 1847.75 | 1693.2735 | 51.3645 | 43.1351
| 1903.11 | 1744.0053 | 47.3684 | 39.7792
| 1948.79 | 1785.8663 | 43.8596 | 36.8326
| 2013.84 | 1845.478 | 38.4016 | 32.2491
Step 4 - Plot the results (the cells highlighted in yellow above) on the pump curve

## Summary
Click here to go to the data used to plot the digital pump curve set
Click here to go to the design condition tabs
Click here to go to the 75% load condition tabs
Click here to go to the 50% load condition tabs
Click here to go to the 25% load condition tabs
Click here to go to the 12.5% load condition tabs
Click here to go to the summary tab
This example is a special case that looks at what happens if you only make enough pump head to satisfy all of the loads at design condition all of the time. It tends to approach what would happen if you controlled for a fixed pressure at the pump discharge.
Summary
Load Condition | Flow Rate, gpm | Head, ft.w.c | Pump Speed, rpm | Pump Efficiency | Pump Bhp | Motor Efficiency | VFD Efficiency | Projected kW | "Cube Rule" kW | kW vs. Flow2.4 | kW vs. Flow2.0 | kW vs. Flow1.5 | Head vs. Flow2.0
Design | 1300 | 70 | 1150 | 86.9% | 26.444 | 93.72% | 97.94% | 28.8115 | 28.8115 | 28.8115 | 28.8115 | 28.8115 | 70
75% | 975 | 70 | 1080.6798 | 83.5% | 20.6405 | 93.65% | 95.85% | 22.9939 | 12.1548 | 14.4448 | 16.2065 | 18.7136 | 70
50% | 650 | 70 | 1063.064 | 72% | 15.9582 | 93.64% | 94.4% | 18.0539 | 3.6014 | 5.4588 | 7.2029 | 10.1864 | 70
25% | 325 | 70 | 1054.8571 | 50% | 11.4899 | 93.85% | 94.7% | 12.9277 | 0.45018 | 1.0342 | 1.8007 | 3.6014 | 70
12.5% | 162.5 | 70 | 1053.8571 | 30% | 9.5749 | 93.44% | 94.53% | 10.8398 | 0.056272 | 0.19595 | 0.45018 | 1.2733 | 70

## Motor Eff Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2016-07-29 14:51
Project Name: | None
Project Number: | None
Engineer: | David
Assumptions
1 | This spreadsheet uses efficiency data for a US Motors 25 hp motor to generate efficiency curves for other motor sizes based on an assumption that the the curve shapes are similar and proportional to the nameplate motor efficiency
2 | Nameplate efficiency from MotorMaster for NEMA Premium Efficiency Motor
3 | ????
4 | ????
5 | ????
6 | ????
7 | ????
8 | ????
Plot Digitizer Data
| Horsepower | Efficiency - Plot Digitizer | Curve From 25 hp Efficiency Equations | 30 hp Motor Load | Projected 30 hp NEMA Premium Efficiency Curve | Curve From 30 hp Efficiency Equations | 40 hp Motor Load | Projected 40 hp NEMA Premium Efficiency Curve | Curve From 40 hp Efficiency Equations | 75 hp Motor Load | Projected 75 hp NEMA Premium Efficiency Curve | Curve From 75 hp Efficiency Equations | 100 hp Motor Load | Projected 100 hp NEMA Premium Efficiency Curve | Curve From 100 hp Efficiency Equations
|  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation
| 0.1255 | 20.09% | 19.77% | 0.1506 | 19.8% | 19.8% | 0.2008 | 19.8% | 19.8% | 0.37651 | 19.99% | 19.99% | 0.50201 | 20.08% | 20.08%
| 0.31376 | 38.43% | 39.12% | 0.37651 | 39.19% | 39.19% | 0.50201 | 39.19% | 39.19% | 0.94127 | 39.56% | 39.56% | 1.255 | 39.73% | 39.73%
| 0.53338 | 49.54% | 50.32% | 0.64006 | 50.42% | 50.42% | 0.85341 | 50.42% | 50.42% | 1.6002 | 50.9% | 50.9% | 2.1335 | 51.11% | 51.11%
| 0.87851 | 61.76% | 60.86% | 1.0542 | 60.97% | 60.97% | 1.4056 | 60.97% | 60.97% | 2.6355 | 61.56% | 61.56% | 3.5141 | 61.82% | 61.82%
| 1.3178 | 70.65% | 69.42% | 1.5813 | 69.55% | 69.55% | 2.1084 | 69.55% | 69.55% | 3.9533 | 70.22% | 70.22% | 5.2711 | 70.51% | 70.51%
| 1.757 | 75.65% | 75.5% | 2.1084 | 75.64% | 75.64% | 2.8112 | 75.64% | 75.64% | 5.2711 | 76.36% | 76.36% | 7.0281 | 76.69% | 76.69%
| 2.259 | 79.68% | 80.8% | 2.7108 | 80.96% | 80.96% | 3.6145 | 80.96% | 80.96% | 6.7771 | 81.73% | 81.73% | 9.0362 | 82.08% | 82.08%
| 3.0748 | 83.7% | 83.36% | 3.6898 | 83.51% | 83.65% | 4.9197 | 83.51% | 83.65% | 9.2244 | 84.31% | 84.45% | 12.2992 | 84.67% | 87.46%
| 3.8592 | 86.34% | 85.71% | 4.631 | 85.87% | 85.95% | 6.1747 | 85.87% | 85.95% | 11.5776 | 86.69% | 86.77% | 15.4368 | 87.06% | 89.67%
| 5.1142 | 89.12% | 88.66% | 6.1371 | 88.83% | 88.84% | 8.1827 | 88.83% | 88.84% | 15.3426 | 89.68% | 89.69% | 20.4568 | 90.05% | 92.26%
| 6.432 | 90.65% | 90.86% | 7.7184 | 91.03% | 91% | 10.2912 | 91.03% | 91% | 19.2959 | 91.9% | 91.87% | 25.7279 | 92.29% | 93.97%
| 7.8125 | 92.04% | 92.38% | 9.375 | 92.55% | 92.5% | 12.5 | 92.55% | 92.5% | 23.4375 | 93.43% | 93.39% | 31.25 | 93.83% | 94.95%
| 10.0088 | 93.15% | 93.59% | 12.0106 | 93.76% | 93.73% | 16.0141 | 93.76% | 93.73% | 30.0264 | 94.66% | 94.62% | 40.0352 | 95.06% | 95.41%
| 13.8052 | 93.84% | 93.82% | 16.5662 | 94% | 94.01% | 22.0883 | 94% | 94.01% | 41.4156 | 94.89% | 94.91% | 55.2208 | 95.29% | 95.08%
| 16.5663 | 93.98% | 93.59% | 19.8796 | 93.77% | 93.81% | 26.5061 | 93.77% | 93.81% | 49.6989 | 94.67% | 94.7% | 66.2652 | 95.07% | 95.05%
| 21.1471 | 93.84% | 93.69% | 25.3765 | 93.87% | 93.88% | 33.8354 | 93.87% | 93.88% | 63.4413 | 94.77% | 94.78% | 84.5884 | 95.17% | 95.49%
| 24.6298 | 93.56% | 93.93% | 29.5558 | 94.11% | 94.08% | 39.4077 | 94.11% | 94.08% | 73.8894 | 95.01% | 94.98% | 98.5192 | 95.41% | 94.04%
| 28.6772 | 92.73% | 92.61% | 34.4126 | 92.78% | 92.8% | 45.8835 | 92.78% | 92.8% | 86.0316 | 93.67% | 93.68% | 114.7088 | 94.07% | 85.01%
|  | Nameplate Horsepower - | 25 |  | 30 |  |  | 40 |  |  | 75 |  |  | 100
|  | Namplate Efficiency - | 93.92% |  | 94.1% |  |  | 94.1% |  |  | 95% |  |  | 95.4%
| 25 hp Motor Equations | y = 0.2111824658028150ln(x) + 0.6359480527478800
| Back to Top | y = -0.00000272882243596700x4 + 0.00020012279554159800x3 - 0.00530280440572924000x2 + 0.05994807399403190000x + 0.69380575105737600000
| 30 hp Motor Equations | y = 0.2115810603234930ln(x) + 0.5985725790998000
| Back to Top | y = -0.00000125333486590551x4 + 0.00011071157367939200x3 - 0.00354093526504893000x2 + 0.04842508461609080000x + 0.70072077798516200000
| 40 hp Motor Equations | y = 0.2115810603234930ln(x) + 0.5377045011743920
| Back to Top | y = -0.00000039656298491363x4 + 0.00004670644514582700x3 - 0.00199177608658508000x2 + 0.03631881346200920000x + 0.70072077798588600000
| 75 hp Motor Equations | y = 0.2136046836422090ln(x) + 0.4085735109043710
| Back to Top | y = -0.00000003239224648108x4 + 0.00000715330890507886x3 - 0.00057196828935814500x2 + 0.01955529453145500000x + 0.70742267703065800000
| 100 hp Motor Equations | y = 0.2145040717838600ln(x) + 0.3485848445038420
| Back to Top | y = -0.00000001977357647103x4 + 0.00000490324034986658x3 - 0.00043734117790208300x2 + 0.01655560495725840000x + 0.72842425147362200000

## VFD Data >= 20 hp
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2016-07-29 14:51
Project Name: | None
Project Number: | None
Engineer: | David
Assumptions
1 | This spreadsheet uses efficiency data for a Safetronics 20 hp VFD to generate efficiency curves for other VFD sizes based on an assumption that the the curve shapes are similar and proportional to the nameplate VFD efficiency. It produces fairly accurate results relative to the DOE data for mpst sizes above 20 hp. In fact, for most sizes about 20 hp, the efficiencis are vitrually identical above about 42% rated load. For less than 20 hp, use the tab for 10 hp and less. The projections are off the most at the 1.6% and 12.5% load conditions,understating efficiency by3% and 1.9% respectsively for the 40 hp projection. Most of the time, minimum speed restrictions will prevent HVAC system operation at these conditons.
2 | Nameplate efficiency from Safetronics Data published in the referenced DOE tip sheet on VFD efficiency
3
4
5
6
7
8
| Horsepower | Efficiency - Safetronics Data | Curve From 20 hp Efficiency Equations | 25 hp VFD Load | Projected 25 hp VFD Efficiency Curve | Curve From 25 hp Efficiency Equations | 30 hp VFD Load | Projected 30 hp VFD Efficiency Curve | Curve From 30 hp Efficiency Equations | 40 hp VFD Load | Projected 40 hp VFD Efficiency Curve | Curve From 40 hp Efficiency Equations | 75 hp VFD Load | Projected 75 hp VFD Efficiency Curve | Curve From 75 hp Efficiency Equations | 100 hp VFD Load | Projected 100 hp VFD Efficiency Curve | Curve From 100 hp Efficiency Equations
|  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation |  |  | Link to Equation
| 0.32 | 47% | 47% | 0.4 | 47% | 47% | 0.48 | 47% | 47% | 0.64 | 47% | 47% | 1.2 | 47% | 47% | 1.6 | 47% | 47%
| 2.5 | 86% | 86.06% | 3.125 | 86.06% | 84.14% | 3.75 | 84.14% | 84.15% | 5 | 86.06% | 86.06% | 9.375 | 86.06% | 86.06% | 12.5 | 86.06% | 86.06%
| 5 | 93% | 92.78% | 6.25 | 92.78% | 92.78% | 7.5 | 92.78% | 92.74% | 10 | 92.78% | 92.78% | 18.75 | 92.78% | 92.78% | 25 | 92.78% | 92.78%
| 8.4 | 94% | 94.57% | 10.5 | 94.57% | 94.57% | 12.6 | 94.57% | 94.68% | 16.8 | 94.57% | 94.57% | 31.5 | 94.57% | 94.57% | 42 | 94.57% | 94.57%
| 10 | 95% | 94.53% | 12.5 | 94.53% | 94.53% | 15 | 94.53% | 94.44% | 20 | 94.53% | 94.53% | 37.5 | 94.53% | 94.53% | 50 | 94.53% | 94.53%
| 15 | 96% | 96.07% | 18.75 | 96.07% | 96.07% | 22.5 | 96.07% | 96.08% | 30 | 96.07% | 96.07% | 56.25 | 96.07% | 96.07% | 75 | 96.07% | 96.07%
| 20 | 97% | 96.99% | 25 | 96.99% | 96.99% | 30 | 96.99% | 96.99% | 40 | 96.99% | 96.99% | 75 | 96.99% | 96.99% | 100 | 96.99% | 96.99%
|  | Rated Horsepower - | 20 |  | 25 |  |  | 30 |  |  | 40 |  |  | 75 |  |  | 100
|  | Rated Efficiency - | 97% |  | 97% |  |  | 97% |  |  | 97% |  |  | 97% |  |  | 97%
| 20 hp VFD Equations | y = 0.1788990825688070x + 0.4127522935779820
| Back to Top | y = -0.00001436037018445750x4 + 0.00071268036973309900x3 - 0.01244805814563230000x2 + 0.09243085290103550000x + 0.69673004683703800000
| 25 hp VFD Equations | y = 0.1433326585307060x + 0.4126669365877180
| Back to Top | y = -0.00000588200762753621x4 + 0.00036489234930193300x3 - 0.00796675721317327000x2 + 0.07394468232088740000x + 0.69673004683416500000
| 30 hp VFD Equations | y = 0.1135902151463750x + 0.4154766967297400
| Back to Top | y = -0.00000380965434349997x4 + 0.00028312423935715800x3 - 0.00738946953923258000x2 + 0.08116549615999030000x + 0.62691382111474400000
| 40 hp VFD Equations | y = 0.0895829115816913x + 0.4126669365877180
| Back to Top | y = -0.00000089752313652599x4 + 0.00008908504621630770x3 - 0.00311201453639731000x2 + 0.04621542645027710000x + 0.69673004683940300000
| 75 hp VFD Equations | y = 0.0477775528435687x + 0.4126669365877180
| Back to Top | y = -0.00000007261737811830x4 + 0.00001351453145572600x3 - 0.00088519524591471800x2 + 0.02464822744039140000x + 0.69673004683638800000
| 100 hp VFD Equations | y = 0.0358331646326765x + 0.4126669365877180
| Back to Top | y = -0.00000002297659229506x4 + 0.00000570144295784271x3 - 0.00049792232582333000x2 + 0.01848617058022180000x + 0.69673004683416500000
| Safetronics Data | DOE Drive Efficiencyh Tip Sheet
Load | 1.6% | 12.5% | 25% | 42% | 50% | 75% |  |  |  | 100%
hp | 0.32 | 2.5 | 5 | 8.4 | 10 | 15 |  |  |  | 20
20 | 47% | 86% | 93% | 94% | 95% | 96% |  |  |  | 97%