## Slide 1: Affinity Laws
David Sellers; Facility Dynamics Engineering
Senior Engineer

## Slide 2: Parallel Pumps
Increasing Flow
Increasing Head
If both pumps are operating at the same speed and one fails, the operating point shifts down the system curve to the point where the single pump curve crosses it; typically more than 50% of the original flow but at less head
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 3
Assume the pumps are 100% redundant
    What should the logic be, specifically, to operate the pumps on a lead/lag basis?

## Slide 4
Assume the pumps are 100% redundant
    Is there any problem with running one pump and starting the other pump if a failure is detected?

## Slide 5
Assume the pumps are 100% redundant
    Will running two pumps at reduced speed save energy relative to running one pump at full speed?

## Slide 6: One Pump Operating Point
Single Pump Operating Point
2,000 gpm
55 ft.w.c.
12.5 inch impeller
1,150 rpm
84% efficiency
33.1 bhp

## Slide 7: Two Pumps Doing What One Could Do Each Pump Moves Half the Flow at the Design Head
Single Pump Operating Point
1,000 gpm
55 ft.w.c.
12.5 inch impeller
1,070 rpm
70% efficiency
19.8 bhp

## Slide 8: Two Pumps Doing What One Could Do Each Pump Moves Half the Flow at the Design Head
Both Pumps Operating Together
2,000 gpm
55 ft.w.c.
12.5 inch impeller
1,070 rpm
70% efficiency
39.6 bhp

## Slide 9: Two Pumps Doing What One Could Do Each Pump Moves Half the Flow at the Design Head
Both Pumps Operating Together
2,000 gpm
55 ft.w.c.
12.5 inch impeller
1,070 rpm
70% efficiency
39.6 bhp (vs. 33.1)

## Slide 10: The Motor Efficiency Changed
33.1 bhp
19.8 bhp

## Slide 11: The Drive Efficiency Changed

## Slide 12: The Fluid Mechanics Changed
One Pump

## Slide 13: The Fluid Mechanics Changed
One Pump

## Slide 14: The Bottom Line You’re Still Doing the Same Amount of Work
But probably not as efficiently

## Slide 15: What About Running Two Tower Fans at Half Speed vs. One at Full Speed?

## Slide 16: Same Question for These Towers?

## Slide 17: Same Question for These Towers?

## Slide 18: Resources
The slides that follow this look at the topic a different way
https://www.av8rdas.com/affinity-laws.html#Wrong
https://www.av8rdas.com/ashrae---engineers-notebook.html#NPlus1

## Slide 19: The Affinity Laws and Pump Energy
When They Can and Can’t Be Used to Predict Energy Savings and Why

## Slide 20: Applying the Affinity Laws To Predict Performance
Approximate relationships
  In most practical applications, the pump impeller is trimmed
  Other dimensions do not change in proportion to the impeller changes
    Leakage losses impacted
    Hydraulic losses impacted
Notes: 900 50.40
750 35.00
500 15.56
250 1.73
0 0.00

## Slide 21: Applying the Affinity Laws To Predict Performance
The affinity laws assume geometric similarity
Proportional relationship between impeller and casing dimensions
Pump drawing courtesy of Bell and Gossett
Notes: 900 50.40
750 35.00
500 15.56
250 1.73
0 0.00

## Slide 22: Applying the Affinity Laws To Predict Performance
Changing the impeller outside diameter with out changing the eye diameter and casing size is different
Pump drawing courtesy of Bell and Gossett
Affinity Law Predictions
Notes: 900 50.40
750 35.00
500 15.56
250 1.73
0 0.00

## Slide 23: Applying the Affinity Laws To Predict Performance
Changing the impeller outside diameter with out changing the eye diameter and casing size is different
Pump drawing courtesy of Bell and Gossett
Actual performance based on testing
Notes: 900 50.40
750 35.00
500 15.56
250 1.73
0 0.00

## Slide 24: Applying the Affinity Laws To Predict Performance
Changing the impeller outside diameter with out changing the eye diameter and casing size is different
Pump drawing courtesy of Bell and Gossett
The effect is most pronounced with smaller pumps and large trims
Notes: 900 50.40
750 35.00
500 15.56
250 1.73
0 0.00

## Slide 25: Parallel Pumps and Affinity Laws
The pump affinity laws say that horse power varies as the cube of the flow rate.
HPNew = HPOld x (FlowNew/FlowOld)3
Will two pumps in parallel use 1/8th (1/2 x 1/2 x 1/2) of the power required by running only one of the pumps to produce the same flow rate and head?

## Slide 26: System 1: Two Independent Fully Redundant Circuits

## Slide 27: System 2: Shared Circuit, Redundant Pumps

## Slide 28: System 1: Head Loss Calculation One Pump Provides All Flow
One circuit has loss as calculated
One circuit is inactive

## Slide 29: System 1: One Pump Provides All Flow
Two redundant piping circuits
  Significant first cost penalty
  Most immune to failure of any component

## Slide 30: Summary

## Slide 31: System 1: Head Loss Calculation Each Pump Provides 50% of Flow
Both circuits have losses as calculated
Both circuits are active
Losses follow square law
Lift (elevation change) does not vary with flow rate
Was 8 ft.w.c. at 800 gpm

## Slide 32: System 1: Each Pump Provides 50% of Flow
Two redundant piping circuits
  Significant first cost penalty
  Most immune to failure of any component
  Approaches the “cube rule” but not quite due to the constant head associated with lift

## Slide 33: Option 1: Operating Mode B – Two pumps run at reduced speed
Two redundant piping circuits
  Significant first cost penalty
  Most immune to failure of any component
  Approaches the “cube rule” but not quite due to the constant head associated with lift

## Slide 34: Summary
Cube rule predicts 1.9 bhp per pump or 3.8 bhp total

## Slide 35: System 2: Shared Circuit, Redundant Pumps

## Slide 36: System 2 versus System 1 Shared Circuit versus Independent Circuit
Shaded piping is the piping that sees 400 gpm with two pumps running at 400 gpm and thus sees a reduction in head that is proportional to the square of the reduction in flow
Notes: 5.47 8.47

## Slide 37: System 2: Head Loss Calculation One Pump Provides All Flow
Losses increase slightly compared to System 1 due to tees and extra elbows

## Slide 38: Option 2: Operating Mode A – One pump runs at full speed
One common circuit
  Minimizes first cost penalty
  Immune to failure of a pump
  Not immune to a piping failure

## Slide 39: Summary

## Slide 40: System 2: Head Loss Calculation Each Pump Provides 50% of Flow
Only a small portion of the system sees a reduction in flow
Losses in common pipe do not change

## Slide 41: Option 2: Operating Mode B – Two pumps run at 50% speed
One common circuit
  Minimizes first cost penalty
  Immune to failure of a pump
  Not immune to a piping failure
  Some, but not all of the piping circuit sees a 50% reduction in flow

## Slide 42: Option 2: Operating Mode B – Two pumps run at reduced speed
One common circuit
  Minimizes first cost penalty
  Immune to failure of a pump
  Not immune to a piping failure
  Some, but not all of the piping circuit sees a 50% reduction in flow

## Slide 43: Option 2: Operating Mode B – Two pumps run at reduced speed
One common circuit
  Minimizes first cost penalty
  Immune to failure of a pump
  Not immune to a piping failure
  Some, but not all of the piping circuit sees a 50% reduction in flow

## Slide 44: Summary

## Slide 45: System 2: Shared Circuit, Non-redundant pumps
One common circuit
  Lowest first cost penalty
    Smaller pump
    Smaller motor
    Smaller electrical service
  Not immune to pump or piping failure
  Better than 50% redundant
Each pump sized for 50% of the required flow at the required head

## Slide 46: System 2 : Shared Circuit, Non-redundant pumps
One common circuit
  Lowest first cost penalty
    Smaller pump
    Smaller motor
    Smaller electrical service
  Not immune to pump or piping failure
  Better than 50% redundant

## Slide 47: Summary

## Slide 48: The Bottom Lines
The cube rule can not be applied directly to parallel pumps running at 50% speed if the pumps share a common piping circuit
Even if the pumps have independent circuits, any lift due to an elevation change in an open system (and pump energy associated with it) will not follow the cube rule

## Slide 49: The Bottom Lines
Parallel pumps sharing a common piping circuit will approach the performance predicted by the cube rule if the amount of shared piping is small relative to the amount of piping associated with each pump
Parallel pumps sharing a common piping circuit will approach the performance predicted by the cube rule if the pressure loss in the common circuit is insignificant relative to the losses in the piping serving each pump