## Slide 1: 2020 RCx Academy Week 4 Air-Side Systems
3 June 2020

## Slide 2: A Few References That Will Come Up
Information about COVID 19 and HVAC systems
https://av8rdas.wordpress.com/2020/05/30/taylor-engineerings-covid-19-white-paper/
Information about system effect
https://av8rdas.wordpress.com/2014/10/02/system-effectdealing-with-the-point-where-the-fan-meets-the-duct/
Information about filtration opportunities
https://www.av8rdas.com/ncbc.html#2015
Mixed air calculations spreadsheet
https://www.av8rdas.com/mixed-air-calculations.html
Economizer evaluation checklist
https://www.av8rdas.com/economizer-evaluation-checklist.html

## Slide 3: A Few References That Will Come Up
Economizer Stratification Video
https://www.av8rdas.com/economizer-stratification.html
Economizer Stratification Blog Post
https://av8rdas.wordpress.com/2013/01/17/retrocommissioning-findings-economizer-mixed-air-plenum-stratificationoverview/
Pacific Energy Center Economizers; Design, Performance and Commissioning Issues Class Materials
https://www.av8rdas.com/pacific-energy-center-design-performance-and-commissioning-issues-classes.html#Economizers
Pacific Energy Center Fans, Ducts and AHUs; Design, Performance and Commissioning Issues Class Materials
https://www.av8rdas.com/pacific-energy-center-design-performance-and-commissioning-issues-classes.html#Fans

## Slide 4: Taking a Closer Look at the Ball Room AHU
Some Floor Plans to Help You Stay Oriented

## Slide 5: AHU Overview

## Slide 6: AHU System Overview

## Slide 7: AHU System Overview

## Slide 8: Ball Room Overview

## Slide 9: Mechanical Room Plan View

## Slide 10: Mechanical Room Plan View – AHU Interior Exposed

## Slide 11
A Bit About Dampers Featuring
Parallel and Opposed Blade Action

## Slide 12: Damper Parts
Parallel Blade Damper
Frame
Axles or Shafts
Blades
Seals

## Slide 13: A Conventional, Flat Plate Blade Cross-Section

## Slide 14: Greenheck’s Airfoil Blade Cross-Section

## Slide 15: Seal Details
Blade seals
Jamb Seal

## Slide 16: Parallel vs. Opposed Blade Dampers
Parallel Blade Damper
Opposed Blade Damper

## Slide 17: Dampers Need to be Sized for Modulating Control
Characteristics vary with damper design
Rules of thumb
  Pressure significant relative to the system
  Target face velocity of 1,500 to 2,500 fpm will usually work
  Air flow velocity conversions count in the over-all pressure loss

## Slide 18: Opposed Blade Characteristics are Different from Parallel Blade Characteristics

## Slide 19: Face Velocities of 1,500 – 2,500 fpm Will Generally Get You in the Range of a Linear Flow vs. Bade Rotation Curve

## Slide 20
Thanks For Watching!
The End

## Slide 21: Taking a Closer Look at an Economizer
Some Floor Plans to Help You Stay Oriented

## Slide 22: Overview

## Slide 23: Plan View

## Slide 24: A Break and an Exercise
Given:
The economizer evaluation checklist
The images that follow
The maximum face velocity rule of thumb;
  Face velocities through filters and coils are generally held between 350 and 500 feet per minute to minimize the potential for blowing water off a condensing cooling coil and to manage fan energy
The damper face velocity rule of thumb:
  Damper face velocities probably need to be in the 1,500 to 2,500 fpm range at design flow to provide a semi-linear control characteristic
Evaluate the economizer in the Le Conte AHU
How well do you think it mixes?
How linear to you think the flow vs. pressure drop relationship is as the dampers stroke?
Is the sensor located in a good position to control the dampers?
Etc.

## Slide 25: Mixed Air Plenum Overview

## Slide 26: Outdoor Air and Return Air Dampers

## Slide 27: A Close-up of the Return Dampers

## Slide 28: A Even Closer-upper of the Return Dampers

## Slide 29: The Filter Bank

## Slide 30: A Close-up of the Filters

## Slide 31: Looking Through the Filter Bank with No Filters

## Slide 32: The Fan Discharge

## Slide 34: A Temperature Sensor

## Slide 35: The Temperature Sensor from a Different Angle

## Slide 36: Indicators of Potential Economizer Issues
Damper sizes are very different (outdoor air vs. return air); thus, they will have different characteristics
  The resistance to flow of the outdoor air damper on 100% outdoor air will likely be less than the resistance to flow or the return air damper on 100% return air
  Assuming the system does not have a large minimum outdoor air percentage and that it has a constant speed fan, as you drive to 100% OA, the fan will run out its curve and move more air than necessary (or on 100% RA, it will move less air than necessary)
No apparent independent minimum outdoor air regulation method
Damper sizing check indicates the outdoor air damper is oversized (next slide)
Single point sensor after the fan will still see stratified air due to the configuration of the fan wheel and the orientation of the fan relative to the stratification
Blade seals are mostly missing

## Slide 37: Damper Sizing Check

## Slide 38: The Office Hours Challenge
Given:
The images that follow
The maximum face velocity rule of thumb;
  Face velocities through filters and coils are generally held between 350 and 500 feet per minute to minimize the potential for blowing water off a condensing cooling coil and to manage fan energy
The formulas that follow
Estimate
The load on the motor
The system static pressure

## Slide 39: The Motor Nameplate

## Slide 40: The Motor Speed

## Slide 41: Filter Bank

## Slide 42: Filter Detail

## Slide 43: The Relationship Between Slip and Motor Load

## Slide 44: The Relationship Between Slip and Motor Load