## Slide 1: Existing Building Commissioning Workshop: Series 17, November 5, 2021
Applied System Diagrams
David Sellers
Senior Engineer, Facility Dynamics Engineering
Presented By:

## Slide 2: Field Verifying a Chilled Water System Diagram

## Slide 3: Field Verifying a Chilled Water System Diagram

## Slide 4: Field Verifying a Chilled Water System

## Slide 5: The Simplified System Diagram
Ch1
Pm
Ch2
Pm
Pm
Pm
VF1
AHU8
AHU9
AHU10
AHU1
AHU7
South FC Riser 1A
South FC Riser 8A
North FC Riser 8D
North FC Riser 1D
AHU5
AHU6
AHU2
AHU3
AHU4
A
B
C
D
MATCH LINE
See Below
A
B
C
D
MATCH LINE
See Above
See Sheet 11
See Sheets 7 - 10
See Sheets 3 - 6
See Sheet 2
See Sheet 1

## Slide 6: The Detailed Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 2
SD
TDV
Chiller 1
SD
TDV
SD
TDV
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1
Developed from the mechanical drawings and submittals
Needs to be field verified

## Slide 7
Match Line – See Sheet 1
A
B
Match Line – See Sheet 3
C
D
73.7 gpm from 42.0°F to 54°F, 9.3 ft.w.c. Δ p, 36.9 tons
157.2 gpm from 42.0°F to 54°F, 9.6 ft.w.c. Δ p, 78.6 tons
43.9 gpm from 42.0°F to 54°F, 7.8 ft.w.c. Δ p, 21.9 tons; bypass balanced for 5 gpm in full bypass.
AHU8 Cafe
AHU9 Rest/Lng
AHU10 Kitchen
141 gpm from 42.0°F to 54°F, 8.6 ft.w.c. Δ p, 42.2 tons
57.9 gpm from 42.0°F to 54°F, 3.1 ft.w.c. Δ p, 29 tons
AHU1 Admin/Lby
AHU7 Laundry
Hijend Hotel CHW System Diagram
Sheet 2

## Slide 8
Match Line – See Sheet 2
C
D
1st Floor (Typical through Floor 23)
Fan Coil Riser 1.5 A, North Face
62 gpm at 42°EWT, LWT varies, 19.1 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
West FCU
24th Floor
West FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 2.5 A, North Face
125.4 gpm at 42°EWT, LWT varies, 34.9 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 4
E
H
G
F
Hijend Hotel CHW System Diagram
Sheet 3

## Slide 9
Match Line – See Sheet 3
1st Floor (Typical through Floor 24)
Fan Coil Riser 3.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 4.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 5
I
L
K
J
E
H
G
F
Hijend Hotel CHW System Diagram
Sheet 4

## Slide 10
Match Line – See Sheet 4
1st Floor (Typical through Floor 24)
Fan Coil Riser 5.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; ; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 6.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 6
M
P
O
N
I
L
K
J
Hijend Hotel CHW System Diagram
Sheet 5

## Slide 11
Match Line – See Sheet 5
1st Floor (Typical through Floor 24)
Fan Coil Riser 7.5 A, North Face
125.4 gpm at 42°EWT, LWT varies, 34.9 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
1st Floor (Typical through Floor 23)
Fan Coil Riser 8.5 A, North Face
121.5 gpm at 42°EWT, LWT varies, 35.5 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
East FCU
Match Line – See Sheet 7
Q
T
S
R
M
P
O
N
Hijend Hotel CHW System Diagram
Sheet 6

## Slide 12
Match Line – See Sheet 6
1st Floor (Typical through Floor 23)
Fan Coil Riser 8.5 D, South Face
90.6 gpm at 42°EWT, LWT varies, 30.6 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 7.5 D, South Face
187.6 gpm at 42°EWT, LWT varies, 63.4 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 8
U
X
W
V
Q
T
S
R
Hijend Hotel CHW System Diagram
Sheet 7

## Slide 13
Match Line – See Sheet 7
1st Floor (Typical through Floor 24)
Fan Coil Riser 6.5 D, South Face
189.5 gpm at 42°EWT, LWT varies, 64.0 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 5.5 D, South Face
94.7 gpm at 42°EWT, LWT varies, 32 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
25th Floor
East FCU
Match Line – See Sheet 9
Y
B
A
Z
U
X
W
V
Hijend Hotel CHW System Diagram
Sheet 8

## Slide 14
Match Line – See Sheet 8
1st Floor (Typical through Floor 24)
Fan Coil Riser 4.5 D, South Face
189.5 gpm at 42°EWT, LWT varies, 64.0 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 10
Y
B
A
Z
U
X
W
V
1st Floor (Typical through Floor 24)
Fan Coil Riser 3.5 D, South Face
185.4 gpm at 42°EWT, LWT varies, 62.6 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
East FCU
Hijend Hotel CHW System Diagram
Sheet 9

## Slide 15
Fan Coil Riser 1.5 D, South Face
467.4 gpm at 42°EWT, LWT varies, 218.3 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
Match Line – See Sheet 9
1st Floor (Typical through Floor 23)
Fan Coil Riser 2.5 D, South Face
181.2 gpm at 42°EWT, LWT varies, 61.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
East FCU
Match Line – See Sheet 11
Y
Z
U
X
W
V
1st Floor
West FCU (Typical through 24th floor)
25th Floor
West FCU
186.3 gpm from 42.0°F to 54°F, 6.9 ft.w.c. Δ p, 91.2 tons (Typical of each MAU)
AHU5 Corr. MAU
AHU6 Corr.MAU
Roof Level
Hijend Hotel CHW System Diagram
Sheet 10

## Slide 16: Cooling Coil Schedule

## Slide 17: Cooling Coil Schedule

## Slide 18: Break Out 1
Using the model of the plant or the video at this link or both …
https://tinyurl.com/Plantv442021-10-28
… answer the following questions
Are the chillers identical?
What is the basis for your conclusion?
How do the chiller run times and starts compare?
What does that tell you if anything?

## Slide 19: Discussion

## Slide 20: Break Out 2
Using the model of the plant or the video at this link or both …
https://tinyurl.com/Plantv442021-10-28
… field verify the portion of the CHW system diagram contained in the plant
Does the field verified diagram match the diagram developed from the mechanical drawings?

## Slide 21: Discussion

## Slide 22: Break Out 3
Using the model of the chilled water system, field verify the details of the fan coil unit piping
Does the actual fan coil piping match the system diagram developed from the mechanical drawings?
If there are differences, what are they?
If there are differences, could they impact the way the central plant operates and if so, how?
(Pay particular attention to scenes 5, 6, and 7)

## Slide 23: Discussion

## Slide 24: Break Out 4
Using the two system diagrams that follow (Design Intent vs. As Installed), assess the entering water temperatures to the chillers with:
1,800 gpm flowing in the distribution loop
42°F supply to the distribution loop
54°F water returning from the distribution loop
Questions:
Does the difference between the design intent and as installed piping configuration make a difference?
Do features of the chillers play into this?

## Slide 25: Design Intent System Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 2
SD
TDV
Chiller 1
SD
TDV
SD
TDV
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1

## Slide 26: As Installed System Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 2
SD
TDV
Chiller 1
SD
TDV
SD
TDV
As Installed
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1

## Slide 27: Discussion

## Slide 28: Scoping an AHU and Developing a Monitoring Plan

## Slide 29: Break Out 5
Using the system diagram that follows along with the model of the Ball Room AHU or the video at this link or both …
https://tinyurl.com/BallRoomAHU2020
… identify potential resource conservation or performance improvement opportunities associated with the system
Note that for approximately 50% of the operating hours, only one side of the Ball Room is in use

## Slide 31: Discussion

## Slide 32: Break Out 6
Based on your scoping observations, what would your monitoring plan for this system look like?
The monitoring plan does not have to be the “full meal deal” version in David’s template but should include:
Points required
Sampling rate
Data source (data logger, control system or other resources)

## Slide 33: Discussion