## Slide 1: As Installed System Diagram
VF-1 Elec. Rm.
SD
TDV
Chiller 2
VFD & HG
SD
TDV
Chiller 1
Fixed Spd
SD
TDV
SD
TDV
1,100 gpm
825 gpm each
1,100 gpm from 51.0°F to 42.0°F, 75% Loaded
Match Line – See Sheet 2
A
B
1,100 gpm from 51.0°F to 42.0°F, 75% Loaded
Hijend Hotel CHW System Diagram
Sheet 1
75% load
1,650 gpm,
54.0°F
1,650 gpm,
42.0°F
2,200 gpm,
42.0°F
2,200 gpm,
51.0°F
550 gpm,
42.0°F
1,100 gpm