## Calculations
Flow - | 1100 | gpm
Head - | 40 | ft.w.c.
Pump efficiency - | 82%
Shaft hp - | 13.5501
Motor hp - | 15
90.33%
Motor efficiency - | 92.4%
hp into the motor - | 14.6646
kW - | 10.9398
Unnecesarry Hours of Operation in San Francisco - | 1463 | hours
kWh per year save - | 16004.9684 | kWh
Electric Rate - | 0.1621 | per kWh
Annual savings - | 2594.4054 | per year
The values in the table below are the answers I came up with using a 52°F set point for the point were the chiller plant would be required to operate.
I have inserted the actual calculations at the end of this spreadsheet so you can reference them if you want to.
The green tab is the savings cacluation and the blue tabs are the weather data files I used.

## WeatherDataFile
Country: USA | [9 empty] | Temperature set point - | 51 | °F
State: CALIFORNIA | [9 empty] | Total Hours - | 1463
City: SAN_FRANCISCO_INTL_AP
Altitude: 6 ft.
Month | Day | Hour | Dry Bulb | Wet Bulb | Dew Point | Humidity Ratio | Enthalpy | Density | Vapor Pressure | Specific Volume | Hours below 51 °F
|  |  | °F | °F | °F | gr/lb | btu/lb | lb/cu.ft. | in. HG | cu.ft./lb
January | 1 | 12AM to 1AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 1 | 1AM to 2AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 1 | 2AM to 3AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 1 | 3AM to 4AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 1 | 4AM to 5AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 1 | 5AM to 6AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 1 | 6AM to 7AM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0787 | 0.25 | 12.78 | 1
January | 1 | 7AM to 8AM | 41 | 39.2 | 37 | 32.5 | 14.85 | 0.079 | 0.22 | 12.71 | 1
January | 1 | 8AM to 9AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
January | 1 | 9AM to 10AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 1 | 10AM to 11AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 1 | 11AM to 12PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 1 | 12PM to 1PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
January | 1 | 1PM to 2PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
January | 1 | 2PM to 3PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
January | 1 | 3PM to 4PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
January | 1 | 4PM to 5PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 1 | 5PM to 6PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
January | 1 | 6PM to 7PM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 0
January | 1 | 7PM to 8PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 0
January | 1 | 8PM to 9PM | 48 | 42.8 | 37 | 32.5 | 16.55 | 0.0779 | 0.22 | 12.89 | 1
January | 1 | 9PM to 10PM | 48.9 | 42.8 | 36 | 31.1 | 16.55 | 0.0778 | 0.21 | 12.91 | 1
January | 1 | 10PM to 11PM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
January | 1 | 11PM to 12AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 2 | 12AM to 1AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
January | 2 | 1AM to 2AM | 43 | 40.2 | 37 | 32.5 | 15.33 | 0.0787 | 0.22 | 12.76 | 1
January | 2 | 2AM to 3AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 2 | 3AM to 4AM | 39 | 37.3 | 35.1 | 30 | 13.99 | 0.0793 | 0.2 | 12.66 | 1
January | 2 | 4AM to 5AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 2 | 5AM to 6AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 2 | 6AM to 7AM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
January | 2 | 7AM to 8AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 2 | 8AM to 9AM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 0
January | 2 | 9AM to 10AM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
January | 2 | 10AM to 11AM | 57 | 46.4 | 35.1 | 30 | 18.34 | 0.0766 | 0.2 | 13.11 | 0
January | 2 | 11AM to 12PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
January | 2 | 12PM to 1PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
January | 2 | 1PM to 2PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
January | 2 | 2PM to 3PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
January | 2 | 3PM to 4PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
January | 2 | 4PM to 5PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
January | 2 | 5PM to 6PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
January | 2 | 6PM to 7PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
January | 2 | 7PM to 8PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
January | 2 | 8PM to 9PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 2 | 9PM to 10PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 2 | 10PM to 11PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 2 | 11PM to 12AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
January | 3 | 12AM to 1AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 3 | 1AM to 2AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
January | 3 | 2AM to 3AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
January | 3 | 3AM to 4AM | 57 | 46 | 34 | 28.7 | 18.15 | 0.0766 | 0.2 | 13.11 | 0
January | 3 | 4AM to 5AM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
January | 3 | 5AM to 6AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
January | 3 | 6AM to 7AM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
January | 3 | 7AM to 8AM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
January | 3 | 8AM to 9AM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
January | 3 | 9AM to 10AM | 55.9 | 45.5 | 34 | 28.7 | 17.88 | 0.0768 | 0.2 | 13.08 | 0
January | 3 | 10AM to 11AM | 54 | 46.5 | 39 | 35.1 | 18.4 | 0.077 | 0.24 | 13.05 | 0
January | 3 | 11AM to 12PM | 59 | 47 | 34 | 28.7 | 18.62 | 0.0763 | 0.2 | 13.16 | 0
January | 3 | 12PM to 1PM | 60.1 | 47.5 | 34 | 28.7 | 18.89 | 0.0761 | 0.2 | 13.19 | 0
January | 3 | 1PM to 2PM | 61 | 46.9 | 30.9 | 25.2 | 18.56 | 0.076 | 0.17 | 13.2 | 0
January | 3 | 2PM to 3PM | 61 | 46.9 | 30.9 | 25.2 | 18.56 | 0.076 | 0.17 | 13.2 | 0
January | 3 | 3PM to 4PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
January | 3 | 4PM to 5PM | 57 | 45.7 | 33.1 | 27.7 | 17.99 | 0.0766 | 0.19 | 13.11 | 0
January | 3 | 5PM to 6PM | 55 | 45.1 | 34 | 28.7 | 17.67 | 0.0769 | 0.2 | 13.06 | 0
January | 3 | 6PM to 7PM | 54 | 44.3 | 33.1 | 27.7 | 17.25 | 0.0771 | 0.19 | 13.03 | 0
January | 3 | 7PM to 8PM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
January | 3 | 8PM to 9PM | 50 | 43 | 35.1 | 30 | 16.64 | 0.0776 | 0.2 | 12.94 | 1
January | 3 | 9PM to 10PM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 3 | 10PM to 11PM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 3 | 11PM to 12AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 4 | 12AM to 1AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
January | 4 | 1AM to 2AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 4 | 2AM to 3AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 4 | 3AM to 4AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 4 | 4AM to 5AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0792 | 0.23 | 12.69 | 1
January | 4 | 5AM to 6AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 4 | 6AM to 7AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 4 | 7AM to 8AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 4 | 8AM to 9AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
January | 4 | 9AM to 10AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 4 | 10AM to 11AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 4 | 11AM to 12PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
January | 4 | 12PM to 1PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 0
January | 4 | 1PM to 2PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 0
January | 4 | 2PM to 3PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 4 | 3PM to 4PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
January | 4 | 4PM to 5PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 4 | 5PM to 6PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 4 | 6PM to 7PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
January | 4 | 7PM to 8PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 4 | 8PM to 9PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 4 | 9PM to 10PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 4 | 10PM to 11PM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
January | 4 | 11PM to 12AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 5 | 12AM to 1AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 5 | 1AM to 2AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 5 | 2AM to 3AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
January | 5 | 3AM to 4AM | 39 | 38.5 | 37.9 | 33.7 | 14.55 | 0.0793 | 0.23 | 12.67 | 1
January | 5 | 4AM to 5AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 5 | 5AM to 6AM | 39 | 38.5 | 37.9 | 33.7 | 14.55 | 0.0793 | 0.23 | 12.67 | 1
January | 5 | 6AM to 7AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 5 | 7AM to 8AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 5 | 8AM to 9AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 5 | 9AM to 10AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 5 | 10AM to 11AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
January | 5 | 11AM to 12PM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 5 | 12PM to 1PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 5 | 1PM to 2PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
January | 5 | 2PM to 3PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 5 | 3PM to 4PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 5 | 4PM to 5PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
January | 5 | 5PM to 6PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
January | 5 | 6PM to 7PM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
January | 5 | 7PM to 8PM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 5 | 8PM to 9PM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
January | 5 | 9PM to 10PM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
January | 5 | 10PM to 11PM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 5 | 11PM to 12AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 6 | 12AM to 1AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
January | 6 | 1AM to 2AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 6 | 2AM to 3AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 6 | 3AM to 4AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 6 | 4AM to 5AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 6 | 5AM to 6AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 6 | 6AM to 7AM | 42.1 | 40.6 | 39 | 35.1 | 15.52 | 0.0788 | 0.24 | 12.75 | 1
January | 6 | 7AM to 8AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
January | 6 | 8AM to 9AM | 42.1 | 40.6 | 39 | 35.1 | 15.52 | 0.0788 | 0.24 | 12.75 | 1
January | 6 | 9AM to 10AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 6 | 10AM to 11AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
January | 6 | 11AM to 12PM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
January | 6 | 12PM to 1PM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
January | 6 | 1PM to 2PM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
January | 6 | 2PM to 3PM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 6 | 3PM to 4PM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
January | 6 | 4PM to 5PM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 6 | 5PM to 6PM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
January | 6 | 6PM to 7PM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
January | 6 | 7PM to 8PM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
January | 6 | 8PM to 9PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 6 | 9PM to 10PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 6 | 10PM to 11PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 6 | 11PM to 12AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 7 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 7 | 1AM to 2AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 7 | 2AM to 3AM | 43 | 43 | 43 | 41 | 16.64 | 0.0786 | 0.28 | 12.79 | 1
January | 7 | 3AM to 4AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 7 | 4AM to 5AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 7 | 5AM to 6AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 7 | 6AM to 7AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
January | 7 | 7AM to 8AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 7 | 8AM to 9AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 7 | 9AM to 10AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 7 | 10AM to 11AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 7 | 11AM to 12PM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 7 | 12PM to 1PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 7 | 1PM to 2PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 7 | 2PM to 3PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 7 | 3PM to 4PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 7 | 4PM to 5PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 7 | 5PM to 6PM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 7 | 6PM to 7PM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 7 | 7PM to 8PM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 7 | 8PM to 9PM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
January | 7 | 9PM to 10PM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
January | 7 | 10PM to 11PM | 43 | 43 | 43 | 41 | 16.64 | 0.0786 | 0.28 | 12.79 | 1
January | 7 | 11PM to 12AM | 42.1 | 42.1 | 42.1 | 39.6 | 16.21 | 0.0788 | 0.27 | 12.76 | 1
January | 8 | 12AM to 1AM | 42.1 | 42.1 | 42.1 | 39.6 | 16.21 | 0.0788 | 0.27 | 12.76 | 1
January | 8 | 1AM to 2AM | 41 | 41 | 41 | 38 | 15.69 | 0.079 | 0.26 | 12.73 | 1
January | 8 | 2AM to 3AM | 41 | 41 | 41 | 38 | 15.69 | 0.079 | 0.26 | 12.73 | 1
January | 8 | 3AM to 4AM | 41 | 41 | 41 | 38 | 15.69 | 0.079 | 0.26 | 12.73 | 1
January | 8 | 4AM to 5AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0792 | 0.25 | 12.7 | 1
January | 8 | 5AM to 6AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0792 | 0.25 | 12.7 | 1
January | 8 | 6AM to 7AM | 39 | 39 | 39 | 35.1 | 14.78 | 0.0793 | 0.24 | 12.67 | 1
January | 8 | 7AM to 8AM | 39 | 39 | 39 | 35.1 | 14.78 | 0.0793 | 0.24 | 12.67 | 1
January | 8 | 8AM to 9AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0793 | 0.24 | 12.68 | 1
January | 8 | 9AM to 10AM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
January | 8 | 10AM to 11AM | 48.2 | 42.3 | 35.6 | 30.7 | 16.31 | 0.0779 | 0.21 | 12.89 | 1
January | 8 | 11AM to 12PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
January | 8 | 12PM to 1PM | 55.4 | 45.2 | 33.8 | 28.5 | 17.72 | 0.0768 | 0.19 | 13.07 | 0
January | 8 | 1PM to 2PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.0771 | 0.24 | 13.04 | 0
January | 8 | 2PM to 3PM | 57.2 | 45.5 | 32 | 26.5 | 17.85 | 0.0766 | 0.18 | 13.11 | 0
January | 8 | 3PM to 4PM | 57 | 45.7 | 33.1 | 27.7 | 17.99 | 0.0766 | 0.19 | 13.11 | 0
January | 8 | 4PM to 5PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 0
January | 8 | 5PM to 6PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
January | 8 | 6PM to 7PM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
January | 8 | 7PM to 8PM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 8 | 8PM to 9PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
January | 8 | 9PM to 10PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 8 | 10PM to 11PM | 48.9 | 43.3 | 37 | 32.5 | 16.77 | 0.0778 | 0.22 | 12.92 | 1
January | 8 | 11PM to 12AM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
January | 9 | 12AM to 1AM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
January | 9 | 1AM to 2AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
January | 9 | 2AM to 3AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
January | 9 | 3AM to 4AM | 43 | 39.8 | 36 | 31.1 | 15.12 | 0.0787 | 0.21 | 12.76 | 1
January | 9 | 4AM to 5AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
January | 9 | 5AM to 6AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 9 | 6AM to 7AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 9 | 7AM to 8AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
January | 9 | 8AM to 9AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.81 | 1
January | 9 | 9AM to 10AM | 45 | 41.3 | 37 | 32.5 | 15.81 | 0.0784 | 0.22 | 12.81 | 1
January | 9 | 10AM to 11AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0782 | 0.22 | 12.85 | 1
January | 9 | 11AM to 12PM | 46.4 | 43.7 | 41 | 38 | 17 | 0.0781 | 0.26 | 12.87 | 1
January | 9 | 12PM to 1PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0779 | 0.24 | 12.91 | 1
January | 9 | 1PM to 2PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0779 | 0.24 | 12.91 | 1
January | 9 | 2PM to 3PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 0
January | 9 | 3PM to 4PM | 51.3 | 46.1 | 41 | 38 | 18.18 | 0.0774 | 0.26 | 12.99 | 0
January | 9 | 4PM to 5PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
January | 9 | 5PM to 6PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 9 | 6PM to 7PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
January | 9 | 7PM to 8PM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
January | 9 | 8PM to 9PM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
January | 9 | 9PM to 10PM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
January | 9 | 10PM to 11PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 9 | 11PM to 12AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 12AM to 1AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 10 | 1AM to 2AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 2AM to 3AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 10 | 3AM to 4AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 10 | 4AM to 5AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
January | 10 | 5AM to 6AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
January | 10 | 6AM to 7AM | 39.9 | 38.6 | 37 | 32.5 | 14.59 | 0.0792 | 0.22 | 12.69 | 1
January | 10 | 7AM to 8AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 10 | 8AM to 9AM | 44.2 | 41.3 | 38.1 | 33.9 | 15.85 | 0.0785 | 0.23 | 12.8 | 1
January | 10 | 9AM to 10AM | 44.2 | 41.2 | 37.8 | 33.4 | 15.78 | 0.0785 | 0.23 | 12.8 | 1
January | 10 | 10AM to 11AM | 44.8 | 41.5 | 37.9 | 33.7 | 15.95 | 0.0784 | 0.23 | 12.81 | 1
January | 10 | 11AM to 12PM | 45.5 | 42.7 | 39.7 | 36.1 | 16.5 | 0.0783 | 0.25 | 12.84 | 1
January | 10 | 12PM to 1PM | 47.1 | 43 | 38.7 | 34.6 | 16.66 | 0.078 | 0.24 | 12.88 | 1
January | 10 | 1PM to 2PM | 46.9 | 42.9 | 38.5 | 34.4 | 16.58 | 0.0781 | 0.23 | 12.87 | 1
January | 10 | 2PM to 3PM | 49.5 | 44.1 | 38.5 | 34.4 | 17.19 | 0.0777 | 0.23 | 12.93 | 1
January | 10 | 3PM to 4PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 10 | 4PM to 5PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 10 | 5PM to 6PM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
January | 10 | 6PM to 7PM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
January | 10 | 7PM to 8PM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
January | 10 | 8PM to 9PM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 9PM to 10PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 10 | 10PM to 11PM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 11PM to 12AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 11 | 12AM to 1AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 11 | 1AM to 2AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 11 | 2AM to 3AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 11 | 3AM to 4AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
January | 11 | 4AM to 5AM | 41 | 39.2 | 37 | 32.5 | 14.85 | 0.079 | 0.22 | 12.71 | 1
January | 11 | 5AM to 6AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
January | 11 | 6AM to 7AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
January | 11 | 7AM to 8AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0792 | 0.23 | 12.69 | 1
January | 11 | 8AM to 9AM | 42.8 | 40.3 | 37.4 | 33 | 15.36 | 0.0787 | 0.22 | 12.76 | 1
January | 11 | 9AM to 10AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 11 | 10AM to 11AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.77 | 1
January | 11 | 11AM to 12PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.81 | 1
January | 11 | 12PM to 1PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.6 | 0.0782 | 0.24 | 12.86 | 1
January | 11 | 1PM to 2PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.6 | 0.0782 | 0.24 | 12.86 | 1
January | 11 | 2PM to 3PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0779 | 0.24 | 12.91 | 1
January | 11 | 3PM to 4PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 11 | 4PM to 5PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
January | 11 | 5PM to 6PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 11 | 6PM to 7PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 11 | 7PM to 8PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 11 | 8PM to 9PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 11 | 9PM to 10PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 11 | 10PM to 11PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 11 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 12 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 12 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 12 | 2AM to 3AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
January | 12 | 3AM to 4AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 12 | 4AM to 5AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 12 | 5AM to 6AM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
January | 12 | 6AM to 7AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
January | 12 | 7AM to 8AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
January | 12 | 8AM to 9AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
January | 12 | 9AM to 10AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
January | 12 | 10AM to 11AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
January | 12 | 11AM to 12PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 12PM to 1PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
January | 12 | 1PM to 2PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 2PM to 3PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
January | 12 | 3PM to 4PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 12 | 4PM to 5PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 12 | 5PM to 6PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 6PM to 7PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 7PM to 8PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 8PM to 9PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 9PM to 10PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 12 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 12 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 13 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 13 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 13 | 2AM to 3AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
January | 13 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 13 | 4AM to 5AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.98 | 1
January | 13 | 5AM to 6AM | 48.9 | 46.7 | 44.6 | 43.7 | 18.49 | 0.0777 | 0.3 | 12.95 | 1
January | 13 | 6AM to 7AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
January | 13 | 7AM to 8AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 13 | 8AM to 9AM | 48.9 | 45.8 | 42.8 | 40.7 | 18.04 | 0.0777 | 0.28 | 12.94 | 1
January | 13 | 9AM to 10AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 13 | 10AM to 11AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 13 | 11AM to 12PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
January | 13 | 12PM to 1PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
January | 13 | 1PM to 2PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 13 | 2PM to 3PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 13 | 3PM to 4PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 13 | 4PM to 5PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 13 | 5PM to 6PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 13 | 6PM to 7PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 13 | 7PM to 8PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 13 | 8PM to 9PM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 13 | 9PM to 10PM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 13 | 10PM to 11PM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 13 | 11PM to 12AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 14 | 12AM to 1AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 14 | 1AM to 2AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 14 | 2AM to 3AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 14 | 3AM to 4AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
January | 14 | 4AM to 5AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 14 | 5AM to 6AM | 46 | 46 | 46 | 46.1 | 18.18 | 0.0781 | 0.31 | 12.88 | 1
January | 14 | 6AM to 7AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
January | 14 | 7AM to 8AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
January | 14 | 8AM to 9AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
January | 14 | 9AM to 10AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
January | 14 | 10AM to 11AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
January | 14 | 11AM to 12PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 14 | 12PM to 1PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 14 | 1PM to 2PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
January | 14 | 2PM to 3PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
January | 14 | 3PM to 4PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 14 | 4PM to 5PM | 54 | 48.2 | 43 | 41 | 19.31 | 0.077 | 0.28 | 13.07 | 0
January | 14 | 5PM to 6PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
January | 14 | 6PM to 7PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
January | 14 | 7PM to 8PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
January | 14 | 8PM to 9PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 14 | 9PM to 10PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
January | 14 | 10PM to 11PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
January | 14 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
January | 15 | 12AM to 1AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 15 | 1AM to 2AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 15 | 2AM to 3AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
January | 15 | 3AM to 4AM | 48 | 47.4 | 46.9 | 47.8 | 18.91 | 0.0778 | 0.32 | 12.94 | 1
January | 15 | 4AM to 5AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
January | 15 | 5AM to 6AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
January | 15 | 6AM to 7AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
January | 15 | 7AM to 8AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
January | 15 | 8AM to 9AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 15 | 9AM to 10AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 15 | 10AM to 11AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
January | 15 | 11AM to 12PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
January | 15 | 12PM to 1PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
January | 15 | 1PM to 2PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
January | 15 | 2PM to 3PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 15 | 3PM to 4PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
January | 15 | 4PM to 5PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 15 | 5PM to 6PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
January | 15 | 6PM to 7PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 15 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 15 | 8PM to 9PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
January | 15 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 15 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 15 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 16 | 12AM to 1AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 16 | 1AM to 2AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 16 | 2AM to 3AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 16 | 3AM to 4AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 16 | 4AM to 5AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 16 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 16 | 6AM to 7AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 16 | 7AM to 8AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 16 | 8AM to 9AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 16 | 9AM to 10AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 16 | 10AM to 11AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
January | 16 | 11AM to 12PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
January | 16 | 12PM to 1PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
January | 16 | 1PM to 2PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 16 | 2PM to 3PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
January | 16 | 3PM to 4PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
January | 16 | 4PM to 5PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
January | 16 | 5PM to 6PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
January | 16 | 6PM to 7PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 16 | 7PM to 8PM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
January | 16 | 8PM to 9PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 16 | 9PM to 10PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
January | 16 | 10PM to 11PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 16 | 11PM to 12AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 17 | 12AM to 1AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 17 | 1AM to 2AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
January | 17 | 2AM to 3AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
January | 17 | 3AM to 4AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
January | 17 | 4AM to 5AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
January | 17 | 5AM to 6AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 17 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
January | 17 | 7AM to 8AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 17 | 8AM to 9AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
January | 17 | 9AM to 10AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
January | 17 | 10AM to 11AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
January | 17 | 11AM to 12PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
January | 17 | 12PM to 1PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
January | 17 | 1PM to 2PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
January | 17 | 2PM to 3PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
January | 17 | 3PM to 4PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 17 | 4PM to 5PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 17 | 5PM to 6PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 17 | 6PM to 7PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 17 | 7PM to 8PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 17 | 8PM to 9PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 17 | 9PM to 10PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 17 | 10PM to 11PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 17 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 18 | 12AM to 1AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 1AM to 2AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 2AM to 3AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 4AM to 5AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 5AM to 6AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 6AM to 7AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 18 | 7AM to 8AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 8AM to 9AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 18 | 9AM to 10AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 10AM to 11AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 11AM to 12PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 12PM to 1PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
January | 18 | 1PM to 2PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 18 | 2PM to 3PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 3PM to 4PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 18 | 4PM to 5PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
January | 18 | 5PM to 6PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
January | 18 | 6PM to 7PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
January | 18 | 7PM to 8PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 18 | 8PM to 9PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
January | 18 | 9PM to 10PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 18 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 19 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 19 | 1AM to 2AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 19 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 19 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 19 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 19 | 5AM to 6AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 19 | 6AM to 7AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 19 | 7AM to 8AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 19 | 8AM to 9AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
January | 19 | 9AM to 10AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 19 | 10AM to 11AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
January | 19 | 11AM to 12PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 19 | 12PM to 1PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
January | 19 | 1PM to 2PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
January | 19 | 2PM to 3PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
January | 19 | 3PM to 4PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
January | 19 | 4PM to 5PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
January | 19 | 5PM to 6PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
January | 19 | 6PM to 7PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 19 | 7PM to 8PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
January | 19 | 8PM to 9PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
January | 19 | 9PM to 10PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
January | 19 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 19 | 11PM to 12AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 20 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 20 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
January | 20 | 2AM to 3AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 20 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 20 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 20 | 5AM to 6AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 20 | 6AM to 7AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 20 | 7AM to 8AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
January | 20 | 8AM to 9AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 20 | 9AM to 10AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 20 | 10AM to 11AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
January | 20 | 11AM to 12PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
January | 20 | 12PM to 1PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
January | 20 | 1PM to 2PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
January | 20 | 2PM to 3PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
January | 20 | 3PM to 4PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 20 | 4PM to 5PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 20 | 5PM to 6PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
January | 20 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
January | 20 | 7PM to 8PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
January | 20 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
January | 20 | 9PM to 10PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
January | 20 | 10PM to 11PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
January | 20 | 11PM to 12AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
January | 21 | 12AM to 1AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 21 | 1AM to 2AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 21 | 2AM to 3AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 21 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 21 | 4AM to 5AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 21 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
January | 21 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 21 | 7AM to 8AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 21 | 8AM to 9AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
January | 21 | 9AM to 10AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
January | 21 | 10AM to 11AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
January | 21 | 11AM to 12PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
January | 21 | 12PM to 1PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
January | 21 | 1PM to 2PM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
January | 21 | 2PM to 3PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
January | 21 | 3PM to 4PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
January | 21 | 4PM to 5PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
January | 21 | 5PM to 6PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
January | 21 | 6PM to 7PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
January | 21 | 7PM to 8PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 21 | 8PM to 9PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
January | 21 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
January | 21 | 10PM to 11PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
January | 21 | 11PM to 12AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 22 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
January | 22 | 1AM to 2AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
January | 22 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
January | 22 | 3AM to 4AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
January | 22 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 22 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 22 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 22 | 7AM to 8AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
January | 22 | 8AM to 9AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
January | 22 | 9AM to 10AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 22 | 10AM to 11AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
January | 22 | 11AM to 12PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
January | 22 | 12PM to 1PM | 57 | 48.7 | 41 | 38 | 19.58 | 0.0765 | 0.26 | 13.14 | 0
January | 22 | 1PM to 2PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
January | 22 | 2PM to 3PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 22 | 3PM to 4PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 22 | 4PM to 5PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 22 | 5PM to 6PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
January | 22 | 6PM to 7PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 22 | 7PM to 8PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 22 | 8PM to 9PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 22 | 9PM to 10PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 22 | 10PM to 11PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 22 | 11PM to 12AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 23 | 12AM to 1AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
January | 23 | 1AM to 2AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 23 | 2AM to 3AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
January | 23 | 3AM to 4AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
January | 23 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 23 | 5AM to 6AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 23 | 6AM to 7AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 23 | 7AM to 8AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 23 | 8AM to 9AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 23 | 9AM to 10AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 23 | 10AM to 11AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 23 | 11AM to 12PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 23 | 12PM to 1PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
January | 23 | 1PM to 2PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
January | 23 | 2PM to 3PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
January | 23 | 3PM to 4PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 23 | 4PM to 5PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
January | 23 | 5PM to 6PM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
January | 23 | 6PM to 7PM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
January | 23 | 7PM to 8PM | 45 | 40.4 | 35.1 | 30 | 15.43 | 0.0784 | 0.2 | 12.81 | 1
January | 23 | 8PM to 9PM | 45 | 40 | 34 | 28.7 | 15.23 | 0.0784 | 0.2 | 12.8 | 1
January | 23 | 9PM to 10PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
January | 23 | 10PM to 11PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
January | 23 | 11PM to 12AM | 44.1 | 39.2 | 33.1 | 27.7 | 14.85 | 0.0786 | 0.19 | 12.78 | 1
January | 24 | 12AM to 1AM | 42.1 | 38.1 | 33.1 | 27.7 | 14.37 | 0.0789 | 0.19 | 12.73 | 1
January | 24 | 1AM to 2AM | 39 | 36 | 32 | 26.5 | 13.45 | 0.0794 | 0.18 | 12.65 | 1
January | 24 | 2AM to 3AM | 37.9 | 35 | 30.9 | 25.2 | 12.99 | 0.0796 | 0.17 | 12.62 | 1
January | 24 | 3AM to 4AM | 37 | 34.5 | 30.9 | 25.2 | 12.78 | 0.0797 | 0.17 | 12.59 | 1
January | 24 | 4AM to 5AM | 39 | 35.2 | 30 | 24.2 | 13.09 | 0.0794 | 0.16 | 12.64 | 1
January | 24 | 5AM to 6AM | 36 | 33.8 | 30.9 | 25.2 | 12.51 | 0.0799 | 0.17 | 12.57 | 1
January | 24 | 6AM to 7AM | 37.9 | 35 | 30.9 | 25.2 | 12.99 | 0.0796 | 0.17 | 12.62 | 1
January | 24 | 7AM to 8AM | 39 | 36 | 32 | 26.5 | 13.45 | 0.0794 | 0.18 | 12.65 | 1
January | 24 | 8AM to 9AM | 43 | 38.2 | 32 | 26.5 | 14.41 | 0.0787 | 0.18 | 12.75 | 1
January | 24 | 9AM to 10AM | 45 | 39.3 | 32 | 26.5 | 14.89 | 0.0784 | 0.18 | 12.8 | 1
January | 24 | 10AM to 11AM | 46 | 40.6 | 34 | 28.7 | 15.49 | 0.0783 | 0.2 | 12.83 | 1
January | 24 | 11AM to 12PM | 46 | 40.6 | 34 | 28.7 | 15.49 | 0.0783 | 0.2 | 12.83 | 1
January | 24 | 12PM to 1PM | 48 | 41.6 | 34 | 28.7 | 15.97 | 0.078 | 0.2 | 12.88 | 1
January | 24 | 1PM to 2PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
January | 24 | 2PM to 3PM | 52 | 43.6 | 34 | 28.7 | 16.93 | 0.0773 | 0.2 | 12.98 | 0
January | 24 | 3PM to 4PM | 50 | 43 | 35.1 | 30 | 16.64 | 0.0776 | 0.2 | 12.94 | 1
January | 24 | 4PM to 5PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
January | 24 | 5PM to 6PM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
January | 24 | 6PM to 7PM | 46.9 | 40.7 | 33.1 | 27.7 | 15.55 | 0.0781 | 0.19 | 12.85 | 1
January | 24 | 7PM to 8PM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
January | 24 | 8PM to 9PM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
January | 24 | 9PM to 10PM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
January | 24 | 10PM to 11PM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
January | 24 | 11PM to 12AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
January | 25 | 12AM to 1AM | 48 | 42 | 35.1 | 30 | 16.17 | 0.0779 | 0.2 | 12.89 | 1
January | 25 | 1AM to 2AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
January | 25 | 2AM to 3AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 25 | 3AM to 4AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 25 | 4AM to 5AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 25 | 5AM to 6AM | 46.9 | 41.1 | 34 | 28.7 | 15.71 | 0.0781 | 0.2 | 12.85 | 1
January | 25 | 6AM to 7AM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
January | 25 | 7AM to 8AM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
January | 25 | 8AM to 9AM | 46.9 | 41.1 | 34 | 28.7 | 15.71 | 0.0781 | 0.2 | 12.85 | 1
January | 25 | 9AM to 10AM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
January | 25 | 10AM to 11AM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 25 | 11AM to 12PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
January | 25 | 12PM to 1PM | 53.1 | 46.1 | 39 | 35.1 | 18.18 | 0.0771 | 0.24 | 13.03 | 0
January | 25 | 1PM to 2PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 25 | 2PM to 3PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 25 | 3PM to 4PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
January | 25 | 4PM to 5PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
January | 25 | 5PM to 6PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 25 | 6PM to 7PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 25 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
January | 25 | 8PM to 9PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
January | 25 | 9PM to 10PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 25 | 10PM to 11PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 25 | 11PM to 12AM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 26 | 12AM to 1AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 26 | 1AM to 2AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
January | 26 | 2AM to 3AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 26 | 3AM to 4AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 26 | 4AM to 5AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 26 | 5AM to 6AM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
January | 26 | 6AM to 7AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 26 | 7AM to 8AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
January | 26 | 8AM to 9AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
January | 26 | 9AM to 10AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
January | 26 | 10AM to 11AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 26 | 11AM to 12PM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 26 | 12PM to 1PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 26 | 1PM to 2PM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 26 | 2PM to 3PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
January | 26 | 3PM to 4PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
January | 26 | 4PM to 5PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 26 | 5PM to 6PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
January | 26 | 6PM to 7PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
January | 26 | 7PM to 8PM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 26 | 8PM to 9PM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
January | 26 | 9PM to 10PM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 26 | 10PM to 11PM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
January | 26 | 11PM to 12AM | 43 | 39.8 | 36 | 31.1 | 15.12 | 0.0787 | 0.21 | 12.76 | 1
January | 27 | 12AM to 1AM | 42.1 | 39.3 | 36 | 31.1 | 14.9 | 0.0789 | 0.21 | 12.74 | 1
January | 27 | 1AM to 2AM | 42.1 | 39.8 | 37 | 32.5 | 15.11 | 0.0788 | 0.22 | 12.74 | 1
January | 27 | 2AM to 3AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
January | 27 | 3AM to 4AM | 39 | 38.5 | 37.9 | 33.7 | 14.55 | 0.0793 | 0.23 | 12.67 | 1
January | 27 | 4AM to 5AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
January | 27 | 5AM to 6AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
January | 27 | 6AM to 7AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 27 | 7AM to 8AM | 39.9 | 38.6 | 37 | 32.5 | 14.59 | 0.0792 | 0.22 | 12.69 | 1
January | 27 | 8AM to 9AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
January | 27 | 9AM to 10AM | 48.9 | 42.8 | 36 | 31.1 | 16.55 | 0.0778 | 0.21 | 12.91 | 1
January | 27 | 10AM to 11AM | 52 | 44.8 | 37 | 32.5 | 17.51 | 0.0773 | 0.22 | 12.99 | 0
January | 27 | 11AM to 12PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
January | 27 | 12PM to 1PM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
January | 27 | 1PM to 2PM | 55.9 | 45.9 | 35.1 | 30 | 18.08 | 0.0767 | 0.2 | 13.09 | 0
January | 27 | 2PM to 3PM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
January | 27 | 3PM to 4PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
January | 27 | 4PM to 5PM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
January | 27 | 5PM to 6PM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
January | 27 | 6PM to 7PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
January | 27 | 7PM to 8PM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
January | 27 | 8PM to 9PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 27 | 9PM to 10PM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
January | 27 | 10PM to 11PM | 46 | 41 | 35.1 | 30 | 15.69 | 0.0782 | 0.2 | 12.83 | 1
January | 27 | 11PM to 12AM | 45 | 40.4 | 35.1 | 30 | 15.43 | 0.0784 | 0.2 | 12.81 | 1
January | 28 | 12AM to 1AM | 43 | 39.8 | 36 | 31.1 | 15.12 | 0.0787 | 0.21 | 12.76 | 1
January | 28 | 1AM to 2AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
January | 28 | 2AM to 3AM | 39.9 | 37.8 | 35.1 | 30 | 14.21 | 0.0792 | 0.2 | 12.68 | 1
January | 28 | 3AM to 4AM | 39 | 37.3 | 35.1 | 30 | 13.99 | 0.0793 | 0.2 | 12.66 | 1
January | 28 | 4AM to 5AM | 39 | 37.3 | 35.1 | 30 | 13.99 | 0.0793 | 0.2 | 12.66 | 1
January | 28 | 5AM to 6AM | 37.9 | 36.2 | 34 | 28.7 | 13.53 | 0.0795 | 0.2 | 12.63 | 1
January | 28 | 6AM to 7AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
January | 28 | 7AM to 8AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 28 | 8AM to 9AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 28 | 9AM to 10AM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
January | 28 | 10AM to 11AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
January | 28 | 11AM to 12PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 28 | 12PM to 1PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
January | 28 | 1PM to 2PM | 54 | 48.2 | 43 | 41 | 19.31 | 0.077 | 0.28 | 13.07 | 0
January | 28 | 2PM to 3PM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
January | 28 | 3PM to 4PM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
January | 28 | 4PM to 5PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
January | 28 | 5PM to 6PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 28 | 6PM to 7PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
January | 28 | 7PM to 8PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 28 | 8PM to 9PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 28 | 9PM to 10PM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 28 | 10PM to 11PM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 28 | 11PM to 12AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 29 | 12AM to 1AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 29 | 1AM to 2AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 29 | 2AM to 3AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
January | 29 | 3AM to 4AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 29 | 4AM to 5AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0792 | 0.25 | 12.7 | 1
January | 29 | 5AM to 6AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 29 | 6AM to 7AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 29 | 7AM to 8AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 29 | 8AM to 9AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 29 | 9AM to 10AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 29 | 10AM to 11AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 29 | 11AM to 12PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 29 | 12PM to 1PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
January | 29 | 1PM to 2PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
January | 29 | 2PM to 3PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
January | 29 | 3PM to 4PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 29 | 4PM to 5PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
January | 29 | 5PM to 6PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
January | 29 | 6PM to 7PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 29 | 7PM to 8PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 29 | 8PM to 9PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 29 | 9PM to 10PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 29 | 10PM to 11PM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 29 | 11PM to 12AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 30 | 12AM to 1AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 30 | 1AM to 2AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 30 | 2AM to 3AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
January | 30 | 3AM to 4AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 30 | 4AM to 5AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
January | 30 | 5AM to 6AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
January | 30 | 6AM to 7AM | 43 | 42.5 | 42.1 | 39.6 | 16.43 | 0.0787 | 0.27 | 12.79 | 1
January | 30 | 7AM to 8AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 30 | 8AM to 9AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 30 | 9AM to 10AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 30 | 10AM to 11AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 30 | 11AM to 12PM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
January | 30 | 12PM to 1PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 30 | 1PM to 2PM | 57.9 | 49.6 | 42.1 | 39.6 | 20.05 | 0.0764 | 0.27 | 13.17 | 0
January | 30 | 2PM to 3PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
January | 30 | 3PM to 4PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
January | 30 | 4PM to 5PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
January | 30 | 5PM to 6PM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
January | 30 | 6PM to 7PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 30 | 7PM to 8PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 30 | 8PM to 9PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
January | 30 | 9PM to 10PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 30 | 10PM to 11PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 30 | 11PM to 12AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 31 | 12AM to 1AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 31 | 1AM to 2AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
January | 31 | 2AM to 3AM | 48 | 47.4 | 46.9 | 47.8 | 18.91 | 0.0778 | 0.32 | 12.94 | 1
January | 31 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 31 | 4AM to 5AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 31 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 31 | 6AM to 7AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 31 | 7AM to 8AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 31 | 8AM to 9AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
January | 31 | 9AM to 10AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
January | 31 | 10AM to 11AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
January | 31 | 11AM to 12PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 0
January | 31 | 12PM to 1PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 31 | 1PM to 2PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
January | 31 | 2PM to 3PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
January | 31 | 3PM to 4PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
January | 31 | 4PM to 5PM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
January | 31 | 5PM to 6PM | 48 | 42.8 | 37 | 32.5 | 16.55 | 0.0779 | 0.22 | 12.89 | 1
January | 31 | 6PM to 7PM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
January | 31 | 7PM to 8PM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
January | 31 | 8PM to 9PM | 46.9 | 42.6 | 37.9 | 33.7 | 16.47 | 0.0781 | 0.23 | 12.87 | 1
January | 31 | 9PM to 10PM | 46.6 | 42.6 | 38.3 | 34.1 | 16.46 | 0.0781 | 0.23 | 12.86 | 1
January | 31 | 10PM to 11PM | 46.4 | 42.6 | 38.5 | 34.4 | 16.45 | 0.0782 | 0.23 | 12.86 | 1
January | 31 | 11PM to 12AM | 46 | 42.6 | 38.8 | 34.9 | 16.44 | 0.0782 | 0.24 | 12.85 | 1
February | 1 | 12AM to 1AM | 45.9 | 42.6 | 39 | 35.1 | 16.43 | 0.0782 | 0.24 | 12.85 | 1
February | 1 | 1AM to 2AM | 45.5 | 42.5 | 39.4 | 35.6 | 16.42 | 0.0783 | 0.24 | 12.84 | 1
February | 1 | 2AM to 3AM | 45.3 | 42.5 | 39.6 | 35.9 | 16.42 | 0.0783 | 0.24 | 12.83 | 1
February | 1 | 3AM to 4AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 1 | 4AM to 5AM | 45.3 | 43.1 | 40.8 | 37.7 | 16.7 | 0.0783 | 0.26 | 12.84 | 1
February | 1 | 5AM to 6AM | 45.7 | 43.9 | 42.1 | 39.6 | 17.08 | 0.0782 | 0.27 | 12.85 | 1
February | 1 | 6AM to 7AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
February | 1 | 7AM to 8AM | 46.9 | 45.1 | 43.3 | 41.6 | 17.69 | 0.078 | 0.28 | 12.89 | 1
February | 1 | 8AM to 9AM | 48 | 45.6 | 43.3 | 41.6 | 17.96 | 0.0779 | 0.28 | 12.92 | 1
February | 1 | 9AM to 10AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
February | 1 | 10AM to 11AM | 51.3 | 46.1 | 41 | 38 | 18.18 | 0.0774 | 0.26 | 12.99 | 0
February | 1 | 11AM to 12PM | 53.6 | 46.3 | 39 | 35.1 | 18.31 | 0.0771 | 0.24 | 13.04 | 0
February | 1 | 12PM to 1PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
February | 1 | 1PM to 2PM | 56.3 | 47.2 | 38.1 | 33.9 | 18.77 | 0.0767 | 0.23 | 13.11 | 0
February | 1 | 2PM to 3PM | 56.7 | 47.7 | 38.8 | 34.9 | 19.01 | 0.0766 | 0.24 | 13.12 | 0
February | 1 | 3PM to 4PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
February | 1 | 4PM to 5PM | 55.4 | 47.9 | 40.6 | 37.4 | 19.1 | 0.0768 | 0.25 | 13.09 | 0
February | 1 | 5PM to 6PM | 53.6 | 47.4 | 41.5 | 38.8 | 18.87 | 0.077 | 0.26 | 13.05 | 0
February | 1 | 6PM to 7PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
February | 1 | 7PM to 8PM | 51.6 | 47.3 | 43.3 | 41.6 | 18.83 | 0.0773 | 0.28 | 13.01 | 0
February | 1 | 8PM to 9PM | 51.4 | 47.6 | 44.1 | 42.8 | 18.97 | 0.0773 | 0.29 | 13.01 | 0
February | 1 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
February | 1 | 10PM to 11PM | 49.1 | 46 | 43 | 41 | 18.13 | 0.0777 | 0.28 | 12.94 | 1
February | 1 | 11PM to 12AM | 46.9 | 44.1 | 41.2 | 38.2 | 17.18 | 0.0781 | 0.26 | 12.88 | 1
February | 2 | 12AM to 1AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 2 | 1AM to 2AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
February | 2 | 2AM to 3AM | 43 | 41 | 38.8 | 34.9 | 15.7 | 0.0787 | 0.24 | 12.77 | 1
February | 2 | 3AM to 4AM | 42.1 | 40.6 | 39 | 35.1 | 15.52 | 0.0788 | 0.24 | 12.75 | 1
February | 2 | 4AM to 5AM | 42.8 | 40.8 | 38.5 | 34.4 | 15.58 | 0.0787 | 0.23 | 12.77 | 1
February | 2 | 5AM to 6AM | 43.3 | 41 | 38.5 | 34.4 | 15.71 | 0.0786 | 0.23 | 12.78 | 1
February | 2 | 6AM to 7AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
February | 2 | 7AM to 8AM | 44.8 | 41.7 | 38.3 | 34.1 | 16.02 | 0.0784 | 0.23 | 12.81 | 1
February | 2 | 8AM to 9AM | 45.3 | 42 | 38.3 | 34.1 | 16.15 | 0.0783 | 0.23 | 12.83 | 1
February | 2 | 9AM to 10AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
February | 2 | 10AM to 11AM | 47.3 | 42.7 | 37.8 | 33.4 | 16.52 | 0.078 | 0.23 | 12.88 | 1
February | 2 | 11AM to 12PM | 48.7 | 43.3 | 37.4 | 33 | 16.79 | 0.0778 | 0.22 | 12.91 | 1
February | 2 | 12PM to 1PM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
February | 2 | 1PM to 2PM | 50.4 | 44.1 | 37.4 | 33 | 17.19 | 0.0776 | 0.22 | 12.95 | 1
February | 2 | 2PM to 3PM | 50.7 | 44.3 | 37.4 | 33 | 17.27 | 0.0775 | 0.22 | 12.96 | 1
February | 2 | 3PM to 4PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 0
February | 2 | 4PM to 5PM | 50.4 | 44.2 | 37.6 | 33.2 | 17.22 | 0.0776 | 0.23 | 12.95 | 1
February | 2 | 5PM to 6PM | 49.6 | 43.8 | 37.6 | 33.2 | 17.05 | 0.0777 | 0.23 | 12.94 | 1
February | 2 | 6PM to 7PM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
February | 2 | 7PM to 8PM | 47.7 | 43 | 37.9 | 33.7 | 16.64 | 0.078 | 0.23 | 12.89 | 1
February | 2 | 8PM to 9PM | 46.2 | 42.4 | 38.3 | 34.1 | 16.37 | 0.0782 | 0.23 | 12.85 | 1
February | 2 | 9PM to 10PM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
February | 2 | 10PM to 11PM | 45.3 | 42.1 | 38.7 | 34.6 | 16.23 | 0.0783 | 0.24 | 12.83 | 1
February | 2 | 11PM to 12AM | 45.7 | 42.3 | 38.7 | 34.6 | 16.31 | 0.0783 | 0.24 | 12.84 | 1
February | 3 | 12AM to 1AM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
February | 3 | 1AM to 2AM | 45.3 | 41.9 | 38.1 | 33.9 | 16.11 | 0.0783 | 0.23 | 12.83 | 1
February | 3 | 2AM to 3AM | 44.8 | 41.5 | 37.8 | 33.4 | 15.91 | 0.0784 | 0.23 | 12.81 | 1
February | 3 | 3AM to 4AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
February | 3 | 4AM to 5AM | 44.1 | 41.1 | 37.8 | 33.4 | 15.73 | 0.0785 | 0.23 | 12.79 | 1
February | 3 | 5AM to 6AM | 44.1 | 41.3 | 38.1 | 33.9 | 15.81 | 0.0785 | 0.23 | 12.8 | 1
February | 3 | 6AM to 7AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
February | 3 | 7AM to 8AM | 44.4 | 41.5 | 38.3 | 34.1 | 15.93 | 0.0785 | 0.23 | 12.81 | 1
February | 3 | 8AM to 9AM | 44.6 | 41.6 | 38.3 | 34.1 | 15.98 | 0.0784 | 0.23 | 12.81 | 1
February | 3 | 9AM to 10AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
February | 3 | 10AM to 11AM | 47.3 | 42.9 | 38.1 | 33.9 | 16.59 | 0.078 | 0.23 | 12.88 | 1
February | 3 | 11AM to 12PM | 49.6 | 44.1 | 38.1 | 33.9 | 17.16 | 0.0777 | 0.23 | 12.94 | 1
February | 3 | 12PM to 1PM | 52 | 45.6 | 39 | 35.1 | 17.92 | 0.0773 | 0.24 | 13 | 0
February | 3 | 1PM to 2PM | 53.2 | 46.1 | 38.8 | 34.9 | 18.18 | 0.0771 | 0.24 | 13.03 | 0
February | 3 | 2PM to 3PM | 54.7 | 46.9 | 39.2 | 35.4 | 18.61 | 0.0769 | 0.24 | 13.07 | 0
February | 3 | 3PM to 4PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
February | 3 | 4PM to 5PM | 54.3 | 46.7 | 39.2 | 35.4 | 18.52 | 0.077 | 0.24 | 13.06 | 0
February | 3 | 5PM to 6PM | 52.7 | 45.8 | 38.8 | 34.9 | 18.05 | 0.0772 | 0.24 | 13.02 | 0
February | 3 | 6PM to 7PM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
February | 3 | 7PM to 8PM | 50.4 | 44.8 | 39 | 35.1 | 17.52 | 0.0776 | 0.24 | 12.96 | 1
February | 3 | 8PM to 9PM | 49.6 | 44.6 | 39.4 | 35.6 | 17.43 | 0.0777 | 0.24 | 12.94 | 1
February | 3 | 9PM to 10PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
February | 3 | 10PM to 11PM | 48 | 43.6 | 38.8 | 34.9 | 16.92 | 0.0779 | 0.24 | 12.9 | 1
February | 3 | 11PM to 12AM | 46.9 | 42.8 | 38.3 | 34.1 | 16.54 | 0.0781 | 0.23 | 12.87 | 1
February | 4 | 12AM to 1AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
February | 4 | 1AM to 2AM | 45.7 | 41.9 | 37.8 | 33.4 | 16.13 | 0.0783 | 0.23 | 12.84 | 1
February | 4 | 2AM to 3AM | 45.3 | 41.9 | 38.1 | 33.9 | 16.11 | 0.0783 | 0.23 | 12.83 | 1
February | 4 | 3AM to 4AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
February | 4 | 4AM to 5AM | 44.1 | 41.1 | 37.8 | 33.4 | 15.73 | 0.0785 | 0.23 | 12.79 | 1
February | 4 | 5AM to 6AM | 43 | 40.2 | 37 | 32.5 | 15.33 | 0.0787 | 0.22 | 12.76 | 1
February | 4 | 6AM to 7AM | 42.1 | 39.8 | 37 | 32.5 | 15.11 | 0.0788 | 0.22 | 12.74 | 1
February | 4 | 7AM to 8AM | 44.1 | 41.3 | 38.1 | 33.9 | 15.81 | 0.0785 | 0.23 | 12.8 | 1
February | 4 | 8AM to 9AM | 46 | 43 | 39.7 | 36.1 | 16.63 | 0.0782 | 0.25 | 12.85 | 1
February | 4 | 9AM to 10AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
February | 4 | 10AM to 11AM | 50.7 | 46 | 41.4 | 38.5 | 18.13 | 0.0775 | 0.26 | 12.98 | 1
February | 4 | 11AM to 12PM | 53.2 | 47.3 | 41.7 | 39.1 | 18.83 | 0.0771 | 0.26 | 13.04 | 0
February | 4 | 12PM to 1PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
February | 4 | 1PM to 2PM | 57.4 | 49.2 | 41.7 | 39.1 | 19.83 | 0.0765 | 0.26 | 13.15 | 0
February | 4 | 2PM to 3PM | 58.6 | 49.5 | 41.2 | 38.2 | 20.01 | 0.0763 | 0.26 | 13.18 | 0
February | 4 | 3PM to 4PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
February | 4 | 4PM to 5PM | 58.1 | 48.9 | 40.3 | 36.9 | 19.68 | 0.0764 | 0.25 | 13.16 | 0
February | 4 | 5PM to 6PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
February | 4 | 6PM to 7PM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
February | 4 | 7PM to 8PM | 53.6 | 46.3 | 39 | 35.1 | 18.31 | 0.0771 | 0.24 | 13.04 | 0
February | 4 | 8PM to 9PM | 53.4 | 46 | 38.3 | 34.1 | 18.11 | 0.0771 | 0.23 | 13.03 | 0
February | 4 | 9PM to 10PM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
February | 4 | 10PM to 11PM | 50.7 | 44.4 | 37.6 | 33.2 | 17.31 | 0.0775 | 0.23 | 12.96 | 1
February | 4 | 11PM to 12AM | 48.4 | 43.2 | 37.6 | 33.2 | 16.74 | 0.0779 | 0.23 | 12.9 | 1
February | 5 | 12AM to 1AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
February | 5 | 1AM to 2AM | 45.7 | 41.8 | 37.4 | 33 | 16.05 | 0.0783 | 0.22 | 12.83 | 1
February | 5 | 2AM to 3AM | 45.3 | 41.6 | 37.4 | 33 | 15.97 | 0.0783 | 0.22 | 12.83 | 1
February | 5 | 3AM to 4AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
February | 5 | 4AM to 5AM | 44.6 | 41.1 | 37 | 32.5 | 15.72 | 0.0785 | 0.22 | 12.81 | 1
February | 5 | 5AM to 6AM | 44.4 | 40.8 | 36.7 | 32 | 15.6 | 0.0785 | 0.22 | 12.8 | 1
February | 5 | 6AM to 7AM | 44.1 | 40.8 | 37 | 32.5 | 15.59 | 0.0785 | 0.22 | 12.79 | 1
February | 5 | 7AM to 8AM | 46.4 | 42.8 | 39 | 35.1 | 16.56 | 0.0782 | 0.24 | 12.86 | 1
February | 5 | 8AM to 9AM | 48.7 | 45.2 | 41.7 | 39.1 | 17.74 | 0.0778 | 0.26 | 12.93 | 1
February | 5 | 9AM to 10AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
February | 5 | 10AM to 11AM | 52.3 | 48 | 44.1 | 42.8 | 19.19 | 0.0772 | 0.29 | 13.03 | 0
February | 5 | 11AM to 12PM | 53.8 | 48.6 | 44.1 | 42.8 | 19.53 | 0.077 | 0.29 | 13.07 | 0
February | 5 | 12PM to 1PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
February | 5 | 1PM to 2PM | 55.4 | 50.1 | 45.5 | 45.2 | 20.31 | 0.0767 | 0.31 | 13.12 | 0
February | 5 | 2PM to 3PM | 55.6 | 50.7 | 46.6 | 47.1 | 20.65 | 0.0767 | 0.32 | 13.13 | 0
February | 5 | 3PM to 4PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
February | 5 | 4PM to 5PM | 55 | 50.4 | 46.6 | 47.1 | 20.51 | 0.0768 | 0.32 | 13.11 | 0
February | 5 | 5PM to 6PM | 54 | 49.4 | 45.5 | 45.2 | 19.96 | 0.0769 | 0.31 | 13.08 | 0
February | 5 | 6PM to 7PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
February | 5 | 7PM to 8PM | 52.7 | 49.1 | 46 | 46.1 | 19.8 | 0.0771 | 0.31 | 13.05 | 0
February | 5 | 8PM to 9PM | 52.3 | 49.6 | 47.3 | 48.4 | 20.06 | 0.0772 | 0.33 | 13.05 | 0
February | 5 | 9PM to 10PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
February | 5 | 10PM to 11PM | 52.3 | 50.4 | 48.9 | 51.5 | 20.54 | 0.0771 | 0.35 | 13.06 | 0
February | 5 | 11PM to 12AM | 52.7 | 50.8 | 49.3 | 52.2 | 20.73 | 0.0771 | 0.35 | 13.07 | 0
February | 6 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
February | 6 | 1AM to 2AM | 52 | 50.4 | 49.1 | 51.8 | 20.5 | 0.0772 | 0.35 | 13.05 | 0
February | 6 | 2AM to 3AM | 51.1 | 49.8 | 48.7 | 51.1 | 20.18 | 0.0773 | 0.35 | 13.03 | 0
February | 6 | 3AM to 4AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
February | 6 | 4AM to 5AM | 50.4 | 49.3 | 48.4 | 50.4 | 19.89 | 0.0774 | 0.34 | 13 | 1
February | 6 | 5AM to 6AM | 50.7 | 49.4 | 48.4 | 50.4 | 19.98 | 0.0774 | 0.34 | 13.01 | 1
February | 6 | 6AM to 7AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
February | 6 | 7AM to 8AM | 51.1 | 49.6 | 48.4 | 50.4 | 20.07 | 0.0773 | 0.34 | 13.02 | 0
February | 6 | 8AM to 9AM | 51.1 | 49.6 | 48.4 | 50.4 | 20.07 | 0.0773 | 0.34 | 13.02 | 0
February | 6 | 9AM to 10AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
February | 6 | 10AM to 11AM | 53.1 | 49.6 | 46.8 | 47.4 | 20.08 | 0.0771 | 0.32 | 13.06 | 0
February | 6 | 11AM to 12PM | 55 | 49.9 | 45.5 | 45.2 | 20.22 | 0.0768 | 0.31 | 13.11 | 0
February | 6 | 12PM to 1PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
February | 6 | 1PM to 2PM | 58.1 | 51.5 | 46 | 46.1 | 21.11 | 0.0763 | 0.31 | 13.19 | 0
February | 6 | 2PM to 3PM | 59 | 52.7 | 47.8 | 49.4 | 21.84 | 0.0762 | 0.33 | 13.22 | 0
February | 6 | 3PM to 4PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
February | 6 | 4PM to 5PM | 57.7 | 52.8 | 48.9 | 51.5 | 21.85 | 0.0763 | 0.35 | 13.2 | 0
February | 6 | 5PM to 6PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0767 | 0.34 | 13.13 | 0
February | 6 | 6PM to 7PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
February | 6 | 7PM to 8PM | 52.3 | 49.1 | 46.4 | 46.8 | 19.81 | 0.0772 | 0.32 | 13.04 | 0
February | 6 | 8PM to 9PM | 51.8 | 48.3 | 45.1 | 44.6 | 19.34 | 0.0773 | 0.3 | 13.02 | 0
February | 6 | 9PM to 10PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
February | 6 | 10PM to 11PM | 50.7 | 47.2 | 44.1 | 42.8 | 18.79 | 0.0774 | 0.29 | 12.99 | 1
February | 6 | 11PM to 12AM | 50.4 | 47.2 | 44.2 | 43.1 | 18.75 | 0.0775 | 0.29 | 12.98 | 1
February | 7 | 12AM to 1AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
February | 7 | 1AM to 2AM | 48.4 | 45.4 | 42.6 | 40.4 | 17.87 | 0.0778 | 0.27 | 12.92 | 1
February | 7 | 2AM to 3AM | 46.6 | 43.9 | 41.2 | 38.2 | 17.09 | 0.0781 | 0.26 | 12.87 | 1
February | 7 | 3AM to 4AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 7 | 4AM to 5AM | 45.7 | 43.4 | 41 | 38 | 16.83 | 0.0782 | 0.26 | 12.85 | 1
February | 7 | 5AM to 6AM | 46.2 | 44.4 | 42.6 | 40.4 | 17.34 | 0.0781 | 0.27 | 12.87 | 1
February | 7 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 7 | 7AM to 8AM | 47.3 | 46.1 | 45 | 44.3 | 18.2 | 0.078 | 0.3 | 12.91 | 1
February | 7 | 8AM to 9AM | 47.7 | 46.6 | 45.7 | 45.5 | 18.47 | 0.0779 | 0.31 | 12.92 | 1
February | 7 | 9AM to 10AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
February | 7 | 10AM to 11AM | 51.3 | 49 | 47.1 | 48.1 | 19.75 | 0.0773 | 0.33 | 13.02 | 0
February | 7 | 11AM to 12PM | 54.7 | 51.1 | 48.2 | 50.1 | 20.89 | 0.0768 | 0.34 | 13.11 | 0
February | 7 | 12PM to 1PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
February | 7 | 1PM to 2PM | 58.3 | 53.1 | 49.1 | 51.8 | 22.04 | 0.0763 | 0.35 | 13.21 | 0
February | 7 | 2PM to 3PM | 58.6 | 53 | 48.7 | 51.1 | 22.02 | 0.0762 | 0.35 | 13.22 | 0
February | 7 | 3PM to 4PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
February | 7 | 4PM to 5PM | 57.4 | 52 | 47.7 | 49.1 | 21.39 | 0.0764 | 0.33 | 13.18 | 0
February | 7 | 5PM to 6PM | 55.6 | 50.7 | 46.6 | 47.1 | 20.65 | 0.0767 | 0.32 | 13.13 | 0
February | 7 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
February | 7 | 7PM to 8PM | 54.3 | 49.1 | 44.4 | 43.4 | 19.76 | 0.0769 | 0.29 | 13.08 | 0
February | 7 | 8PM to 9PM | 54.7 | 48.6 | 43.2 | 41.3 | 19.53 | 0.0769 | 0.28 | 13.09 | 0
February | 7 | 9PM to 10PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
February | 7 | 10PM to 11PM | 54.3 | 48.9 | 44.1 | 42.8 | 19.67 | 0.0769 | 0.29 | 13.08 | 0
February | 7 | 11PM to 12AM | 53.8 | 49.7 | 46.2 | 46.5 | 20.11 | 0.077 | 0.31 | 13.08 | 0
February | 8 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 8 | 1AM to 2AM | 53.1 | 50.5 | 48.4 | 50.4 | 20.55 | 0.077 | 0.34 | 13.07 | 0
February | 8 | 2AM to 3AM | 53.1 | 50.5 | 48.4 | 50.4 | 20.55 | 0.077 | 0.34 | 13.07 | 0
February | 8 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 8 | 4AM to 5AM | 52 | 49.3 | 47.1 | 48.1 | 19.92 | 0.0772 | 0.33 | 13.04 | 0
February | 8 | 5AM to 6AM | 51.1 | 48.2 | 45.7 | 45.5 | 19.31 | 0.0774 | 0.31 | 13.01 | 0
February | 8 | 6AM to 7AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
February | 8 | 7AM to 8AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
February | 8 | 8AM to 9AM | 54 | 50.5 | 47.7 | 49.1 | 20.56 | 0.0769 | 0.33 | 13.09 | 0
February | 8 | 9AM to 10AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
February | 8 | 10AM to 11AM | 56.3 | 52.2 | 49.1 | 51.8 | 21.56 | 0.0765 | 0.35 | 13.16 | 0
February | 8 | 11AM to 12PM | 56.7 | 52.4 | 49.1 | 51.8 | 21.64 | 0.0765 | 0.35 | 13.17 | 0
February | 8 | 12PM to 1PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
February | 8 | 1PM to 2PM | 55.9 | 52.3 | 49.5 | 52.6 | 21.58 | 0.0766 | 0.36 | 13.15 | 0
February | 8 | 2PM to 3PM | 55 | 51.9 | 49.5 | 52.6 | 21.36 | 0.0767 | 0.36 | 13.13 | 0
February | 8 | 3PM to 4PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
February | 8 | 4PM to 5PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
February | 8 | 5PM to 6PM | 54 | 50.8 | 48.2 | 50.1 | 20.72 | 0.0769 | 0.34 | 13.1 | 0
February | 8 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
February | 8 | 7PM to 8PM | 53.2 | 50 | 47.3 | 48.4 | 20.28 | 0.077 | 0.33 | 13.07 | 0
February | 8 | 8PM to 9PM | 52.7 | 49.6 | 46.9 | 47.8 | 20.05 | 0.0771 | 0.32 | 13.06 | 0
February | 8 | 9PM to 10PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
February | 8 | 10PM to 11PM | 51.3 | 48.6 | 46.2 | 46.5 | 19.5 | 0.0773 | 0.31 | 13.02 | 0
February | 8 | 11PM to 12AM | 50.7 | 48.2 | 46 | 46.1 | 19.32 | 0.0774 | 0.31 | 13 | 1
February | 9 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
February | 9 | 1AM to 2AM | 48.9 | 46.8 | 44.8 | 44 | 18.54 | 0.0777 | 0.3 | 12.95 | 1
February | 9 | 2AM to 3AM | 48 | 46.1 | 44.2 | 43.1 | 18.18 | 0.0779 | 0.29 | 12.92 | 1
February | 9 | 3AM to 4AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
February | 9 | 4AM to 5AM | 46.2 | 44.5 | 42.8 | 40.7 | 17.39 | 0.0781 | 0.28 | 12.87 | 1
February | 9 | 5AM to 6AM | 45.7 | 43.9 | 42.1 | 39.6 | 17.08 | 0.0782 | 0.27 | 12.85 | 1
February | 9 | 6AM to 7AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
February | 9 | 7AM to 8AM | 48 | 45.8 | 43.7 | 42.2 | 18.05 | 0.0779 | 0.29 | 12.92 | 1
February | 9 | 8AM to 9AM | 50.9 | 48.3 | 46 | 46.1 | 19.36 | 0.0774 | 0.31 | 13.01 | 1
February | 9 | 9AM to 10AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
February | 9 | 10AM to 11AM | 54.3 | 50.6 | 47.5 | 48.8 | 20.59 | 0.0769 | 0.33 | 13.1 | 0
February | 9 | 11AM to 12PM | 54.7 | 50.4 | 46.8 | 47.4 | 20.48 | 0.0768 | 0.32 | 13.11 | 0
February | 9 | 12PM to 1PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
February | 9 | 1PM to 2PM | 55.9 | 51.1 | 47.1 | 48.1 | 20.89 | 0.0766 | 0.33 | 13.14 | 0
February | 9 | 2PM to 3PM | 57 | 51.9 | 47.8 | 49.4 | 21.35 | 0.0765 | 0.33 | 13.17 | 0
February | 9 | 3PM to 4PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
February | 9 | 4PM to 5PM | 56.7 | 51.7 | 47.8 | 49.4 | 21.27 | 0.0765 | 0.33 | 13.16 | 0
February | 9 | 5PM to 6PM | 55.2 | 50.8 | 47.1 | 48.1 | 20.71 | 0.0767 | 0.33 | 13.12 | 0
February | 9 | 6PM to 7PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
February | 9 | 7PM to 8PM | 53.2 | 49.8 | 46.9 | 47.8 | 20.18 | 0.077 | 0.32 | 13.07 | 0
February | 9 | 8PM to 9PM | 52.7 | 49.7 | 47.3 | 48.4 | 20.15 | 0.0771 | 0.33 | 13.06 | 0
February | 9 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
February | 9 | 10PM to 11PM | 52 | 49.6 | 47.7 | 49.1 | 20.08 | 0.0772 | 0.33 | 13.04 | 0
February | 9 | 11PM to 12AM | 52 | 49.6 | 47.7 | 49.1 | 20.08 | 0.0772 | 0.33 | 13.04 | 0
February | 10 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
February | 10 | 1AM to 2AM | 50.4 | 48.2 | 46.4 | 46.8 | 19.33 | 0.0775 | 0.32 | 12.99 | 1
February | 10 | 2AM to 3AM | 48.6 | 46.9 | 45.5 | 45.2 | 18.64 | 0.0778 | 0.31 | 12.94 | 1
February | 10 | 3AM to 4AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 10 | 4AM to 5AM | 46.6 | 45.1 | 43.7 | 42.2 | 17.7 | 0.0781 | 0.29 | 12.88 | 1
February | 10 | 5AM to 6AM | 46.4 | 44.7 | 43 | 41 | 17.47 | 0.0781 | 0.28 | 12.88 | 1
February | 10 | 6AM to 7AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
February | 10 | 7AM to 8AM | 46.8 | 45.2 | 43.7 | 42.2 | 17.74 | 0.0781 | 0.29 | 12.89 | 1
February | 10 | 8AM to 9AM | 47.3 | 46.1 | 45 | 44.3 | 18.2 | 0.078 | 0.3 | 12.91 | 1
February | 10 | 9AM to 10AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
February | 10 | 10AM to 11AM | 49.3 | 47.9 | 46.8 | 47.4 | 19.16 | 0.0776 | 0.32 | 12.97 | 1
February | 10 | 11AM to 12PM | 50.7 | 49 | 47.5 | 48.8 | 19.72 | 0.0774 | 0.33 | 13.01 | 1
February | 10 | 12PM to 1PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
February | 10 | 1PM to 2PM | 55.4 | 51.7 | 48.7 | 51.1 | 21.23 | 0.0767 | 0.35 | 13.14 | 0
February | 10 | 2PM to 3PM | 58.6 | 53.2 | 49.1 | 51.8 | 22.12 | 0.0762 | 0.35 | 13.22 | 0
February | 10 | 3PM to 4PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
February | 10 | 4PM to 5PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
February | 10 | 5PM to 6PM | 56.1 | 51.7 | 48.2 | 50.1 | 21.24 | 0.0766 | 0.34 | 13.15 | 0
February | 10 | 6PM to 7PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
February | 10 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
February | 10 | 8PM to 9PM | 53.1 | 50.5 | 48.4 | 50.4 | 20.55 | 0.077 | 0.34 | 13.07 | 0
February | 10 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 10 | 10PM to 11PM | 52.3 | 50.1 | 48.2 | 50.1 | 20.32 | 0.0772 | 0.34 | 13.05 | 0
February | 10 | 11PM to 12AM | 51.8 | 49.7 | 48 | 49.8 | 20.14 | 0.0772 | 0.34 | 13.04 | 0
February | 11 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
February | 11 | 1AM to 2AM | 49.6 | 47.5 | 45.7 | 45.5 | 18.96 | 0.0776 | 0.31 | 12.97 | 1
February | 11 | 2AM to 3AM | 48.4 | 46.2 | 44.2 | 43.1 | 18.27 | 0.0778 | 0.29 | 12.93 | 1
February | 11 | 3AM to 4AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
February | 11 | 4AM to 5AM | 46.9 | 45 | 43.2 | 41.3 | 17.65 | 0.078 | 0.28 | 12.89 | 1
February | 11 | 5AM to 6AM | 46.9 | 45.3 | 43.7 | 42.2 | 17.78 | 0.078 | 0.29 | 12.89 | 1
February | 11 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 11 | 7AM to 8AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 11 | 8AM to 9AM | 46.9 | 46.3 | 45.7 | 45.5 | 18.3 | 0.078 | 0.31 | 12.9 | 1
February | 11 | 9AM to 10AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
February | 11 | 10AM to 11AM | 50.4 | 48.6 | 47.1 | 48.1 | 19.53 | 0.0775 | 0.33 | 13 | 1
February | 11 | 11AM to 12PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
February | 11 | 12PM to 1PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
February | 11 | 1PM to 2PM | 58.6 | 53.6 | 49.8 | 53.3 | 22.35 | 0.0762 | 0.36 | 13.22 | 0
February | 11 | 2PM to 3PM | 60.4 | 54.5 | 50.2 | 54 | 22.9 | 0.0759 | 0.37 | 13.27 | 0
February | 11 | 3PM to 4PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
February | 11 | 4PM to 5PM | 59.4 | 54.2 | 50.4 | 54.4 | 22.69 | 0.0761 | 0.37 | 13.25 | 0
February | 11 | 5PM to 6PM | 56.7 | 52.9 | 50 | 53.6 | 21.92 | 0.0765 | 0.36 | 13.17 | 0
February | 11 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
February | 11 | 7PM to 8PM | 53.2 | 51 | 49.3 | 52.2 | 20.87 | 0.077 | 0.35 | 13.08 | 0
February | 11 | 8PM to 9PM | 52.7 | 50.6 | 48.9 | 51.5 | 20.62 | 0.0771 | 0.35 | 13.07 | 0
February | 11 | 9PM to 10PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
February | 11 | 10PM to 11PM | 51.6 | 49.9 | 48.6 | 50.8 | 20.25 | 0.0773 | 0.34 | 13.04 | 0
February | 11 | 11PM to 12AM | 51.4 | 49.9 | 48.6 | 50.8 | 20.21 | 0.0773 | 0.34 | 13.03 | 0
February | 12 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
February | 12 | 1AM to 2AM | 51.1 | 49.8 | 48.7 | 51.1 | 20.18 | 0.0773 | 0.35 | 13.03 | 0
February | 12 | 2AM to 3AM | 51.1 | 50 | 49.1 | 51.8 | 20.29 | 0.0773 | 0.35 | 13.03 | 0
February | 12 | 3AM to 4AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
February | 12 | 4AM to 5AM | 50.4 | 49.3 | 48.4 | 50.4 | 19.89 | 0.0774 | 0.34 | 13 | 1
February | 12 | 5AM to 6AM | 49.6 | 48.4 | 47.3 | 48.4 | 19.41 | 0.0776 | 0.33 | 12.98 | 1
February | 12 | 6AM to 7AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
February | 12 | 7AM to 8AM | 49.3 | 48 | 46.9 | 47.8 | 19.22 | 0.0776 | 0.32 | 12.97 | 1
February | 12 | 8AM to 9AM | 49.6 | 48.6 | 47.7 | 49.1 | 19.51 | 0.0776 | 0.33 | 12.98 | 1
February | 12 | 9AM to 10AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
February | 12 | 10AM to 11AM | 51.3 | 49.7 | 48.4 | 50.4 | 20.11 | 0.0773 | 0.34 | 13.03 | 0
February | 12 | 11AM to 12PM | 52.7 | 50.5 | 48.7 | 51.1 | 20.57 | 0.0771 | 0.35 | 13.07 | 0
February | 12 | 12PM to 1PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
February | 12 | 1PM to 2PM | 55.9 | 52.7 | 50.2 | 54 | 21.8 | 0.0766 | 0.37 | 13.16 | 0
February | 12 | 2PM to 3PM | 58.1 | 53.9 | 50.9 | 55.5 | 22.56 | 0.0763 | 0.37 | 13.22 | 0
February | 12 | 3PM to 4PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
February | 12 | 4PM to 5PM | 57.7 | 53.8 | 50.9 | 55.5 | 22.47 | 0.0763 | 0.37 | 13.21 | 0
February | 12 | 5PM to 6PM | 55.4 | 52.4 | 50.2 | 54 | 21.67 | 0.0767 | 0.37 | 13.14 | 0
February | 12 | 6PM to 7PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
February | 12 | 7PM to 8PM | 52.3 | 50.5 | 49.1 | 51.8 | 20.59 | 0.0771 | 0.35 | 13.06 | 0
February | 12 | 8PM to 9PM | 51.8 | 49.9 | 48.4 | 50.4 | 20.24 | 0.0772 | 0.34 | 13.04 | 0
February | 12 | 9PM to 10PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
February | 12 | 10PM to 11PM | 50.7 | 48.9 | 47.3 | 48.4 | 19.67 | 0.0774 | 0.33 | 13.01 | 1
February | 12 | 11PM to 12AM | 50.4 | 48.5 | 46.9 | 47.8 | 19.48 | 0.0775 | 0.32 | 13 | 1
February | 13 | 12AM to 1AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
February | 13 | 1AM to 2AM | 49.3 | 47.2 | 45.3 | 44.9 | 18.77 | 0.0777 | 0.3 | 12.96 | 1
February | 13 | 2AM to 3AM | 48.7 | 46.6 | 44.6 | 43.7 | 18.45 | 0.0777 | 0.3 | 12.94 | 1
February | 13 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
February | 13 | 4AM to 5AM | 47.7 | 45.7 | 43.9 | 42.5 | 18 | 0.0779 | 0.29 | 12.91 | 1
February | 13 | 5AM to 6AM | 47.3 | 45.6 | 44.1 | 42.8 | 17.96 | 0.078 | 0.29 | 12.9 | 1
February | 13 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 13 | 7AM to 8AM | 48 | 46.8 | 45.7 | 45.5 | 18.56 | 0.0778 | 0.31 | 12.93 | 1
February | 13 | 8AM to 9AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
February | 13 | 9AM to 10AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
February | 13 | 10AM to 11AM | 53.4 | 50.8 | 48.7 | 51.1 | 20.75 | 0.077 | 0.35 | 13.08 | 0
February | 13 | 11AM to 12PM | 56.7 | 52.6 | 49.5 | 52.6 | 21.75 | 0.0765 | 0.36 | 13.17 | 0
February | 13 | 12PM to 1PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
February | 13 | 1PM to 2PM | 62.1 | 55.4 | 50.5 | 54.7 | 23.41 | 0.0757 | 0.37 | 13.32 | 0
February | 13 | 2PM to 3PM | 64 | 56.1 | 50.5 | 54.7 | 23.89 | 0.0754 | 0.37 | 13.37 | 0
February | 13 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
February | 13 | 4PM to 5PM | 64 | 55.7 | 49.6 | 52.9 | 23.6 | 0.0754 | 0.36 | 13.36 | 0
February | 13 | 5PM to 6PM | 62.1 | 54.4 | 48.6 | 50.8 | 22.79 | 0.0757 | 0.34 | 13.3 | 0
February | 13 | 6PM to 7PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
February | 13 | 7PM to 8PM | 57.7 | 52.3 | 48 | 49.8 | 21.58 | 0.0763 | 0.34 | 13.19 | 0
February | 13 | 8PM to 9PM | 55.4 | 51.5 | 48.4 | 50.4 | 21.12 | 0.0767 | 0.34 | 13.13 | 0
February | 13 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 13 | 10PM to 11PM | 52 | 49.9 | 48.2 | 50.1 | 20.23 | 0.0772 | 0.34 | 13.05 | 0
February | 13 | 11PM to 12AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
February | 14 | 12AM to 1AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
February | 14 | 1AM to 2AM | 49.3 | 47.4 | 45.7 | 45.5 | 18.87 | 0.0776 | 0.31 | 12.96 | 1
February | 14 | 2AM to 3AM | 48.7 | 46.4 | 44.2 | 43.1 | 18.36 | 0.0777 | 0.29 | 12.94 | 1
February | 14 | 3AM to 4AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
February | 14 | 4AM to 5AM | 47.7 | 45.2 | 42.8 | 40.7 | 17.73 | 0.0779 | 0.28 | 12.91 | 1
February | 14 | 5AM to 6AM | 47.3 | 45.2 | 43.2 | 41.3 | 17.74 | 0.078 | 0.28 | 12.9 | 1
February | 14 | 6AM to 7AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
February | 14 | 7AM to 8AM | 50.9 | 48.1 | 45.7 | 45.5 | 19.26 | 0.0774 | 0.31 | 13 | 1
February | 14 | 8AM to 9AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
February | 14 | 9AM to 10AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
February | 14 | 10AM to 11AM | 63.3 | 53.7 | 46 | 46.1 | 22.38 | 0.0756 | 0.31 | 13.32 | 0
February | 14 | 11AM to 12PM | 67.6 | 53.8 | 42.1 | 39.6 | 22.41 | 0.075 | 0.27 | 13.41 | 0
February | 14 | 12PM to 1PM | 72 | 54.4 | 39 | 35.1 | 22.76 | 0.0744 | 0.24 | 13.51 | 0
February | 14 | 1PM to 2PM | 69.6 | 54.6 | 42.1 | 39.6 | 22.89 | 0.0747 | 0.27 | 13.46 | 0
February | 14 | 2PM to 3PM | 67.3 | 55.2 | 45.9 | 45.8 | 23.29 | 0.075 | 0.31 | 13.42 | 0
February | 14 | 3PM to 4PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
February | 14 | 4PM to 5PM | 63.7 | 54.2 | 46.9 | 47.8 | 22.72 | 0.0755 | 0.32 | 13.34 | 0
February | 14 | 5PM to 6PM | 62.2 | 52.4 | 44.2 | 43.1 | 21.63 | 0.0757 | 0.29 | 13.29 | 0
February | 14 | 6PM to 7PM | 61 | 51 | 42.1 | 39.6 | 20.79 | 0.0759 | 0.27 | 13.24 | 0
February | 14 | 7PM to 8PM | 57.7 | 50 | 43.2 | 41.3 | 20.27 | 0.0764 | 0.28 | 13.17 | 0
February | 14 | 8PM to 9PM | 54.3 | 49.1 | 44.4 | 43.4 | 19.76 | 0.0769 | 0.29 | 13.08 | 0
February | 14 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
February | 14 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
February | 14 | 11PM to 12AM | 49.1 | 46.7 | 44.4 | 43.4 | 18.49 | 0.0777 | 0.29 | 12.95 | 1
February | 15 | 12AM to 1AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
February | 15 | 1AM to 2AM | 47.7 | 45.2 | 42.8 | 40.7 | 17.73 | 0.0779 | 0.28 | 12.91 | 1
February | 15 | 2AM to 3AM | 47.3 | 44.8 | 42.3 | 39.9 | 17.52 | 0.078 | 0.27 | 12.9 | 1
February | 15 | 3AM to 4AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
February | 15 | 4AM to 5AM | 47.7 | 44.9 | 42.3 | 39.9 | 17.6 | 0.0779 | 0.27 | 12.9 | 1
February | 15 | 5AM to 6AM | 48.2 | 45.4 | 42.8 | 40.7 | 17.87 | 0.0778 | 0.28 | 12.92 | 1
February | 15 | 6AM to 7AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
February | 15 | 7AM to 8AM | 52 | 48.6 | 45.7 | 45.5 | 19.52 | 0.0772 | 0.31 | 13.03 | 0
February | 15 | 8AM to 9AM | 54.9 | 51.1 | 48 | 49.8 | 20.88 | 0.0768 | 0.34 | 13.12 | 0
February | 15 | 9AM to 10AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
February | 15 | 10AM to 11AM | 61 | 54.6 | 49.8 | 53.3 | 22.92 | 0.0759 | 0.36 | 13.28 | 0
February | 15 | 11AM to 12PM | 63.9 | 55.5 | 49.5 | 52.6 | 23.5 | 0.0754 | 0.36 | 13.36 | 0
February | 15 | 12PM to 1PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
February | 15 | 1PM to 2PM | 68.5 | 57.7 | 50.2 | 54 | 24.87 | 0.0748 | 0.37 | 13.48 | 0
February | 15 | 2PM to 3PM | 70.3 | 58.7 | 50.9 | 55.5 | 25.54 | 0.0745 | 0.37 | 13.53 | 0
February | 15 | 3PM to 4PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
February | 15 | 4PM to 5PM | 69.3 | 58.3 | 50.9 | 55.5 | 25.28 | 0.0746 | 0.37 | 13.5 | 0
February | 15 | 5PM to 6PM | 66.7 | 57 | 50.2 | 54 | 24.43 | 0.075 | 0.37 | 13.43 | 0
February | 15 | 6PM to 7PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
February | 15 | 7PM to 8PM | 62.4 | 54.8 | 49.1 | 51.8 | 23.04 | 0.0757 | 0.35 | 13.32 | 0
February | 15 | 8PM to 9PM | 60.6 | 53.7 | 48.4 | 50.4 | 22.39 | 0.0759 | 0.34 | 13.27 | 0
February | 15 | 9PM to 10PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
February | 15 | 10PM to 11PM | 57.7 | 51.8 | 46.9 | 47.8 | 21.27 | 0.0764 | 0.32 | 13.18 | 0
February | 15 | 11PM to 12AM | 56.3 | 50.9 | 46.4 | 46.8 | 20.77 | 0.0766 | 0.32 | 13.15 | 0
February | 16 | 12AM to 1AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
February | 16 | 1AM to 2AM | 53.8 | 49 | 44.8 | 44 | 19.72 | 0.077 | 0.3 | 13.07 | 0
February | 16 | 2AM to 3AM | 52.3 | 48.1 | 44.2 | 43.1 | 19.23 | 0.0772 | 0.29 | 13.03 | 0
February | 16 | 3AM to 4AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
February | 16 | 4AM to 5AM | 50.7 | 47.4 | 44.4 | 43.4 | 18.88 | 0.0774 | 0.29 | 12.99 | 1
February | 16 | 5AM to 6AM | 50.4 | 47.7 | 45.3 | 44.9 | 19.03 | 0.0775 | 0.3 | 12.99 | 1
February | 16 | 6AM to 7AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
February | 16 | 7AM to 8AM | 52.3 | 49.8 | 47.7 | 49.1 | 20.16 | 0.0772 | 0.33 | 13.05 | 0
February | 16 | 8AM to 9AM | 54.7 | 51.5 | 48.9 | 51.5 | 21.11 | 0.0768 | 0.35 | 13.12 | 0
February | 16 | 9AM to 10AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
February | 16 | 10AM to 11AM | 59.7 | 54.2 | 50.2 | 54 | 22.72 | 0.076 | 0.37 | 13.25 | 0
February | 16 | 11AM to 12PM | 62.2 | 55.2 | 50.2 | 54 | 23.34 | 0.0757 | 0.37 | 13.32 | 0
February | 16 | 12PM to 1PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
February | 16 | 1PM to 2PM | 64.6 | 56.4 | 50.5 | 54.7 | 24.02 | 0.0753 | 0.37 | 13.38 | 0
February | 16 | 2PM to 3PM | 64.4 | 56.3 | 50.5 | 54.7 | 23.98 | 0.0753 | 0.37 | 13.38 | 0
February | 16 | 3PM to 4PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
February | 16 | 4PM to 5PM | 61.3 | 54.8 | 50 | 53.6 | 23.06 | 0.0758 | 0.36 | 13.29 | 0
February | 16 | 5PM to 6PM | 58.6 | 53.3 | 49.3 | 52.2 | 22.18 | 0.0762 | 0.35 | 13.22 | 0
February | 16 | 6PM to 7PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
February | 16 | 7PM to 8PM | 55 | 51.3 | 48.4 | 50.4 | 21.03 | 0.0767 | 0.34 | 13.12 | 0
February | 16 | 8PM to 9PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
February | 16 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
February | 16 | 10PM to 11PM | 52.3 | 49.6 | 47.3 | 48.4 | 20.06 | 0.0772 | 0.33 | 13.05 | 0
February | 16 | 11PM to 12AM | 51.8 | 49.2 | 46.9 | 47.8 | 19.83 | 0.0772 | 0.32 | 13.03 | 0
February | 17 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
February | 17 | 1AM to 2AM | 50.7 | 48.4 | 46.4 | 46.8 | 19.41 | 0.0774 | 0.32 | 13 | 1
February | 17 | 2AM to 3AM | 50.4 | 48.2 | 46.4 | 46.8 | 19.33 | 0.0775 | 0.32 | 12.99 | 1
February | 17 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
February | 17 | 4AM to 5AM | 48.4 | 45.8 | 43.3 | 41.6 | 18.04 | 0.0778 | 0.28 | 12.93 | 1
February | 17 | 5AM to 6AM | 46.6 | 43.5 | 40.3 | 36.9 | 16.88 | 0.0781 | 0.25 | 12.87 | 1
February | 17 | 6AM to 7AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
February | 17 | 7AM to 8AM | 48.6 | 45.1 | 41.7 | 39.1 | 17.69 | 0.0778 | 0.26 | 12.93 | 1
February | 17 | 8AM to 9AM | 52.3 | 49 | 46 | 46.1 | 19.71 | 0.0772 | 0.31 | 13.04 | 0
February | 17 | 9AM to 10AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
February | 17 | 10AM to 11AM | 59.4 | 53.9 | 49.8 | 53.3 | 22.52 | 0.0761 | 0.36 | 13.24 | 0
February | 17 | 11AM to 12PM | 62.6 | 55 | 49.5 | 52.6 | 23.2 | 0.0756 | 0.36 | 13.32 | 0
February | 17 | 12PM to 1PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
February | 17 | 1PM to 2PM | 67.3 | 56.5 | 48.7 | 51.1 | 24.12 | 0.075 | 0.35 | 13.44 | 0
February | 17 | 2PM to 3PM | 68.7 | 56.8 | 48.2 | 50.1 | 24.31 | 0.0748 | 0.34 | 13.47 | 0
February | 17 | 3PM to 4PM | 70 | 57.2 | 48 | 49.8 | 24.56 | 0.0746 | 0.34 | 13.5 | 0
February | 17 | 4PM to 5PM | 67.6 | 55 | 45 | 44.3 | 23.13 | 0.075 | 0.3 | 13.43 | 0
February | 17 | 5PM to 6PM | 65.3 | 52.9 | 42.3 | 39.9 | 21.88 | 0.0753 | 0.27 | 13.35 | 0
February | 17 | 6PM to 7PM | 63 | 50.9 | 39.9 | 36.4 | 20.77 | 0.0757 | 0.25 | 13.28 | 0
February | 17 | 7PM to 8PM | 61 | 50.2 | 40.3 | 36.9 | 20.37 | 0.076 | 0.25 | 13.23 | 0
February | 17 | 8PM to 9PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
February | 17 | 9PM to 10PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
February | 17 | 10PM to 11PM | 55.8 | 48.9 | 42.6 | 40.4 | 19.66 | 0.0767 | 0.27 | 13.11 | 0
February | 17 | 11PM to 12AM | 54.3 | 48.7 | 43.7 | 42.2 | 19.57 | 0.0769 | 0.29 | 13.08 | 0
February | 18 | 12AM to 1AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
February | 18 | 1AM to 2AM | 51.4 | 46.9 | 42.6 | 40.4 | 18.61 | 0.0774 | 0.27 | 13 | 0
February | 18 | 2AM to 3AM | 49.6 | 45.4 | 41.2 | 38.2 | 17.83 | 0.0776 | 0.26 | 12.95 | 1
February | 18 | 3AM to 4AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
February | 18 | 4AM to 5AM | 47.3 | 43.8 | 40.1 | 36.7 | 17.02 | 0.078 | 0.25 | 12.89 | 1
February | 18 | 5AM to 6AM | 46.8 | 43.8 | 40.8 | 37.7 | 17.05 | 0.0781 | 0.26 | 12.88 | 1
February | 18 | 6AM to 7AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
February | 18 | 7AM to 8AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
February | 18 | 8AM to 9AM | 54 | 49.9 | 46.6 | 47.1 | 20.25 | 0.0769 | 0.32 | 13.09 | 0
February | 18 | 9AM to 10AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
February | 18 | 10AM to 11AM | 60.3 | 53 | 47.3 | 48.4 | 21.99 | 0.076 | 0.33 | 13.25 | 0
February | 18 | 11AM to 12PM | 62.6 | 53.2 | 45.7 | 45.5 | 22.1 | 0.0757 | 0.31 | 13.3 | 0
February | 18 | 12PM to 1PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
February | 18 | 1PM to 2PM | 64.9 | 54.7 | 46.8 | 47.4 | 22.97 | 0.0753 | 0.32 | 13.37 | 0
February | 18 | 2PM to 3PM | 64.9 | 55.8 | 49.1 | 51.8 | 23.66 | 0.0753 | 0.35 | 13.38 | 0
February | 18 | 3PM to 4PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
February | 18 | 4PM to 5PM | 60.3 | 54.4 | 50 | 53.6 | 22.8 | 0.076 | 0.36 | 13.27 | 0
February | 18 | 5PM to 6PM | 55.8 | 51.5 | 48.2 | 50.1 | 21.15 | 0.0766 | 0.34 | 13.14 | 0
February | 18 | 6PM to 7PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
February | 18 | 7PM to 8PM | 50.7 | 48.4 | 46.4 | 46.8 | 19.41 | 0.0774 | 0.32 | 13 | 1
February | 18 | 8PM to 9PM | 50.4 | 48.1 | 46 | 46.1 | 19.23 | 0.0775 | 0.31 | 12.99 | 1
February | 18 | 9PM to 10PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
February | 18 | 10PM to 11PM | 49.6 | 47.5 | 45.7 | 45.5 | 18.96 | 0.0776 | 0.31 | 12.97 | 1
February | 18 | 11PM to 12AM | 49.3 | 47.4 | 45.7 | 45.5 | 18.87 | 0.0776 | 0.31 | 12.96 | 1
February | 19 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
February | 19 | 1AM to 2AM | 48.9 | 47.1 | 45.5 | 45.2 | 18.73 | 0.0777 | 0.31 | 12.95 | 1
February | 19 | 2AM to 3AM | 48.9 | 47.1 | 45.5 | 45.2 | 18.73 | 0.0777 | 0.31 | 12.95 | 1
February | 19 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
February | 19 | 4AM to 5AM | 48.2 | 46.2 | 44.4 | 43.4 | 18.27 | 0.0778 | 0.29 | 12.93 | 1
February | 19 | 5AM to 6AM | 47.7 | 45.4 | 43.3 | 41.6 | 17.87 | 0.0779 | 0.28 | 12.91 | 1
February | 19 | 6AM to 7AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
February | 19 | 7AM to 8AM | 48.4 | 46 | 43.7 | 42.2 | 18.13 | 0.0778 | 0.29 | 12.93 | 1
February | 19 | 8AM to 9AM | 49.6 | 47.2 | 45 | 44.3 | 18.76 | 0.0776 | 0.3 | 12.97 | 1
February | 19 | 9AM to 10AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
February | 19 | 10AM to 11AM | 53.1 | 49.6 | 46.8 | 47.4 | 20.08 | 0.0771 | 0.32 | 13.06 | 0
February | 19 | 11AM to 12PM | 55 | 50.9 | 47.5 | 48.8 | 20.77 | 0.0768 | 0.33 | 13.12 | 0
February | 19 | 12PM to 1PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
February | 19 | 1PM to 2PM | 56.7 | 51.7 | 47.7 | 49.1 | 21.22 | 0.0765 | 0.33 | 13.16 | 0
February | 19 | 2PM to 3PM | 56.3 | 51.2 | 47.1 | 48.1 | 20.97 | 0.0766 | 0.33 | 13.15 | 0
February | 19 | 3PM to 4PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
February | 19 | 4PM to 5PM | 54.3 | 49.7 | 45.9 | 45.8 | 20.14 | 0.0769 | 0.31 | 13.09 | 0
February | 19 | 5PM to 6PM | 52.7 | 48.7 | 45.1 | 44.6 | 19.55 | 0.0771 | 0.3 | 13.05 | 0
February | 19 | 6PM to 7PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
February | 19 | 7PM to 8PM | 50.4 | 47.2 | 44.4 | 43.4 | 18.8 | 0.0775 | 0.29 | 12.98 | 1
February | 19 | 8PM to 9PM | 49.6 | 46.7 | 44.1 | 42.8 | 18.53 | 0.0776 | 0.29 | 12.96 | 1
February | 19 | 9PM to 10PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
February | 19 | 10PM to 11PM | 48.6 | 45.7 | 43 | 41 | 18 | 0.0778 | 0.28 | 12.93 | 1
February | 19 | 11PM to 12AM | 48.4 | 45.4 | 42.4 | 40.2 | 17.82 | 0.0778 | 0.27 | 12.92 | 1
February | 20 | 12AM to 1AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
February | 20 | 1AM to 2AM | 47.7 | 44.4 | 41.2 | 38.2 | 17.35 | 0.0779 | 0.26 | 12.9 | 1
February | 20 | 2AM to 3AM | 47.3 | 44.1 | 40.8 | 37.7 | 17.18 | 0.078 | 0.26 | 12.89 | 1
February | 20 | 3AM to 4AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
February | 20 | 4AM to 5AM | 48 | 44.6 | 41.2 | 38.2 | 17.44 | 0.0779 | 0.26 | 12.91 | 1
February | 20 | 5AM to 6AM | 48.9 | 45.3 | 41.7 | 39.1 | 17.78 | 0.0777 | 0.26 | 12.93 | 1
February | 20 | 6AM to 7AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
February | 20 | 7AM to 8AM | 51.1 | 47.1 | 43.3 | 41.6 | 18.7 | 0.0774 | 0.28 | 13 | 0
February | 20 | 8AM to 9AM | 52 | 47.9 | 44.2 | 43.1 | 19.14 | 0.0773 | 0.29 | 13.02 | 0
February | 20 | 9AM to 10AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
February | 20 | 10AM to 11AM | 53.1 | 48.9 | 45.3 | 44.9 | 19.69 | 0.0771 | 0.3 | 13.06 | 0
February | 20 | 11AM to 12PM | 53.1 | 49.1 | 45.7 | 45.5 | 19.79 | 0.0771 | 0.31 | 13.06 | 0
February | 20 | 12PM to 1PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
February | 20 | 1PM to 2PM | 52.3 | 49.3 | 46.8 | 47.4 | 19.91 | 0.0772 | 0.32 | 13.05 | 0
February | 20 | 2PM to 3PM | 51.8 | 49.3 | 47.1 | 48.1 | 19.88 | 0.0772 | 0.33 | 13.03 | 0
February | 20 | 3PM to 4PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
February | 20 | 4PM to 5PM | 51.1 | 49.2 | 47.7 | 49.1 | 19.86 | 0.0773 | 0.33 | 13.02 | 0
February | 20 | 5PM to 6PM | 51.1 | 49.2 | 47.7 | 49.1 | 19.86 | 0.0773 | 0.33 | 13.02 | 0
February | 20 | 6PM to 7PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
February | 20 | 7PM to 8PM | 51.8 | 49.7 | 48 | 49.8 | 20.14 | 0.0772 | 0.34 | 13.04 | 0
February | 20 | 8PM to 9PM | 52.3 | 50.2 | 48.4 | 50.4 | 20.38 | 0.0771 | 0.34 | 13.06 | 0
February | 20 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 20 | 10PM to 11PM | 53.8 | 51.1 | 48.9 | 51.5 | 20.89 | 0.0769 | 0.35 | 13.1 | 0
February | 20 | 11PM to 12AM | 54.3 | 51.5 | 49.3 | 52.2 | 21.13 | 0.0768 | 0.35 | 13.11 | 0
February | 21 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
February | 21 | 1AM to 2AM | 55.9 | 52.9 | 50.7 | 55.1 | 21.97 | 0.0766 | 0.37 | 13.16 | 0
February | 21 | 2AM to 3AM | 57 | 54.2 | 52.2 | 58.2 | 22.71 | 0.0764 | 0.39 | 13.2 | 0
February | 21 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
February | 21 | 4AM to 5AM | 57 | 54.2 | 52.2 | 58.2 | 22.71 | 0.0764 | 0.39 | 13.2 | 0
February | 21 | 5AM to 6AM | 55.9 | 52.9 | 50.7 | 55.1 | 21.97 | 0.0766 | 0.37 | 13.16 | 0
February | 21 | 6AM to 7AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
February | 21 | 7AM to 8AM | 54.7 | 51.4 | 48.7 | 51.1 | 21.05 | 0.0768 | 0.35 | 13.12 | 0
February | 21 | 8AM to 9AM | 54.3 | 50.8 | 48 | 49.8 | 20.75 | 0.0769 | 0.34 | 13.1 | 0
February | 21 | 9AM to 10AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
February | 21 | 10AM to 11AM | 54.3 | 49.8 | 46 | 46.1 | 20.19 | 0.0769 | 0.31 | 13.09 | 0
February | 21 | 11AM to 12PM | 54.7 | 49.6 | 45.1 | 44.6 | 20.03 | 0.0768 | 0.3 | 13.1 | 0
February | 21 | 12PM to 1PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
February | 21 | 1PM to 2PM | 55 | 49.5 | 44.8 | 44 | 20.03 | 0.0768 | 0.3 | 13.1 | 0
February | 21 | 2PM to 3PM | 55 | 49.7 | 45.1 | 44.6 | 20.12 | 0.0768 | 0.3 | 13.11 | 0
February | 21 | 3PM to 4PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
February | 21 | 4PM to 5PM | 54.7 | 49.6 | 45.3 | 44.9 | 20.08 | 0.0768 | 0.3 | 13.1 | 0
February | 21 | 5PM to 6PM | 54.3 | 49.3 | 45 | 44.3 | 19.9 | 0.0769 | 0.3 | 13.09 | 0
February | 21 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
February | 21 | 7PM to 8PM | 53.6 | 49.2 | 45.3 | 44.9 | 19.82 | 0.077 | 0.3 | 13.07 | 0
February | 21 | 8PM to 9PM | 53.4 | 49.4 | 46 | 46.1 | 19.97 | 0.077 | 0.31 | 13.07 | 0
February | 21 | 9PM to 10PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
February | 21 | 10PM to 11PM | 52 | 48.4 | 45.3 | 44.9 | 19.43 | 0.0772 | 0.3 | 13.03 | 0
February | 21 | 11PM to 12AM | 51.1 | 47.3 | 43.9 | 42.5 | 18.83 | 0.0774 | 0.29 | 13 | 0
February | 22 | 12AM to 1AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
February | 22 | 1AM to 2AM | 48.4 | 44.9 | 41.4 | 38.5 | 17.57 | 0.0778 | 0.26 | 12.92 | 1
February | 22 | 2AM to 3AM | 46.6 | 43.6 | 40.5 | 37.2 | 16.92 | 0.0781 | 0.25 | 12.87 | 1
February | 22 | 3AM to 4AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 22 | 4AM to 5AM | 45.7 | 42.8 | 39.7 | 36.1 | 16.55 | 0.0783 | 0.25 | 12.84 | 1
February | 22 | 5AM to 6AM | 46.2 | 43.2 | 40.1 | 36.7 | 16.76 | 0.0782 | 0.25 | 12.86 | 1
February | 22 | 6AM to 7AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
February | 22 | 7AM to 8AM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
February | 22 | 8AM to 9AM | 51.1 | 47.2 | 43.7 | 42.2 | 18.79 | 0.0774 | 0.29 | 13 | 0
February | 22 | 9AM to 10AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
February | 22 | 10AM to 11AM | 53.8 | 48.3 | 43.3 | 41.6 | 19.35 | 0.077 | 0.28 | 13.07 | 0
February | 22 | 11AM to 12PM | 54.3 | 47.8 | 41.7 | 39.1 | 19.09 | 0.0769 | 0.26 | 13.07 | 0
February | 22 | 12PM to 1PM | 55 | 47.8 | 41 | 38 | 19.1 | 0.0768 | 0.26 | 13.09 | 0
February | 22 | 1PM to 2PM | 55.4 | 47.3 | 39.4 | 35.6 | 18.82 | 0.0768 | 0.24 | 13.09 | 0
February | 22 | 2PM to 3PM | 55.6 | 47 | 38.5 | 34.4 | 18.67 | 0.0768 | 0.23 | 13.09 | 0
February | 22 | 3PM to 4PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
February | 22 | 4PM to 5PM | 55 | 46.3 | 37.2 | 32.7 | 18.28 | 0.0769 | 0.22 | 13.07 | 0
February | 22 | 5PM to 6PM | 54 | 45.6 | 36.9 | 32.3 | 17.95 | 0.077 | 0.22 | 13.04 | 0
February | 22 | 6PM to 7PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
February | 22 | 7PM to 8PM | 52.7 | 45.1 | 37 | 32.5 | 17.68 | 0.0772 | 0.22 | 13.01 | 0
February | 22 | 8PM to 9PM | 52.3 | 45.1 | 37.4 | 33 | 17.67 | 0.0773 | 0.22 | 13 | 0
February | 22 | 9PM to 10PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
February | 22 | 10PM to 11PM | 51.3 | 44.9 | 38.3 | 34.1 | 17.59 | 0.0774 | 0.23 | 12.98 | 0
February | 22 | 11PM to 12AM | 50.7 | 44.9 | 38.8 | 34.9 | 17.57 | 0.0775 | 0.24 | 12.97 | 1
February | 23 | 12AM to 1AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
February | 23 | 1AM to 2AM | 48.9 | 44.6 | 40.3 | 36.9 | 17.45 | 0.0778 | 0.25 | 12.93 | 1
February | 23 | 2AM to 3AM | 48 | 44.8 | 41.5 | 38.8 | 17.52 | 0.0779 | 0.26 | 12.91 | 1
February | 23 | 3AM to 4AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
February | 23 | 4AM to 5AM | 48.9 | 46.1 | 43.5 | 41.9 | 18.22 | 0.0777 | 0.28 | 12.94 | 1
February | 23 | 5AM to 6AM | 51.1 | 47.6 | 44.4 | 43.4 | 18.97 | 0.0774 | 0.29 | 13 | 0
February | 23 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
February | 23 | 7AM to 8AM | 53.4 | 48.6 | 44.4 | 43.4 | 19.54 | 0.077 | 0.29 | 13.06 | 0
February | 23 | 8AM to 9AM | 53.6 | 48.2 | 43.3 | 41.6 | 19.31 | 0.077 | 0.28 | 13.06 | 0
February | 23 | 9AM to 10AM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
February | 23 | 10AM to 11AM | 55 | 47.8 | 40.8 | 37.7 | 19.06 | 0.0768 | 0.26 | 13.09 | 0
February | 23 | 11AM to 12PM | 55.9 | 47.6 | 39.6 | 35.9 | 18.99 | 0.0767 | 0.24 | 13.1 | 0
February | 23 | 12PM to 1PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
February | 23 | 1PM to 2PM | 55.9 | 46.8 | 37.4 | 33 | 18.54 | 0.0767 | 0.22 | 13.09 | 0
February | 23 | 2PM to 3PM | 55 | 46 | 36.5 | 31.8 | 18.14 | 0.0769 | 0.22 | 13.07 | 0
February | 23 | 3PM to 4PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
February | 23 | 4PM to 5PM | 53.1 | 44.6 | 35.2 | 30.2 | 17.42 | 0.0772 | 0.21 | 13.01 | 0
February | 23 | 5PM to 6PM | 52 | 43.9 | 34.9 | 29.8 | 17.09 | 0.0773 | 0.2 | 12.98 | 0
February | 23 | 6PM to 7PM | 51.1 | 43.6 | 35.1 | 30 | 16.91 | 0.0775 | 0.2 | 12.96 | 0
February | 23 | 7PM to 8PM | 50.4 | 43.1 | 34.7 | 29.6 | 16.67 | 0.0776 | 0.2 | 12.94 | 1
February | 23 | 8PM to 9PM | 49.6 | 42.7 | 34.7 | 29.6 | 16.49 | 0.0777 | 0.2 | 12.92 | 1
February | 23 | 9PM to 10PM | 48.9 | 42.5 | 35.1 | 30 | 16.38 | 0.0778 | 0.2 | 12.91 | 1
February | 23 | 10PM to 11PM | 48.6 | 42.3 | 35.1 | 30 | 16.3 | 0.0779 | 0.2 | 12.9 | 1
February | 23 | 11PM to 12AM | 48.4 | 42.3 | 35.2 | 30.2 | 16.29 | 0.0779 | 0.21 | 12.89 | 1
February | 24 | 12AM to 1AM | 48 | 42.4 | 36 | 31.1 | 16.34 | 0.0779 | 0.21 | 12.89 | 1
February | 24 | 1AM to 2AM | 46.9 | 41.6 | 35.4 | 30.5 | 15.97 | 0.0781 | 0.21 | 12.86 | 1
February | 24 | 2AM to 3AM | 46 | 41.1 | 35.4 | 30.5 | 15.75 | 0.0782 | 0.21 | 12.84 | 1
February | 24 | 3AM to 4AM | 45 | 40.8 | 36 | 31.1 | 15.6 | 0.0784 | 0.21 | 12.81 | 1
February | 24 | 4AM to 5AM | 45 | 40.2 | 34.5 | 29.4 | 15.33 | 0.0784 | 0.2 | 12.81 | 1
February | 24 | 5AM to 6AM | 45 | 39.8 | 33.4 | 28.1 | 15.13 | 0.0784 | 0.19 | 12.8 | 1
February | 24 | 6AM to 7AM | 45 | 39.7 | 33.1 | 27.7 | 15.07 | 0.0784 | 0.19 | 12.8 | 1
February | 24 | 7AM to 8AM | 46.6 | 40.9 | 34.2 | 29 | 15.65 | 0.0782 | 0.2 | 12.85 | 1
February | 24 | 8AM to 9AM | 48.4 | 42.5 | 35.8 | 30.9 | 16.39 | 0.0779 | 0.21 | 12.9 | 1
February | 24 | 9AM to 10AM | 50 | 43.8 | 37 | 32.5 | 17.03 | 0.0776 | 0.22 | 12.94 | 1
February | 24 | 10AM to 11AM | 51.6 | 44.5 | 36.9 | 32.3 | 17.38 | 0.0774 | 0.22 | 12.98 | 0
February | 24 | 11AM to 12PM | 53.4 | 45.2 | 36.5 | 31.8 | 17.75 | 0.0771 | 0.22 | 13.03 | 0
February | 24 | 12PM to 1PM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
February | 24 | 1PM to 2PM | 55.4 | 46.5 | 37.2 | 32.7 | 18.37 | 0.0768 | 0.22 | 13.08 | 0
February | 24 | 2PM to 3PM | 55.6 | 46.8 | 37.9 | 33.7 | 18.56 | 0.0768 | 0.23 | 13.09 | 0
February | 24 | 3PM to 4PM | 55.9 | 47.4 | 39 | 35.1 | 18.88 | 0.0767 | 0.24 | 13.1 | 0
February | 24 | 4PM to 5PM | 54.3 | 46.2 | 37.9 | 33.7 | 18.26 | 0.077 | 0.23 | 13.06 | 0
February | 24 | 5PM to 6PM | 52.7 | 45.2 | 37.2 | 32.7 | 17.72 | 0.0772 | 0.22 | 13.01 | 0
February | 24 | 6PM to 7PM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 0
February | 24 | 7PM to 8PM | 50.7 | 44.4 | 37.8 | 33.4 | 17.35 | 0.0775 | 0.23 | 12.96 | 1
February | 24 | 8PM to 9PM | 50.4 | 44.6 | 38.7 | 34.6 | 17.45 | 0.0776 | 0.24 | 12.96 | 1
February | 24 | 9PM to 10PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
February | 24 | 10PM to 11PM | 49.3 | 44 | 38.3 | 34.1 | 17.11 | 0.0777 | 0.23 | 12.93 | 1
February | 24 | 11PM to 12AM | 48.7 | 43.1 | 36.9 | 32.3 | 16.69 | 0.0778 | 0.22 | 12.91 | 1
February | 25 | 12AM to 1AM | 48 | 42.4 | 36 | 31.1 | 16.34 | 0.0779 | 0.21 | 12.89 | 1
February | 25 | 1AM to 2AM | 46.8 | 41.5 | 35.4 | 30.5 | 15.93 | 0.0781 | 0.21 | 12.85 | 1
February | 25 | 2AM to 3AM | 45.3 | 40.8 | 35.4 | 30.5 | 15.58 | 0.0784 | 0.21 | 12.82 | 1
February | 25 | 3AM to 4AM | 44.1 | 40.3 | 36 | 31.1 | 15.38 | 0.0785 | 0.21 | 12.79 | 1
February | 25 | 4AM to 5AM | 43.3 | 39.6 | 35.1 | 30 | 15.03 | 0.0787 | 0.2 | 12.77 | 1
February | 25 | 5AM to 6AM | 42.8 | 39.2 | 34.7 | 29.6 | 14.84 | 0.0788 | 0.2 | 12.75 | 1
February | 25 | 6AM to 7AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
February | 25 | 7AM to 8AM | 45.3 | 41.3 | 36.7 | 32 | 15.82 | 0.0783 | 0.22 | 12.82 | 1
February | 25 | 8AM to 9AM | 48.7 | 44 | 39 | 35.1 | 17.13 | 0.0778 | 0.24 | 12.92 | 1
February | 25 | 9AM to 10AM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
February | 25 | 10AM to 11AM | 53.2 | 45.9 | 38.5 | 34.4 | 18.11 | 0.0771 | 0.23 | 13.03 | 0
February | 25 | 11AM to 12PM | 54.7 | 45.6 | 35.8 | 30.9 | 17.91 | 0.0769 | 0.21 | 13.06 | 0
February | 25 | 12PM to 1PM | 55.9 | 45.5 | 34 | 28.7 | 17.88 | 0.0768 | 0.2 | 13.08 | 0
February | 25 | 1PM to 2PM | 55.9 | 45.7 | 34.5 | 29.4 | 17.98 | 0.0767 | 0.2 | 13.08 | 0
February | 25 | 2PM to 3PM | 55.9 | 46.1 | 35.6 | 30.7 | 18.18 | 0.0767 | 0.21 | 13.09 | 0
February | 25 | 3PM to 4PM | 55.9 | 46.6 | 37 | 32.5 | 18.46 | 0.0767 | 0.22 | 13.09 | 0
February | 25 | 4PM to 5PM | 54.7 | 46.3 | 37.6 | 33.2 | 18.27 | 0.0769 | 0.23 | 13.06 | 0
February | 25 | 5PM to 6PM | 53.2 | 45.9 | 38.5 | 34.4 | 18.11 | 0.0771 | 0.23 | 13.03 | 0
February | 25 | 6PM to 7PM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
February | 25 | 7PM to 8PM | 51.6 | 45.8 | 39.9 | 36.4 | 18.02 | 0.0774 | 0.25 | 13 | 0
February | 25 | 8PM to 9PM | 51.4 | 45.8 | 40.3 | 36.9 | 18.06 | 0.0774 | 0.25 | 12.99 | 0
February | 25 | 9PM to 10PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
February | 25 | 10PM to 11PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
February | 25 | 11PM to 12AM | 49.1 | 44.3 | 39.4 | 35.6 | 17.3 | 0.0777 | 0.24 | 12.93 | 1
February | 26 | 12AM to 1AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
February | 26 | 1AM to 2AM | 46.4 | 42.3 | 37.8 | 33.4 | 16.3 | 0.0782 | 0.23 | 12.85 | 1
February | 26 | 2AM to 3AM | 44.6 | 41.1 | 37.2 | 32.7 | 15.76 | 0.0785 | 0.22 | 12.81 | 1
February | 26 | 3AM to 4AM | 43 | 40.2 | 37 | 32.5 | 15.33 | 0.0787 | 0.22 | 12.76 | 1
February | 26 | 4AM to 5AM | 42.3 | 39.5 | 36.1 | 31.3 | 14.98 | 0.0788 | 0.21 | 12.74 | 1
February | 26 | 5AM to 6AM | 41.7 | 39 | 35.8 | 30.9 | 14.78 | 0.0789 | 0.21 | 12.73 | 1
February | 26 | 6AM to 7AM | 41 | 38.7 | 36 | 31.1 | 14.64 | 0.079 | 0.21 | 12.71 | 1
February | 26 | 7AM to 8AM | 44.4 | 41.1 | 37.4 | 33 | 15.75 | 0.0785 | 0.22 | 12.8 | 1
February | 26 | 8AM to 9AM | 47.7 | 43.6 | 39.4 | 35.6 | 16.95 | 0.078 | 0.24 | 12.89 | 1
February | 26 | 9AM to 10AM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
February | 26 | 10AM to 11AM | 52.7 | 46.7 | 40.8 | 37.7 | 18.49 | 0.0772 | 0.26 | 13.03 | 0
February | 26 | 11AM to 12PM | 54.3 | 47.3 | 40.5 | 37.2 | 18.8 | 0.0769 | 0.25 | 13.07 | 0
February | 26 | 12PM to 1PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
February | 26 | 1PM to 2PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
February | 26 | 2PM to 3PM | 57.9 | 50.4 | 43.9 | 42.5 | 20.49 | 0.0764 | 0.29 | 13.17 | 0
February | 26 | 3PM to 4PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
February | 26 | 4PM to 5PM | 57.4 | 51 | 45.7 | 45.5 | 20.84 | 0.0764 | 0.31 | 13.17 | 0
February | 26 | 5PM to 6PM | 55.6 | 50.2 | 45.7 | 45.5 | 20.4 | 0.0767 | 0.31 | 13.12 | 0
February | 26 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
February | 26 | 7PM to 8PM | 53.6 | 49.3 | 45.7 | 45.5 | 19.92 | 0.077 | 0.31 | 13.07 | 0
February | 26 | 8PM to 9PM | 53.4 | 49.3 | 45.7 | 45.5 | 19.87 | 0.077 | 0.31 | 13.07 | 0
February | 26 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
February | 26 | 10PM to 11PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
February | 26 | 11PM to 12AM | 51.1 | 47.6 | 44.4 | 43.4 | 18.97 | 0.0774 | 0.29 | 13 | 0
February | 27 | 12AM to 1AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
February | 27 | 1AM to 2AM | 48.7 | 45.5 | 42.4 | 40.2 | 17.91 | 0.0778 | 0.27 | 12.93 | 1
February | 27 | 2AM to 3AM | 47.3 | 44.4 | 41.5 | 38.8 | 17.35 | 0.078 | 0.26 | 12.89 | 1
February | 27 | 3AM to 4AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
February | 27 | 4AM to 5AM | 45.7 | 43 | 40.1 | 36.7 | 16.63 | 0.0783 | 0.25 | 12.85 | 1
February | 27 | 5AM to 6AM | 45.3 | 42.6 | 39.7 | 36.1 | 16.46 | 0.0783 | 0.25 | 12.83 | 1
February | 27 | 6AM to 7AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 27 | 7AM to 8AM | 47.3 | 44.5 | 41.7 | 39.1 | 17.39 | 0.078 | 0.26 | 12.89 | 1
February | 27 | 8AM to 9AM | 49.6 | 46.7 | 44.1 | 42.8 | 18.53 | 0.0776 | 0.29 | 12.96 | 1
February | 27 | 9AM to 10AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
February | 27 | 10AM to 11AM | 54.7 | 49.4 | 44.8 | 44 | 19.94 | 0.0768 | 0.3 | 13.1 | 0
February | 27 | 11AM to 12PM | 57.4 | 50 | 43.5 | 41.9 | 20.27 | 0.0765 | 0.28 | 13.16 | 0
February | 27 | 12PM to 1PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
February | 27 | 1PM to 2PM | 60.8 | 51.3 | 43.2 | 41.3 | 21.01 | 0.076 | 0.28 | 13.24 | 0
February | 27 | 2PM to 3PM | 61.3 | 51.9 | 43.9 | 42.5 | 21.32 | 0.0759 | 0.29 | 13.26 | 0
February | 27 | 3PM to 4PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
February | 27 | 4PM to 5PM | 59.4 | 51.5 | 45 | 44.3 | 21.12 | 0.0761 | 0.3 | 13.22 | 0
February | 27 | 5PM to 6PM | 56.7 | 50.5 | 45.3 | 44.9 | 20.56 | 0.0765 | 0.3 | 13.15 | 0
February | 27 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
February | 27 | 7PM to 8PM | 53.6 | 49.3 | 45.7 | 45.5 | 19.92 | 0.077 | 0.31 | 13.07 | 0
February | 27 | 8PM to 9PM | 53.4 | 49.3 | 45.7 | 45.5 | 19.87 | 0.077 | 0.31 | 13.07 | 0
February | 27 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
February | 27 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
February | 27 | 11PM to 12AM | 53.1 | 49.4 | 46.2 | 46.5 | 19.93 | 0.0771 | 0.31 | 13.06 | 0
February | 28 | 12AM to 1AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
February | 28 | 1AM to 2AM | 52.7 | 49.3 | 46.4 | 46.8 | 19.9 | 0.0771 | 0.32 | 13.05 | 0
February | 28 | 2AM to 3AM | 52.3 | 49.1 | 46.4 | 46.8 | 19.81 | 0.0772 | 0.32 | 13.04 | 0
February | 28 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
February | 28 | 4AM to 5AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
February | 28 | 5AM to 6AM | 52 | 48.6 | 45.7 | 45.5 | 19.52 | 0.0772 | 0.31 | 13.03 | 0
February | 28 | 6AM to 7AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
February | 28 | 7AM to 8AM | 51.3 | 48 | 45.1 | 44.6 | 19.2 | 0.0774 | 0.3 | 13.01 | 0
February | 28 | 8AM to 9AM | 50.7 | 47.6 | 44.8 | 44 | 18.98 | 0.0774 | 0.3 | 12.99 | 1
February | 28 | 9AM to 10AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
February | 28 | 10AM to 11AM | 51.6 | 46.7 | 42.1 | 39.6 | 18.52 | 0.0773 | 0.27 | 13 | 0
February | 28 | 11AM to 12PM | 53.4 | 46.7 | 40.1 | 36.7 | 18.5 | 0.0771 | 0.25 | 13.04 | 0
February | 28 | 12PM to 1PM | 55 | 47 | 39 | 35.1 | 18.66 | 0.0768 | 0.24 | 13.08 | 0
February | 28 | 1PM to 2PM | 54.7 | 46.2 | 37.4 | 33 | 18.23 | 0.0769 | 0.22 | 13.06 | 0
February | 28 | 2PM to 3PM | 54.3 | 45.7 | 36.5 | 31.8 | 17.97 | 0.077 | 0.22 | 13.05 | 0
February | 28 | 3PM to 4PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
February | 28 | 4PM to 5PM | 52.3 | 44.5 | 36 | 31.1 | 17.38 | 0.0773 | 0.21 | 13 | 0
February | 28 | 5PM to 6PM | 50.5 | 43.8 | 36.3 | 31.6 | 17.02 | 0.0775 | 0.21 | 12.95 | 1
February | 28 | 6PM to 7PM | 48.9 | 43.3 | 37 | 32.5 | 16.77 | 0.0778 | 0.22 | 12.92 | 1
February | 28 | 7PM to 8PM | 48.2 | 42.3 | 35.4 | 30.5 | 16.28 | 0.0779 | 0.21 | 12.89 | 1
February | 28 | 8PM to 9PM | 47.7 | 41.5 | 34.2 | 29 | 15.91 | 0.078 | 0.2 | 12.87 | 1
February | 28 | 9PM to 10PM | 47.8 | 42.4 | 36.3 | 31.6 | 16.36 | 0.078 | 0.21 | 12.89 | 1
February | 28 | 10PM to 11PM | 48 | 43.3 | 38.3 | 34.1 | 16.8 | 0.0779 | 0.23 | 12.9 | 1
February | 28 | 11PM to 12AM | 48.2 | 44.4 | 40.5 | 37.2 | 17.32 | 0.0779 | 0.25 | 12.91 | 1
March | 1 | 12AM to 1AM | 48.4 | 45.4 | 42.6 | 40.4 | 17.87 | 0.0778 | 0.27 | 12.92 | 1
March | 1 | 1AM to 2AM | 48.6 | 46.6 | 44.8 | 44 | 18.45 | 0.0778 | 0.3 | 12.94 | 1
March | 1 | 2AM to 3AM | 48.7 | 47.7 | 46.8 | 47.4 | 19.03 | 0.0777 | 0.32 | 12.95 | 1
March | 1 | 3AM to 4AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 1 | 4AM to 5AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 5AM to 6AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 1 | 6AM to 7AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 1 | 7AM to 8AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 8AM to 9AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 9AM to 10AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 10AM to 11AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 11AM to 12PM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
March | 1 | 12PM to 1PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
March | 1 | 1PM to 2PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
March | 1 | 2PM to 3PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
March | 1 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
March | 1 | 4PM to 5PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
March | 1 | 5PM to 6PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
March | 1 | 6PM to 7PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
March | 1 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
March | 1 | 8PM to 9PM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
March | 1 | 9PM to 10PM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
March | 1 | 10PM to 11PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
March | 1 | 11PM to 12AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
March | 2 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 2 | 1AM to 2AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
March | 2 | 2AM to 3AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
March | 2 | 3AM to 4AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 2 | 4AM to 5AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 2 | 5AM to 6AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 2 | 6AM to 7AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
March | 2 | 7AM to 8AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 2 | 8AM to 9AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
March | 2 | 9AM to 10AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
March | 2 | 10AM to 11AM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
March | 2 | 11AM to 12PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
March | 2 | 12PM to 1PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
March | 2 | 1PM to 2PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
March | 2 | 2PM to 3PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
March | 2 | 3PM to 4PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
March | 2 | 4PM to 5PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
March | 2 | 5PM to 6PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
March | 2 | 6PM to 7PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
March | 2 | 7PM to 8PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
March | 2 | 8PM to 9PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 2 | 9PM to 10PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 2 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 2 | 11PM to 12AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 3 | 12AM to 1AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 3 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 3 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 3 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
March | 3 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 3 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 3 | 6AM to 7AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 3 | 7AM to 8AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 3 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
March | 3 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
March | 3 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
March | 3 | 11AM to 12PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
March | 3 | 12PM to 1PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
March | 3 | 1PM to 2PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
March | 3 | 2PM to 3PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
March | 3 | 3PM to 4PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
March | 3 | 4PM to 5PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
March | 3 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
March | 3 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
March | 3 | 7PM to 8PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
March | 3 | 8PM to 9PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
March | 3 | 9PM to 10PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
March | 3 | 10PM to 11PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
March | 3 | 11PM to 12AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 4 | 12AM to 1AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 4 | 1AM to 2AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 2AM to 3AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 3AM to 4AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 4 | 4AM to 5AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 5AM to 6AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 6AM to 7AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 7AM to 8AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 8AM to 9AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 4 | 9AM to 10AM | 55 | 55 | 55 | 64.7 | 23.25 | 0.0767 | 0.44 | 13.17 | 0
March | 4 | 10AM to 11AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 11AM to 12PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
March | 4 | 12PM to 1PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
March | 4 | 1PM to 2PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
March | 4 | 2PM to 3PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
March | 4 | 3PM to 4PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
March | 4 | 4PM to 5PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
March | 4 | 5PM to 6PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 6PM to 7PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
March | 4 | 7PM to 8PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 8PM to 9PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 9PM to 10PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
March | 4 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 11PM to 12AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 5 | 12AM to 1AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
March | 5 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 5 | 2AM to 3AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 5 | 3AM to 4AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
March | 5 | 4AM to 5AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 5 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 5 | 6AM to 7AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 5 | 7AM to 8AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 5 | 8AM to 9AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
March | 5 | 9AM to 10AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
March | 5 | 10AM to 11AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 5 | 11AM to 12PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 5 | 12PM to 1PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 5 | 1PM to 2PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 5 | 2PM to 3PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 5 | 3PM to 4PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
March | 5 | 4PM to 5PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 5 | 5PM to 6PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 5 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 5 | 7PM to 8PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 5 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 5 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
March | 5 | 10PM to 11PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
March | 5 | 11PM to 12AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 6 | 12AM to 1AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 6 | 1AM to 2AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 6 | 2AM to 3AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 6 | 3AM to 4AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 6 | 4AM to 5AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 6 | 5AM to 6AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 6 | 6AM to 7AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 6 | 7AM to 8AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 6 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 6 | 9AM to 10AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
March | 6 | 10AM to 11AM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
March | 6 | 11AM to 12PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
March | 6 | 12PM to 1PM | 66 | 53.9 | 44.1 | 42.8 | 22.51 | 0.0752 | 0.29 | 13.38 | 0
March | 6 | 1PM to 2PM | 68 | 54.7 | 44.1 | 42.8 | 22.99 | 0.0749 | 0.29 | 13.43 | 0
March | 6 | 2PM to 3PM | 66.9 | 56.5 | 48.9 | 51.5 | 24.08 | 0.075 | 0.35 | 13.43 | 0
March | 6 | 3PM to 4PM | 64.9 | 54.8 | 46.9 | 47.8 | 23.02 | 0.0753 | 0.32 | 13.37 | 0
March | 6 | 4PM to 5PM | 63 | 52.2 | 43 | 41 | 21.49 | 0.0756 | 0.28 | 13.3 | 0
March | 6 | 5PM to 6PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
March | 6 | 6PM to 7PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
March | 6 | 7PM to 8PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
March | 6 | 8PM to 9PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
March | 6 | 9PM to 10PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 6 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 6 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 7 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 7 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
March | 7 | 2AM to 3AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
March | 7 | 3AM to 4AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 7 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 7 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 7 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 7 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 7 | 8AM to 9AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
March | 7 | 9AM to 10AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
March | 7 | 10AM to 11AM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
March | 7 | 11AM to 12PM | 69.1 | 52.8 | 37.9 | 33.7 | 21.83 | 0.0748 | 0.23 | 13.43 | 0
March | 7 | 12PM to 1PM | 71.1 | 51.4 | 30.9 | 25.2 | 20.99 | 0.0746 | 0.17 | 13.46 | 0
March | 7 | 1PM to 2PM | 71.1 | 52.7 | 35.1 | 30 | 21.74 | 0.0746 | 0.2 | 13.47 | 0
March | 7 | 2PM to 3PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
March | 7 | 3PM to 4PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
March | 7 | 4PM to 5PM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
March | 7 | 5PM to 6PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 7 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
March | 7 | 7PM to 8PM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
March | 7 | 8PM to 9PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
March | 7 | 9PM to 10PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 7 | 10PM to 11PM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 7 | 11PM to 12AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 8 | 12AM to 1AM | 48 | 48 | 48 | 49.8 | 19.22 | 0.0778 | 0.34 | 12.94 | 1
March | 8 | 1AM to 2AM | 48 | 48 | 48 | 49.8 | 19.22 | 0.0778 | 0.34 | 12.94 | 1
March | 8 | 2AM to 3AM | 46.9 | 46.9 | 46.9 | 47.8 | 18.65 | 0.078 | 0.32 | 12.91 | 1
March | 8 | 3AM to 4AM | 46 | 46 | 46 | 46.1 | 18.18 | 0.0781 | 0.31 | 12.88 | 1
March | 8 | 4AM to 5AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
March | 8 | 5AM to 6AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
March | 8 | 6AM to 7AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
March | 8 | 7AM to 8AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
March | 8 | 8AM to 9AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
March | 8 | 9AM to 10AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 8 | 10AM to 11AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 8 | 11AM to 12PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
March | 8 | 12PM to 1PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
March | 8 | 1PM to 2PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
March | 8 | 2PM to 3PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
March | 8 | 3PM to 4PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
March | 8 | 4PM to 5PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
March | 8 | 5PM to 6PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 8 | 6PM to 7PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 8 | 7PM to 8PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
March | 8 | 8PM to 9PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 8 | 9PM to 10PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 8 | 10PM to 11PM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 8 | 11PM to 12AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 9 | 12AM to 1AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 9 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 9 | 2AM to 3AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 9 | 3AM to 4AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 9 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 9 | 5AM to 6AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 9 | 6AM to 7AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 9 | 7AM to 8AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 9 | 8AM to 9AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 9 | 9AM to 10AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 9 | 10AM to 11AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 9 | 11AM to 12PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
March | 9 | 12PM to 1PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
March | 9 | 1PM to 2PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
March | 9 | 2PM to 3PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
March | 9 | 3PM to 4PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 9 | 4PM to 5PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 9 | 5PM to 6PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 9 | 6PM to 7PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 9 | 7PM to 8PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 9 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 9 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 9 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 9 | 11PM to 12AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
March | 10 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
March | 10 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 10 | 2AM to 3AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
March | 10 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
March | 10 | 4AM to 5AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 10 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 10 | 6AM to 7AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
March | 10 | 7AM to 8AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
March | 10 | 8AM to 9AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
March | 10 | 9AM to 10AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
March | 10 | 10AM to 11AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
March | 10 | 11AM to 12PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
March | 10 | 12PM to 1PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
March | 10 | 1PM to 2PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
March | 10 | 2PM to 3PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
March | 10 | 3PM to 4PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
March | 10 | 4PM to 5PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
March | 10 | 5PM to 6PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
March | 10 | 6PM to 7PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
March | 10 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 10 | 8PM to 9PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
March | 10 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
March | 10 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
March | 10 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
March | 11 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 11 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 11 | 2AM to 3AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 11 | 3AM to 4AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 11 | 4AM to 5AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
March | 11 | 5AM to 6AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 11 | 6AM to 7AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 11 | 7AM to 8AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
March | 11 | 8AM to 9AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 11 | 9AM to 10AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 11 | 10AM to 11AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 11 | 11AM to 12PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
March | 11 | 12PM to 1PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
March | 11 | 1PM to 2PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
March | 11 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
March | 11 | 3PM to 4PM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
March | 11 | 4PM to 5PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
March | 11 | 5PM to 6PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
March | 11 | 6PM to 7PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 11 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 11 | 8PM to 9PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 11 | 9PM to 10PM | 62.1 | 49.1 | 36 | 31.1 | 19.73 | 0.0758 | 0.21 | 13.24 | 0
March | 11 | 10PM to 11PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
March | 11 | 11PM to 12AM | 59 | 50.5 | 43 | 41 | 20.53 | 0.0762 | 0.28 | 13.2 | 0
March | 12 | 12AM to 1AM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
March | 12 | 1AM to 2AM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
March | 12 | 2AM to 3AM | 61 | 47.9 | 34 | 28.7 | 19.1 | 0.076 | 0.2 | 13.21 | 0
March | 12 | 3AM to 4AM | 59 | 47.7 | 36 | 31.1 | 18.99 | 0.0763 | 0.21 | 13.17 | 0
March | 12 | 4AM to 5AM | 59 | 47.7 | 36 | 31.1 | 18.99 | 0.0763 | 0.21 | 13.17 | 0
March | 12 | 5AM to 6AM | 57.9 | 47.9 | 37.9 | 33.7 | 19.13 | 0.0764 | 0.23 | 13.15 | 0
March | 12 | 6AM to 7AM | 59 | 46.7 | 33.1 | 27.7 | 18.47 | 0.0763 | 0.19 | 13.16 | 0
March | 12 | 7AM to 8AM | 60.1 | 48.6 | 37 | 32.5 | 19.47 | 0.0761 | 0.22 | 13.2 | 0
March | 12 | 8AM to 9AM | 62.1 | 50.2 | 39 | 35.1 | 20.36 | 0.0758 | 0.24 | 13.26 | 0
March | 12 | 9AM to 10AM | 64.9 | 51.8 | 39.9 | 36.4 | 21.25 | 0.0754 | 0.25 | 13.33 | 0
March | 12 | 10AM to 11AM | 68 | 51 | 34 | 28.7 | 20.8 | 0.075 | 0.2 | 13.39 | 0
March | 12 | 11AM to 12PM | 70 | 52.5 | 36 | 31.1 | 21.65 | 0.0747 | 0.21 | 13.45 | 0
March | 12 | 12PM to 1PM | 72 | 52.7 | 34 | 28.7 | 21.76 | 0.0744 | 0.2 | 13.49 | 0
March | 12 | 1PM to 2PM | 73.9 | 53 | 32 | 26.5 | 21.89 | 0.0742 | 0.18 | 13.53 | 0
March | 12 | 2PM to 3PM | 75 | 52.8 | 30 | 24.2 | 21.79 | 0.074 | 0.16 | 13.55 | 0
March | 12 | 3PM to 4PM | 75 | 53.1 | 30.9 | 25.2 | 21.95 | 0.074 | 0.17 | 13.56 | 0
March | 12 | 4PM to 5PM | 73.9 | 53.9 | 35.1 | 30 | 22.44 | 0.0742 | 0.2 | 13.54 | 0
March | 12 | 5PM to 6PM | 71.1 | 51.7 | 32 | 26.5 | 21.2 | 0.0746 | 0.18 | 13.46 | 0
March | 12 | 6PM to 7PM | 66 | 53.1 | 42.1 | 39.6 | 22.01 | 0.0752 | 0.27 | 13.37 | 0
March | 12 | 7PM to 8PM | 63 | 50.9 | 39.9 | 36.4 | 20.77 | 0.0757 | 0.25 | 13.28 | 0
March | 12 | 8PM to 9PM | 61 | 49 | 37 | 32.5 | 19.68 | 0.076 | 0.22 | 13.22 | 0
March | 12 | 9PM to 10PM | 59 | 48.4 | 37.9 | 33.7 | 19.39 | 0.0763 | 0.23 | 13.17 | 0
March | 12 | 10PM to 11PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
March | 12 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
March | 13 | 12AM to 1AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
March | 13 | 1AM to 2AM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 0
March | 13 | 2AM to 3AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
March | 13 | 3AM to 4AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
March | 13 | 4AM to 5AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
March | 13 | 5AM to 6AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
March | 13 | 6AM to 7AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
March | 13 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
March | 13 | 8AM to 9AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
March | 13 | 9AM to 10AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
March | 13 | 10AM to 11AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
March | 13 | 11AM to 12PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
March | 13 | 12PM to 1PM | 69.1 | 56 | 46 | 46.1 | 23.78 | 0.0747 | 0.31 | 13.47 | 0
March | 13 | 1PM to 2PM | 73 | 54.8 | 39 | 35.1 | 23.02 | 0.0742 | 0.24 | 13.54 | 0
March | 13 | 2PM to 3PM | 73 | 57.1 | 45 | 44.3 | 24.45 | 0.0742 | 0.3 | 13.56 | 0
March | 13 | 3PM to 4PM | 75 | 54.3 | 35.1 | 30 | 22.7 | 0.074 | 0.2 | 13.57 | 0
March | 13 | 4PM to 5PM | 73 | 52.9 | 33.1 | 27.7 | 21.86 | 0.0743 | 0.19 | 13.51 | 0
March | 13 | 5PM to 6PM | 68 | 52.4 | 37.9 | 33.7 | 21.57 | 0.075 | 0.23 | 13.4 | 0
March | 13 | 6PM to 7PM | 62.1 | 50.5 | 39.9 | 36.4 | 20.55 | 0.0758 | 0.25 | 13.26 | 0
March | 13 | 7PM to 8PM | 61 | 50.5 | 41 | 38 | 20.54 | 0.0759 | 0.26 | 13.24 | 0
March | 13 | 8PM to 9PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
March | 13 | 9PM to 10PM | 57.9 | 49.6 | 42.1 | 39.6 | 20.05 | 0.0764 | 0.27 | 13.17 | 0
March | 13 | 10PM to 11PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
March | 13 | 11PM to 12AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 14 | 12AM to 1AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
March | 14 | 1AM to 2AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
March | 14 | 2AM to 3AM | 50 | 43.4 | 36 | 31.1 | 16.82 | 0.0776 | 0.21 | 12.94 | 1
March | 14 | 3AM to 4AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 14 | 4AM to 5AM | 48 | 48 | 48 | 49.8 | 19.22 | 0.0778 | 0.34 | 12.94 | 1
March | 14 | 5AM to 6AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
March | 14 | 6AM to 7AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
March | 14 | 7AM to 8AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 14 | 8AM to 9AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
March | 14 | 9AM to 10AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
March | 14 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
March | 14 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
March | 14 | 12PM to 1PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
March | 14 | 1PM to 2PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
March | 14 | 2PM to 3PM | 72 | 55.1 | 41 | 38 | 23.2 | 0.0744 | 0.26 | 13.52 | 0
March | 14 | 3PM to 4PM | 66 | 50.5 | 35.1 | 30 | 20.52 | 0.0753 | 0.2 | 13.34 | 0
March | 14 | 4PM to 5PM | 64 | 51.1 | 39 | 35.1 | 20.84 | 0.0755 | 0.24 | 13.31 | 0
March | 14 | 5PM to 6PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
March | 14 | 6PM to 7PM | 57 | 46.4 | 35.1 | 30 | 18.34 | 0.0766 | 0.2 | 13.11 | 0
March | 14 | 7PM to 8PM | 55.9 | 46.2 | 36 | 31.1 | 18.25 | 0.0767 | 0.21 | 13.09 | 0
March | 14 | 8PM to 9PM | 55 | 47.8 | 41 | 38 | 19.1 | 0.0768 | 0.26 | 13.09 | 0
March | 14 | 9PM to 10PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
March | 14 | 10PM to 11PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
March | 14 | 11PM to 12AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
March | 15 | 12AM to 1AM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
March | 15 | 1AM to 2AM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
March | 15 | 2AM to 3AM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
March | 15 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 15 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 15 | 5AM to 6AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 15 | 6AM to 7AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 15 | 7AM to 8AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 15 | 8AM to 9AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
March | 15 | 9AM to 10AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
March | 15 | 10AM to 11AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
March | 15 | 11AM to 12PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
March | 15 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
March | 15 | 1PM to 2PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
March | 15 | 2PM to 3PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
March | 15 | 3PM to 4PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
March | 15 | 4PM to 5PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
March | 15 | 5PM to 6PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
March | 15 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
March | 15 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 15 | 8PM to 9PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 15 | 9PM to 10PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 15 | 10PM to 11PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 15 | 11PM to 12AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 16 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 16 | 1AM to 2AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
March | 16 | 2AM to 3AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
March | 16 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
March | 16 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 16 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 16 | 6AM to 7AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
March | 16 | 7AM to 8AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
March | 16 | 8AM to 9AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
March | 16 | 9AM to 10AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 16 | 10AM to 11AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 16 | 11AM to 12PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 16 | 12PM to 1PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 16 | 1PM to 2PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 16 | 2PM to 3PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
March | 16 | 3PM to 4PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
March | 16 | 4PM to 5PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 16 | 5PM to 6PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
March | 16 | 6PM to 7PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
March | 16 | 7PM to 8PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
March | 16 | 8PM to 9PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
March | 16 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
March | 16 | 10PM to 11PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
March | 16 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 17 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 17 | 1AM to 2AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
March | 17 | 2AM to 3AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
March | 17 | 3AM to 4AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
March | 17 | 4AM to 5AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
March | 17 | 5AM to 6AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
March | 17 | 6AM to 7AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
March | 17 | 7AM to 8AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
March | 17 | 8AM to 9AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
March | 17 | 9AM to 10AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 17 | 10AM to 11AM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
March | 17 | 11AM to 12PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
March | 17 | 12PM to 1PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
March | 17 | 1PM to 2PM | 62.1 | 50.5 | 39.9 | 36.4 | 20.55 | 0.0758 | 0.25 | 13.26 | 0
March | 17 | 2PM to 3PM | 64 | 52.3 | 42.1 | 39.6 | 21.53 | 0.0755 | 0.27 | 13.32 | 0
March | 17 | 3PM to 4PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
March | 17 | 4PM to 5PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
March | 17 | 5PM to 6PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
March | 17 | 6PM to 7PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 17 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
March | 17 | 8PM to 9PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 17 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 17 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 17 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 18 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 4AM to 5AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 18 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 18 | 6AM to 7AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 18 | 8AM to 9AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
March | 18 | 9AM to 10AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 18 | 10AM to 11AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 18 | 11AM to 12PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
March | 18 | 12PM to 1PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
March | 18 | 1PM to 2PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
March | 18 | 2PM to 3PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
March | 18 | 3PM to 4PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
March | 18 | 4PM to 5PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 18 | 5PM to 6PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
March | 18 | 6PM to 7PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
March | 18 | 7PM to 8PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 18 | 9PM to 10PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 18 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 18 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 19 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 19 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 19 | 2AM to 3AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 19 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 19 | 4AM to 5AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
March | 19 | 5AM to 6AM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
March | 19 | 6AM to 7AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 19 | 7AM to 8AM | 50 | 43 | 35.1 | 30 | 16.64 | 0.0776 | 0.2 | 12.94 | 1
March | 19 | 8AM to 9AM | 51.1 | 43.9 | 36 | 31.1 | 17.08 | 0.0775 | 0.21 | 12.97 | 0
March | 19 | 9AM to 10AM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
March | 19 | 10AM to 11AM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
March | 19 | 11AM to 12PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
March | 19 | 12PM to 1PM | 57.9 | 48.3 | 39 | 35.1 | 19.35 | 0.0764 | 0.24 | 13.15 | 0
March | 19 | 1PM to 2PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
March | 19 | 2PM to 3PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
March | 19 | 3PM to 4PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
March | 19 | 4PM to 5PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
March | 19 | 5PM to 6PM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
March | 19 | 6PM to 7PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
March | 19 | 7PM to 8PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
March | 19 | 8PM to 9PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
March | 19 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
March | 19 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 19 | 11PM to 12AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 20 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 20 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 20 | 2AM to 3AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 20 | 3AM to 4AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
March | 20 | 4AM to 5AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
March | 20 | 5AM to 6AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
March | 20 | 6AM to 7AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
March | 20 | 7AM to 8AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
March | 20 | 8AM to 9AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 20 | 9AM to 10AM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
March | 20 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
March | 20 | 11AM to 12PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
March | 20 | 12PM to 1PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
March | 20 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
March | 20 | 2PM to 3PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
March | 20 | 3PM to 4PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
March | 20 | 4PM to 5PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
March | 20 | 5PM to 6PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
March | 20 | 6PM to 7PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
March | 20 | 7PM to 8PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
March | 20 | 8PM to 9PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
March | 20 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
March | 20 | 10PM to 11PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
March | 20 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
March | 21 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
March | 21 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 21 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 21 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 21 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 21 | 5AM to 6AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 21 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 21 | 7AM to 8AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 21 | 8AM to 9AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
March | 21 | 9AM to 10AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
March | 21 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
March | 21 | 11AM to 12PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
March | 21 | 12PM to 1PM | 60.1 | 49.7 | 39.9 | 36.4 | 20.07 | 0.0761 | 0.25 | 13.21 | 0
March | 21 | 1PM to 2PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
March | 21 | 2PM to 3PM | 57 | 46.8 | 36 | 31.1 | 18.51 | 0.0766 | 0.21 | 13.12 | 0
March | 21 | 3PM to 4PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
March | 21 | 4PM to 5PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
March | 21 | 5PM to 6PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
March | 21 | 6PM to 7PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 0
March | 21 | 7PM to 8PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
March | 21 | 8PM to 9PM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
March | 21 | 9PM to 10PM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
March | 21 | 10PM to 11PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
March | 21 | 11PM to 12AM | 48 | 42.8 | 37 | 32.5 | 16.55 | 0.0779 | 0.22 | 12.89 | 1
March | 22 | 12AM to 1AM | 48 | 42 | 35.1 | 30 | 16.17 | 0.0779 | 0.2 | 12.89 | 1
March | 22 | 1AM to 2AM | 46.9 | 41.1 | 34 | 28.7 | 15.71 | 0.0781 | 0.2 | 12.85 | 1
March | 22 | 2AM to 3AM | 46.9 | 41.1 | 34 | 28.7 | 15.71 | 0.0781 | 0.2 | 12.85 | 1
March | 22 | 3AM to 4AM | 48 | 42 | 35.1 | 30 | 16.17 | 0.0779 | 0.2 | 12.89 | 1
March | 22 | 4AM to 5AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 22 | 5AM to 6AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 22 | 6AM to 7AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
March | 22 | 7AM to 8AM | 48.9 | 44.1 | 39 | 35.1 | 17.17 | 0.0778 | 0.24 | 12.92 | 1
March | 22 | 8AM to 9AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
March | 22 | 9AM to 10AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
March | 22 | 10AM to 11AM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
March | 22 | 11AM to 12PM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
March | 22 | 12PM to 1PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
March | 22 | 1PM to 2PM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
March | 22 | 2PM to 3PM | 52 | 44.8 | 37 | 32.5 | 17.51 | 0.0773 | 0.22 | 12.99 | 0
March | 22 | 3PM to 4PM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 0
March | 22 | 4PM to 5PM | 50 | 43 | 35.1 | 30 | 16.64 | 0.0776 | 0.2 | 12.94 | 1
March | 22 | 5PM to 6PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
March | 22 | 6PM to 7PM | 48 | 41.6 | 34 | 28.7 | 15.97 | 0.078 | 0.2 | 12.88 | 1
March | 22 | 7PM to 8PM | 48 | 42 | 35.1 | 30 | 16.17 | 0.0779 | 0.2 | 12.89 | 1
March | 22 | 8PM to 9PM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 22 | 9PM to 10PM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 22 | 10PM to 11PM | 44.1 | 40.8 | 37 | 32.5 | 15.59 | 0.0785 | 0.22 | 12.79 | 1
March | 22 | 11PM to 12AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
March | 23 | 12AM to 1AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
March | 23 | 1AM to 2AM | 41 | 39.2 | 37 | 32.5 | 14.85 | 0.079 | 0.22 | 12.71 | 1
March | 23 | 2AM to 3AM | 43 | 40.2 | 37 | 32.5 | 15.33 | 0.0787 | 0.22 | 12.76 | 1
March | 23 | 3AM to 4AM | 41 | 39.2 | 37 | 32.5 | 14.85 | 0.079 | 0.22 | 12.71 | 1
March | 23 | 4AM to 5AM | 39.9 | 38.6 | 37 | 32.5 | 14.59 | 0.0792 | 0.22 | 12.69 | 1
March | 23 | 5AM to 6AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0792 | 0.23 | 12.69 | 1
March | 23 | 6AM to 7AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
March | 23 | 7AM to 8AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
March | 23 | 8AM to 9AM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
March | 23 | 9AM to 10AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
March | 23 | 10AM to 11AM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
March | 23 | 11AM to 12PM | 55 | 47.4 | 39.9 | 36.4 | 18.85 | 0.0768 | 0.25 | 13.08 | 0
March | 23 | 12PM to 1PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
March | 23 | 1PM to 2PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
March | 23 | 2PM to 3PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
March | 23 | 3PM to 4PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
March | 23 | 4PM to 5PM | 55 | 47.4 | 39.9 | 36.4 | 18.85 | 0.0768 | 0.25 | 13.08 | 0
March | 23 | 5PM to 6PM | 54 | 47.3 | 41 | 38 | 18.84 | 0.077 | 0.26 | 13.06 | 0
March | 23 | 6PM to 7PM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
March | 23 | 7PM to 8PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
March | 23 | 8PM to 9PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
March | 23 | 9PM to 10PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
March | 23 | 10PM to 11PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
March | 23 | 11PM to 12AM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
March | 24 | 12AM to 1AM | 53.1 | 46.1 | 39 | 35.1 | 18.18 | 0.0771 | 0.24 | 13.03 | 0
March | 24 | 1AM to 2AM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
March | 24 | 2AM to 3AM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 0
March | 24 | 3AM to 4AM | 50 | 43.4 | 36 | 31.1 | 16.82 | 0.0776 | 0.21 | 12.94 | 1
March | 24 | 4AM to 5AM | 50 | 43.8 | 37 | 32.5 | 17.03 | 0.0776 | 0.22 | 12.94 | 1
March | 24 | 5AM to 6AM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
March | 24 | 6AM to 7AM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
March | 24 | 7AM to 8AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
March | 24 | 8AM to 9AM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
March | 24 | 9AM to 10AM | 55 | 47 | 39 | 35.1 | 18.66 | 0.0768 | 0.24 | 13.08 | 0
March | 24 | 10AM to 11AM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
March | 24 | 11AM to 12PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
March | 24 | 12PM to 1PM | 57 | 48.7 | 41 | 38 | 19.58 | 0.0765 | 0.26 | 13.14 | 0
March | 24 | 1PM to 2PM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
March | 24 | 2PM to 3PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 24 | 3PM to 4PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 24 | 4PM to 5PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 24 | 5PM to 6PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 24 | 6PM to 7PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 24 | 7PM to 8PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
March | 24 | 8PM to 9PM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 24 | 9PM to 10PM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
March | 24 | 10PM to 11PM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
March | 24 | 11PM to 12AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
March | 25 | 12AM to 1AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
March | 25 | 1AM to 2AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
March | 25 | 2AM to 3AM | 46 | 46 | 46 | 46.1 | 18.18 | 0.0781 | 0.31 | 12.88 | 1
March | 25 | 3AM to 4AM | 46 | 46 | 46 | 46.1 | 18.18 | 0.0781 | 0.31 | 12.88 | 1
March | 25 | 4AM to 5AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
March | 25 | 5AM to 6AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
March | 25 | 6AM to 7AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
March | 25 | 7AM to 8AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
March | 25 | 8AM to 9AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
March | 25 | 9AM to 10AM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
March | 25 | 10AM to 11AM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
March | 25 | 11AM to 12PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
March | 25 | 12PM to 1PM | 57 | 49.6 | 43 | 41 | 20.05 | 0.0765 | 0.28 | 13.15 | 0
March | 25 | 1PM to 2PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
March | 25 | 2PM to 3PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
March | 25 | 3PM to 4PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
March | 25 | 4PM to 5PM | 55 | 49.2 | 44.1 | 42.8 | 19.84 | 0.0768 | 0.29 | 13.1 | 0
March | 25 | 5PM to 6PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
March | 25 | 6PM to 7PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
March | 25 | 7PM to 8PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
March | 25 | 8PM to 9PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 25 | 9PM to 10PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 25 | 10PM to 11PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 25 | 11PM to 12AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 26 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
March | 26 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 26 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 26 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 26 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 26 | 5AM to 6AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 26 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 26 | 7AM to 8AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 26 | 8AM to 9AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 26 | 9AM to 10AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
March | 26 | 10AM to 11AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
March | 26 | 11AM to 12PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
March | 26 | 12PM to 1PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
March | 26 | 1PM to 2PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
March | 26 | 2PM to 3PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
March | 26 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
March | 26 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
March | 26 | 5PM to 6PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 26 | 6PM to 7PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 26 | 7PM to 8PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
March | 26 | 8PM to 9PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 26 | 9PM to 10PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 26 | 10PM to 11PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 26 | 11PM to 12AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 27 | 12AM to 1AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 27 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 27 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 27 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 27 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 27 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 27 | 6AM to 7AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 27 | 7AM to 8AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 27 | 8AM to 9AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 27 | 9AM to 10AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 27 | 10AM to 11AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
March | 27 | 11AM to 12PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
March | 27 | 12PM to 1PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
March | 27 | 1PM to 2PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
March | 27 | 2PM to 3PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
March | 27 | 3PM to 4PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
March | 27 | 4PM to 5PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
March | 27 | 5PM to 6PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
March | 27 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 27 | 7PM to 8PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 27 | 8PM to 9PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 27 | 9PM to 10PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 27 | 10PM to 11PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 27 | 11PM to 12AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 28 | 12AM to 1AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 28 | 1AM to 2AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 28 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 28 | 3AM to 4AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 28 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
March | 28 | 5AM to 6AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 28 | 6AM to 7AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 28 | 7AM to 8AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
March | 28 | 8AM to 9AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 28 | 9AM to 10AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 28 | 10AM to 11AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
March | 28 | 11AM to 12PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
March | 28 | 12PM to 1PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
March | 28 | 1PM to 2PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
March | 28 | 2PM to 3PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
March | 28 | 3PM to 4PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
March | 28 | 4PM to 5PM | 64 | 51.1 | 39 | 35.1 | 20.84 | 0.0755 | 0.24 | 13.31 | 0
March | 28 | 5PM to 6PM | 60.1 | 48.2 | 36 | 31.1 | 19.25 | 0.0761 | 0.21 | 13.19 | 0
March | 28 | 6PM to 7PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
March | 28 | 7PM to 8PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
March | 28 | 8PM to 9PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 28 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 28 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 28 | 11PM to 12AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
March | 29 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 29 | 1AM to 2AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 29 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 29 | 3AM to 4AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
March | 29 | 4AM to 5AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
March | 29 | 5AM to 6AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
March | 29 | 6AM to 7AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 29 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 29 | 8AM to 9AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 29 | 9AM to 10AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
March | 29 | 10AM to 11AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
March | 29 | 11AM to 12PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
March | 29 | 12PM to 1PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
March | 29 | 1PM to 2PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
March | 29 | 2PM to 3PM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 29 | 3PM to 4PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
March | 29 | 4PM to 5PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
March | 29 | 5PM to 6PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
March | 29 | 6PM to 7PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
March | 29 | 7PM to 8PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 29 | 8PM to 9PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 29 | 9PM to 10PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 29 | 10PM to 11PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 29 | 11PM to 12AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
March | 30 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 30 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 30 | 2AM to 3AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 30 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 30 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 30 | 5AM to 6AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
March | 30 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 30 | 7AM to 8AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 30 | 8AM to 9AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
March | 30 | 9AM to 10AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
March | 30 | 10AM to 11AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
March | 30 | 11AM to 12PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
March | 30 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
March | 30 | 1PM to 2PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
March | 30 | 2PM to 3PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
March | 30 | 3PM to 4PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
March | 30 | 4PM to 5PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
March | 30 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
March | 30 | 6PM to 7PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 30 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 30 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
March | 30 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 30 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
March | 30 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
March | 31 | 12AM to 1AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 31 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 31 | 2AM to 3AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
March | 31 | 3AM to 4AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
March | 31 | 4AM to 5AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
March | 31 | 5AM to 6AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
March | 31 | 6AM to 7AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
March | 31 | 7AM to 8AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
March | 31 | 8AM to 9AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
March | 31 | 9AM to 10AM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
March | 31 | 10AM to 11AM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
March | 31 | 11AM to 12PM | 64 | 51.1 | 39 | 35.1 | 20.84 | 0.0755 | 0.24 | 13.31 | 0
March | 31 | 12PM to 1PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
March | 31 | 1PM to 2PM | 66 | 53.5 | 43 | 41 | 22.23 | 0.0752 | 0.28 | 13.38 | 0
March | 31 | 2PM to 3PM | 64 | 51.8 | 41 | 38 | 21.28 | 0.0755 | 0.26 | 13.32 | 0
March | 31 | 3PM to 4PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
March | 31 | 4PM to 5PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
March | 31 | 5PM to 6PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
March | 31 | 6PM to 7PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
March | 31 | 7PM to 8PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
March | 31 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 31 | 9PM to 10PM | 54.1 | 50.4 | 47.3 | 48.4 | 20.5 | 0.0769 | 0.33 | 13.1 | 0
March | 31 | 10PM to 11PM | 55 | 50.1 | 45.9 | 45.8 | 20.32 | 0.0768 | 0.31 | 13.11 | 0
March | 31 | 11PM to 12AM | 56.1 | 49.8 | 44.2 | 43.1 | 20.15 | 0.0766 | 0.29 | 13.13 | 0
April | 1 | 12AM to 1AM | 57 | 49.4 | 42.6 | 40.4 | 19.96 | 0.0765 | 0.27 | 13.14 | 0
April | 1 | 1AM to 2AM | 58.1 | 49.2 | 41 | 38 | 19.84 | 0.0764 | 0.26 | 13.16 | 0
April | 1 | 2AM to 3AM | 59 | 49 | 39.6 | 35.9 | 19.73 | 0.0763 | 0.24 | 13.18 | 0
April | 1 | 3AM to 4AM | 60.1 | 48.9 | 37.9 | 33.7 | 19.65 | 0.0761 | 0.23 | 13.2 | 0
April | 1 | 4AM to 5AM | 61 | 49.3 | 37.9 | 33.7 | 19.87 | 0.076 | 0.23 | 13.23 | 0
April | 1 | 5AM to 6AM | 64 | 50.7 | 37.9 | 33.7 | 20.61 | 0.0755 | 0.23 | 13.3 | 0
April | 1 | 6AM to 7AM | 64.9 | 53 | 43 | 41 | 21.97 | 0.0754 | 0.28 | 13.35 | 0
April | 1 | 7AM to 8AM | 66 | 53.9 | 44.1 | 42.8 | 22.51 | 0.0752 | 0.29 | 13.38 | 0
April | 1 | 8AM to 9AM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
April | 1 | 9AM to 10AM | 71.1 | 56.3 | 45 | 44.3 | 23.96 | 0.0745 | 0.3 | 13.51 | 0
April | 1 | 10AM to 11AM | 75 | 54.6 | 36 | 31.1 | 22.87 | 0.074 | 0.21 | 13.57 | 0
April | 1 | 11AM to 12PM | 75.9 | 56.3 | 39.9 | 36.4 | 23.91 | 0.0738 | 0.25 | 13.61 | 0
April | 1 | 12PM to 1PM | 71.1 | 57.7 | 48 | 49.8 | 24.82 | 0.0744 | 0.34 | 13.53 | 0
April | 1 | 1PM to 2PM | 75.9 | 57.8 | 44.1 | 42.8 | 24.91 | 0.0738 | 0.29 | 13.63 | 0
April | 1 | 2PM to 3PM | 80.1 | 56.6 | 36 | 31.1 | 24.09 | 0.0733 | 0.21 | 13.7 | 0
April | 1 | 3PM to 4PM | 81 | 57.9 | 39 | 35.1 | 24.94 | 0.0732 | 0.24 | 13.74 | 0
April | 1 | 4PM to 5PM | 79 | 57.2 | 39 | 35.1 | 24.46 | 0.0734 | 0.24 | 13.69 | 0
April | 1 | 5PM to 6PM | 71.1 | 53.3 | 37 | 32.5 | 22.12 | 0.0745 | 0.22 | 13.48 | 0
April | 1 | 6PM to 7PM | 69.1 | 52.5 | 37 | 32.5 | 21.65 | 0.0748 | 0.22 | 13.43 | 0
April | 1 | 7PM to 8PM | 66 | 51.9 | 39 | 35.1 | 21.32 | 0.0752 | 0.24 | 13.36 | 0
April | 1 | 8PM to 9PM | 64 | 51.8 | 41 | 38 | 21.28 | 0.0755 | 0.26 | 13.32 | 0
April | 1 | 9PM to 10PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
April | 1 | 10PM to 11PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 1 | 11PM to 12AM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
April | 2 | 12AM to 1AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 2 | 1AM to 2AM | 56.8 | 50.9 | 46 | 46.1 | 20.8 | 0.0765 | 0.31 | 13.16 | 0
April | 2 | 2AM to 3AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 2 | 3AM to 4AM | 59 | 50.5 | 43 | 41 | 20.53 | 0.0762 | 0.28 | 13.2 | 0
April | 2 | 4AM to 5AM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
April | 2 | 5AM to 6AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 2 | 6AM to 7AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 2 | 7AM to 8AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
April | 2 | 8AM to 9AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
April | 2 | 9AM to 10AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
April | 2 | 10AM to 11AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
April | 2 | 11AM to 12PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
April | 2 | 12PM to 1PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
April | 2 | 1PM to 2PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
April | 2 | 2PM to 3PM | 82.9 | 62.8 | 50 | 53.6 | 28.32 | 0.0728 | 0.36 | 13.85 | 0
April | 2 | 3PM to 4PM | 82.9 | 60 | 43 | 41 | 26.34 | 0.0729 | 0.28 | 13.81 | 0
April | 2 | 4PM to 5PM | 82 | 59 | 41 | 38 | 25.64 | 0.073 | 0.26 | 13.77 | 0
April | 2 | 5PM to 6PM | 73.9 | 55.9 | 41 | 38 | 23.68 | 0.0741 | 0.26 | 13.57 | 0
April | 2 | 6PM to 7PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
April | 2 | 7PM to 8PM | 66.9 | 53.8 | 43 | 41 | 22.45 | 0.0751 | 0.28 | 13.4 | 0
April | 2 | 8PM to 9PM | 69.1 | 53.2 | 39 | 35.1 | 22.06 | 0.0748 | 0.24 | 13.44 | 0
April | 2 | 9PM to 10PM | 68 | 52.7 | 39 | 35.1 | 21.8 | 0.075 | 0.24 | 13.41 | 0
April | 2 | 10PM to 11PM | 64 | 52.3 | 42.1 | 39.6 | 21.53 | 0.0755 | 0.27 | 13.32 | 0
April | 2 | 11PM to 12AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
April | 3 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
April | 3 | 1AM to 2AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
April | 3 | 2AM to 3AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 3 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 3 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 3 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 3 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 3 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 3 | 8AM to 9AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
April | 3 | 9AM to 10AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
April | 3 | 10AM to 11AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
April | 3 | 11AM to 12PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
April | 3 | 12PM to 1PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
April | 3 | 1PM to 2PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
April | 3 | 2PM to 3PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
April | 3 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
April | 3 | 4PM to 5PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
April | 3 | 5PM to 6PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
April | 3 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 3 | 7PM to 8PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 3 | 8PM to 9PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 3 | 9PM to 10PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 3 | 10PM to 11PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 3 | 11PM to 12AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 4 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 4 | 1AM to 2AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
April | 4 | 2AM to 3AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
April | 4 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 4 | 4AM to 5AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 4 | 5AM to 6AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 4 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 4 | 7AM to 8AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 4 | 8AM to 9AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 4 | 9AM to 10AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 4 | 10AM to 11AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 4 | 11AM to 12PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
April | 4 | 12PM to 1PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
April | 4 | 1PM to 2PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
April | 4 | 2PM to 3PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 4 | 3PM to 4PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
April | 4 | 4PM to 5PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 4 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 4 | 6PM to 7PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 4 | 7PM to 8PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 4 | 8PM to 9PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 4 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 4 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 4 | 11PM to 12AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 1AM to 2AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 2AM to 3AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 5 | 3AM to 4AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 5 | 4AM to 5AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 5AM to 6AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 6AM to 7AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 5 | 7AM to 8AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 5 | 8AM to 9AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
April | 5 | 9AM to 10AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 5 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 5 | 11AM to 12PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 5 | 12PM to 1PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
April | 5 | 1PM to 2PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
April | 5 | 2PM to 3PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
April | 5 | 3PM to 4PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
April | 5 | 4PM to 5PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 5 | 5PM to 6PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 5 | 6PM to 7PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 5 | 7PM to 8PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
April | 5 | 8PM to 9PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 5 | 9PM to 10PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 5 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 5 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 6 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
April | 6 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
April | 6 | 2AM to 3AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 6 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 6 | 4AM to 5AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 6 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 6 | 6AM to 7AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
April | 6 | 7AM to 8AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
April | 6 | 8AM to 9AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 6 | 9AM to 10AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 6 | 10AM to 11AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 6 | 11AM to 12PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
April | 6 | 12PM to 1PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 6 | 1PM to 2PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
April | 6 | 2PM to 3PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
April | 6 | 3PM to 4PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 6 | 4PM to 5PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 6 | 5PM to 6PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
April | 6 | 6PM to 7PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 6 | 7PM to 8PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
April | 6 | 8PM to 9PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 6 | 9PM to 10PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 6 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 6 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 7 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
April | 7 | 1AM to 2AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
April | 7 | 2AM to 3AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
April | 7 | 3AM to 4AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
April | 7 | 4AM to 5AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
April | 7 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 7 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 7 | 7AM to 8AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 7 | 8AM to 9AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 7 | 9AM to 10AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 7 | 10AM to 11AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 7 | 11AM to 12PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
April | 7 | 12PM to 1PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
April | 7 | 1PM to 2PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
April | 7 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
April | 7 | 3PM to 4PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
April | 7 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 7 | 5PM to 6PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 7 | 6PM to 7PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 7 | 7PM to 8PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 7 | 8PM to 9PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 7 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
April | 7 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 7 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 8 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 8 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 8 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
April | 8 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
April | 8 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
April | 8 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 8 | 6AM to 7AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 8 | 7AM to 8AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
April | 8 | 8AM to 9AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 8 | 9AM to 10AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
April | 8 | 10AM to 11AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 8 | 11AM to 12PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 8 | 12PM to 1PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 8 | 1PM to 2PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 8 | 2PM to 3PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 8 | 3PM to 4PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
April | 8 | 4PM to 5PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 8 | 5PM to 6PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 8 | 6PM to 7PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 8 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 8 | 8PM to 9PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 8 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 8 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 8 | 11PM to 12AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 9 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 9 | 1AM to 2AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 9 | 2AM to 3AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 9 | 3AM to 4AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 9 | 4AM to 5AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
April | 9 | 5AM to 6AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 9 | 6AM to 7AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 9 | 7AM to 8AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 9 | 8AM to 9AM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
April | 9 | 9AM to 10AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 9 | 10AM to 11AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 9 | 11AM to 12PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 9 | 12PM to 1PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 9 | 1PM to 2PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 9 | 2PM to 3PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 9 | 3PM to 4PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 9 | 4PM to 5PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 9 | 5PM to 6PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 9 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 9 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 9 | 8PM to 9PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 9 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
April | 9 | 10PM to 11PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
April | 9 | 11PM to 12AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
April | 10 | 12AM to 1AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
April | 10 | 1AM to 2AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 10 | 2AM to 3AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
April | 10 | 3AM to 4AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
April | 10 | 4AM to 5AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 10 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 10 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 10 | 7AM to 8AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 10 | 8AM to 9AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 10 | 9AM to 10AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 10 | 10AM to 11AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
April | 10 | 11AM to 12PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 10 | 12PM to 1PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
April | 10 | 1PM to 2PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 10 | 2PM to 3PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 10 | 3PM to 4PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 10 | 4PM to 5PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 10 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 10 | 6PM to 7PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
April | 10 | 7PM to 8PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 10 | 8PM to 9PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 10 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 10 | 10PM to 11PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
April | 10 | 11PM to 12AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
April | 11 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
April | 11 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
April | 11 | 2AM to 3AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
April | 11 | 3AM to 4AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
April | 11 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
April | 11 | 5AM to 6AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
April | 11 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 11 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 11 | 8AM to 9AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
April | 11 | 9AM to 10AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
April | 11 | 10AM to 11AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
April | 11 | 11AM to 12PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
April | 11 | 12PM to 1PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
April | 11 | 1PM to 2PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
April | 11 | 2PM to 3PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
April | 11 | 3PM to 4PM | 70 | 56.8 | 46.9 | 47.8 | 24.25 | 0.0746 | 0.32 | 13.5 | 0
April | 11 | 4PM to 5PM | 68 | 55.1 | 45 | 44.3 | 23.22 | 0.0749 | 0.3 | 13.44 | 0
April | 11 | 5PM to 6PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
April | 11 | 6PM to 7PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 11 | 7PM to 8PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
April | 11 | 8PM to 9PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 11 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 11 | 10PM to 11PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 11 | 11PM to 12AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 12 | 12AM to 1AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 12 | 1AM to 2AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 12 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 12 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 12 | 4AM to 5AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 12 | 5AM to 6AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 12 | 6AM to 7AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 12 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
April | 12 | 8AM to 9AM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
April | 12 | 9AM to 10AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
April | 12 | 10AM to 11AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
April | 12 | 11AM to 12PM | 71.1 | 55.5 | 43 | 41 | 23.46 | 0.0745 | 0.28 | 13.5 | 0
April | 12 | 12PM to 1PM | 70 | 50.9 | 30.9 | 25.2 | 20.73 | 0.0747 | 0.17 | 13.43 | 0
April | 12 | 1PM to 2PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
April | 12 | 2PM to 3PM | 66.9 | 53.8 | 42.8 | 40.7 | 22.41 | 0.0751 | 0.28 | 13.4 | 0
April | 12 | 3PM to 4PM | 66.9 | 53.8 | 43 | 41 | 22.45 | 0.0751 | 0.28 | 13.4 | 0
April | 12 | 4PM to 5PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
April | 12 | 5PM to 6PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
April | 12 | 6PM to 7PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
April | 12 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
April | 12 | 8PM to 9PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
April | 12 | 9PM to 10PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
April | 12 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
April | 12 | 11PM to 12AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
April | 13 | 12AM to 1AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
April | 13 | 1AM to 2AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
April | 13 | 2AM to 3AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
April | 13 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
April | 13 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
April | 13 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
April | 13 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
April | 13 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
April | 13 | 8AM to 9AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
April | 13 | 9AM to 10AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
April | 13 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
April | 13 | 11AM to 12PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
April | 13 | 12PM to 1PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
April | 13 | 1PM to 2PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
April | 13 | 2PM to 3PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
April | 13 | 3PM to 4PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
April | 13 | 4PM to 5PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
April | 13 | 5PM to 6PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
April | 13 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 13 | 7PM to 8PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 13 | 8PM to 9PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 13 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 13 | 10PM to 11PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 13 | 11PM to 12AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 12AM to 1AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 1AM to 2AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 14 | 2AM to 3AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 3AM to 4AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 4AM to 5AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 14 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 14 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 14 | 7AM to 8AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
April | 14 | 8AM to 9AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 14 | 9AM to 10AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 14 | 10AM to 11AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 14 | 11AM to 12PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 14 | 12PM to 1PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
April | 14 | 1PM to 2PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
April | 14 | 2PM to 3PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
April | 14 | 3PM to 4PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
April | 14 | 4PM to 5PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
April | 14 | 5PM to 6PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
April | 14 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
April | 14 | 7PM to 8PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 14 | 8PM to 9PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 14 | 9PM to 10PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 10PM to 11PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 14 | 11PM to 12AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 15 | 12AM to 1AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 15 | 1AM to 2AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 15 | 2AM to 3AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 15 | 3AM to 4AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 15 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 15 | 5AM to 6AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 15 | 6AM to 7AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 15 | 7AM to 8AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 15 | 8AM to 9AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 15 | 9AM to 10AM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 15 | 10AM to 11AM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 15 | 11AM to 12PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
April | 15 | 12PM to 1PM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
April | 15 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 15 | 2PM to 3PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 15 | 3PM to 4PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 15 | 4PM to 5PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
April | 15 | 5PM to 6PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 15 | 6PM to 7PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 15 | 7PM to 8PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 15 | 8PM to 9PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 15 | 9PM to 10PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 15 | 10PM to 11PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 15 | 11PM to 12AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 16 | 12AM to 1AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 16 | 1AM to 2AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 16 | 2AM to 3AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 16 | 3AM to 4AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 16 | 4AM to 5AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 16 | 5AM to 6AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 16 | 6AM to 7AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 16 | 7AM to 8AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 16 | 8AM to 9AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
April | 16 | 9AM to 10AM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
April | 16 | 10AM to 11AM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
April | 16 | 11AM to 12PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
April | 16 | 12PM to 1PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
April | 16 | 1PM to 2PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
April | 16 | 2PM to 3PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
April | 16 | 3PM to 4PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
April | 16 | 4PM to 5PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
April | 16 | 5PM to 6PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
April | 16 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
April | 16 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
April | 16 | 8PM to 9PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
April | 16 | 9PM to 10PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
April | 16 | 10PM to 11PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
April | 16 | 11PM to 12AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
April | 17 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
April | 17 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 17 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 17 | 3AM to 4AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
April | 17 | 4AM to 5AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 17 | 5AM to 6AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 17 | 6AM to 7AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 17 | 7AM to 8AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 17 | 8AM to 9AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 17 | 9AM to 10AM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
April | 17 | 10AM to 11AM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
April | 17 | 11AM to 12PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
April | 17 | 12PM to 1PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
April | 17 | 1PM to 2PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
April | 17 | 2PM to 3PM | 63 | 52.2 | 43 | 41 | 21.49 | 0.0756 | 0.28 | 13.3 | 0
April | 17 | 3PM to 4PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
April | 17 | 4PM to 5PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
April | 17 | 5PM to 6PM | 57.9 | 49.6 | 42.1 | 39.6 | 20.05 | 0.0764 | 0.27 | 13.17 | 0
April | 17 | 6PM to 7PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 17 | 7PM to 8PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 17 | 8PM to 9PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
April | 17 | 9PM to 10PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 17 | 10PM to 11PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
April | 17 | 11PM to 12AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 18 | 12AM to 1AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
April | 18 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 18 | 2AM to 3AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 18 | 3AM to 4AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 18 | 4AM to 5AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
April | 18 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 18 | 6AM to 7AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 18 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 18 | 8AM to 9AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 18 | 9AM to 10AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 18 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 18 | 11AM to 12PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
April | 18 | 12PM to 1PM | 63 | 52.2 | 43 | 41 | 21.49 | 0.0756 | 0.28 | 13.3 | 0
April | 18 | 1PM to 2PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
April | 18 | 2PM to 3PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
April | 18 | 3PM to 4PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
April | 18 | 4PM to 5PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
April | 18 | 5PM to 6PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 18 | 6PM to 7PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 18 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 18 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 18 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 18 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 18 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 19 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 19 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 19 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
April | 19 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
April | 19 | 4AM to 5AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
April | 19 | 5AM to 6AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
April | 19 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 19 | 7AM to 8AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 19 | 8AM to 9AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 19 | 9AM to 10AM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 19 | 10AM to 11AM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
April | 19 | 11AM to 12PM | 63 | 52.6 | 44.1 | 42.8 | 21.76 | 0.0756 | 0.29 | 13.3 | 0
April | 19 | 12PM to 1PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
April | 19 | 1PM to 2PM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
April | 19 | 2PM to 3PM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
April | 19 | 3PM to 4PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
April | 19 | 4PM to 5PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
April | 19 | 5PM to 6PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 19 | 6PM to 7PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 19 | 7PM to 8PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 19 | 8PM to 9PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 19 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 19 | 10PM to 11PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 19 | 11PM to 12AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 20 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 20 | 1AM to 2AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 20 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 20 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 20 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 20 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 20 | 6AM to 7AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 20 | 7AM to 8AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
April | 20 | 8AM to 9AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 20 | 9AM to 10AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
April | 20 | 10AM to 11AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
April | 20 | 11AM to 12PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
April | 20 | 12PM to 1PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
April | 20 | 1PM to 2PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
April | 20 | 2PM to 3PM | 64 | 53.1 | 44.1 | 42.8 | 22.02 | 0.0755 | 0.29 | 13.33 | 0
April | 20 | 3PM to 4PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
April | 20 | 4PM to 5PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
April | 20 | 5PM to 6PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 20 | 6PM to 7PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 20 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 20 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
April | 20 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 20 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 20 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 21 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 21 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 21 | 7AM to 8AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 21 | 8AM to 9AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
April | 21 | 9AM to 10AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 21 | 10AM to 11AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 21 | 11AM to 12PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
April | 21 | 12PM to 1PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 21 | 1PM to 2PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 21 | 2PM to 3PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 21 | 3PM to 4PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 21 | 4PM to 5PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 21 | 5PM to 6PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 21 | 6PM to 7PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 21 | 7PM to 8PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 21 | 8PM to 9PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 21 | 9PM to 10PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 21 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 21 | 11PM to 12AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 22 | 12AM to 1AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 22 | 1AM to 2AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 22 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
April | 22 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
April | 22 | 4AM to 5AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
April | 22 | 5AM to 6AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
April | 22 | 6AM to 7AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
April | 22 | 7AM to 8AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
April | 22 | 8AM to 9AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
April | 22 | 9AM to 10AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
April | 22 | 10AM to 11AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
April | 22 | 11AM to 12PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
April | 22 | 12PM to 1PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
April | 22 | 1PM to 2PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
April | 22 | 2PM to 3PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 22 | 3PM to 4PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
April | 22 | 4PM to 5PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
April | 22 | 5PM to 6PM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
April | 22 | 6PM to 7PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
April | 22 | 7PM to 8PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
April | 22 | 8PM to 9PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
April | 22 | 9PM to 10PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 22 | 10PM to 11PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 22 | 11PM to 12AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 23 | 12AM to 1AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
April | 23 | 1AM to 2AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
April | 23 | 2AM to 3AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
April | 23 | 3AM to 4AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
April | 23 | 4AM to 5AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
April | 23 | 5AM to 6AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
April | 23 | 6AM to 7AM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
April | 23 | 7AM to 8AM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
April | 23 | 8AM to 9AM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
April | 23 | 9AM to 10AM | 57.9 | 49.1 | 41 | 38 | 19.8 | 0.0764 | 0.26 | 13.16 | 0
April | 23 | 10AM to 11AM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
April | 23 | 11AM to 12PM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
April | 23 | 12PM to 1PM | 61 | 51 | 42.1 | 39.6 | 20.79 | 0.0759 | 0.27 | 13.24 | 0
April | 23 | 1PM to 2PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
April | 23 | 2PM to 3PM | 61 | 51.8 | 44.1 | 42.8 | 21.28 | 0.0759 | 0.29 | 13.25 | 0
April | 23 | 3PM to 4PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
April | 23 | 4PM to 5PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 23 | 5PM to 6PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
April | 23 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 23 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 23 | 8PM to 9PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 23 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 23 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 23 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
April | 24 | 12AM to 1AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 24 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 24 | 2AM to 3AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
April | 24 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
April | 24 | 4AM to 5AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
April | 24 | 5AM to 6AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
April | 24 | 6AM to 7AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 24 | 7AM to 8AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 24 | 8AM to 9AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
April | 24 | 9AM to 10AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 24 | 10AM to 11AM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
April | 24 | 11AM to 12PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
April | 24 | 12PM to 1PM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
April | 24 | 1PM to 2PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
April | 24 | 2PM to 3PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 24 | 3PM to 4PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
April | 24 | 4PM to 5PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 24 | 5PM to 6PM | 57 | 49.6 | 43 | 41 | 20.05 | 0.0765 | 0.28 | 13.15 | 0
April | 24 | 6PM to 7PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
April | 24 | 7PM to 8PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
April | 24 | 8PM to 9PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 24 | 9PM to 10PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 24 | 10PM to 11PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
April | 24 | 11PM to 12AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
April | 25 | 12AM to 1AM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
April | 25 | 1AM to 2AM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
April | 25 | 2AM to 3AM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
April | 25 | 3AM to 4AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 25 | 4AM to 5AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 25 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 25 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 25 | 7AM to 8AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 25 | 8AM to 9AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 25 | 9AM to 10AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
April | 25 | 10AM to 11AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
April | 25 | 11AM to 12PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
April | 25 | 12PM to 1PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
April | 25 | 1PM to 2PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
April | 25 | 2PM to 3PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
April | 25 | 3PM to 4PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
April | 25 | 4PM to 5PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
April | 25 | 5PM to 6PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
April | 25 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
April | 25 | 7PM to 8PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 25 | 8PM to 9PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
April | 25 | 9PM to 10PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 25 | 10PM to 11PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 25 | 11PM to 12AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 26 | 12AM to 1AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 26 | 1AM to 2AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 26 | 2AM to 3AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 26 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 26 | 4AM to 5AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 26 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 26 | 6AM to 7AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 26 | 7AM to 8AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
April | 26 | 8AM to 9AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
April | 26 | 9AM to 10AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
April | 26 | 10AM to 11AM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
April | 26 | 11AM to 12PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
April | 26 | 12PM to 1PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
April | 26 | 1PM to 2PM | 75.9 | 60.9 | 51.1 | 55.9 | 26.96 | 0.0737 | 0.38 | 13.67 | 0
April | 26 | 2PM to 3PM | 68 | 55.6 | 46 | 46.1 | 23.51 | 0.0749 | 0.31 | 13.44 | 0
April | 26 | 3PM to 4PM | 68 | 54.3 | 43 | 41 | 22.71 | 0.0749 | 0.28 | 13.43 | 0
April | 26 | 4PM to 5PM | 66.9 | 53 | 41 | 38 | 21.98 | 0.0751 | 0.26 | 13.39 | 0
April | 26 | 5PM to 6PM | 64.9 | 51.4 | 39 | 35.1 | 21.06 | 0.0754 | 0.24 | 13.33 | 0
April | 26 | 6PM to 7PM | 61 | 49 | 37 | 32.5 | 19.68 | 0.076 | 0.22 | 13.22 | 0
April | 26 | 7PM to 8PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
April | 26 | 8PM to 9PM | 57.9 | 47.9 | 37.9 | 33.7 | 19.13 | 0.0764 | 0.23 | 13.15 | 0
April | 26 | 9PM to 10PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
April | 26 | 10PM to 11PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
April | 26 | 11PM to 12AM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
April | 27 | 12AM to 1AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 27 | 1AM to 2AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
April | 27 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 27 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 27 | 4AM to 5AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 27 | 5AM to 6AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 27 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
April | 27 | 7AM to 8AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
April | 27 | 8AM to 9AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
April | 27 | 9AM to 10AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
April | 27 | 10AM to 11AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
April | 27 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
April | 27 | 12PM to 1PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
April | 27 | 1PM to 2PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
April | 27 | 2PM to 3PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 27 | 3PM to 4PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 27 | 4PM to 5PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 27 | 5PM to 6PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 27 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 27 | 7PM to 8PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
April | 27 | 8PM to 9PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
April | 27 | 9PM to 10PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
April | 27 | 10PM to 11PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
April | 27 | 11PM to 12AM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
April | 28 | 12AM to 1AM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
April | 28 | 1AM to 2AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
April | 28 | 2AM to 3AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
April | 28 | 3AM to 4AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
April | 28 | 4AM to 5AM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
April | 28 | 5AM to 6AM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
April | 28 | 6AM to 7AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
April | 28 | 7AM to 8AM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
April | 28 | 8AM to 9AM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
April | 28 | 9AM to 10AM | 57 | 47.5 | 37.9 | 33.7 | 18.91 | 0.0766 | 0.23 | 13.12 | 0
April | 28 | 10AM to 11AM | 57.9 | 48.3 | 39 | 35.1 | 19.35 | 0.0764 | 0.24 | 13.15 | 0
April | 28 | 11AM to 12PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
April | 28 | 12PM to 1PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
April | 28 | 1PM to 2PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
April | 28 | 2PM to 3PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
April | 28 | 3PM to 4PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
April | 28 | 4PM to 5PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
April | 28 | 5PM to 6PM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
April | 28 | 6PM to 7PM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
April | 28 | 7PM to 8PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 28 | 8PM to 9PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
April | 28 | 9PM to 10PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
April | 28 | 10PM to 11PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
April | 28 | 11PM to 12AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
April | 29 | 12AM to 1AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
April | 29 | 1AM to 2AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
April | 29 | 2AM to 3AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
April | 29 | 3AM to 4AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
April | 29 | 4AM to 5AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
April | 29 | 5AM to 6AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
April | 29 | 6AM to 7AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 29 | 7AM to 8AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 29 | 8AM to 9AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
April | 29 | 9AM to 10AM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
April | 29 | 10AM to 11AM | 62.1 | 50.5 | 39.9 | 36.4 | 20.55 | 0.0758 | 0.25 | 13.26 | 0
April | 29 | 11AM to 12PM | 64 | 52.3 | 42.1 | 39.6 | 21.53 | 0.0755 | 0.27 | 13.32 | 0
April | 29 | 12PM to 1PM | 66.9 | 53.5 | 42.1 | 39.6 | 22.23 | 0.0751 | 0.27 | 13.39 | 0
April | 29 | 1PM to 2PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
April | 29 | 2PM to 3PM | 63 | 52.2 | 43 | 41 | 21.49 | 0.0756 | 0.28 | 13.3 | 0
April | 29 | 3PM to 4PM | 61 | 51 | 42.1 | 39.6 | 20.79 | 0.0759 | 0.27 | 13.24 | 0
April | 29 | 4PM to 5PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
April | 29 | 5PM to 6PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 29 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 29 | 7PM to 8PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 29 | 8PM to 9PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 29 | 9PM to 10PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 29 | 10PM to 11PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 29 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
April | 30 | 12AM to 1AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
April | 30 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 30 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
April | 30 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 30 | 4AM to 5AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 30 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 30 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 30 | 7AM to 8AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 30 | 8AM to 9AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 30 | 9AM to 10AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
April | 30 | 10AM to 11AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
April | 30 | 11AM to 12PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
April | 30 | 12PM to 1PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
April | 30 | 1PM to 2PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
April | 30 | 2PM to 3PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
April | 30 | 3PM to 4PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 30 | 4PM to 5PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 30 | 5PM to 6PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 30 | 6PM to 7PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
April | 30 | 7PM to 8PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
April | 30 | 8PM to 9PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 30 | 9PM to 10PM | 54.1 | 49.8 | 46 | 46.1 | 20.15 | 0.0769 | 0.31 | 13.09 | 0
April | 30 | 10PM to 11PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 30 | 11PM to 12AM | 56.1 | 51.6 | 48 | 49.8 | 21.19 | 0.0766 | 0.34 | 13.15 | 0
May | 1 | 12AM to 1AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
May | 1 | 1AM to 2AM | 58.1 | 53.5 | 50 | 53.6 | 22.27 | 0.0763 | 0.36 | 13.21 | 0
May | 1 | 2AM to 3AM | 59 | 54.3 | 50.9 | 55.5 | 22.78 | 0.0761 | 0.37 | 13.24 | 0
May | 1 | 3AM to 4AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
May | 1 | 4AM to 5AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
May | 1 | 5AM to 6AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
May | 1 | 6AM to 7AM | 68 | 55.6 | 46 | 46.1 | 23.51 | 0.0749 | 0.31 | 13.44 | 0
May | 1 | 7AM to 8AM | 73 | 57.5 | 46 | 46.1 | 24.74 | 0.0742 | 0.31 | 13.57 | 0
May | 1 | 8AM to 9AM | 75 | 58.3 | 46 | 46.1 | 25.22 | 0.0739 | 0.31 | 13.62 | 0
May | 1 | 9AM to 10AM | 77 | 58.2 | 44.1 | 42.8 | 25.17 | 0.0737 | 0.29 | 13.66 | 0
May | 1 | 10AM to 11AM | 80.1 | 59.7 | 45 | 44.3 | 26.15 | 0.0732 | 0.3 | 13.74 | 0
May | 1 | 11AM to 12PM | 84.9 | 60.8 | 43 | 41 | 26.82 | 0.0726 | 0.28 | 13.86 | 0
May | 1 | 12PM to 1PM | 81 | 59.3 | 43 | 41 | 25.86 | 0.0731 | 0.28 | 13.76 | 0
May | 1 | 1PM to 2PM | 77 | 59 | 46 | 46.1 | 25.7 | 0.0736 | 0.31 | 13.67 | 0
May | 1 | 2PM to 3PM | 73.9 | 58.3 | 46.9 | 47.8 | 25.21 | 0.074 | 0.32 | 13.6 | 0
May | 1 | 3PM to 4PM | 73 | 57.9 | 46.9 | 47.8 | 24.99 | 0.0742 | 0.32 | 13.57 | 0
May | 1 | 4PM to 5PM | 71.1 | 57.2 | 46.9 | 47.8 | 24.51 | 0.0744 | 0.32 | 13.52 | 0
May | 1 | 5PM to 6PM | 70 | 56.8 | 46.9 | 47.8 | 24.25 | 0.0746 | 0.32 | 13.5 | 0
May | 1 | 6PM to 7PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
May | 1 | 7PM to 8PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
May | 1 | 8PM to 9PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
May | 1 | 9PM to 10PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
May | 1 | 10PM to 11PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
May | 1 | 11PM to 12AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 2 | 12AM to 1AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 2 | 1AM to 2AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 2 | 2AM to 3AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 2 | 3AM to 4AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 2 | 4AM to 5AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
May | 2 | 5AM to 6AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
May | 2 | 6AM to 7AM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
May | 2 | 7AM to 8AM | 68 | 56.5 | 48 | 49.8 | 24.08 | 0.0749 | 0.34 | 13.45 | 0
May | 2 | 8AM to 9AM | 70 | 58.2 | 50 | 53.6 | 25.16 | 0.0746 | 0.36 | 13.51 | 0
May | 2 | 9AM to 10AM | 73.9 | 57.4 | 45 | 44.3 | 24.66 | 0.0741 | 0.3 | 13.59 | 0
May | 2 | 10AM to 11AM | 78.1 | 59.4 | 46 | 46.1 | 25.96 | 0.0735 | 0.31 | 13.7 | 0
May | 2 | 11AM to 12PM | 73.9 | 57.4 | 45 | 44.3 | 24.66 | 0.0741 | 0.3 | 13.59 | 0
May | 2 | 12PM to 1PM | 72 | 55.1 | 41 | 38 | 23.2 | 0.0744 | 0.26 | 13.52 | 0
May | 2 | 1PM to 2PM | 72 | 55.1 | 41 | 38 | 23.2 | 0.0744 | 0.26 | 13.52 | 0
May | 2 | 2PM to 3PM | 73 | 54.8 | 39 | 35.1 | 23.02 | 0.0742 | 0.24 | 13.54 | 0
May | 2 | 3PM to 4PM | 69.1 | 51.8 | 35.1 | 30 | 21.26 | 0.0748 | 0.2 | 13.42 | 0
May | 2 | 4PM to 5PM | 68 | 50.4 | 32 | 26.5 | 20.46 | 0.075 | 0.18 | 13.38 | 0
May | 2 | 5PM to 6PM | 66.9 | 50.6 | 34 | 28.7 | 20.54 | 0.0752 | 0.2 | 13.36 | 0
May | 2 | 6PM to 7PM | 63 | 49.9 | 37 | 32.5 | 20.16 | 0.0757 | 0.22 | 13.27 | 0
May | 2 | 7PM to 8PM | 61 | 49.7 | 39 | 35.1 | 20.1 | 0.076 | 0.24 | 13.23 | 0
May | 2 | 8PM to 9PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
May | 2 | 9PM to 10PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
May | 2 | 10PM to 11PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 2 | 11PM to 12AM | 55 | 49.2 | 44.1 | 42.8 | 19.84 | 0.0768 | 0.29 | 13.1 | 0
May | 3 | 12AM to 1AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 3 | 1AM to 2AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 3 | 2AM to 3AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 3 | 3AM to 4AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
May | 3 | 4AM to 5AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
May | 3 | 5AM to 6AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
May | 3 | 6AM to 7AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 3 | 7AM to 8AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
May | 3 | 8AM to 9AM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
May | 3 | 9AM to 10AM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
May | 3 | 10AM to 11AM | 62.1 | 51.4 | 42.1 | 39.6 | 21.05 | 0.0758 | 0.27 | 13.27 | 0
May | 3 | 11AM to 12PM | 62.1 | 51.4 | 42.1 | 39.6 | 21.05 | 0.0758 | 0.27 | 13.27 | 0
May | 3 | 12PM to 1PM | 62.1 | 50.2 | 39 | 35.1 | 20.36 | 0.0758 | 0.24 | 13.26 | 0
May | 3 | 1PM to 2PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
May | 3 | 2PM to 3PM | 60.1 | 49.7 | 39.9 | 36.4 | 20.07 | 0.0761 | 0.25 | 13.21 | 0
May | 3 | 3PM to 4PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
May | 3 | 4PM to 5PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
May | 3 | 5PM to 6PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
May | 3 | 6PM to 7PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
May | 3 | 7PM to 8PM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
May | 3 | 8PM to 9PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
May | 3 | 9PM to 10PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
May | 3 | 10PM to 11PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
May | 3 | 11PM to 12AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
May | 4 | 12AM to 1AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
May | 4 | 1AM to 2AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
May | 4 | 2AM to 3AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
May | 4 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
May | 4 | 4AM to 5AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
May | 4 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 4 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 4 | 7AM to 8AM | 57 | 49.6 | 43 | 41 | 20.05 | 0.0765 | 0.28 | 13.15 | 0
May | 4 | 8AM to 9AM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
May | 4 | 9AM to 10AM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
May | 4 | 10AM to 11AM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
May | 4 | 11AM to 12PM | 64.9 | 52.6 | 42.1 | 39.6 | 21.75 | 0.0754 | 0.27 | 13.34 | 0
May | 4 | 12PM to 1PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
May | 4 | 1PM to 2PM | 66.9 | 53.5 | 42.1 | 39.6 | 22.23 | 0.0751 | 0.27 | 13.39 | 0
May | 4 | 2PM to 3PM | 66 | 53.1 | 42.1 | 39.6 | 22.01 | 0.0752 | 0.27 | 13.37 | 0
May | 4 | 3PM to 4PM | 63 | 50.6 | 39 | 35.1 | 20.58 | 0.0757 | 0.24 | 13.28 | 0
May | 4 | 4PM to 5PM | 62.1 | 49.5 | 37 | 32.5 | 19.95 | 0.0758 | 0.22 | 13.25 | 0
May | 4 | 5PM to 6PM | 61 | 48.6 | 36 | 31.1 | 19.47 | 0.076 | 0.21 | 13.22 | 0
May | 4 | 6PM to 7PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
May | 4 | 7PM to 8PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
May | 4 | 8PM to 9PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 4 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 4 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 4 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 5 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 5 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 5 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 5 | 3AM to 4AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
May | 5 | 4AM to 5AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
May | 5 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 5 | 6AM to 7AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
May | 5 | 7AM to 8AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 5 | 8AM to 9AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 5 | 9AM to 10AM | 64 | 49.9 | 36 | 31.1 | 20.21 | 0.0756 | 0.21 | 13.3 | 0
May | 5 | 10AM to 11AM | 64 | 50.3 | 37 | 32.5 | 20.43 | 0.0755 | 0.22 | 13.3 | 0
May | 5 | 11AM to 12PM | 66 | 50.8 | 36 | 31.1 | 20.69 | 0.0753 | 0.21 | 13.35 | 0
May | 5 | 12PM to 1PM | 66 | 50.5 | 35.1 | 30 | 20.52 | 0.0753 | 0.2 | 13.34 | 0
May | 5 | 1PM to 2PM | 66 | 50.2 | 34 | 28.7 | 20.32 | 0.0753 | 0.2 | 13.34 | 0
May | 5 | 2PM to 3PM | 63 | 50.6 | 39 | 35.1 | 20.58 | 0.0757 | 0.24 | 13.28 | 0
May | 5 | 3PM to 4PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
May | 5 | 4PM to 5PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
May | 5 | 5PM to 6PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 5 | 6PM to 7PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
May | 5 | 7PM to 8PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 5 | 8PM to 9PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 5 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 5 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 5 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 6 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 6 | 1AM to 2AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 6AM to 7AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 6 | 7AM to 8AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 6 | 8AM to 9AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 6 | 9AM to 10AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
May | 6 | 10AM to 11AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 6 | 11AM to 12PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 6 | 12PM to 1PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 6 | 1PM to 2PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 6 | 2PM to 3PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 6 | 3PM to 4PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 6 | 4PM to 5PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 6 | 5PM to 6PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 6 | 6PM to 7PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 6 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 6 | 8PM to 9PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 6 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 6 | 10PM to 11PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 6 | 11PM to 12AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 7 | 12AM to 1AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 7 | 1AM to 2AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 7 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 7 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 7 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 7 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 7 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 7 | 7AM to 8AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 7 | 8AM to 9AM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
May | 7 | 9AM to 10AM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
May | 7 | 10AM to 11AM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
May | 7 | 11AM to 12PM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
May | 7 | 12PM to 1PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
May | 7 | 1PM to 2PM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
May | 7 | 2PM to 3PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
May | 7 | 3PM to 4PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
May | 7 | 4PM to 5PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
May | 7 | 5PM to 6PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 7 | 6PM to 7PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
May | 7 | 7PM to 8PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 7 | 8PM to 9PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 7 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 7 | 10PM to 11PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 7 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 8 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 6AM to 7AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 8 | 7AM to 8AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 8 | 8AM to 9AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
May | 8 | 9AM to 10AM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 8 | 10AM to 11AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 8 | 11AM to 12PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
May | 8 | 12PM to 1PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
May | 8 | 1PM to 2PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
May | 8 | 2PM to 3PM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
May | 8 | 3PM to 4PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
May | 8 | 4PM to 5PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 8 | 5PM to 6PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
May | 8 | 6PM to 7PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
May | 8 | 7PM to 8PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
May | 8 | 8PM to 9PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
May | 8 | 9PM to 10PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
May | 8 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
May | 8 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 9 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 9 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 9 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 9 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
May | 9 | 4AM to 5AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 9 | 5AM to 6AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
May | 9 | 6AM to 7AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 9 | 7AM to 8AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 9 | 8AM to 9AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
May | 9 | 9AM to 10AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 9 | 10AM to 11AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 9 | 11AM to 12PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
May | 9 | 12PM to 1PM | 66 | 53.9 | 44.1 | 42.8 | 22.51 | 0.0752 | 0.29 | 13.38 | 0
May | 9 | 1PM to 2PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
May | 9 | 2PM to 3PM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
May | 9 | 3PM to 4PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 9 | 4PM to 5PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 9 | 5PM to 6PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
May | 9 | 6PM to 7PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 9 | 7PM to 8PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 9 | 8PM to 9PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
May | 9 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
May | 9 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
May | 9 | 11PM to 12AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
May | 10 | 12AM to 1AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 10 | 1AM to 2AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
May | 10 | 2AM to 3AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
May | 10 | 3AM to 4AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
May | 10 | 4AM to 5AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 10 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 10 | 6AM to 7AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 10 | 7AM to 8AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 10 | 8AM to 9AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
May | 10 | 9AM to 10AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 10 | 10AM to 11AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 10 | 11AM to 12PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
May | 10 | 12PM to 1PM | 69.1 | 56.4 | 46.9 | 47.8 | 24.03 | 0.0747 | 0.32 | 13.47 | 0
May | 10 | 1PM to 2PM | 69.1 | 55.5 | 45 | 44.3 | 23.48 | 0.0747 | 0.3 | 13.46 | 0
May | 10 | 2PM to 3PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
May | 10 | 3PM to 4PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
May | 10 | 4PM to 5PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
May | 10 | 5PM to 6PM | 61 | 50.5 | 41 | 38 | 20.54 | 0.0759 | 0.26 | 13.24 | 0
May | 10 | 6PM to 7PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
May | 10 | 7PM to 8PM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
May | 10 | 8PM to 9PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 10 | 9PM to 10PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 10 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 10 | 11PM to 12AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 11 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 11 | 1AM to 2AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 11 | 2AM to 3AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 11 | 3AM to 4AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
May | 11 | 4AM to 5AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
May | 11 | 5AM to 6AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
May | 11 | 6AM to 7AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
May | 11 | 7AM to 8AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
May | 11 | 8AM to 9AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
May | 11 | 9AM to 10AM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
May | 11 | 10AM to 11AM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
May | 11 | 11AM to 12PM | 80.1 | 61 | 48 | 49.8 | 27.01 | 0.0732 | 0.34 | 13.76 | 0
May | 11 | 12PM to 1PM | 81 | 62.6 | 51.1 | 55.9 | 28.18 | 0.073 | 0.38 | 13.8 | 0
May | 11 | 1PM to 2PM | 81 | 59.7 | 44.1 | 42.8 | 26.13 | 0.0731 | 0.29 | 13.76 | 0
May | 11 | 2PM to 3PM | 82.9 | 60 | 43 | 41 | 26.34 | 0.0729 | 0.28 | 13.81 | 0
May | 11 | 3PM to 4PM | 77 | 56.7 | 39.9 | 36.4 | 24.17 | 0.0737 | 0.25 | 13.64 | 0
May | 11 | 4PM to 5PM | 75 | 55.6 | 39 | 35.1 | 23.5 | 0.074 | 0.24 | 13.59 | 0
May | 11 | 5PM to 6PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
May | 11 | 6PM to 7PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
May | 11 | 7PM to 8PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
May | 11 | 8PM to 9PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
May | 11 | 9PM to 10PM | 59 | 50.5 | 43 | 41 | 20.53 | 0.0762 | 0.28 | 13.2 | 0
May | 11 | 10PM to 11PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
May | 11 | 11PM to 12AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
May | 12 | 12AM to 1AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 12 | 1AM to 2AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 12 | 2AM to 3AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 12 | 3AM to 4AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 12 | 4AM to 5AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 12 | 5AM to 6AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 12 | 6AM to 7AM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
May | 12 | 7AM to 8AM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
May | 12 | 8AM to 9AM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
May | 12 | 9AM to 10AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
May | 12 | 10AM to 11AM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
May | 12 | 11AM to 12PM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
May | 12 | 12PM to 1PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
May | 12 | 1PM to 2PM | 72 | 59.4 | 51.1 | 55.9 | 25.99 | 0.0743 | 0.38 | 13.57 | 0
May | 12 | 2PM to 3PM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
May | 12 | 3PM to 4PM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
May | 12 | 4PM to 5PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
May | 12 | 5PM to 6PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
May | 12 | 6PM to 7PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
May | 12 | 7PM to 8PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
May | 12 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
May | 12 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
May | 12 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
May | 12 | 11PM to 12AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
May | 13 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
May | 13 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
May | 13 | 2AM to 3AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
May | 13 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 13 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 13 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
May | 13 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
May | 13 | 7AM to 8AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
May | 13 | 8AM to 9AM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
May | 13 | 9AM to 10AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
May | 13 | 10AM to 11AM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
May | 13 | 11AM to 12PM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
May | 13 | 12PM to 1PM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
May | 13 | 1PM to 2PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
May | 13 | 2PM to 3PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
May | 13 | 3PM to 4PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
May | 13 | 4PM to 5PM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.53 | 0
May | 13 | 5PM to 6PM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
May | 13 | 6PM to 7PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 13 | 7PM to 8PM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
May | 13 | 8PM to 9PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 13 | 9PM to 10PM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
May | 13 | 10PM to 11PM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
May | 13 | 11PM to 12AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
May | 14 | 12AM to 1AM | 55 | 55 | 55 | 64.7 | 23.25 | 0.0767 | 0.44 | 13.17 | 0
May | 14 | 1AM to 2AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
May | 14 | 2AM to 3AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
May | 14 | 3AM to 4AM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
May | 14 | 4AM to 5AM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
May | 14 | 5AM to 6AM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
May | 14 | 6AM to 7AM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 14 | 7AM to 8AM | 64 | 62.1 | 61 | 80.4 | 27.89 | 0.0752 | 0.54 | 13.44 | 0
May | 14 | 8AM to 9AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
May | 14 | 9AM to 10AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
May | 14 | 10AM to 11AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
May | 14 | 11AM to 12PM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
May | 14 | 12PM to 1PM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
May | 14 | 1PM to 2PM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
May | 14 | 2PM to 3PM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
May | 14 | 3PM to 4PM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
May | 14 | 4PM to 5PM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
May | 14 | 5PM to 6PM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
May | 14 | 6PM to 7PM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
May | 14 | 7PM to 8PM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
May | 14 | 8PM to 9PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 14 | 9PM to 10PM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
May | 14 | 10PM to 11PM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
May | 14 | 11PM to 12AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
May | 15 | 12AM to 1AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
May | 15 | 1AM to 2AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
May | 15 | 2AM to 3AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
May | 15 | 3AM to 4AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
May | 15 | 4AM to 5AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
May | 15 | 5AM to 6AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
May | 15 | 6AM to 7AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
May | 15 | 7AM to 8AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
May | 15 | 8AM to 9AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
May | 15 | 9AM to 10AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
May | 15 | 10AM to 11AM | 63 | 61.1 | 60.1 | 77.8 | 27.22 | 0.0754 | 0.52 | 13.41 | 0
May | 15 | 11AM to 12PM | 61 | 61 | 61 | 80.4 | 27.14 | 0.0757 | 0.54 | 13.37 | 0
May | 15 | 12PM to 1PM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 15 | 1PM to 2PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 15 | 2PM to 3PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 15 | 3PM to 4PM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 15 | 4PM to 5PM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 15 | 5PM to 6PM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 15 | 6PM to 7PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 15 | 7PM to 8PM | 60.1 | 60.1 | 60.1 | 77.8 | 26.51 | 0.0758 | 0.52 | 13.33 | 0
May | 15 | 8PM to 9PM | 62.1 | 60.8 | 60.1 | 77.8 | 27 | 0.0755 | 0.52 | 13.39 | 0
May | 15 | 9PM to 10PM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 15 | 10PM to 11PM | 62.1 | 60.8 | 60.1 | 77.8 | 27 | 0.0755 | 0.52 | 13.39 | 0
May | 15 | 11PM to 12AM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
May | 16 | 12AM to 1AM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 16 | 1AM to 2AM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 16 | 2AM to 3AM | 59 | 59 | 59 | 74.9 | 25.79 | 0.076 | 0.5 | 13.3 | 0
May | 16 | 3AM to 4AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
May | 16 | 4AM to 5AM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 16 | 5AM to 6AM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 16 | 6AM to 7AM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
May | 16 | 7AM to 8AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
May | 16 | 8AM to 9AM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 16 | 9AM to 10AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
May | 16 | 10AM to 11AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
May | 16 | 11AM to 12PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
May | 16 | 12PM to 1PM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
May | 16 | 1PM to 2PM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
May | 16 | 2PM to 3PM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
May | 16 | 3PM to 4PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
May | 16 | 4PM to 5PM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
May | 16 | 5PM to 6PM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
May | 16 | 6PM to 7PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 16 | 7PM to 8PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
May | 16 | 8PM to 9PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
May | 16 | 9PM to 10PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 16 | 10PM to 11PM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
May | 16 | 11PM to 12AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
May | 17 | 12AM to 1AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 17 | 1AM to 2AM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
May | 17 | 2AM to 3AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
May | 17 | 3AM to 4AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
May | 17 | 4AM to 5AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
May | 17 | 5AM to 6AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
May | 17 | 6AM to 7AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
May | 17 | 7AM to 8AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
May | 17 | 8AM to 9AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
May | 17 | 9AM to 10AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
May | 17 | 10AM to 11AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
May | 17 | 11AM to 12PM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
May | 17 | 12PM to 1PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
May | 17 | 1PM to 2PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
May | 17 | 2PM to 3PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
May | 17 | 3PM to 4PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
May | 17 | 4PM to 5PM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 17 | 5PM to 6PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 17 | 6PM to 7PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 17 | 7PM to 8PM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
May | 17 | 8PM to 9PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 17 | 9PM to 10PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 17 | 10PM to 11PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 17 | 11PM to 12AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
May | 18 | 12AM to 1AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
May | 18 | 1AM to 2AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
May | 18 | 2AM to 3AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
May | 18 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
May | 18 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
May | 18 | 5AM to 6AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
May | 18 | 6AM to 7AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
May | 18 | 7AM to 8AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
May | 18 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
May | 18 | 9AM to 10AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
May | 18 | 10AM to 11AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
May | 18 | 11AM to 12PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
May | 18 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
May | 18 | 1PM to 2PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
May | 18 | 2PM to 3PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
May | 18 | 3PM to 4PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
May | 18 | 4PM to 5PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
May | 18 | 5PM to 6PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
May | 18 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
May | 18 | 7PM to 8PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
May | 18 | 8PM to 9PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
May | 18 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
May | 18 | 10PM to 11PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
May | 18 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
May | 19 | 12AM to 1AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
May | 19 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 19 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 19 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
May | 19 | 4AM to 5AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
May | 19 | 5AM to 6AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 19 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
May | 19 | 7AM to 8AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
May | 19 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
May | 19 | 9AM to 10AM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
May | 19 | 10AM to 11AM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
May | 19 | 11AM to 12PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
May | 19 | 12PM to 1PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
May | 19 | 1PM to 2PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
May | 19 | 2PM to 3PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
May | 19 | 3PM to 4PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
May | 19 | 4PM to 5PM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
May | 19 | 5PM to 6PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 19 | 6PM to 7PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 19 | 7PM to 8PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
May | 19 | 8PM to 9PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 19 | 9PM to 10PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 19 | 10PM to 11PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 19 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
May | 20 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 20 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 20 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
May | 20 | 3AM to 4AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
May | 20 | 4AM to 5AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
May | 20 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
May | 20 | 6AM to 7AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 20 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
May | 20 | 8AM to 9AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
May | 20 | 9AM to 10AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
May | 20 | 10AM to 11AM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
May | 20 | 11AM to 12PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
May | 20 | 12PM to 1PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 20 | 1PM to 2PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 20 | 2PM to 3PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
May | 20 | 3PM to 4PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
May | 20 | 4PM to 5PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 20 | 5PM to 6PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 20 | 6PM to 7PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 20 | 7PM to 8PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 20 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 20 | 9PM to 10PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 20 | 10PM to 11PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 20 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 21 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 21 | 1AM to 2AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 21 | 2AM to 3AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 21 | 3AM to 4AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 21 | 4AM to 5AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 21 | 5AM to 6AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 21 | 6AM to 7AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
May | 21 | 7AM to 8AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 21 | 8AM to 9AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
May | 21 | 9AM to 10AM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 21 | 10AM to 11AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
May | 21 | 11AM to 12PM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
May | 21 | 12PM to 1PM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
May | 21 | 1PM to 2PM | 63 | 61.7 | 61 | 80.4 | 27.62 | 0.0754 | 0.54 | 13.42 | 0
May | 21 | 2PM to 3PM | 63 | 61.1 | 60.1 | 77.8 | 27.22 | 0.0754 | 0.52 | 13.41 | 0
May | 21 | 3PM to 4PM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 21 | 4PM to 5PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
May | 21 | 5PM to 6PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
May | 21 | 6PM to 7PM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
May | 21 | 7PM to 8PM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
May | 21 | 8PM to 9PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
May | 21 | 9PM to 10PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
May | 21 | 10PM to 11PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 21 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
May | 22 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
May | 22 | 1AM to 2AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
May | 22 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 22 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 22 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
May | 22 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 22 | 6AM to 7AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 22 | 7AM to 8AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
May | 22 | 8AM to 9AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
May | 22 | 9AM to 10AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
May | 22 | 10AM to 11AM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
May | 22 | 11AM to 12PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
May | 22 | 12PM to 1PM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
May | 22 | 1PM to 2PM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
May | 22 | 2PM to 3PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
May | 22 | 3PM to 4PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
May | 22 | 4PM to 5PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 22 | 5PM to 6PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 22 | 6PM to 7PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
May | 22 | 7PM to 8PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 22 | 8PM to 9PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 22 | 9PM to 10PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 22 | 10PM to 11PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 22 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 23 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 23 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
May | 23 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 23 | 3AM to 4AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
May | 23 | 4AM to 5AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
May | 23 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
May | 23 | 6AM to 7AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 23 | 7AM to 8AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 23 | 8AM to 9AM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
May | 23 | 9AM to 10AM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
May | 23 | 10AM to 11AM | 66 | 54.3 | 45 | 44.3 | 22.74 | 0.0752 | 0.3 | 13.39 | 0
May | 23 | 11AM to 12PM | 66 | 54.3 | 45 | 44.3 | 22.74 | 0.0752 | 0.3 | 13.39 | 0
May | 23 | 12PM to 1PM | 66 | 55.2 | 46.9 | 47.8 | 23.28 | 0.0752 | 0.32 | 13.4 | 0
May | 23 | 1PM to 2PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
May | 23 | 2PM to 3PM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
May | 23 | 3PM to 4PM | 64 | 53.1 | 44.1 | 42.8 | 22.02 | 0.0755 | 0.29 | 13.33 | 0
May | 23 | 4PM to 5PM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
May | 23 | 5PM to 6PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 23 | 6PM to 7PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 23 | 7PM to 8PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
May | 23 | 8PM to 9PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 23 | 9PM to 10PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 23 | 10PM to 11PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
May | 23 | 11PM to 12AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 24 | 12AM to 1AM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
May | 24 | 1AM to 2AM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
May | 24 | 2AM to 3AM | 63 | 50.2 | 37.9 | 33.7 | 20.35 | 0.0757 | 0.23 | 13.28 | 0
May | 24 | 3AM to 4AM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
May | 24 | 4AM to 5AM | 62.1 | 51.4 | 42.1 | 39.6 | 21.05 | 0.0758 | 0.27 | 13.27 | 0
May | 24 | 5AM to 6AM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
May | 24 | 6AM to 7AM | 64 | 52.6 | 43 | 41 | 21.75 | 0.0755 | 0.28 | 13.32 | 0
May | 24 | 7AM to 8AM | 66 | 53.1 | 42.1 | 39.6 | 22.01 | 0.0752 | 0.27 | 13.37 | 0
May | 24 | 8AM to 9AM | 68 | 54.7 | 44.1 | 42.8 | 22.99 | 0.0749 | 0.29 | 13.43 | 0
May | 24 | 9AM to 10AM | 70 | 55.1 | 43 | 41 | 23.19 | 0.0746 | 0.28 | 13.48 | 0
May | 24 | 10AM to 11AM | 72 | 56.7 | 45 | 44.3 | 24.18 | 0.0743 | 0.3 | 13.54 | 0
May | 24 | 11AM to 12PM | 73.9 | 56.6 | 43 | 41 | 24.15 | 0.0741 | 0.28 | 13.58 | 0
May | 24 | 12PM to 1PM | 73.9 | 57.1 | 44.1 | 42.8 | 24.43 | 0.0741 | 0.29 | 13.58 | 0
May | 24 | 1PM to 2PM | 73 | 56.3 | 43 | 41 | 23.94 | 0.0742 | 0.28 | 13.55 | 0
May | 24 | 2PM to 3PM | 70 | 56.4 | 46 | 46.1 | 23.99 | 0.0746 | 0.31 | 13.49 | 0
May | 24 | 3PM to 4PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
May | 24 | 4PM to 5PM | 68 | 55.1 | 45 | 44.3 | 23.22 | 0.0749 | 0.3 | 13.44 | 0
May | 24 | 5PM to 6PM | 64.9 | 54.8 | 46.9 | 47.8 | 23.02 | 0.0753 | 0.32 | 13.37 | 0
May | 24 | 6PM to 7PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
May | 24 | 7PM to 8PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
May | 24 | 8PM to 9PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 24 | 9PM to 10PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 24 | 10PM to 11PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
May | 24 | 11PM to 12AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 25 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 25 | 1AM to 2AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 25 | 2AM to 3AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 25 | 3AM to 4AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
May | 25 | 4AM to 5AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 25 | 5AM to 6AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
May | 25 | 6AM to 7AM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
May | 25 | 7AM to 8AM | 72 | 59.4 | 51.1 | 55.9 | 25.99 | 0.0743 | 0.38 | 13.57 | 0
May | 25 | 8AM to 9AM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
May | 25 | 9AM to 10AM | 75 | 60.5 | 51.1 | 55.9 | 26.74 | 0.0738 | 0.38 | 13.65 | 0
May | 25 | 10AM to 11AM | 77 | 61.3 | 51.1 | 55.9 | 27.22 | 0.0736 | 0.38 | 13.7 | 0
May | 25 | 11AM to 12PM | 80.1 | 61 | 48 | 49.8 | 27.01 | 0.0732 | 0.34 | 13.76 | 0
May | 25 | 12PM to 1PM | 81 | 62.2 | 50 | 53.6 | 27.84 | 0.073 | 0.36 | 13.79 | 0
May | 25 | 1PM to 2PM | 78.1 | 60.7 | 48.9 | 51.5 | 26.8 | 0.0735 | 0.35 | 13.71 | 0
May | 25 | 2PM to 3PM | 75.9 | 59.5 | 48 | 49.8 | 26 | 0.0738 | 0.34 | 13.65 | 0
May | 25 | 3PM to 4PM | 77 | 59.4 | 46.9 | 47.8 | 25.95 | 0.0736 | 0.32 | 13.68 | 0
May | 25 | 4PM to 5PM | 75 | 58.3 | 46 | 46.1 | 25.22 | 0.0739 | 0.31 | 13.62 | 0
May | 25 | 5PM to 6PM | 72 | 57.1 | 46 | 46.1 | 24.48 | 0.0743 | 0.31 | 13.54 | 0
May | 25 | 6PM to 7PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
May | 25 | 7PM to 8PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 25 | 8PM to 9PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
May | 25 | 9PM to 10PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 25 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
May | 25 | 11PM to 12AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
May | 26 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
May | 26 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
May | 26 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
May | 26 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
May | 26 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
May | 26 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
May | 26 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
May | 26 | 7AM to 8AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
May | 26 | 8AM to 9AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
May | 26 | 9AM to 10AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
May | 26 | 10AM to 11AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
May | 26 | 11AM to 12PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
May | 26 | 12PM to 1PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 26 | 1PM to 2PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
May | 26 | 2PM to 3PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
May | 26 | 3PM to 4PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
May | 26 | 4PM to 5PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 26 | 5PM to 6PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 26 | 6PM to 7PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 26 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 26 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 26 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 26 | 10PM to 11PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 26 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 27 | 12AM to 1AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 27 | 1AM to 2AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 27 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 27 | 3AM to 4AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
May | 27 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
May | 27 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
May | 27 | 6AM to 7AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 27 | 7AM to 8AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
May | 27 | 8AM to 9AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
May | 27 | 9AM to 10AM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
May | 27 | 10AM to 11AM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
May | 27 | 11AM to 12PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
May | 27 | 12PM to 1PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
May | 27 | 1PM to 2PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
May | 27 | 2PM to 3PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
May | 27 | 3PM to 4PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
May | 27 | 4PM to 5PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 27 | 5PM to 6PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
May | 27 | 6PM to 7PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 27 | 7PM to 8PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
May | 27 | 8PM to 9PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
May | 27 | 9PM to 10PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
May | 27 | 10PM to 11PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 27 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 28 | 12AM to 1AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 28 | 1AM to 2AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 28 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 28 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 28 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 28 | 5AM to 6AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 28 | 6AM to 7AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
May | 28 | 7AM to 8AM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
May | 28 | 8AM to 9AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 28 | 9AM to 10AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
May | 28 | 10AM to 11AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
May | 28 | 11AM to 12PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 28 | 12PM to 1PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
May | 28 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 28 | 2PM to 3PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
May | 28 | 3PM to 4PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
May | 28 | 4PM to 5PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 28 | 5PM to 6PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 28 | 6PM to 7PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 28 | 7PM to 8PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 28 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 28 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 28 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 28 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 29 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 5AM to 6AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 29 | 6AM to 7AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
May | 29 | 7AM to 8AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 29 | 8AM to 9AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
May | 29 | 9AM to 10AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 29 | 10AM to 11AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 29 | 11AM to 12PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
May | 29 | 12PM to 1PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 29 | 1PM to 2PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 29 | 2PM to 3PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 29 | 3PM to 4PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 29 | 4PM to 5PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 29 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 29 | 6PM to 7PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
May | 29 | 7PM to 8PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 29 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 29 | 9PM to 10PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 29 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 29 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 30 | 12AM to 1AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 30 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 30 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 30 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
May | 30 | 4AM to 5AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
May | 30 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 30 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 30 | 7AM to 8AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
May | 30 | 8AM to 9AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 30 | 9AM to 10AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
May | 30 | 10AM to 11AM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
May | 30 | 11AM to 12PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 30 | 12PM to 1PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 30 | 1PM to 2PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 30 | 2PM to 3PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 30 | 3PM to 4PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 30 | 4PM to 5PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 30 | 5PM to 6PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
May | 30 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
May | 30 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 30 | 8PM to 9PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 30 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 30 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 30 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 31 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 31 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 31 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 31 | 3AM to 4AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 31 | 4AM to 5AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
May | 31 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 31 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 31 | 7AM to 8AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 31 | 8AM to 9AM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 31 | 9AM to 10AM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
May | 31 | 10AM to 11AM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
May | 31 | 11AM to 12PM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
May | 31 | 12PM to 1PM | 66 | 55.2 | 46.9 | 47.8 | 23.28 | 0.0752 | 0.32 | 13.4 | 0
May | 31 | 1PM to 2PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
May | 31 | 2PM to 3PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
May | 31 | 3PM to 4PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
May | 31 | 4PM to 5PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
May | 31 | 5PM to 6PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
May | 31 | 6PM to 7PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
May | 31 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
May | 31 | 8PM to 9PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
May | 31 | 9PM to 10PM | 54.3 | 52.8 | 51.6 | 57 | 21.87 | 0.0768 | 0.39 | 13.13 | 0
May | 31 | 10PM to 11PM | 53.6 | 52.4 | 51.4 | 56.6 | 21.64 | 0.0769 | 0.38 | 13.11 | 0
May | 31 | 11PM to 12AM | 52.9 | 51.9 | 51.1 | 55.9 | 21.34 | 0.077 | 0.38 | 13.09 | 0
June | 1 | 12AM to 1AM | 52.2 | 51.4 | 50.9 | 55.5 | 21.11 | 0.0771 | 0.37 | 13.07 | 0
June | 1 | 1AM to 2AM | 51.4 | 50.9 | 50.5 | 54.7 | 20.82 | 0.0773 | 0.37 | 13.04 | 0
June | 1 | 2AM to 3AM | 50.7 | 50.5 | 50.4 | 54.4 | 20.59 | 0.0774 | 0.37 | 13.03 | 1
June | 1 | 3AM to 4AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
June | 1 | 4AM to 5AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
June | 1 | 5AM to 6AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
June | 1 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 1 | 7AM to 8AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
June | 1 | 8AM to 9AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
June | 1 | 9AM to 10AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
June | 1 | 10AM to 11AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
June | 1 | 11AM to 12PM | 73 | 61.8 | 55 | 64.7 | 27.64 | 0.0741 | 0.44 | 13.63 | 0
June | 1 | 12PM to 1PM | 75.9 | 63.3 | 55.9 | 66.9 | 28.69 | 0.0737 | 0.45 | 13.71 | 0
June | 1 | 1PM to 2PM | 82 | 64.4 | 54 | 62.2 | 29.44 | 0.0728 | 0.42 | 13.85 | 0
June | 1 | 2PM to 3PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
June | 1 | 3PM to 4PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
June | 1 | 4PM to 5PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 1 | 5PM to 6PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 1 | 6PM to 7PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 1 | 7PM to 8PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 1 | 8PM to 9PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 1 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 1 | 10PM to 11PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 1 | 11PM to 12AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 2 | 12AM to 1AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 2 | 1AM to 2AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 2 | 2AM to 3AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 2 | 3AM to 4AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 2 | 4AM to 5AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 2 | 5AM to 6AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
June | 2 | 6AM to 7AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
June | 2 | 7AM to 8AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
June | 2 | 8AM to 9AM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
June | 2 | 9AM to 10AM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
June | 2 | 10AM to 11AM | 75.9 | 63.8 | 57 | 69.6 | 29.11 | 0.0736 | 0.47 | 13.72 | 0
June | 2 | 11AM to 12PM | 80.1 | 63.3 | 53.1 | 60.1 | 28.64 | 0.0731 | 0.41 | 13.79 | 0
June | 2 | 12PM to 1PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
June | 2 | 1PM to 2PM | 84 | 67.5 | 59 | 74.9 | 31.91 | 0.0725 | 0.5 | 13.94 | 0
June | 2 | 2PM to 3PM | 89.1 | 68.1 | 57 | 69.6 | 32.32 | 0.0719 | 0.47 | 14.05 | 0
June | 2 | 3PM to 4PM | 80.1 | 64.2 | 55 | 64.7 | 29.35 | 0.0731 | 0.44 | 13.81 | 0
June | 2 | 4PM to 5PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
June | 2 | 5PM to 6PM | 77 | 61.7 | 52 | 57.8 | 27.52 | 0.0736 | 0.39 | 13.71 | 0
June | 2 | 6PM to 7PM | 73 | 60.3 | 52 | 57.8 | 26.55 | 0.0741 | 0.39 | 13.61 | 0
June | 2 | 7PM to 8PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
June | 2 | 8PM to 9PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
June | 2 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
June | 2 | 10PM to 11PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 2 | 11PM to 12AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 3 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 3 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 3 | 2AM to 3AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 3 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 3 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 3 | 5AM to 6AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 3 | 6AM to 7AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
June | 3 | 7AM to 8AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 3 | 8AM to 9AM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
June | 3 | 9AM to 10AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
June | 3 | 10AM to 11AM | 77 | 63.2 | 55 | 64.7 | 28.61 | 0.0735 | 0.44 | 13.73 | 0
June | 3 | 11AM to 12PM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
June | 3 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
June | 3 | 1PM to 2PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
June | 3 | 2PM to 3PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
June | 3 | 3PM to 4PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
June | 3 | 4PM to 5PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 3 | 5PM to 6PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
June | 3 | 6PM to 7PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
June | 3 | 7PM to 8PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 3 | 8PM to 9PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 3 | 9PM to 10PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
June | 3 | 10PM to 11PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
June | 3 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 4 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 4 | 1AM to 2AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 4 | 2AM to 3AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
June | 4 | 3AM to 4AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
June | 4 | 4AM to 5AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
June | 4 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 4 | 6AM to 7AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 4 | 7AM to 8AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 4 | 8AM to 9AM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 4 | 9AM to 10AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 4 | 10AM to 11AM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 4 | 11AM to 12PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
June | 4 | 12PM to 1PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 4 | 1PM to 2PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
June | 4 | 2PM to 3PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
June | 4 | 3PM to 4PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 4 | 4PM to 5PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 4 | 5PM to 6PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 4 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 4 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 4 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 4 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 4 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 4 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 5 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 5 | 1AM to 2AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 5 | 2AM to 3AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 5 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 5 | 4AM to 5AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 5 | 5AM to 6AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 5 | 6AM to 7AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
June | 5 | 7AM to 8AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
June | 5 | 8AM to 9AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
June | 5 | 9AM to 10AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
June | 5 | 10AM to 11AM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
June | 5 | 11AM to 12PM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
June | 5 | 12PM to 1PM | 84.9 | 65.8 | 55 | 64.7 | 30.54 | 0.0724 | 0.44 | 13.93 | 0
June | 5 | 1PM to 2PM | 82.9 | 65.2 | 55 | 64.7 | 30.06 | 0.0727 | 0.44 | 13.88 | 0
June | 5 | 2PM to 3PM | 77 | 62.2 | 53.1 | 60.1 | 27.89 | 0.0735 | 0.41 | 13.71 | 0
June | 5 | 3PM to 4PM | 73 | 60.3 | 52 | 57.8 | 26.55 | 0.0741 | 0.39 | 13.61 | 0
June | 5 | 4PM to 5PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
June | 5 | 5PM to 6PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
June | 5 | 6PM to 7PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 5 | 7PM to 8PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 5 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 5 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 5 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 5 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 6 | 12AM to 1AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 6 | 1AM to 2AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 6 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 6 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 6 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 6 | 5AM to 6AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 6 | 6AM to 7AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 6 | 7AM to 8AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
June | 6 | 8AM to 9AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
June | 6 | 9AM to 10AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
June | 6 | 10AM to 11AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
June | 6 | 11AM to 12PM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
June | 6 | 12PM to 1PM | 79 | 63.9 | 55 | 64.7 | 29.09 | 0.0732 | 0.44 | 13.78 | 0
June | 6 | 1PM to 2PM | 77 | 62.2 | 53.1 | 60.1 | 27.89 | 0.0735 | 0.41 | 13.71 | 0
June | 6 | 2PM to 3PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
June | 6 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
June | 6 | 4PM to 5PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 6 | 5PM to 6PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 6 | 6PM to 7PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 6 | 7PM to 8PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
June | 6 | 8PM to 9PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
June | 6 | 9PM to 10PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
June | 6 | 10PM to 11PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
June | 6 | 11PM to 12AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
June | 7 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 7 | 1AM to 2AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 7 | 2AM to 3AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 7 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 7 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 7 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 7 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 7 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
June | 7 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 7 | 9AM to 10AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
June | 7 | 10AM to 11AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 7 | 11AM to 12PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 7 | 12PM to 1PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 7 | 1PM to 2PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 7 | 2PM to 3PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 7 | 3PM to 4PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
June | 7 | 4PM to 5PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
June | 7 | 5PM to 6PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 7 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 7 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 7 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 7 | 9PM to 10PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 7 | 10PM to 11PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 7 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 8 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 8 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 8 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 8 | 3AM to 4AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
June | 8 | 4AM to 5AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
June | 8 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 8 | 6AM to 7AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 8 | 7AM to 8AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 8 | 8AM to 9AM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
June | 8 | 9AM to 10AM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
June | 8 | 10AM to 11AM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
June | 8 | 11AM to 12PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
June | 8 | 12PM to 1PM | 71.1 | 58.1 | 48.9 | 51.5 | 25.09 | 0.0744 | 0.35 | 13.54 | 0
June | 8 | 1PM to 2PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
June | 8 | 2PM to 3PM | 69.1 | 56.9 | 48 | 49.8 | 24.34 | 0.0747 | 0.34 | 13.48 | 0
June | 8 | 3PM to 4PM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
June | 8 | 4PM to 5PM | 64.9 | 54.8 | 46.9 | 47.8 | 23.02 | 0.0753 | 0.32 | 13.37 | 0
June | 8 | 5PM to 6PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
June | 8 | 6PM to 7PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
June | 8 | 7PM to 8PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
June | 8 | 8PM to 9PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
June | 8 | 9PM to 10PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
June | 8 | 10PM to 11PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 8 | 11PM to 12AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 9 | 12AM to 1AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 9 | 1AM to 2AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 9 | 2AM to 3AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 9 | 3AM to 4AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 9 | 4AM to 5AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 9 | 5AM to 6AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 9 | 6AM to 7AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 9 | 7AM to 8AM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
June | 9 | 8AM to 9AM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
June | 9 | 9AM to 10AM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
June | 9 | 10AM to 11AM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
June | 9 | 11AM to 12PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
June | 9 | 12PM to 1PM | 69.1 | 55.5 | 45 | 44.3 | 23.48 | 0.0747 | 0.3 | 13.46 | 0
June | 9 | 1PM to 2PM | 68 | 55.1 | 45 | 44.3 | 23.22 | 0.0749 | 0.3 | 13.44 | 0
June | 9 | 2PM to 3PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
June | 9 | 3PM to 4PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
June | 9 | 4PM to 5PM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
June | 9 | 5PM to 6PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
June | 9 | 6PM to 7PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
June | 9 | 7PM to 8PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
June | 9 | 8PM to 9PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 9 | 9PM to 10PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 9 | 10PM to 11PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
June | 9 | 11PM to 12AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 10 | 12AM to 1AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 10 | 1AM to 2AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 10 | 2AM to 3AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 10 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 10 | 4AM to 5AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 10 | 5AM to 6AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 10 | 6AM to 7AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 10 | 7AM to 8AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
June | 10 | 8AM to 9AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 10 | 9AM to 10AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 10 | 10AM to 11AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 10 | 11AM to 12PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
June | 10 | 12PM to 1PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
June | 10 | 1PM to 2PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
June | 10 | 2PM to 3PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
June | 10 | 3PM to 4PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
June | 10 | 4PM to 5PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 10 | 5PM to 6PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
June | 10 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 10 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 10 | 8PM to 9PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 10 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 10 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 10 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 11 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 11 | 1AM to 2AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 11 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 11 | 3AM to 4AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
June | 11 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 11 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 11 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 11 | 7AM to 8AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 11 | 8AM to 9AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
June | 11 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
June | 11 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
June | 11 | 11AM to 12PM | 71.1 | 59.5 | 52 | 57.8 | 26.07 | 0.0744 | 0.39 | 13.56 | 0
June | 11 | 12PM to 1PM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
June | 11 | 1PM to 2PM | 72 | 59.4 | 51.1 | 55.9 | 25.99 | 0.0743 | 0.38 | 13.57 | 0
June | 11 | 2PM to 3PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
June | 11 | 3PM to 4PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
June | 11 | 4PM to 5PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
June | 11 | 5PM to 6PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 11 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 11 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 11 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 11 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 11 | 10PM to 11PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 11 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 12AM to 1AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 12 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 12 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 12 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 12 | 5AM to 6AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 12 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 12 | 7AM to 8AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 12 | 8AM to 9AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 12 | 9AM to 10AM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
June | 12 | 10AM to 11AM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
June | 12 | 11AM to 12PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 12 | 12PM to 1PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 12 | 1PM to 2PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 12 | 2PM to 3PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 12 | 3PM to 4PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 12 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 12 | 5PM to 6PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 12 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 12 | 7PM to 8PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 8PM to 9PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 13 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 13 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 13 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 13 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 13 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 13 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 13 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 13 | 7AM to 8AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 13 | 8AM to 9AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 13 | 9AM to 10AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 13 | 10AM to 11AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 13 | 11AM to 12PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 13 | 12PM to 1PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 13 | 1PM to 2PM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
June | 13 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 13 | 3PM to 4PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 13 | 4PM to 5PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 13 | 5PM to 6PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 13 | 6PM to 7PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
June | 13 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 13 | 8PM to 9PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 13 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 13 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 13 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 14 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 14 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 14 | 2AM to 3AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
June | 14 | 3AM to 4AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 14 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
June | 14 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 14 | 6AM to 7AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
June | 14 | 7AM to 8AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 14 | 8AM to 9AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 14 | 9AM to 10AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 14 | 10AM to 11AM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
June | 14 | 11AM to 12PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
June | 14 | 12PM to 1PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
June | 14 | 1PM to 2PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
June | 14 | 2PM to 3PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
June | 14 | 3PM to 4PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
June | 14 | 4PM to 5PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
June | 14 | 5PM to 6PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
June | 14 | 6PM to 7PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 14 | 7PM to 8PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 14 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 14 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 14 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 14 | 11PM to 12AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 15 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 15 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 15 | 6AM to 7AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 15 | 7AM to 8AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 8AM to 9AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 15 | 9AM to 10AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 15 | 10AM to 11AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 15 | 11AM to 12PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 15 | 12PM to 1PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 15 | 1PM to 2PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 15 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 15 | 3PM to 4PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 15 | 4PM to 5PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 15 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 15 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 15 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 15 | 8PM to 9PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 15 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 15 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 15 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 16 | 4AM to 5AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
June | 16 | 5AM to 6AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
June | 16 | 6AM to 7AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
June | 16 | 7AM to 8AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
June | 16 | 8AM to 9AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 16 | 9AM to 10AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 16 | 10AM to 11AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 11AM to 12PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 16 | 12PM to 1PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 16 | 1PM to 2PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 16 | 2PM to 3PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 16 | 3PM to 4PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 16 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 16 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 16 | 6PM to 7PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 16 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 16 | 8PM to 9PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 16 | 9PM to 10PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 16 | 10PM to 11PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 16 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
June | 17 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 5AM to 6AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
June | 17 | 6AM to 7AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 17 | 7AM to 8AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
June | 17 | 8AM to 9AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
June | 17 | 9AM to 10AM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
June | 17 | 10AM to 11AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
June | 17 | 11AM to 12PM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
June | 17 | 12PM to 1PM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
June | 17 | 1PM to 2PM | 64.9 | 53.5 | 44.1 | 42.8 | 22.24 | 0.0753 | 0.29 | 13.35 | 0
June | 17 | 2PM to 3PM | 63 | 52.6 | 44.1 | 42.8 | 21.76 | 0.0756 | 0.29 | 13.3 | 0
June | 17 | 3PM to 4PM | 64 | 53.1 | 44.1 | 42.8 | 22.02 | 0.0755 | 0.29 | 13.33 | 0
June | 17 | 4PM to 5PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
June | 17 | 5PM to 6PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
June | 17 | 6PM to 7PM | 57.9 | 50 | 43 | 41 | 20.27 | 0.0764 | 0.28 | 13.17 | 0
June | 17 | 7PM to 8PM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
June | 17 | 8PM to 9PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
June | 17 | 9PM to 10PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
June | 17 | 10PM to 11PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
June | 17 | 11PM to 12AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
June | 18 | 12AM to 1AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
June | 18 | 1AM to 2AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
June | 18 | 2AM to 3AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 18 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
June | 18 | 4AM to 5AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
June | 18 | 5AM to 6AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
June | 18 | 6AM to 7AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
June | 18 | 7AM to 8AM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
June | 18 | 8AM to 9AM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
June | 18 | 9AM to 10AM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
June | 18 | 10AM to 11AM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
June | 18 | 11AM to 12PM | 72 | 56.3 | 44.1 | 42.8 | 23.95 | 0.0744 | 0.29 | 13.53 | 0
June | 18 | 12PM to 1PM | 69.1 | 56.4 | 46.9 | 47.8 | 24.03 | 0.0747 | 0.32 | 13.47 | 0
June | 18 | 1PM to 2PM | 66.9 | 54.3 | 44.1 | 42.8 | 22.72 | 0.0751 | 0.29 | 13.4 | 0
June | 18 | 2PM to 3PM | 66.9 | 53.8 | 43 | 41 | 22.45 | 0.0751 | 0.28 | 13.4 | 0
June | 18 | 3PM to 4PM | 64.9 | 52.6 | 42.1 | 39.6 | 21.75 | 0.0754 | 0.27 | 13.34 | 0
June | 18 | 4PM to 5PM | 64 | 51.8 | 41 | 38 | 21.28 | 0.0755 | 0.26 | 13.32 | 0
June | 18 | 5PM to 6PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
June | 18 | 6PM to 7PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
June | 18 | 7PM to 8PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
June | 18 | 8PM to 9PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
June | 18 | 9PM to 10PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
June | 18 | 10PM to 11PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
June | 18 | 11PM to 12AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
June | 19 | 12AM to 1AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
June | 19 | 1AM to 2AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 19 | 2AM to 3AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 19 | 3AM to 4AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
June | 19 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 19 | 5AM to 6AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 19 | 6AM to 7AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
June | 19 | 7AM to 8AM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
June | 19 | 8AM to 9AM | 66 | 55.2 | 46.9 | 47.8 | 23.28 | 0.0752 | 0.32 | 13.4 | 0
June | 19 | 9AM to 10AM | 66.9 | 56.1 | 48 | 49.8 | 23.81 | 0.075 | 0.34 | 13.42 | 0
June | 19 | 10AM to 11AM | 73 | 57.9 | 46.9 | 47.8 | 24.99 | 0.0742 | 0.32 | 13.57 | 0
June | 19 | 11AM to 12PM | 70 | 57.2 | 48 | 49.8 | 24.56 | 0.0746 | 0.34 | 13.5 | 0
June | 19 | 12PM to 1PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
June | 19 | 1PM to 2PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
June | 19 | 2PM to 3PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
June | 19 | 3PM to 4PM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
June | 19 | 4PM to 5PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 19 | 5PM to 6PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 19 | 6PM to 7PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 19 | 7PM to 8PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 19 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 19 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 19 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 19 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 20 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 20 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 20 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 7AM to 8AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 20 | 8AM to 9AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 20 | 9AM to 10AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 20 | 10AM to 11AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 20 | 11AM to 12PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 20 | 12PM to 1PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 20 | 1PM to 2PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 20 | 2PM to 3PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 20 | 3PM to 4PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 20 | 4PM to 5PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 20 | 5PM to 6PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 20 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 20 | 7PM to 8PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 20 | 8PM to 9PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 20 | 9PM to 10PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 20 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 21 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 4AM to 5AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 5AM to 6AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 6AM to 7AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 21 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 21 | 8AM to 9AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 21 | 9AM to 10AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
June | 21 | 10AM to 11AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 21 | 11AM to 12PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 21 | 12PM to 1PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 21 | 1PM to 2PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 21 | 2PM to 3PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 21 | 3PM to 4PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
June | 21 | 4PM to 5PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
June | 21 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 21 | 6PM to 7PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 21 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 21 | 8PM to 9PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 21 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 21 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 11PM to 12AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 22 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
June | 22 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
June | 22 | 2AM to 3AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
June | 22 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
June | 22 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
June | 22 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 22 | 6AM to 7AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 22 | 7AM to 8AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
June | 22 | 8AM to 9AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 22 | 9AM to 10AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
June | 22 | 10AM to 11AM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 22 | 11AM to 12PM | 70 | 57.7 | 48.9 | 51.5 | 24.83 | 0.0746 | 0.35 | 13.51 | 0
June | 22 | 12PM to 1PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
June | 22 | 1PM to 2PM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
June | 22 | 2PM to 3PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
June | 22 | 3PM to 4PM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
June | 22 | 4PM to 5PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
June | 22 | 5PM to 6PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
June | 22 | 6PM to 7PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
June | 22 | 7PM to 8PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
June | 22 | 8PM to 9PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
June | 22 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
June | 22 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 22 | 11PM to 12AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 23 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 23 | 1AM to 2AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
June | 23 | 2AM to 3AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
June | 23 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 23 | 4AM to 5AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
June | 23 | 5AM to 6AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
June | 23 | 6AM to 7AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 23 | 7AM to 8AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
June | 23 | 8AM to 9AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
June | 23 | 9AM to 10AM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
June | 23 | 10AM to 11AM | 71.1 | 58.6 | 50 | 53.6 | 25.43 | 0.0744 | 0.36 | 13.54 | 0
June | 23 | 11AM to 12PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
June | 23 | 12PM to 1PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
June | 23 | 1PM to 2PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 23 | 2PM to 3PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 23 | 3PM to 4PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
June | 23 | 4PM to 5PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
June | 23 | 5PM to 6PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
June | 23 | 6PM to 7PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
June | 23 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
June | 23 | 8PM to 9PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
June | 23 | 9PM to 10PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
June | 23 | 10PM to 11PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
June | 23 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
June | 24 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 24 | 1AM to 2AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
June | 24 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 24 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 24 | 4AM to 5AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
June | 24 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 24 | 6AM to 7AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 24 | 7AM to 8AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
June | 24 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 24 | 9AM to 10AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
June | 24 | 10AM to 11AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 24 | 11AM to 12PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
June | 24 | 12PM to 1PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 24 | 1PM to 2PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
June | 24 | 2PM to 3PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 24 | 3PM to 4PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 24 | 4PM to 5PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 24 | 5PM to 6PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 24 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 24 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 24 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 24 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 24 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 24 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 25 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 2AM to 3AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 25 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 25 | 4AM to 5AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 25 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 25 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 25 | 8AM to 9AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 25 | 9AM to 10AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 25 | 10AM to 11AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 25 | 11AM to 12PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 25 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 25 | 1PM to 2PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 25 | 2PM to 3PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 25 | 3PM to 4PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
June | 25 | 4PM to 5PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
June | 25 | 5PM to 6PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 25 | 6PM to 7PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 25 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 25 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 10PM to 11PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
June | 25 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 26 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 26 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 26 | 2AM to 3AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 26 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 26 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 26 | 5AM to 6AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 26 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 26 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 26 | 8AM to 9AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 26 | 9AM to 10AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 26 | 10AM to 11AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 26 | 11AM to 12PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 26 | 12PM to 1PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 26 | 1PM to 2PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 26 | 2PM to 3PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 26 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 26 | 4PM to 5PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 26 | 5PM to 6PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 26 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 26 | 7PM to 8PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 26 | 8PM to 9PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 26 | 9PM to 10PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 26 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 26 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 27 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
June | 27 | 1AM to 2AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 27 | 2AM to 3AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 27 | 3AM to 4AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 27 | 4AM to 5AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 27 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 27 | 6AM to 7AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 27 | 7AM to 8AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 27 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 27 | 9AM to 10AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 27 | 10AM to 11AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
June | 27 | 11AM to 12PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 27 | 12PM to 1PM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
June | 27 | 1PM to 2PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
June | 27 | 2PM to 3PM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
June | 27 | 3PM to 4PM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
June | 27 | 4PM to 5PM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
June | 27 | 5PM to 6PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
June | 27 | 6PM to 7PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 27 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 27 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 27 | 9PM to 10PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 27 | 10PM to 11PM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
June | 27 | 11PM to 12AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 28 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 5AM to 6AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
June | 28 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 28 | 7AM to 8AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
June | 28 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 28 | 9AM to 10AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
June | 28 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
June | 28 | 11AM to 12PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
June | 28 | 12PM to 1PM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
June | 28 | 1PM to 2PM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
June | 28 | 2PM to 3PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
June | 28 | 3PM to 4PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
June | 28 | 4PM to 5PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
June | 28 | 5PM to 6PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
June | 28 | 6PM to 7PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
June | 28 | 7PM to 8PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 28 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 28 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 28 | 10PM to 11PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 28 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 29 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 29 | 1AM to 2AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 29 | 2AM to 3AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 29 | 3AM to 4AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 29 | 4AM to 5AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 29 | 5AM to 6AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 29 | 6AM to 7AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
June | 29 | 7AM to 8AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
June | 29 | 8AM to 9AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
June | 29 | 9AM to 10AM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
June | 29 | 10AM to 11AM | 80.1 | 62.7 | 52 | 57.8 | 28.26 | 0.0731 | 0.39 | 13.78 | 0
June | 29 | 11AM to 12PM | 82 | 64.9 | 55 | 64.7 | 29.84 | 0.0728 | 0.44 | 13.86 | 0
June | 29 | 12PM to 1PM | 84 | 65 | 54 | 62.2 | 29.92 | 0.0726 | 0.42 | 13.9 | 0
June | 29 | 1PM to 2PM | 81 | 63.1 | 52 | 57.8 | 28.48 | 0.073 | 0.39 | 13.81 | 0
June | 29 | 2PM to 3PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
June | 29 | 3PM to 4PM | 77 | 61.7 | 52 | 57.8 | 27.52 | 0.0736 | 0.39 | 13.71 | 0
June | 29 | 4PM to 5PM | 75.9 | 60.4 | 50 | 53.6 | 26.61 | 0.0737 | 0.36 | 13.67 | 0
June | 29 | 5PM to 6PM | 73.9 | 59.6 | 50 | 53.6 | 26.13 | 0.074 | 0.36 | 13.62 | 0
June | 29 | 6PM to 7PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
June | 29 | 7PM to 8PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 29 | 8PM to 9PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 29 | 9PM to 10PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 29 | 10PM to 11PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 29 | 11PM to 12AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 30 | 12AM to 1AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 30 | 1AM to 2AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 30 | 2AM to 3AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 30 | 3AM to 4AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 30 | 4AM to 5AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 30 | 5AM to 6AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
June | 30 | 6AM to 7AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
June | 30 | 7AM to 8AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
June | 30 | 8AM to 9AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
June | 30 | 9AM to 10AM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
June | 30 | 10AM to 11AM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
June | 30 | 11AM to 12PM | 82 | 63.9 | 53.1 | 60.1 | 29.12 | 0.0729 | 0.41 | 13.84 | 0
June | 30 | 12PM to 1PM | 90 | 67.4 | 55 | 64.7 | 31.77 | 0.0718 | 0.44 | 14.06 | 0
June | 30 | 1PM to 2PM | 91 | 67.8 | 55 | 64.7 | 32.03 | 0.0716 | 0.44 | 14.09 | 0
June | 30 | 2PM to 3PM | 86 | 65.7 | 54 | 62.2 | 30.41 | 0.0723 | 0.42 | 13.95 | 0
June | 30 | 3PM to 4PM | 82.9 | 64.2 | 53.1 | 60.1 | 29.34 | 0.0727 | 0.41 | 13.87 | 0
June | 30 | 4PM to 5PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
June | 30 | 5PM to 6PM | 78.1 | 62.6 | 53.1 | 60.1 | 28.15 | 0.0734 | 0.41 | 13.74 | 0
June | 30 | 6PM to 7PM | 77 | 61.7 | 52 | 57.8 | 27.52 | 0.0736 | 0.39 | 13.71 | 0
June | 30 | 7PM to 8PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 30 | 8PM to 9PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 30 | 9PM to 10PM | 63.1 | 56 | 50.9 | 55.5 | 23.79 | 0.0755 | 0.37 | 13.35 | 0
June | 30 | 10PM to 11PM | 61.2 | 54.7 | 50 | 53.6 | 23.02 | 0.0758 | 0.36 | 13.29 | 0
June | 30 | 11PM to 12AM | 59.4 | 53.4 | 48.9 | 51.5 | 22.24 | 0.0761 | 0.35 | 13.24 | 0
July | 1 | 12AM to 1AM | 57.6 | 52.2 | 48 | 49.8 | 21.54 | 0.0764 | 0.34 | 13.19 | 0
July | 1 | 1AM to 2AM | 55.8 | 50.9 | 46.9 | 47.8 | 20.79 | 0.0767 | 0.32 | 13.13 | 0
July | 1 | 2AM to 3AM | 53.8 | 49.6 | 46 | 46.1 | 20.06 | 0.077 | 0.31 | 13.08 | 0
July | 1 | 3AM to 4AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
July | 1 | 4AM to 5AM | 53.2 | 49 | 45.3 | 44.9 | 19.73 | 0.0771 | 0.3 | 13.06 | 0
July | 1 | 5AM to 6AM | 54.7 | 49.9 | 45.9 | 45.8 | 20.23 | 0.0768 | 0.31 | 13.1 | 0
July | 1 | 6AM to 7AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
July | 1 | 7AM to 8AM | 59 | 52 | 46.2 | 46.5 | 21.38 | 0.0762 | 0.31 | 13.21 | 0
July | 1 | 8AM to 9AM | 61.9 | 53 | 45.9 | 45.8 | 21.98 | 0.0758 | 0.31 | 13.28 | 0
July | 1 | 9AM to 10AM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
July | 1 | 10AM to 11AM | 64.6 | 54 | 45.7 | 45.5 | 22.58 | 0.0754 | 0.31 | 13.35 | 0
July | 1 | 11AM to 12PM | 64.4 | 54.1 | 46 | 46.1 | 22.64 | 0.0754 | 0.31 | 13.35 | 0
July | 1 | 12PM to 1PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
July | 1 | 1PM to 2PM | 64 | 54.1 | 46.2 | 46.5 | 22.6 | 0.0755 | 0.31 | 13.34 | 0
July | 1 | 2PM to 3PM | 64 | 54.1 | 46.2 | 46.5 | 22.6 | 0.0755 | 0.31 | 13.34 | 0
July | 1 | 3PM to 4PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
July | 1 | 4PM to 5PM | 61.7 | 53.4 | 46.9 | 47.8 | 22.23 | 0.0758 | 0.32 | 13.29 | 0
July | 1 | 5PM to 6PM | 59.4 | 52.7 | 47.5 | 48.8 | 21.82 | 0.0761 | 0.33 | 13.23 | 0
July | 1 | 6PM to 7PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
July | 1 | 7PM to 8PM | 56.3 | 51.7 | 48 | 49.8 | 21.23 | 0.0766 | 0.34 | 13.15 | 0
July | 1 | 8PM to 9PM | 55.8 | 51.3 | 47.7 | 49.1 | 21 | 0.0766 | 0.33 | 13.14 | 0
July | 1 | 9PM to 10PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
July | 1 | 10PM to 11PM | 55 | 50.7 | 47.1 | 48.1 | 20.67 | 0.0768 | 0.33 | 13.12 | 0
July | 1 | 11PM to 12AM | 55 | 50.5 | 46.8 | 47.4 | 20.56 | 0.0768 | 0.32 | 13.12 | 0
July | 2 | 12AM to 1AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
July | 2 | 1AM to 2AM | 54.7 | 50.1 | 46.2 | 46.5 | 20.33 | 0.0768 | 0.31 | 13.1 | 0
July | 2 | 2AM to 3AM | 54.3 | 49.7 | 45.7 | 45.5 | 20.09 | 0.0769 | 0.31 | 13.09 | 0
July | 2 | 3AM to 4AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
July | 2 | 4AM to 5AM | 55.2 | 49.9 | 45.3 | 44.9 | 20.21 | 0.0768 | 0.3 | 13.11 | 0
July | 2 | 5AM to 6AM | 56.7 | 50.8 | 45.9 | 45.8 | 20.71 | 0.0765 | 0.31 | 13.15 | 0
July | 2 | 6AM to 7AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
July | 2 | 7AM to 8AM | 60.6 | 52.5 | 45.9 | 45.8 | 21.67 | 0.076 | 0.31 | 13.25 | 0
July | 2 | 8AM to 9AM | 63.3 | 53.4 | 45.3 | 44.9 | 22.18 | 0.0756 | 0.3 | 13.32 | 0
July | 2 | 9AM to 10AM | 66 | 53.9 | 44.1 | 42.8 | 22.51 | 0.0752 | 0.29 | 13.38 | 0
July | 2 | 10AM to 11AM | 66.7 | 54.2 | 44.1 | 42.8 | 22.68 | 0.0751 | 0.29 | 13.4 | 0
July | 2 | 11AM to 12PM | 67.3 | 54.3 | 43.7 | 42.2 | 22.72 | 0.075 | 0.29 | 13.41 | 0
July | 2 | 12PM to 1PM | 68 | 54.3 | 43 | 41 | 22.71 | 0.0749 | 0.28 | 13.43 | 0
July | 2 | 1PM to 2PM | 66.7 | 54.7 | 45.1 | 44.6 | 22.96 | 0.0751 | 0.3 | 13.4 | 0
July | 2 | 2PM to 3PM | 65.3 | 55 | 47.1 | 48.1 | 23.16 | 0.0753 | 0.33 | 13.38 | 0
July | 2 | 3PM to 4PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
July | 2 | 4PM to 5PM | 61.7 | 54.8 | 49.8 | 53.3 | 23.09 | 0.0757 | 0.36 | 13.3 | 0
July | 2 | 5PM to 6PM | 59.4 | 54.3 | 50.5 | 54.7 | 22.75 | 0.0761 | 0.37 | 13.25 | 0
July | 2 | 6PM to 7PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
July | 2 | 7PM to 8PM | 56.3 | 52.9 | 50.4 | 54.4 | 21.95 | 0.0765 | 0.37 | 13.17 | 0
July | 2 | 8PM to 9PM | 55.8 | 52.2 | 49.5 | 52.6 | 21.53 | 0.0766 | 0.36 | 13.15 | 0
July | 2 | 9PM to 10PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
July | 2 | 10PM to 11PM | 55 | 51.5 | 48.7 | 51.1 | 21.14 | 0.0767 | 0.35 | 13.13 | 0
July | 2 | 11PM to 12AM | 55 | 51.7 | 49.1 | 51.8 | 21.25 | 0.0767 | 0.35 | 13.13 | 0
July | 3 | 12AM to 1AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
July | 3 | 1AM to 2AM | 55.4 | 52 | 49.5 | 52.6 | 21.45 | 0.0767 | 0.36 | 13.14 | 0
July | 3 | 2AM to 3AM | 55.6 | 52 | 49.3 | 52.2 | 21.43 | 0.0767 | 0.35 | 13.14 | 0
July | 3 | 3AM to 4AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 3 | 4AM to 5AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 3 | 5AM to 6AM | 55.9 | 52.1 | 49.1 | 51.8 | 21.47 | 0.0766 | 0.35 | 13.15 | 0
July | 3 | 6AM to 7AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 3 | 7AM to 8AM | 57 | 52.9 | 49.8 | 53.3 | 21.95 | 0.0764 | 0.36 | 13.18 | 0
July | 3 | 8AM to 9AM | 57.9 | 53.5 | 50.2 | 54 | 22.28 | 0.0763 | 0.37 | 13.21 | 0
July | 3 | 9AM to 10AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
July | 3 | 10AM to 11AM | 60.1 | 54.7 | 50.7 | 55.1 | 22.98 | 0.076 | 0.37 | 13.27 | 0
July | 3 | 11AM to 12PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
July | 3 | 12PM to 1PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
July | 3 | 1PM to 2PM | 61.7 | 55.6 | 51.3 | 56.2 | 23.55 | 0.0757 | 0.38 | 13.31 | 0
July | 3 | 2PM to 3PM | 61.3 | 55.4 | 51.3 | 56.2 | 23.46 | 0.0758 | 0.38 | 13.3 | 0
July | 3 | 3PM to 4PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
July | 3 | 4PM to 5PM | 59.7 | 54.8 | 51.3 | 56.2 | 23.07 | 0.076 | 0.38 | 13.26 | 0
July | 3 | 5PM to 6PM | 58.3 | 54.2 | 51.3 | 56.2 | 22.72 | 0.0762 | 0.38 | 13.22 | 0
July | 3 | 6PM to 7PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
July | 3 | 7PM to 8PM | 56.3 | 53.3 | 51.1 | 55.9 | 22.18 | 0.0765 | 0.38 | 13.17 | 0
July | 3 | 8PM to 9PM | 55.8 | 52.9 | 50.7 | 55.1 | 21.93 | 0.0766 | 0.37 | 13.16 | 0
July | 3 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 3 | 10PM to 11PM | 54.7 | 52 | 50 | 53.6 | 21.44 | 0.0768 | 0.36 | 13.12 | 0
July | 3 | 11PM to 12AM | 54.3 | 51.7 | 49.6 | 52.9 | 21.24 | 0.0768 | 0.36 | 13.11 | 0
July | 4 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
July | 4 | 1AM to 2AM | 54.3 | 51.8 | 49.8 | 53.3 | 21.29 | 0.0768 | 0.36 | 13.11 | 0
July | 4 | 2AM to 3AM | 54.7 | 52 | 50 | 53.6 | 21.44 | 0.0768 | 0.36 | 13.12 | 0
July | 4 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 4 | 4AM to 5AM | 55.8 | 52.7 | 50.4 | 54.4 | 21.82 | 0.0766 | 0.37 | 13.15 | 0
July | 4 | 5AM to 6AM | 56.3 | 53.2 | 50.9 | 55.5 | 22.12 | 0.0765 | 0.37 | 13.17 | 0
July | 4 | 6AM to 7AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
July | 4 | 7AM to 8AM | 59.4 | 55.3 | 52.5 | 58.9 | 23.4 | 0.0761 | 0.4 | 13.26 | 0
July | 4 | 8AM to 9AM | 61.7 | 56.8 | 53.6 | 61.4 | 24.35 | 0.0757 | 0.41 | 13.33 | 0
July | 4 | 9AM to 10AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
July | 4 | 10AM to 11AM | 65.3 | 59 | 55 | 64.7 | 25.75 | 0.0752 | 0.44 | 13.43 | 0
July | 4 | 11AM to 12PM | 66.7 | 59.8 | 55.6 | 66 | 26.31 | 0.0749 | 0.45 | 13.47 | 0
July | 4 | 12PM to 1PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
July | 4 | 1PM to 2PM | 67.3 | 60.1 | 55.8 | 66.5 | 26.51 | 0.0749 | 0.45 | 13.48 | 0
July | 4 | 2PM to 3PM | 66.7 | 59.8 | 55.6 | 66 | 26.31 | 0.0749 | 0.45 | 13.47 | 0
July | 4 | 3PM to 4PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
July | 4 | 4PM to 5PM | 64 | 58.4 | 54.9 | 64.3 | 25.38 | 0.0753 | 0.43 | 13.4 | 0
July | 4 | 5PM to 6PM | 62.1 | 57.5 | 54.5 | 63.5 | 24.76 | 0.0756 | 0.43 | 13.34 | 0
July | 4 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
July | 4 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
July | 4 | 8PM to 9PM | 60.1 | 56.3 | 53.8 | 61.8 | 24.02 | 0.0759 | 0.42 | 13.29 | 0
July | 4 | 9PM to 10PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
July | 4 | 10PM to 11PM | 58.5 | 55.2 | 52.9 | 59.7 | 23.31 | 0.0762 | 0.4 | 13.24 | 0
July | 4 | 11PM to 12AM | 56.7 | 54 | 52.2 | 58.2 | 22.62 | 0.0765 | 0.39 | 13.19 | 0
July | 5 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 5 | 1AM to 2AM | 54.3 | 52.6 | 51.3 | 56.2 | 21.75 | 0.0768 | 0.38 | 13.12 | 0
July | 5 | 2AM to 3AM | 53.8 | 52 | 50.7 | 55.1 | 21.45 | 0.0769 | 0.37 | 13.11 | 0
July | 5 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
July | 5 | 4AM to 5AM | 54 | 51.9 | 50.4 | 54.4 | 21.38 | 0.0769 | 0.37 | 13.11 | 0
July | 5 | 5AM to 6AM | 55 | 52.7 | 50.9 | 55.5 | 21.81 | 0.0767 | 0.37 | 13.14 | 0
July | 5 | 6AM to 7AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 5 | 7AM to 8AM | 57.9 | 54.3 | 51.6 | 57 | 22.75 | 0.0763 | 0.39 | 13.22 | 0
July | 5 | 8AM to 9AM | 60.1 | 55.1 | 51.6 | 57 | 23.28 | 0.076 | 0.39 | 13.27 | 0
July | 5 | 9AM to 10AM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
July | 5 | 10AM to 11AM | 62.4 | 56.2 | 51.8 | 57.4 | 23.91 | 0.0756 | 0.39 | 13.33 | 0
July | 5 | 11AM to 12PM | 62.6 | 56.3 | 52 | 57.8 | 24.01 | 0.0756 | 0.39 | 13.34 | 0
July | 5 | 12PM to 1PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
July | 5 | 1PM to 2PM | 62.6 | 56.4 | 52.2 | 58.2 | 24.07 | 0.0756 | 0.39 | 13.34 | 0
July | 5 | 2PM to 3PM | 62.4 | 56.3 | 52.2 | 58.2 | 24.03 | 0.0756 | 0.39 | 13.34 | 0
July | 5 | 3PM to 4PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
July | 5 | 4PM to 5PM | 61.3 | 55.5 | 51.4 | 56.6 | 23.52 | 0.0758 | 0.38 | 13.3 | 0
July | 5 | 5PM to 6PM | 60.8 | 55 | 50.9 | 55.5 | 23.22 | 0.0759 | 0.37 | 13.29 | 0
July | 5 | 6PM to 7PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
July | 5 | 7PM to 8PM | 59.7 | 54.1 | 50 | 53.6 | 22.67 | 0.076 | 0.36 | 13.25 | 0
July | 5 | 8PM to 9PM | 59.4 | 53.8 | 49.6 | 52.9 | 22.47 | 0.0761 | 0.36 | 13.24 | 0
July | 5 | 9PM to 10PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
July | 5 | 10PM to 11PM | 57.9 | 53 | 49.3 | 52.2 | 22 | 0.0763 | 0.35 | 13.2 | 0
July | 5 | 11PM to 12AM | 57 | 52.6 | 49.3 | 52.2 | 21.79 | 0.0764 | 0.35 | 13.18 | 0
July | 6 | 12AM to 1AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 6 | 1AM to 2AM | 55.6 | 51.9 | 49.1 | 51.8 | 21.38 | 0.0767 | 0.35 | 13.14 | 0
July | 6 | 2AM to 3AM | 55.4 | 51.7 | 48.7 | 51.1 | 21.23 | 0.0767 | 0.35 | 13.14 | 0
July | 6 | 3AM to 4AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
July | 6 | 4AM to 5AM | 55.9 | 51.9 | 48.7 | 51.1 | 21.36 | 0.0766 | 0.35 | 13.15 | 0
July | 6 | 5AM to 6AM | 57 | 52.7 | 49.5 | 52.6 | 21.84 | 0.0764 | 0.36 | 13.18 | 0
July | 6 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
July | 6 | 7AM to 8AM | 59.5 | 54.5 | 50.9 | 55.5 | 22.91 | 0.076 | 0.37 | 13.25 | 0
July | 6 | 8AM to 9AM | 61.3 | 55.4 | 51.3 | 56.2 | 23.46 | 0.0758 | 0.38 | 13.3 | 0
July | 6 | 9AM to 10AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
July | 6 | 10AM to 11AM | 64.9 | 57.1 | 51.8 | 57.4 | 24.52 | 0.0753 | 0.39 | 13.4 | 0
July | 6 | 11AM to 12PM | 67.1 | 58.1 | 52 | 57.8 | 25.11 | 0.0749 | 0.39 | 13.45 | 0
July | 6 | 12PM to 1PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
July | 6 | 1PM to 2PM | 68.4 | 58.8 | 52.5 | 58.9 | 25.6 | 0.0748 | 0.4 | 13.49 | 0
July | 6 | 2PM to 3PM | 67.6 | 58.7 | 52.9 | 59.7 | 25.55 | 0.0749 | 0.4 | 13.47 | 0
July | 6 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
July | 6 | 4PM to 5PM | 64.6 | 57.8 | 53.2 | 60.6 | 24.93 | 0.0753 | 0.41 | 13.4 | 0
July | 6 | 5PM to 6PM | 62.4 | 56.9 | 53.2 | 60.6 | 24.4 | 0.0756 | 0.41 | 13.34 | 0
July | 6 | 6PM to 7PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
July | 6 | 7PM to 8PM | 59.7 | 56 | 53.4 | 61 | 23.8 | 0.076 | 0.41 | 13.27 | 0
July | 6 | 8PM to 9PM | 59.4 | 55.8 | 53.4 | 61 | 23.72 | 0.076 | 0.41 | 13.27 | 0
July | 6 | 9PM to 10PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
July | 6 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 6 | 11PM to 12AM | 57 | 54.5 | 52.7 | 59.3 | 22.89 | 0.0764 | 0.4 | 13.2 | 0
July | 7 | 12AM to 1AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
July | 7 | 1AM to 2AM | 55.2 | 53.2 | 51.8 | 57.4 | 22.15 | 0.0767 | 0.39 | 13.15 | 0
July | 7 | 2AM to 3AM | 54.7 | 52.6 | 51.1 | 55.9 | 21.78 | 0.0768 | 0.38 | 13.13 | 0
July | 7 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 7 | 4AM to 5AM | 55 | 52.4 | 50.4 | 54.4 | 21.64 | 0.0767 | 0.37 | 13.14 | 0
July | 7 | 5AM to 6AM | 55.9 | 53 | 50.9 | 55.5 | 22.03 | 0.0766 | 0.37 | 13.16 | 0
July | 7 | 6AM to 7AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
July | 7 | 7AM to 8AM | 57.7 | 54.4 | 52 | 57.8 | 22.83 | 0.0763 | 0.39 | 13.21 | 0
July | 7 | 8AM to 9AM | 58.3 | 54.7 | 52.2 | 58.2 | 23.02 | 0.0762 | 0.39 | 13.23 | 0
July | 7 | 9AM to 10AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
July | 7 | 10AM to 11AM | 61 | 56.1 | 52.7 | 59.3 | 23.86 | 0.0758 | 0.4 | 13.3 | 0
July | 7 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
July | 7 | 12PM to 1PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
July | 7 | 1PM to 2PM | 65.3 | 58 | 53.2 | 60.6 | 25.1 | 0.0752 | 0.41 | 13.42 | 0
July | 7 | 2PM to 3PM | 65.7 | 58.2 | 53.2 | 60.6 | 25.19 | 0.0751 | 0.41 | 13.43 | 0
July | 7 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 7 | 4PM to 5PM | 64 | 57.7 | 53.6 | 61.4 | 24.92 | 0.0754 | 0.41 | 13.39 | 0
July | 7 | 5PM to 6PM | 62.1 | 57.1 | 53.8 | 61.8 | 24.5 | 0.0756 | 0.42 | 13.34 | 0
July | 7 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
July | 7 | 7PM to 8PM | 60.1 | 56.6 | 54.3 | 63 | 24.21 | 0.0759 | 0.43 | 13.29 | 0
July | 7 | 8PM to 9PM | 60.1 | 56.6 | 54.3 | 63 | 24.21 | 0.0759 | 0.43 | 13.29 | 0
July | 7 | 9PM to 10PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
July | 7 | 10PM to 11PM | 59.4 | 56.2 | 54.1 | 62.6 | 23.97 | 0.076 | 0.42 | 13.27 | 0
July | 7 | 11PM to 12AM | 58.6 | 55.7 | 53.8 | 61.8 | 23.67 | 0.0761 | 0.42 | 13.25 | 0
July | 8 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 8 | 1AM to 2AM | 57.6 | 55.2 | 53.6 | 61.4 | 23.34 | 0.0763 | 0.41 | 13.22 | 0
July | 8 | 2AM to 3AM | 57.4 | 55 | 53.4 | 61 | 23.23 | 0.0763 | 0.41 | 13.22 | 0
July | 8 | 3AM to 4AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
July | 8 | 4AM to 5AM | 57.4 | 55 | 53.4 | 61 | 23.23 | 0.0763 | 0.41 | 13.22 | 0
July | 8 | 5AM to 6AM | 57.6 | 55.3 | 53.8 | 61.8 | 23.4 | 0.0763 | 0.42 | 13.22 | 0
July | 8 | 6AM to 7AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
July | 8 | 7AM to 8AM | 59.4 | 56.4 | 54.5 | 63.5 | 24.1 | 0.076 | 0.43 | 13.27 | 0
July | 8 | 8AM to 9AM | 60.6 | 56.9 | 54.5 | 63.5 | 24.41 | 0.0758 | 0.43 | 13.31 | 0
July | 8 | 9AM to 10AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
July | 8 | 10AM to 11AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0753 | 0.44 | 13.41 | 0
July | 8 | 11AM to 12PM | 66.7 | 60.2 | 56.3 | 67.8 | 26.58 | 0.0749 | 0.46 | 13.48 | 0
July | 8 | 12PM to 1PM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
July | 8 | 1PM to 2PM | 69.1 | 61.6 | 57.2 | 70.1 | 27.51 | 0.0746 | 0.47 | 13.54 | 0
July | 8 | 2PM to 3PM | 69.1 | 61.6 | 57.2 | 70.1 | 27.51 | 0.0746 | 0.47 | 13.54 | 0
July | 8 | 3PM to 4PM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
July | 8 | 4PM to 5PM | 67.6 | 60.9 | 56.8 | 69.2 | 27.01 | 0.0748 | 0.47 | 13.5 | 0
July | 8 | 5PM to 6PM | 66.4 | 60.2 | 56.5 | 68.3 | 26.56 | 0.075 | 0.46 | 13.47 | 0
July | 8 | 6PM to 7PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
July | 8 | 7PM to 8PM | 63.3 | 58.4 | 55.2 | 65.2 | 25.34 | 0.0754 | 0.44 | 13.38 | 0
July | 8 | 8PM to 9PM | 61.7 | 57.2 | 54.3 | 63 | 24.61 | 0.0757 | 0.43 | 13.33 | 0
July | 8 | 9PM to 10PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
July | 8 | 10PM to 11PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
July | 8 | 11PM to 12AM | 58.1 | 54.9 | 52.7 | 59.3 | 23.16 | 0.0762 | 0.4 | 13.23 | 0
July | 9 | 12AM to 1AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
July | 9 | 1AM to 2AM | 56.7 | 54 | 52.2 | 58.2 | 22.62 | 0.0765 | 0.39 | 13.19 | 0
July | 9 | 2AM to 3AM | 56.3 | 53.7 | 51.8 | 57.4 | 22.41 | 0.0765 | 0.39 | 13.18 | 0
July | 9 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 9 | 4AM to 5AM | 56.3 | 53.5 | 51.4 | 56.6 | 22.3 | 0.0765 | 0.38 | 13.17 | 0
July | 9 | 5AM to 6AM | 56.7 | 53.8 | 51.8 | 57.4 | 22.5 | 0.0765 | 0.39 | 13.19 | 0
July | 9 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
July | 9 | 7AM to 8AM | 58.3 | 55.1 | 52.9 | 59.7 | 23.26 | 0.0762 | 0.4 | 13.23 | 0
July | 9 | 8AM to 9AM | 59.7 | 55.9 | 53.2 | 60.6 | 23.74 | 0.076 | 0.41 | 13.27 | 0
July | 9 | 9AM to 10AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
July | 9 | 10AM to 11AM | 62.6 | 56.9 | 53.1 | 60.1 | 24.38 | 0.0756 | 0.41 | 13.35 | 0
July | 9 | 11AM to 12PM | 64.4 | 57.4 | 52.7 | 59.3 | 24.69 | 0.0753 | 0.4 | 13.39 | 0
July | 9 | 12PM to 1PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
July | 9 | 1PM to 2PM | 66 | 57.6 | 51.8 | 57.4 | 24.78 | 0.0751 | 0.39 | 13.43 | 0
July | 9 | 2PM to 3PM | 66 | 57.5 | 51.6 | 57 | 24.72 | 0.0751 | 0.39 | 13.42 | 0
July | 9 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
July | 9 | 4PM to 5PM | 64.4 | 56.5 | 50.9 | 55.5 | 24.09 | 0.0753 | 0.37 | 13.38 | 0
July | 9 | 5PM to 6PM | 62.6 | 55.6 | 50.5 | 54.7 | 23.54 | 0.0756 | 0.37 | 13.33 | 0
July | 9 | 6PM to 7PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
July | 9 | 7PM to 8PM | 59.9 | 54 | 49.6 | 52.9 | 22.6 | 0.076 | 0.36 | 13.26 | 0
July | 9 | 8PM to 9PM | 59 | 53.4 | 49.1 | 51.8 | 22.21 | 0.0761 | 0.35 | 13.23 | 0
July | 9 | 9PM to 10PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
July | 9 | 10PM to 11PM | 57.2 | 52.3 | 48.4 | 50.4 | 21.56 | 0.0764 | 0.34 | 13.18 | 0
July | 9 | 11PM to 12AM | 56.7 | 52 | 48.4 | 50.4 | 21.43 | 0.0765 | 0.34 | 13.17 | 0
July | 10 | 12AM to 1AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
July | 10 | 1AM to 2AM | 55.2 | 51.5 | 48.6 | 50.8 | 21.13 | 0.0767 | 0.34 | 13.13 | 0
July | 10 | 2AM to 3AM | 54.7 | 51.2 | 48.4 | 50.4 | 20.94 | 0.0768 | 0.34 | 13.11 | 0
July | 10 | 3AM to 4AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
July | 10 | 4AM to 5AM | 55.6 | 51.4 | 48 | 49.8 | 21.06 | 0.0767 | 0.34 | 13.14 | 0
July | 10 | 5AM to 6AM | 57.4 | 52.2 | 48.2 | 50.1 | 21.55 | 0.0764 | 0.34 | 13.18 | 0
July | 10 | 6AM to 7AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
July | 10 | 7AM to 8AM | 62.4 | 54.9 | 49.3 | 52.2 | 23.1 | 0.0756 | 0.35 | 13.32 | 0
July | 10 | 8AM to 9AM | 65.7 | 56.4 | 49.8 | 53.3 | 24.05 | 0.0752 | 0.36 | 13.4 | 0
July | 10 | 9AM to 10AM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
July | 10 | 10AM to 11AM | 68.4 | 57.9 | 50.7 | 55.1 | 25 | 0.0748 | 0.37 | 13.48 | 0
July | 10 | 11AM to 12PM | 67.6 | 57.8 | 51.1 | 55.9 | 24.94 | 0.0749 | 0.38 | 13.46 | 0
July | 10 | 12PM to 1PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
July | 10 | 1PM to 2PM | 66.6 | 57.5 | 51.3 | 56.2 | 24.74 | 0.075 | 0.38 | 13.44 | 0
July | 10 | 2PM to 3PM | 66.4 | 57.4 | 51.3 | 56.2 | 24.69 | 0.0751 | 0.38 | 13.43 | 0
July | 10 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
July | 10 | 4PM to 5PM | 64.9 | 56.3 | 50.2 | 54 | 23.99 | 0.0753 | 0.37 | 13.39 | 0
July | 10 | 5PM to 6PM | 64 | 55.5 | 49.3 | 52.2 | 23.49 | 0.0754 | 0.35 | 13.36 | 0
July | 10 | 6PM to 7PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
July | 10 | 7PM to 8PM | 62.1 | 54.3 | 48.4 | 50.4 | 22.74 | 0.0757 | 0.34 | 13.3 | 0
July | 10 | 8PM to 9PM | 61 | 53.8 | 48.4 | 50.4 | 22.48 | 0.0759 | 0.34 | 13.28 | 0
July | 10 | 9PM to 10PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
July | 10 | 10PM to 11PM | 59.4 | 53.3 | 48.7 | 51.1 | 22.19 | 0.0761 | 0.35 | 13.24 | 0
July | 10 | 11PM to 12AM | 58.6 | 53.2 | 49.1 | 51.8 | 22.12 | 0.0762 | 0.35 | 13.22 | 0
July | 11 | 12AM to 1AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
July | 11 | 1AM to 2AM | 57.2 | 53 | 49.8 | 53.3 | 22 | 0.0764 | 0.36 | 13.19 | 0
July | 11 | 2AM to 3AM | 56.7 | 52.9 | 50 | 53.6 | 21.92 | 0.0765 | 0.36 | 13.17 | 0
July | 11 | 3AM to 4AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
July | 11 | 4AM to 5AM | 56.7 | 53.4 | 51.1 | 55.9 | 22.27 | 0.0765 | 0.38 | 13.18 | 0
July | 11 | 5AM to 6AM | 57.2 | 54.3 | 52.2 | 58.2 | 22.75 | 0.0764 | 0.39 | 13.2 | 0
July | 11 | 6AM to 7AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 11 | 7AM to 8AM | 60.3 | 56.8 | 54.5 | 63.5 | 24.32 | 0.0759 | 0.43 | 13.3 | 0
July | 11 | 8AM to 9AM | 62.6 | 58.3 | 55.6 | 66 | 25.3 | 0.0755 | 0.45 | 13.36 | 0
July | 11 | 9AM to 10AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
July | 11 | 10AM to 11AM | 66 | 60.2 | 56.7 | 68.7 | 26.55 | 0.075 | 0.46 | 13.46 | 0
July | 11 | 11AM to 12PM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
July | 11 | 12PM to 1PM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
July | 11 | 1PM to 2PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.51 | 0
July | 11 | 2PM to 3PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.51 | 0
July | 11 | 3PM to 4PM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
July | 11 | 4PM to 5PM | 65.7 | 59.7 | 56.1 | 67.4 | 26.25 | 0.0751 | 0.45 | 13.45 | 0
July | 11 | 5PM to 6PM | 63.3 | 58.4 | 55.2 | 65.2 | 25.34 | 0.0754 | 0.44 | 13.38 | 0
July | 11 | 6PM to 7PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
July | 11 | 7PM to 8PM | 59.7 | 56.1 | 53.6 | 61.4 | 23.87 | 0.076 | 0.41 | 13.28 | 0
July | 11 | 8PM to 9PM | 58.3 | 55.2 | 53.1 | 60.1 | 23.33 | 0.0762 | 0.41 | 13.24 | 0
July | 11 | 9PM to 10PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
July | 11 | 10PM to 11PM | 57 | 54.5 | 52.7 | 59.3 | 22.89 | 0.0764 | 0.4 | 13.2 | 0
July | 11 | 11PM to 12AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
July | 12 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
July | 12 | 1AM to 2AM | 57.4 | 55.1 | 53.6 | 61.4 | 23.3 | 0.0763 | 0.41 | 13.22 | 0
July | 12 | 2AM to 3AM | 57.6 | 55.1 | 53.4 | 61 | 23.28 | 0.0763 | 0.41 | 13.22 | 0
July | 12 | 3AM to 4AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 12 | 4AM to 5AM | 57.6 | 54.7 | 52.7 | 59.3 | 23.03 | 0.0763 | 0.4 | 13.21 | 0
July | 12 | 5AM to 6AM | 57.4 | 54.5 | 52.5 | 58.9 | 22.92 | 0.0763 | 0.4 | 13.21 | 0
July | 12 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
July | 12 | 7AM to 8AM | 59.4 | 55.7 | 53.2 | 60.6 | 23.65 | 0.076 | 0.41 | 13.26 | 0
July | 12 | 8AM to 9AM | 61.7 | 56.9 | 53.8 | 61.8 | 24.41 | 0.0757 | 0.42 | 13.33 | 0
July | 12 | 9AM to 10AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
July | 12 | 10AM to 11AM | 69.4 | 60.7 | 55.4 | 65.6 | 26.9 | 0.0746 | 0.44 | 13.54 | 0
July | 12 | 11AM to 12PM | 74.7 | 63 | 56.3 | 67.8 | 28.52 | 0.0738 | 0.46 | 13.68 | 0
July | 12 | 12PM to 1PM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
July | 12 | 1PM to 2PM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
July | 12 | 2PM to 3PM | 74.1 | 61.9 | 54.5 | 63.5 | 27.7 | 0.0739 | 0.43 | 13.65 | 0
July | 12 | 3PM to 4PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
July | 12 | 4PM to 5PM | 68 | 58.5 | 52.2 | 58.2 | 25.39 | 0.0748 | 0.39 | 13.48 | 0
July | 12 | 5PM to 6PM | 65.1 | 56.9 | 51.3 | 56.2 | 24.38 | 0.0752 | 0.38 | 13.4 | 0
July | 12 | 6PM to 7PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
July | 12 | 7PM to 8PM | 60.6 | 54.5 | 50 | 53.6 | 22.88 | 0.0759 | 0.36 | 13.28 | 0
July | 12 | 8PM to 9PM | 59.4 | 53.8 | 49.6 | 52.9 | 22.47 | 0.0761 | 0.36 | 13.24 | 0
July | 12 | 9PM to 10PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
July | 12 | 10PM to 11PM | 57 | 52.5 | 49.1 | 51.8 | 21.73 | 0.0764 | 0.35 | 13.18 | 0
July | 12 | 11PM to 12AM | 55.9 | 51.9 | 48.7 | 51.1 | 21.36 | 0.0766 | 0.35 | 13.15 | 0
July | 13 | 12AM to 1AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
July | 13 | 1AM to 2AM | 54.7 | 51.1 | 48.2 | 50.1 | 20.89 | 0.0768 | 0.34 | 13.11 | 0
July | 13 | 2AM to 3AM | 54.3 | 50.6 | 47.7 | 49.1 | 20.65 | 0.0769 | 0.33 | 13.1 | 0
July | 13 | 3AM to 4AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
July | 13 | 4AM to 5AM | 55.9 | 51.3 | 47.7 | 49.1 | 21.04 | 0.0766 | 0.33 | 13.14 | 0
July | 13 | 5AM to 6AM | 58.1 | 52.6 | 48.4 | 50.4 | 21.78 | 0.0763 | 0.34 | 13.2 | 0
July | 13 | 6AM to 7AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
July | 13 | 7AM to 8AM | 62.4 | 55.3 | 50.2 | 54 | 23.38 | 0.0756 | 0.37 | 13.32 | 0
July | 13 | 8AM to 9AM | 64.6 | 56.5 | 50.9 | 55.5 | 24.14 | 0.0753 | 0.37 | 13.38 | 0
July | 13 | 9AM to 10AM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
July | 13 | 10AM to 11AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
July | 13 | 11AM to 12PM | 68.9 | 58.7 | 52 | 57.8 | 25.55 | 0.0747 | 0.39 | 13.5 | 0
July | 13 | 12PM to 1PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
July | 13 | 1PM to 2PM | 68.7 | 58.6 | 51.8 | 57.4 | 25.44 | 0.0747 | 0.39 | 13.49 | 0
July | 13 | 2PM to 3PM | 67.3 | 57.9 | 51.6 | 57 | 25.03 | 0.0749 | 0.39 | 13.46 | 0
July | 13 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
July | 13 | 4PM to 5PM | 64 | 56.3 | 50.9 | 55.5 | 24 | 0.0754 | 0.37 | 13.37 | 0
July | 13 | 5PM to 6PM | 62.1 | 55.4 | 50.5 | 54.7 | 23.41 | 0.0757 | 0.37 | 13.32 | 0
July | 13 | 6PM to 7PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
July | 13 | 7PM to 8PM | 58.6 | 53.7 | 50 | 53.6 | 22.4 | 0.0762 | 0.36 | 13.23 | 0
July | 13 | 8PM to 9PM | 57.4 | 53 | 49.6 | 52.9 | 21.98 | 0.0764 | 0.36 | 13.19 | 0
July | 13 | 9PM to 10PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 13 | 10PM to 11PM | 55.6 | 52 | 49.3 | 52.2 | 21.43 | 0.0767 | 0.35 | 13.14 | 0
July | 13 | 11PM to 12AM | 55.4 | 52 | 49.3 | 52.2 | 21.39 | 0.0767 | 0.35 | 13.14 | 0
July | 14 | 12AM to 1AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
July | 14 | 1AM to 2AM | 54.3 | 51.4 | 49.1 | 51.8 | 21.07 | 0.0768 | 0.35 | 13.11 | 0
July | 14 | 2AM to 3AM | 53.8 | 51 | 48.7 | 51.1 | 20.83 | 0.0769 | 0.35 | 13.09 | 0
July | 14 | 3AM to 4AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
July | 14 | 4AM to 5AM | 55 | 51.5 | 48.7 | 51.1 | 21.14 | 0.0767 | 0.35 | 13.13 | 0
July | 14 | 5AM to 6AM | 57 | 52.7 | 49.5 | 52.6 | 21.84 | 0.0764 | 0.36 | 13.18 | 0
July | 14 | 6AM to 7AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
July | 14 | 7AM to 8AM | 61.7 | 55.6 | 51.3 | 56.2 | 23.55 | 0.0757 | 0.38 | 13.31 | 0
July | 14 | 8AM to 9AM | 64.2 | 56.9 | 51.8 | 57.4 | 24.34 | 0.0754 | 0.39 | 13.38 | 0
July | 14 | 9AM to 10AM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
July | 14 | 10AM to 11AM | 68.9 | 59.3 | 53.1 | 60.1 | 25.92 | 0.0747 | 0.41 | 13.51 | 0
July | 14 | 11AM to 12PM | 71.1 | 60.4 | 53.6 | 61.4 | 26.63 | 0.0744 | 0.41 | 13.57 | 0
July | 14 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
July | 14 | 1PM to 2PM | 72.7 | 61 | 53.8 | 61.8 | 27.09 | 0.0741 | 0.42 | 13.61 | 0
July | 14 | 2PM to 3PM | 72.3 | 60.8 | 53.6 | 61.4 | 26.94 | 0.0742 | 0.41 | 13.6 | 0
July | 14 | 3PM to 4PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
July | 14 | 4PM to 5PM | 68.9 | 58.8 | 52.2 | 58.2 | 25.61 | 0.0747 | 0.39 | 13.5 | 0
July | 14 | 5PM to 6PM | 66 | 57.3 | 51.3 | 56.2 | 24.6 | 0.0751 | 0.38 | 13.42 | 0
July | 14 | 6PM to 7PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
July | 14 | 7PM to 8PM | 61 | 54.8 | 50.4 | 54.4 | 23.09 | 0.0758 | 0.37 | 13.29 | 0
July | 14 | 8PM to 9PM | 59 | 54 | 50.4 | 54.4 | 22.6 | 0.0761 | 0.37 | 13.24 | 0
July | 14 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 14 | 10PM to 11PM | 56.7 | 53.1 | 50.4 | 54.4 | 22.03 | 0.0765 | 0.37 | 13.18 | 0
July | 14 | 11PM to 12AM | 56.3 | 52.9 | 50.4 | 54.4 | 21.95 | 0.0765 | 0.37 | 13.17 | 0
July | 15 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
July | 15 | 1AM to 2AM | 55.9 | 52.7 | 50.2 | 54 | 21.8 | 0.0766 | 0.37 | 13.16 | 0
July | 15 | 2AM to 3AM | 55.9 | 52.4 | 49.6 | 52.9 | 21.63 | 0.0766 | 0.36 | 13.15 | 0
July | 15 | 3AM to 4AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 15 | 4AM to 5AM | 56.7 | 52.5 | 49.3 | 52.2 | 21.7 | 0.0765 | 0.35 | 13.17 | 0
July | 15 | 5AM to 6AM | 57.2 | 53 | 49.8 | 53.3 | 22 | 0.0764 | 0.36 | 13.19 | 0
July | 15 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
July | 15 | 7AM to 8AM | 59.5 | 54.7 | 51.3 | 56.2 | 23.03 | 0.076 | 0.38 | 13.26 | 0
July | 15 | 8AM to 9AM | 61.3 | 55.7 | 51.8 | 57.4 | 23.64 | 0.0758 | 0.39 | 13.31 | 0
July | 15 | 9AM to 10AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
July | 15 | 10AM to 11AM | 65.7 | 58.1 | 53.1 | 60.1 | 25.13 | 0.0751 | 0.41 | 13.42 | 0
July | 15 | 11AM to 12PM | 68.4 | 59.4 | 53.6 | 61.4 | 25.97 | 0.0747 | 0.41 | 13.5 | 0
July | 15 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
July | 15 | 1PM to 2PM | 69.6 | 59.9 | 53.8 | 61.8 | 26.35 | 0.0746 | 0.42 | 13.53 | 0
July | 15 | 2PM to 3PM | 68.4 | 59.4 | 53.6 | 61.4 | 25.97 | 0.0747 | 0.41 | 13.5 | 0
July | 15 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
July | 15 | 4PM to 5PM | 64.9 | 57.5 | 52.5 | 58.9 | 24.76 | 0.0752 | 0.4 | 13.4 | 0
July | 15 | 5PM to 6PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
July | 15 | 6PM to 7PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
July | 15 | 7PM to 8PM | 59.9 | 54.8 | 51.1 | 55.9 | 23.05 | 0.076 | 0.38 | 13.26 | 0
July | 15 | 8PM to 9PM | 59 | 54.2 | 50.7 | 55.1 | 22.72 | 0.0761 | 0.37 | 13.24 | 0
July | 15 | 9PM to 10PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
July | 15 | 10PM to 11PM | 57.2 | 53.3 | 50.4 | 54.4 | 22.17 | 0.0764 | 0.37 | 13.19 | 0
July | 15 | 11PM to 12AM | 56.7 | 53.1 | 50.4 | 54.4 | 22.03 | 0.0765 | 0.37 | 13.18 | 0
July | 16 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
July | 16 | 1AM to 2AM | 56.3 | 53 | 50.5 | 54.7 | 22 | 0.0765 | 0.37 | 13.17 | 0
July | 16 | 2AM to 3AM | 56.7 | 53.1 | 50.4 | 54.4 | 22.03 | 0.0765 | 0.37 | 13.18 | 0
July | 16 | 3AM to 4AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 16 | 4AM to 5AM | 58.3 | 53.5 | 50 | 53.6 | 22.31 | 0.0762 | 0.36 | 13.22 | 0
July | 16 | 5AM to 6AM | 59.7 | 54.2 | 50.2 | 54 | 22.72 | 0.076 | 0.37 | 13.25 | 0
July | 16 | 6AM to 7AM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
July | 16 | 7AM to 8AM | 62.6 | 55.9 | 51.3 | 56.2 | 23.77 | 0.0756 | 0.38 | 13.33 | 0
July | 16 | 8AM to 9AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.38 | 0
July | 16 | 9AM to 10AM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
July | 16 | 10AM to 11AM | 66.7 | 58.5 | 53.1 | 60.1 | 25.39 | 0.075 | 0.41 | 13.45 | 0
July | 16 | 11AM to 12PM | 67.3 | 59 | 53.6 | 61.4 | 25.71 | 0.0749 | 0.41 | 13.47 | 0
July | 16 | 12PM to 1PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
July | 16 | 1PM to 2PM | 67.3 | 59.1 | 53.8 | 61.8 | 25.78 | 0.0749 | 0.42 | 13.47 | 0
July | 16 | 2PM to 3PM | 66.7 | 58.8 | 53.6 | 61.4 | 25.58 | 0.075 | 0.41 | 13.46 | 0
July | 16 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 16 | 4PM to 5PM | 64.4 | 57.5 | 52.9 | 59.7 | 24.76 | 0.0753 | 0.4 | 13.39 | 0
July | 16 | 5PM to 6PM | 62.6 | 56.6 | 52.5 | 58.9 | 24.19 | 0.0756 | 0.4 | 13.34 | 0
July | 16 | 6PM to 7PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
July | 16 | 7PM to 8PM | 60.6 | 55.7 | 52.3 | 58.6 | 23.65 | 0.0759 | 0.4 | 13.29 | 0
July | 16 | 8PM to 9PM | 60.4 | 55.7 | 52.3 | 58.6 | 23.61 | 0.0759 | 0.4 | 13.29 | 0
July | 16 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 16 | 10PM to 11PM | 59.7 | 55.3 | 52.2 | 58.2 | 23.37 | 0.076 | 0.39 | 13.27 | 0
July | 16 | 11PM to 12AM | 59.4 | 54.9 | 51.8 | 57.4 | 23.16 | 0.0761 | 0.39 | 13.26 | 0
July | 17 | 12AM to 1AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
July | 17 | 1AM to 2AM | 59 | 54.8 | 51.8 | 57.4 | 23.07 | 0.0761 | 0.39 | 13.25 | 0
July | 17 | 2AM to 3AM | 59 | 55 | 52.2 | 58.2 | 23.19 | 0.0761 | 0.39 | 13.25 | 0
July | 17 | 3AM to 4AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
July | 17 | 4AM to 5AM | 59.4 | 55 | 52 | 57.8 | 23.22 | 0.0761 | 0.39 | 13.26 | 0
July | 17 | 5AM to 6AM | 59.7 | 55.3 | 52.2 | 58.2 | 23.37 | 0.076 | 0.39 | 13.27 | 0
July | 17 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 17 | 7AM to 8AM | 60.8 | 55.9 | 52.5 | 58.9 | 23.75 | 0.0758 | 0.4 | 13.3 | 0
July | 17 | 8AM to 9AM | 61.3 | 56.1 | 52.5 | 58.9 | 23.89 | 0.0758 | 0.4 | 13.31 | 0
July | 17 | 9AM to 10AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
July | 17 | 10AM to 11AM | 63.3 | 57 | 52.7 | 59.3 | 24.43 | 0.0755 | 0.4 | 13.36 | 0
July | 17 | 11AM to 12PM | 64.8 | 57.7 | 53.1 | 60.1 | 24.91 | 0.0753 | 0.41 | 13.4 | 0
July | 17 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 17 | 1PM to 2PM | 66.7 | 58.8 | 53.6 | 61.4 | 25.58 | 0.075 | 0.41 | 13.46 | 0
July | 17 | 2PM to 3PM | 67.3 | 59.1 | 53.8 | 61.8 | 25.78 | 0.0749 | 0.42 | 13.47 | 0
July | 17 | 3PM to 4PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
July | 17 | 4PM to 5PM | 65.3 | 58 | 53.2 | 60.6 | 25.1 | 0.0752 | 0.41 | 13.42 | 0
July | 17 | 5PM to 6PM | 62.8 | 56.5 | 52.2 | 58.2 | 24.11 | 0.0756 | 0.39 | 13.34 | 0
July | 17 | 6PM to 7PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
July | 17 | 7PM to 8PM | 59.4 | 54.8 | 51.6 | 57 | 23.1 | 0.0761 | 0.39 | 13.25 | 0
July | 17 | 8PM to 9PM | 58.6 | 54.7 | 52 | 57.8 | 23.05 | 0.0762 | 0.39 | 13.24 | 0
July | 17 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
July | 17 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.63 | 0.0764 | 0.39 | 13.2 | 0
July | 17 | 11PM to 12AM | 56.7 | 53.4 | 51.1 | 55.9 | 22.27 | 0.0765 | 0.38 | 13.18 | 0
July | 18 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
July | 18 | 1AM to 2AM | 55.6 | 52.7 | 50.5 | 54.7 | 21.83 | 0.0766 | 0.37 | 13.15 | 0
July | 18 | 2AM to 3AM | 55.4 | 52.5 | 50.4 | 54.4 | 21.73 | 0.0767 | 0.37 | 13.14 | 0
July | 18 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 18 | 4AM to 5AM | 54.7 | 51.8 | 49.6 | 52.9 | 21.33 | 0.0768 | 0.36 | 13.12 | 0
July | 18 | 5AM to 6AM | 54.3 | 51.6 | 49.5 | 52.6 | 21.18 | 0.0768 | 0.36 | 13.11 | 0
July | 18 | 6AM to 7AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
July | 18 | 7AM to 8AM | 54.7 | 51.7 | 49.5 | 52.6 | 21.27 | 0.0768 | 0.36 | 13.12 | 0
July | 18 | 8AM to 9AM | 55.2 | 52 | 49.5 | 52.6 | 21.4 | 0.0767 | 0.36 | 13.13 | 0
July | 18 | 9AM to 10AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 18 | 10AM to 11AM | 57.9 | 53.2 | 49.6 | 52.9 | 22.12 | 0.0763 | 0.36 | 13.2 | 0
July | 18 | 11AM to 12PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
July | 18 | 12PM to 1PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
July | 18 | 1PM to 2PM | 61.7 | 54.8 | 49.8 | 53.3 | 23.09 | 0.0757 | 0.36 | 13.3 | 0
July | 18 | 2PM to 3PM | 61.3 | 54.5 | 49.5 | 52.6 | 22.89 | 0.0758 | 0.36 | 13.29 | 0
July | 18 | 3PM to 4PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
July | 18 | 4PM to 5PM | 59.9 | 53.7 | 49.1 | 51.8 | 22.43 | 0.076 | 0.35 | 13.25 | 0
July | 18 | 5PM to 6PM | 59 | 53.4 | 49.1 | 51.8 | 22.21 | 0.0761 | 0.35 | 13.23 | 0
July | 18 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
July | 18 | 7PM to 8PM | 57.2 | 52.5 | 48.9 | 51.5 | 21.72 | 0.0764 | 0.35 | 13.18 | 0
July | 18 | 8PM to 9PM | 56.7 | 52.2 | 48.7 | 51.1 | 21.53 | 0.0765 | 0.35 | 13.17 | 0
July | 18 | 9PM to 10PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
July | 18 | 10PM to 11PM | 55.6 | 51.7 | 48.7 | 51.1 | 21.27 | 0.0767 | 0.35 | 13.14 | 0
July | 18 | 11PM to 12AM | 55.4 | 51.9 | 49.1 | 51.8 | 21.34 | 0.0767 | 0.35 | 13.14 | 0
July | 19 | 12AM to 1AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
July | 19 | 1AM to 2AM | 55 | 51.9 | 49.5 | 52.6 | 21.36 | 0.0767 | 0.36 | 13.13 | 0
July | 19 | 2AM to 3AM | 55 | 51.8 | 49.3 | 52.2 | 21.3 | 0.0767 | 0.35 | 13.13 | 0
July | 19 | 3AM to 4AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
July | 19 | 4AM to 5AM | 55 | 51.5 | 48.7 | 51.1 | 21.14 | 0.0767 | 0.35 | 13.13 | 0
July | 19 | 5AM to 6AM | 55 | 51.4 | 48.6 | 50.8 | 21.09 | 0.0767 | 0.34 | 13.13 | 0
July | 19 | 6AM to 7AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
July | 19 | 7AM to 8AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
July | 19 | 8AM to 9AM | 59 | 53.4 | 49.1 | 51.8 | 22.21 | 0.0761 | 0.35 | 13.23 | 0
July | 19 | 9AM to 10AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
July | 19 | 10AM to 11AM | 62.1 | 54.7 | 49.3 | 52.2 | 23.01 | 0.0757 | 0.35 | 13.31 | 0
July | 19 | 11AM to 12PM | 63 | 55.1 | 49.3 | 52.2 | 23.23 | 0.0756 | 0.35 | 13.33 | 0
July | 19 | 12PM to 1PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
July | 19 | 1PM to 2PM | 63.7 | 55.5 | 49.5 | 52.6 | 23.46 | 0.0755 | 0.36 | 13.35 | 0
July | 19 | 2PM to 3PM | 63.3 | 55.5 | 49.8 | 53.3 | 23.49 | 0.0755 | 0.36 | 13.34 | 0
July | 19 | 3PM to 4PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
July | 19 | 4PM to 5PM | 62.1 | 55 | 49.8 | 53.3 | 23.18 | 0.0757 | 0.36 | 13.31 | 0
July | 19 | 5PM to 6PM | 61 | 54.4 | 49.5 | 52.6 | 22.8 | 0.0759 | 0.36 | 13.28 | 0
July | 19 | 6PM to 7PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
July | 19 | 7PM to 8PM | 58.6 | 53.3 | 49.3 | 52.2 | 22.18 | 0.0762 | 0.35 | 13.22 | 0
July | 19 | 8PM to 9PM | 57.4 | 52.8 | 49.3 | 52.2 | 21.87 | 0.0764 | 0.35 | 13.19 | 0
July | 19 | 9PM to 10PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 19 | 10PM to 11PM | 55.6 | 52.2 | 49.6 | 52.9 | 21.55 | 0.0766 | 0.36 | 13.15 | 0
July | 19 | 11PM to 12AM | 55.4 | 52.3 | 50 | 53.6 | 21.61 | 0.0767 | 0.36 | 13.14 | 0
July | 20 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 20 | 1AM to 2AM | 54.7 | 52.3 | 50.5 | 54.7 | 21.61 | 0.0768 | 0.37 | 13.13 | 0
July | 20 | 2AM to 3AM | 54.3 | 52.1 | 50.4 | 54.4 | 21.46 | 0.0768 | 0.37 | 13.12 | 0
July | 20 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 20 | 4AM to 5AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 20 | 5AM to 6AM | 55.9 | 52.7 | 50.2 | 54 | 21.8 | 0.0766 | 0.37 | 13.16 | 0
July | 20 | 6AM to 7AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 20 | 7AM to 8AM | 58.6 | 54.4 | 51.3 | 56.2 | 22.81 | 0.0762 | 0.38 | 13.23 | 0
July | 20 | 8AM to 9AM | 60.4 | 55.4 | 51.8 | 57.4 | 23.42 | 0.0759 | 0.39 | 13.28 | 0
July | 20 | 9AM to 10AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
July | 20 | 10AM to 11AM | 63.3 | 57 | 52.7 | 59.3 | 24.43 | 0.0755 | 0.4 | 13.36 | 0
July | 20 | 11AM to 12PM | 64.8 | 57.7 | 53.1 | 60.1 | 24.91 | 0.0753 | 0.41 | 13.4 | 0
July | 20 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 20 | 1PM to 2PM | 65.7 | 58.2 | 53.2 | 60.6 | 25.19 | 0.0751 | 0.41 | 13.43 | 0
July | 20 | 2PM to 3PM | 65.3 | 58 | 53.2 | 60.6 | 25.1 | 0.0752 | 0.41 | 13.42 | 0
July | 20 | 3PM to 4PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
July | 20 | 4PM to 5PM | 63.3 | 56.5 | 51.8 | 57.4 | 24.13 | 0.0755 | 0.39 | 13.36 | 0
July | 20 | 5PM to 6PM | 61.7 | 55.2 | 50.5 | 54.7 | 23.32 | 0.0757 | 0.37 | 13.31 | 0
July | 20 | 6PM to 7PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
July | 20 | 7PM to 8PM | 59 | 53.1 | 48.6 | 50.8 | 22.05 | 0.0762 | 0.34 | 13.23 | 0
July | 20 | 8PM to 9PM | 58.1 | 52.5 | 48 | 49.8 | 21.67 | 0.0763 | 0.34 | 13.2 | 0
July | 20 | 9PM to 10PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
July | 20 | 10PM to 11PM | 55.9 | 51.1 | 47.1 | 48.1 | 20.89 | 0.0766 | 0.33 | 13.14 | 0
July | 20 | 11PM to 12AM | 55 | 50.5 | 46.8 | 47.4 | 20.56 | 0.0768 | 0.32 | 13.12 | 0
July | 21 | 12AM to 1AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
July | 21 | 1AM to 2AM | 54.7 | 50.1 | 46.2 | 46.5 | 20.33 | 0.0768 | 0.31 | 13.1 | 0
July | 21 | 2AM to 3AM | 55.2 | 50.1 | 45.7 | 45.5 | 20.31 | 0.0768 | 0.31 | 13.11 | 0
July | 21 | 3AM to 4AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
July | 21 | 4AM to 5AM | 56.7 | 50.3 | 45 | 44.3 | 20.47 | 0.0765 | 0.3 | 13.15 | 0
July | 21 | 5AM to 6AM | 57.2 | 50.7 | 45.1 | 44.6 | 20.65 | 0.0765 | 0.3 | 13.16 | 0
July | 21 | 6AM to 7AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
July | 21 | 7AM to 8AM | 58.6 | 52 | 46.6 | 47.1 | 21.39 | 0.0762 | 0.32 | 13.21 | 0
July | 21 | 8AM to 9AM | 59.4 | 52.7 | 47.5 | 48.8 | 21.82 | 0.0761 | 0.33 | 13.23 | 0
July | 21 | 9AM to 10AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
July | 21 | 10AM to 11AM | 61.3 | 54 | 48.4 | 50.4 | 22.56 | 0.0758 | 0.34 | 13.28 | 0
July | 21 | 11AM to 12PM | 62.8 | 54.6 | 48.4 | 50.4 | 22.91 | 0.0756 | 0.34 | 13.32 | 0
July | 21 | 12PM to 1PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
July | 21 | 1PM to 2PM | 63.7 | 54.8 | 48.2 | 50.1 | 23.08 | 0.0755 | 0.34 | 13.34 | 0
July | 21 | 2PM to 3PM | 63.3 | 54.7 | 48.2 | 50.1 | 22.99 | 0.0755 | 0.34 | 13.33 | 0
July | 21 | 3PM to 4PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
July | 21 | 4PM to 5PM | 61.7 | 53.9 | 47.8 | 49.4 | 22.49 | 0.0758 | 0.33 | 13.29 | 0
July | 21 | 5PM to 6PM | 60.3 | 53.1 | 47.5 | 48.8 | 22.04 | 0.076 | 0.33 | 13.25 | 0
July | 21 | 6PM to 7PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
July | 21 | 7PM to 8PM | 57.9 | 52 | 47.3 | 48.4 | 21.42 | 0.0763 | 0.33 | 13.19 | 0
July | 21 | 8PM to 9PM | 57 | 51.6 | 47.3 | 48.4 | 21.2 | 0.0765 | 0.33 | 13.17 | 0
July | 21 | 9PM to 10PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
July | 21 | 10PM to 11PM | 55.6 | 50.9 | 47.1 | 48.1 | 20.8 | 0.0767 | 0.33 | 13.13 | 0
July | 21 | 11PM to 12AM | 55.4 | 50.7 | 46.8 | 47.4 | 20.65 | 0.0767 | 0.32 | 13.12 | 0
July | 22 | 12AM to 1AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
July | 22 | 1AM to 2AM | 54 | 49.9 | 46.6 | 47.1 | 20.25 | 0.0769 | 0.32 | 13.09 | 0
July | 22 | 2AM to 3AM | 53.1 | 49.5 | 46.4 | 46.8 | 19.98 | 0.0771 | 0.32 | 13.06 | 0
July | 22 | 3AM to 4AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
July | 22 | 4AM to 5AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.11 | 0.077 | 0.32 | 13.08 | 0
July | 22 | 5AM to 6AM | 55.4 | 50.7 | 46.8 | 47.4 | 20.65 | 0.0767 | 0.32 | 13.12 | 0
July | 22 | 6AM to 7AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
July | 22 | 7AM to 8AM | 59.7 | 53.7 | 49.1 | 51.8 | 22.39 | 0.076 | 0.35 | 13.25 | 0
July | 22 | 8AM to 9AM | 62.2 | 55.6 | 50.9 | 55.5 | 23.57 | 0.0757 | 0.37 | 13.32 | 0
July | 22 | 9AM to 10AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
July | 22 | 10AM to 11AM | 68.5 | 59 | 52.7 | 59.3 | 25.7 | 0.0747 | 0.4 | 13.5 | 0
July | 22 | 11AM to 12PM | 72.3 | 60.5 | 53.1 | 60.1 | 26.75 | 0.0742 | 0.41 | 13.59 | 0
July | 22 | 12PM to 1PM | 75.9 | 61.8 | 53.1 | 60.1 | 27.63 | 0.0737 | 0.41 | 13.69 | 0
July | 22 | 1PM to 2PM | 73.9 | 61.2 | 53.2 | 60.6 | 27.21 | 0.074 | 0.41 | 13.64 | 0
July | 22 | 2PM to 3PM | 72 | 60.5 | 53.2 | 60.6 | 26.72 | 0.0742 | 0.41 | 13.59 | 0
July | 22 | 3PM to 4PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
July | 22 | 4PM to 5PM | 67.6 | 58.5 | 52.5 | 58.9 | 25.42 | 0.0749 | 0.4 | 13.47 | 0
July | 22 | 5PM to 6PM | 65.3 | 57.4 | 52 | 57.8 | 24.67 | 0.0752 | 0.39 | 13.41 | 0
July | 22 | 6PM to 7PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
July | 22 | 7PM to 8PM | 61.7 | 55.7 | 51.4 | 56.6 | 23.61 | 0.0757 | 0.38 | 13.31 | 0
July | 22 | 8PM to 9PM | 60.3 | 55.1 | 51.4 | 56.6 | 23.26 | 0.0759 | 0.38 | 13.28 | 0
July | 22 | 9PM to 10PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
July | 22 | 10PM to 11PM | 58.3 | 54.1 | 51.1 | 55.9 | 22.66 | 0.0762 | 0.38 | 13.22 | 0
July | 22 | 11PM to 12AM | 57.7 | 53.7 | 50.7 | 55.1 | 22.41 | 0.0763 | 0.37 | 13.21 | 0
July | 23 | 12AM to 1AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 23 | 1AM to 2AM | 57 | 53.3 | 50.5 | 54.7 | 22.18 | 0.0764 | 0.37 | 13.19 | 0
July | 23 | 2AM to 3AM | 57 | 53.2 | 50.4 | 54.4 | 22.12 | 0.0764 | 0.37 | 13.19 | 0
July | 23 | 3AM to 4AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 23 | 4AM to 5AM | 57.4 | 53.4 | 50.4 | 54.4 | 22.21 | 0.0764 | 0.37 | 13.2 | 0
July | 23 | 5AM to 6AM | 57.6 | 53.7 | 50.9 | 55.5 | 22.43 | 0.0763 | 0.37 | 13.2 | 0
July | 23 | 6AM to 7AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 23 | 7AM to 8AM | 60.3 | 55.4 | 52 | 57.8 | 23.44 | 0.0759 | 0.39 | 13.28 | 0
July | 23 | 8AM to 9AM | 62.6 | 56.4 | 52.2 | 58.2 | 24.07 | 0.0756 | 0.39 | 13.34 | 0
July | 23 | 9AM to 10AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
July | 23 | 10AM to 11AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
July | 23 | 11AM to 12PM | 69.1 | 59.6 | 53.6 | 61.4 | 26.15 | 0.0746 | 0.41 | 13.52 | 0
July | 23 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
July | 23 | 1PM to 2PM | 70 | 60.1 | 53.8 | 61.8 | 26.43 | 0.0745 | 0.42 | 13.54 | 0
July | 23 | 2PM to 3PM | 69.1 | 59.6 | 53.6 | 61.4 | 26.15 | 0.0746 | 0.41 | 13.52 | 0
July | 23 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
July | 23 | 4PM to 5PM | 66 | 58.1 | 52.9 | 59.7 | 25.15 | 0.0751 | 0.4 | 13.43 | 0
July | 23 | 5PM to 6PM | 64 | 57.2 | 52.5 | 58.9 | 24.54 | 0.0754 | 0.4 | 13.38 | 0
July | 23 | 6PM to 7PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
July | 23 | 7PM to 8PM | 60.6 | 55.5 | 52 | 57.8 | 23.53 | 0.0759 | 0.39 | 13.29 | 0
July | 23 | 8PM to 9PM | 59.4 | 54.9 | 51.8 | 57.4 | 23.16 | 0.0761 | 0.39 | 13.26 | 0
July | 23 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 23 | 10PM to 11PM | 57.2 | 53.9 | 51.4 | 56.6 | 22.51 | 0.0764 | 0.38 | 13.2 | 0
July | 23 | 11PM to 12AM | 56.7 | 53.6 | 51.4 | 56.6 | 22.38 | 0.0765 | 0.38 | 13.18 | 0
July | 24 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 24 | 1AM to 2AM | 55.2 | 52.9 | 51.3 | 56.2 | 21.97 | 0.0767 | 0.38 | 13.15 | 0
July | 24 | 2AM to 3AM | 54.7 | 52.4 | 50.7 | 55.1 | 21.67 | 0.0768 | 0.37 | 13.13 | 0
July | 24 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 24 | 4AM to 5AM | 54.3 | 52.1 | 50.4 | 54.4 | 21.46 | 0.0768 | 0.37 | 13.12 | 0
July | 24 | 5AM to 6AM | 54.7 | 52.5 | 50.9 | 55.5 | 21.73 | 0.0768 | 0.37 | 13.13 | 0
July | 24 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 24 | 7AM to 8AM | 58.1 | 54.7 | 52.3 | 58.6 | 23.04 | 0.0762 | 0.4 | 13.23 | 0
July | 24 | 8AM to 9AM | 61 | 56.2 | 52.9 | 59.7 | 23.92 | 0.0758 | 0.4 | 13.3 | 0
July | 24 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
July | 24 | 10AM to 11AM | 66 | 58.4 | 53.4 | 61 | 25.34 | 0.0751 | 0.41 | 13.44 | 0
July | 24 | 11AM to 12PM | 68 | 59.1 | 53.4 | 61 | 25.82 | 0.0748 | 0.41 | 13.49 | 0
July | 24 | 12PM to 1PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
July | 24 | 1PM to 2PM | 68.7 | 59.3 | 53.2 | 60.6 | 25.93 | 0.0747 | 0.41 | 13.5 | 0
July | 24 | 2PM to 3PM | 67.3 | 58.8 | 53.2 | 60.6 | 25.58 | 0.0749 | 0.41 | 13.47 | 0
July | 24 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 24 | 4PM to 5PM | 63.7 | 57 | 52.5 | 58.9 | 24.46 | 0.0754 | 0.4 | 13.37 | 0
July | 24 | 5PM to 6PM | 61.3 | 55.8 | 52 | 57.8 | 23.7 | 0.0758 | 0.39 | 13.31 | 0
July | 24 | 6PM to 7PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
July | 24 | 7PM to 8PM | 57.7 | 53.9 | 51.1 | 55.9 | 22.53 | 0.0763 | 0.38 | 13.21 | 0
July | 24 | 8PM to 9PM | 56.3 | 53.1 | 50.7 | 55.1 | 22.06 | 0.0765 | 0.37 | 13.17 | 0
July | 24 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 24 | 10PM to 11PM | 55 | 52.4 | 50.4 | 54.4 | 21.64 | 0.0767 | 0.37 | 13.14 | 0
July | 24 | 11PM to 12AM | 55 | 52.4 | 50.4 | 54.4 | 21.64 | 0.0767 | 0.37 | 13.14 | 0
July | 25 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 25 | 1AM to 2AM | 54.7 | 52.3 | 50.5 | 54.7 | 21.61 | 0.0768 | 0.37 | 13.13 | 0
July | 25 | 2AM to 3AM | 54.3 | 52.1 | 50.4 | 54.4 | 21.46 | 0.0768 | 0.37 | 13.12 | 0
July | 25 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 25 | 4AM to 5AM | 55.2 | 52.5 | 50.4 | 54.4 | 21.68 | 0.0767 | 0.37 | 13.14 | 0
July | 25 | 5AM to 6AM | 56.7 | 53.3 | 50.9 | 55.5 | 22.21 | 0.0765 | 0.37 | 13.18 | 0
July | 25 | 6AM to 7AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 25 | 7AM to 8AM | 60.6 | 55.8 | 52.5 | 58.9 | 23.71 | 0.0759 | 0.4 | 13.29 | 0
July | 25 | 8AM to 9AM | 63.3 | 57.5 | 53.6 | 61.4 | 24.75 | 0.0755 | 0.41 | 13.37 | 0
July | 25 | 9AM to 10AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
July | 25 | 10AM to 11AM | 68.4 | 59.7 | 54.3 | 63 | 26.23 | 0.0747 | 0.43 | 13.5 | 0
July | 25 | 11AM to 12PM | 70.7 | 60.6 | 54.3 | 63 | 26.8 | 0.0744 | 0.43 | 13.56 | 0
July | 25 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
July | 25 | 1PM to 2PM | 71.4 | 60.6 | 53.8 | 61.8 | 26.78 | 0.0743 | 0.42 | 13.58 | 0
July | 25 | 2PM to 3PM | 69.6 | 59.8 | 53.6 | 61.4 | 26.28 | 0.0746 | 0.41 | 13.53 | 0
July | 25 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
July | 25 | 4PM to 5PM | 64.6 | 57.4 | 52.5 | 58.9 | 24.68 | 0.0753 | 0.4 | 13.39 | 0
July | 25 | 5PM to 6PM | 61.3 | 55.8 | 52 | 57.8 | 23.7 | 0.0758 | 0.39 | 13.31 | 0
July | 25 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 25 | 7PM to 8PM | 57 | 53.8 | 51.4 | 56.6 | 22.47 | 0.0764 | 0.38 | 13.19 | 0
July | 25 | 8PM to 9PM | 55.9 | 53.3 | 51.4 | 56.6 | 22.21 | 0.0766 | 0.38 | 13.17 | 0
July | 25 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 25 | 10PM to 11PM | 54.7 | 52.6 | 51.1 | 55.9 | 21.78 | 0.0768 | 0.38 | 13.13 | 0
July | 25 | 11PM to 12AM | 54.3 | 52.3 | 50.7 | 55.1 | 21.58 | 0.0768 | 0.37 | 13.12 | 0
July | 26 | 12AM to 1AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 26 | 1AM to 2AM | 53.6 | 51.9 | 50.5 | 54.7 | 21.35 | 0.0769 | 0.37 | 13.1 | 0
July | 26 | 2AM to 3AM | 53.4 | 51.7 | 50.4 | 54.4 | 21.25 | 0.077 | 0.37 | 13.09 | 0
July | 26 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
July | 26 | 4AM to 5AM | 54.7 | 52.6 | 51.1 | 55.9 | 21.78 | 0.0768 | 0.38 | 13.13 | 0
July | 26 | 5AM to 6AM | 56.3 | 53.9 | 52.2 | 58.2 | 22.54 | 0.0765 | 0.39 | 13.18 | 0
July | 26 | 6AM to 7AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 26 | 7AM to 8AM | 60.3 | 56.7 | 54.3 | 63 | 24.26 | 0.0759 | 0.43 | 13.3 | 0
July | 26 | 8AM to 9AM | 62.6 | 57.9 | 54.9 | 64.3 | 25.03 | 0.0755 | 0.43 | 13.36 | 0
July | 26 | 9AM to 10AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
July | 26 | 10AM to 11AM | 67.6 | 60.5 | 56.1 | 67.4 | 26.73 | 0.0748 | 0.45 | 13.5 | 0
July | 26 | 11AM to 12PM | 70.3 | 61.7 | 56.7 | 68.7 | 27.6 | 0.0744 | 0.46 | 13.57 | 0
July | 26 | 12PM to 1PM | 73 | 62.9 | 57 | 69.6 | 28.41 | 0.074 | 0.47 | 13.64 | 0
July | 26 | 1PM to 2PM | 70.7 | 61.6 | 56.1 | 67.4 | 27.48 | 0.0744 | 0.45 | 13.58 | 0
July | 26 | 2PM to 3PM | 68.4 | 60.2 | 55.2 | 65.2 | 26.57 | 0.0747 | 0.44 | 13.51 | 0
July | 26 | 3PM to 4PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
July | 26 | 4PM to 5PM | 63.3 | 57.3 | 53.2 | 60.6 | 24.62 | 0.0755 | 0.41 | 13.37 | 0
July | 26 | 5PM to 6PM | 60.6 | 55.6 | 52.2 | 58.2 | 23.59 | 0.0759 | 0.39 | 13.29 | 0
July | 26 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 26 | 7PM to 8PM | 57 | 53.8 | 51.4 | 56.6 | 22.47 | 0.0764 | 0.38 | 13.19 | 0
July | 26 | 8PM to 9PM | 55.9 | 53.3 | 51.4 | 56.6 | 22.21 | 0.0766 | 0.38 | 13.17 | 0
July | 26 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 26 | 10PM to 11PM | 55 | 53 | 51.4 | 56.6 | 21.99 | 0.0767 | 0.38 | 13.14 | 0
July | 26 | 11PM to 12AM | 55 | 53 | 51.4 | 56.6 | 21.99 | 0.0767 | 0.38 | 13.14 | 0
July | 27 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 27 | 1AM to 2AM | 55 | 53.1 | 51.6 | 57 | 22.05 | 0.0767 | 0.39 | 13.14 | 0
July | 27 | 2AM to 3AM | 55 | 53 | 51.4 | 56.6 | 21.99 | 0.0767 | 0.38 | 13.14 | 0
July | 27 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 27 | 4AM to 5AM | 56.3 | 53.7 | 51.8 | 57.4 | 22.41 | 0.0765 | 0.39 | 13.18 | 0
July | 27 | 5AM to 6AM | 57.7 | 54.7 | 52.5 | 58.9 | 23.01 | 0.0763 | 0.4 | 13.22 | 0
July | 27 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
July | 27 | 7AM to 8AM | 61.7 | 57.3 | 54.5 | 63.5 | 24.67 | 0.0757 | 0.43 | 13.33 | 0
July | 27 | 8AM to 9AM | 64.2 | 58.9 | 55.6 | 66 | 25.69 | 0.0753 | 0.45 | 13.41 | 0
July | 27 | 9AM to 10AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
July | 27 | 10AM to 11AM | 68.5 | 60.9 | 56.3 | 67.8 | 27.02 | 0.0747 | 0.46 | 13.52 | 0
July | 27 | 11AM to 12PM | 70.3 | 61.5 | 56.3 | 67.8 | 27.46 | 0.0744 | 0.46 | 13.57 | 0
July | 27 | 12PM to 1PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
July | 27 | 1PM to 2PM | 70.3 | 60.9 | 55.2 | 65.2 | 27.05 | 0.0744 | 0.44 | 13.56 | 0
July | 27 | 2PM to 3PM | 68.5 | 59.7 | 54.1 | 62.6 | 26.21 | 0.0747 | 0.42 | 13.51 | 0
July | 27 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
July | 27 | 4PM to 5PM | 66 | 57.9 | 52.5 | 58.9 | 25.03 | 0.0751 | 0.4 | 13.43 | 0
July | 27 | 5PM to 6PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
July | 27 | 6PM to 7PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
July | 27 | 7PM to 8PM | 62.1 | 55.9 | 51.6 | 57 | 23.76 | 0.0757 | 0.39 | 13.32 | 0
July | 27 | 8PM to 9PM | 59.9 | 55.3 | 52 | 57.8 | 23.35 | 0.076 | 0.39 | 13.27 | 0
July | 27 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
July | 27 | 10PM to 11PM | 57.2 | 54.3 | 52.2 | 58.2 | 22.75 | 0.0764 | 0.39 | 13.2 | 0
July | 27 | 11PM to 12AM | 56.7 | 53.8 | 51.8 | 57.4 | 22.5 | 0.0765 | 0.39 | 13.19 | 0
July | 28 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 28 | 1AM to 2AM | 55.9 | 53.4 | 51.6 | 57 | 22.27 | 0.0766 | 0.39 | 13.17 | 0
July | 28 | 2AM to 3AM | 55.9 | 53.3 | 51.4 | 56.6 | 22.21 | 0.0766 | 0.38 | 13.17 | 0
July | 28 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 28 | 4AM to 5AM | 56.7 | 53.6 | 51.4 | 56.6 | 22.38 | 0.0765 | 0.38 | 13.18 | 0
July | 28 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.63 | 0.0764 | 0.39 | 13.2 | 0
July | 28 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
July | 28 | 7AM to 8AM | 59 | 55.2 | 52.5 | 58.9 | 23.32 | 0.0761 | 0.4 | 13.25 | 0
July | 28 | 8AM to 9AM | 59.9 | 55.5 | 52.5 | 58.9 | 23.54 | 0.076 | 0.4 | 13.27 | 0
July | 28 | 9AM to 10AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
July | 28 | 10AM to 11AM | 62.1 | 56.3 | 52.3 | 58.6 | 24 | 0.0757 | 0.4 | 13.33 | 0
July | 28 | 11AM to 12PM | 63 | 56.7 | 52.3 | 58.6 | 24.22 | 0.0755 | 0.4 | 13.35 | 0
July | 28 | 12PM to 1PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
July | 28 | 1PM to 2PM | 63.7 | 56.8 | 52.2 | 58.2 | 24.33 | 0.0754 | 0.39 | 13.37 | 0
July | 28 | 2PM to 3PM | 63.3 | 56.7 | 52.2 | 58.2 | 24.25 | 0.0755 | 0.39 | 13.36 | 0
July | 28 | 3PM to 4PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
July | 28 | 4PM to 5PM | 61.3 | 55.7 | 51.8 | 57.4 | 23.64 | 0.0758 | 0.39 | 13.31 | 0
July | 28 | 5PM to 6PM | 59.5 | 54.9 | 51.6 | 57 | 23.14 | 0.076 | 0.39 | 13.26 | 0
July | 28 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 28 | 7PM to 8PM | 57.2 | 53.9 | 51.4 | 56.6 | 22.51 | 0.0764 | 0.38 | 13.2 | 0
July | 28 | 8PM to 9PM | 56.7 | 53.6 | 51.4 | 56.6 | 22.38 | 0.0765 | 0.38 | 13.18 | 0
July | 28 | 9PM to 10PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 28 | 10PM to 11PM | 55.6 | 53.2 | 51.4 | 56.6 | 22.12 | 0.0766 | 0.38 | 13.16 | 0
July | 28 | 11PM to 12AM | 55.4 | 53.1 | 51.4 | 56.6 | 22.08 | 0.0767 | 0.38 | 13.15 | 0
July | 29 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 29 | 1AM to 2AM | 55 | 53.1 | 51.6 | 57 | 22.05 | 0.0767 | 0.39 | 13.14 | 0
July | 29 | 2AM to 3AM | 55 | 53 | 51.4 | 56.6 | 21.99 | 0.0767 | 0.38 | 13.14 | 0
July | 29 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 29 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 29 | 5AM to 6AM | 57 | 53.7 | 51.3 | 56.2 | 22.41 | 0.0764 | 0.38 | 13.19 | 0
July | 29 | 6AM to 7AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 29 | 7AM to 8AM | 60.6 | 55.8 | 52.5 | 58.9 | 23.71 | 0.0759 | 0.4 | 13.29 | 0
July | 29 | 8AM to 9AM | 63.3 | 57.5 | 53.6 | 61.4 | 24.75 | 0.0755 | 0.41 | 13.37 | 0
July | 29 | 9AM to 10AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
July | 29 | 10AM to 11AM | 68 | 59.6 | 54.3 | 63 | 26.15 | 0.0748 | 0.43 | 13.49 | 0
July | 29 | 11AM to 12PM | 70 | 60.3 | 54.3 | 63 | 26.63 | 0.0745 | 0.43 | 13.54 | 0
July | 29 | 12PM to 1PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
July | 29 | 1PM to 2PM | 71.2 | 60.9 | 54.5 | 63.5 | 27 | 0.0743 | 0.43 | 13.58 | 0
July | 29 | 2PM to 3PM | 70.7 | 60.9 | 54.9 | 64.3 | 27 | 0.0744 | 0.43 | 13.57 | 0
July | 29 | 3PM to 4PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
July | 29 | 4PM to 5PM | 67.3 | 59.4 | 54.5 | 63.5 | 26.04 | 0.0749 | 0.43 | 13.48 | 0
July | 29 | 5PM to 6PM | 64.8 | 58.2 | 54 | 62.2 | 25.22 | 0.0752 | 0.42 | 13.41 | 0
July | 29 | 6PM to 7PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
July | 29 | 7PM to 8PM | 61.3 | 56.6 | 53.4 | 61 | 24.2 | 0.0757 | 0.41 | 13.32 | 0
July | 29 | 8PM to 9PM | 60.8 | 56.4 | 53.4 | 61 | 24.07 | 0.0758 | 0.41 | 13.3 | 0
July | 29 | 9PM to 10PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
July | 29 | 10PM to 11PM | 59.7 | 55.7 | 52.9 | 59.7 | 23.61 | 0.076 | 0.4 | 13.27 | 0
July | 29 | 11PM to 12AM | 59.4 | 55.1 | 52.2 | 58.2 | 23.28 | 0.0761 | 0.39 | 13.26 | 0
July | 30 | 12AM to 1AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
July | 30 | 1AM to 2AM | 58.6 | 54.5 | 51.6 | 57 | 22.93 | 0.0762 | 0.39 | 13.24 | 0
July | 30 | 2AM to 3AM | 58.3 | 54.3 | 51.4 | 56.6 | 22.78 | 0.0762 | 0.38 | 13.23 | 0
July | 30 | 3AM to 4AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 30 | 4AM to 5AM | 59 | 54.6 | 51.4 | 56.6 | 22.95 | 0.0761 | 0.38 | 13.24 | 0
July | 30 | 5AM to 6AM | 59.9 | 55.2 | 51.8 | 57.4 | 23.29 | 0.076 | 0.39 | 13.27 | 0
July | 30 | 6AM to 7AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
July | 30 | 7AM to 8AM | 62.6 | 56.8 | 52.9 | 59.7 | 24.32 | 0.0756 | 0.4 | 13.34 | 0
July | 30 | 8AM to 9AM | 64.4 | 57.7 | 53.2 | 60.6 | 24.88 | 0.0753 | 0.41 | 13.39 | 0
July | 30 | 9AM to 10AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 30 | 10AM to 11AM | 67.6 | 59.2 | 53.8 | 61.8 | 25.86 | 0.0748 | 0.42 | 13.48 | 0
July | 30 | 11AM to 12PM | 69.4 | 60 | 54 | 62.2 | 26.37 | 0.0746 | 0.42 | 13.53 | 0
July | 30 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
July | 30 | 1PM to 2PM | 70 | 60.1 | 53.8 | 61.8 | 26.43 | 0.0745 | 0.42 | 13.54 | 0
July | 30 | 2PM to 3PM | 69.1 | 59.6 | 53.6 | 61.4 | 26.15 | 0.0746 | 0.41 | 13.52 | 0
July | 30 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
July | 30 | 4PM to 5PM | 66.4 | 58.4 | 53.2 | 60.6 | 25.36 | 0.075 | 0.41 | 13.44 | 0
July | 30 | 5PM to 6PM | 64.6 | 57.8 | 53.2 | 60.6 | 24.93 | 0.0753 | 0.41 | 13.4 | 0
July | 30 | 6PM to 7PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
July | 30 | 7PM to 8PM | 62.1 | 56.5 | 52.7 | 59.3 | 24.12 | 0.0757 | 0.4 | 13.33 | 0
July | 30 | 8PM to 9PM | 61 | 55.8 | 52.2 | 58.2 | 23.68 | 0.0758 | 0.39 | 13.3 | 0
July | 30 | 9PM to 10PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
July | 30 | 10PM to 11PM | 60.4 | 55.4 | 51.8 | 57.4 | 23.42 | 0.0759 | 0.39 | 13.28 | 0
July | 30 | 11PM to 12AM | 60.6 | 55.6 | 52.2 | 58.2 | 23.59 | 0.0759 | 0.39 | 13.29 | 0
July | 31 | 12AM to 1AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
July | 31 | 1AM to 2AM | 60.6 | 55.7 | 52.3 | 58.6 | 23.65 | 0.0759 | 0.4 | 13.29 | 0
July | 31 | 2AM to 3AM | 60.4 | 55.7 | 52.3 | 58.6 | 23.61 | 0.0759 | 0.4 | 13.29 | 0
July | 31 | 3AM to 4AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 31 | 4AM to 5AM | 60.1 | 55.4 | 52.2 | 58.2 | 23.46 | 0.076 | 0.39 | 13.28 | 0
July | 31 | 5AM to 6AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 31 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 31 | 7AM to 8AM | 61 | 56.4 | 53.2 | 60.6 | 24.05 | 0.0758 | 0.41 | 13.31 | 0
July | 31 | 8AM to 9AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
July | 31 | 9AM to 10AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
July | 31 | 10AM to 11AM | 64 | 58.2 | 54.5 | 63.5 | 25.24 | 0.0753 | 0.43 | 13.39 | 0
July | 31 | 11AM to 12PM | 64.9 | 58.5 | 54.3 | 63 | 25.4 | 0.0752 | 0.43 | 13.41 | 0
July | 31 | 12PM to 1PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
July | 31 | 1PM to 2PM | 66.7 | 59.1 | 54.1 | 62.6 | 25.77 | 0.075 | 0.42 | 13.46 | 0
July | 31 | 2PM to 3PM | 67.3 | 59.3 | 54.1 | 62.6 | 25.9 | 0.0749 | 0.42 | 13.47 | 0
July | 31 | 3PM to 4PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
July | 31 | 4PM to 5PM | 66 | 58.9 | 54.3 | 63 | 25.66 | 0.0751 | 0.43 | 13.44 | 0
July | 31 | 5PM to 6PM | 64 | 58.1 | 54.3 | 63 | 25.18 | 0.0753 | 0.43 | 13.39 | 0
July | 31 | 6PM to 7PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
July | 31 | 7PM to 8PM | 61.3 | 57 | 54.1 | 62.6 | 24.46 | 0.0757 | 0.42 | 13.32 | 0
July | 31 | 8PM to 9PM | 60.8 | 56.6 | 53.8 | 61.8 | 24.19 | 0.0758 | 0.42 | 13.31 | 0
July | 31 | 9PM to 10PM | 60.6 | 56.5 | 53.8 | 61.8 | 24.15 | 0.0758 | 0.42 | 13.3 | 0
July | 31 | 10PM to 11PM | 60.3 | 56.4 | 53.8 | 61.8 | 24.06 | 0.0759 | 0.42 | 13.29 | 0
July | 31 | 11PM to 12AM | 60.1 | 56.3 | 53.8 | 61.8 | 24.02 | 0.0759 | 0.42 | 13.29 | 0
August | 1 | 12AM to 1AM | 59.7 | 56.3 | 54 | 62.2 | 24 | 0.076 | 0.42 | 13.28 | 0
August | 1 | 1AM to 2AM | 59.5 | 56.2 | 54 | 62.2 | 23.95 | 0.076 | 0.42 | 13.27 | 0
August | 1 | 2AM to 3AM | 59.2 | 56.1 | 54 | 62.2 | 23.86 | 0.0761 | 0.42 | 13.26 | 0
August | 1 | 3AM to 4AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 1 | 4AM to 5AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 1 | 5AM to 6AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 1 | 6AM to 7AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 1 | 7AM to 8AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 1 | 8AM to 9AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 1 | 9AM to 10AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
August | 1 | 10AM to 11AM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 1 | 11AM to 12PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
August | 1 | 12PM to 1PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
August | 1 | 1PM to 2PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
August | 1 | 2PM to 3PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
August | 1 | 3PM to 4PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
August | 1 | 4PM to 5PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
August | 1 | 5PM to 6PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 1 | 6PM to 7PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
August | 1 | 7PM to 8PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
August | 1 | 8PM to 9PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 1 | 9PM to 10PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
August | 1 | 10PM to 11PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 1 | 11PM to 12AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 2 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 2 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 2 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 2 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 2 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 2 | 5AM to 6AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 2 | 6AM to 7AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
August | 2 | 7AM to 8AM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
August | 2 | 8AM to 9AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
August | 2 | 9AM to 10AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
August | 2 | 10AM to 11AM | 78.1 | 62.6 | 53.1 | 60.1 | 28.15 | 0.0734 | 0.41 | 13.74 | 0
August | 2 | 11AM to 12PM | 80.1 | 63.7 | 54 | 62.2 | 28.96 | 0.0731 | 0.42 | 13.8 | 0
August | 2 | 12PM to 1PM | 84.9 | 65.3 | 54 | 62.2 | 30.14 | 0.0725 | 0.42 | 13.92 | 0
August | 2 | 1PM to 2PM | 82 | 63.9 | 53.1 | 60.1 | 29.12 | 0.0729 | 0.41 | 13.84 | 0
August | 2 | 2PM to 3PM | 82.9 | 63.7 | 52 | 57.8 | 28.97 | 0.0728 | 0.39 | 13.86 | 0
August | 2 | 3PM to 4PM | 78.1 | 62.6 | 53.1 | 60.1 | 28.15 | 0.0734 | 0.41 | 13.74 | 0
August | 2 | 4PM to 5PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
August | 2 | 5PM to 6PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
August | 2 | 6PM to 7PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 2 | 7PM to 8PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 2 | 8PM to 9PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 2 | 9PM to 10PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 2 | 10PM to 11PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 2 | 11PM to 12AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 3 | 12AM to 1AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 3 | 1AM to 2AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 3 | 2AM to 3AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 3 | 3AM to 4AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 3 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 3 | 5AM to 6AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 3 | 6AM to 7AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
August | 3 | 7AM to 8AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
August | 3 | 8AM to 9AM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
August | 3 | 9AM to 10AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
August | 3 | 10AM to 11AM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
August | 3 | 11AM to 12PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
August | 3 | 12PM to 1PM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
August | 3 | 1PM to 2PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
August | 3 | 2PM to 3PM | 81 | 64.5 | 55 | 64.7 | 29.57 | 0.073 | 0.44 | 13.83 | 0
August | 3 | 3PM to 4PM | 78.1 | 64 | 55.9 | 66.9 | 29.21 | 0.0734 | 0.45 | 13.76 | 0
August | 3 | 4PM to 5PM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
August | 3 | 5PM to 6PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
August | 3 | 6PM to 7PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
August | 3 | 7PM to 8PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
August | 3 | 8PM to 9PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
August | 3 | 9PM to 10PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
August | 3 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 3 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 4 | 12AM to 1AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 4 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 4 | 2AM to 3AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 4 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 4 | 4AM to 5AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 4 | 5AM to 6AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 4 | 6AM to 7AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 4 | 7AM to 8AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
August | 4 | 8AM to 9AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
August | 4 | 9AM to 10AM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
August | 4 | 10AM to 11AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
August | 4 | 11AM to 12PM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
August | 4 | 12PM to 1PM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
August | 4 | 1PM to 2PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
August | 4 | 2PM to 3PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
August | 4 | 3PM to 4PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 4 | 4PM to 5PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 4 | 5PM to 6PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 4 | 6PM to 7PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 4 | 7PM to 8PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
August | 4 | 8PM to 9PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 4 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 4 | 10PM to 11PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 4 | 11PM to 12AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
August | 5 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 5 | 1AM to 2AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 5 | 2AM to 3AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 5 | 3AM to 4AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 5 | 4AM to 5AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 5 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 5 | 6AM to 7AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 5 | 7AM to 8AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 5 | 8AM to 9AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 5 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 5 | 10AM to 11AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 5 | 11AM to 12PM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
August | 5 | 12PM to 1PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 5 | 1PM to 2PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
August | 5 | 2PM to 3PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 5 | 3PM to 4PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 5 | 4PM to 5PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 5 | 5PM to 6PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 5 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 5 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 5 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 5 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 5 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 5 | 11PM to 12AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 6 | 12AM to 1AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 6 | 1AM to 2AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 6 | 2AM to 3AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 6 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 6 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
August | 6 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 6 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 6 | 7AM to 8AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 6 | 8AM to 9AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 6 | 9AM to 10AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
August | 6 | 10AM to 11AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
August | 6 | 11AM to 12PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
August | 6 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
August | 6 | 1PM to 2PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
August | 6 | 2PM to 3PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
August | 6 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 6 | 4PM to 5PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 6 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 6 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 6 | 7PM to 8PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
August | 6 | 8PM to 9PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 6 | 9PM to 10PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 6 | 10PM to 11PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 6 | 11PM to 12AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 7 | 12AM to 1AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 7 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 7 | 2AM to 3AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
August | 7 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 7 | 4AM to 5AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
August | 7 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 7 | 6AM to 7AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 7 | 7AM to 8AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 7 | 8AM to 9AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 7 | 9AM to 10AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 7 | 10AM to 11AM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
August | 7 | 11AM to 12PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 7 | 12PM to 1PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 7 | 1PM to 2PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
August | 7 | 2PM to 3PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 7 | 3PM to 4PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
August | 7 | 4PM to 5PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 7 | 5PM to 6PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
August | 7 | 6PM to 7PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
August | 7 | 7PM to 8PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
August | 7 | 8PM to 9PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 7 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 7 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 7 | 11PM to 12AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
August | 8 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 8 | 1AM to 2AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 8 | 2AM to 3AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 8 | 3AM to 4AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
August | 8 | 4AM to 5AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
August | 8 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
August | 8 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 8 | 7AM to 8AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
August | 8 | 8AM to 9AM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
August | 8 | 9AM to 10AM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
August | 8 | 10AM to 11AM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 8 | 11AM to 12PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
August | 8 | 12PM to 1PM | 77 | 61.3 | 51.1 | 55.9 | 27.22 | 0.0736 | 0.38 | 13.7 | 0
August | 8 | 1PM to 2PM | 75 | 59.5 | 48.9 | 51.5 | 26.05 | 0.0739 | 0.35 | 13.64 | 0
August | 8 | 2PM to 3PM | 73.9 | 58.7 | 48 | 49.8 | 25.52 | 0.074 | 0.34 | 13.6 | 0
August | 8 | 3PM to 4PM | 73 | 57.9 | 46.9 | 47.8 | 24.99 | 0.0742 | 0.32 | 13.57 | 0
August | 8 | 4PM to 5PM | 72 | 58 | 48 | 49.8 | 25.04 | 0.0743 | 0.34 | 13.55 | 0
August | 8 | 5PM to 6PM | 70 | 57.2 | 48 | 49.8 | 24.56 | 0.0746 | 0.34 | 13.5 | 0
August | 8 | 6PM to 7PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
August | 8 | 7PM to 8PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
August | 8 | 8PM to 9PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 8 | 9PM to 10PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 8 | 10PM to 11PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 8 | 11PM to 12AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
August | 9 | 12AM to 1AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 9 | 1AM to 2AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 9 | 2AM to 3AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
August | 9 | 3AM to 4AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
August | 9 | 4AM to 5AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
August | 9 | 5AM to 6AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 9 | 6AM to 7AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 9 | 7AM to 8AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
August | 9 | 8AM to 9AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
August | 9 | 9AM to 10AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
August | 9 | 10AM to 11AM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
August | 9 | 11AM to 12PM | 80.1 | 63.3 | 53.1 | 60.1 | 28.64 | 0.0731 | 0.41 | 13.79 | 0
August | 9 | 12PM to 1PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
August | 9 | 1PM to 2PM | 82.9 | 63.7 | 52 | 57.8 | 28.97 | 0.0728 | 0.39 | 13.86 | 0
August | 9 | 2PM to 3PM | 84 | 62.8 | 48.9 | 51.5 | 28.24 | 0.0726 | 0.35 | 13.87 | 0
August | 9 | 3PM to 4PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
August | 9 | 4PM to 5PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
August | 9 | 5PM to 6PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 9 | 6PM to 7PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 9 | 7PM to 8PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 9 | 8PM to 9PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 9 | 9PM to 10PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 9 | 10PM to 11PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 9 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
August | 10 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 10 | 1AM to 2AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
August | 10 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
August | 10 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 10 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 10 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 10 | 6AM to 7AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 10 | 7AM to 8AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 10 | 8AM to 9AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 10 | 9AM to 10AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
August | 10 | 10AM to 11AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
August | 10 | 11AM to 12PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
August | 10 | 12PM to 1PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
August | 10 | 1PM to 2PM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
August | 10 | 2PM to 3PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
August | 10 | 3PM to 4PM | 71.1 | 59.5 | 52 | 57.8 | 26.07 | 0.0744 | 0.39 | 13.56 | 0
August | 10 | 4PM to 5PM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
August | 10 | 5PM to 6PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
August | 10 | 6PM to 7PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 10 | 7PM to 8PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 10 | 8PM to 9PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 10 | 9PM to 10PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 10 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 10 | 11PM to 12AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
August | 11 | 12AM to 1AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 11 | 1AM to 2AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
August | 11 | 2AM to 3AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 11 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 11 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 11 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 11 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 11 | 7AM to 8AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 11 | 8AM to 9AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 11 | 9AM to 10AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 11 | 10AM to 11AM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 11 | 11AM to 12PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
August | 11 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
August | 11 | 1PM to 2PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
August | 11 | 2PM to 3PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
August | 11 | 3PM to 4PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
August | 11 | 4PM to 5PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
August | 11 | 5PM to 6PM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
August | 11 | 6PM to 7PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 11 | 7PM to 8PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 11 | 8PM to 9PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 11 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 11 | 10PM to 11PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 11 | 11PM to 12AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
August | 12 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 12 | 1AM to 2AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 12 | 2AM to 3AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 12 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 12 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 12 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 12 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 12 | 7AM to 8AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 12 | 8AM to 9AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 12 | 9AM to 10AM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 12 | 10AM to 11AM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 12 | 11AM to 12PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
August | 12 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
August | 12 | 1PM to 2PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
August | 12 | 2PM to 3PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
August | 12 | 3PM to 4PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 12 | 4PM to 5PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 12 | 5PM to 6PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 12 | 6PM to 7PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 12 | 7PM to 8PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 12 | 8PM to 9PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 12 | 9PM to 10PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 12 | 10PM to 11PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 12 | 11PM to 12AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 13 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 1AM to 2AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 2AM to 3AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 3AM to 4AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 13 | 4AM to 5AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 13 | 5AM to 6AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 13 | 6AM to 7AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 13 | 7AM to 8AM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
August | 13 | 8AM to 9AM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
August | 13 | 9AM to 10AM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
August | 13 | 10AM to 11AM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
August | 13 | 11AM to 12PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
August | 13 | 12PM to 1PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
August | 13 | 1PM to 2PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 13 | 2PM to 3PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
August | 13 | 3PM to 4PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 13 | 4PM to 5PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
August | 13 | 5PM to 6PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 13 | 6PM to 7PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 13 | 7PM to 8PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
August | 13 | 8PM to 9PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 13 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 13 | 10PM to 11PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 11PM to 12AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 14 | 12AM to 1AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 14 | 1AM to 2AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 14 | 2AM to 3AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 14 | 3AM to 4AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 14 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 14 | 5AM to 6AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 14 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 14 | 7AM to 8AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 14 | 8AM to 9AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 14 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 14 | 10AM to 11AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 14 | 11AM to 12PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 14 | 12PM to 1PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 14 | 1PM to 2PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 14 | 2PM to 3PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 14 | 3PM to 4PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
August | 14 | 4PM to 5PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 14 | 5PM to 6PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 14 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 14 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 14 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 14 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 14 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 14 | 11PM to 12AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 15 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 3AM to 4AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 15 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 15 | 5AM to 6AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 15 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 15 | 7AM to 8AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 8AM to 9AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 9AM to 10AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 15 | 10AM to 11AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 15 | 11AM to 12PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 15 | 12PM to 1PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
August | 15 | 1PM to 2PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 15 | 2PM to 3PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 15 | 3PM to 4PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 15 | 4PM to 5PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 15 | 5PM to 6PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 15 | 6PM to 7PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 15 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 15 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 10PM to 11PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 15 | 11PM to 12AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
August | 16 | 12AM to 1AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 16 | 1AM to 2AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 16 | 2AM to 3AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 16 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 16 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 16 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 16 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 16 | 7AM to 8AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 16 | 8AM to 9AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 16 | 9AM to 10AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 16 | 10AM to 11AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 16 | 11AM to 12PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 16 | 12PM to 1PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 16 | 1PM to 2PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
August | 16 | 2PM to 3PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 16 | 3PM to 4PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 16 | 4PM to 5PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 16 | 5PM to 6PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
August | 16 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 16 | 7PM to 8PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 16 | 8PM to 9PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 16 | 9PM to 10PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 16 | 10PM to 11PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 16 | 11PM to 12AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
August | 17 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 17 | 1AM to 2AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 17 | 2AM to 3AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 17 | 3AM to 4AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 17 | 4AM to 5AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 17 | 5AM to 6AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 17 | 6AM to 7AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 17 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 17 | 8AM to 9AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 17 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 17 | 10AM to 11AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 17 | 11AM to 12PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
August | 17 | 12PM to 1PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
August | 17 | 1PM to 2PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 17 | 2PM to 3PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
August | 17 | 3PM to 4PM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
August | 17 | 4PM to 5PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
August | 17 | 5PM to 6PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
August | 17 | 6PM to 7PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
August | 17 | 7PM to 8PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
August | 17 | 8PM to 9PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 17 | 9PM to 10PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 17 | 10PM to 11PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 17 | 11PM to 12AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
August | 18 | 12AM to 1AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 18 | 1AM to 2AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 18 | 2AM to 3AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 18 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 18 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 18 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 18 | 6AM to 7AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 18 | 7AM to 8AM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
August | 18 | 8AM to 9AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 18 | 9AM to 10AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 18 | 10AM to 11AM | 71.1 | 58.6 | 50 | 53.6 | 25.43 | 0.0744 | 0.36 | 13.54 | 0
August | 18 | 11AM to 12PM | 71.1 | 58.1 | 48.9 | 51.5 | 25.09 | 0.0744 | 0.35 | 13.54 | 0
August | 18 | 12PM to 1PM | 72 | 58.4 | 48.9 | 51.5 | 25.31 | 0.0743 | 0.35 | 13.56 | 0
August | 18 | 1PM to 2PM | 73.9 | 58.7 | 48 | 49.8 | 25.52 | 0.074 | 0.34 | 13.6 | 0
August | 18 | 2PM to 3PM | 72 | 58.4 | 48.9 | 51.5 | 25.31 | 0.0743 | 0.35 | 13.56 | 0
August | 18 | 3PM to 4PM | 72 | 58.9 | 50 | 53.6 | 25.64 | 0.0743 | 0.36 | 13.57 | 0
August | 18 | 4PM to 5PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 18 | 5PM to 6PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 18 | 6PM to 7PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
August | 18 | 7PM to 8PM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
August | 18 | 8PM to 9PM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
August | 18 | 9PM to 10PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 18 | 10PM to 11PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
August | 18 | 11PM to 12AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
August | 19 | 12AM to 1AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
August | 19 | 1AM to 2AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
August | 19 | 2AM to 3AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 19 | 3AM to 4AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 19 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 19 | 5AM to 6AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 19 | 6AM to 7AM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 19 | 7AM to 8AM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
August | 19 | 8AM to 9AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 19 | 9AM to 10AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 19 | 10AM to 11AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 19 | 11AM to 12PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 19 | 12PM to 1PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
August | 19 | 1PM to 2PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 19 | 2PM to 3PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 19 | 3PM to 4PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
August | 19 | 4PM to 5PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
August | 19 | 5PM to 6PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
August | 19 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 19 | 7PM to 8PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 19 | 8PM to 9PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
August | 19 | 9PM to 10PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 19 | 10PM to 11PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 19 | 11PM to 12AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 20 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 1AM to 2AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 20 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 20 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 20 | 6AM to 7AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 20 | 7AM to 8AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 20 | 8AM to 9AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 20 | 9AM to 10AM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 20 | 10AM to 11AM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 20 | 11AM to 12PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 20 | 12PM to 1PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 20 | 1PM to 2PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
August | 20 | 2PM to 3PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 20 | 3PM to 4PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 20 | 4PM to 5PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 20 | 5PM to 6PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 20 | 6PM to 7PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 20 | 7PM to 8PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 20 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 11PM to 12AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 21 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 21 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 21 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 21 | 3AM to 4AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 21 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 21 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 21 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 21 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 21 | 8AM to 9AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 9AM to 10AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 11AM to 12PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 12PM to 1PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 21 | 1PM to 2PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 21 | 2PM to 3PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
August | 21 | 3PM to 4PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 21 | 4PM to 5PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 21 | 5PM to 6PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 6PM to 7PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 21 | 7PM to 8PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 21 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 21 | 9PM to 10PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 21 | 10PM to 11PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 21 | 11PM to 12AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 22 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 22 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 22 | 2AM to 3AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 22 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 22 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
August | 22 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 22 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 22 | 7AM to 8AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 22 | 8AM to 9AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 22 | 9AM to 10AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 22 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 22 | 11AM to 12PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 22 | 12PM to 1PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 22 | 1PM to 2PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 22 | 2PM to 3PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 22 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 22 | 4PM to 5PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 22 | 5PM to 6PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 22 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 22 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 22 | 8PM to 9PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 22 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 22 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 22 | 11PM to 12AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 23 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 23 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 23 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 23 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
August | 23 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 23 | 5AM to 6AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 23 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 23 | 7AM to 8AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 23 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
August | 23 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 23 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 23 | 11AM to 12PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 23 | 12PM to 1PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
August | 23 | 1PM to 2PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
August | 23 | 2PM to 3PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
August | 23 | 3PM to 4PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 23 | 4PM to 5PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 23 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 23 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 23 | 7PM to 8PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 23 | 8PM to 9PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 23 | 9PM to 10PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 23 | 10PM to 11PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 23 | 11PM to 12AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 24 | 12AM to 1AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 24 | 1AM to 2AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 24 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 24 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 24 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 24 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 24 | 6AM to 7AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 24 | 7AM to 8AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 24 | 8AM to 9AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 24 | 9AM to 10AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 24 | 10AM to 11AM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
August | 24 | 11AM to 12PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 24 | 12PM to 1PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
August | 24 | 1PM to 2PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
August | 24 | 2PM to 3PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
August | 24 | 3PM to 4PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
August | 24 | 4PM to 5PM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
August | 24 | 5PM to 6PM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
August | 24 | 6PM to 7PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
August | 24 | 7PM to 8PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
August | 24 | 8PM to 9PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
August | 24 | 9PM to 10PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 24 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 24 | 11PM to 12AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 12AM to 1AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 25 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 2AM to 3AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 3AM to 4AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 5AM to 6AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 6AM to 7AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
August | 25 | 7AM to 8AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 8AM to 9AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 9AM to 10AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
August | 25 | 10AM to 11AM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
August | 25 | 11AM to 12PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 25 | 12PM to 1PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 25 | 1PM to 2PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 25 | 2PM to 3PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 25 | 3PM to 4PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 25 | 4PM to 5PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 25 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 25 | 6PM to 7PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 25 | 7PM to 8PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 8PM to 9PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 9PM to 10PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 25 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 11PM to 12AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
August | 26 | 12AM to 1AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
August | 26 | 1AM to 2AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 26 | 2AM to 3AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 26 | 3AM to 4AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
August | 26 | 4AM to 5AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
August | 26 | 5AM to 6AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 26 | 6AM to 7AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 26 | 7AM to 8AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 26 | 8AM to 9AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 26 | 9AM to 10AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 26 | 10AM to 11AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 26 | 11AM to 12PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 26 | 12PM to 1PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 26 | 1PM to 2PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 26 | 2PM to 3PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 26 | 3PM to 4PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 26 | 4PM to 5PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 26 | 5PM to 6PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 26 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 26 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 26 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 26 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 26 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 26 | 11PM to 12AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 27 | 12AM to 1AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 27 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 27 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 27 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 27 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 27 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 27 | 6AM to 7AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 27 | 7AM to 8AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 27 | 8AM to 9AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 27 | 9AM to 10AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 27 | 10AM to 11AM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
August | 27 | 11AM to 12PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
August | 27 | 12PM to 1PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
August | 27 | 1PM to 2PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
August | 27 | 2PM to 3PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
August | 27 | 3PM to 4PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
August | 27 | 4PM to 5PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 27 | 5PM to 6PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 27 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 27 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 27 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 27 | 9PM to 10PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 27 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 27 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 28 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 28 | 4AM to 5AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
August | 28 | 5AM to 6AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
August | 28 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 7AM to 8AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 28 | 8AM to 9AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 28 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 28 | 10AM to 11AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
August | 28 | 11AM to 12PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 28 | 12PM to 1PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 28 | 1PM to 2PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 28 | 2PM to 3PM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
August | 28 | 3PM to 4PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 28 | 4PM to 5PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
August | 28 | 5PM to 6PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 28 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 28 | 7PM to 8PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 28 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 28 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 29 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 2AM to 3AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
August | 29 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 6AM to 7AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 29 | 7AM to 8AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 29 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 29 | 9AM to 10AM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
August | 29 | 10AM to 11AM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
August | 29 | 11AM to 12PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
August | 29 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 29 | 1PM to 2PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
August | 29 | 2PM to 3PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 29 | 3PM to 4PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 29 | 4PM to 5PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
August | 29 | 5PM to 6PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
August | 29 | 6PM to 7PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 29 | 7PM to 8PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 29 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 29 | 9PM to 10PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 29 | 10PM to 11PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
August | 29 | 11PM to 12AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 30 | 12AM to 1AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 30 | 1AM to 2AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 30 | 2AM to 3AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
August | 30 | 3AM to 4AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
August | 30 | 4AM to 5AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 30 | 5AM to 6AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 30 | 6AM to 7AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 30 | 7AM to 8AM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
August | 30 | 8AM to 9AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
August | 30 | 9AM to 10AM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
August | 30 | 10AM to 11AM | 73 | 60.3 | 52 | 57.8 | 26.55 | 0.0741 | 0.39 | 13.61 | 0
August | 30 | 11AM to 12PM | 79 | 57.5 | 39.9 | 36.4 | 24.65 | 0.0734 | 0.25 | 13.69 | 0
August | 30 | 12PM to 1PM | 75.9 | 58.6 | 46 | 46.1 | 25.44 | 0.0738 | 0.31 | 13.64 | 0
August | 30 | 1PM to 2PM | 75.9 | 59.5 | 48 | 49.8 | 26 | 0.0738 | 0.34 | 13.65 | 0
August | 30 | 2PM to 3PM | 73 | 58.8 | 48.9 | 51.5 | 25.57 | 0.0741 | 0.35 | 13.59 | 0
August | 30 | 3PM to 4PM | 71.1 | 58.1 | 48.9 | 51.5 | 25.09 | 0.0744 | 0.35 | 13.54 | 0
August | 30 | 4PM to 5PM | 70 | 58.2 | 50 | 53.6 | 25.16 | 0.0746 | 0.36 | 13.51 | 0
August | 30 | 5PM to 6PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
August | 30 | 6PM to 7PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
August | 30 | 7PM to 8PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
August | 30 | 8PM to 9PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 30 | 9PM to 10PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 30 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 30 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 31 | 12AM to 1AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 31 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 31 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 31 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 31 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 31 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 31 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 31 | 7AM to 8AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 31 | 8AM to 9AM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
August | 31 | 9AM to 10AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
August | 31 | 10AM to 11AM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
August | 31 | 11AM to 12PM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
August | 31 | 12PM to 1PM | 82 | 62.1 | 48.9 | 51.5 | 27.76 | 0.0729 | 0.35 | 13.82 | 0
August | 31 | 1PM to 2PM | 75.9 | 60.9 | 51.1 | 55.9 | 26.96 | 0.0737 | 0.38 | 13.67 | 0
August | 31 | 2PM to 3PM | 73 | 59.8 | 51.1 | 55.9 | 26.25 | 0.0741 | 0.38 | 13.6 | 0
August | 31 | 3PM to 4PM | 73 | 56.3 | 43 | 41 | 23.94 | 0.0742 | 0.28 | 13.55 | 0
August | 31 | 4PM to 5PM | 71.1 | 55.5 | 43 | 41 | 23.46 | 0.0745 | 0.28 | 13.5 | 0
August | 31 | 5PM to 6PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
August | 31 | 6PM to 7PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
August | 31 | 7PM to 8PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
August | 31 | 8PM to 9PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
August | 31 | 9PM to 10PM | 61.3 | 54.2 | 48.7 | 51.1 | 22.67 | 0.0758 | 0.35 | 13.29 | 0
August | 31 | 10PM to 11PM | 60.6 | 54.2 | 49.5 | 52.6 | 22.72 | 0.0759 | 0.36 | 13.27 | 0
August | 31 | 11PM to 12AM | 59.9 | 54.3 | 50.2 | 54 | 22.77 | 0.076 | 0.37 | 13.26 | 0
September | 1 | 12AM to 1AM | 59.2 | 54.4 | 50.9 | 55.5 | 22.82 | 0.0761 | 0.37 | 13.24 | 0
September | 1 | 1AM to 2AM | 58.5 | 54.5 | 51.6 | 57 | 22.88 | 0.0762 | 0.39 | 13.23 | 0
September | 1 | 2AM to 3AM | 57.7 | 54.6 | 52.3 | 58.6 | 22.95 | 0.0763 | 0.4 | 13.22 | 0
September | 1 | 3AM to 4AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 1 | 4AM to 5AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 1 | 5AM to 6AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 1 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 1 | 7AM to 8AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 1 | 8AM to 9AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
September | 1 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 1 | 10AM to 11AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 1 | 11AM to 12PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 1 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 1 | 1PM to 2PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 1 | 2PM to 3PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 1 | 3PM to 4PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 1 | 4PM to 5PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
September | 1 | 5PM to 6PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
September | 1 | 6PM to 7PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
September | 1 | 7PM to 8PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
September | 1 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 1 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 1 | 10PM to 11PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
September | 1 | 11PM to 12AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 2 | 12AM to 1AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
September | 2 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 2 | 2AM to 3AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 2 | 3AM to 4AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 2 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 2 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 2 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
September | 2 | 7AM to 8AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
September | 2 | 8AM to 9AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
September | 2 | 9AM to 10AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
September | 2 | 10AM to 11AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 2 | 11AM to 12PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 2 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 2 | 1PM to 2PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 2 | 2PM to 3PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 2 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 2 | 4PM to 5PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 2 | 5PM to 6PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 2 | 6PM to 7PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 2 | 7PM to 8PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 2 | 8PM to 9PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 2 | 9PM to 10PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 2 | 10PM to 11PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 2 | 11PM to 12AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 3 | 12AM to 1AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 3 | 1AM to 2AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 3 | 2AM to 3AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
September | 3 | 3AM to 4AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
September | 3 | 4AM to 5AM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
September | 3 | 5AM to 6AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 3 | 6AM to 7AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
September | 3 | 7AM to 8AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
September | 3 | 8AM to 9AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
September | 3 | 9AM to 10AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 3 | 10AM to 11AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
September | 3 | 11AM to 12PM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
September | 3 | 12PM to 1PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
September | 3 | 1PM to 2PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
September | 3 | 2PM to 3PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 3 | 3PM to 4PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 3 | 4PM to 5PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 3 | 5PM to 6PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
September | 3 | 6PM to 7PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 3 | 7PM to 8PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 3 | 8PM to 9PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 3 | 9PM to 10PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 3 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 3 | 11PM to 12AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 4 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 4 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 4 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 4 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 4 | 4AM to 5AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 4 | 5AM to 6AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 4 | 6AM to 7AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 4 | 7AM to 8AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 4 | 8AM to 9AM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 4 | 9AM to 10AM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
September | 4 | 10AM to 11AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
September | 4 | 11AM to 12PM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
September | 4 | 12PM to 1PM | 81 | 65 | 55.9 | 66.9 | 29.92 | 0.073 | 0.45 | 13.84 | 0
September | 4 | 1PM to 2PM | 81 | 65 | 55.9 | 66.9 | 29.92 | 0.073 | 0.45 | 13.84 | 0
September | 4 | 2PM to 3PM | 75.9 | 63.3 | 55.9 | 66.9 | 28.69 | 0.0737 | 0.45 | 13.71 | 0
September | 4 | 3PM to 4PM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
September | 4 | 4PM to 5PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
September | 4 | 5PM to 6PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
September | 4 | 6PM to 7PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
September | 4 | 7PM to 8PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 4 | 8PM to 9PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 4 | 9PM to 10PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 4 | 10PM to 11PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 4 | 11PM to 12AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 5 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 5 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 5 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 5 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 5 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 5 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 5 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
September | 5 | 7AM to 8AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 5 | 8AM to 9AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 5 | 9AM to 10AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 5 | 10AM to 11AM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
September | 5 | 11AM to 12PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 5 | 12PM to 1PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
September | 5 | 1PM to 2PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 5 | 2PM to 3PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
September | 5 | 3PM to 4PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 5 | 4PM to 5PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 5 | 5PM to 6PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 5 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 5 | 7PM to 8PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 5 | 8PM to 9PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 5 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 5 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 5 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 6 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 6 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 6 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 6 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 6 | 4AM to 5AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
September | 6 | 5AM to 6AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
September | 6 | 6AM to 7AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 6 | 7AM to 8AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 6 | 8AM to 9AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 6 | 9AM to 10AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 6 | 10AM to 11AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 6 | 11AM to 12PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 6 | 12PM to 1PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
September | 6 | 1PM to 2PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
September | 6 | 2PM to 3PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
September | 6 | 3PM to 4PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
September | 6 | 4PM to 5PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
September | 6 | 5PM to 6PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 6 | 6PM to 7PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 6 | 7PM to 8PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 6 | 8PM to 9PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 6 | 9PM to 10PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 6 | 10PM to 11PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 6 | 11PM to 12AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 7 | 12AM to 1AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
September | 7 | 1AM to 2AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
September | 7 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
September | 7 | 3AM to 4AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
September | 7 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 7 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 7 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 7 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 7 | 8AM to 9AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
September | 7 | 9AM to 10AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
September | 7 | 10AM to 11AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 7 | 11AM to 12PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 7 | 12PM to 1PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 7 | 1PM to 2PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
September | 7 | 2PM to 3PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
September | 7 | 3PM to 4PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
September | 7 | 4PM to 5PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
September | 7 | 5PM to 6PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
September | 7 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 7 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 7 | 8PM to 9PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 7 | 9PM to 10PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 7 | 10PM to 11PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 7 | 11PM to 12AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 8 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 8 | 1AM to 2AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 8 | 2AM to 3AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 8 | 3AM to 4AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 8 | 4AM to 5AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 8 | 5AM to 6AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 8 | 6AM to 7AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 8 | 7AM to 8AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
September | 8 | 8AM to 9AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 8 | 9AM to 10AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
September | 8 | 10AM to 11AM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
September | 8 | 11AM to 12PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
September | 8 | 12PM to 1PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
September | 8 | 1PM to 2PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
September | 8 | 2PM to 3PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
September | 8 | 3PM to 4PM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
September | 8 | 4PM to 5PM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
September | 8 | 5PM to 6PM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
September | 8 | 6PM to 7PM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
September | 8 | 7PM to 8PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 8 | 8PM to 9PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 8 | 9PM to 10PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 8 | 10PM to 11PM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 8 | 11PM to 12AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 9 | 12AM to 1AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 9 | 1AM to 2AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 9 | 2AM to 3AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 9 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 9 | 4AM to 5AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 9 | 5AM to 6AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 9 | 6AM to 7AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
September | 9 | 7AM to 8AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 9 | 8AM to 9AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
September | 9 | 9AM to 10AM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 9 | 10AM to 11AM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 9 | 11AM to 12PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 9 | 12PM to 1PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 9 | 1PM to 2PM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
September | 9 | 2PM to 3PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 9 | 3PM to 4PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
September | 9 | 4PM to 5PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 9 | 5PM to 6PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 9 | 6PM to 7PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
September | 9 | 7PM to 8PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
September | 9 | 8PM to 9PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 9 | 9PM to 10PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 9 | 10PM to 11PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 9 | 11PM to 12AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 10 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 10 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 10 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 10 | 3AM to 4AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 10 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 10 | 5AM to 6AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 10 | 6AM to 7AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 10 | 7AM to 8AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 10 | 8AM to 9AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 10 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 10 | 10AM to 11AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
September | 10 | 11AM to 12PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
September | 10 | 12PM to 1PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 10 | 1PM to 2PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 10 | 2PM to 3PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
September | 10 | 3PM to 4PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
September | 10 | 4PM to 5PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 10 | 5PM to 6PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 10 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 10 | 7PM to 8PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 10 | 8PM to 9PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 10 | 9PM to 10PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 10 | 10PM to 11PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 10 | 11PM to 12AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 12AM to 1AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 1AM to 2AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 2AM to 3AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 3AM to 4AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 5AM to 6AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 6AM to 7AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 11 | 7AM to 8AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 11 | 8AM to 9AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
September | 11 | 9AM to 10AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 11 | 10AM to 11AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 11 | 11AM to 12PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 11 | 12PM to 1PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
September | 11 | 1PM to 2PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
September | 11 | 2PM to 3PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 11 | 3PM to 4PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 11 | 4PM to 5PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
September | 11 | 5PM to 6PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 11 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 11 | 7PM to 8PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 11 | 8PM to 9PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 9PM to 10PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 10PM to 11PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 11PM to 12AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 12 | 12AM to 1AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 12 | 1AM to 2AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 12 | 2AM to 3AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 12 | 3AM to 4AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 12 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 12 | 5AM to 6AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 12 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 12 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
September | 12 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
September | 12 | 9AM to 10AM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
September | 12 | 10AM to 11AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 12 | 11AM to 12PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 12 | 12PM to 1PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
September | 12 | 1PM to 2PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
September | 12 | 2PM to 3PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
September | 12 | 3PM to 4PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
September | 12 | 4PM to 5PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 12 | 5PM to 6PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
September | 12 | 6PM to 7PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
September | 12 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 12 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 12 | 9PM to 10PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
September | 12 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 12 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 13 | 12AM to 1AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 13 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 13 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 13 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
September | 13 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
September | 13 | 5AM to 6AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
September | 13 | 6AM to 7AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 13 | 7AM to 8AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
September | 13 | 8AM to 9AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 13 | 9AM to 10AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 13 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 13 | 11AM to 12PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
September | 13 | 12PM to 1PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
September | 13 | 1PM to 2PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
September | 13 | 2PM to 3PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
September | 13 | 3PM to 4PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
September | 13 | 4PM to 5PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
September | 13 | 5PM to 6PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
September | 13 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
September | 13 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 13 | 8PM to 9PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 13 | 9PM to 10PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 13 | 10PM to 11PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 13 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 14 | 12AM to 1AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 14 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 14 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 14 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 14 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 14 | 5AM to 6AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 14 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 14 | 7AM to 8AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 14 | 8AM to 9AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 14 | 9AM to 10AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 14 | 10AM to 11AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 14 | 11AM to 12PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 14 | 12PM to 1PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
September | 14 | 1PM to 2PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
September | 14 | 2PM to 3PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
September | 14 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 14 | 4PM to 5PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
September | 14 | 5PM to 6PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
September | 14 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 14 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 14 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 14 | 9PM to 10PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 14 | 10PM to 11PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
September | 14 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 15 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 15 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 15 | 2AM to 3AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 15 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 15 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 15 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
September | 15 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
September | 15 | 7AM to 8AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
September | 15 | 8AM to 9AM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
September | 15 | 9AM to 10AM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
September | 15 | 10AM to 11AM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
September | 15 | 11AM to 12PM | 75 | 65.2 | 60.1 | 77.8 | 30.17 | 0.0737 | 0.52 | 13.72 | 0
September | 15 | 12PM to 1PM | 80.1 | 63.7 | 54 | 62.2 | 28.96 | 0.0731 | 0.42 | 13.8 | 0
September | 15 | 1PM to 2PM | 86 | 64.4 | 51.1 | 55.9 | 29.41 | 0.0724 | 0.38 | 13.93 | 0
September | 15 | 2PM to 3PM | 84.9 | 65.3 | 54 | 62.2 | 30.14 | 0.0725 | 0.42 | 13.92 | 0
September | 15 | 3PM to 4PM | 79 | 61 | 48.9 | 51.5 | 27.02 | 0.0733 | 0.35 | 13.74 | 0
September | 15 | 4PM to 5PM | 79 | 59.8 | 46 | 46.1 | 26.18 | 0.0734 | 0.31 | 13.72 | 0
September | 15 | 5PM to 6PM | 77 | 59.4 | 46.9 | 47.8 | 25.95 | 0.0736 | 0.32 | 13.68 | 0
September | 15 | 6PM to 7PM | 75 | 58.3 | 46 | 46.1 | 25.22 | 0.0739 | 0.31 | 13.62 | 0
September | 15 | 7PM to 8PM | 71.1 | 57.7 | 48 | 49.8 | 24.82 | 0.0744 | 0.34 | 13.53 | 0
September | 15 | 8PM to 9PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
September | 15 | 9PM to 10PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 15 | 10PM to 11PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
September | 15 | 11PM to 12AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
September | 16 | 12AM to 1AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 16 | 1AM to 2AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
September | 16 | 2AM to 3AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 16 | 3AM to 4AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 16 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 16 | 5AM to 6AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 16 | 6AM to 7AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 16 | 7AM to 8AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
September | 16 | 8AM to 9AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
September | 16 | 9AM to 10AM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
September | 16 | 10AM to 11AM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
September | 16 | 11AM to 12PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
September | 16 | 12PM to 1PM | 86 | 64.4 | 51.1 | 55.9 | 29.41 | 0.0724 | 0.38 | 13.93 | 0
September | 16 | 1PM to 2PM | 84 | 63.2 | 50 | 53.6 | 28.58 | 0.0726 | 0.36 | 13.87 | 0
September | 16 | 2PM to 3PM | 84.9 | 63.1 | 48.9 | 51.5 | 28.46 | 0.0725 | 0.35 | 13.89 | 0
September | 16 | 3PM to 4PM | 77 | 61.3 | 51.1 | 55.9 | 27.22 | 0.0736 | 0.38 | 13.7 | 0
September | 16 | 4PM to 5PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
September | 16 | 5PM to 6PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 16 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 16 | 7PM to 8PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 16 | 8PM to 9PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 16 | 9PM to 10PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 16 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 16 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 17 | 12AM to 1AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 17 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 17 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 17 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 17 | 4AM to 5AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
September | 17 | 5AM to 6AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 17 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 17 | 7AM to 8AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
September | 17 | 8AM to 9AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
September | 17 | 9AM to 10AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 17 | 10AM to 11AM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 17 | 11AM to 12PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 17 | 12PM to 1PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 17 | 1PM to 2PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
September | 17 | 2PM to 3PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
September | 17 | 3PM to 4PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 17 | 4PM to 5PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 17 | 5PM to 6PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 17 | 6PM to 7PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 17 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 17 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 17 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 17 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 17 | 11PM to 12AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 18 | 12AM to 1AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 18 | 1AM to 2AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 18 | 2AM to 3AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 18 | 3AM to 4AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 18 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 18 | 5AM to 6AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 18 | 6AM to 7AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 18 | 7AM to 8AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 18 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
September | 18 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 18 | 10AM to 11AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 18 | 11AM to 12PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 18 | 12PM to 1PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
September | 18 | 1PM to 2PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 18 | 2PM to 3PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 18 | 3PM to 4PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 18 | 4PM to 5PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 18 | 5PM to 6PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 18 | 6PM to 7PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 18 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 18 | 8PM to 9PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 18 | 9PM to 10PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 18 | 10PM to 11PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 18 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 19 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 19 | 1AM to 2AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
September | 19 | 2AM to 3AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
September | 19 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 19 | 4AM to 5AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 19 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
September | 19 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 19 | 7AM to 8AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 19 | 8AM to 9AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 19 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 19 | 10AM to 11AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 19 | 11AM to 12PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
September | 19 | 12PM to 1PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
September | 19 | 1PM to 2PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 19 | 2PM to 3PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 19 | 3PM to 4PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
September | 19 | 4PM to 5PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 19 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 19 | 6PM to 7PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 19 | 7PM to 8PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 19 | 8PM to 9PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 19 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 19 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 19 | 11PM to 12AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 20 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 20 | 1AM to 2AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 20 | 2AM to 3AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 20 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 20 | 4AM to 5AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 20 | 5AM to 6AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 20 | 6AM to 7AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 20 | 7AM to 8AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 20 | 8AM to 9AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
September | 20 | 9AM to 10AM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 20 | 10AM to 11AM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 20 | 11AM to 12PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
September | 20 | 12PM to 1PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
September | 20 | 1PM to 2PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
September | 20 | 2PM to 3PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 20 | 3PM to 4PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
September | 20 | 4PM to 5PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 20 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 20 | 6PM to 7PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 20 | 7PM to 8PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 20 | 8PM to 9PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 20 | 9PM to 10PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 20 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 20 | 11PM to 12AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 21 | 12AM to 1AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 21 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 21 | 2AM to 3AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 21 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 21 | 4AM to 5AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 21 | 5AM to 6AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 21 | 6AM to 7AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 21 | 7AM to 8AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 21 | 8AM to 9AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 21 | 9AM to 10AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
September | 21 | 10AM to 11AM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 21 | 11AM to 12PM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 21 | 12PM to 1PM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
September | 21 | 1PM to 2PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
September | 21 | 2PM to 3PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
September | 21 | 3PM to 4PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 21 | 4PM to 5PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 21 | 5PM to 6PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 21 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 21 | 7PM to 8PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 21 | 8PM to 9PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 21 | 9PM to 10PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 21 | 10PM to 11PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 21 | 11PM to 12AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 22 | 12AM to 1AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 22 | 1AM to 2AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 22 | 2AM to 3AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 22 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 22 | 4AM to 5AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 22 | 5AM to 6AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 22 | 6AM to 7AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 22 | 7AM to 8AM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 22 | 8AM to 9AM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 22 | 9AM to 10AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 22 | 10AM to 11AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
September | 22 | 11AM to 12PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 22 | 12PM to 1PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
September | 22 | 1PM to 2PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
September | 22 | 2PM to 3PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 22 | 3PM to 4PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 22 | 4PM to 5PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 22 | 5PM to 6PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 22 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 22 | 7PM to 8PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 22 | 8PM to 9PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 22 | 9PM to 10PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 22 | 10PM to 11PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 22 | 11PM to 12AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 12AM to 1AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 1AM to 2AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 2AM to 3AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 3AM to 4AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 4AM to 5AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 23 | 5AM to 6AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 23 | 6AM to 7AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 23 | 7AM to 8AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
September | 23 | 8AM to 9AM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
September | 23 | 9AM to 10AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
September | 23 | 10AM to 11AM | 63 | 61.1 | 60.1 | 77.8 | 27.22 | 0.0754 | 0.52 | 13.41 | 0
September | 23 | 11AM to 12PM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
September | 23 | 12PM to 1PM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
September | 23 | 1PM to 2PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
September | 23 | 2PM to 3PM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
September | 23 | 3PM to 4PM | 78.1 | 65.1 | 57.9 | 72 | 30 | 0.0733 | 0.48 | 13.78 | 0
September | 23 | 4PM to 5PM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
September | 23 | 5PM to 6PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
September | 23 | 6PM to 7PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
September | 23 | 7PM to 8PM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 23 | 8PM to 9PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
September | 23 | 9PM to 10PM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
September | 23 | 10PM to 11PM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
September | 23 | 11PM to 12AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
September | 24 | 12AM to 1AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 24 | 1AM to 2AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
September | 24 | 2AM to 3AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 24 | 3AM to 4AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
September | 24 | 4AM to 5AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 24 | 5AM to 6AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 24 | 6AM to 7AM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
September | 24 | 7AM to 8AM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
September | 24 | 8AM to 9AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
September | 24 | 9AM to 10AM | 66.9 | 62.5 | 60.1 | 77.8 | 28.19 | 0.0748 | 0.52 | 13.51 | 0
September | 24 | 10AM to 11AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
September | 24 | 11AM to 12PM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
September | 24 | 12PM to 1PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
September | 24 | 1PM to 2PM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
September | 24 | 2PM to 3PM | 75 | 63.5 | 57 | 69.6 | 28.89 | 0.0738 | 0.47 | 13.69 | 0
September | 24 | 3PM to 4PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
September | 24 | 4PM to 5PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
September | 24 | 5PM to 6PM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 24 | 6PM to 7PM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
September | 24 | 7PM to 8PM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
September | 24 | 8PM to 9PM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
September | 24 | 9PM to 10PM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
September | 24 | 10PM to 11PM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
September | 24 | 11PM to 12AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 12AM to 1AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 1AM to 2AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
September | 25 | 2AM to 3AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 3AM to 4AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 4AM to 5AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 5AM to 6AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 6AM to 7AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 7AM to 8AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
September | 25 | 8AM to 9AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
September | 25 | 9AM to 10AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
September | 25 | 10AM to 11AM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
September | 25 | 11AM to 12PM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 25 | 12PM to 1PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
September | 25 | 1PM to 2PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
September | 25 | 2PM to 3PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
September | 25 | 3PM to 4PM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 25 | 4PM to 5PM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
September | 25 | 5PM to 6PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 25 | 6PM to 7PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 25 | 7PM to 8PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 25 | 8PM to 9PM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 25 | 9PM to 10PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 25 | 10PM to 11PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 25 | 11PM to 12AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 12AM to 1AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 1AM to 2AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 2AM to 3AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 3AM to 4AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 4AM to 5AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
September | 26 | 5AM to 6AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
September | 26 | 6AM to 7AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 7AM to 8AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 8AM to 9AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 26 | 9AM to 10AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 26 | 10AM to 11AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 26 | 11AM to 12PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 26 | 12PM to 1PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 26 | 1PM to 2PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 26 | 2PM to 3PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 26 | 3PM to 4PM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 26 | 4PM to 5PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 26 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 26 | 6PM to 7PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 26 | 7PM to 8PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 26 | 8PM to 9PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 26 | 9PM to 10PM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 26 | 10PM to 11PM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 26 | 11PM to 12AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 27 | 12AM to 1AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 1AM to 2AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 2AM to 3AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 27 | 3AM to 4AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 4AM to 5AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 5AM to 6AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 6AM to 7AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 27 | 7AM to 8AM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 27 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
September | 27 | 9AM to 10AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 27 | 10AM to 11AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 27 | 11AM to 12PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 27 | 12PM to 1PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
September | 27 | 1PM to 2PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
September | 27 | 2PM to 3PM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 27 | 3PM to 4PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 27 | 4PM to 5PM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
September | 27 | 5PM to 6PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 27 | 6PM to 7PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 27 | 7PM to 8PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 27 | 8PM to 9PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 27 | 9PM to 10PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 27 | 10PM to 11PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 27 | 11PM to 12AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 28 | 12AM to 1AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 28 | 1AM to 2AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 28 | 2AM to 3AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 28 | 3AM to 4AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 28 | 4AM to 5AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 28 | 5AM to 6AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 28 | 6AM to 7AM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 28 | 7AM to 8AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
September | 28 | 8AM to 9AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 28 | 9AM to 10AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 28 | 10AM to 11AM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 28 | 11AM to 12PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
September | 28 | 12PM to 1PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 28 | 1PM to 2PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
September | 28 | 2PM to 3PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
September | 28 | 3PM to 4PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
September | 28 | 4PM to 5PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
September | 28 | 5PM to 6PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 28 | 6PM to 7PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 28 | 7PM to 8PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 28 | 8PM to 9PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 28 | 9PM to 10PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 28 | 10PM to 11PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 28 | 11PM to 12AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 29 | 12AM to 1AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 29 | 1AM to 2AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 29 | 2AM to 3AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 29 | 3AM to 4AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 29 | 4AM to 5AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 29 | 5AM to 6AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 29 | 6AM to 7AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 29 | 7AM to 8AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
September | 29 | 8AM to 9AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 29 | 9AM to 10AM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 29 | 10AM to 11AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
September | 29 | 11AM to 12PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
September | 29 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
September | 29 | 1PM to 2PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
September | 29 | 2PM to 3PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 29 | 3PM to 4PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
September | 29 | 4PM to 5PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 29 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 29 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 29 | 7PM to 8PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 29 | 8PM to 9PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 29 | 9PM to 10PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 29 | 10PM to 11PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 29 | 11PM to 12AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 30 | 12AM to 1AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 30 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 30 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 30 | 3AM to 4AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
September | 30 | 4AM to 5AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 30 | 5AM to 6AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 30 | 6AM to 7AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 30 | 7AM to 8AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 30 | 8AM to 9AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 30 | 9AM to 10AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
September | 30 | 10AM to 11AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
September | 30 | 11AM to 12PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
September | 30 | 12PM to 1PM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
September | 30 | 1PM to 2PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 30 | 2PM to 3PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 30 | 3PM to 4PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 30 | 4PM to 5PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
September | 30 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 30 | 6PM to 7PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 30 | 7PM to 8PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 30 | 8PM to 9PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 30 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 30 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 30 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 1AM to 2AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 3AM to 4AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 4AM to 5AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
October | 1 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
October | 1 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
October | 1 | 7AM to 8AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 8AM to 9AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 9AM to 10AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 10AM to 11AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
October | 1 | 11AM to 12PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
October | 1 | 12PM to 1PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
October | 1 | 1PM to 2PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
October | 1 | 2PM to 3PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
October | 1 | 3PM to 4PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
October | 1 | 4PM to 5PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 5PM to 6PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 1 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 1 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 11PM to 12AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 2 | 12AM to 1AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 1AM to 2AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 2AM to 3AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 5AM to 6AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 6AM to 7AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
October | 2 | 7AM to 8AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
October | 2 | 8AM to 9AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
October | 2 | 9AM to 10AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 2 | 10AM to 11AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
October | 2 | 11AM to 12PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
October | 2 | 12PM to 1PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
October | 2 | 1PM to 2PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
October | 2 | 2PM to 3PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 2 | 3PM to 4PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
October | 2 | 4PM to 5PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 2 | 5PM to 6PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 2 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 2 | 7PM to 8PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 2 | 8PM to 9PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 2 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 2 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 2 | 11PM to 12AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 3 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 3 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 3 | 2AM to 3AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 3 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 3 | 4AM to 5AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 3 | 5AM to 6AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
October | 3 | 6AM to 7AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 3 | 7AM to 8AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 3 | 8AM to 9AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
October | 3 | 9AM to 10AM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
October | 3 | 10AM to 11AM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
October | 3 | 11AM to 12PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
October | 3 | 12PM to 1PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
October | 3 | 1PM to 2PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 3 | 2PM to 3PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
October | 3 | 3PM to 4PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
October | 3 | 4PM to 5PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
October | 3 | 5PM to 6PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 3 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
October | 3 | 7PM to 8PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 3 | 8PM to 9PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 3 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 3 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 3 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 4 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 4 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
October | 4 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 4 | 3AM to 4AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
October | 4 | 4AM to 5AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 4 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
October | 4 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 4 | 7AM to 8AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
October | 4 | 8AM to 9AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 4 | 9AM to 10AM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
October | 4 | 10AM to 11AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 4 | 11AM to 12PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
October | 4 | 12PM to 1PM | 71.1 | 56.8 | 46 | 46.1 | 24.26 | 0.0745 | 0.31 | 13.52 | 0
October | 4 | 1PM to 2PM | 70 | 57.7 | 48.9 | 51.5 | 24.83 | 0.0746 | 0.35 | 13.51 | 0
October | 4 | 2PM to 3PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
October | 4 | 3PM to 4PM | 66.9 | 56.1 | 48 | 49.8 | 23.81 | 0.075 | 0.34 | 13.42 | 0
October | 4 | 4PM to 5PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
October | 4 | 5PM to 6PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 4 | 6PM to 7PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 4 | 7PM to 8PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 4 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 4 | 9PM to 10PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 4 | 10PM to 11PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 4 | 11PM to 12AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 5 | 12AM to 1AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
October | 5 | 1AM to 2AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
October | 5 | 2AM to 3AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
October | 5 | 3AM to 4AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
October | 5 | 4AM to 5AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
October | 5 | 5AM to 6AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
October | 5 | 6AM to 7AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
October | 5 | 7AM to 8AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 5 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
October | 5 | 9AM to 10AM | 68 | 55.6 | 46 | 46.1 | 23.51 | 0.0749 | 0.31 | 13.44 | 0
October | 5 | 10AM to 11AM | 71.1 | 57.7 | 48 | 49.8 | 24.82 | 0.0744 | 0.34 | 13.53 | 0
October | 5 | 11AM to 12PM | 71.1 | 58.6 | 50 | 53.6 | 25.43 | 0.0744 | 0.36 | 13.54 | 0
October | 5 | 12PM to 1PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
October | 5 | 1PM to 2PM | 73.9 | 59.1 | 48.9 | 51.5 | 25.79 | 0.074 | 0.35 | 13.61 | 0
October | 5 | 2PM to 3PM | 77 | 59 | 46 | 46.1 | 25.7 | 0.0736 | 0.31 | 13.67 | 0
October | 5 | 3PM to 4PM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
October | 5 | 4PM to 5PM | 73.9 | 59.1 | 48.9 | 51.5 | 25.79 | 0.074 | 0.35 | 13.61 | 0
October | 5 | 5PM to 6PM | 71.1 | 57.7 | 48 | 49.8 | 24.82 | 0.0744 | 0.34 | 13.53 | 0
October | 5 | 6PM to 7PM | 71.1 | 56.3 | 45 | 44.3 | 23.96 | 0.0745 | 0.3 | 13.51 | 0
October | 5 | 7PM to 8PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
October | 5 | 8PM to 9PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
October | 5 | 9PM to 10PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 5 | 10PM to 11PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
October | 5 | 11PM to 12AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
October | 6 | 12AM to 1AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 6 | 1AM to 2AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
October | 6 | 2AM to 3AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
October | 6 | 3AM to 4AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 6 | 4AM to 5AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
October | 6 | 5AM to 6AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
October | 6 | 6AM to 7AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 6 | 7AM to 8AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 6 | 8AM to 9AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
October | 6 | 9AM to 10AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
October | 6 | 10AM to 11AM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
October | 6 | 11AM to 12PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
October | 6 | 12PM to 1PM | 72 | 57.5 | 46.9 | 47.8 | 24.73 | 0.0743 | 0.32 | 13.55 | 0
October | 6 | 1PM to 2PM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
October | 6 | 2PM to 3PM | 75.9 | 59.5 | 48 | 49.8 | 26 | 0.0738 | 0.34 | 13.65 | 0
October | 6 | 3PM to 4PM | 78.1 | 59.4 | 46 | 46.1 | 25.96 | 0.0735 | 0.31 | 13.7 | 0
October | 6 | 4PM to 5PM | 73 | 54.8 | 39 | 35.1 | 23.02 | 0.0742 | 0.24 | 13.54 | 0
October | 6 | 5PM to 6PM | 68 | 52.7 | 39 | 35.1 | 21.8 | 0.075 | 0.24 | 13.41 | 0
October | 6 | 6PM to 7PM | 64.9 | 53 | 43 | 41 | 21.97 | 0.0754 | 0.28 | 13.35 | 0
October | 6 | 7PM to 8PM | 64 | 51.8 | 41 | 38 | 21.28 | 0.0755 | 0.26 | 13.32 | 0
October | 6 | 8PM to 9PM | 63 | 50.6 | 39 | 35.1 | 20.58 | 0.0757 | 0.24 | 13.28 | 0
October | 6 | 9PM to 10PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
October | 6 | 10PM to 11PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
October | 6 | 11PM to 12AM | 60.1 | 50.6 | 42.1 | 39.6 | 20.57 | 0.0761 | 0.27 | 13.22 | 0
October | 7 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 7 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
October | 7 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 7 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 7 | 4AM to 5AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
October | 7 | 5AM to 6AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
October | 7 | 6AM to 7AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
October | 7 | 7AM to 8AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
October | 7 | 8AM to 9AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
October | 7 | 9AM to 10AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 7 | 10AM to 11AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
October | 7 | 11AM to 12PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
October | 7 | 12PM to 1PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
October | 7 | 1PM to 2PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
October | 7 | 2PM to 3PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
October | 7 | 3PM to 4PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
October | 7 | 4PM to 5PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
October | 7 | 5PM to 6PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 7 | 6PM to 7PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
October | 7 | 7PM to 8PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
October | 7 | 8PM to 9PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
October | 7 | 9PM to 10PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
October | 7 | 10PM to 11PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
October | 7 | 11PM to 12AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
October | 8 | 12AM to 1AM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
October | 8 | 1AM to 2AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 8 | 2AM to 3AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 8 | 3AM to 4AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
October | 8 | 4AM to 5AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 8 | 5AM to 6AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
October | 8 | 6AM to 7AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
October | 8 | 7AM to 8AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
October | 8 | 8AM to 9AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
October | 8 | 9AM to 10AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
October | 8 | 10AM to 11AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
October | 8 | 11AM to 12PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
October | 8 | 12PM to 1PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
October | 8 | 1PM to 2PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
October | 8 | 2PM to 3PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
October | 8 | 3PM to 4PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
October | 8 | 4PM to 5PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
October | 8 | 5PM to 6PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 8 | 6PM to 7PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 8 | 7PM to 8PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 8 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 8 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 8 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 8 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 9 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 9 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 9 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 7AM to 8AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 9 | 8AM to 9AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
October | 9 | 9AM to 10AM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
October | 9 | 10AM to 11AM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
October | 9 | 11AM to 12PM | 68 | 56.5 | 48 | 49.8 | 24.08 | 0.0749 | 0.34 | 13.45 | 0
October | 9 | 12PM to 1PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
October | 9 | 1PM to 2PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
October | 9 | 2PM to 3PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
October | 9 | 3PM to 4PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 9 | 4PM to 5PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
October | 9 | 5PM to 6PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 9 | 6PM to 7PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 9 | 7PM to 8PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
October | 9 | 8PM to 9PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 9 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 9 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 9 | 11PM to 12AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 10 | 12AM to 1AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 10 | 1AM to 2AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 10 | 2AM to 3AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 10 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 10 | 4AM to 5AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
October | 10 | 5AM to 6AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 10 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 10 | 7AM to 8AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
October | 10 | 8AM to 9AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 10 | 9AM to 10AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 10 | 10AM to 11AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
October | 10 | 11AM to 12PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 10 | 12PM to 1PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
October | 10 | 1PM to 2PM | 66 | 55.2 | 46.9 | 47.8 | 23.28 | 0.0752 | 0.32 | 13.4 | 0
October | 10 | 2PM to 3PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
October | 10 | 3PM to 4PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
October | 10 | 4PM to 5PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 10 | 5PM to 6PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
October | 10 | 6PM to 7PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 10 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 10 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 10 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 10 | 10PM to 11PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
October | 10 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 11 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 11 | 1AM to 2AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
October | 11 | 2AM to 3AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
October | 11 | 3AM to 4AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
October | 11 | 4AM to 5AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
October | 11 | 5AM to 6AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
October | 11 | 6AM to 7AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
October | 11 | 7AM to 8AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 11 | 8AM to 9AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 11 | 9AM to 10AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 11 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
October | 11 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
October | 11 | 12PM to 1PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
October | 11 | 1PM to 2PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
October | 11 | 2PM to 3PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
October | 11 | 3PM to 4PM | 64 | 53.5 | 45 | 44.3 | 22.26 | 0.0755 | 0.3 | 13.33 | 0
October | 11 | 4PM to 5PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
October | 11 | 5PM to 6PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
October | 11 | 6PM to 7PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
October | 11 | 7PM to 8PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
October | 11 | 8PM to 9PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
October | 11 | 9PM to 10PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
October | 11 | 10PM to 11PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 11 | 11PM to 12AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 12 | 12AM to 1AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 12 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 12 | 2AM to 3AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
October | 12 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 12 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 12 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 12 | 6AM to 7AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 12 | 7AM to 8AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 12 | 8AM to 9AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
October | 12 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
October | 12 | 10AM to 11AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
October | 12 | 11AM to 12PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
October | 12 | 12PM to 1PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
October | 12 | 1PM to 2PM | 70 | 57.2 | 48 | 49.8 | 24.56 | 0.0746 | 0.34 | 13.5 | 0
October | 12 | 2PM to 3PM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
October | 12 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
October | 12 | 4PM to 5PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
October | 12 | 5PM to 6PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 12 | 6PM to 7PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
October | 12 | 7PM to 8PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
October | 12 | 8PM to 9PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
October | 12 | 9PM to 10PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
October | 12 | 10PM to 11PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
October | 12 | 11PM to 12AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
October | 13 | 12AM to 1AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
October | 13 | 1AM to 2AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
October | 13 | 2AM to 3AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
October | 13 | 3AM to 4AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
October | 13 | 4AM to 5AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
October | 13 | 5AM to 6AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
October | 13 | 6AM to 7AM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
October | 13 | 7AM to 8AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
October | 13 | 8AM to 9AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
October | 13 | 9AM to 10AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
October | 13 | 10AM to 11AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
October | 13 | 11AM to 12PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
October | 13 | 12PM to 1PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
October | 13 | 1PM to 2PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
October | 13 | 2PM to 3PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
October | 13 | 3PM to 4PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
October | 13 | 4PM to 5PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
October | 13 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
October | 13 | 6PM to 7PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 13 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 13 | 8PM to 9PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
October | 13 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
October | 13 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 13 | 11PM to 12AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 14 | 12AM to 1AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 14 | 1AM to 2AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
October | 14 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 14 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 14 | 4AM to 5AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 14 | 5AM to 6AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
October | 14 | 6AM to 7AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 14 | 7AM to 8AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
October | 14 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 14 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
October | 14 | 10AM to 11AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
October | 14 | 11AM to 12PM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
October | 14 | 12PM to 1PM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
October | 14 | 1PM to 2PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 14 | 2PM to 3PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
October | 14 | 3PM to 4PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 14 | 4PM to 5PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 14 | 5PM to 6PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 14 | 6PM to 7PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 14 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 14 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 14 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 14 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 14 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 15 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 15 | 1AM to 2AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 15 | 2AM to 3AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
October | 15 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 15 | 4AM to 5AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
October | 15 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
October | 15 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 15 | 7AM to 8AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 15 | 8AM to 9AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 15 | 9AM to 10AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 15 | 10AM to 11AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 15 | 11AM to 12PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
October | 15 | 12PM to 1PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
October | 15 | 1PM to 2PM | 64.9 | 53 | 43 | 41 | 21.97 | 0.0754 | 0.28 | 13.35 | 0
October | 15 | 2PM to 3PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
October | 15 | 3PM to 4PM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
October | 15 | 4PM to 5PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 15 | 5PM to 6PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 15 | 6PM to 7PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 15 | 7PM to 8PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 15 | 8PM to 9PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 15 | 9PM to 10PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
October | 15 | 10PM to 11PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
October | 15 | 11PM to 12AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
October | 16 | 12AM to 1AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
October | 16 | 1AM to 2AM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
October | 16 | 2AM to 3AM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
October | 16 | 3AM to 4AM | 59 | 48.4 | 37.9 | 33.7 | 19.39 | 0.0763 | 0.23 | 13.17 | 0
October | 16 | 4AM to 5AM | 59 | 48.8 | 39 | 35.1 | 19.62 | 0.0763 | 0.24 | 13.18 | 0
October | 16 | 5AM to 6AM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
October | 16 | 6AM to 7AM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
October | 16 | 7AM to 8AM | 62.1 | 50.2 | 39 | 35.1 | 20.36 | 0.0758 | 0.24 | 13.26 | 0
October | 16 | 8AM to 9AM | 63 | 50.2 | 37.9 | 33.7 | 20.35 | 0.0757 | 0.23 | 13.28 | 0
October | 16 | 9AM to 10AM | 64 | 50.7 | 37.9 | 33.7 | 20.61 | 0.0755 | 0.23 | 13.3 | 0
October | 16 | 10AM to 11AM | 66 | 51.9 | 39 | 35.1 | 21.32 | 0.0752 | 0.24 | 13.36 | 0
October | 16 | 11AM to 12PM | 66.9 | 51.2 | 36 | 31.1 | 20.91 | 0.0751 | 0.21 | 13.37 | 0
October | 16 | 12PM to 1PM | 69.1 | 52.1 | 36 | 31.1 | 21.43 | 0.0748 | 0.21 | 13.42 | 0
October | 16 | 1PM to 2PM | 71.1 | 53 | 36 | 31.1 | 21.91 | 0.0746 | 0.21 | 13.47 | 0
October | 16 | 2PM to 3PM | 70 | 52.2 | 35.1 | 30 | 21.48 | 0.0747 | 0.2 | 13.44 | 0
October | 16 | 3PM to 4PM | 69.1 | 52.5 | 37 | 32.5 | 21.65 | 0.0748 | 0.22 | 13.43 | 0
October | 16 | 4PM to 5PM | 66.9 | 51.9 | 37.9 | 33.7 | 21.31 | 0.0751 | 0.23 | 13.38 | 0
October | 16 | 5PM to 6PM | 63 | 50.6 | 39 | 35.1 | 20.58 | 0.0757 | 0.24 | 13.28 | 0
October | 16 | 6PM to 7PM | 63 | 50.2 | 37.9 | 33.7 | 20.35 | 0.0757 | 0.23 | 13.28 | 0
October | 16 | 7PM to 8PM | 66.9 | 51.2 | 36 | 31.1 | 20.91 | 0.0751 | 0.21 | 13.37 | 0
October | 16 | 8PM to 9PM | 66.9 | 48.9 | 28.9 | 23 | 19.65 | 0.0752 | 0.16 | 13.34 | 0
October | 16 | 9PM to 10PM | 66 | 50.5 | 35.1 | 30 | 20.52 | 0.0753 | 0.2 | 13.34 | 0
October | 16 | 10PM to 11PM | 64.9 | 51 | 37.9 | 33.7 | 20.83 | 0.0754 | 0.23 | 13.33 | 0
October | 16 | 11PM to 12AM | 64 | 49 | 33.1 | 27.7 | 19.68 | 0.0756 | 0.19 | 13.28 | 0
October | 17 | 12AM to 1AM | 62.1 | 49.1 | 36 | 31.1 | 19.73 | 0.0758 | 0.21 | 13.24 | 0
October | 17 | 1AM to 2AM | 55.9 | 44.5 | 30.9 | 25.2 | 17.34 | 0.0768 | 0.17 | 13.07 | 0
October | 17 | 2AM to 3AM | 55.9 | 44.5 | 30.9 | 25.2 | 17.34 | 0.0768 | 0.17 | 13.07 | 0
October | 17 | 3AM to 4AM | 60.1 | 45.8 | 28.9 | 23 | 18 | 0.0762 | 0.16 | 13.17 | 0
October | 17 | 4AM to 5AM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
October | 17 | 5AM to 6AM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
October | 17 | 6AM to 7AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
October | 17 | 7AM to 8AM | 61 | 50.5 | 41 | 38 | 20.54 | 0.0759 | 0.26 | 13.24 | 0
October | 17 | 8AM to 9AM | 64 | 48.6 | 32 | 26.5 | 19.5 | 0.0756 | 0.18 | 13.28 | 0
October | 17 | 9AM to 10AM | 66 | 49.5 | 32 | 26.5 | 19.98 | 0.0753 | 0.18 | 13.33 | 0
October | 17 | 10AM to 11AM | 69.1 | 51.2 | 33.1 | 27.7 | 20.9 | 0.0749 | 0.19 | 13.41 | 0
October | 17 | 11AM to 12PM | 70 | 51.3 | 32 | 26.5 | 20.94 | 0.0747 | 0.18 | 13.43 | 0
October | 17 | 12PM to 1PM | 72 | 52.4 | 33.1 | 27.7 | 21.6 | 0.0744 | 0.19 | 13.49 | 0
October | 17 | 1PM to 2PM | 72 | 54.7 | 39.9 | 36.4 | 22.95 | 0.0744 | 0.25 | 13.51 | 0
October | 17 | 2PM to 3PM | 70 | 52.5 | 36 | 31.1 | 21.65 | 0.0747 | 0.21 | 13.45 | 0
October | 17 | 3PM to 4PM | 66 | 51.9 | 39 | 35.1 | 21.32 | 0.0752 | 0.24 | 13.36 | 0
October | 17 | 4PM to 5PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
October | 17 | 5PM to 6PM | 62.1 | 49.5 | 37 | 32.5 | 19.95 | 0.0758 | 0.22 | 13.25 | 0
October | 17 | 6PM to 7PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
October | 17 | 7PM to 8PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
October | 17 | 8PM to 9PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 17 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 17 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 17 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 18 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 18 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
October | 18 | 2AM to 3AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
October | 18 | 3AM to 4AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
October | 18 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
October | 18 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
October | 18 | 6AM to 7AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
October | 18 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 18 | 8AM to 9AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 18 | 9AM to 10AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 18 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
October | 18 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
October | 18 | 12PM to 1PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
October | 18 | 1PM to 2PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
October | 18 | 2PM to 3PM | 66.9 | 56.1 | 48 | 49.8 | 23.81 | 0.075 | 0.34 | 13.42 | 0
October | 18 | 3PM to 4PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
October | 18 | 4PM to 5PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 18 | 5PM to 6PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 18 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 18 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 18 | 8PM to 9PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
October | 18 | 9PM to 10PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
October | 18 | 10PM to 11PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 18 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 19 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 19 | 1AM to 2AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
October | 19 | 2AM to 3AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
October | 19 | 3AM to 4AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
October | 19 | 4AM to 5AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
October | 19 | 5AM to 6AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
October | 19 | 6AM to 7AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
October | 19 | 7AM to 8AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 19 | 8AM to 9AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 19 | 9AM to 10AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
October | 19 | 10AM to 11AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
October | 19 | 11AM to 12PM | 69.1 | 54.4 | 42.1 | 39.6 | 22.76 | 0.0748 | 0.27 | 13.45 | 0
October | 19 | 12PM to 1PM | 75.9 | 56.7 | 41 | 38 | 24.16 | 0.0738 | 0.26 | 13.62 | 0
October | 19 | 1PM to 2PM | 75.9 | 57.4 | 43 | 41 | 24.63 | 0.0738 | 0.28 | 13.63 | 0
October | 19 | 2PM to 3PM | 78.1 | 58.7 | 44.1 | 42.8 | 25.43 | 0.0735 | 0.29 | 13.69 | 0
October | 19 | 3PM to 4PM | 72 | 54.4 | 39 | 35.1 | 22.76 | 0.0744 | 0.24 | 13.51 | 0
October | 19 | 4PM to 5PM | 70 | 54.7 | 42.1 | 39.6 | 22.97 | 0.0746 | 0.27 | 13.47 | 0
October | 19 | 5PM to 6PM | 68 | 51.7 | 36 | 31.1 | 21.17 | 0.075 | 0.21 | 13.4 | 0
October | 19 | 6PM to 7PM | 68 | 52.4 | 37.9 | 33.7 | 21.57 | 0.075 | 0.23 | 13.4 | 0
October | 19 | 7PM to 8PM | 64.9 | 53.5 | 44.1 | 42.8 | 22.24 | 0.0753 | 0.29 | 13.35 | 0
October | 19 | 8PM to 9PM | 64 | 51.1 | 39 | 35.1 | 20.84 | 0.0755 | 0.24 | 13.31 | 0
October | 19 | 9PM to 10PM | 64 | 50.7 | 37.9 | 33.7 | 20.61 | 0.0755 | 0.23 | 13.3 | 0
October | 19 | 10PM to 11PM | 60.1 | 50.6 | 42.1 | 39.6 | 20.57 | 0.0761 | 0.27 | 13.22 | 0
October | 19 | 11PM to 12AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
October | 20 | 12AM to 1AM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
October | 20 | 1AM to 2AM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
October | 20 | 2AM to 3AM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
October | 20 | 3AM to 4AM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
October | 20 | 4AM to 5AM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
October | 20 | 5AM to 6AM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
October | 20 | 6AM to 7AM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
October | 20 | 7AM to 8AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 20 | 8AM to 9AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 20 | 9AM to 10AM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
October | 20 | 10AM to 11AM | 73.9 | 53 | 32 | 26.5 | 21.89 | 0.0742 | 0.18 | 13.53 | 0
October | 20 | 11AM to 12PM | 75.9 | 54.7 | 35.1 | 30 | 22.92 | 0.0739 | 0.2 | 13.59 | 0
October | 20 | 12PM to 1PM | 78.1 | 55.8 | 36 | 31.1 | 23.61 | 0.0736 | 0.21 | 13.65 | 0
October | 20 | 1PM to 2PM | 80.1 | 57.2 | 37.9 | 33.7 | 24.49 | 0.0733 | 0.23 | 13.71 | 0
October | 20 | 2PM to 3PM | 79 | 58.6 | 43 | 41 | 25.38 | 0.0734 | 0.28 | 13.71 | 0
October | 20 | 3PM to 4PM | 77 | 55.4 | 36 | 31.1 | 23.35 | 0.0737 | 0.21 | 13.62 | 0
October | 20 | 4PM to 5PM | 73.9 | 53.3 | 33.1 | 27.7 | 22.08 | 0.0742 | 0.19 | 13.54 | 0
October | 20 | 5PM to 6PM | 70 | 51.9 | 34 | 28.7 | 21.28 | 0.0747 | 0.2 | 13.44 | 0
October | 20 | 6PM to 7PM | 69.1 | 52.5 | 37 | 32.5 | 21.65 | 0.0748 | 0.22 | 13.43 | 0
October | 20 | 7PM to 8PM | 68 | 51.7 | 36 | 31.1 | 21.17 | 0.075 | 0.21 | 13.4 | 0
October | 20 | 8PM to 9PM | 64.9 | 51.8 | 39.9 | 36.4 | 21.25 | 0.0754 | 0.25 | 13.33 | 0
October | 20 | 9PM to 10PM | 64.9 | 51.4 | 39 | 35.1 | 21.06 | 0.0754 | 0.24 | 13.33 | 0
October | 20 | 10PM to 11PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
October | 20 | 11PM to 12AM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
October | 21 | 12AM to 1AM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
October | 21 | 1AM to 2AM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
October | 21 | 2AM to 3AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
October | 21 | 3AM to 4AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 21 | 4AM to 5AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
October | 21 | 5AM to 6AM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
October | 21 | 6AM to 7AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
October | 21 | 7AM to 8AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
October | 21 | 8AM to 9AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
October | 21 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
October | 21 | 10AM to 11AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
October | 21 | 11AM to 12PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
October | 21 | 12PM to 1PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
October | 21 | 1PM to 2PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
October | 21 | 2PM to 3PM | 77 | 59 | 46 | 46.1 | 25.7 | 0.0736 | 0.31 | 13.67 | 0
October | 21 | 3PM to 4PM | 73 | 57.9 | 46.9 | 47.8 | 24.99 | 0.0742 | 0.32 | 13.57 | 0
October | 21 | 4PM to 5PM | 68 | 55.6 | 46 | 46.1 | 23.51 | 0.0749 | 0.31 | 13.44 | 0
October | 21 | 5PM to 6PM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
October | 21 | 6PM to 7PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
October | 21 | 7PM to 8PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
October | 21 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 21 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 21 | 10PM to 11PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 21 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 22 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
October | 22 | 1AM to 2AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
October | 22 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
October | 22 | 3AM to 4AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
October | 22 | 4AM to 5AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
October | 22 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
October | 22 | 6AM to 7AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 22 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
October | 22 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 22 | 9AM to 10AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 22 | 10AM to 11AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 22 | 11AM to 12PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 22 | 12PM to 1PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 22 | 1PM to 2PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
October | 22 | 2PM to 3PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 22 | 3PM to 4PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 22 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 22 | 5PM to 6PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 22 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 22 | 7PM to 8PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 22 | 8PM to 9PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 22 | 9PM to 10PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 22 | 10PM to 11PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 22 | 11PM to 12AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
October | 23 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 23 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
October | 23 | 2AM to 3AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
October | 23 | 3AM to 4AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
October | 23 | 4AM to 5AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
October | 23 | 5AM to 6AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
October | 23 | 6AM to 7AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
October | 23 | 7AM to 8AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 23 | 8AM to 9AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 23 | 9AM to 10AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 23 | 10AM to 11AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 23 | 11AM to 12PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 23 | 12PM to 1PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 23 | 1PM to 2PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
October | 23 | 2PM to 3PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 23 | 3PM to 4PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
October | 23 | 4PM to 5PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 23 | 5PM to 6PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 23 | 6PM to 7PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
October | 23 | 7PM to 8PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 23 | 8PM to 9PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 23 | 9PM to 10PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 23 | 10PM to 11PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 23 | 11PM to 12AM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 24 | 12AM to 1AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
October | 24 | 1AM to 2AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
October | 24 | 2AM to 3AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
October | 24 | 3AM to 4AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 24 | 4AM to 5AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 24 | 5AM to 6AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 24 | 6AM to 7AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 24 | 7AM to 8AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
October | 24 | 8AM to 9AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
October | 24 | 9AM to 10AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
October | 24 | 10AM to 11AM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
October | 24 | 11AM to 12PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
October | 24 | 12PM to 1PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 24 | 1PM to 2PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 24 | 2PM to 3PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
October | 24 | 3PM to 4PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
October | 24 | 4PM to 5PM | 61.3 | 57.1 | 54.3 | 63 | 24.52 | 0.0757 | 0.43 | 13.32 | 0
October | 24 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
October | 24 | 6PM to 7PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 24 | 7PM to 8PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 24 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 24 | 9PM to 10PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 24 | 10PM to 11PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 24 | 11PM to 12AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 25 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
October | 25 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 25 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
October | 25 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 25 | 4AM to 5AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
October | 25 | 5AM to 6AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
October | 25 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 25 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 25 | 8AM to 9AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 25 | 9AM to 10AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 25 | 10AM to 11AM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
October | 25 | 11AM to 12PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 25 | 12PM to 1PM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
October | 25 | 1PM to 2PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
October | 25 | 2PM to 3PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
October | 25 | 3PM to 4PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 25 | 4PM to 5PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 25 | 5PM to 6PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 25 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 25 | 7PM to 8PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 25 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 25 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 25 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 25 | 11PM to 12AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 26 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 26 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 26 | 2AM to 3AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
October | 26 | 3AM to 4AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
October | 26 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
October | 26 | 5AM to 6AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
October | 26 | 6AM to 7AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 26 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 26 | 8AM to 9AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 26 | 9AM to 10AM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
October | 26 | 10AM to 11AM | 64.9 | 54.8 | 46.9 | 47.8 | 23.02 | 0.0753 | 0.32 | 13.37 | 0
October | 26 | 11AM to 12PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
October | 26 | 12PM to 1PM | 70 | 56.4 | 46 | 46.1 | 23.99 | 0.0746 | 0.31 | 13.49 | 0
October | 26 | 1PM to 2PM | 72 | 58 | 48 | 49.8 | 25.04 | 0.0743 | 0.34 | 13.55 | 0
October | 26 | 2PM to 3PM | 73 | 58.4 | 48 | 49.8 | 25.3 | 0.0742 | 0.34 | 13.58 | 0
October | 26 | 3PM to 4PM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
October | 26 | 4PM to 5PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
October | 26 | 5PM to 6PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
October | 26 | 6PM to 7PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
October | 26 | 7PM to 8PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 26 | 8PM to 9PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 26 | 9PM to 10PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 26 | 10PM to 11PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 26 | 11PM to 12AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 27 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
October | 27 | 1AM to 2AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 27 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 27 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 27 | 4AM to 5AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 27 | 5AM to 6AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
October | 27 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 27 | 7AM to 8AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 27 | 8AM to 9AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 27 | 9AM to 10AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 27 | 10AM to 11AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
October | 27 | 11AM to 12PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
October | 27 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
October | 27 | 1PM to 2PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
October | 27 | 2PM to 3PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 27 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 27 | 4PM to 5PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 27 | 5PM to 6PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 27 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 27 | 7PM to 8PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 27 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 27 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 27 | 10PM to 11PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 27 | 11PM to 12AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 28 | 12AM to 1AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 28 | 1AM to 2AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 28 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 28 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 28 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 28 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 28 | 6AM to 7AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 28 | 7AM to 8AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
October | 28 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 28 | 9AM to 10AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 28 | 10AM to 11AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
October | 28 | 11AM to 12PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 28 | 12PM to 1PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 28 | 1PM to 2PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 28 | 2PM to 3PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 28 | 3PM to 4PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 28 | 4PM to 5PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 28 | 5PM to 6PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 28 | 6PM to 7PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 28 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 28 | 8PM to 9PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 28 | 9PM to 10PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 28 | 10PM to 11PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 28 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 29 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
October | 29 | 1AM to 2AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 29 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 29 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 29 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 29 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 29 | 6AM to 7AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
October | 29 | 7AM to 8AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 29 | 8AM to 9AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 29 | 9AM to 10AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 29 | 10AM to 11AM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
October | 29 | 11AM to 12PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
October | 29 | 12PM to 1PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
October | 29 | 1PM to 2PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
October | 29 | 2PM to 3PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
October | 29 | 3PM to 4PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
October | 29 | 4PM to 5PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 29 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
October | 29 | 6PM to 7PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
October | 29 | 7PM to 8PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
October | 29 | 8PM to 9PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
October | 29 | 9PM to 10PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
October | 29 | 10PM to 11PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
October | 29 | 11PM to 12AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
October | 30 | 12AM to 1AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
October | 30 | 1AM to 2AM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
October | 30 | 2AM to 3AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
October | 30 | 3AM to 4AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
October | 30 | 4AM to 5AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
October | 30 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
October | 30 | 6AM to 7AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
October | 30 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
October | 30 | 8AM to 9AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 30 | 9AM to 10AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 30 | 10AM to 11AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 30 | 11AM to 12PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 30 | 12PM to 1PM | 64 | 53.5 | 45 | 44.3 | 22.26 | 0.0755 | 0.3 | 13.33 | 0
October | 30 | 1PM to 2PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
October | 30 | 2PM to 3PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
October | 30 | 3PM to 4PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
October | 30 | 4PM to 5PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
October | 30 | 5PM to 6PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
October | 30 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
October | 30 | 7PM to 8PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
October | 30 | 8PM to 9PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
October | 30 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 30 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 30 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
October | 31 | 12AM to 1AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
October | 31 | 1AM to 2AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
October | 31 | 2AM to 3AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
October | 31 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
October | 31 | 4AM to 5AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
October | 31 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
October | 31 | 6AM to 7AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
October | 31 | 7AM to 8AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
October | 31 | 8AM to 9AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 31 | 9AM to 10AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 31 | 10AM to 11AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 31 | 11AM to 12PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 31 | 12PM to 1PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
October | 31 | 1PM to 2PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 31 | 2PM to 3PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 31 | 3PM to 4PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 31 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 31 | 5PM to 6PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 31 | 6PM to 7PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 31 | 7PM to 8PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 31 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 31 | 9PM to 10PM | 55.6 | 52.4 | 50 | 53.6 | 21.66 | 0.0766 | 0.36 | 13.15 | 0
October | 31 | 10PM to 11PM | 55.4 | 51.7 | 48.7 | 51.1 | 21.23 | 0.0767 | 0.35 | 13.14 | 0
October | 31 | 11PM to 12AM | 55 | 51 | 47.7 | 49.1 | 20.82 | 0.0768 | 0.33 | 13.12 | 0
November | 1 | 12AM to 1AM | 54.9 | 50.3 | 46.4 | 46.8 | 20.42 | 0.0768 | 0.32 | 13.11 | 0
November | 1 | 1AM to 2AM | 54.5 | 49.6 | 45.3 | 44.9 | 20.04 | 0.0769 | 0.3 | 13.09 | 0
November | 1 | 2AM to 3AM | 54.3 | 48.9 | 44.1 | 42.8 | 19.67 | 0.0769 | 0.29 | 13.08 | 0
November | 1 | 3AM to 4AM | 54 | 48.2 | 43 | 41 | 19.31 | 0.077 | 0.28 | 13.07 | 0
November | 1 | 4AM to 5AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
November | 1 | 5AM to 6AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
November | 1 | 6AM to 7AM | 50 | 43.8 | 37 | 32.5 | 17.03 | 0.0776 | 0.22 | 12.94 | 1
November | 1 | 7AM to 8AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
November | 1 | 8AM to 9AM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
November | 1 | 9AM to 10AM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
November | 1 | 10AM to 11AM | 63 | 49.5 | 36 | 31.1 | 19.95 | 0.0757 | 0.21 | 13.27 | 0
November | 1 | 11AM to 12PM | 64.9 | 49.7 | 34 | 28.7 | 20.06 | 0.0754 | 0.2 | 13.31 | 0
November | 1 | 12PM to 1PM | 68 | 51.4 | 35.1 | 30 | 21 | 0.075 | 0.2 | 13.39 | 0
November | 1 | 1PM to 2PM | 69.1 | 51.8 | 35.1 | 30 | 21.26 | 0.0748 | 0.2 | 13.42 | 0
November | 1 | 2PM to 3PM | 69.1 | 50.9 | 32 | 26.5 | 20.72 | 0.0749 | 0.18 | 13.41 | 0
November | 1 | 3PM to 4PM | 69.1 | 51.2 | 33.1 | 27.7 | 20.9 | 0.0749 | 0.19 | 13.41 | 0
November | 1 | 4PM to 5PM | 64 | 52.3 | 42.1 | 39.6 | 21.53 | 0.0755 | 0.27 | 13.32 | 0
November | 1 | 5PM to 6PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
November | 1 | 6PM to 7PM | 60.1 | 48.9 | 37.9 | 33.7 | 19.65 | 0.0761 | 0.23 | 13.2 | 0
November | 1 | 7PM to 8PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
November | 1 | 8PM to 9PM | 59 | 47.3 | 35.1 | 30 | 18.82 | 0.0763 | 0.2 | 13.16 | 0
November | 1 | 9PM to 10PM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
November | 1 | 10PM to 11PM | 55.9 | 46.6 | 37 | 32.5 | 18.46 | 0.0767 | 0.22 | 13.09 | 0
November | 1 | 11PM to 12AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
November | 2 | 12AM to 1AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
November | 2 | 1AM to 2AM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
November | 2 | 2AM to 3AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
November | 2 | 3AM to 4AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
November | 2 | 4AM to 5AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
November | 2 | 5AM to 6AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
November | 2 | 6AM to 7AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
November | 2 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 2 | 8AM to 9AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 2 | 9AM to 10AM | 59 | 50.5 | 43 | 41 | 20.53 | 0.0762 | 0.28 | 13.2 | 0
November | 2 | 10AM to 11AM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
November | 2 | 11AM to 12PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
November | 2 | 12PM to 1PM | 64 | 53.5 | 45 | 44.3 | 22.26 | 0.0755 | 0.3 | 13.33 | 0
November | 2 | 1PM to 2PM | 64.9 | 53 | 43 | 41 | 21.97 | 0.0754 | 0.28 | 13.35 | 0
November | 2 | 2PM to 3PM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
November | 2 | 3PM to 4PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
November | 2 | 4PM to 5PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
November | 2 | 5PM to 6PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
November | 2 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 2 | 7PM to 8PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 2 | 8PM to 9PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
November | 2 | 9PM to 10PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
November | 2 | 10PM to 11PM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 2 | 11PM to 12AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 3 | 12AM to 1AM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
November | 3 | 1AM to 2AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
November | 3 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 3 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 3 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 3 | 5AM to 6AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 3 | 6AM to 7AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
November | 3 | 7AM to 8AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
November | 3 | 8AM to 9AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
November | 3 | 9AM to 10AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 3 | 10AM to 11AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 3 | 11AM to 12PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
November | 3 | 12PM to 1PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
November | 3 | 1PM to 2PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 3 | 2PM to 3PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
November | 3 | 3PM to 4PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
November | 3 | 4PM to 5PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
November | 3 | 5PM to 6PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
November | 3 | 6PM to 7PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
November | 3 | 7PM to 8PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
November | 3 | 8PM to 9PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 3 | 9PM to 10PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
November | 3 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
November | 3 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
November | 4 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
November | 4 | 1AM to 2AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
November | 4 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
November | 4 | 3AM to 4AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
November | 4 | 4AM to 5AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
November | 4 | 5AM to 6AM | 48 | 47.4 | 46.9 | 47.8 | 18.91 | 0.0778 | 0.32 | 12.94 | 1
November | 4 | 6AM to 7AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
November | 4 | 7AM to 8AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
November | 4 | 8AM to 9AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
November | 4 | 9AM to 10AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
November | 4 | 10AM to 11AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 4 | 11AM to 12PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
November | 4 | 12PM to 1PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
November | 4 | 1PM to 2PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 4 | 2PM to 3PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 4 | 3PM to 4PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 4 | 4PM to 5PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
November | 4 | 5PM to 6PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 4 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 4 | 7PM to 8PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 4 | 8PM to 9PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 4 | 9PM to 10PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 4 | 10PM to 11PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 4 | 11PM to 12AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
November | 5 | 12AM to 1AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 5 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 5 | 2AM to 3AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 5 | 3AM to 4AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
November | 5 | 4AM to 5AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
November | 5 | 5AM to 6AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
November | 5 | 6AM to 7AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
November | 5 | 7AM to 8AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
November | 5 | 8AM to 9AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
November | 5 | 9AM to 10AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
November | 5 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
November | 5 | 11AM to 12PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
November | 5 | 12PM to 1PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
November | 5 | 1PM to 2PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
November | 5 | 2PM to 3PM | 64 | 52.6 | 43 | 41 | 21.75 | 0.0755 | 0.28 | 13.32 | 0
November | 5 | 3PM to 4PM | 62.1 | 49.8 | 37.9 | 33.7 | 20.13 | 0.0758 | 0.23 | 13.25 | 0
November | 5 | 4PM to 5PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
November | 5 | 5PM to 6PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
November | 5 | 6PM to 7PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 5 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 5 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 5 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
November | 5 | 10PM to 11PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 5 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
November | 6 | 12AM to 1AM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
November | 6 | 1AM to 2AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
November | 6 | 2AM to 3AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
November | 6 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 6 | 4AM to 5AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
November | 6 | 5AM to 6AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 6 | 6AM to 7AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 6 | 7AM to 8AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
November | 6 | 8AM to 9AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 6 | 9AM to 10AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 6 | 10AM to 11AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 6 | 11AM to 12PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 6 | 12PM to 1PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 6 | 1PM to 2PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
November | 6 | 2PM to 3PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 6 | 3PM to 4PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 6 | 4PM to 5PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 6 | 5PM to 6PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 6 | 6PM to 7PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 6 | 7PM to 8PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
November | 6 | 8PM to 9PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
November | 6 | 9PM to 10PM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
November | 6 | 10PM to 11PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
November | 6 | 11PM to 12AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 7 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 7 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 7 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 7 | 8AM to 9AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 7 | 9AM to 10AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
November | 7 | 10AM to 11AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 7 | 11AM to 12PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 7 | 12PM to 1PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 7 | 1PM to 2PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
November | 7 | 2PM to 3PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
November | 7 | 3PM to 4PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
November | 7 | 4PM to 5PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 7 | 5PM to 6PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
November | 7 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 7 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 7 | 8PM to 9PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 7 | 9PM to 10PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 7 | 10PM to 11PM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
November | 7 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 8 | 12AM to 1AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 8 | 1AM to 2AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 8 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 8 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 8 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 8 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 8 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 8 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 8 | 8AM to 9AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
November | 8 | 9AM to 10AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 8 | 10AM to 11AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
November | 8 | 11AM to 12PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 8 | 12PM to 1PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 8 | 1PM to 2PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 8 | 2PM to 3PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 8 | 3PM to 4PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 8 | 4PM to 5PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 8 | 5PM to 6PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 8 | 6PM to 7PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 8 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 8 | 8PM to 9PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
November | 8 | 9PM to 10PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 8 | 10PM to 11PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
November | 8 | 11PM to 12AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
November | 9 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 9 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 9 | 2AM to 3AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 3AM to 4AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 4AM to 5AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 6AM to 7AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 7AM to 8AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 9 | 8AM to 9AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 9 | 9AM to 10AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 9 | 10AM to 11AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 9 | 11AM to 12PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
November | 9 | 12PM to 1PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
November | 9 | 1PM to 2PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
November | 9 | 2PM to 3PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
November | 9 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
November | 9 | 4PM to 5PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
November | 9 | 5PM to 6PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
November | 9 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 9 | 7PM to 8PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 9 | 8PM to 9PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 9 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
November | 9 | 10PM to 11PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
November | 9 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
November | 10 | 12AM to 1AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 10 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 10 | 2AM to 3AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 10 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 10 | 4AM to 5AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 10 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 10 | 6AM to 7AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 10 | 7AM to 8AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 10 | 8AM to 9AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 10 | 9AM to 10AM | 55 | 55 | 55 | 64.7 | 23.25 | 0.0767 | 0.44 | 13.17 | 0
November | 10 | 10AM to 11AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 10 | 11AM to 12PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
November | 10 | 12PM to 1PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
November | 10 | 1PM to 2PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
November | 10 | 2PM to 3PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
November | 10 | 3PM to 4PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
November | 10 | 4PM to 5PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
November | 10 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
November | 10 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 10 | 7PM to 8PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 10 | 8PM to 9PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
November | 10 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 10 | 10PM to 11PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
November | 10 | 11PM to 12AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
November | 11 | 12AM to 1AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 11 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 11 | 2AM to 3AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 11 | 3AM to 4AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 11 | 4AM to 5AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
November | 11 | 5AM to 6AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
November | 11 | 6AM to 7AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
November | 11 | 7AM to 8AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
November | 11 | 8AM to 9AM | 57 | 57 | 57 | 69.6 | 24.49 | 0.0763 | 0.47 | 13.23 | 0
November | 11 | 9AM to 10AM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
November | 11 | 10AM to 11AM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
November | 11 | 11AM to 12PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
November | 11 | 12PM to 1PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
November | 11 | 1PM to 2PM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
November | 11 | 2PM to 3PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
November | 11 | 3PM to 4PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 11 | 4PM to 5PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 11 | 5PM to 6PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 11 | 6PM to 7PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 11 | 7PM to 8PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
November | 11 | 8PM to 9PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
November | 11 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 11 | 10PM to 11PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0767 | 0.34 | 13.13 | 0
November | 11 | 11PM to 12AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 12 | 12AM to 1AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 12 | 1AM to 2AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0767 | 0.34 | 13.13 | 0
November | 12 | 2AM to 3AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 12 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 12 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 12 | 5AM to 6AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 7AM to 8AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 8AM to 9AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
November | 12 | 9AM to 10AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 12 | 10AM to 11AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
November | 12 | 11AM to 12PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
November | 12 | 12PM to 1PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
November | 12 | 1PM to 2PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
November | 12 | 2PM to 3PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
November | 12 | 3PM to 4PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 12 | 4PM to 5PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 12 | 5PM to 6PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 12 | 6PM to 7PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 12 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 12 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 10PM to 11PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 12 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 13 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 13 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 13 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 13 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 13 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 13 | 5AM to 6AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 13 | 6AM to 7AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
November | 13 | 7AM to 8AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 13 | 8AM to 9AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 13 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
November | 13 | 10AM to 11AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
November | 13 | 11AM to 12PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
November | 13 | 12PM to 1PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
November | 13 | 1PM to 2PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
November | 13 | 2PM to 3PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
November | 13 | 3PM to 4PM | 66.9 | 56.5 | 48.9 | 51.5 | 24.08 | 0.075 | 0.35 | 13.43 | 0
November | 13 | 4PM to 5PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
November | 13 | 5PM to 6PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 13 | 6PM to 7PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 13 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 13 | 8PM to 9PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 13 | 9PM to 10PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 13 | 10PM to 11PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 13 | 11PM to 12AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 14 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 14 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 14 | 2AM to 3AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
November | 14 | 3AM to 4AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
November | 14 | 4AM to 5AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
November | 14 | 5AM to 6AM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 0
November | 14 | 6AM to 7AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
November | 14 | 7AM to 8AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
November | 14 | 8AM to 9AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
November | 14 | 9AM to 10AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
November | 14 | 10AM to 11AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
November | 14 | 11AM to 12PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 14 | 12PM to 1PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
November | 14 | 1PM to 2PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
November | 14 | 2PM to 3PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
November | 14 | 3PM to 4PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
November | 14 | 4PM to 5PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
November | 14 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 14 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 14 | 7PM to 8PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 14 | 8PM to 9PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 14 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 14 | 10PM to 11PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 14 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 15 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 15 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 15 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 15 | 3AM to 4AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 15 | 4AM to 5AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 15 | 5AM to 6AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 15 | 6AM to 7AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 15 | 7AM to 8AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 15 | 8AM to 9AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 15 | 9AM to 10AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 15 | 10AM to 11AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 15 | 11AM to 12PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 15 | 12PM to 1PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 15 | 1PM to 2PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
November | 15 | 2PM to 3PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
November | 15 | 3PM to 4PM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
November | 15 | 4PM to 5PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 15 | 5PM to 6PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
November | 15 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 15 | 7PM to 8PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 15 | 8PM to 9PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 15 | 9PM to 10PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 15 | 10PM to 11PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 15 | 11PM to 12AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 16 | 12AM to 1AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 16 | 1AM to 2AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
November | 16 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.19 | 0.0772 | 0.34 | 13.04 | 0
November | 16 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0773 | 0.32 | 13.03 | 0
November | 16 | 4AM to 5AM | 51.8 | 48 | 44.6 | 43.7 | 19.19 | 0.0773 | 0.3 | 13.02 | 0
November | 16 | 5AM to 6AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.19 | 0.0772 | 0.34 | 13.04 | 0
November | 16 | 6AM to 7AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 16 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 16 | 8AM to 9AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 16 | 9AM to 10AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 16 | 10AM to 11AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 16 | 11AM to 12PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 16 | 12PM to 1PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 16 | 1PM to 2PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 16 | 2PM to 3PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
November | 16 | 3PM to 4PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
November | 16 | 4PM to 5PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
November | 16 | 5PM to 6PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 16 | 6PM to 7PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 16 | 7PM to 8PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 16 | 8PM to 9PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 16 | 9PM to 10PM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 16 | 10PM to 11PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 16 | 11PM to 12AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
November | 17 | 12AM to 1AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
November | 17 | 1AM to 2AM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 0
November | 17 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0773 | 0.32 | 13.03 | 0
November | 17 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0773 | 0.32 | 13.03 | 0
November | 17 | 4AM to 5AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.93 | 1
November | 17 | 5AM to 6AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
November | 17 | 6AM to 7AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
November | 17 | 7AM to 8AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.11 | 0.077 | 0.32 | 13.08 | 0
November | 17 | 8AM to 9AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.11 | 0.077 | 0.32 | 13.08 | 0
November | 17 | 9AM to 10AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0767 | 0.34 | 13.13 | 0
November | 17 | 10AM to 11AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 17 | 11AM to 12PM | 57 | 57 | 57 | 69.6 | 24.49 | 0.0763 | 0.47 | 13.23 | 0
November | 17 | 12PM to 1PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
November | 17 | 1PM to 2PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
November | 17 | 2PM to 3PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
November | 17 | 3PM to 4PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
November | 17 | 4PM to 5PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
November | 17 | 5PM to 6PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 17 | 6PM to 7PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 17 | 7PM to 8PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 17 | 8PM to 9PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 17 | 9PM to 10PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 17 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 17 | 11PM to 12AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 18 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 18 | 1AM to 2AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
November | 18 | 2AM to 3AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
November | 18 | 3AM to 4AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
November | 18 | 4AM to 5AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
November | 18 | 5AM to 6AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
November | 18 | 6AM to 7AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 18 | 7AM to 8AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 18 | 8AM to 9AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 18 | 9AM to 10AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 18 | 10AM to 11AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 18 | 11AM to 12PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 18 | 12PM to 1PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 18 | 1PM to 2PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 18 | 2PM to 3PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 18 | 3PM to 4PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 18 | 4PM to 5PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
November | 18 | 5PM to 6PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 18 | 6PM to 7PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 18 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 18 | 8PM to 9PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 18 | 9PM to 10PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 18 | 10PM to 11PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 18 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 19 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 19 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 19 | 2AM to 3AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 19 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 19 | 4AM to 5AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 19 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 19 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 19 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 19 | 8AM to 9AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
November | 19 | 9AM to 10AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 19 | 10AM to 11AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
November | 19 | 11AM to 12PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 19 | 12PM to 1PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
November | 19 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
November | 19 | 2PM to 3PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
November | 19 | 3PM to 4PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
November | 19 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
November | 19 | 5PM to 6PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
November | 19 | 6PM to 7PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 19 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 19 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 19 | 9PM to 10PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 19 | 10PM to 11PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
November | 19 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
November | 20 | 12AM to 1AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
November | 20 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
November | 20 | 2AM to 3AM | 54 | 46.5 | 39 | 35.1 | 18.4 | 0.077 | 0.24 | 13.05 | 0
November | 20 | 3AM to 4AM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
November | 20 | 4AM to 5AM | 54 | 46.1 | 37.9 | 33.7 | 18.17 | 0.077 | 0.23 | 13.05 | 0
November | 20 | 5AM to 6AM | 54 | 46.1 | 37.9 | 33.7 | 18.17 | 0.077 | 0.23 | 13.05 | 0
November | 20 | 6AM to 7AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
November | 20 | 7AM to 8AM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
November | 20 | 8AM to 9AM | 55 | 45.1 | 34 | 28.7 | 17.67 | 0.0769 | 0.2 | 13.06 | 0
November | 20 | 9AM to 10AM | 57 | 46 | 34 | 28.7 | 18.15 | 0.0766 | 0.2 | 13.11 | 0
November | 20 | 10AM to 11AM | 59 | 44.6 | 27 | 21 | 17.42 | 0.0764 | 0.14 | 13.14 | 0
November | 20 | 11AM to 12PM | 60.1 | 45.2 | 27 | 21 | 17.68 | 0.0762 | 0.14 | 13.16 | 0
November | 20 | 12PM to 1PM | 60.1 | 45.8 | 28.9 | 23 | 18 | 0.0762 | 0.16 | 13.17 | 0
November | 20 | 1PM to 2PM | 61 | 47.6 | 33.1 | 27.7 | 18.94 | 0.076 | 0.19 | 13.21 | 0
November | 20 | 2PM to 3PM | 64.9 | 50.7 | 37 | 32.5 | 20.64 | 0.0754 | 0.22 | 13.32 | 0
November | 20 | 3PM to 4PM | 66.9 | 51.6 | 37 | 32.5 | 21.12 | 0.0751 | 0.22 | 13.37 | 0
November | 20 | 4PM to 5PM | 64 | 51.4 | 39.9 | 36.4 | 21.03 | 0.0755 | 0.25 | 13.31 | 0
November | 20 | 5PM to 6PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
November | 20 | 6PM to 7PM | 62.1 | 49.5 | 37 | 32.5 | 19.95 | 0.0758 | 0.22 | 13.25 | 0
November | 20 | 7PM to 8PM | 61 | 49.3 | 37.9 | 33.7 | 19.87 | 0.076 | 0.23 | 13.23 | 0
November | 20 | 8PM to 9PM | 60.1 | 48.2 | 36 | 31.1 | 19.25 | 0.0761 | 0.21 | 13.19 | 0
November | 20 | 9PM to 10PM | 57.9 | 47.2 | 36 | 31.1 | 18.73 | 0.0764 | 0.21 | 13.14 | 0
November | 20 | 10PM to 11PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
November | 20 | 11PM to 12AM | 55.9 | 46.6 | 37 | 32.5 | 18.46 | 0.0767 | 0.22 | 13.09 | 0
November | 21 | 12AM to 1AM | 55 | 44.8 | 33.1 | 27.7 | 17.51 | 0.0769 | 0.19 | 13.06 | 0
November | 21 | 1AM to 2AM | 55 | 44.8 | 33.1 | 27.7 | 17.51 | 0.0769 | 0.19 | 13.06 | 0
November | 21 | 2AM to 3AM | 55 | 45.1 | 34 | 28.7 | 17.67 | 0.0769 | 0.2 | 13.06 | 0
November | 21 | 3AM to 4AM | 54 | 44.6 | 34 | 28.7 | 17.41 | 0.077 | 0.2 | 13.03 | 0
November | 21 | 4AM to 5AM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
November | 21 | 5AM to 6AM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
November | 21 | 6AM to 7AM | 52 | 42.5 | 30.9 | 25.2 | 16.38 | 0.0774 | 0.17 | 12.97 | 0
November | 21 | 7AM to 8AM | 53.1 | 43 | 30.9 | 25.2 | 16.65 | 0.0772 | 0.17 | 13 | 0
November | 21 | 8AM to 9AM | 55 | 44.8 | 33.1 | 27.7 | 17.51 | 0.0769 | 0.19 | 13.06 | 0
November | 21 | 9AM to 10AM | 55 | 44 | 30.9 | 25.2 | 17.12 | 0.0769 | 0.17 | 13.05 | 0
November | 21 | 10AM to 11AM | 57.9 | 46.5 | 34 | 28.7 | 18.36 | 0.0765 | 0.2 | 13.13 | 0
November | 21 | 11AM to 12PM | 59 | 47.3 | 35.1 | 30 | 18.82 | 0.0763 | 0.2 | 13.16 | 0
November | 21 | 12PM to 1PM | 60.1 | 47.8 | 35.1 | 30 | 19.08 | 0.0761 | 0.2 | 13.19 | 0
November | 21 | 1PM to 2PM | 61 | 48.6 | 36 | 31.1 | 19.47 | 0.076 | 0.21 | 13.22 | 0
November | 21 | 2PM to 3PM | 60.1 | 49.7 | 39.9 | 36.4 | 20.07 | 0.0761 | 0.25 | 13.21 | 0
November | 21 | 3PM to 4PM | 60.1 | 48.9 | 37.9 | 33.7 | 19.65 | 0.0761 | 0.23 | 13.2 | 0
November | 21 | 4PM to 5PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
November | 21 | 5PM to 6PM | 57.9 | 49.6 | 42.1 | 39.6 | 20.05 | 0.0764 | 0.27 | 13.17 | 0
November | 21 | 6PM to 7PM | 59 | 47.7 | 36 | 31.1 | 18.99 | 0.0763 | 0.21 | 13.17 | 0
November | 21 | 7PM to 8PM | 57.9 | 47.2 | 36 | 31.1 | 18.73 | 0.0764 | 0.21 | 13.14 | 0
November | 21 | 8PM to 9PM | 55.9 | 42.8 | 26.1 | 20.1 | 16.55 | 0.0768 | 0.14 | 13.06 | 0
November | 21 | 9PM to 10PM | 55 | 44 | 30.9 | 25.2 | 17.12 | 0.0769 | 0.17 | 13.05 | 0
November | 21 | 10PM to 11PM | 57 | 43.4 | 26.1 | 20.1 | 16.81 | 0.0766 | 0.14 | 13.08 | 0
November | 21 | 11PM to 12AM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 0
November | 22 | 12AM to 1AM | 46 | 38.3 | 28 | 22.1 | 14.46 | 0.0783 | 0.15 | 12.81 | 1
November | 22 | 1AM to 2AM | 46 | 38 | 27 | 21 | 14.29 | 0.0783 | 0.14 | 12.81 | 1
November | 22 | 2AM to 3AM | 46.9 | 38.8 | 28 | 22.1 | 14.68 | 0.0782 | 0.15 | 12.83 | 1
November | 22 | 3AM to 4AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
November | 22 | 4AM to 5AM | 42.1 | 36.9 | 30 | 24.2 | 13.83 | 0.0789 | 0.16 | 12.72 | 1
November | 22 | 5AM to 6AM | 48 | 40.5 | 30.9 | 25.2 | 15.43 | 0.078 | 0.17 | 12.87 | 1
November | 22 | 6AM to 7AM | 48 | 42.8 | 37 | 32.5 | 16.55 | 0.0779 | 0.22 | 12.89 | 1
November | 22 | 7AM to 8AM | 46.9 | 41.5 | 35.1 | 30 | 15.9 | 0.0781 | 0.2 | 12.86 | 1
November | 22 | 8AM to 9AM | 54 | 44.6 | 34 | 28.7 | 17.41 | 0.077 | 0.2 | 13.03 | 0
November | 22 | 9AM to 10AM | 57 | 45.4 | 32 | 26.5 | 17.8 | 0.0766 | 0.18 | 13.1 | 0
November | 22 | 10AM to 11AM | 59 | 47.7 | 36 | 31.1 | 18.99 | 0.0763 | 0.21 | 13.17 | 0
November | 22 | 11AM to 12PM | 59 | 45.9 | 30.9 | 25.2 | 18.08 | 0.0763 | 0.17 | 13.15 | 0
November | 22 | 12PM to 1PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
November | 22 | 1PM to 2PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
November | 22 | 2PM to 3PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
November | 22 | 3PM to 4PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
November | 22 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 22 | 5PM to 6PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 22 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
November | 22 | 7PM to 8PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 22 | 8PM to 9PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
November | 22 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
November | 22 | 10PM to 11PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 22 | 11PM to 12AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 23 | 12AM to 1AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
November | 23 | 1AM to 2AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 23 | 2AM to 3AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
November | 23 | 3AM to 4AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
November | 23 | 4AM to 5AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
November | 23 | 5AM to 6AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
November | 23 | 6AM to 7AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 23 | 7AM to 8AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
November | 23 | 8AM to 9AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
November | 23 | 9AM to 10AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 23 | 10AM to 11AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 23 | 11AM to 12PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 23 | 12PM to 1PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
November | 23 | 1PM to 2PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
November | 23 | 2PM to 3PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
November | 23 | 3PM to 4PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
November | 23 | 4PM to 5PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 23 | 5PM to 6PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 23 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 23 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
November | 23 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
November | 23 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
November | 23 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
November | 23 | 11PM to 12AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 24 | 12AM to 1AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
November | 24 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
November | 24 | 2AM to 3AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
November | 24 | 3AM to 4AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
November | 24 | 4AM to 5AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
November | 24 | 5AM to 6AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
November | 24 | 6AM to 7AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 24 | 7AM to 8AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 24 | 8AM to 9AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
November | 24 | 9AM to 10AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
November | 24 | 10AM to 11AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
November | 24 | 11AM to 12PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
November | 24 | 12PM to 1PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 24 | 1PM to 2PM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
November | 24 | 2PM to 3PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
November | 24 | 3PM to 4PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
November | 24 | 4PM to 5PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
November | 24 | 5PM to 6PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 24 | 6PM to 7PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 24 | 7PM to 8PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 24 | 8PM to 9PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 24 | 9PM to 10PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 24 | 10PM to 11PM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 24 | 11PM to 12AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
November | 25 | 12AM to 1AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
November | 25 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 25 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 25 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 25 | 4AM to 5AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 25 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 25 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 25 | 7AM to 8AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 25 | 8AM to 9AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 25 | 9AM to 10AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 25 | 10AM to 11AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 25 | 11AM to 12PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 25 | 12PM to 1PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 25 | 1PM to 2PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 25 | 2PM to 3PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 25 | 3PM to 4PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
November | 25 | 4PM to 5PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
November | 25 | 5PM to 6PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 25 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 25 | 7PM to 8PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 25 | 8PM to 9PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
November | 25 | 9PM to 10PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
November | 25 | 10PM to 11PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
November | 25 | 11PM to 12AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 26 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 26 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 26 | 2AM to 3AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 26 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 26 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 26 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 26 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 26 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 26 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 26 | 9AM to 10AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 26 | 10AM to 11AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 26 | 11AM to 12PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 26 | 12PM to 1PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
November | 26 | 1PM to 2PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 26 | 2PM to 3PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 26 | 3PM to 4PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 26 | 4PM to 5PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 26 | 5PM to 6PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 26 | 6PM to 7PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 26 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 26 | 8PM to 9PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 26 | 9PM to 10PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 26 | 10PM to 11PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 26 | 11PM to 12AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 27 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 27 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 27 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 27 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 27 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 27 | 5AM to 6AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
November | 27 | 6AM to 7AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 27 | 7AM to 8AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 27 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 27 | 9AM to 10AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 27 | 10AM to 11AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 27 | 11AM to 12PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 27 | 12PM to 1PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
November | 27 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
November | 27 | 2PM to 3PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
November | 27 | 3PM to 4PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 27 | 4PM to 5PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
November | 27 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
November | 27 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
November | 27 | 7PM to 8PM | 55 | 47.4 | 39.9 | 36.4 | 18.85 | 0.0768 | 0.25 | 13.08 | 0
November | 27 | 8PM to 9PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
November | 27 | 9PM to 10PM | 55 | 45.8 | 36 | 31.1 | 18.03 | 0.0769 | 0.21 | 13.07 | 0
November | 27 | 10PM to 11PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
November | 27 | 11PM to 12AM | 53.1 | 43.8 | 33.1 | 27.7 | 17.03 | 0.0772 | 0.19 | 13.01 | 0
November | 28 | 12AM to 1AM | 53.1 | 43 | 30.9 | 25.2 | 16.65 | 0.0772 | 0.17 | 13 | 0
November | 28 | 1AM to 2AM | 52 | 42.9 | 32 | 26.5 | 16.58 | 0.0774 | 0.18 | 12.98 | 0
November | 28 | 2AM to 3AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 0
November | 28 | 3AM to 4AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 0
November | 28 | 4AM to 5AM | 50 | 41.5 | 30.9 | 25.2 | 15.91 | 0.0777 | 0.17 | 12.92 | 1
November | 28 | 5AM to 6AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 0
November | 28 | 6AM to 7AM | 51.1 | 41.7 | 30 | 24.2 | 16.01 | 0.0775 | 0.16 | 12.95 | 0
November | 28 | 7AM to 8AM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 0
November | 28 | 8AM to 9AM | 52 | 42.9 | 32 | 26.5 | 16.58 | 0.0774 | 0.18 | 12.98 | 0
November | 28 | 9AM to 10AM | 52 | 42.5 | 30.9 | 25.2 | 16.38 | 0.0774 | 0.17 | 12.97 | 0
November | 28 | 10AM to 11AM | 53.1 | 43.8 | 33.1 | 27.7 | 17.03 | 0.0772 | 0.19 | 13.01 | 0
November | 28 | 11AM to 12PM | 54 | 43.9 | 32 | 26.5 | 17.06 | 0.0771 | 0.18 | 13.03 | 0
November | 28 | 12PM to 1PM | 55.9 | 44.9 | 32 | 26.5 | 17.54 | 0.0768 | 0.18 | 13.08 | 0
November | 28 | 1PM to 2PM | 55.9 | 44.5 | 30.9 | 25.2 | 17.34 | 0.0768 | 0.17 | 13.07 | 0
November | 28 | 2PM to 3PM | 57 | 45.7 | 33.1 | 27.7 | 17.99 | 0.0766 | 0.19 | 13.11 | 0
November | 28 | 3PM to 4PM | 57 | 45.4 | 32 | 26.5 | 17.8 | 0.0766 | 0.18 | 13.1 | 0
November | 28 | 4PM to 5PM | 55.9 | 45.9 | 35.1 | 30 | 18.08 | 0.0767 | 0.2 | 13.09 | 0
November | 28 | 5PM to 6PM | 55 | 43.7 | 30 | 24.2 | 16.96 | 0.0769 | 0.16 | 13.05 | 0
November | 28 | 6PM to 7PM | 54 | 44.3 | 33.1 | 27.7 | 17.25 | 0.0771 | 0.19 | 13.03 | 0
November | 28 | 7PM to 8PM | 53.1 | 43.4 | 32 | 26.5 | 16.85 | 0.0772 | 0.18 | 13 | 0
November | 28 | 8PM to 9PM | 52 | 42.2 | 30 | 24.2 | 16.23 | 0.0774 | 0.16 | 12.97 | 0
November | 28 | 9PM to 10PM | 51.1 | 42.8 | 33.1 | 27.7 | 16.55 | 0.0775 | 0.19 | 12.96 | 0
November | 28 | 10PM to 11PM | 52 | 42.5 | 30.9 | 25.2 | 16.38 | 0.0774 | 0.17 | 12.97 | 0
November | 28 | 11PM to 12AM | 52 | 43.3 | 33.1 | 27.7 | 16.77 | 0.0774 | 0.19 | 12.98 | 0
November | 29 | 12AM to 1AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 0
November | 29 | 1AM to 2AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 0
November | 29 | 2AM to 3AM | 50 | 40.8 | 28.9 | 23 | 15.56 | 0.0777 | 0.16 | 12.91 | 1
November | 29 | 3AM to 4AM | 48 | 40.9 | 32 | 26.5 | 15.63 | 0.078 | 0.18 | 12.87 | 1
November | 29 | 4AM to 5AM | 48.9 | 41.4 | 32 | 26.5 | 15.85 | 0.0778 | 0.18 | 12.9 | 1
November | 29 | 5AM to 6AM | 48 | 40.5 | 30.9 | 25.2 | 15.43 | 0.078 | 0.17 | 12.87 | 1
November | 29 | 6AM to 7AM | 44.1 | 37.3 | 28 | 22.1 | 13.98 | 0.0786 | 0.15 | 12.76 | 1
November | 29 | 7AM to 8AM | 48 | 38.7 | 26.1 | 20.1 | 14.64 | 0.078 | 0.14 | 12.86 | 1
November | 29 | 8AM to 9AM | 46.9 | 38.8 | 28 | 22.1 | 14.68 | 0.0782 | 0.15 | 12.83 | 1
November | 29 | 9AM to 10AM | 48.9 | 39.9 | 28 | 22.1 | 15.16 | 0.0779 | 0.15 | 12.88 | 1
November | 29 | 10AM to 11AM | 48.9 | 39.5 | 27 | 21 | 14.99 | 0.0779 | 0.14 | 12.88 | 1
November | 29 | 11AM to 12PM | 50 | 39.8 | 26.1 | 20.1 | 15.11 | 0.0777 | 0.14 | 12.91 | 1
November | 29 | 12PM to 1PM | 51.1 | 40.4 | 26.1 | 20.1 | 15.37 | 0.0775 | 0.14 | 12.93 | 0
November | 29 | 1PM to 2PM | 53.1 | 41.7 | 27 | 21 | 15.99 | 0.0772 | 0.14 | 12.99 | 0
November | 29 | 2PM to 3PM | 53.1 | 42.3 | 28.9 | 23 | 16.3 | 0.0772 | 0.16 | 12.99 | 0
November | 29 | 3PM to 4PM | 54 | 43.9 | 32 | 26.5 | 17.06 | 0.0771 | 0.18 | 13.03 | 0
November | 29 | 4PM to 5PM | 52 | 43.3 | 33.1 | 27.7 | 16.77 | 0.0774 | 0.19 | 12.98 | 0
November | 29 | 5PM to 6PM | 50 | 42.3 | 33.1 | 27.7 | 16.29 | 0.0777 | 0.19 | 12.93 | 1
November | 29 | 6PM to 7PM | 48.9 | 39.9 | 28 | 22.1 | 15.16 | 0.0779 | 0.15 | 12.88 | 1
November | 29 | 7PM to 8PM | 46.9 | 40.3 | 32 | 26.5 | 15.37 | 0.0781 | 0.18 | 12.85 | 1
November | 29 | 8PM to 9PM | 45 | 39.3 | 32 | 26.5 | 14.89 | 0.0784 | 0.18 | 12.8 | 1
November | 29 | 9PM to 10PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
November | 29 | 10PM to 11PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
November | 29 | 11PM to 12AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
November | 30 | 12AM to 1AM | 41 | 37.9 | 34 | 28.7 | 14.27 | 0.079 | 0.2 | 12.7 | 1
November | 30 | 1AM to 2AM | 41 | 38.3 | 35.1 | 30 | 14.47 | 0.079 | 0.2 | 12.71 | 1
November | 30 | 2AM to 3AM | 39.9 | 38.1 | 36 | 31.1 | 14.38 | 0.0792 | 0.21 | 12.68 | 1
November | 30 | 3AM to 4AM | 39 | 36.8 | 34 | 28.7 | 13.79 | 0.0794 | 0.2 | 12.65 | 1
November | 30 | 4AM to 5AM | 37.9 | 36.7 | 35.1 | 30 | 13.73 | 0.0795 | 0.2 | 12.63 | 1
November | 30 | 5AM to 6AM | 39 | 37.6 | 36 | 31.1 | 14.16 | 0.0793 | 0.21 | 12.66 | 1
November | 30 | 6AM to 7AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
November | 30 | 7AM to 8AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0792 | 0.23 | 12.69 | 1
November | 30 | 8AM to 9AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
November | 30 | 9AM to 10AM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
November | 30 | 10AM to 11AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
November | 30 | 11AM to 12PM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
November | 30 | 12PM to 1PM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
November | 30 | 1PM to 2PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
November | 30 | 2PM to 3PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
November | 30 | 3PM to 4PM | 52 | 45.6 | 39 | 35.1 | 17.92 | 0.0773 | 0.24 | 13 | 0
November | 30 | 4PM to 5PM | 52 | 45.6 | 39 | 35.1 | 17.92 | 0.0773 | 0.24 | 13 | 0
November | 30 | 5PM to 6PM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
November | 30 | 6PM to 7PM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
November | 30 | 7PM to 8PM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
November | 30 | 8PM to 9PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
November | 30 | 9PM to 10PM | 49.3 | 45.8 | 42.4 | 40.2 | 18.04 | 0.0777 | 0.27 | 12.95 | 1
November | 30 | 10PM to 11PM | 48.6 | 45.7 | 43 | 41 | 18 | 0.0778 | 0.28 | 12.93 | 1
November | 30 | 11PM to 12AM | 47.8 | 45.5 | 43.3 | 41.6 | 17.91 | 0.0779 | 0.28 | 12.91 | 1
December | 1 | 12AM to 1AM | 47.1 | 45.4 | 43.7 | 42.2 | 17.83 | 0.078 | 0.29 | 12.9 | 1
December | 1 | 1AM to 2AM | 46.4 | 45.2 | 44.1 | 42.8 | 17.74 | 0.0781 | 0.29 | 12.88 | 1
December | 1 | 2AM to 3AM | 45.7 | 45.1 | 44.6 | 43.7 | 17.71 | 0.0782 | 0.3 | 12.87 | 1
December | 1 | 3AM to 4AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
December | 1 | 4AM to 5AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
December | 1 | 5AM to 6AM | 48 | 48 | 48 | 49.8 | 19.22 | 0.0778 | 0.34 | 12.94 | 1
December | 1 | 6AM to 7AM | 46.9 | 46.9 | 46.9 | 47.8 | 18.65 | 0.078 | 0.32 | 12.91 | 1
December | 1 | 7AM to 8AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
December | 1 | 8AM to 9AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 1 | 9AM to 10AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 1 | 10AM to 11AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
December | 1 | 11AM to 12PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
December | 1 | 12PM to 1PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
December | 1 | 1PM to 2PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
December | 1 | 2PM to 3PM | 61 | 49.7 | 39 | 35.1 | 20.1 | 0.076 | 0.24 | 13.23 | 0
December | 1 | 3PM to 4PM | 60.1 | 50.6 | 42.1 | 39.6 | 20.57 | 0.0761 | 0.27 | 13.22 | 0
December | 1 | 4PM to 5PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
December | 1 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
December | 1 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 1 | 7PM to 8PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 1 | 8PM to 9PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 1 | 9PM to 10PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 1 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 1 | 11PM to 12AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
December | 2 | 12AM to 1AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
December | 2 | 1AM to 2AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
December | 2 | 2AM to 3AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
December | 2 | 3AM to 4AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
December | 2 | 4AM to 5AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
December | 2 | 5AM to 6AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
December | 2 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
December | 2 | 7AM to 8AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 2 | 8AM to 9AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 2 | 9AM to 10AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
December | 2 | 10AM to 11AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
December | 2 | 11AM to 12PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
December | 2 | 12PM to 1PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
December | 2 | 1PM to 2PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 2 | 2PM to 3PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
December | 2 | 3PM to 4PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
December | 2 | 4PM to 5PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 2 | 5PM to 6PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 2 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 7PM to 8PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 8PM to 9PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 6AM to 7AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 7AM to 8AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 3 | 9AM to 10AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
December | 3 | 10AM to 11AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 3 | 11AM to 12PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 3 | 12PM to 1PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
December | 3 | 1PM to 2PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
December | 3 | 2PM to 3PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 3 | 3PM to 4PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
December | 3 | 4PM to 5PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
December | 3 | 5PM to 6PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
December | 3 | 6PM to 7PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 3 | 7PM to 8PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 3 | 8PM to 9PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 3 | 9PM to 10PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 3 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 3 | 11PM to 12AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 3AM to 4AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
December | 4 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 4 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 4 | 6AM to 7AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
December | 4 | 7AM to 8AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
December | 4 | 8AM to 9AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 4 | 9AM to 10AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 4 | 10AM to 11AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 4 | 11AM to 12PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
December | 4 | 12PM to 1PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 1PM to 2PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 4 | 2PM to 3PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 4 | 3PM to 4PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 4 | 4PM to 5PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
December | 4 | 5PM to 6PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 4 | 6PM to 7PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 4 | 7PM to 8PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
December | 4 | 8PM to 9PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
December | 4 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 4 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
December | 5 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
December | 5 | 1AM to 2AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 5 | 2AM to 3AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 5 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 5 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 5 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 5 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 5 | 7AM to 8AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 5 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 5 | 9AM to 10AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 5 | 10AM to 11AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
December | 5 | 11AM to 12PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
December | 5 | 12PM to 1PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
December | 5 | 1PM to 2PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
December | 5 | 2PM to 3PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
December | 5 | 3PM to 4PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
December | 5 | 4PM to 5PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
December | 5 | 5PM to 6PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 5 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 5 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 5 | 8PM to 9PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
December | 5 | 9PM to 10PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 5 | 10PM to 11PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 5 | 11PM to 12AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
December | 6 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 6 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 6 | 2AM to 3AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
December | 6 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 7AM to 8AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 8AM to 9AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
December | 6 | 9AM to 10AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
December | 6 | 10AM to 11AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
December | 6 | 11AM to 12PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 6 | 12PM to 1PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 1PM to 2PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 2PM to 3PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
December | 6 | 3PM to 4PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 4PM to 5PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 5PM to 6PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 6PM to 7PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 6 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 6 | 8PM to 9PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 6 | 9PM to 10PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
December | 6 | 10PM to 11PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
December | 6 | 11PM to 12AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
December | 7 | 12AM to 1AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
December | 7 | 1AM to 2AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
December | 7 | 2AM to 3AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
December | 7 | 3AM to 4AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
December | 7 | 4AM to 5AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
December | 7 | 5AM to 6AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
December | 7 | 6AM to 7AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
December | 7 | 7AM to 8AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
December | 7 | 8AM to 9AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
December | 7 | 9AM to 10AM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
December | 7 | 10AM to 11AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
December | 7 | 11AM to 12PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
December | 7 | 12PM to 1PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 7 | 1PM to 2PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
December | 7 | 2PM to 3PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 7 | 3PM to 4PM | 54 | 48.8 | 44.2 | 43.1 | 19.62 | 0.077 | 0.29 | 13.07 | 0
December | 7 | 4PM to 5PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
December | 7 | 5PM to 6PM | 50.5 | 48.1 | 46 | 46.1 | 19.27 | 0.0775 | 0.31 | 13 | 1
December | 7 | 6PM to 7PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
December | 7 | 7PM to 8PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
December | 7 | 8PM to 9PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 7 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
December | 7 | 10PM to 11PM | 48 | 45.6 | 43.3 | 41.6 | 17.96 | 0.0779 | 0.28 | 12.92 | 1
December | 7 | 11PM to 12AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
December | 8 | 12AM to 1AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 8 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 8 | 2AM to 3AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 0
December | 8 | 3AM to 4AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
December | 8 | 4AM to 5AM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 0
December | 8 | 5AM to 6AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
December | 8 | 6AM to 7AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
December | 8 | 7AM to 8AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 8 | 8AM to 9AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
December | 8 | 9AM to 10AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
December | 8 | 10AM to 11AM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
December | 8 | 11AM to 12PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
December | 8 | 12PM to 1PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 8 | 1PM to 2PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
December | 8 | 2PM to 3PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
December | 8 | 3PM to 4PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
December | 8 | 4PM to 5PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 8 | 5PM to 6PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 8 | 6PM to 7PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
December | 8 | 7PM to 8PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 8 | 8PM to 9PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 8 | 9PM to 10PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
December | 8 | 10PM to 11PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 8 | 11PM to 12AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 9 | 12AM to 1AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 9 | 1AM to 2AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
December | 9 | 2AM to 3AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
December | 9 | 3AM to 4AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
December | 9 | 4AM to 5AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
December | 9 | 5AM to 6AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
December | 9 | 6AM to 7AM | 42.1 | 41 | 39.9 | 36.4 | 15.71 | 0.0788 | 0.25 | 12.75 | 1
December | 9 | 7AM to 8AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
December | 9 | 8AM to 9AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 9 | 9AM to 10AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 9 | 10AM to 11AM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
December | 9 | 11AM to 12PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
December | 9 | 12PM to 1PM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
December | 9 | 1PM to 2PM | 55 | 47.4 | 39.9 | 36.4 | 18.85 | 0.0768 | 0.25 | 13.08 | 0
December | 9 | 2PM to 3PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 9 | 3PM to 4PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 9 | 4PM to 5PM | 54 | 46.1 | 37.9 | 33.7 | 18.17 | 0.077 | 0.23 | 13.05 | 0
December | 9 | 5PM to 6PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 0
December | 9 | 6PM to 7PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 9 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 9 | 8PM to 9PM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 9 | 9PM to 10PM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
December | 9 | 10PM to 11PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 9 | 11PM to 12AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 10 | 12AM to 1AM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
December | 10 | 1AM to 2AM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
December | 10 | 2AM to 3AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
December | 10 | 3AM to 4AM | 42.1 | 40.6 | 39 | 35.1 | 15.52 | 0.0788 | 0.24 | 12.75 | 1
December | 10 | 4AM to 5AM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0787 | 0.25 | 12.78 | 1
December | 10 | 5AM to 6AM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0787 | 0.25 | 12.78 | 1
December | 10 | 6AM to 7AM | 44.1 | 40.8 | 37 | 32.5 | 15.59 | 0.0785 | 0.22 | 12.79 | 1
December | 10 | 7AM to 8AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
December | 10 | 8AM to 9AM | 48.9 | 44.1 | 39 | 35.1 | 17.17 | 0.0778 | 0.24 | 12.92 | 1
December | 10 | 9AM to 10AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
December | 10 | 10AM to 11AM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
December | 10 | 11AM to 12PM | 54 | 46.1 | 37.9 | 33.7 | 18.17 | 0.077 | 0.23 | 13.05 | 0
December | 10 | 12PM to 1PM | 55.9 | 47.4 | 39 | 35.1 | 18.88 | 0.0767 | 0.24 | 13.1 | 0
December | 10 | 1PM to 2PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
December | 10 | 2PM to 3PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
December | 10 | 3PM to 4PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
December | 10 | 4PM to 5PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
December | 10 | 5PM to 6PM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
December | 10 | 6PM to 7PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
December | 10 | 7PM to 8PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
December | 10 | 8PM to 9PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 0
December | 10 | 9PM to 10PM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 0
December | 10 | 10PM to 11PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 0
December | 10 | 11PM to 12AM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
December | 11 | 12AM to 1AM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
December | 11 | 1AM to 2AM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
December | 11 | 2AM to 3AM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
December | 11 | 3AM to 4AM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
December | 11 | 4AM to 5AM | 48.9 | 43.3 | 37 | 32.5 | 16.77 | 0.0778 | 0.22 | 12.92 | 1
December | 11 | 5AM to 6AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
December | 11 | 6AM to 7AM | 48.9 | 43.3 | 37 | 32.5 | 16.77 | 0.0778 | 0.22 | 12.92 | 1
December | 11 | 7AM to 8AM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
December | 11 | 8AM to 9AM | 52 | 44.8 | 37 | 32.5 | 17.51 | 0.0773 | 0.22 | 12.99 | 0
December | 11 | 9AM to 10AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
December | 11 | 10AM to 11AM | 55.9 | 46.2 | 36 | 31.1 | 18.25 | 0.0767 | 0.21 | 13.09 | 0
December | 11 | 11AM to 12PM | 57 | 46.8 | 36 | 31.1 | 18.51 | 0.0766 | 0.21 | 13.12 | 0
December | 11 | 12PM to 1PM | 57.9 | 48.3 | 39 | 35.1 | 19.35 | 0.0764 | 0.24 | 13.15 | 0
December | 11 | 1PM to 2PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
December | 11 | 2PM to 3PM | 60.1 | 48.6 | 37 | 32.5 | 19.47 | 0.0761 | 0.22 | 13.2 | 0
December | 11 | 3PM to 4PM | 57 | 47.5 | 37.9 | 33.7 | 18.91 | 0.0766 | 0.23 | 13.12 | 0
December | 11 | 4PM to 5PM | 55.9 | 47.4 | 39 | 35.1 | 18.88 | 0.0767 | 0.24 | 13.1 | 0
December | 11 | 5PM to 6PM | 55 | 47 | 39 | 35.1 | 18.66 | 0.0768 | 0.24 | 13.08 | 0
December | 11 | 6PM to 7PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
December | 11 | 7PM to 8PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
December | 11 | 8PM to 9PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
December | 11 | 9PM to 10PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
December | 11 | 10PM to 11PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
December | 11 | 11PM to 12AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 12 | 12AM to 1AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
December | 12 | 1AM to 2AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
December | 12 | 2AM to 3AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
December | 12 | 3AM to 4AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
December | 12 | 4AM to 5AM | 42.1 | 41 | 39.9 | 36.4 | 15.71 | 0.0788 | 0.25 | 12.75 | 1
December | 12 | 5AM to 6AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
December | 12 | 6AM to 7AM | 43 | 42.5 | 42.1 | 39.6 | 16.43 | 0.0787 | 0.27 | 12.79 | 1
December | 12 | 7AM to 8AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
December | 12 | 8AM to 9AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 12 | 9AM to 10AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
December | 12 | 10AM to 11AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 12 | 11AM to 12PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 12 | 12PM to 1PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 12 | 1PM to 2PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
December | 12 | 2PM to 3PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 12 | 3PM to 4PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
December | 12 | 4PM to 5PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
December | 12 | 5PM to 6PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 12 | 6PM to 7PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 12 | 7PM to 8PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 12 | 8PM to 9PM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
December | 12 | 9PM to 10PM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
December | 12 | 10PM to 11PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
December | 12 | 11PM to 12AM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
December | 13 | 12AM to 1AM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
December | 13 | 1AM to 2AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
December | 13 | 2AM to 3AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
December | 13 | 3AM to 4AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
December | 13 | 4AM to 5AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
December | 13 | 5AM to 6AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
December | 13 | 6AM to 7AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
December | 13 | 7AM to 8AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
December | 13 | 8AM to 9AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
December | 13 | 9AM to 10AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
December | 13 | 10AM to 11AM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
December | 13 | 11AM to 12PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 13 | 12PM to 1PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 13 | 1PM to 2PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 13 | 2PM to 3PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 13 | 3PM to 4PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 13 | 4PM to 5PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 13 | 5PM to 6PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 13 | 6PM to 7PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 13 | 7PM to 8PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 13 | 8PM to 9PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
December | 13 | 9PM to 10PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
December | 13 | 10PM to 11PM | 54.9 | 53.4 | 52.3 | 58.6 | 22.25 | 0.0767 | 0.4 | 13.14 | 0
December | 13 | 11PM to 12AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
December | 14 | 12AM to 1AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
December | 14 | 1AM to 2AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 2AM to 3AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 3AM to 4AM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 0
December | 14 | 4AM to 5AM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 0
December | 14 | 5AM to 6AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 6AM to 7AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 7AM to 8AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 8AM to 9AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 9AM to 10AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
December | 14 | 10AM to 11AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
December | 14 | 11AM to 12PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
December | 14 | 12PM to 1PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 14 | 1PM to 2PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
December | 14 | 2PM to 3PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 14 | 3PM to 4PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
December | 14 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
December | 14 | 5PM to 6PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 14 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 14 | 7PM to 8PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
December | 14 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
December | 14 | 9PM to 10PM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
December | 14 | 10PM to 11PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 14 | 11PM to 12AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
December | 15 | 12AM to 1AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
December | 15 | 1AM to 2AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
December | 15 | 2AM to 3AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
December | 15 | 3AM to 4AM | 42.1 | 42.1 | 42.1 | 39.6 | 16.21 | 0.0788 | 0.27 | 12.76 | 1
December | 15 | 4AM to 5AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
December | 15 | 5AM to 6AM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
December | 15 | 6AM to 7AM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
December | 15 | 7AM to 8AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
December | 15 | 8AM to 9AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
December | 15 | 9AM to 10AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 15 | 10AM to 11AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 15 | 11AM to 12PM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
December | 15 | 12PM to 1PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 15 | 1PM to 2PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
December | 15 | 2PM to 3PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
December | 15 | 3PM to 4PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
December | 15 | 4PM to 5PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
December | 15 | 5PM to 6PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
December | 15 | 6PM to 7PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
December | 15 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 15 | 8PM to 9PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
December | 15 | 9PM to 10PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 15 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 15 | 11PM to 12AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 16 | 12AM to 1AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
December | 16 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
December | 16 | 2AM to 3AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
December | 16 | 3AM to 4AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
December | 16 | 4AM to 5AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
December | 16 | 5AM to 6AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
December | 16 | 6AM to 7AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
December | 16 | 7AM to 8AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
December | 16 | 8AM to 9AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
December | 16 | 9AM to 10AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 16 | 10AM to 11AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
December | 16 | 11AM to 12PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 16 | 12PM to 1PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
December | 16 | 1PM to 2PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
December | 16 | 2PM to 3PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
December | 16 | 3PM to 4PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
December | 16 | 4PM to 5PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 16 | 5PM to 6PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 16 | 6PM to 7PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
December | 16 | 7PM to 8PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 16 | 8PM to 9PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
December | 16 | 9PM to 10PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
December | 16 | 10PM to 11PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
December | 16 | 11PM to 12AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 17 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
December | 17 | 1AM to 2AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 17 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 17 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 17 | 4AM to 5AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 17 | 5AM to 6AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 17 | 6AM to 7AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 17 | 7AM to 8AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 17 | 8AM to 9AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 17 | 9AM to 10AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 17 | 10AM to 11AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
December | 17 | 11AM to 12PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
December | 17 | 12PM to 1PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 17 | 1PM to 2PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
December | 17 | 2PM to 3PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
December | 17 | 3PM to 4PM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 17 | 4PM to 5PM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
December | 17 | 5PM to 6PM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
December | 17 | 6PM to 7PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
December | 17 | 7PM to 8PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
December | 17 | 8PM to 9PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 0
December | 17 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
December | 17 | 10PM to 11PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
December | 17 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 18 | 12AM to 1AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
December | 18 | 1AM to 2AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 18 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 18 | 3AM to 4AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
December | 18 | 4AM to 5AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
December | 18 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 18 | 6AM to 7AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
December | 18 | 7AM to 8AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 18 | 8AM to 9AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 18 | 9AM to 10AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 18 | 10AM to 11AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
December | 18 | 11AM to 12PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 18 | 12PM to 1PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
December | 18 | 1PM to 2PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
December | 18 | 2PM to 3PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
December | 18 | 3PM to 4PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
December | 18 | 4PM to 5PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
December | 18 | 5PM to 6PM | 57.9 | 47.6 | 37 | 32.5 | 18.94 | 0.0764 | 0.22 | 13.14 | 0
December | 18 | 6PM to 7PM | 57 | 47.5 | 37.9 | 33.7 | 18.91 | 0.0766 | 0.23 | 13.12 | 0
December | 18 | 7PM to 8PM | 55.9 | 46.2 | 36 | 31.1 | 18.25 | 0.0767 | 0.21 | 13.09 | 0
December | 18 | 8PM to 9PM | 55 | 45.8 | 36 | 31.1 | 18.03 | 0.0769 | 0.21 | 13.07 | 0
December | 18 | 9PM to 10PM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
December | 18 | 10PM to 11PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 18 | 11PM to 12AM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 19 | 12AM to 1AM | 53.1 | 42 | 28 | 22.1 | 16.16 | 0.0772 | 0.15 | 12.99 | 0
December | 19 | 1AM to 2AM | 53.1 | 43.8 | 33.1 | 27.7 | 17.03 | 0.0772 | 0.19 | 13.01 | 0
December | 19 | 2AM to 3AM | 53.1 | 44.1 | 34 | 28.7 | 17.19 | 0.0772 | 0.2 | 13.01 | 0
December | 19 | 3AM to 4AM | 53.1 | 44.9 | 36 | 31.1 | 17.56 | 0.0772 | 0.21 | 13.02 | 0
December | 19 | 4AM to 5AM | 53.1 | 43.8 | 33.1 | 27.7 | 17.03 | 0.0772 | 0.19 | 13.01 | 0
December | 19 | 5AM to 6AM | 51.1 | 43.9 | 36 | 31.1 | 17.08 | 0.0775 | 0.21 | 12.97 | 0
December | 19 | 6AM to 7AM | 48 | 41.6 | 34 | 28.7 | 15.97 | 0.078 | 0.2 | 12.88 | 1
December | 19 | 7AM to 8AM | 46 | 41 | 35.1 | 30 | 15.69 | 0.0782 | 0.2 | 12.83 | 1
December | 19 | 8AM to 9AM | 51.1 | 43.2 | 34 | 28.7 | 16.71 | 0.0775 | 0.2 | 12.96 | 0
December | 19 | 9AM to 10AM | 54 | 43.2 | 30 | 24.2 | 16.7 | 0.0771 | 0.16 | 13.02 | 0
December | 19 | 10AM to 11AM | 55 | 42.1 | 25 | 19.1 | 16.17 | 0.077 | 0.13 | 13.03 | 0
December | 19 | 11AM to 12PM | 57 | 42.2 | 21.9 | 16.5 | 16.25 | 0.0767 | 0.11 | 13.07 | 0
December | 19 | 12PM to 1PM | 57.9 | 43.5 | 25 | 19.1 | 16.87 | 0.0765 | 0.13 | 13.1 | 0
December | 19 | 1PM to 2PM | 59 | 45.6 | 30 | 24.2 | 17.92 | 0.0763 | 0.16 | 13.15 | 0
December | 19 | 2PM to 3PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
December | 19 | 3PM to 4PM | 59 | 46.3 | 32 | 26.5 | 18.28 | 0.0763 | 0.18 | 13.15 | 0
December | 19 | 4PM to 5PM | 57 | 44 | 28 | 22.1 | 17.11 | 0.0766 | 0.15 | 13.09 | 0
December | 19 | 5PM to 6PM | 55 | 44 | 30.9 | 25.2 | 17.12 | 0.0769 | 0.17 | 13.05 | 0
December | 19 | 6PM to 7PM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
December | 19 | 7PM to 8PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 0
December | 19 | 8PM to 9PM | 51.1 | 43.9 | 36 | 31.1 | 17.08 | 0.0775 | 0.21 | 12.97 | 0
December | 19 | 9PM to 10PM | 50 | 43.4 | 36 | 31.1 | 16.82 | 0.0776 | 0.21 | 12.94 | 1
December | 19 | 10PM to 11PM | 48.9 | 42.8 | 36 | 31.1 | 16.55 | 0.0778 | 0.21 | 12.91 | 1
December | 19 | 11PM to 12AM | 50 | 42.6 | 34 | 28.7 | 16.45 | 0.0776 | 0.2 | 12.93 | 1
December | 20 | 12AM to 1AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
December | 20 | 1AM to 2AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 20 | 2AM to 3AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 20 | 3AM to 4AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
December | 20 | 4AM to 5AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
December | 20 | 5AM to 6AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
December | 20 | 6AM to 7AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
December | 20 | 7AM to 8AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
December | 20 | 8AM to 9AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
December | 20 | 9AM to 10AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 20 | 10AM to 11AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
December | 20 | 11AM to 12PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 20 | 12PM to 1PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
December | 20 | 1PM to 2PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
December | 20 | 2PM to 3PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
December | 20 | 3PM to 4PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
December | 20 | 4PM to 5PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
December | 20 | 5PM to 6PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
December | 20 | 6PM to 7PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 20 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 20 | 8PM to 9PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 20 | 9PM to 10PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 20 | 10PM to 11PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 20 | 11PM to 12AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 21 | 12AM to 1AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 21 | 1AM to 2AM | 48.9 | 44.1 | 39 | 35.1 | 17.17 | 0.0778 | 0.24 | 12.92 | 1
December | 21 | 2AM to 3AM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 21 | 3AM to 4AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
December | 21 | 4AM to 5AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
December | 21 | 5AM to 6AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
December | 21 | 6AM to 7AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
December | 21 | 7AM to 8AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 21 | 8AM to 9AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 21 | 9AM to 10AM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 21 | 10AM to 11AM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
December | 21 | 11AM to 12PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
December | 21 | 12PM to 1PM | 54 | 44.3 | 33.1 | 27.7 | 17.25 | 0.0771 | 0.19 | 13.03 | 0
December | 21 | 1PM to 2PM | 55 | 45.1 | 34 | 28.7 | 17.67 | 0.0769 | 0.2 | 13.06 | 0
December | 21 | 2PM to 3PM | 55.9 | 45.2 | 33.1 | 27.7 | 17.73 | 0.0768 | 0.19 | 13.08 | 0
December | 21 | 3PM to 4PM | 55.9 | 45.5 | 34 | 28.7 | 17.88 | 0.0768 | 0.2 | 13.08 | 0
December | 21 | 4PM to 5PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
December | 21 | 5PM to 6PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
December | 21 | 6PM to 7PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 21 | 7PM to 8PM | 52 | 42.2 | 30 | 24.2 | 16.23 | 0.0774 | 0.16 | 12.97 | 0
December | 21 | 8PM to 9PM | 52 | 43.3 | 33.1 | 27.7 | 16.77 | 0.0774 | 0.19 | 12.98 | 0
December | 21 | 9PM to 10PM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 0
December | 21 | 10PM to 11PM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 0
December | 21 | 11PM to 12AM | 50 | 42.3 | 33.1 | 27.7 | 16.29 | 0.0777 | 0.19 | 12.93 | 1
December | 22 | 12AM to 1AM | 50 | 41.9 | 32 | 26.5 | 16.11 | 0.0777 | 0.18 | 12.93 | 1
December | 22 | 1AM to 2AM | 50 | 41.1 | 30 | 24.2 | 15.75 | 0.0777 | 0.16 | 12.92 | 1
December | 22 | 2AM to 3AM | 48.9 | 40.9 | 30.9 | 25.2 | 15.65 | 0.0778 | 0.17 | 12.89 | 1
December | 22 | 3AM to 4AM | 48 | 40.5 | 30.9 | 25.2 | 15.43 | 0.078 | 0.17 | 12.87 | 1
December | 22 | 4AM to 5AM | 48 | 39.7 | 28.9 | 23 | 15.09 | 0.078 | 0.16 | 12.86 | 1
December | 22 | 5AM to 6AM | 48 | 39.7 | 28.9 | 23 | 15.09 | 0.078 | 0.16 | 12.86 | 1
December | 22 | 6AM to 7AM | 48 | 40.1 | 30 | 24.2 | 15.27 | 0.078 | 0.16 | 12.87 | 1
December | 22 | 7AM to 8AM | 48 | 40.1 | 30 | 24.2 | 15.27 | 0.078 | 0.16 | 12.87 | 1
December | 22 | 8AM to 9AM | 48.9 | 40.2 | 28.9 | 23 | 15.3 | 0.0779 | 0.16 | 12.89 | 1
December | 22 | 9AM to 10AM | 48.9 | 39.9 | 28 | 22.1 | 15.16 | 0.0779 | 0.15 | 12.88 | 1
December | 22 | 10AM to 11AM | 50 | 40.1 | 27 | 21 | 15.25 | 0.0777 | 0.14 | 12.91 | 1
December | 22 | 11AM to 12PM | 52 | 41.8 | 28.9 | 23 | 16.04 | 0.0774 | 0.16 | 12.96 | 0
December | 22 | 12PM to 1PM | 53.1 | 42.3 | 28.9 | 23 | 16.3 | 0.0772 | 0.16 | 12.99 | 0
December | 22 | 1PM to 2PM | 54 | 44.6 | 34 | 28.7 | 17.41 | 0.077 | 0.2 | 13.03 | 0
December | 22 | 2PM to 3PM | 55 | 44.8 | 33.1 | 27.7 | 17.51 | 0.0769 | 0.19 | 13.06 | 0
December | 22 | 3PM to 4PM | 55.9 | 45.2 | 33.1 | 27.7 | 17.73 | 0.0768 | 0.19 | 13.08 | 0
December | 22 | 4PM to 5PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
December | 22 | 5PM to 6PM | 52 | 42.5 | 30.9 | 25.2 | 16.38 | 0.0774 | 0.17 | 12.97 | 0
December | 22 | 6PM to 7PM | 50 | 41.1 | 30 | 24.2 | 15.75 | 0.0777 | 0.16 | 12.92 | 1
December | 22 | 7PM to 8PM | 48.9 | 39.5 | 27 | 21 | 14.99 | 0.0779 | 0.14 | 12.88 | 1
December | 22 | 8PM to 9PM | 46 | 39.9 | 32 | 26.5 | 15.15 | 0.0783 | 0.18 | 12.82 | 1
December | 22 | 9PM to 10PM | 46.9 | 39.2 | 28.9 | 23 | 14.82 | 0.0782 | 0.16 | 12.84 | 1
December | 22 | 10PM to 11PM | 44.1 | 38.8 | 32 | 26.5 | 14.67 | 0.0786 | 0.18 | 12.77 | 1
December | 22 | 11PM to 12AM | 44.1 | 36.9 | 27 | 21 | 13.82 | 0.0786 | 0.14 | 12.76 | 1
December | 23 | 12AM to 1AM | 44.1 | 39.5 | 34 | 28.7 | 15.01 | 0.0786 | 0.2 | 12.78 | 1
December | 23 | 1AM to 2AM | 42.1 | 38.5 | 34 | 28.7 | 14.53 | 0.0789 | 0.2 | 12.73 | 1
December | 23 | 2AM to 3AM | 39.9 | 37.8 | 35.1 | 30 | 14.21 | 0.0792 | 0.2 | 12.68 | 1
December | 23 | 3AM to 4AM | 37.9 | 36.2 | 34 | 28.7 | 13.53 | 0.0795 | 0.2 | 12.63 | 1
December | 23 | 4AM to 5AM | 41 | 37.9 | 34 | 28.7 | 14.27 | 0.079 | 0.2 | 12.7 | 1
December | 23 | 5AM to 6AM | 39 | 35.2 | 30 | 24.2 | 13.09 | 0.0794 | 0.16 | 12.64 | 1
December | 23 | 6AM to 7AM | 39 | 36 | 32 | 26.5 | 13.45 | 0.0794 | 0.18 | 12.65 | 1
December | 23 | 7AM to 8AM | 41 | 38.3 | 35.1 | 30 | 14.47 | 0.079 | 0.2 | 12.71 | 1
December | 23 | 8AM to 9AM | 45 | 41.3 | 37 | 32.5 | 15.81 | 0.0784 | 0.22 | 12.81 | 1
December | 23 | 9AM to 10AM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
December | 23 | 10AM to 11AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 23 | 11AM to 12PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 23 | 12PM to 1PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 0
December | 23 | 1PM to 2PM | 52 | 44.8 | 37 | 32.5 | 17.51 | 0.0773 | 0.22 | 12.99 | 0
December | 23 | 2PM to 3PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 23 | 3PM to 4PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
December | 23 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
December | 23 | 5PM to 6PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 23 | 6PM to 7PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
December | 23 | 7PM to 8PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 23 | 8PM to 9PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
December | 23 | 9PM to 10PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
December | 23 | 10PM to 11PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
December | 23 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
December | 24 | 12AM to 1AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 0
December | 24 | 1AM to 2AM | 48 | 42.4 | 36 | 31.1 | 16.34 | 0.0779 | 0.21 | 12.89 | 1
December | 24 | 2AM to 3AM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 0
December | 24 | 3AM to 4AM | 50 | 43.4 | 36 | 31.1 | 16.82 | 0.0776 | 0.21 | 12.94 | 1
December | 24 | 4AM to 5AM | 48 | 42.4 | 36 | 31.1 | 16.34 | 0.0779 | 0.21 | 12.89 | 1
December | 24 | 5AM to 6AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
December | 24 | 6AM to 7AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 24 | 7AM to 8AM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
December | 24 | 8AM to 9AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 24 | 9AM to 10AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 0
December | 24 | 10AM to 11AM | 54 | 46.5 | 39 | 35.1 | 18.4 | 0.077 | 0.24 | 13.05 | 0
December | 24 | 11AM to 12PM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
December | 24 | 12PM to 1PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
December | 24 | 1PM to 2PM | 55.9 | 45.9 | 35.1 | 30 | 18.08 | 0.0767 | 0.2 | 13.09 | 0
December | 24 | 2PM to 3PM | 55.9 | 44.9 | 32 | 26.5 | 17.54 | 0.0768 | 0.18 | 13.08 | 0
December | 24 | 3PM to 4PM | 55 | 45.8 | 36 | 31.1 | 18.03 | 0.0769 | 0.21 | 13.07 | 0
December | 24 | 4PM to 5PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 24 | 5PM to 6PM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
December | 24 | 6PM to 7PM | 53.1 | 44.9 | 36 | 31.1 | 17.56 | 0.0772 | 0.21 | 13.02 | 0
December | 24 | 7PM to 8PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 24 | 8PM to 9PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 24 | 9PM to 10PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
December | 24 | 10PM to 11PM | 52 | 44 | 35.1 | 30 | 17.12 | 0.0773 | 0.2 | 12.99 | 0
December | 24 | 11PM to 12AM | 51.1 | 43.6 | 35.1 | 30 | 16.91 | 0.0775 | 0.2 | 12.96 | 0
December | 25 | 12AM to 1AM | 51.1 | 42.8 | 33.1 | 27.7 | 16.55 | 0.0775 | 0.19 | 12.96 | 0
December | 25 | 1AM to 2AM | 51.1 | 42.8 | 33.1 | 27.7 | 16.55 | 0.0775 | 0.19 | 12.96 | 0
December | 25 | 2AM to 3AM | 50 | 41.9 | 32 | 26.5 | 16.11 | 0.0777 | 0.18 | 12.93 | 1
December | 25 | 3AM to 4AM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 0
December | 25 | 4AM to 5AM | 50 | 42.6 | 34 | 28.7 | 16.45 | 0.0776 | 0.2 | 12.93 | 1
December | 25 | 5AM to 6AM | 48.9 | 40.9 | 30.9 | 25.2 | 15.65 | 0.0778 | 0.17 | 12.89 | 1
December | 25 | 6AM to 7AM | 48 | 40.9 | 32 | 26.5 | 15.63 | 0.078 | 0.18 | 12.87 | 1
December | 25 | 7AM to 8AM | 48 | 41.3 | 33.1 | 27.7 | 15.81 | 0.078 | 0.19 | 12.88 | 1
December | 25 | 8AM to 9AM | 50 | 41.9 | 32 | 26.5 | 16.11 | 0.0777 | 0.18 | 12.93 | 1
December | 25 | 9AM to 10AM | 50 | 42.3 | 33.1 | 27.7 | 16.29 | 0.0777 | 0.19 | 12.93 | 1
December | 25 | 10AM to 11AM | 52 | 43.6 | 34 | 28.7 | 16.93 | 0.0773 | 0.2 | 12.98 | 0
December | 25 | 11AM to 12PM | 53.1 | 44.1 | 34 | 28.7 | 17.19 | 0.0772 | 0.2 | 13.01 | 0
December | 25 | 12PM to 1PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 25 | 1PM to 2PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 25 | 2PM to 3PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
December | 25 | 3PM to 4PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 25 | 4PM to 5PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
December | 25 | 5PM to 6PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 0
December | 25 | 6PM to 7PM | 48.9 | 42.5 | 35.1 | 30 | 16.38 | 0.0778 | 0.2 | 12.91 | 1
December | 25 | 7PM to 8PM | 48 | 41.3 | 33.1 | 27.7 | 15.81 | 0.078 | 0.19 | 12.88 | 1
December | 25 | 8PM to 9PM | 45 | 39.7 | 33.1 | 27.7 | 15.07 | 0.0784 | 0.19 | 12.8 | 1
December | 25 | 9PM to 10PM | 45 | 38.1 | 28.9 | 23 | 14.35 | 0.0785 | 0.16 | 12.79 | 1
December | 25 | 10PM to 11PM | 46 | 38.7 | 28.9 | 23 | 14.61 | 0.0783 | 0.16 | 12.81 | 1
December | 25 | 11PM to 12AM | 44.1 | 37.3 | 28 | 22.1 | 13.98 | 0.0786 | 0.15 | 12.76 | 1
December | 26 | 12AM to 1AM | 43 | 38.2 | 32 | 26.5 | 14.41 | 0.0787 | 0.18 | 12.75 | 1
December | 26 | 1AM to 2AM | 41 | 36.3 | 30 | 24.2 | 13.57 | 0.0791 | 0.16 | 12.69 | 1
December | 26 | 2AM to 3AM | 37.9 | 34.6 | 30 | 24.2 | 12.83 | 0.0796 | 0.16 | 12.61 | 1
December | 26 | 3AM to 4AM | 37.9 | 35 | 30.9 | 25.2 | 12.99 | 0.0796 | 0.17 | 12.62 | 1
December | 26 | 4AM to 5AM | 37 | 34.5 | 30.9 | 25.2 | 12.78 | 0.0797 | 0.17 | 12.59 | 1
December | 26 | 5AM to 6AM | 37.9 | 35.4 | 32 | 26.5 | 13.19 | 0.0795 | 0.18 | 12.62 | 1
December | 26 | 6AM to 7AM | 37.9 | 35.9 | 33.1 | 27.7 | 13.37 | 0.0795 | 0.19 | 12.62 | 1
December | 26 | 7AM to 8AM | 39.9 | 37.8 | 35.1 | 30 | 14.21 | 0.0792 | 0.2 | 12.68 | 1
December | 26 | 8AM to 9AM | 42.1 | 39.8 | 37 | 32.5 | 15.11 | 0.0788 | 0.22 | 12.74 | 1
December | 26 | 9AM to 10AM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
December | 26 | 10AM to 11AM | 48.9 | 42.8 | 36 | 31.1 | 16.55 | 0.0778 | 0.21 | 12.91 | 1
December | 26 | 11AM to 12PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
December | 26 | 12PM to 1PM | 51.1 | 43.2 | 34 | 28.7 | 16.71 | 0.0775 | 0.2 | 12.96 | 0
December | 26 | 1PM to 2PM | 53.1 | 43.4 | 32 | 26.5 | 16.85 | 0.0772 | 0.18 | 13 | 0
December | 26 | 2PM to 3PM | 54 | 43.5 | 30.9 | 25.2 | 16.86 | 0.0771 | 0.17 | 13.02 | 0
December | 26 | 3PM to 4PM | 52 | 43.6 | 34 | 28.7 | 16.93 | 0.0773 | 0.2 | 12.98 | 0
December | 26 | 4PM to 5PM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 0
December | 26 | 5PM to 6PM | 51.1 | 43.2 | 34 | 28.7 | 16.71 | 0.0775 | 0.2 | 12.96 | 0
December | 26 | 6PM to 7PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 26 | 7PM to 8PM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
December | 26 | 8PM to 9PM | 46 | 40.2 | 33.1 | 27.7 | 15.33 | 0.0783 | 0.19 | 12.83 | 1
December | 26 | 9PM to 10PM | 45 | 40 | 34 | 28.7 | 15.23 | 0.0784 | 0.2 | 12.8 | 1
December | 26 | 10PM to 11PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
December | 26 | 11PM to 12AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
December | 27 | 12AM to 1AM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
December | 27 | 1AM to 2AM | 41 | 38.3 | 35.1 | 30 | 14.47 | 0.079 | 0.2 | 12.71 | 1
December | 27 | 2AM to 3AM | 41 | 38.7 | 36 | 31.1 | 14.64 | 0.079 | 0.21 | 12.71 | 1
December | 27 | 3AM to 4AM | 37 | 35.7 | 34 | 28.7 | 13.31 | 0.0797 | 0.2 | 12.6 | 1
December | 27 | 4AM to 5AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
December | 27 | 5AM to 6AM | 37 | 35.7 | 34 | 28.7 | 13.31 | 0.0797 | 0.2 | 12.6 | 1
December | 27 | 6AM to 7AM | 37.9 | 36.2 | 34 | 28.7 | 13.53 | 0.0795 | 0.2 | 12.63 | 1
December | 27 | 7AM to 8AM | 42.1 | 39.3 | 36 | 31.1 | 14.9 | 0.0789 | 0.21 | 12.74 | 1
December | 27 | 8AM to 9AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
December | 27 | 9AM to 10AM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
December | 27 | 10AM to 11AM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
December | 27 | 11AM to 12PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 27 | 12PM to 1PM | 48.9 | 44.1 | 39 | 35.1 | 17.17 | 0.0778 | 0.24 | 12.92 | 1
December | 27 | 1PM to 2PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 27 | 2PM to 3PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 27 | 3PM to 4PM | 53.1 | 46.1 | 39 | 35.1 | 18.18 | 0.0771 | 0.24 | 13.03 | 0
December | 27 | 4PM to 5PM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
December | 27 | 5PM to 6PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 27 | 6PM to 7PM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
December | 27 | 7PM to 8PM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
December | 27 | 8PM to 9PM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
December | 27 | 9PM to 10PM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
December | 27 | 10PM to 11PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
December | 27 | 11PM to 12AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
December | 28 | 12AM to 1AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
December | 28 | 1AM to 2AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
December | 28 | 2AM to 3AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
December | 28 | 3AM to 4AM | 42.1 | 41 | 39.9 | 36.4 | 15.71 | 0.0788 | 0.25 | 12.75 | 1
December | 28 | 4AM to 5AM | 39.9 | 38.6 | 37 | 32.5 | 14.59 | 0.0792 | 0.22 | 12.69 | 1
December | 28 | 5AM to 6AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
December | 28 | 6AM to 7AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
December | 28 | 7AM to 8AM | 42.1 | 39.8 | 37 | 32.5 | 15.11 | 0.0788 | 0.22 | 12.74 | 1
December | 28 | 8AM to 9AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
December | 28 | 9AM to 10AM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
December | 28 | 10AM to 11AM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
December | 28 | 11AM to 12PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
December | 28 | 12PM to 1PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
December | 28 | 1PM to 2PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
December | 28 | 2PM to 3PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
December | 28 | 3PM to 4PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
December | 28 | 4PM to 5PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 28 | 5PM to 6PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
December | 28 | 6PM to 7PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
December | 28 | 7PM to 8PM | 52 | 45.6 | 39 | 35.1 | 17.92 | 0.0773 | 0.24 | 13 | 0
December | 28 | 8PM to 9PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
December | 28 | 9PM to 10PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 28 | 10PM to 11PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
December | 28 | 11PM to 12AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 29 | 12AM to 1AM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 29 | 1AM to 2AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
December | 29 | 2AM to 3AM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 29 | 3AM to 4AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
December | 29 | 4AM to 5AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 29 | 5AM to 6AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
December | 29 | 6AM to 7AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
December | 29 | 7AM to 8AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 29 | 8AM to 9AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 29 | 9AM to 10AM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 29 | 10AM to 11AM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
December | 29 | 11AM to 12PM | 54 | 48.2 | 43 | 41 | 19.31 | 0.077 | 0.28 | 13.07 | 0
December | 29 | 12PM to 1PM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
December | 29 | 1PM to 2PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
December | 29 | 2PM to 3PM | 57.9 | 48.3 | 39 | 35.1 | 19.35 | 0.0764 | 0.24 | 13.15 | 0
December | 29 | 3PM to 4PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
December | 29 | 4PM to 5PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
December | 29 | 5PM to 6PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
December | 29 | 6PM to 7PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
December | 29 | 7PM to 8PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 29 | 8PM to 9PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 29 | 9PM to 10PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 29 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 29 | 11PM to 12AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 30 | 12AM to 1AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 30 | 1AM to 2AM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
December | 30 | 2AM to 3AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
December | 30 | 3AM to 4AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 30 | 4AM to 5AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
December | 30 | 5AM to 6AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
December | 30 | 6AM to 7AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
December | 30 | 7AM to 8AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
December | 30 | 8AM to 9AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
December | 30 | 9AM to 10AM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
December | 30 | 10AM to 11AM | 55 | 47 | 39 | 35.1 | 18.66 | 0.0768 | 0.24 | 13.08 | 0
December | 30 | 11AM to 12PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
December | 30 | 12PM to 1PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
December | 30 | 1PM to 2PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
December | 30 | 2PM to 3PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
December | 30 | 3PM to 4PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
December | 30 | 4PM to 5PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 30 | 5PM to 6PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
December | 30 | 6PM to 7PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
December | 30 | 7PM to 8PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
December | 30 | 8PM to 9PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
December | 30 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
December | 30 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 0
December | 30 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 0
December | 31 | 12AM to 1AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 0
December | 31 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
December | 31 | 2AM to 3AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 31 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 31 | 4AM to 5AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 31 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
December | 31 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
December | 31 | 7AM to 8AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 31 | 8AM to 9AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 31 | 9AM to 10AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 31 | 10AM to 11AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 0
December | 31 | 11AM to 12PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 31 | 12PM to 1PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 31 | 1PM to 2PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 31 | 2PM to 3PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 31 | 3PM to 4PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
December | 31 | 4PM to 5PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
December | 31 | 5PM to 6PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 31 | 6PM to 7PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
December | 31 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 31 | 8PM to 9PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
December | 31 | 9PM to 10PM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 0
December | 31 | 10PM to 11PM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 0
December | 31 | 11PM to 12AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0

## HOA kW and kWh Savings
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2017-05-03 15:38
Project Name: | Chiller Model
Project Number:
Engineer: | David
Savings By Returning the Lead Chiller Evaporator Pump (CHWP-2) to "Auto in a Climate with 24/7 Operation and where Chilled Water was Required above 52°F
Throttled kW
| Flow rate throttled - | 1100 | gpm (assume throttled to design)
| Pump head throttled - | 40 | ft.w.c. (assume throttled to design)
| Pump efficiency throttled - | 82% | (from the pump curve at the design point)
| bhp throttled - | 13.5501 | hp
| Motor efficiency throttled - | 93% | (from the motor curve below)
| Hp into motor - | 14.57 | hp
| Closest larger VFD size - | No Drive | hp (from the VFD curves below)
| % load on VFD - | No Drive
| VFD efficiency throttled - | 100% | (from the VFD curves below)
| hp into the drive throttled - | 14.57 | hp
| kW into the drive throttled - | 10.8692 | kW
Throttled kWh (assumes 24/7 operation when above the trigger temperature)
| Temperature below which chilled water is not required - | 52 | °F, Follow the link to set the value
| Location | San Francisco, CA | Sacramento, CA | Honolulu, HI | St. Louis, MO
| Hours when Chilled Water is Not Required | 1872 | 2819 | 0 | 3617
| kW savings | 10.8692 | 10.8692 | 10.8692 | 10.8692
| Annual kWh Savings | 20347.2331 | 30640.4115 | 0 | 39314.0717
| Electric Rate (2014 Basis) | 0.1621 | 0.13308 | 0.2917 | 0.057116
| Annual $ Savings | 3298.2865 | 4077.7516 | 0 | 2245.4625

## San Francisco CA TMY3 Weather
Country: USA | [7 empty] | OAT Flag Trigger Set Point - | 52 | °F (Changing this one will change it in all four weather file tabs)
State: CALIFORNIA | [8 empty] | Back to HOA kW and kWh Saving tab
City: SAN_FRANCISCO_INTL_AP | [8 empty] | Back to Optimized kW and kWh Savings tab
Altitude: 6 ft. | [9 empty] | Number of hours less than 52.0°F in the data set - | 1872
Month | Day | Hour | Dry Bulb | Wet Bulb | Dew Point | Humidity Ratio | Enthalpy | Density | Vapor Pressure | Specific Volume | 1 if the OAT is less than 52.0°F
|  |  | °F | °F | °F | gr/lb | btu/lb | lb/cu.ft. | in. HG | cu.ft./lb
January | 1 | 12AM to 1AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 1 | 1AM to 2AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 1 | 2AM to 3AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 1 | 3AM to 4AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 1 | 4AM to 5AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 1 | 5AM to 6AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 1 | 6AM to 7AM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0787 | 0.25 | 12.78 | 1
January | 1 | 7AM to 8AM | 41 | 39.2 | 37 | 32.5 | 14.85 | 0.079 | 0.22 | 12.71 | 1
January | 1 | 8AM to 9AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
January | 1 | 9AM to 10AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 1 | 10AM to 11AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 1 | 11AM to 12PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 1 | 12PM to 1PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
January | 1 | 1PM to 2PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
January | 1 | 2PM to 3PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
January | 1 | 3PM to 4PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
January | 1 | 4PM to 5PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 1 | 5PM to 6PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
January | 1 | 6PM to 7PM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 1
January | 1 | 7PM to 8PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 1
January | 1 | 8PM to 9PM | 48 | 42.8 | 37 | 32.5 | 16.55 | 0.0779 | 0.22 | 12.89 | 1
January | 1 | 9PM to 10PM | 48.9 | 42.8 | 36 | 31.1 | 16.55 | 0.0778 | 0.21 | 12.91 | 1
January | 1 | 10PM to 11PM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
January | 1 | 11PM to 12AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 2 | 12AM to 1AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
January | 2 | 1AM to 2AM | 43 | 40.2 | 37 | 32.5 | 15.33 | 0.0787 | 0.22 | 12.76 | 1
January | 2 | 2AM to 3AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 2 | 3AM to 4AM | 39 | 37.3 | 35.1 | 30 | 13.99 | 0.0793 | 0.2 | 12.66 | 1
January | 2 | 4AM to 5AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 2 | 5AM to 6AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 2 | 6AM to 7AM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
January | 2 | 7AM to 8AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 2 | 8AM to 9AM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 1
January | 2 | 9AM to 10AM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
January | 2 | 10AM to 11AM | 57 | 46.4 | 35.1 | 30 | 18.34 | 0.0766 | 0.2 | 13.11 | 0
January | 2 | 11AM to 12PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
January | 2 | 12PM to 1PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
January | 2 | 1PM to 2PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
January | 2 | 2PM to 3PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
January | 2 | 3PM to 4PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
January | 2 | 4PM to 5PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
January | 2 | 5PM to 6PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
January | 2 | 6PM to 7PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
January | 2 | 7PM to 8PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
January | 2 | 8PM to 9PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 2 | 9PM to 10PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 2 | 10PM to 11PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 2 | 11PM to 12AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
January | 3 | 12AM to 1AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 3 | 1AM to 2AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
January | 3 | 2AM to 3AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
January | 3 | 3AM to 4AM | 57 | 46 | 34 | 28.7 | 18.15 | 0.0766 | 0.2 | 13.11 | 0
January | 3 | 4AM to 5AM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
January | 3 | 5AM to 6AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
January | 3 | 6AM to 7AM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
January | 3 | 7AM to 8AM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
January | 3 | 8AM to 9AM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
January | 3 | 9AM to 10AM | 55.9 | 45.5 | 34 | 28.7 | 17.88 | 0.0768 | 0.2 | 13.08 | 0
January | 3 | 10AM to 11AM | 54 | 46.5 | 39 | 35.1 | 18.4 | 0.077 | 0.24 | 13.05 | 0
January | 3 | 11AM to 12PM | 59 | 47 | 34 | 28.7 | 18.62 | 0.0763 | 0.2 | 13.16 | 0
January | 3 | 12PM to 1PM | 60.1 | 47.5 | 34 | 28.7 | 18.89 | 0.0761 | 0.2 | 13.19 | 0
January | 3 | 1PM to 2PM | 61 | 46.9 | 30.9 | 25.2 | 18.56 | 0.076 | 0.17 | 13.2 | 0
January | 3 | 2PM to 3PM | 61 | 46.9 | 30.9 | 25.2 | 18.56 | 0.076 | 0.17 | 13.2 | 0
January | 3 | 3PM to 4PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
January | 3 | 4PM to 5PM | 57 | 45.7 | 33.1 | 27.7 | 17.99 | 0.0766 | 0.19 | 13.11 | 0
January | 3 | 5PM to 6PM | 55 | 45.1 | 34 | 28.7 | 17.67 | 0.0769 | 0.2 | 13.06 | 0
January | 3 | 6PM to 7PM | 54 | 44.3 | 33.1 | 27.7 | 17.25 | 0.0771 | 0.19 | 13.03 | 0
January | 3 | 7PM to 8PM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
January | 3 | 8PM to 9PM | 50 | 43 | 35.1 | 30 | 16.64 | 0.0776 | 0.2 | 12.94 | 1
January | 3 | 9PM to 10PM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 3 | 10PM to 11PM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 3 | 11PM to 12AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 4 | 12AM to 1AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
January | 4 | 1AM to 2AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 4 | 2AM to 3AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 4 | 3AM to 4AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 4 | 4AM to 5AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0792 | 0.23 | 12.69 | 1
January | 4 | 5AM to 6AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 4 | 6AM to 7AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 4 | 7AM to 8AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 4 | 8AM to 9AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
January | 4 | 9AM to 10AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 4 | 10AM to 11AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 4 | 11AM to 12PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
January | 4 | 12PM to 1PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 1
January | 4 | 1PM to 2PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 1
January | 4 | 2PM to 3PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 4 | 3PM to 4PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
January | 4 | 4PM to 5PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 4 | 5PM to 6PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 4 | 6PM to 7PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
January | 4 | 7PM to 8PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 4 | 8PM to 9PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 4 | 9PM to 10PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 4 | 10PM to 11PM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
January | 4 | 11PM to 12AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 5 | 12AM to 1AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 5 | 1AM to 2AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 5 | 2AM to 3AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
January | 5 | 3AM to 4AM | 39 | 38.5 | 37.9 | 33.7 | 14.55 | 0.0793 | 0.23 | 12.67 | 1
January | 5 | 4AM to 5AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 5 | 5AM to 6AM | 39 | 38.5 | 37.9 | 33.7 | 14.55 | 0.0793 | 0.23 | 12.67 | 1
January | 5 | 6AM to 7AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 5 | 7AM to 8AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 5 | 8AM to 9AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 5 | 9AM to 10AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 5 | 10AM to 11AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
January | 5 | 11AM to 12PM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 5 | 12PM to 1PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 5 | 1PM to 2PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
January | 5 | 2PM to 3PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 5 | 3PM to 4PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 5 | 4PM to 5PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
January | 5 | 5PM to 6PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
January | 5 | 6PM to 7PM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
January | 5 | 7PM to 8PM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 5 | 8PM to 9PM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
January | 5 | 9PM to 10PM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
January | 5 | 10PM to 11PM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 5 | 11PM to 12AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 6 | 12AM to 1AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
January | 6 | 1AM to 2AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 6 | 2AM to 3AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 6 | 3AM to 4AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 6 | 4AM to 5AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 6 | 5AM to 6AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 6 | 6AM to 7AM | 42.1 | 40.6 | 39 | 35.1 | 15.52 | 0.0788 | 0.24 | 12.75 | 1
January | 6 | 7AM to 8AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
January | 6 | 8AM to 9AM | 42.1 | 40.6 | 39 | 35.1 | 15.52 | 0.0788 | 0.24 | 12.75 | 1
January | 6 | 9AM to 10AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 6 | 10AM to 11AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
January | 6 | 11AM to 12PM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
January | 6 | 12PM to 1PM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
January | 6 | 1PM to 2PM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
January | 6 | 2PM to 3PM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 6 | 3PM to 4PM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
January | 6 | 4PM to 5PM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 6 | 5PM to 6PM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
January | 6 | 6PM to 7PM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
January | 6 | 7PM to 8PM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
January | 6 | 8PM to 9PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 6 | 9PM to 10PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 6 | 10PM to 11PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 6 | 11PM to 12AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 7 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 7 | 1AM to 2AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 7 | 2AM to 3AM | 43 | 43 | 43 | 41 | 16.64 | 0.0786 | 0.28 | 12.79 | 1
January | 7 | 3AM to 4AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 7 | 4AM to 5AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 7 | 5AM to 6AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 7 | 6AM to 7AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
January | 7 | 7AM to 8AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 7 | 8AM to 9AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 7 | 9AM to 10AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 7 | 10AM to 11AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 7 | 11AM to 12PM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 7 | 12PM to 1PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 7 | 1PM to 2PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 7 | 2PM to 3PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 7 | 3PM to 4PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 7 | 4PM to 5PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 7 | 5PM to 6PM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 7 | 6PM to 7PM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 7 | 7PM to 8PM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 7 | 8PM to 9PM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
January | 7 | 9PM to 10PM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
January | 7 | 10PM to 11PM | 43 | 43 | 43 | 41 | 16.64 | 0.0786 | 0.28 | 12.79 | 1
January | 7 | 11PM to 12AM | 42.1 | 42.1 | 42.1 | 39.6 | 16.21 | 0.0788 | 0.27 | 12.76 | 1
January | 8 | 12AM to 1AM | 42.1 | 42.1 | 42.1 | 39.6 | 16.21 | 0.0788 | 0.27 | 12.76 | 1
January | 8 | 1AM to 2AM | 41 | 41 | 41 | 38 | 15.69 | 0.079 | 0.26 | 12.73 | 1
January | 8 | 2AM to 3AM | 41 | 41 | 41 | 38 | 15.69 | 0.079 | 0.26 | 12.73 | 1
January | 8 | 3AM to 4AM | 41 | 41 | 41 | 38 | 15.69 | 0.079 | 0.26 | 12.73 | 1
January | 8 | 4AM to 5AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0792 | 0.25 | 12.7 | 1
January | 8 | 5AM to 6AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0792 | 0.25 | 12.7 | 1
January | 8 | 6AM to 7AM | 39 | 39 | 39 | 35.1 | 14.78 | 0.0793 | 0.24 | 12.67 | 1
January | 8 | 7AM to 8AM | 39 | 39 | 39 | 35.1 | 14.78 | 0.0793 | 0.24 | 12.67 | 1
January | 8 | 8AM to 9AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0793 | 0.24 | 12.68 | 1
January | 8 | 9AM to 10AM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
January | 8 | 10AM to 11AM | 48.2 | 42.3 | 35.6 | 30.7 | 16.31 | 0.0779 | 0.21 | 12.89 | 1
January | 8 | 11AM to 12PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
January | 8 | 12PM to 1PM | 55.4 | 45.2 | 33.8 | 28.5 | 17.72 | 0.0768 | 0.19 | 13.07 | 0
January | 8 | 1PM to 2PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.0771 | 0.24 | 13.04 | 0
January | 8 | 2PM to 3PM | 57.2 | 45.5 | 32 | 26.5 | 17.85 | 0.0766 | 0.18 | 13.11 | 0
January | 8 | 3PM to 4PM | 57 | 45.7 | 33.1 | 27.7 | 17.99 | 0.0766 | 0.19 | 13.11 | 0
January | 8 | 4PM to 5PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 1
January | 8 | 5PM to 6PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
January | 8 | 6PM to 7PM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
January | 8 | 7PM to 8PM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 8 | 8PM to 9PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
January | 8 | 9PM to 10PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 8 | 10PM to 11PM | 48.9 | 43.3 | 37 | 32.5 | 16.77 | 0.0778 | 0.22 | 12.92 | 1
January | 8 | 11PM to 12AM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
January | 9 | 12AM to 1AM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
January | 9 | 1AM to 2AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
January | 9 | 2AM to 3AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
January | 9 | 3AM to 4AM | 43 | 39.8 | 36 | 31.1 | 15.12 | 0.0787 | 0.21 | 12.76 | 1
January | 9 | 4AM to 5AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
January | 9 | 5AM to 6AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 9 | 6AM to 7AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 9 | 7AM to 8AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
January | 9 | 8AM to 9AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.81 | 1
January | 9 | 9AM to 10AM | 45 | 41.3 | 37 | 32.5 | 15.81 | 0.0784 | 0.22 | 12.81 | 1
January | 9 | 10AM to 11AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0782 | 0.22 | 12.85 | 1
January | 9 | 11AM to 12PM | 46.4 | 43.7 | 41 | 38 | 17 | 0.0781 | 0.26 | 12.87 | 1
January | 9 | 12PM to 1PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0779 | 0.24 | 12.91 | 1
January | 9 | 1PM to 2PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0779 | 0.24 | 12.91 | 1
January | 9 | 2PM to 3PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
January | 9 | 3PM to 4PM | 51.3 | 46.1 | 41 | 38 | 18.18 | 0.0774 | 0.26 | 12.99 | 1
January | 9 | 4PM to 5PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
January | 9 | 5PM to 6PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 9 | 6PM to 7PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
January | 9 | 7PM to 8PM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
January | 9 | 8PM to 9PM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
January | 9 | 9PM to 10PM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
January | 9 | 10PM to 11PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 9 | 11PM to 12AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 12AM to 1AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 10 | 1AM to 2AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 2AM to 3AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 10 | 3AM to 4AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 10 | 4AM to 5AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
January | 10 | 5AM to 6AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
January | 10 | 6AM to 7AM | 39.9 | 38.6 | 37 | 32.5 | 14.59 | 0.0792 | 0.22 | 12.69 | 1
January | 10 | 7AM to 8AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 10 | 8AM to 9AM | 44.2 | 41.3 | 38.1 | 33.9 | 15.85 | 0.0785 | 0.23 | 12.8 | 1
January | 10 | 9AM to 10AM | 44.2 | 41.2 | 37.8 | 33.4 | 15.78 | 0.0785 | 0.23 | 12.8 | 1
January | 10 | 10AM to 11AM | 44.8 | 41.5 | 37.9 | 33.7 | 15.95 | 0.0784 | 0.23 | 12.81 | 1
January | 10 | 11AM to 12PM | 45.5 | 42.7 | 39.7 | 36.1 | 16.5 | 0.0783 | 0.25 | 12.84 | 1
January | 10 | 12PM to 1PM | 47.1 | 43 | 38.7 | 34.6 | 16.66 | 0.078 | 0.24 | 12.88 | 1
January | 10 | 1PM to 2PM | 46.9 | 42.9 | 38.5 | 34.4 | 16.58 | 0.0781 | 0.23 | 12.87 | 1
January | 10 | 2PM to 3PM | 49.5 | 44.1 | 38.5 | 34.4 | 17.19 | 0.0777 | 0.23 | 12.93 | 1
January | 10 | 3PM to 4PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 10 | 4PM to 5PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 10 | 5PM to 6PM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
January | 10 | 6PM to 7PM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
January | 10 | 7PM to 8PM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
January | 10 | 8PM to 9PM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 9PM to 10PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 10 | 10PM to 11PM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 11PM to 12AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 11 | 12AM to 1AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 11 | 1AM to 2AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 11 | 2AM to 3AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
January | 11 | 3AM to 4AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
January | 11 | 4AM to 5AM | 41 | 39.2 | 37 | 32.5 | 14.85 | 0.079 | 0.22 | 12.71 | 1
January | 11 | 5AM to 6AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
January | 11 | 6AM to 7AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
January | 11 | 7AM to 8AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0792 | 0.23 | 12.69 | 1
January | 11 | 8AM to 9AM | 42.8 | 40.3 | 37.4 | 33 | 15.36 | 0.0787 | 0.22 | 12.76 | 1
January | 11 | 9AM to 10AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
January | 11 | 10AM to 11AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.77 | 1
January | 11 | 11AM to 12PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.81 | 1
January | 11 | 12PM to 1PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.6 | 0.0782 | 0.24 | 12.86 | 1
January | 11 | 1PM to 2PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.6 | 0.0782 | 0.24 | 12.86 | 1
January | 11 | 2PM to 3PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0779 | 0.24 | 12.91 | 1
January | 11 | 3PM to 4PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 11 | 4PM to 5PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
January | 11 | 5PM to 6PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 11 | 6PM to 7PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 11 | 7PM to 8PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 11 | 8PM to 9PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 11 | 9PM to 10PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 11 | 10PM to 11PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 11 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 12 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 12 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 12 | 2AM to 3AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
January | 12 | 3AM to 4AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 12 | 4AM to 5AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 12 | 5AM to 6AM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
January | 12 | 6AM to 7AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
January | 12 | 7AM to 8AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
January | 12 | 8AM to 9AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
January | 12 | 9AM to 10AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
January | 12 | 10AM to 11AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
January | 12 | 11AM to 12PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 12PM to 1PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
January | 12 | 1PM to 2PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 2PM to 3PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
January | 12 | 3PM to 4PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 12 | 4PM to 5PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 12 | 5PM to 6PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 6PM to 7PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 7PM to 8PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 8PM to 9PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 12 | 9PM to 10PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 12 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 12 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 13 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 13 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 13 | 2AM to 3AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
January | 13 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 13 | 4AM to 5AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.98 | 1
January | 13 | 5AM to 6AM | 48.9 | 46.7 | 44.6 | 43.7 | 18.49 | 0.0777 | 0.3 | 12.95 | 1
January | 13 | 6AM to 7AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
January | 13 | 7AM to 8AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 13 | 8AM to 9AM | 48.9 | 45.8 | 42.8 | 40.7 | 18.04 | 0.0777 | 0.28 | 12.94 | 1
January | 13 | 9AM to 10AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 13 | 10AM to 11AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 13 | 11AM to 12PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
January | 13 | 12PM to 1PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
January | 13 | 1PM to 2PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 13 | 2PM to 3PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 13 | 3PM to 4PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 13 | 4PM to 5PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 13 | 5PM to 6PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 13 | 6PM to 7PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 13 | 7PM to 8PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 13 | 8PM to 9PM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 13 | 9PM to 10PM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 13 | 10PM to 11PM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 13 | 11PM to 12AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 14 | 12AM to 1AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 14 | 1AM to 2AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 14 | 2AM to 3AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 14 | 3AM to 4AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
January | 14 | 4AM to 5AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 14 | 5AM to 6AM | 46 | 46 | 46 | 46.1 | 18.18 | 0.0781 | 0.31 | 12.88 | 1
January | 14 | 6AM to 7AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
January | 14 | 7AM to 8AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
January | 14 | 8AM to 9AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
January | 14 | 9AM to 10AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
January | 14 | 10AM to 11AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
January | 14 | 11AM to 12PM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 14 | 12PM to 1PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 14 | 1PM to 2PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
January | 14 | 2PM to 3PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
January | 14 | 3PM to 4PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 14 | 4PM to 5PM | 54 | 48.2 | 43 | 41 | 19.31 | 0.077 | 0.28 | 13.07 | 0
January | 14 | 5PM to 6PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
January | 14 | 6PM to 7PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
January | 14 | 7PM to 8PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
January | 14 | 8PM to 9PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 14 | 9PM to 10PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
January | 14 | 10PM to 11PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
January | 14 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
January | 15 | 12AM to 1AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 15 | 1AM to 2AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 15 | 2AM to 3AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
January | 15 | 3AM to 4AM | 48 | 47.4 | 46.9 | 47.8 | 18.91 | 0.0778 | 0.32 | 12.94 | 1
January | 15 | 4AM to 5AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
January | 15 | 5AM to 6AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
January | 15 | 6AM to 7AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
January | 15 | 7AM to 8AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
January | 15 | 8AM to 9AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 15 | 9AM to 10AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 15 | 10AM to 11AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
January | 15 | 11AM to 12PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
January | 15 | 12PM to 1PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
January | 15 | 1PM to 2PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
January | 15 | 2PM to 3PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 15 | 3PM to 4PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
January | 15 | 4PM to 5PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 15 | 5PM to 6PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
January | 15 | 6PM to 7PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 15 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 15 | 8PM to 9PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
January | 15 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 15 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 15 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 16 | 12AM to 1AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 16 | 1AM to 2AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 16 | 2AM to 3AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 16 | 3AM to 4AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 16 | 4AM to 5AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 16 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 16 | 6AM to 7AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 16 | 7AM to 8AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 16 | 8AM to 9AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 16 | 9AM to 10AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 16 | 10AM to 11AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
January | 16 | 11AM to 12PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
January | 16 | 12PM to 1PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
January | 16 | 1PM to 2PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 16 | 2PM to 3PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
January | 16 | 3PM to 4PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
January | 16 | 4PM to 5PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
January | 16 | 5PM to 6PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
January | 16 | 6PM to 7PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 16 | 7PM to 8PM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
January | 16 | 8PM to 9PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 16 | 9PM to 10PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
January | 16 | 10PM to 11PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 16 | 11PM to 12AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 17 | 12AM to 1AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 17 | 1AM to 2AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
January | 17 | 2AM to 3AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
January | 17 | 3AM to 4AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
January | 17 | 4AM to 5AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
January | 17 | 5AM to 6AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 17 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
January | 17 | 7AM to 8AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 17 | 8AM to 9AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
January | 17 | 9AM to 10AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
January | 17 | 10AM to 11AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
January | 17 | 11AM to 12PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
January | 17 | 12PM to 1PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
January | 17 | 1PM to 2PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
January | 17 | 2PM to 3PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
January | 17 | 3PM to 4PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 17 | 4PM to 5PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 17 | 5PM to 6PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 17 | 6PM to 7PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 17 | 7PM to 8PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 17 | 8PM to 9PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 17 | 9PM to 10PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
January | 17 | 10PM to 11PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 17 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 18 | 12AM to 1AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 1AM to 2AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 2AM to 3AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 4AM to 5AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 5AM to 6AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 6AM to 7AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 18 | 7AM to 8AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 8AM to 9AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 18 | 9AM to 10AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 10AM to 11AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 18 | 11AM to 12PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 12PM to 1PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
January | 18 | 1PM to 2PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 18 | 2PM to 3PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 3PM to 4PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 18 | 4PM to 5PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
January | 18 | 5PM to 6PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
January | 18 | 6PM to 7PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
January | 18 | 7PM to 8PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 18 | 8PM to 9PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
January | 18 | 9PM to 10PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
January | 18 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 18 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 19 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 19 | 1AM to 2AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
January | 19 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 19 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 19 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 19 | 5AM to 6AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 19 | 6AM to 7AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 19 | 7AM to 8AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 19 | 8AM to 9AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
January | 19 | 9AM to 10AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 19 | 10AM to 11AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
January | 19 | 11AM to 12PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 19 | 12PM to 1PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
January | 19 | 1PM to 2PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
January | 19 | 2PM to 3PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
January | 19 | 3PM to 4PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
January | 19 | 4PM to 5PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
January | 19 | 5PM to 6PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
January | 19 | 6PM to 7PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 19 | 7PM to 8PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
January | 19 | 8PM to 9PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
January | 19 | 9PM to 10PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
January | 19 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 19 | 11PM to 12AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 20 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
January | 20 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
January | 20 | 2AM to 3AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 20 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 20 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 20 | 5AM to 6AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 20 | 6AM to 7AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 20 | 7AM to 8AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
January | 20 | 8AM to 9AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 20 | 9AM to 10AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 20 | 10AM to 11AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
January | 20 | 11AM to 12PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
January | 20 | 12PM to 1PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
January | 20 | 1PM to 2PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
January | 20 | 2PM to 3PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
January | 20 | 3PM to 4PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
January | 20 | 4PM to 5PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
January | 20 | 5PM to 6PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
January | 20 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
January | 20 | 7PM to 8PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
January | 20 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
January | 20 | 9PM to 10PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
January | 20 | 10PM to 11PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
January | 20 | 11PM to 12AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
January | 21 | 12AM to 1AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 21 | 1AM to 2AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 21 | 2AM to 3AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 21 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 21 | 4AM to 5AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 21 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
January | 21 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 21 | 7AM to 8AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 21 | 8AM to 9AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
January | 21 | 9AM to 10AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
January | 21 | 10AM to 11AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
January | 21 | 11AM to 12PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
January | 21 | 12PM to 1PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
January | 21 | 1PM to 2PM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
January | 21 | 2PM to 3PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
January | 21 | 3PM to 4PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
January | 21 | 4PM to 5PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
January | 21 | 5PM to 6PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
January | 21 | 6PM to 7PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
January | 21 | 7PM to 8PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
January | 21 | 8PM to 9PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
January | 21 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
January | 21 | 10PM to 11PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
January | 21 | 11PM to 12AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 22 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
January | 22 | 1AM to 2AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
January | 22 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
January | 22 | 3AM to 4AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
January | 22 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 22 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 22 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
January | 22 | 7AM to 8AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
January | 22 | 8AM to 9AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
January | 22 | 9AM to 10AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 22 | 10AM to 11AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
January | 22 | 11AM to 12PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
January | 22 | 12PM to 1PM | 57 | 48.7 | 41 | 38 | 19.58 | 0.0765 | 0.26 | 13.14 | 0
January | 22 | 1PM to 2PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
January | 22 | 2PM to 3PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
January | 22 | 3PM to 4PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 22 | 4PM to 5PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
January | 22 | 5PM to 6PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
January | 22 | 6PM to 7PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 22 | 7PM to 8PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
January | 22 | 8PM to 9PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
January | 22 | 9PM to 10PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
January | 22 | 10PM to 11PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 22 | 11PM to 12AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
January | 23 | 12AM to 1AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
January | 23 | 1AM to 2AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
January | 23 | 2AM to 3AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
January | 23 | 3AM to 4AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
January | 23 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
January | 23 | 5AM to 6AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 23 | 6AM to 7AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
January | 23 | 7AM to 8AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 23 | 8AM to 9AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 23 | 9AM to 10AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
January | 23 | 10AM to 11AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 23 | 11AM to 12PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 23 | 12PM to 1PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
January | 23 | 1PM to 2PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
January | 23 | 2PM to 3PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
January | 23 | 3PM to 4PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 23 | 4PM to 5PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
January | 23 | 5PM to 6PM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
January | 23 | 6PM to 7PM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
January | 23 | 7PM to 8PM | 45 | 40.4 | 35.1 | 30 | 15.43 | 0.0784 | 0.2 | 12.81 | 1
January | 23 | 8PM to 9PM | 45 | 40 | 34 | 28.7 | 15.23 | 0.0784 | 0.2 | 12.8 | 1
January | 23 | 9PM to 10PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
January | 23 | 10PM to 11PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
January | 23 | 11PM to 12AM | 44.1 | 39.2 | 33.1 | 27.7 | 14.85 | 0.0786 | 0.19 | 12.78 | 1
January | 24 | 12AM to 1AM | 42.1 | 38.1 | 33.1 | 27.7 | 14.37 | 0.0789 | 0.19 | 12.73 | 1
January | 24 | 1AM to 2AM | 39 | 36 | 32 | 26.5 | 13.45 | 0.0794 | 0.18 | 12.65 | 1
January | 24 | 2AM to 3AM | 37.9 | 35 | 30.9 | 25.2 | 12.99 | 0.0796 | 0.17 | 12.62 | 1
January | 24 | 3AM to 4AM | 37 | 34.5 | 30.9 | 25.2 | 12.78 | 0.0797 | 0.17 | 12.59 | 1
January | 24 | 4AM to 5AM | 39 | 35.2 | 30 | 24.2 | 13.09 | 0.0794 | 0.16 | 12.64 | 1
January | 24 | 5AM to 6AM | 36 | 33.8 | 30.9 | 25.2 | 12.51 | 0.0799 | 0.17 | 12.57 | 1
January | 24 | 6AM to 7AM | 37.9 | 35 | 30.9 | 25.2 | 12.99 | 0.0796 | 0.17 | 12.62 | 1
January | 24 | 7AM to 8AM | 39 | 36 | 32 | 26.5 | 13.45 | 0.0794 | 0.18 | 12.65 | 1
January | 24 | 8AM to 9AM | 43 | 38.2 | 32 | 26.5 | 14.41 | 0.0787 | 0.18 | 12.75 | 1
January | 24 | 9AM to 10AM | 45 | 39.3 | 32 | 26.5 | 14.89 | 0.0784 | 0.18 | 12.8 | 1
January | 24 | 10AM to 11AM | 46 | 40.6 | 34 | 28.7 | 15.49 | 0.0783 | 0.2 | 12.83 | 1
January | 24 | 11AM to 12PM | 46 | 40.6 | 34 | 28.7 | 15.49 | 0.0783 | 0.2 | 12.83 | 1
January | 24 | 12PM to 1PM | 48 | 41.6 | 34 | 28.7 | 15.97 | 0.078 | 0.2 | 12.88 | 1
January | 24 | 1PM to 2PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
January | 24 | 2PM to 3PM | 52 | 43.6 | 34 | 28.7 | 16.93 | 0.0773 | 0.2 | 12.98 | 0
January | 24 | 3PM to 4PM | 50 | 43 | 35.1 | 30 | 16.64 | 0.0776 | 0.2 | 12.94 | 1
January | 24 | 4PM to 5PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
January | 24 | 5PM to 6PM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
January | 24 | 6PM to 7PM | 46.9 | 40.7 | 33.1 | 27.7 | 15.55 | 0.0781 | 0.19 | 12.85 | 1
January | 24 | 7PM to 8PM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
January | 24 | 8PM to 9PM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
January | 24 | 9PM to 10PM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
January | 24 | 10PM to 11PM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
January | 24 | 11PM to 12AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
January | 25 | 12AM to 1AM | 48 | 42 | 35.1 | 30 | 16.17 | 0.0779 | 0.2 | 12.89 | 1
January | 25 | 1AM to 2AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
January | 25 | 2AM to 3AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 25 | 3AM to 4AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 25 | 4AM to 5AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 25 | 5AM to 6AM | 46.9 | 41.1 | 34 | 28.7 | 15.71 | 0.0781 | 0.2 | 12.85 | 1
January | 25 | 6AM to 7AM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
January | 25 | 7AM to 8AM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
January | 25 | 8AM to 9AM | 46.9 | 41.1 | 34 | 28.7 | 15.71 | 0.0781 | 0.2 | 12.85 | 1
January | 25 | 9AM to 10AM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
January | 25 | 10AM to 11AM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 25 | 11AM to 12PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
January | 25 | 12PM to 1PM | 53.1 | 46.1 | 39 | 35.1 | 18.18 | 0.0771 | 0.24 | 13.03 | 0
January | 25 | 1PM to 2PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 25 | 2PM to 3PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 25 | 3PM to 4PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
January | 25 | 4PM to 5PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
January | 25 | 5PM to 6PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 25 | 6PM to 7PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
January | 25 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
January | 25 | 8PM to 9PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
January | 25 | 9PM to 10PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 25 | 10PM to 11PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 25 | 11PM to 12AM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 26 | 12AM to 1AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 26 | 1AM to 2AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
January | 26 | 2AM to 3AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 26 | 3AM to 4AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 26 | 4AM to 5AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 26 | 5AM to 6AM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
January | 26 | 6AM to 7AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 26 | 7AM to 8AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
January | 26 | 8AM to 9AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
January | 26 | 9AM to 10AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
January | 26 | 10AM to 11AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 26 | 11AM to 12PM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 26 | 12PM to 1PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 26 | 1PM to 2PM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
January | 26 | 2PM to 3PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
January | 26 | 3PM to 4PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
January | 26 | 4PM to 5PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 26 | 5PM to 6PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
January | 26 | 6PM to 7PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
January | 26 | 7PM to 8PM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
January | 26 | 8PM to 9PM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
January | 26 | 9PM to 10PM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
January | 26 | 10PM to 11PM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
January | 26 | 11PM to 12AM | 43 | 39.8 | 36 | 31.1 | 15.12 | 0.0787 | 0.21 | 12.76 | 1
January | 27 | 12AM to 1AM | 42.1 | 39.3 | 36 | 31.1 | 14.9 | 0.0789 | 0.21 | 12.74 | 1
January | 27 | 1AM to 2AM | 42.1 | 39.8 | 37 | 32.5 | 15.11 | 0.0788 | 0.22 | 12.74 | 1
January | 27 | 2AM to 3AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
January | 27 | 3AM to 4AM | 39 | 38.5 | 37.9 | 33.7 | 14.55 | 0.0793 | 0.23 | 12.67 | 1
January | 27 | 4AM to 5AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
January | 27 | 5AM to 6AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
January | 27 | 6AM to 7AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 27 | 7AM to 8AM | 39.9 | 38.6 | 37 | 32.5 | 14.59 | 0.0792 | 0.22 | 12.69 | 1
January | 27 | 8AM to 9AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
January | 27 | 9AM to 10AM | 48.9 | 42.8 | 36 | 31.1 | 16.55 | 0.0778 | 0.21 | 12.91 | 1
January | 27 | 10AM to 11AM | 52 | 44.8 | 37 | 32.5 | 17.51 | 0.0773 | 0.22 | 12.99 | 0
January | 27 | 11AM to 12PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
January | 27 | 12PM to 1PM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
January | 27 | 1PM to 2PM | 55.9 | 45.9 | 35.1 | 30 | 18.08 | 0.0767 | 0.2 | 13.09 | 0
January | 27 | 2PM to 3PM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
January | 27 | 3PM to 4PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
January | 27 | 4PM to 5PM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
January | 27 | 5PM to 6PM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
January | 27 | 6PM to 7PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
January | 27 | 7PM to 8PM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
January | 27 | 8PM to 9PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 27 | 9PM to 10PM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
January | 27 | 10PM to 11PM | 46 | 41 | 35.1 | 30 | 15.69 | 0.0782 | 0.2 | 12.83 | 1
January | 27 | 11PM to 12AM | 45 | 40.4 | 35.1 | 30 | 15.43 | 0.0784 | 0.2 | 12.81 | 1
January | 28 | 12AM to 1AM | 43 | 39.8 | 36 | 31.1 | 15.12 | 0.0787 | 0.21 | 12.76 | 1
January | 28 | 1AM to 2AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
January | 28 | 2AM to 3AM | 39.9 | 37.8 | 35.1 | 30 | 14.21 | 0.0792 | 0.2 | 12.68 | 1
January | 28 | 3AM to 4AM | 39 | 37.3 | 35.1 | 30 | 13.99 | 0.0793 | 0.2 | 12.66 | 1
January | 28 | 4AM to 5AM | 39 | 37.3 | 35.1 | 30 | 13.99 | 0.0793 | 0.2 | 12.66 | 1
January | 28 | 5AM to 6AM | 37.9 | 36.2 | 34 | 28.7 | 13.53 | 0.0795 | 0.2 | 12.63 | 1
January | 28 | 6AM to 7AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
January | 28 | 7AM to 8AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
January | 28 | 8AM to 9AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
January | 28 | 9AM to 10AM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
January | 28 | 10AM to 11AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
January | 28 | 11AM to 12PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 28 | 12PM to 1PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
January | 28 | 1PM to 2PM | 54 | 48.2 | 43 | 41 | 19.31 | 0.077 | 0.28 | 13.07 | 0
January | 28 | 2PM to 3PM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
January | 28 | 3PM to 4PM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
January | 28 | 4PM to 5PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
January | 28 | 5PM to 6PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 28 | 6PM to 7PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
January | 28 | 7PM to 8PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 28 | 8PM to 9PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 28 | 9PM to 10PM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 28 | 10PM to 11PM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
January | 28 | 11PM to 12AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
January | 29 | 12AM to 1AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 29 | 1AM to 2AM | 43 | 42 | 41 | 38 | 16.17 | 0.0787 | 0.26 | 12.78 | 1
January | 29 | 2AM to 3AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
January | 29 | 3AM to 4AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 29 | 4AM to 5AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0792 | 0.25 | 12.7 | 1
January | 29 | 5AM to 6AM | 39.9 | 39.5 | 39 | 35.1 | 14.99 | 0.0792 | 0.24 | 12.69 | 1
January | 29 | 6AM to 7AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 29 | 7AM to 8AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 29 | 8AM to 9AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
January | 29 | 9AM to 10AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
January | 29 | 10AM to 11AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 29 | 11AM to 12PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 29 | 12PM to 1PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
January | 29 | 1PM to 2PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
January | 29 | 2PM to 3PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
January | 29 | 3PM to 4PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 29 | 4PM to 5PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
January | 29 | 5PM to 6PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
January | 29 | 6PM to 7PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
January | 29 | 7PM to 8PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 29 | 8PM to 9PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 29 | 9PM to 10PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 29 | 10PM to 11PM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 29 | 11PM to 12AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 30 | 12AM to 1AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
January | 30 | 1AM to 2AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 30 | 2AM to 3AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
January | 30 | 3AM to 4AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 30 | 4AM to 5AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
January | 30 | 5AM to 6AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
January | 30 | 6AM to 7AM | 43 | 42.5 | 42.1 | 39.6 | 16.43 | 0.0787 | 0.27 | 12.79 | 1
January | 30 | 7AM to 8AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
January | 30 | 8AM to 9AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 30 | 9AM to 10AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
January | 30 | 10AM to 11AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
January | 30 | 11AM to 12PM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
January | 30 | 12PM to 1PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
January | 30 | 1PM to 2PM | 57.9 | 49.6 | 42.1 | 39.6 | 20.05 | 0.0764 | 0.27 | 13.17 | 0
January | 30 | 2PM to 3PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
January | 30 | 3PM to 4PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
January | 30 | 4PM to 5PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
January | 30 | 5PM to 6PM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
January | 30 | 6PM to 7PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 30 | 7PM to 8PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 30 | 8PM to 9PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
January | 30 | 9PM to 10PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 30 | 10PM to 11PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
January | 30 | 11PM to 12AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
January | 31 | 12AM to 1AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 31 | 1AM to 2AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
January | 31 | 2AM to 3AM | 48 | 47.4 | 46.9 | 47.8 | 18.91 | 0.0778 | 0.32 | 12.94 | 1
January | 31 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 31 | 4AM to 5AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
January | 31 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 31 | 6AM to 7AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
January | 31 | 7AM to 8AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
January | 31 | 8AM to 9AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
January | 31 | 9AM to 10AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
January | 31 | 10AM to 11AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
January | 31 | 11AM to 12PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 1
January | 31 | 12PM to 1PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
January | 31 | 1PM to 2PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
January | 31 | 2PM to 3PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
January | 31 | 3PM to 4PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
January | 31 | 4PM to 5PM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
January | 31 | 5PM to 6PM | 48 | 42.8 | 37 | 32.5 | 16.55 | 0.0779 | 0.22 | 12.89 | 1
January | 31 | 6PM to 7PM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
January | 31 | 7PM to 8PM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
January | 31 | 8PM to 9PM | 46.9 | 42.6 | 37.9 | 33.7 | 16.47 | 0.0781 | 0.23 | 12.87 | 1
January | 31 | 9PM to 10PM | 46.6 | 42.6 | 38.3 | 34.1 | 16.46 | 0.0781 | 0.23 | 12.86 | 1
January | 31 | 10PM to 11PM | 46.4 | 42.6 | 38.5 | 34.4 | 16.45 | 0.0782 | 0.23 | 12.86 | 1
January | 31 | 11PM to 12AM | 46 | 42.6 | 38.8 | 34.9 | 16.44 | 0.0782 | 0.24 | 12.85 | 1
February | 1 | 12AM to 1AM | 45.9 | 42.6 | 39 | 35.1 | 16.43 | 0.0782 | 0.24 | 12.85 | 1
February | 1 | 1AM to 2AM | 45.5 | 42.5 | 39.4 | 35.6 | 16.42 | 0.0783 | 0.24 | 12.84 | 1
February | 1 | 2AM to 3AM | 45.3 | 42.5 | 39.6 | 35.9 | 16.42 | 0.0783 | 0.24 | 12.83 | 1
February | 1 | 3AM to 4AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 1 | 4AM to 5AM | 45.3 | 43.1 | 40.8 | 37.7 | 16.7 | 0.0783 | 0.26 | 12.84 | 1
February | 1 | 5AM to 6AM | 45.7 | 43.9 | 42.1 | 39.6 | 17.08 | 0.0782 | 0.27 | 12.85 | 1
February | 1 | 6AM to 7AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
February | 1 | 7AM to 8AM | 46.9 | 45.1 | 43.3 | 41.6 | 17.69 | 0.078 | 0.28 | 12.89 | 1
February | 1 | 8AM to 9AM | 48 | 45.6 | 43.3 | 41.6 | 17.96 | 0.0779 | 0.28 | 12.92 | 1
February | 1 | 9AM to 10AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
February | 1 | 10AM to 11AM | 51.3 | 46.1 | 41 | 38 | 18.18 | 0.0774 | 0.26 | 12.99 | 1
February | 1 | 11AM to 12PM | 53.6 | 46.3 | 39 | 35.1 | 18.31 | 0.0771 | 0.24 | 13.04 | 0
February | 1 | 12PM to 1PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
February | 1 | 1PM to 2PM | 56.3 | 47.2 | 38.1 | 33.9 | 18.77 | 0.0767 | 0.23 | 13.11 | 0
February | 1 | 2PM to 3PM | 56.7 | 47.7 | 38.8 | 34.9 | 19.01 | 0.0766 | 0.24 | 13.12 | 0
February | 1 | 3PM to 4PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
February | 1 | 4PM to 5PM | 55.4 | 47.9 | 40.6 | 37.4 | 19.1 | 0.0768 | 0.25 | 13.09 | 0
February | 1 | 5PM to 6PM | 53.6 | 47.4 | 41.5 | 38.8 | 18.87 | 0.077 | 0.26 | 13.05 | 0
February | 1 | 6PM to 7PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
February | 1 | 7PM to 8PM | 51.6 | 47.3 | 43.3 | 41.6 | 18.83 | 0.0773 | 0.28 | 13.01 | 1
February | 1 | 8PM to 9PM | 51.4 | 47.6 | 44.1 | 42.8 | 18.97 | 0.0773 | 0.29 | 13.01 | 1
February | 1 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
February | 1 | 10PM to 11PM | 49.1 | 46 | 43 | 41 | 18.13 | 0.0777 | 0.28 | 12.94 | 1
February | 1 | 11PM to 12AM | 46.9 | 44.1 | 41.2 | 38.2 | 17.18 | 0.0781 | 0.26 | 12.88 | 1
February | 2 | 12AM to 1AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 2 | 1AM to 2AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
February | 2 | 2AM to 3AM | 43 | 41 | 38.8 | 34.9 | 15.7 | 0.0787 | 0.24 | 12.77 | 1
February | 2 | 3AM to 4AM | 42.1 | 40.6 | 39 | 35.1 | 15.52 | 0.0788 | 0.24 | 12.75 | 1
February | 2 | 4AM to 5AM | 42.8 | 40.8 | 38.5 | 34.4 | 15.58 | 0.0787 | 0.23 | 12.77 | 1
February | 2 | 5AM to 6AM | 43.3 | 41 | 38.5 | 34.4 | 15.71 | 0.0786 | 0.23 | 12.78 | 1
February | 2 | 6AM to 7AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
February | 2 | 7AM to 8AM | 44.8 | 41.7 | 38.3 | 34.1 | 16.02 | 0.0784 | 0.23 | 12.81 | 1
February | 2 | 8AM to 9AM | 45.3 | 42 | 38.3 | 34.1 | 16.15 | 0.0783 | 0.23 | 12.83 | 1
February | 2 | 9AM to 10AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
February | 2 | 10AM to 11AM | 47.3 | 42.7 | 37.8 | 33.4 | 16.52 | 0.078 | 0.23 | 12.88 | 1
February | 2 | 11AM to 12PM | 48.7 | 43.3 | 37.4 | 33 | 16.79 | 0.0778 | 0.22 | 12.91 | 1
February | 2 | 12PM to 1PM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
February | 2 | 1PM to 2PM | 50.4 | 44.1 | 37.4 | 33 | 17.19 | 0.0776 | 0.22 | 12.95 | 1
February | 2 | 2PM to 3PM | 50.7 | 44.3 | 37.4 | 33 | 17.27 | 0.0775 | 0.22 | 12.96 | 1
February | 2 | 3PM to 4PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 1
February | 2 | 4PM to 5PM | 50.4 | 44.2 | 37.6 | 33.2 | 17.22 | 0.0776 | 0.23 | 12.95 | 1
February | 2 | 5PM to 6PM | 49.6 | 43.8 | 37.6 | 33.2 | 17.05 | 0.0777 | 0.23 | 12.94 | 1
February | 2 | 6PM to 7PM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
February | 2 | 7PM to 8PM | 47.7 | 43 | 37.9 | 33.7 | 16.64 | 0.078 | 0.23 | 12.89 | 1
February | 2 | 8PM to 9PM | 46.2 | 42.4 | 38.3 | 34.1 | 16.37 | 0.0782 | 0.23 | 12.85 | 1
February | 2 | 9PM to 10PM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
February | 2 | 10PM to 11PM | 45.3 | 42.1 | 38.7 | 34.6 | 16.23 | 0.0783 | 0.24 | 12.83 | 1
February | 2 | 11PM to 12AM | 45.7 | 42.3 | 38.7 | 34.6 | 16.31 | 0.0783 | 0.24 | 12.84 | 1
February | 3 | 12AM to 1AM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
February | 3 | 1AM to 2AM | 45.3 | 41.9 | 38.1 | 33.9 | 16.11 | 0.0783 | 0.23 | 12.83 | 1
February | 3 | 2AM to 3AM | 44.8 | 41.5 | 37.8 | 33.4 | 15.91 | 0.0784 | 0.23 | 12.81 | 1
February | 3 | 3AM to 4AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
February | 3 | 4AM to 5AM | 44.1 | 41.1 | 37.8 | 33.4 | 15.73 | 0.0785 | 0.23 | 12.79 | 1
February | 3 | 5AM to 6AM | 44.1 | 41.3 | 38.1 | 33.9 | 15.81 | 0.0785 | 0.23 | 12.8 | 1
February | 3 | 6AM to 7AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
February | 3 | 7AM to 8AM | 44.4 | 41.5 | 38.3 | 34.1 | 15.93 | 0.0785 | 0.23 | 12.81 | 1
February | 3 | 8AM to 9AM | 44.6 | 41.6 | 38.3 | 34.1 | 15.98 | 0.0784 | 0.23 | 12.81 | 1
February | 3 | 9AM to 10AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
February | 3 | 10AM to 11AM | 47.3 | 42.9 | 38.1 | 33.9 | 16.59 | 0.078 | 0.23 | 12.88 | 1
February | 3 | 11AM to 12PM | 49.6 | 44.1 | 38.1 | 33.9 | 17.16 | 0.0777 | 0.23 | 12.94 | 1
February | 3 | 12PM to 1PM | 52 | 45.6 | 39 | 35.1 | 17.92 | 0.0773 | 0.24 | 13 | 0
February | 3 | 1PM to 2PM | 53.2 | 46.1 | 38.8 | 34.9 | 18.18 | 0.0771 | 0.24 | 13.03 | 0
February | 3 | 2PM to 3PM | 54.7 | 46.9 | 39.2 | 35.4 | 18.61 | 0.0769 | 0.24 | 13.07 | 0
February | 3 | 3PM to 4PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
February | 3 | 4PM to 5PM | 54.3 | 46.7 | 39.2 | 35.4 | 18.52 | 0.077 | 0.24 | 13.06 | 0
February | 3 | 5PM to 6PM | 52.7 | 45.8 | 38.8 | 34.9 | 18.05 | 0.0772 | 0.24 | 13.02 | 0
February | 3 | 6PM to 7PM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
February | 3 | 7PM to 8PM | 50.4 | 44.8 | 39 | 35.1 | 17.52 | 0.0776 | 0.24 | 12.96 | 1
February | 3 | 8PM to 9PM | 49.6 | 44.6 | 39.4 | 35.6 | 17.43 | 0.0777 | 0.24 | 12.94 | 1
February | 3 | 9PM to 10PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
February | 3 | 10PM to 11PM | 48 | 43.6 | 38.8 | 34.9 | 16.92 | 0.0779 | 0.24 | 12.9 | 1
February | 3 | 11PM to 12AM | 46.9 | 42.8 | 38.3 | 34.1 | 16.54 | 0.0781 | 0.23 | 12.87 | 1
February | 4 | 12AM to 1AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
February | 4 | 1AM to 2AM | 45.7 | 41.9 | 37.8 | 33.4 | 16.13 | 0.0783 | 0.23 | 12.84 | 1
February | 4 | 2AM to 3AM | 45.3 | 41.9 | 38.1 | 33.9 | 16.11 | 0.0783 | 0.23 | 12.83 | 1
February | 4 | 3AM to 4AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
February | 4 | 4AM to 5AM | 44.1 | 41.1 | 37.8 | 33.4 | 15.73 | 0.0785 | 0.23 | 12.79 | 1
February | 4 | 5AM to 6AM | 43 | 40.2 | 37 | 32.5 | 15.33 | 0.0787 | 0.22 | 12.76 | 1
February | 4 | 6AM to 7AM | 42.1 | 39.8 | 37 | 32.5 | 15.11 | 0.0788 | 0.22 | 12.74 | 1
February | 4 | 7AM to 8AM | 44.1 | 41.3 | 38.1 | 33.9 | 15.81 | 0.0785 | 0.23 | 12.8 | 1
February | 4 | 8AM to 9AM | 46 | 43 | 39.7 | 36.1 | 16.63 | 0.0782 | 0.25 | 12.85 | 1
February | 4 | 9AM to 10AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
February | 4 | 10AM to 11AM | 50.7 | 46 | 41.4 | 38.5 | 18.13 | 0.0775 | 0.26 | 12.98 | 1
February | 4 | 11AM to 12PM | 53.2 | 47.3 | 41.7 | 39.1 | 18.83 | 0.0771 | 0.26 | 13.04 | 0
February | 4 | 12PM to 1PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
February | 4 | 1PM to 2PM | 57.4 | 49.2 | 41.7 | 39.1 | 19.83 | 0.0765 | 0.26 | 13.15 | 0
February | 4 | 2PM to 3PM | 58.6 | 49.5 | 41.2 | 38.2 | 20.01 | 0.0763 | 0.26 | 13.18 | 0
February | 4 | 3PM to 4PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
February | 4 | 4PM to 5PM | 58.1 | 48.9 | 40.3 | 36.9 | 19.68 | 0.0764 | 0.25 | 13.16 | 0
February | 4 | 5PM to 6PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
February | 4 | 6PM to 7PM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
February | 4 | 7PM to 8PM | 53.6 | 46.3 | 39 | 35.1 | 18.31 | 0.0771 | 0.24 | 13.04 | 0
February | 4 | 8PM to 9PM | 53.4 | 46 | 38.3 | 34.1 | 18.11 | 0.0771 | 0.23 | 13.03 | 0
February | 4 | 9PM to 10PM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
February | 4 | 10PM to 11PM | 50.7 | 44.4 | 37.6 | 33.2 | 17.31 | 0.0775 | 0.23 | 12.96 | 1
February | 4 | 11PM to 12AM | 48.4 | 43.2 | 37.6 | 33.2 | 16.74 | 0.0779 | 0.23 | 12.9 | 1
February | 5 | 12AM to 1AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
February | 5 | 1AM to 2AM | 45.7 | 41.8 | 37.4 | 33 | 16.05 | 0.0783 | 0.22 | 12.83 | 1
February | 5 | 2AM to 3AM | 45.3 | 41.6 | 37.4 | 33 | 15.97 | 0.0783 | 0.22 | 12.83 | 1
February | 5 | 3AM to 4AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
February | 5 | 4AM to 5AM | 44.6 | 41.1 | 37 | 32.5 | 15.72 | 0.0785 | 0.22 | 12.81 | 1
February | 5 | 5AM to 6AM | 44.4 | 40.8 | 36.7 | 32 | 15.6 | 0.0785 | 0.22 | 12.8 | 1
February | 5 | 6AM to 7AM | 44.1 | 40.8 | 37 | 32.5 | 15.59 | 0.0785 | 0.22 | 12.79 | 1
February | 5 | 7AM to 8AM | 46.4 | 42.8 | 39 | 35.1 | 16.56 | 0.0782 | 0.24 | 12.86 | 1
February | 5 | 8AM to 9AM | 48.7 | 45.2 | 41.7 | 39.1 | 17.74 | 0.0778 | 0.26 | 12.93 | 1
February | 5 | 9AM to 10AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
February | 5 | 10AM to 11AM | 52.3 | 48 | 44.1 | 42.8 | 19.19 | 0.0772 | 0.29 | 13.03 | 0
February | 5 | 11AM to 12PM | 53.8 | 48.6 | 44.1 | 42.8 | 19.53 | 0.077 | 0.29 | 13.07 | 0
February | 5 | 12PM to 1PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
February | 5 | 1PM to 2PM | 55.4 | 50.1 | 45.5 | 45.2 | 20.31 | 0.0767 | 0.31 | 13.12 | 0
February | 5 | 2PM to 3PM | 55.6 | 50.7 | 46.6 | 47.1 | 20.65 | 0.0767 | 0.32 | 13.13 | 0
February | 5 | 3PM to 4PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
February | 5 | 4PM to 5PM | 55 | 50.4 | 46.6 | 47.1 | 20.51 | 0.0768 | 0.32 | 13.11 | 0
February | 5 | 5PM to 6PM | 54 | 49.4 | 45.5 | 45.2 | 19.96 | 0.0769 | 0.31 | 13.08 | 0
February | 5 | 6PM to 7PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
February | 5 | 7PM to 8PM | 52.7 | 49.1 | 46 | 46.1 | 19.8 | 0.0771 | 0.31 | 13.05 | 0
February | 5 | 8PM to 9PM | 52.3 | 49.6 | 47.3 | 48.4 | 20.06 | 0.0772 | 0.33 | 13.05 | 0
February | 5 | 9PM to 10PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
February | 5 | 10PM to 11PM | 52.3 | 50.4 | 48.9 | 51.5 | 20.54 | 0.0771 | 0.35 | 13.06 | 0
February | 5 | 11PM to 12AM | 52.7 | 50.8 | 49.3 | 52.2 | 20.73 | 0.0771 | 0.35 | 13.07 | 0
February | 6 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
February | 6 | 1AM to 2AM | 52 | 50.4 | 49.1 | 51.8 | 20.5 | 0.0772 | 0.35 | 13.05 | 0
February | 6 | 2AM to 3AM | 51.1 | 49.8 | 48.7 | 51.1 | 20.18 | 0.0773 | 0.35 | 13.03 | 1
February | 6 | 3AM to 4AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
February | 6 | 4AM to 5AM | 50.4 | 49.3 | 48.4 | 50.4 | 19.89 | 0.0774 | 0.34 | 13 | 1
February | 6 | 5AM to 6AM | 50.7 | 49.4 | 48.4 | 50.4 | 19.98 | 0.0774 | 0.34 | 13.01 | 1
February | 6 | 6AM to 7AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
February | 6 | 7AM to 8AM | 51.1 | 49.6 | 48.4 | 50.4 | 20.07 | 0.0773 | 0.34 | 13.02 | 1
February | 6 | 8AM to 9AM | 51.1 | 49.6 | 48.4 | 50.4 | 20.07 | 0.0773 | 0.34 | 13.02 | 1
February | 6 | 9AM to 10AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
February | 6 | 10AM to 11AM | 53.1 | 49.6 | 46.8 | 47.4 | 20.08 | 0.0771 | 0.32 | 13.06 | 0
February | 6 | 11AM to 12PM | 55 | 49.9 | 45.5 | 45.2 | 20.22 | 0.0768 | 0.31 | 13.11 | 0
February | 6 | 12PM to 1PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
February | 6 | 1PM to 2PM | 58.1 | 51.5 | 46 | 46.1 | 21.11 | 0.0763 | 0.31 | 13.19 | 0
February | 6 | 2PM to 3PM | 59 | 52.7 | 47.8 | 49.4 | 21.84 | 0.0762 | 0.33 | 13.22 | 0
February | 6 | 3PM to 4PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
February | 6 | 4PM to 5PM | 57.7 | 52.8 | 48.9 | 51.5 | 21.85 | 0.0763 | 0.35 | 13.2 | 0
February | 6 | 5PM to 6PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0767 | 0.34 | 13.13 | 0
February | 6 | 6PM to 7PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
February | 6 | 7PM to 8PM | 52.3 | 49.1 | 46.4 | 46.8 | 19.81 | 0.0772 | 0.32 | 13.04 | 0
February | 6 | 8PM to 9PM | 51.8 | 48.3 | 45.1 | 44.6 | 19.34 | 0.0773 | 0.3 | 13.02 | 1
February | 6 | 9PM to 10PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
February | 6 | 10PM to 11PM | 50.7 | 47.2 | 44.1 | 42.8 | 18.79 | 0.0774 | 0.29 | 12.99 | 1
February | 6 | 11PM to 12AM | 50.4 | 47.2 | 44.2 | 43.1 | 18.75 | 0.0775 | 0.29 | 12.98 | 1
February | 7 | 12AM to 1AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
February | 7 | 1AM to 2AM | 48.4 | 45.4 | 42.6 | 40.4 | 17.87 | 0.0778 | 0.27 | 12.92 | 1
February | 7 | 2AM to 3AM | 46.6 | 43.9 | 41.2 | 38.2 | 17.09 | 0.0781 | 0.26 | 12.87 | 1
February | 7 | 3AM to 4AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 7 | 4AM to 5AM | 45.7 | 43.4 | 41 | 38 | 16.83 | 0.0782 | 0.26 | 12.85 | 1
February | 7 | 5AM to 6AM | 46.2 | 44.4 | 42.6 | 40.4 | 17.34 | 0.0781 | 0.27 | 12.87 | 1
February | 7 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 7 | 7AM to 8AM | 47.3 | 46.1 | 45 | 44.3 | 18.2 | 0.078 | 0.3 | 12.91 | 1
February | 7 | 8AM to 9AM | 47.7 | 46.6 | 45.7 | 45.5 | 18.47 | 0.0779 | 0.31 | 12.92 | 1
February | 7 | 9AM to 10AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
February | 7 | 10AM to 11AM | 51.3 | 49 | 47.1 | 48.1 | 19.75 | 0.0773 | 0.33 | 13.02 | 1
February | 7 | 11AM to 12PM | 54.7 | 51.1 | 48.2 | 50.1 | 20.89 | 0.0768 | 0.34 | 13.11 | 0
February | 7 | 12PM to 1PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
February | 7 | 1PM to 2PM | 58.3 | 53.1 | 49.1 | 51.8 | 22.04 | 0.0763 | 0.35 | 13.21 | 0
February | 7 | 2PM to 3PM | 58.6 | 53 | 48.7 | 51.1 | 22.02 | 0.0762 | 0.35 | 13.22 | 0
February | 7 | 3PM to 4PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
February | 7 | 4PM to 5PM | 57.4 | 52 | 47.7 | 49.1 | 21.39 | 0.0764 | 0.33 | 13.18 | 0
February | 7 | 5PM to 6PM | 55.6 | 50.7 | 46.6 | 47.1 | 20.65 | 0.0767 | 0.32 | 13.13 | 0
February | 7 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
February | 7 | 7PM to 8PM | 54.3 | 49.1 | 44.4 | 43.4 | 19.76 | 0.0769 | 0.29 | 13.08 | 0
February | 7 | 8PM to 9PM | 54.7 | 48.6 | 43.2 | 41.3 | 19.53 | 0.0769 | 0.28 | 13.09 | 0
February | 7 | 9PM to 10PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
February | 7 | 10PM to 11PM | 54.3 | 48.9 | 44.1 | 42.8 | 19.67 | 0.0769 | 0.29 | 13.08 | 0
February | 7 | 11PM to 12AM | 53.8 | 49.7 | 46.2 | 46.5 | 20.11 | 0.077 | 0.31 | 13.08 | 0
February | 8 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 8 | 1AM to 2AM | 53.1 | 50.5 | 48.4 | 50.4 | 20.55 | 0.077 | 0.34 | 13.07 | 0
February | 8 | 2AM to 3AM | 53.1 | 50.5 | 48.4 | 50.4 | 20.55 | 0.077 | 0.34 | 13.07 | 0
February | 8 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 8 | 4AM to 5AM | 52 | 49.3 | 47.1 | 48.1 | 19.92 | 0.0772 | 0.33 | 13.04 | 0
February | 8 | 5AM to 6AM | 51.1 | 48.2 | 45.7 | 45.5 | 19.31 | 0.0774 | 0.31 | 13.01 | 1
February | 8 | 6AM to 7AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
February | 8 | 7AM to 8AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
February | 8 | 8AM to 9AM | 54 | 50.5 | 47.7 | 49.1 | 20.56 | 0.0769 | 0.33 | 13.09 | 0
February | 8 | 9AM to 10AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
February | 8 | 10AM to 11AM | 56.3 | 52.2 | 49.1 | 51.8 | 21.56 | 0.0765 | 0.35 | 13.16 | 0
February | 8 | 11AM to 12PM | 56.7 | 52.4 | 49.1 | 51.8 | 21.64 | 0.0765 | 0.35 | 13.17 | 0
February | 8 | 12PM to 1PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
February | 8 | 1PM to 2PM | 55.9 | 52.3 | 49.5 | 52.6 | 21.58 | 0.0766 | 0.36 | 13.15 | 0
February | 8 | 2PM to 3PM | 55 | 51.9 | 49.5 | 52.6 | 21.36 | 0.0767 | 0.36 | 13.13 | 0
February | 8 | 3PM to 4PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
February | 8 | 4PM to 5PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
February | 8 | 5PM to 6PM | 54 | 50.8 | 48.2 | 50.1 | 20.72 | 0.0769 | 0.34 | 13.1 | 0
February | 8 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
February | 8 | 7PM to 8PM | 53.2 | 50 | 47.3 | 48.4 | 20.28 | 0.077 | 0.33 | 13.07 | 0
February | 8 | 8PM to 9PM | 52.7 | 49.6 | 46.9 | 47.8 | 20.05 | 0.0771 | 0.32 | 13.06 | 0
February | 8 | 9PM to 10PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
February | 8 | 10PM to 11PM | 51.3 | 48.6 | 46.2 | 46.5 | 19.5 | 0.0773 | 0.31 | 13.02 | 1
February | 8 | 11PM to 12AM | 50.7 | 48.2 | 46 | 46.1 | 19.32 | 0.0774 | 0.31 | 13 | 1
February | 9 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
February | 9 | 1AM to 2AM | 48.9 | 46.8 | 44.8 | 44 | 18.54 | 0.0777 | 0.3 | 12.95 | 1
February | 9 | 2AM to 3AM | 48 | 46.1 | 44.2 | 43.1 | 18.18 | 0.0779 | 0.29 | 12.92 | 1
February | 9 | 3AM to 4AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
February | 9 | 4AM to 5AM | 46.2 | 44.5 | 42.8 | 40.7 | 17.39 | 0.0781 | 0.28 | 12.87 | 1
February | 9 | 5AM to 6AM | 45.7 | 43.9 | 42.1 | 39.6 | 17.08 | 0.0782 | 0.27 | 12.85 | 1
February | 9 | 6AM to 7AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
February | 9 | 7AM to 8AM | 48 | 45.8 | 43.7 | 42.2 | 18.05 | 0.0779 | 0.29 | 12.92 | 1
February | 9 | 8AM to 9AM | 50.9 | 48.3 | 46 | 46.1 | 19.36 | 0.0774 | 0.31 | 13.01 | 1
February | 9 | 9AM to 10AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
February | 9 | 10AM to 11AM | 54.3 | 50.6 | 47.5 | 48.8 | 20.59 | 0.0769 | 0.33 | 13.1 | 0
February | 9 | 11AM to 12PM | 54.7 | 50.4 | 46.8 | 47.4 | 20.48 | 0.0768 | 0.32 | 13.11 | 0
February | 9 | 12PM to 1PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
February | 9 | 1PM to 2PM | 55.9 | 51.1 | 47.1 | 48.1 | 20.89 | 0.0766 | 0.33 | 13.14 | 0
February | 9 | 2PM to 3PM | 57 | 51.9 | 47.8 | 49.4 | 21.35 | 0.0765 | 0.33 | 13.17 | 0
February | 9 | 3PM to 4PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
February | 9 | 4PM to 5PM | 56.7 | 51.7 | 47.8 | 49.4 | 21.27 | 0.0765 | 0.33 | 13.16 | 0
February | 9 | 5PM to 6PM | 55.2 | 50.8 | 47.1 | 48.1 | 20.71 | 0.0767 | 0.33 | 13.12 | 0
February | 9 | 6PM to 7PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
February | 9 | 7PM to 8PM | 53.2 | 49.8 | 46.9 | 47.8 | 20.18 | 0.077 | 0.32 | 13.07 | 0
February | 9 | 8PM to 9PM | 52.7 | 49.7 | 47.3 | 48.4 | 20.15 | 0.0771 | 0.33 | 13.06 | 0
February | 9 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
February | 9 | 10PM to 11PM | 52 | 49.6 | 47.7 | 49.1 | 20.08 | 0.0772 | 0.33 | 13.04 | 0
February | 9 | 11PM to 12AM | 52 | 49.6 | 47.7 | 49.1 | 20.08 | 0.0772 | 0.33 | 13.04 | 0
February | 10 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
February | 10 | 1AM to 2AM | 50.4 | 48.2 | 46.4 | 46.8 | 19.33 | 0.0775 | 0.32 | 12.99 | 1
February | 10 | 2AM to 3AM | 48.6 | 46.9 | 45.5 | 45.2 | 18.64 | 0.0778 | 0.31 | 12.94 | 1
February | 10 | 3AM to 4AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 10 | 4AM to 5AM | 46.6 | 45.1 | 43.7 | 42.2 | 17.7 | 0.0781 | 0.29 | 12.88 | 1
February | 10 | 5AM to 6AM | 46.4 | 44.7 | 43 | 41 | 17.47 | 0.0781 | 0.28 | 12.88 | 1
February | 10 | 6AM to 7AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
February | 10 | 7AM to 8AM | 46.8 | 45.2 | 43.7 | 42.2 | 17.74 | 0.0781 | 0.29 | 12.89 | 1
February | 10 | 8AM to 9AM | 47.3 | 46.1 | 45 | 44.3 | 18.2 | 0.078 | 0.3 | 12.91 | 1
February | 10 | 9AM to 10AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
February | 10 | 10AM to 11AM | 49.3 | 47.9 | 46.8 | 47.4 | 19.16 | 0.0776 | 0.32 | 12.97 | 1
February | 10 | 11AM to 12PM | 50.7 | 49 | 47.5 | 48.8 | 19.72 | 0.0774 | 0.33 | 13.01 | 1
February | 10 | 12PM to 1PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
February | 10 | 1PM to 2PM | 55.4 | 51.7 | 48.7 | 51.1 | 21.23 | 0.0767 | 0.35 | 13.14 | 0
February | 10 | 2PM to 3PM | 58.6 | 53.2 | 49.1 | 51.8 | 22.12 | 0.0762 | 0.35 | 13.22 | 0
February | 10 | 3PM to 4PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
February | 10 | 4PM to 5PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
February | 10 | 5PM to 6PM | 56.1 | 51.7 | 48.2 | 50.1 | 21.24 | 0.0766 | 0.34 | 13.15 | 0
February | 10 | 6PM to 7PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
February | 10 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
February | 10 | 8PM to 9PM | 53.1 | 50.5 | 48.4 | 50.4 | 20.55 | 0.077 | 0.34 | 13.07 | 0
February | 10 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 10 | 10PM to 11PM | 52.3 | 50.1 | 48.2 | 50.1 | 20.32 | 0.0772 | 0.34 | 13.05 | 0
February | 10 | 11PM to 12AM | 51.8 | 49.7 | 48 | 49.8 | 20.14 | 0.0772 | 0.34 | 13.04 | 1
February | 11 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
February | 11 | 1AM to 2AM | 49.6 | 47.5 | 45.7 | 45.5 | 18.96 | 0.0776 | 0.31 | 12.97 | 1
February | 11 | 2AM to 3AM | 48.4 | 46.2 | 44.2 | 43.1 | 18.27 | 0.0778 | 0.29 | 12.93 | 1
February | 11 | 3AM to 4AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
February | 11 | 4AM to 5AM | 46.9 | 45 | 43.2 | 41.3 | 17.65 | 0.078 | 0.28 | 12.89 | 1
February | 11 | 5AM to 6AM | 46.9 | 45.3 | 43.7 | 42.2 | 17.78 | 0.078 | 0.29 | 12.89 | 1
February | 11 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 11 | 7AM to 8AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 11 | 8AM to 9AM | 46.9 | 46.3 | 45.7 | 45.5 | 18.3 | 0.078 | 0.31 | 12.9 | 1
February | 11 | 9AM to 10AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
February | 11 | 10AM to 11AM | 50.4 | 48.6 | 47.1 | 48.1 | 19.53 | 0.0775 | 0.33 | 13 | 1
February | 11 | 11AM to 12PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
February | 11 | 12PM to 1PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
February | 11 | 1PM to 2PM | 58.6 | 53.6 | 49.8 | 53.3 | 22.35 | 0.0762 | 0.36 | 13.22 | 0
February | 11 | 2PM to 3PM | 60.4 | 54.5 | 50.2 | 54 | 22.9 | 0.0759 | 0.37 | 13.27 | 0
February | 11 | 3PM to 4PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
February | 11 | 4PM to 5PM | 59.4 | 54.2 | 50.4 | 54.4 | 22.69 | 0.0761 | 0.37 | 13.25 | 0
February | 11 | 5PM to 6PM | 56.7 | 52.9 | 50 | 53.6 | 21.92 | 0.0765 | 0.36 | 13.17 | 0
February | 11 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
February | 11 | 7PM to 8PM | 53.2 | 51 | 49.3 | 52.2 | 20.87 | 0.077 | 0.35 | 13.08 | 0
February | 11 | 8PM to 9PM | 52.7 | 50.6 | 48.9 | 51.5 | 20.62 | 0.0771 | 0.35 | 13.07 | 0
February | 11 | 9PM to 10PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
February | 11 | 10PM to 11PM | 51.6 | 49.9 | 48.6 | 50.8 | 20.25 | 0.0773 | 0.34 | 13.04 | 1
February | 11 | 11PM to 12AM | 51.4 | 49.9 | 48.6 | 50.8 | 20.21 | 0.0773 | 0.34 | 13.03 | 1
February | 12 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
February | 12 | 1AM to 2AM | 51.1 | 49.8 | 48.7 | 51.1 | 20.18 | 0.0773 | 0.35 | 13.03 | 1
February | 12 | 2AM to 3AM | 51.1 | 50 | 49.1 | 51.8 | 20.29 | 0.0773 | 0.35 | 13.03 | 1
February | 12 | 3AM to 4AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
February | 12 | 4AM to 5AM | 50.4 | 49.3 | 48.4 | 50.4 | 19.89 | 0.0774 | 0.34 | 13 | 1
February | 12 | 5AM to 6AM | 49.6 | 48.4 | 47.3 | 48.4 | 19.41 | 0.0776 | 0.33 | 12.98 | 1
February | 12 | 6AM to 7AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
February | 12 | 7AM to 8AM | 49.3 | 48 | 46.9 | 47.8 | 19.22 | 0.0776 | 0.32 | 12.97 | 1
February | 12 | 8AM to 9AM | 49.6 | 48.6 | 47.7 | 49.1 | 19.51 | 0.0776 | 0.33 | 12.98 | 1
February | 12 | 9AM to 10AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
February | 12 | 10AM to 11AM | 51.3 | 49.7 | 48.4 | 50.4 | 20.11 | 0.0773 | 0.34 | 13.03 | 1
February | 12 | 11AM to 12PM | 52.7 | 50.5 | 48.7 | 51.1 | 20.57 | 0.0771 | 0.35 | 13.07 | 0
February | 12 | 12PM to 1PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
February | 12 | 1PM to 2PM | 55.9 | 52.7 | 50.2 | 54 | 21.8 | 0.0766 | 0.37 | 13.16 | 0
February | 12 | 2PM to 3PM | 58.1 | 53.9 | 50.9 | 55.5 | 22.56 | 0.0763 | 0.37 | 13.22 | 0
February | 12 | 3PM to 4PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
February | 12 | 4PM to 5PM | 57.7 | 53.8 | 50.9 | 55.5 | 22.47 | 0.0763 | 0.37 | 13.21 | 0
February | 12 | 5PM to 6PM | 55.4 | 52.4 | 50.2 | 54 | 21.67 | 0.0767 | 0.37 | 13.14 | 0
February | 12 | 6PM to 7PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
February | 12 | 7PM to 8PM | 52.3 | 50.5 | 49.1 | 51.8 | 20.59 | 0.0771 | 0.35 | 13.06 | 0
February | 12 | 8PM to 9PM | 51.8 | 49.9 | 48.4 | 50.4 | 20.24 | 0.0772 | 0.34 | 13.04 | 1
February | 12 | 9PM to 10PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
February | 12 | 10PM to 11PM | 50.7 | 48.9 | 47.3 | 48.4 | 19.67 | 0.0774 | 0.33 | 13.01 | 1
February | 12 | 11PM to 12AM | 50.4 | 48.5 | 46.9 | 47.8 | 19.48 | 0.0775 | 0.32 | 13 | 1
February | 13 | 12AM to 1AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
February | 13 | 1AM to 2AM | 49.3 | 47.2 | 45.3 | 44.9 | 18.77 | 0.0777 | 0.3 | 12.96 | 1
February | 13 | 2AM to 3AM | 48.7 | 46.6 | 44.6 | 43.7 | 18.45 | 0.0777 | 0.3 | 12.94 | 1
February | 13 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
February | 13 | 4AM to 5AM | 47.7 | 45.7 | 43.9 | 42.5 | 18 | 0.0779 | 0.29 | 12.91 | 1
February | 13 | 5AM to 6AM | 47.3 | 45.6 | 44.1 | 42.8 | 17.96 | 0.078 | 0.29 | 12.9 | 1
February | 13 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
February | 13 | 7AM to 8AM | 48 | 46.8 | 45.7 | 45.5 | 18.56 | 0.0778 | 0.31 | 12.93 | 1
February | 13 | 8AM to 9AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
February | 13 | 9AM to 10AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
February | 13 | 10AM to 11AM | 53.4 | 50.8 | 48.7 | 51.1 | 20.75 | 0.077 | 0.35 | 13.08 | 0
February | 13 | 11AM to 12PM | 56.7 | 52.6 | 49.5 | 52.6 | 21.75 | 0.0765 | 0.36 | 13.17 | 0
February | 13 | 12PM to 1PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
February | 13 | 1PM to 2PM | 62.1 | 55.4 | 50.5 | 54.7 | 23.41 | 0.0757 | 0.37 | 13.32 | 0
February | 13 | 2PM to 3PM | 64 | 56.1 | 50.5 | 54.7 | 23.89 | 0.0754 | 0.37 | 13.37 | 0
February | 13 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
February | 13 | 4PM to 5PM | 64 | 55.7 | 49.6 | 52.9 | 23.6 | 0.0754 | 0.36 | 13.36 | 0
February | 13 | 5PM to 6PM | 62.1 | 54.4 | 48.6 | 50.8 | 22.79 | 0.0757 | 0.34 | 13.3 | 0
February | 13 | 6PM to 7PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
February | 13 | 7PM to 8PM | 57.7 | 52.3 | 48 | 49.8 | 21.58 | 0.0763 | 0.34 | 13.19 | 0
February | 13 | 8PM to 9PM | 55.4 | 51.5 | 48.4 | 50.4 | 21.12 | 0.0767 | 0.34 | 13.13 | 0
February | 13 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 13 | 10PM to 11PM | 52 | 49.9 | 48.2 | 50.1 | 20.23 | 0.0772 | 0.34 | 13.05 | 0
February | 13 | 11PM to 12AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
February | 14 | 12AM to 1AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
February | 14 | 1AM to 2AM | 49.3 | 47.4 | 45.7 | 45.5 | 18.87 | 0.0776 | 0.31 | 12.96 | 1
February | 14 | 2AM to 3AM | 48.7 | 46.4 | 44.2 | 43.1 | 18.36 | 0.0777 | 0.29 | 12.94 | 1
February | 14 | 3AM to 4AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
February | 14 | 4AM to 5AM | 47.7 | 45.2 | 42.8 | 40.7 | 17.73 | 0.0779 | 0.28 | 12.91 | 1
February | 14 | 5AM to 6AM | 47.3 | 45.2 | 43.2 | 41.3 | 17.74 | 0.078 | 0.28 | 12.9 | 1
February | 14 | 6AM to 7AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
February | 14 | 7AM to 8AM | 50.9 | 48.1 | 45.7 | 45.5 | 19.26 | 0.0774 | 0.31 | 13 | 1
February | 14 | 8AM to 9AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
February | 14 | 9AM to 10AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
February | 14 | 10AM to 11AM | 63.3 | 53.7 | 46 | 46.1 | 22.38 | 0.0756 | 0.31 | 13.32 | 0
February | 14 | 11AM to 12PM | 67.6 | 53.8 | 42.1 | 39.6 | 22.41 | 0.075 | 0.27 | 13.41 | 0
February | 14 | 12PM to 1PM | 72 | 54.4 | 39 | 35.1 | 22.76 | 0.0744 | 0.24 | 13.51 | 0
February | 14 | 1PM to 2PM | 69.6 | 54.6 | 42.1 | 39.6 | 22.89 | 0.0747 | 0.27 | 13.46 | 0
February | 14 | 2PM to 3PM | 67.3 | 55.2 | 45.9 | 45.8 | 23.29 | 0.075 | 0.31 | 13.42 | 0
February | 14 | 3PM to 4PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
February | 14 | 4PM to 5PM | 63.7 | 54.2 | 46.9 | 47.8 | 22.72 | 0.0755 | 0.32 | 13.34 | 0
February | 14 | 5PM to 6PM | 62.2 | 52.4 | 44.2 | 43.1 | 21.63 | 0.0757 | 0.29 | 13.29 | 0
February | 14 | 6PM to 7PM | 61 | 51 | 42.1 | 39.6 | 20.79 | 0.0759 | 0.27 | 13.24 | 0
February | 14 | 7PM to 8PM | 57.7 | 50 | 43.2 | 41.3 | 20.27 | 0.0764 | 0.28 | 13.17 | 0
February | 14 | 8PM to 9PM | 54.3 | 49.1 | 44.4 | 43.4 | 19.76 | 0.0769 | 0.29 | 13.08 | 0
February | 14 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
February | 14 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
February | 14 | 11PM to 12AM | 49.1 | 46.7 | 44.4 | 43.4 | 18.49 | 0.0777 | 0.29 | 12.95 | 1
February | 15 | 12AM to 1AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
February | 15 | 1AM to 2AM | 47.7 | 45.2 | 42.8 | 40.7 | 17.73 | 0.0779 | 0.28 | 12.91 | 1
February | 15 | 2AM to 3AM | 47.3 | 44.8 | 42.3 | 39.9 | 17.52 | 0.078 | 0.27 | 12.9 | 1
February | 15 | 3AM to 4AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
February | 15 | 4AM to 5AM | 47.7 | 44.9 | 42.3 | 39.9 | 17.6 | 0.0779 | 0.27 | 12.9 | 1
February | 15 | 5AM to 6AM | 48.2 | 45.4 | 42.8 | 40.7 | 17.87 | 0.0778 | 0.28 | 12.92 | 1
February | 15 | 6AM to 7AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
February | 15 | 7AM to 8AM | 52 | 48.6 | 45.7 | 45.5 | 19.52 | 0.0772 | 0.31 | 13.03 | 0
February | 15 | 8AM to 9AM | 54.9 | 51.1 | 48 | 49.8 | 20.88 | 0.0768 | 0.34 | 13.12 | 0
February | 15 | 9AM to 10AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
February | 15 | 10AM to 11AM | 61 | 54.6 | 49.8 | 53.3 | 22.92 | 0.0759 | 0.36 | 13.28 | 0
February | 15 | 11AM to 12PM | 63.9 | 55.5 | 49.5 | 52.6 | 23.5 | 0.0754 | 0.36 | 13.36 | 0
February | 15 | 12PM to 1PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
February | 15 | 1PM to 2PM | 68.5 | 57.7 | 50.2 | 54 | 24.87 | 0.0748 | 0.37 | 13.48 | 0
February | 15 | 2PM to 3PM | 70.3 | 58.7 | 50.9 | 55.5 | 25.54 | 0.0745 | 0.37 | 13.53 | 0
February | 15 | 3PM to 4PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
February | 15 | 4PM to 5PM | 69.3 | 58.3 | 50.9 | 55.5 | 25.28 | 0.0746 | 0.37 | 13.5 | 0
February | 15 | 5PM to 6PM | 66.7 | 57 | 50.2 | 54 | 24.43 | 0.075 | 0.37 | 13.43 | 0
February | 15 | 6PM to 7PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
February | 15 | 7PM to 8PM | 62.4 | 54.8 | 49.1 | 51.8 | 23.04 | 0.0757 | 0.35 | 13.32 | 0
February | 15 | 8PM to 9PM | 60.6 | 53.7 | 48.4 | 50.4 | 22.39 | 0.0759 | 0.34 | 13.27 | 0
February | 15 | 9PM to 10PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
February | 15 | 10PM to 11PM | 57.7 | 51.8 | 46.9 | 47.8 | 21.27 | 0.0764 | 0.32 | 13.18 | 0
February | 15 | 11PM to 12AM | 56.3 | 50.9 | 46.4 | 46.8 | 20.77 | 0.0766 | 0.32 | 13.15 | 0
February | 16 | 12AM to 1AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
February | 16 | 1AM to 2AM | 53.8 | 49 | 44.8 | 44 | 19.72 | 0.077 | 0.3 | 13.07 | 0
February | 16 | 2AM to 3AM | 52.3 | 48.1 | 44.2 | 43.1 | 19.23 | 0.0772 | 0.29 | 13.03 | 0
February | 16 | 3AM to 4AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
February | 16 | 4AM to 5AM | 50.7 | 47.4 | 44.4 | 43.4 | 18.88 | 0.0774 | 0.29 | 12.99 | 1
February | 16 | 5AM to 6AM | 50.4 | 47.7 | 45.3 | 44.9 | 19.03 | 0.0775 | 0.3 | 12.99 | 1
February | 16 | 6AM to 7AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
February | 16 | 7AM to 8AM | 52.3 | 49.8 | 47.7 | 49.1 | 20.16 | 0.0772 | 0.33 | 13.05 | 0
February | 16 | 8AM to 9AM | 54.7 | 51.5 | 48.9 | 51.5 | 21.11 | 0.0768 | 0.35 | 13.12 | 0
February | 16 | 9AM to 10AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
February | 16 | 10AM to 11AM | 59.7 | 54.2 | 50.2 | 54 | 22.72 | 0.076 | 0.37 | 13.25 | 0
February | 16 | 11AM to 12PM | 62.2 | 55.2 | 50.2 | 54 | 23.34 | 0.0757 | 0.37 | 13.32 | 0
February | 16 | 12PM to 1PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
February | 16 | 1PM to 2PM | 64.6 | 56.4 | 50.5 | 54.7 | 24.02 | 0.0753 | 0.37 | 13.38 | 0
February | 16 | 2PM to 3PM | 64.4 | 56.3 | 50.5 | 54.7 | 23.98 | 0.0753 | 0.37 | 13.38 | 0
February | 16 | 3PM to 4PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
February | 16 | 4PM to 5PM | 61.3 | 54.8 | 50 | 53.6 | 23.06 | 0.0758 | 0.36 | 13.29 | 0
February | 16 | 5PM to 6PM | 58.6 | 53.3 | 49.3 | 52.2 | 22.18 | 0.0762 | 0.35 | 13.22 | 0
February | 16 | 6PM to 7PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
February | 16 | 7PM to 8PM | 55 | 51.3 | 48.4 | 50.4 | 21.03 | 0.0767 | 0.34 | 13.12 | 0
February | 16 | 8PM to 9PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
February | 16 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
February | 16 | 10PM to 11PM | 52.3 | 49.6 | 47.3 | 48.4 | 20.06 | 0.0772 | 0.33 | 13.05 | 0
February | 16 | 11PM to 12AM | 51.8 | 49.2 | 46.9 | 47.8 | 19.83 | 0.0772 | 0.32 | 13.03 | 1
February | 17 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
February | 17 | 1AM to 2AM | 50.7 | 48.4 | 46.4 | 46.8 | 19.41 | 0.0774 | 0.32 | 13 | 1
February | 17 | 2AM to 3AM | 50.4 | 48.2 | 46.4 | 46.8 | 19.33 | 0.0775 | 0.32 | 12.99 | 1
February | 17 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
February | 17 | 4AM to 5AM | 48.4 | 45.8 | 43.3 | 41.6 | 18.04 | 0.0778 | 0.28 | 12.93 | 1
February | 17 | 5AM to 6AM | 46.6 | 43.5 | 40.3 | 36.9 | 16.88 | 0.0781 | 0.25 | 12.87 | 1
February | 17 | 6AM to 7AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
February | 17 | 7AM to 8AM | 48.6 | 45.1 | 41.7 | 39.1 | 17.69 | 0.0778 | 0.26 | 12.93 | 1
February | 17 | 8AM to 9AM | 52.3 | 49 | 46 | 46.1 | 19.71 | 0.0772 | 0.31 | 13.04 | 0
February | 17 | 9AM to 10AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
February | 17 | 10AM to 11AM | 59.4 | 53.9 | 49.8 | 53.3 | 22.52 | 0.0761 | 0.36 | 13.24 | 0
February | 17 | 11AM to 12PM | 62.6 | 55 | 49.5 | 52.6 | 23.2 | 0.0756 | 0.36 | 13.32 | 0
February | 17 | 12PM to 1PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
February | 17 | 1PM to 2PM | 67.3 | 56.5 | 48.7 | 51.1 | 24.12 | 0.075 | 0.35 | 13.44 | 0
February | 17 | 2PM to 3PM | 68.7 | 56.8 | 48.2 | 50.1 | 24.31 | 0.0748 | 0.34 | 13.47 | 0
February | 17 | 3PM to 4PM | 70 | 57.2 | 48 | 49.8 | 24.56 | 0.0746 | 0.34 | 13.5 | 0
February | 17 | 4PM to 5PM | 67.6 | 55 | 45 | 44.3 | 23.13 | 0.075 | 0.3 | 13.43 | 0
February | 17 | 5PM to 6PM | 65.3 | 52.9 | 42.3 | 39.9 | 21.88 | 0.0753 | 0.27 | 13.35 | 0
February | 17 | 6PM to 7PM | 63 | 50.9 | 39.9 | 36.4 | 20.77 | 0.0757 | 0.25 | 13.28 | 0
February | 17 | 7PM to 8PM | 61 | 50.2 | 40.3 | 36.9 | 20.37 | 0.076 | 0.25 | 13.23 | 0
February | 17 | 8PM to 9PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
February | 17 | 9PM to 10PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
February | 17 | 10PM to 11PM | 55.8 | 48.9 | 42.6 | 40.4 | 19.66 | 0.0767 | 0.27 | 13.11 | 0
February | 17 | 11PM to 12AM | 54.3 | 48.7 | 43.7 | 42.2 | 19.57 | 0.0769 | 0.29 | 13.08 | 0
February | 18 | 12AM to 1AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
February | 18 | 1AM to 2AM | 51.4 | 46.9 | 42.6 | 40.4 | 18.61 | 0.0774 | 0.27 | 13 | 1
February | 18 | 2AM to 3AM | 49.6 | 45.4 | 41.2 | 38.2 | 17.83 | 0.0776 | 0.26 | 12.95 | 1
February | 18 | 3AM to 4AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
February | 18 | 4AM to 5AM | 47.3 | 43.8 | 40.1 | 36.7 | 17.02 | 0.078 | 0.25 | 12.89 | 1
February | 18 | 5AM to 6AM | 46.8 | 43.8 | 40.8 | 37.7 | 17.05 | 0.0781 | 0.26 | 12.88 | 1
February | 18 | 6AM to 7AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
February | 18 | 7AM to 8AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
February | 18 | 8AM to 9AM | 54 | 49.9 | 46.6 | 47.1 | 20.25 | 0.0769 | 0.32 | 13.09 | 0
February | 18 | 9AM to 10AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
February | 18 | 10AM to 11AM | 60.3 | 53 | 47.3 | 48.4 | 21.99 | 0.076 | 0.33 | 13.25 | 0
February | 18 | 11AM to 12PM | 62.6 | 53.2 | 45.7 | 45.5 | 22.1 | 0.0757 | 0.31 | 13.3 | 0
February | 18 | 12PM to 1PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
February | 18 | 1PM to 2PM | 64.9 | 54.7 | 46.8 | 47.4 | 22.97 | 0.0753 | 0.32 | 13.37 | 0
February | 18 | 2PM to 3PM | 64.9 | 55.8 | 49.1 | 51.8 | 23.66 | 0.0753 | 0.35 | 13.38 | 0
February | 18 | 3PM to 4PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
February | 18 | 4PM to 5PM | 60.3 | 54.4 | 50 | 53.6 | 22.8 | 0.076 | 0.36 | 13.27 | 0
February | 18 | 5PM to 6PM | 55.8 | 51.5 | 48.2 | 50.1 | 21.15 | 0.0766 | 0.34 | 13.14 | 0
February | 18 | 6PM to 7PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
February | 18 | 7PM to 8PM | 50.7 | 48.4 | 46.4 | 46.8 | 19.41 | 0.0774 | 0.32 | 13 | 1
February | 18 | 8PM to 9PM | 50.4 | 48.1 | 46 | 46.1 | 19.23 | 0.0775 | 0.31 | 12.99 | 1
February | 18 | 9PM to 10PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
February | 18 | 10PM to 11PM | 49.6 | 47.5 | 45.7 | 45.5 | 18.96 | 0.0776 | 0.31 | 12.97 | 1
February | 18 | 11PM to 12AM | 49.3 | 47.4 | 45.7 | 45.5 | 18.87 | 0.0776 | 0.31 | 12.96 | 1
February | 19 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
February | 19 | 1AM to 2AM | 48.9 | 47.1 | 45.5 | 45.2 | 18.73 | 0.0777 | 0.31 | 12.95 | 1
February | 19 | 2AM to 3AM | 48.9 | 47.1 | 45.5 | 45.2 | 18.73 | 0.0777 | 0.31 | 12.95 | 1
February | 19 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
February | 19 | 4AM to 5AM | 48.2 | 46.2 | 44.4 | 43.4 | 18.27 | 0.0778 | 0.29 | 12.93 | 1
February | 19 | 5AM to 6AM | 47.7 | 45.4 | 43.3 | 41.6 | 17.87 | 0.0779 | 0.28 | 12.91 | 1
February | 19 | 6AM to 7AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
February | 19 | 7AM to 8AM | 48.4 | 46 | 43.7 | 42.2 | 18.13 | 0.0778 | 0.29 | 12.93 | 1
February | 19 | 8AM to 9AM | 49.6 | 47.2 | 45 | 44.3 | 18.76 | 0.0776 | 0.3 | 12.97 | 1
February | 19 | 9AM to 10AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
February | 19 | 10AM to 11AM | 53.1 | 49.6 | 46.8 | 47.4 | 20.08 | 0.0771 | 0.32 | 13.06 | 0
February | 19 | 11AM to 12PM | 55 | 50.9 | 47.5 | 48.8 | 20.77 | 0.0768 | 0.33 | 13.12 | 0
February | 19 | 12PM to 1PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
February | 19 | 1PM to 2PM | 56.7 | 51.7 | 47.7 | 49.1 | 21.22 | 0.0765 | 0.33 | 13.16 | 0
February | 19 | 2PM to 3PM | 56.3 | 51.2 | 47.1 | 48.1 | 20.97 | 0.0766 | 0.33 | 13.15 | 0
February | 19 | 3PM to 4PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
February | 19 | 4PM to 5PM | 54.3 | 49.7 | 45.9 | 45.8 | 20.14 | 0.0769 | 0.31 | 13.09 | 0
February | 19 | 5PM to 6PM | 52.7 | 48.7 | 45.1 | 44.6 | 19.55 | 0.0771 | 0.3 | 13.05 | 0
February | 19 | 6PM to 7PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
February | 19 | 7PM to 8PM | 50.4 | 47.2 | 44.4 | 43.4 | 18.8 | 0.0775 | 0.29 | 12.98 | 1
February | 19 | 8PM to 9PM | 49.6 | 46.7 | 44.1 | 42.8 | 18.53 | 0.0776 | 0.29 | 12.96 | 1
February | 19 | 9PM to 10PM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
February | 19 | 10PM to 11PM | 48.6 | 45.7 | 43 | 41 | 18 | 0.0778 | 0.28 | 12.93 | 1
February | 19 | 11PM to 12AM | 48.4 | 45.4 | 42.4 | 40.2 | 17.82 | 0.0778 | 0.27 | 12.92 | 1
February | 20 | 12AM to 1AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
February | 20 | 1AM to 2AM | 47.7 | 44.4 | 41.2 | 38.2 | 17.35 | 0.0779 | 0.26 | 12.9 | 1
February | 20 | 2AM to 3AM | 47.3 | 44.1 | 40.8 | 37.7 | 17.18 | 0.078 | 0.26 | 12.89 | 1
February | 20 | 3AM to 4AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
February | 20 | 4AM to 5AM | 48 | 44.6 | 41.2 | 38.2 | 17.44 | 0.0779 | 0.26 | 12.91 | 1
February | 20 | 5AM to 6AM | 48.9 | 45.3 | 41.7 | 39.1 | 17.78 | 0.0777 | 0.26 | 12.93 | 1
February | 20 | 6AM to 7AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
February | 20 | 7AM to 8AM | 51.1 | 47.1 | 43.3 | 41.6 | 18.7 | 0.0774 | 0.28 | 13 | 1
February | 20 | 8AM to 9AM | 52 | 47.9 | 44.2 | 43.1 | 19.14 | 0.0773 | 0.29 | 13.02 | 0
February | 20 | 9AM to 10AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
February | 20 | 10AM to 11AM | 53.1 | 48.9 | 45.3 | 44.9 | 19.69 | 0.0771 | 0.3 | 13.06 | 0
February | 20 | 11AM to 12PM | 53.1 | 49.1 | 45.7 | 45.5 | 19.79 | 0.0771 | 0.31 | 13.06 | 0
February | 20 | 12PM to 1PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
February | 20 | 1PM to 2PM | 52.3 | 49.3 | 46.8 | 47.4 | 19.91 | 0.0772 | 0.32 | 13.05 | 0
February | 20 | 2PM to 3PM | 51.8 | 49.3 | 47.1 | 48.1 | 19.88 | 0.0772 | 0.33 | 13.03 | 1
February | 20 | 3PM to 4PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
February | 20 | 4PM to 5PM | 51.1 | 49.2 | 47.7 | 49.1 | 19.86 | 0.0773 | 0.33 | 13.02 | 1
February | 20 | 5PM to 6PM | 51.1 | 49.2 | 47.7 | 49.1 | 19.86 | 0.0773 | 0.33 | 13.02 | 1
February | 20 | 6PM to 7PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
February | 20 | 7PM to 8PM | 51.8 | 49.7 | 48 | 49.8 | 20.14 | 0.0772 | 0.34 | 13.04 | 1
February | 20 | 8PM to 9PM | 52.3 | 50.2 | 48.4 | 50.4 | 20.38 | 0.0771 | 0.34 | 13.06 | 0
February | 20 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
February | 20 | 10PM to 11PM | 53.8 | 51.1 | 48.9 | 51.5 | 20.89 | 0.0769 | 0.35 | 13.1 | 0
February | 20 | 11PM to 12AM | 54.3 | 51.5 | 49.3 | 52.2 | 21.13 | 0.0768 | 0.35 | 13.11 | 0
February | 21 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
February | 21 | 1AM to 2AM | 55.9 | 52.9 | 50.7 | 55.1 | 21.97 | 0.0766 | 0.37 | 13.16 | 0
February | 21 | 2AM to 3AM | 57 | 54.2 | 52.2 | 58.2 | 22.71 | 0.0764 | 0.39 | 13.2 | 0
February | 21 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
February | 21 | 4AM to 5AM | 57 | 54.2 | 52.2 | 58.2 | 22.71 | 0.0764 | 0.39 | 13.2 | 0
February | 21 | 5AM to 6AM | 55.9 | 52.9 | 50.7 | 55.1 | 21.97 | 0.0766 | 0.37 | 13.16 | 0
February | 21 | 6AM to 7AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
February | 21 | 7AM to 8AM | 54.7 | 51.4 | 48.7 | 51.1 | 21.05 | 0.0768 | 0.35 | 13.12 | 0
February | 21 | 8AM to 9AM | 54.3 | 50.8 | 48 | 49.8 | 20.75 | 0.0769 | 0.34 | 13.1 | 0
February | 21 | 9AM to 10AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
February | 21 | 10AM to 11AM | 54.3 | 49.8 | 46 | 46.1 | 20.19 | 0.0769 | 0.31 | 13.09 | 0
February | 21 | 11AM to 12PM | 54.7 | 49.6 | 45.1 | 44.6 | 20.03 | 0.0768 | 0.3 | 13.1 | 0
February | 21 | 12PM to 1PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
February | 21 | 1PM to 2PM | 55 | 49.5 | 44.8 | 44 | 20.03 | 0.0768 | 0.3 | 13.1 | 0
February | 21 | 2PM to 3PM | 55 | 49.7 | 45.1 | 44.6 | 20.12 | 0.0768 | 0.3 | 13.11 | 0
February | 21 | 3PM to 4PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
February | 21 | 4PM to 5PM | 54.7 | 49.6 | 45.3 | 44.9 | 20.08 | 0.0768 | 0.3 | 13.1 | 0
February | 21 | 5PM to 6PM | 54.3 | 49.3 | 45 | 44.3 | 19.9 | 0.0769 | 0.3 | 13.09 | 0
February | 21 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
February | 21 | 7PM to 8PM | 53.6 | 49.2 | 45.3 | 44.9 | 19.82 | 0.077 | 0.3 | 13.07 | 0
February | 21 | 8PM to 9PM | 53.4 | 49.4 | 46 | 46.1 | 19.97 | 0.077 | 0.31 | 13.07 | 0
February | 21 | 9PM to 10PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
February | 21 | 10PM to 11PM | 52 | 48.4 | 45.3 | 44.9 | 19.43 | 0.0772 | 0.3 | 13.03 | 0
February | 21 | 11PM to 12AM | 51.1 | 47.3 | 43.9 | 42.5 | 18.83 | 0.0774 | 0.29 | 13 | 1
February | 22 | 12AM to 1AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
February | 22 | 1AM to 2AM | 48.4 | 44.9 | 41.4 | 38.5 | 17.57 | 0.0778 | 0.26 | 12.92 | 1
February | 22 | 2AM to 3AM | 46.6 | 43.6 | 40.5 | 37.2 | 16.92 | 0.0781 | 0.25 | 12.87 | 1
February | 22 | 3AM to 4AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 22 | 4AM to 5AM | 45.7 | 42.8 | 39.7 | 36.1 | 16.55 | 0.0783 | 0.25 | 12.84 | 1
February | 22 | 5AM to 6AM | 46.2 | 43.2 | 40.1 | 36.7 | 16.76 | 0.0782 | 0.25 | 12.86 | 1
February | 22 | 6AM to 7AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
February | 22 | 7AM to 8AM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
February | 22 | 8AM to 9AM | 51.1 | 47.2 | 43.7 | 42.2 | 18.79 | 0.0774 | 0.29 | 13 | 1
February | 22 | 9AM to 10AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
February | 22 | 10AM to 11AM | 53.8 | 48.3 | 43.3 | 41.6 | 19.35 | 0.077 | 0.28 | 13.07 | 0
February | 22 | 11AM to 12PM | 54.3 | 47.8 | 41.7 | 39.1 | 19.09 | 0.0769 | 0.26 | 13.07 | 0
February | 22 | 12PM to 1PM | 55 | 47.8 | 41 | 38 | 19.1 | 0.0768 | 0.26 | 13.09 | 0
February | 22 | 1PM to 2PM | 55.4 | 47.3 | 39.4 | 35.6 | 18.82 | 0.0768 | 0.24 | 13.09 | 0
February | 22 | 2PM to 3PM | 55.6 | 47 | 38.5 | 34.4 | 18.67 | 0.0768 | 0.23 | 13.09 | 0
February | 22 | 3PM to 4PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
February | 22 | 4PM to 5PM | 55 | 46.3 | 37.2 | 32.7 | 18.28 | 0.0769 | 0.22 | 13.07 | 0
February | 22 | 5PM to 6PM | 54 | 45.6 | 36.9 | 32.3 | 17.95 | 0.077 | 0.22 | 13.04 | 0
February | 22 | 6PM to 7PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
February | 22 | 7PM to 8PM | 52.7 | 45.1 | 37 | 32.5 | 17.68 | 0.0772 | 0.22 | 13.01 | 0
February | 22 | 8PM to 9PM | 52.3 | 45.1 | 37.4 | 33 | 17.67 | 0.0773 | 0.22 | 13 | 0
February | 22 | 9PM to 10PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
February | 22 | 10PM to 11PM | 51.3 | 44.9 | 38.3 | 34.1 | 17.59 | 0.0774 | 0.23 | 12.98 | 1
February | 22 | 11PM to 12AM | 50.7 | 44.9 | 38.8 | 34.9 | 17.57 | 0.0775 | 0.24 | 12.97 | 1
February | 23 | 12AM to 1AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
February | 23 | 1AM to 2AM | 48.9 | 44.6 | 40.3 | 36.9 | 17.45 | 0.0778 | 0.25 | 12.93 | 1
February | 23 | 2AM to 3AM | 48 | 44.8 | 41.5 | 38.8 | 17.52 | 0.0779 | 0.26 | 12.91 | 1
February | 23 | 3AM to 4AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
February | 23 | 4AM to 5AM | 48.9 | 46.1 | 43.5 | 41.9 | 18.22 | 0.0777 | 0.28 | 12.94 | 1
February | 23 | 5AM to 6AM | 51.1 | 47.6 | 44.4 | 43.4 | 18.97 | 0.0774 | 0.29 | 13 | 1
February | 23 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
February | 23 | 7AM to 8AM | 53.4 | 48.6 | 44.4 | 43.4 | 19.54 | 0.077 | 0.29 | 13.06 | 0
February | 23 | 8AM to 9AM | 53.6 | 48.2 | 43.3 | 41.6 | 19.31 | 0.077 | 0.28 | 13.06 | 0
February | 23 | 9AM to 10AM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
February | 23 | 10AM to 11AM | 55 | 47.8 | 40.8 | 37.7 | 19.06 | 0.0768 | 0.26 | 13.09 | 0
February | 23 | 11AM to 12PM | 55.9 | 47.6 | 39.6 | 35.9 | 18.99 | 0.0767 | 0.24 | 13.1 | 0
February | 23 | 12PM to 1PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
February | 23 | 1PM to 2PM | 55.9 | 46.8 | 37.4 | 33 | 18.54 | 0.0767 | 0.22 | 13.09 | 0
February | 23 | 2PM to 3PM | 55 | 46 | 36.5 | 31.8 | 18.14 | 0.0769 | 0.22 | 13.07 | 0
February | 23 | 3PM to 4PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
February | 23 | 4PM to 5PM | 53.1 | 44.6 | 35.2 | 30.2 | 17.42 | 0.0772 | 0.21 | 13.01 | 0
February | 23 | 5PM to 6PM | 52 | 43.9 | 34.9 | 29.8 | 17.09 | 0.0773 | 0.2 | 12.98 | 0
February | 23 | 6PM to 7PM | 51.1 | 43.6 | 35.1 | 30 | 16.91 | 0.0775 | 0.2 | 12.96 | 1
February | 23 | 7PM to 8PM | 50.4 | 43.1 | 34.7 | 29.6 | 16.67 | 0.0776 | 0.2 | 12.94 | 1
February | 23 | 8PM to 9PM | 49.6 | 42.7 | 34.7 | 29.6 | 16.49 | 0.0777 | 0.2 | 12.92 | 1
February | 23 | 9PM to 10PM | 48.9 | 42.5 | 35.1 | 30 | 16.38 | 0.0778 | 0.2 | 12.91 | 1
February | 23 | 10PM to 11PM | 48.6 | 42.3 | 35.1 | 30 | 16.3 | 0.0779 | 0.2 | 12.9 | 1
February | 23 | 11PM to 12AM | 48.4 | 42.3 | 35.2 | 30.2 | 16.29 | 0.0779 | 0.21 | 12.89 | 1
February | 24 | 12AM to 1AM | 48 | 42.4 | 36 | 31.1 | 16.34 | 0.0779 | 0.21 | 12.89 | 1
February | 24 | 1AM to 2AM | 46.9 | 41.6 | 35.4 | 30.5 | 15.97 | 0.0781 | 0.21 | 12.86 | 1
February | 24 | 2AM to 3AM | 46 | 41.1 | 35.4 | 30.5 | 15.75 | 0.0782 | 0.21 | 12.84 | 1
February | 24 | 3AM to 4AM | 45 | 40.8 | 36 | 31.1 | 15.6 | 0.0784 | 0.21 | 12.81 | 1
February | 24 | 4AM to 5AM | 45 | 40.2 | 34.5 | 29.4 | 15.33 | 0.0784 | 0.2 | 12.81 | 1
February | 24 | 5AM to 6AM | 45 | 39.8 | 33.4 | 28.1 | 15.13 | 0.0784 | 0.19 | 12.8 | 1
February | 24 | 6AM to 7AM | 45 | 39.7 | 33.1 | 27.7 | 15.07 | 0.0784 | 0.19 | 12.8 | 1
February | 24 | 7AM to 8AM | 46.6 | 40.9 | 34.2 | 29 | 15.65 | 0.0782 | 0.2 | 12.85 | 1
February | 24 | 8AM to 9AM | 48.4 | 42.5 | 35.8 | 30.9 | 16.39 | 0.0779 | 0.21 | 12.9 | 1
February | 24 | 9AM to 10AM | 50 | 43.8 | 37 | 32.5 | 17.03 | 0.0776 | 0.22 | 12.94 | 1
February | 24 | 10AM to 11AM | 51.6 | 44.5 | 36.9 | 32.3 | 17.38 | 0.0774 | 0.22 | 12.98 | 1
February | 24 | 11AM to 12PM | 53.4 | 45.2 | 36.5 | 31.8 | 17.75 | 0.0771 | 0.22 | 13.03 | 0
February | 24 | 12PM to 1PM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
February | 24 | 1PM to 2PM | 55.4 | 46.5 | 37.2 | 32.7 | 18.37 | 0.0768 | 0.22 | 13.08 | 0
February | 24 | 2PM to 3PM | 55.6 | 46.8 | 37.9 | 33.7 | 18.56 | 0.0768 | 0.23 | 13.09 | 0
February | 24 | 3PM to 4PM | 55.9 | 47.4 | 39 | 35.1 | 18.88 | 0.0767 | 0.24 | 13.1 | 0
February | 24 | 4PM to 5PM | 54.3 | 46.2 | 37.9 | 33.7 | 18.26 | 0.077 | 0.23 | 13.06 | 0
February | 24 | 5PM to 6PM | 52.7 | 45.2 | 37.2 | 32.7 | 17.72 | 0.0772 | 0.22 | 13.01 | 0
February | 24 | 6PM to 7PM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 1
February | 24 | 7PM to 8PM | 50.7 | 44.4 | 37.8 | 33.4 | 17.35 | 0.0775 | 0.23 | 12.96 | 1
February | 24 | 8PM to 9PM | 50.4 | 44.6 | 38.7 | 34.6 | 17.45 | 0.0776 | 0.24 | 12.96 | 1
February | 24 | 9PM to 10PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
February | 24 | 10PM to 11PM | 49.3 | 44 | 38.3 | 34.1 | 17.11 | 0.0777 | 0.23 | 12.93 | 1
February | 24 | 11PM to 12AM | 48.7 | 43.1 | 36.9 | 32.3 | 16.69 | 0.0778 | 0.22 | 12.91 | 1
February | 25 | 12AM to 1AM | 48 | 42.4 | 36 | 31.1 | 16.34 | 0.0779 | 0.21 | 12.89 | 1
February | 25 | 1AM to 2AM | 46.8 | 41.5 | 35.4 | 30.5 | 15.93 | 0.0781 | 0.21 | 12.85 | 1
February | 25 | 2AM to 3AM | 45.3 | 40.8 | 35.4 | 30.5 | 15.58 | 0.0784 | 0.21 | 12.82 | 1
February | 25 | 3AM to 4AM | 44.1 | 40.3 | 36 | 31.1 | 15.38 | 0.0785 | 0.21 | 12.79 | 1
February | 25 | 4AM to 5AM | 43.3 | 39.6 | 35.1 | 30 | 15.03 | 0.0787 | 0.2 | 12.77 | 1
February | 25 | 5AM to 6AM | 42.8 | 39.2 | 34.7 | 29.6 | 14.84 | 0.0788 | 0.2 | 12.75 | 1
February | 25 | 6AM to 7AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
February | 25 | 7AM to 8AM | 45.3 | 41.3 | 36.7 | 32 | 15.82 | 0.0783 | 0.22 | 12.82 | 1
February | 25 | 8AM to 9AM | 48.7 | 44 | 39 | 35.1 | 17.13 | 0.0778 | 0.24 | 12.92 | 1
February | 25 | 9AM to 10AM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
February | 25 | 10AM to 11AM | 53.2 | 45.9 | 38.5 | 34.4 | 18.11 | 0.0771 | 0.23 | 13.03 | 0
February | 25 | 11AM to 12PM | 54.7 | 45.6 | 35.8 | 30.9 | 17.91 | 0.0769 | 0.21 | 13.06 | 0
February | 25 | 12PM to 1PM | 55.9 | 45.5 | 34 | 28.7 | 17.88 | 0.0768 | 0.2 | 13.08 | 0
February | 25 | 1PM to 2PM | 55.9 | 45.7 | 34.5 | 29.4 | 17.98 | 0.0767 | 0.2 | 13.08 | 0
February | 25 | 2PM to 3PM | 55.9 | 46.1 | 35.6 | 30.7 | 18.18 | 0.0767 | 0.21 | 13.09 | 0
February | 25 | 3PM to 4PM | 55.9 | 46.6 | 37 | 32.5 | 18.46 | 0.0767 | 0.22 | 13.09 | 0
February | 25 | 4PM to 5PM | 54.7 | 46.3 | 37.6 | 33.2 | 18.27 | 0.0769 | 0.23 | 13.06 | 0
February | 25 | 5PM to 6PM | 53.2 | 45.9 | 38.5 | 34.4 | 18.11 | 0.0771 | 0.23 | 13.03 | 0
February | 25 | 6PM to 7PM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
February | 25 | 7PM to 8PM | 51.6 | 45.8 | 39.9 | 36.4 | 18.02 | 0.0774 | 0.25 | 13 | 1
February | 25 | 8PM to 9PM | 51.4 | 45.8 | 40.3 | 36.9 | 18.06 | 0.0774 | 0.25 | 12.99 | 1
February | 25 | 9PM to 10PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
February | 25 | 10PM to 11PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
February | 25 | 11PM to 12AM | 49.1 | 44.3 | 39.4 | 35.6 | 17.3 | 0.0777 | 0.24 | 12.93 | 1
February | 26 | 12AM to 1AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
February | 26 | 1AM to 2AM | 46.4 | 42.3 | 37.8 | 33.4 | 16.3 | 0.0782 | 0.23 | 12.85 | 1
February | 26 | 2AM to 3AM | 44.6 | 41.1 | 37.2 | 32.7 | 15.76 | 0.0785 | 0.22 | 12.81 | 1
February | 26 | 3AM to 4AM | 43 | 40.2 | 37 | 32.5 | 15.33 | 0.0787 | 0.22 | 12.76 | 1
February | 26 | 4AM to 5AM | 42.3 | 39.5 | 36.1 | 31.3 | 14.98 | 0.0788 | 0.21 | 12.74 | 1
February | 26 | 5AM to 6AM | 41.7 | 39 | 35.8 | 30.9 | 14.78 | 0.0789 | 0.21 | 12.73 | 1
February | 26 | 6AM to 7AM | 41 | 38.7 | 36 | 31.1 | 14.64 | 0.079 | 0.21 | 12.71 | 1
February | 26 | 7AM to 8AM | 44.4 | 41.1 | 37.4 | 33 | 15.75 | 0.0785 | 0.22 | 12.8 | 1
February | 26 | 8AM to 9AM | 47.7 | 43.6 | 39.4 | 35.6 | 16.95 | 0.078 | 0.24 | 12.89 | 1
February | 26 | 9AM to 10AM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
February | 26 | 10AM to 11AM | 52.7 | 46.7 | 40.8 | 37.7 | 18.49 | 0.0772 | 0.26 | 13.03 | 0
February | 26 | 11AM to 12PM | 54.3 | 47.3 | 40.5 | 37.2 | 18.8 | 0.0769 | 0.25 | 13.07 | 0
February | 26 | 12PM to 1PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
February | 26 | 1PM to 2PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
February | 26 | 2PM to 3PM | 57.9 | 50.4 | 43.9 | 42.5 | 20.49 | 0.0764 | 0.29 | 13.17 | 0
February | 26 | 3PM to 4PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
February | 26 | 4PM to 5PM | 57.4 | 51 | 45.7 | 45.5 | 20.84 | 0.0764 | 0.31 | 13.17 | 0
February | 26 | 5PM to 6PM | 55.6 | 50.2 | 45.7 | 45.5 | 20.4 | 0.0767 | 0.31 | 13.12 | 0
February | 26 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
February | 26 | 7PM to 8PM | 53.6 | 49.3 | 45.7 | 45.5 | 19.92 | 0.077 | 0.31 | 13.07 | 0
February | 26 | 8PM to 9PM | 53.4 | 49.3 | 45.7 | 45.5 | 19.87 | 0.077 | 0.31 | 13.07 | 0
February | 26 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
February | 26 | 10PM to 11PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
February | 26 | 11PM to 12AM | 51.1 | 47.6 | 44.4 | 43.4 | 18.97 | 0.0774 | 0.29 | 13 | 1
February | 27 | 12AM to 1AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
February | 27 | 1AM to 2AM | 48.7 | 45.5 | 42.4 | 40.2 | 17.91 | 0.0778 | 0.27 | 12.93 | 1
February | 27 | 2AM to 3AM | 47.3 | 44.4 | 41.5 | 38.8 | 17.35 | 0.078 | 0.26 | 12.89 | 1
February | 27 | 3AM to 4AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
February | 27 | 4AM to 5AM | 45.7 | 43 | 40.1 | 36.7 | 16.63 | 0.0783 | 0.25 | 12.85 | 1
February | 27 | 5AM to 6AM | 45.3 | 42.6 | 39.7 | 36.1 | 16.46 | 0.0783 | 0.25 | 12.83 | 1
February | 27 | 6AM to 7AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
February | 27 | 7AM to 8AM | 47.3 | 44.5 | 41.7 | 39.1 | 17.39 | 0.078 | 0.26 | 12.89 | 1
February | 27 | 8AM to 9AM | 49.6 | 46.7 | 44.1 | 42.8 | 18.53 | 0.0776 | 0.29 | 12.96 | 1
February | 27 | 9AM to 10AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
February | 27 | 10AM to 11AM | 54.7 | 49.4 | 44.8 | 44 | 19.94 | 0.0768 | 0.3 | 13.1 | 0
February | 27 | 11AM to 12PM | 57.4 | 50 | 43.5 | 41.9 | 20.27 | 0.0765 | 0.28 | 13.16 | 0
February | 27 | 12PM to 1PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
February | 27 | 1PM to 2PM | 60.8 | 51.3 | 43.2 | 41.3 | 21.01 | 0.076 | 0.28 | 13.24 | 0
February | 27 | 2PM to 3PM | 61.3 | 51.9 | 43.9 | 42.5 | 21.32 | 0.0759 | 0.29 | 13.26 | 0
February | 27 | 3PM to 4PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
February | 27 | 4PM to 5PM | 59.4 | 51.5 | 45 | 44.3 | 21.12 | 0.0761 | 0.3 | 13.22 | 0
February | 27 | 5PM to 6PM | 56.7 | 50.5 | 45.3 | 44.9 | 20.56 | 0.0765 | 0.3 | 13.15 | 0
February | 27 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
February | 27 | 7PM to 8PM | 53.6 | 49.3 | 45.7 | 45.5 | 19.92 | 0.077 | 0.31 | 13.07 | 0
February | 27 | 8PM to 9PM | 53.4 | 49.3 | 45.7 | 45.5 | 19.87 | 0.077 | 0.31 | 13.07 | 0
February | 27 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
February | 27 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
February | 27 | 11PM to 12AM | 53.1 | 49.4 | 46.2 | 46.5 | 19.93 | 0.0771 | 0.31 | 13.06 | 0
February | 28 | 12AM to 1AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
February | 28 | 1AM to 2AM | 52.7 | 49.3 | 46.4 | 46.8 | 19.9 | 0.0771 | 0.32 | 13.05 | 0
February | 28 | 2AM to 3AM | 52.3 | 49.1 | 46.4 | 46.8 | 19.81 | 0.0772 | 0.32 | 13.04 | 0
February | 28 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
February | 28 | 4AM to 5AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
February | 28 | 5AM to 6AM | 52 | 48.6 | 45.7 | 45.5 | 19.52 | 0.0772 | 0.31 | 13.03 | 0
February | 28 | 6AM to 7AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
February | 28 | 7AM to 8AM | 51.3 | 48 | 45.1 | 44.6 | 19.2 | 0.0774 | 0.3 | 13.01 | 1
February | 28 | 8AM to 9AM | 50.7 | 47.6 | 44.8 | 44 | 18.98 | 0.0774 | 0.3 | 12.99 | 1
February | 28 | 9AM to 10AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
February | 28 | 10AM to 11AM | 51.6 | 46.7 | 42.1 | 39.6 | 18.52 | 0.0773 | 0.27 | 13 | 1
February | 28 | 11AM to 12PM | 53.4 | 46.7 | 40.1 | 36.7 | 18.5 | 0.0771 | 0.25 | 13.04 | 0
February | 28 | 12PM to 1PM | 55 | 47 | 39 | 35.1 | 18.66 | 0.0768 | 0.24 | 13.08 | 0
February | 28 | 1PM to 2PM | 54.7 | 46.2 | 37.4 | 33 | 18.23 | 0.0769 | 0.22 | 13.06 | 0
February | 28 | 2PM to 3PM | 54.3 | 45.7 | 36.5 | 31.8 | 17.97 | 0.077 | 0.22 | 13.05 | 0
February | 28 | 3PM to 4PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
February | 28 | 4PM to 5PM | 52.3 | 44.5 | 36 | 31.1 | 17.38 | 0.0773 | 0.21 | 13 | 0
February | 28 | 5PM to 6PM | 50.5 | 43.8 | 36.3 | 31.6 | 17.02 | 0.0775 | 0.21 | 12.95 | 1
February | 28 | 6PM to 7PM | 48.9 | 43.3 | 37 | 32.5 | 16.77 | 0.0778 | 0.22 | 12.92 | 1
February | 28 | 7PM to 8PM | 48.2 | 42.3 | 35.4 | 30.5 | 16.28 | 0.0779 | 0.21 | 12.89 | 1
February | 28 | 8PM to 9PM | 47.7 | 41.5 | 34.2 | 29 | 15.91 | 0.078 | 0.2 | 12.87 | 1
February | 28 | 9PM to 10PM | 47.8 | 42.4 | 36.3 | 31.6 | 16.36 | 0.078 | 0.21 | 12.89 | 1
February | 28 | 10PM to 11PM | 48 | 43.3 | 38.3 | 34.1 | 16.8 | 0.0779 | 0.23 | 12.9 | 1
February | 28 | 11PM to 12AM | 48.2 | 44.4 | 40.5 | 37.2 | 17.32 | 0.0779 | 0.25 | 12.91 | 1
March | 1 | 12AM to 1AM | 48.4 | 45.4 | 42.6 | 40.4 | 17.87 | 0.0778 | 0.27 | 12.92 | 1
March | 1 | 1AM to 2AM | 48.6 | 46.6 | 44.8 | 44 | 18.45 | 0.0778 | 0.3 | 12.94 | 1
March | 1 | 2AM to 3AM | 48.7 | 47.7 | 46.8 | 47.4 | 19.03 | 0.0777 | 0.32 | 12.95 | 1
March | 1 | 3AM to 4AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 1 | 4AM to 5AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 5AM to 6AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 1 | 6AM to 7AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 1 | 7AM to 8AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 8AM to 9AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 9AM to 10AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 10AM to 11AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 1 | 11AM to 12PM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
March | 1 | 12PM to 1PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
March | 1 | 1PM to 2PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
March | 1 | 2PM to 3PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
March | 1 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
March | 1 | 4PM to 5PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
March | 1 | 5PM to 6PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
March | 1 | 6PM to 7PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
March | 1 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
March | 1 | 8PM to 9PM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
March | 1 | 9PM to 10PM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
March | 1 | 10PM to 11PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
March | 1 | 11PM to 12AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
March | 2 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 2 | 1AM to 2AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
March | 2 | 2AM to 3AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
March | 2 | 3AM to 4AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 2 | 4AM to 5AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 2 | 5AM to 6AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 2 | 6AM to 7AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
March | 2 | 7AM to 8AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 2 | 8AM to 9AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
March | 2 | 9AM to 10AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
March | 2 | 10AM to 11AM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
March | 2 | 11AM to 12PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
March | 2 | 12PM to 1PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
March | 2 | 1PM to 2PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
March | 2 | 2PM to 3PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
March | 2 | 3PM to 4PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
March | 2 | 4PM to 5PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
March | 2 | 5PM to 6PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
March | 2 | 6PM to 7PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
March | 2 | 7PM to 8PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
March | 2 | 8PM to 9PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 2 | 9PM to 10PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 2 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 2 | 11PM to 12AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 3 | 12AM to 1AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 3 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 3 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 3 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
March | 3 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 3 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 3 | 6AM to 7AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 3 | 7AM to 8AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 3 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
March | 3 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
March | 3 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
March | 3 | 11AM to 12PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
March | 3 | 12PM to 1PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
March | 3 | 1PM to 2PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
March | 3 | 2PM to 3PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
March | 3 | 3PM to 4PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
March | 3 | 4PM to 5PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
March | 3 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
March | 3 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
March | 3 | 7PM to 8PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
March | 3 | 8PM to 9PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
March | 3 | 9PM to 10PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
March | 3 | 10PM to 11PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
March | 3 | 11PM to 12AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 4 | 12AM to 1AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 4 | 1AM to 2AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 2AM to 3AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 3AM to 4AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 4 | 4AM to 5AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 5AM to 6AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 6AM to 7AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 7AM to 8AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 4 | 8AM to 9AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 4 | 9AM to 10AM | 55 | 55 | 55 | 64.7 | 23.25 | 0.0767 | 0.44 | 13.17 | 0
March | 4 | 10AM to 11AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 11AM to 12PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
March | 4 | 12PM to 1PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
March | 4 | 1PM to 2PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
March | 4 | 2PM to 3PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
March | 4 | 3PM to 4PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
March | 4 | 4PM to 5PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
March | 4 | 5PM to 6PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 6PM to 7PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
March | 4 | 7PM to 8PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 8PM to 9PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 9PM to 10PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
March | 4 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 4 | 11PM to 12AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 5 | 12AM to 1AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
March | 5 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
March | 5 | 2AM to 3AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 5 | 3AM to 4AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
March | 5 | 4AM to 5AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 5 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 5 | 6AM to 7AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 5 | 7AM to 8AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 5 | 8AM to 9AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
March | 5 | 9AM to 10AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
March | 5 | 10AM to 11AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 5 | 11AM to 12PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 5 | 12PM to 1PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 5 | 1PM to 2PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 5 | 2PM to 3PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 5 | 3PM to 4PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
March | 5 | 4PM to 5PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 5 | 5PM to 6PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 5 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 5 | 7PM to 8PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 5 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 5 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
March | 5 | 10PM to 11PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
March | 5 | 11PM to 12AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 6 | 12AM to 1AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 6 | 1AM to 2AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 6 | 2AM to 3AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 6 | 3AM to 4AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 6 | 4AM to 5AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 6 | 5AM to 6AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 6 | 6AM to 7AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 6 | 7AM to 8AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 6 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 6 | 9AM to 10AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
March | 6 | 10AM to 11AM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
March | 6 | 11AM to 12PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
March | 6 | 12PM to 1PM | 66 | 53.9 | 44.1 | 42.8 | 22.51 | 0.0752 | 0.29 | 13.38 | 0
March | 6 | 1PM to 2PM | 68 | 54.7 | 44.1 | 42.8 | 22.99 | 0.0749 | 0.29 | 13.43 | 0
March | 6 | 2PM to 3PM | 66.9 | 56.5 | 48.9 | 51.5 | 24.08 | 0.075 | 0.35 | 13.43 | 0
March | 6 | 3PM to 4PM | 64.9 | 54.8 | 46.9 | 47.8 | 23.02 | 0.0753 | 0.32 | 13.37 | 0
March | 6 | 4PM to 5PM | 63 | 52.2 | 43 | 41 | 21.49 | 0.0756 | 0.28 | 13.3 | 0
March | 6 | 5PM to 6PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
March | 6 | 6PM to 7PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
March | 6 | 7PM to 8PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
March | 6 | 8PM to 9PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
March | 6 | 9PM to 10PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 6 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 6 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 7 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 7 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
March | 7 | 2AM to 3AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
March | 7 | 3AM to 4AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 7 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 7 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 7 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 7 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 7 | 8AM to 9AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
March | 7 | 9AM to 10AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
March | 7 | 10AM to 11AM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
March | 7 | 11AM to 12PM | 69.1 | 52.8 | 37.9 | 33.7 | 21.83 | 0.0748 | 0.23 | 13.43 | 0
March | 7 | 12PM to 1PM | 71.1 | 51.4 | 30.9 | 25.2 | 20.99 | 0.0746 | 0.17 | 13.46 | 0
March | 7 | 1PM to 2PM | 71.1 | 52.7 | 35.1 | 30 | 21.74 | 0.0746 | 0.2 | 13.47 | 0
March | 7 | 2PM to 3PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
March | 7 | 3PM to 4PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
March | 7 | 4PM to 5PM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
March | 7 | 5PM to 6PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 7 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
March | 7 | 7PM to 8PM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
March | 7 | 8PM to 9PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
March | 7 | 9PM to 10PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 7 | 10PM to 11PM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 7 | 11PM to 12AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 8 | 12AM to 1AM | 48 | 48 | 48 | 49.8 | 19.22 | 0.0778 | 0.34 | 12.94 | 1
March | 8 | 1AM to 2AM | 48 | 48 | 48 | 49.8 | 19.22 | 0.0778 | 0.34 | 12.94 | 1
March | 8 | 2AM to 3AM | 46.9 | 46.9 | 46.9 | 47.8 | 18.65 | 0.078 | 0.32 | 12.91 | 1
March | 8 | 3AM to 4AM | 46 | 46 | 46 | 46.1 | 18.18 | 0.0781 | 0.31 | 12.88 | 1
March | 8 | 4AM to 5AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
March | 8 | 5AM to 6AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
March | 8 | 6AM to 7AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
March | 8 | 7AM to 8AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
March | 8 | 8AM to 9AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
March | 8 | 9AM to 10AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 8 | 10AM to 11AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 8 | 11AM to 12PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
March | 8 | 12PM to 1PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
March | 8 | 1PM to 2PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
March | 8 | 2PM to 3PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
March | 8 | 3PM to 4PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
March | 8 | 4PM to 5PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
March | 8 | 5PM to 6PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 8 | 6PM to 7PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 8 | 7PM to 8PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
March | 8 | 8PM to 9PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 8 | 9PM to 10PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 8 | 10PM to 11PM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 8 | 11PM to 12AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 9 | 12AM to 1AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 9 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 9 | 2AM to 3AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 9 | 3AM to 4AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 9 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 9 | 5AM to 6AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 9 | 6AM to 7AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 9 | 7AM to 8AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 9 | 8AM to 9AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 9 | 9AM to 10AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 9 | 10AM to 11AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 9 | 11AM to 12PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
March | 9 | 12PM to 1PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
March | 9 | 1PM to 2PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
March | 9 | 2PM to 3PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
March | 9 | 3PM to 4PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 9 | 4PM to 5PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 9 | 5PM to 6PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 9 | 6PM to 7PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 9 | 7PM to 8PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 9 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 9 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 9 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 9 | 11PM to 12AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
March | 10 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
March | 10 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 10 | 2AM to 3AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
March | 10 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
March | 10 | 4AM to 5AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 10 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 10 | 6AM to 7AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
March | 10 | 7AM to 8AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
March | 10 | 8AM to 9AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
March | 10 | 9AM to 10AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
March | 10 | 10AM to 11AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
March | 10 | 11AM to 12PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
March | 10 | 12PM to 1PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
March | 10 | 1PM to 2PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
March | 10 | 2PM to 3PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
March | 10 | 3PM to 4PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
March | 10 | 4PM to 5PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
March | 10 | 5PM to 6PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
March | 10 | 6PM to 7PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
March | 10 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 10 | 8PM to 9PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
March | 10 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
March | 10 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
March | 10 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
March | 11 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 11 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 11 | 2AM to 3AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 11 | 3AM to 4AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 11 | 4AM to 5AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
March | 11 | 5AM to 6AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 11 | 6AM to 7AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 11 | 7AM to 8AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
March | 11 | 8AM to 9AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 11 | 9AM to 10AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 11 | 10AM to 11AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 11 | 11AM to 12PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
March | 11 | 12PM to 1PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
March | 11 | 1PM to 2PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
March | 11 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
March | 11 | 3PM to 4PM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
March | 11 | 4PM to 5PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
March | 11 | 5PM to 6PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
March | 11 | 6PM to 7PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 11 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 11 | 8PM to 9PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 11 | 9PM to 10PM | 62.1 | 49.1 | 36 | 31.1 | 19.73 | 0.0758 | 0.21 | 13.24 | 0
March | 11 | 10PM to 11PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
March | 11 | 11PM to 12AM | 59 | 50.5 | 43 | 41 | 20.53 | 0.0762 | 0.28 | 13.2 | 0
March | 12 | 12AM to 1AM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
March | 12 | 1AM to 2AM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
March | 12 | 2AM to 3AM | 61 | 47.9 | 34 | 28.7 | 19.1 | 0.076 | 0.2 | 13.21 | 0
March | 12 | 3AM to 4AM | 59 | 47.7 | 36 | 31.1 | 18.99 | 0.0763 | 0.21 | 13.17 | 0
March | 12 | 4AM to 5AM | 59 | 47.7 | 36 | 31.1 | 18.99 | 0.0763 | 0.21 | 13.17 | 0
March | 12 | 5AM to 6AM | 57.9 | 47.9 | 37.9 | 33.7 | 19.13 | 0.0764 | 0.23 | 13.15 | 0
March | 12 | 6AM to 7AM | 59 | 46.7 | 33.1 | 27.7 | 18.47 | 0.0763 | 0.19 | 13.16 | 0
March | 12 | 7AM to 8AM | 60.1 | 48.6 | 37 | 32.5 | 19.47 | 0.0761 | 0.22 | 13.2 | 0
March | 12 | 8AM to 9AM | 62.1 | 50.2 | 39 | 35.1 | 20.36 | 0.0758 | 0.24 | 13.26 | 0
March | 12 | 9AM to 10AM | 64.9 | 51.8 | 39.9 | 36.4 | 21.25 | 0.0754 | 0.25 | 13.33 | 0
March | 12 | 10AM to 11AM | 68 | 51 | 34 | 28.7 | 20.8 | 0.075 | 0.2 | 13.39 | 0
March | 12 | 11AM to 12PM | 70 | 52.5 | 36 | 31.1 | 21.65 | 0.0747 | 0.21 | 13.45 | 0
March | 12 | 12PM to 1PM | 72 | 52.7 | 34 | 28.7 | 21.76 | 0.0744 | 0.2 | 13.49 | 0
March | 12 | 1PM to 2PM | 73.9 | 53 | 32 | 26.5 | 21.89 | 0.0742 | 0.18 | 13.53 | 0
March | 12 | 2PM to 3PM | 75 | 52.8 | 30 | 24.2 | 21.79 | 0.074 | 0.16 | 13.55 | 0
March | 12 | 3PM to 4PM | 75 | 53.1 | 30.9 | 25.2 | 21.95 | 0.074 | 0.17 | 13.56 | 0
March | 12 | 4PM to 5PM | 73.9 | 53.9 | 35.1 | 30 | 22.44 | 0.0742 | 0.2 | 13.54 | 0
March | 12 | 5PM to 6PM | 71.1 | 51.7 | 32 | 26.5 | 21.2 | 0.0746 | 0.18 | 13.46 | 0
March | 12 | 6PM to 7PM | 66 | 53.1 | 42.1 | 39.6 | 22.01 | 0.0752 | 0.27 | 13.37 | 0
March | 12 | 7PM to 8PM | 63 | 50.9 | 39.9 | 36.4 | 20.77 | 0.0757 | 0.25 | 13.28 | 0
March | 12 | 8PM to 9PM | 61 | 49 | 37 | 32.5 | 19.68 | 0.076 | 0.22 | 13.22 | 0
March | 12 | 9PM to 10PM | 59 | 48.4 | 37.9 | 33.7 | 19.39 | 0.0763 | 0.23 | 13.17 | 0
March | 12 | 10PM to 11PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
March | 12 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
March | 13 | 12AM to 1AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
March | 13 | 1AM to 2AM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 1
March | 13 | 2AM to 3AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
March | 13 | 3AM to 4AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
March | 13 | 4AM to 5AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
March | 13 | 5AM to 6AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
March | 13 | 6AM to 7AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
March | 13 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
March | 13 | 8AM to 9AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
March | 13 | 9AM to 10AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
March | 13 | 10AM to 11AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
March | 13 | 11AM to 12PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
March | 13 | 12PM to 1PM | 69.1 | 56 | 46 | 46.1 | 23.78 | 0.0747 | 0.31 | 13.47 | 0
March | 13 | 1PM to 2PM | 73 | 54.8 | 39 | 35.1 | 23.02 | 0.0742 | 0.24 | 13.54 | 0
March | 13 | 2PM to 3PM | 73 | 57.1 | 45 | 44.3 | 24.45 | 0.0742 | 0.3 | 13.56 | 0
March | 13 | 3PM to 4PM | 75 | 54.3 | 35.1 | 30 | 22.7 | 0.074 | 0.2 | 13.57 | 0
March | 13 | 4PM to 5PM | 73 | 52.9 | 33.1 | 27.7 | 21.86 | 0.0743 | 0.19 | 13.51 | 0
March | 13 | 5PM to 6PM | 68 | 52.4 | 37.9 | 33.7 | 21.57 | 0.075 | 0.23 | 13.4 | 0
March | 13 | 6PM to 7PM | 62.1 | 50.5 | 39.9 | 36.4 | 20.55 | 0.0758 | 0.25 | 13.26 | 0
March | 13 | 7PM to 8PM | 61 | 50.5 | 41 | 38 | 20.54 | 0.0759 | 0.26 | 13.24 | 0
March | 13 | 8PM to 9PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
March | 13 | 9PM to 10PM | 57.9 | 49.6 | 42.1 | 39.6 | 20.05 | 0.0764 | 0.27 | 13.17 | 0
March | 13 | 10PM to 11PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
March | 13 | 11PM to 12AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 14 | 12AM to 1AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
March | 14 | 1AM to 2AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
March | 14 | 2AM to 3AM | 50 | 43.4 | 36 | 31.1 | 16.82 | 0.0776 | 0.21 | 12.94 | 1
March | 14 | 3AM to 4AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
March | 14 | 4AM to 5AM | 48 | 48 | 48 | 49.8 | 19.22 | 0.0778 | 0.34 | 12.94 | 1
March | 14 | 5AM to 6AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
March | 14 | 6AM to 7AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
March | 14 | 7AM to 8AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 14 | 8AM to 9AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
March | 14 | 9AM to 10AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
March | 14 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
March | 14 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
March | 14 | 12PM to 1PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
March | 14 | 1PM to 2PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
March | 14 | 2PM to 3PM | 72 | 55.1 | 41 | 38 | 23.2 | 0.0744 | 0.26 | 13.52 | 0
March | 14 | 3PM to 4PM | 66 | 50.5 | 35.1 | 30 | 20.52 | 0.0753 | 0.2 | 13.34 | 0
March | 14 | 4PM to 5PM | 64 | 51.1 | 39 | 35.1 | 20.84 | 0.0755 | 0.24 | 13.31 | 0
March | 14 | 5PM to 6PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
March | 14 | 6PM to 7PM | 57 | 46.4 | 35.1 | 30 | 18.34 | 0.0766 | 0.2 | 13.11 | 0
March | 14 | 7PM to 8PM | 55.9 | 46.2 | 36 | 31.1 | 18.25 | 0.0767 | 0.21 | 13.09 | 0
March | 14 | 8PM to 9PM | 55 | 47.8 | 41 | 38 | 19.1 | 0.0768 | 0.26 | 13.09 | 0
March | 14 | 9PM to 10PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
March | 14 | 10PM to 11PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
March | 14 | 11PM to 12AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
March | 15 | 12AM to 1AM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
March | 15 | 1AM to 2AM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
March | 15 | 2AM to 3AM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
March | 15 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 15 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 15 | 5AM to 6AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
March | 15 | 6AM to 7AM | 48.9 | 48.4 | 48 | 49.8 | 19.44 | 0.0777 | 0.34 | 12.97 | 1
March | 15 | 7AM to 8AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 15 | 8AM to 9AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
March | 15 | 9AM to 10AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
March | 15 | 10AM to 11AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
March | 15 | 11AM to 12PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
March | 15 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
March | 15 | 1PM to 2PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
March | 15 | 2PM to 3PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
March | 15 | 3PM to 4PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
March | 15 | 4PM to 5PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
March | 15 | 5PM to 6PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
March | 15 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
March | 15 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 15 | 8PM to 9PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 15 | 9PM to 10PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 15 | 10PM to 11PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 15 | 11PM to 12AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
March | 16 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 16 | 1AM to 2AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
March | 16 | 2AM to 3AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
March | 16 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
March | 16 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 16 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 16 | 6AM to 7AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
March | 16 | 7AM to 8AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
March | 16 | 8AM to 9AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
March | 16 | 9AM to 10AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 16 | 10AM to 11AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 16 | 11AM to 12PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 16 | 12PM to 1PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 16 | 1PM to 2PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 16 | 2PM to 3PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
March | 16 | 3PM to 4PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
March | 16 | 4PM to 5PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 16 | 5PM to 6PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
March | 16 | 6PM to 7PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
March | 16 | 7PM to 8PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
March | 16 | 8PM to 9PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
March | 16 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
March | 16 | 10PM to 11PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
March | 16 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 17 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 17 | 1AM to 2AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
March | 17 | 2AM to 3AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
March | 17 | 3AM to 4AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
March | 17 | 4AM to 5AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
March | 17 | 5AM to 6AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
March | 17 | 6AM to 7AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
March | 17 | 7AM to 8AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
March | 17 | 8AM to 9AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
March | 17 | 9AM to 10AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 17 | 10AM to 11AM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
March | 17 | 11AM to 12PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
March | 17 | 12PM to 1PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
March | 17 | 1PM to 2PM | 62.1 | 50.5 | 39.9 | 36.4 | 20.55 | 0.0758 | 0.25 | 13.26 | 0
March | 17 | 2PM to 3PM | 64 | 52.3 | 42.1 | 39.6 | 21.53 | 0.0755 | 0.27 | 13.32 | 0
March | 17 | 3PM to 4PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
March | 17 | 4PM to 5PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
March | 17 | 5PM to 6PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
March | 17 | 6PM to 7PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 17 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
March | 17 | 8PM to 9PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 17 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 17 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 17 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 18 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 4AM to 5AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 18 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 18 | 6AM to 7AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 18 | 8AM to 9AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
March | 18 | 9AM to 10AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
March | 18 | 10AM to 11AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 18 | 11AM to 12PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
March | 18 | 12PM to 1PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
March | 18 | 1PM to 2PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
March | 18 | 2PM to 3PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
March | 18 | 3PM to 4PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
March | 18 | 4PM to 5PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
March | 18 | 5PM to 6PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
March | 18 | 6PM to 7PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
March | 18 | 7PM to 8PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 18 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 18 | 9PM to 10PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 18 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 18 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 19 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 19 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 19 | 2AM to 3AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 19 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 19 | 4AM to 5AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
March | 19 | 5AM to 6AM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
March | 19 | 6AM to 7AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 19 | 7AM to 8AM | 50 | 43 | 35.1 | 30 | 16.64 | 0.0776 | 0.2 | 12.94 | 1
March | 19 | 8AM to 9AM | 51.1 | 43.9 | 36 | 31.1 | 17.08 | 0.0775 | 0.21 | 12.97 | 1
March | 19 | 9AM to 10AM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
March | 19 | 10AM to 11AM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
March | 19 | 11AM to 12PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
March | 19 | 12PM to 1PM | 57.9 | 48.3 | 39 | 35.1 | 19.35 | 0.0764 | 0.24 | 13.15 | 0
March | 19 | 1PM to 2PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
March | 19 | 2PM to 3PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
March | 19 | 3PM to 4PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
March | 19 | 4PM to 5PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
March | 19 | 5PM to 6PM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
March | 19 | 6PM to 7PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
March | 19 | 7PM to 8PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
March | 19 | 8PM to 9PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
March | 19 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
March | 19 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 19 | 11PM to 12AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 20 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 20 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
March | 20 | 2AM to 3AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 20 | 3AM to 4AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
March | 20 | 4AM to 5AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
March | 20 | 5AM to 6AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
March | 20 | 6AM to 7AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
March | 20 | 7AM to 8AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
March | 20 | 8AM to 9AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
March | 20 | 9AM to 10AM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
March | 20 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
March | 20 | 11AM to 12PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
March | 20 | 12PM to 1PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
March | 20 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
March | 20 | 2PM to 3PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
March | 20 | 3PM to 4PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
March | 20 | 4PM to 5PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
March | 20 | 5PM to 6PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
March | 20 | 6PM to 7PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
March | 20 | 7PM to 8PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
March | 20 | 8PM to 9PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
March | 20 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
March | 20 | 10PM to 11PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
March | 20 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
March | 21 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
March | 21 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 21 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 21 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 21 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 21 | 5AM to 6AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 21 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 21 | 7AM to 8AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
March | 21 | 8AM to 9AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
March | 21 | 9AM to 10AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
March | 21 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
March | 21 | 11AM to 12PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
March | 21 | 12PM to 1PM | 60.1 | 49.7 | 39.9 | 36.4 | 20.07 | 0.0761 | 0.25 | 13.21 | 0
March | 21 | 1PM to 2PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
March | 21 | 2PM to 3PM | 57 | 46.8 | 36 | 31.1 | 18.51 | 0.0766 | 0.21 | 13.12 | 0
March | 21 | 3PM to 4PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
March | 21 | 4PM to 5PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
March | 21 | 5PM to 6PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
March | 21 | 6PM to 7PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 1
March | 21 | 7PM to 8PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
March | 21 | 8PM to 9PM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
March | 21 | 9PM to 10PM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
March | 21 | 10PM to 11PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
March | 21 | 11PM to 12AM | 48 | 42.8 | 37 | 32.5 | 16.55 | 0.0779 | 0.22 | 12.89 | 1
March | 22 | 12AM to 1AM | 48 | 42 | 35.1 | 30 | 16.17 | 0.0779 | 0.2 | 12.89 | 1
March | 22 | 1AM to 2AM | 46.9 | 41.1 | 34 | 28.7 | 15.71 | 0.0781 | 0.2 | 12.85 | 1
March | 22 | 2AM to 3AM | 46.9 | 41.1 | 34 | 28.7 | 15.71 | 0.0781 | 0.2 | 12.85 | 1
March | 22 | 3AM to 4AM | 48 | 42 | 35.1 | 30 | 16.17 | 0.0779 | 0.2 | 12.89 | 1
March | 22 | 4AM to 5AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 22 | 5AM to 6AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 22 | 6AM to 7AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
March | 22 | 7AM to 8AM | 48.9 | 44.1 | 39 | 35.1 | 17.17 | 0.0778 | 0.24 | 12.92 | 1
March | 22 | 8AM to 9AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
March | 22 | 9AM to 10AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
March | 22 | 10AM to 11AM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
March | 22 | 11AM to 12PM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
March | 22 | 12PM to 1PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
March | 22 | 1PM to 2PM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
March | 22 | 2PM to 3PM | 52 | 44.8 | 37 | 32.5 | 17.51 | 0.0773 | 0.22 | 12.99 | 0
March | 22 | 3PM to 4PM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 1
March | 22 | 4PM to 5PM | 50 | 43 | 35.1 | 30 | 16.64 | 0.0776 | 0.2 | 12.94 | 1
March | 22 | 5PM to 6PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
March | 22 | 6PM to 7PM | 48 | 41.6 | 34 | 28.7 | 15.97 | 0.078 | 0.2 | 12.88 | 1
March | 22 | 7PM to 8PM | 48 | 42 | 35.1 | 30 | 16.17 | 0.0779 | 0.2 | 12.89 | 1
March | 22 | 8PM to 9PM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 22 | 9PM to 10PM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
March | 22 | 10PM to 11PM | 44.1 | 40.8 | 37 | 32.5 | 15.59 | 0.0785 | 0.22 | 12.79 | 1
March | 22 | 11PM to 12AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
March | 23 | 12AM to 1AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
March | 23 | 1AM to 2AM | 41 | 39.2 | 37 | 32.5 | 14.85 | 0.079 | 0.22 | 12.71 | 1
March | 23 | 2AM to 3AM | 43 | 40.2 | 37 | 32.5 | 15.33 | 0.0787 | 0.22 | 12.76 | 1
March | 23 | 3AM to 4AM | 41 | 39.2 | 37 | 32.5 | 14.85 | 0.079 | 0.22 | 12.71 | 1
March | 23 | 4AM to 5AM | 39.9 | 38.6 | 37 | 32.5 | 14.59 | 0.0792 | 0.22 | 12.69 | 1
March | 23 | 5AM to 6AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0792 | 0.23 | 12.69 | 1
March | 23 | 6AM to 7AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
March | 23 | 7AM to 8AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
March | 23 | 8AM to 9AM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
March | 23 | 9AM to 10AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
March | 23 | 10AM to 11AM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
March | 23 | 11AM to 12PM | 55 | 47.4 | 39.9 | 36.4 | 18.85 | 0.0768 | 0.25 | 13.08 | 0
March | 23 | 12PM to 1PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
March | 23 | 1PM to 2PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
March | 23 | 2PM to 3PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
March | 23 | 3PM to 4PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
March | 23 | 4PM to 5PM | 55 | 47.4 | 39.9 | 36.4 | 18.85 | 0.0768 | 0.25 | 13.08 | 0
March | 23 | 5PM to 6PM | 54 | 47.3 | 41 | 38 | 18.84 | 0.077 | 0.26 | 13.06 | 0
March | 23 | 6PM to 7PM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
March | 23 | 7PM to 8PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
March | 23 | 8PM to 9PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
March | 23 | 9PM to 10PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
March | 23 | 10PM to 11PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
March | 23 | 11PM to 12AM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
March | 24 | 12AM to 1AM | 53.1 | 46.1 | 39 | 35.1 | 18.18 | 0.0771 | 0.24 | 13.03 | 0
March | 24 | 1AM to 2AM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
March | 24 | 2AM to 3AM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 1
March | 24 | 3AM to 4AM | 50 | 43.4 | 36 | 31.1 | 16.82 | 0.0776 | 0.21 | 12.94 | 1
March | 24 | 4AM to 5AM | 50 | 43.8 | 37 | 32.5 | 17.03 | 0.0776 | 0.22 | 12.94 | 1
March | 24 | 5AM to 6AM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
March | 24 | 6AM to 7AM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
March | 24 | 7AM to 8AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
March | 24 | 8AM to 9AM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
March | 24 | 9AM to 10AM | 55 | 47 | 39 | 35.1 | 18.66 | 0.0768 | 0.24 | 13.08 | 0
March | 24 | 10AM to 11AM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
March | 24 | 11AM to 12PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
March | 24 | 12PM to 1PM | 57 | 48.7 | 41 | 38 | 19.58 | 0.0765 | 0.26 | 13.14 | 0
March | 24 | 1PM to 2PM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
March | 24 | 2PM to 3PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
March | 24 | 3PM to 4PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 24 | 4PM to 5PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 24 | 5PM to 6PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 24 | 6PM to 7PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 24 | 7PM to 8PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
March | 24 | 8PM to 9PM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
March | 24 | 9PM to 10PM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
March | 24 | 10PM to 11PM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
March | 24 | 11PM to 12AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
March | 25 | 12AM to 1AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
March | 25 | 1AM to 2AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
March | 25 | 2AM to 3AM | 46 | 46 | 46 | 46.1 | 18.18 | 0.0781 | 0.31 | 12.88 | 1
March | 25 | 3AM to 4AM | 46 | 46 | 46 | 46.1 | 18.18 | 0.0781 | 0.31 | 12.88 | 1
March | 25 | 4AM to 5AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
March | 25 | 5AM to 6AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
March | 25 | 6AM to 7AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
March | 25 | 7AM to 8AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
March | 25 | 8AM to 9AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
March | 25 | 9AM to 10AM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
March | 25 | 10AM to 11AM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
March | 25 | 11AM to 12PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
March | 25 | 12PM to 1PM | 57 | 49.6 | 43 | 41 | 20.05 | 0.0765 | 0.28 | 13.15 | 0
March | 25 | 1PM to 2PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
March | 25 | 2PM to 3PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
March | 25 | 3PM to 4PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
March | 25 | 4PM to 5PM | 55 | 49.2 | 44.1 | 42.8 | 19.84 | 0.0768 | 0.29 | 13.1 | 0
March | 25 | 5PM to 6PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
March | 25 | 6PM to 7PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
March | 25 | 7PM to 8PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
March | 25 | 8PM to 9PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 25 | 9PM to 10PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 25 | 10PM to 11PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 25 | 11PM to 12AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 26 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
March | 26 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 26 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 26 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 26 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 26 | 5AM to 6AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
March | 26 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 26 | 7AM to 8AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 26 | 8AM to 9AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 26 | 9AM to 10AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
March | 26 | 10AM to 11AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
March | 26 | 11AM to 12PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
March | 26 | 12PM to 1PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
March | 26 | 1PM to 2PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
March | 26 | 2PM to 3PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
March | 26 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
March | 26 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
March | 26 | 5PM to 6PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 26 | 6PM to 7PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 26 | 7PM to 8PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
March | 26 | 8PM to 9PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 26 | 9PM to 10PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 26 | 10PM to 11PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 26 | 11PM to 12AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 27 | 12AM to 1AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 27 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 27 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 27 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 27 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 27 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 27 | 6AM to 7AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 27 | 7AM to 8AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 27 | 8AM to 9AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 27 | 9AM to 10AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 27 | 10AM to 11AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
March | 27 | 11AM to 12PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
March | 27 | 12PM to 1PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
March | 27 | 1PM to 2PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
March | 27 | 2PM to 3PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
March | 27 | 3PM to 4PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
March | 27 | 4PM to 5PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
March | 27 | 5PM to 6PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
March | 27 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
March | 27 | 7PM to 8PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 27 | 8PM to 9PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 27 | 9PM to 10PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 27 | 10PM to 11PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 27 | 11PM to 12AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
March | 28 | 12AM to 1AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 28 | 1AM to 2AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 28 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
March | 28 | 3AM to 4AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
March | 28 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
March | 28 | 5AM to 6AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 28 | 6AM to 7AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 28 | 7AM to 8AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
March | 28 | 8AM to 9AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 28 | 9AM to 10AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
March | 28 | 10AM to 11AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
March | 28 | 11AM to 12PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
March | 28 | 12PM to 1PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
March | 28 | 1PM to 2PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
March | 28 | 2PM to 3PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
March | 28 | 3PM to 4PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
March | 28 | 4PM to 5PM | 64 | 51.1 | 39 | 35.1 | 20.84 | 0.0755 | 0.24 | 13.31 | 0
March | 28 | 5PM to 6PM | 60.1 | 48.2 | 36 | 31.1 | 19.25 | 0.0761 | 0.21 | 13.19 | 0
March | 28 | 6PM to 7PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
March | 28 | 7PM to 8PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
March | 28 | 8PM to 9PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 28 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 28 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 28 | 11PM to 12AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
March | 29 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 29 | 1AM to 2AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 29 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 29 | 3AM to 4AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
March | 29 | 4AM to 5AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
March | 29 | 5AM to 6AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
March | 29 | 6AM to 7AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
March | 29 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
March | 29 | 8AM to 9AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
March | 29 | 9AM to 10AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
March | 29 | 10AM to 11AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
March | 29 | 11AM to 12PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
March | 29 | 12PM to 1PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
March | 29 | 1PM to 2PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
March | 29 | 2PM to 3PM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 29 | 3PM to 4PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
March | 29 | 4PM to 5PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
March | 29 | 5PM to 6PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
March | 29 | 6PM to 7PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
March | 29 | 7PM to 8PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 29 | 8PM to 9PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
March | 29 | 9PM to 10PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
March | 29 | 10PM to 11PM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
March | 29 | 11PM to 12AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
March | 30 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 30 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
March | 30 | 2AM to 3AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
March | 30 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 30 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
March | 30 | 5AM to 6AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
March | 30 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 30 | 7AM to 8AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
March | 30 | 8AM to 9AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
March | 30 | 9AM to 10AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
March | 30 | 10AM to 11AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
March | 30 | 11AM to 12PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
March | 30 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
March | 30 | 1PM to 2PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
March | 30 | 2PM to 3PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
March | 30 | 3PM to 4PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
March | 30 | 4PM to 5PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
March | 30 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
March | 30 | 6PM to 7PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 30 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
March | 30 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
March | 30 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 30 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
March | 30 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
March | 31 | 12AM to 1AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
March | 31 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
March | 31 | 2AM to 3AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
March | 31 | 3AM to 4AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
March | 31 | 4AM to 5AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
March | 31 | 5AM to 6AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
March | 31 | 6AM to 7AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
March | 31 | 7AM to 8AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
March | 31 | 8AM to 9AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
March | 31 | 9AM to 10AM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
March | 31 | 10AM to 11AM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
March | 31 | 11AM to 12PM | 64 | 51.1 | 39 | 35.1 | 20.84 | 0.0755 | 0.24 | 13.31 | 0
March | 31 | 12PM to 1PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
March | 31 | 1PM to 2PM | 66 | 53.5 | 43 | 41 | 22.23 | 0.0752 | 0.28 | 13.38 | 0
March | 31 | 2PM to 3PM | 64 | 51.8 | 41 | 38 | 21.28 | 0.0755 | 0.26 | 13.32 | 0
March | 31 | 3PM to 4PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
March | 31 | 4PM to 5PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
March | 31 | 5PM to 6PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
March | 31 | 6PM to 7PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
March | 31 | 7PM to 8PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
March | 31 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
March | 31 | 9PM to 10PM | 54.1 | 50.4 | 47.3 | 48.4 | 20.5 | 0.0769 | 0.33 | 13.1 | 0
March | 31 | 10PM to 11PM | 55 | 50.1 | 45.9 | 45.8 | 20.32 | 0.0768 | 0.31 | 13.11 | 0
March | 31 | 11PM to 12AM | 56.1 | 49.8 | 44.2 | 43.1 | 20.15 | 0.0766 | 0.29 | 13.13 | 0
April | 1 | 12AM to 1AM | 57 | 49.4 | 42.6 | 40.4 | 19.96 | 0.0765 | 0.27 | 13.14 | 0
April | 1 | 1AM to 2AM | 58.1 | 49.2 | 41 | 38 | 19.84 | 0.0764 | 0.26 | 13.16 | 0
April | 1 | 2AM to 3AM | 59 | 49 | 39.6 | 35.9 | 19.73 | 0.0763 | 0.24 | 13.18 | 0
April | 1 | 3AM to 4AM | 60.1 | 48.9 | 37.9 | 33.7 | 19.65 | 0.0761 | 0.23 | 13.2 | 0
April | 1 | 4AM to 5AM | 61 | 49.3 | 37.9 | 33.7 | 19.87 | 0.076 | 0.23 | 13.23 | 0
April | 1 | 5AM to 6AM | 64 | 50.7 | 37.9 | 33.7 | 20.61 | 0.0755 | 0.23 | 13.3 | 0
April | 1 | 6AM to 7AM | 64.9 | 53 | 43 | 41 | 21.97 | 0.0754 | 0.28 | 13.35 | 0
April | 1 | 7AM to 8AM | 66 | 53.9 | 44.1 | 42.8 | 22.51 | 0.0752 | 0.29 | 13.38 | 0
April | 1 | 8AM to 9AM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
April | 1 | 9AM to 10AM | 71.1 | 56.3 | 45 | 44.3 | 23.96 | 0.0745 | 0.3 | 13.51 | 0
April | 1 | 10AM to 11AM | 75 | 54.6 | 36 | 31.1 | 22.87 | 0.074 | 0.21 | 13.57 | 0
April | 1 | 11AM to 12PM | 75.9 | 56.3 | 39.9 | 36.4 | 23.91 | 0.0738 | 0.25 | 13.61 | 0
April | 1 | 12PM to 1PM | 71.1 | 57.7 | 48 | 49.8 | 24.82 | 0.0744 | 0.34 | 13.53 | 0
April | 1 | 1PM to 2PM | 75.9 | 57.8 | 44.1 | 42.8 | 24.91 | 0.0738 | 0.29 | 13.63 | 0
April | 1 | 2PM to 3PM | 80.1 | 56.6 | 36 | 31.1 | 24.09 | 0.0733 | 0.21 | 13.7 | 0
April | 1 | 3PM to 4PM | 81 | 57.9 | 39 | 35.1 | 24.94 | 0.0732 | 0.24 | 13.74 | 0
April | 1 | 4PM to 5PM | 79 | 57.2 | 39 | 35.1 | 24.46 | 0.0734 | 0.24 | 13.69 | 0
April | 1 | 5PM to 6PM | 71.1 | 53.3 | 37 | 32.5 | 22.12 | 0.0745 | 0.22 | 13.48 | 0
April | 1 | 6PM to 7PM | 69.1 | 52.5 | 37 | 32.5 | 21.65 | 0.0748 | 0.22 | 13.43 | 0
April | 1 | 7PM to 8PM | 66 | 51.9 | 39 | 35.1 | 21.32 | 0.0752 | 0.24 | 13.36 | 0
April | 1 | 8PM to 9PM | 64 | 51.8 | 41 | 38 | 21.28 | 0.0755 | 0.26 | 13.32 | 0
April | 1 | 9PM to 10PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
April | 1 | 10PM to 11PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 1 | 11PM to 12AM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
April | 2 | 12AM to 1AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 2 | 1AM to 2AM | 56.8 | 50.9 | 46 | 46.1 | 20.8 | 0.0765 | 0.31 | 13.16 | 0
April | 2 | 2AM to 3AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 2 | 3AM to 4AM | 59 | 50.5 | 43 | 41 | 20.53 | 0.0762 | 0.28 | 13.2 | 0
April | 2 | 4AM to 5AM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
April | 2 | 5AM to 6AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 2 | 6AM to 7AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 2 | 7AM to 8AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
April | 2 | 8AM to 9AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
April | 2 | 9AM to 10AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
April | 2 | 10AM to 11AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
April | 2 | 11AM to 12PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
April | 2 | 12PM to 1PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
April | 2 | 1PM to 2PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
April | 2 | 2PM to 3PM | 82.9 | 62.8 | 50 | 53.6 | 28.32 | 0.0728 | 0.36 | 13.85 | 0
April | 2 | 3PM to 4PM | 82.9 | 60 | 43 | 41 | 26.34 | 0.0729 | 0.28 | 13.81 | 0
April | 2 | 4PM to 5PM | 82 | 59 | 41 | 38 | 25.64 | 0.073 | 0.26 | 13.77 | 0
April | 2 | 5PM to 6PM | 73.9 | 55.9 | 41 | 38 | 23.68 | 0.0741 | 0.26 | 13.57 | 0
April | 2 | 6PM to 7PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
April | 2 | 7PM to 8PM | 66.9 | 53.8 | 43 | 41 | 22.45 | 0.0751 | 0.28 | 13.4 | 0
April | 2 | 8PM to 9PM | 69.1 | 53.2 | 39 | 35.1 | 22.06 | 0.0748 | 0.24 | 13.44 | 0
April | 2 | 9PM to 10PM | 68 | 52.7 | 39 | 35.1 | 21.8 | 0.075 | 0.24 | 13.41 | 0
April | 2 | 10PM to 11PM | 64 | 52.3 | 42.1 | 39.6 | 21.53 | 0.0755 | 0.27 | 13.32 | 0
April | 2 | 11PM to 12AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
April | 3 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
April | 3 | 1AM to 2AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
April | 3 | 2AM to 3AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 3 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 3 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 3 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 3 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 3 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 3 | 8AM to 9AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
April | 3 | 9AM to 10AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
April | 3 | 10AM to 11AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
April | 3 | 11AM to 12PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
April | 3 | 12PM to 1PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
April | 3 | 1PM to 2PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
April | 3 | 2PM to 3PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
April | 3 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
April | 3 | 4PM to 5PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
April | 3 | 5PM to 6PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
April | 3 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 3 | 7PM to 8PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 3 | 8PM to 9PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 3 | 9PM to 10PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 3 | 10PM to 11PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 3 | 11PM to 12AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 4 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 4 | 1AM to 2AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
April | 4 | 2AM to 3AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
April | 4 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 4 | 4AM to 5AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 4 | 5AM to 6AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 4 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 4 | 7AM to 8AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 4 | 8AM to 9AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 4 | 9AM to 10AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 4 | 10AM to 11AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 4 | 11AM to 12PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
April | 4 | 12PM to 1PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
April | 4 | 1PM to 2PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
April | 4 | 2PM to 3PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 4 | 3PM to 4PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
April | 4 | 4PM to 5PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 4 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 4 | 6PM to 7PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 4 | 7PM to 8PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 4 | 8PM to 9PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 4 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 4 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 4 | 11PM to 12AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 1AM to 2AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 2AM to 3AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 5 | 3AM to 4AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 5 | 4AM to 5AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 5AM to 6AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 5 | 6AM to 7AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 5 | 7AM to 8AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 5 | 8AM to 9AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
April | 5 | 9AM to 10AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 5 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 5 | 11AM to 12PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 5 | 12PM to 1PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
April | 5 | 1PM to 2PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
April | 5 | 2PM to 3PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
April | 5 | 3PM to 4PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
April | 5 | 4PM to 5PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 5 | 5PM to 6PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 5 | 6PM to 7PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 5 | 7PM to 8PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
April | 5 | 8PM to 9PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 5 | 9PM to 10PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 5 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 5 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 6 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
April | 6 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
April | 6 | 2AM to 3AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 6 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 6 | 4AM to 5AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 6 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 6 | 6AM to 7AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
April | 6 | 7AM to 8AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
April | 6 | 8AM to 9AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 6 | 9AM to 10AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 6 | 10AM to 11AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 6 | 11AM to 12PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
April | 6 | 12PM to 1PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 6 | 1PM to 2PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
April | 6 | 2PM to 3PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
April | 6 | 3PM to 4PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 6 | 4PM to 5PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 6 | 5PM to 6PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
April | 6 | 6PM to 7PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 6 | 7PM to 8PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
April | 6 | 8PM to 9PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 6 | 9PM to 10PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 6 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 6 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 7 | 12AM to 1AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
April | 7 | 1AM to 2AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
April | 7 | 2AM to 3AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
April | 7 | 3AM to 4AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
April | 7 | 4AM to 5AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
April | 7 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 7 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 7 | 7AM to 8AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 7 | 8AM to 9AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 7 | 9AM to 10AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 7 | 10AM to 11AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 7 | 11AM to 12PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
April | 7 | 12PM to 1PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
April | 7 | 1PM to 2PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
April | 7 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
April | 7 | 3PM to 4PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
April | 7 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 7 | 5PM to 6PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 7 | 6PM to 7PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 7 | 7PM to 8PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 7 | 8PM to 9PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 7 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
April | 7 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 7 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 8 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 8 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 8 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
April | 8 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
April | 8 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
April | 8 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 8 | 6AM to 7AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 8 | 7AM to 8AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
April | 8 | 8AM to 9AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 8 | 9AM to 10AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
April | 8 | 10AM to 11AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 8 | 11AM to 12PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 8 | 12PM to 1PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 8 | 1PM to 2PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 8 | 2PM to 3PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 8 | 3PM to 4PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
April | 8 | 4PM to 5PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 8 | 5PM to 6PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 8 | 6PM to 7PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 8 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 8 | 8PM to 9PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 8 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 8 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 8 | 11PM to 12AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 9 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 9 | 1AM to 2AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 9 | 2AM to 3AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 9 | 3AM to 4AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 9 | 4AM to 5AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
April | 9 | 5AM to 6AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 9 | 6AM to 7AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 9 | 7AM to 8AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 9 | 8AM to 9AM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
April | 9 | 9AM to 10AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 9 | 10AM to 11AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 9 | 11AM to 12PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 9 | 12PM to 1PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 9 | 1PM to 2PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 9 | 2PM to 3PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 9 | 3PM to 4PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 9 | 4PM to 5PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 9 | 5PM to 6PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 9 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 9 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 9 | 8PM to 9PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 9 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
April | 9 | 10PM to 11PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
April | 9 | 11PM to 12AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
April | 10 | 12AM to 1AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
April | 10 | 1AM to 2AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 10 | 2AM to 3AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
April | 10 | 3AM to 4AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
April | 10 | 4AM to 5AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 10 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 10 | 6AM to 7AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 10 | 7AM to 8AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 10 | 8AM to 9AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 10 | 9AM to 10AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 10 | 10AM to 11AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
April | 10 | 11AM to 12PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 10 | 12PM to 1PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
April | 10 | 1PM to 2PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 10 | 2PM to 3PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 10 | 3PM to 4PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 10 | 4PM to 5PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 10 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 10 | 6PM to 7PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
April | 10 | 7PM to 8PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 10 | 8PM to 9PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 10 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 10 | 10PM to 11PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
April | 10 | 11PM to 12AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
April | 11 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
April | 11 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
April | 11 | 2AM to 3AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
April | 11 | 3AM to 4AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
April | 11 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
April | 11 | 5AM to 6AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
April | 11 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 11 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 11 | 8AM to 9AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
April | 11 | 9AM to 10AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
April | 11 | 10AM to 11AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
April | 11 | 11AM to 12PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
April | 11 | 12PM to 1PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
April | 11 | 1PM to 2PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
April | 11 | 2PM to 3PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
April | 11 | 3PM to 4PM | 70 | 56.8 | 46.9 | 47.8 | 24.25 | 0.0746 | 0.32 | 13.5 | 0
April | 11 | 4PM to 5PM | 68 | 55.1 | 45 | 44.3 | 23.22 | 0.0749 | 0.3 | 13.44 | 0
April | 11 | 5PM to 6PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
April | 11 | 6PM to 7PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 11 | 7PM to 8PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
April | 11 | 8PM to 9PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 11 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 11 | 10PM to 11PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 11 | 11PM to 12AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 12 | 12AM to 1AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 12 | 1AM to 2AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 12 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 12 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 12 | 4AM to 5AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 12 | 5AM to 6AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 12 | 6AM to 7AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 12 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
April | 12 | 8AM to 9AM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
April | 12 | 9AM to 10AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
April | 12 | 10AM to 11AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
April | 12 | 11AM to 12PM | 71.1 | 55.5 | 43 | 41 | 23.46 | 0.0745 | 0.28 | 13.5 | 0
April | 12 | 12PM to 1PM | 70 | 50.9 | 30.9 | 25.2 | 20.73 | 0.0747 | 0.17 | 13.43 | 0
April | 12 | 1PM to 2PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
April | 12 | 2PM to 3PM | 66.9 | 53.8 | 42.8 | 40.7 | 22.41 | 0.0751 | 0.28 | 13.4 | 0
April | 12 | 3PM to 4PM | 66.9 | 53.8 | 43 | 41 | 22.45 | 0.0751 | 0.28 | 13.4 | 0
April | 12 | 4PM to 5PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
April | 12 | 5PM to 6PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
April | 12 | 6PM to 7PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
April | 12 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
April | 12 | 8PM to 9PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
April | 12 | 9PM to 10PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
April | 12 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
April | 12 | 11PM to 12AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
April | 13 | 12AM to 1AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
April | 13 | 1AM to 2AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
April | 13 | 2AM to 3AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
April | 13 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
April | 13 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
April | 13 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
April | 13 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
April | 13 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
April | 13 | 8AM to 9AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
April | 13 | 9AM to 10AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
April | 13 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
April | 13 | 11AM to 12PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
April | 13 | 12PM to 1PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
April | 13 | 1PM to 2PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
April | 13 | 2PM to 3PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
April | 13 | 3PM to 4PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
April | 13 | 4PM to 5PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
April | 13 | 5PM to 6PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
April | 13 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 13 | 7PM to 8PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 13 | 8PM to 9PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 13 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 13 | 10PM to 11PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 13 | 11PM to 12AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 12AM to 1AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 1AM to 2AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 14 | 2AM to 3AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 3AM to 4AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 4AM to 5AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 14 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 14 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 14 | 7AM to 8AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
April | 14 | 8AM to 9AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 14 | 9AM to 10AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 14 | 10AM to 11AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 14 | 11AM to 12PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 14 | 12PM to 1PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
April | 14 | 1PM to 2PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
April | 14 | 2PM to 3PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
April | 14 | 3PM to 4PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
April | 14 | 4PM to 5PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
April | 14 | 5PM to 6PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
April | 14 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
April | 14 | 7PM to 8PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 14 | 8PM to 9PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 14 | 9PM to 10PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 14 | 10PM to 11PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 14 | 11PM to 12AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 15 | 12AM to 1AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 15 | 1AM to 2AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 15 | 2AM to 3AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 15 | 3AM to 4AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 15 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 15 | 5AM to 6AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 15 | 6AM to 7AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 15 | 7AM to 8AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 15 | 8AM to 9AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 15 | 9AM to 10AM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 15 | 10AM to 11AM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 15 | 11AM to 12PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
April | 15 | 12PM to 1PM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
April | 15 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
April | 15 | 2PM to 3PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 15 | 3PM to 4PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
April | 15 | 4PM to 5PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
April | 15 | 5PM to 6PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 15 | 6PM to 7PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 15 | 7PM to 8PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 15 | 8PM to 9PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 15 | 9PM to 10PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 15 | 10PM to 11PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 15 | 11PM to 12AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 16 | 12AM to 1AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 16 | 1AM to 2AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 16 | 2AM to 3AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 16 | 3AM to 4AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 16 | 4AM to 5AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 16 | 5AM to 6AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 16 | 6AM to 7AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 16 | 7AM to 8AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 16 | 8AM to 9AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
April | 16 | 9AM to 10AM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
April | 16 | 10AM to 11AM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
April | 16 | 11AM to 12PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
April | 16 | 12PM to 1PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
April | 16 | 1PM to 2PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
April | 16 | 2PM to 3PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
April | 16 | 3PM to 4PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
April | 16 | 4PM to 5PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
April | 16 | 5PM to 6PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
April | 16 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
April | 16 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
April | 16 | 8PM to 9PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
April | 16 | 9PM to 10PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
April | 16 | 10PM to 11PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
April | 16 | 11PM to 12AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
April | 17 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
April | 17 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 17 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 17 | 3AM to 4AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
April | 17 | 4AM to 5AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 17 | 5AM to 6AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 17 | 6AM to 7AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 17 | 7AM to 8AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 17 | 8AM to 9AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 17 | 9AM to 10AM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
April | 17 | 10AM to 11AM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
April | 17 | 11AM to 12PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
April | 17 | 12PM to 1PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
April | 17 | 1PM to 2PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
April | 17 | 2PM to 3PM | 63 | 52.2 | 43 | 41 | 21.49 | 0.0756 | 0.28 | 13.3 | 0
April | 17 | 3PM to 4PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
April | 17 | 4PM to 5PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
April | 17 | 5PM to 6PM | 57.9 | 49.6 | 42.1 | 39.6 | 20.05 | 0.0764 | 0.27 | 13.17 | 0
April | 17 | 6PM to 7PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
April | 17 | 7PM to 8PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 17 | 8PM to 9PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
April | 17 | 9PM to 10PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 17 | 10PM to 11PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
April | 17 | 11PM to 12AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 18 | 12AM to 1AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
April | 18 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 18 | 2AM to 3AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 18 | 3AM to 4AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 18 | 4AM to 5AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
April | 18 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 18 | 6AM to 7AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 18 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 18 | 8AM to 9AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 18 | 9AM to 10AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 18 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 18 | 11AM to 12PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
April | 18 | 12PM to 1PM | 63 | 52.2 | 43 | 41 | 21.49 | 0.0756 | 0.28 | 13.3 | 0
April | 18 | 1PM to 2PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
April | 18 | 2PM to 3PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
April | 18 | 3PM to 4PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
April | 18 | 4PM to 5PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
April | 18 | 5PM to 6PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 18 | 6PM to 7PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 18 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 18 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 18 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 18 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 18 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 19 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 19 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
April | 19 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
April | 19 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
April | 19 | 4AM to 5AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
April | 19 | 5AM to 6AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
April | 19 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 19 | 7AM to 8AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 19 | 8AM to 9AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
April | 19 | 9AM to 10AM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 19 | 10AM to 11AM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
April | 19 | 11AM to 12PM | 63 | 52.6 | 44.1 | 42.8 | 21.76 | 0.0756 | 0.29 | 13.3 | 0
April | 19 | 12PM to 1PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
April | 19 | 1PM to 2PM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
April | 19 | 2PM to 3PM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
April | 19 | 3PM to 4PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
April | 19 | 4PM to 5PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
April | 19 | 5PM to 6PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
April | 19 | 6PM to 7PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
April | 19 | 7PM to 8PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 19 | 8PM to 9PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 19 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 19 | 10PM to 11PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 19 | 11PM to 12AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
April | 20 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 20 | 1AM to 2AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 20 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 20 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 20 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 20 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 20 | 6AM to 7AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
April | 20 | 7AM to 8AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
April | 20 | 8AM to 9AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 20 | 9AM to 10AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
April | 20 | 10AM to 11AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
April | 20 | 11AM to 12PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
April | 20 | 12PM to 1PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
April | 20 | 1PM to 2PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
April | 20 | 2PM to 3PM | 64 | 53.1 | 44.1 | 42.8 | 22.02 | 0.0755 | 0.29 | 13.33 | 0
April | 20 | 3PM to 4PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
April | 20 | 4PM to 5PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
April | 20 | 5PM to 6PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 20 | 6PM to 7PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 20 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 20 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
April | 20 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 20 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 20 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 21 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 21 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
April | 21 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 21 | 7AM to 8AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 21 | 8AM to 9AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
April | 21 | 9AM to 10AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 21 | 10AM to 11AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 21 | 11AM to 12PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
April | 21 | 12PM to 1PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 21 | 1PM to 2PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 21 | 2PM to 3PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 21 | 3PM to 4PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 21 | 4PM to 5PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 21 | 5PM to 6PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 21 | 6PM to 7PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
April | 21 | 7PM to 8PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 21 | 8PM to 9PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 21 | 9PM to 10PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 21 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 21 | 11PM to 12AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 22 | 12AM to 1AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 22 | 1AM to 2AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 22 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
April | 22 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
April | 22 | 4AM to 5AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
April | 22 | 5AM to 6AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
April | 22 | 6AM to 7AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
April | 22 | 7AM to 8AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
April | 22 | 8AM to 9AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
April | 22 | 9AM to 10AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
April | 22 | 10AM to 11AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
April | 22 | 11AM to 12PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
April | 22 | 12PM to 1PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
April | 22 | 1PM to 2PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
April | 22 | 2PM to 3PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
April | 22 | 3PM to 4PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
April | 22 | 4PM to 5PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
April | 22 | 5PM to 6PM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
April | 22 | 6PM to 7PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
April | 22 | 7PM to 8PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
April | 22 | 8PM to 9PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
April | 22 | 9PM to 10PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 22 | 10PM to 11PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 22 | 11PM to 12AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 23 | 12AM to 1AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
April | 23 | 1AM to 2AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
April | 23 | 2AM to 3AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
April | 23 | 3AM to 4AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
April | 23 | 4AM to 5AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
April | 23 | 5AM to 6AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
April | 23 | 6AM to 7AM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
April | 23 | 7AM to 8AM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
April | 23 | 8AM to 9AM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
April | 23 | 9AM to 10AM | 57.9 | 49.1 | 41 | 38 | 19.8 | 0.0764 | 0.26 | 13.16 | 0
April | 23 | 10AM to 11AM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
April | 23 | 11AM to 12PM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
April | 23 | 12PM to 1PM | 61 | 51 | 42.1 | 39.6 | 20.79 | 0.0759 | 0.27 | 13.24 | 0
April | 23 | 1PM to 2PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
April | 23 | 2PM to 3PM | 61 | 51.8 | 44.1 | 42.8 | 21.28 | 0.0759 | 0.29 | 13.25 | 0
April | 23 | 3PM to 4PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
April | 23 | 4PM to 5PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 23 | 5PM to 6PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
April | 23 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 23 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 23 | 8PM to 9PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 23 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 23 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 23 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
April | 24 | 12AM to 1AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 24 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 24 | 2AM to 3AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
April | 24 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
April | 24 | 4AM to 5AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
April | 24 | 5AM to 6AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
April | 24 | 6AM to 7AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 24 | 7AM to 8AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 24 | 8AM to 9AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
April | 24 | 9AM to 10AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 24 | 10AM to 11AM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
April | 24 | 11AM to 12PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
April | 24 | 12PM to 1PM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
April | 24 | 1PM to 2PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
April | 24 | 2PM to 3PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 24 | 3PM to 4PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
April | 24 | 4PM to 5PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
April | 24 | 5PM to 6PM | 57 | 49.6 | 43 | 41 | 20.05 | 0.0765 | 0.28 | 13.15 | 0
April | 24 | 6PM to 7PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
April | 24 | 7PM to 8PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
April | 24 | 8PM to 9PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 24 | 9PM to 10PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 24 | 10PM to 11PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
April | 24 | 11PM to 12AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
April | 25 | 12AM to 1AM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
April | 25 | 1AM to 2AM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
April | 25 | 2AM to 3AM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
April | 25 | 3AM to 4AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
April | 25 | 4AM to 5AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 25 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 25 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
April | 25 | 7AM to 8AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
April | 25 | 8AM to 9AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
April | 25 | 9AM to 10AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
April | 25 | 10AM to 11AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
April | 25 | 11AM to 12PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
April | 25 | 12PM to 1PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
April | 25 | 1PM to 2PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
April | 25 | 2PM to 3PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
April | 25 | 3PM to 4PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
April | 25 | 4PM to 5PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
April | 25 | 5PM to 6PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
April | 25 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
April | 25 | 7PM to 8PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
April | 25 | 8PM to 9PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
April | 25 | 9PM to 10PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
April | 25 | 10PM to 11PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 25 | 11PM to 12AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 26 | 12AM to 1AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 26 | 1AM to 2AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 26 | 2AM to 3AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 26 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 26 | 4AM to 5AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
April | 26 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 26 | 6AM to 7AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
April | 26 | 7AM to 8AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
April | 26 | 8AM to 9AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
April | 26 | 9AM to 10AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
April | 26 | 10AM to 11AM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
April | 26 | 11AM to 12PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
April | 26 | 12PM to 1PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
April | 26 | 1PM to 2PM | 75.9 | 60.9 | 51.1 | 55.9 | 26.96 | 0.0737 | 0.38 | 13.67 | 0
April | 26 | 2PM to 3PM | 68 | 55.6 | 46 | 46.1 | 23.51 | 0.0749 | 0.31 | 13.44 | 0
April | 26 | 3PM to 4PM | 68 | 54.3 | 43 | 41 | 22.71 | 0.0749 | 0.28 | 13.43 | 0
April | 26 | 4PM to 5PM | 66.9 | 53 | 41 | 38 | 21.98 | 0.0751 | 0.26 | 13.39 | 0
April | 26 | 5PM to 6PM | 64.9 | 51.4 | 39 | 35.1 | 21.06 | 0.0754 | 0.24 | 13.33 | 0
April | 26 | 6PM to 7PM | 61 | 49 | 37 | 32.5 | 19.68 | 0.076 | 0.22 | 13.22 | 0
April | 26 | 7PM to 8PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
April | 26 | 8PM to 9PM | 57.9 | 47.9 | 37.9 | 33.7 | 19.13 | 0.0764 | 0.23 | 13.15 | 0
April | 26 | 9PM to 10PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
April | 26 | 10PM to 11PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
April | 26 | 11PM to 12AM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
April | 27 | 12AM to 1AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 27 | 1AM to 2AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
April | 27 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
April | 27 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 27 | 4AM to 5AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
April | 27 | 5AM to 6AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
April | 27 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
April | 27 | 7AM to 8AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
April | 27 | 8AM to 9AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
April | 27 | 9AM to 10AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
April | 27 | 10AM to 11AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
April | 27 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
April | 27 | 12PM to 1PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
April | 27 | 1PM to 2PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
April | 27 | 2PM to 3PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
April | 27 | 3PM to 4PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 27 | 4PM to 5PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
April | 27 | 5PM to 6PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
April | 27 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 27 | 7PM to 8PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
April | 27 | 8PM to 9PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
April | 27 | 9PM to 10PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
April | 27 | 10PM to 11PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
April | 27 | 11PM to 12AM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
April | 28 | 12AM to 1AM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
April | 28 | 1AM to 2AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
April | 28 | 2AM to 3AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
April | 28 | 3AM to 4AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
April | 28 | 4AM to 5AM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
April | 28 | 5AM to 6AM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
April | 28 | 6AM to 7AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
April | 28 | 7AM to 8AM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
April | 28 | 8AM to 9AM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
April | 28 | 9AM to 10AM | 57 | 47.5 | 37.9 | 33.7 | 18.91 | 0.0766 | 0.23 | 13.12 | 0
April | 28 | 10AM to 11AM | 57.9 | 48.3 | 39 | 35.1 | 19.35 | 0.0764 | 0.24 | 13.15 | 0
April | 28 | 11AM to 12PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
April | 28 | 12PM to 1PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
April | 28 | 1PM to 2PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
April | 28 | 2PM to 3PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
April | 28 | 3PM to 4PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
April | 28 | 4PM to 5PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
April | 28 | 5PM to 6PM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
April | 28 | 6PM to 7PM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
April | 28 | 7PM to 8PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 28 | 8PM to 9PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
April | 28 | 9PM to 10PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
April | 28 | 10PM to 11PM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
April | 28 | 11PM to 12AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
April | 29 | 12AM to 1AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
April | 29 | 1AM to 2AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
April | 29 | 2AM to 3AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
April | 29 | 3AM to 4AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
April | 29 | 4AM to 5AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
April | 29 | 5AM to 6AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
April | 29 | 6AM to 7AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
April | 29 | 7AM to 8AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
April | 29 | 8AM to 9AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
April | 29 | 9AM to 10AM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
April | 29 | 10AM to 11AM | 62.1 | 50.5 | 39.9 | 36.4 | 20.55 | 0.0758 | 0.25 | 13.26 | 0
April | 29 | 11AM to 12PM | 64 | 52.3 | 42.1 | 39.6 | 21.53 | 0.0755 | 0.27 | 13.32 | 0
April | 29 | 12PM to 1PM | 66.9 | 53.5 | 42.1 | 39.6 | 22.23 | 0.0751 | 0.27 | 13.39 | 0
April | 29 | 1PM to 2PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
April | 29 | 2PM to 3PM | 63 | 52.2 | 43 | 41 | 21.49 | 0.0756 | 0.28 | 13.3 | 0
April | 29 | 3PM to 4PM | 61 | 51 | 42.1 | 39.6 | 20.79 | 0.0759 | 0.27 | 13.24 | 0
April | 29 | 4PM to 5PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
April | 29 | 5PM to 6PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 29 | 6PM to 7PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
April | 29 | 7PM to 8PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 29 | 8PM to 9PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
April | 29 | 9PM to 10PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
April | 29 | 10PM to 11PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 29 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
April | 30 | 12AM to 1AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
April | 30 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 30 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
April | 30 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 30 | 4AM to 5AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
April | 30 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
April | 30 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
April | 30 | 7AM to 8AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
April | 30 | 8AM to 9AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
April | 30 | 9AM to 10AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
April | 30 | 10AM to 11AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
April | 30 | 11AM to 12PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
April | 30 | 12PM to 1PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
April | 30 | 1PM to 2PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
April | 30 | 2PM to 3PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
April | 30 | 3PM to 4PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
April | 30 | 4PM to 5PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
April | 30 | 5PM to 6PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
April | 30 | 6PM to 7PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
April | 30 | 7PM to 8PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
April | 30 | 8PM to 9PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
April | 30 | 9PM to 10PM | 54.1 | 49.8 | 46 | 46.1 | 20.15 | 0.0769 | 0.31 | 13.09 | 0
April | 30 | 10PM to 11PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
April | 30 | 11PM to 12AM | 56.1 | 51.6 | 48 | 49.8 | 21.19 | 0.0766 | 0.34 | 13.15 | 0
May | 1 | 12AM to 1AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
May | 1 | 1AM to 2AM | 58.1 | 53.5 | 50 | 53.6 | 22.27 | 0.0763 | 0.36 | 13.21 | 0
May | 1 | 2AM to 3AM | 59 | 54.3 | 50.9 | 55.5 | 22.78 | 0.0761 | 0.37 | 13.24 | 0
May | 1 | 3AM to 4AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
May | 1 | 4AM to 5AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
May | 1 | 5AM to 6AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
May | 1 | 6AM to 7AM | 68 | 55.6 | 46 | 46.1 | 23.51 | 0.0749 | 0.31 | 13.44 | 0
May | 1 | 7AM to 8AM | 73 | 57.5 | 46 | 46.1 | 24.74 | 0.0742 | 0.31 | 13.57 | 0
May | 1 | 8AM to 9AM | 75 | 58.3 | 46 | 46.1 | 25.22 | 0.0739 | 0.31 | 13.62 | 0
May | 1 | 9AM to 10AM | 77 | 58.2 | 44.1 | 42.8 | 25.17 | 0.0737 | 0.29 | 13.66 | 0
May | 1 | 10AM to 11AM | 80.1 | 59.7 | 45 | 44.3 | 26.15 | 0.0732 | 0.3 | 13.74 | 0
May | 1 | 11AM to 12PM | 84.9 | 60.8 | 43 | 41 | 26.82 | 0.0726 | 0.28 | 13.86 | 0
May | 1 | 12PM to 1PM | 81 | 59.3 | 43 | 41 | 25.86 | 0.0731 | 0.28 | 13.76 | 0
May | 1 | 1PM to 2PM | 77 | 59 | 46 | 46.1 | 25.7 | 0.0736 | 0.31 | 13.67 | 0
May | 1 | 2PM to 3PM | 73.9 | 58.3 | 46.9 | 47.8 | 25.21 | 0.074 | 0.32 | 13.6 | 0
May | 1 | 3PM to 4PM | 73 | 57.9 | 46.9 | 47.8 | 24.99 | 0.0742 | 0.32 | 13.57 | 0
May | 1 | 4PM to 5PM | 71.1 | 57.2 | 46.9 | 47.8 | 24.51 | 0.0744 | 0.32 | 13.52 | 0
May | 1 | 5PM to 6PM | 70 | 56.8 | 46.9 | 47.8 | 24.25 | 0.0746 | 0.32 | 13.5 | 0
May | 1 | 6PM to 7PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
May | 1 | 7PM to 8PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
May | 1 | 8PM to 9PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
May | 1 | 9PM to 10PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
May | 1 | 10PM to 11PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
May | 1 | 11PM to 12AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 2 | 12AM to 1AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 2 | 1AM to 2AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 2 | 2AM to 3AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 2 | 3AM to 4AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 2 | 4AM to 5AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
May | 2 | 5AM to 6AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
May | 2 | 6AM to 7AM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
May | 2 | 7AM to 8AM | 68 | 56.5 | 48 | 49.8 | 24.08 | 0.0749 | 0.34 | 13.45 | 0
May | 2 | 8AM to 9AM | 70 | 58.2 | 50 | 53.6 | 25.16 | 0.0746 | 0.36 | 13.51 | 0
May | 2 | 9AM to 10AM | 73.9 | 57.4 | 45 | 44.3 | 24.66 | 0.0741 | 0.3 | 13.59 | 0
May | 2 | 10AM to 11AM | 78.1 | 59.4 | 46 | 46.1 | 25.96 | 0.0735 | 0.31 | 13.7 | 0
May | 2 | 11AM to 12PM | 73.9 | 57.4 | 45 | 44.3 | 24.66 | 0.0741 | 0.3 | 13.59 | 0
May | 2 | 12PM to 1PM | 72 | 55.1 | 41 | 38 | 23.2 | 0.0744 | 0.26 | 13.52 | 0
May | 2 | 1PM to 2PM | 72 | 55.1 | 41 | 38 | 23.2 | 0.0744 | 0.26 | 13.52 | 0
May | 2 | 2PM to 3PM | 73 | 54.8 | 39 | 35.1 | 23.02 | 0.0742 | 0.24 | 13.54 | 0
May | 2 | 3PM to 4PM | 69.1 | 51.8 | 35.1 | 30 | 21.26 | 0.0748 | 0.2 | 13.42 | 0
May | 2 | 4PM to 5PM | 68 | 50.4 | 32 | 26.5 | 20.46 | 0.075 | 0.18 | 13.38 | 0
May | 2 | 5PM to 6PM | 66.9 | 50.6 | 34 | 28.7 | 20.54 | 0.0752 | 0.2 | 13.36 | 0
May | 2 | 6PM to 7PM | 63 | 49.9 | 37 | 32.5 | 20.16 | 0.0757 | 0.22 | 13.27 | 0
May | 2 | 7PM to 8PM | 61 | 49.7 | 39 | 35.1 | 20.1 | 0.076 | 0.24 | 13.23 | 0
May | 2 | 8PM to 9PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
May | 2 | 9PM to 10PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
May | 2 | 10PM to 11PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 2 | 11PM to 12AM | 55 | 49.2 | 44.1 | 42.8 | 19.84 | 0.0768 | 0.29 | 13.1 | 0
May | 3 | 12AM to 1AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 3 | 1AM to 2AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 3 | 2AM to 3AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 3 | 3AM to 4AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
May | 3 | 4AM to 5AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
May | 3 | 5AM to 6AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
May | 3 | 6AM to 7AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 3 | 7AM to 8AM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
May | 3 | 8AM to 9AM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
May | 3 | 9AM to 10AM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
May | 3 | 10AM to 11AM | 62.1 | 51.4 | 42.1 | 39.6 | 21.05 | 0.0758 | 0.27 | 13.27 | 0
May | 3 | 11AM to 12PM | 62.1 | 51.4 | 42.1 | 39.6 | 21.05 | 0.0758 | 0.27 | 13.27 | 0
May | 3 | 12PM to 1PM | 62.1 | 50.2 | 39 | 35.1 | 20.36 | 0.0758 | 0.24 | 13.26 | 0
May | 3 | 1PM to 2PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
May | 3 | 2PM to 3PM | 60.1 | 49.7 | 39.9 | 36.4 | 20.07 | 0.0761 | 0.25 | 13.21 | 0
May | 3 | 3PM to 4PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
May | 3 | 4PM to 5PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
May | 3 | 5PM to 6PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
May | 3 | 6PM to 7PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
May | 3 | 7PM to 8PM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
May | 3 | 8PM to 9PM | 52 | 46.4 | 41 | 38 | 18.36 | 0.0773 | 0.26 | 13.01 | 0
May | 3 | 9PM to 10PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
May | 3 | 10PM to 11PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
May | 3 | 11PM to 12AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
May | 4 | 12AM to 1AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
May | 4 | 1AM to 2AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
May | 4 | 2AM to 3AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
May | 4 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
May | 4 | 4AM to 5AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
May | 4 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 4 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 4 | 7AM to 8AM | 57 | 49.6 | 43 | 41 | 20.05 | 0.0765 | 0.28 | 13.15 | 0
May | 4 | 8AM to 9AM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
May | 4 | 9AM to 10AM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
May | 4 | 10AM to 11AM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
May | 4 | 11AM to 12PM | 64.9 | 52.6 | 42.1 | 39.6 | 21.75 | 0.0754 | 0.27 | 13.34 | 0
May | 4 | 12PM to 1PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
May | 4 | 1PM to 2PM | 66.9 | 53.5 | 42.1 | 39.6 | 22.23 | 0.0751 | 0.27 | 13.39 | 0
May | 4 | 2PM to 3PM | 66 | 53.1 | 42.1 | 39.6 | 22.01 | 0.0752 | 0.27 | 13.37 | 0
May | 4 | 3PM to 4PM | 63 | 50.6 | 39 | 35.1 | 20.58 | 0.0757 | 0.24 | 13.28 | 0
May | 4 | 4PM to 5PM | 62.1 | 49.5 | 37 | 32.5 | 19.95 | 0.0758 | 0.22 | 13.25 | 0
May | 4 | 5PM to 6PM | 61 | 48.6 | 36 | 31.1 | 19.47 | 0.076 | 0.21 | 13.22 | 0
May | 4 | 6PM to 7PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
May | 4 | 7PM to 8PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
May | 4 | 8PM to 9PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 4 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 4 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 4 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 5 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 5 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 5 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 5 | 3AM to 4AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
May | 5 | 4AM to 5AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
May | 5 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 5 | 6AM to 7AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
May | 5 | 7AM to 8AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 5 | 8AM to 9AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 5 | 9AM to 10AM | 64 | 49.9 | 36 | 31.1 | 20.21 | 0.0756 | 0.21 | 13.3 | 0
May | 5 | 10AM to 11AM | 64 | 50.3 | 37 | 32.5 | 20.43 | 0.0755 | 0.22 | 13.3 | 0
May | 5 | 11AM to 12PM | 66 | 50.8 | 36 | 31.1 | 20.69 | 0.0753 | 0.21 | 13.35 | 0
May | 5 | 12PM to 1PM | 66 | 50.5 | 35.1 | 30 | 20.52 | 0.0753 | 0.2 | 13.34 | 0
May | 5 | 1PM to 2PM | 66 | 50.2 | 34 | 28.7 | 20.32 | 0.0753 | 0.2 | 13.34 | 0
May | 5 | 2PM to 3PM | 63 | 50.6 | 39 | 35.1 | 20.58 | 0.0757 | 0.24 | 13.28 | 0
May | 5 | 3PM to 4PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
May | 5 | 4PM to 5PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
May | 5 | 5PM to 6PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 5 | 6PM to 7PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
May | 5 | 7PM to 8PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 5 | 8PM to 9PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 5 | 9PM to 10PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 5 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 5 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 6 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 6 | 1AM to 2AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 6 | 6AM to 7AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 6 | 7AM to 8AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 6 | 8AM to 9AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 6 | 9AM to 10AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
May | 6 | 10AM to 11AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 6 | 11AM to 12PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 6 | 12PM to 1PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 6 | 1PM to 2PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 6 | 2PM to 3PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 6 | 3PM to 4PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 6 | 4PM to 5PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 6 | 5PM to 6PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 6 | 6PM to 7PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 6 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 6 | 8PM to 9PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 6 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 6 | 10PM to 11PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 6 | 11PM to 12AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 7 | 12AM to 1AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 7 | 1AM to 2AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 7 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 7 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 7 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 7 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 7 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 7 | 7AM to 8AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 7 | 8AM to 9AM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
May | 7 | 9AM to 10AM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
May | 7 | 10AM to 11AM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
May | 7 | 11AM to 12PM | 62.1 | 51.8 | 43 | 41 | 21.27 | 0.0758 | 0.28 | 13.27 | 0
May | 7 | 12PM to 1PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
May | 7 | 1PM to 2PM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
May | 7 | 2PM to 3PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
May | 7 | 3PM to 4PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
May | 7 | 4PM to 5PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
May | 7 | 5PM to 6PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 7 | 6PM to 7PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
May | 7 | 7PM to 8PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 7 | 8PM to 9PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 7 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 7 | 10PM to 11PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 7 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 8 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 8 | 6AM to 7AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 8 | 7AM to 8AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 8 | 8AM to 9AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
May | 8 | 9AM to 10AM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 8 | 10AM to 11AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 8 | 11AM to 12PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
May | 8 | 12PM to 1PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
May | 8 | 1PM to 2PM | 62.1 | 52.7 | 45 | 44.3 | 21.78 | 0.0758 | 0.3 | 13.28 | 0
May | 8 | 2PM to 3PM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
May | 8 | 3PM to 4PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
May | 8 | 4PM to 5PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 8 | 5PM to 6PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
May | 8 | 6PM to 7PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
May | 8 | 7PM to 8PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
May | 8 | 8PM to 9PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
May | 8 | 9PM to 10PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
May | 8 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
May | 8 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 9 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 9 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 9 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 9 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
May | 9 | 4AM to 5AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 9 | 5AM to 6AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
May | 9 | 6AM to 7AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 9 | 7AM to 8AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 9 | 8AM to 9AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
May | 9 | 9AM to 10AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 9 | 10AM to 11AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 9 | 11AM to 12PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
May | 9 | 12PM to 1PM | 66 | 53.9 | 44.1 | 42.8 | 22.51 | 0.0752 | 0.29 | 13.38 | 0
May | 9 | 1PM to 2PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
May | 9 | 2PM to 3PM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
May | 9 | 3PM to 4PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 9 | 4PM to 5PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 9 | 5PM to 6PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
May | 9 | 6PM to 7PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 9 | 7PM to 8PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 9 | 8PM to 9PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
May | 9 | 9PM to 10PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
May | 9 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
May | 9 | 11PM to 12AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
May | 10 | 12AM to 1AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 10 | 1AM to 2AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
May | 10 | 2AM to 3AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
May | 10 | 3AM to 4AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
May | 10 | 4AM to 5AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 10 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
May | 10 | 6AM to 7AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 10 | 7AM to 8AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 10 | 8AM to 9AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
May | 10 | 9AM to 10AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 10 | 10AM to 11AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 10 | 11AM to 12PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
May | 10 | 12PM to 1PM | 69.1 | 56.4 | 46.9 | 47.8 | 24.03 | 0.0747 | 0.32 | 13.47 | 0
May | 10 | 1PM to 2PM | 69.1 | 55.5 | 45 | 44.3 | 23.48 | 0.0747 | 0.3 | 13.46 | 0
May | 10 | 2PM to 3PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
May | 10 | 3PM to 4PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
May | 10 | 4PM to 5PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
May | 10 | 5PM to 6PM | 61 | 50.5 | 41 | 38 | 20.54 | 0.0759 | 0.26 | 13.24 | 0
May | 10 | 6PM to 7PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
May | 10 | 7PM to 8PM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
May | 10 | 8PM to 9PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 10 | 9PM to 10PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
May | 10 | 10PM to 11PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 10 | 11PM to 12AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 11 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 11 | 1AM to 2AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 11 | 2AM to 3AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 11 | 3AM to 4AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
May | 11 | 4AM to 5AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
May | 11 | 5AM to 6AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
May | 11 | 6AM to 7AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
May | 11 | 7AM to 8AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
May | 11 | 8AM to 9AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
May | 11 | 9AM to 10AM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
May | 11 | 10AM to 11AM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
May | 11 | 11AM to 12PM | 80.1 | 61 | 48 | 49.8 | 27.01 | 0.0732 | 0.34 | 13.76 | 0
May | 11 | 12PM to 1PM | 81 | 62.6 | 51.1 | 55.9 | 28.18 | 0.073 | 0.38 | 13.8 | 0
May | 11 | 1PM to 2PM | 81 | 59.7 | 44.1 | 42.8 | 26.13 | 0.0731 | 0.29 | 13.76 | 0
May | 11 | 2PM to 3PM | 82.9 | 60 | 43 | 41 | 26.34 | 0.0729 | 0.28 | 13.81 | 0
May | 11 | 3PM to 4PM | 77 | 56.7 | 39.9 | 36.4 | 24.17 | 0.0737 | 0.25 | 13.64 | 0
May | 11 | 4PM to 5PM | 75 | 55.6 | 39 | 35.1 | 23.5 | 0.074 | 0.24 | 13.59 | 0
May | 11 | 5PM to 6PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
May | 11 | 6PM to 7PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
May | 11 | 7PM to 8PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
May | 11 | 8PM to 9PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
May | 11 | 9PM to 10PM | 59 | 50.5 | 43 | 41 | 20.53 | 0.0762 | 0.28 | 13.2 | 0
May | 11 | 10PM to 11PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
May | 11 | 11PM to 12AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
May | 12 | 12AM to 1AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 12 | 1AM to 2AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 12 | 2AM to 3AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 12 | 3AM to 4AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 12 | 4AM to 5AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 12 | 5AM to 6AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 12 | 6AM to 7AM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
May | 12 | 7AM to 8AM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
May | 12 | 8AM to 9AM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
May | 12 | 9AM to 10AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
May | 12 | 10AM to 11AM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
May | 12 | 11AM to 12PM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
May | 12 | 12PM to 1PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
May | 12 | 1PM to 2PM | 72 | 59.4 | 51.1 | 55.9 | 25.99 | 0.0743 | 0.38 | 13.57 | 0
May | 12 | 2PM to 3PM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
May | 12 | 3PM to 4PM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
May | 12 | 4PM to 5PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
May | 12 | 5PM to 6PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
May | 12 | 6PM to 7PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
May | 12 | 7PM to 8PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
May | 12 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
May | 12 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
May | 12 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
May | 12 | 11PM to 12AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
May | 13 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
May | 13 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
May | 13 | 2AM to 3AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
May | 13 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 13 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 13 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
May | 13 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
May | 13 | 7AM to 8AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
May | 13 | 8AM to 9AM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
May | 13 | 9AM to 10AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
May | 13 | 10AM to 11AM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
May | 13 | 11AM to 12PM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
May | 13 | 12PM to 1PM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
May | 13 | 1PM to 2PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
May | 13 | 2PM to 3PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
May | 13 | 3PM to 4PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
May | 13 | 4PM to 5PM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.53 | 0
May | 13 | 5PM to 6PM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
May | 13 | 6PM to 7PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 13 | 7PM to 8PM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
May | 13 | 8PM to 9PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 13 | 9PM to 10PM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
May | 13 | 10PM to 11PM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
May | 13 | 11PM to 12AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
May | 14 | 12AM to 1AM | 55 | 55 | 55 | 64.7 | 23.25 | 0.0767 | 0.44 | 13.17 | 0
May | 14 | 1AM to 2AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
May | 14 | 2AM to 3AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
May | 14 | 3AM to 4AM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
May | 14 | 4AM to 5AM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
May | 14 | 5AM to 6AM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
May | 14 | 6AM to 7AM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 14 | 7AM to 8AM | 64 | 62.1 | 61 | 80.4 | 27.89 | 0.0752 | 0.54 | 13.44 | 0
May | 14 | 8AM to 9AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
May | 14 | 9AM to 10AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
May | 14 | 10AM to 11AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
May | 14 | 11AM to 12PM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
May | 14 | 12PM to 1PM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
May | 14 | 1PM to 2PM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
May | 14 | 2PM to 3PM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
May | 14 | 3PM to 4PM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
May | 14 | 4PM to 5PM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
May | 14 | 5PM to 6PM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
May | 14 | 6PM to 7PM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
May | 14 | 7PM to 8PM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
May | 14 | 8PM to 9PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 14 | 9PM to 10PM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
May | 14 | 10PM to 11PM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
May | 14 | 11PM to 12AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
May | 15 | 12AM to 1AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
May | 15 | 1AM to 2AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
May | 15 | 2AM to 3AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
May | 15 | 3AM to 4AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
May | 15 | 4AM to 5AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
May | 15 | 5AM to 6AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
May | 15 | 6AM to 7AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
May | 15 | 7AM to 8AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
May | 15 | 8AM to 9AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
May | 15 | 9AM to 10AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
May | 15 | 10AM to 11AM | 63 | 61.1 | 60.1 | 77.8 | 27.22 | 0.0754 | 0.52 | 13.41 | 0
May | 15 | 11AM to 12PM | 61 | 61 | 61 | 80.4 | 27.14 | 0.0757 | 0.54 | 13.37 | 0
May | 15 | 12PM to 1PM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 15 | 1PM to 2PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 15 | 2PM to 3PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 15 | 3PM to 4PM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 15 | 4PM to 5PM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 15 | 5PM to 6PM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 15 | 6PM to 7PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 15 | 7PM to 8PM | 60.1 | 60.1 | 60.1 | 77.8 | 26.51 | 0.0758 | 0.52 | 13.33 | 0
May | 15 | 8PM to 9PM | 62.1 | 60.8 | 60.1 | 77.8 | 27 | 0.0755 | 0.52 | 13.39 | 0
May | 15 | 9PM to 10PM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 15 | 10PM to 11PM | 62.1 | 60.8 | 60.1 | 77.8 | 27 | 0.0755 | 0.52 | 13.39 | 0
May | 15 | 11PM to 12AM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
May | 16 | 12AM to 1AM | 61 | 60.4 | 60.1 | 77.8 | 26.74 | 0.0757 | 0.52 | 13.36 | 0
May | 16 | 1AM to 2AM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 16 | 2AM to 3AM | 59 | 59 | 59 | 74.9 | 25.79 | 0.076 | 0.5 | 13.3 | 0
May | 16 | 3AM to 4AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
May | 16 | 4AM to 5AM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 16 | 5AM to 6AM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 16 | 6AM to 7AM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
May | 16 | 7AM to 8AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
May | 16 | 8AM to 9AM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 16 | 9AM to 10AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
May | 16 | 10AM to 11AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
May | 16 | 11AM to 12PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
May | 16 | 12PM to 1PM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
May | 16 | 1PM to 2PM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
May | 16 | 2PM to 3PM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
May | 16 | 3PM to 4PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
May | 16 | 4PM to 5PM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
May | 16 | 5PM to 6PM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
May | 16 | 6PM to 7PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 16 | 7PM to 8PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
May | 16 | 8PM to 9PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
May | 16 | 9PM to 10PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 16 | 10PM to 11PM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
May | 16 | 11PM to 12AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
May | 17 | 12AM to 1AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
May | 17 | 1AM to 2AM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
May | 17 | 2AM to 3AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
May | 17 | 3AM to 4AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
May | 17 | 4AM to 5AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
May | 17 | 5AM to 6AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
May | 17 | 6AM to 7AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
May | 17 | 7AM to 8AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
May | 17 | 8AM to 9AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
May | 17 | 9AM to 10AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
May | 17 | 10AM to 11AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
May | 17 | 11AM to 12PM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
May | 17 | 12PM to 1PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
May | 17 | 1PM to 2PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
May | 17 | 2PM to 3PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
May | 17 | 3PM to 4PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
May | 17 | 4PM to 5PM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 17 | 5PM to 6PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 17 | 6PM to 7PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 17 | 7PM to 8PM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
May | 17 | 8PM to 9PM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 17 | 9PM to 10PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 17 | 10PM to 11PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
May | 17 | 11PM to 12AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
May | 18 | 12AM to 1AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
May | 18 | 1AM to 2AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
May | 18 | 2AM to 3AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
May | 18 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
May | 18 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
May | 18 | 5AM to 6AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
May | 18 | 6AM to 7AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
May | 18 | 7AM to 8AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
May | 18 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
May | 18 | 9AM to 10AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
May | 18 | 10AM to 11AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
May | 18 | 11AM to 12PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
May | 18 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
May | 18 | 1PM to 2PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
May | 18 | 2PM to 3PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
May | 18 | 3PM to 4PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
May | 18 | 4PM to 5PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
May | 18 | 5PM to 6PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
May | 18 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
May | 18 | 7PM to 8PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
May | 18 | 8PM to 9PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
May | 18 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
May | 18 | 10PM to 11PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
May | 18 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
May | 19 | 12AM to 1AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
May | 19 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 19 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 19 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
May | 19 | 4AM to 5AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
May | 19 | 5AM to 6AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
May | 19 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
May | 19 | 7AM to 8AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
May | 19 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
May | 19 | 9AM to 10AM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
May | 19 | 10AM to 11AM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
May | 19 | 11AM to 12PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
May | 19 | 12PM to 1PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
May | 19 | 1PM to 2PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
May | 19 | 2PM to 3PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
May | 19 | 3PM to 4PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
May | 19 | 4PM to 5PM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
May | 19 | 5PM to 6PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 19 | 6PM to 7PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 19 | 7PM to 8PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
May | 19 | 8PM to 9PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 19 | 9PM to 10PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 19 | 10PM to 11PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 19 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
May | 20 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 20 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 20 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
May | 20 | 3AM to 4AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
May | 20 | 4AM to 5AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
May | 20 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
May | 20 | 6AM to 7AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 20 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
May | 20 | 8AM to 9AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
May | 20 | 9AM to 10AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
May | 20 | 10AM to 11AM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
May | 20 | 11AM to 12PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
May | 20 | 12PM to 1PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 20 | 1PM to 2PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 20 | 2PM to 3PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
May | 20 | 3PM to 4PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
May | 20 | 4PM to 5PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 20 | 5PM to 6PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 20 | 6PM to 7PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 20 | 7PM to 8PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 20 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 20 | 9PM to 10PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 20 | 10PM to 11PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 20 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 21 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 21 | 1AM to 2AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 21 | 2AM to 3AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 21 | 3AM to 4AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 21 | 4AM to 5AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 21 | 5AM to 6AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
May | 21 | 6AM to 7AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
May | 21 | 7AM to 8AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 21 | 8AM to 9AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
May | 21 | 9AM to 10AM | 60.1 | 59.4 | 59 | 74.9 | 26.05 | 0.0758 | 0.5 | 13.33 | 0
May | 21 | 10AM to 11AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
May | 21 | 11AM to 12PM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
May | 21 | 12PM to 1PM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
May | 21 | 1PM to 2PM | 63 | 61.7 | 61 | 80.4 | 27.62 | 0.0754 | 0.54 | 13.42 | 0
May | 21 | 2PM to 3PM | 63 | 61.1 | 60.1 | 77.8 | 27.22 | 0.0754 | 0.52 | 13.41 | 0
May | 21 | 3PM to 4PM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
May | 21 | 4PM to 5PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
May | 21 | 5PM to 6PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
May | 21 | 6PM to 7PM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
May | 21 | 7PM to 8PM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
May | 21 | 8PM to 9PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
May | 21 | 9PM to 10PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
May | 21 | 10PM to 11PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 21 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
May | 22 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
May | 22 | 1AM to 2AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
May | 22 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 22 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 22 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
May | 22 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
May | 22 | 6AM to 7AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 22 | 7AM to 8AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
May | 22 | 8AM to 9AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
May | 22 | 9AM to 10AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
May | 22 | 10AM to 11AM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
May | 22 | 11AM to 12PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
May | 22 | 12PM to 1PM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
May | 22 | 1PM to 2PM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
May | 22 | 2PM to 3PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
May | 22 | 3PM to 4PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
May | 22 | 4PM to 5PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 22 | 5PM to 6PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 22 | 6PM to 7PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
May | 22 | 7PM to 8PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 22 | 8PM to 9PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 22 | 9PM to 10PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 22 | 10PM to 11PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 22 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 23 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 23 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
May | 23 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 23 | 3AM to 4AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
May | 23 | 4AM to 5AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
May | 23 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
May | 23 | 6AM to 7AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 23 | 7AM to 8AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 23 | 8AM to 9AM | 62.1 | 53.2 | 46 | 46.1 | 22.07 | 0.0757 | 0.31 | 13.29 | 0
May | 23 | 9AM to 10AM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
May | 23 | 10AM to 11AM | 66 | 54.3 | 45 | 44.3 | 22.74 | 0.0752 | 0.3 | 13.39 | 0
May | 23 | 11AM to 12PM | 66 | 54.3 | 45 | 44.3 | 22.74 | 0.0752 | 0.3 | 13.39 | 0
May | 23 | 12PM to 1PM | 66 | 55.2 | 46.9 | 47.8 | 23.28 | 0.0752 | 0.32 | 13.4 | 0
May | 23 | 1PM to 2PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
May | 23 | 2PM to 3PM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
May | 23 | 3PM to 4PM | 64 | 53.1 | 44.1 | 42.8 | 22.02 | 0.0755 | 0.29 | 13.33 | 0
May | 23 | 4PM to 5PM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
May | 23 | 5PM to 6PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 23 | 6PM to 7PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
May | 23 | 7PM to 8PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
May | 23 | 8PM to 9PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 23 | 9PM to 10PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
May | 23 | 10PM to 11PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
May | 23 | 11PM to 12AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 24 | 12AM to 1AM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
May | 24 | 1AM to 2AM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
May | 24 | 2AM to 3AM | 63 | 50.2 | 37.9 | 33.7 | 20.35 | 0.0757 | 0.23 | 13.28 | 0
May | 24 | 3AM to 4AM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
May | 24 | 4AM to 5AM | 62.1 | 51.4 | 42.1 | 39.6 | 21.05 | 0.0758 | 0.27 | 13.27 | 0
May | 24 | 5AM to 6AM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
May | 24 | 6AM to 7AM | 64 | 52.6 | 43 | 41 | 21.75 | 0.0755 | 0.28 | 13.32 | 0
May | 24 | 7AM to 8AM | 66 | 53.1 | 42.1 | 39.6 | 22.01 | 0.0752 | 0.27 | 13.37 | 0
May | 24 | 8AM to 9AM | 68 | 54.7 | 44.1 | 42.8 | 22.99 | 0.0749 | 0.29 | 13.43 | 0
May | 24 | 9AM to 10AM | 70 | 55.1 | 43 | 41 | 23.19 | 0.0746 | 0.28 | 13.48 | 0
May | 24 | 10AM to 11AM | 72 | 56.7 | 45 | 44.3 | 24.18 | 0.0743 | 0.3 | 13.54 | 0
May | 24 | 11AM to 12PM | 73.9 | 56.6 | 43 | 41 | 24.15 | 0.0741 | 0.28 | 13.58 | 0
May | 24 | 12PM to 1PM | 73.9 | 57.1 | 44.1 | 42.8 | 24.43 | 0.0741 | 0.29 | 13.58 | 0
May | 24 | 1PM to 2PM | 73 | 56.3 | 43 | 41 | 23.94 | 0.0742 | 0.28 | 13.55 | 0
May | 24 | 2PM to 3PM | 70 | 56.4 | 46 | 46.1 | 23.99 | 0.0746 | 0.31 | 13.49 | 0
May | 24 | 3PM to 4PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
May | 24 | 4PM to 5PM | 68 | 55.1 | 45 | 44.3 | 23.22 | 0.0749 | 0.3 | 13.44 | 0
May | 24 | 5PM to 6PM | 64.9 | 54.8 | 46.9 | 47.8 | 23.02 | 0.0753 | 0.32 | 13.37 | 0
May | 24 | 6PM to 7PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
May | 24 | 7PM to 8PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
May | 24 | 8PM to 9PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 24 | 9PM to 10PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 24 | 10PM to 11PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
May | 24 | 11PM to 12AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 25 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
May | 25 | 1AM to 2AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 25 | 2AM to 3AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
May | 25 | 3AM to 4AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
May | 25 | 4AM to 5AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 25 | 5AM to 6AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
May | 25 | 6AM to 7AM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
May | 25 | 7AM to 8AM | 72 | 59.4 | 51.1 | 55.9 | 25.99 | 0.0743 | 0.38 | 13.57 | 0
May | 25 | 8AM to 9AM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
May | 25 | 9AM to 10AM | 75 | 60.5 | 51.1 | 55.9 | 26.74 | 0.0738 | 0.38 | 13.65 | 0
May | 25 | 10AM to 11AM | 77 | 61.3 | 51.1 | 55.9 | 27.22 | 0.0736 | 0.38 | 13.7 | 0
May | 25 | 11AM to 12PM | 80.1 | 61 | 48 | 49.8 | 27.01 | 0.0732 | 0.34 | 13.76 | 0
May | 25 | 12PM to 1PM | 81 | 62.2 | 50 | 53.6 | 27.84 | 0.073 | 0.36 | 13.79 | 0
May | 25 | 1PM to 2PM | 78.1 | 60.7 | 48.9 | 51.5 | 26.8 | 0.0735 | 0.35 | 13.71 | 0
May | 25 | 2PM to 3PM | 75.9 | 59.5 | 48 | 49.8 | 26 | 0.0738 | 0.34 | 13.65 | 0
May | 25 | 3PM to 4PM | 77 | 59.4 | 46.9 | 47.8 | 25.95 | 0.0736 | 0.32 | 13.68 | 0
May | 25 | 4PM to 5PM | 75 | 58.3 | 46 | 46.1 | 25.22 | 0.0739 | 0.31 | 13.62 | 0
May | 25 | 5PM to 6PM | 72 | 57.1 | 46 | 46.1 | 24.48 | 0.0743 | 0.31 | 13.54 | 0
May | 25 | 6PM to 7PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
May | 25 | 7PM to 8PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 25 | 8PM to 9PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
May | 25 | 9PM to 10PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 25 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
May | 25 | 11PM to 12AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
May | 26 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
May | 26 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
May | 26 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
May | 26 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
May | 26 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
May | 26 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
May | 26 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
May | 26 | 7AM to 8AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
May | 26 | 8AM to 9AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
May | 26 | 9AM to 10AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
May | 26 | 10AM to 11AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
May | 26 | 11AM to 12PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
May | 26 | 12PM to 1PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
May | 26 | 1PM to 2PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
May | 26 | 2PM to 3PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
May | 26 | 3PM to 4PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
May | 26 | 4PM to 5PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 26 | 5PM to 6PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 26 | 6PM to 7PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
May | 26 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 26 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 26 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 26 | 10PM to 11PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
May | 26 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 27 | 12AM to 1AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 27 | 1AM to 2AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 27 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
May | 27 | 3AM to 4AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
May | 27 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
May | 27 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
May | 27 | 6AM to 7AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
May | 27 | 7AM to 8AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
May | 27 | 8AM to 9AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
May | 27 | 9AM to 10AM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
May | 27 | 10AM to 11AM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
May | 27 | 11AM to 12PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
May | 27 | 12PM to 1PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
May | 27 | 1PM to 2PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
May | 27 | 2PM to 3PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
May | 27 | 3PM to 4PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
May | 27 | 4PM to 5PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 27 | 5PM to 6PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
May | 27 | 6PM to 7PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 27 | 7PM to 8PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
May | 27 | 8PM to 9PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
May | 27 | 9PM to 10PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
May | 27 | 10PM to 11PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 27 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 28 | 12AM to 1AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 28 | 1AM to 2AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 28 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 28 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 28 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 28 | 5AM to 6AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 28 | 6AM to 7AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
May | 28 | 7AM to 8AM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
May | 28 | 8AM to 9AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 28 | 9AM to 10AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
May | 28 | 10AM to 11AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
May | 28 | 11AM to 12PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
May | 28 | 12PM to 1PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
May | 28 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 28 | 2PM to 3PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
May | 28 | 3PM to 4PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
May | 28 | 4PM to 5PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 28 | 5PM to 6PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
May | 28 | 6PM to 7PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 28 | 7PM to 8PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 28 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 28 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 28 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 28 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 29 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 29 | 5AM to 6AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 29 | 6AM to 7AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
May | 29 | 7AM to 8AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
May | 29 | 8AM to 9AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
May | 29 | 9AM to 10AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
May | 29 | 10AM to 11AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 29 | 11AM to 12PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
May | 29 | 12PM to 1PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 29 | 1PM to 2PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 29 | 2PM to 3PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
May | 29 | 3PM to 4PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 29 | 4PM to 5PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 29 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
May | 29 | 6PM to 7PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
May | 29 | 7PM to 8PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 29 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 29 | 9PM to 10PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 29 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 29 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 30 | 12AM to 1AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
May | 30 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 30 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 30 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
May | 30 | 4AM to 5AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
May | 30 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
May | 30 | 6AM to 7AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 30 | 7AM to 8AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
May | 30 | 8AM to 9AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
May | 30 | 9AM to 10AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
May | 30 | 10AM to 11AM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
May | 30 | 11AM to 12PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 30 | 12PM to 1PM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
May | 30 | 1PM to 2PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 30 | 2PM to 3PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
May | 30 | 3PM to 4PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 30 | 4PM to 5PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
May | 30 | 5PM to 6PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
May | 30 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
May | 30 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 30 | 8PM to 9PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 30 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
May | 30 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
May | 30 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 31 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 31 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 31 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 31 | 3AM to 4AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 31 | 4AM to 5AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
May | 31 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
May | 31 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
May | 31 | 7AM to 8AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
May | 31 | 8AM to 9AM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
May | 31 | 9AM to 10AM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
May | 31 | 10AM to 11AM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
May | 31 | 11AM to 12PM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
May | 31 | 12PM to 1PM | 66 | 55.2 | 46.9 | 47.8 | 23.28 | 0.0752 | 0.32 | 13.4 | 0
May | 31 | 1PM to 2PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
May | 31 | 2PM to 3PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
May | 31 | 3PM to 4PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
May | 31 | 4PM to 5PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
May | 31 | 5PM to 6PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
May | 31 | 6PM to 7PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
May | 31 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
May | 31 | 8PM to 9PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
May | 31 | 9PM to 10PM | 54.3 | 52.8 | 51.6 | 57 | 21.87 | 0.0768 | 0.39 | 13.13 | 0
May | 31 | 10PM to 11PM | 53.6 | 52.4 | 51.4 | 56.6 | 21.64 | 0.0769 | 0.38 | 13.11 | 0
May | 31 | 11PM to 12AM | 52.9 | 51.9 | 51.1 | 55.9 | 21.34 | 0.077 | 0.38 | 13.09 | 0
June | 1 | 12AM to 1AM | 52.2 | 51.4 | 50.9 | 55.5 | 21.11 | 0.0771 | 0.37 | 13.07 | 0
June | 1 | 1AM to 2AM | 51.4 | 50.9 | 50.5 | 54.7 | 20.82 | 0.0773 | 0.37 | 13.04 | 1
June | 1 | 2AM to 3AM | 50.7 | 50.5 | 50.4 | 54.4 | 20.59 | 0.0774 | 0.37 | 13.03 | 1
June | 1 | 3AM to 4AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
June | 1 | 4AM to 5AM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
June | 1 | 5AM to 6AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
June | 1 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 1 | 7AM to 8AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
June | 1 | 8AM to 9AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
June | 1 | 9AM to 10AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
June | 1 | 10AM to 11AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
June | 1 | 11AM to 12PM | 73 | 61.8 | 55 | 64.7 | 27.64 | 0.0741 | 0.44 | 13.63 | 0
June | 1 | 12PM to 1PM | 75.9 | 63.3 | 55.9 | 66.9 | 28.69 | 0.0737 | 0.45 | 13.71 | 0
June | 1 | 1PM to 2PM | 82 | 64.4 | 54 | 62.2 | 29.44 | 0.0728 | 0.42 | 13.85 | 0
June | 1 | 2PM to 3PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
June | 1 | 3PM to 4PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
June | 1 | 4PM to 5PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 1 | 5PM to 6PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 1 | 6PM to 7PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 1 | 7PM to 8PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 1 | 8PM to 9PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 1 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 1 | 10PM to 11PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 1 | 11PM to 12AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 2 | 12AM to 1AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 2 | 1AM to 2AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 2 | 2AM to 3AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 2 | 3AM to 4AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 2 | 4AM to 5AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 2 | 5AM to 6AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
June | 2 | 6AM to 7AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
June | 2 | 7AM to 8AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
June | 2 | 8AM to 9AM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
June | 2 | 9AM to 10AM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
June | 2 | 10AM to 11AM | 75.9 | 63.8 | 57 | 69.6 | 29.11 | 0.0736 | 0.47 | 13.72 | 0
June | 2 | 11AM to 12PM | 80.1 | 63.3 | 53.1 | 60.1 | 28.64 | 0.0731 | 0.41 | 13.79 | 0
June | 2 | 12PM to 1PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
June | 2 | 1PM to 2PM | 84 | 67.5 | 59 | 74.9 | 31.91 | 0.0725 | 0.5 | 13.94 | 0
June | 2 | 2PM to 3PM | 89.1 | 68.1 | 57 | 69.6 | 32.32 | 0.0719 | 0.47 | 14.05 | 0
June | 2 | 3PM to 4PM | 80.1 | 64.2 | 55 | 64.7 | 29.35 | 0.0731 | 0.44 | 13.81 | 0
June | 2 | 4PM to 5PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
June | 2 | 5PM to 6PM | 77 | 61.7 | 52 | 57.8 | 27.52 | 0.0736 | 0.39 | 13.71 | 0
June | 2 | 6PM to 7PM | 73 | 60.3 | 52 | 57.8 | 26.55 | 0.0741 | 0.39 | 13.61 | 0
June | 2 | 7PM to 8PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
June | 2 | 8PM to 9PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
June | 2 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
June | 2 | 10PM to 11PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 2 | 11PM to 12AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 3 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 3 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 3 | 2AM to 3AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 3 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 3 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 3 | 5AM to 6AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 3 | 6AM to 7AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
June | 3 | 7AM to 8AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 3 | 8AM to 9AM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
June | 3 | 9AM to 10AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
June | 3 | 10AM to 11AM | 77 | 63.2 | 55 | 64.7 | 28.61 | 0.0735 | 0.44 | 13.73 | 0
June | 3 | 11AM to 12PM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
June | 3 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
June | 3 | 1PM to 2PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
June | 3 | 2PM to 3PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
June | 3 | 3PM to 4PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
June | 3 | 4PM to 5PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 3 | 5PM to 6PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
June | 3 | 6PM to 7PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
June | 3 | 7PM to 8PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 3 | 8PM to 9PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 3 | 9PM to 10PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
June | 3 | 10PM to 11PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
June | 3 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 4 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 4 | 1AM to 2AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 4 | 2AM to 3AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
June | 4 | 3AM to 4AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
June | 4 | 4AM to 5AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
June | 4 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 4 | 6AM to 7AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 4 | 7AM to 8AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 4 | 8AM to 9AM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 4 | 9AM to 10AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 4 | 10AM to 11AM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 4 | 11AM to 12PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
June | 4 | 12PM to 1PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 4 | 1PM to 2PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
June | 4 | 2PM to 3PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
June | 4 | 3PM to 4PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 4 | 4PM to 5PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 4 | 5PM to 6PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 4 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 4 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 4 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 4 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 4 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 4 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 5 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 5 | 1AM to 2AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 5 | 2AM to 3AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 5 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 5 | 4AM to 5AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 5 | 5AM to 6AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 5 | 6AM to 7AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
June | 5 | 7AM to 8AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
June | 5 | 8AM to 9AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
June | 5 | 9AM to 10AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
June | 5 | 10AM to 11AM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
June | 5 | 11AM to 12PM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
June | 5 | 12PM to 1PM | 84.9 | 65.8 | 55 | 64.7 | 30.54 | 0.0724 | 0.44 | 13.93 | 0
June | 5 | 1PM to 2PM | 82.9 | 65.2 | 55 | 64.7 | 30.06 | 0.0727 | 0.44 | 13.88 | 0
June | 5 | 2PM to 3PM | 77 | 62.2 | 53.1 | 60.1 | 27.89 | 0.0735 | 0.41 | 13.71 | 0
June | 5 | 3PM to 4PM | 73 | 60.3 | 52 | 57.8 | 26.55 | 0.0741 | 0.39 | 13.61 | 0
June | 5 | 4PM to 5PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
June | 5 | 5PM to 6PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
June | 5 | 6PM to 7PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 5 | 7PM to 8PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 5 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 5 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 5 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 5 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 6 | 12AM to 1AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 6 | 1AM to 2AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 6 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 6 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 6 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 6 | 5AM to 6AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 6 | 6AM to 7AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 6 | 7AM to 8AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
June | 6 | 8AM to 9AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
June | 6 | 9AM to 10AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
June | 6 | 10AM to 11AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
June | 6 | 11AM to 12PM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
June | 6 | 12PM to 1PM | 79 | 63.9 | 55 | 64.7 | 29.09 | 0.0732 | 0.44 | 13.78 | 0
June | 6 | 1PM to 2PM | 77 | 62.2 | 53.1 | 60.1 | 27.89 | 0.0735 | 0.41 | 13.71 | 0
June | 6 | 2PM to 3PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
June | 6 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
June | 6 | 4PM to 5PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 6 | 5PM to 6PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 6 | 6PM to 7PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 6 | 7PM to 8PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
June | 6 | 8PM to 9PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
June | 6 | 9PM to 10PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
June | 6 | 10PM to 11PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
June | 6 | 11PM to 12AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
June | 7 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 7 | 1AM to 2AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 7 | 2AM to 3AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 7 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 7 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 7 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 7 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 7 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
June | 7 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 7 | 9AM to 10AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
June | 7 | 10AM to 11AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 7 | 11AM to 12PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 7 | 12PM to 1PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 7 | 1PM to 2PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 7 | 2PM to 3PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 7 | 3PM to 4PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
June | 7 | 4PM to 5PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
June | 7 | 5PM to 6PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 7 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 7 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 7 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 7 | 9PM to 10PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 7 | 10PM to 11PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 7 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 8 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 8 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 8 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 8 | 3AM to 4AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
June | 8 | 4AM to 5AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
June | 8 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 8 | 6AM to 7AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 8 | 7AM to 8AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 8 | 8AM to 9AM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
June | 8 | 9AM to 10AM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
June | 8 | 10AM to 11AM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
June | 8 | 11AM to 12PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
June | 8 | 12PM to 1PM | 71.1 | 58.1 | 48.9 | 51.5 | 25.09 | 0.0744 | 0.35 | 13.54 | 0
June | 8 | 1PM to 2PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
June | 8 | 2PM to 3PM | 69.1 | 56.9 | 48 | 49.8 | 24.34 | 0.0747 | 0.34 | 13.48 | 0
June | 8 | 3PM to 4PM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
June | 8 | 4PM to 5PM | 64.9 | 54.8 | 46.9 | 47.8 | 23.02 | 0.0753 | 0.32 | 13.37 | 0
June | 8 | 5PM to 6PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
June | 8 | 6PM to 7PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
June | 8 | 7PM to 8PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
June | 8 | 8PM to 9PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
June | 8 | 9PM to 10PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
June | 8 | 10PM to 11PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 8 | 11PM to 12AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 9 | 12AM to 1AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 9 | 1AM to 2AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 9 | 2AM to 3AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 9 | 3AM to 4AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 9 | 4AM to 5AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 9 | 5AM to 6AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 9 | 6AM to 7AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 9 | 7AM to 8AM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
June | 9 | 8AM to 9AM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
June | 9 | 9AM to 10AM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
June | 9 | 10AM to 11AM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
June | 9 | 11AM to 12PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
June | 9 | 12PM to 1PM | 69.1 | 55.5 | 45 | 44.3 | 23.48 | 0.0747 | 0.3 | 13.46 | 0
June | 9 | 1PM to 2PM | 68 | 55.1 | 45 | 44.3 | 23.22 | 0.0749 | 0.3 | 13.44 | 0
June | 9 | 2PM to 3PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
June | 9 | 3PM to 4PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
June | 9 | 4PM to 5PM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
June | 9 | 5PM to 6PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
June | 9 | 6PM to 7PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
June | 9 | 7PM to 8PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
June | 9 | 8PM to 9PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 9 | 9PM to 10PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 9 | 10PM to 11PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
June | 9 | 11PM to 12AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 10 | 12AM to 1AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 10 | 1AM to 2AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 10 | 2AM to 3AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 10 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 10 | 4AM to 5AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 10 | 5AM to 6AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 10 | 6AM to 7AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 10 | 7AM to 8AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
June | 10 | 8AM to 9AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 10 | 9AM to 10AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 10 | 10AM to 11AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 10 | 11AM to 12PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
June | 10 | 12PM to 1PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
June | 10 | 1PM to 2PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
June | 10 | 2PM to 3PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
June | 10 | 3PM to 4PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
June | 10 | 4PM to 5PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 10 | 5PM to 6PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
June | 10 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 10 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 10 | 8PM to 9PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 10 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 10 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 10 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 11 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 11 | 1AM to 2AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 11 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 11 | 3AM to 4AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
June | 11 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 11 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 11 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 11 | 7AM to 8AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 11 | 8AM to 9AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
June | 11 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
June | 11 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
June | 11 | 11AM to 12PM | 71.1 | 59.5 | 52 | 57.8 | 26.07 | 0.0744 | 0.39 | 13.56 | 0
June | 11 | 12PM to 1PM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
June | 11 | 1PM to 2PM | 72 | 59.4 | 51.1 | 55.9 | 25.99 | 0.0743 | 0.38 | 13.57 | 0
June | 11 | 2PM to 3PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
June | 11 | 3PM to 4PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
June | 11 | 4PM to 5PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
June | 11 | 5PM to 6PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 11 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 11 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 11 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 11 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 11 | 10PM to 11PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 11 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 12AM to 1AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 12 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 12 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 12 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 12 | 5AM to 6AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 12 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 12 | 7AM to 8AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 12 | 8AM to 9AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 12 | 9AM to 10AM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
June | 12 | 10AM to 11AM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
June | 12 | 11AM to 12PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 12 | 12PM to 1PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 12 | 1PM to 2PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 12 | 2PM to 3PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 12 | 3PM to 4PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 12 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 12 | 5PM to 6PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 12 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 12 | 7PM to 8PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 8PM to 9PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 12 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 13 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 13 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 13 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 13 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 13 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 13 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 13 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 13 | 7AM to 8AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 13 | 8AM to 9AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 13 | 9AM to 10AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 13 | 10AM to 11AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 13 | 11AM to 12PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 13 | 12PM to 1PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 13 | 1PM to 2PM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
June | 13 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 13 | 3PM to 4PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 13 | 4PM to 5PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 13 | 5PM to 6PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 13 | 6PM to 7PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
June | 13 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 13 | 8PM to 9PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 13 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 13 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 13 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 14 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 14 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 14 | 2AM to 3AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
June | 14 | 3AM to 4AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 14 | 4AM to 5AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
June | 14 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 14 | 6AM to 7AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
June | 14 | 7AM to 8AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 14 | 8AM to 9AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 14 | 9AM to 10AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 14 | 10AM to 11AM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
June | 14 | 11AM to 12PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
June | 14 | 12PM to 1PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
June | 14 | 1PM to 2PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
June | 14 | 2PM to 3PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
June | 14 | 3PM to 4PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
June | 14 | 4PM to 5PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
June | 14 | 5PM to 6PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
June | 14 | 6PM to 7PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 14 | 7PM to 8PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 14 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 14 | 9PM to 10PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 14 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 14 | 11PM to 12AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 15 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 4AM to 5AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 15 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 15 | 6AM to 7AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 15 | 7AM to 8AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 15 | 8AM to 9AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 15 | 9AM to 10AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
June | 15 | 10AM to 11AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 15 | 11AM to 12PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 15 | 12PM to 1PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 15 | 1PM to 2PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 15 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 15 | 3PM to 4PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 15 | 4PM to 5PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
June | 15 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 15 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 15 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 15 | 8PM to 9PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 15 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 15 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 15 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 16 | 4AM to 5AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
June | 16 | 5AM to 6AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
June | 16 | 6AM to 7AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
June | 16 | 7AM to 8AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
June | 16 | 8AM to 9AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 16 | 9AM to 10AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 16 | 10AM to 11AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 16 | 11AM to 12PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 16 | 12PM to 1PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 16 | 1PM to 2PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 16 | 2PM to 3PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 16 | 3PM to 4PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 16 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 16 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 16 | 6PM to 7PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 16 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 16 | 8PM to 9PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 16 | 9PM to 10PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 16 | 10PM to 11PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 16 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
June | 17 | 12AM to 1AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 2AM to 3AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 3AM to 4AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 17 | 5AM to 6AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
June | 17 | 6AM to 7AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 17 | 7AM to 8AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
June | 17 | 8AM to 9AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
June | 17 | 9AM to 10AM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
June | 17 | 10AM to 11AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
June | 17 | 11AM to 12PM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
June | 17 | 12PM to 1PM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
June | 17 | 1PM to 2PM | 64.9 | 53.5 | 44.1 | 42.8 | 22.24 | 0.0753 | 0.29 | 13.35 | 0
June | 17 | 2PM to 3PM | 63 | 52.6 | 44.1 | 42.8 | 21.76 | 0.0756 | 0.29 | 13.3 | 0
June | 17 | 3PM to 4PM | 64 | 53.1 | 44.1 | 42.8 | 22.02 | 0.0755 | 0.29 | 13.33 | 0
June | 17 | 4PM to 5PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
June | 17 | 5PM to 6PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
June | 17 | 6PM to 7PM | 57.9 | 50 | 43 | 41 | 20.27 | 0.0764 | 0.28 | 13.17 | 0
June | 17 | 7PM to 8PM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
June | 17 | 8PM to 9PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
June | 17 | 9PM to 10PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
June | 17 | 10PM to 11PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
June | 17 | 11PM to 12AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
June | 18 | 12AM to 1AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
June | 18 | 1AM to 2AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
June | 18 | 2AM to 3AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 18 | 3AM to 4AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
June | 18 | 4AM to 5AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
June | 18 | 5AM to 6AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
June | 18 | 6AM to 7AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
June | 18 | 7AM to 8AM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
June | 18 | 8AM to 9AM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
June | 18 | 9AM to 10AM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
June | 18 | 10AM to 11AM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
June | 18 | 11AM to 12PM | 72 | 56.3 | 44.1 | 42.8 | 23.95 | 0.0744 | 0.29 | 13.53 | 0
June | 18 | 12PM to 1PM | 69.1 | 56.4 | 46.9 | 47.8 | 24.03 | 0.0747 | 0.32 | 13.47 | 0
June | 18 | 1PM to 2PM | 66.9 | 54.3 | 44.1 | 42.8 | 22.72 | 0.0751 | 0.29 | 13.4 | 0
June | 18 | 2PM to 3PM | 66.9 | 53.8 | 43 | 41 | 22.45 | 0.0751 | 0.28 | 13.4 | 0
June | 18 | 3PM to 4PM | 64.9 | 52.6 | 42.1 | 39.6 | 21.75 | 0.0754 | 0.27 | 13.34 | 0
June | 18 | 4PM to 5PM | 64 | 51.8 | 41 | 38 | 21.28 | 0.0755 | 0.26 | 13.32 | 0
June | 18 | 5PM to 6PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
June | 18 | 6PM to 7PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
June | 18 | 7PM to 8PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
June | 18 | 8PM to 9PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
June | 18 | 9PM to 10PM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
June | 18 | 10PM to 11PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
June | 18 | 11PM to 12AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
June | 19 | 12AM to 1AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
June | 19 | 1AM to 2AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 19 | 2AM to 3AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 19 | 3AM to 4AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
June | 19 | 4AM to 5AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
June | 19 | 5AM to 6AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
June | 19 | 6AM to 7AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
June | 19 | 7AM to 8AM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
June | 19 | 8AM to 9AM | 66 | 55.2 | 46.9 | 47.8 | 23.28 | 0.0752 | 0.32 | 13.4 | 0
June | 19 | 9AM to 10AM | 66.9 | 56.1 | 48 | 49.8 | 23.81 | 0.075 | 0.34 | 13.42 | 0
June | 19 | 10AM to 11AM | 73 | 57.9 | 46.9 | 47.8 | 24.99 | 0.0742 | 0.32 | 13.57 | 0
June | 19 | 11AM to 12PM | 70 | 57.2 | 48 | 49.8 | 24.56 | 0.0746 | 0.34 | 13.5 | 0
June | 19 | 12PM to 1PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
June | 19 | 1PM to 2PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
June | 19 | 2PM to 3PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
June | 19 | 3PM to 4PM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
June | 19 | 4PM to 5PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
June | 19 | 5PM to 6PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 19 | 6PM to 7PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 19 | 7PM to 8PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 19 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 19 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 19 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 19 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 20 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 20 | 1AM to 2AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 4AM to 5AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
June | 20 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 7AM to 8AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 20 | 8AM to 9AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
June | 20 | 9AM to 10AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 20 | 10AM to 11AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 20 | 11AM to 12PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 20 | 12PM to 1PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 20 | 1PM to 2PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
June | 20 | 2PM to 3PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 20 | 3PM to 4PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 20 | 4PM to 5PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 20 | 5PM to 6PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 20 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 20 | 7PM to 8PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 20 | 8PM to 9PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 20 | 9PM to 10PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
June | 20 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 20 | 11PM to 12AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
June | 21 | 12AM to 1AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 2AM to 3AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 3AM to 4AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 4AM to 5AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 5AM to 6AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 6AM to 7AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 21 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
June | 21 | 8AM to 9AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 21 | 9AM to 10AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
June | 21 | 10AM to 11AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 21 | 11AM to 12PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 21 | 12PM to 1PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 21 | 1PM to 2PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
June | 21 | 2PM to 3PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 21 | 3PM to 4PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
June | 21 | 4PM to 5PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
June | 21 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
June | 21 | 6PM to 7PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 21 | 7PM to 8PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 21 | 8PM to 9PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 21 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
June | 21 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
June | 21 | 11PM to 12AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 22 | 12AM to 1AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
June | 22 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
June | 22 | 2AM to 3AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
June | 22 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
June | 22 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
June | 22 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 22 | 6AM to 7AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
June | 22 | 7AM to 8AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
June | 22 | 8AM to 9AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
June | 22 | 9AM to 10AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
June | 22 | 10AM to 11AM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
June | 22 | 11AM to 12PM | 70 | 57.7 | 48.9 | 51.5 | 24.83 | 0.0746 | 0.35 | 13.51 | 0
June | 22 | 12PM to 1PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
June | 22 | 1PM to 2PM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
June | 22 | 2PM to 3PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
June | 22 | 3PM to 4PM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
June | 22 | 4PM to 5PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
June | 22 | 5PM to 6PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
June | 22 | 6PM to 7PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
June | 22 | 7PM to 8PM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
June | 22 | 8PM to 9PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
June | 22 | 9PM to 10PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
June | 22 | 10PM to 11PM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 22 | 11PM to 12AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 23 | 12AM to 1AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
June | 23 | 1AM to 2AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
June | 23 | 2AM to 3AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
June | 23 | 3AM to 4AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
June | 23 | 4AM to 5AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
June | 23 | 5AM to 6AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
June | 23 | 6AM to 7AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 23 | 7AM to 8AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
June | 23 | 8AM to 9AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
June | 23 | 9AM to 10AM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
June | 23 | 10AM to 11AM | 71.1 | 58.6 | 50 | 53.6 | 25.43 | 0.0744 | 0.36 | 13.54 | 0
June | 23 | 11AM to 12PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
June | 23 | 12PM to 1PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
June | 23 | 1PM to 2PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 23 | 2PM to 3PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 23 | 3PM to 4PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
June | 23 | 4PM to 5PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
June | 23 | 5PM to 6PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
June | 23 | 6PM to 7PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
June | 23 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
June | 23 | 8PM to 9PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
June | 23 | 9PM to 10PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
June | 23 | 10PM to 11PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
June | 23 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
June | 24 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 24 | 1AM to 2AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
June | 24 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 24 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 24 | 4AM to 5AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
June | 24 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 24 | 6AM to 7AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 24 | 7AM to 8AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
June | 24 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 24 | 9AM to 10AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
June | 24 | 10AM to 11AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 24 | 11AM to 12PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
June | 24 | 12PM to 1PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 24 | 1PM to 2PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
June | 24 | 2PM to 3PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 24 | 3PM to 4PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
June | 24 | 4PM to 5PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 24 | 5PM to 6PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 24 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 24 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 24 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 24 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 24 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 24 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 25 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 2AM to 3AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 25 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 25 | 4AM to 5AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 25 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 25 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 25 | 8AM to 9AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 25 | 9AM to 10AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 25 | 10AM to 11AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 25 | 11AM to 12PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 25 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 25 | 1PM to 2PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 25 | 2PM to 3PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 25 | 3PM to 4PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
June | 25 | 4PM to 5PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
June | 25 | 5PM to 6PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 25 | 6PM to 7PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 25 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 25 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 25 | 10PM to 11PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
June | 25 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 26 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 26 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 26 | 2AM to 3AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 26 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
June | 26 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
June | 26 | 5AM to 6AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
June | 26 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 26 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 26 | 8AM to 9AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 26 | 9AM to 10AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 26 | 10AM to 11AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 26 | 11AM to 12PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 26 | 12PM to 1PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 26 | 1PM to 2PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 26 | 2PM to 3PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 26 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 26 | 4PM to 5PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
June | 26 | 5PM to 6PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 26 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 26 | 7PM to 8PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 26 | 8PM to 9PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 26 | 9PM to 10PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 26 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 26 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 27 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
June | 27 | 1AM to 2AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 27 | 2AM to 3AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 27 | 3AM to 4AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 27 | 4AM to 5AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 27 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 27 | 6AM to 7AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 27 | 7AM to 8AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 27 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 27 | 9AM to 10AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 27 | 10AM to 11AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
June | 27 | 11AM to 12PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
June | 27 | 12PM to 1PM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
June | 27 | 1PM to 2PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
June | 27 | 2PM to 3PM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
June | 27 | 3PM to 4PM | 68 | 56 | 46.9 | 47.8 | 23.76 | 0.0749 | 0.32 | 13.45 | 0
June | 27 | 4PM to 5PM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
June | 27 | 5PM to 6PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
June | 27 | 6PM to 7PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
June | 27 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 27 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
June | 27 | 9PM to 10PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 27 | 10PM to 11PM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
June | 27 | 11PM to 12AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
June | 28 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
June | 28 | 5AM to 6AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
June | 28 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 28 | 7AM to 8AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
June | 28 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
June | 28 | 9AM to 10AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
June | 28 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
June | 28 | 11AM to 12PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
June | 28 | 12PM to 1PM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
June | 28 | 1PM to 2PM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
June | 28 | 2PM to 3PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
June | 28 | 3PM to 4PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
June | 28 | 4PM to 5PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
June | 28 | 5PM to 6PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
June | 28 | 6PM to 7PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
June | 28 | 7PM to 8PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 28 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
June | 28 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 28 | 10PM to 11PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
June | 28 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 29 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
June | 29 | 1AM to 2AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 29 | 2AM to 3AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
June | 29 | 3AM to 4AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
June | 29 | 4AM to 5AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
June | 29 | 5AM to 6AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 29 | 6AM to 7AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
June | 29 | 7AM to 8AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
June | 29 | 8AM to 9AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
June | 29 | 9AM to 10AM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
June | 29 | 10AM to 11AM | 80.1 | 62.7 | 52 | 57.8 | 28.26 | 0.0731 | 0.39 | 13.78 | 0
June | 29 | 11AM to 12PM | 82 | 64.9 | 55 | 64.7 | 29.84 | 0.0728 | 0.44 | 13.86 | 0
June | 29 | 12PM to 1PM | 84 | 65 | 54 | 62.2 | 29.92 | 0.0726 | 0.42 | 13.9 | 0
June | 29 | 1PM to 2PM | 81 | 63.1 | 52 | 57.8 | 28.48 | 0.073 | 0.39 | 13.81 | 0
June | 29 | 2PM to 3PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
June | 29 | 3PM to 4PM | 77 | 61.7 | 52 | 57.8 | 27.52 | 0.0736 | 0.39 | 13.71 | 0
June | 29 | 4PM to 5PM | 75.9 | 60.4 | 50 | 53.6 | 26.61 | 0.0737 | 0.36 | 13.67 | 0
June | 29 | 5PM to 6PM | 73.9 | 59.6 | 50 | 53.6 | 26.13 | 0.074 | 0.36 | 13.62 | 0
June | 29 | 6PM to 7PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
June | 29 | 7PM to 8PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
June | 29 | 8PM to 9PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
June | 29 | 9PM to 10PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
June | 29 | 10PM to 11PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 29 | 11PM to 12AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 30 | 12AM to 1AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 30 | 1AM to 2AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
June | 30 | 2AM to 3AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
June | 30 | 3AM to 4AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
June | 30 | 4AM to 5AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
June | 30 | 5AM to 6AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
June | 30 | 6AM to 7AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
June | 30 | 7AM to 8AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
June | 30 | 8AM to 9AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
June | 30 | 9AM to 10AM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
June | 30 | 10AM to 11AM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
June | 30 | 11AM to 12PM | 82 | 63.9 | 53.1 | 60.1 | 29.12 | 0.0729 | 0.41 | 13.84 | 0
June | 30 | 12PM to 1PM | 90 | 67.4 | 55 | 64.7 | 31.77 | 0.0718 | 0.44 | 14.06 | 0
June | 30 | 1PM to 2PM | 91 | 67.8 | 55 | 64.7 | 32.03 | 0.0716 | 0.44 | 14.09 | 0
June | 30 | 2PM to 3PM | 86 | 65.7 | 54 | 62.2 | 30.41 | 0.0723 | 0.42 | 13.95 | 0
June | 30 | 3PM to 4PM | 82.9 | 64.2 | 53.1 | 60.1 | 29.34 | 0.0727 | 0.41 | 13.87 | 0
June | 30 | 4PM to 5PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
June | 30 | 5PM to 6PM | 78.1 | 62.6 | 53.1 | 60.1 | 28.15 | 0.0734 | 0.41 | 13.74 | 0
June | 30 | 6PM to 7PM | 77 | 61.7 | 52 | 57.8 | 27.52 | 0.0736 | 0.39 | 13.71 | 0
June | 30 | 7PM to 8PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
June | 30 | 8PM to 9PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
June | 30 | 9PM to 10PM | 63.1 | 56 | 50.9 | 55.5 | 23.79 | 0.0755 | 0.37 | 13.35 | 0
June | 30 | 10PM to 11PM | 61.2 | 54.7 | 50 | 53.6 | 23.02 | 0.0758 | 0.36 | 13.29 | 0
June | 30 | 11PM to 12AM | 59.4 | 53.4 | 48.9 | 51.5 | 22.24 | 0.0761 | 0.35 | 13.24 | 0
July | 1 | 12AM to 1AM | 57.6 | 52.2 | 48 | 49.8 | 21.54 | 0.0764 | 0.34 | 13.19 | 0
July | 1 | 1AM to 2AM | 55.8 | 50.9 | 46.9 | 47.8 | 20.79 | 0.0767 | 0.32 | 13.13 | 0
July | 1 | 2AM to 3AM | 53.8 | 49.6 | 46 | 46.1 | 20.06 | 0.077 | 0.31 | 13.08 | 0
July | 1 | 3AM to 4AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
July | 1 | 4AM to 5AM | 53.2 | 49 | 45.3 | 44.9 | 19.73 | 0.0771 | 0.3 | 13.06 | 0
July | 1 | 5AM to 6AM | 54.7 | 49.9 | 45.9 | 45.8 | 20.23 | 0.0768 | 0.31 | 13.1 | 0
July | 1 | 6AM to 7AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
July | 1 | 7AM to 8AM | 59 | 52 | 46.2 | 46.5 | 21.38 | 0.0762 | 0.31 | 13.21 | 0
July | 1 | 8AM to 9AM | 61.9 | 53 | 45.9 | 45.8 | 21.98 | 0.0758 | 0.31 | 13.28 | 0
July | 1 | 9AM to 10AM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
July | 1 | 10AM to 11AM | 64.6 | 54 | 45.7 | 45.5 | 22.58 | 0.0754 | 0.31 | 13.35 | 0
July | 1 | 11AM to 12PM | 64.4 | 54.1 | 46 | 46.1 | 22.64 | 0.0754 | 0.31 | 13.35 | 0
July | 1 | 12PM to 1PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
July | 1 | 1PM to 2PM | 64 | 54.1 | 46.2 | 46.5 | 22.6 | 0.0755 | 0.31 | 13.34 | 0
July | 1 | 2PM to 3PM | 64 | 54.1 | 46.2 | 46.5 | 22.6 | 0.0755 | 0.31 | 13.34 | 0
July | 1 | 3PM to 4PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
July | 1 | 4PM to 5PM | 61.7 | 53.4 | 46.9 | 47.8 | 22.23 | 0.0758 | 0.32 | 13.29 | 0
July | 1 | 5PM to 6PM | 59.4 | 52.7 | 47.5 | 48.8 | 21.82 | 0.0761 | 0.33 | 13.23 | 0
July | 1 | 6PM to 7PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
July | 1 | 7PM to 8PM | 56.3 | 51.7 | 48 | 49.8 | 21.23 | 0.0766 | 0.34 | 13.15 | 0
July | 1 | 8PM to 9PM | 55.8 | 51.3 | 47.7 | 49.1 | 21 | 0.0766 | 0.33 | 13.14 | 0
July | 1 | 9PM to 10PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
July | 1 | 10PM to 11PM | 55 | 50.7 | 47.1 | 48.1 | 20.67 | 0.0768 | 0.33 | 13.12 | 0
July | 1 | 11PM to 12AM | 55 | 50.5 | 46.8 | 47.4 | 20.56 | 0.0768 | 0.32 | 13.12 | 0
July | 2 | 12AM to 1AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
July | 2 | 1AM to 2AM | 54.7 | 50.1 | 46.2 | 46.5 | 20.33 | 0.0768 | 0.31 | 13.1 | 0
July | 2 | 2AM to 3AM | 54.3 | 49.7 | 45.7 | 45.5 | 20.09 | 0.0769 | 0.31 | 13.09 | 0
July | 2 | 3AM to 4AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
July | 2 | 4AM to 5AM | 55.2 | 49.9 | 45.3 | 44.9 | 20.21 | 0.0768 | 0.3 | 13.11 | 0
July | 2 | 5AM to 6AM | 56.7 | 50.8 | 45.9 | 45.8 | 20.71 | 0.0765 | 0.31 | 13.15 | 0
July | 2 | 6AM to 7AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
July | 2 | 7AM to 8AM | 60.6 | 52.5 | 45.9 | 45.8 | 21.67 | 0.076 | 0.31 | 13.25 | 0
July | 2 | 8AM to 9AM | 63.3 | 53.4 | 45.3 | 44.9 | 22.18 | 0.0756 | 0.3 | 13.32 | 0
July | 2 | 9AM to 10AM | 66 | 53.9 | 44.1 | 42.8 | 22.51 | 0.0752 | 0.29 | 13.38 | 0
July | 2 | 10AM to 11AM | 66.7 | 54.2 | 44.1 | 42.8 | 22.68 | 0.0751 | 0.29 | 13.4 | 0
July | 2 | 11AM to 12PM | 67.3 | 54.3 | 43.7 | 42.2 | 22.72 | 0.075 | 0.29 | 13.41 | 0
July | 2 | 12PM to 1PM | 68 | 54.3 | 43 | 41 | 22.71 | 0.0749 | 0.28 | 13.43 | 0
July | 2 | 1PM to 2PM | 66.7 | 54.7 | 45.1 | 44.6 | 22.96 | 0.0751 | 0.3 | 13.4 | 0
July | 2 | 2PM to 3PM | 65.3 | 55 | 47.1 | 48.1 | 23.16 | 0.0753 | 0.33 | 13.38 | 0
July | 2 | 3PM to 4PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
July | 2 | 4PM to 5PM | 61.7 | 54.8 | 49.8 | 53.3 | 23.09 | 0.0757 | 0.36 | 13.3 | 0
July | 2 | 5PM to 6PM | 59.4 | 54.3 | 50.5 | 54.7 | 22.75 | 0.0761 | 0.37 | 13.25 | 0
July | 2 | 6PM to 7PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
July | 2 | 7PM to 8PM | 56.3 | 52.9 | 50.4 | 54.4 | 21.95 | 0.0765 | 0.37 | 13.17 | 0
July | 2 | 8PM to 9PM | 55.8 | 52.2 | 49.5 | 52.6 | 21.53 | 0.0766 | 0.36 | 13.15 | 0
July | 2 | 9PM to 10PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
July | 2 | 10PM to 11PM | 55 | 51.5 | 48.7 | 51.1 | 21.14 | 0.0767 | 0.35 | 13.13 | 0
July | 2 | 11PM to 12AM | 55 | 51.7 | 49.1 | 51.8 | 21.25 | 0.0767 | 0.35 | 13.13 | 0
July | 3 | 12AM to 1AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
July | 3 | 1AM to 2AM | 55.4 | 52 | 49.5 | 52.6 | 21.45 | 0.0767 | 0.36 | 13.14 | 0
July | 3 | 2AM to 3AM | 55.6 | 52 | 49.3 | 52.2 | 21.43 | 0.0767 | 0.35 | 13.14 | 0
July | 3 | 3AM to 4AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 3 | 4AM to 5AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 3 | 5AM to 6AM | 55.9 | 52.1 | 49.1 | 51.8 | 21.47 | 0.0766 | 0.35 | 13.15 | 0
July | 3 | 6AM to 7AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 3 | 7AM to 8AM | 57 | 52.9 | 49.8 | 53.3 | 21.95 | 0.0764 | 0.36 | 13.18 | 0
July | 3 | 8AM to 9AM | 57.9 | 53.5 | 50.2 | 54 | 22.28 | 0.0763 | 0.37 | 13.21 | 0
July | 3 | 9AM to 10AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
July | 3 | 10AM to 11AM | 60.1 | 54.7 | 50.7 | 55.1 | 22.98 | 0.076 | 0.37 | 13.27 | 0
July | 3 | 11AM to 12PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
July | 3 | 12PM to 1PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
July | 3 | 1PM to 2PM | 61.7 | 55.6 | 51.3 | 56.2 | 23.55 | 0.0757 | 0.38 | 13.31 | 0
July | 3 | 2PM to 3PM | 61.3 | 55.4 | 51.3 | 56.2 | 23.46 | 0.0758 | 0.38 | 13.3 | 0
July | 3 | 3PM to 4PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
July | 3 | 4PM to 5PM | 59.7 | 54.8 | 51.3 | 56.2 | 23.07 | 0.076 | 0.38 | 13.26 | 0
July | 3 | 5PM to 6PM | 58.3 | 54.2 | 51.3 | 56.2 | 22.72 | 0.0762 | 0.38 | 13.22 | 0
July | 3 | 6PM to 7PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
July | 3 | 7PM to 8PM | 56.3 | 53.3 | 51.1 | 55.9 | 22.18 | 0.0765 | 0.38 | 13.17 | 0
July | 3 | 8PM to 9PM | 55.8 | 52.9 | 50.7 | 55.1 | 21.93 | 0.0766 | 0.37 | 13.16 | 0
July | 3 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 3 | 10PM to 11PM | 54.7 | 52 | 50 | 53.6 | 21.44 | 0.0768 | 0.36 | 13.12 | 0
July | 3 | 11PM to 12AM | 54.3 | 51.7 | 49.6 | 52.9 | 21.24 | 0.0768 | 0.36 | 13.11 | 0
July | 4 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
July | 4 | 1AM to 2AM | 54.3 | 51.8 | 49.8 | 53.3 | 21.29 | 0.0768 | 0.36 | 13.11 | 0
July | 4 | 2AM to 3AM | 54.7 | 52 | 50 | 53.6 | 21.44 | 0.0768 | 0.36 | 13.12 | 0
July | 4 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 4 | 4AM to 5AM | 55.8 | 52.7 | 50.4 | 54.4 | 21.82 | 0.0766 | 0.37 | 13.15 | 0
July | 4 | 5AM to 6AM | 56.3 | 53.2 | 50.9 | 55.5 | 22.12 | 0.0765 | 0.37 | 13.17 | 0
July | 4 | 6AM to 7AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
July | 4 | 7AM to 8AM | 59.4 | 55.3 | 52.5 | 58.9 | 23.4 | 0.0761 | 0.4 | 13.26 | 0
July | 4 | 8AM to 9AM | 61.7 | 56.8 | 53.6 | 61.4 | 24.35 | 0.0757 | 0.41 | 13.33 | 0
July | 4 | 9AM to 10AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
July | 4 | 10AM to 11AM | 65.3 | 59 | 55 | 64.7 | 25.75 | 0.0752 | 0.44 | 13.43 | 0
July | 4 | 11AM to 12PM | 66.7 | 59.8 | 55.6 | 66 | 26.31 | 0.0749 | 0.45 | 13.47 | 0
July | 4 | 12PM to 1PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
July | 4 | 1PM to 2PM | 67.3 | 60.1 | 55.8 | 66.5 | 26.51 | 0.0749 | 0.45 | 13.48 | 0
July | 4 | 2PM to 3PM | 66.7 | 59.8 | 55.6 | 66 | 26.31 | 0.0749 | 0.45 | 13.47 | 0
July | 4 | 3PM to 4PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
July | 4 | 4PM to 5PM | 64 | 58.4 | 54.9 | 64.3 | 25.38 | 0.0753 | 0.43 | 13.4 | 0
July | 4 | 5PM to 6PM | 62.1 | 57.5 | 54.5 | 63.5 | 24.76 | 0.0756 | 0.43 | 13.34 | 0
July | 4 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
July | 4 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
July | 4 | 8PM to 9PM | 60.1 | 56.3 | 53.8 | 61.8 | 24.02 | 0.0759 | 0.42 | 13.29 | 0
July | 4 | 9PM to 10PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
July | 4 | 10PM to 11PM | 58.5 | 55.2 | 52.9 | 59.7 | 23.31 | 0.0762 | 0.4 | 13.24 | 0
July | 4 | 11PM to 12AM | 56.7 | 54 | 52.2 | 58.2 | 22.62 | 0.0765 | 0.39 | 13.19 | 0
July | 5 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 5 | 1AM to 2AM | 54.3 | 52.6 | 51.3 | 56.2 | 21.75 | 0.0768 | 0.38 | 13.12 | 0
July | 5 | 2AM to 3AM | 53.8 | 52 | 50.7 | 55.1 | 21.45 | 0.0769 | 0.37 | 13.11 | 0
July | 5 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
July | 5 | 4AM to 5AM | 54 | 51.9 | 50.4 | 54.4 | 21.38 | 0.0769 | 0.37 | 13.11 | 0
July | 5 | 5AM to 6AM | 55 | 52.7 | 50.9 | 55.5 | 21.81 | 0.0767 | 0.37 | 13.14 | 0
July | 5 | 6AM to 7AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 5 | 7AM to 8AM | 57.9 | 54.3 | 51.6 | 57 | 22.75 | 0.0763 | 0.39 | 13.22 | 0
July | 5 | 8AM to 9AM | 60.1 | 55.1 | 51.6 | 57 | 23.28 | 0.076 | 0.39 | 13.27 | 0
July | 5 | 9AM to 10AM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
July | 5 | 10AM to 11AM | 62.4 | 56.2 | 51.8 | 57.4 | 23.91 | 0.0756 | 0.39 | 13.33 | 0
July | 5 | 11AM to 12PM | 62.6 | 56.3 | 52 | 57.8 | 24.01 | 0.0756 | 0.39 | 13.34 | 0
July | 5 | 12PM to 1PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
July | 5 | 1PM to 2PM | 62.6 | 56.4 | 52.2 | 58.2 | 24.07 | 0.0756 | 0.39 | 13.34 | 0
July | 5 | 2PM to 3PM | 62.4 | 56.3 | 52.2 | 58.2 | 24.03 | 0.0756 | 0.39 | 13.34 | 0
July | 5 | 3PM to 4PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
July | 5 | 4PM to 5PM | 61.3 | 55.5 | 51.4 | 56.6 | 23.52 | 0.0758 | 0.38 | 13.3 | 0
July | 5 | 5PM to 6PM | 60.8 | 55 | 50.9 | 55.5 | 23.22 | 0.0759 | 0.37 | 13.29 | 0
July | 5 | 6PM to 7PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
July | 5 | 7PM to 8PM | 59.7 | 54.1 | 50 | 53.6 | 22.67 | 0.076 | 0.36 | 13.25 | 0
July | 5 | 8PM to 9PM | 59.4 | 53.8 | 49.6 | 52.9 | 22.47 | 0.0761 | 0.36 | 13.24 | 0
July | 5 | 9PM to 10PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
July | 5 | 10PM to 11PM | 57.9 | 53 | 49.3 | 52.2 | 22 | 0.0763 | 0.35 | 13.2 | 0
July | 5 | 11PM to 12AM | 57 | 52.6 | 49.3 | 52.2 | 21.79 | 0.0764 | 0.35 | 13.18 | 0
July | 6 | 12AM to 1AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 6 | 1AM to 2AM | 55.6 | 51.9 | 49.1 | 51.8 | 21.38 | 0.0767 | 0.35 | 13.14 | 0
July | 6 | 2AM to 3AM | 55.4 | 51.7 | 48.7 | 51.1 | 21.23 | 0.0767 | 0.35 | 13.14 | 0
July | 6 | 3AM to 4AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
July | 6 | 4AM to 5AM | 55.9 | 51.9 | 48.7 | 51.1 | 21.36 | 0.0766 | 0.35 | 13.15 | 0
July | 6 | 5AM to 6AM | 57 | 52.7 | 49.5 | 52.6 | 21.84 | 0.0764 | 0.36 | 13.18 | 0
July | 6 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
July | 6 | 7AM to 8AM | 59.5 | 54.5 | 50.9 | 55.5 | 22.91 | 0.076 | 0.37 | 13.25 | 0
July | 6 | 8AM to 9AM | 61.3 | 55.4 | 51.3 | 56.2 | 23.46 | 0.0758 | 0.38 | 13.3 | 0
July | 6 | 9AM to 10AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
July | 6 | 10AM to 11AM | 64.9 | 57.1 | 51.8 | 57.4 | 24.52 | 0.0753 | 0.39 | 13.4 | 0
July | 6 | 11AM to 12PM | 67.1 | 58.1 | 52 | 57.8 | 25.11 | 0.0749 | 0.39 | 13.45 | 0
July | 6 | 12PM to 1PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
July | 6 | 1PM to 2PM | 68.4 | 58.8 | 52.5 | 58.9 | 25.6 | 0.0748 | 0.4 | 13.49 | 0
July | 6 | 2PM to 3PM | 67.6 | 58.7 | 52.9 | 59.7 | 25.55 | 0.0749 | 0.4 | 13.47 | 0
July | 6 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
July | 6 | 4PM to 5PM | 64.6 | 57.8 | 53.2 | 60.6 | 24.93 | 0.0753 | 0.41 | 13.4 | 0
July | 6 | 5PM to 6PM | 62.4 | 56.9 | 53.2 | 60.6 | 24.4 | 0.0756 | 0.41 | 13.34 | 0
July | 6 | 6PM to 7PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
July | 6 | 7PM to 8PM | 59.7 | 56 | 53.4 | 61 | 23.8 | 0.076 | 0.41 | 13.27 | 0
July | 6 | 8PM to 9PM | 59.4 | 55.8 | 53.4 | 61 | 23.72 | 0.076 | 0.41 | 13.27 | 0
July | 6 | 9PM to 10PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
July | 6 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 6 | 11PM to 12AM | 57 | 54.5 | 52.7 | 59.3 | 22.89 | 0.0764 | 0.4 | 13.2 | 0
July | 7 | 12AM to 1AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
July | 7 | 1AM to 2AM | 55.2 | 53.2 | 51.8 | 57.4 | 22.15 | 0.0767 | 0.39 | 13.15 | 0
July | 7 | 2AM to 3AM | 54.7 | 52.6 | 51.1 | 55.9 | 21.78 | 0.0768 | 0.38 | 13.13 | 0
July | 7 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 7 | 4AM to 5AM | 55 | 52.4 | 50.4 | 54.4 | 21.64 | 0.0767 | 0.37 | 13.14 | 0
July | 7 | 5AM to 6AM | 55.9 | 53 | 50.9 | 55.5 | 22.03 | 0.0766 | 0.37 | 13.16 | 0
July | 7 | 6AM to 7AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
July | 7 | 7AM to 8AM | 57.7 | 54.4 | 52 | 57.8 | 22.83 | 0.0763 | 0.39 | 13.21 | 0
July | 7 | 8AM to 9AM | 58.3 | 54.7 | 52.2 | 58.2 | 23.02 | 0.0762 | 0.39 | 13.23 | 0
July | 7 | 9AM to 10AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
July | 7 | 10AM to 11AM | 61 | 56.1 | 52.7 | 59.3 | 23.86 | 0.0758 | 0.4 | 13.3 | 0
July | 7 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
July | 7 | 12PM to 1PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
July | 7 | 1PM to 2PM | 65.3 | 58 | 53.2 | 60.6 | 25.1 | 0.0752 | 0.41 | 13.42 | 0
July | 7 | 2PM to 3PM | 65.7 | 58.2 | 53.2 | 60.6 | 25.19 | 0.0751 | 0.41 | 13.43 | 0
July | 7 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 7 | 4PM to 5PM | 64 | 57.7 | 53.6 | 61.4 | 24.92 | 0.0754 | 0.41 | 13.39 | 0
July | 7 | 5PM to 6PM | 62.1 | 57.1 | 53.8 | 61.8 | 24.5 | 0.0756 | 0.42 | 13.34 | 0
July | 7 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
July | 7 | 7PM to 8PM | 60.1 | 56.6 | 54.3 | 63 | 24.21 | 0.0759 | 0.43 | 13.29 | 0
July | 7 | 8PM to 9PM | 60.1 | 56.6 | 54.3 | 63 | 24.21 | 0.0759 | 0.43 | 13.29 | 0
July | 7 | 9PM to 10PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
July | 7 | 10PM to 11PM | 59.4 | 56.2 | 54.1 | 62.6 | 23.97 | 0.076 | 0.42 | 13.27 | 0
July | 7 | 11PM to 12AM | 58.6 | 55.7 | 53.8 | 61.8 | 23.67 | 0.0761 | 0.42 | 13.25 | 0
July | 8 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 8 | 1AM to 2AM | 57.6 | 55.2 | 53.6 | 61.4 | 23.34 | 0.0763 | 0.41 | 13.22 | 0
July | 8 | 2AM to 3AM | 57.4 | 55 | 53.4 | 61 | 23.23 | 0.0763 | 0.41 | 13.22 | 0
July | 8 | 3AM to 4AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
July | 8 | 4AM to 5AM | 57.4 | 55 | 53.4 | 61 | 23.23 | 0.0763 | 0.41 | 13.22 | 0
July | 8 | 5AM to 6AM | 57.6 | 55.3 | 53.8 | 61.8 | 23.4 | 0.0763 | 0.42 | 13.22 | 0
July | 8 | 6AM to 7AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
July | 8 | 7AM to 8AM | 59.4 | 56.4 | 54.5 | 63.5 | 24.1 | 0.076 | 0.43 | 13.27 | 0
July | 8 | 8AM to 9AM | 60.6 | 56.9 | 54.5 | 63.5 | 24.41 | 0.0758 | 0.43 | 13.31 | 0
July | 8 | 9AM to 10AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
July | 8 | 10AM to 11AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0753 | 0.44 | 13.41 | 0
July | 8 | 11AM to 12PM | 66.7 | 60.2 | 56.3 | 67.8 | 26.58 | 0.0749 | 0.46 | 13.48 | 0
July | 8 | 12PM to 1PM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
July | 8 | 1PM to 2PM | 69.1 | 61.6 | 57.2 | 70.1 | 27.51 | 0.0746 | 0.47 | 13.54 | 0
July | 8 | 2PM to 3PM | 69.1 | 61.6 | 57.2 | 70.1 | 27.51 | 0.0746 | 0.47 | 13.54 | 0
July | 8 | 3PM to 4PM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
July | 8 | 4PM to 5PM | 67.6 | 60.9 | 56.8 | 69.2 | 27.01 | 0.0748 | 0.47 | 13.5 | 0
July | 8 | 5PM to 6PM | 66.4 | 60.2 | 56.5 | 68.3 | 26.56 | 0.075 | 0.46 | 13.47 | 0
July | 8 | 6PM to 7PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
July | 8 | 7PM to 8PM | 63.3 | 58.4 | 55.2 | 65.2 | 25.34 | 0.0754 | 0.44 | 13.38 | 0
July | 8 | 8PM to 9PM | 61.7 | 57.2 | 54.3 | 63 | 24.61 | 0.0757 | 0.43 | 13.33 | 0
July | 8 | 9PM to 10PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
July | 8 | 10PM to 11PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
July | 8 | 11PM to 12AM | 58.1 | 54.9 | 52.7 | 59.3 | 23.16 | 0.0762 | 0.4 | 13.23 | 0
July | 9 | 12AM to 1AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
July | 9 | 1AM to 2AM | 56.7 | 54 | 52.2 | 58.2 | 22.62 | 0.0765 | 0.39 | 13.19 | 0
July | 9 | 2AM to 3AM | 56.3 | 53.7 | 51.8 | 57.4 | 22.41 | 0.0765 | 0.39 | 13.18 | 0
July | 9 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 9 | 4AM to 5AM | 56.3 | 53.5 | 51.4 | 56.6 | 22.3 | 0.0765 | 0.38 | 13.17 | 0
July | 9 | 5AM to 6AM | 56.7 | 53.8 | 51.8 | 57.4 | 22.5 | 0.0765 | 0.39 | 13.19 | 0
July | 9 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
July | 9 | 7AM to 8AM | 58.3 | 55.1 | 52.9 | 59.7 | 23.26 | 0.0762 | 0.4 | 13.23 | 0
July | 9 | 8AM to 9AM | 59.7 | 55.9 | 53.2 | 60.6 | 23.74 | 0.076 | 0.41 | 13.27 | 0
July | 9 | 9AM to 10AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
July | 9 | 10AM to 11AM | 62.6 | 56.9 | 53.1 | 60.1 | 24.38 | 0.0756 | 0.41 | 13.35 | 0
July | 9 | 11AM to 12PM | 64.4 | 57.4 | 52.7 | 59.3 | 24.69 | 0.0753 | 0.4 | 13.39 | 0
July | 9 | 12PM to 1PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
July | 9 | 1PM to 2PM | 66 | 57.6 | 51.8 | 57.4 | 24.78 | 0.0751 | 0.39 | 13.43 | 0
July | 9 | 2PM to 3PM | 66 | 57.5 | 51.6 | 57 | 24.72 | 0.0751 | 0.39 | 13.42 | 0
July | 9 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
July | 9 | 4PM to 5PM | 64.4 | 56.5 | 50.9 | 55.5 | 24.09 | 0.0753 | 0.37 | 13.38 | 0
July | 9 | 5PM to 6PM | 62.6 | 55.6 | 50.5 | 54.7 | 23.54 | 0.0756 | 0.37 | 13.33 | 0
July | 9 | 6PM to 7PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
July | 9 | 7PM to 8PM | 59.9 | 54 | 49.6 | 52.9 | 22.6 | 0.076 | 0.36 | 13.26 | 0
July | 9 | 8PM to 9PM | 59 | 53.4 | 49.1 | 51.8 | 22.21 | 0.0761 | 0.35 | 13.23 | 0
July | 9 | 9PM to 10PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
July | 9 | 10PM to 11PM | 57.2 | 52.3 | 48.4 | 50.4 | 21.56 | 0.0764 | 0.34 | 13.18 | 0
July | 9 | 11PM to 12AM | 56.7 | 52 | 48.4 | 50.4 | 21.43 | 0.0765 | 0.34 | 13.17 | 0
July | 10 | 12AM to 1AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
July | 10 | 1AM to 2AM | 55.2 | 51.5 | 48.6 | 50.8 | 21.13 | 0.0767 | 0.34 | 13.13 | 0
July | 10 | 2AM to 3AM | 54.7 | 51.2 | 48.4 | 50.4 | 20.94 | 0.0768 | 0.34 | 13.11 | 0
July | 10 | 3AM to 4AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
July | 10 | 4AM to 5AM | 55.6 | 51.4 | 48 | 49.8 | 21.06 | 0.0767 | 0.34 | 13.14 | 0
July | 10 | 5AM to 6AM | 57.4 | 52.2 | 48.2 | 50.1 | 21.55 | 0.0764 | 0.34 | 13.18 | 0
July | 10 | 6AM to 7AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
July | 10 | 7AM to 8AM | 62.4 | 54.9 | 49.3 | 52.2 | 23.1 | 0.0756 | 0.35 | 13.32 | 0
July | 10 | 8AM to 9AM | 65.7 | 56.4 | 49.8 | 53.3 | 24.05 | 0.0752 | 0.36 | 13.4 | 0
July | 10 | 9AM to 10AM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
July | 10 | 10AM to 11AM | 68.4 | 57.9 | 50.7 | 55.1 | 25 | 0.0748 | 0.37 | 13.48 | 0
July | 10 | 11AM to 12PM | 67.6 | 57.8 | 51.1 | 55.9 | 24.94 | 0.0749 | 0.38 | 13.46 | 0
July | 10 | 12PM to 1PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
July | 10 | 1PM to 2PM | 66.6 | 57.5 | 51.3 | 56.2 | 24.74 | 0.075 | 0.38 | 13.44 | 0
July | 10 | 2PM to 3PM | 66.4 | 57.4 | 51.3 | 56.2 | 24.69 | 0.0751 | 0.38 | 13.43 | 0
July | 10 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
July | 10 | 4PM to 5PM | 64.9 | 56.3 | 50.2 | 54 | 23.99 | 0.0753 | 0.37 | 13.39 | 0
July | 10 | 5PM to 6PM | 64 | 55.5 | 49.3 | 52.2 | 23.49 | 0.0754 | 0.35 | 13.36 | 0
July | 10 | 6PM to 7PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
July | 10 | 7PM to 8PM | 62.1 | 54.3 | 48.4 | 50.4 | 22.74 | 0.0757 | 0.34 | 13.3 | 0
July | 10 | 8PM to 9PM | 61 | 53.8 | 48.4 | 50.4 | 22.48 | 0.0759 | 0.34 | 13.28 | 0
July | 10 | 9PM to 10PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
July | 10 | 10PM to 11PM | 59.4 | 53.3 | 48.7 | 51.1 | 22.19 | 0.0761 | 0.35 | 13.24 | 0
July | 10 | 11PM to 12AM | 58.6 | 53.2 | 49.1 | 51.8 | 22.12 | 0.0762 | 0.35 | 13.22 | 0
July | 11 | 12AM to 1AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
July | 11 | 1AM to 2AM | 57.2 | 53 | 49.8 | 53.3 | 22 | 0.0764 | 0.36 | 13.19 | 0
July | 11 | 2AM to 3AM | 56.7 | 52.9 | 50 | 53.6 | 21.92 | 0.0765 | 0.36 | 13.17 | 0
July | 11 | 3AM to 4AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
July | 11 | 4AM to 5AM | 56.7 | 53.4 | 51.1 | 55.9 | 22.27 | 0.0765 | 0.38 | 13.18 | 0
July | 11 | 5AM to 6AM | 57.2 | 54.3 | 52.2 | 58.2 | 22.75 | 0.0764 | 0.39 | 13.2 | 0
July | 11 | 6AM to 7AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 11 | 7AM to 8AM | 60.3 | 56.8 | 54.5 | 63.5 | 24.32 | 0.0759 | 0.43 | 13.3 | 0
July | 11 | 8AM to 9AM | 62.6 | 58.3 | 55.6 | 66 | 25.3 | 0.0755 | 0.45 | 13.36 | 0
July | 11 | 9AM to 10AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
July | 11 | 10AM to 11AM | 66 | 60.2 | 56.7 | 68.7 | 26.55 | 0.075 | 0.46 | 13.46 | 0
July | 11 | 11AM to 12PM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
July | 11 | 12PM to 1PM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
July | 11 | 1PM to 2PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.51 | 0
July | 11 | 2PM to 3PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.51 | 0
July | 11 | 3PM to 4PM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
July | 11 | 4PM to 5PM | 65.7 | 59.7 | 56.1 | 67.4 | 26.25 | 0.0751 | 0.45 | 13.45 | 0
July | 11 | 5PM to 6PM | 63.3 | 58.4 | 55.2 | 65.2 | 25.34 | 0.0754 | 0.44 | 13.38 | 0
July | 11 | 6PM to 7PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
July | 11 | 7PM to 8PM | 59.7 | 56.1 | 53.6 | 61.4 | 23.87 | 0.076 | 0.41 | 13.28 | 0
July | 11 | 8PM to 9PM | 58.3 | 55.2 | 53.1 | 60.1 | 23.33 | 0.0762 | 0.41 | 13.24 | 0
July | 11 | 9PM to 10PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
July | 11 | 10PM to 11PM | 57 | 54.5 | 52.7 | 59.3 | 22.89 | 0.0764 | 0.4 | 13.2 | 0
July | 11 | 11PM to 12AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
July | 12 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
July | 12 | 1AM to 2AM | 57.4 | 55.1 | 53.6 | 61.4 | 23.3 | 0.0763 | 0.41 | 13.22 | 0
July | 12 | 2AM to 3AM | 57.6 | 55.1 | 53.4 | 61 | 23.28 | 0.0763 | 0.41 | 13.22 | 0
July | 12 | 3AM to 4AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 12 | 4AM to 5AM | 57.6 | 54.7 | 52.7 | 59.3 | 23.03 | 0.0763 | 0.4 | 13.21 | 0
July | 12 | 5AM to 6AM | 57.4 | 54.5 | 52.5 | 58.9 | 22.92 | 0.0763 | 0.4 | 13.21 | 0
July | 12 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
July | 12 | 7AM to 8AM | 59.4 | 55.7 | 53.2 | 60.6 | 23.65 | 0.076 | 0.41 | 13.26 | 0
July | 12 | 8AM to 9AM | 61.7 | 56.9 | 53.8 | 61.8 | 24.41 | 0.0757 | 0.42 | 13.33 | 0
July | 12 | 9AM to 10AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
July | 12 | 10AM to 11AM | 69.4 | 60.7 | 55.4 | 65.6 | 26.9 | 0.0746 | 0.44 | 13.54 | 0
July | 12 | 11AM to 12PM | 74.7 | 63 | 56.3 | 67.8 | 28.52 | 0.0738 | 0.46 | 13.68 | 0
July | 12 | 12PM to 1PM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
July | 12 | 1PM to 2PM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
July | 12 | 2PM to 3PM | 74.1 | 61.9 | 54.5 | 63.5 | 27.7 | 0.0739 | 0.43 | 13.65 | 0
July | 12 | 3PM to 4PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
July | 12 | 4PM to 5PM | 68 | 58.5 | 52.2 | 58.2 | 25.39 | 0.0748 | 0.39 | 13.48 | 0
July | 12 | 5PM to 6PM | 65.1 | 56.9 | 51.3 | 56.2 | 24.38 | 0.0752 | 0.38 | 13.4 | 0
July | 12 | 6PM to 7PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
July | 12 | 7PM to 8PM | 60.6 | 54.5 | 50 | 53.6 | 22.88 | 0.0759 | 0.36 | 13.28 | 0
July | 12 | 8PM to 9PM | 59.4 | 53.8 | 49.6 | 52.9 | 22.47 | 0.0761 | 0.36 | 13.24 | 0
July | 12 | 9PM to 10PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
July | 12 | 10PM to 11PM | 57 | 52.5 | 49.1 | 51.8 | 21.73 | 0.0764 | 0.35 | 13.18 | 0
July | 12 | 11PM to 12AM | 55.9 | 51.9 | 48.7 | 51.1 | 21.36 | 0.0766 | 0.35 | 13.15 | 0
July | 13 | 12AM to 1AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
July | 13 | 1AM to 2AM | 54.7 | 51.1 | 48.2 | 50.1 | 20.89 | 0.0768 | 0.34 | 13.11 | 0
July | 13 | 2AM to 3AM | 54.3 | 50.6 | 47.7 | 49.1 | 20.65 | 0.0769 | 0.33 | 13.1 | 0
July | 13 | 3AM to 4AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
July | 13 | 4AM to 5AM | 55.9 | 51.3 | 47.7 | 49.1 | 21.04 | 0.0766 | 0.33 | 13.14 | 0
July | 13 | 5AM to 6AM | 58.1 | 52.6 | 48.4 | 50.4 | 21.78 | 0.0763 | 0.34 | 13.2 | 0
July | 13 | 6AM to 7AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
July | 13 | 7AM to 8AM | 62.4 | 55.3 | 50.2 | 54 | 23.38 | 0.0756 | 0.37 | 13.32 | 0
July | 13 | 8AM to 9AM | 64.6 | 56.5 | 50.9 | 55.5 | 24.14 | 0.0753 | 0.37 | 13.38 | 0
July | 13 | 9AM to 10AM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
July | 13 | 10AM to 11AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
July | 13 | 11AM to 12PM | 68.9 | 58.7 | 52 | 57.8 | 25.55 | 0.0747 | 0.39 | 13.5 | 0
July | 13 | 12PM to 1PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
July | 13 | 1PM to 2PM | 68.7 | 58.6 | 51.8 | 57.4 | 25.44 | 0.0747 | 0.39 | 13.49 | 0
July | 13 | 2PM to 3PM | 67.3 | 57.9 | 51.6 | 57 | 25.03 | 0.0749 | 0.39 | 13.46 | 0
July | 13 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
July | 13 | 4PM to 5PM | 64 | 56.3 | 50.9 | 55.5 | 24 | 0.0754 | 0.37 | 13.37 | 0
July | 13 | 5PM to 6PM | 62.1 | 55.4 | 50.5 | 54.7 | 23.41 | 0.0757 | 0.37 | 13.32 | 0
July | 13 | 6PM to 7PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
July | 13 | 7PM to 8PM | 58.6 | 53.7 | 50 | 53.6 | 22.4 | 0.0762 | 0.36 | 13.23 | 0
July | 13 | 8PM to 9PM | 57.4 | 53 | 49.6 | 52.9 | 21.98 | 0.0764 | 0.36 | 13.19 | 0
July | 13 | 9PM to 10PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 13 | 10PM to 11PM | 55.6 | 52 | 49.3 | 52.2 | 21.43 | 0.0767 | 0.35 | 13.14 | 0
July | 13 | 11PM to 12AM | 55.4 | 52 | 49.3 | 52.2 | 21.39 | 0.0767 | 0.35 | 13.14 | 0
July | 14 | 12AM to 1AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
July | 14 | 1AM to 2AM | 54.3 | 51.4 | 49.1 | 51.8 | 21.07 | 0.0768 | 0.35 | 13.11 | 0
July | 14 | 2AM to 3AM | 53.8 | 51 | 48.7 | 51.1 | 20.83 | 0.0769 | 0.35 | 13.09 | 0
July | 14 | 3AM to 4AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
July | 14 | 4AM to 5AM | 55 | 51.5 | 48.7 | 51.1 | 21.14 | 0.0767 | 0.35 | 13.13 | 0
July | 14 | 5AM to 6AM | 57 | 52.7 | 49.5 | 52.6 | 21.84 | 0.0764 | 0.36 | 13.18 | 0
July | 14 | 6AM to 7AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
July | 14 | 7AM to 8AM | 61.7 | 55.6 | 51.3 | 56.2 | 23.55 | 0.0757 | 0.38 | 13.31 | 0
July | 14 | 8AM to 9AM | 64.2 | 56.9 | 51.8 | 57.4 | 24.34 | 0.0754 | 0.39 | 13.38 | 0
July | 14 | 9AM to 10AM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
July | 14 | 10AM to 11AM | 68.9 | 59.3 | 53.1 | 60.1 | 25.92 | 0.0747 | 0.41 | 13.51 | 0
July | 14 | 11AM to 12PM | 71.1 | 60.4 | 53.6 | 61.4 | 26.63 | 0.0744 | 0.41 | 13.57 | 0
July | 14 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
July | 14 | 1PM to 2PM | 72.7 | 61 | 53.8 | 61.8 | 27.09 | 0.0741 | 0.42 | 13.61 | 0
July | 14 | 2PM to 3PM | 72.3 | 60.8 | 53.6 | 61.4 | 26.94 | 0.0742 | 0.41 | 13.6 | 0
July | 14 | 3PM to 4PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
July | 14 | 4PM to 5PM | 68.9 | 58.8 | 52.2 | 58.2 | 25.61 | 0.0747 | 0.39 | 13.5 | 0
July | 14 | 5PM to 6PM | 66 | 57.3 | 51.3 | 56.2 | 24.6 | 0.0751 | 0.38 | 13.42 | 0
July | 14 | 6PM to 7PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
July | 14 | 7PM to 8PM | 61 | 54.8 | 50.4 | 54.4 | 23.09 | 0.0758 | 0.37 | 13.29 | 0
July | 14 | 8PM to 9PM | 59 | 54 | 50.4 | 54.4 | 22.6 | 0.0761 | 0.37 | 13.24 | 0
July | 14 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 14 | 10PM to 11PM | 56.7 | 53.1 | 50.4 | 54.4 | 22.03 | 0.0765 | 0.37 | 13.18 | 0
July | 14 | 11PM to 12AM | 56.3 | 52.9 | 50.4 | 54.4 | 21.95 | 0.0765 | 0.37 | 13.17 | 0
July | 15 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
July | 15 | 1AM to 2AM | 55.9 | 52.7 | 50.2 | 54 | 21.8 | 0.0766 | 0.37 | 13.16 | 0
July | 15 | 2AM to 3AM | 55.9 | 52.4 | 49.6 | 52.9 | 21.63 | 0.0766 | 0.36 | 13.15 | 0
July | 15 | 3AM to 4AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 15 | 4AM to 5AM | 56.7 | 52.5 | 49.3 | 52.2 | 21.7 | 0.0765 | 0.35 | 13.17 | 0
July | 15 | 5AM to 6AM | 57.2 | 53 | 49.8 | 53.3 | 22 | 0.0764 | 0.36 | 13.19 | 0
July | 15 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
July | 15 | 7AM to 8AM | 59.5 | 54.7 | 51.3 | 56.2 | 23.03 | 0.076 | 0.38 | 13.26 | 0
July | 15 | 8AM to 9AM | 61.3 | 55.7 | 51.8 | 57.4 | 23.64 | 0.0758 | 0.39 | 13.31 | 0
July | 15 | 9AM to 10AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
July | 15 | 10AM to 11AM | 65.7 | 58.1 | 53.1 | 60.1 | 25.13 | 0.0751 | 0.41 | 13.42 | 0
July | 15 | 11AM to 12PM | 68.4 | 59.4 | 53.6 | 61.4 | 25.97 | 0.0747 | 0.41 | 13.5 | 0
July | 15 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
July | 15 | 1PM to 2PM | 69.6 | 59.9 | 53.8 | 61.8 | 26.35 | 0.0746 | 0.42 | 13.53 | 0
July | 15 | 2PM to 3PM | 68.4 | 59.4 | 53.6 | 61.4 | 25.97 | 0.0747 | 0.41 | 13.5 | 0
July | 15 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
July | 15 | 4PM to 5PM | 64.9 | 57.5 | 52.5 | 58.9 | 24.76 | 0.0752 | 0.4 | 13.4 | 0
July | 15 | 5PM to 6PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
July | 15 | 6PM to 7PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
July | 15 | 7PM to 8PM | 59.9 | 54.8 | 51.1 | 55.9 | 23.05 | 0.076 | 0.38 | 13.26 | 0
July | 15 | 8PM to 9PM | 59 | 54.2 | 50.7 | 55.1 | 22.72 | 0.0761 | 0.37 | 13.24 | 0
July | 15 | 9PM to 10PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
July | 15 | 10PM to 11PM | 57.2 | 53.3 | 50.4 | 54.4 | 22.17 | 0.0764 | 0.37 | 13.19 | 0
July | 15 | 11PM to 12AM | 56.7 | 53.1 | 50.4 | 54.4 | 22.03 | 0.0765 | 0.37 | 13.18 | 0
July | 16 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
July | 16 | 1AM to 2AM | 56.3 | 53 | 50.5 | 54.7 | 22 | 0.0765 | 0.37 | 13.17 | 0
July | 16 | 2AM to 3AM | 56.7 | 53.1 | 50.4 | 54.4 | 22.03 | 0.0765 | 0.37 | 13.18 | 0
July | 16 | 3AM to 4AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 16 | 4AM to 5AM | 58.3 | 53.5 | 50 | 53.6 | 22.31 | 0.0762 | 0.36 | 13.22 | 0
July | 16 | 5AM to 6AM | 59.7 | 54.2 | 50.2 | 54 | 22.72 | 0.076 | 0.37 | 13.25 | 0
July | 16 | 6AM to 7AM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
July | 16 | 7AM to 8AM | 62.6 | 55.9 | 51.3 | 56.2 | 23.77 | 0.0756 | 0.38 | 13.33 | 0
July | 16 | 8AM to 9AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.38 | 0
July | 16 | 9AM to 10AM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
July | 16 | 10AM to 11AM | 66.7 | 58.5 | 53.1 | 60.1 | 25.39 | 0.075 | 0.41 | 13.45 | 0
July | 16 | 11AM to 12PM | 67.3 | 59 | 53.6 | 61.4 | 25.71 | 0.0749 | 0.41 | 13.47 | 0
July | 16 | 12PM to 1PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
July | 16 | 1PM to 2PM | 67.3 | 59.1 | 53.8 | 61.8 | 25.78 | 0.0749 | 0.42 | 13.47 | 0
July | 16 | 2PM to 3PM | 66.7 | 58.8 | 53.6 | 61.4 | 25.58 | 0.075 | 0.41 | 13.46 | 0
July | 16 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 16 | 4PM to 5PM | 64.4 | 57.5 | 52.9 | 59.7 | 24.76 | 0.0753 | 0.4 | 13.39 | 0
July | 16 | 5PM to 6PM | 62.6 | 56.6 | 52.5 | 58.9 | 24.19 | 0.0756 | 0.4 | 13.34 | 0
July | 16 | 6PM to 7PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
July | 16 | 7PM to 8PM | 60.6 | 55.7 | 52.3 | 58.6 | 23.65 | 0.0759 | 0.4 | 13.29 | 0
July | 16 | 8PM to 9PM | 60.4 | 55.7 | 52.3 | 58.6 | 23.61 | 0.0759 | 0.4 | 13.29 | 0
July | 16 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 16 | 10PM to 11PM | 59.7 | 55.3 | 52.2 | 58.2 | 23.37 | 0.076 | 0.39 | 13.27 | 0
July | 16 | 11PM to 12AM | 59.4 | 54.9 | 51.8 | 57.4 | 23.16 | 0.0761 | 0.39 | 13.26 | 0
July | 17 | 12AM to 1AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
July | 17 | 1AM to 2AM | 59 | 54.8 | 51.8 | 57.4 | 23.07 | 0.0761 | 0.39 | 13.25 | 0
July | 17 | 2AM to 3AM | 59 | 55 | 52.2 | 58.2 | 23.19 | 0.0761 | 0.39 | 13.25 | 0
July | 17 | 3AM to 4AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
July | 17 | 4AM to 5AM | 59.4 | 55 | 52 | 57.8 | 23.22 | 0.0761 | 0.39 | 13.26 | 0
July | 17 | 5AM to 6AM | 59.7 | 55.3 | 52.2 | 58.2 | 23.37 | 0.076 | 0.39 | 13.27 | 0
July | 17 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 17 | 7AM to 8AM | 60.8 | 55.9 | 52.5 | 58.9 | 23.75 | 0.0758 | 0.4 | 13.3 | 0
July | 17 | 8AM to 9AM | 61.3 | 56.1 | 52.5 | 58.9 | 23.89 | 0.0758 | 0.4 | 13.31 | 0
July | 17 | 9AM to 10AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
July | 17 | 10AM to 11AM | 63.3 | 57 | 52.7 | 59.3 | 24.43 | 0.0755 | 0.4 | 13.36 | 0
July | 17 | 11AM to 12PM | 64.8 | 57.7 | 53.1 | 60.1 | 24.91 | 0.0753 | 0.41 | 13.4 | 0
July | 17 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 17 | 1PM to 2PM | 66.7 | 58.8 | 53.6 | 61.4 | 25.58 | 0.075 | 0.41 | 13.46 | 0
July | 17 | 2PM to 3PM | 67.3 | 59.1 | 53.8 | 61.8 | 25.78 | 0.0749 | 0.42 | 13.47 | 0
July | 17 | 3PM to 4PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
July | 17 | 4PM to 5PM | 65.3 | 58 | 53.2 | 60.6 | 25.1 | 0.0752 | 0.41 | 13.42 | 0
July | 17 | 5PM to 6PM | 62.8 | 56.5 | 52.2 | 58.2 | 24.11 | 0.0756 | 0.39 | 13.34 | 0
July | 17 | 6PM to 7PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
July | 17 | 7PM to 8PM | 59.4 | 54.8 | 51.6 | 57 | 23.1 | 0.0761 | 0.39 | 13.25 | 0
July | 17 | 8PM to 9PM | 58.6 | 54.7 | 52 | 57.8 | 23.05 | 0.0762 | 0.39 | 13.24 | 0
July | 17 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
July | 17 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.63 | 0.0764 | 0.39 | 13.2 | 0
July | 17 | 11PM to 12AM | 56.7 | 53.4 | 51.1 | 55.9 | 22.27 | 0.0765 | 0.38 | 13.18 | 0
July | 18 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
July | 18 | 1AM to 2AM | 55.6 | 52.7 | 50.5 | 54.7 | 21.83 | 0.0766 | 0.37 | 13.15 | 0
July | 18 | 2AM to 3AM | 55.4 | 52.5 | 50.4 | 54.4 | 21.73 | 0.0767 | 0.37 | 13.14 | 0
July | 18 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 18 | 4AM to 5AM | 54.7 | 51.8 | 49.6 | 52.9 | 21.33 | 0.0768 | 0.36 | 13.12 | 0
July | 18 | 5AM to 6AM | 54.3 | 51.6 | 49.5 | 52.6 | 21.18 | 0.0768 | 0.36 | 13.11 | 0
July | 18 | 6AM to 7AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
July | 18 | 7AM to 8AM | 54.7 | 51.7 | 49.5 | 52.6 | 21.27 | 0.0768 | 0.36 | 13.12 | 0
July | 18 | 8AM to 9AM | 55.2 | 52 | 49.5 | 52.6 | 21.4 | 0.0767 | 0.36 | 13.13 | 0
July | 18 | 9AM to 10AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 18 | 10AM to 11AM | 57.9 | 53.2 | 49.6 | 52.9 | 22.12 | 0.0763 | 0.36 | 13.2 | 0
July | 18 | 11AM to 12PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
July | 18 | 12PM to 1PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
July | 18 | 1PM to 2PM | 61.7 | 54.8 | 49.8 | 53.3 | 23.09 | 0.0757 | 0.36 | 13.3 | 0
July | 18 | 2PM to 3PM | 61.3 | 54.5 | 49.5 | 52.6 | 22.89 | 0.0758 | 0.36 | 13.29 | 0
July | 18 | 3PM to 4PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
July | 18 | 4PM to 5PM | 59.9 | 53.7 | 49.1 | 51.8 | 22.43 | 0.076 | 0.35 | 13.25 | 0
July | 18 | 5PM to 6PM | 59 | 53.4 | 49.1 | 51.8 | 22.21 | 0.0761 | 0.35 | 13.23 | 0
July | 18 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
July | 18 | 7PM to 8PM | 57.2 | 52.5 | 48.9 | 51.5 | 21.72 | 0.0764 | 0.35 | 13.18 | 0
July | 18 | 8PM to 9PM | 56.7 | 52.2 | 48.7 | 51.1 | 21.53 | 0.0765 | 0.35 | 13.17 | 0
July | 18 | 9PM to 10PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
July | 18 | 10PM to 11PM | 55.6 | 51.7 | 48.7 | 51.1 | 21.27 | 0.0767 | 0.35 | 13.14 | 0
July | 18 | 11PM to 12AM | 55.4 | 51.9 | 49.1 | 51.8 | 21.34 | 0.0767 | 0.35 | 13.14 | 0
July | 19 | 12AM to 1AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
July | 19 | 1AM to 2AM | 55 | 51.9 | 49.5 | 52.6 | 21.36 | 0.0767 | 0.36 | 13.13 | 0
July | 19 | 2AM to 3AM | 55 | 51.8 | 49.3 | 52.2 | 21.3 | 0.0767 | 0.35 | 13.13 | 0
July | 19 | 3AM to 4AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
July | 19 | 4AM to 5AM | 55 | 51.5 | 48.7 | 51.1 | 21.14 | 0.0767 | 0.35 | 13.13 | 0
July | 19 | 5AM to 6AM | 55 | 51.4 | 48.6 | 50.8 | 21.09 | 0.0767 | 0.34 | 13.13 | 0
July | 19 | 6AM to 7AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
July | 19 | 7AM to 8AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
July | 19 | 8AM to 9AM | 59 | 53.4 | 49.1 | 51.8 | 22.21 | 0.0761 | 0.35 | 13.23 | 0
July | 19 | 9AM to 10AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
July | 19 | 10AM to 11AM | 62.1 | 54.7 | 49.3 | 52.2 | 23.01 | 0.0757 | 0.35 | 13.31 | 0
July | 19 | 11AM to 12PM | 63 | 55.1 | 49.3 | 52.2 | 23.23 | 0.0756 | 0.35 | 13.33 | 0
July | 19 | 12PM to 1PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
July | 19 | 1PM to 2PM | 63.7 | 55.5 | 49.5 | 52.6 | 23.46 | 0.0755 | 0.36 | 13.35 | 0
July | 19 | 2PM to 3PM | 63.3 | 55.5 | 49.8 | 53.3 | 23.49 | 0.0755 | 0.36 | 13.34 | 0
July | 19 | 3PM to 4PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
July | 19 | 4PM to 5PM | 62.1 | 55 | 49.8 | 53.3 | 23.18 | 0.0757 | 0.36 | 13.31 | 0
July | 19 | 5PM to 6PM | 61 | 54.4 | 49.5 | 52.6 | 22.8 | 0.0759 | 0.36 | 13.28 | 0
July | 19 | 6PM to 7PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
July | 19 | 7PM to 8PM | 58.6 | 53.3 | 49.3 | 52.2 | 22.18 | 0.0762 | 0.35 | 13.22 | 0
July | 19 | 8PM to 9PM | 57.4 | 52.8 | 49.3 | 52.2 | 21.87 | 0.0764 | 0.35 | 13.19 | 0
July | 19 | 9PM to 10PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
July | 19 | 10PM to 11PM | 55.6 | 52.2 | 49.6 | 52.9 | 21.55 | 0.0766 | 0.36 | 13.15 | 0
July | 19 | 11PM to 12AM | 55.4 | 52.3 | 50 | 53.6 | 21.61 | 0.0767 | 0.36 | 13.14 | 0
July | 20 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 20 | 1AM to 2AM | 54.7 | 52.3 | 50.5 | 54.7 | 21.61 | 0.0768 | 0.37 | 13.13 | 0
July | 20 | 2AM to 3AM | 54.3 | 52.1 | 50.4 | 54.4 | 21.46 | 0.0768 | 0.37 | 13.12 | 0
July | 20 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 20 | 4AM to 5AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 20 | 5AM to 6AM | 55.9 | 52.7 | 50.2 | 54 | 21.8 | 0.0766 | 0.37 | 13.16 | 0
July | 20 | 6AM to 7AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 20 | 7AM to 8AM | 58.6 | 54.4 | 51.3 | 56.2 | 22.81 | 0.0762 | 0.38 | 13.23 | 0
July | 20 | 8AM to 9AM | 60.4 | 55.4 | 51.8 | 57.4 | 23.42 | 0.0759 | 0.39 | 13.28 | 0
July | 20 | 9AM to 10AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
July | 20 | 10AM to 11AM | 63.3 | 57 | 52.7 | 59.3 | 24.43 | 0.0755 | 0.4 | 13.36 | 0
July | 20 | 11AM to 12PM | 64.8 | 57.7 | 53.1 | 60.1 | 24.91 | 0.0753 | 0.41 | 13.4 | 0
July | 20 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 20 | 1PM to 2PM | 65.7 | 58.2 | 53.2 | 60.6 | 25.19 | 0.0751 | 0.41 | 13.43 | 0
July | 20 | 2PM to 3PM | 65.3 | 58 | 53.2 | 60.6 | 25.1 | 0.0752 | 0.41 | 13.42 | 0
July | 20 | 3PM to 4PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
July | 20 | 4PM to 5PM | 63.3 | 56.5 | 51.8 | 57.4 | 24.13 | 0.0755 | 0.39 | 13.36 | 0
July | 20 | 5PM to 6PM | 61.7 | 55.2 | 50.5 | 54.7 | 23.32 | 0.0757 | 0.37 | 13.31 | 0
July | 20 | 6PM to 7PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
July | 20 | 7PM to 8PM | 59 | 53.1 | 48.6 | 50.8 | 22.05 | 0.0762 | 0.34 | 13.23 | 0
July | 20 | 8PM to 9PM | 58.1 | 52.5 | 48 | 49.8 | 21.67 | 0.0763 | 0.34 | 13.2 | 0
July | 20 | 9PM to 10PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
July | 20 | 10PM to 11PM | 55.9 | 51.1 | 47.1 | 48.1 | 20.89 | 0.0766 | 0.33 | 13.14 | 0
July | 20 | 11PM to 12AM | 55 | 50.5 | 46.8 | 47.4 | 20.56 | 0.0768 | 0.32 | 13.12 | 0
July | 21 | 12AM to 1AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
July | 21 | 1AM to 2AM | 54.7 | 50.1 | 46.2 | 46.5 | 20.33 | 0.0768 | 0.31 | 13.1 | 0
July | 21 | 2AM to 3AM | 55.2 | 50.1 | 45.7 | 45.5 | 20.31 | 0.0768 | 0.31 | 13.11 | 0
July | 21 | 3AM to 4AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
July | 21 | 4AM to 5AM | 56.7 | 50.3 | 45 | 44.3 | 20.47 | 0.0765 | 0.3 | 13.15 | 0
July | 21 | 5AM to 6AM | 57.2 | 50.7 | 45.1 | 44.6 | 20.65 | 0.0765 | 0.3 | 13.16 | 0
July | 21 | 6AM to 7AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
July | 21 | 7AM to 8AM | 58.6 | 52 | 46.6 | 47.1 | 21.39 | 0.0762 | 0.32 | 13.21 | 0
July | 21 | 8AM to 9AM | 59.4 | 52.7 | 47.5 | 48.8 | 21.82 | 0.0761 | 0.33 | 13.23 | 0
July | 21 | 9AM to 10AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
July | 21 | 10AM to 11AM | 61.3 | 54 | 48.4 | 50.4 | 22.56 | 0.0758 | 0.34 | 13.28 | 0
July | 21 | 11AM to 12PM | 62.8 | 54.6 | 48.4 | 50.4 | 22.91 | 0.0756 | 0.34 | 13.32 | 0
July | 21 | 12PM to 1PM | 64 | 54.9 | 48 | 49.8 | 23.11 | 0.0754 | 0.34 | 13.35 | 0
July | 21 | 1PM to 2PM | 63.7 | 54.8 | 48.2 | 50.1 | 23.08 | 0.0755 | 0.34 | 13.34 | 0
July | 21 | 2PM to 3PM | 63.3 | 54.7 | 48.2 | 50.1 | 22.99 | 0.0755 | 0.34 | 13.33 | 0
July | 21 | 3PM to 4PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
July | 21 | 4PM to 5PM | 61.7 | 53.9 | 47.8 | 49.4 | 22.49 | 0.0758 | 0.33 | 13.29 | 0
July | 21 | 5PM to 6PM | 60.3 | 53.1 | 47.5 | 48.8 | 22.04 | 0.076 | 0.33 | 13.25 | 0
July | 21 | 6PM to 7PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
July | 21 | 7PM to 8PM | 57.9 | 52 | 47.3 | 48.4 | 21.42 | 0.0763 | 0.33 | 13.19 | 0
July | 21 | 8PM to 9PM | 57 | 51.6 | 47.3 | 48.4 | 21.2 | 0.0765 | 0.33 | 13.17 | 0
July | 21 | 9PM to 10PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
July | 21 | 10PM to 11PM | 55.6 | 50.9 | 47.1 | 48.1 | 20.8 | 0.0767 | 0.33 | 13.13 | 0
July | 21 | 11PM to 12AM | 55.4 | 50.7 | 46.8 | 47.4 | 20.65 | 0.0767 | 0.32 | 13.12 | 0
July | 22 | 12AM to 1AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
July | 22 | 1AM to 2AM | 54 | 49.9 | 46.6 | 47.1 | 20.25 | 0.0769 | 0.32 | 13.09 | 0
July | 22 | 2AM to 3AM | 53.1 | 49.5 | 46.4 | 46.8 | 19.98 | 0.0771 | 0.32 | 13.06 | 0
July | 22 | 3AM to 4AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
July | 22 | 4AM to 5AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.11 | 0.077 | 0.32 | 13.08 | 0
July | 22 | 5AM to 6AM | 55.4 | 50.7 | 46.8 | 47.4 | 20.65 | 0.0767 | 0.32 | 13.12 | 0
July | 22 | 6AM to 7AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
July | 22 | 7AM to 8AM | 59.7 | 53.7 | 49.1 | 51.8 | 22.39 | 0.076 | 0.35 | 13.25 | 0
July | 22 | 8AM to 9AM | 62.2 | 55.6 | 50.9 | 55.5 | 23.57 | 0.0757 | 0.37 | 13.32 | 0
July | 22 | 9AM to 10AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
July | 22 | 10AM to 11AM | 68.5 | 59 | 52.7 | 59.3 | 25.7 | 0.0747 | 0.4 | 13.5 | 0
July | 22 | 11AM to 12PM | 72.3 | 60.5 | 53.1 | 60.1 | 26.75 | 0.0742 | 0.41 | 13.59 | 0
July | 22 | 12PM to 1PM | 75.9 | 61.8 | 53.1 | 60.1 | 27.63 | 0.0737 | 0.41 | 13.69 | 0
July | 22 | 1PM to 2PM | 73.9 | 61.2 | 53.2 | 60.6 | 27.21 | 0.074 | 0.41 | 13.64 | 0
July | 22 | 2PM to 3PM | 72 | 60.5 | 53.2 | 60.6 | 26.72 | 0.0742 | 0.41 | 13.59 | 0
July | 22 | 3PM to 4PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
July | 22 | 4PM to 5PM | 67.6 | 58.5 | 52.5 | 58.9 | 25.42 | 0.0749 | 0.4 | 13.47 | 0
July | 22 | 5PM to 6PM | 65.3 | 57.4 | 52 | 57.8 | 24.67 | 0.0752 | 0.39 | 13.41 | 0
July | 22 | 6PM to 7PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
July | 22 | 7PM to 8PM | 61.7 | 55.7 | 51.4 | 56.6 | 23.61 | 0.0757 | 0.38 | 13.31 | 0
July | 22 | 8PM to 9PM | 60.3 | 55.1 | 51.4 | 56.6 | 23.26 | 0.0759 | 0.38 | 13.28 | 0
July | 22 | 9PM to 10PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
July | 22 | 10PM to 11PM | 58.3 | 54.1 | 51.1 | 55.9 | 22.66 | 0.0762 | 0.38 | 13.22 | 0
July | 22 | 11PM to 12AM | 57.7 | 53.7 | 50.7 | 55.1 | 22.41 | 0.0763 | 0.37 | 13.21 | 0
July | 23 | 12AM to 1AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 23 | 1AM to 2AM | 57 | 53.3 | 50.5 | 54.7 | 22.18 | 0.0764 | 0.37 | 13.19 | 0
July | 23 | 2AM to 3AM | 57 | 53.2 | 50.4 | 54.4 | 22.12 | 0.0764 | 0.37 | 13.19 | 0
July | 23 | 3AM to 4AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
July | 23 | 4AM to 5AM | 57.4 | 53.4 | 50.4 | 54.4 | 22.21 | 0.0764 | 0.37 | 13.2 | 0
July | 23 | 5AM to 6AM | 57.6 | 53.7 | 50.9 | 55.5 | 22.43 | 0.0763 | 0.37 | 13.2 | 0
July | 23 | 6AM to 7AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 23 | 7AM to 8AM | 60.3 | 55.4 | 52 | 57.8 | 23.44 | 0.0759 | 0.39 | 13.28 | 0
July | 23 | 8AM to 9AM | 62.6 | 56.4 | 52.2 | 58.2 | 24.07 | 0.0756 | 0.39 | 13.34 | 0
July | 23 | 9AM to 10AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
July | 23 | 10AM to 11AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
July | 23 | 11AM to 12PM | 69.1 | 59.6 | 53.6 | 61.4 | 26.15 | 0.0746 | 0.41 | 13.52 | 0
July | 23 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
July | 23 | 1PM to 2PM | 70 | 60.1 | 53.8 | 61.8 | 26.43 | 0.0745 | 0.42 | 13.54 | 0
July | 23 | 2PM to 3PM | 69.1 | 59.6 | 53.6 | 61.4 | 26.15 | 0.0746 | 0.41 | 13.52 | 0
July | 23 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
July | 23 | 4PM to 5PM | 66 | 58.1 | 52.9 | 59.7 | 25.15 | 0.0751 | 0.4 | 13.43 | 0
July | 23 | 5PM to 6PM | 64 | 57.2 | 52.5 | 58.9 | 24.54 | 0.0754 | 0.4 | 13.38 | 0
July | 23 | 6PM to 7PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
July | 23 | 7PM to 8PM | 60.6 | 55.5 | 52 | 57.8 | 23.53 | 0.0759 | 0.39 | 13.29 | 0
July | 23 | 8PM to 9PM | 59.4 | 54.9 | 51.8 | 57.4 | 23.16 | 0.0761 | 0.39 | 13.26 | 0
July | 23 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 23 | 10PM to 11PM | 57.2 | 53.9 | 51.4 | 56.6 | 22.51 | 0.0764 | 0.38 | 13.2 | 0
July | 23 | 11PM to 12AM | 56.7 | 53.6 | 51.4 | 56.6 | 22.38 | 0.0765 | 0.38 | 13.18 | 0
July | 24 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 24 | 1AM to 2AM | 55.2 | 52.9 | 51.3 | 56.2 | 21.97 | 0.0767 | 0.38 | 13.15 | 0
July | 24 | 2AM to 3AM | 54.7 | 52.4 | 50.7 | 55.1 | 21.67 | 0.0768 | 0.37 | 13.13 | 0
July | 24 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 24 | 4AM to 5AM | 54.3 | 52.1 | 50.4 | 54.4 | 21.46 | 0.0768 | 0.37 | 13.12 | 0
July | 24 | 5AM to 6AM | 54.7 | 52.5 | 50.9 | 55.5 | 21.73 | 0.0768 | 0.37 | 13.13 | 0
July | 24 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 24 | 7AM to 8AM | 58.1 | 54.7 | 52.3 | 58.6 | 23.04 | 0.0762 | 0.4 | 13.23 | 0
July | 24 | 8AM to 9AM | 61 | 56.2 | 52.9 | 59.7 | 23.92 | 0.0758 | 0.4 | 13.3 | 0
July | 24 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
July | 24 | 10AM to 11AM | 66 | 58.4 | 53.4 | 61 | 25.34 | 0.0751 | 0.41 | 13.44 | 0
July | 24 | 11AM to 12PM | 68 | 59.1 | 53.4 | 61 | 25.82 | 0.0748 | 0.41 | 13.49 | 0
July | 24 | 12PM to 1PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
July | 24 | 1PM to 2PM | 68.7 | 59.3 | 53.2 | 60.6 | 25.93 | 0.0747 | 0.41 | 13.5 | 0
July | 24 | 2PM to 3PM | 67.3 | 58.8 | 53.2 | 60.6 | 25.58 | 0.0749 | 0.41 | 13.47 | 0
July | 24 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 24 | 4PM to 5PM | 63.7 | 57 | 52.5 | 58.9 | 24.46 | 0.0754 | 0.4 | 13.37 | 0
July | 24 | 5PM to 6PM | 61.3 | 55.8 | 52 | 57.8 | 23.7 | 0.0758 | 0.39 | 13.31 | 0
July | 24 | 6PM to 7PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
July | 24 | 7PM to 8PM | 57.7 | 53.9 | 51.1 | 55.9 | 22.53 | 0.0763 | 0.38 | 13.21 | 0
July | 24 | 8PM to 9PM | 56.3 | 53.1 | 50.7 | 55.1 | 22.06 | 0.0765 | 0.37 | 13.17 | 0
July | 24 | 9PM to 10PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 24 | 10PM to 11PM | 55 | 52.4 | 50.4 | 54.4 | 21.64 | 0.0767 | 0.37 | 13.14 | 0
July | 24 | 11PM to 12AM | 55 | 52.4 | 50.4 | 54.4 | 21.64 | 0.0767 | 0.37 | 13.14 | 0
July | 25 | 12AM to 1AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
July | 25 | 1AM to 2AM | 54.7 | 52.3 | 50.5 | 54.7 | 21.61 | 0.0768 | 0.37 | 13.13 | 0
July | 25 | 2AM to 3AM | 54.3 | 52.1 | 50.4 | 54.4 | 21.46 | 0.0768 | 0.37 | 13.12 | 0
July | 25 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 25 | 4AM to 5AM | 55.2 | 52.5 | 50.4 | 54.4 | 21.68 | 0.0767 | 0.37 | 13.14 | 0
July | 25 | 5AM to 6AM | 56.7 | 53.3 | 50.9 | 55.5 | 22.21 | 0.0765 | 0.37 | 13.18 | 0
July | 25 | 6AM to 7AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 25 | 7AM to 8AM | 60.6 | 55.8 | 52.5 | 58.9 | 23.71 | 0.0759 | 0.4 | 13.29 | 0
July | 25 | 8AM to 9AM | 63.3 | 57.5 | 53.6 | 61.4 | 24.75 | 0.0755 | 0.41 | 13.37 | 0
July | 25 | 9AM to 10AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
July | 25 | 10AM to 11AM | 68.4 | 59.7 | 54.3 | 63 | 26.23 | 0.0747 | 0.43 | 13.5 | 0
July | 25 | 11AM to 12PM | 70.7 | 60.6 | 54.3 | 63 | 26.8 | 0.0744 | 0.43 | 13.56 | 0
July | 25 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
July | 25 | 1PM to 2PM | 71.4 | 60.6 | 53.8 | 61.8 | 26.78 | 0.0743 | 0.42 | 13.58 | 0
July | 25 | 2PM to 3PM | 69.6 | 59.8 | 53.6 | 61.4 | 26.28 | 0.0746 | 0.41 | 13.53 | 0
July | 25 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
July | 25 | 4PM to 5PM | 64.6 | 57.4 | 52.5 | 58.9 | 24.68 | 0.0753 | 0.4 | 13.39 | 0
July | 25 | 5PM to 6PM | 61.3 | 55.8 | 52 | 57.8 | 23.7 | 0.0758 | 0.39 | 13.31 | 0
July | 25 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 25 | 7PM to 8PM | 57 | 53.8 | 51.4 | 56.6 | 22.47 | 0.0764 | 0.38 | 13.19 | 0
July | 25 | 8PM to 9PM | 55.9 | 53.3 | 51.4 | 56.6 | 22.21 | 0.0766 | 0.38 | 13.17 | 0
July | 25 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 25 | 10PM to 11PM | 54.7 | 52.6 | 51.1 | 55.9 | 21.78 | 0.0768 | 0.38 | 13.13 | 0
July | 25 | 11PM to 12AM | 54.3 | 52.3 | 50.7 | 55.1 | 21.58 | 0.0768 | 0.37 | 13.12 | 0
July | 26 | 12AM to 1AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
July | 26 | 1AM to 2AM | 53.6 | 51.9 | 50.5 | 54.7 | 21.35 | 0.0769 | 0.37 | 13.1 | 0
July | 26 | 2AM to 3AM | 53.4 | 51.7 | 50.4 | 54.4 | 21.25 | 0.077 | 0.37 | 13.09 | 0
July | 26 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
July | 26 | 4AM to 5AM | 54.7 | 52.6 | 51.1 | 55.9 | 21.78 | 0.0768 | 0.38 | 13.13 | 0
July | 26 | 5AM to 6AM | 56.3 | 53.9 | 52.2 | 58.2 | 22.54 | 0.0765 | 0.39 | 13.18 | 0
July | 26 | 6AM to 7AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
July | 26 | 7AM to 8AM | 60.3 | 56.7 | 54.3 | 63 | 24.26 | 0.0759 | 0.43 | 13.3 | 0
July | 26 | 8AM to 9AM | 62.6 | 57.9 | 54.9 | 64.3 | 25.03 | 0.0755 | 0.43 | 13.36 | 0
July | 26 | 9AM to 10AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
July | 26 | 10AM to 11AM | 67.6 | 60.5 | 56.1 | 67.4 | 26.73 | 0.0748 | 0.45 | 13.5 | 0
July | 26 | 11AM to 12PM | 70.3 | 61.7 | 56.7 | 68.7 | 27.6 | 0.0744 | 0.46 | 13.57 | 0
July | 26 | 12PM to 1PM | 73 | 62.9 | 57 | 69.6 | 28.41 | 0.074 | 0.47 | 13.64 | 0
July | 26 | 1PM to 2PM | 70.7 | 61.6 | 56.1 | 67.4 | 27.48 | 0.0744 | 0.45 | 13.58 | 0
July | 26 | 2PM to 3PM | 68.4 | 60.2 | 55.2 | 65.2 | 26.57 | 0.0747 | 0.44 | 13.51 | 0
July | 26 | 3PM to 4PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
July | 26 | 4PM to 5PM | 63.3 | 57.3 | 53.2 | 60.6 | 24.62 | 0.0755 | 0.41 | 13.37 | 0
July | 26 | 5PM to 6PM | 60.6 | 55.6 | 52.2 | 58.2 | 23.59 | 0.0759 | 0.39 | 13.29 | 0
July | 26 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 26 | 7PM to 8PM | 57 | 53.8 | 51.4 | 56.6 | 22.47 | 0.0764 | 0.38 | 13.19 | 0
July | 26 | 8PM to 9PM | 55.9 | 53.3 | 51.4 | 56.6 | 22.21 | 0.0766 | 0.38 | 13.17 | 0
July | 26 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 26 | 10PM to 11PM | 55 | 53 | 51.4 | 56.6 | 21.99 | 0.0767 | 0.38 | 13.14 | 0
July | 26 | 11PM to 12AM | 55 | 53 | 51.4 | 56.6 | 21.99 | 0.0767 | 0.38 | 13.14 | 0
July | 27 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 27 | 1AM to 2AM | 55 | 53.1 | 51.6 | 57 | 22.05 | 0.0767 | 0.39 | 13.14 | 0
July | 27 | 2AM to 3AM | 55 | 53 | 51.4 | 56.6 | 21.99 | 0.0767 | 0.38 | 13.14 | 0
July | 27 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 27 | 4AM to 5AM | 56.3 | 53.7 | 51.8 | 57.4 | 22.41 | 0.0765 | 0.39 | 13.18 | 0
July | 27 | 5AM to 6AM | 57.7 | 54.7 | 52.5 | 58.9 | 23.01 | 0.0763 | 0.4 | 13.22 | 0
July | 27 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
July | 27 | 7AM to 8AM | 61.7 | 57.3 | 54.5 | 63.5 | 24.67 | 0.0757 | 0.43 | 13.33 | 0
July | 27 | 8AM to 9AM | 64.2 | 58.9 | 55.6 | 66 | 25.69 | 0.0753 | 0.45 | 13.41 | 0
July | 27 | 9AM to 10AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
July | 27 | 10AM to 11AM | 68.5 | 60.9 | 56.3 | 67.8 | 27.02 | 0.0747 | 0.46 | 13.52 | 0
July | 27 | 11AM to 12PM | 70.3 | 61.5 | 56.3 | 67.8 | 27.46 | 0.0744 | 0.46 | 13.57 | 0
July | 27 | 12PM to 1PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
July | 27 | 1PM to 2PM | 70.3 | 60.9 | 55.2 | 65.2 | 27.05 | 0.0744 | 0.44 | 13.56 | 0
July | 27 | 2PM to 3PM | 68.5 | 59.7 | 54.1 | 62.6 | 26.21 | 0.0747 | 0.42 | 13.51 | 0
July | 27 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
July | 27 | 4PM to 5PM | 66 | 57.9 | 52.5 | 58.9 | 25.03 | 0.0751 | 0.4 | 13.43 | 0
July | 27 | 5PM to 6PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
July | 27 | 6PM to 7PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
July | 27 | 7PM to 8PM | 62.1 | 55.9 | 51.6 | 57 | 23.76 | 0.0757 | 0.39 | 13.32 | 0
July | 27 | 8PM to 9PM | 59.9 | 55.3 | 52 | 57.8 | 23.35 | 0.076 | 0.39 | 13.27 | 0
July | 27 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
July | 27 | 10PM to 11PM | 57.2 | 54.3 | 52.2 | 58.2 | 22.75 | 0.0764 | 0.39 | 13.2 | 0
July | 27 | 11PM to 12AM | 56.7 | 53.8 | 51.8 | 57.4 | 22.5 | 0.0765 | 0.39 | 13.19 | 0
July | 28 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 28 | 1AM to 2AM | 55.9 | 53.4 | 51.6 | 57 | 22.27 | 0.0766 | 0.39 | 13.17 | 0
July | 28 | 2AM to 3AM | 55.9 | 53.3 | 51.4 | 56.6 | 22.21 | 0.0766 | 0.38 | 13.17 | 0
July | 28 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 28 | 4AM to 5AM | 56.7 | 53.6 | 51.4 | 56.6 | 22.38 | 0.0765 | 0.38 | 13.18 | 0
July | 28 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.63 | 0.0764 | 0.39 | 13.2 | 0
July | 28 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
July | 28 | 7AM to 8AM | 59 | 55.2 | 52.5 | 58.9 | 23.32 | 0.0761 | 0.4 | 13.25 | 0
July | 28 | 8AM to 9AM | 59.9 | 55.5 | 52.5 | 58.9 | 23.54 | 0.076 | 0.4 | 13.27 | 0
July | 28 | 9AM to 10AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
July | 28 | 10AM to 11AM | 62.1 | 56.3 | 52.3 | 58.6 | 24 | 0.0757 | 0.4 | 13.33 | 0
July | 28 | 11AM to 12PM | 63 | 56.7 | 52.3 | 58.6 | 24.22 | 0.0755 | 0.4 | 13.35 | 0
July | 28 | 12PM to 1PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
July | 28 | 1PM to 2PM | 63.7 | 56.8 | 52.2 | 58.2 | 24.33 | 0.0754 | 0.39 | 13.37 | 0
July | 28 | 2PM to 3PM | 63.3 | 56.7 | 52.2 | 58.2 | 24.25 | 0.0755 | 0.39 | 13.36 | 0
July | 28 | 3PM to 4PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
July | 28 | 4PM to 5PM | 61.3 | 55.7 | 51.8 | 57.4 | 23.64 | 0.0758 | 0.39 | 13.31 | 0
July | 28 | 5PM to 6PM | 59.5 | 54.9 | 51.6 | 57 | 23.14 | 0.076 | 0.39 | 13.26 | 0
July | 28 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 28 | 7PM to 8PM | 57.2 | 53.9 | 51.4 | 56.6 | 22.51 | 0.0764 | 0.38 | 13.2 | 0
July | 28 | 8PM to 9PM | 56.7 | 53.6 | 51.4 | 56.6 | 22.38 | 0.0765 | 0.38 | 13.18 | 0
July | 28 | 9PM to 10PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 28 | 10PM to 11PM | 55.6 | 53.2 | 51.4 | 56.6 | 22.12 | 0.0766 | 0.38 | 13.16 | 0
July | 28 | 11PM to 12AM | 55.4 | 53.1 | 51.4 | 56.6 | 22.08 | 0.0767 | 0.38 | 13.15 | 0
July | 29 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 29 | 1AM to 2AM | 55 | 53.1 | 51.6 | 57 | 22.05 | 0.0767 | 0.39 | 13.14 | 0
July | 29 | 2AM to 3AM | 55 | 53 | 51.4 | 56.6 | 21.99 | 0.0767 | 0.38 | 13.14 | 0
July | 29 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
July | 29 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
July | 29 | 5AM to 6AM | 57 | 53.7 | 51.3 | 56.2 | 22.41 | 0.0764 | 0.38 | 13.19 | 0
July | 29 | 6AM to 7AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 29 | 7AM to 8AM | 60.6 | 55.8 | 52.5 | 58.9 | 23.71 | 0.0759 | 0.4 | 13.29 | 0
July | 29 | 8AM to 9AM | 63.3 | 57.5 | 53.6 | 61.4 | 24.75 | 0.0755 | 0.41 | 13.37 | 0
July | 29 | 9AM to 10AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
July | 29 | 10AM to 11AM | 68 | 59.6 | 54.3 | 63 | 26.15 | 0.0748 | 0.43 | 13.49 | 0
July | 29 | 11AM to 12PM | 70 | 60.3 | 54.3 | 63 | 26.63 | 0.0745 | 0.43 | 13.54 | 0
July | 29 | 12PM to 1PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
July | 29 | 1PM to 2PM | 71.2 | 60.9 | 54.5 | 63.5 | 27 | 0.0743 | 0.43 | 13.58 | 0
July | 29 | 2PM to 3PM | 70.7 | 60.9 | 54.9 | 64.3 | 27 | 0.0744 | 0.43 | 13.57 | 0
July | 29 | 3PM to 4PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
July | 29 | 4PM to 5PM | 67.3 | 59.4 | 54.5 | 63.5 | 26.04 | 0.0749 | 0.43 | 13.48 | 0
July | 29 | 5PM to 6PM | 64.8 | 58.2 | 54 | 62.2 | 25.22 | 0.0752 | 0.42 | 13.41 | 0
July | 29 | 6PM to 7PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
July | 29 | 7PM to 8PM | 61.3 | 56.6 | 53.4 | 61 | 24.2 | 0.0757 | 0.41 | 13.32 | 0
July | 29 | 8PM to 9PM | 60.8 | 56.4 | 53.4 | 61 | 24.07 | 0.0758 | 0.41 | 13.3 | 0
July | 29 | 9PM to 10PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
July | 29 | 10PM to 11PM | 59.7 | 55.7 | 52.9 | 59.7 | 23.61 | 0.076 | 0.4 | 13.27 | 0
July | 29 | 11PM to 12AM | 59.4 | 55.1 | 52.2 | 58.2 | 23.28 | 0.0761 | 0.39 | 13.26 | 0
July | 30 | 12AM to 1AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
July | 30 | 1AM to 2AM | 58.6 | 54.5 | 51.6 | 57 | 22.93 | 0.0762 | 0.39 | 13.24 | 0
July | 30 | 2AM to 3AM | 58.3 | 54.3 | 51.4 | 56.6 | 22.78 | 0.0762 | 0.38 | 13.23 | 0
July | 30 | 3AM to 4AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
July | 30 | 4AM to 5AM | 59 | 54.6 | 51.4 | 56.6 | 22.95 | 0.0761 | 0.38 | 13.24 | 0
July | 30 | 5AM to 6AM | 59.9 | 55.2 | 51.8 | 57.4 | 23.29 | 0.076 | 0.39 | 13.27 | 0
July | 30 | 6AM to 7AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
July | 30 | 7AM to 8AM | 62.6 | 56.8 | 52.9 | 59.7 | 24.32 | 0.0756 | 0.4 | 13.34 | 0
July | 30 | 8AM to 9AM | 64.4 | 57.7 | 53.2 | 60.6 | 24.88 | 0.0753 | 0.41 | 13.39 | 0
July | 30 | 9AM to 10AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
July | 30 | 10AM to 11AM | 67.6 | 59.2 | 53.8 | 61.8 | 25.86 | 0.0748 | 0.42 | 13.48 | 0
July | 30 | 11AM to 12PM | 69.4 | 60 | 54 | 62.2 | 26.37 | 0.0746 | 0.42 | 13.53 | 0
July | 30 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
July | 30 | 1PM to 2PM | 70 | 60.1 | 53.8 | 61.8 | 26.43 | 0.0745 | 0.42 | 13.54 | 0
July | 30 | 2PM to 3PM | 69.1 | 59.6 | 53.6 | 61.4 | 26.15 | 0.0746 | 0.41 | 13.52 | 0
July | 30 | 3PM to 4PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
July | 30 | 4PM to 5PM | 66.4 | 58.4 | 53.2 | 60.6 | 25.36 | 0.075 | 0.41 | 13.44 | 0
July | 30 | 5PM to 6PM | 64.6 | 57.8 | 53.2 | 60.6 | 24.93 | 0.0753 | 0.41 | 13.4 | 0
July | 30 | 6PM to 7PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
July | 30 | 7PM to 8PM | 62.1 | 56.5 | 52.7 | 59.3 | 24.12 | 0.0757 | 0.4 | 13.33 | 0
July | 30 | 8PM to 9PM | 61 | 55.8 | 52.2 | 58.2 | 23.68 | 0.0758 | 0.39 | 13.3 | 0
July | 30 | 9PM to 10PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
July | 30 | 10PM to 11PM | 60.4 | 55.4 | 51.8 | 57.4 | 23.42 | 0.0759 | 0.39 | 13.28 | 0
July | 30 | 11PM to 12AM | 60.6 | 55.6 | 52.2 | 58.2 | 23.59 | 0.0759 | 0.39 | 13.29 | 0
July | 31 | 12AM to 1AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
July | 31 | 1AM to 2AM | 60.6 | 55.7 | 52.3 | 58.6 | 23.65 | 0.0759 | 0.4 | 13.29 | 0
July | 31 | 2AM to 3AM | 60.4 | 55.7 | 52.3 | 58.6 | 23.61 | 0.0759 | 0.4 | 13.29 | 0
July | 31 | 3AM to 4AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 31 | 4AM to 5AM | 60.1 | 55.4 | 52.2 | 58.2 | 23.46 | 0.076 | 0.39 | 13.28 | 0
July | 31 | 5AM to 6AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 31 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
July | 31 | 7AM to 8AM | 61 | 56.4 | 53.2 | 60.6 | 24.05 | 0.0758 | 0.41 | 13.31 | 0
July | 31 | 8AM to 9AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
July | 31 | 9AM to 10AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
July | 31 | 10AM to 11AM | 64 | 58.2 | 54.5 | 63.5 | 25.24 | 0.0753 | 0.43 | 13.39 | 0
July | 31 | 11AM to 12PM | 64.9 | 58.5 | 54.3 | 63 | 25.4 | 0.0752 | 0.43 | 13.41 | 0
July | 31 | 12PM to 1PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
July | 31 | 1PM to 2PM | 66.7 | 59.1 | 54.1 | 62.6 | 25.77 | 0.075 | 0.42 | 13.46 | 0
July | 31 | 2PM to 3PM | 67.3 | 59.3 | 54.1 | 62.6 | 25.9 | 0.0749 | 0.42 | 13.47 | 0
July | 31 | 3PM to 4PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
July | 31 | 4PM to 5PM | 66 | 58.9 | 54.3 | 63 | 25.66 | 0.0751 | 0.43 | 13.44 | 0
July | 31 | 5PM to 6PM | 64 | 58.1 | 54.3 | 63 | 25.18 | 0.0753 | 0.43 | 13.39 | 0
July | 31 | 6PM to 7PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
July | 31 | 7PM to 8PM | 61.3 | 57 | 54.1 | 62.6 | 24.46 | 0.0757 | 0.42 | 13.32 | 0
July | 31 | 8PM to 9PM | 60.8 | 56.6 | 53.8 | 61.8 | 24.19 | 0.0758 | 0.42 | 13.31 | 0
July | 31 | 9PM to 10PM | 60.6 | 56.5 | 53.8 | 61.8 | 24.15 | 0.0758 | 0.42 | 13.3 | 0
July | 31 | 10PM to 11PM | 60.3 | 56.4 | 53.8 | 61.8 | 24.06 | 0.0759 | 0.42 | 13.29 | 0
July | 31 | 11PM to 12AM | 60.1 | 56.3 | 53.8 | 61.8 | 24.02 | 0.0759 | 0.42 | 13.29 | 0
August | 1 | 12AM to 1AM | 59.7 | 56.3 | 54 | 62.2 | 24 | 0.076 | 0.42 | 13.28 | 0
August | 1 | 1AM to 2AM | 59.5 | 56.2 | 54 | 62.2 | 23.95 | 0.076 | 0.42 | 13.27 | 0
August | 1 | 2AM to 3AM | 59.2 | 56.1 | 54 | 62.2 | 23.86 | 0.0761 | 0.42 | 13.26 | 0
August | 1 | 3AM to 4AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 1 | 4AM to 5AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 1 | 5AM to 6AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 1 | 6AM to 7AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 1 | 7AM to 8AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 1 | 8AM to 9AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 1 | 9AM to 10AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
August | 1 | 10AM to 11AM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 1 | 11AM to 12PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
August | 1 | 12PM to 1PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
August | 1 | 1PM to 2PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
August | 1 | 2PM to 3PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
August | 1 | 3PM to 4PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
August | 1 | 4PM to 5PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
August | 1 | 5PM to 6PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 1 | 6PM to 7PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
August | 1 | 7PM to 8PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
August | 1 | 8PM to 9PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 1 | 9PM to 10PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
August | 1 | 10PM to 11PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 1 | 11PM to 12AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 2 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 2 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 2 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 2 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 2 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 2 | 5AM to 6AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 2 | 6AM to 7AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
August | 2 | 7AM to 8AM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
August | 2 | 8AM to 9AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
August | 2 | 9AM to 10AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
August | 2 | 10AM to 11AM | 78.1 | 62.6 | 53.1 | 60.1 | 28.15 | 0.0734 | 0.41 | 13.74 | 0
August | 2 | 11AM to 12PM | 80.1 | 63.7 | 54 | 62.2 | 28.96 | 0.0731 | 0.42 | 13.8 | 0
August | 2 | 12PM to 1PM | 84.9 | 65.3 | 54 | 62.2 | 30.14 | 0.0725 | 0.42 | 13.92 | 0
August | 2 | 1PM to 2PM | 82 | 63.9 | 53.1 | 60.1 | 29.12 | 0.0729 | 0.41 | 13.84 | 0
August | 2 | 2PM to 3PM | 82.9 | 63.7 | 52 | 57.8 | 28.97 | 0.0728 | 0.39 | 13.86 | 0
August | 2 | 3PM to 4PM | 78.1 | 62.6 | 53.1 | 60.1 | 28.15 | 0.0734 | 0.41 | 13.74 | 0
August | 2 | 4PM to 5PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
August | 2 | 5PM to 6PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
August | 2 | 6PM to 7PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 2 | 7PM to 8PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 2 | 8PM to 9PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 2 | 9PM to 10PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 2 | 10PM to 11PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 2 | 11PM to 12AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 3 | 12AM to 1AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 3 | 1AM to 2AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 3 | 2AM to 3AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 3 | 3AM to 4AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 3 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 3 | 5AM to 6AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 3 | 6AM to 7AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
August | 3 | 7AM to 8AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
August | 3 | 8AM to 9AM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
August | 3 | 9AM to 10AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
August | 3 | 10AM to 11AM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
August | 3 | 11AM to 12PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
August | 3 | 12PM to 1PM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
August | 3 | 1PM to 2PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
August | 3 | 2PM to 3PM | 81 | 64.5 | 55 | 64.7 | 29.57 | 0.073 | 0.44 | 13.83 | 0
August | 3 | 3PM to 4PM | 78.1 | 64 | 55.9 | 66.9 | 29.21 | 0.0734 | 0.45 | 13.76 | 0
August | 3 | 4PM to 5PM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
August | 3 | 5PM to 6PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
August | 3 | 6PM to 7PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
August | 3 | 7PM to 8PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
August | 3 | 8PM to 9PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
August | 3 | 9PM to 10PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
August | 3 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 3 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 4 | 12AM to 1AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 4 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 4 | 2AM to 3AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 4 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 4 | 4AM to 5AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 4 | 5AM to 6AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 4 | 6AM to 7AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 4 | 7AM to 8AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
August | 4 | 8AM to 9AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
August | 4 | 9AM to 10AM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
August | 4 | 10AM to 11AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
August | 4 | 11AM to 12PM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
August | 4 | 12PM to 1PM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
August | 4 | 1PM to 2PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
August | 4 | 2PM to 3PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
August | 4 | 3PM to 4PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 4 | 4PM to 5PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 4 | 5PM to 6PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 4 | 6PM to 7PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 4 | 7PM to 8PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
August | 4 | 8PM to 9PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 4 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 4 | 10PM to 11PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 4 | 11PM to 12AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
August | 5 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 5 | 1AM to 2AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 5 | 2AM to 3AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 5 | 3AM to 4AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 5 | 4AM to 5AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 5 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 5 | 6AM to 7AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 5 | 7AM to 8AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 5 | 8AM to 9AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 5 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 5 | 10AM to 11AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 5 | 11AM to 12PM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
August | 5 | 12PM to 1PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 5 | 1PM to 2PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
August | 5 | 2PM to 3PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 5 | 3PM to 4PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 5 | 4PM to 5PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 5 | 5PM to 6PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 5 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 5 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 5 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 5 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 5 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 5 | 11PM to 12AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 6 | 12AM to 1AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 6 | 1AM to 2AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 6 | 2AM to 3AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 6 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 6 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
August | 6 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 6 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 6 | 7AM to 8AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 6 | 8AM to 9AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 6 | 9AM to 10AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
August | 6 | 10AM to 11AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
August | 6 | 11AM to 12PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
August | 6 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
August | 6 | 1PM to 2PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
August | 6 | 2PM to 3PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
August | 6 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 6 | 4PM to 5PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 6 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 6 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 6 | 7PM to 8PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
August | 6 | 8PM to 9PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 6 | 9PM to 10PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 6 | 10PM to 11PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 6 | 11PM to 12AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 7 | 12AM to 1AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 7 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 7 | 2AM to 3AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
August | 7 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 7 | 4AM to 5AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
August | 7 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 7 | 6AM to 7AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 7 | 7AM to 8AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 7 | 8AM to 9AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 7 | 9AM to 10AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 7 | 10AM to 11AM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
August | 7 | 11AM to 12PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 7 | 12PM to 1PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 7 | 1PM to 2PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
August | 7 | 2PM to 3PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 7 | 3PM to 4PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
August | 7 | 4PM to 5PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 7 | 5PM to 6PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
August | 7 | 6PM to 7PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
August | 7 | 7PM to 8PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
August | 7 | 8PM to 9PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 7 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 7 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 7 | 11PM to 12AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
August | 8 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 8 | 1AM to 2AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 8 | 2AM to 3AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 8 | 3AM to 4AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
August | 8 | 4AM to 5AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
August | 8 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
August | 8 | 6AM to 7AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 8 | 7AM to 8AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
August | 8 | 8AM to 9AM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
August | 8 | 9AM to 10AM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
August | 8 | 10AM to 11AM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 8 | 11AM to 12PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
August | 8 | 12PM to 1PM | 77 | 61.3 | 51.1 | 55.9 | 27.22 | 0.0736 | 0.38 | 13.7 | 0
August | 8 | 1PM to 2PM | 75 | 59.5 | 48.9 | 51.5 | 26.05 | 0.0739 | 0.35 | 13.64 | 0
August | 8 | 2PM to 3PM | 73.9 | 58.7 | 48 | 49.8 | 25.52 | 0.074 | 0.34 | 13.6 | 0
August | 8 | 3PM to 4PM | 73 | 57.9 | 46.9 | 47.8 | 24.99 | 0.0742 | 0.32 | 13.57 | 0
August | 8 | 4PM to 5PM | 72 | 58 | 48 | 49.8 | 25.04 | 0.0743 | 0.34 | 13.55 | 0
August | 8 | 5PM to 6PM | 70 | 57.2 | 48 | 49.8 | 24.56 | 0.0746 | 0.34 | 13.5 | 0
August | 8 | 6PM to 7PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
August | 8 | 7PM to 8PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
August | 8 | 8PM to 9PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 8 | 9PM to 10PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 8 | 10PM to 11PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 8 | 11PM to 12AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
August | 9 | 12AM to 1AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 9 | 1AM to 2AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 9 | 2AM to 3AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
August | 9 | 3AM to 4AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
August | 9 | 4AM to 5AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
August | 9 | 5AM to 6AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 9 | 6AM to 7AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 9 | 7AM to 8AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
August | 9 | 8AM to 9AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
August | 9 | 9AM to 10AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
August | 9 | 10AM to 11AM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
August | 9 | 11AM to 12PM | 80.1 | 63.3 | 53.1 | 60.1 | 28.64 | 0.0731 | 0.41 | 13.79 | 0
August | 9 | 12PM to 1PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
August | 9 | 1PM to 2PM | 82.9 | 63.7 | 52 | 57.8 | 28.97 | 0.0728 | 0.39 | 13.86 | 0
August | 9 | 2PM to 3PM | 84 | 62.8 | 48.9 | 51.5 | 28.24 | 0.0726 | 0.35 | 13.87 | 0
August | 9 | 3PM to 4PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
August | 9 | 4PM to 5PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
August | 9 | 5PM to 6PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 9 | 6PM to 7PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 9 | 7PM to 8PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 9 | 8PM to 9PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 9 | 9PM to 10PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 9 | 10PM to 11PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 9 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
August | 10 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 10 | 1AM to 2AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
August | 10 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
August | 10 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 10 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 10 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 10 | 6AM to 7AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 10 | 7AM to 8AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 10 | 8AM to 9AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 10 | 9AM to 10AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
August | 10 | 10AM to 11AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
August | 10 | 11AM to 12PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
August | 10 | 12PM to 1PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
August | 10 | 1PM to 2PM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
August | 10 | 2PM to 3PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
August | 10 | 3PM to 4PM | 71.1 | 59.5 | 52 | 57.8 | 26.07 | 0.0744 | 0.39 | 13.56 | 0
August | 10 | 4PM to 5PM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
August | 10 | 5PM to 6PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
August | 10 | 6PM to 7PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 10 | 7PM to 8PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 10 | 8PM to 9PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 10 | 9PM to 10PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 10 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 10 | 11PM to 12AM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
August | 11 | 12AM to 1AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 11 | 1AM to 2AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
August | 11 | 2AM to 3AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 11 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 11 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 11 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 11 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 11 | 7AM to 8AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 11 | 8AM to 9AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 11 | 9AM to 10AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 11 | 10AM to 11AM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 11 | 11AM to 12PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
August | 11 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
August | 11 | 1PM to 2PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
August | 11 | 2PM to 3PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
August | 11 | 3PM to 4PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
August | 11 | 4PM to 5PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
August | 11 | 5PM to 6PM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
August | 11 | 6PM to 7PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 11 | 7PM to 8PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 11 | 8PM to 9PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 11 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 11 | 10PM to 11PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 11 | 11PM to 12AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
August | 12 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 12 | 1AM to 2AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 12 | 2AM to 3AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 12 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 12 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 12 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 12 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 12 | 7AM to 8AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 12 | 8AM to 9AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 12 | 9AM to 10AM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 12 | 10AM to 11AM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 12 | 11AM to 12PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
August | 12 | 12PM to 1PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
August | 12 | 1PM to 2PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
August | 12 | 2PM to 3PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
August | 12 | 3PM to 4PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 12 | 4PM to 5PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 12 | 5PM to 6PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 12 | 6PM to 7PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 12 | 7PM to 8PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 12 | 8PM to 9PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 12 | 9PM to 10PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 12 | 10PM to 11PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 12 | 11PM to 12AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 13 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 1AM to 2AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 2AM to 3AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 3AM to 4AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 13 | 4AM to 5AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 13 | 5AM to 6AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 13 | 6AM to 7AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 13 | 7AM to 8AM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
August | 13 | 8AM to 9AM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
August | 13 | 9AM to 10AM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
August | 13 | 10AM to 11AM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
August | 13 | 11AM to 12PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
August | 13 | 12PM to 1PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
August | 13 | 1PM to 2PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 13 | 2PM to 3PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
August | 13 | 3PM to 4PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 13 | 4PM to 5PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
August | 13 | 5PM to 6PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 13 | 6PM to 7PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 13 | 7PM to 8PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
August | 13 | 8PM to 9PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 13 | 9PM to 10PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 13 | 10PM to 11PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 11PM to 12AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 14 | 12AM to 1AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 14 | 1AM to 2AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 14 | 2AM to 3AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 14 | 3AM to 4AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 14 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 14 | 5AM to 6AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 14 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 14 | 7AM to 8AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 14 | 8AM to 9AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 14 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 14 | 10AM to 11AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 14 | 11AM to 12PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 14 | 12PM to 1PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 14 | 1PM to 2PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 14 | 2PM to 3PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 14 | 3PM to 4PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
August | 14 | 4PM to 5PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 14 | 5PM to 6PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 14 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 14 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 14 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 14 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 14 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 14 | 11PM to 12AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 15 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 3AM to 4AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 15 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 15 | 5AM to 6AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 15 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 15 | 7AM to 8AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 8AM to 9AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 9AM to 10AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 15 | 10AM to 11AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 15 | 11AM to 12PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 15 | 12PM to 1PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
August | 15 | 1PM to 2PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 15 | 2PM to 3PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 15 | 3PM to 4PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 15 | 4PM to 5PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 15 | 5PM to 6PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 15 | 6PM to 7PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 15 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 15 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 15 | 10PM to 11PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 15 | 11PM to 12AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
August | 16 | 12AM to 1AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 16 | 1AM to 2AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 16 | 2AM to 3AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 16 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 16 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 16 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 16 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 16 | 7AM to 8AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 16 | 8AM to 9AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 16 | 9AM to 10AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 16 | 10AM to 11AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 16 | 11AM to 12PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 16 | 12PM to 1PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 16 | 1PM to 2PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
August | 16 | 2PM to 3PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 16 | 3PM to 4PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 16 | 4PM to 5PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 16 | 5PM to 6PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
August | 16 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 16 | 7PM to 8PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 16 | 8PM to 9PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 16 | 9PM to 10PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 16 | 10PM to 11PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 16 | 11PM to 12AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
August | 17 | 12AM to 1AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 17 | 1AM to 2AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 17 | 2AM to 3AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 17 | 3AM to 4AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 17 | 4AM to 5AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 17 | 5AM to 6AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 17 | 6AM to 7AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 17 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 17 | 8AM to 9AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 17 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 17 | 10AM to 11AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 17 | 11AM to 12PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
August | 17 | 12PM to 1PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
August | 17 | 1PM to 2PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 17 | 2PM to 3PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
August | 17 | 3PM to 4PM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
August | 17 | 4PM to 5PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
August | 17 | 5PM to 6PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
August | 17 | 6PM to 7PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
August | 17 | 7PM to 8PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
August | 17 | 8PM to 9PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 17 | 9PM to 10PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
August | 17 | 10PM to 11PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 17 | 11PM to 12AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
August | 18 | 12AM to 1AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 18 | 1AM to 2AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 18 | 2AM to 3AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
August | 18 | 3AM to 4AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 18 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 18 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 18 | 6AM to 7AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 18 | 7AM to 8AM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
August | 18 | 8AM to 9AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 18 | 9AM to 10AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 18 | 10AM to 11AM | 71.1 | 58.6 | 50 | 53.6 | 25.43 | 0.0744 | 0.36 | 13.54 | 0
August | 18 | 11AM to 12PM | 71.1 | 58.1 | 48.9 | 51.5 | 25.09 | 0.0744 | 0.35 | 13.54 | 0
August | 18 | 12PM to 1PM | 72 | 58.4 | 48.9 | 51.5 | 25.31 | 0.0743 | 0.35 | 13.56 | 0
August | 18 | 1PM to 2PM | 73.9 | 58.7 | 48 | 49.8 | 25.52 | 0.074 | 0.34 | 13.6 | 0
August | 18 | 2PM to 3PM | 72 | 58.4 | 48.9 | 51.5 | 25.31 | 0.0743 | 0.35 | 13.56 | 0
August | 18 | 3PM to 4PM | 72 | 58.9 | 50 | 53.6 | 25.64 | 0.0743 | 0.36 | 13.57 | 0
August | 18 | 4PM to 5PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 18 | 5PM to 6PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 18 | 6PM to 7PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
August | 18 | 7PM to 8PM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
August | 18 | 8PM to 9PM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
August | 18 | 9PM to 10PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 18 | 10PM to 11PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
August | 18 | 11PM to 12AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
August | 19 | 12AM to 1AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
August | 19 | 1AM to 2AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
August | 19 | 2AM to 3AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 19 | 3AM to 4AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 19 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 19 | 5AM to 6AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 19 | 6AM to 7AM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 19 | 7AM to 8AM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
August | 19 | 8AM to 9AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 19 | 9AM to 10AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 19 | 10AM to 11AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 19 | 11AM to 12PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 19 | 12PM to 1PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
August | 19 | 1PM to 2PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 19 | 2PM to 3PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 19 | 3PM to 4PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
August | 19 | 4PM to 5PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
August | 19 | 5PM to 6PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
August | 19 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 19 | 7PM to 8PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
August | 19 | 8PM to 9PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
August | 19 | 9PM to 10PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 19 | 10PM to 11PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 19 | 11PM to 12AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 20 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 1AM to 2AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 20 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 20 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 20 | 6AM to 7AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 20 | 7AM to 8AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 20 | 8AM to 9AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 20 | 9AM to 10AM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 20 | 10AM to 11AM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 20 | 11AM to 12PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 20 | 12PM to 1PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
August | 20 | 1PM to 2PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
August | 20 | 2PM to 3PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 20 | 3PM to 4PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 20 | 4PM to 5PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
August | 20 | 5PM to 6PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 20 | 6PM to 7PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 20 | 7PM to 8PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 20 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 20 | 11PM to 12AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 21 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 21 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 21 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 21 | 3AM to 4AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 21 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 21 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 21 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 21 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 21 | 8AM to 9AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 9AM to 10AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 11AM to 12PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 12PM to 1PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 21 | 1PM to 2PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 21 | 2PM to 3PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
August | 21 | 3PM to 4PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
August | 21 | 4PM to 5PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 21 | 5PM to 6PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 21 | 6PM to 7PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 21 | 7PM to 8PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 21 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 21 | 9PM to 10PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 21 | 10PM to 11PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 21 | 11PM to 12AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 22 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 22 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 22 | 2AM to 3AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 22 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 22 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
August | 22 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 22 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 22 | 7AM to 8AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 22 | 8AM to 9AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
August | 22 | 9AM to 10AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 22 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 22 | 11AM to 12PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 22 | 12PM to 1PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 22 | 1PM to 2PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
August | 22 | 2PM to 3PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 22 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
August | 22 | 4PM to 5PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
August | 22 | 5PM to 6PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 22 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 22 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 22 | 8PM to 9PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 22 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 22 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 22 | 11PM to 12AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 23 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 23 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 23 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 23 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
August | 23 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 23 | 5AM to 6AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
August | 23 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 23 | 7AM to 8AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 23 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
August | 23 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 23 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
August | 23 | 11AM to 12PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 23 | 12PM to 1PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
August | 23 | 1PM to 2PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
August | 23 | 2PM to 3PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
August | 23 | 3PM to 4PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
August | 23 | 4PM to 5PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 23 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 23 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 23 | 7PM to 8PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 23 | 8PM to 9PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
August | 23 | 9PM to 10PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 23 | 10PM to 11PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 23 | 11PM to 12AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 24 | 12AM to 1AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 24 | 1AM to 2AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 24 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 24 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
August | 24 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 24 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
August | 24 | 6AM to 7AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 24 | 7AM to 8AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
August | 24 | 8AM to 9AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 24 | 9AM to 10AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 24 | 10AM to 11AM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
August | 24 | 11AM to 12PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 24 | 12PM to 1PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
August | 24 | 1PM to 2PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
August | 24 | 2PM to 3PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
August | 24 | 3PM to 4PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
August | 24 | 4PM to 5PM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
August | 24 | 5PM to 6PM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
August | 24 | 6PM to 7PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
August | 24 | 7PM to 8PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
August | 24 | 8PM to 9PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
August | 24 | 9PM to 10PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 24 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 24 | 11PM to 12AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 12AM to 1AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 25 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 2AM to 3AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 3AM to 4AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 5AM to 6AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 6AM to 7AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
August | 25 | 7AM to 8AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 8AM to 9AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 9AM to 10AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
August | 25 | 10AM to 11AM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
August | 25 | 11AM to 12PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
August | 25 | 12PM to 1PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
August | 25 | 1PM to 2PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 25 | 2PM to 3PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
August | 25 | 3PM to 4PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
August | 25 | 4PM to 5PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 25 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
August | 25 | 6PM to 7PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 25 | 7PM to 8PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 25 | 8PM to 9PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 9PM to 10PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
August | 25 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
August | 25 | 11PM to 12AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
August | 26 | 12AM to 1AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
August | 26 | 1AM to 2AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 26 | 2AM to 3AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 26 | 3AM to 4AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
August | 26 | 4AM to 5AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
August | 26 | 5AM to 6AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 26 | 6AM to 7AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
August | 26 | 7AM to 8AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
August | 26 | 8AM to 9AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
August | 26 | 9AM to 10AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
August | 26 | 10AM to 11AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
August | 26 | 11AM to 12PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 26 | 12PM to 1PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 26 | 1PM to 2PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 26 | 2PM to 3PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 26 | 3PM to 4PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
August | 26 | 4PM to 5PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 26 | 5PM to 6PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 26 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
August | 26 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 26 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 26 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
August | 26 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
August | 26 | 11PM to 12AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 27 | 12AM to 1AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 27 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 27 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 27 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 27 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 27 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 27 | 6AM to 7AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 27 | 7AM to 8AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 27 | 8AM to 9AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 27 | 9AM to 10AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 27 | 10AM to 11AM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
August | 27 | 11AM to 12PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
August | 27 | 12PM to 1PM | 66 | 56.6 | 50 | 53.6 | 24.2 | 0.0751 | 0.36 | 13.41 | 0
August | 27 | 1PM to 2PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
August | 27 | 2PM to 3PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
August | 27 | 3PM to 4PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
August | 27 | 4PM to 5PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
August | 27 | 5PM to 6PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
August | 27 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
August | 27 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
August | 27 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 27 | 9PM to 10PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 27 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 27 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 28 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 28 | 4AM to 5AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
August | 28 | 5AM to 6AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
August | 28 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 7AM to 8AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
August | 28 | 8AM to 9AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
August | 28 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
August | 28 | 10AM to 11AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
August | 28 | 11AM to 12PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
August | 28 | 12PM to 1PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 28 | 1PM to 2PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
August | 28 | 2PM to 3PM | 68 | 58.4 | 52 | 57.8 | 25.33 | 0.0748 | 0.39 | 13.48 | 0
August | 28 | 3PM to 4PM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
August | 28 | 4PM to 5PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
August | 28 | 5PM to 6PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 28 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 28 | 7PM to 8PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 28 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 28 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 28 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 29 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 2AM to 3AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
August | 29 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 29 | 6AM to 7AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
August | 29 | 7AM to 8AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 29 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
August | 29 | 9AM to 10AM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
August | 29 | 10AM to 11AM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
August | 29 | 11AM to 12PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
August | 29 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 29 | 1PM to 2PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
August | 29 | 2PM to 3PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 29 | 3PM to 4PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
August | 29 | 4PM to 5PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
August | 29 | 5PM to 6PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
August | 29 | 6PM to 7PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 29 | 7PM to 8PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 29 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
August | 29 | 9PM to 10PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 29 | 10PM to 11PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
August | 29 | 11PM to 12AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 30 | 12AM to 1AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 30 | 1AM to 2AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
August | 30 | 2AM to 3AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
August | 30 | 3AM to 4AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
August | 30 | 4AM to 5AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 30 | 5AM to 6AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 30 | 6AM to 7AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
August | 30 | 7AM to 8AM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
August | 30 | 8AM to 9AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
August | 30 | 9AM to 10AM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
August | 30 | 10AM to 11AM | 73 | 60.3 | 52 | 57.8 | 26.55 | 0.0741 | 0.39 | 13.61 | 0
August | 30 | 11AM to 12PM | 79 | 57.5 | 39.9 | 36.4 | 24.65 | 0.0734 | 0.25 | 13.69 | 0
August | 30 | 12PM to 1PM | 75.9 | 58.6 | 46 | 46.1 | 25.44 | 0.0738 | 0.31 | 13.64 | 0
August | 30 | 1PM to 2PM | 75.9 | 59.5 | 48 | 49.8 | 26 | 0.0738 | 0.34 | 13.65 | 0
August | 30 | 2PM to 3PM | 73 | 58.8 | 48.9 | 51.5 | 25.57 | 0.0741 | 0.35 | 13.59 | 0
August | 30 | 3PM to 4PM | 71.1 | 58.1 | 48.9 | 51.5 | 25.09 | 0.0744 | 0.35 | 13.54 | 0
August | 30 | 4PM to 5PM | 70 | 58.2 | 50 | 53.6 | 25.16 | 0.0746 | 0.36 | 13.51 | 0
August | 30 | 5PM to 6PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
August | 30 | 6PM to 7PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
August | 30 | 7PM to 8PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
August | 30 | 8PM to 9PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 30 | 9PM to 10PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
August | 30 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 30 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 31 | 12AM to 1AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
August | 31 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 31 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 31 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 31 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
August | 31 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
August | 31 | 6AM to 7AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
August | 31 | 7AM to 8AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
August | 31 | 8AM to 9AM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
August | 31 | 9AM to 10AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
August | 31 | 10AM to 11AM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
August | 31 | 11AM to 12PM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
August | 31 | 12PM to 1PM | 82 | 62.1 | 48.9 | 51.5 | 27.76 | 0.0729 | 0.35 | 13.82 | 0
August | 31 | 1PM to 2PM | 75.9 | 60.9 | 51.1 | 55.9 | 26.96 | 0.0737 | 0.38 | 13.67 | 0
August | 31 | 2PM to 3PM | 73 | 59.8 | 51.1 | 55.9 | 26.25 | 0.0741 | 0.38 | 13.6 | 0
August | 31 | 3PM to 4PM | 73 | 56.3 | 43 | 41 | 23.94 | 0.0742 | 0.28 | 13.55 | 0
August | 31 | 4PM to 5PM | 71.1 | 55.5 | 43 | 41 | 23.46 | 0.0745 | 0.28 | 13.5 | 0
August | 31 | 5PM to 6PM | 66 | 54.8 | 46 | 46.1 | 23.03 | 0.0752 | 0.31 | 13.39 | 0
August | 31 | 6PM to 7PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
August | 31 | 7PM to 8PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
August | 31 | 8PM to 9PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
August | 31 | 9PM to 10PM | 61.3 | 54.2 | 48.7 | 51.1 | 22.67 | 0.0758 | 0.35 | 13.29 | 0
August | 31 | 10PM to 11PM | 60.6 | 54.2 | 49.5 | 52.6 | 22.72 | 0.0759 | 0.36 | 13.27 | 0
August | 31 | 11PM to 12AM | 59.9 | 54.3 | 50.2 | 54 | 22.77 | 0.076 | 0.37 | 13.26 | 0
September | 1 | 12AM to 1AM | 59.2 | 54.4 | 50.9 | 55.5 | 22.82 | 0.0761 | 0.37 | 13.24 | 0
September | 1 | 1AM to 2AM | 58.5 | 54.5 | 51.6 | 57 | 22.88 | 0.0762 | 0.39 | 13.23 | 0
September | 1 | 2AM to 3AM | 57.7 | 54.6 | 52.3 | 58.6 | 22.95 | 0.0763 | 0.4 | 13.22 | 0
September | 1 | 3AM to 4AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 1 | 4AM to 5AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 1 | 5AM to 6AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 1 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 1 | 7AM to 8AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 1 | 8AM to 9AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
September | 1 | 9AM to 10AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 1 | 10AM to 11AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 1 | 11AM to 12PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 1 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 1 | 1PM to 2PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 1 | 2PM to 3PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 1 | 3PM to 4PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 1 | 4PM to 5PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
September | 1 | 5PM to 6PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
September | 1 | 6PM to 7PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
September | 1 | 7PM to 8PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
September | 1 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 1 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 1 | 10PM to 11PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
September | 1 | 11PM to 12AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 2 | 12AM to 1AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
September | 2 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 2 | 2AM to 3AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 2 | 3AM to 4AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 2 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 2 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 2 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
September | 2 | 7AM to 8AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
September | 2 | 8AM to 9AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
September | 2 | 9AM to 10AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
September | 2 | 10AM to 11AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 2 | 11AM to 12PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 2 | 12PM to 1PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 2 | 1PM to 2PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 2 | 2PM to 3PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 2 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 2 | 4PM to 5PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 2 | 5PM to 6PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 2 | 6PM to 7PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 2 | 7PM to 8PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 2 | 8PM to 9PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 2 | 9PM to 10PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 2 | 10PM to 11PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 2 | 11PM to 12AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 3 | 12AM to 1AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 3 | 1AM to 2AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 3 | 2AM to 3AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
September | 3 | 3AM to 4AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
September | 3 | 4AM to 5AM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
September | 3 | 5AM to 6AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 3 | 6AM to 7AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
September | 3 | 7AM to 8AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
September | 3 | 8AM to 9AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
September | 3 | 9AM to 10AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 3 | 10AM to 11AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
September | 3 | 11AM to 12PM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
September | 3 | 12PM to 1PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
September | 3 | 1PM to 2PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
September | 3 | 2PM to 3PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 3 | 3PM to 4PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 3 | 4PM to 5PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 3 | 5PM to 6PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
September | 3 | 6PM to 7PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 3 | 7PM to 8PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 3 | 8PM to 9PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 3 | 9PM to 10PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 3 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 3 | 11PM to 12AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 4 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 4 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 4 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 4 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 4 | 4AM to 5AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 4 | 5AM to 6AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 4 | 6AM to 7AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 4 | 7AM to 8AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 4 | 8AM to 9AM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 4 | 9AM to 10AM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
September | 4 | 10AM to 11AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
September | 4 | 11AM to 12PM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
September | 4 | 12PM to 1PM | 81 | 65 | 55.9 | 66.9 | 29.92 | 0.073 | 0.45 | 13.84 | 0
September | 4 | 1PM to 2PM | 81 | 65 | 55.9 | 66.9 | 29.92 | 0.073 | 0.45 | 13.84 | 0
September | 4 | 2PM to 3PM | 75.9 | 63.3 | 55.9 | 66.9 | 28.69 | 0.0737 | 0.45 | 13.71 | 0
September | 4 | 3PM to 4PM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
September | 4 | 4PM to 5PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
September | 4 | 5PM to 6PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
September | 4 | 6PM to 7PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
September | 4 | 7PM to 8PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 4 | 8PM to 9PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 4 | 9PM to 10PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 4 | 10PM to 11PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 4 | 11PM to 12AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 5 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 5 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 5 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 5 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 5 | 4AM to 5AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 5 | 5AM to 6AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 5 | 6AM to 7AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
September | 5 | 7AM to 8AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 5 | 8AM to 9AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 5 | 9AM to 10AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 5 | 10AM to 11AM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
September | 5 | 11AM to 12PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 5 | 12PM to 1PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
September | 5 | 1PM to 2PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 5 | 2PM to 3PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
September | 5 | 3PM to 4PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 5 | 4PM to 5PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 5 | 5PM to 6PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 5 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 5 | 7PM to 8PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 5 | 8PM to 9PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 5 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 5 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 5 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 6 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 6 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 6 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 6 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 6 | 4AM to 5AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
September | 6 | 5AM to 6AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
September | 6 | 6AM to 7AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 6 | 7AM to 8AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 6 | 8AM to 9AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 6 | 9AM to 10AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 6 | 10AM to 11AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 6 | 11AM to 12PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 6 | 12PM to 1PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
September | 6 | 1PM to 2PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
September | 6 | 2PM to 3PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
September | 6 | 3PM to 4PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
September | 6 | 4PM to 5PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
September | 6 | 5PM to 6PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 6 | 6PM to 7PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 6 | 7PM to 8PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 6 | 8PM to 9PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 6 | 9PM to 10PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 6 | 10PM to 11PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 6 | 11PM to 12AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 7 | 12AM to 1AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
September | 7 | 1AM to 2AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
September | 7 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
September | 7 | 3AM to 4AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
September | 7 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 7 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 7 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 7 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 7 | 8AM to 9AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
September | 7 | 9AM to 10AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
September | 7 | 10AM to 11AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 7 | 11AM to 12PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 7 | 12PM to 1PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 7 | 1PM to 2PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
September | 7 | 2PM to 3PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
September | 7 | 3PM to 4PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
September | 7 | 4PM to 5PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
September | 7 | 5PM to 6PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
September | 7 | 6PM to 7PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 7 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 7 | 8PM to 9PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 7 | 9PM to 10PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 7 | 10PM to 11PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 7 | 11PM to 12AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 8 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 8 | 1AM to 2AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 8 | 2AM to 3AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 8 | 3AM to 4AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 8 | 4AM to 5AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 8 | 5AM to 6AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 8 | 6AM to 7AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 8 | 7AM to 8AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
September | 8 | 8AM to 9AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 8 | 9AM to 10AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
September | 8 | 10AM to 11AM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
September | 8 | 11AM to 12PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
September | 8 | 12PM to 1PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
September | 8 | 1PM to 2PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
September | 8 | 2PM to 3PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
September | 8 | 3PM to 4PM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
September | 8 | 4PM to 5PM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
September | 8 | 5PM to 6PM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
September | 8 | 6PM to 7PM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
September | 8 | 7PM to 8PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 8 | 8PM to 9PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 8 | 9PM to 10PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 8 | 10PM to 11PM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 8 | 11PM to 12AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 9 | 12AM to 1AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 9 | 1AM to 2AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 9 | 2AM to 3AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 9 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 9 | 4AM to 5AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 9 | 5AM to 6AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 9 | 6AM to 7AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
September | 9 | 7AM to 8AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 9 | 8AM to 9AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
September | 9 | 9AM to 10AM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 9 | 10AM to 11AM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 9 | 11AM to 12PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 9 | 12PM to 1PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 9 | 1PM to 2PM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
September | 9 | 2PM to 3PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 9 | 3PM to 4PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
September | 9 | 4PM to 5PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 9 | 5PM to 6PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 9 | 6PM to 7PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
September | 9 | 7PM to 8PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
September | 9 | 8PM to 9PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 9 | 9PM to 10PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 9 | 10PM to 11PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 9 | 11PM to 12AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 10 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 10 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 10 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 10 | 3AM to 4AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 10 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 10 | 5AM to 6AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 10 | 6AM to 7AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 10 | 7AM to 8AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 10 | 8AM to 9AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 10 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 10 | 10AM to 11AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
September | 10 | 11AM to 12PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
September | 10 | 12PM to 1PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 10 | 1PM to 2PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 10 | 2PM to 3PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
September | 10 | 3PM to 4PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
September | 10 | 4PM to 5PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 10 | 5PM to 6PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 10 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 10 | 7PM to 8PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 10 | 8PM to 9PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 10 | 9PM to 10PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 10 | 10PM to 11PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 10 | 11PM to 12AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 12AM to 1AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 1AM to 2AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 2AM to 3AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 3AM to 4AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 11 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 5AM to 6AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 6AM to 7AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 11 | 7AM to 8AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 11 | 8AM to 9AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
September | 11 | 9AM to 10AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 11 | 10AM to 11AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 11 | 11AM to 12PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 11 | 12PM to 1PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
September | 11 | 1PM to 2PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
September | 11 | 2PM to 3PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 11 | 3PM to 4PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 11 | 4PM to 5PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
September | 11 | 5PM to 6PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 11 | 6PM to 7PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 11 | 7PM to 8PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 11 | 8PM to 9PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 9PM to 10PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 10PM to 11PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 11 | 11PM to 12AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 12 | 12AM to 1AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 12 | 1AM to 2AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 12 | 2AM to 3AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 12 | 3AM to 4AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 12 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 12 | 5AM to 6AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 12 | 6AM to 7AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 12 | 7AM to 8AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
September | 12 | 8AM to 9AM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
September | 12 | 9AM to 10AM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
September | 12 | 10AM to 11AM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 12 | 11AM to 12PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 12 | 12PM to 1PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
September | 12 | 1PM to 2PM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
September | 12 | 2PM to 3PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
September | 12 | 3PM to 4PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
September | 12 | 4PM to 5PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 12 | 5PM to 6PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
September | 12 | 6PM to 7PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
September | 12 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 12 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 12 | 9PM to 10PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
September | 12 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 12 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 13 | 12AM to 1AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
September | 13 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
September | 13 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 13 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
September | 13 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
September | 13 | 5AM to 6AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
September | 13 | 6AM to 7AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 13 | 7AM to 8AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
September | 13 | 8AM to 9AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 13 | 9AM to 10AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
September | 13 | 10AM to 11AM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 13 | 11AM to 12PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
September | 13 | 12PM to 1PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
September | 13 | 1PM to 2PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
September | 13 | 2PM to 3PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
September | 13 | 3PM to 4PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
September | 13 | 4PM to 5PM | 64 | 56.9 | 52 | 57.8 | 24.36 | 0.0754 | 0.39 | 13.38 | 0
September | 13 | 5PM to 6PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
September | 13 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
September | 13 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 13 | 8PM to 9PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 13 | 9PM to 10PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 13 | 10PM to 11PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 13 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 14 | 12AM to 1AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 14 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 14 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 14 | 3AM to 4AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 14 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 14 | 5AM to 6AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 14 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 14 | 7AM to 8AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 14 | 8AM to 9AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
September | 14 | 9AM to 10AM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 14 | 10AM to 11AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 14 | 11AM to 12PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 14 | 12PM to 1PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
September | 14 | 1PM to 2PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
September | 14 | 2PM to 3PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
September | 14 | 3PM to 4PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
September | 14 | 4PM to 5PM | 66.9 | 57.5 | 51.1 | 55.9 | 24.76 | 0.075 | 0.38 | 13.44 | 0
September | 14 | 5PM to 6PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
September | 14 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
September | 14 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
September | 14 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 14 | 9PM to 10PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 14 | 10PM to 11PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
September | 14 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 15 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 15 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 15 | 2AM to 3AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 15 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 15 | 4AM to 5AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 15 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
September | 15 | 6AM to 7AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
September | 15 | 7AM to 8AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
September | 15 | 8AM to 9AM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
September | 15 | 9AM to 10AM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
September | 15 | 10AM to 11AM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
September | 15 | 11AM to 12PM | 75 | 65.2 | 60.1 | 77.8 | 30.17 | 0.0737 | 0.52 | 13.72 | 0
September | 15 | 12PM to 1PM | 80.1 | 63.7 | 54 | 62.2 | 28.96 | 0.0731 | 0.42 | 13.8 | 0
September | 15 | 1PM to 2PM | 86 | 64.4 | 51.1 | 55.9 | 29.41 | 0.0724 | 0.38 | 13.93 | 0
September | 15 | 2PM to 3PM | 84.9 | 65.3 | 54 | 62.2 | 30.14 | 0.0725 | 0.42 | 13.92 | 0
September | 15 | 3PM to 4PM | 79 | 61 | 48.9 | 51.5 | 27.02 | 0.0733 | 0.35 | 13.74 | 0
September | 15 | 4PM to 5PM | 79 | 59.8 | 46 | 46.1 | 26.18 | 0.0734 | 0.31 | 13.72 | 0
September | 15 | 5PM to 6PM | 77 | 59.4 | 46.9 | 47.8 | 25.95 | 0.0736 | 0.32 | 13.68 | 0
September | 15 | 6PM to 7PM | 75 | 58.3 | 46 | 46.1 | 25.22 | 0.0739 | 0.31 | 13.62 | 0
September | 15 | 7PM to 8PM | 71.1 | 57.7 | 48 | 49.8 | 24.82 | 0.0744 | 0.34 | 13.53 | 0
September | 15 | 8PM to 9PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
September | 15 | 9PM to 10PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 15 | 10PM to 11PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
September | 15 | 11PM to 12AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
September | 16 | 12AM to 1AM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 16 | 1AM to 2AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
September | 16 | 2AM to 3AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 16 | 3AM to 4AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 16 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 16 | 5AM to 6AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 16 | 6AM to 7AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 16 | 7AM to 8AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
September | 16 | 8AM to 9AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
September | 16 | 9AM to 10AM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
September | 16 | 10AM to 11AM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
September | 16 | 11AM to 12PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
September | 16 | 12PM to 1PM | 86 | 64.4 | 51.1 | 55.9 | 29.41 | 0.0724 | 0.38 | 13.93 | 0
September | 16 | 1PM to 2PM | 84 | 63.2 | 50 | 53.6 | 28.58 | 0.0726 | 0.36 | 13.87 | 0
September | 16 | 2PM to 3PM | 84.9 | 63.1 | 48.9 | 51.5 | 28.46 | 0.0725 | 0.35 | 13.89 | 0
September | 16 | 3PM to 4PM | 77 | 61.3 | 51.1 | 55.9 | 27.22 | 0.0736 | 0.38 | 13.7 | 0
September | 16 | 4PM to 5PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
September | 16 | 5PM to 6PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 16 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 16 | 7PM to 8PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 16 | 8PM to 9PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 16 | 9PM to 10PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 16 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 16 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 17 | 12AM to 1AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 17 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 17 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
September | 17 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
September | 17 | 4AM to 5AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
September | 17 | 5AM to 6AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
September | 17 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
September | 17 | 7AM to 8AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
September | 17 | 8AM to 9AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
September | 17 | 9AM to 10AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 17 | 10AM to 11AM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 17 | 11AM to 12PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 17 | 12PM to 1PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 17 | 1PM to 2PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
September | 17 | 2PM to 3PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
September | 17 | 3PM to 4PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 17 | 4PM to 5PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
September | 17 | 5PM to 6PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
September | 17 | 6PM to 7PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
September | 17 | 7PM to 8PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 17 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 17 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 17 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 17 | 11PM to 12AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 18 | 12AM to 1AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 18 | 1AM to 2AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 18 | 2AM to 3AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 18 | 3AM to 4AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 18 | 4AM to 5AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 18 | 5AM to 6AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 18 | 6AM to 7AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 18 | 7AM to 8AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 18 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
September | 18 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 18 | 10AM to 11AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 18 | 11AM to 12PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
September | 18 | 12PM to 1PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
September | 18 | 1PM to 2PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 18 | 2PM to 3PM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
September | 18 | 3PM to 4PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
September | 18 | 4PM to 5PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
September | 18 | 5PM to 6PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
September | 18 | 6PM to 7PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 18 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
September | 18 | 8PM to 9PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 18 | 9PM to 10PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 18 | 10PM to 11PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 18 | 11PM to 12AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 19 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 19 | 1AM to 2AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
September | 19 | 2AM to 3AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
September | 19 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 19 | 4AM to 5AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 19 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
September | 19 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 19 | 7AM to 8AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 19 | 8AM to 9AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 19 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 19 | 10AM to 11AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 19 | 11AM to 12PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
September | 19 | 12PM to 1PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
September | 19 | 1PM to 2PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 19 | 2PM to 3PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 19 | 3PM to 4PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
September | 19 | 4PM to 5PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 19 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 19 | 6PM to 7PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 19 | 7PM to 8PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 19 | 8PM to 9PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 19 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 19 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 19 | 11PM to 12AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 20 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 20 | 1AM to 2AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 20 | 2AM to 3AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
September | 20 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 20 | 4AM to 5AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 20 | 5AM to 6AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 20 | 6AM to 7AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 20 | 7AM to 8AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 20 | 8AM to 9AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
September | 20 | 9AM to 10AM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 20 | 10AM to 11AM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 20 | 11AM to 12PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
September | 20 | 12PM to 1PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
September | 20 | 1PM to 2PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
September | 20 | 2PM to 3PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 20 | 3PM to 4PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
September | 20 | 4PM to 5PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 20 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 20 | 6PM to 7PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 20 | 7PM to 8PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 20 | 8PM to 9PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 20 | 9PM to 10PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 20 | 10PM to 11PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 20 | 11PM to 12AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 21 | 12AM to 1AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 21 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 21 | 2AM to 3AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 21 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 21 | 4AM to 5AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 21 | 5AM to 6AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 21 | 6AM to 7AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 21 | 7AM to 8AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 21 | 8AM to 9AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 21 | 9AM to 10AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
September | 21 | 10AM to 11AM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 21 | 11AM to 12PM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 21 | 12PM to 1PM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
September | 21 | 1PM to 2PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
September | 21 | 2PM to 3PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
September | 21 | 3PM to 4PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 21 | 4PM to 5PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 21 | 5PM to 6PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 21 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 21 | 7PM to 8PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 21 | 8PM to 9PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 21 | 9PM to 10PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 21 | 10PM to 11PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 21 | 11PM to 12AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 22 | 12AM to 1AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 22 | 1AM to 2AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 22 | 2AM to 3AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 22 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 22 | 4AM to 5AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 22 | 5AM to 6AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 22 | 6AM to 7AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
September | 22 | 7AM to 8AM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 22 | 8AM to 9AM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 22 | 9AM to 10AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 22 | 10AM to 11AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
September | 22 | 11AM to 12PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 22 | 12PM to 1PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
September | 22 | 1PM to 2PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
September | 22 | 2PM to 3PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 22 | 3PM to 4PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 22 | 4PM to 5PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 22 | 5PM to 6PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 22 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 22 | 7PM to 8PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
September | 22 | 8PM to 9PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 22 | 9PM to 10PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 22 | 10PM to 11PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 22 | 11PM to 12AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 12AM to 1AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 1AM to 2AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 2AM to 3AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 3AM to 4AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 23 | 4AM to 5AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 23 | 5AM to 6AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 23 | 6AM to 7AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 23 | 7AM to 8AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
September | 23 | 8AM to 9AM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
September | 23 | 9AM to 10AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
September | 23 | 10AM to 11AM | 63 | 61.1 | 60.1 | 77.8 | 27.22 | 0.0754 | 0.52 | 13.41 | 0
September | 23 | 11AM to 12PM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
September | 23 | 12PM to 1PM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
September | 23 | 1PM to 2PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
September | 23 | 2PM to 3PM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
September | 23 | 3PM to 4PM | 78.1 | 65.1 | 57.9 | 72 | 30 | 0.0733 | 0.48 | 13.78 | 0
September | 23 | 4PM to 5PM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
September | 23 | 5PM to 6PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
September | 23 | 6PM to 7PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
September | 23 | 7PM to 8PM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 23 | 8PM to 9PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
September | 23 | 9PM to 10PM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
September | 23 | 10PM to 11PM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
September | 23 | 11PM to 12AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
September | 24 | 12AM to 1AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 24 | 1AM to 2AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
September | 24 | 2AM to 3AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 24 | 3AM to 4AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
September | 24 | 4AM to 5AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 24 | 5AM to 6AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 24 | 6AM to 7AM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
September | 24 | 7AM to 8AM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
September | 24 | 8AM to 9AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
September | 24 | 9AM to 10AM | 66.9 | 62.5 | 60.1 | 77.8 | 28.19 | 0.0748 | 0.52 | 13.51 | 0
September | 24 | 10AM to 11AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
September | 24 | 11AM to 12PM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
September | 24 | 12PM to 1PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
September | 24 | 1PM to 2PM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
September | 24 | 2PM to 3PM | 75 | 63.5 | 57 | 69.6 | 28.89 | 0.0738 | 0.47 | 13.69 | 0
September | 24 | 3PM to 4PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
September | 24 | 4PM to 5PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
September | 24 | 5PM to 6PM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 24 | 6PM to 7PM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
September | 24 | 7PM to 8PM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
September | 24 | 8PM to 9PM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
September | 24 | 9PM to 10PM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
September | 24 | 10PM to 11PM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
September | 24 | 11PM to 12AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 12AM to 1AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 1AM to 2AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
September | 25 | 2AM to 3AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 3AM to 4AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 4AM to 5AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 5AM to 6AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 6AM to 7AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 25 | 7AM to 8AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
September | 25 | 8AM to 9AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
September | 25 | 9AM to 10AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
September | 25 | 10AM to 11AM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
September | 25 | 11AM to 12PM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 25 | 12PM to 1PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
September | 25 | 1PM to 2PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
September | 25 | 2PM to 3PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
September | 25 | 3PM to 4PM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
September | 25 | 4PM to 5PM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
September | 25 | 5PM to 6PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 25 | 6PM to 7PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 25 | 7PM to 8PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 25 | 8PM to 9PM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 25 | 9PM to 10PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 25 | 10PM to 11PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 25 | 11PM to 12AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 12AM to 1AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 1AM to 2AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 2AM to 3AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 3AM to 4AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 4AM to 5AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
September | 26 | 5AM to 6AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
September | 26 | 6AM to 7AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 7AM to 8AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 26 | 8AM to 9AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 26 | 9AM to 10AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 26 | 10AM to 11AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 26 | 11AM to 12PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 26 | 12PM to 1PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 26 | 1PM to 2PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 26 | 2PM to 3PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 26 | 3PM to 4PM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 26 | 4PM to 5PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 26 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 26 | 6PM to 7PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 26 | 7PM to 8PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
September | 26 | 8PM to 9PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 26 | 9PM to 10PM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 26 | 10PM to 11PM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 26 | 11PM to 12AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 27 | 12AM to 1AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 1AM to 2AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 2AM to 3AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 27 | 3AM to 4AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 4AM to 5AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 5AM to 6AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
September | 27 | 6AM to 7AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 27 | 7AM to 8AM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 27 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
September | 27 | 9AM to 10AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
September | 27 | 10AM to 11AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 27 | 11AM to 12PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
September | 27 | 12PM to 1PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
September | 27 | 1PM to 2PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
September | 27 | 2PM to 3PM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 27 | 3PM to 4PM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 27 | 4PM to 5PM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
September | 27 | 5PM to 6PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 27 | 6PM to 7PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 27 | 7PM to 8PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 27 | 8PM to 9PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 27 | 9PM to 10PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 27 | 10PM to 11PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 27 | 11PM to 12AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 28 | 12AM to 1AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 28 | 1AM to 2AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 28 | 2AM to 3AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 28 | 3AM to 4AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 28 | 4AM to 5AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 28 | 5AM to 6AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 28 | 6AM to 7AM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
September | 28 | 7AM to 8AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
September | 28 | 8AM to 9AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 28 | 9AM to 10AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
September | 28 | 10AM to 11AM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
September | 28 | 11AM to 12PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
September | 28 | 12PM to 1PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
September | 28 | 1PM to 2PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
September | 28 | 2PM to 3PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
September | 28 | 3PM to 4PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
September | 28 | 4PM to 5PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
September | 28 | 5PM to 6PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 28 | 6PM to 7PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 28 | 7PM to 8PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 28 | 8PM to 9PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
September | 28 | 9PM to 10PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 28 | 10PM to 11PM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 28 | 11PM to 12AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 29 | 12AM to 1AM | 61 | 59.1 | 57.9 | 72 | 25.82 | 0.0757 | 0.48 | 13.34 | 0
September | 29 | 1AM to 2AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
September | 29 | 2AM to 3AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 29 | 3AM to 4AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 29 | 4AM to 5AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 29 | 5AM to 6AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 29 | 6AM to 7AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 29 | 7AM to 8AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
September | 29 | 8AM to 9AM | 64.9 | 59.4 | 55.9 | 66.9 | 26 | 0.0752 | 0.45 | 13.43 | 0
September | 29 | 9AM to 10AM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
September | 29 | 10AM to 11AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
September | 29 | 11AM to 12PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
September | 29 | 12PM to 1PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
September | 29 | 1PM to 2PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
September | 29 | 2PM to 3PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
September | 29 | 3PM to 4PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
September | 29 | 4PM to 5PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
September | 29 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 29 | 6PM to 7PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
September | 29 | 7PM to 8PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
September | 29 | 8PM to 9PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 29 | 9PM to 10PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
September | 29 | 10PM to 11PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 29 | 11PM to 12AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 30 | 12AM to 1AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
September | 30 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 30 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
September | 30 | 3AM to 4AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
September | 30 | 4AM to 5AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
September | 30 | 5AM to 6AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
September | 30 | 6AM to 7AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
September | 30 | 7AM to 8AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
September | 30 | 8AM to 9AM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
September | 30 | 9AM to 10AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
September | 30 | 10AM to 11AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
September | 30 | 11AM to 12PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
September | 30 | 12PM to 1PM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
September | 30 | 1PM to 2PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
September | 30 | 2PM to 3PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
September | 30 | 3PM to 4PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
September | 30 | 4PM to 5PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
September | 30 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
September | 30 | 6PM to 7PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
September | 30 | 7PM to 8PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
September | 30 | 8PM to 9PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 30 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 30 | 10PM to 11PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
September | 30 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 1AM to 2AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 3AM to 4AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 1 | 4AM to 5AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
October | 1 | 5AM to 6AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
October | 1 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
October | 1 | 7AM to 8AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 8AM to 9AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 9AM to 10AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 10AM to 11AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
October | 1 | 11AM to 12PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
October | 1 | 12PM to 1PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
October | 1 | 1PM to 2PM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
October | 1 | 2PM to 3PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
October | 1 | 3PM to 4PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
October | 1 | 4PM to 5PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 5PM to 6PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 1 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 1 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 9PM to 10PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 10PM to 11PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 1 | 11PM to 12AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 2 | 12AM to 1AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 1AM to 2AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 2AM to 3AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 3AM to 4AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 5AM to 6AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 2 | 6AM to 7AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
October | 2 | 7AM to 8AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
October | 2 | 8AM to 9AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
October | 2 | 9AM to 10AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 2 | 10AM to 11AM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
October | 2 | 11AM to 12PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
October | 2 | 12PM to 1PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
October | 2 | 1PM to 2PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
October | 2 | 2PM to 3PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 2 | 3PM to 4PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
October | 2 | 4PM to 5PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 2 | 5PM to 6PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 2 | 6PM to 7PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 2 | 7PM to 8PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 2 | 8PM to 9PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 2 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 2 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 2 | 11PM to 12AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 3 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 3 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 3 | 2AM to 3AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 3 | 3AM to 4AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 3 | 4AM to 5AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 3 | 5AM to 6AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
October | 3 | 6AM to 7AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 3 | 7AM to 8AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 3 | 8AM to 9AM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
October | 3 | 9AM to 10AM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
October | 3 | 10AM to 11AM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
October | 3 | 11AM to 12PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
October | 3 | 12PM to 1PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
October | 3 | 1PM to 2PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 3 | 2PM to 3PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
October | 3 | 3PM to 4PM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
October | 3 | 4PM to 5PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
October | 3 | 5PM to 6PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 3 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
October | 3 | 7PM to 8PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 3 | 8PM to 9PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 3 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 3 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 3 | 11PM to 12AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 4 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 4 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
October | 4 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 4 | 3AM to 4AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
October | 4 | 4AM to 5AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 4 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
October | 4 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 4 | 7AM to 8AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
October | 4 | 8AM to 9AM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 4 | 9AM to 10AM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
October | 4 | 10AM to 11AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 4 | 11AM to 12PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
October | 4 | 12PM to 1PM | 71.1 | 56.8 | 46 | 46.1 | 24.26 | 0.0745 | 0.31 | 13.52 | 0
October | 4 | 1PM to 2PM | 70 | 57.7 | 48.9 | 51.5 | 24.83 | 0.0746 | 0.35 | 13.51 | 0
October | 4 | 2PM to 3PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
October | 4 | 3PM to 4PM | 66.9 | 56.1 | 48 | 49.8 | 23.81 | 0.075 | 0.34 | 13.42 | 0
October | 4 | 4PM to 5PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
October | 4 | 5PM to 6PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 4 | 6PM to 7PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 4 | 7PM to 8PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 4 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 4 | 9PM to 10PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 4 | 10PM to 11PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 4 | 11PM to 12AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 5 | 12AM to 1AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
October | 5 | 1AM to 2AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
October | 5 | 2AM to 3AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
October | 5 | 3AM to 4AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
October | 5 | 4AM to 5AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
October | 5 | 5AM to 6AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
October | 5 | 6AM to 7AM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
October | 5 | 7AM to 8AM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 5 | 8AM to 9AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
October | 5 | 9AM to 10AM | 68 | 55.6 | 46 | 46.1 | 23.51 | 0.0749 | 0.31 | 13.44 | 0
October | 5 | 10AM to 11AM | 71.1 | 57.7 | 48 | 49.8 | 24.82 | 0.0744 | 0.34 | 13.53 | 0
October | 5 | 11AM to 12PM | 71.1 | 58.6 | 50 | 53.6 | 25.43 | 0.0744 | 0.36 | 13.54 | 0
October | 5 | 12PM to 1PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
October | 5 | 1PM to 2PM | 73.9 | 59.1 | 48.9 | 51.5 | 25.79 | 0.074 | 0.35 | 13.61 | 0
October | 5 | 2PM to 3PM | 77 | 59 | 46 | 46.1 | 25.7 | 0.0736 | 0.31 | 13.67 | 0
October | 5 | 3PM to 4PM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
October | 5 | 4PM to 5PM | 73.9 | 59.1 | 48.9 | 51.5 | 25.79 | 0.074 | 0.35 | 13.61 | 0
October | 5 | 5PM to 6PM | 71.1 | 57.7 | 48 | 49.8 | 24.82 | 0.0744 | 0.34 | 13.53 | 0
October | 5 | 6PM to 7PM | 71.1 | 56.3 | 45 | 44.3 | 23.96 | 0.0745 | 0.3 | 13.51 | 0
October | 5 | 7PM to 8PM | 66.9 | 55.1 | 46 | 46.1 | 23.25 | 0.075 | 0.31 | 13.41 | 0
October | 5 | 8PM to 9PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
October | 5 | 9PM to 10PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 5 | 10PM to 11PM | 63 | 54 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.32 | 0
October | 5 | 11PM to 12AM | 62.1 | 53.6 | 46.9 | 47.8 | 22.32 | 0.0757 | 0.32 | 13.29 | 0
October | 6 | 12AM to 1AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 6 | 1AM to 2AM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
October | 6 | 2AM to 3AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
October | 6 | 3AM to 4AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 6 | 4AM to 5AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
October | 6 | 5AM to 6AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
October | 6 | 6AM to 7AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 6 | 7AM to 8AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 6 | 8AM to 9AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
October | 6 | 9AM to 10AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
October | 6 | 10AM to 11AM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
October | 6 | 11AM to 12PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
October | 6 | 12PM to 1PM | 72 | 57.5 | 46.9 | 47.8 | 24.73 | 0.0743 | 0.32 | 13.55 | 0
October | 6 | 1PM to 2PM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
October | 6 | 2PM to 3PM | 75.9 | 59.5 | 48 | 49.8 | 26 | 0.0738 | 0.34 | 13.65 | 0
October | 6 | 3PM to 4PM | 78.1 | 59.4 | 46 | 46.1 | 25.96 | 0.0735 | 0.31 | 13.7 | 0
October | 6 | 4PM to 5PM | 73 | 54.8 | 39 | 35.1 | 23.02 | 0.0742 | 0.24 | 13.54 | 0
October | 6 | 5PM to 6PM | 68 | 52.7 | 39 | 35.1 | 21.8 | 0.075 | 0.24 | 13.41 | 0
October | 6 | 6PM to 7PM | 64.9 | 53 | 43 | 41 | 21.97 | 0.0754 | 0.28 | 13.35 | 0
October | 6 | 7PM to 8PM | 64 | 51.8 | 41 | 38 | 21.28 | 0.0755 | 0.26 | 13.32 | 0
October | 6 | 8PM to 9PM | 63 | 50.6 | 39 | 35.1 | 20.58 | 0.0757 | 0.24 | 13.28 | 0
October | 6 | 9PM to 10PM | 61 | 53.7 | 48 | 49.8 | 22.37 | 0.0759 | 0.34 | 13.27 | 0
October | 6 | 10PM to 11PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
October | 6 | 11PM to 12AM | 60.1 | 50.6 | 42.1 | 39.6 | 20.57 | 0.0761 | 0.27 | 13.22 | 0
October | 7 | 12AM to 1AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 7 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
October | 7 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 7 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 7 | 4AM to 5AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
October | 7 | 5AM to 6AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
October | 7 | 6AM to 7AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
October | 7 | 7AM to 8AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
October | 7 | 8AM to 9AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
October | 7 | 9AM to 10AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 7 | 10AM to 11AM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
October | 7 | 11AM to 12PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
October | 7 | 12PM to 1PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
October | 7 | 1PM to 2PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
October | 7 | 2PM to 3PM | 66.9 | 58.5 | 53.1 | 60.1 | 25.43 | 0.075 | 0.41 | 13.46 | 0
October | 7 | 3PM to 4PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
October | 7 | 4PM to 5PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
October | 7 | 5PM to 6PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 7 | 6PM to 7PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
October | 7 | 7PM to 8PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
October | 7 | 8PM to 9PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
October | 7 | 9PM to 10PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
October | 7 | 10PM to 11PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
October | 7 | 11PM to 12AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
October | 8 | 12AM to 1AM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
October | 8 | 1AM to 2AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 8 | 2AM to 3AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 8 | 3AM to 4AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
October | 8 | 4AM to 5AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 8 | 5AM to 6AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
October | 8 | 6AM to 7AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
October | 8 | 7AM to 8AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
October | 8 | 8AM to 9AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
October | 8 | 9AM to 10AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
October | 8 | 10AM to 11AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
October | 8 | 11AM to 12PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
October | 8 | 12PM to 1PM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
October | 8 | 1PM to 2PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
October | 8 | 2PM to 3PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
October | 8 | 3PM to 4PM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
October | 8 | 4PM to 5PM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
October | 8 | 5PM to 6PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 8 | 6PM to 7PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 8 | 7PM to 8PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 8 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 8 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 8 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 8 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 9 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 9 | 1AM to 2AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 2AM to 3AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 5AM to 6AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 9 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 9 | 7AM to 8AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 9 | 8AM to 9AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
October | 9 | 9AM to 10AM | 64 | 54.4 | 46.9 | 47.8 | 22.8 | 0.0754 | 0.32 | 13.35 | 0
October | 9 | 10AM to 11AM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
October | 9 | 11AM to 12PM | 68 | 56.5 | 48 | 49.8 | 24.08 | 0.0749 | 0.34 | 13.45 | 0
October | 9 | 12PM to 1PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
October | 9 | 1PM to 2PM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
October | 9 | 2PM to 3PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
October | 9 | 3PM to 4PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 9 | 4PM to 5PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
October | 9 | 5PM to 6PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 9 | 6PM to 7PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 9 | 7PM to 8PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
October | 9 | 8PM to 9PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 9 | 9PM to 10PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 9 | 10PM to 11PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 9 | 11PM to 12AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 10 | 12AM to 1AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 10 | 1AM to 2AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 10 | 2AM to 3AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 10 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 10 | 4AM to 5AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
October | 10 | 5AM to 6AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 10 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 10 | 7AM to 8AM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
October | 10 | 8AM to 9AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 10 | 9AM to 10AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 10 | 10AM to 11AM | 62.1 | 54.5 | 48.9 | 51.5 | 22.9 | 0.0757 | 0.35 | 13.31 | 0
October | 10 | 11AM to 12PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 10 | 12PM to 1PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
October | 10 | 1PM to 2PM | 66 | 55.2 | 46.9 | 47.8 | 23.28 | 0.0752 | 0.32 | 13.4 | 0
October | 10 | 2PM to 3PM | 64.9 | 54.3 | 46 | 46.1 | 22.77 | 0.0753 | 0.31 | 13.36 | 0
October | 10 | 3PM to 4PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
October | 10 | 4PM to 5PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 10 | 5PM to 6PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
October | 10 | 6PM to 7PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 10 | 7PM to 8PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 10 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 10 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 10 | 10PM to 11PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
October | 10 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 11 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 11 | 1AM to 2AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
October | 11 | 2AM to 3AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
October | 11 | 3AM to 4AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
October | 11 | 4AM to 5AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
October | 11 | 5AM to 6AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
October | 11 | 6AM to 7AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
October | 11 | 7AM to 8AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 11 | 8AM to 9AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 11 | 9AM to 10AM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 11 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
October | 11 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
October | 11 | 12PM to 1PM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
October | 11 | 1PM to 2PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
October | 11 | 2PM to 3PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
October | 11 | 3PM to 4PM | 64 | 53.5 | 45 | 44.3 | 22.26 | 0.0755 | 0.3 | 13.33 | 0
October | 11 | 4PM to 5PM | 62.1 | 52.3 | 44.1 | 42.8 | 21.54 | 0.0758 | 0.29 | 13.28 | 0
October | 11 | 5PM to 6PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
October | 11 | 6PM to 7PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
October | 11 | 7PM to 8PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
October | 11 | 8PM to 9PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
October | 11 | 9PM to 10PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
October | 11 | 10PM to 11PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 11 | 11PM to 12AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 12 | 12AM to 1AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 12 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 12 | 2AM to 3AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
October | 12 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 12 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 12 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 12 | 6AM to 7AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 12 | 7AM to 8AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 12 | 8AM to 9AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
October | 12 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
October | 12 | 10AM to 11AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
October | 12 | 11AM to 12PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
October | 12 | 12PM to 1PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
October | 12 | 1PM to 2PM | 70 | 57.2 | 48 | 49.8 | 24.56 | 0.0746 | 0.34 | 13.5 | 0
October | 12 | 2PM to 3PM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
October | 12 | 3PM to 4PM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
October | 12 | 4PM to 5PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
October | 12 | 5PM to 6PM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
October | 12 | 6PM to 7PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
October | 12 | 7PM to 8PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
October | 12 | 8PM to 9PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
October | 12 | 9PM to 10PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
October | 12 | 10PM to 11PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
October | 12 | 11PM to 12AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
October | 13 | 12AM to 1AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
October | 13 | 1AM to 2AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
October | 13 | 2AM to 3AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
October | 13 | 3AM to 4AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
October | 13 | 4AM to 5AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
October | 13 | 5AM to 6AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
October | 13 | 6AM to 7AM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
October | 13 | 7AM to 8AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
October | 13 | 8AM to 9AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
October | 13 | 9AM to 10AM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
October | 13 | 10AM to 11AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
October | 13 | 11AM to 12PM | 64.9 | 58.9 | 55 | 64.7 | 25.66 | 0.0752 | 0.44 | 13.42 | 0
October | 13 | 12PM to 1PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
October | 13 | 1PM to 2PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
October | 13 | 2PM to 3PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
October | 13 | 3PM to 4PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
October | 13 | 4PM to 5PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
October | 13 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
October | 13 | 6PM to 7PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
October | 13 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 13 | 8PM to 9PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
October | 13 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
October | 13 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 13 | 11PM to 12AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 14 | 12AM to 1AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 14 | 1AM to 2AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
October | 14 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 14 | 3AM to 4AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 14 | 4AM to 5AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 14 | 5AM to 6AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
October | 14 | 6AM to 7AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 14 | 7AM to 8AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
October | 14 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 14 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
October | 14 | 10AM to 11AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
October | 14 | 11AM to 12PM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
October | 14 | 12PM to 1PM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
October | 14 | 1PM to 2PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 14 | 2PM to 3PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
October | 14 | 3PM to 4PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 14 | 4PM to 5PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 14 | 5PM to 6PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 14 | 6PM to 7PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 14 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 14 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 14 | 9PM to 10PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 14 | 10PM to 11PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 14 | 11PM to 12AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 15 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 15 | 1AM to 2AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 15 | 2AM to 3AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
October | 15 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 15 | 4AM to 5AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
October | 15 | 5AM to 6AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
October | 15 | 6AM to 7AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 15 | 7AM to 8AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 15 | 8AM to 9AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 15 | 9AM to 10AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 15 | 10AM to 11AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 15 | 11AM to 12PM | 64.9 | 55.3 | 48 | 49.8 | 23.33 | 0.0753 | 0.34 | 13.37 | 0
October | 15 | 12PM to 1PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.36 | 0
October | 15 | 1PM to 2PM | 64.9 | 53 | 43 | 41 | 21.97 | 0.0754 | 0.28 | 13.35 | 0
October | 15 | 2PM to 3PM | 64 | 54 | 46 | 46.1 | 22.55 | 0.0755 | 0.31 | 13.34 | 0
October | 15 | 3PM to 4PM | 63 | 53.5 | 46 | 46.1 | 22.29 | 0.0756 | 0.31 | 13.31 | 0
October | 15 | 4PM to 5PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 15 | 5PM to 6PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 15 | 6PM to 7PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 15 | 7PM to 8PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 15 | 8PM to 9PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 15 | 9PM to 10PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
October | 15 | 10PM to 11PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
October | 15 | 11PM to 12AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
October | 16 | 12AM to 1AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
October | 16 | 1AM to 2AM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
October | 16 | 2AM to 3AM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
October | 16 | 3AM to 4AM | 59 | 48.4 | 37.9 | 33.7 | 19.39 | 0.0763 | 0.23 | 13.17 | 0
October | 16 | 4AM to 5AM | 59 | 48.8 | 39 | 35.1 | 19.62 | 0.0763 | 0.24 | 13.18 | 0
October | 16 | 5AM to 6AM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
October | 16 | 6AM to 7AM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
October | 16 | 7AM to 8AM | 62.1 | 50.2 | 39 | 35.1 | 20.36 | 0.0758 | 0.24 | 13.26 | 0
October | 16 | 8AM to 9AM | 63 | 50.2 | 37.9 | 33.7 | 20.35 | 0.0757 | 0.23 | 13.28 | 0
October | 16 | 9AM to 10AM | 64 | 50.7 | 37.9 | 33.7 | 20.61 | 0.0755 | 0.23 | 13.3 | 0
October | 16 | 10AM to 11AM | 66 | 51.9 | 39 | 35.1 | 21.32 | 0.0752 | 0.24 | 13.36 | 0
October | 16 | 11AM to 12PM | 66.9 | 51.2 | 36 | 31.1 | 20.91 | 0.0751 | 0.21 | 13.37 | 0
October | 16 | 12PM to 1PM | 69.1 | 52.1 | 36 | 31.1 | 21.43 | 0.0748 | 0.21 | 13.42 | 0
October | 16 | 1PM to 2PM | 71.1 | 53 | 36 | 31.1 | 21.91 | 0.0746 | 0.21 | 13.47 | 0
October | 16 | 2PM to 3PM | 70 | 52.2 | 35.1 | 30 | 21.48 | 0.0747 | 0.2 | 13.44 | 0
October | 16 | 3PM to 4PM | 69.1 | 52.5 | 37 | 32.5 | 21.65 | 0.0748 | 0.22 | 13.43 | 0
October | 16 | 4PM to 5PM | 66.9 | 51.9 | 37.9 | 33.7 | 21.31 | 0.0751 | 0.23 | 13.38 | 0
October | 16 | 5PM to 6PM | 63 | 50.6 | 39 | 35.1 | 20.58 | 0.0757 | 0.24 | 13.28 | 0
October | 16 | 6PM to 7PM | 63 | 50.2 | 37.9 | 33.7 | 20.35 | 0.0757 | 0.23 | 13.28 | 0
October | 16 | 7PM to 8PM | 66.9 | 51.2 | 36 | 31.1 | 20.91 | 0.0751 | 0.21 | 13.37 | 0
October | 16 | 8PM to 9PM | 66.9 | 48.9 | 28.9 | 23 | 19.65 | 0.0752 | 0.16 | 13.34 | 0
October | 16 | 9PM to 10PM | 66 | 50.5 | 35.1 | 30 | 20.52 | 0.0753 | 0.2 | 13.34 | 0
October | 16 | 10PM to 11PM | 64.9 | 51 | 37.9 | 33.7 | 20.83 | 0.0754 | 0.23 | 13.33 | 0
October | 16 | 11PM to 12AM | 64 | 49 | 33.1 | 27.7 | 19.68 | 0.0756 | 0.19 | 13.28 | 0
October | 17 | 12AM to 1AM | 62.1 | 49.1 | 36 | 31.1 | 19.73 | 0.0758 | 0.21 | 13.24 | 0
October | 17 | 1AM to 2AM | 55.9 | 44.5 | 30.9 | 25.2 | 17.34 | 0.0768 | 0.17 | 13.07 | 0
October | 17 | 2AM to 3AM | 55.9 | 44.5 | 30.9 | 25.2 | 17.34 | 0.0768 | 0.17 | 13.07 | 0
October | 17 | 3AM to 4AM | 60.1 | 45.8 | 28.9 | 23 | 18 | 0.0762 | 0.16 | 13.17 | 0
October | 17 | 4AM to 5AM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
October | 17 | 5AM to 6AM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
October | 17 | 6AM to 7AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
October | 17 | 7AM to 8AM | 61 | 50.5 | 41 | 38 | 20.54 | 0.0759 | 0.26 | 13.24 | 0
October | 17 | 8AM to 9AM | 64 | 48.6 | 32 | 26.5 | 19.5 | 0.0756 | 0.18 | 13.28 | 0
October | 17 | 9AM to 10AM | 66 | 49.5 | 32 | 26.5 | 19.98 | 0.0753 | 0.18 | 13.33 | 0
October | 17 | 10AM to 11AM | 69.1 | 51.2 | 33.1 | 27.7 | 20.9 | 0.0749 | 0.19 | 13.41 | 0
October | 17 | 11AM to 12PM | 70 | 51.3 | 32 | 26.5 | 20.94 | 0.0747 | 0.18 | 13.43 | 0
October | 17 | 12PM to 1PM | 72 | 52.4 | 33.1 | 27.7 | 21.6 | 0.0744 | 0.19 | 13.49 | 0
October | 17 | 1PM to 2PM | 72 | 54.7 | 39.9 | 36.4 | 22.95 | 0.0744 | 0.25 | 13.51 | 0
October | 17 | 2PM to 3PM | 70 | 52.5 | 36 | 31.1 | 21.65 | 0.0747 | 0.21 | 13.45 | 0
October | 17 | 3PM to 4PM | 66 | 51.9 | 39 | 35.1 | 21.32 | 0.0752 | 0.24 | 13.36 | 0
October | 17 | 4PM to 5PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
October | 17 | 5PM to 6PM | 62.1 | 49.5 | 37 | 32.5 | 19.95 | 0.0758 | 0.22 | 13.25 | 0
October | 17 | 6PM to 7PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
October | 17 | 7PM to 8PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
October | 17 | 8PM to 9PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 17 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 17 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 17 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 18 | 12AM to 1AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 18 | 1AM to 2AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
October | 18 | 2AM to 3AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
October | 18 | 3AM to 4AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
October | 18 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
October | 18 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
October | 18 | 6AM to 7AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
October | 18 | 7AM to 8AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 18 | 8AM to 9AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 18 | 9AM to 10AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 18 | 10AM to 11AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
October | 18 | 11AM to 12PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
October | 18 | 12PM to 1PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
October | 18 | 1PM to 2PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
October | 18 | 2PM to 3PM | 66.9 | 56.1 | 48 | 49.8 | 23.81 | 0.075 | 0.34 | 13.42 | 0
October | 18 | 3PM to 4PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
October | 18 | 4PM to 5PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 18 | 5PM to 6PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
October | 18 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 18 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 18 | 8PM to 9PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
October | 18 | 9PM to 10PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
October | 18 | 10PM to 11PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 18 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 19 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 19 | 1AM to 2AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
October | 19 | 2AM to 3AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
October | 19 | 3AM to 4AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
October | 19 | 4AM to 5AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
October | 19 | 5AM to 6AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
October | 19 | 6AM to 7AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
October | 19 | 7AM to 8AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 19 | 8AM to 9AM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 19 | 9AM to 10AM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
October | 19 | 10AM to 11AM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
October | 19 | 11AM to 12PM | 69.1 | 54.4 | 42.1 | 39.6 | 22.76 | 0.0748 | 0.27 | 13.45 | 0
October | 19 | 12PM to 1PM | 75.9 | 56.7 | 41 | 38 | 24.16 | 0.0738 | 0.26 | 13.62 | 0
October | 19 | 1PM to 2PM | 75.9 | 57.4 | 43 | 41 | 24.63 | 0.0738 | 0.28 | 13.63 | 0
October | 19 | 2PM to 3PM | 78.1 | 58.7 | 44.1 | 42.8 | 25.43 | 0.0735 | 0.29 | 13.69 | 0
October | 19 | 3PM to 4PM | 72 | 54.4 | 39 | 35.1 | 22.76 | 0.0744 | 0.24 | 13.51 | 0
October | 19 | 4PM to 5PM | 70 | 54.7 | 42.1 | 39.6 | 22.97 | 0.0746 | 0.27 | 13.47 | 0
October | 19 | 5PM to 6PM | 68 | 51.7 | 36 | 31.1 | 21.17 | 0.075 | 0.21 | 13.4 | 0
October | 19 | 6PM to 7PM | 68 | 52.4 | 37.9 | 33.7 | 21.57 | 0.075 | 0.23 | 13.4 | 0
October | 19 | 7PM to 8PM | 64.9 | 53.5 | 44.1 | 42.8 | 22.24 | 0.0753 | 0.29 | 13.35 | 0
October | 19 | 8PM to 9PM | 64 | 51.1 | 39 | 35.1 | 20.84 | 0.0755 | 0.24 | 13.31 | 0
October | 19 | 9PM to 10PM | 64 | 50.7 | 37.9 | 33.7 | 20.61 | 0.0755 | 0.23 | 13.3 | 0
October | 19 | 10PM to 11PM | 60.1 | 50.6 | 42.1 | 39.6 | 20.57 | 0.0761 | 0.27 | 13.22 | 0
October | 19 | 11PM to 12AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
October | 20 | 12AM to 1AM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
October | 20 | 1AM to 2AM | 55.9 | 49.6 | 44.1 | 42.8 | 20.06 | 0.0767 | 0.29 | 13.12 | 0
October | 20 | 2AM to 3AM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
October | 20 | 3AM to 4AM | 55 | 48.7 | 43 | 41 | 19.57 | 0.0768 | 0.28 | 13.1 | 0
October | 20 | 4AM to 5AM | 54 | 47.8 | 42.1 | 39.6 | 19.09 | 0.077 | 0.27 | 13.06 | 0
October | 20 | 5AM to 6AM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
October | 20 | 6AM to 7AM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
October | 20 | 7AM to 8AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 20 | 8AM to 9AM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 20 | 9AM to 10AM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
October | 20 | 10AM to 11AM | 73.9 | 53 | 32 | 26.5 | 21.89 | 0.0742 | 0.18 | 13.53 | 0
October | 20 | 11AM to 12PM | 75.9 | 54.7 | 35.1 | 30 | 22.92 | 0.0739 | 0.2 | 13.59 | 0
October | 20 | 12PM to 1PM | 78.1 | 55.8 | 36 | 31.1 | 23.61 | 0.0736 | 0.21 | 13.65 | 0
October | 20 | 1PM to 2PM | 80.1 | 57.2 | 37.9 | 33.7 | 24.49 | 0.0733 | 0.23 | 13.71 | 0
October | 20 | 2PM to 3PM | 79 | 58.6 | 43 | 41 | 25.38 | 0.0734 | 0.28 | 13.71 | 0
October | 20 | 3PM to 4PM | 77 | 55.4 | 36 | 31.1 | 23.35 | 0.0737 | 0.21 | 13.62 | 0
October | 20 | 4PM to 5PM | 73.9 | 53.3 | 33.1 | 27.7 | 22.08 | 0.0742 | 0.19 | 13.54 | 0
October | 20 | 5PM to 6PM | 70 | 51.9 | 34 | 28.7 | 21.28 | 0.0747 | 0.2 | 13.44 | 0
October | 20 | 6PM to 7PM | 69.1 | 52.5 | 37 | 32.5 | 21.65 | 0.0748 | 0.22 | 13.43 | 0
October | 20 | 7PM to 8PM | 68 | 51.7 | 36 | 31.1 | 21.17 | 0.075 | 0.21 | 13.4 | 0
October | 20 | 8PM to 9PM | 64.9 | 51.8 | 39.9 | 36.4 | 21.25 | 0.0754 | 0.25 | 13.33 | 0
October | 20 | 9PM to 10PM | 64.9 | 51.4 | 39 | 35.1 | 21.06 | 0.0754 | 0.24 | 13.33 | 0
October | 20 | 10PM to 11PM | 61 | 51.3 | 43 | 41 | 21.01 | 0.0759 | 0.28 | 13.25 | 0
October | 20 | 11PM to 12AM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
October | 21 | 12AM to 1AM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
October | 21 | 1AM to 2AM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
October | 21 | 2AM to 3AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
October | 21 | 3AM to 4AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 21 | 4AM to 5AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
October | 21 | 5AM to 6AM | 55 | 49.6 | 45 | 44.3 | 20.07 | 0.0768 | 0.3 | 13.11 | 0
October | 21 | 6AM to 7AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
October | 21 | 7AM to 8AM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
October | 21 | 8AM to 9AM | 63 | 56.5 | 52 | 57.8 | 24.1 | 0.0755 | 0.39 | 13.35 | 0
October | 21 | 9AM to 10AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
October | 21 | 10AM to 11AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
October | 21 | 11AM to 12PM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
October | 21 | 12PM to 1PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
October | 21 | 1PM to 2PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
October | 21 | 2PM to 3PM | 77 | 59 | 46 | 46.1 | 25.7 | 0.0736 | 0.31 | 13.67 | 0
October | 21 | 3PM to 4PM | 73 | 57.9 | 46.9 | 47.8 | 24.99 | 0.0742 | 0.32 | 13.57 | 0
October | 21 | 4PM to 5PM | 68 | 55.6 | 46 | 46.1 | 23.51 | 0.0749 | 0.31 | 13.44 | 0
October | 21 | 5PM to 6PM | 63 | 53 | 45 | 44.3 | 22 | 0.0756 | 0.3 | 13.31 | 0
October | 21 | 6PM to 7PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
October | 21 | 7PM to 8PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
October | 21 | 8PM to 9PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 21 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 21 | 10PM to 11PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 21 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 22 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
October | 22 | 1AM to 2AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
October | 22 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
October | 22 | 3AM to 4AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
October | 22 | 4AM to 5AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
October | 22 | 5AM to 6AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
October | 22 | 6AM to 7AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 22 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
October | 22 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 22 | 9AM to 10AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 22 | 10AM to 11AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 22 | 11AM to 12PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 22 | 12PM to 1PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 22 | 1PM to 2PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
October | 22 | 2PM to 3PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
October | 22 | 3PM to 4PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 22 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 22 | 5PM to 6PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 22 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 22 | 7PM to 8PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 22 | 8PM to 9PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 22 | 9PM to 10PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 22 | 10PM to 11PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 22 | 11PM to 12AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
October | 23 | 12AM to 1AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
October | 23 | 1AM to 2AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
October | 23 | 2AM to 3AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
October | 23 | 3AM to 4AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
October | 23 | 4AM to 5AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
October | 23 | 5AM to 6AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
October | 23 | 6AM to 7AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
October | 23 | 7AM to 8AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 23 | 8AM to 9AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
October | 23 | 9AM to 10AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 23 | 10AM to 11AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 23 | 11AM to 12PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 23 | 12PM to 1PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 23 | 1PM to 2PM | 64 | 55.3 | 48.9 | 51.5 | 23.38 | 0.0754 | 0.35 | 13.36 | 0
October | 23 | 2PM to 3PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 23 | 3PM to 4PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
October | 23 | 4PM to 5PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 23 | 5PM to 6PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 23 | 6PM to 7PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
October | 23 | 7PM to 8PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 23 | 8PM to 9PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 23 | 9PM to 10PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 23 | 10PM to 11PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 23 | 11PM to 12AM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
October | 24 | 12AM to 1AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
October | 24 | 1AM to 2AM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
October | 24 | 2AM to 3AM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
October | 24 | 3AM to 4AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 24 | 4AM to 5AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 24 | 5AM to 6AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 24 | 6AM to 7AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
October | 24 | 7AM to 8AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
October | 24 | 8AM to 9AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
October | 24 | 9AM to 10AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
October | 24 | 10AM to 11AM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
October | 24 | 11AM to 12PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
October | 24 | 12PM to 1PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 24 | 1PM to 2PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
October | 24 | 2PM to 3PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
October | 24 | 3PM to 4PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
October | 24 | 4PM to 5PM | 61.3 | 57.1 | 54.3 | 63 | 24.52 | 0.0757 | 0.43 | 13.32 | 0
October | 24 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
October | 24 | 6PM to 7PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 24 | 7PM to 8PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 24 | 8PM to 9PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 24 | 9PM to 10PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 24 | 10PM to 11PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 24 | 11PM to 12AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 25 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
October | 25 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 25 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
October | 25 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 25 | 4AM to 5AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
October | 25 | 5AM to 6AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
October | 25 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 25 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 25 | 8AM to 9AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 25 | 9AM to 10AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 25 | 10AM to 11AM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
October | 25 | 11AM to 12PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 25 | 12PM to 1PM | 64.9 | 55.7 | 48.9 | 51.5 | 23.6 | 0.0753 | 0.35 | 13.38 | 0
October | 25 | 1PM to 2PM | 64.9 | 56.2 | 50 | 53.6 | 23.94 | 0.0753 | 0.36 | 13.39 | 0
October | 25 | 2PM to 3PM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
October | 25 | 3PM to 4PM | 63 | 55.4 | 50 | 53.6 | 23.45 | 0.0756 | 0.36 | 13.34 | 0
October | 25 | 4PM to 5PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 25 | 5PM to 6PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 25 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 25 | 7PM to 8PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 25 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 25 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 25 | 10PM to 11PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 25 | 11PM to 12AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 26 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 26 | 1AM to 2AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 26 | 2AM to 3AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
October | 26 | 3AM to 4AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
October | 26 | 4AM to 5AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
October | 26 | 5AM to 6AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
October | 26 | 6AM to 7AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 26 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 26 | 8AM to 9AM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 26 | 9AM to 10AM | 63 | 54.9 | 48.9 | 51.5 | 23.12 | 0.0756 | 0.35 | 13.33 | 0
October | 26 | 10AM to 11AM | 64.9 | 54.8 | 46.9 | 47.8 | 23.02 | 0.0753 | 0.32 | 13.37 | 0
October | 26 | 11AM to 12PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
October | 26 | 12PM to 1PM | 70 | 56.4 | 46 | 46.1 | 23.99 | 0.0746 | 0.31 | 13.49 | 0
October | 26 | 1PM to 2PM | 72 | 58 | 48 | 49.8 | 25.04 | 0.0743 | 0.34 | 13.55 | 0
October | 26 | 2PM to 3PM | 73 | 58.4 | 48 | 49.8 | 25.3 | 0.0742 | 0.34 | 13.58 | 0
October | 26 | 3PM to 4PM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
October | 26 | 4PM to 5PM | 66 | 56.1 | 48.9 | 51.5 | 23.87 | 0.0751 | 0.35 | 13.41 | 0
October | 26 | 5PM to 6PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
October | 26 | 6PM to 7PM | 61 | 54.6 | 50 | 53.6 | 22.97 | 0.0758 | 0.36 | 13.29 | 0
October | 26 | 7PM to 8PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 26 | 8PM to 9PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 26 | 9PM to 10PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 26 | 10PM to 11PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 26 | 11PM to 12AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 27 | 12AM to 1AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
October | 27 | 1AM to 2AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 27 | 2AM to 3AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 27 | 3AM to 4AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
October | 27 | 4AM to 5AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 27 | 5AM to 6AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
October | 27 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
October | 27 | 7AM to 8AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 27 | 8AM to 9AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 27 | 9AM to 10AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
October | 27 | 10AM to 11AM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
October | 27 | 11AM to 12PM | 62.1 | 55.1 | 50 | 53.6 | 23.24 | 0.0757 | 0.36 | 13.31 | 0
October | 27 | 12PM to 1PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
October | 27 | 1PM to 2PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
October | 27 | 2PM to 3PM | 63 | 56 | 51.1 | 55.9 | 23.8 | 0.0755 | 0.38 | 13.34 | 0
October | 27 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 27 | 4PM to 5PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 27 | 5PM to 6PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 27 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 27 | 7PM to 8PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 27 | 8PM to 9PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 27 | 9PM to 10PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 27 | 10PM to 11PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 27 | 11PM to 12AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 28 | 12AM to 1AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 28 | 1AM to 2AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 28 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
October | 28 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 28 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 28 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 28 | 6AM to 7AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 28 | 7AM to 8AM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
October | 28 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 28 | 9AM to 10AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
October | 28 | 10AM to 11AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
October | 28 | 11AM to 12PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 28 | 12PM to 1PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
October | 28 | 1PM to 2PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
October | 28 | 2PM to 3PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
October | 28 | 3PM to 4PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
October | 28 | 4PM to 5PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 28 | 5PM to 6PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
October | 28 | 6PM to 7PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 28 | 7PM to 8PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 28 | 8PM to 9PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 28 | 9PM to 10PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
October | 28 | 10PM to 11PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 28 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
October | 29 | 12AM to 1AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
October | 29 | 1AM to 2AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 29 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 29 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
October | 29 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 29 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
October | 29 | 6AM to 7AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
October | 29 | 7AM to 8AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
October | 29 | 8AM to 9AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 29 | 9AM to 10AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
October | 29 | 10AM to 11AM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
October | 29 | 11AM to 12PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
October | 29 | 12PM to 1PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
October | 29 | 1PM to 2PM | 61 | 52.7 | 46 | 46.1 | 21.81 | 0.0759 | 0.31 | 13.26 | 0
October | 29 | 2PM to 3PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
October | 29 | 3PM to 4PM | 60.1 | 52.8 | 46.9 | 47.8 | 21.84 | 0.076 | 0.32 | 13.24 | 0
October | 29 | 4PM to 5PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 29 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
October | 29 | 6PM to 7PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
October | 29 | 7PM to 8PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
October | 29 | 8PM to 9PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
October | 29 | 9PM to 10PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
October | 29 | 10PM to 11PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
October | 29 | 11PM to 12AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
October | 30 | 12AM to 1AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
October | 30 | 1AM to 2AM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
October | 30 | 2AM to 3AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
October | 30 | 3AM to 4AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
October | 30 | 4AM to 5AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
October | 30 | 5AM to 6AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
October | 30 | 6AM to 7AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
October | 30 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
October | 30 | 8AM to 9AM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 30 | 9AM to 10AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 30 | 10AM to 11AM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 30 | 11AM to 12PM | 60.1 | 53.3 | 48 | 49.8 | 22.15 | 0.076 | 0.34 | 13.25 | 0
October | 30 | 12PM to 1PM | 64 | 53.5 | 45 | 44.3 | 22.26 | 0.0755 | 0.3 | 13.33 | 0
October | 30 | 1PM to 2PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
October | 30 | 2PM to 3PM | 63 | 51.8 | 42.1 | 39.6 | 21.27 | 0.0757 | 0.27 | 13.29 | 0
October | 30 | 3PM to 4PM | 60.1 | 51.4 | 44.1 | 42.8 | 21.06 | 0.0761 | 0.29 | 13.23 | 0
October | 30 | 4PM to 5PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
October | 30 | 5PM to 6PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
October | 30 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
October | 30 | 7PM to 8PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
October | 30 | 8PM to 9PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
October | 30 | 9PM to 10PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 30 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
October | 30 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
October | 31 | 12AM to 1AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
October | 31 | 1AM to 2AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
October | 31 | 2AM to 3AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
October | 31 | 3AM to 4AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
October | 31 | 4AM to 5AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
October | 31 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
October | 31 | 6AM to 7AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
October | 31 | 7AM to 8AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
October | 31 | 8AM to 9AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 31 | 9AM to 10AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 31 | 10AM to 11AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 31 | 11AM to 12PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 31 | 12PM to 1PM | 62.1 | 55.6 | 51.1 | 55.9 | 23.58 | 0.0757 | 0.38 | 13.32 | 0
October | 31 | 1PM to 2PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0759 | 0.35 | 13.28 | 0
October | 31 | 2PM to 3PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
October | 31 | 3PM to 4PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
October | 31 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
October | 31 | 5PM to 6PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
October | 31 | 6PM to 7PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
October | 31 | 7PM to 8PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
October | 31 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
October | 31 | 9PM to 10PM | 55.6 | 52.4 | 50 | 53.6 | 21.66 | 0.0766 | 0.36 | 13.15 | 0
October | 31 | 10PM to 11PM | 55.4 | 51.7 | 48.7 | 51.1 | 21.23 | 0.0767 | 0.35 | 13.14 | 0
October | 31 | 11PM to 12AM | 55 | 51 | 47.7 | 49.1 | 20.82 | 0.0768 | 0.33 | 13.12 | 0
November | 1 | 12AM to 1AM | 54.9 | 50.3 | 46.4 | 46.8 | 20.42 | 0.0768 | 0.32 | 13.11 | 0
November | 1 | 1AM to 2AM | 54.5 | 49.6 | 45.3 | 44.9 | 20.04 | 0.0769 | 0.3 | 13.09 | 0
November | 1 | 2AM to 3AM | 54.3 | 48.9 | 44.1 | 42.8 | 19.67 | 0.0769 | 0.29 | 13.08 | 0
November | 1 | 3AM to 4AM | 54 | 48.2 | 43 | 41 | 19.31 | 0.077 | 0.28 | 13.07 | 0
November | 1 | 4AM to 5AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
November | 1 | 5AM to 6AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
November | 1 | 6AM to 7AM | 50 | 43.8 | 37 | 32.5 | 17.03 | 0.0776 | 0.22 | 12.94 | 1
November | 1 | 7AM to 8AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
November | 1 | 8AM to 9AM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
November | 1 | 9AM to 10AM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
November | 1 | 10AM to 11AM | 63 | 49.5 | 36 | 31.1 | 19.95 | 0.0757 | 0.21 | 13.27 | 0
November | 1 | 11AM to 12PM | 64.9 | 49.7 | 34 | 28.7 | 20.06 | 0.0754 | 0.2 | 13.31 | 0
November | 1 | 12PM to 1PM | 68 | 51.4 | 35.1 | 30 | 21 | 0.075 | 0.2 | 13.39 | 0
November | 1 | 1PM to 2PM | 69.1 | 51.8 | 35.1 | 30 | 21.26 | 0.0748 | 0.2 | 13.42 | 0
November | 1 | 2PM to 3PM | 69.1 | 50.9 | 32 | 26.5 | 20.72 | 0.0749 | 0.18 | 13.41 | 0
November | 1 | 3PM to 4PM | 69.1 | 51.2 | 33.1 | 27.7 | 20.9 | 0.0749 | 0.19 | 13.41 | 0
November | 1 | 4PM to 5PM | 64 | 52.3 | 42.1 | 39.6 | 21.53 | 0.0755 | 0.27 | 13.32 | 0
November | 1 | 5PM to 6PM | 61 | 50.1 | 39.9 | 36.4 | 20.29 | 0.076 | 0.25 | 13.23 | 0
November | 1 | 6PM to 7PM | 60.1 | 48.9 | 37.9 | 33.7 | 19.65 | 0.0761 | 0.23 | 13.2 | 0
November | 1 | 7PM to 8PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
November | 1 | 8PM to 9PM | 59 | 47.3 | 35.1 | 30 | 18.82 | 0.0763 | 0.2 | 13.16 | 0
November | 1 | 9PM to 10PM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
November | 1 | 10PM to 11PM | 55.9 | 46.6 | 37 | 32.5 | 18.46 | 0.0767 | 0.22 | 13.09 | 0
November | 1 | 11PM to 12AM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
November | 2 | 12AM to 1AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
November | 2 | 1AM to 2AM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
November | 2 | 2AM to 3AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
November | 2 | 3AM to 4AM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
November | 2 | 4AM to 5AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
November | 2 | 5AM to 6AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
November | 2 | 6AM to 7AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
November | 2 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 2 | 8AM to 9AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 2 | 9AM to 10AM | 59 | 50.5 | 43 | 41 | 20.53 | 0.0762 | 0.28 | 13.2 | 0
November | 2 | 10AM to 11AM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
November | 2 | 11AM to 12PM | 62.1 | 54.1 | 48 | 49.8 | 22.63 | 0.0757 | 0.34 | 13.3 | 0
November | 2 | 12PM to 1PM | 64 | 53.5 | 45 | 44.3 | 22.26 | 0.0755 | 0.3 | 13.33 | 0
November | 2 | 1PM to 2PM | 64.9 | 53 | 43 | 41 | 21.97 | 0.0754 | 0.28 | 13.35 | 0
November | 2 | 2PM to 3PM | 66 | 55.7 | 48 | 49.8 | 23.6 | 0.0751 | 0.34 | 13.4 | 0
November | 2 | 3PM to 4PM | 66.9 | 55.6 | 46.9 | 47.8 | 23.5 | 0.075 | 0.32 | 13.42 | 0
November | 2 | 4PM to 5PM | 64 | 55.9 | 50 | 53.6 | 23.72 | 0.0754 | 0.36 | 13.36 | 0
November | 2 | 5PM to 6PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
November | 2 | 6PM to 7PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 2 | 7PM to 8PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 2 | 8PM to 9PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
November | 2 | 9PM to 10PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
November | 2 | 10PM to 11PM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 2 | 11PM to 12AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 3 | 12AM to 1AM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
November | 3 | 1AM to 2AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
November | 3 | 2AM to 3AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 3 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 3 | 4AM to 5AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 3 | 5AM to 6AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 3 | 6AM to 7AM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
November | 3 | 7AM to 8AM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
November | 3 | 8AM to 9AM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
November | 3 | 9AM to 10AM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 3 | 10AM to 11AM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 3 | 11AM to 12PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
November | 3 | 12PM to 1PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
November | 3 | 1PM to 2PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 3 | 2PM to 3PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
November | 3 | 3PM to 4PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
November | 3 | 4PM to 5PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
November | 3 | 5PM to 6PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
November | 3 | 6PM to 7PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
November | 3 | 7PM to 8PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
November | 3 | 8PM to 9PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 3 | 9PM to 10PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
November | 3 | 10PM to 11PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
November | 3 | 11PM to 12AM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
November | 4 | 12AM to 1AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
November | 4 | 1AM to 2AM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
November | 4 | 2AM to 3AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
November | 4 | 3AM to 4AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
November | 4 | 4AM to 5AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
November | 4 | 5AM to 6AM | 48 | 47.4 | 46.9 | 47.8 | 18.91 | 0.0778 | 0.32 | 12.94 | 1
November | 4 | 6AM to 7AM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
November | 4 | 7AM to 8AM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
November | 4 | 8AM to 9AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
November | 4 | 9AM to 10AM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
November | 4 | 10AM to 11AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 4 | 11AM to 12PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
November | 4 | 12PM to 1PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
November | 4 | 1PM to 2PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 4 | 2PM to 3PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 4 | 3PM to 4PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 4 | 4PM to 5PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
November | 4 | 5PM to 6PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 4 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 4 | 7PM to 8PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 4 | 8PM to 9PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 4 | 9PM to 10PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 4 | 10PM to 11PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 4 | 11PM to 12AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
November | 5 | 12AM to 1AM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
November | 5 | 1AM to 2AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 5 | 2AM to 3AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 5 | 3AM to 4AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
November | 5 | 4AM to 5AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
November | 5 | 5AM to 6AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
November | 5 | 6AM to 7AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
November | 5 | 7AM to 8AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
November | 5 | 8AM to 9AM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
November | 5 | 9AM to 10AM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
November | 5 | 10AM to 11AM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
November | 5 | 11AM to 12PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
November | 5 | 12PM to 1PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
November | 5 | 1PM to 2PM | 63 | 54.5 | 48 | 49.8 | 22.85 | 0.0756 | 0.34 | 13.32 | 0
November | 5 | 2PM to 3PM | 64 | 52.6 | 43 | 41 | 21.75 | 0.0755 | 0.28 | 13.32 | 0
November | 5 | 3PM to 4PM | 62.1 | 49.8 | 37.9 | 33.7 | 20.13 | 0.0758 | 0.23 | 13.25 | 0
November | 5 | 4PM to 5PM | 59 | 51 | 44.1 | 42.8 | 20.8 | 0.0762 | 0.29 | 13.2 | 0
November | 5 | 5PM to 6PM | 57 | 52.5 | 48.9 | 51.5 | 21.68 | 0.0764 | 0.35 | 13.18 | 0
November | 5 | 6PM to 7PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 5 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 5 | 8PM to 9PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 5 | 9PM to 10PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
November | 5 | 10PM to 11PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 5 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
November | 6 | 12AM to 1AM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
November | 6 | 1AM to 2AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
November | 6 | 2AM to 3AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
November | 6 | 3AM to 4AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 6 | 4AM to 5AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
November | 6 | 5AM to 6AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 6 | 6AM to 7AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 6 | 7AM to 8AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
November | 6 | 8AM to 9AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 6 | 9AM to 10AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 6 | 10AM to 11AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 6 | 11AM to 12PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 6 | 12PM to 1PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 6 | 1PM to 2PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
November | 6 | 2PM to 3PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 6 | 3PM to 4PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 6 | 4PM to 5PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 6 | 5PM to 6PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 6 | 6PM to 7PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 6 | 7PM to 8PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
November | 6 | 8PM to 9PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
November | 6 | 9PM to 10PM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
November | 6 | 10PM to 11PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
November | 6 | 11PM to 12AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 7 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 3AM to 4AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 7 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 7 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 7 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 7 | 8AM to 9AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 7 | 9AM to 10AM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
November | 7 | 10AM to 11AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 7 | 11AM to 12PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 7 | 12PM to 1PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 7 | 1PM to 2PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
November | 7 | 2PM to 3PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
November | 7 | 3PM to 4PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
November | 7 | 4PM to 5PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 7 | 5PM to 6PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
November | 7 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 7 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 7 | 8PM to 9PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 7 | 9PM to 10PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 7 | 10PM to 11PM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
November | 7 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 8 | 12AM to 1AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 8 | 1AM to 2AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 8 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 8 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 8 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 8 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 8 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 8 | 7AM to 8AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 8 | 8AM to 9AM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
November | 8 | 9AM to 10AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 8 | 10AM to 11AM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
November | 8 | 11AM to 12PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 8 | 12PM to 1PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 8 | 1PM to 2PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 8 | 2PM to 3PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 8 | 3PM to 4PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 8 | 4PM to 5PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 8 | 5PM to 6PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 8 | 6PM to 7PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 8 | 7PM to 8PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 8 | 8PM to 9PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
November | 8 | 9PM to 10PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 8 | 10PM to 11PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
November | 8 | 11PM to 12AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
November | 9 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
November | 9 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 9 | 2AM to 3AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 3AM to 4AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 4AM to 5AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 6AM to 7AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 9 | 7AM to 8AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 9 | 8AM to 9AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 9 | 9AM to 10AM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 9 | 10AM to 11AM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 9 | 11AM to 12PM | 60.1 | 52.3 | 46 | 46.1 | 21.59 | 0.076 | 0.31 | 13.24 | 0
November | 9 | 12PM to 1PM | 60.1 | 51.8 | 45 | 44.3 | 21.3 | 0.076 | 0.3 | 13.23 | 0
November | 9 | 1PM to 2PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
November | 9 | 2PM to 3PM | 60.1 | 54.3 | 50 | 53.6 | 22.75 | 0.076 | 0.36 | 13.26 | 0
November | 9 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 55.9 | 23.1 | 0.076 | 0.38 | 13.27 | 0
November | 9 | 4PM to 5PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
November | 9 | 5PM to 6PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
November | 9 | 6PM to 7PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 9 | 7PM to 8PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 9 | 8PM to 9PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 9 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
November | 9 | 10PM to 11PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
November | 9 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
November | 10 | 12AM to 1AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 10 | 1AM to 2AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 10 | 2AM to 3AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 10 | 3AM to 4AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 10 | 4AM to 5AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 10 | 5AM to 6AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 10 | 6AM to 7AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 10 | 7AM to 8AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 10 | 8AM to 9AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 10 | 9AM to 10AM | 55 | 55 | 55 | 64.7 | 23.25 | 0.0767 | 0.44 | 13.17 | 0
November | 10 | 10AM to 11AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 10 | 11AM to 12PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
November | 10 | 12PM to 1PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
November | 10 | 1PM to 2PM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
November | 10 | 2PM to 3PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
November | 10 | 3PM to 4PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
November | 10 | 4PM to 5PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
November | 10 | 5PM to 6PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
November | 10 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 10 | 7PM to 8PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 10 | 8PM to 9PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
November | 10 | 9PM to 10PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 10 | 10PM to 11PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
November | 10 | 11PM to 12AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
November | 11 | 12AM to 1AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 11 | 1AM to 2AM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 11 | 2AM to 3AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 11 | 3AM to 4AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 11 | 4AM to 5AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
November | 11 | 5AM to 6AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
November | 11 | 6AM to 7AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
November | 11 | 7AM to 8AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
November | 11 | 8AM to 9AM | 57 | 57 | 57 | 69.6 | 24.49 | 0.0763 | 0.47 | 13.23 | 0
November | 11 | 9AM to 10AM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
November | 11 | 10AM to 11AM | 57.9 | 57.4 | 57 | 69.6 | 24.71 | 0.0762 | 0.47 | 13.25 | 0
November | 11 | 11AM to 12PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
November | 11 | 12PM to 1PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
November | 11 | 1PM to 2PM | 59 | 58.3 | 57.9 | 72 | 25.34 | 0.076 | 0.48 | 13.29 | 0
November | 11 | 2PM to 3PM | 60.1 | 58.7 | 57.9 | 72 | 25.6 | 0.0759 | 0.48 | 13.32 | 0
November | 11 | 3PM to 4PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 11 | 4PM to 5PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 11 | 5PM to 6PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 11 | 6PM to 7PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 11 | 7PM to 8PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
November | 11 | 8PM to 9PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
November | 11 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 11 | 10PM to 11PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0767 | 0.34 | 13.13 | 0
November | 11 | 11PM to 12AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 12 | 12AM to 1AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 12 | 1AM to 2AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0767 | 0.34 | 13.13 | 0
November | 12 | 2AM to 3AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 12 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 12 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 12 | 5AM to 6AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 6AM to 7AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 7AM to 8AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 8AM to 9AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
November | 12 | 9AM to 10AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 12 | 10AM to 11AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
November | 12 | 11AM to 12PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
November | 12 | 12PM to 1PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
November | 12 | 1PM to 2PM | 62.1 | 56.1 | 52 | 57.8 | 23.88 | 0.0757 | 0.39 | 13.33 | 0
November | 12 | 2PM to 3PM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
November | 12 | 3PM to 4PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 12 | 4PM to 5PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 12 | 5PM to 6PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 12 | 6PM to 7PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 12 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 8PM to 9PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 12 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 12 | 10PM to 11PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 12 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 13 | 12AM to 1AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 13 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 13 | 2AM to 3AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 13 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 13 | 4AM to 5AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 13 | 5AM to 6AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 13 | 6AM to 7AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
November | 13 | 7AM to 8AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 13 | 8AM to 9AM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 13 | 9AM to 10AM | 60.1 | 55.9 | 53.1 | 60.1 | 23.77 | 0.0759 | 0.41 | 13.28 | 0
November | 13 | 10AM to 11AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
November | 13 | 11AM to 12PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
November | 13 | 12PM to 1PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
November | 13 | 1PM to 2PM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
November | 13 | 2PM to 3PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
November | 13 | 3PM to 4PM | 66.9 | 56.5 | 48.9 | 51.5 | 24.08 | 0.075 | 0.35 | 13.43 | 0
November | 13 | 4PM to 5PM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
November | 13 | 5PM to 6PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 13 | 6PM to 7PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 13 | 7PM to 8PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 13 | 8PM to 9PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 13 | 9PM to 10PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 13 | 10PM to 11PM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 13 | 11PM to 12AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 14 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 14 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 14 | 2AM to 3AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
November | 14 | 3AM to 4AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
November | 14 | 4AM to 5AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
November | 14 | 5AM to 6AM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 1
November | 14 | 6AM to 7AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
November | 14 | 7AM to 8AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
November | 14 | 8AM to 9AM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
November | 14 | 9AM to 10AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
November | 14 | 10AM to 11AM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
November | 14 | 11AM to 12PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 14 | 12PM to 1PM | 61 | 58.5 | 57 | 69.6 | 25.46 | 0.0757 | 0.47 | 13.33 | 0
November | 14 | 1PM to 2PM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
November | 14 | 2PM to 3PM | 63 | 57 | 53.1 | 60.1 | 24.47 | 0.0755 | 0.41 | 13.36 | 0
November | 14 | 3PM to 4PM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
November | 14 | 4PM to 5PM | 61 | 56.8 | 54 | 62.2 | 24.3 | 0.0758 | 0.42 | 13.31 | 0
November | 14 | 5PM to 6PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 14 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 14 | 7PM to 8PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 14 | 8PM to 9PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 14 | 9PM to 10PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 14 | 10PM to 11PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 14 | 11PM to 12AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 15 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 15 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 15 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 15 | 3AM to 4AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 15 | 4AM to 5AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 15 | 5AM to 6AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 15 | 6AM to 7AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 15 | 7AM to 8AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 15 | 8AM to 9AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 15 | 9AM to 10AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 15 | 10AM to 11AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 15 | 11AM to 12PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 15 | 12PM to 1PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 15 | 1PM to 2PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
November | 15 | 2PM to 3PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
November | 15 | 3PM to 4PM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
November | 15 | 4PM to 5PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 15 | 5PM to 6PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
November | 15 | 6PM to 7PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 15 | 7PM to 8PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 15 | 8PM to 9PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 15 | 9PM to 10PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 15 | 10PM to 11PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 15 | 11PM to 12AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 16 | 12AM to 1AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 16 | 1AM to 2AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
November | 16 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.19 | 0.0772 | 0.34 | 13.04 | 1
November | 16 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0773 | 0.32 | 13.03 | 1
November | 16 | 4AM to 5AM | 51.8 | 48 | 44.6 | 43.7 | 19.19 | 0.0773 | 0.3 | 13.02 | 1
November | 16 | 5AM to 6AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.19 | 0.0772 | 0.34 | 13.04 | 1
November | 16 | 6AM to 7AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 16 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.077 | 0.34 | 13.09 | 0
November | 16 | 8AM to 9AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 16 | 9AM to 10AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 16 | 10AM to 11AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 16 | 11AM to 12PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 16 | 12PM to 1PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
November | 16 | 1PM to 2PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 16 | 2PM to 3PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
November | 16 | 3PM to 4PM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
November | 16 | 4PM to 5PM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
November | 16 | 5PM to 6PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 16 | 6PM to 7PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 16 | 7PM to 8PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 16 | 8PM to 9PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 16 | 9PM to 10PM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 16 | 10PM to 11PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 16 | 11PM to 12AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
November | 17 | 12AM to 1AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0
November | 17 | 1AM to 2AM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 1
November | 17 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0773 | 0.32 | 13.03 | 1
November | 17 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0773 | 0.32 | 13.03 | 1
November | 17 | 4AM to 5AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.93 | 1
November | 17 | 5AM to 6AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
November | 17 | 6AM to 7AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
November | 17 | 7AM to 8AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.11 | 0.077 | 0.32 | 13.08 | 0
November | 17 | 8AM to 9AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.11 | 0.077 | 0.32 | 13.08 | 0
November | 17 | 9AM to 10AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0767 | 0.34 | 13.13 | 0
November | 17 | 10AM to 11AM | 57 | 56.4 | 55.9 | 66.9 | 24.07 | 0.0763 | 0.45 | 13.22 | 0
November | 17 | 11AM to 12PM | 57 | 57 | 57 | 69.6 | 24.49 | 0.0763 | 0.47 | 13.23 | 0
November | 17 | 12PM to 1PM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
November | 17 | 1PM to 2PM | 61 | 57.4 | 55 | 64.7 | 24.7 | 0.0758 | 0.44 | 13.32 | 0
November | 17 | 2PM to 3PM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
November | 17 | 3PM to 4PM | 64.9 | 56.8 | 51.1 | 55.9 | 24.28 | 0.0753 | 0.38 | 13.39 | 0
November | 17 | 4PM to 5PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
November | 17 | 5PM to 6PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
November | 17 | 6PM to 7PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
November | 17 | 7PM to 8PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 17 | 8PM to 9PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 17 | 9PM to 10PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 17 | 10PM to 11PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 17 | 11PM to 12AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 18 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 18 | 1AM to 2AM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
November | 18 | 2AM to 3AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
November | 18 | 3AM to 4AM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
November | 18 | 4AM to 5AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
November | 18 | 5AM to 6AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
November | 18 | 6AM to 7AM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 18 | 7AM to 8AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 18 | 8AM to 9AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 18 | 9AM to 10AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 18 | 10AM to 11AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 18 | 11AM to 12PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 18 | 12PM to 1PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 18 | 1PM to 2PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 18 | 2PM to 3PM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
November | 18 | 3PM to 4PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
November | 18 | 4PM to 5PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
November | 18 | 5PM to 6PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 18 | 6PM to 7PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 18 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 18 | 8PM to 9PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 18 | 9PM to 10PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 18 | 10PM to 11PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 18 | 11PM to 12AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
November | 19 | 12AM to 1AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 19 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 19 | 2AM to 3AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 19 | 3AM to 4AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 19 | 4AM to 5AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 19 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 19 | 6AM to 7AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 19 | 7AM to 8AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 19 | 8AM to 9AM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
November | 19 | 9AM to 10AM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 19 | 10AM to 11AM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
November | 19 | 11AM to 12PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 19 | 12PM to 1PM | 57.9 | 51.4 | 46 | 46.1 | 21.06 | 0.0763 | 0.31 | 13.18 | 0
November | 19 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
November | 19 | 2PM to 3PM | 60.1 | 53.7 | 48.9 | 51.5 | 22.42 | 0.076 | 0.35 | 13.26 | 0
November | 19 | 3PM to 4PM | 59 | 51.9 | 46 | 46.1 | 21.33 | 0.0762 | 0.31 | 13.21 | 0
November | 19 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
November | 19 | 5PM to 6PM | 55 | 51.1 | 48 | 49.8 | 20.93 | 0.0767 | 0.34 | 13.12 | 0
November | 19 | 6PM to 7PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 19 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 19 | 8PM to 9PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 19 | 9PM to 10PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 19 | 10PM to 11PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
November | 19 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
November | 20 | 12AM to 1AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
November | 20 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
November | 20 | 2AM to 3AM | 54 | 46.5 | 39 | 35.1 | 18.4 | 0.077 | 0.24 | 13.05 | 0
November | 20 | 3AM to 4AM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
November | 20 | 4AM to 5AM | 54 | 46.1 | 37.9 | 33.7 | 18.17 | 0.077 | 0.23 | 13.05 | 0
November | 20 | 5AM to 6AM | 54 | 46.1 | 37.9 | 33.7 | 18.17 | 0.077 | 0.23 | 13.05 | 0
November | 20 | 6AM to 7AM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
November | 20 | 7AM to 8AM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
November | 20 | 8AM to 9AM | 55 | 45.1 | 34 | 28.7 | 17.67 | 0.0769 | 0.2 | 13.06 | 0
November | 20 | 9AM to 10AM | 57 | 46 | 34 | 28.7 | 18.15 | 0.0766 | 0.2 | 13.11 | 0
November | 20 | 10AM to 11AM | 59 | 44.6 | 27 | 21 | 17.42 | 0.0764 | 0.14 | 13.14 | 0
November | 20 | 11AM to 12PM | 60.1 | 45.2 | 27 | 21 | 17.68 | 0.0762 | 0.14 | 13.16 | 0
November | 20 | 12PM to 1PM | 60.1 | 45.8 | 28.9 | 23 | 18 | 0.0762 | 0.16 | 13.17 | 0
November | 20 | 1PM to 2PM | 61 | 47.6 | 33.1 | 27.7 | 18.94 | 0.076 | 0.19 | 13.21 | 0
November | 20 | 2PM to 3PM | 64.9 | 50.7 | 37 | 32.5 | 20.64 | 0.0754 | 0.22 | 13.32 | 0
November | 20 | 3PM to 4PM | 66.9 | 51.6 | 37 | 32.5 | 21.12 | 0.0751 | 0.22 | 13.37 | 0
November | 20 | 4PM to 5PM | 64 | 51.4 | 39.9 | 36.4 | 21.03 | 0.0755 | 0.25 | 13.31 | 0
November | 20 | 5PM to 6PM | 62.1 | 51 | 41 | 38 | 20.8 | 0.0758 | 0.26 | 13.27 | 0
November | 20 | 6PM to 7PM | 62.1 | 49.5 | 37 | 32.5 | 19.95 | 0.0758 | 0.22 | 13.25 | 0
November | 20 | 7PM to 8PM | 61 | 49.3 | 37.9 | 33.7 | 19.87 | 0.076 | 0.23 | 13.23 | 0
November | 20 | 8PM to 9PM | 60.1 | 48.2 | 36 | 31.1 | 19.25 | 0.0761 | 0.21 | 13.19 | 0
November | 20 | 9PM to 10PM | 57.9 | 47.2 | 36 | 31.1 | 18.73 | 0.0764 | 0.21 | 13.14 | 0
November | 20 | 10PM to 11PM | 57 | 47.2 | 37 | 32.5 | 18.73 | 0.0766 | 0.22 | 13.12 | 0
November | 20 | 11PM to 12AM | 55.9 | 46.6 | 37 | 32.5 | 18.46 | 0.0767 | 0.22 | 13.09 | 0
November | 21 | 12AM to 1AM | 55 | 44.8 | 33.1 | 27.7 | 17.51 | 0.0769 | 0.19 | 13.06 | 0
November | 21 | 1AM to 2AM | 55 | 44.8 | 33.1 | 27.7 | 17.51 | 0.0769 | 0.19 | 13.06 | 0
November | 21 | 2AM to 3AM | 55 | 45.1 | 34 | 28.7 | 17.67 | 0.0769 | 0.2 | 13.06 | 0
November | 21 | 3AM to 4AM | 54 | 44.6 | 34 | 28.7 | 17.41 | 0.077 | 0.2 | 13.03 | 0
November | 21 | 4AM to 5AM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
November | 21 | 5AM to 6AM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
November | 21 | 6AM to 7AM | 52 | 42.5 | 30.9 | 25.2 | 16.38 | 0.0774 | 0.17 | 12.97 | 0
November | 21 | 7AM to 8AM | 53.1 | 43 | 30.9 | 25.2 | 16.65 | 0.0772 | 0.17 | 13 | 0
November | 21 | 8AM to 9AM | 55 | 44.8 | 33.1 | 27.7 | 17.51 | 0.0769 | 0.19 | 13.06 | 0
November | 21 | 9AM to 10AM | 55 | 44 | 30.9 | 25.2 | 17.12 | 0.0769 | 0.17 | 13.05 | 0
November | 21 | 10AM to 11AM | 57.9 | 46.5 | 34 | 28.7 | 18.36 | 0.0765 | 0.2 | 13.13 | 0
November | 21 | 11AM to 12PM | 59 | 47.3 | 35.1 | 30 | 18.82 | 0.0763 | 0.2 | 13.16 | 0
November | 21 | 12PM to 1PM | 60.1 | 47.8 | 35.1 | 30 | 19.08 | 0.0761 | 0.2 | 13.19 | 0
November | 21 | 1PM to 2PM | 61 | 48.6 | 36 | 31.1 | 19.47 | 0.076 | 0.21 | 13.22 | 0
November | 21 | 2PM to 3PM | 60.1 | 49.7 | 39.9 | 36.4 | 20.07 | 0.0761 | 0.25 | 13.21 | 0
November | 21 | 3PM to 4PM | 60.1 | 48.9 | 37.9 | 33.7 | 19.65 | 0.0761 | 0.23 | 13.2 | 0
November | 21 | 4PM to 5PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
November | 21 | 5PM to 6PM | 57.9 | 49.6 | 42.1 | 39.6 | 20.05 | 0.0764 | 0.27 | 13.17 | 0
November | 21 | 6PM to 7PM | 59 | 47.7 | 36 | 31.1 | 18.99 | 0.0763 | 0.21 | 13.17 | 0
November | 21 | 7PM to 8PM | 57.9 | 47.2 | 36 | 31.1 | 18.73 | 0.0764 | 0.21 | 13.14 | 0
November | 21 | 8PM to 9PM | 55.9 | 42.8 | 26.1 | 20.1 | 16.55 | 0.0768 | 0.14 | 13.06 | 0
November | 21 | 9PM to 10PM | 55 | 44 | 30.9 | 25.2 | 17.12 | 0.0769 | 0.17 | 13.05 | 0
November | 21 | 10PM to 11PM | 57 | 43.4 | 26.1 | 20.1 | 16.81 | 0.0766 | 0.14 | 13.08 | 0
November | 21 | 11PM to 12AM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 1
November | 22 | 12AM to 1AM | 46 | 38.3 | 28 | 22.1 | 14.46 | 0.0783 | 0.15 | 12.81 | 1
November | 22 | 1AM to 2AM | 46 | 38 | 27 | 21 | 14.29 | 0.0783 | 0.14 | 12.81 | 1
November | 22 | 2AM to 3AM | 46.9 | 38.8 | 28 | 22.1 | 14.68 | 0.0782 | 0.15 | 12.83 | 1
November | 22 | 3AM to 4AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
November | 22 | 4AM to 5AM | 42.1 | 36.9 | 30 | 24.2 | 13.83 | 0.0789 | 0.16 | 12.72 | 1
November | 22 | 5AM to 6AM | 48 | 40.5 | 30.9 | 25.2 | 15.43 | 0.078 | 0.17 | 12.87 | 1
November | 22 | 6AM to 7AM | 48 | 42.8 | 37 | 32.5 | 16.55 | 0.0779 | 0.22 | 12.89 | 1
November | 22 | 7AM to 8AM | 46.9 | 41.5 | 35.1 | 30 | 15.9 | 0.0781 | 0.2 | 12.86 | 1
November | 22 | 8AM to 9AM | 54 | 44.6 | 34 | 28.7 | 17.41 | 0.077 | 0.2 | 13.03 | 0
November | 22 | 9AM to 10AM | 57 | 45.4 | 32 | 26.5 | 17.8 | 0.0766 | 0.18 | 13.1 | 0
November | 22 | 10AM to 11AM | 59 | 47.7 | 36 | 31.1 | 18.99 | 0.0763 | 0.21 | 13.17 | 0
November | 22 | 11AM to 12PM | 59 | 45.9 | 30.9 | 25.2 | 18.08 | 0.0763 | 0.17 | 13.15 | 0
November | 22 | 12PM to 1PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.19 | 0
November | 22 | 1PM to 2PM | 60.1 | 50.1 | 41 | 38 | 20.32 | 0.0761 | 0.26 | 13.22 | 0
November | 22 | 2PM to 3PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
November | 22 | 3PM to 4PM | 61 | 55.2 | 51.1 | 55.9 | 23.32 | 0.0758 | 0.38 | 13.29 | 0
November | 22 | 4PM to 5PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 22 | 5PM to 6PM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 22 | 6PM to 7PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
November | 22 | 7PM to 8PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 22 | 8PM to 9PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
November | 22 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
November | 22 | 10PM to 11PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
November | 22 | 11PM to 12AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 23 | 12AM to 1AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
November | 23 | 1AM to 2AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 23 | 2AM to 3AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
November | 23 | 3AM to 4AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
November | 23 | 4AM to 5AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
November | 23 | 5AM to 6AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
November | 23 | 6AM to 7AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 23 | 7AM to 8AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
November | 23 | 8AM to 9AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
November | 23 | 9AM to 10AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
November | 23 | 10AM to 11AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 23 | 11AM to 12PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 23 | 12PM to 1PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
November | 23 | 1PM to 2PM | 57.9 | 50.9 | 45 | 44.3 | 20.77 | 0.0764 | 0.3 | 13.18 | 0
November | 23 | 2PM to 3PM | 60.1 | 50.9 | 43 | 41 | 20.79 | 0.0761 | 0.28 | 13.22 | 0
November | 23 | 3PM to 4PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
November | 23 | 4PM to 5PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 23 | 5PM to 6PM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 23 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 23 | 7PM to 8PM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
November | 23 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
November | 23 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
November | 23 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
November | 23 | 11PM to 12AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 24 | 12AM to 1AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
November | 24 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
November | 24 | 2AM to 3AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
November | 24 | 3AM to 4AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
November | 24 | 4AM to 5AM | 44.1 | 43.1 | 42.1 | 39.6 | 16.69 | 0.0785 | 0.27 | 12.81 | 1
November | 24 | 5AM to 6AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
November | 24 | 6AM to 7AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
November | 24 | 7AM to 8AM | 48.9 | 47.4 | 46 | 46.1 | 18.88 | 0.0777 | 0.31 | 12.96 | 1
November | 24 | 8AM to 9AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
November | 24 | 9AM to 10AM | 53.1 | 49.3 | 46 | 46.1 | 19.88 | 0.0771 | 0.31 | 13.06 | 0
November | 24 | 10AM to 11AM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
November | 24 | 11AM to 12PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
November | 24 | 12PM to 1PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 24 | 1PM to 2PM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
November | 24 | 2PM to 3PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0759 | 0.32 | 13.27 | 0
November | 24 | 3PM to 4PM | 59 | 53.8 | 50 | 53.6 | 22.49 | 0.0761 | 0.36 | 13.23 | 0
November | 24 | 4PM to 5PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
November | 24 | 5PM to 6PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 24 | 6PM to 7PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 24 | 7PM to 8PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 24 | 8PM to 9PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 24 | 9PM to 10PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 24 | 10PM to 11PM | 53.1 | 52.4 | 52 | 57.8 | 21.69 | 0.077 | 0.39 | 13.1 | 0
November | 24 | 11PM to 12AM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
November | 25 | 12AM to 1AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
November | 25 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 25 | 2AM to 3AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 25 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 25 | 4AM to 5AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 25 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 25 | 6AM to 7AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 25 | 7AM to 8AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 25 | 8AM to 9AM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
November | 25 | 9AM to 10AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
November | 25 | 10AM to 11AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 25 | 11AM to 12PM | 57.9 | 54 | 51.1 | 55.9 | 22.57 | 0.0763 | 0.38 | 13.21 | 0
November | 25 | 12PM to 1PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 25 | 1PM to 2PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 25 | 2PM to 3PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
November | 25 | 3PM to 4PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
November | 25 | 4PM to 5PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0762 | 0.35 | 13.23 | 0
November | 25 | 5PM to 6PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.89 | 0.0763 | 0.35 | 13.2 | 0
November | 25 | 6PM to 7PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 25 | 7PM to 8PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
November | 25 | 8PM to 9PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
November | 25 | 9PM to 10PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
November | 25 | 10PM to 11PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
November | 25 | 11PM to 12AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
November | 26 | 12AM to 1AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 26 | 1AM to 2AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 26 | 2AM to 3AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 26 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
November | 26 | 4AM to 5AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 26 | 5AM to 6AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 26 | 6AM to 7AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
November | 26 | 7AM to 8AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 26 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 26 | 9AM to 10AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 26 | 10AM to 11AM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 26 | 11AM to 12PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
November | 26 | 12PM to 1PM | 57.9 | 53.4 | 50 | 53.6 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
November | 26 | 1PM to 2PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
November | 26 | 2PM to 3PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 26 | 3PM to 4PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
November | 26 | 4PM to 5PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
November | 26 | 5PM to 6PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
November | 26 | 6PM to 7PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 26 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
November | 26 | 8PM to 9PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 26 | 9PM to 10PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 26 | 10PM to 11PM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 26 | 11PM to 12AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
November | 27 | 12AM to 1AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
November | 27 | 1AM to 2AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 27 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
November | 27 | 3AM to 4AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 27 | 4AM to 5AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
November | 27 | 5AM to 6AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
November | 27 | 6AM to 7AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
November | 27 | 7AM to 8AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
November | 27 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 27 | 9AM to 10AM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
November | 27 | 10AM to 11AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
November | 27 | 11AM to 12PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
November | 27 | 12PM to 1PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
November | 27 | 1PM to 2PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
November | 27 | 2PM to 3PM | 59 | 52.3 | 46.9 | 47.8 | 21.58 | 0.0762 | 0.32 | 13.22 | 0
November | 27 | 3PM to 4PM | 57 | 51.5 | 46.9 | 47.8 | 21.1 | 0.0765 | 0.32 | 13.17 | 0
November | 27 | 4PM to 5PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
November | 27 | 5PM to 6PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
November | 27 | 6PM to 7PM | 54 | 49.7 | 46 | 46.1 | 20.1 | 0.0769 | 0.31 | 13.08 | 0
November | 27 | 7PM to 8PM | 55 | 47.4 | 39.9 | 36.4 | 18.85 | 0.0768 | 0.25 | 13.08 | 0
November | 27 | 8PM to 9PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
November | 27 | 9PM to 10PM | 55 | 45.8 | 36 | 31.1 | 18.03 | 0.0769 | 0.21 | 13.07 | 0
November | 27 | 10PM to 11PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
November | 27 | 11PM to 12AM | 53.1 | 43.8 | 33.1 | 27.7 | 17.03 | 0.0772 | 0.19 | 13.01 | 0
November | 28 | 12AM to 1AM | 53.1 | 43 | 30.9 | 25.2 | 16.65 | 0.0772 | 0.17 | 13 | 0
November | 28 | 1AM to 2AM | 52 | 42.9 | 32 | 26.5 | 16.58 | 0.0774 | 0.18 | 12.98 | 0
November | 28 | 2AM to 3AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 1
November | 28 | 3AM to 4AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 1
November | 28 | 4AM to 5AM | 50 | 41.5 | 30.9 | 25.2 | 15.91 | 0.0777 | 0.17 | 12.92 | 1
November | 28 | 5AM to 6AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 1
November | 28 | 6AM to 7AM | 51.1 | 41.7 | 30 | 24.2 | 16.01 | 0.0775 | 0.16 | 12.95 | 1
November | 28 | 7AM to 8AM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 1
November | 28 | 8AM to 9AM | 52 | 42.9 | 32 | 26.5 | 16.58 | 0.0774 | 0.18 | 12.98 | 0
November | 28 | 9AM to 10AM | 52 | 42.5 | 30.9 | 25.2 | 16.38 | 0.0774 | 0.17 | 12.97 | 0
November | 28 | 10AM to 11AM | 53.1 | 43.8 | 33.1 | 27.7 | 17.03 | 0.0772 | 0.19 | 13.01 | 0
November | 28 | 11AM to 12PM | 54 | 43.9 | 32 | 26.5 | 17.06 | 0.0771 | 0.18 | 13.03 | 0
November | 28 | 12PM to 1PM | 55.9 | 44.9 | 32 | 26.5 | 17.54 | 0.0768 | 0.18 | 13.08 | 0
November | 28 | 1PM to 2PM | 55.9 | 44.5 | 30.9 | 25.2 | 17.34 | 0.0768 | 0.17 | 13.07 | 0
November | 28 | 2PM to 3PM | 57 | 45.7 | 33.1 | 27.7 | 17.99 | 0.0766 | 0.19 | 13.11 | 0
November | 28 | 3PM to 4PM | 57 | 45.4 | 32 | 26.5 | 17.8 | 0.0766 | 0.18 | 13.1 | 0
November | 28 | 4PM to 5PM | 55.9 | 45.9 | 35.1 | 30 | 18.08 | 0.0767 | 0.2 | 13.09 | 0
November | 28 | 5PM to 6PM | 55 | 43.7 | 30 | 24.2 | 16.96 | 0.0769 | 0.16 | 13.05 | 0
November | 28 | 6PM to 7PM | 54 | 44.3 | 33.1 | 27.7 | 17.25 | 0.0771 | 0.19 | 13.03 | 0
November | 28 | 7PM to 8PM | 53.1 | 43.4 | 32 | 26.5 | 16.85 | 0.0772 | 0.18 | 13 | 0
November | 28 | 8PM to 9PM | 52 | 42.2 | 30 | 24.2 | 16.23 | 0.0774 | 0.16 | 12.97 | 0
November | 28 | 9PM to 10PM | 51.1 | 42.8 | 33.1 | 27.7 | 16.55 | 0.0775 | 0.19 | 12.96 | 1
November | 28 | 10PM to 11PM | 52 | 42.5 | 30.9 | 25.2 | 16.38 | 0.0774 | 0.17 | 12.97 | 0
November | 28 | 11PM to 12AM | 52 | 43.3 | 33.1 | 27.7 | 16.77 | 0.0774 | 0.19 | 12.98 | 0
November | 29 | 12AM to 1AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 1
November | 29 | 1AM to 2AM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 1
November | 29 | 2AM to 3AM | 50 | 40.8 | 28.9 | 23 | 15.56 | 0.0777 | 0.16 | 12.91 | 1
November | 29 | 3AM to 4AM | 48 | 40.9 | 32 | 26.5 | 15.63 | 0.078 | 0.18 | 12.87 | 1
November | 29 | 4AM to 5AM | 48.9 | 41.4 | 32 | 26.5 | 15.85 | 0.0778 | 0.18 | 12.9 | 1
November | 29 | 5AM to 6AM | 48 | 40.5 | 30.9 | 25.2 | 15.43 | 0.078 | 0.17 | 12.87 | 1
November | 29 | 6AM to 7AM | 44.1 | 37.3 | 28 | 22.1 | 13.98 | 0.0786 | 0.15 | 12.76 | 1
November | 29 | 7AM to 8AM | 48 | 38.7 | 26.1 | 20.1 | 14.64 | 0.078 | 0.14 | 12.86 | 1
November | 29 | 8AM to 9AM | 46.9 | 38.8 | 28 | 22.1 | 14.68 | 0.0782 | 0.15 | 12.83 | 1
November | 29 | 9AM to 10AM | 48.9 | 39.9 | 28 | 22.1 | 15.16 | 0.0779 | 0.15 | 12.88 | 1
November | 29 | 10AM to 11AM | 48.9 | 39.5 | 27 | 21 | 14.99 | 0.0779 | 0.14 | 12.88 | 1
November | 29 | 11AM to 12PM | 50 | 39.8 | 26.1 | 20.1 | 15.11 | 0.0777 | 0.14 | 12.91 | 1
November | 29 | 12PM to 1PM | 51.1 | 40.4 | 26.1 | 20.1 | 15.37 | 0.0775 | 0.14 | 12.93 | 1
November | 29 | 1PM to 2PM | 53.1 | 41.7 | 27 | 21 | 15.99 | 0.0772 | 0.14 | 12.99 | 0
November | 29 | 2PM to 3PM | 53.1 | 42.3 | 28.9 | 23 | 16.3 | 0.0772 | 0.16 | 12.99 | 0
November | 29 | 3PM to 4PM | 54 | 43.9 | 32 | 26.5 | 17.06 | 0.0771 | 0.18 | 13.03 | 0
November | 29 | 4PM to 5PM | 52 | 43.3 | 33.1 | 27.7 | 16.77 | 0.0774 | 0.19 | 12.98 | 0
November | 29 | 5PM to 6PM | 50 | 42.3 | 33.1 | 27.7 | 16.29 | 0.0777 | 0.19 | 12.93 | 1
November | 29 | 6PM to 7PM | 48.9 | 39.9 | 28 | 22.1 | 15.16 | 0.0779 | 0.15 | 12.88 | 1
November | 29 | 7PM to 8PM | 46.9 | 40.3 | 32 | 26.5 | 15.37 | 0.0781 | 0.18 | 12.85 | 1
November | 29 | 8PM to 9PM | 45 | 39.3 | 32 | 26.5 | 14.89 | 0.0784 | 0.18 | 12.8 | 1
November | 29 | 9PM to 10PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
November | 29 | 10PM to 11PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
November | 29 | 11PM to 12AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
November | 30 | 12AM to 1AM | 41 | 37.9 | 34 | 28.7 | 14.27 | 0.079 | 0.2 | 12.7 | 1
November | 30 | 1AM to 2AM | 41 | 38.3 | 35.1 | 30 | 14.47 | 0.079 | 0.2 | 12.71 | 1
November | 30 | 2AM to 3AM | 39.9 | 38.1 | 36 | 31.1 | 14.38 | 0.0792 | 0.21 | 12.68 | 1
November | 30 | 3AM to 4AM | 39 | 36.8 | 34 | 28.7 | 13.79 | 0.0794 | 0.2 | 12.65 | 1
November | 30 | 4AM to 5AM | 37.9 | 36.7 | 35.1 | 30 | 13.73 | 0.0795 | 0.2 | 12.63 | 1
November | 30 | 5AM to 6AM | 39 | 37.6 | 36 | 31.1 | 14.16 | 0.0793 | 0.21 | 12.66 | 1
November | 30 | 6AM to 7AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
November | 30 | 7AM to 8AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0792 | 0.23 | 12.69 | 1
November | 30 | 8AM to 9AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
November | 30 | 9AM to 10AM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
November | 30 | 10AM to 11AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
November | 30 | 11AM to 12PM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
November | 30 | 12PM to 1PM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
November | 30 | 1PM to 2PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
November | 30 | 2PM to 3PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
November | 30 | 3PM to 4PM | 52 | 45.6 | 39 | 35.1 | 17.92 | 0.0773 | 0.24 | 13 | 0
November | 30 | 4PM to 5PM | 52 | 45.6 | 39 | 35.1 | 17.92 | 0.0773 | 0.24 | 13 | 0
November | 30 | 5PM to 6PM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
November | 30 | 6PM to 7PM | 50 | 44.6 | 39 | 35.1 | 17.44 | 0.0776 | 0.24 | 12.95 | 1
November | 30 | 7PM to 8PM | 50 | 44.2 | 37.9 | 33.7 | 17.21 | 0.0776 | 0.23 | 12.95 | 1
November | 30 | 8PM to 9PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
November | 30 | 9PM to 10PM | 49.3 | 45.8 | 42.4 | 40.2 | 18.04 | 0.0777 | 0.27 | 12.95 | 1
November | 30 | 10PM to 11PM | 48.6 | 45.7 | 43 | 41 | 18 | 0.0778 | 0.28 | 12.93 | 1
November | 30 | 11PM to 12AM | 47.8 | 45.5 | 43.3 | 41.6 | 17.91 | 0.0779 | 0.28 | 12.91 | 1
December | 1 | 12AM to 1AM | 47.1 | 45.4 | 43.7 | 42.2 | 17.83 | 0.078 | 0.29 | 12.9 | 1
December | 1 | 1AM to 2AM | 46.4 | 45.2 | 44.1 | 42.8 | 17.74 | 0.0781 | 0.29 | 12.88 | 1
December | 1 | 2AM to 3AM | 45.7 | 45.1 | 44.6 | 43.7 | 17.71 | 0.0782 | 0.3 | 12.87 | 1
December | 1 | 3AM to 4AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
December | 1 | 4AM to 5AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
December | 1 | 5AM to 6AM | 48 | 48 | 48 | 49.8 | 19.22 | 0.0778 | 0.34 | 12.94 | 1
December | 1 | 6AM to 7AM | 46.9 | 46.9 | 46.9 | 47.8 | 18.65 | 0.078 | 0.32 | 12.91 | 1
December | 1 | 7AM to 8AM | 48.9 | 48.9 | 48.9 | 51.5 | 19.71 | 0.0777 | 0.35 | 12.97 | 1
December | 1 | 8AM to 9AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 1 | 9AM to 10AM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 1 | 10AM to 11AM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
December | 1 | 11AM to 12PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
December | 1 | 12PM to 1PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.19 | 0
December | 1 | 1PM to 2PM | 57.9 | 52.4 | 48 | 49.8 | 21.63 | 0.0763 | 0.34 | 13.2 | 0
December | 1 | 2PM to 3PM | 61 | 49.7 | 39 | 35.1 | 20.1 | 0.076 | 0.24 | 13.23 | 0
December | 1 | 3PM to 4PM | 60.1 | 50.6 | 42.1 | 39.6 | 20.57 | 0.0761 | 0.27 | 13.22 | 0
December | 1 | 4PM to 5PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
December | 1 | 5PM to 6PM | 55.9 | 51.5 | 48 | 49.8 | 21.14 | 0.0766 | 0.34 | 13.14 | 0
December | 1 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 1 | 7PM to 8PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 1 | 8PM to 9PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 1 | 9PM to 10PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 1 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 1 | 11PM to 12AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
December | 2 | 12AM to 1AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
December | 2 | 1AM to 2AM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
December | 2 | 2AM to 3AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
December | 2 | 3AM to 4AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
December | 2 | 4AM to 5AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
December | 2 | 5AM to 6AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
December | 2 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
December | 2 | 7AM to 8AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 2 | 8AM to 9AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 2 | 9AM to 10AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
December | 2 | 10AM to 11AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
December | 2 | 11AM to 12PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
December | 2 | 12PM to 1PM | 54 | 51.1 | 48.9 | 51.5 | 20.93 | 0.0769 | 0.35 | 13.1 | 0
December | 2 | 1PM to 2PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 2 | 2PM to 3PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
December | 2 | 3PM to 4PM | 55 | 51.6 | 48.9 | 51.5 | 21.19 | 0.0767 | 0.35 | 13.13 | 0
December | 2 | 4PM to 5PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 2 | 5PM to 6PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 2 | 6PM to 7PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 7PM to 8PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 8PM to 9PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 9PM to 10PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 10PM to 11PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 2 | 11PM to 12AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 12AM to 1AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 1AM to 2AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 2AM to 3AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 3AM to 4AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 4AM to 5AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 5AM to 6AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 6AM to 7AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 7AM to 8AM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 3 | 8AM to 9AM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 3 | 9AM to 10AM | 55.9 | 52.6 | 50 | 53.6 | 21.75 | 0.0766 | 0.36 | 13.16 | 0
December | 3 | 10AM to 11AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 3 | 11AM to 12PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 3 | 12PM to 1PM | 59 | 54.4 | 51.1 | 55.9 | 22.84 | 0.0761 | 0.38 | 13.24 | 0
December | 3 | 1PM to 2PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
December | 3 | 2PM to 3PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 3 | 3PM to 4PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
December | 3 | 4PM to 5PM | 55.9 | 55.4 | 55 | 64.7 | 23.47 | 0.0765 | 0.44 | 13.19 | 0
December | 3 | 5PM to 6PM | 57 | 55.8 | 55 | 64.7 | 23.73 | 0.0764 | 0.44 | 13.22 | 0
December | 3 | 6PM to 7PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 3 | 7PM to 8PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 3 | 8PM to 9PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 3 | 9PM to 10PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 3 | 10PM to 11PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 3 | 11PM to 12AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 12AM to 1AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 1AM to 2AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 2AM to 3AM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 3AM to 4AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
December | 4 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 4 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 4 | 6AM to 7AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
December | 4 | 7AM to 8AM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
December | 4 | 8AM to 9AM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 4 | 9AM to 10AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 4 | 10AM to 11AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 4 | 11AM to 12PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
December | 4 | 12PM to 1PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 1PM to 2PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 4 | 2PM to 3PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 4 | 3PM to 4PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 4 | 4PM to 5PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
December | 4 | 5PM to 6PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 4 | 6PM to 7PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 4 | 7PM to 8PM | 59 | 54.9 | 52 | 57.8 | 23.13 | 0.0761 | 0.39 | 13.25 | 0
December | 4 | 8PM to 9PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
December | 4 | 9PM to 10PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 4 | 10PM to 11PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 4 | 11PM to 12AM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
December | 5 | 12AM to 1AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
December | 5 | 1AM to 2AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 5 | 2AM to 3AM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 5 | 3AM to 4AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 5 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 5 | 5AM to 6AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 5 | 6AM to 7AM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 5 | 7AM to 8AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 5 | 8AM to 9AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 5 | 9AM to 10AM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 5 | 10AM to 11AM | 60.1 | 55.3 | 52 | 57.8 | 23.4 | 0.076 | 0.39 | 13.27 | 0
December | 5 | 11AM to 12PM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
December | 5 | 12PM to 1PM | 59 | 55.5 | 53.1 | 60.1 | 23.5 | 0.0761 | 0.41 | 13.25 | 0
December | 5 | 1PM to 2PM | 61 | 56.3 | 53.1 | 60.1 | 23.98 | 0.0758 | 0.41 | 13.3 | 0
December | 5 | 2PM to 3PM | 61 | 55.7 | 52 | 57.8 | 23.62 | 0.0758 | 0.39 | 13.3 | 0
December | 5 | 3PM to 4PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
December | 5 | 4PM to 5PM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
December | 5 | 5PM to 6PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 5 | 6PM to 7PM | 57.9 | 54.5 | 52 | 57.8 | 22.87 | 0.0763 | 0.39 | 13.22 | 0
December | 5 | 7PM to 8PM | 57 | 54.7 | 53.1 | 60.1 | 23.02 | 0.0764 | 0.41 | 13.2 | 0
December | 5 | 8PM to 9PM | 57 | 53.6 | 51.1 | 55.9 | 22.35 | 0.0764 | 0.38 | 13.19 | 0
December | 5 | 9PM to 10PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 5 | 10PM to 11PM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 5 | 11PM to 12AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
December | 6 | 12AM to 1AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 6 | 1AM to 2AM | 55.9 | 53.1 | 51.1 | 55.9 | 22.09 | 0.0766 | 0.38 | 13.16 | 0
December | 6 | 2AM to 3AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
December | 6 | 3AM to 4AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 4AM to 5AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 5AM to 6AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 6AM to 7AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 7AM to 8AM | 55 | 52.8 | 51.1 | 55.9 | 21.87 | 0.0767 | 0.38 | 13.14 | 0
December | 6 | 8AM to 9AM | 55 | 53.3 | 52 | 57.8 | 22.17 | 0.0767 | 0.39 | 13.15 | 0
December | 6 | 9AM to 10AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
December | 6 | 10AM to 11AM | 55.9 | 53.6 | 52 | 57.8 | 22.39 | 0.0766 | 0.39 | 13.17 | 0
December | 6 | 11AM to 12PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 6 | 12PM to 1PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 1PM to 2PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 2PM to 3PM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
December | 6 | 3PM to 4PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 4PM to 5PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 5PM to 6PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 6 | 6PM to 7PM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
December | 6 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 6 | 8PM to 9PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 6 | 9PM to 10PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
December | 6 | 10PM to 11PM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
December | 6 | 11PM to 12AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
December | 7 | 12AM to 1AM | 54 | 54 | 54 | 62.2 | 22.59 | 0.0768 | 0.42 | 13.13 | 0
December | 7 | 1AM to 2AM | 55.9 | 55.9 | 55.9 | 66.9 | 23.81 | 0.0765 | 0.45 | 13.2 | 0
December | 7 | 2AM to 3AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
December | 7 | 3AM to 4AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
December | 7 | 4AM to 5AM | 59 | 57.8 | 57 | 69.6 | 24.97 | 0.076 | 0.47 | 13.28 | 0
December | 7 | 5AM to 6AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
December | 7 | 6AM to 7AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
December | 7 | 7AM to 8AM | 57.9 | 56.7 | 55.9 | 66.9 | 24.29 | 0.0762 | 0.45 | 13.25 | 0
December | 7 | 8AM to 9AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
December | 7 | 9AM to 10AM | 60.1 | 57 | 55 | 64.7 | 24.48 | 0.0759 | 0.44 | 13.3 | 0
December | 7 | 10AM to 11AM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
December | 7 | 11AM to 12PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
December | 7 | 12PM to 1PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 7 | 1PM to 2PM | 59 | 52.8 | 48 | 49.8 | 21.89 | 0.0762 | 0.34 | 13.22 | 0
December | 7 | 2PM to 3PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 7 | 3PM to 4PM | 54 | 48.8 | 44.2 | 43.1 | 19.62 | 0.077 | 0.29 | 13.07 | 0
December | 7 | 4PM to 5PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
December | 7 | 5PM to 6PM | 50.5 | 48.1 | 46 | 46.1 | 19.27 | 0.0775 | 0.31 | 13 | 1
December | 7 | 6PM to 7PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
December | 7 | 7PM to 8PM | 50 | 48.9 | 48 | 49.8 | 19.7 | 0.0775 | 0.34 | 12.99 | 1
December | 7 | 8PM to 9PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 7 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
December | 7 | 10PM to 11PM | 48 | 45.6 | 43.3 | 41.6 | 17.96 | 0.0779 | 0.28 | 12.92 | 1
December | 7 | 11PM to 12AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
December | 8 | 12AM to 1AM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 8 | 1AM to 2AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 8 | 2AM to 3AM | 51.1 | 46.9 | 43 | 41 | 18.61 | 0.0774 | 0.28 | 13 | 1
December | 8 | 3AM to 4AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
December | 8 | 4AM to 5AM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 1
December | 8 | 5AM to 6AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
December | 8 | 6AM to 7AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
December | 8 | 7AM to 8AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 8 | 8AM to 9AM | 48 | 47 | 46 | 46.1 | 18.66 | 0.0778 | 0.31 | 12.93 | 1
December | 8 | 9AM to 10AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
December | 8 | 10AM to 11AM | 54 | 48.7 | 44.1 | 42.8 | 19.58 | 0.077 | 0.29 | 13.07 | 0
December | 8 | 11AM to 12PM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
December | 8 | 12PM to 1PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 8 | 1PM to 2PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
December | 8 | 2PM to 3PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
December | 8 | 3PM to 4PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
December | 8 | 4PM to 5PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 8 | 5PM to 6PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 8 | 6PM to 7PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
December | 8 | 7PM to 8PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 8 | 8PM to 9PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 8 | 9PM to 10PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
December | 8 | 10PM to 11PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 8 | 11PM to 12AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 9 | 12AM to 1AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 9 | 1AM to 2AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
December | 9 | 2AM to 3AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
December | 9 | 3AM to 4AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
December | 9 | 4AM to 5AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
December | 9 | 5AM to 6AM | 41 | 40.1 | 39 | 35.1 | 15.26 | 0.079 | 0.24 | 12.72 | 1
December | 9 | 6AM to 7AM | 42.1 | 41 | 39.9 | 36.4 | 15.71 | 0.0788 | 0.25 | 12.75 | 1
December | 9 | 7AM to 8AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
December | 9 | 8AM to 9AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 9 | 9AM to 10AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 9 | 10AM to 11AM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
December | 9 | 11AM to 12PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
December | 9 | 12PM to 1PM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
December | 9 | 1PM to 2PM | 55 | 47.4 | 39.9 | 36.4 | 18.85 | 0.0768 | 0.25 | 13.08 | 0
December | 9 | 2PM to 3PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 9 | 3PM to 4PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 9 | 4PM to 5PM | 54 | 46.1 | 37.9 | 33.7 | 18.17 | 0.077 | 0.23 | 13.05 | 0
December | 9 | 5PM to 6PM | 51.1 | 46.5 | 42.1 | 39.6 | 18.39 | 0.0774 | 0.27 | 12.99 | 1
December | 9 | 6PM to 7PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 9 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 9 | 8PM to 9PM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 9 | 9PM to 10PM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
December | 9 | 10PM to 11PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 9 | 11PM to 12AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 10 | 12AM to 1AM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
December | 10 | 1AM to 2AM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
December | 10 | 2AM to 3AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
December | 10 | 3AM to 4AM | 42.1 | 40.6 | 39 | 35.1 | 15.52 | 0.0788 | 0.24 | 12.75 | 1
December | 10 | 4AM to 5AM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0787 | 0.25 | 12.78 | 1
December | 10 | 5AM to 6AM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0787 | 0.25 | 12.78 | 1
December | 10 | 6AM to 7AM | 44.1 | 40.8 | 37 | 32.5 | 15.59 | 0.0785 | 0.22 | 12.79 | 1
December | 10 | 7AM to 8AM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
December | 10 | 8AM to 9AM | 48.9 | 44.1 | 39 | 35.1 | 17.17 | 0.0778 | 0.24 | 12.92 | 1
December | 10 | 9AM to 10AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
December | 10 | 10AM to 11AM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
December | 10 | 11AM to 12PM | 54 | 46.1 | 37.9 | 33.7 | 18.17 | 0.077 | 0.23 | 13.05 | 0
December | 10 | 12PM to 1PM | 55.9 | 47.4 | 39 | 35.1 | 18.88 | 0.0767 | 0.24 | 13.1 | 0
December | 10 | 1PM to 2PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
December | 10 | 2PM to 3PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
December | 10 | 3PM to 4PM | 55.9 | 47.8 | 39.9 | 36.4 | 19.07 | 0.0767 | 0.25 | 13.11 | 0
December | 10 | 4PM to 5PM | 55.9 | 50 | 45 | 44.3 | 20.29 | 0.0767 | 0.3 | 13.13 | 0
December | 10 | 5PM to 6PM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
December | 10 | 6PM to 7PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
December | 10 | 7PM to 8PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
December | 10 | 8PM to 9PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 1
December | 10 | 9PM to 10PM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 1
December | 10 | 10PM to 11PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 1
December | 10 | 11PM to 12AM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
December | 11 | 12AM to 1AM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
December | 11 | 1AM to 2AM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
December | 11 | 2AM to 3AM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
December | 11 | 3AM to 4AM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
December | 11 | 4AM to 5AM | 48.9 | 43.3 | 37 | 32.5 | 16.77 | 0.0778 | 0.22 | 12.92 | 1
December | 11 | 5AM to 6AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
December | 11 | 6AM to 7AM | 48.9 | 43.3 | 37 | 32.5 | 16.77 | 0.0778 | 0.22 | 12.92 | 1
December | 11 | 7AM to 8AM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
December | 11 | 8AM to 9AM | 52 | 44.8 | 37 | 32.5 | 17.51 | 0.0773 | 0.22 | 12.99 | 0
December | 11 | 9AM to 10AM | 54 | 45.7 | 37 | 32.5 | 17.99 | 0.077 | 0.22 | 13.04 | 0
December | 11 | 10AM to 11AM | 55.9 | 46.2 | 36 | 31.1 | 18.25 | 0.0767 | 0.21 | 13.09 | 0
December | 11 | 11AM to 12PM | 57 | 46.8 | 36 | 31.1 | 18.51 | 0.0766 | 0.21 | 13.12 | 0
December | 11 | 12PM to 1PM | 57.9 | 48.3 | 39 | 35.1 | 19.35 | 0.0764 | 0.24 | 13.15 | 0
December | 11 | 1PM to 2PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
December | 11 | 2PM to 3PM | 60.1 | 48.6 | 37 | 32.5 | 19.47 | 0.0761 | 0.22 | 13.2 | 0
December | 11 | 3PM to 4PM | 57 | 47.5 | 37.9 | 33.7 | 18.91 | 0.0766 | 0.23 | 13.12 | 0
December | 11 | 4PM to 5PM | 55.9 | 47.4 | 39 | 35.1 | 18.88 | 0.0767 | 0.24 | 13.1 | 0
December | 11 | 5PM to 6PM | 55 | 47 | 39 | 35.1 | 18.66 | 0.0768 | 0.24 | 13.08 | 0
December | 11 | 6PM to 7PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
December | 11 | 7PM to 8PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
December | 11 | 8PM to 9PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
December | 11 | 9PM to 10PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
December | 11 | 10PM to 11PM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
December | 11 | 11PM to 12AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 12 | 12AM to 1AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
December | 12 | 1AM to 2AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
December | 12 | 2AM to 3AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
December | 12 | 3AM to 4AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
December | 12 | 4AM to 5AM | 42.1 | 41 | 39.9 | 36.4 | 15.71 | 0.0788 | 0.25 | 12.75 | 1
December | 12 | 5AM to 6AM | 42.1 | 41.6 | 41 | 38 | 15.96 | 0.0788 | 0.26 | 12.76 | 1
December | 12 | 6AM to 7AM | 43 | 42.5 | 42.1 | 39.6 | 16.43 | 0.0787 | 0.27 | 12.79 | 1
December | 12 | 7AM to 8AM | 45 | 43.5 | 42.1 | 39.6 | 16.91 | 0.0784 | 0.27 | 12.84 | 1
December | 12 | 8AM to 9AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 12 | 9AM to 10AM | 46.9 | 44.9 | 43 | 41 | 17.6 | 0.078 | 0.28 | 12.89 | 1
December | 12 | 10AM to 11AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 12 | 11AM to 12PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 12 | 12PM to 1PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 12 | 1PM to 2PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
December | 12 | 2PM to 3PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 12 | 3PM to 4PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
December | 12 | 4PM to 5PM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
December | 12 | 5PM to 6PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 12 | 6PM to 7PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 12 | 7PM to 8PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 12 | 8PM to 9PM | 46 | 45 | 44.1 | 42.8 | 17.66 | 0.0782 | 0.29 | 12.87 | 1
December | 12 | 9PM to 10PM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
December | 12 | 10PM to 11PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
December | 12 | 11PM to 12AM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
December | 13 | 12AM to 1AM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
December | 13 | 1AM to 2AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
December | 13 | 2AM to 3AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
December | 13 | 3AM to 4AM | 45 | 42.1 | 39 | 35.1 | 16.22 | 0.0784 | 0.24 | 12.82 | 1
December | 13 | 4AM to 5AM | 45 | 41.6 | 37.9 | 33.7 | 15.99 | 0.0784 | 0.23 | 12.82 | 1
December | 13 | 5AM to 6AM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
December | 13 | 6AM to 7AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
December | 13 | 7AM to 8AM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0784 | 0.25 | 12.83 | 1
December | 13 | 8AM to 9AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
December | 13 | 9AM to 10AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
December | 13 | 10AM to 11AM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
December | 13 | 11AM to 12PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 13 | 12PM to 1PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 13 | 1PM to 2PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 13 | 2PM to 3PM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 13 | 3PM to 4PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 13 | 4PM to 5PM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 13 | 5PM to 6PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 13 | 6PM to 7PM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 13 | 7PM to 8PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 13 | 8PM to 9PM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
December | 13 | 9PM to 10PM | 52 | 47.8 | 44.1 | 42.8 | 19.1 | 0.0773 | 0.29 | 13.02 | 0
December | 13 | 10PM to 11PM | 54.9 | 53.4 | 52.3 | 58.6 | 22.25 | 0.0767 | 0.4 | 13.14 | 0
December | 13 | 11PM to 12AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
December | 14 | 12AM to 1AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
December | 14 | 1AM to 2AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 2AM to 3AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 3AM to 4AM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 1
December | 14 | 4AM to 5AM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 1
December | 14 | 5AM to 6AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 6AM to 7AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 7AM to 8AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 8AM to 9AM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 14 | 9AM to 10AM | 53.1 | 53.1 | 53.1 | 60.1 | 22.05 | 0.077 | 0.41 | 13.1 | 0
December | 14 | 10AM to 11AM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
December | 14 | 11AM to 12PM | 54 | 53.4 | 53.1 | 60.1 | 22.27 | 0.0768 | 0.41 | 13.13 | 0
December | 14 | 12PM to 1PM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
December | 14 | 1PM to 2PM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
December | 14 | 2PM to 3PM | 57.9 | 55.1 | 53.1 | 60.1 | 23.24 | 0.0763 | 0.41 | 13.23 | 0
December | 14 | 3PM to 4PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
December | 14 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
December | 14 | 5PM to 6PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 14 | 6PM to 7PM | 54 | 50.7 | 48 | 49.8 | 20.66 | 0.0769 | 0.34 | 13.09 | 0
December | 14 | 7PM to 8PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
December | 14 | 8PM to 9PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
December | 14 | 9PM to 10PM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0777 | 0.32 | 12.96 | 1
December | 14 | 10PM to 11PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 14 | 11PM to 12AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
December | 15 | 12AM to 1AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
December | 15 | 1AM to 2AM | 45 | 45 | 45 | 44.3 | 17.63 | 0.0783 | 0.3 | 12.85 | 1
December | 15 | 2AM to 3AM | 44.1 | 44.1 | 44.1 | 42.8 | 17.18 | 0.0785 | 0.29 | 12.82 | 1
December | 15 | 3AM to 4AM | 42.1 | 42.1 | 42.1 | 39.6 | 16.21 | 0.0788 | 0.27 | 12.76 | 1
December | 15 | 4AM to 5AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
December | 15 | 5AM to 6AM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
December | 15 | 6AM to 7AM | 44.1 | 43.5 | 43 | 41 | 16.91 | 0.0785 | 0.28 | 12.82 | 1
December | 15 | 7AM to 8AM | 45 | 44.5 | 44.1 | 42.8 | 17.39 | 0.0783 | 0.29 | 12.84 | 1
December | 15 | 8AM to 9AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
December | 15 | 9AM to 10AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 15 | 10AM to 11AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 15 | 11AM to 12PM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
December | 15 | 12PM to 1PM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 15 | 1PM to 2PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
December | 15 | 2PM to 3PM | 52 | 49.2 | 46.9 | 47.8 | 19.87 | 0.0772 | 0.32 | 13.04 | 0
December | 15 | 3PM to 4PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
December | 15 | 4PM to 5PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
December | 15 | 5PM to 6PM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
December | 15 | 6PM to 7PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
December | 15 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 15 | 8PM to 9PM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
December | 15 | 9PM to 10PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 15 | 10PM to 11PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
December | 15 | 11PM to 12AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 16 | 12AM to 1AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
December | 16 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
December | 16 | 2AM to 3AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
December | 16 | 3AM to 4AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
December | 16 | 4AM to 5AM | 46.9 | 46.5 | 46 | 46.1 | 18.4 | 0.078 | 0.31 | 12.9 | 1
December | 16 | 5AM to 6AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
December | 16 | 6AM to 7AM | 46 | 45.5 | 45 | 44.3 | 17.89 | 0.0782 | 0.3 | 12.88 | 1
December | 16 | 7AM to 8AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
December | 16 | 8AM to 9AM | 48 | 46.4 | 45 | 44.3 | 18.37 | 0.0778 | 0.3 | 12.93 | 1
December | 16 | 9AM to 10AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 16 | 10AM to 11AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
December | 16 | 11AM to 12PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 16 | 12PM to 1PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
December | 16 | 1PM to 2PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
December | 16 | 2PM to 3PM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
December | 16 | 3PM to 4PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
December | 16 | 4PM to 5PM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 16 | 5PM to 6PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 16 | 6PM to 7PM | 52 | 49.8 | 48 | 49.8 | 20.18 | 0.0772 | 0.34 | 13.04 | 0
December | 16 | 7PM to 8PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 16 | 8PM to 9PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
December | 16 | 9PM to 10PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
December | 16 | 10PM to 11PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
December | 16 | 11PM to 12AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 17 | 12AM to 1AM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
December | 17 | 1AM to 2AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 17 | 2AM to 3AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 17 | 3AM to 4AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 17 | 4AM to 5AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 17 | 5AM to 6AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 17 | 6AM to 7AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 17 | 7AM to 8AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 17 | 8AM to 9AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 17 | 9AM to 10AM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 17 | 10AM to 11AM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
December | 17 | 11AM to 12PM | 53.1 | 50.8 | 48.9 | 51.5 | 20.71 | 0.077 | 0.35 | 13.08 | 0
December | 17 | 12PM to 1PM | 54 | 51.7 | 50 | 53.6 | 21.26 | 0.0769 | 0.36 | 13.11 | 0
December | 17 | 1PM to 2PM | 54 | 52.3 | 51.1 | 55.9 | 21.61 | 0.0769 | 0.38 | 13.11 | 0
December | 17 | 2PM to 3PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.09 | 0
December | 17 | 3PM to 4PM | 52 | 52 | 52 | 57.8 | 21.42 | 0.0772 | 0.39 | 13.07 | 0
December | 17 | 4PM to 5PM | 50 | 50 | 50 | 53.6 | 20.3 | 0.0775 | 0.36 | 13 | 1
December | 17 | 5PM to 6PM | 50 | 49.4 | 48.9 | 51.5 | 19.97 | 0.0775 | 0.35 | 13 | 1
December | 17 | 6PM to 7PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
December | 17 | 7PM to 8PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
December | 17 | 8PM to 9PM | 51.1 | 49.4 | 48 | 49.8 | 19.96 | 0.0773 | 0.34 | 13.02 | 1
December | 17 | 9PM to 10PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
December | 17 | 10PM to 11PM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
December | 17 | 11PM to 12AM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 18 | 12AM to 1AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
December | 18 | 1AM to 2AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 18 | 2AM to 3AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 18 | 3AM to 4AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
December | 18 | 4AM to 5AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
December | 18 | 5AM to 6AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 18 | 6AM to 7AM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
December | 18 | 7AM to 8AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 18 | 8AM to 9AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 18 | 9AM to 10AM | 52 | 50.3 | 48.9 | 51.5 | 20.45 | 0.0772 | 0.35 | 13.05 | 0
December | 18 | 10AM to 11AM | 53.1 | 50.3 | 48 | 49.8 | 20.44 | 0.077 | 0.34 | 13.07 | 0
December | 18 | 11AM to 12PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 18 | 12PM to 1PM | 55.9 | 50.5 | 46 | 46.1 | 20.58 | 0.0766 | 0.31 | 13.13 | 0
December | 18 | 1PM to 2PM | 57 | 51 | 46 | 46.1 | 20.85 | 0.0765 | 0.31 | 13.16 | 0
December | 18 | 2PM to 3PM | 59 | 50.1 | 42.1 | 39.6 | 20.31 | 0.0762 | 0.27 | 13.19 | 0
December | 18 | 3PM to 4PM | 57.9 | 50.5 | 44.1 | 42.8 | 20.54 | 0.0764 | 0.29 | 13.17 | 0
December | 18 | 4PM to 5PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
December | 18 | 5PM to 6PM | 57.9 | 47.6 | 37 | 32.5 | 18.94 | 0.0764 | 0.22 | 13.14 | 0
December | 18 | 6PM to 7PM | 57 | 47.5 | 37.9 | 33.7 | 18.91 | 0.0766 | 0.23 | 13.12 | 0
December | 18 | 7PM to 8PM | 55.9 | 46.2 | 36 | 31.1 | 18.25 | 0.0767 | 0.21 | 13.09 | 0
December | 18 | 8PM to 9PM | 55 | 45.8 | 36 | 31.1 | 18.03 | 0.0769 | 0.21 | 13.07 | 0
December | 18 | 9PM to 10PM | 55 | 46.2 | 37 | 32.5 | 18.25 | 0.0769 | 0.22 | 13.07 | 0
December | 18 | 10PM to 11PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 18 | 11PM to 12AM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 19 | 12AM to 1AM | 53.1 | 42 | 28 | 22.1 | 16.16 | 0.0772 | 0.15 | 12.99 | 0
December | 19 | 1AM to 2AM | 53.1 | 43.8 | 33.1 | 27.7 | 17.03 | 0.0772 | 0.19 | 13.01 | 0
December | 19 | 2AM to 3AM | 53.1 | 44.1 | 34 | 28.7 | 17.19 | 0.0772 | 0.2 | 13.01 | 0
December | 19 | 3AM to 4AM | 53.1 | 44.9 | 36 | 31.1 | 17.56 | 0.0772 | 0.21 | 13.02 | 0
December | 19 | 4AM to 5AM | 53.1 | 43.8 | 33.1 | 27.7 | 17.03 | 0.0772 | 0.19 | 13.01 | 0
December | 19 | 5AM to 6AM | 51.1 | 43.9 | 36 | 31.1 | 17.08 | 0.0775 | 0.21 | 12.97 | 1
December | 19 | 6AM to 7AM | 48 | 41.6 | 34 | 28.7 | 15.97 | 0.078 | 0.2 | 12.88 | 1
December | 19 | 7AM to 8AM | 46 | 41 | 35.1 | 30 | 15.69 | 0.0782 | 0.2 | 12.83 | 1
December | 19 | 8AM to 9AM | 51.1 | 43.2 | 34 | 28.7 | 16.71 | 0.0775 | 0.2 | 12.96 | 1
December | 19 | 9AM to 10AM | 54 | 43.2 | 30 | 24.2 | 16.7 | 0.0771 | 0.16 | 13.02 | 0
December | 19 | 10AM to 11AM | 55 | 42.1 | 25 | 19.1 | 16.17 | 0.077 | 0.13 | 13.03 | 0
December | 19 | 11AM to 12PM | 57 | 42.2 | 21.9 | 16.5 | 16.25 | 0.0767 | 0.11 | 13.07 | 0
December | 19 | 12PM to 1PM | 57.9 | 43.5 | 25 | 19.1 | 16.87 | 0.0765 | 0.13 | 13.1 | 0
December | 19 | 1PM to 2PM | 59 | 45.6 | 30 | 24.2 | 17.92 | 0.0763 | 0.16 | 13.15 | 0
December | 19 | 2PM to 3PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
December | 19 | 3PM to 4PM | 59 | 46.3 | 32 | 26.5 | 18.28 | 0.0763 | 0.18 | 13.15 | 0
December | 19 | 4PM to 5PM | 57 | 44 | 28 | 22.1 | 17.11 | 0.0766 | 0.15 | 13.09 | 0
December | 19 | 5PM to 6PM | 55 | 44 | 30.9 | 25.2 | 17.12 | 0.0769 | 0.17 | 13.05 | 0
December | 19 | 6PM to 7PM | 52 | 45.9 | 39.9 | 36.4 | 18.11 | 0.0773 | 0.25 | 13 | 0
December | 19 | 7PM to 8PM | 51.1 | 44.7 | 37.9 | 33.7 | 17.47 | 0.0775 | 0.23 | 12.97 | 1
December | 19 | 8PM to 9PM | 51.1 | 43.9 | 36 | 31.1 | 17.08 | 0.0775 | 0.21 | 12.97 | 1
December | 19 | 9PM to 10PM | 50 | 43.4 | 36 | 31.1 | 16.82 | 0.0776 | 0.21 | 12.94 | 1
December | 19 | 10PM to 11PM | 48.9 | 42.8 | 36 | 31.1 | 16.55 | 0.0778 | 0.21 | 12.91 | 1
December | 19 | 11PM to 12AM | 50 | 42.6 | 34 | 28.7 | 16.45 | 0.0776 | 0.2 | 12.93 | 1
December | 20 | 12AM to 1AM | 48 | 43.6 | 39 | 35.1 | 16.96 | 0.0779 | 0.24 | 12.9 | 1
December | 20 | 1AM to 2AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 20 | 2AM to 3AM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 20 | 3AM to 4AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
December | 20 | 4AM to 5AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
December | 20 | 5AM to 6AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
December | 20 | 6AM to 7AM | 46 | 43.5 | 41 | 38 | 16.92 | 0.0782 | 0.26 | 12.86 | 1
December | 20 | 7AM to 8AM | 45 | 43 | 41 | 38 | 16.65 | 0.0784 | 0.26 | 12.83 | 1
December | 20 | 8AM to 9AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
December | 20 | 9AM to 10AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 20 | 10AM to 11AM | 52 | 48.8 | 46 | 46.1 | 19.62 | 0.0772 | 0.31 | 13.03 | 0
December | 20 | 11AM to 12PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 20 | 12PM to 1PM | 57 | 54.1 | 52 | 57.8 | 22.65 | 0.0764 | 0.39 | 13.2 | 0
December | 20 | 1PM to 2PM | 57 | 53 | 50 | 53.6 | 22.01 | 0.0764 | 0.36 | 13.18 | 0
December | 20 | 2PM to 3PM | 57 | 52 | 48 | 49.8 | 21.41 | 0.0765 | 0.34 | 13.17 | 0
December | 20 | 3PM to 4PM | 55.9 | 51 | 46.9 | 47.8 | 20.83 | 0.0766 | 0.32 | 13.14 | 0
December | 20 | 4PM to 5PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
December | 20 | 5PM to 6PM | 54 | 49.1 | 45 | 44.3 | 19.81 | 0.0769 | 0.3 | 13.08 | 0
December | 20 | 6PM to 7PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 20 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 20 | 8PM to 9PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 20 | 9PM to 10PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 20 | 10PM to 11PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 20 | 11PM to 12AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 21 | 12AM to 1AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 21 | 1AM to 2AM | 48.9 | 44.1 | 39 | 35.1 | 17.17 | 0.0778 | 0.24 | 12.92 | 1
December | 21 | 2AM to 3AM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 21 | 3AM to 4AM | 48.9 | 45.9 | 43 | 41 | 18.08 | 0.0777 | 0.28 | 12.94 | 1
December | 21 | 4AM to 5AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
December | 21 | 5AM to 6AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
December | 21 | 6AM to 7AM | 46 | 44.1 | 42.1 | 39.6 | 17.17 | 0.0782 | 0.27 | 12.86 | 1
December | 21 | 7AM to 8AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 21 | 8AM to 9AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 21 | 9AM to 10AM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 21 | 10AM to 11AM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
December | 21 | 11AM to 12PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
December | 21 | 12PM to 1PM | 54 | 44.3 | 33.1 | 27.7 | 17.25 | 0.0771 | 0.19 | 13.03 | 0
December | 21 | 1PM to 2PM | 55 | 45.1 | 34 | 28.7 | 17.67 | 0.0769 | 0.2 | 13.06 | 0
December | 21 | 2PM to 3PM | 55.9 | 45.2 | 33.1 | 27.7 | 17.73 | 0.0768 | 0.19 | 13.08 | 0
December | 21 | 3PM to 4PM | 55.9 | 45.5 | 34 | 28.7 | 17.88 | 0.0768 | 0.2 | 13.08 | 0
December | 21 | 4PM to 5PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
December | 21 | 5PM to 6PM | 54 | 45 | 35.1 | 30 | 17.6 | 0.077 | 0.2 | 13.04 | 0
December | 21 | 6PM to 7PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 21 | 7PM to 8PM | 52 | 42.2 | 30 | 24.2 | 16.23 | 0.0774 | 0.16 | 12.97 | 0
December | 21 | 8PM to 9PM | 52 | 43.3 | 33.1 | 27.7 | 16.77 | 0.0774 | 0.19 | 12.98 | 0
December | 21 | 9PM to 10PM | 51.1 | 42 | 30.9 | 25.2 | 16.17 | 0.0775 | 0.17 | 12.95 | 1
December | 21 | 10PM to 11PM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 1
December | 21 | 11PM to 12AM | 50 | 42.3 | 33.1 | 27.7 | 16.29 | 0.0777 | 0.19 | 12.93 | 1
December | 22 | 12AM to 1AM | 50 | 41.9 | 32 | 26.5 | 16.11 | 0.0777 | 0.18 | 12.93 | 1
December | 22 | 1AM to 2AM | 50 | 41.1 | 30 | 24.2 | 15.75 | 0.0777 | 0.16 | 12.92 | 1
December | 22 | 2AM to 3AM | 48.9 | 40.9 | 30.9 | 25.2 | 15.65 | 0.0778 | 0.17 | 12.89 | 1
December | 22 | 3AM to 4AM | 48 | 40.5 | 30.9 | 25.2 | 15.43 | 0.078 | 0.17 | 12.87 | 1
December | 22 | 4AM to 5AM | 48 | 39.7 | 28.9 | 23 | 15.09 | 0.078 | 0.16 | 12.86 | 1
December | 22 | 5AM to 6AM | 48 | 39.7 | 28.9 | 23 | 15.09 | 0.078 | 0.16 | 12.86 | 1
December | 22 | 6AM to 7AM | 48 | 40.1 | 30 | 24.2 | 15.27 | 0.078 | 0.16 | 12.87 | 1
December | 22 | 7AM to 8AM | 48 | 40.1 | 30 | 24.2 | 15.27 | 0.078 | 0.16 | 12.87 | 1
December | 22 | 8AM to 9AM | 48.9 | 40.2 | 28.9 | 23 | 15.3 | 0.0779 | 0.16 | 12.89 | 1
December | 22 | 9AM to 10AM | 48.9 | 39.9 | 28 | 22.1 | 15.16 | 0.0779 | 0.15 | 12.88 | 1
December | 22 | 10AM to 11AM | 50 | 40.1 | 27 | 21 | 15.25 | 0.0777 | 0.14 | 12.91 | 1
December | 22 | 11AM to 12PM | 52 | 41.8 | 28.9 | 23 | 16.04 | 0.0774 | 0.16 | 12.96 | 0
December | 22 | 12PM to 1PM | 53.1 | 42.3 | 28.9 | 23 | 16.3 | 0.0772 | 0.16 | 12.99 | 0
December | 22 | 1PM to 2PM | 54 | 44.6 | 34 | 28.7 | 17.41 | 0.077 | 0.2 | 13.03 | 0
December | 22 | 2PM to 3PM | 55 | 44.8 | 33.1 | 27.7 | 17.51 | 0.0769 | 0.19 | 13.06 | 0
December | 22 | 3PM to 4PM | 55.9 | 45.2 | 33.1 | 27.7 | 17.73 | 0.0768 | 0.19 | 13.08 | 0
December | 22 | 4PM to 5PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
December | 22 | 5PM to 6PM | 52 | 42.5 | 30.9 | 25.2 | 16.38 | 0.0774 | 0.17 | 12.97 | 0
December | 22 | 6PM to 7PM | 50 | 41.1 | 30 | 24.2 | 15.75 | 0.0777 | 0.16 | 12.92 | 1
December | 22 | 7PM to 8PM | 48.9 | 39.5 | 27 | 21 | 14.99 | 0.0779 | 0.14 | 12.88 | 1
December | 22 | 8PM to 9PM | 46 | 39.9 | 32 | 26.5 | 15.15 | 0.0783 | 0.18 | 12.82 | 1
December | 22 | 9PM to 10PM | 46.9 | 39.2 | 28.9 | 23 | 14.82 | 0.0782 | 0.16 | 12.84 | 1
December | 22 | 10PM to 11PM | 44.1 | 38.8 | 32 | 26.5 | 14.67 | 0.0786 | 0.18 | 12.77 | 1
December | 22 | 11PM to 12AM | 44.1 | 36.9 | 27 | 21 | 13.82 | 0.0786 | 0.14 | 12.76 | 1
December | 23 | 12AM to 1AM | 44.1 | 39.5 | 34 | 28.7 | 15.01 | 0.0786 | 0.2 | 12.78 | 1
December | 23 | 1AM to 2AM | 42.1 | 38.5 | 34 | 28.7 | 14.53 | 0.0789 | 0.2 | 12.73 | 1
December | 23 | 2AM to 3AM | 39.9 | 37.8 | 35.1 | 30 | 14.21 | 0.0792 | 0.2 | 12.68 | 1
December | 23 | 3AM to 4AM | 37.9 | 36.2 | 34 | 28.7 | 13.53 | 0.0795 | 0.2 | 12.63 | 1
December | 23 | 4AM to 5AM | 41 | 37.9 | 34 | 28.7 | 14.27 | 0.079 | 0.2 | 12.7 | 1
December | 23 | 5AM to 6AM | 39 | 35.2 | 30 | 24.2 | 13.09 | 0.0794 | 0.16 | 12.64 | 1
December | 23 | 6AM to 7AM | 39 | 36 | 32 | 26.5 | 13.45 | 0.0794 | 0.18 | 12.65 | 1
December | 23 | 7AM to 8AM | 41 | 38.3 | 35.1 | 30 | 14.47 | 0.079 | 0.2 | 12.71 | 1
December | 23 | 8AM to 9AM | 45 | 41.3 | 37 | 32.5 | 15.81 | 0.0784 | 0.22 | 12.81 | 1
December | 23 | 9AM to 10AM | 48 | 43.2 | 37.9 | 33.7 | 16.73 | 0.0779 | 0.23 | 12.9 | 1
December | 23 | 10AM to 11AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 23 | 11AM to 12PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 23 | 12PM to 1PM | 51.1 | 45.5 | 39.9 | 36.4 | 17.89 | 0.0774 | 0.25 | 12.98 | 1
December | 23 | 1PM to 2PM | 52 | 44.8 | 37 | 32.5 | 17.51 | 0.0773 | 0.22 | 12.99 | 0
December | 23 | 2PM to 3PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 23 | 3PM to 4PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
December | 23 | 4PM to 5PM | 55.9 | 52 | 48.9 | 51.5 | 21.41 | 0.0766 | 0.35 | 13.15 | 0
December | 23 | 5PM to 6PM | 55 | 52.2 | 50 | 53.6 | 21.53 | 0.0767 | 0.36 | 13.13 | 0
December | 23 | 6PM to 7PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
December | 23 | 7PM to 8PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 23 | 8PM to 9PM | 52 | 48.3 | 45 | 44.3 | 19.33 | 0.0772 | 0.3 | 13.03 | 0
December | 23 | 9PM to 10PM | 52 | 46.9 | 42.1 | 39.6 | 18.61 | 0.0773 | 0.27 | 13.01 | 0
December | 23 | 10PM to 11PM | 53.1 | 47.8 | 43 | 41 | 19.09 | 0.0771 | 0.28 | 13.05 | 0
December | 23 | 11PM to 12AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
December | 24 | 12AM to 1AM | 51.1 | 45.1 | 39 | 35.1 | 17.7 | 0.0774 | 0.24 | 12.98 | 1
December | 24 | 1AM to 2AM | 48 | 42.4 | 36 | 31.1 | 16.34 | 0.0779 | 0.21 | 12.89 | 1
December | 24 | 2AM to 3AM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 1
December | 24 | 3AM to 4AM | 50 | 43.4 | 36 | 31.1 | 16.82 | 0.0776 | 0.21 | 12.94 | 1
December | 24 | 4AM to 5AM | 48 | 42.4 | 36 | 31.1 | 16.34 | 0.0779 | 0.21 | 12.89 | 1
December | 24 | 5AM to 6AM | 46.9 | 41.8 | 36 | 31.1 | 16.07 | 0.0781 | 0.21 | 12.86 | 1
December | 24 | 6AM to 7AM | 48.9 | 44.5 | 39.9 | 36.4 | 17.37 | 0.0778 | 0.25 | 12.93 | 1
December | 24 | 7AM to 8AM | 48.9 | 43.6 | 37.9 | 33.7 | 16.95 | 0.0778 | 0.23 | 12.92 | 1
December | 24 | 8AM to 9AM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0776 | 0.28 | 12.97 | 1
December | 24 | 9AM to 10AM | 51.1 | 47.4 | 44.1 | 42.8 | 18.88 | 0.0774 | 0.29 | 13 | 1
December | 24 | 10AM to 11AM | 54 | 46.5 | 39 | 35.1 | 18.4 | 0.077 | 0.24 | 13.05 | 0
December | 24 | 11AM to 12PM | 54 | 46.9 | 39.9 | 36.4 | 18.59 | 0.077 | 0.25 | 13.05 | 0
December | 24 | 12PM to 1PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
December | 24 | 1PM to 2PM | 55.9 | 45.9 | 35.1 | 30 | 18.08 | 0.0767 | 0.2 | 13.09 | 0
December | 24 | 2PM to 3PM | 55.9 | 44.9 | 32 | 26.5 | 17.54 | 0.0768 | 0.18 | 13.08 | 0
December | 24 | 3PM to 4PM | 55 | 45.8 | 36 | 31.1 | 18.03 | 0.0769 | 0.21 | 13.07 | 0
December | 24 | 4PM to 5PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 24 | 5PM to 6PM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
December | 24 | 6PM to 7PM | 53.1 | 44.9 | 36 | 31.1 | 17.56 | 0.0772 | 0.21 | 13.02 | 0
December | 24 | 7PM to 8PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 24 | 8PM to 9PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 24 | 9PM to 10PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
December | 24 | 10PM to 11PM | 52 | 44 | 35.1 | 30 | 17.12 | 0.0773 | 0.2 | 12.99 | 0
December | 24 | 11PM to 12AM | 51.1 | 43.6 | 35.1 | 30 | 16.91 | 0.0775 | 0.2 | 12.96 | 1
December | 25 | 12AM to 1AM | 51.1 | 42.8 | 33.1 | 27.7 | 16.55 | 0.0775 | 0.19 | 12.96 | 1
December | 25 | 1AM to 2AM | 51.1 | 42.8 | 33.1 | 27.7 | 16.55 | 0.0775 | 0.19 | 12.96 | 1
December | 25 | 2AM to 3AM | 50 | 41.9 | 32 | 26.5 | 16.11 | 0.0777 | 0.18 | 12.93 | 1
December | 25 | 3AM to 4AM | 51.1 | 42.5 | 32 | 26.5 | 16.37 | 0.0775 | 0.18 | 12.95 | 1
December | 25 | 4AM to 5AM | 50 | 42.6 | 34 | 28.7 | 16.45 | 0.0776 | 0.2 | 12.93 | 1
December | 25 | 5AM to 6AM | 48.9 | 40.9 | 30.9 | 25.2 | 15.65 | 0.0778 | 0.17 | 12.89 | 1
December | 25 | 6AM to 7AM | 48 | 40.9 | 32 | 26.5 | 15.63 | 0.078 | 0.18 | 12.87 | 1
December | 25 | 7AM to 8AM | 48 | 41.3 | 33.1 | 27.7 | 15.81 | 0.078 | 0.19 | 12.88 | 1
December | 25 | 8AM to 9AM | 50 | 41.9 | 32 | 26.5 | 16.11 | 0.0777 | 0.18 | 12.93 | 1
December | 25 | 9AM to 10AM | 50 | 42.3 | 33.1 | 27.7 | 16.29 | 0.0777 | 0.19 | 12.93 | 1
December | 25 | 10AM to 11AM | 52 | 43.6 | 34 | 28.7 | 16.93 | 0.0773 | 0.2 | 12.98 | 0
December | 25 | 11AM to 12PM | 53.1 | 44.1 | 34 | 28.7 | 17.19 | 0.0772 | 0.2 | 13.01 | 0
December | 25 | 12PM to 1PM | 53.1 | 44.5 | 35.1 | 30 | 17.39 | 0.0772 | 0.2 | 13.01 | 0
December | 25 | 1PM to 2PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 25 | 2PM to 3PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
December | 25 | 3PM to 4PM | 54 | 45.3 | 36 | 31.1 | 17.77 | 0.077 | 0.21 | 13.04 | 0
December | 25 | 4PM to 5PM | 53.1 | 45.3 | 37 | 32.5 | 17.77 | 0.0772 | 0.22 | 13.02 | 0
December | 25 | 5PM to 6PM | 51.1 | 46 | 41 | 38 | 18.14 | 0.0774 | 0.26 | 12.99 | 1
December | 25 | 6PM to 7PM | 48.9 | 42.5 | 35.1 | 30 | 16.38 | 0.0778 | 0.2 | 12.91 | 1
December | 25 | 7PM to 8PM | 48 | 41.3 | 33.1 | 27.7 | 15.81 | 0.078 | 0.19 | 12.88 | 1
December | 25 | 8PM to 9PM | 45 | 39.7 | 33.1 | 27.7 | 15.07 | 0.0784 | 0.19 | 12.8 | 1
December | 25 | 9PM to 10PM | 45 | 38.1 | 28.9 | 23 | 14.35 | 0.0785 | 0.16 | 12.79 | 1
December | 25 | 10PM to 11PM | 46 | 38.7 | 28.9 | 23 | 14.61 | 0.0783 | 0.16 | 12.81 | 1
December | 25 | 11PM to 12AM | 44.1 | 37.3 | 28 | 22.1 | 13.98 | 0.0786 | 0.15 | 12.76 | 1
December | 26 | 12AM to 1AM | 43 | 38.2 | 32 | 26.5 | 14.41 | 0.0787 | 0.18 | 12.75 | 1
December | 26 | 1AM to 2AM | 41 | 36.3 | 30 | 24.2 | 13.57 | 0.0791 | 0.16 | 12.69 | 1
December | 26 | 2AM to 3AM | 37.9 | 34.6 | 30 | 24.2 | 12.83 | 0.0796 | 0.16 | 12.61 | 1
December | 26 | 3AM to 4AM | 37.9 | 35 | 30.9 | 25.2 | 12.99 | 0.0796 | 0.17 | 12.62 | 1
December | 26 | 4AM to 5AM | 37 | 34.5 | 30.9 | 25.2 | 12.78 | 0.0797 | 0.17 | 12.59 | 1
December | 26 | 5AM to 6AM | 37.9 | 35.4 | 32 | 26.5 | 13.19 | 0.0795 | 0.18 | 12.62 | 1
December | 26 | 6AM to 7AM | 37.9 | 35.9 | 33.1 | 27.7 | 13.37 | 0.0795 | 0.19 | 12.62 | 1
December | 26 | 7AM to 8AM | 39.9 | 37.8 | 35.1 | 30 | 14.21 | 0.0792 | 0.2 | 12.68 | 1
December | 26 | 8AM to 9AM | 42.1 | 39.8 | 37 | 32.5 | 15.11 | 0.0788 | 0.22 | 12.74 | 1
December | 26 | 9AM to 10AM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
December | 26 | 10AM to 11AM | 48.9 | 42.8 | 36 | 31.1 | 16.55 | 0.0778 | 0.21 | 12.91 | 1
December | 26 | 11AM to 12PM | 48.9 | 42.1 | 34 | 28.7 | 16.19 | 0.0778 | 0.2 | 12.9 | 1
December | 26 | 12PM to 1PM | 51.1 | 43.2 | 34 | 28.7 | 16.71 | 0.0775 | 0.2 | 12.96 | 1
December | 26 | 1PM to 2PM | 53.1 | 43.4 | 32 | 26.5 | 16.85 | 0.0772 | 0.18 | 13 | 0
December | 26 | 2PM to 3PM | 54 | 43.5 | 30.9 | 25.2 | 16.86 | 0.0771 | 0.17 | 13.02 | 0
December | 26 | 3PM to 4PM | 52 | 43.6 | 34 | 28.7 | 16.93 | 0.0773 | 0.2 | 12.98 | 0
December | 26 | 4PM to 5PM | 51.1 | 44.3 | 37 | 32.5 | 17.29 | 0.0775 | 0.22 | 12.97 | 1
December | 26 | 5PM to 6PM | 51.1 | 43.2 | 34 | 28.7 | 16.71 | 0.0775 | 0.2 | 12.96 | 1
December | 26 | 6PM to 7PM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 26 | 7PM to 8PM | 46 | 41.4 | 36 | 31.1 | 15.86 | 0.0782 | 0.21 | 12.84 | 1
December | 26 | 8PM to 9PM | 46 | 40.2 | 33.1 | 27.7 | 15.33 | 0.0783 | 0.19 | 12.83 | 1
December | 26 | 9PM to 10PM | 45 | 40 | 34 | 28.7 | 15.23 | 0.0784 | 0.2 | 12.8 | 1
December | 26 | 10PM to 11PM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
December | 26 | 11PM to 12AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
December | 27 | 12AM to 1AM | 44.1 | 40 | 35.1 | 30 | 15.21 | 0.0786 | 0.2 | 12.78 | 1
December | 27 | 1AM to 2AM | 41 | 38.3 | 35.1 | 30 | 14.47 | 0.079 | 0.2 | 12.71 | 1
December | 27 | 2AM to 3AM | 41 | 38.7 | 36 | 31.1 | 14.64 | 0.079 | 0.21 | 12.71 | 1
December | 27 | 3AM to 4AM | 37 | 35.7 | 34 | 28.7 | 13.31 | 0.0797 | 0.2 | 12.6 | 1
December | 27 | 4AM to 5AM | 42.1 | 38.9 | 35.1 | 30 | 14.73 | 0.0789 | 0.2 | 12.73 | 1
December | 27 | 5AM to 6AM | 37 | 35.7 | 34 | 28.7 | 13.31 | 0.0797 | 0.2 | 12.6 | 1
December | 27 | 6AM to 7AM | 37.9 | 36.2 | 34 | 28.7 | 13.53 | 0.0795 | 0.2 | 12.63 | 1
December | 27 | 7AM to 8AM | 42.1 | 39.3 | 36 | 31.1 | 14.9 | 0.0789 | 0.21 | 12.74 | 1
December | 27 | 8AM to 9AM | 43 | 40.6 | 37.9 | 33.7 | 15.51 | 0.0787 | 0.23 | 12.77 | 1
December | 27 | 9AM to 10AM | 46 | 42.7 | 39 | 35.1 | 16.48 | 0.0782 | 0.24 | 12.85 | 1
December | 27 | 10AM to 11AM | 46.9 | 43.1 | 39 | 35.1 | 16.7 | 0.0781 | 0.24 | 12.87 | 1
December | 27 | 11AM to 12PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 27 | 12PM to 1PM | 48.9 | 44.1 | 39 | 35.1 | 17.17 | 0.0778 | 0.24 | 12.92 | 1
December | 27 | 1PM to 2PM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 27 | 2PM to 3PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0776 | 0.26 | 12.96 | 1
December | 27 | 3PM to 4PM | 53.1 | 46.1 | 39 | 35.1 | 18.18 | 0.0771 | 0.24 | 13.03 | 0
December | 27 | 4PM to 5PM | 52 | 44.3 | 36 | 31.1 | 17.29 | 0.0773 | 0.21 | 12.99 | 0
December | 27 | 5PM to 6PM | 48 | 44 | 39.9 | 36.4 | 17.15 | 0.0779 | 0.25 | 12.9 | 1
December | 27 | 6PM to 7PM | 46 | 42.2 | 37.9 | 33.7 | 16.25 | 0.0782 | 0.23 | 12.85 | 1
December | 27 | 7PM to 8PM | 46.9 | 42.3 | 37 | 32.5 | 16.29 | 0.0781 | 0.22 | 12.86 | 1
December | 27 | 8PM to 9PM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
December | 27 | 9PM to 10PM | 46 | 41.8 | 37 | 32.5 | 16.07 | 0.0782 | 0.22 | 12.84 | 1
December | 27 | 10PM to 11PM | 44.1 | 42.1 | 39.9 | 36.4 | 16.19 | 0.0785 | 0.25 | 12.8 | 1
December | 27 | 11PM to 12AM | 44.1 | 41.2 | 37.9 | 33.7 | 15.77 | 0.0785 | 0.23 | 12.8 | 1
December | 28 | 12AM to 1AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
December | 28 | 1AM to 2AM | 44.1 | 41.7 | 39 | 35.1 | 16 | 0.0785 | 0.24 | 12.8 | 1
December | 28 | 2AM to 3AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
December | 28 | 3AM to 4AM | 42.1 | 41 | 39.9 | 36.4 | 15.71 | 0.0788 | 0.25 | 12.75 | 1
December | 28 | 4AM to 5AM | 39.9 | 38.6 | 37 | 32.5 | 14.59 | 0.0792 | 0.22 | 12.69 | 1
December | 28 | 5AM to 6AM | 39 | 38.1 | 37 | 32.5 | 14.37 | 0.0793 | 0.22 | 12.66 | 1
December | 28 | 6AM to 7AM | 42.1 | 40.1 | 37.9 | 33.7 | 15.29 | 0.0788 | 0.23 | 12.74 | 1
December | 28 | 7AM to 8AM | 42.1 | 39.8 | 37 | 32.5 | 15.11 | 0.0788 | 0.22 | 12.74 | 1
December | 28 | 8AM to 9AM | 46.9 | 43.5 | 39.9 | 36.4 | 16.89 | 0.0781 | 0.25 | 12.88 | 1
December | 28 | 9AM to 10AM | 53.1 | 45.6 | 37.9 | 33.7 | 17.95 | 0.0772 | 0.23 | 13.02 | 0
December | 28 | 10AM to 11AM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
December | 28 | 11AM to 12PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
December | 28 | 12PM to 1PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
December | 28 | 1PM to 2PM | 55.9 | 48.3 | 41 | 38 | 19.32 | 0.0767 | 0.26 | 13.11 | 0
December | 28 | 2PM to 3PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
December | 28 | 3PM to 4PM | 57 | 50.1 | 44.1 | 42.8 | 20.32 | 0.0765 | 0.29 | 13.15 | 0
December | 28 | 4PM to 5PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 28 | 5PM to 6PM | 55 | 48.3 | 42.1 | 39.6 | 19.35 | 0.0768 | 0.27 | 13.09 | 0
December | 28 | 6PM to 7PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
December | 28 | 7PM to 8PM | 52 | 45.6 | 39 | 35.1 | 17.92 | 0.0773 | 0.24 | 13 | 0
December | 28 | 8PM to 9PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
December | 28 | 9PM to 10PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0773 | 0.28 | 13.02 | 0
December | 28 | 10PM to 11PM | 53.1 | 46.5 | 39.9 | 36.4 | 18.37 | 0.0771 | 0.25 | 13.03 | 0
December | 28 | 11PM to 12AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 29 | 12AM to 1AM | 48.9 | 45 | 41 | 38 | 17.61 | 0.0778 | 0.26 | 12.93 | 1
December | 29 | 1AM to 2AM | 48 | 44.5 | 41 | 38 | 17.4 | 0.0779 | 0.26 | 12.91 | 1
December | 29 | 2AM to 3AM | 48.9 | 45.5 | 42.1 | 39.6 | 17.87 | 0.0777 | 0.27 | 12.94 | 1
December | 29 | 3AM to 4AM | 46.9 | 45.5 | 44.1 | 42.8 | 17.87 | 0.078 | 0.29 | 12.9 | 1
December | 29 | 4AM to 5AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 29 | 5AM to 6AM | 48.9 | 46.4 | 44.1 | 42.8 | 18.36 | 0.0777 | 0.29 | 12.95 | 1
December | 29 | 6AM to 7AM | 45 | 44 | 43 | 41 | 17.12 | 0.0783 | 0.28 | 12.84 | 1
December | 29 | 7AM to 8AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 29 | 8AM to 9AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 29 | 9AM to 10AM | 50 | 46 | 42.1 | 39.6 | 18.13 | 0.0776 | 0.27 | 12.96 | 1
December | 29 | 10AM to 11AM | 53.1 | 47.4 | 42.1 | 39.6 | 18.87 | 0.0771 | 0.27 | 13.04 | 0
December | 29 | 11AM to 12PM | 54 | 48.2 | 43 | 41 | 19.31 | 0.077 | 0.28 | 13.07 | 0
December | 29 | 12PM to 1PM | 55 | 46.6 | 37.9 | 33.7 | 18.43 | 0.0769 | 0.23 | 13.07 | 0
December | 29 | 1PM to 2PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
December | 29 | 2PM to 3PM | 57.9 | 48.3 | 39 | 35.1 | 19.35 | 0.0764 | 0.24 | 13.15 | 0
December | 29 | 3PM to 4PM | 59 | 49.2 | 39.9 | 36.4 | 19.81 | 0.0763 | 0.25 | 13.18 | 0
December | 29 | 4PM to 5PM | 57 | 48.3 | 39.9 | 36.4 | 19.33 | 0.0765 | 0.25 | 13.13 | 0
December | 29 | 5PM to 6PM | 53.1 | 48.7 | 45 | 44.3 | 19.59 | 0.0771 | 0.3 | 13.06 | 0
December | 29 | 6PM to 7PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
December | 29 | 7PM to 8PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 29 | 8PM to 9PM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 29 | 9PM to 10PM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 29 | 10PM to 11PM | 50 | 47.9 | 46 | 46.1 | 19.14 | 0.0775 | 0.31 | 12.98 | 1
December | 29 | 11PM to 12AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 30 | 12AM to 1AM | 48 | 45 | 42.1 | 39.6 | 17.65 | 0.0779 | 0.27 | 12.91 | 1
December | 30 | 1AM to 2AM | 46 | 43.1 | 39.9 | 36.4 | 16.67 | 0.0782 | 0.25 | 12.85 | 1
December | 30 | 2AM to 3AM | 46 | 44.5 | 43 | 41 | 17.39 | 0.0782 | 0.28 | 12.87 | 1
December | 30 | 3AM to 4AM | 46.9 | 44.5 | 42.1 | 39.6 | 17.39 | 0.078 | 0.27 | 12.89 | 1
December | 30 | 4AM to 5AM | 43 | 41.1 | 39 | 35.1 | 15.74 | 0.0787 | 0.24 | 12.77 | 1
December | 30 | 5AM to 6AM | 44.1 | 42.6 | 41 | 38 | 16.44 | 0.0785 | 0.26 | 12.81 | 1
December | 30 | 6AM to 7AM | 46.9 | 44 | 41 | 38 | 17.13 | 0.0781 | 0.26 | 12.88 | 1
December | 30 | 7AM to 8AM | 48 | 46 | 44.1 | 42.8 | 18.14 | 0.0779 | 0.29 | 12.92 | 1
December | 30 | 8AM to 9AM | 50 | 45 | 39.9 | 36.4 | 17.63 | 0.0776 | 0.25 | 12.95 | 1
December | 30 | 9AM to 10AM | 53.1 | 46.9 | 41 | 38 | 18.62 | 0.0771 | 0.26 | 13.04 | 0
December | 30 | 10AM to 11AM | 55 | 47 | 39 | 35.1 | 18.66 | 0.0768 | 0.24 | 13.08 | 0
December | 30 | 11AM to 12PM | 57 | 47.9 | 39 | 35.1 | 19.14 | 0.0766 | 0.24 | 13.13 | 0
December | 30 | 12PM to 1PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
December | 30 | 1PM to 2PM | 54 | 50.1 | 46.9 | 47.8 | 20.35 | 0.0769 | 0.32 | 13.09 | 0
December | 30 | 2PM to 3PM | 55 | 50.2 | 46 | 46.1 | 20.36 | 0.0768 | 0.31 | 13.11 | 0
December | 30 | 3PM to 4PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0767 | 0.28 | 13.12 | 0
December | 30 | 4PM to 5PM | 55.9 | 48.7 | 42.1 | 39.6 | 19.57 | 0.0767 | 0.27 | 13.11 | 0
December | 30 | 5PM to 6PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
December | 30 | 6PM to 7PM | 57 | 50.5 | 45 | 44.3 | 20.56 | 0.0765 | 0.3 | 13.16 | 0
December | 30 | 7PM to 8PM | 57 | 49.2 | 42.1 | 39.6 | 19.83 | 0.0765 | 0.27 | 13.14 | 0
December | 30 | 8PM to 9PM | 53.1 | 48.3 | 44.1 | 42.8 | 19.36 | 0.0771 | 0.29 | 13.05 | 0
December | 30 | 9PM to 10PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
December | 30 | 10PM to 11PM | 51.1 | 48.8 | 46.9 | 47.8 | 19.65 | 0.0774 | 0.32 | 13.02 | 1
December | 30 | 11PM to 12AM | 51.1 | 48.4 | 46 | 46.1 | 19.4 | 0.0774 | 0.31 | 13.01 | 1
December | 31 | 12AM to 1AM | 51.1 | 47.8 | 45 | 44.3 | 19.11 | 0.0774 | 0.3 | 13 | 1
December | 31 | 1AM to 2AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
December | 31 | 2AM to 3AM | 50 | 46.9 | 44.1 | 42.8 | 18.62 | 0.0776 | 0.29 | 12.97 | 1
December | 31 | 3AM to 4AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 31 | 4AM to 5AM | 48 | 45.4 | 43 | 41 | 17.87 | 0.0779 | 0.28 | 12.92 | 1
December | 31 | 5AM to 6AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.95 | 1
December | 31 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.9 | 1
December | 31 | 7AM to 8AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 31 | 8AM to 9AM | 50 | 48.4 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 12.99 | 1
December | 31 | 9AM to 10AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 31 | 10AM to 11AM | 51.1 | 49.9 | 48.9 | 51.5 | 20.23 | 0.0773 | 0.35 | 13.03 | 1
December | 31 | 11AM to 12PM | 52 | 50.9 | 50 | 53.6 | 20.78 | 0.0772 | 0.36 | 13.06 | 0
December | 31 | 12PM to 1PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 31 | 1PM to 2PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 31 | 2PM to 3PM | 53.1 | 51.3 | 50 | 53.6 | 21.04 | 0.077 | 0.36 | 13.08 | 0
December | 31 | 3PM to 4PM | 55 | 50.6 | 46.9 | 47.8 | 20.62 | 0.0768 | 0.32 | 13.12 | 0
December | 31 | 4PM to 5PM | 53.1 | 49.7 | 46.9 | 47.8 | 20.13 | 0.0771 | 0.32 | 13.07 | 0
December | 31 | 5PM to 6PM | 55 | 54.4 | 54 | 62.2 | 22.85 | 0.0767 | 0.42 | 13.16 | 0
December | 31 | 6PM to 7PM | 55 | 53.9 | 53.1 | 60.1 | 22.54 | 0.0767 | 0.41 | 13.15 | 0
December | 31 | 7PM to 8PM | 55.9 | 54.2 | 53.1 | 60.1 | 22.76 | 0.0765 | 0.41 | 13.18 | 0
December | 31 | 8PM to 9PM | 54 | 52.8 | 52 | 57.8 | 21.9 | 0.0769 | 0.39 | 13.12 | 0
December | 31 | 9PM to 10PM | 51.1 | 50.5 | 50 | 53.6 | 20.56 | 0.0773 | 0.36 | 13.03 | 1
December | 31 | 10PM to 11PM | 51.1 | 51.1 | 51.1 | 55.9 | 20.91 | 0.0773 | 0.38 | 13.04 | 1
December | 31 | 11PM to 12AM | 52 | 51.5 | 51.1 | 55.9 | 21.13 | 0.0772 | 0.38 | 13.06 | 0

## Sacramento CA TMY3 Weather
Country: USA | [7 empty] | OAT Flag Trigger Set Point - | 52 | °F
State: CALIFORNIA | [8 empty] | Back to HOA kW and kWh Saving tab
City: SACRAMENTO_METROPOLITAN_AP | [8 empty] | Back to Optimized kW and kWh Savings tab
Altitude: 22 ft. | [9 empty] | Number of hours less than 52.0°F in the data set - | 2819
Month | Day | Hour | Dry Bulb | Wet Bulb | Dew Point | Humidity Ratio | Enthalpy | Density | Vapor Pressure | Specific Volume | 1 if the OAT is less than 52.0°F
|  |  | °F | °F | °F | gr/lb | btu/lb | lb/cu.ft. | in. HG | cu.ft./lb
January | 1 | 12AM to 1AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 1 | 1AM to 2AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 1 | 2AM to 3AM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 1 | 3AM to 4AM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 1 | 4AM to 5AM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 1 | 5AM to 6AM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 1 | 6AM to 7AM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 1 | 7AM to 8AM | 41.9 | 41.9 | 41.9 | 39.4 | 16.13 | 0.0788 | 0.27 | 12.76 | 1
January | 1 | 8AM to 9AM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 1 | 9AM to 10AM | 43 | 43 | 43 | 41 | 16.65 | 0.0786 | 0.28 | 12.8 | 1
January | 1 | 10AM to 11AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 1 | 11AM to 12PM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 1 | 12PM to 1PM | 45.9 | 44.4 | 43 | 41 | 17.35 | 0.0782 | 0.28 | 12.87 | 1
January | 1 | 1PM to 2PM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 1 | 2PM to 3PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 1 | 3PM to 4PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 1 | 4PM to 5PM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 1 | 5PM to 6PM | 46.8 | 45.3 | 43.9 | 42.5 | 17.79 | 0.078 | 0.29 | 12.9 | 1
January | 1 | 6PM to 7PM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 1 | 7PM to 8PM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 1 | 8PM to 9PM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 1 | 9PM to 10PM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 1 | 10PM to 11PM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 1 | 11PM to 12AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 2 | 12AM to 1AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 2 | 1AM to 2AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 2 | 2AM to 3AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 2 | 3AM to 4AM | 43.5 | 42.8 | 42.1 | 39.6 | 16.56 | 0.0785 | 0.27 | 12.81 | 1
January | 2 | 4AM to 5AM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 2 | 5AM to 6AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
January | 2 | 6AM to 7AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 2 | 7AM to 8AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 2 | 8AM to 9AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 2 | 9AM to 10AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 2 | 10AM to 11AM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 2 | 11AM to 12PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 2 | 12PM to 1PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 2 | 1PM to 2PM | 50.9 | 47.8 | 45 | 44.3 | 19.07 | 0.0774 | 0.3 | 13.01 | 1
January | 2 | 2PM to 3PM | 52 | 48.3 | 45 | 44.3 | 19.34 | 0.0772 | 0.3 | 13.04 | 0
January | 2 | 3PM to 4PM | 52 | 48.7 | 45.9 | 45.9 | 19.58 | 0.0772 | 0.31 | 13.04 | 0
January | 2 | 4PM to 5PM | 52 | 48.3 | 45 | 44.3 | 19.34 | 0.0772 | 0.3 | 13.04 | 0
January | 2 | 5PM to 6PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 2 | 6PM to 7PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 2 | 7PM to 8PM | 48.9 | 47.3 | 45.9 | 45.9 | 18.83 | 0.0777 | 0.31 | 12.96 | 1
January | 2 | 8PM to 9PM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 2 | 9PM to 10PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 2 | 10PM to 11PM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 2 | 11PM to 12AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 3 | 12AM to 1AM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 3 | 1AM to 2AM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 3 | 2AM to 3AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 3 | 3AM to 4AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 3 | 4AM to 5AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 3 | 5AM to 6AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 3 | 6AM to 7AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 3 | 7AM to 8AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 3 | 8AM to 9AM | 43.9 | 42.9 | 41.9 | 39.4 | 16.61 | 0.0785 | 0.27 | 12.81 | 1
January | 3 | 9AM to 10AM | 44.4 | 43.4 | 42.4 | 40.2 | 16.87 | 0.0784 | 0.27 | 12.83 | 1
January | 3 | 10AM to 11AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 11AM to 12PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 12PM to 1PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 1PM to 2PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 2PM to 3PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 3PM to 4PM | 45.7 | 44.2 | 42.8 | 40.8 | 17.26 | 0.0782 | 0.28 | 12.86 | 1
January | 3 | 4PM to 5PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 5PM to 6PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 6PM to 7PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 7PM to 8PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 8PM to 9PM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 3 | 9PM to 10PM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 3 | 10PM to 11PM | 44.8 | 44.1 | 43.5 | 41.9 | 17.22 | 0.0783 | 0.28 | 12.85 | 1
January | 3 | 11PM to 12AM | 44.8 | 44 | 43.2 | 41.3 | 17.13 | 0.0783 | 0.28 | 12.84 | 1
January | 4 | 12AM to 1AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 4 | 1AM to 2AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 4 | 2AM to 3AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 4 | 3AM to 4AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 4 | 4AM to 5AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 4 | 5AM to 6AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 4 | 6AM to 7AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 4 | 7AM to 8AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 4 | 8AM to 9AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 4 | 9AM to 10AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 4 | 10AM to 11AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 4 | 11AM to 12PM | 45.9 | 44.4 | 43 | 41 | 17.35 | 0.0782 | 0.28 | 12.87 | 1
January | 4 | 12PM to 1PM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 4 | 1PM to 2PM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 4 | 2PM to 3PM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 4 | 3PM to 4PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 4 | 4PM to 5PM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 4 | 5PM to 6PM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 4 | 6PM to 7PM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 4 | 7PM to 8PM | 47.3 | 46.3 | 45.3 | 44.9 | 18.29 | 0.0779 | 0.3 | 12.92 | 1
January | 4 | 8PM to 9PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 4 | 9PM to 10PM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 4 | 10PM to 11PM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 4 | 11PM to 12AM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 5 | 12AM to 1AM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 5 | 1AM to 2AM | 45.5 | 44.9 | 44.4 | 43.4 | 17.62 | 0.0782 | 0.29 | 12.87 | 1
January | 5 | 2AM to 3AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 5 | 3AM to 4AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 5 | 4AM to 5AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 5 | 5AM to 6AM | 45.9 | 44.4 | 43 | 41 | 17.35 | 0.0782 | 0.28 | 12.87 | 1
January | 5 | 6AM to 7AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 5 | 7AM to 8AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 5 | 8AM to 9AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 5 | 9AM to 10AM | 46.9 | 44.9 | 43 | 41 | 17.61 | 0.078 | 0.28 | 12.9 | 1
January | 5 | 10AM to 11AM | 46.9 | 44.9 | 43 | 41 | 17.61 | 0.078 | 0.28 | 12.9 | 1
January | 5 | 11AM to 12PM | 47.8 | 45.8 | 43.9 | 42.5 | 18.05 | 0.0778 | 0.29 | 12.92 | 1
January | 5 | 12PM to 1PM | 48.9 | 46.3 | 43.9 | 42.5 | 18.31 | 0.0777 | 0.29 | 12.95 | 1
January | 5 | 1PM to 2PM | 50 | 46.8 | 43.9 | 42.5 | 18.58 | 0.0775 | 0.29 | 12.98 | 1
January | 5 | 2PM to 3PM | 50.9 | 48.2 | 45.9 | 45.9 | 19.31 | 0.0774 | 0.31 | 13.01 | 1
January | 5 | 3PM to 4PM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 5 | 4PM to 5PM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 5 | 5PM to 6PM | 45.9 | 44.4 | 43 | 41 | 17.35 | 0.0782 | 0.28 | 12.87 | 1
January | 5 | 6PM to 7PM | 43.9 | 42.9 | 41.9 | 39.4 | 16.61 | 0.0785 | 0.27 | 12.81 | 1
January | 5 | 7PM to 8PM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 5 | 8PM to 9PM | 39.9 | 39.4 | 38.8 | 34.9 | 14.96 | 0.0791 | 0.24 | 12.7 | 1
January | 5 | 9PM to 10PM | 41 | 39.6 | 37.9 | 33.7 | 15.03 | 0.079 | 0.23 | 12.72 | 1
January | 5 | 10PM to 11PM | 41 | 39.6 | 37.9 | 33.7 | 15.03 | 0.079 | 0.23 | 12.72 | 1
January | 5 | 11PM to 12AM | 41.4 | 39.5 | 37.4 | 33 | 15.01 | 0.0789 | 0.22 | 12.73 | 1
January | 6 | 12AM to 1AM | 41.9 | 39.6 | 36.9 | 32.3 | 15.03 | 0.0788 | 0.22 | 12.74 | 1
January | 6 | 1AM to 2AM | 39.9 | 38.1 | 36 | 31.1 | 14.38 | 0.0792 | 0.21 | 12.69 | 1
January | 6 | 2AM to 3AM | 38.8 | 37.1 | 34.9 | 29.8 | 13.91 | 0.0793 | 0.2 | 12.66 | 1
January | 6 | 3AM to 4AM | 38.8 | 37.1 | 34.9 | 29.8 | 13.91 | 0.0793 | 0.2 | 12.66 | 1
January | 6 | 4AM to 5AM | 38.8 | 37.1 | 34.9 | 29.8 | 13.91 | 0.0793 | 0.2 | 12.66 | 1
January | 6 | 5AM to 6AM | 39.9 | 38.1 | 36 | 31.1 | 14.38 | 0.0792 | 0.21 | 12.69 | 1
January | 6 | 6AM to 7AM | 39.9 | 37.7 | 34.9 | 29.8 | 14.18 | 0.0792 | 0.2 | 12.69 | 1
January | 6 | 7AM to 8AM | 39.9 | 37.7 | 34.9 | 29.8 | 14.18 | 0.0792 | 0.2 | 12.69 | 1
January | 6 | 8AM to 9AM | 43.9 | 39.8 | 34.9 | 29.8 | 15.13 | 0.0785 | 0.2 | 12.79 | 1
January | 6 | 9AM to 10AM | 46.9 | 42.2 | 36.9 | 32.3 | 16.25 | 0.078 | 0.22 | 12.87 | 1
January | 6 | 10AM to 11AM | 50.9 | 44.6 | 37.9 | 33.7 | 17.43 | 0.0774 | 0.23 | 12.98 | 1
January | 6 | 11AM to 12PM | 54.9 | 46.5 | 37.9 | 33.7 | 18.39 | 0.0768 | 0.23 | 13.08 | 0
January | 6 | 12PM to 1PM | 56.8 | 47.8 | 38.8 | 34.9 | 19.06 | 0.0765 | 0.24 | 13.13 | 0
January | 6 | 1PM to 2PM | 57.9 | 48.7 | 39.9 | 36.4 | 19.55 | 0.0764 | 0.25 | 13.16 | 0
January | 6 | 2PM to 3PM | 59 | 48.4 | 37.9 | 33.7 | 19.39 | 0.0762 | 0.23 | 13.18 | 0
January | 6 | 3PM to 4PM | 59 | 49.2 | 39.9 | 36.4 | 19.82 | 0.0762 | 0.25 | 13.19 | 0
January | 6 | 4PM to 5PM | 53.6 | 46.8 | 40.1 | 36.7 | 18.55 | 0.077 | 0.25 | 13.05 | 0
January | 6 | 5PM to 6PM | 47.8 | 43.9 | 39.9 | 36.4 | 17.11 | 0.0779 | 0.25 | 12.91 | 1
January | 6 | 6PM to 7PM | 41 | 39.6 | 37.9 | 33.7 | 15.03 | 0.079 | 0.23 | 12.72 | 1
January | 6 | 7PM to 8PM | 41.9 | 40.1 | 37.9 | 33.7 | 15.25 | 0.0788 | 0.23 | 12.75 | 1
January | 6 | 8PM to 9PM | 41.9 | 40.1 | 37.9 | 33.7 | 15.25 | 0.0788 | 0.23 | 12.75 | 1
January | 6 | 9PM to 10PM | 37.9 | 37.1 | 36 | 31.1 | 13.9 | 0.0795 | 0.21 | 12.64 | 1
January | 6 | 10PM to 11PM | 38.3 | 37.4 | 36.3 | 31.6 | 14.06 | 0.0794 | 0.21 | 12.65 | 1
January | 6 | 11PM to 12AM | 38.8 | 37.9 | 36.9 | 32.3 | 14.29 | 0.0793 | 0.22 | 12.67 | 1
January | 7 | 12AM to 1AM | 36 | 35.5 | 34.9 | 29.8 | 13.22 | 0.0798 | 0.2 | 12.59 | 1
January | 7 | 1AM to 2AM | 33.4 | 33 | 32.4 | 26.9 | 12.17 | 0.0802 | 0.18 | 12.51 | 1
January | 7 | 2AM to 3AM | 30.9 | 30.4 | 29.8 | 24 | 11.11 | 0.0807 | 0.16 | 12.44 | 1
January | 7 | 3AM to 4AM | 30.9 | 30.9 | 30.9 | 25.3 | 11.3 | 0.0806 | 0.17 | 12.44 | 1
January | 7 | 4AM to 5AM | 32 | 31.5 | 30.9 | 25.3 | 11.56 | 0.0805 | 0.17 | 12.47 | 1
January | 7 | 5AM to 6AM | 30.9 | 30.9 | 30.9 | 25.3 | 11.3 | 0.0806 | 0.17 | 12.44 | 1
January | 7 | 6AM to 7AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
January | 7 | 7AM to 8AM | 43 | 38.6 | 32.9 | 27.5 | 14.56 | 0.0787 | 0.19 | 12.76 | 1
January | 7 | 8AM to 9AM | 34.9 | 34.5 | 34 | 28.8 | 12.79 | 0.08 | 0.2 | 12.56 | 1
January | 7 | 9AM to 10AM | 36.9 | 36.5 | 36 | 31.1 | 13.64 | 0.0796 | 0.21 | 12.61 | 1
January | 7 | 10AM to 11AM | 41 | 40 | 38.8 | 34.9 | 15.22 | 0.079 | 0.24 | 12.73 | 1
January | 7 | 11AM to 12PM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0786 | 0.25 | 12.78 | 1
January | 7 | 12PM to 1PM | 45 | 43 | 41 | 38 | 16.66 | 0.0783 | 0.26 | 12.84 | 1
January | 7 | 1PM to 2PM | 47.8 | 45.4 | 43 | 41 | 17.83 | 0.0779 | 0.28 | 12.92 | 1
January | 7 | 2PM to 3PM | 47.8 | 44.4 | 41 | 38 | 17.36 | 0.0779 | 0.26 | 12.91 | 1
January | 7 | 3PM to 4PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
January | 7 | 4PM to 5PM | 47.8 | 43.9 | 39.9 | 36.4 | 17.11 | 0.0779 | 0.25 | 12.91 | 1
January | 7 | 5PM to 6PM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 7 | 6PM to 7PM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0786 | 0.25 | 12.78 | 1
January | 7 | 7PM to 8PM | 39.9 | 39.4 | 38.8 | 34.9 | 14.96 | 0.0791 | 0.24 | 12.7 | 1
January | 7 | 8PM to 9PM | 38.8 | 38.4 | 37.9 | 33.7 | 14.51 | 0.0793 | 0.23 | 12.67 | 1
January | 7 | 9PM to 10PM | 41 | 38.7 | 36 | 31.1 | 14.64 | 0.079 | 0.21 | 12.72 | 1
January | 7 | 10PM to 11PM | 41 | 40 | 38.8 | 34.9 | 15.22 | 0.079 | 0.24 | 12.73 | 1
January | 7 | 11PM to 12AM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0786 | 0.25 | 12.78 | 1
January | 8 | 12AM to 1AM | 41.9 | 41 | 39.9 | 36.4 | 15.67 | 0.0788 | 0.25 | 12.76 | 1
January | 8 | 1AM to 2AM | 39.9 | 39.4 | 38.8 | 34.9 | 14.96 | 0.0791 | 0.24 | 12.7 | 1
January | 8 | 2AM to 3AM | 39.9 | 39.4 | 38.8 | 34.9 | 14.96 | 0.0791 | 0.24 | 12.7 | 1
January | 8 | 3AM to 4AM | 39.9 | 39.2 | 38.5 | 34.4 | 14.88 | 0.0791 | 0.23 | 12.7 | 1
January | 8 | 4AM to 5AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0791 | 0.23 | 12.7 | 1
January | 8 | 5AM to 6AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0791 | 0.23 | 12.7 | 1
January | 8 | 6AM to 7AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0791 | 0.23 | 12.7 | 1
January | 8 | 7AM to 8AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0791 | 0.23 | 12.7 | 1
January | 8 | 8AM to 9AM | 41.9 | 41 | 39.9 | 36.4 | 15.67 | 0.0788 | 0.25 | 12.76 | 1
January | 8 | 9AM to 10AM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 8 | 10AM to 11AM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 8 | 11AM to 12PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 8 | 12PM to 1PM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 8 | 1PM to 2PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 8 | 2PM to 3PM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 8 | 3PM to 4PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 8 | 4PM to 5PM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 8 | 5PM to 6PM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 8 | 6PM to 7PM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 8 | 7PM to 8PM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 8 | 8PM to 9PM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 8 | 9PM to 10PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 8 | 10PM to 11PM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 8 | 11PM to 12AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 9 | 12AM to 1AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 9 | 1AM to 2AM | 45.9 | 45.9 | 45.9 | 45.9 | 18.09 | 0.0781 | 0.31 | 12.88 | 1
January | 9 | 2AM to 3AM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 9 | 3AM to 4AM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 9 | 4AM to 5AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 9 | 5AM to 6AM | 45.9 | 44.4 | 43 | 41 | 17.35 | 0.0782 | 0.28 | 12.87 | 1
January | 9 | 6AM to 7AM | 43.9 | 42.9 | 41.9 | 39.4 | 16.61 | 0.0785 | 0.27 | 12.81 | 1
January | 9 | 7AM to 8AM | 41.9 | 41 | 39.9 | 36.4 | 15.67 | 0.0788 | 0.25 | 12.76 | 1
January | 9 | 8AM to 9AM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 9 | 9AM to 10AM | 46.9 | 44.4 | 41.9 | 39.4 | 17.35 | 0.078 | 0.27 | 12.89 | 1
January | 9 | 10AM to 11AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 9 | 11AM to 12PM | 50 | 46.8 | 43.9 | 42.5 | 18.58 | 0.0775 | 0.29 | 12.98 | 1
January | 9 | 12PM to 1PM | 54 | 48.6 | 43.9 | 42.5 | 19.54 | 0.0769 | 0.29 | 13.08 | 0
January | 9 | 1PM to 2PM | 55.9 | 49.5 | 43.9 | 42.5 | 20.02 | 0.0766 | 0.29 | 13.13 | 0
January | 9 | 2PM to 3PM | 56.8 | 50.4 | 45 | 44.3 | 20.52 | 0.0765 | 0.3 | 13.16 | 0
January | 9 | 3PM to 4PM | 56.8 | 49 | 41.9 | 39.4 | 19.75 | 0.0765 | 0.27 | 13.14 | 0
January | 9 | 4PM to 5PM | 54.7 | 48.1 | 42.1 | 39.6 | 19.27 | 0.0768 | 0.27 | 13.09 | 0
January | 9 | 5PM to 6PM | 52 | 46.8 | 41.9 | 39.4 | 18.57 | 0.0772 | 0.27 | 13.02 | 0
January | 9 | 6PM to 7PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
January | 9 | 7PM to 8PM | 46.9 | 44 | 41 | 38 | 17.14 | 0.078 | 0.26 | 12.89 | 1
January | 9 | 8PM to 9PM | 46.9 | 44 | 41 | 38 | 17.14 | 0.078 | 0.26 | 12.89 | 1
January | 9 | 9PM to 10PM | 45 | 43 | 41 | 38 | 16.66 | 0.0783 | 0.26 | 12.84 | 1
January | 9 | 10PM to 11PM | 43.9 | 42 | 39.9 | 36.4 | 16.15 | 0.0785 | 0.25 | 12.81 | 1
January | 9 | 11PM to 12AM | 43.9 | 41.5 | 38.8 | 34.9 | 15.92 | 0.0785 | 0.24 | 12.8 | 1
January | 10 | 12AM to 1AM | 45 | 42 | 38.8 | 34.9 | 16.18 | 0.0783 | 0.24 | 12.83 | 1
January | 10 | 1AM to 2AM | 41.9 | 40.1 | 37.9 | 33.7 | 15.25 | 0.0788 | 0.23 | 12.75 | 1
January | 10 | 2AM to 3AM | 37.9 | 37.1 | 36 | 31.1 | 13.9 | 0.0795 | 0.21 | 12.64 | 1
January | 10 | 3AM to 4AM | 36 | 35.5 | 34.9 | 29.8 | 13.22 | 0.0798 | 0.2 | 12.59 | 1
January | 10 | 4AM to 5AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 10 | 5AM to 6AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 10 | 6AM to 7AM | 38.8 | 38.4 | 37.9 | 33.7 | 14.51 | 0.0793 | 0.23 | 12.67 | 1
January | 10 | 7AM to 8AM | 38.8 | 38.4 | 37.9 | 33.7 | 14.51 | 0.0793 | 0.23 | 12.67 | 1
January | 10 | 8AM to 9AM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0791 | 0.23 | 12.7 | 1
January | 10 | 9AM to 10AM | 43 | 41 | 38.8 | 34.9 | 15.7 | 0.0786 | 0.24 | 12.78 | 1
January | 10 | 10AM to 11AM | 46.9 | 44 | 41 | 38 | 17.14 | 0.078 | 0.26 | 12.89 | 1
January | 10 | 11AM to 12PM | 48.9 | 45.6 | 42.4 | 40.2 | 17.96 | 0.0777 | 0.27 | 12.95 | 1
January | 10 | 12PM to 1PM | 50.9 | 47.2 | 43.9 | 42.5 | 18.79 | 0.0774 | 0.29 | 13 | 1
January | 10 | 1PM to 2PM | 54 | 49.1 | 45 | 44.3 | 19.82 | 0.0769 | 0.3 | 13.09 | 0
January | 10 | 2PM to 3PM | 54 | 48.6 | 43.9 | 42.5 | 19.54 | 0.0769 | 0.29 | 13.08 | 0
January | 10 | 3PM to 4PM | 54.9 | 49 | 43.9 | 42.5 | 19.75 | 0.0768 | 0.29 | 13.1 | 0
January | 10 | 4PM to 5PM | 54 | 48.6 | 43.9 | 42.5 | 19.54 | 0.0769 | 0.29 | 13.08 | 0
January | 10 | 5PM to 6PM | 50.9 | 47.2 | 43.9 | 42.5 | 18.79 | 0.0774 | 0.29 | 13 | 1
January | 10 | 6PM to 7PM | 48.9 | 45.9 | 43 | 41 | 18.09 | 0.0777 | 0.28 | 12.95 | 1
January | 10 | 7PM to 8PM | 47.8 | 45.4 | 43 | 41 | 17.83 | 0.0779 | 0.28 | 12.92 | 1
January | 10 | 8PM to 9PM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 10 | 9PM to 10PM | 41.9 | 41 | 39.9 | 36.4 | 15.67 | 0.0788 | 0.25 | 12.76 | 1
January | 10 | 10PM to 11PM | 39.9 | 39 | 37.9 | 33.7 | 14.77 | 0.0791 | 0.23 | 12.7 | 1
January | 10 | 11PM to 12AM | 38.8 | 38.4 | 37.9 | 33.7 | 14.51 | 0.0793 | 0.23 | 12.67 | 1
January | 11 | 12AM to 1AM | 36.9 | 36.5 | 36 | 31.1 | 13.64 | 0.0796 | 0.21 | 12.61 | 1
January | 11 | 1AM to 2AM | 36.9 | 36.5 | 36 | 31.1 | 13.64 | 0.0796 | 0.21 | 12.61 | 1
January | 11 | 2AM to 3AM | 35.8 | 35.6 | 35.4 | 30.5 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
January | 11 | 3AM to 4AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 11 | 4AM to 5AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 11 | 5AM to 6AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 11 | 6AM to 7AM | 34 | 33.5 | 32.9 | 27.5 | 12.39 | 0.0801 | 0.19 | 12.53 | 1
January | 11 | 7AM to 8AM | 36.9 | 36.9 | 36.9 | 32.3 | 13.81 | 0.0796 | 0.22 | 12.62 | 1
January | 11 | 8AM to 9AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 11 | 9AM to 10AM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 11 | 10AM to 11AM | 46.9 | 44.9 | 43 | 41 | 17.61 | 0.078 | 0.28 | 12.9 | 1
January | 11 | 11AM to 12PM | 50.9 | 47.8 | 45 | 44.3 | 19.07 | 0.0774 | 0.3 | 13.01 | 1
January | 11 | 12PM to 1PM | 54.9 | 49.6 | 45 | 44.3 | 20.03 | 0.0768 | 0.3 | 13.11 | 0
January | 11 | 1PM to 2PM | 57.9 | 51.3 | 45.9 | 45.9 | 21.02 | 0.0763 | 0.31 | 13.19 | 0
January | 11 | 2PM to 3PM | 59 | 51.4 | 45 | 44.3 | 21.04 | 0.0762 | 0.3 | 13.21 | 0
January | 11 | 3PM to 4PM | 59 | 50.9 | 43.9 | 42.5 | 20.76 | 0.0762 | 0.29 | 13.21 | 0
January | 11 | 4PM to 5PM | 55.9 | 49.5 | 43.9 | 42.5 | 20.02 | 0.0766 | 0.29 | 13.13 | 0
January | 11 | 5PM to 6PM | 52.9 | 48.1 | 43.9 | 42.5 | 19.27 | 0.0771 | 0.29 | 13.05 | 0
January | 11 | 6PM to 7PM | 52.9 | 47.7 | 43 | 41 | 19.05 | 0.0771 | 0.28 | 13.05 | 0
January | 11 | 7PM to 8PM | 50.9 | 46.3 | 41.9 | 39.4 | 18.31 | 0.0774 | 0.27 | 12.99 | 1
January | 11 | 8PM to 9PM | 50.9 | 45.9 | 41 | 38 | 18.1 | 0.0774 | 0.26 | 12.99 | 1
January | 11 | 9PM to 10PM | 47.8 | 43.9 | 39.9 | 36.4 | 17.11 | 0.0779 | 0.25 | 12.91 | 1
January | 11 | 10PM to 11PM | 50 | 45 | 39.9 | 36.4 | 17.64 | 0.0776 | 0.25 | 12.96 | 1
January | 11 | 11PM to 12AM | 43.9 | 41.5 | 38.8 | 34.9 | 15.92 | 0.0785 | 0.24 | 12.8 | 1
January | 12 | 12AM to 1AM | 40.8 | 39.4 | 37.8 | 33.4 | 14.95 | 0.079 | 0.23 | 12.72 | 1
January | 12 | 1AM to 2AM | 37.9 | 37.5 | 36.9 | 32.3 | 14.07 | 0.0795 | 0.22 | 12.64 | 1
January | 12 | 2AM to 3AM | 36.9 | 36.5 | 36 | 31.1 | 13.64 | 0.0796 | 0.21 | 12.61 | 1
January | 12 | 3AM to 4AM | 36.5 | 36.3 | 36 | 31.1 | 13.55 | 0.0797 | 0.21 | 12.6 | 1
January | 12 | 4AM to 5AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 12 | 5AM to 6AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 12 | 6AM to 7AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 12 | 7AM to 8AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
January | 12 | 8AM to 9AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 12 | 9AM to 10AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 12 | 10AM to 11AM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 12 | 11AM to 12PM | 48.9 | 46.3 | 43.9 | 42.5 | 18.31 | 0.0777 | 0.29 | 12.95 | 1
January | 12 | 12PM to 1PM | 52 | 47.3 | 43 | 41 | 18.83 | 0.0772 | 0.28 | 13.03 | 0
January | 12 | 1PM to 2PM | 54 | 48.2 | 43 | 41 | 19.31 | 0.0769 | 0.28 | 13.08 | 0
January | 12 | 2PM to 3PM | 55.9 | 49.5 | 43.9 | 42.5 | 20.02 | 0.0766 | 0.29 | 13.13 | 0
January | 12 | 3PM to 4PM | 56.8 | 50.9 | 45.9 | 45.9 | 20.76 | 0.0765 | 0.31 | 13.16 | 0
January | 12 | 4PM to 5PM | 54.9 | 49.6 | 45 | 44.3 | 20.03 | 0.0768 | 0.3 | 13.11 | 0
January | 12 | 5PM to 6PM | 52.7 | 48.3 | 44.4 | 43.4 | 19.37 | 0.0771 | 0.29 | 13.05 | 0
January | 12 | 6PM to 7PM | 50.9 | 47.2 | 43.9 | 42.5 | 18.79 | 0.0774 | 0.29 | 13 | 1
January | 12 | 7PM to 8PM | 47.3 | 45 | 42.8 | 40.8 | 17.65 | 0.0779 | 0.28 | 12.91 | 1
January | 12 | 8PM to 9PM | 43.9 | 42.9 | 41.9 | 39.4 | 16.61 | 0.0785 | 0.27 | 12.81 | 1
January | 12 | 9PM to 10PM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
January | 12 | 10PM to 11PM | 41.9 | 41.9 | 41.9 | 39.4 | 16.13 | 0.0788 | 0.27 | 12.76 | 1
January | 12 | 11PM to 12AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 13 | 12AM to 1AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 13 | 1AM to 2AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 13 | 2AM to 3AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 13 | 3AM to 4AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 13 | 4AM to 5AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 13 | 5AM to 6AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 13 | 6AM to 7AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 13 | 7AM to 8AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 13 | 8AM to 9AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 13 | 9AM to 10AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 13 | 10AM to 11AM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 13 | 11AM to 12PM | 45.9 | 44.6 | 43.3 | 41.6 | 17.43 | 0.0782 | 0.28 | 12.87 | 1
January | 13 | 12PM to 1PM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 13 | 1PM to 2PM | 56.8 | 51.4 | 46.9 | 47.8 | 21.06 | 0.0765 | 0.32 | 13.17 | 0
January | 13 | 2PM to 3PM | 57.9 | 50.4 | 43.9 | 42.5 | 20.5 | 0.0763 | 0.29 | 13.18 | 0
January | 13 | 3PM to 4PM | 59.9 | 50.9 | 43 | 41 | 20.75 | 0.076 | 0.28 | 13.23 | 0
January | 13 | 4PM to 5PM | 55.9 | 49.5 | 43.9 | 42.5 | 20.02 | 0.0766 | 0.29 | 13.13 | 0
January | 13 | 5PM to 6PM | 52.7 | 47.9 | 43.5 | 41.9 | 19.14 | 0.0771 | 0.28 | 13.05 | 0
January | 13 | 6PM to 7PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0775 | 0.28 | 12.98 | 1
January | 13 | 7PM to 8PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 13 | 8PM to 9PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 13 | 9PM to 10PM | 43.2 | 42.4 | 41.5 | 38.8 | 16.35 | 0.0786 | 0.26 | 12.79 | 1
January | 13 | 10PM to 11PM | 41.5 | 40.8 | 40.1 | 36.7 | 15.63 | 0.0789 | 0.25 | 12.75 | 1
January | 13 | 11PM to 12AM | 39.9 | 39.4 | 38.8 | 34.9 | 14.96 | 0.0791 | 0.24 | 12.7 | 1
January | 14 | 12AM to 1AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 14 | 1AM to 2AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 14 | 2AM to 3AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 14 | 3AM to 4AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 14 | 4AM to 5AM | 36 | 35.5 | 34.9 | 29.8 | 13.22 | 0.0798 | 0.2 | 12.59 | 1
January | 14 | 5AM to 6AM | 34.2 | 34 | 33.8 | 28.6 | 12.59 | 0.0801 | 0.19 | 12.54 | 1
January | 14 | 6AM to 7AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 14 | 7AM to 8AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 14 | 8AM to 9AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 14 | 9AM to 10AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 14 | 10AM to 11AM | 40.6 | 40.5 | 40.3 | 36.9 | 15.45 | 0.079 | 0.25 | 12.73 | 1
January | 14 | 11AM to 12PM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 14 | 12PM to 1PM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 14 | 1PM to 2PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 14 | 2PM to 3PM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 14 | 3PM to 4PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 14 | 4PM to 5PM | 48.7 | 46.6 | 44.6 | 43.7 | 18.45 | 0.0777 | 0.3 | 12.95 | 1
January | 14 | 5PM to 6PM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 14 | 6PM to 7PM | 45.9 | 44.6 | 43.3 | 41.6 | 17.43 | 0.0782 | 0.28 | 12.87 | 1
January | 14 | 7PM to 8PM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 14 | 8PM to 9PM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 14 | 9PM to 10PM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 14 | 10PM to 11PM | 41.9 | 41.9 | 41.9 | 39.4 | 16.13 | 0.0788 | 0.27 | 12.76 | 1
January | 14 | 11PM to 12AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 15 | 12AM to 1AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
January | 15 | 1AM to 2AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.0789 | 0.25 | 12.73 | 1
January | 15 | 2AM to 3AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 15 | 3AM to 4AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 15 | 4AM to 5AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 15 | 5AM to 6AM | 36.9 | 36.9 | 36.9 | 32.3 | 13.81 | 0.0796 | 0.22 | 12.62 | 1
January | 15 | 6AM to 7AM | 36.9 | 36.9 | 36.9 | 32.3 | 13.81 | 0.0796 | 0.22 | 12.62 | 1
January | 15 | 7AM to 8AM | 36.9 | 36.9 | 36.9 | 32.3 | 13.81 | 0.0796 | 0.22 | 12.62 | 1
January | 15 | 8AM to 9AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 15 | 9AM to 10AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 15 | 10AM to 11AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 15 | 11AM to 12PM | 43 | 43 | 43 | 41 | 16.65 | 0.0786 | 0.28 | 12.8 | 1
January | 15 | 12PM to 1PM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 15 | 1PM to 2PM | 53.1 | 49.6 | 46.8 | 47.5 | 20.09 | 0.077 | 0.32 | 13.07 | 0
January | 15 | 2PM to 3PM | 59 | 52.7 | 47.8 | 49.5 | 21.84 | 0.0761 | 0.33 | 13.23 | 0
January | 15 | 3PM to 4PM | 59.9 | 53.1 | 47.8 | 49.5 | 22.06 | 0.076 | 0.33 | 13.25 | 0
January | 15 | 4PM to 5PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.2 | 0
January | 15 | 5PM to 6PM | 52 | 48.7 | 45.9 | 45.9 | 19.58 | 0.0772 | 0.31 | 13.04 | 0
January | 15 | 6PM to 7PM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 15 | 7PM to 8PM | 48.9 | 47.3 | 45.9 | 45.9 | 18.83 | 0.0777 | 0.31 | 12.96 | 1
January | 15 | 8PM to 9PM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 15 | 9PM to 10PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 15 | 10PM to 11PM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.0789 | 0.25 | 12.73 | 1
January | 15 | 11PM to 12AM | 39.4 | 39.2 | 39 | 35.2 | 14.87 | 0.0792 | 0.24 | 12.69 | 1
January | 16 | 12AM to 1AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 16 | 1AM to 2AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 16 | 2AM to 3AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 16 | 3AM to 4AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 16 | 4AM to 5AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 16 | 5AM to 6AM | 38.8 | 38.4 | 37.9 | 33.7 | 14.51 | 0.0793 | 0.23 | 12.67 | 1
January | 16 | 6AM to 7AM | 36.9 | 36.9 | 36.9 | 32.3 | 13.81 | 0.0796 | 0.22 | 12.62 | 1
January | 16 | 7AM to 8AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 16 | 8AM to 9AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 16 | 9AM to 10AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.0789 | 0.25 | 12.73 | 1
January | 16 | 10AM to 11AM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 16 | 11AM to 12PM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 16 | 12PM to 1PM | 50.9 | 46.3 | 41.9 | 39.4 | 18.31 | 0.0774 | 0.27 | 12.99 | 1
January | 16 | 1PM to 2PM | 56.8 | 49.5 | 43 | 41 | 20.01 | 0.0765 | 0.28 | 13.15 | 0
January | 16 | 2PM to 3PM | 59.9 | 51.3 | 43.9 | 42.5 | 20.98 | 0.076 | 0.29 | 13.23 | 0
January | 16 | 3PM to 4PM | 59.9 | 52.2 | 45.9 | 45.9 | 21.5 | 0.076 | 0.31 | 13.24 | 0
January | 16 | 4PM to 5PM | 57.6 | 51.3 | 46 | 46.2 | 20.98 | 0.0764 | 0.31 | 13.18 | 0
January | 16 | 5PM to 6PM | 54.9 | 50 | 45.9 | 45.9 | 20.28 | 0.0768 | 0.31 | 13.11 | 0
January | 16 | 6PM to 7PM | 50 | 46.8 | 43.9 | 42.5 | 18.58 | 0.0775 | 0.29 | 12.98 | 1
January | 16 | 7PM to 8PM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 16 | 8PM to 9PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 16 | 9PM to 10PM | 43 | 43 | 43 | 41 | 16.65 | 0.0786 | 0.28 | 12.8 | 1
January | 16 | 10PM to 11PM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 16 | 11PM to 12AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 17 | 12AM to 1AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 17 | 1AM to 2AM | 36.9 | 36.9 | 36.9 | 32.3 | 13.81 | 0.0796 | 0.22 | 12.62 | 1
January | 17 | 2AM to 3AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 17 | 3AM to 4AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 17 | 4AM to 5AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 17 | 5AM to 6AM | 36.1 | 36.1 | 36.1 | 31.4 | 13.5 | 0.0798 | 0.21 | 12.59 | 1
January | 17 | 6AM to 7AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 17 | 7AM to 8AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 17 | 8AM to 9AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 17 | 9AM to 10AM | 43 | 43 | 43 | 41 | 16.65 | 0.0786 | 0.28 | 12.8 | 1
January | 17 | 10AM to 11AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 17 | 11AM to 12PM | 54 | 50.1 | 46.9 | 47.8 | 20.36 | 0.0769 | 0.32 | 13.1 | 0
January | 17 | 12PM to 1PM | 57.9 | 52.3 | 47.8 | 49.5 | 21.58 | 0.0763 | 0.33 | 13.2 | 0
January | 17 | 1PM to 2PM | 61 | 53.1 | 46.9 | 47.8 | 22.06 | 0.0758 | 0.32 | 13.28 | 0
January | 17 | 2PM to 3PM | 64.9 | 53.9 | 45 | 44.3 | 22.48 | 0.0753 | 0.3 | 13.37 | 0
January | 17 | 3PM to 4PM | 63.9 | 53.8 | 45.9 | 45.9 | 22.46 | 0.0754 | 0.31 | 13.34 | 0
January | 17 | 4PM to 5PM | 61.9 | 53 | 45.9 | 45.9 | 21.98 | 0.0757 | 0.31 | 13.29 | 0
January | 17 | 5PM to 6PM | 57.9 | 51.8 | 46.9 | 47.8 | 21.32 | 0.0763 | 0.32 | 13.2 | 0
January | 17 | 6PM to 7PM | 54.9 | 50 | 45.9 | 45.9 | 20.28 | 0.0768 | 0.31 | 13.11 | 0
January | 17 | 7PM to 8PM | 50.9 | 47.8 | 45 | 44.3 | 19.07 | 0.0774 | 0.3 | 13.01 | 1
January | 17 | 8PM to 9PM | 47.8 | 45.9 | 44.1 | 42.8 | 18.1 | 0.0778 | 0.29 | 12.93 | 1
January | 17 | 9PM to 10PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 17 | 10PM to 11PM | 41 | 40 | 38.8 | 34.9 | 15.22 | 0.079 | 0.24 | 12.73 | 1
January | 17 | 11PM to 12AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.0789 | 0.25 | 12.73 | 1
January | 18 | 12AM to 1AM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 18 | 1AM to 2AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 18 | 2AM to 3AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
January | 18 | 3AM to 4AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 18 | 4AM to 5AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 18 | 5AM to 6AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 18 | 6AM to 7AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 18 | 7AM to 8AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 18 | 8AM to 9AM | 36.9 | 36.9 | 36.9 | 32.3 | 13.81 | 0.0796 | 0.22 | 12.62 | 1
January | 18 | 9AM to 10AM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 18 | 10AM to 11AM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 18 | 11AM to 12PM | 54 | 50.6 | 47.8 | 49.5 | 20.62 | 0.0769 | 0.33 | 13.1 | 0
January | 18 | 12PM to 1PM | 57.9 | 52.3 | 47.8 | 49.5 | 21.58 | 0.0763 | 0.33 | 13.2 | 0
January | 18 | 1PM to 2PM | 60.6 | 53.2 | 47.5 | 48.8 | 22.13 | 0.0759 | 0.33 | 13.27 | 0
January | 18 | 2PM to 3PM | 63 | 54.1 | 47.3 | 48.4 | 22.65 | 0.0756 | 0.33 | 13.33 | 0
January | 18 | 3PM to 4PM | 63 | 53.9 | 46.9 | 47.8 | 22.54 | 0.0756 | 0.32 | 13.33 | 0
January | 18 | 4PM to 5PM | 61.9 | 53.5 | 46.9 | 47.8 | 22.28 | 0.0757 | 0.32 | 13.3 | 0
January | 18 | 5PM to 6PM | 56.8 | 51.4 | 46.9 | 47.8 | 21.06 | 0.0765 | 0.32 | 13.17 | 0
January | 18 | 6PM to 7PM | 52.9 | 49.6 | 46.9 | 47.8 | 20.09 | 0.077 | 0.32 | 13.07 | 0
January | 18 | 7PM to 8PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 18 | 8PM to 9PM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 18 | 9PM to 10PM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 18 | 10PM to 11PM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 18 | 11PM to 12AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 19 | 12AM to 1AM | 36.9 | 36.5 | 36 | 31.1 | 13.64 | 0.0796 | 0.21 | 12.61 | 1
January | 19 | 1AM to 2AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 19 | 2AM to 3AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 19 | 3AM to 4AM | 34.9 | 34.5 | 34 | 28.8 | 12.79 | 0.08 | 0.2 | 12.56 | 1
January | 19 | 4AM to 5AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 19 | 5AM to 6AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 19 | 6AM to 7AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 19 | 7AM to 8AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 19 | 8AM to 9AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 19 | 9AM to 10AM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 19 | 10AM to 11AM | 50.9 | 46.3 | 41.9 | 39.4 | 18.31 | 0.0774 | 0.27 | 12.99 | 1
January | 19 | 11AM to 12PM | 55.9 | 50.5 | 45.9 | 45.9 | 20.54 | 0.0766 | 0.31 | 13.14 | 0
January | 19 | 12PM to 1PM | 57.9 | 51.3 | 45.9 | 45.9 | 21.02 | 0.0763 | 0.31 | 13.19 | 0
January | 19 | 1PM to 2PM | 61.9 | 53.5 | 46.9 | 47.8 | 22.28 | 0.0757 | 0.32 | 13.3 | 0
January | 19 | 2PM to 3PM | 65.8 | 53.8 | 43.9 | 42.5 | 22.42 | 0.0752 | 0.29 | 13.38 | 0
January | 19 | 3PM to 4PM | 63.9 | 52.9 | 43.9 | 42.5 | 21.94 | 0.0755 | 0.29 | 13.33 | 0
January | 19 | 4PM to 5PM | 63.9 | 52.9 | 43.9 | 42.5 | 21.94 | 0.0755 | 0.29 | 13.33 | 0
January | 19 | 5PM to 6PM | 59.9 | 51.3 | 43.9 | 42.5 | 20.98 | 0.076 | 0.29 | 13.23 | 0
January | 19 | 6PM to 7PM | 55.9 | 49.1 | 43 | 41 | 19.79 | 0.0766 | 0.28 | 13.13 | 0
January | 19 | 7PM to 8PM | 50 | 46.4 | 43 | 41 | 18.35 | 0.0775 | 0.28 | 12.98 | 1
January | 19 | 8PM to 9PM | 48.9 | 45.9 | 43 | 41 | 18.09 | 0.0777 | 0.28 | 12.95 | 1
January | 19 | 9PM to 10PM | 47.5 | 45.4 | 43.3 | 41.6 | 17.83 | 0.0779 | 0.28 | 12.91 | 1
January | 19 | 10PM to 11PM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 19 | 11PM to 12AM | 43 | 42 | 41 | 38 | 16.18 | 0.0786 | 0.26 | 12.79 | 1
January | 20 | 12AM to 1AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.0789 | 0.25 | 12.73 | 1
January | 20 | 1AM to 2AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 20 | 2AM to 3AM | 37.9 | 37.5 | 36.9 | 32.3 | 14.07 | 0.0795 | 0.22 | 12.64 | 1
January | 20 | 3AM to 4AM | 36 | 36 | 36 | 31.1 | 13.42 | 0.0798 | 0.21 | 12.59 | 1
January | 20 | 4AM to 5AM | 34.3 | 34.2 | 34 | 28.8 | 12.66 | 0.0801 | 0.2 | 12.54 | 1
January | 20 | 5AM to 6AM | 32.9 | 32.5 | 32 | 26.6 | 11.98 | 0.0803 | 0.18 | 12.5 | 1
January | 20 | 6AM to 7AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 20 | 7AM to 8AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
January | 20 | 8AM to 9AM | 36.9 | 36.5 | 36 | 31.1 | 13.64 | 0.0796 | 0.21 | 12.61 | 1
January | 20 | 9AM to 10AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 20 | 10AM to 11AM | 52 | 48.3 | 45 | 44.3 | 19.34 | 0.0772 | 0.3 | 13.04 | 0
January | 20 | 11AM to 12PM | 57.9 | 50.9 | 45 | 44.3 | 20.78 | 0.0763 | 0.3 | 13.19 | 0
January | 20 | 12PM to 1PM | 59.9 | 51.8 | 45 | 44.3 | 21.26 | 0.076 | 0.3 | 13.24 | 0
January | 20 | 1PM to 2PM | 63 | 53.4 | 45.9 | 45.9 | 22.24 | 0.0756 | 0.31 | 13.32 | 0
January | 20 | 2PM to 3PM | 62.8 | 53.5 | 46 | 46.2 | 22.25 | 0.0756 | 0.31 | 13.32 | 0
January | 20 | 3PM to 4PM | 61.9 | 53 | 45.9 | 45.9 | 21.98 | 0.0757 | 0.31 | 13.29 | 0
January | 20 | 4PM to 5PM | 57.9 | 52.3 | 47.8 | 49.5 | 21.58 | 0.0763 | 0.33 | 13.2 | 0
January | 20 | 5PM to 6PM | 56.8 | 51.4 | 46.9 | 47.8 | 21.06 | 0.0765 | 0.32 | 13.17 | 0
January | 20 | 6PM to 7PM | 52.9 | 49.1 | 45.9 | 45.9 | 19.8 | 0.0771 | 0.31 | 13.06 | 0
January | 20 | 7PM to 8PM | 54 | 50.1 | 46.9 | 47.8 | 20.36 | 0.0769 | 0.32 | 13.1 | 0
January | 20 | 8PM to 9PM | 50.9 | 48.2 | 45.9 | 45.9 | 19.31 | 0.0774 | 0.31 | 13.01 | 1
January | 20 | 9PM to 10PM | 47.5 | 45.9 | 44.4 | 43.4 | 18.1 | 0.0779 | 0.29 | 12.92 | 1
January | 20 | 10PM to 11PM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 20 | 11PM to 12AM | 43.9 | 42.9 | 41.9 | 39.4 | 16.61 | 0.0785 | 0.27 | 12.81 | 1
January | 21 | 12AM to 1AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 21 | 1AM to 2AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 21 | 2AM to 3AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 21 | 3AM to 4AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 21 | 4AM to 5AM | 43.9 | 42.9 | 41.9 | 39.4 | 16.61 | 0.0785 | 0.27 | 12.81 | 1
January | 21 | 5AM to 6AM | 43 | 42.4 | 41.9 | 39.4 | 16.39 | 0.0786 | 0.27 | 12.79 | 1
January | 21 | 6AM to 7AM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.0789 | 0.25 | 12.73 | 1
January | 21 | 7AM to 8AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 21 | 8AM to 9AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 21 | 9AM to 10AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 21 | 10AM to 11AM | 52.9 | 49.6 | 46.9 | 47.8 | 20.09 | 0.077 | 0.32 | 13.07 | 0
January | 21 | 11AM to 12PM | 54.9 | 51 | 47.8 | 49.5 | 20.83 | 0.0767 | 0.33 | 13.12 | 0
January | 21 | 12PM to 1PM | 59.9 | 53.7 | 48.9 | 51.5 | 22.38 | 0.076 | 0.35 | 13.26 | 0
January | 21 | 1PM to 2PM | 61 | 54.1 | 48.9 | 51.5 | 22.64 | 0.0758 | 0.35 | 13.29 | 0
January | 21 | 2PM to 3PM | 63 | 55.4 | 50 | 53.7 | 23.46 | 0.0755 | 0.36 | 13.34 | 0
January | 21 | 3PM to 4PM | 63 | 54.4 | 47.8 | 49.5 | 22.8 | 0.0755 | 0.33 | 13.33 | 0
January | 21 | 4PM to 5PM | 61.9 | 54.5 | 48.9 | 51.5 | 22.86 | 0.0757 | 0.35 | 13.31 | 0
January | 21 | 5PM to 6PM | 56.8 | 51.8 | 47.8 | 49.5 | 21.32 | 0.0764 | 0.33 | 13.17 | 0
January | 21 | 6PM to 7PM | 54 | 50.6 | 47.8 | 49.5 | 20.62 | 0.0769 | 0.33 | 13.1 | 0
January | 21 | 7PM to 8PM | 52.9 | 49.1 | 45.9 | 45.9 | 19.8 | 0.0771 | 0.31 | 13.06 | 0
January | 21 | 8PM to 9PM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 21 | 9PM to 10PM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 21 | 10PM to 11PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 21 | 11PM to 12AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 22 | 12AM to 1AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 22 | 1AM to 2AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 22 | 2AM to 3AM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 22 | 3AM to 4AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 22 | 4AM to 5AM | 40.8 | 40.8 | 40.8 | 37.7 | 15.61 | 0.079 | 0.26 | 12.73 | 1
January | 22 | 5AM to 6AM | 43 | 43 | 43 | 41 | 16.65 | 0.0786 | 0.28 | 12.8 | 1
January | 22 | 6AM to 7AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 22 | 7AM to 8AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 22 | 8AM to 9AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 22 | 9AM to 10AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 22 | 10AM to 11AM | 52.9 | 49.1 | 45.9 | 45.9 | 19.8 | 0.0771 | 0.31 | 13.06 | 0
January | 22 | 11AM to 12PM | 54.9 | 48.6 | 43 | 41 | 19.53 | 0.0768 | 0.28 | 13.1 | 0
January | 22 | 12PM to 1PM | 57.9 | 49.5 | 41.9 | 39.4 | 20.01 | 0.0763 | 0.27 | 13.17 | 0
January | 22 | 1PM to 2PM | 59 | 50.9 | 43.9 | 42.5 | 20.76 | 0.0762 | 0.29 | 13.21 | 0
January | 22 | 2PM to 3PM | 61.9 | 53 | 45.9 | 45.9 | 21.98 | 0.0757 | 0.31 | 13.29 | 0
January | 22 | 3PM to 4PM | 61 | 52.2 | 45 | 44.3 | 21.52 | 0.0759 | 0.3 | 13.26 | 0
January | 22 | 4PM to 5PM | 59 | 52.7 | 47.8 | 49.5 | 21.84 | 0.0761 | 0.33 | 13.23 | 0
January | 22 | 5PM to 6PM | 56.8 | 51.4 | 46.9 | 47.8 | 21.06 | 0.0765 | 0.32 | 13.17 | 0
January | 22 | 6PM to 7PM | 55.9 | 52 | 48.9 | 51.5 | 21.42 | 0.0766 | 0.35 | 13.16 | 0
January | 22 | 7PM to 8PM | 54 | 51.1 | 48.9 | 51.5 | 20.94 | 0.0769 | 0.35 | 13.11 | 0
January | 22 | 8PM to 9PM | 54 | 51.1 | 48.9 | 51.5 | 20.94 | 0.0769 | 0.35 | 13.11 | 0
January | 22 | 9PM to 10PM | 52 | 50.9 | 50 | 53.7 | 20.79 | 0.0771 | 0.36 | 13.06 | 0
January | 22 | 10PM to 11PM | 52 | 50.9 | 50 | 53.7 | 20.79 | 0.0771 | 0.36 | 13.06 | 0
January | 22 | 11PM to 12AM | 52.2 | 51.1 | 50.4 | 54.4 | 20.94 | 0.0771 | 0.37 | 13.07 | 0
January | 23 | 12AM to 1AM | 52.3 | 51.3 | 50.5 | 54.8 | 21.04 | 0.0771 | 0.37 | 13.08 | 0
January | 23 | 1AM to 2AM | 52.9 | 51.8 | 50.9 | 55.5 | 21.29 | 0.077 | 0.37 | 13.09 | 0
January | 23 | 2AM to 3AM | 54 | 52.8 | 52 | 57.8 | 21.91 | 0.0768 | 0.39 | 13.13 | 0
January | 23 | 3AM to 4AM | 54 | 51.7 | 50 | 53.7 | 21.27 | 0.0768 | 0.36 | 13.11 | 0
January | 23 | 4AM to 5AM | 55.9 | 53 | 50.9 | 55.5 | 22.04 | 0.0765 | 0.37 | 13.17 | 0
January | 23 | 5AM to 6AM | 54 | 52.2 | 50.9 | 55.5 | 21.55 | 0.0768 | 0.37 | 13.12 | 0
January | 23 | 6AM to 7AM | 54 | 52.8 | 52 | 57.8 | 21.91 | 0.0768 | 0.39 | 13.13 | 0
January | 23 | 7AM to 8AM | 52 | 51.4 | 50.9 | 55.5 | 21.07 | 0.0771 | 0.37 | 13.07 | 0
January | 23 | 8AM to 9AM | 52 | 50.9 | 50 | 53.7 | 20.79 | 0.0771 | 0.36 | 13.06 | 0
January | 23 | 9AM to 10AM | 54 | 51.7 | 50 | 53.7 | 21.27 | 0.0768 | 0.36 | 13.11 | 0
January | 23 | 10AM to 11AM | 54 | 51.7 | 50 | 53.7 | 21.27 | 0.0768 | 0.36 | 13.11 | 0
January | 23 | 11AM to 12PM | 57.9 | 52.8 | 48.9 | 51.5 | 21.9 | 0.0763 | 0.35 | 13.21 | 0
January | 23 | 12PM to 1PM | 59 | 52.7 | 47.8 | 49.5 | 21.84 | 0.0761 | 0.33 | 13.23 | 0
January | 23 | 1PM to 2PM | 59 | 52.7 | 47.8 | 49.5 | 21.84 | 0.0761 | 0.33 | 13.23 | 0
January | 23 | 2PM to 3PM | 59 | 53.3 | 48.9 | 51.5 | 22.16 | 0.0761 | 0.35 | 13.24 | 0
January | 23 | 3PM to 4PM | 57.9 | 53.4 | 50 | 53.7 | 22.23 | 0.0763 | 0.36 | 13.21 | 0
January | 23 | 4PM to 5PM | 57.9 | 52.3 | 47.8 | 49.5 | 21.58 | 0.0763 | 0.33 | 13.2 | 0
January | 23 | 5PM to 6PM | 54.9 | 51 | 47.8 | 49.5 | 20.83 | 0.0767 | 0.33 | 13.12 | 0
January | 23 | 6PM to 7PM | 54 | 50.6 | 47.8 | 49.5 | 20.62 | 0.0769 | 0.33 | 13.1 | 0
January | 23 | 7PM to 8PM | 52 | 49.2 | 46.9 | 47.8 | 19.88 | 0.0772 | 0.32 | 13.05 | 0
January | 23 | 8PM to 9PM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 23 | 9PM to 10PM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 23 | 10PM to 11PM | 50 | 48.3 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 13 | 1
January | 23 | 11PM to 12AM | 50.9 | 47.8 | 45 | 44.3 | 19.07 | 0.0774 | 0.3 | 13.01 | 1
January | 24 | 12AM to 1AM | 50.9 | 47.8 | 45 | 44.3 | 19.07 | 0.0774 | 0.3 | 13.01 | 1
January | 24 | 1AM to 2AM | 50.9 | 48.2 | 45.9 | 45.9 | 19.31 | 0.0774 | 0.31 | 13.01 | 1
January | 24 | 2AM to 3AM | 50.9 | 48.2 | 45.9 | 45.9 | 19.31 | 0.0774 | 0.31 | 13.01 | 1
January | 24 | 3AM to 4AM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 24 | 4AM to 5AM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0776 | 0.32 | 12.97 | 1
January | 24 | 5AM to 6AM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 24 | 6AM to 7AM | 48.9 | 47.3 | 45.9 | 45.9 | 18.83 | 0.0777 | 0.31 | 12.96 | 1
January | 24 | 7AM to 8AM | 47.8 | 45.4 | 43 | 41 | 17.83 | 0.0779 | 0.28 | 12.92 | 1
January | 24 | 8AM to 9AM | 48.2 | 46.1 | 44.1 | 42.8 | 18.18 | 0.0778 | 0.29 | 12.93 | 1
January | 24 | 9AM to 10AM | 48.9 | 46.8 | 45 | 44.3 | 18.59 | 0.0777 | 0.3 | 12.96 | 1
January | 24 | 10AM to 11AM | 48.9 | 47.3 | 45.9 | 45.9 | 18.83 | 0.0777 | 0.31 | 12.96 | 1
January | 24 | 11AM to 12PM | 50 | 48.3 | 46.9 | 47.8 | 19.39 | 0.0775 | 0.32 | 13 | 1
January | 24 | 12PM to 1PM | 50.9 | 48.8 | 46.9 | 47.8 | 19.61 | 0.0773 | 0.32 | 13.02 | 1
January | 24 | 1PM to 2PM | 52.9 | 48.7 | 45 | 44.3 | 19.55 | 0.0771 | 0.3 | 13.06 | 0
January | 24 | 2PM to 3PM | 52.9 | 49.6 | 46.9 | 47.8 | 20.09 | 0.077 | 0.32 | 13.07 | 0
January | 24 | 3PM to 4PM | 52 | 48.3 | 45 | 44.3 | 19.34 | 0.0772 | 0.3 | 13.04 | 0
January | 24 | 4PM to 5PM | 50.9 | 48.2 | 45.9 | 45.9 | 19.31 | 0.0774 | 0.31 | 13.01 | 1
January | 24 | 5PM to 6PM | 48.2 | 46.5 | 45 | 44.3 | 18.42 | 0.0778 | 0.3 | 12.94 | 1
January | 24 | 6PM to 7PM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 24 | 7PM to 8PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 24 | 8PM to 9PM | 43.9 | 42.9 | 41.9 | 39.4 | 16.61 | 0.0785 | 0.27 | 12.81 | 1
January | 24 | 9PM to 10PM | 43 | 42 | 41 | 38 | 16.18 | 0.0786 | 0.26 | 12.79 | 1
January | 24 | 10PM to 11PM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 24 | 11PM to 12AM | 41.9 | 41.5 | 41 | 38 | 15.92 | 0.0788 | 0.26 | 12.76 | 1
January | 25 | 12AM to 1AM | 41.9 | 41 | 39.9 | 36.4 | 15.67 | 0.0788 | 0.25 | 12.76 | 1
January | 25 | 1AM to 2AM | 43.9 | 43.4 | 43 | 41 | 16.87 | 0.0785 | 0.28 | 12.82 | 1
January | 25 | 2AM to 3AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 25 | 3AM to 4AM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 25 | 4AM to 5AM | 45 | 44.4 | 43.9 | 42.5 | 17.35 | 0.0783 | 0.29 | 12.85 | 1
January | 25 | 5AM to 6AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 25 | 6AM to 7AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 25 | 7AM to 8AM | 45.9 | 44.8 | 43.9 | 42.5 | 17.57 | 0.0781 | 0.29 | 12.87 | 1
January | 25 | 8AM to 9AM | 46.9 | 45.4 | 43.9 | 42.5 | 17.83 | 0.078 | 0.29 | 12.9 | 1
January | 25 | 9AM to 10AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 25 | 10AM to 11AM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 25 | 11AM to 12PM | 48.9 | 47 | 45.3 | 44.9 | 18.69 | 0.0777 | 0.3 | 12.96 | 1
January | 25 | 12PM to 1PM | 50 | 47.8 | 45.9 | 45.9 | 19.1 | 0.0775 | 0.31 | 12.99 | 1
January | 25 | 1PM to 2PM | 52 | 48.3 | 45 | 44.3 | 19.34 | 0.0772 | 0.3 | 13.04 | 0
January | 25 | 2PM to 3PM | 52 | 48.3 | 45 | 44.3 | 19.34 | 0.0772 | 0.3 | 13.04 | 0
January | 25 | 3PM to 4PM | 50.9 | 48.2 | 45.9 | 45.9 | 19.31 | 0.0774 | 0.31 | 13.01 | 1
January | 25 | 4PM to 5PM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0776 | 0.32 | 12.97 | 1
January | 25 | 5PM to 6PM | 48.9 | 47.9 | 46.9 | 47.8 | 19.13 | 0.0776 | 0.32 | 12.97 | 1
January | 25 | 6PM to 7PM | 47.8 | 47.4 | 46.9 | 47.8 | 18.87 | 0.0778 | 0.32 | 12.94 | 1
January | 25 | 7PM to 8PM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 25 | 8PM to 9PM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 25 | 9PM to 10PM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 25 | 10PM to 11PM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 25 | 11PM to 12AM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 26 | 12AM to 1AM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 26 | 1AM to 2AM | 47.8 | 46.8 | 45.9 | 45.9 | 18.57 | 0.0778 | 0.31 | 12.93 | 1
January | 26 | 2AM to 3AM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 26 | 3AM to 4AM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 26 | 4AM to 5AM | 46.9 | 46.4 | 45.9 | 45.9 | 18.35 | 0.078 | 0.31 | 12.91 | 1
January | 26 | 5AM to 6AM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 26 | 6AM to 7AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 26 | 7AM to 8AM | 45.9 | 45.4 | 45 | 44.3 | 17.85 | 0.0781 | 0.3 | 12.88 | 1
January | 26 | 8AM to 9AM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 26 | 9AM to 10AM | 48.4 | 46.6 | 45 | 44.3 | 18.46 | 0.0777 | 0.3 | 12.94 | 1
January | 26 | 10AM to 11AM | 50 | 47.3 | 45 | 44.3 | 18.85 | 0.0775 | 0.3 | 12.98 | 1
January | 26 | 11AM to 12PM | 50.9 | 48.2 | 45.9 | 45.9 | 19.31 | 0.0774 | 0.31 | 13.01 | 1
January | 26 | 12PM to 1PM | 50.9 | 47.8 | 45 | 44.3 | 19.07 | 0.0774 | 0.3 | 13.01 | 1
January | 26 | 1PM to 2PM | 52 | 48.3 | 45 | 44.3 | 19.34 | 0.0772 | 0.3 | 13.04 | 0
January | 26 | 2PM to 3PM | 52 | 47.7 | 43.9 | 42.5 | 19.06 | 0.0772 | 0.29 | 13.03 | 0
January | 26 | 3PM to 4PM | 52 | 47.7 | 43.9 | 42.5 | 19.06 | 0.0772 | 0.29 | 13.03 | 0
January | 26 | 4PM to 5PM | 52 | 47.7 | 43.9 | 42.5 | 19.06 | 0.0772 | 0.29 | 13.03 | 0
January | 26 | 5PM to 6PM | 50.7 | 47.2 | 43.9 | 42.5 | 18.75 | 0.0774 | 0.29 | 13 | 1
January | 26 | 6PM to 7PM | 50 | 46.8 | 43.9 | 42.5 | 18.58 | 0.0775 | 0.29 | 12.98 | 1
January | 26 | 7PM to 8PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 26 | 8PM to 9PM | 47.8 | 46.3 | 45 | 44.3 | 18.33 | 0.0778 | 0.3 | 12.93 | 1
January | 26 | 9PM to 10PM | 46.9 | 45.9 | 45 | 44.3 | 18.11 | 0.078 | 0.3 | 12.91 | 1
January | 26 | 10PM to 11PM | 45 | 44 | 43 | 41 | 17.13 | 0.0783 | 0.28 | 12.85 | 1
January | 26 | 11PM to 12AM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 27 | 12AM to 1AM | 41.9 | 41 | 39.9 | 36.4 | 15.67 | 0.0788 | 0.25 | 12.76 | 1
January | 27 | 1AM to 2AM | 43 | 42 | 41 | 38 | 16.18 | 0.0786 | 0.26 | 12.79 | 1
January | 27 | 2AM to 3AM | 43 | 41.5 | 39.9 | 36.4 | 15.93 | 0.0786 | 0.25 | 12.78 | 1
January | 27 | 3AM to 4AM | 41 | 39.6 | 37.9 | 33.7 | 15.03 | 0.079 | 0.23 | 12.72 | 1
January | 27 | 4AM to 5AM | 39.9 | 38.5 | 36.9 | 32.3 | 14.55 | 0.0791 | 0.22 | 12.69 | 1
January | 27 | 5AM to 6AM | 38.8 | 37.6 | 36 | 31.1 | 14.12 | 0.0793 | 0.21 | 12.66 | 1
January | 27 | 6AM to 7AM | 40.5 | 38.2 | 35.4 | 30.5 | 14.41 | 0.0791 | 0.21 | 12.7 | 1
January | 27 | 7AM to 8AM | 41.9 | 38.8 | 34.9 | 29.8 | 14.65 | 0.0788 | 0.2 | 12.74 | 1
January | 27 | 8AM to 9AM | 45.9 | 41.6 | 36.9 | 32.3 | 15.99 | 0.0782 | 0.22 | 12.84 | 1
January | 27 | 9AM to 10AM | 50.9 | 44 | 36.5 | 31.8 | 17.14 | 0.0774 | 0.22 | 12.97 | 1
January | 27 | 10AM to 11AM | 55.9 | 46.2 | 36 | 31.1 | 18.26 | 0.0767 | 0.21 | 13.1 | 0
January | 27 | 11AM to 12PM | 56.8 | 46.3 | 34.9 | 29.8 | 18.27 | 0.0766 | 0.2 | 13.12 | 0
January | 27 | 12PM to 1PM | 59 | 47 | 34 | 28.8 | 18.63 | 0.0763 | 0.2 | 13.17 | 0
January | 27 | 1PM to 2PM | 59.9 | 48.1 | 36 | 31.1 | 19.21 | 0.0761 | 0.21 | 13.2 | 0
January | 27 | 2PM to 3PM | 61.9 | 49 | 36 | 31.1 | 19.69 | 0.0758 | 0.21 | 13.25 | 0
January | 27 | 3PM to 4PM | 59 | 47.7 | 36 | 31.1 | 19 | 0.0762 | 0.21 | 13.17 | 0
January | 27 | 4PM to 5PM | 54.9 | 46.5 | 37.9 | 33.7 | 18.39 | 0.0768 | 0.23 | 13.08 | 0
January | 27 | 5PM to 6PM | 52 | 45.1 | 37.9 | 33.7 | 17.69 | 0.0773 | 0.23 | 13 | 0
January | 27 | 6PM to 7PM | 50 | 43.7 | 36.9 | 32.3 | 16.99 | 0.0776 | 0.22 | 12.95 | 1
January | 27 | 7PM to 8PM | 48.9 | 42.8 | 36 | 31.1 | 16.56 | 0.0778 | 0.21 | 12.92 | 1
January | 27 | 8PM to 9PM | 45.9 | 41.3 | 36 | 31.1 | 15.82 | 0.0782 | 0.21 | 12.84 | 1
January | 27 | 9PM to 10PM | 45 | 40.8 | 36 | 31.1 | 15.6 | 0.0784 | 0.21 | 12.82 | 1
January | 27 | 10PM to 11PM | 43.9 | 39.8 | 34.9 | 29.8 | 15.13 | 0.0785 | 0.2 | 12.79 | 1
January | 27 | 11PM to 12AM | 43 | 39 | 34 | 28.8 | 14.75 | 0.0787 | 0.2 | 12.76 | 1
January | 28 | 12AM to 1AM | 38.8 | 36.7 | 34 | 28.8 | 13.75 | 0.0793 | 0.2 | 12.66 | 1
January | 28 | 1AM to 2AM | 37.9 | 35.4 | 32 | 26.6 | 13.19 | 0.0795 | 0.18 | 12.63 | 1
January | 28 | 2AM to 3AM | 36 | 35.5 | 34.9 | 29.8 | 13.22 | 0.0798 | 0.2 | 12.59 | 1
January | 28 | 3AM to 4AM | 34 | 33.5 | 32.9 | 27.5 | 12.39 | 0.0801 | 0.19 | 12.53 | 1
January | 28 | 4AM to 5AM | 34 | 33.5 | 32.9 | 27.5 | 12.39 | 0.0801 | 0.19 | 12.53 | 1
January | 28 | 5AM to 6AM | 34.7 | 34.3 | 33.8 | 28.6 | 12.72 | 0.08 | 0.19 | 12.55 | 1
January | 28 | 6AM to 7AM | 36 | 35.5 | 34.9 | 29.8 | 13.22 | 0.0798 | 0.2 | 12.59 | 1
January | 28 | 7AM to 8AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 28 | 8AM to 9AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 28 | 9AM to 10AM | 41 | 39.1 | 36.9 | 32.3 | 14.82 | 0.079 | 0.22 | 12.72 | 1
January | 28 | 10AM to 11AM | 47.8 | 43.1 | 37.9 | 33.7 | 16.69 | 0.0779 | 0.23 | 12.9 | 1
January | 28 | 11AM to 12PM | 50.4 | 43.7 | 36.3 | 31.6 | 16.97 | 0.0775 | 0.21 | 12.96 | 1
January | 28 | 12PM to 1PM | 52.9 | 44.4 | 34.9 | 29.8 | 17.31 | 0.0772 | 0.2 | 13.02 | 0
January | 28 | 1PM to 2PM | 54.9 | 45.3 | 34.9 | 29.8 | 17.79 | 0.0769 | 0.2 | 13.07 | 0
January | 28 | 2PM to 3PM | 57.9 | 45.8 | 32 | 26.6 | 18.02 | 0.0764 | 0.18 | 13.13 | 0
January | 28 | 3PM to 4PM | 57.6 | 46.6 | 34.9 | 29.8 | 18.44 | 0.0765 | 0.2 | 13.13 | 0
January | 28 | 4PM to 5PM | 55.9 | 47 | 37.9 | 33.7 | 18.65 | 0.0767 | 0.23 | 13.1 | 0
January | 28 | 5PM to 6PM | 52.9 | 44.8 | 36 | 31.1 | 17.51 | 0.0772 | 0.21 | 13.02 | 0
January | 28 | 6PM to 7PM | 50.9 | 44.2 | 36.9 | 32.3 | 17.21 | 0.0774 | 0.22 | 12.97 | 1
January | 28 | 7PM to 8PM | 48.9 | 42.4 | 34.9 | 29.8 | 16.35 | 0.0778 | 0.2 | 12.91 | 1
January | 28 | 8PM to 9PM | 45 | 40.4 | 34.9 | 29.8 | 15.4 | 0.0784 | 0.2 | 12.81 | 1
January | 28 | 9PM to 10PM | 41.9 | 39.2 | 36 | 31.1 | 14.86 | 0.0788 | 0.21 | 12.74 | 1
January | 28 | 10PM to 11PM | 39.9 | 38.1 | 36 | 31.1 | 14.38 | 0.0792 | 0.21 | 12.69 | 1
January | 28 | 11PM to 12AM | 38.8 | 37.6 | 36 | 31.1 | 14.12 | 0.0793 | 0.21 | 12.66 | 1
January | 29 | 12AM to 1AM | 37.9 | 36.2 | 34 | 28.8 | 13.53 | 0.0795 | 0.2 | 12.63 | 1
January | 29 | 1AM to 2AM | 37.9 | 35.8 | 32.9 | 27.5 | 13.35 | 0.0795 | 0.19 | 12.63 | 1
January | 29 | 2AM to 3AM | 36 | 34.7 | 32.9 | 27.5 | 12.87 | 0.0798 | 0.19 | 12.58 | 1
January | 29 | 3AM to 4AM | 36.9 | 35.2 | 32.9 | 27.5 | 13.08 | 0.0797 | 0.19 | 12.6 | 1
January | 29 | 4AM to 5AM | 34.9 | 33.7 | 32 | 26.6 | 12.45 | 0.08 | 0.18 | 12.55 | 1
January | 29 | 5AM to 6AM | 34.9 | 33.7 | 32 | 26.6 | 12.45 | 0.08 | 0.18 | 12.55 | 1
January | 29 | 6AM to 7AM | 34.9 | 33.7 | 32 | 26.6 | 12.45 | 0.08 | 0.18 | 12.55 | 1
January | 29 | 7AM to 8AM | 34 | 32.2 | 29.8 | 24 | 11.85 | 0.0802 | 0.16 | 12.52 | 1
January | 29 | 8AM to 9AM | 39.9 | 37.7 | 34.9 | 29.8 | 14.18 | 0.0792 | 0.2 | 12.69 | 1
January | 29 | 9AM to 10AM | 43.9 | 39.5 | 34 | 28.8 | 14.97 | 0.0785 | 0.2 | 12.78 | 1
January | 29 | 10AM to 11AM | 47.8 | 41.5 | 34 | 28.8 | 15.93 | 0.0779 | 0.2 | 12.88 | 1
January | 29 | 11AM to 12PM | 52 | 43.9 | 34.9 | 29.8 | 17.09 | 0.0773 | 0.2 | 12.99 | 0
January | 29 | 12PM to 1PM | 54.9 | 45.7 | 36 | 31.1 | 17.99 | 0.0769 | 0.21 | 13.07 | 0
January | 29 | 1PM to 2PM | 55.9 | 45.2 | 32.9 | 27.5 | 17.7 | 0.0767 | 0.19 | 13.09 | 0
January | 29 | 2PM to 3PM | 59 | 48.8 | 38.8 | 34.9 | 19.58 | 0.0762 | 0.24 | 13.19 | 0
January | 29 | 3PM to 4PM | 59.9 | 48.4 | 36.9 | 32.3 | 19.39 | 0.0761 | 0.22 | 13.2 | 0
January | 29 | 4PM to 5PM | 61 | 50.1 | 39.9 | 36.4 | 20.3 | 0.0759 | 0.25 | 13.24 | 0
January | 29 | 5PM to 6PM | 50.9 | 45.9 | 41 | 38 | 18.1 | 0.0774 | 0.26 | 12.99 | 1
January | 29 | 6PM to 7PM | 46.9 | 42.6 | 37.9 | 33.7 | 16.47 | 0.078 | 0.23 | 12.88 | 1
January | 29 | 7PM to 8PM | 45 | 42 | 38.8 | 34.9 | 16.18 | 0.0783 | 0.24 | 12.83 | 1
January | 29 | 8PM to 9PM | 45.9 | 42.5 | 38.8 | 34.9 | 16.4 | 0.0782 | 0.24 | 12.85 | 1
January | 29 | 9PM to 10PM | 43 | 41 | 38.8 | 34.9 | 15.7 | 0.0786 | 0.24 | 12.78 | 1
January | 29 | 10PM to 11PM | 41 | 39.6 | 37.9 | 33.7 | 15.03 | 0.079 | 0.23 | 12.72 | 1
January | 29 | 11PM to 12AM | 39.9 | 38.8 | 37.6 | 33.2 | 14.7 | 0.0791 | 0.23 | 12.7 | 1
January | 30 | 12AM to 1AM | 38.8 | 38.1 | 37.2 | 32.7 | 14.36 | 0.0793 | 0.22 | 12.67 | 1
January | 30 | 1AM to 2AM | 37.9 | 37.5 | 36.9 | 32.3 | 14.07 | 0.0795 | 0.22 | 12.64 | 1
January | 30 | 2AM to 3AM | 34.9 | 34.9 | 34.9 | 29.8 | 12.96 | 0.08 | 0.2 | 12.56 | 1
January | 30 | 3AM to 4AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 30 | 4AM to 5AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
January | 30 | 5AM to 6AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
January | 30 | 6AM to 7AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 30 | 7AM to 8AM | 37.9 | 37.5 | 36.9 | 32.3 | 14.07 | 0.0795 | 0.22 | 12.64 | 1
January | 30 | 8AM to 9AM | 38.8 | 38.8 | 38.8 | 34.9 | 14.7 | 0.0793 | 0.24 | 12.67 | 1
January | 30 | 9AM to 10AM | 39.9 | 39.4 | 38.8 | 34.9 | 14.96 | 0.0791 | 0.24 | 12.7 | 1
January | 30 | 10AM to 11AM | 39.9 | 39.9 | 39.9 | 36.4 | 15.19 | 0.0791 | 0.25 | 12.71 | 1
January | 30 | 11AM to 12PM | 41 | 40.5 | 39.9 | 36.4 | 15.45 | 0.0789 | 0.25 | 12.73 | 1
January | 30 | 12PM to 1PM | 43.3 | 42.2 | 41 | 38 | 16.26 | 0.0786 | 0.26 | 12.8 | 1
January | 30 | 1PM to 2PM | 45 | 43.4 | 41.9 | 39.4 | 16.87 | 0.0783 | 0.27 | 12.84 | 1
January | 30 | 2PM to 3PM | 47.8 | 45.4 | 43 | 41 | 17.83 | 0.0779 | 0.28 | 12.92 | 1
January | 30 | 3PM to 4PM | 50.9 | 46.3 | 41.9 | 39.4 | 18.31 | 0.0774 | 0.27 | 12.99 | 1
January | 30 | 4PM to 5PM | 50 | 45.9 | 41.9 | 39.4 | 18.09 | 0.0775 | 0.27 | 12.97 | 1
January | 30 | 5PM to 6PM | 46.9 | 44.4 | 41.9 | 39.4 | 17.35 | 0.078 | 0.27 | 12.89 | 1
January | 30 | 6PM to 7PM | 45 | 42.5 | 39.9 | 36.4 | 16.41 | 0.0783 | 0.25 | 12.83 | 1
January | 30 | 7PM to 8PM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 30 | 8PM to 9PM | 38.8 | 38.4 | 37.9 | 33.7 | 14.51 | 0.0793 | 0.23 | 12.67 | 1
January | 30 | 9PM to 10PM | 37.9 | 37.9 | 37.9 | 33.7 | 14.29 | 0.0794 | 0.23 | 12.65 | 1
January | 30 | 10PM to 11PM | 36 | 35.5 | 34.9 | 29.8 | 13.22 | 0.0798 | 0.2 | 12.59 | 1
January | 30 | 11PM to 12AM | 32.9 | 32.9 | 32.9 | 27.5 | 12.13 | 0.0803 | 0.19 | 12.5 | 1
January | 31 | 12AM to 1AM | 30.9 | 30.9 | 30.9 | 25.3 | 11.3 | 0.0806 | 0.17 | 12.44 | 1
January | 31 | 1AM to 2AM | 29.8 | 29.8 | 29.8 | 24 | 10.85 | 0.0808 | 0.16 | 12.41 | 1
January | 31 | 2AM to 3AM | 34.9 | 34.5 | 34 | 28.8 | 12.79 | 0.08 | 0.2 | 12.56 | 1
January | 31 | 3AM to 4AM | 34 | 34 | 34 | 28.8 | 12.58 | 0.0801 | 0.2 | 12.53 | 1
January | 31 | 4AM to 5AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
January | 31 | 5AM to 6AM | 30.9 | 30.4 | 29.8 | 24 | 11.11 | 0.0807 | 0.16 | 12.44 | 1
January | 31 | 6AM to 7AM | 30.9 | 30.9 | 30.9 | 25.3 | 11.3 | 0.0806 | 0.17 | 12.44 | 1
January | 31 | 7AM to 8AM | 30.9 | 30.4 | 29.8 | 24 | 11.11 | 0.0807 | 0.16 | 12.44 | 1
January | 31 | 8AM to 9AM | 36 | 34.7 | 32.9 | 27.5 | 12.87 | 0.0798 | 0.19 | 12.58 | 1
January | 31 | 9AM to 10AM | 41 | 36.7 | 30.9 | 25.3 | 13.73 | 0.079 | 0.17 | 12.7 | 1
January | 31 | 10AM to 11AM | 47.8 | 42.3 | 36 | 31.1 | 16.3 | 0.0779 | 0.21 | 12.89 | 1
January | 31 | 11AM to 12PM | 54 | 43.5 | 30.9 | 25.3 | 16.87 | 0.077 | 0.17 | 13.03 | 0
January | 31 | 12PM to 1PM | 56.8 | 43.9 | 27.9 | 21.9 | 17.04 | 0.0766 | 0.15 | 13.09 | 0
January | 31 | 1PM to 2PM | 58.5 | 44.3 | 26.8 | 20.8 | 17.26 | 0.0764 | 0.14 | 13.13 | 0
January | 31 | 2PM to 3PM | 59.9 | 44.7 | 25.9 | 20 | 17.48 | 0.0762 | 0.14 | 13.16 | 0
January | 31 | 3PM to 4PM | 59.9 | 44.7 | 25.9 | 20 | 17.48 | 0.0762 | 0.14 | 13.16 | 0
January | 31 | 4PM to 5PM | 57.9 | 46.1 | 32.9 | 27.5 | 18.18 | 0.0764 | 0.19 | 13.14 | 0
January | 31 | 5PM to 6PM | 55.9 | 44.1 | 29.8 | 24 | 17.15 | 0.0767 | 0.16 | 13.08 | 0
January | 31 | 6PM to 7PM | 52.9 | 42.9 | 30.9 | 25.3 | 16.6 | 0.0772 | 0.17 | 13 | 0
January | 31 | 7PM to 8PM | 46.9 | 44.4 | 41.9 | 39.4 | 17.35 | 0.078 | 0.27 | 12.89 | 1
January | 31 | 8PM to 9PM | 43.9 | 42.5 | 41 | 38 | 16.4 | 0.0785 | 0.26 | 12.81 | 1
January | 31 | 9PM to 10PM | 43 | 41.8 | 40.5 | 37.2 | 16.06 | 0.0786 | 0.25 | 12.79 | 1
January | 31 | 10PM to 11PM | 42.1 | 41 | 39.9 | 36.4 | 15.72 | 0.0788 | 0.25 | 12.76 | 1
January | 31 | 11PM to 12AM | 41.2 | 40.3 | 39.4 | 35.7 | 15.38 | 0.0789 | 0.24 | 12.74 | 1
February | 1 | 12AM to 1AM | 40.1 | 39.6 | 39 | 35.2 | 15.04 | 0.0791 | 0.24 | 12.71 | 1
February | 1 | 1AM to 2AM | 39.2 | 38.9 | 38.5 | 34.4 | 14.71 | 0.0792 | 0.23 | 12.68 | 1
February | 1 | 2AM to 3AM | 38.3 | 38.1 | 37.9 | 33.7 | 14.38 | 0.0794 | 0.23 | 12.66 | 1
February | 1 | 3AM to 4AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 1 | 4AM to 5AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 1 | 5AM to 6AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 1 | 6AM to 7AM | 37 | 36.7 | 36.3 | 31.6 | 13.75 | 0.0796 | 0.21 | 12.62 | 1
February | 1 | 7AM to 8AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 1 | 8AM to 9AM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
February | 1 | 9AM to 10AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 1 | 10AM to 11AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 1 | 11AM to 12PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
February | 1 | 12PM to 1PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
February | 1 | 1PM to 2PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
February | 1 | 2PM to 3PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
February | 1 | 3PM to 4PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
February | 1 | 4PM to 5PM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
February | 1 | 5PM to 6PM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
February | 1 | 6PM to 7PM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
February | 1 | 7PM to 8PM | 41 | 38.6 | 35.6 | 30.7 | 14.57 | 0.079 | 0.21 | 12.72 | 1
February | 1 | 8PM to 9PM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
February | 1 | 9PM to 10PM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
February | 1 | 10PM to 11PM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 1 | 11PM to 12AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 2 | 12AM to 1AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 2 | 1AM to 2AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
February | 2 | 2AM to 3AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
February | 2 | 3AM to 4AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
February | 2 | 4AM to 5AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
February | 2 | 5AM to 6AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
February | 2 | 6AM to 7AM | 28.4 | 28.4 | 28.4 | 22.5 | 10.26 | 0.0811 | 0.15 | 12.37 | 1
February | 2 | 7AM to 8AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
February | 2 | 8AM to 9AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 2 | 9AM to 10AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 2 | 10AM to 11AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
February | 2 | 11AM to 12PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 2 | 12PM to 1PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
February | 2 | 1PM to 2PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
February | 2 | 2PM to 3PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 2 | 3PM to 4PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
February | 2 | 4PM to 5PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 2 | 5PM to 6PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
February | 2 | 6PM to 7PM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
February | 2 | 7PM to 8PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
February | 2 | 8PM to 9PM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
February | 2 | 9PM to 10PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 2 | 10PM to 11PM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
February | 2 | 11PM to 12AM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
February | 3 | 12AM to 1AM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
February | 3 | 1AM to 2AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 3 | 2AM to 3AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 3 | 3AM to 4AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 3 | 4AM to 5AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
February | 3 | 5AM to 6AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
February | 3 | 6AM to 7AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
February | 3 | 7AM to 8AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
February | 3 | 8AM to 9AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 3 | 9AM to 10AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 3 | 10AM to 11AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
February | 3 | 11AM to 12PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 3 | 12PM to 1PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
February | 3 | 1PM to 2PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
February | 3 | 2PM to 3PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.2 | 0
February | 3 | 3PM to 4PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
February | 3 | 4PM to 5PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
February | 3 | 5PM to 6PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 3 | 6PM to 7PM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
February | 3 | 7PM to 8PM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
February | 3 | 8PM to 9PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
February | 3 | 9PM to 10PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 3 | 10PM to 11PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
February | 3 | 11PM to 12AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 4 | 12AM to 1AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 4 | 1AM to 2AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 4 | 2AM to 3AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 4 | 3AM to 4AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 4 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 4 | 5AM to 6AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
February | 4 | 6AM to 7AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
February | 4 | 7AM to 8AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 4 | 8AM to 9AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
February | 4 | 9AM to 10AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 4 | 10AM to 11AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 4 | 11AM to 12PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 4 | 12PM to 1PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 4 | 1PM to 2PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 4 | 2PM to 3PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 4 | 3PM to 4PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 4 | 4PM to 5PM | 53.6 | 46.5 | 39.4 | 35.7 | 18.39 | 0.077 | 0.24 | 13.05 | 0
February | 4 | 5PM to 6PM | 50.7 | 45.1 | 39.4 | 35.7 | 17.69 | 0.0774 | 0.24 | 12.98 | 1
February | 4 | 6PM to 7PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 4 | 7PM to 8PM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
February | 4 | 8PM to 9PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 4 | 9PM to 10PM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
February | 4 | 10PM to 11PM | 42.8 | 38.8 | 33.8 | 28.6 | 14.68 | 0.0787 | 0.19 | 12.76 | 1
February | 4 | 11PM to 12AM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
February | 5 | 12AM to 1AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 5 | 1AM to 2AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
February | 5 | 2AM to 3AM | 35.6 | 33.3 | 30.2 | 24.4 | 12.3 | 0.0799 | 0.17 | 12.56 | 1
February | 5 | 3AM to 4AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
February | 5 | 4AM to 5AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
February | 5 | 5AM to 6AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
February | 5 | 6AM to 7AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
February | 5 | 7AM to 8AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
February | 5 | 8AM to 9AM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
February | 5 | 9AM to 10AM | 46.6 | 42.8 | 38.7 | 34.7 | 16.53 | 0.0781 | 0.24 | 12.87 | 1
February | 5 | 10AM to 11AM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
February | 5 | 11AM to 12PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 5 | 12PM to 1PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 5 | 1PM to 2PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
February | 5 | 2PM to 3PM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
February | 5 | 3PM to 4PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
February | 5 | 4PM to 5PM | 51.8 | 44.8 | 37.4 | 33 | 17.54 | 0.0773 | 0.22 | 13 | 1
February | 5 | 5PM to 6PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 5 | 6PM to 7PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 5 | 7PM to 8PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 5 | 8PM to 9PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
February | 5 | 9PM to 10PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 5 | 10PM to 11PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 5 | 11PM to 12AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
February | 6 | 12AM to 1AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
February | 6 | 1AM to 2AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
February | 6 | 2AM to 3AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 6 | 3AM to 4AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
February | 6 | 4AM to 5AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 6 | 5AM to 6AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 6 | 6AM to 7AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
February | 6 | 7AM to 8AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 6 | 8AM to 9AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
February | 6 | 9AM to 10AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 6 | 10AM to 11AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 6 | 11AM to 12PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 6 | 12PM to 1PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 6 | 1PM to 2PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 6 | 2PM to 3PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 6 | 3PM to 4PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 6 | 4PM to 5PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 6 | 5PM to 6PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 6 | 6PM to 7PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
February | 6 | 7PM to 8PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
February | 6 | 8PM to 9PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
February | 6 | 9PM to 10PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 6 | 10PM to 11PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 6 | 11PM to 12AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 7 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 7 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 7 | 2AM to 3AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 7 | 3AM to 4AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 7 | 4AM to 5AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 7 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 7 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 7 | 7AM to 8AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 7 | 8AM to 9AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 7 | 9AM to 10AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
February | 7 | 10AM to 11AM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
February | 7 | 11AM to 12PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 7 | 12PM to 1PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
February | 7 | 1PM to 2PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
February | 7 | 2PM to 3PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
February | 7 | 3PM to 4PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
February | 7 | 4PM to 5PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
February | 7 | 5PM to 6PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
February | 7 | 6PM to 7PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 7 | 7PM to 8PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 7 | 8PM to 9PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 7 | 9PM to 10PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 7 | 10PM to 11PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 7 | 11PM to 12AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 8 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 8 | 1AM to 2AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 8 | 2AM to 3AM | 49.1 | 48.1 | 47.3 | 48.4 | 19.28 | 0.0776 | 0.33 | 12.97 | 1
February | 8 | 3AM to 4AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 8 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 8 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 8 | 6AM to 7AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 8 | 7AM to 8AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 8 | 8AM to 9AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 8 | 9AM to 10AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
February | 8 | 10AM to 11AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
February | 8 | 11AM to 12PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
February | 8 | 12PM to 1PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 1PM to 2PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 2PM to 3PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 3PM to 4PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 4PM to 5PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
February | 8 | 5PM to 6PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 6PM to 7PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 7PM to 8PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 8PM to 9PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 9PM to 10PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 10PM to 11PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 8 | 11PM to 12AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 9 | 12AM to 1AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 9 | 1AM to 2AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 9 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
February | 9 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
February | 9 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
February | 9 | 5AM to 6AM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
February | 9 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 9 | 7AM to 8AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 9 | 8AM to 9AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
February | 9 | 9AM to 10AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
February | 9 | 10AM to 11AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
February | 9 | 11AM to 12PM | 50 | 43.9 | 37.4 | 33 | 17.1 | 0.0776 | 0.22 | 12.95 | 1
February | 9 | 12PM to 1PM | 51.8 | 43.4 | 33.8 | 28.6 | 16.85 | 0.0773 | 0.19 | 12.98 | 1
February | 9 | 1PM to 2PM | 51.8 | 42.8 | 32 | 26.6 | 16.54 | 0.0773 | 0.18 | 12.98 | 1
February | 9 | 2PM to 3PM | 51.8 | 41.5 | 28.4 | 22.5 | 15.91 | 0.0774 | 0.15 | 12.97 | 1
February | 9 | 3PM to 4PM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
February | 9 | 4PM to 5PM | 46.4 | 39.3 | 30.2 | 24.4 | 14.91 | 0.0782 | 0.17 | 12.84 | 1
February | 9 | 5PM to 6PM | 44.6 | 38.4 | 30.2 | 24.4 | 14.48 | 0.0785 | 0.17 | 12.79 | 1
February | 9 | 6PM to 7PM | 42.8 | 36.7 | 28.4 | 22.5 | 13.74 | 0.0788 | 0.15 | 12.74 | 1
February | 9 | 7PM to 8PM | 39.2 | 34.7 | 28.4 | 22.5 | 12.87 | 0.0793 | 0.15 | 12.65 | 1
February | 9 | 8PM to 9PM | 39.2 | 34.7 | 28.4 | 22.5 | 12.87 | 0.0793 | 0.15 | 12.65 | 1
February | 9 | 9PM to 10PM | 39.2 | 34.7 | 28.4 | 22.5 | 12.87 | 0.0793 | 0.15 | 12.65 | 1
February | 9 | 10PM to 11PM | 35.6 | 33.3 | 30.2 | 24.4 | 12.3 | 0.0799 | 0.17 | 12.56 | 1
February | 9 | 11PM to 12AM | 34.7 | 32.7 | 30 | 24.2 | 12.05 | 0.08 | 0.16 | 12.54 | 1
February | 10 | 12AM to 1AM | 33.8 | 32.3 | 30.2 | 24.4 | 11.87 | 0.0802 | 0.17 | 12.52 | 1
February | 10 | 1AM to 2AM | 33.8 | 32.3 | 30.2 | 24.4 | 11.87 | 0.0802 | 0.17 | 12.52 | 1
February | 10 | 2AM to 3AM | 30.2 | 29.4 | 28.4 | 22.5 | 10.7 | 0.0808 | 0.15 | 12.42 | 1
February | 10 | 3AM to 4AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
February | 10 | 4AM to 5AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
February | 10 | 5AM to 6AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
February | 10 | 6AM to 7AM | 30.2 | 29.4 | 28.4 | 22.5 | 10.7 | 0.0808 | 0.15 | 12.42 | 1
February | 10 | 7AM to 8AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
February | 10 | 8AM to 9AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 10 | 9AM to 10AM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
February | 10 | 10AM to 11AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
February | 10 | 11AM to 12PM | 46.4 | 41.4 | 35.6 | 30.7 | 15.88 | 0.0781 | 0.21 | 12.85 | 1
February | 10 | 12PM to 1PM | 46.4 | 41.4 | 35.6 | 30.7 | 15.88 | 0.0781 | 0.21 | 12.85 | 1
February | 10 | 1PM to 2PM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
February | 10 | 2PM to 3PM | 50 | 40.6 | 28.4 | 22.5 | 15.48 | 0.0776 | 0.15 | 12.92 | 1
February | 10 | 3PM to 4PM | 50 | 41.2 | 30.2 | 24.4 | 15.78 | 0.0776 | 0.17 | 12.93 | 1
February | 10 | 4PM to 5PM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
February | 10 | 5PM to 6PM | 44.6 | 39.8 | 33.8 | 28.6 | 15.11 | 0.0784 | 0.19 | 12.8 | 1
February | 10 | 6PM to 7PM | 41 | 37.8 | 33.8 | 28.6 | 14.24 | 0.079 | 0.19 | 12.71 | 1
February | 10 | 7PM to 8PM | 41 | 37.1 | 32 | 26.6 | 13.93 | 0.079 | 0.18 | 12.7 | 1
February | 10 | 8PM to 9PM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
February | 10 | 9PM to 10PM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
February | 10 | 10PM to 11PM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 10 | 11PM to 12AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 11 | 12AM to 1AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 11 | 1AM to 2AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 11 | 2AM to 3AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
February | 11 | 3AM to 4AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
February | 11 | 4AM to 5AM | 33.8 | 32.3 | 30.2 | 24.4 | 11.87 | 0.0802 | 0.17 | 12.52 | 1
February | 11 | 5AM to 6AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
February | 11 | 6AM to 7AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
February | 11 | 7AM to 8AM | 33.8 | 32.3 | 30.2 | 24.4 | 11.87 | 0.0802 | 0.17 | 12.52 | 1
February | 11 | 8AM to 9AM | 37.4 | 35.1 | 32 | 26.6 | 13.06 | 0.0796 | 0.18 | 12.61 | 1
February | 11 | 9AM to 10AM | 41 | 36.4 | 30.2 | 24.4 | 13.61 | 0.079 | 0.17 | 12.7 | 1
February | 11 | 10AM to 11AM | 44.6 | 38.4 | 30.2 | 24.4 | 14.48 | 0.0785 | 0.17 | 12.79 | 1
February | 11 | 11AM to 12PM | 48.2 | 41.6 | 33.8 | 28.6 | 15.98 | 0.0779 | 0.19 | 12.89 | 1
February | 11 | 12PM to 1PM | 50 | 42.5 | 33.8 | 28.6 | 16.42 | 0.0776 | 0.19 | 12.94 | 1
February | 11 | 1PM to 2PM | 50 | 43.2 | 35.6 | 30.7 | 16.75 | 0.0776 | 0.21 | 12.94 | 1
February | 11 | 2PM to 3PM | 51.8 | 44.1 | 35.6 | 30.7 | 17.18 | 0.0773 | 0.21 | 12.99 | 1
February | 11 | 3PM to 4PM | 50 | 43.2 | 35.6 | 30.7 | 16.75 | 0.0776 | 0.21 | 12.94 | 1
February | 11 | 4PM to 5PM | 50 | 43.9 | 37.4 | 33 | 17.1 | 0.0776 | 0.22 | 12.95 | 1
February | 11 | 5PM to 6PM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
February | 11 | 6PM to 7PM | 42.8 | 40.3 | 37.4 | 33 | 15.36 | 0.0787 | 0.22 | 12.77 | 1
February | 11 | 7PM to 8PM | 41 | 38.6 | 35.6 | 30.7 | 14.57 | 0.079 | 0.21 | 12.72 | 1
February | 11 | 8PM to 9PM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
February | 11 | 9PM to 10PM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
February | 11 | 10PM to 11PM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
February | 11 | 11PM to 12AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 12 | 12AM to 1AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 12 | 1AM to 2AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 12 | 2AM to 3AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 12 | 3AM to 4AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 12 | 4AM to 5AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 12 | 5AM to 6AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
February | 12 | 6AM to 7AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
February | 12 | 7AM to 8AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
February | 12 | 8AM to 9AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
February | 12 | 9AM to 10AM | 41 | 37.8 | 33.8 | 28.6 | 14.24 | 0.079 | 0.19 | 12.71 | 1
February | 12 | 10AM to 11AM | 42.8 | 39.5 | 35.6 | 30.7 | 15.01 | 0.0787 | 0.21 | 12.76 | 1
February | 12 | 11AM to 12PM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
February | 12 | 12PM to 1PM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
February | 12 | 1PM to 2PM | 50 | 43.9 | 37.4 | 33 | 17.1 | 0.0776 | 0.22 | 12.95 | 1
February | 12 | 2PM to 3PM | 50 | 43.9 | 37.4 | 33 | 17.1 | 0.0776 | 0.22 | 12.95 | 1
February | 12 | 3PM to 4PM | 51.8 | 44.8 | 37.4 | 33 | 17.54 | 0.0773 | 0.22 | 13 | 1
February | 12 | 4PM to 5PM | 51.8 | 44.8 | 37.4 | 33 | 17.54 | 0.0773 | 0.22 | 13 | 1
February | 12 | 5PM to 6PM | 48.2 | 42.3 | 35.6 | 30.7 | 16.31 | 0.0779 | 0.21 | 12.9 | 1
February | 12 | 6PM to 7PM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
February | 12 | 7PM to 8PM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
February | 12 | 8PM to 9PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 12 | 9PM to 10PM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
February | 12 | 10PM to 11PM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
February | 12 | 11PM to 12AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 13 | 12AM to 1AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
February | 13 | 1AM to 2AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
February | 13 | 2AM to 3AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 13 | 3AM to 4AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 13 | 4AM to 5AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 13 | 5AM to 6AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 13 | 6AM to 7AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 13 | 7AM to 8AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
February | 13 | 8AM to 9AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 13 | 9AM to 10AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 13 | 10AM to 11AM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
February | 13 | 11AM to 12PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
February | 13 | 12PM to 1PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 13 | 1PM to 2PM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
February | 13 | 2PM to 3PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 13 | 3PM to 4PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 13 | 4PM to 5PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
February | 13 | 5PM to 6PM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
February | 13 | 6PM to 7PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
February | 13 | 7PM to 8PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 13 | 8PM to 9PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 13 | 9PM to 10PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 13 | 10PM to 11PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 13 | 11PM to 12AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 14 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 14 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 14 | 2AM to 3AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 14 | 3AM to 4AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
February | 14 | 4AM to 5AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
February | 14 | 5AM to 6AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 14 | 6AM to 7AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 14 | 7AM to 8AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
February | 14 | 8AM to 9AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 14 | 9AM to 10AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 14 | 10AM to 11AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 14 | 11AM to 12PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 14 | 12PM to 1PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 14 | 1PM to 2PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 14 | 2PM to 3PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 14 | 3PM to 4PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 14 | 4PM to 5PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
February | 14 | 5PM to 6PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
February | 14 | 6PM to 7PM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
February | 14 | 7PM to 8PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 14 | 8PM to 9PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
February | 14 | 9PM to 10PM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
February | 14 | 10PM to 11PM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 14 | 11PM to 12AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
February | 15 | 12AM to 1AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 15 | 1AM to 2AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 15 | 2AM to 3AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 15 | 3AM to 4AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
February | 15 | 4AM to 5AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
February | 15 | 5AM to 6AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
February | 15 | 6AM to 7AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 15 | 7AM to 8AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 15 | 8AM to 9AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
February | 15 | 9AM to 10AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 15 | 10AM to 11AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 15 | 11AM to 12PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
February | 15 | 12PM to 1PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
February | 15 | 1PM to 2PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 15 | 2PM to 3PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 15 | 3PM to 4PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 15 | 4PM to 5PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 15 | 5PM to 6PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 15 | 6PM to 7PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
February | 15 | 7PM to 8PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
February | 15 | 8PM to 9PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
February | 15 | 9PM to 10PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
February | 15 | 10PM to 11PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
February | 15 | 11PM to 12AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 16 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 16 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 16 | 2AM to 3AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 16 | 3AM to 4AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 16 | 4AM to 5AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 16 | 5AM to 6AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 16 | 6AM to 7AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 16 | 7AM to 8AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 16 | 8AM to 9AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 16 | 9AM to 10AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
February | 16 | 10AM to 11AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 16 | 11AM to 12PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 16 | 12PM to 1PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 1PM to 2PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 2PM to 3PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 3PM to 4PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 4PM to 5PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 5PM to 6PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 6PM to 7PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 7PM to 8PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 8PM to 9PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 16 | 9PM to 10PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 16 | 10PM to 11PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 16 | 11PM to 12AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 17 | 12AM to 1AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 17 | 1AM to 2AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 17 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 17 | 3AM to 4AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 17 | 4AM to 5AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 17 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 17 | 6AM to 7AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 17 | 7AM to 8AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 17 | 8AM to 9AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
February | 17 | 9AM to 10AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
February | 17 | 10AM to 11AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
February | 17 | 11AM to 12PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
February | 17 | 12PM to 1PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
February | 17 | 1PM to 2PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
February | 17 | 2PM to 3PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
February | 17 | 3PM to 4PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
February | 17 | 4PM to 5PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
February | 17 | 5PM to 6PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
February | 17 | 6PM to 7PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 17 | 7PM to 8PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 17 | 8PM to 9PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 17 | 9PM to 10PM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 17 | 10PM to 11PM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 17 | 11PM to 12AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 18 | 12AM to 1AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 18 | 1AM to 2AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 18 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 18 | 3AM to 4AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 18 | 4AM to 5AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 18 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 18 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 18 | 7AM to 8AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 18 | 8AM to 9AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 18 | 9AM to 10AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
February | 18 | 10AM to 11AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
February | 18 | 11AM to 12PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
February | 18 | 12PM to 1PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
February | 18 | 1PM to 2PM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
February | 18 | 2PM to 3PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 18 | 3PM to 4PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
February | 18 | 4PM to 5PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 18 | 5PM to 6PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
February | 18 | 6PM to 7PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 18 | 7PM to 8PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 18 | 8PM to 9PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 18 | 9PM to 10PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 18 | 10PM to 11PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
February | 18 | 11PM to 12AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
February | 19 | 12AM to 1AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 19 | 1AM to 2AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 19 | 2AM to 3AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 19 | 3AM to 4AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 19 | 4AM to 5AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
February | 19 | 5AM to 6AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
February | 19 | 6AM to 7AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
February | 19 | 7AM to 8AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
February | 19 | 8AM to 9AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 19 | 9AM to 10AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 19 | 10AM to 11AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 19 | 11AM to 12PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
February | 19 | 12PM to 1PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
February | 19 | 1PM to 2PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
February | 19 | 2PM to 3PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
February | 19 | 3PM to 4PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
February | 19 | 4PM to 5PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
February | 19 | 5PM to 6PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
February | 19 | 6PM to 7PM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
February | 19 | 7PM to 8PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 19 | 8PM to 9PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 19 | 9PM to 10PM | 42.8 | 40.3 | 37.4 | 33 | 15.36 | 0.0787 | 0.22 | 12.77 | 1
February | 19 | 10PM to 11PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 19 | 11PM to 12AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
February | 20 | 12AM to 1AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 20 | 1AM to 2AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
February | 20 | 2AM to 3AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 20 | 3AM to 4AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 20 | 4AM to 5AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 20 | 5AM to 6AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 20 | 6AM to 7AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
February | 20 | 7AM to 8AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
February | 20 | 8AM to 9AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
February | 20 | 9AM to 10AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 20 | 10AM to 11AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 20 | 11AM to 12PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 20 | 12PM to 1PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 20 | 1PM to 2PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 20 | 2PM to 3PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 20 | 3PM to 4PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 20 | 4PM to 5PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 20 | 5PM to 6PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 20 | 6PM to 7PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 20 | 7PM to 8PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 20 | 8PM to 9PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
February | 20 | 9PM to 10PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 20 | 10PM to 11PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 20 | 11PM to 12AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 21 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 21 | 1AM to 2AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 21 | 2AM to 3AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 21 | 3AM to 4AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 21 | 4AM to 5AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 21 | 5AM to 6AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 21 | 6AM to 7AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
February | 21 | 7AM to 8AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 21 | 8AM to 9AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
February | 21 | 9AM to 10AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
February | 21 | 10AM to 11AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
February | 21 | 11AM to 12PM | 50 | 43.9 | 37.4 | 33 | 17.1 | 0.0776 | 0.22 | 12.95 | 1
February | 21 | 12PM to 1PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
February | 21 | 1PM to 2PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
February | 21 | 2PM to 3PM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
February | 21 | 3PM to 4PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
February | 21 | 4PM to 5PM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
February | 21 | 5PM to 6PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
February | 21 | 6PM to 7PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 21 | 7PM to 8PM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
February | 21 | 8PM to 9PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
February | 21 | 9PM to 10PM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
February | 21 | 10PM to 11PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 21 | 11PM to 12AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
February | 22 | 12AM to 1AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 22 | 1AM to 2AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
February | 22 | 2AM to 3AM | 47.3 | 44.6 | 41.9 | 39.4 | 17.43 | 0.0779 | 0.27 | 12.9 | 1
February | 22 | 3AM to 4AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 22 | 4AM to 5AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 22 | 5AM to 6AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 22 | 6AM to 7AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 22 | 7AM to 8AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 22 | 8AM to 9AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 22 | 9AM to 10AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 22 | 10AM to 11AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 22 | 11AM to 12PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
February | 22 | 12PM to 1PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
February | 22 | 1PM to 2PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
February | 22 | 2PM to 3PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
February | 22 | 3PM to 4PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
February | 22 | 4PM to 5PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
February | 22 | 5PM to 6PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 22 | 6PM to 7PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 22 | 7PM to 8PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 22 | 8PM to 9PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 22 | 9PM to 10PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 22 | 10PM to 11PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 22 | 11PM to 12AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 23 | 12AM to 1AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 23 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 23 | 2AM to 3AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 23 | 3AM to 4AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 23 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 23 | 5AM to 6AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
February | 23 | 6AM to 7AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
February | 23 | 7AM to 8AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 23 | 8AM to 9AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 23 | 9AM to 10AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
February | 23 | 10AM to 11AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
February | 23 | 11AM to 12PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
February | 23 | 12PM to 1PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
February | 23 | 1PM to 2PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
February | 23 | 2PM to 3PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
February | 23 | 3PM to 4PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
February | 23 | 4PM to 5PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
February | 23 | 5PM to 6PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
February | 23 | 6PM to 7PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
February | 23 | 7PM to 8PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
February | 23 | 8PM to 9PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
February | 23 | 9PM to 10PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 23 | 10PM to 11PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
February | 23 | 11PM to 12AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 24 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 24 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 24 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 24 | 3AM to 4AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
February | 24 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 24 | 5AM to 6AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 24 | 6AM to 7AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 24 | 7AM to 8AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
February | 24 | 8AM to 9AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 24 | 9AM to 10AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
February | 24 | 10AM to 11AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
February | 24 | 11AM to 12PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
February | 24 | 12PM to 1PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
February | 24 | 1PM to 2PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
February | 24 | 2PM to 3PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
February | 24 | 3PM to 4PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
February | 24 | 4PM to 5PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
February | 24 | 5PM to 6PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 24 | 6PM to 7PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 24 | 7PM to 8PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 24 | 8PM to 9PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 24 | 9PM to 10PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
February | 24 | 10PM to 11PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 24 | 11PM to 12AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 25 | 12AM to 1AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 25 | 1AM to 2AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
February | 25 | 2AM to 3AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 25 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 25 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 25 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
February | 25 | 6AM to 7AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
February | 25 | 7AM to 8AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
February | 25 | 8AM to 9AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
February | 25 | 9AM to 10AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
February | 25 | 10AM to 11AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 25 | 11AM to 12PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 25 | 12PM to 1PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
February | 25 | 1PM to 2PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
February | 25 | 2PM to 3PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 25 | 3PM to 4PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
February | 25 | 4PM to 5PM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
February | 25 | 5PM to 6PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
February | 25 | 6PM to 7PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 25 | 7PM to 8PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
February | 25 | 8PM to 9PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
February | 25 | 9PM to 10PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
February | 25 | 10PM to 11PM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
February | 25 | 11PM to 12AM | 42.8 | 40.3 | 37.4 | 33 | 15.36 | 0.0787 | 0.22 | 12.77 | 1
February | 26 | 12AM to 1AM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
February | 26 | 1AM to 2AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
February | 26 | 2AM to 3AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 26 | 3AM to 4AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 26 | 4AM to 5AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 26 | 5AM to 6AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 26 | 6AM to 7AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
February | 26 | 7AM to 8AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
February | 26 | 8AM to 9AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
February | 26 | 9AM to 10AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
February | 26 | 10AM to 11AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
February | 26 | 11AM to 12PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 26 | 12PM to 1PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 26 | 1PM to 2PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 26 | 2PM to 3PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 26 | 3PM to 4PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 26 | 4PM to 5PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
February | 26 | 5PM to 6PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
February | 26 | 6PM to 7PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 26 | 7PM to 8PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 26 | 8PM to 9PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 26 | 9PM to 10PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 26 | 10PM to 11PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
February | 26 | 11PM to 12AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 27 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 27 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 27 | 2AM to 3AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
February | 27 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 27 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 27 | 5AM to 6AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
February | 27 | 6AM to 7AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
February | 27 | 7AM to 8AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
February | 27 | 8AM to 9AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
February | 27 | 9AM to 10AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 27 | 10AM to 11AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
February | 27 | 11AM to 12PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
February | 27 | 12PM to 1PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
February | 27 | 1PM to 2PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
February | 27 | 2PM to 3PM | 60.8 | 47.7 | 33.8 | 28.6 | 19.03 | 0.076 | 0.19 | 13.21 | 0
February | 27 | 3PM to 4PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
February | 27 | 4PM to 5PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
February | 27 | 5PM to 6PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
February | 27 | 6PM to 7PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
February | 27 | 7PM to 8PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
February | 27 | 8PM to 9PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
February | 27 | 9PM to 10PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 27 | 10PM to 11PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 27 | 11PM to 12AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 28 | 12AM to 1AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 28 | 1AM to 2AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
February | 28 | 2AM to 3AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
February | 28 | 3AM to 4AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 28 | 4AM to 5AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 28 | 5AM to 6AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 28 | 6AM to 7AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
February | 28 | 7AM to 8AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
February | 28 | 8AM to 9AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
February | 28 | 9AM to 10AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
February | 28 | 10AM to 11AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
February | 28 | 11AM to 12PM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
February | 28 | 12PM to 1PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
February | 28 | 1PM to 2PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
February | 28 | 2PM to 3PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
February | 28 | 3PM to 4PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
February | 28 | 4PM to 5PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
February | 28 | 5PM to 6PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
February | 28 | 6PM to 7PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
February | 28 | 7PM to 8PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 28 | 8PM to 9PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
February | 28 | 9PM to 10PM | 53.1 | 51.9 | 51.1 | 55.9 | 21.39 | 0.077 | 0.38 | 13.1 | 0
February | 28 | 10PM to 11PM | 50.7 | 49.4 | 48.4 | 50.5 | 19.99 | 0.0773 | 0.34 | 13.02 | 1
February | 28 | 11PM to 12AM | 48.4 | 47 | 45.9 | 45.9 | 18.7 | 0.0777 | 0.31 | 12.95 | 1
March | 1 | 12AM to 1AM | 46.2 | 44.8 | 43.3 | 41.6 | 17.52 | 0.0781 | 0.28 | 12.88 | 1
March | 1 | 1AM to 2AM | 43.9 | 42.4 | 40.8 | 37.7 | 16.35 | 0.0785 | 0.26 | 12.81 | 1
March | 1 | 2AM to 3AM | 41.5 | 39.9 | 38.1 | 33.9 | 15.2 | 0.0789 | 0.23 | 12.74 | 1
March | 1 | 3AM to 4AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
March | 1 | 4AM to 5AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
March | 1 | 5AM to 6AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
March | 1 | 6AM to 7AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
March | 1 | 7AM to 8AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
March | 1 | 8AM to 9AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
March | 1 | 9AM to 10AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
March | 1 | 10AM to 11AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
March | 1 | 11AM to 12PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
March | 1 | 12PM to 1PM | 57.2 | 48.1 | 39.2 | 35.4 | 19.22 | 0.0765 | 0.24 | 13.14 | 0
March | 1 | 1PM to 2PM | 57.2 | 48.1 | 39.2 | 35.4 | 19.22 | 0.0765 | 0.24 | 13.14 | 0
March | 1 | 2PM to 3PM | 57.2 | 48.1 | 39.2 | 35.4 | 19.22 | 0.0765 | 0.24 | 13.14 | 0
March | 1 | 3PM to 4PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
March | 1 | 4PM to 5PM | 57.2 | 48.1 | 39.2 | 35.4 | 19.22 | 0.0765 | 0.24 | 13.14 | 0
March | 1 | 5PM to 6PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
March | 1 | 6PM to 7PM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
March | 1 | 7PM to 8PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 1 | 8PM to 9PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
March | 1 | 9PM to 10PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
March | 1 | 10PM to 11PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 1 | 11PM to 12AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 2 | 12AM to 1AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 2 | 1AM to 2AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 2 | 2AM to 3AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 2 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
March | 2 | 4AM to 5AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
March | 2 | 5AM to 6AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
March | 2 | 6AM to 7AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
March | 2 | 7AM to 8AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
March | 2 | 8AM to 9AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
March | 2 | 9AM to 10AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 2 | 10AM to 11AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 2 | 11AM to 12PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 2 | 12PM to 1PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 2 | 1PM to 2PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 2 | 2PM to 3PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
March | 2 | 3PM to 4PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 2 | 4PM to 5PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 2 | 5PM to 6PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 2 | 6PM to 7PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 2 | 7PM to 8PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
March | 2 | 8PM to 9PM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 2 | 9PM to 10PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
March | 2 | 10PM to 11PM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
March | 2 | 11PM to 12AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
March | 3 | 12AM to 1AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
March | 3 | 1AM to 2AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
March | 3 | 2AM to 3AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
March | 3 | 3AM to 4AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
March | 3 | 4AM to 5AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
March | 3 | 5AM to 6AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
March | 3 | 6AM to 7AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
March | 3 | 7AM to 8AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
March | 3 | 8AM to 9AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 3 | 9AM to 10AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
March | 3 | 10AM to 11AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 3 | 11AM to 12PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
March | 3 | 12PM to 1PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 3 | 1PM to 2PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 3 | 2PM to 3PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
March | 3 | 3PM to 4PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
March | 3 | 4PM to 5PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 3 | 5PM to 6PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
March | 3 | 6PM to 7PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 3 | 7PM to 8PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 3 | 8PM to 9PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 3 | 9PM to 10PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 3 | 10PM to 11PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 3 | 11PM to 12AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 4 | 12AM to 1AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 4 | 1AM to 2AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 4 | 2AM to 3AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 4 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 4 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 4 | 5AM to 6AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 4 | 6AM to 7AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 4 | 7AM to 8AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
March | 4 | 8AM to 9AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
March | 4 | 9AM to 10AM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
March | 4 | 10AM to 11AM | 57.2 | 48.1 | 39.2 | 35.4 | 19.22 | 0.0765 | 0.24 | 13.14 | 0
March | 4 | 11AM to 12PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
March | 4 | 12PM to 1PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
March | 4 | 1PM to 2PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
March | 4 | 2PM to 3PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
March | 4 | 3PM to 4PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
March | 4 | 4PM to 5PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 4 | 5PM to 6PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
March | 4 | 6PM to 7PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 4 | 7PM to 8PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 4 | 8PM to 9PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 4 | 9PM to 10PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 4 | 10PM to 11PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 4 | 11PM to 12AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 5 | 12AM to 1AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 5 | 1AM to 2AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
March | 5 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 5 | 3AM to 4AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 5 | 4AM to 5AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 5 | 5AM to 6AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 5 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 5 | 7AM to 8AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 5 | 8AM to 9AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 5 | 9AM to 10AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
March | 5 | 10AM to 11AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
March | 5 | 11AM to 12PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
March | 5 | 12PM to 1PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
March | 5 | 1PM to 2PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
March | 5 | 2PM to 3PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
March | 5 | 3PM to 4PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
March | 5 | 4PM to 5PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 5 | 5PM to 6PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
March | 5 | 6PM to 7PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
March | 5 | 7PM to 8PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
March | 5 | 8PM to 9PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
March | 5 | 9PM to 10PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
March | 5 | 10PM to 11PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
March | 5 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 6 | 12AM to 1AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 6 | 1AM to 2AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 6 | 2AM to 3AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 6 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 6 | 4AM to 5AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 6 | 5AM to 6AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
March | 6 | 6AM to 7AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 6 | 7AM to 8AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
March | 6 | 8AM to 9AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
March | 6 | 9AM to 10AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
March | 6 | 10AM to 11AM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
March | 6 | 11AM to 12PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
March | 6 | 12PM to 1PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
March | 6 | 1PM to 2PM | 63 | 56 | 51.1 | 55.9 | 23.81 | 0.0755 | 0.38 | 13.35 | 0
March | 6 | 2PM to 3PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 6 | 3PM to 4PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
March | 6 | 4PM to 5PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 6 | 5PM to 6PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
March | 6 | 6PM to 7PM | 57.7 | 54.7 | 52.5 | 59 | 23.01 | 0.0762 | 0.4 | 13.23 | 0
March | 6 | 7PM to 8PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
March | 6 | 8PM to 9PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
March | 6 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 6 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 6 | 11PM to 12AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 7 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 7 | 1AM to 2AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
March | 7 | 2AM to 3AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
March | 7 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
March | 7 | 4AM to 5AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
March | 7 | 5AM to 6AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
March | 7 | 6AM to 7AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
March | 7 | 7AM to 8AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 7 | 8AM to 9AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
March | 7 | 9AM to 10AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
March | 7 | 10AM to 11AM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
March | 7 | 11AM to 12PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
March | 7 | 12PM to 1PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
March | 7 | 1PM to 2PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 7 | 2PM to 3PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 7 | 3PM to 4PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 7 | 4PM to 5PM | 64.2 | 58.4 | 54.7 | 63.9 | 25.36 | 0.0753 | 0.43 | 13.41 | 0
March | 7 | 5PM to 6PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
March | 7 | 6PM to 7PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
March | 7 | 7PM to 8PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
March | 7 | 8PM to 9PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
March | 7 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 7 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 7 | 11PM to 12AM | 52.3 | 49.7 | 47.5 | 48.8 | 20.12 | 0.0771 | 0.33 | 13.06 | 0
March | 8 | 12AM to 1AM | 51.4 | 49.1 | 47.1 | 48.1 | 19.8 | 0.0773 | 0.33 | 13.03 | 1
March | 8 | 1AM to 2AM | 50.7 | 48.5 | 46.6 | 47.1 | 19.47 | 0.0774 | 0.32 | 13.01 | 1
March | 8 | 2AM to 3AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 8 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 8 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 8 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
March | 8 | 6AM to 7AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 8 | 7AM to 8AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 8 | 8AM to 9AM | 53.8 | 50.8 | 48.4 | 50.5 | 20.73 | 0.0769 | 0.34 | 13.1 | 0
March | 8 | 9AM to 10AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
March | 8 | 10AM to 11AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
March | 8 | 11AM to 12PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
March | 8 | 12PM to 1PM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
March | 8 | 1PM to 2PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
March | 8 | 2PM to 3PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
March | 8 | 3PM to 4PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
March | 8 | 4PM to 5PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
March | 8 | 5PM to 6PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
March | 8 | 6PM to 7PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
March | 8 | 7PM to 8PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
March | 8 | 8PM to 9PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 8 | 9PM to 10PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
March | 8 | 10PM to 11PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 8 | 11PM to 12AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 9 | 12AM to 1AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 9 | 1AM to 2AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 9 | 2AM to 3AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
March | 9 | 3AM to 4AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
March | 9 | 4AM to 5AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
March | 9 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
March | 9 | 6AM to 7AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
March | 9 | 7AM to 8AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 9 | 8AM to 9AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 9 | 9AM to 10AM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
March | 9 | 10AM to 11AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
March | 9 | 11AM to 12PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
March | 9 | 12PM to 1PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
March | 9 | 1PM to 2PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
March | 9 | 2PM to 3PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
March | 9 | 3PM to 4PM | 60.8 | 48.4 | 35.6 | 30.7 | 19.36 | 0.076 | 0.21 | 13.22 | 0
March | 9 | 4PM to 5PM | 60.8 | 48.4 | 35.6 | 30.7 | 19.36 | 0.076 | 0.21 | 13.22 | 0
March | 9 | 5PM to 6PM | 55.4 | 47 | 38.5 | 34.4 | 18.63 | 0.0768 | 0.23 | 13.09 | 0
March | 9 | 6PM to 7PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
March | 9 | 7PM to 8PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
March | 9 | 8PM to 9PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
March | 9 | 9PM to 10PM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
March | 9 | 10PM to 11PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
March | 9 | 11PM to 12AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
March | 10 | 12AM to 1AM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
March | 10 | 1AM to 2AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
March | 10 | 2AM to 3AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
March | 10 | 3AM to 4AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
March | 10 | 4AM to 5AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
March | 10 | 5AM to 6AM | 44.6 | 39.8 | 33.8 | 28.6 | 15.11 | 0.0784 | 0.19 | 12.8 | 1
March | 10 | 6AM to 7AM | 44.6 | 39.8 | 33.8 | 28.6 | 15.11 | 0.0784 | 0.19 | 12.8 | 1
March | 10 | 7AM to 8AM | 46.4 | 40.7 | 33.8 | 28.6 | 15.55 | 0.0782 | 0.19 | 12.85 | 1
March | 10 | 8AM to 9AM | 51.8 | 44.1 | 35.6 | 30.7 | 17.18 | 0.0773 | 0.21 | 12.99 | 1
March | 10 | 9AM to 10AM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
March | 10 | 10AM to 11AM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
March | 10 | 11AM to 12PM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
March | 10 | 12PM to 1PM | 62.6 | 51.2 | 41 | 38 | 20.93 | 0.0757 | 0.26 | 13.29 | 0
March | 10 | 1PM to 2PM | 64.4 | 50.6 | 37.4 | 33 | 20.59 | 0.0754 | 0.22 | 13.32 | 0
March | 10 | 2PM to 3PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
March | 10 | 3PM to 4PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
March | 10 | 4PM to 5PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
March | 10 | 5PM to 6PM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
March | 10 | 6PM to 7PM | 59 | 48.2 | 37.4 | 33 | 19.28 | 0.0762 | 0.22 | 13.18 | 0
March | 10 | 7PM to 8PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
March | 10 | 8PM to 9PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
March | 10 | 9PM to 10PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
March | 10 | 10PM to 11PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
March | 10 | 11PM to 12AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
March | 11 | 12AM to 1AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
March | 11 | 1AM to 2AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 11 | 2AM to 3AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 11 | 3AM to 4AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 11 | 4AM to 5AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
March | 11 | 5AM to 6AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
March | 11 | 6AM to 7AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 11 | 7AM to 8AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 11 | 8AM to 9AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 11 | 9AM to 10AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
March | 11 | 10AM to 11AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
March | 11 | 11AM to 12PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
March | 11 | 12PM to 1PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
March | 11 | 1PM to 2PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
March | 11 | 2PM to 3PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
March | 11 | 3PM to 4PM | 66.2 | 52.7 | 41 | 38 | 21.81 | 0.0752 | 0.26 | 13.38 | 0
March | 11 | 4PM to 5PM | 64.4 | 50.6 | 37.4 | 33 | 20.59 | 0.0754 | 0.22 | 13.32 | 0
March | 11 | 5PM to 6PM | 60.8 | 50.4 | 41 | 38 | 20.5 | 0.0759 | 0.26 | 13.24 | 0
March | 11 | 6PM to 7PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
March | 11 | 7PM to 8PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
March | 11 | 8PM to 9PM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
March | 11 | 9PM to 10PM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
March | 11 | 10PM to 11PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
March | 11 | 11PM to 12AM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
March | 12 | 12AM to 1AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
March | 12 | 1AM to 2AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
March | 12 | 2AM to 3AM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
March | 12 | 3AM to 4AM | 41 | 38.6 | 35.6 | 30.7 | 14.57 | 0.079 | 0.21 | 12.72 | 1
March | 12 | 4AM to 5AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
March | 12 | 5AM to 6AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
March | 12 | 6AM to 7AM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
March | 12 | 7AM to 8AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
March | 12 | 8AM to 9AM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
March | 12 | 9AM to 10AM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
March | 12 | 10AM to 11AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
March | 12 | 11AM to 12PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
March | 12 | 12PM to 1PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
March | 12 | 1PM to 2PM | 64.4 | 52 | 41 | 38 | 21.37 | 0.0754 | 0.26 | 13.33 | 0
March | 12 | 2PM to 3PM | 66.2 | 52.7 | 41 | 38 | 21.81 | 0.0752 | 0.26 | 13.38 | 0
March | 12 | 3PM to 4PM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
March | 12 | 4PM to 5PM | 66.2 | 52 | 39.2 | 35.4 | 21.4 | 0.0752 | 0.24 | 13.37 | 0
March | 12 | 5PM to 6PM | 62.6 | 51.2 | 41 | 38 | 20.93 | 0.0757 | 0.26 | 13.29 | 0
March | 12 | 6PM to 7PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
March | 12 | 7PM to 8PM | 59 | 48.9 | 39.2 | 35.4 | 19.66 | 0.0762 | 0.24 | 13.19 | 0
March | 12 | 8PM to 9PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
March | 12 | 9PM to 10PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
March | 12 | 10PM to 11PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 12 | 11PM to 12AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
March | 13 | 12AM to 1AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 13 | 1AM to 2AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 13 | 2AM to 3AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
March | 13 | 3AM to 4AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
March | 13 | 4AM to 5AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
March | 13 | 5AM to 6AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
March | 13 | 6AM to 7AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
March | 13 | 7AM to 8AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
March | 13 | 8AM to 9AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 13 | 9AM to 10AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
March | 13 | 10AM to 11AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
March | 13 | 11AM to 12PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
March | 13 | 12PM to 1PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
March | 13 | 1PM to 2PM | 66.2 | 54.2 | 44.6 | 43.7 | 22.69 | 0.0751 | 0.3 | 13.4 | 0
March | 13 | 2PM to 3PM | 68 | 55 | 44.6 | 43.7 | 23.13 | 0.0749 | 0.3 | 13.44 | 0
March | 13 | 3PM to 4PM | 68 | 56.6 | 48.2 | 50.1 | 24.14 | 0.0748 | 0.34 | 13.46 | 0
March | 13 | 4PM to 5PM | 68 | 56.6 | 48.2 | 50.1 | 24.14 | 0.0748 | 0.34 | 13.46 | 0
March | 13 | 5PM to 6PM | 66.2 | 54.2 | 44.6 | 43.7 | 22.69 | 0.0751 | 0.3 | 13.4 | 0
March | 13 | 6PM to 7PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
March | 13 | 7PM to 8PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
March | 13 | 8PM to 9PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
March | 13 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 13 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 13 | 11PM to 12AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 14 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 14 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
March | 14 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 14 | 3AM to 4AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
March | 14 | 4AM to 5AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
March | 14 | 5AM to 6AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
March | 14 | 6AM to 7AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 14 | 7AM to 8AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 14 | 8AM to 9AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 14 | 9AM to 10AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 14 | 10AM to 11AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
March | 14 | 11AM to 12PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
March | 14 | 12PM to 1PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
March | 14 | 1PM to 2PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
March | 14 | 2PM to 3PM | 69.8 | 53.6 | 39.2 | 35.4 | 22.27 | 0.0747 | 0.24 | 13.46 | 0
March | 14 | 3PM to 4PM | 69.8 | 54.9 | 42.8 | 40.8 | 23.11 | 0.0746 | 0.28 | 13.48 | 0
March | 14 | 4PM to 5PM | 68 | 55.7 | 46.4 | 46.8 | 23.62 | 0.0748 | 0.32 | 13.45 | 0
March | 14 | 5PM to 6PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
March | 14 | 6PM to 7PM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
March | 14 | 7PM to 8PM | 60.8 | 48.4 | 35.6 | 30.7 | 19.36 | 0.076 | 0.21 | 13.22 | 0
March | 14 | 8PM to 9PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
March | 14 | 9PM to 10PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
March | 14 | 10PM to 11PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 14 | 11PM to 12AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
March | 15 | 12AM to 1AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
March | 15 | 1AM to 2AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
March | 15 | 2AM to 3AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
March | 15 | 3AM to 4AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 15 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
March | 15 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
March | 15 | 6AM to 7AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
March | 15 | 7AM to 8AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 15 | 8AM to 9AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 15 | 9AM to 10AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 15 | 10AM to 11AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
March | 15 | 11AM to 12PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
March | 15 | 12PM to 1PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
March | 15 | 1PM to 2PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
March | 15 | 2PM to 3PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
March | 15 | 3PM to 4PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
March | 15 | 4PM to 5PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
March | 15 | 5PM to 6PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
March | 15 | 6PM to 7PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
March | 15 | 7PM to 8PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 15 | 8PM to 9PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 15 | 9PM to 10PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 15 | 10PM to 11PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 15 | 11PM to 12AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
March | 16 | 12AM to 1AM | 44.6 | 44.1 | 43.7 | 42.2 | 17.22 | 0.0783 | 0.29 | 12.84 | 1
March | 16 | 1AM to 2AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
March | 16 | 2AM to 3AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
March | 16 | 3AM to 4AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
March | 16 | 4AM to 5AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
March | 16 | 5AM to 6AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
March | 16 | 6AM to 7AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
March | 16 | 7AM to 8AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
March | 16 | 8AM to 9AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
March | 16 | 9AM to 10AM | 57.2 | 48.1 | 39.2 | 35.4 | 19.22 | 0.0765 | 0.24 | 13.14 | 0
March | 16 | 10AM to 11AM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.2 | 0
March | 16 | 11AM to 12PM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
March | 16 | 12PM to 1PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
March | 16 | 1PM to 2PM | 64.4 | 50.6 | 37.4 | 33 | 20.59 | 0.0754 | 0.22 | 13.32 | 0
March | 16 | 2PM to 3PM | 64.4 | 50 | 35.6 | 30.7 | 20.23 | 0.0755 | 0.21 | 13.31 | 0
March | 16 | 3PM to 4PM | 66.2 | 50.8 | 35.6 | 30.7 | 20.67 | 0.0752 | 0.21 | 13.36 | 0
March | 16 | 4PM to 5PM | 64.4 | 49.4 | 33.8 | 28.6 | 19.9 | 0.0755 | 0.19 | 13.3 | 0
March | 16 | 5PM to 6PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
March | 16 | 6PM to 7PM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
March | 16 | 7PM to 8PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
March | 16 | 8PM to 9PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
March | 16 | 9PM to 10PM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
March | 16 | 10PM to 11PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
March | 16 | 11PM to 12AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
March | 17 | 12AM to 1AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
March | 17 | 1AM to 2AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 17 | 2AM to 3AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 17 | 3AM to 4AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 17 | 4AM to 5AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
March | 17 | 5AM to 6AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
March | 17 | 6AM to 7AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
March | 17 | 7AM to 8AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 17 | 8AM to 9AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
March | 17 | 9AM to 10AM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
March | 17 | 10AM to 11AM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
March | 17 | 11AM to 12PM | 66.2 | 53.5 | 42.8 | 40.8 | 22.24 | 0.0751 | 0.28 | 13.39 | 0
March | 17 | 12PM to 1PM | 68 | 55 | 44.6 | 43.7 | 23.13 | 0.0749 | 0.3 | 13.44 | 0
March | 17 | 1PM to 2PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
March | 17 | 2PM to 3PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
March | 17 | 3PM to 4PM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
March | 17 | 4PM to 5PM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
March | 17 | 5PM to 6PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 17 | 6PM to 7PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
March | 17 | 7PM to 8PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
March | 17 | 8PM to 9PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
March | 17 | 9PM to 10PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
March | 17 | 10PM to 11PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
March | 17 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 18 | 12AM to 1AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 18 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 18 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 18 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
March | 18 | 4AM to 5AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
March | 18 | 5AM to 6AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
March | 18 | 6AM to 7AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 18 | 7AM to 8AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
March | 18 | 8AM to 9AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
March | 18 | 9AM to 10AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
March | 18 | 10AM to 11AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
March | 18 | 11AM to 12PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
March | 18 | 12PM to 1PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
March | 18 | 1PM to 2PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
March | 18 | 2PM to 3PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
March | 18 | 3PM to 4PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
March | 18 | 4PM to 5PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
March | 18 | 5PM to 6PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
March | 18 | 6PM to 7PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
March | 18 | 7PM to 8PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
March | 18 | 8PM to 9PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 18 | 9PM to 10PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
March | 18 | 10PM to 11PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
March | 18 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 19 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 19 | 1AM to 2AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
March | 19 | 2AM to 3AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
March | 19 | 3AM to 4AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 19 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 19 | 5AM to 6AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 19 | 6AM to 7AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 19 | 7AM to 8AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
March | 19 | 8AM to 9AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
March | 19 | 9AM to 10AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
March | 19 | 10AM to 11AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
March | 19 | 11AM to 12PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
March | 19 | 12PM to 1PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
March | 19 | 1PM to 2PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
March | 19 | 2PM to 3PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
March | 19 | 3PM to 4PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
March | 19 | 4PM to 5PM | 73.4 | 66.2 | 62.6 | 85.3 | 30.94 | 0.0738 | 0.57 | 13.71 | 0
March | 19 | 5PM to 6PM | 71.6 | 64.5 | 60.8 | 79.9 | 29.67 | 0.0741 | 0.54 | 13.64 | 0
March | 19 | 6PM to 7PM | 66.2 | 61.6 | 59 | 74.9 | 27.55 | 0.0749 | 0.5 | 13.49 | 0
March | 19 | 7PM to 8PM | 66.2 | 62.7 | 60.8 | 79.9 | 28.34 | 0.0749 | 0.54 | 13.51 | 0
March | 19 | 8PM to 9PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
March | 19 | 9PM to 10PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
March | 19 | 10PM to 11PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
March | 19 | 11PM to 12AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
March | 20 | 12AM to 1AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 20 | 1AM to 2AM | 55.4 | 55.4 | 55.4 | 65.6 | 23.48 | 0.0765 | 0.44 | 13.19 | 0
March | 20 | 2AM to 3AM | 55.4 | 55.4 | 55.4 | 65.6 | 23.48 | 0.0765 | 0.44 | 13.19 | 0
March | 20 | 3AM to 4AM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
March | 20 | 4AM to 5AM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
March | 20 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
March | 20 | 6AM to 7AM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
March | 20 | 7AM to 8AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
March | 20 | 8AM to 9AM | 62.6 | 60.3 | 59 | 74.9 | 26.67 | 0.0754 | 0.5 | 13.4 | 0
March | 20 | 9AM to 10AM | 66.2 | 61.6 | 59 | 74.9 | 27.55 | 0.0749 | 0.5 | 13.49 | 0
March | 20 | 10AM to 11AM | 69.8 | 63.9 | 60.8 | 79.9 | 29.22 | 0.0744 | 0.54 | 13.6 | 0
March | 20 | 11AM to 12PM | 71.6 | 63.5 | 59 | 74.9 | 28.88 | 0.0742 | 0.5 | 13.63 | 0
March | 20 | 12PM to 1PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
March | 20 | 1PM to 2PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
March | 20 | 2PM to 3PM | 77 | 65.3 | 59 | 74.9 | 30.2 | 0.0734 | 0.5 | 13.77 | 0
March | 20 | 3PM to 4PM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
March | 20 | 4PM to 5PM | 75.2 | 65.7 | 60.8 | 79.9 | 30.55 | 0.0736 | 0.54 | 13.74 | 0
March | 20 | 5PM to 6PM | 73.4 | 65.1 | 60.8 | 79.9 | 30.11 | 0.0739 | 0.54 | 13.69 | 0
March | 20 | 6PM to 7PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
March | 20 | 7PM to 8PM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.54 | 0
March | 20 | 8PM to 9PM | 66.2 | 61.6 | 59 | 74.9 | 27.55 | 0.0749 | 0.5 | 13.49 | 0
March | 20 | 9PM to 10PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
March | 20 | 10PM to 11PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
March | 20 | 11PM to 12AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
March | 21 | 12AM to 1AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
March | 21 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
March | 21 | 2AM to 3AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
March | 21 | 3AM to 4AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 21 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 21 | 5AM to 6AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 21 | 6AM to 7AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
March | 21 | 7AM to 8AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
March | 21 | 8AM to 9AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
March | 21 | 9AM to 10AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
March | 21 | 10AM to 11AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
March | 21 | 11AM to 12PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
March | 21 | 12PM to 1PM | 75.2 | 64.7 | 59 | 74.9 | 29.76 | 0.0737 | 0.5 | 13.72 | 0
March | 21 | 1PM to 2PM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
March | 21 | 2PM to 3PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
March | 21 | 3PM to 4PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
March | 21 | 4PM to 5PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
March | 21 | 5PM to 6PM | 69.8 | 63.9 | 60.8 | 79.9 | 29.22 | 0.0744 | 0.54 | 13.6 | 0
March | 21 | 6PM to 7PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
March | 21 | 7PM to 8PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
March | 21 | 8PM to 9PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
March | 21 | 9PM to 10PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
March | 21 | 10PM to 11PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 21 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
March | 22 | 12AM to 1AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
March | 22 | 1AM to 2AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
March | 22 | 2AM to 3AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
March | 22 | 3AM to 4AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 22 | 4AM to 5AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 22 | 5AM to 6AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
March | 22 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 22 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 22 | 8AM to 9AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
March | 22 | 9AM to 10AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
March | 22 | 10AM to 11AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
March | 22 | 11AM to 12PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
March | 22 | 12PM to 1PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
March | 22 | 1PM to 2PM | 69.8 | 62.9 | 59 | 74.9 | 28.44 | 0.0744 | 0.5 | 13.58 | 0
March | 22 | 2PM to 3PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
March | 22 | 3PM to 4PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
March | 22 | 4PM to 5PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
March | 22 | 5PM to 6PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
March | 22 | 6PM to 7PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
March | 22 | 7PM to 8PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 22 | 8PM to 9PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
March | 22 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 22 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 22 | 11PM to 12AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 23 | 12AM to 1AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 23 | 1AM to 2AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 23 | 2AM to 3AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 23 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 23 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 23 | 5AM to 6AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 23 | 6AM to 7AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
March | 23 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 23 | 8AM to 9AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
March | 23 | 9AM to 10AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
March | 23 | 10AM to 11AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
March | 23 | 11AM to 12PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
March | 23 | 12PM to 1PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
March | 23 | 1PM to 2PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
March | 23 | 2PM to 3PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
March | 23 | 3PM to 4PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
March | 23 | 4PM to 5PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
March | 23 | 5PM to 6PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 23 | 6PM to 7PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
March | 23 | 7PM to 8PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
March | 23 | 8PM to 9PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
March | 23 | 9PM to 10PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
March | 23 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 23 | 11PM to 12AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 24 | 12AM to 1AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 24 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 24 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 24 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 24 | 4AM to 5AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 24 | 5AM to 6AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 24 | 6AM to 7AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 24 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
March | 24 | 8AM to 9AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
March | 24 | 9AM to 10AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
March | 24 | 10AM to 11AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
March | 24 | 11AM to 12PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
March | 24 | 12PM to 1PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
March | 24 | 1PM to 2PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
March | 24 | 2PM to 3PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
March | 24 | 3PM to 4PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
March | 24 | 4PM to 5PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
March | 24 | 5PM to 6PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
March | 24 | 6PM to 7PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
March | 24 | 7PM to 8PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
March | 24 | 8PM to 9PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
March | 24 | 9PM to 10PM | 59 | 57.9 | 57.2 | 70.1 | 25.05 | 0.076 | 0.47 | 13.29 | 0
March | 24 | 10PM to 11PM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
March | 24 | 11PM to 12AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
March | 25 | 12AM to 1AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
March | 25 | 1AM to 2AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 25 | 2AM to 3AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 25 | 3AM to 4AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 25 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
March | 25 | 5AM to 6AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
March | 25 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 25 | 7AM to 8AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
March | 25 | 8AM to 9AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
March | 25 | 9AM to 10AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
March | 25 | 10AM to 11AM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
March | 25 | 11AM to 12PM | 66.2 | 51.4 | 37.4 | 33 | 21.02 | 0.0752 | 0.22 | 13.36 | 0
March | 25 | 12PM to 1PM | 66.2 | 50.8 | 35.6 | 30.7 | 20.67 | 0.0752 | 0.21 | 13.36 | 0
March | 25 | 1PM to 2PM | 66.2 | 52 | 39.2 | 35.4 | 21.4 | 0.0752 | 0.24 | 13.37 | 0
March | 25 | 2PM to 3PM | 68 | 53.5 | 41 | 38 | 22.24 | 0.0749 | 0.26 | 13.42 | 0
March | 25 | 3PM to 4PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
March | 25 | 4PM to 5PM | 64.4 | 52 | 41 | 38 | 21.37 | 0.0754 | 0.26 | 13.33 | 0
March | 25 | 5PM to 6PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
March | 25 | 6PM to 7PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
March | 25 | 7PM to 8PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
March | 25 | 8PM to 9PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
March | 25 | 9PM to 10PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
March | 25 | 10PM to 11PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
March | 25 | 11PM to 12AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
March | 26 | 12AM to 1AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
March | 26 | 1AM to 2AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
March | 26 | 2AM to 3AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
March | 26 | 3AM to 4AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
March | 26 | 4AM to 5AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
March | 26 | 5AM to 6AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
March | 26 | 6AM to 7AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
March | 26 | 7AM to 8AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
March | 26 | 8AM to 9AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
March | 26 | 9AM to 10AM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
March | 26 | 10AM to 11AM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
March | 26 | 11AM to 12PM | 66.2 | 53.5 | 42.8 | 40.8 | 22.24 | 0.0751 | 0.28 | 13.39 | 0
March | 26 | 12PM to 1PM | 68 | 53.5 | 41 | 38 | 22.24 | 0.0749 | 0.26 | 13.42 | 0
March | 26 | 1PM to 2PM | 69.8 | 53.6 | 39.2 | 35.4 | 22.27 | 0.0747 | 0.24 | 13.46 | 0
March | 26 | 2PM to 3PM | 71.6 | 53.7 | 37.4 | 33 | 22.33 | 0.0744 | 0.22 | 13.5 | 0
March | 26 | 3PM to 4PM | 71.6 | 52 | 32 | 26.6 | 21.33 | 0.0745 | 0.18 | 13.48 | 0
March | 26 | 4PM to 5PM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
March | 26 | 5PM to 6PM | 66.2 | 52 | 39.2 | 35.4 | 21.4 | 0.0752 | 0.24 | 13.37 | 0
March | 26 | 6PM to 7PM | 62.6 | 49.8 | 37.4 | 33 | 20.15 | 0.0757 | 0.22 | 13.27 | 0
March | 26 | 7PM to 8PM | 59 | 48.2 | 37.4 | 33 | 19.28 | 0.0762 | 0.22 | 13.18 | 0
March | 26 | 8PM to 9PM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
March | 26 | 9PM to 10PM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
March | 26 | 10PM to 11PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
March | 26 | 11PM to 12AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
March | 27 | 12AM to 1AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
March | 27 | 1AM to 2AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
March | 27 | 2AM to 3AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
March | 27 | 3AM to 4AM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
March | 27 | 4AM to 5AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
March | 27 | 5AM to 6AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
March | 27 | 6AM to 7AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
March | 27 | 7AM to 8AM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
March | 27 | 8AM to 9AM | 57.2 | 48.1 | 39.2 | 35.4 | 19.22 | 0.0765 | 0.24 | 13.14 | 0
March | 27 | 9AM to 10AM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
March | 27 | 10AM to 11AM | 66.2 | 52.7 | 41 | 38 | 21.81 | 0.0752 | 0.26 | 13.38 | 0
March | 27 | 11AM to 12PM | 71.6 | 53.7 | 37.4 | 33 | 22.33 | 0.0744 | 0.22 | 13.5 | 0
March | 27 | 12PM to 1PM | 73.4 | 54.4 | 37.4 | 33 | 22.77 | 0.0742 | 0.22 | 13.55 | 0
March | 27 | 1PM to 2PM | 75.2 | 54.6 | 35.6 | 30.7 | 22.85 | 0.0739 | 0.21 | 13.58 | 0
March | 27 | 2PM to 3PM | 75.2 | 55.7 | 39.2 | 35.4 | 23.58 | 0.0739 | 0.24 | 13.6 | 0
March | 27 | 3PM to 4PM | 75.2 | 55.7 | 39.2 | 35.4 | 23.58 | 0.0739 | 0.24 | 13.6 | 0
March | 27 | 4PM to 5PM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
March | 27 | 5PM to 6PM | 71.6 | 55.7 | 42.8 | 40.8 | 23.55 | 0.0744 | 0.28 | 13.52 | 0
March | 27 | 6PM to 7PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 27 | 7PM to 8PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
March | 27 | 8PM to 9PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
March | 27 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
March | 27 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 27 | 11PM to 12AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
March | 28 | 12AM to 1AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
March | 28 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 28 | 2AM to 3AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 28 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
March | 28 | 4AM to 5AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
March | 28 | 5AM to 6AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
March | 28 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
March | 28 | 7AM to 8AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
March | 28 | 8AM to 9AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
March | 28 | 9AM to 10AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
March | 28 | 10AM to 11AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
March | 28 | 11AM to 12PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
March | 28 | 12PM to 1PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
March | 28 | 1PM to 2PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
March | 28 | 2PM to 3PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
March | 28 | 3PM to 4PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
March | 28 | 4PM to 5PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
March | 28 | 5PM to 6PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
March | 28 | 6PM to 7PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
March | 28 | 7PM to 8PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
March | 28 | 8PM to 9PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
March | 28 | 9PM to 10PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
March | 28 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
March | 28 | 11PM to 12AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
March | 29 | 12AM to 1AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
March | 29 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 29 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 29 | 3AM to 4AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
March | 29 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
March | 29 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
March | 29 | 6AM to 7AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
March | 29 | 7AM to 8AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
March | 29 | 8AM to 9AM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
March | 29 | 9AM to 10AM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
March | 29 | 10AM to 11AM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
March | 29 | 11AM to 12PM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
March | 29 | 12PM to 1PM | 77 | 60 | 48.2 | 50.1 | 26.32 | 0.0736 | 0.34 | 13.69 | 0
March | 29 | 1PM to 2PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
March | 29 | 2PM to 3PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
March | 29 | 3PM to 4PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
March | 29 | 4PM to 5PM | 78.8 | 57.8 | 41 | 38 | 24.86 | 0.0734 | 0.26 | 13.7 | 0
March | 29 | 5PM to 6PM | 75.2 | 56.4 | 41 | 38 | 23.99 | 0.0739 | 0.26 | 13.61 | 0
March | 29 | 6PM to 7PM | 66.2 | 52 | 39.2 | 35.4 | 21.4 | 0.0752 | 0.24 | 13.37 | 0
March | 29 | 7PM to 8PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
March | 29 | 8PM to 9PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
March | 29 | 9PM to 10PM | 60.8 | 50.4 | 41 | 38 | 20.5 | 0.0759 | 0.26 | 13.24 | 0
March | 29 | 10PM to 11PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
March | 29 | 11PM to 12AM | 62.6 | 51.2 | 41 | 38 | 20.93 | 0.0757 | 0.26 | 13.29 | 0
March | 30 | 12AM to 1AM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
March | 30 | 1AM to 2AM | 55.4 | 48 | 41 | 38 | 19.19 | 0.0767 | 0.26 | 13.1 | 0
March | 30 | 2AM to 3AM | 55.4 | 48 | 41 | 38 | 19.19 | 0.0767 | 0.26 | 13.1 | 0
March | 30 | 3AM to 4AM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
March | 30 | 4AM to 5AM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
March | 30 | 5AM to 6AM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
March | 30 | 6AM to 7AM | 55.4 | 48 | 41 | 38 | 19.19 | 0.0767 | 0.26 | 13.1 | 0
March | 30 | 7AM to 8AM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
March | 30 | 8AM to 9AM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
March | 30 | 9AM to 10AM | 69.8 | 55.7 | 44.6 | 43.7 | 23.57 | 0.0746 | 0.3 | 13.49 | 0
March | 30 | 10AM to 11AM | 73.4 | 57.1 | 44.6 | 43.7 | 24.44 | 0.0741 | 0.3 | 13.58 | 0
March | 30 | 11AM to 12PM | 75.2 | 57.8 | 44.6 | 43.7 | 24.88 | 0.0739 | 0.3 | 13.63 | 0
March | 30 | 12PM to 1PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
March | 30 | 1PM to 2PM | 80.6 | 57.3 | 37.4 | 33 | 24.51 | 0.0732 | 0.22 | 13.73 | 0
March | 30 | 2PM to 3PM | 82.4 | 56.9 | 33.8 | 28.6 | 24.25 | 0.073 | 0.19 | 13.76 | 0
March | 30 | 3PM to 4PM | 82.4 | 56.9 | 33.8 | 28.6 | 24.25 | 0.073 | 0.19 | 13.76 | 0
March | 30 | 4PM to 5PM | 80.6 | 55.7 | 32 | 26.6 | 23.5 | 0.0732 | 0.18 | 13.71 | 0
March | 30 | 5PM to 6PM | 73.4 | 55 | 39.2 | 35.4 | 23.15 | 0.0742 | 0.24 | 13.55 | 0
March | 30 | 6PM to 7PM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
March | 30 | 7PM to 8PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
March | 30 | 8PM to 9PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
March | 30 | 9PM to 10PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
March | 30 | 10PM to 11PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
March | 30 | 11PM to 12AM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
March | 31 | 12AM to 1AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
March | 31 | 1AM to 2AM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
March | 31 | 2AM to 3AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 31 | 3AM to 4AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
March | 31 | 4AM to 5AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
March | 31 | 5AM to 6AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
March | 31 | 6AM to 7AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
March | 31 | 7AM to 8AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
March | 31 | 8AM to 9AM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
March | 31 | 9AM to 10AM | 70 | 57 | 47.5 | 48.8 | 24.41 | 0.0745 | 0.33 | 13.51 | 0
March | 31 | 10AM to 11AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
March | 31 | 11AM to 12PM | 77 | 60 | 48.2 | 50.1 | 26.32 | 0.0736 | 0.34 | 13.69 | 0
March | 31 | 12PM to 1PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
March | 31 | 1PM to 2PM | 82.4 | 62.7 | 50 | 53.7 | 28.19 | 0.0728 | 0.36 | 13.84 | 0
March | 31 | 2PM to 3PM | 84.2 | 61.8 | 46.4 | 46.8 | 27.55 | 0.0726 | 0.32 | 13.86 | 0
March | 31 | 3PM to 4PM | 84.2 | 61.8 | 46.4 | 46.8 | 27.55 | 0.0726 | 0.32 | 13.86 | 0
March | 31 | 4PM to 5PM | 82.4 | 61.9 | 48.2 | 50.1 | 27.64 | 0.0728 | 0.34 | 13.83 | 0
March | 31 | 5PM to 6PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
March | 31 | 6PM to 7PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
March | 31 | 7PM to 8PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
March | 31 | 8PM to 9PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
March | 31 | 9PM to 10PM | 58.8 | 54.6 | 51.6 | 57 | 22.97 | 0.0761 | 0.39 | 13.25 | 0
March | 31 | 10PM to 11PM | 56.7 | 52.6 | 49.5 | 52.6 | 21.76 | 0.0764 | 0.36 | 13.18 | 0
March | 31 | 11PM to 12AM | 54.7 | 50.7 | 47.5 | 48.8 | 20.69 | 0.0768 | 0.33 | 13.12 | 0
April | 1 | 12AM to 1AM | 52.5 | 48.7 | 45.3 | 44.9 | 19.56 | 0.0771 | 0.3 | 13.05 | 0
April | 1 | 1AM to 2AM | 50.5 | 46.8 | 43.3 | 41.6 | 18.57 | 0.0774 | 0.28 | 12.99 | 1
April | 1 | 2AM to 3AM | 48.4 | 44.8 | 41.2 | 38.3 | 17.53 | 0.0778 | 0.26 | 12.93 | 1
April | 1 | 3AM to 4AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
April | 1 | 4AM to 5AM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
April | 1 | 5AM to 6AM | 48.2 | 42.3 | 35.6 | 30.7 | 16.31 | 0.0779 | 0.21 | 12.9 | 1
April | 1 | 6AM to 7AM | 50 | 43.2 | 35.6 | 30.7 | 16.75 | 0.0776 | 0.21 | 12.94 | 1
April | 1 | 7AM to 8AM | 53.6 | 45 | 35.6 | 30.7 | 17.62 | 0.077 | 0.21 | 13.04 | 0
April | 1 | 8AM to 9AM | 57.2 | 46.7 | 35.6 | 30.7 | 18.49 | 0.0765 | 0.21 | 13.13 | 0
April | 1 | 9AM to 10AM | 62.6 | 49.2 | 35.6 | 30.7 | 19.8 | 0.0757 | 0.21 | 13.26 | 0
April | 1 | 10AM to 11AM | 64.4 | 49.4 | 33.8 | 28.6 | 19.9 | 0.0755 | 0.19 | 13.3 | 0
April | 1 | 11AM to 12PM | 66.2 | 50.8 | 35.6 | 30.7 | 20.67 | 0.0752 | 0.21 | 13.36 | 0
April | 1 | 12PM to 1PM | 66.2 | 50.2 | 33.8 | 28.6 | 20.34 | 0.0752 | 0.19 | 13.35 | 0
April | 1 | 1PM to 2PM | 69.8 | 51.7 | 33.8 | 28.6 | 21.21 | 0.0747 | 0.19 | 13.44 | 0
April | 1 | 2PM to 3PM | 69.8 | 50.6 | 30.2 | 24.4 | 20.56 | 0.0747 | 0.17 | 13.43 | 0
April | 1 | 3PM to 4PM | 69.8 | 51.2 | 32 | 26.6 | 20.89 | 0.0747 | 0.18 | 13.44 | 0
April | 1 | 4PM to 5PM | 68 | 51 | 33.8 | 28.6 | 20.77 | 0.075 | 0.19 | 13.4 | 0
April | 1 | 5PM to 6PM | 66.2 | 50.2 | 33.8 | 28.6 | 20.34 | 0.0752 | 0.19 | 13.35 | 0
April | 1 | 6PM to 7PM | 62.6 | 48.6 | 33.8 | 28.6 | 19.47 | 0.0757 | 0.19 | 13.26 | 0
April | 1 | 7PM to 8PM | 60.8 | 47.7 | 33.8 | 28.6 | 19.03 | 0.076 | 0.19 | 13.21 | 0
April | 1 | 8PM to 9PM | 60.8 | 47.2 | 32 | 26.6 | 18.72 | 0.076 | 0.18 | 13.21 | 0
April | 1 | 9PM to 10PM | 57.2 | 44.8 | 30.2 | 24.4 | 17.52 | 0.0765 | 0.17 | 13.11 | 0
April | 1 | 10PM to 11PM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
April | 1 | 11PM to 12AM | 57.2 | 43.6 | 26.6 | 20.7 | 16.93 | 0.0766 | 0.14 | 13.1 | 0
April | 2 | 12AM to 1AM | 57.2 | 43.1 | 24.8 | 19 | 16.67 | 0.0766 | 0.13 | 13.09 | 0
April | 2 | 1AM to 2AM | 55.4 | 42.2 | 24.8 | 19 | 16.24 | 0.0769 | 0.13 | 13.05 | 0
April | 2 | 2AM to 3AM | 53.6 | 42.4 | 28.4 | 22.5 | 16.35 | 0.0771 | 0.15 | 13.01 | 0
April | 2 | 3AM to 4AM | 50 | 41.2 | 30.2 | 24.4 | 15.78 | 0.0776 | 0.17 | 12.93 | 1
April | 2 | 4AM to 5AM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
April | 2 | 5AM to 6AM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
April | 2 | 6AM to 7AM | 51.8 | 42.1 | 30.2 | 24.4 | 16.22 | 0.0774 | 0.17 | 12.97 | 1
April | 2 | 7AM to 8AM | 55.4 | 45.2 | 33.8 | 28.6 | 17.72 | 0.0768 | 0.19 | 13.08 | 0
April | 2 | 8AM to 9AM | 60.8 | 47.7 | 33.8 | 28.6 | 19.03 | 0.076 | 0.19 | 13.21 | 0
April | 2 | 9AM to 10AM | 64.4 | 49.4 | 33.8 | 28.6 | 19.9 | 0.0755 | 0.19 | 13.3 | 0
April | 2 | 10AM to 11AM | 66.2 | 50.8 | 35.6 | 30.7 | 20.67 | 0.0752 | 0.21 | 13.36 | 0
April | 2 | 11AM to 12PM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
April | 2 | 12PM to 1PM | 71.6 | 53.7 | 37.4 | 33 | 22.33 | 0.0744 | 0.22 | 13.5 | 0
April | 2 | 1PM to 2PM | 73.4 | 54.4 | 37.4 | 33 | 22.77 | 0.0742 | 0.22 | 13.55 | 0
April | 2 | 2PM to 3PM | 73.4 | 54.4 | 37.4 | 33 | 22.77 | 0.0742 | 0.22 | 13.55 | 0
April | 2 | 3PM to 4PM | 73.4 | 55.7 | 41 | 38 | 23.55 | 0.0741 | 0.26 | 13.56 | 0
April | 2 | 4PM to 5PM | 73.4 | 56.4 | 42.8 | 40.8 | 23.98 | 0.0741 | 0.28 | 13.57 | 0
April | 2 | 5PM to 6PM | 69.8 | 54.9 | 42.8 | 40.8 | 23.11 | 0.0746 | 0.28 | 13.48 | 0
April | 2 | 6PM to 7PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
April | 2 | 7PM to 8PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
April | 2 | 8PM to 9PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
April | 2 | 9PM to 10PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
April | 2 | 10PM to 11PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
April | 2 | 11PM to 12AM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
April | 3 | 12AM to 1AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
April | 3 | 1AM to 2AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
April | 3 | 2AM to 3AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
April | 3 | 3AM to 4AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 3 | 4AM to 5AM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
April | 3 | 5AM to 6AM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
April | 3 | 6AM to 7AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
April | 3 | 7AM to 8AM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
April | 3 | 8AM to 9AM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
April | 3 | 9AM to 10AM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
April | 3 | 10AM to 11AM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
April | 3 | 11AM to 12PM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
April | 3 | 12PM to 1PM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
April | 3 | 1PM to 2PM | 75.2 | 60.1 | 50 | 53.7 | 26.44 | 0.0738 | 0.36 | 13.66 | 0
April | 3 | 2PM to 3PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
April | 3 | 3PM to 4PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
April | 3 | 4PM to 5PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
April | 3 | 5PM to 6PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
April | 3 | 6PM to 7PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
April | 3 | 7PM to 8PM | 59 | 51.2 | 44.6 | 43.7 | 20.95 | 0.0762 | 0.3 | 13.21 | 0
April | 3 | 8PM to 9PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
April | 3 | 9PM to 10PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
April | 3 | 10PM to 11PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
April | 3 | 11PM to 12AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
April | 4 | 12AM to 1AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 4 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 4 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 4 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 4 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 4 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 4 | 6AM to 7AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 4 | 7AM to 8AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 4 | 8AM to 9AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
April | 4 | 9AM to 10AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
April | 4 | 10AM to 11AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
April | 4 | 11AM to 12PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
April | 4 | 12PM to 1PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
April | 4 | 1PM to 2PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
April | 4 | 2PM to 3PM | 65.5 | 56.8 | 50.7 | 55.1 | 24.3 | 0.0751 | 0.37 | 13.41 | 0
April | 4 | 3PM to 4PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
April | 4 | 4PM to 5PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
April | 4 | 5PM to 6PM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
April | 4 | 6PM to 7PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
April | 4 | 7PM to 8PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 4 | 8PM to 9PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 4 | 9PM to 10PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 4 | 10PM to 11PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 4 | 11PM to 12AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 5 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 5 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 5 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 5 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 5 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 5 | 5AM to 6AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 5 | 6AM to 7AM | 47.7 | 46.6 | 45.7 | 45.5 | 18.48 | 0.0778 | 0.31 | 12.93 | 1
April | 5 | 7AM to 8AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 5 | 8AM to 9AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 5 | 9AM to 10AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
April | 5 | 10AM to 11AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
April | 5 | 11AM to 12PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
April | 5 | 12PM to 1PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
April | 5 | 1PM to 2PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
April | 5 | 2PM to 3PM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
April | 5 | 3PM to 4PM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
April | 5 | 4PM to 5PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
April | 5 | 5PM to 6PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
April | 5 | 6PM to 7PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
April | 5 | 7PM to 8PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
April | 5 | 8PM to 9PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
April | 5 | 9PM to 10PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 5 | 10PM to 11PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 5 | 11PM to 12AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 6 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 6 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 6 | 2AM to 3AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 6 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 6 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 6 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 6 | 6AM to 7AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 6 | 7AM to 8AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 6 | 8AM to 9AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
April | 6 | 9AM to 10AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
April | 6 | 10AM to 11AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
April | 6 | 11AM to 12PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
April | 6 | 12PM to 1PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
April | 6 | 1PM to 2PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
April | 6 | 2PM to 3PM | 66.2 | 54.2 | 44.6 | 43.7 | 22.69 | 0.0751 | 0.3 | 13.4 | 0
April | 6 | 3PM to 4PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
April | 6 | 4PM to 5PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
April | 6 | 5PM to 6PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
April | 6 | 6PM to 7PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
April | 6 | 7PM to 8PM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
April | 6 | 8PM to 9PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
April | 6 | 9PM to 10PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
April | 6 | 10PM to 11PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 6 | 11PM to 12AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 7 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 7 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 7 | 2AM to 3AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 7 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 7 | 4AM to 5AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
April | 7 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 7 | 6AM to 7AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 7 | 7AM to 8AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 7 | 8AM to 9AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
April | 7 | 9AM to 10AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
April | 7 | 10AM to 11AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
April | 7 | 11AM to 12PM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
April | 7 | 12PM to 1PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
April | 7 | 1PM to 2PM | 78.8 | 58.4 | 42.8 | 40.8 | 25.29 | 0.0734 | 0.28 | 13.71 | 0
April | 7 | 2PM to 3PM | 78.8 | 57.2 | 39.2 | 35.4 | 24.46 | 0.0734 | 0.24 | 13.69 | 0
April | 7 | 3PM to 4PM | 80.6 | 57.8 | 39.2 | 35.4 | 24.89 | 0.0732 | 0.24 | 13.74 | 0
April | 7 | 4PM to 5PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
April | 7 | 5PM to 6PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
April | 7 | 6PM to 7PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
April | 7 | 7PM to 8PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
April | 7 | 8PM to 9PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
April | 7 | 9PM to 10PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
April | 7 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
April | 7 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 8 | 12AM to 1AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
April | 8 | 1AM to 2AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 8 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 8 | 3AM to 4AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
April | 8 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 8 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 8 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 8 | 7AM to 8AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
April | 8 | 8AM to 9AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
April | 8 | 9AM to 10AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
April | 8 | 10AM to 11AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
April | 8 | 11AM to 12PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
April | 8 | 12PM to 1PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
April | 8 | 1PM to 2PM | 78.8 | 61.4 | 50 | 53.7 | 27.31 | 0.0733 | 0.36 | 13.75 | 0
April | 8 | 2PM to 3PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
April | 8 | 3PM to 4PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
April | 8 | 4PM to 5PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
April | 8 | 5PM to 6PM | 77 | 61.6 | 51.8 | 57.4 | 27.46 | 0.0735 | 0.39 | 13.71 | 0
April | 8 | 6PM to 7PM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
April | 8 | 7PM to 8PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
April | 8 | 8PM to 9PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
April | 8 | 9PM to 10PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
April | 8 | 10PM to 11PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
April | 8 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 9 | 12AM to 1AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 9 | 1AM to 2AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 9 | 2AM to 3AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
April | 9 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 9 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
April | 9 | 5AM to 6AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
April | 9 | 6AM to 7AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
April | 9 | 7AM to 8AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
April | 9 | 8AM to 9AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
April | 9 | 9AM to 10AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
April | 9 | 10AM to 11AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
April | 9 | 11AM to 12PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
April | 9 | 12PM to 1PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
April | 9 | 1PM to 2PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
April | 9 | 2PM to 3PM | 86 | 63.1 | 48.2 | 50.1 | 28.51 | 0.0724 | 0.34 | 13.92 | 0
April | 9 | 3PM to 4PM | 86 | 60.5 | 41 | 38 | 26.61 | 0.0724 | 0.26 | 13.88 | 0
April | 9 | 4PM to 5PM | 84.2 | 59.2 | 39.2 | 35.4 | 25.76 | 0.0727 | 0.24 | 13.83 | 0
April | 9 | 5PM to 6PM | 80.6 | 59.8 | 44.6 | 43.7 | 26.19 | 0.0731 | 0.3 | 13.76 | 0
April | 9 | 6PM to 7PM | 73.4 | 56.4 | 42.8 | 40.8 | 23.98 | 0.0741 | 0.28 | 13.57 | 0
April | 9 | 7PM to 8PM | 68 | 54.2 | 42.8 | 40.8 | 22.67 | 0.0749 | 0.28 | 13.43 | 0
April | 9 | 8PM to 9PM | 66.2 | 52 | 39.2 | 35.4 | 21.4 | 0.0752 | 0.24 | 13.37 | 0
April | 9 | 9PM to 10PM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
April | 9 | 10PM to 11PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
April | 9 | 11PM to 12AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
April | 10 | 12AM to 1AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
April | 10 | 1AM to 2AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
April | 10 | 2AM to 3AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 10 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 10 | 4AM to 5AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 10 | 5AM to 6AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 10 | 6AM to 7AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
April | 10 | 7AM to 8AM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
April | 10 | 8AM to 9AM | 69.8 | 55.7 | 44.6 | 43.7 | 23.57 | 0.0746 | 0.3 | 13.49 | 0
April | 10 | 9AM to 10AM | 77 | 57.8 | 42.8 | 40.8 | 24.86 | 0.0736 | 0.28 | 13.66 | 0
April | 10 | 10AM to 11AM | 82.4 | 58.5 | 39.2 | 35.4 | 25.33 | 0.0729 | 0.24 | 13.78 | 0
April | 10 | 11AM to 12PM | 84.2 | 59.8 | 41 | 38 | 26.17 | 0.0727 | 0.26 | 13.84 | 0
April | 10 | 12PM to 1PM | 86 | 59.9 | 39.2 | 35.4 | 26.2 | 0.0724 | 0.24 | 13.87 | 0
April | 10 | 1PM to 2PM | 87.8 | 61.1 | 41 | 38 | 27.04 | 0.0722 | 0.26 | 13.93 | 0
April | 10 | 2PM to 3PM | 87.8 | 60.5 | 39.2 | 35.4 | 26.64 | 0.0722 | 0.24 | 13.92 | 0
April | 10 | 3PM to 4PM | 86 | 59.9 | 39.2 | 35.4 | 26.2 | 0.0724 | 0.24 | 13.87 | 0
April | 10 | 4PM to 5PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
April | 10 | 5PM to 6PM | 80.6 | 59.8 | 44.6 | 43.7 | 26.19 | 0.0731 | 0.3 | 13.76 | 0
April | 10 | 6PM to 7PM | 71.6 | 56.4 | 44.6 | 43.7 | 24 | 0.0744 | 0.3 | 13.53 | 0
April | 10 | 7PM to 8PM | 69.8 | 54.9 | 42.8 | 40.8 | 23.11 | 0.0746 | 0.28 | 13.48 | 0
April | 10 | 8PM to 9PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
April | 10 | 9PM to 10PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
April | 10 | 10PM to 11PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
April | 10 | 11PM to 12AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
April | 11 | 12AM to 1AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
April | 11 | 1AM to 2AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
April | 11 | 2AM to 3AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
April | 11 | 3AM to 4AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
April | 11 | 4AM to 5AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
April | 11 | 5AM to 6AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
April | 11 | 6AM to 7AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 11 | 7AM to 8AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
April | 11 | 8AM to 9AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
April | 11 | 9AM to 10AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
April | 11 | 10AM to 11AM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
April | 11 | 11AM to 12PM | 77 | 60.8 | 50 | 53.7 | 26.88 | 0.0735 | 0.36 | 13.7 | 0
April | 11 | 12PM to 1PM | 77 | 60 | 48.2 | 50.1 | 26.32 | 0.0736 | 0.34 | 13.69 | 0
April | 11 | 1PM to 2PM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
April | 11 | 2PM to 3PM | 77 | 61.6 | 51.8 | 57.4 | 27.46 | 0.0735 | 0.39 | 13.71 | 0
April | 11 | 3PM to 4PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
April | 11 | 4PM to 5PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
April | 11 | 5PM to 6PM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
April | 11 | 6PM to 7PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
April | 11 | 7PM to 8PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
April | 11 | 8PM to 9PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
April | 11 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 11 | 10PM to 11PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
April | 11 | 11PM to 12AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
April | 12 | 12AM to 1AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 12 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 12 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 12 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 12 | 4AM to 5AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 12 | 5AM to 6AM | 49.5 | 47.9 | 46.6 | 47.1 | 19.16 | 0.0776 | 0.32 | 12.98 | 1
April | 12 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 12 | 7AM to 8AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 12 | 8AM to 9AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
April | 12 | 9AM to 10AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
April | 12 | 10AM to 11AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
April | 12 | 11AM to 12PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
April | 12 | 12PM to 1PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
April | 12 | 1PM to 2PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
April | 12 | 2PM to 3PM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
April | 12 | 3PM to 4PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
April | 12 | 4PM to 5PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
April | 12 | 5PM to 6PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
April | 12 | 6PM to 7PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
April | 12 | 7PM to 8PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
April | 12 | 8PM to 9PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
April | 12 | 9PM to 10PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
April | 12 | 10PM to 11PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 12 | 11PM to 12AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 13 | 12AM to 1AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 13 | 1AM to 2AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 13 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 13 | 3AM to 4AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
April | 13 | 4AM to 5AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 13 | 5AM to 6AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 13 | 6AM to 7AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
April | 13 | 7AM to 8AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
April | 13 | 8AM to 9AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
April | 13 | 9AM to 10AM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
April | 13 | 10AM to 11AM | 64.4 | 52 | 41 | 38 | 21.37 | 0.0754 | 0.26 | 13.33 | 0
April | 13 | 11AM to 12PM | 68 | 52.8 | 39.2 | 35.4 | 21.84 | 0.0749 | 0.24 | 13.42 | 0
April | 13 | 12PM to 1PM | 69.8 | 54.9 | 42.8 | 40.8 | 23.11 | 0.0746 | 0.28 | 13.48 | 0
April | 13 | 1PM to 2PM | 69.8 | 54.9 | 42.8 | 40.8 | 23.11 | 0.0746 | 0.28 | 13.48 | 0
April | 13 | 2PM to 3PM | 69.8 | 55.7 | 44.6 | 43.7 | 23.57 | 0.0746 | 0.3 | 13.49 | 0
April | 13 | 3PM to 4PM | 68 | 55 | 44.6 | 43.7 | 23.13 | 0.0749 | 0.3 | 13.44 | 0
April | 13 | 4PM to 5PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
April | 13 | 5PM to 6PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
April | 13 | 6PM to 7PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
April | 13 | 7PM to 8PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
April | 13 | 8PM to 9PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
April | 13 | 9PM to 10PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
April | 13 | 10PM to 11PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
April | 13 | 11PM to 12AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
April | 14 | 12AM to 1AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
April | 14 | 1AM to 2AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 14 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 14 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 14 | 4AM to 5AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 14 | 5AM to 6AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 14 | 6AM to 7AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
April | 14 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 14 | 8AM to 9AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
April | 14 | 9AM to 10AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
April | 14 | 10AM to 11AM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
April | 14 | 11AM to 12PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
April | 14 | 12PM to 1PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
April | 14 | 1PM to 2PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
April | 14 | 2PM to 3PM | 66.2 | 54.2 | 44.6 | 43.7 | 22.69 | 0.0751 | 0.3 | 13.4 | 0
April | 14 | 3PM to 4PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
April | 14 | 4PM to 5PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
April | 14 | 5PM to 6PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
April | 14 | 6PM to 7PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
April | 14 | 7PM to 8PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
April | 14 | 8PM to 9PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
April | 14 | 9PM to 10PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
April | 14 | 10PM to 11PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
April | 14 | 11PM to 12AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
April | 15 | 12AM to 1AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
April | 15 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 15 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 15 | 3AM to 4AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 15 | 4AM to 5AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
April | 15 | 5AM to 6AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
April | 15 | 6AM to 7AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
April | 15 | 7AM to 8AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 15 | 8AM to 9AM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
April | 15 | 9AM to 10AM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
April | 15 | 10AM to 11AM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
April | 15 | 11AM to 12PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
April | 15 | 12PM to 1PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
April | 15 | 1PM to 2PM | 62.6 | 49.8 | 37.4 | 33 | 20.15 | 0.0757 | 0.22 | 13.27 | 0
April | 15 | 2PM to 3PM | 62.6 | 48.6 | 33.8 | 28.6 | 19.47 | 0.0757 | 0.19 | 13.26 | 0
April | 15 | 3PM to 4PM | 62.6 | 48.6 | 33.8 | 28.6 | 19.47 | 0.0757 | 0.19 | 13.26 | 0
April | 15 | 4PM to 5PM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
April | 15 | 5PM to 6PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
April | 15 | 6PM to 7PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
April | 15 | 7PM to 8PM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
April | 15 | 8PM to 9PM | 48.9 | 45 | 41.2 | 38.3 | 17.66 | 0.0777 | 0.26 | 12.94 | 1
April | 15 | 9PM to 10PM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
April | 15 | 10PM to 11PM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
April | 15 | 11PM to 12AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
April | 16 | 12AM to 1AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
April | 16 | 1AM to 2AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
April | 16 | 2AM to 3AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
April | 16 | 3AM to 4AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
April | 16 | 4AM to 5AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
April | 16 | 5AM to 6AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
April | 16 | 6AM to 7AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 16 | 7AM to 8AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 16 | 8AM to 9AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
April | 16 | 9AM to 10AM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
April | 16 | 10AM to 11AM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
April | 16 | 11AM to 12PM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
April | 16 | 12PM to 1PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
April | 16 | 1PM to 2PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
April | 16 | 2PM to 3PM | 62.6 | 49.8 | 37.4 | 33 | 20.15 | 0.0757 | 0.22 | 13.27 | 0
April | 16 | 3PM to 4PM | 62.6 | 49.8 | 37.4 | 33 | 20.15 | 0.0757 | 0.22 | 13.27 | 0
April | 16 | 4PM to 5PM | 62.6 | 49.8 | 37.4 | 33 | 20.15 | 0.0757 | 0.22 | 13.27 | 0
April | 16 | 5PM to 6PM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
April | 16 | 6PM to 7PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
April | 16 | 7PM to 8PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
April | 16 | 8PM to 9PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
April | 16 | 9PM to 10PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 16 | 10PM to 11PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 16 | 11PM to 12AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 17 | 12AM to 1AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 17 | 1AM to 2AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 17 | 2AM to 3AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 17 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 17 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 17 | 5AM to 6AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 17 | 6AM to 7AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
April | 17 | 7AM to 8AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
April | 17 | 8AM to 9AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
April | 17 | 9AM to 10AM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
April | 17 | 10AM to 11AM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
April | 17 | 11AM to 12PM | 62.6 | 51.2 | 41 | 38 | 20.93 | 0.0757 | 0.26 | 13.29 | 0
April | 17 | 12PM to 1PM | 60.8 | 50.4 | 41 | 38 | 20.5 | 0.0759 | 0.26 | 13.24 | 0
April | 17 | 1PM to 2PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
April | 17 | 2PM to 3PM | 60.8 | 50.4 | 41 | 38 | 20.5 | 0.0759 | 0.26 | 13.24 | 0
April | 17 | 3PM to 4PM | 62.6 | 49.8 | 37.4 | 33 | 20.15 | 0.0757 | 0.22 | 13.27 | 0
April | 17 | 4PM to 5PM | 60.8 | 50.4 | 41 | 38 | 20.5 | 0.0759 | 0.26 | 13.24 | 0
April | 17 | 5PM to 6PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.2 | 0
April | 17 | 6PM to 7PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
April | 17 | 7PM to 8PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
April | 17 | 8PM to 9PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
April | 17 | 9PM to 10PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
April | 17 | 10PM to 11PM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
April | 17 | 11PM to 12AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 18 | 12AM to 1AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 18 | 1AM to 2AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 18 | 2AM to 3AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
April | 18 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 18 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 18 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 18 | 6AM to 7AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 18 | 7AM to 8AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
April | 18 | 8AM to 9AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
April | 18 | 9AM to 10AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
April | 18 | 10AM to 11AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
April | 18 | 11AM to 12PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 18 | 12PM to 1PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 18 | 1PM to 2PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
April | 18 | 2PM to 3PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
April | 18 | 3PM to 4PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
April | 18 | 4PM to 5PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
April | 18 | 5PM to 6PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
April | 18 | 6PM to 7PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
April | 18 | 7PM to 8PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
April | 18 | 8PM to 9PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 18 | 9PM to 10PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 18 | 10PM to 11PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 18 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 19 | 12AM to 1AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
April | 19 | 1AM to 2AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
April | 19 | 2AM to 3AM | 50 | 50 | 50 | 53.7 | 20.3 | 0.0774 | 0.36 | 13.01 | 1
April | 19 | 3AM to 4AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
April | 19 | 4AM to 5AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
April | 19 | 5AM to 6AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
April | 19 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 19 | 7AM to 8AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 19 | 8AM to 9AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 19 | 9AM to 10AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
April | 19 | 10AM to 11AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
April | 19 | 11AM to 12PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
April | 19 | 12PM to 1PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
April | 19 | 1PM to 2PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
April | 19 | 2PM to 3PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
April | 19 | 3PM to 4PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
April | 19 | 4PM to 5PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
April | 19 | 5PM to 6PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
April | 19 | 6PM to 7PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
April | 19 | 7PM to 8PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
April | 19 | 8PM to 9PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 19 | 9PM to 10PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 19 | 10PM to 11PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
April | 19 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 20 | 12AM to 1AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
April | 20 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 20 | 2AM to 3AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
April | 20 | 3AM to 4AM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
April | 20 | 4AM to 5AM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
April | 20 | 5AM to 6AM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
April | 20 | 6AM to 7AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
April | 20 | 7AM to 8AM | 55.4 | 55.4 | 55.4 | 65.6 | 23.48 | 0.0765 | 0.44 | 13.19 | 0
April | 20 | 8AM to 9AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
April | 20 | 9AM to 10AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
April | 20 | 10AM to 11AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
April | 20 | 11AM to 12PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
April | 20 | 12PM to 1PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
April | 20 | 1PM to 2PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
April | 20 | 2PM to 3PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
April | 20 | 3PM to 4PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
April | 20 | 4PM to 5PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
April | 20 | 5PM to 6PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
April | 20 | 6PM to 7PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
April | 20 | 7PM to 8PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
April | 20 | 8PM to 9PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
April | 20 | 9PM to 10PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
April | 20 | 10PM to 11PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 20 | 11PM to 12AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 21 | 12AM to 1AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 21 | 1AM to 2AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 21 | 2AM to 3AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 21 | 3AM to 4AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 21 | 4AM to 5AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 21 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 21 | 6AM to 7AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
April | 21 | 7AM to 8AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
April | 21 | 8AM to 9AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
April | 21 | 9AM to 10AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
April | 21 | 10AM to 11AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
April | 21 | 11AM to 12PM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
April | 21 | 12PM to 1PM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
April | 21 | 1PM to 2PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
April | 21 | 2PM to 3PM | 68 | 56.6 | 48.2 | 50.1 | 24.14 | 0.0748 | 0.34 | 13.46 | 0
April | 21 | 3PM to 4PM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
April | 21 | 4PM to 5PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
April | 21 | 5PM to 6PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
April | 21 | 6PM to 7PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
April | 21 | 7PM to 8PM | 59 | 51.2 | 44.6 | 43.7 | 20.95 | 0.0762 | 0.3 | 13.21 | 0
April | 21 | 8PM to 9PM | 59 | 48.2 | 37.4 | 33 | 19.28 | 0.0762 | 0.22 | 13.18 | 0
April | 21 | 9PM to 10PM | 57.2 | 46.7 | 35.6 | 30.7 | 18.49 | 0.0765 | 0.21 | 13.13 | 0
April | 21 | 10PM to 11PM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
April | 21 | 11PM to 12AM | 51.8 | 44.1 | 35.6 | 30.7 | 17.18 | 0.0773 | 0.21 | 12.99 | 1
April | 22 | 12AM to 1AM | 51.8 | 44.8 | 37.4 | 33 | 17.54 | 0.0773 | 0.22 | 13 | 1
April | 22 | 1AM to 2AM | 51.8 | 44.8 | 37.4 | 33 | 17.54 | 0.0773 | 0.22 | 13 | 1
April | 22 | 2AM to 3AM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
April | 22 | 3AM to 4AM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
April | 22 | 4AM to 5AM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
April | 22 | 5AM to 6AM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
April | 22 | 6AM to 7AM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
April | 22 | 7AM to 8AM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
April | 22 | 8AM to 9AM | 64.4 | 49.4 | 33.8 | 28.6 | 19.9 | 0.0755 | 0.19 | 13.3 | 0
April | 22 | 9AM to 10AM | 66.2 | 50.8 | 35.6 | 30.7 | 20.67 | 0.0752 | 0.21 | 13.36 | 0
April | 22 | 10AM to 11AM | 69.8 | 52.3 | 35.6 | 30.7 | 21.54 | 0.0747 | 0.21 | 13.45 | 0
April | 22 | 11AM to 12PM | 71.6 | 53.7 | 37.4 | 33 | 22.33 | 0.0744 | 0.22 | 13.5 | 0
April | 22 | 12PM to 1PM | 75.2 | 55.1 | 37.4 | 33 | 23.2 | 0.0739 | 0.22 | 13.59 | 0
April | 22 | 1PM to 2PM | 77 | 55.9 | 37.4 | 33 | 23.64 | 0.0737 | 0.22 | 13.64 | 0
April | 22 | 2PM to 3PM | 77 | 56.5 | 39.2 | 35.4 | 24.02 | 0.0737 | 0.24 | 13.65 | 0
April | 22 | 3PM to 4PM | 77 | 56.5 | 39.2 | 35.4 | 24.02 | 0.0737 | 0.24 | 13.65 | 0
April | 22 | 4PM to 5PM | 77 | 56.5 | 39.2 | 35.4 | 24.02 | 0.0737 | 0.24 | 13.65 | 0
April | 22 | 5PM to 6PM | 73.4 | 55 | 39.2 | 35.4 | 23.15 | 0.0742 | 0.24 | 13.55 | 0
April | 22 | 6PM to 7PM | 69.8 | 54.2 | 41 | 38 | 22.68 | 0.0746 | 0.26 | 13.47 | 0
April | 22 | 7PM to 8PM | 66.2 | 53.5 | 42.8 | 40.8 | 22.24 | 0.0751 | 0.28 | 13.39 | 0
April | 22 | 8PM to 9PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
April | 22 | 9PM to 10PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
April | 22 | 10PM to 11PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
April | 22 | 11PM to 12AM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
April | 23 | 12AM to 1AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 23 | 1AM to 2AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
April | 23 | 2AM to 3AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
April | 23 | 3AM to 4AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
April | 23 | 4AM to 5AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
April | 23 | 5AM to 6AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 23 | 6AM to 7AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
April | 23 | 7AM to 8AM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
April | 23 | 8AM to 9AM | 69.8 | 54.2 | 41 | 38 | 22.68 | 0.0746 | 0.26 | 13.47 | 0
April | 23 | 9AM to 10AM | 69.8 | 54.2 | 41 | 38 | 22.68 | 0.0746 | 0.26 | 13.47 | 0
April | 23 | 10AM to 11AM | 73.4 | 55 | 39.2 | 35.4 | 23.15 | 0.0742 | 0.24 | 13.55 | 0
April | 23 | 11AM to 12PM | 80.6 | 57.3 | 37.4 | 33 | 24.51 | 0.0732 | 0.22 | 13.73 | 0
April | 23 | 12PM to 1PM | 80.6 | 57.3 | 37.4 | 33 | 24.51 | 0.0732 | 0.22 | 13.73 | 0
April | 23 | 1PM to 2PM | 82.4 | 57.9 | 37.4 | 33 | 24.95 | 0.0729 | 0.22 | 13.77 | 0
April | 23 | 2PM to 3PM | 84.2 | 58.1 | 35.6 | 30.7 | 25.02 | 0.0727 | 0.21 | 13.81 | 0
April | 23 | 3PM to 4PM | 82.4 | 57.9 | 37.4 | 33 | 24.95 | 0.0729 | 0.22 | 13.77 | 0
April | 23 | 4PM to 5PM | 82.4 | 58.5 | 39.2 | 35.4 | 25.33 | 0.0729 | 0.24 | 13.78 | 0
April | 23 | 5PM to 6PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
April | 23 | 6PM to 7PM | 73.4 | 56.4 | 42.8 | 40.8 | 23.98 | 0.0741 | 0.28 | 13.57 | 0
April | 23 | 7PM to 8PM | 69.8 | 54.2 | 41 | 38 | 22.68 | 0.0746 | 0.26 | 13.47 | 0
April | 23 | 8PM to 9PM | 66.2 | 52.7 | 41 | 38 | 21.81 | 0.0752 | 0.26 | 13.38 | 0
April | 23 | 9PM to 10PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
April | 23 | 10PM to 11PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
April | 23 | 11PM to 12AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
April | 24 | 12AM to 1AM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
April | 24 | 1AM to 2AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 24 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 24 | 3AM to 4AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 24 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
April | 24 | 5AM to 6AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 24 | 6AM to 7AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
April | 24 | 7AM to 8AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
April | 24 | 8AM to 9AM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
April | 24 | 9AM to 10AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
April | 24 | 10AM to 11AM | 77 | 59.2 | 46.4 | 46.8 | 25.8 | 0.0736 | 0.32 | 13.68 | 0
April | 24 | 11AM to 12PM | 80.6 | 59.8 | 44.6 | 43.7 | 26.19 | 0.0731 | 0.3 | 13.76 | 0
April | 24 | 12PM to 1PM | 82.4 | 61.1 | 46.4 | 46.8 | 27.12 | 0.0729 | 0.32 | 13.82 | 0
April | 24 | 1PM to 2PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
April | 24 | 2PM to 3PM | 86 | 61.7 | 44.6 | 43.7 | 27.5 | 0.0724 | 0.3 | 13.9 | 0
April | 24 | 3PM to 4PM | 86 | 61.1 | 42.8 | 40.8 | 27.04 | 0.0724 | 0.28 | 13.89 | 0
April | 24 | 4PM to 5PM | 84.2 | 60.4 | 42.8 | 40.8 | 26.6 | 0.0726 | 0.28 | 13.85 | 0
April | 24 | 5PM to 6PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
April | 24 | 6PM to 7PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
April | 24 | 7PM to 8PM | 68 | 57.4 | 50 | 53.7 | 24.69 | 0.0748 | 0.36 | 13.47 | 0
April | 24 | 8PM to 9PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
April | 24 | 9PM to 10PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
April | 24 | 10PM to 11PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
April | 24 | 11PM to 12AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
April | 25 | 12AM to 1AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
April | 25 | 1AM to 2AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
April | 25 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 25 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 25 | 4AM to 5AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
April | 25 | 5AM to 6AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
April | 25 | 6AM to 7AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
April | 25 | 7AM to 8AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
April | 25 | 8AM to 9AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
April | 25 | 9AM to 10AM | 77 | 61.6 | 51.8 | 57.4 | 27.46 | 0.0735 | 0.39 | 13.71 | 0
April | 25 | 10AM to 11AM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
April | 25 | 11AM to 12PM | 84.2 | 63.3 | 50 | 53.7 | 28.63 | 0.0726 | 0.36 | 13.89 | 0
April | 25 | 12PM to 1PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
April | 25 | 1PM to 2PM | 86 | 63.1 | 48.2 | 50.1 | 28.51 | 0.0724 | 0.34 | 13.92 | 0
April | 25 | 2PM to 3PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
April | 25 | 3PM to 4PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
April | 25 | 4PM to 5PM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
April | 25 | 5PM to 6PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
April | 25 | 6PM to 7PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
April | 25 | 7PM to 8PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
April | 25 | 8PM to 9PM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
April | 25 | 9PM to 10PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
April | 25 | 10PM to 11PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
April | 25 | 11PM to 12AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
April | 26 | 12AM to 1AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
April | 26 | 1AM to 2AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
April | 26 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 26 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 26 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 26 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 26 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
April | 26 | 7AM to 8AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
April | 26 | 8AM to 9AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
April | 26 | 9AM to 10AM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
April | 26 | 10AM to 11AM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
April | 26 | 11AM to 12PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
April | 26 | 12PM to 1PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
April | 26 | 1PM to 2PM | 93.2 | 66.3 | 50 | 53.7 | 30.82 | 0.0714 | 0.36 | 14.12 | 0
April | 26 | 2PM to 3PM | 95 | 64.8 | 44.6 | 43.7 | 29.69 | 0.0712 | 0.3 | 14.13 | 0
April | 26 | 3PM to 4PM | 95 | 64.2 | 42.8 | 40.8 | 29.22 | 0.0712 | 0.28 | 14.12 | 0
April | 26 | 4PM to 5PM | 93.2 | 66.3 | 50 | 53.7 | 30.82 | 0.0714 | 0.36 | 14.12 | 0
April | 26 | 5PM to 6PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
April | 26 | 6PM to 7PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
April | 26 | 7PM to 8PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
April | 26 | 8PM to 9PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
April | 26 | 9PM to 10PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
April | 26 | 10PM to 11PM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
April | 26 | 11PM to 12AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
April | 27 | 12AM to 1AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
April | 27 | 1AM to 2AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
April | 27 | 2AM to 3AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
April | 27 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
April | 27 | 4AM to 5AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
April | 27 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
April | 27 | 6AM to 7AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
April | 27 | 7AM to 8AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
April | 27 | 8AM to 9AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
April | 27 | 9AM to 10AM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
April | 27 | 10AM to 11AM | 84.2 | 63.3 | 50 | 53.7 | 28.63 | 0.0726 | 0.36 | 13.89 | 0
April | 27 | 11AM to 12PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
April | 27 | 12PM to 1PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
April | 27 | 1PM to 2PM | 91.4 | 65.7 | 50 | 53.7 | 30.38 | 0.0716 | 0.36 | 14.07 | 0
April | 27 | 2PM to 3PM | 93.2 | 65.5 | 48.2 | 50.1 | 30.26 | 0.0714 | 0.34 | 14.1 | 0
April | 27 | 3PM to 4PM | 93.2 | 64.2 | 44.6 | 43.7 | 29.25 | 0.0714 | 0.3 | 14.08 | 0
April | 27 | 4PM to 5PM | 91.4 | 63.6 | 44.6 | 43.7 | 28.81 | 0.0717 | 0.3 | 14.04 | 0
April | 27 | 5PM to 6PM | 87.8 | 63 | 46.4 | 46.8 | 28.43 | 0.0721 | 0.32 | 13.96 | 0
April | 27 | 6PM to 7PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
April | 27 | 7PM to 8PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
April | 27 | 8PM to 9PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
April | 27 | 9PM to 10PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
April | 27 | 10PM to 11PM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
April | 27 | 11PM to 12AM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
April | 28 | 12AM to 1AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
April | 28 | 1AM to 2AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
April | 28 | 2AM to 3AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
April | 28 | 3AM to 4AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 28 | 4AM to 5AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 28 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
April | 28 | 6AM to 7AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
April | 28 | 7AM to 8AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
April | 28 | 8AM to 9AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
April | 28 | 9AM to 10AM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
April | 28 | 10AM to 11AM | 80.6 | 55.1 | 30.2 | 24.4 | 23.17 | 0.0732 | 0.17 | 13.7 | 0
April | 28 | 11AM to 12PM | 84.2 | 55.6 | 26.6 | 20.7 | 23.45 | 0.0728 | 0.14 | 13.78 | 0
April | 28 | 12PM to 1PM | 82.4 | 54.5 | 24.8 | 19 | 22.75 | 0.073 | 0.13 | 13.73 | 0
April | 28 | 1PM to 2PM | 84.2 | 56.1 | 28.4 | 22.5 | 23.73 | 0.0728 | 0.15 | 13.79 | 0
April | 28 | 2PM to 3PM | 84.2 | 56.1 | 28.4 | 22.5 | 23.73 | 0.0728 | 0.15 | 13.79 | 0
April | 28 | 3PM to 4PM | 82.4 | 55.4 | 28.4 | 22.5 | 23.3 | 0.073 | 0.15 | 13.74 | 0
April | 28 | 4PM to 5PM | 80.6 | 55.1 | 30.2 | 24.4 | 23.17 | 0.0732 | 0.17 | 13.7 | 0
April | 28 | 5PM to 6PM | 78.8 | 54.4 | 30.2 | 24.4 | 22.74 | 0.0735 | 0.17 | 13.66 | 0
April | 28 | 6PM to 7PM | 73.4 | 52.7 | 32 | 26.6 | 21.76 | 0.0742 | 0.18 | 13.53 | 0
April | 28 | 7PM to 8PM | 71.6 | 51.4 | 30.2 | 24.4 | 21 | 0.0745 | 0.17 | 13.47 | 0
April | 28 | 8PM to 9PM | 69.8 | 50.6 | 30.2 | 24.4 | 20.56 | 0.0747 | 0.17 | 13.43 | 0
April | 28 | 9PM to 10PM | 66.2 | 50.2 | 33.8 | 28.6 | 20.34 | 0.0752 | 0.19 | 13.35 | 0
April | 28 | 10PM to 11PM | 62.6 | 49.2 | 35.6 | 30.7 | 19.8 | 0.0757 | 0.21 | 13.26 | 0
April | 28 | 11PM to 12AM | 64.4 | 48.2 | 30.2 | 24.4 | 19.26 | 0.0755 | 0.17 | 13.29 | 0
April | 29 | 12AM to 1AM | 62.6 | 47.4 | 30.2 | 24.4 | 18.82 | 0.0758 | 0.17 | 13.25 | 0
April | 29 | 1AM to 2AM | 62.6 | 47.4 | 30.2 | 24.4 | 18.82 | 0.0758 | 0.17 | 13.25 | 0
April | 29 | 2AM to 3AM | 53.6 | 45 | 35.6 | 30.7 | 17.62 | 0.077 | 0.21 | 13.04 | 0
April | 29 | 3AM to 4AM | 53.6 | 45 | 35.6 | 30.7 | 17.62 | 0.077 | 0.21 | 13.04 | 0
April | 29 | 4AM to 5AM | 53.6 | 44.3 | 33.8 | 28.6 | 17.29 | 0.0771 | 0.19 | 13.03 | 0
April | 29 | 5AM to 6AM | 55.4 | 45.2 | 33.8 | 28.6 | 17.72 | 0.0768 | 0.19 | 13.08 | 0
April | 29 | 6AM to 7AM | 60.8 | 48.4 | 35.6 | 30.7 | 19.36 | 0.076 | 0.21 | 13.22 | 0
April | 29 | 7AM to 8AM | 66.2 | 50.2 | 33.8 | 28.6 | 20.34 | 0.0752 | 0.19 | 13.35 | 0
April | 29 | 8AM to 9AM | 69.8 | 51.2 | 32 | 26.6 | 20.89 | 0.0747 | 0.18 | 13.44 | 0
April | 29 | 9AM to 10AM | 73.4 | 53.3 | 33.8 | 28.6 | 22.08 | 0.0742 | 0.19 | 13.53 | 0
April | 29 | 10AM to 11AM | 75.2 | 54 | 33.8 | 28.6 | 22.51 | 0.0739 | 0.19 | 13.58 | 0
April | 29 | 11AM to 12PM | 78.8 | 54.9 | 32 | 26.6 | 23.07 | 0.0735 | 0.18 | 13.66 | 0
April | 29 | 12PM to 1PM | 80.6 | 55.7 | 32 | 26.6 | 23.5 | 0.0732 | 0.18 | 13.71 | 0
April | 29 | 1PM to 2PM | 80.6 | 56.2 | 33.8 | 28.6 | 23.82 | 0.0732 | 0.19 | 13.72 | 0
April | 29 | 2PM to 3PM | 82.4 | 56.9 | 33.8 | 28.6 | 24.25 | 0.073 | 0.19 | 13.76 | 0
April | 29 | 3PM to 4PM | 82.4 | 56.9 | 33.8 | 28.6 | 24.25 | 0.073 | 0.19 | 13.76 | 0
April | 29 | 4PM to 5PM | 80.6 | 56.2 | 33.8 | 28.6 | 23.82 | 0.0732 | 0.19 | 13.72 | 0
April | 29 | 5PM to 6PM | 78.8 | 56 | 35.6 | 30.7 | 23.72 | 0.0734 | 0.21 | 13.68 | 0
April | 29 | 6PM to 7PM | 71.6 | 53.1 | 35.6 | 30.7 | 21.98 | 0.0744 | 0.21 | 13.49 | 0
April | 29 | 7PM to 8PM | 68 | 51.5 | 35.6 | 30.7 | 21.1 | 0.0749 | 0.21 | 13.4 | 0
April | 29 | 8PM to 9PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
April | 29 | 9PM to 10PM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
April | 29 | 10PM to 11PM | 61.5 | 49.6 | 38.1 | 33.9 | 20.04 | 0.0759 | 0.23 | 13.25 | 0
April | 29 | 11PM to 12AM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
April | 30 | 12AM to 1AM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
April | 30 | 1AM to 2AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
April | 30 | 2AM to 3AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
April | 30 | 3AM to 4AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
April | 30 | 4AM to 5AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
April | 30 | 5AM to 6AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
April | 30 | 6AM to 7AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
April | 30 | 7AM to 8AM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
April | 30 | 8AM to 9AM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
April | 30 | 9AM to 10AM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
April | 30 | 10AM to 11AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
April | 30 | 11AM to 12PM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
April | 30 | 12PM to 1PM | 80.6 | 59.8 | 44.6 | 43.7 | 26.19 | 0.0731 | 0.3 | 13.76 | 0
April | 30 | 1PM to 2PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
April | 30 | 2PM to 3PM | 84.2 | 59.2 | 39.2 | 35.4 | 25.76 | 0.0727 | 0.24 | 13.83 | 0
April | 30 | 3PM to 4PM | 86 | 58.8 | 35.6 | 30.7 | 25.46 | 0.0725 | 0.21 | 13.86 | 0
April | 30 | 4PM to 5PM | 84.2 | 58.6 | 37.4 | 33 | 25.38 | 0.0727 | 0.22 | 13.82 | 0
April | 30 | 5PM to 6PM | 82.4 | 57.9 | 37.4 | 33 | 24.95 | 0.0729 | 0.22 | 13.77 | 0
April | 30 | 6PM to 7PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
April | 30 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
April | 30 | 8PM to 9PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
April | 30 | 9PM to 10PM | 63.1 | 56.4 | 51.8 | 57.4 | 24.09 | 0.0755 | 0.39 | 13.36 | 0
April | 30 | 10PM to 11PM | 60.1 | 54.3 | 50 | 53.7 | 22.76 | 0.0759 | 0.36 | 13.27 | 0
April | 30 | 11PM to 12AM | 57 | 52.1 | 48.2 | 50.1 | 21.47 | 0.0764 | 0.34 | 13.18 | 0
May | 1 | 12AM to 1AM | 53.8 | 49.8 | 46.4 | 46.8 | 20.16 | 0.0769 | 0.32 | 13.09 | 0
May | 1 | 1AM to 2AM | 50.7 | 47.5 | 44.6 | 43.7 | 18.94 | 0.0774 | 0.3 | 13 | 1
May | 1 | 2AM to 3AM | 47.7 | 45.2 | 42.8 | 40.8 | 17.74 | 0.0779 | 0.28 | 12.91 | 1
May | 1 | 3AM to 4AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
May | 1 | 4AM to 5AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
May | 1 | 5AM to 6AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
May | 1 | 6AM to 7AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 1 | 7AM to 8AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
May | 1 | 8AM to 9AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
May | 1 | 9AM to 10AM | 59 | 51.2 | 44.6 | 43.7 | 20.95 | 0.0762 | 0.3 | 13.21 | 0
May | 1 | 10AM to 11AM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
May | 1 | 11AM to 12PM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
May | 1 | 12PM to 1PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
May | 1 | 1PM to 2PM | 66.2 | 52 | 39.2 | 35.4 | 21.4 | 0.0752 | 0.24 | 13.37 | 0
May | 1 | 2PM to 3PM | 68 | 52.8 | 39.2 | 35.4 | 21.84 | 0.0749 | 0.24 | 13.42 | 0
May | 1 | 3PM to 4PM | 68 | 54.2 | 42.8 | 40.8 | 22.67 | 0.0749 | 0.28 | 13.43 | 0
May | 1 | 4PM to 5PM | 69.8 | 54.2 | 41 | 38 | 22.68 | 0.0746 | 0.26 | 13.47 | 0
May | 1 | 5PM to 6PM | 66.2 | 52.7 | 41 | 38 | 21.81 | 0.0752 | 0.26 | 13.38 | 0
May | 1 | 6PM to 7PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
May | 1 | 7PM to 8PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 1 | 8PM to 9PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 1 | 9PM to 10PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 1 | 10PM to 11PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
May | 1 | 11PM to 12AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 2 | 12AM to 1AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 2 | 1AM to 2AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 2 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 2 | 3AM to 4AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 2 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
May | 2 | 5AM to 6AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 2 | 6AM to 7AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 2 | 7AM to 8AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 2 | 8AM to 9AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
May | 2 | 9AM to 10AM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
May | 2 | 10AM to 11AM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
May | 2 | 11AM to 12PM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
May | 2 | 12PM to 1PM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
May | 2 | 1PM to 2PM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
May | 2 | 2PM to 3PM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
May | 2 | 3PM to 4PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
May | 2 | 4PM to 5PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
May | 2 | 5PM to 6PM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
May | 2 | 6PM to 7PM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
May | 2 | 7PM to 8PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 2 | 8PM to 9PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 2 | 9PM to 10PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 2 | 10PM to 11PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 2 | 11PM to 12AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 3 | 12AM to 1AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 3 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 3 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 3 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 3 | 4AM to 5AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 3 | 5AM to 6AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 3 | 6AM to 7AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 3 | 7AM to 8AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 3 | 8AM to 9AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 3 | 9AM to 10AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 3 | 10AM to 11AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
May | 3 | 11AM to 12PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
May | 3 | 12PM to 1PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
May | 3 | 1PM to 2PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
May | 3 | 2PM to 3PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
May | 3 | 3PM to 4PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
May | 3 | 4PM to 5PM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
May | 3 | 5PM to 6PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
May | 3 | 6PM to 7PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
May | 3 | 7PM to 8PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
May | 3 | 8PM to 9PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
May | 3 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 3 | 10PM to 11PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 3 | 11PM to 12AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 4 | 12AM to 1AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 4 | 1AM to 2AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 4 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 4 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
May | 4 | 4AM to 5AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
May | 4 | 5AM to 6AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
May | 4 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 4 | 7AM to 8AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 4 | 8AM to 9AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
May | 4 | 9AM to 10AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
May | 4 | 10AM to 11AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
May | 4 | 11AM to 12PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
May | 4 | 12PM to 1PM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
May | 4 | 1PM to 2PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
May | 4 | 2PM to 3PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
May | 4 | 3PM to 4PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
May | 4 | 4PM to 5PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
May | 4 | 5PM to 6PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
May | 4 | 6PM to 7PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
May | 4 | 7PM to 8PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
May | 4 | 8PM to 9PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
May | 4 | 9PM to 10PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
May | 4 | 10PM to 11PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 4 | 11PM to 12AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 5 | 12AM to 1AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
May | 5 | 1AM to 2AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 5 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 5 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 5 | 4AM to 5AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
May | 5 | 5AM to 6AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 5 | 6AM to 7AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
May | 5 | 7AM to 8AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
May | 5 | 8AM to 9AM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
May | 5 | 9AM to 10AM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
May | 5 | 10AM to 11AM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
May | 5 | 11AM to 12PM | 80.6 | 59.8 | 44.6 | 43.7 | 26.19 | 0.0731 | 0.3 | 13.76 | 0
May | 5 | 12PM to 1PM | 80.6 | 59.1 | 42.8 | 40.8 | 25.73 | 0.0731 | 0.28 | 13.75 | 0
May | 5 | 1PM to 2PM | 84.2 | 60.4 | 42.8 | 40.8 | 26.6 | 0.0726 | 0.28 | 13.85 | 0
May | 5 | 2PM to 3PM | 84.2 | 58.1 | 35.6 | 30.7 | 25.02 | 0.0727 | 0.21 | 13.81 | 0
May | 5 | 3PM to 4PM | 84.2 | 58.1 | 35.6 | 30.7 | 25.02 | 0.0727 | 0.21 | 13.81 | 0
May | 5 | 4PM to 5PM | 84.2 | 58.6 | 37.4 | 33 | 25.38 | 0.0727 | 0.22 | 13.82 | 0
May | 5 | 5PM to 6PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
May | 5 | 6PM to 7PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
May | 5 | 7PM to 8PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
May | 5 | 8PM to 9PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
May | 5 | 9PM to 10PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
May | 5 | 10PM to 11PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 5 | 11PM to 12AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 6 | 12AM to 1AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 6 | 1AM to 2AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
May | 6 | 2AM to 3AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
May | 6 | 3AM to 4AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 6 | 4AM to 5AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
May | 6 | 5AM to 6AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 6 | 6AM to 7AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
May | 6 | 7AM to 8AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
May | 6 | 8AM to 9AM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
May | 6 | 9AM to 10AM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
May | 6 | 10AM to 11AM | 73.4 | 57.1 | 44.6 | 43.7 | 24.44 | 0.0741 | 0.3 | 13.58 | 0
May | 6 | 11AM to 12PM | 77 | 56.5 | 39.2 | 35.4 | 24.02 | 0.0737 | 0.24 | 13.65 | 0
May | 6 | 12PM to 1PM | 80.6 | 59.1 | 42.8 | 40.8 | 25.73 | 0.0731 | 0.28 | 13.75 | 0
May | 6 | 1PM to 2PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
May | 6 | 2PM to 3PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
May | 6 | 3PM to 4PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
May | 6 | 4PM to 5PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
May | 6 | 5PM to 6PM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
May | 6 | 6PM to 7PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
May | 6 | 7PM to 8PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
May | 6 | 8PM to 9PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 6 | 9PM to 10PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
May | 6 | 10PM to 11PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
May | 6 | 11PM to 12AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
May | 7 | 12AM to 1AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 7 | 1AM to 2AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 7 | 2AM to 3AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
May | 7 | 3AM to 4AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
May | 7 | 4AM to 5AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 7 | 5AM to 6AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
May | 7 | 6AM to 7AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 7 | 7AM to 8AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
May | 7 | 8AM to 9AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
May | 7 | 9AM to 10AM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
May | 7 | 10AM to 11AM | 69.8 | 54.2 | 41 | 38 | 22.68 | 0.0746 | 0.26 | 13.47 | 0
May | 7 | 11AM to 12PM | 71.6 | 52.5 | 33.8 | 28.6 | 21.64 | 0.0744 | 0.19 | 13.49 | 0
May | 7 | 12PM to 1PM | 73.4 | 53.8 | 35.6 | 30.7 | 22.41 | 0.0742 | 0.21 | 13.54 | 0
May | 7 | 1PM to 2PM | 75.2 | 52.4 | 28.4 | 22.5 | 21.56 | 0.074 | 0.15 | 13.56 | 0
May | 7 | 2PM to 3PM | 73.4 | 51.1 | 26.6 | 20.7 | 20.84 | 0.0742 | 0.14 | 13.51 | 0
May | 7 | 3PM to 4PM | 73.4 | 50.2 | 23 | 17.4 | 20.34 | 0.0743 | 0.12 | 13.5 | 0
May | 7 | 4PM to 5PM | 73.4 | 49.5 | 19.4 | 14.7 | 19.91 | 0.0743 | 0.1 | 13.49 | 0
May | 7 | 5PM to 6PM | 71.6 | 49 | 21.2 | 16 | 19.68 | 0.0745 | 0.11 | 13.45 | 0
May | 7 | 6PM to 7PM | 68 | 47.4 | 21.2 | 16 | 18.81 | 0.075 | 0.11 | 13.36 | 0
May | 7 | 7PM to 8PM | 62.6 | 45.7 | 24.8 | 19 | 17.98 | 0.0758 | 0.13 | 13.23 | 0
May | 7 | 8PM to 9PM | 57.2 | 43.6 | 26.6 | 20.7 | 16.93 | 0.0766 | 0.14 | 13.1 | 0
May | 7 | 9PM to 10PM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
May | 7 | 10PM to 11PM | 59 | 44.5 | 26.6 | 20.7 | 17.37 | 0.0763 | 0.14 | 13.14 | 0
May | 7 | 11PM to 12AM | 59 | 44 | 24.8 | 19 | 17.11 | 0.0763 | 0.13 | 13.14 | 0
May | 8 | 12AM to 1AM | 57.2 | 43.6 | 26.6 | 20.7 | 16.93 | 0.0766 | 0.14 | 13.1 | 0
May | 8 | 1AM to 2AM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
May | 8 | 2AM to 3AM | 55.4 | 43.3 | 28.4 | 22.5 | 16.78 | 0.0768 | 0.15 | 13.06 | 0
May | 8 | 3AM to 4AM | 55.4 | 43.3 | 28.4 | 22.5 | 16.78 | 0.0768 | 0.15 | 13.06 | 0
May | 8 | 4AM to 5AM | 53.6 | 42.4 | 28.4 | 22.5 | 16.35 | 0.0771 | 0.15 | 13.01 | 0
May | 8 | 5AM to 6AM | 53.6 | 42.4 | 28.4 | 22.5 | 16.35 | 0.0771 | 0.15 | 13.01 | 0
May | 8 | 6AM to 7AM | 59 | 45.1 | 28.4 | 22.5 | 17.65 | 0.0763 | 0.15 | 13.15 | 0
May | 8 | 7AM to 8AM | 62.6 | 46.8 | 28.4 | 22.5 | 18.52 | 0.0758 | 0.15 | 13.24 | 0
May | 8 | 8AM to 9AM | 66.2 | 48.4 | 28.4 | 22.5 | 19.39 | 0.0753 | 0.15 | 13.33 | 0
May | 8 | 9AM to 10AM | 69.8 | 50.1 | 28.4 | 22.5 | 20.26 | 0.0747 | 0.15 | 13.42 | 0
May | 8 | 10AM to 11AM | 73.4 | 51.1 | 26.6 | 20.7 | 20.84 | 0.0742 | 0.14 | 13.51 | 0
May | 8 | 11AM to 12PM | 75.2 | 51 | 23 | 17.4 | 20.77 | 0.074 | 0.12 | 13.54 | 0
May | 8 | 12PM to 1PM | 75.2 | 50.6 | 21.2 | 16 | 20.55 | 0.074 | 0.11 | 13.54 | 0
May | 8 | 1PM to 2PM | 77 | 51 | 19.4 | 14.7 | 20.77 | 0.0738 | 0.1 | 13.58 | 0
May | 8 | 2PM to 3PM | 78.8 | 51.5 | 17.6 | 13.4 | 21.01 | 0.0735 | 0.09 | 13.62 | 0
May | 8 | 3PM to 4PM | 78.8 | 51.5 | 17.6 | 13.4 | 21.01 | 0.0735 | 0.09 | 13.62 | 0
May | 8 | 4PM to 5PM | 78.8 | 51.5 | 17.6 | 13.4 | 21.01 | 0.0735 | 0.09 | 13.62 | 0
May | 8 | 5PM to 6PM | 78.8 | 51.8 | 19.4 | 14.7 | 21.21 | 0.0735 | 0.1 | 13.63 | 0
May | 8 | 6PM to 7PM | 71.6 | 55.7 | 42.8 | 40.8 | 23.55 | 0.0744 | 0.28 | 13.52 | 0
May | 8 | 7PM to 8PM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
May | 8 | 8PM to 9PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
May | 8 | 9PM to 10PM | 59 | 48.9 | 39.2 | 35.4 | 19.66 | 0.0762 | 0.24 | 13.19 | 0
May | 8 | 10PM to 11PM | 55.4 | 48 | 41 | 38 | 19.19 | 0.0767 | 0.26 | 13.1 | 0
May | 8 | 11PM to 12AM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
May | 9 | 12AM to 1AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 9 | 1AM to 2AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 9 | 2AM to 3AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
May | 9 | 3AM to 4AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
May | 9 | 4AM to 5AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
May | 9 | 5AM to 6AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
May | 9 | 6AM to 7AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
May | 9 | 7AM to 8AM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
May | 9 | 8AM to 9AM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
May | 9 | 9AM to 10AM | 66.2 | 51.4 | 37.4 | 33 | 21.02 | 0.0752 | 0.22 | 13.36 | 0
May | 9 | 10AM to 11AM | 69.8 | 52.3 | 35.6 | 30.7 | 21.54 | 0.0747 | 0.21 | 13.45 | 0
May | 9 | 11AM to 12PM | 71.6 | 53.1 | 35.6 | 30.7 | 21.98 | 0.0744 | 0.21 | 13.49 | 0
May | 9 | 12PM to 1PM | 73.4 | 54.4 | 37.4 | 33 | 22.77 | 0.0742 | 0.22 | 13.55 | 0
May | 9 | 1PM to 2PM | 75.2 | 54.6 | 35.6 | 30.7 | 22.85 | 0.0739 | 0.21 | 13.58 | 0
May | 9 | 2PM to 3PM | 78.8 | 56.6 | 37.4 | 33 | 24.07 | 0.0734 | 0.22 | 13.68 | 0
May | 9 | 3PM to 4PM | 77 | 56.5 | 39.2 | 35.4 | 24.02 | 0.0737 | 0.24 | 13.65 | 0
May | 9 | 4PM to 5PM | 73.4 | 56.4 | 42.8 | 40.8 | 23.98 | 0.0741 | 0.28 | 13.57 | 0
May | 9 | 5PM to 6PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
May | 9 | 6PM to 7PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
May | 9 | 7PM to 8PM | 60.8 | 50.4 | 41 | 38 | 20.5 | 0.0759 | 0.26 | 13.24 | 0
May | 9 | 8PM to 9PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
May | 9 | 9PM to 10PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
May | 9 | 10PM to 11PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
May | 9 | 11PM to 12AM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
May | 10 | 12AM to 1AM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
May | 10 | 1AM to 2AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
May | 10 | 2AM to 3AM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
May | 10 | 3AM to 4AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
May | 10 | 4AM to 5AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
May | 10 | 5AM to 6AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
May | 10 | 6AM to 7AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
May | 10 | 7AM to 8AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 10 | 8AM to 9AM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
May | 10 | 9AM to 10AM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
May | 10 | 10AM to 11AM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
May | 10 | 11AM to 12PM | 66.2 | 52 | 39.2 | 35.4 | 21.4 | 0.0752 | 0.24 | 13.37 | 0
May | 10 | 12PM to 1PM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
May | 10 | 1PM to 2PM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
May | 10 | 2PM to 3PM | 69.8 | 52.3 | 35.6 | 30.7 | 21.54 | 0.0747 | 0.21 | 13.45 | 0
May | 10 | 3PM to 4PM | 71.6 | 51.4 | 30.2 | 24.4 | 21 | 0.0745 | 0.17 | 13.47 | 0
May | 10 | 4PM to 5PM | 71.6 | 50.9 | 28.4 | 22.5 | 20.69 | 0.0745 | 0.15 | 13.47 | 0
May | 10 | 5PM to 6PM | 69.8 | 53.6 | 39.2 | 35.4 | 22.27 | 0.0747 | 0.24 | 13.46 | 0
May | 10 | 6PM to 7PM | 64.4 | 51.3 | 39.2 | 35.4 | 20.97 | 0.0754 | 0.24 | 13.32 | 0
May | 10 | 7PM to 8PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
May | 10 | 8PM to 9PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
May | 10 | 9PM to 10PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 10 | 10PM to 11PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
May | 10 | 11PM to 12AM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
May | 11 | 12AM to 1AM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
May | 11 | 1AM to 2AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 11 | 2AM to 3AM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
May | 11 | 3AM to 4AM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
May | 11 | 4AM to 5AM | 51.8 | 44.8 | 37.4 | 33 | 17.54 | 0.0773 | 0.22 | 13 | 1
May | 11 | 5AM to 6AM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
May | 11 | 6AM to 7AM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
May | 11 | 7AM to 8AM | 64.4 | 50.6 | 37.4 | 33 | 20.59 | 0.0754 | 0.22 | 13.32 | 0
May | 11 | 8AM to 9AM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
May | 11 | 9AM to 10AM | 73.4 | 53.8 | 35.6 | 30.7 | 22.41 | 0.0742 | 0.21 | 13.54 | 0
May | 11 | 10AM to 11AM | 75.2 | 54.6 | 35.6 | 30.7 | 22.85 | 0.0739 | 0.21 | 13.58 | 0
May | 11 | 11AM to 12PM | 80.6 | 56.7 | 35.6 | 30.7 | 24.15 | 0.0732 | 0.21 | 13.72 | 0
May | 11 | 12PM to 1PM | 80.6 | 56.7 | 35.6 | 30.7 | 24.15 | 0.0732 | 0.21 | 13.72 | 0
May | 11 | 1PM to 2PM | 82.4 | 57.4 | 35.6 | 30.7 | 24.59 | 0.073 | 0.21 | 13.77 | 0
May | 11 | 2PM to 3PM | 82.4 | 57.4 | 35.6 | 30.7 | 24.59 | 0.073 | 0.21 | 13.77 | 0
May | 11 | 3PM to 4PM | 82.4 | 57.4 | 35.6 | 30.7 | 24.59 | 0.073 | 0.21 | 13.77 | 0
May | 11 | 4PM to 5PM | 80.6 | 56.7 | 35.6 | 30.7 | 24.15 | 0.0732 | 0.21 | 13.72 | 0
May | 11 | 5PM to 6PM | 80.6 | 56.2 | 33.8 | 28.6 | 23.82 | 0.0732 | 0.19 | 13.72 | 0
May | 11 | 6PM to 7PM | 75.2 | 55.1 | 37.4 | 33 | 23.2 | 0.0739 | 0.22 | 13.59 | 0
May | 11 | 7PM to 8PM | 69.8 | 54.2 | 41 | 38 | 22.68 | 0.0746 | 0.26 | 13.47 | 0
May | 11 | 8PM to 9PM | 62.6 | 51.2 | 41 | 38 | 20.93 | 0.0757 | 0.26 | 13.29 | 0
May | 11 | 9PM to 10PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
May | 11 | 10PM to 11PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
May | 11 | 11PM to 12AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
May | 12 | 12AM to 1AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 12 | 1AM to 2AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
May | 12 | 2AM to 3AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
May | 12 | 3AM to 4AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
May | 12 | 4AM to 5AM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
May | 12 | 5AM to 6AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 12 | 6AM to 7AM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
May | 12 | 7AM to 8AM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
May | 12 | 8AM to 9AM | 68 | 55 | 44.6 | 43.7 | 23.13 | 0.0749 | 0.3 | 13.44 | 0
May | 12 | 9AM to 10AM | 72.7 | 55.9 | 42.3 | 39.9 | 23.68 | 0.0742 | 0.27 | 13.55 | 0
May | 12 | 10AM to 11AM | 76.6 | 56.5 | 39.7 | 36.2 | 24.05 | 0.0737 | 0.25 | 13.64 | 0
May | 12 | 11AM to 12PM | 80.6 | 57.3 | 37.4 | 33 | 24.51 | 0.0732 | 0.22 | 13.73 | 0
May | 12 | 12PM to 1PM | 82.4 | 58.5 | 39.2 | 35.4 | 25.33 | 0.0729 | 0.24 | 13.78 | 0
May | 12 | 1PM to 2PM | 82.4 | 58.5 | 39.2 | 35.4 | 25.33 | 0.0729 | 0.24 | 13.78 | 0
May | 12 | 2PM to 3PM | 84.2 | 59.2 | 39.2 | 35.4 | 25.76 | 0.0727 | 0.24 | 13.83 | 0
May | 12 | 3PM to 4PM | 84.2 | 59.2 | 39.2 | 35.4 | 25.76 | 0.0727 | 0.24 | 13.83 | 0
May | 12 | 4PM to 5PM | 84.2 | 59.2 | 39.2 | 35.4 | 25.76 | 0.0727 | 0.24 | 13.83 | 0
May | 12 | 5PM to 6PM | 80.6 | 57.8 | 39.2 | 35.4 | 24.89 | 0.0732 | 0.24 | 13.74 | 0
May | 12 | 6PM to 7PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
May | 12 | 7PM to 8PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
May | 12 | 8PM to 9PM | 71.6 | 56.4 | 44.6 | 43.7 | 24 | 0.0744 | 0.3 | 13.53 | 0
May | 12 | 9PM to 10PM | 66.2 | 54.2 | 44.6 | 43.7 | 22.69 | 0.0751 | 0.3 | 13.4 | 0
May | 12 | 10PM to 11PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
May | 12 | 11PM to 12AM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
May | 13 | 12AM to 1AM | 56.1 | 48.3 | 40.8 | 37.7 | 19.32 | 0.0766 | 0.26 | 13.12 | 0
May | 13 | 1AM to 2AM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
May | 13 | 2AM to 3AM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
May | 13 | 3AM to 4AM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
May | 13 | 4AM to 5AM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
May | 13 | 5AM to 6AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 13 | 6AM to 7AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
May | 13 | 7AM to 8AM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
May | 13 | 8AM to 9AM | 66.2 | 53.5 | 42.8 | 40.8 | 22.24 | 0.0751 | 0.28 | 13.39 | 0
May | 13 | 9AM to 10AM | 71.6 | 54.3 | 39.2 | 35.4 | 22.71 | 0.0744 | 0.24 | 13.51 | 0
May | 13 | 10AM to 11AM | 75.2 | 55.1 | 37.4 | 33 | 23.2 | 0.0739 | 0.22 | 13.59 | 0
May | 13 | 11AM to 12PM | 78.8 | 55.5 | 33.8 | 28.6 | 23.38 | 0.0735 | 0.19 | 13.67 | 0
May | 13 | 12PM to 1PM | 80.6 | 57.3 | 37.4 | 33 | 24.51 | 0.0732 | 0.22 | 13.73 | 0
May | 13 | 1PM to 2PM | 80.6 | 57.8 | 39.2 | 35.4 | 24.89 | 0.0732 | 0.24 | 13.74 | 0
May | 13 | 2PM to 3PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
May | 13 | 3PM to 4PM | 81 | 59.4 | 43.3 | 41.6 | 25.95 | 0.0731 | 0.28 | 13.77 | 0
May | 13 | 4PM to 5PM | 78.4 | 58.7 | 43.9 | 42.5 | 25.48 | 0.0734 | 0.29 | 13.7 | 0
May | 13 | 5PM to 6PM | 74.7 | 58 | 45.7 | 45.5 | 25.04 | 0.0739 | 0.31 | 13.62 | 0
May | 13 | 6PM to 7PM | 68.9 | 56.6 | 47.5 | 48.8 | 24.14 | 0.0747 | 0.33 | 13.48 | 0
May | 13 | 7PM to 8PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
May | 13 | 8PM to 9PM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
May | 13 | 9PM to 10PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 13 | 10PM to 11PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 13 | 11PM to 12AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 14 | 12AM to 1AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 14 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 14 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
May | 14 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
May | 14 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
May | 14 | 5AM to 6AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 14 | 6AM to 7AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
May | 14 | 7AM to 8AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
May | 14 | 8AM to 9AM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
May | 14 | 9AM to 10AM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
May | 14 | 10AM to 11AM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
May | 14 | 11AM to 12PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
May | 14 | 12PM to 1PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
May | 14 | 1PM to 2PM | 84.2 | 61.1 | 44.6 | 43.7 | 27.06 | 0.0726 | 0.3 | 13.85 | 0
May | 14 | 2PM to 3PM | 84.2 | 59.8 | 41 | 38 | 26.17 | 0.0727 | 0.26 | 13.84 | 0
May | 14 | 3PM to 4PM | 84.2 | 60.4 | 42.8 | 40.8 | 26.6 | 0.0726 | 0.28 | 13.85 | 0
May | 14 | 4PM to 5PM | 84.2 | 58.6 | 37.4 | 33 | 25.38 | 0.0727 | 0.22 | 13.82 | 0
May | 14 | 5PM to 6PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
May | 14 | 6PM to 7PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
May | 14 | 7PM to 8PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
May | 14 | 8PM to 9PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
May | 14 | 9PM to 10PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
May | 14 | 10PM to 11PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 14 | 11PM to 12AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 15 | 12AM to 1AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 15 | 1AM to 2AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 15 | 2AM to 3AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 15 | 3AM to 4AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 15 | 4AM to 5AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 15 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 15 | 6AM to 7AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 15 | 7AM to 8AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
May | 15 | 8AM to 9AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
May | 15 | 9AM to 10AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
May | 15 | 10AM to 11AM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
May | 15 | 11AM to 12PM | 80.6 | 59.8 | 44.6 | 43.7 | 26.19 | 0.0731 | 0.3 | 13.76 | 0
May | 15 | 12PM to 1PM | 82.4 | 61.9 | 48.2 | 50.1 | 27.64 | 0.0728 | 0.34 | 13.83 | 0
May | 15 | 1PM to 2PM | 86 | 62.4 | 46.4 | 46.8 | 27.99 | 0.0724 | 0.32 | 13.91 | 0
May | 15 | 2PM to 3PM | 86 | 62.4 | 46.4 | 46.8 | 27.99 | 0.0724 | 0.32 | 13.91 | 0
May | 15 | 3PM to 4PM | 86 | 61.1 | 42.8 | 40.8 | 27.04 | 0.0724 | 0.28 | 13.89 | 0
May | 15 | 4PM to 5PM | 84.2 | 59.8 | 41 | 38 | 26.17 | 0.0727 | 0.26 | 13.84 | 0
May | 15 | 5PM to 6PM | 84.2 | 59.8 | 41 | 38 | 26.17 | 0.0727 | 0.26 | 13.84 | 0
May | 15 | 6PM to 7PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
May | 15 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
May | 15 | 8PM to 9PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
May | 15 | 9PM to 10PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
May | 15 | 10PM to 11PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
May | 15 | 11PM to 12AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
May | 16 | 12AM to 1AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
May | 16 | 1AM to 2AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 16 | 2AM to 3AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 16 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 16 | 4AM to 5AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 16 | 5AM to 6AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
May | 16 | 6AM to 7AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
May | 16 | 7AM to 8AM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
May | 16 | 8AM to 9AM | 73.4 | 57.1 | 44.6 | 43.7 | 24.44 | 0.0741 | 0.3 | 13.58 | 0
May | 16 | 9AM to 10AM | 77 | 57.1 | 41 | 38 | 24.42 | 0.0736 | 0.26 | 13.65 | 0
May | 16 | 10AM to 11AM | 80.6 | 59.1 | 42.8 | 40.8 | 25.73 | 0.0731 | 0.28 | 13.75 | 0
May | 16 | 11AM to 12PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
May | 16 | 12PM to 1PM | 84.2 | 59.8 | 41 | 38 | 26.17 | 0.0727 | 0.26 | 13.84 | 0
May | 16 | 1PM to 2PM | 87.8 | 59.4 | 35.6 | 30.7 | 25.89 | 0.0722 | 0.21 | 13.9 | 0
May | 16 | 2PM to 3PM | 89.6 | 61.2 | 39.2 | 35.4 | 27.07 | 0.072 | 0.24 | 13.97 | 0
May | 16 | 3PM to 4PM | 87.8 | 60.5 | 39.2 | 35.4 | 26.64 | 0.0722 | 0.24 | 13.92 | 0
May | 16 | 4PM to 5PM | 86 | 63.1 | 48.2 | 50.1 | 28.51 | 0.0724 | 0.34 | 13.92 | 0
May | 16 | 5PM to 6PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
May | 16 | 6PM to 7PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
May | 16 | 7PM to 8PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
May | 16 | 8PM to 9PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
May | 16 | 9PM to 10PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
May | 16 | 10PM to 11PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
May | 16 | 11PM to 12AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
May | 17 | 12AM to 1AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 17 | 1AM to 2AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 17 | 2AM to 3AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 17 | 3AM to 4AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 17 | 4AM to 5AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 17 | 5AM to 6AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 17 | 6AM to 7AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 17 | 7AM to 8AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
May | 17 | 8AM to 9AM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
May | 17 | 9AM to 10AM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
May | 17 | 10AM to 11AM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
May | 17 | 11AM to 12PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
May | 17 | 12PM to 1PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
May | 17 | 1PM to 2PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
May | 17 | 2PM to 3PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
May | 17 | 3PM to 4PM | 86 | 64.7 | 51.8 | 57.4 | 29.66 | 0.0723 | 0.39 | 13.94 | 0
May | 17 | 4PM to 5PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
May | 17 | 5PM to 6PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
May | 17 | 6PM to 7PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
May | 17 | 7PM to 8PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
May | 17 | 8PM to 9PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
May | 17 | 9PM to 10PM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
May | 17 | 10PM to 11PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 17 | 11PM to 12AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 18 | 12AM to 1AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 18 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 18 | 2AM to 3AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 18 | 3AM to 4AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
May | 18 | 4AM to 5AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
May | 18 | 5AM to 6AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
May | 18 | 6AM to 7AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 18 | 7AM to 8AM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
May | 18 | 8AM to 9AM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
May | 18 | 9AM to 10AM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
May | 18 | 10AM to 11AM | 69.8 | 53.6 | 39.2 | 35.4 | 22.27 | 0.0747 | 0.24 | 13.46 | 0
May | 18 | 11AM to 12PM | 75.2 | 55.1 | 37.4 | 33 | 23.2 | 0.0739 | 0.22 | 13.59 | 0
May | 18 | 12PM to 1PM | 75.2 | 54 | 33.8 | 28.6 | 22.51 | 0.0739 | 0.19 | 13.58 | 0
May | 18 | 1PM to 2PM | 75.2 | 54 | 33.8 | 28.6 | 22.51 | 0.0739 | 0.19 | 13.58 | 0
May | 18 | 2PM to 3PM | 75.2 | 52.9 | 30.2 | 24.4 | 21.87 | 0.074 | 0.17 | 13.57 | 0
May | 18 | 3PM to 4PM | 73.4 | 53.3 | 33.8 | 28.6 | 22.08 | 0.0742 | 0.19 | 13.53 | 0
May | 18 | 4PM to 5PM | 69.8 | 51.7 | 33.8 | 28.6 | 21.21 | 0.0747 | 0.19 | 13.44 | 0
May | 18 | 5PM to 6PM | 64.4 | 50.6 | 37.4 | 33 | 20.59 | 0.0754 | 0.22 | 13.32 | 0
May | 18 | 6PM to 7PM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
May | 18 | 7PM to 8PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
May | 18 | 8PM to 9PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
May | 18 | 9PM to 10PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
May | 18 | 10PM to 11PM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
May | 18 | 11PM to 12AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
May | 19 | 12AM to 1AM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
May | 19 | 1AM to 2AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
May | 19 | 2AM to 3AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 19 | 3AM to 4AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 19 | 4AM to 5AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
May | 19 | 5AM to 6AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
May | 19 | 6AM to 7AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
May | 19 | 7AM to 8AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
May | 19 | 8AM to 9AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
May | 19 | 9AM to 10AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
May | 19 | 10AM to 11AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
May | 19 | 11AM to 12PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
May | 19 | 12PM to 1PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
May | 19 | 1PM to 2PM | 55.4 | 55.4 | 55.4 | 65.6 | 23.48 | 0.0765 | 0.44 | 13.19 | 0
May | 19 | 2PM to 3PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
May | 19 | 3PM to 4PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
May | 19 | 4PM to 5PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 19 | 5PM to 6PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
May | 19 | 6PM to 7PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 19 | 7PM to 8PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 19 | 8PM to 9PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
May | 19 | 9PM to 10PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
May | 19 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 19 | 11PM to 12AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 20 | 12AM to 1AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 20 | 1AM to 2AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 20 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
May | 20 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 20 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 20 | 5AM to 6AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 20 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 20 | 7AM to 8AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
May | 20 | 8AM to 9AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 20 | 9AM to 10AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 20 | 10AM to 11AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
May | 20 | 11AM to 12PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
May | 20 | 12PM to 1PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 20 | 1PM to 2PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
May | 20 | 2PM to 3PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
May | 20 | 3PM to 4PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 20 | 4PM to 5PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
May | 20 | 5PM to 6PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 20 | 6PM to 7PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 20 | 7PM to 8PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 20 | 8PM to 9PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 20 | 9PM to 10PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
May | 20 | 10PM to 11PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
May | 20 | 11PM to 12AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
May | 21 | 12AM to 1AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
May | 21 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 21 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 21 | 3AM to 4AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
May | 21 | 4AM to 5AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
May | 21 | 5AM to 6AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 21 | 6AM to 7AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 21 | 7AM to 8AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
May | 21 | 8AM to 9AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 21 | 9AM to 10AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
May | 21 | 10AM to 11AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
May | 21 | 11AM to 12PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
May | 21 | 12PM to 1PM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
May | 21 | 1PM to 2PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
May | 21 | 2PM to 3PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
May | 21 | 3PM to 4PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
May | 21 | 4PM to 5PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
May | 21 | 5PM to 6PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
May | 21 | 6PM to 7PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
May | 21 | 7PM to 8PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
May | 21 | 8PM to 9PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
May | 21 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 21 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 21 | 11PM to 12AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
May | 22 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 22 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 22 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 22 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
May | 22 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
May | 22 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
May | 22 | 6AM to 7AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
May | 22 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 22 | 8AM to 9AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 22 | 9AM to 10AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
May | 22 | 10AM to 11AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
May | 22 | 11AM to 12PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
May | 22 | 12PM to 1PM | 68 | 55 | 44.6 | 43.7 | 23.13 | 0.0749 | 0.3 | 13.44 | 0
May | 22 | 1PM to 2PM | 69.8 | 54.9 | 42.8 | 40.8 | 23.11 | 0.0746 | 0.28 | 13.48 | 0
May | 22 | 2PM to 3PM | 71.6 | 53.7 | 37.4 | 33 | 22.33 | 0.0744 | 0.22 | 13.5 | 0
May | 22 | 3PM to 4PM | 71.6 | 53.1 | 35.6 | 30.7 | 21.98 | 0.0744 | 0.21 | 13.49 | 0
May | 22 | 4PM to 5PM | 71.6 | 53.1 | 35.6 | 30.7 | 21.98 | 0.0744 | 0.21 | 13.49 | 0
May | 22 | 5PM to 6PM | 71.6 | 53.7 | 37.4 | 33 | 22.33 | 0.0744 | 0.22 | 13.5 | 0
May | 22 | 6PM to 7PM | 69.8 | 54.2 | 41 | 38 | 22.68 | 0.0746 | 0.26 | 13.47 | 0
May | 22 | 7PM to 8PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
May | 22 | 8PM to 9PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
May | 22 | 9PM to 10PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
May | 22 | 10PM to 11PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
May | 22 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 23 | 12AM to 1AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 23 | 1AM to 2AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
May | 23 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 23 | 3AM to 4AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 23 | 4AM to 5AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
May | 23 | 5AM to 6AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
May | 23 | 6AM to 7AM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
May | 23 | 7AM to 8AM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
May | 23 | 8AM to 9AM | 66.2 | 53.5 | 42.8 | 40.8 | 22.24 | 0.0751 | 0.28 | 13.39 | 0
May | 23 | 9AM to 10AM | 71.6 | 56.4 | 44.6 | 43.7 | 24 | 0.0744 | 0.3 | 13.53 | 0
May | 23 | 10AM to 11AM | 73.4 | 56.4 | 42.8 | 40.8 | 23.98 | 0.0741 | 0.28 | 13.57 | 0
May | 23 | 11AM to 12PM | 77 | 57.8 | 42.8 | 40.8 | 24.86 | 0.0736 | 0.28 | 13.66 | 0
May | 23 | 12PM to 1PM | 78.8 | 58.4 | 42.8 | 40.8 | 25.29 | 0.0734 | 0.28 | 13.71 | 0
May | 23 | 1PM to 2PM | 80.6 | 58.5 | 41 | 38 | 25.3 | 0.0731 | 0.26 | 13.74 | 0
May | 23 | 2PM to 3PM | 80.6 | 57.8 | 39.2 | 35.4 | 24.89 | 0.0732 | 0.24 | 13.74 | 0
May | 23 | 3PM to 4PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
May | 23 | 4PM to 5PM | 80.6 | 58.5 | 41 | 38 | 25.3 | 0.0731 | 0.26 | 13.74 | 0
May | 23 | 5PM to 6PM | 80.6 | 59.1 | 42.8 | 40.8 | 25.73 | 0.0731 | 0.28 | 13.75 | 0
May | 23 | 6PM to 7PM | 75.2 | 57.8 | 44.6 | 43.7 | 24.88 | 0.0739 | 0.3 | 13.63 | 0
May | 23 | 7PM to 8PM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
May | 23 | 8PM to 9PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
May | 23 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
May | 23 | 10PM to 11PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
May | 23 | 11PM to 12AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
May | 24 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 24 | 1AM to 2AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
May | 24 | 2AM to 3AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
May | 24 | 3AM to 4AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
May | 24 | 4AM to 5AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
May | 24 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
May | 24 | 6AM to 7AM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
May | 24 | 7AM to 8AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
May | 24 | 8AM to 9AM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
May | 24 | 9AM to 10AM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
May | 24 | 10AM to 11AM | 77 | 59.2 | 46.4 | 46.8 | 25.8 | 0.0736 | 0.32 | 13.68 | 0
May | 24 | 11AM to 12PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
May | 24 | 12PM to 1PM | 80.6 | 59.1 | 42.8 | 40.8 | 25.73 | 0.0731 | 0.28 | 13.75 | 0
May | 24 | 1PM to 2PM | 84.2 | 61.1 | 44.6 | 43.7 | 27.06 | 0.0726 | 0.3 | 13.85 | 0
May | 24 | 2PM to 3PM | 84.2 | 61.8 | 46.4 | 46.8 | 27.55 | 0.0726 | 0.32 | 13.86 | 0
May | 24 | 3PM to 4PM | 87.8 | 63.7 | 48.2 | 50.1 | 28.95 | 0.0721 | 0.34 | 13.97 | 0
May | 24 | 4PM to 5PM | 86.7 | 63.2 | 47.7 | 49.1 | 28.53 | 0.0723 | 0.33 | 13.94 | 0
May | 24 | 5PM to 6PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
May | 24 | 6PM to 7PM | 82.4 | 61.1 | 46.4 | 46.8 | 27.12 | 0.0729 | 0.32 | 13.82 | 0
May | 24 | 7PM to 8PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
May | 24 | 8PM to 9PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
May | 24 | 9PM to 10PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
May | 24 | 10PM to 11PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
May | 24 | 11PM to 12AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
May | 25 | 12AM to 1AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
May | 25 | 1AM to 2AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
May | 25 | 2AM to 3AM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
May | 25 | 3AM to 4AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
May | 25 | 4AM to 5AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
May | 25 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 25 | 6AM to 7AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
May | 25 | 7AM to 8AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
May | 25 | 8AM to 9AM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
May | 25 | 9AM to 10AM | 78.8 | 61.4 | 50 | 53.7 | 27.31 | 0.0733 | 0.36 | 13.75 | 0
May | 25 | 10AM to 11AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
May | 25 | 11AM to 12PM | 82.4 | 62.7 | 50 | 53.7 | 28.19 | 0.0728 | 0.36 | 13.84 | 0
May | 25 | 12PM to 1PM | 86 | 64.7 | 51.8 | 57.4 | 29.66 | 0.0723 | 0.39 | 13.94 | 0
May | 25 | 1PM to 2PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
May | 25 | 2PM to 3PM | 89.6 | 63 | 44.6 | 43.7 | 28.37 | 0.0719 | 0.3 | 13.99 | 0
May | 25 | 3PM to 4PM | 87.8 | 62.4 | 44.6 | 43.7 | 27.94 | 0.0722 | 0.3 | 13.95 | 0
May | 25 | 4PM to 5PM | 84.2 | 63.3 | 50 | 53.7 | 28.63 | 0.0726 | 0.36 | 13.89 | 0
May | 25 | 5PM to 6PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
May | 25 | 6PM to 7PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
May | 25 | 7PM to 8PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
May | 25 | 8PM to 9PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
May | 25 | 9PM to 10PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
May | 25 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 25 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 26 | 12AM to 1AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
May | 26 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
May | 26 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
May | 26 | 3AM to 4AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
May | 26 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
May | 26 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
May | 26 | 6AM to 7AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 26 | 7AM to 8AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
May | 26 | 8AM to 9AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
May | 26 | 9AM to 10AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
May | 26 | 10AM to 11AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
May | 26 | 11AM to 12PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
May | 26 | 12PM to 1PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
May | 26 | 1PM to 2PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
May | 26 | 2PM to 3PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
May | 26 | 3PM to 4PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
May | 26 | 4PM to 5PM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
May | 26 | 5PM to 6PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
May | 26 | 6PM to 7PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
May | 26 | 7PM to 8PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
May | 26 | 8PM to 9PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
May | 26 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
May | 26 | 10PM to 11PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
May | 26 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 27 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 27 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 27 | 2AM to 3AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
May | 27 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
May | 27 | 4AM to 5AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
May | 27 | 5AM to 6AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
May | 27 | 6AM to 7AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
May | 27 | 7AM to 8AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
May | 27 | 8AM to 9AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
May | 27 | 9AM to 10AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
May | 27 | 10AM to 11AM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
May | 27 | 11AM to 12PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
May | 27 | 12PM to 1PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
May | 27 | 1PM to 2PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
May | 27 | 2PM to 3PM | 78.8 | 61.4 | 50 | 53.7 | 27.31 | 0.0733 | 0.36 | 13.75 | 0
May | 27 | 3PM to 4PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
May | 27 | 4PM to 5PM | 75.2 | 60.1 | 50 | 53.7 | 26.44 | 0.0738 | 0.36 | 13.66 | 0
May | 27 | 5PM to 6PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
May | 27 | 6PM to 7PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
May | 27 | 7PM to 8PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
May | 27 | 8PM to 9PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
May | 27 | 9PM to 10PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
May | 27 | 10PM to 11PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
May | 27 | 11PM to 12AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
May | 28 | 12AM to 1AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
May | 28 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
May | 28 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
May | 28 | 3AM to 4AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
May | 28 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
May | 28 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
May | 28 | 6AM to 7AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
May | 28 | 7AM to 8AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
May | 28 | 8AM to 9AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
May | 28 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
May | 28 | 10AM to 11AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
May | 28 | 11AM to 12PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
May | 28 | 12PM to 1PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
May | 28 | 1PM to 2PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
May | 28 | 2PM to 3PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
May | 28 | 3PM to 4PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
May | 28 | 4PM to 5PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
May | 28 | 5PM to 6PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
May | 28 | 6PM to 7PM | 78.8 | 67.9 | 62.6 | 85.3 | 32.27 | 0.0731 | 0.57 | 13.85 | 0
May | 28 | 7PM to 8PM | 71.6 | 64.5 | 60.8 | 79.9 | 29.67 | 0.0741 | 0.54 | 13.64 | 0
May | 28 | 8PM to 9PM | 66.2 | 62.7 | 60.8 | 79.9 | 28.34 | 0.0749 | 0.54 | 13.51 | 0
May | 28 | 9PM to 10PM | 64.4 | 61 | 59 | 74.9 | 27.11 | 0.0752 | 0.5 | 13.44 | 0
May | 28 | 10PM to 11PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
May | 28 | 11PM to 12AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
May | 29 | 12AM to 1AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
May | 29 | 1AM to 2AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
May | 29 | 2AM to 3AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
May | 29 | 3AM to 4AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
May | 29 | 4AM to 5AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
May | 29 | 5AM to 6AM | 61.5 | 58.7 | 57 | 69.7 | 25.6 | 0.0756 | 0.47 | 13.35 | 0
May | 29 | 6AM to 7AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
May | 29 | 7AM to 8AM | 68 | 63.3 | 60.8 | 79.9 | 28.78 | 0.0746 | 0.54 | 13.55 | 0
May | 29 | 8AM to 9AM | 73.4 | 65.1 | 60.8 | 79.9 | 30.11 | 0.0739 | 0.54 | 13.69 | 0
May | 29 | 9AM to 10AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
May | 29 | 10AM to 11AM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
May | 29 | 11AM to 12PM | 84.2 | 69.6 | 62.6 | 85.3 | 33.59 | 0.0724 | 0.57 | 13.99 | 0
May | 29 | 12PM to 1PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
May | 29 | 1PM to 2PM | 91.4 | 69.8 | 59 | 74.9 | 33.72 | 0.0715 | 0.5 | 14.14 | 0
May | 29 | 2PM to 3PM | 91.4 | 69.8 | 59 | 74.9 | 33.72 | 0.0715 | 0.5 | 14.14 | 0
May | 29 | 3PM to 4PM | 91.4 | 72.7 | 64.4 | 91 | 36.25 | 0.0714 | 0.61 | 14.19 | 0
May | 29 | 4PM to 5PM | 91.4 | 72.7 | 64.4 | 91 | 36.25 | 0.0714 | 0.61 | 14.19 | 0
May | 29 | 5PM to 6PM | 91.4 | 72.7 | 64.4 | 91 | 36.25 | 0.0714 | 0.61 | 14.19 | 0
May | 29 | 6PM to 7PM | 89.6 | 72.1 | 64.4 | 91 | 35.81 | 0.0716 | 0.61 | 14.14 | 0
May | 29 | 7PM to 8PM | 80.6 | 70.6 | 66.2 | 97 | 34.54 | 0.0728 | 0.65 | 13.93 | 0
May | 29 | 8PM to 9PM | 78.8 | 71.2 | 68 | 103.4 | 35.1 | 0.073 | 0.69 | 13.9 | 0
May | 29 | 9PM to 10PM | 75.2 | 67.9 | 64.4 | 91 | 32.27 | 0.0736 | 0.61 | 13.77 | 0
May | 29 | 10PM to 11PM | 73.4 | 67.3 | 64.4 | 91 | 31.83 | 0.0738 | 0.61 | 13.73 | 0
May | 29 | 11PM to 12AM | 71.6 | 66.7 | 64.4 | 91 | 31.39 | 0.0741 | 0.61 | 13.68 | 0
May | 30 | 12AM to 1AM | 71.6 | 66.7 | 64.4 | 91 | 31.39 | 0.0741 | 0.61 | 13.68 | 0
May | 30 | 1AM to 2AM | 71.6 | 66.7 | 64.4 | 91 | 31.39 | 0.0741 | 0.61 | 13.68 | 0
May | 30 | 2AM to 3AM | 69.8 | 65 | 62.6 | 85.3 | 30.06 | 0.0743 | 0.57 | 13.61 | 0
May | 30 | 3AM to 4AM | 66.2 | 63.8 | 62.6 | 85.3 | 29.18 | 0.0749 | 0.57 | 13.52 | 0
May | 30 | 4AM to 5AM | 64.4 | 63.2 | 62.6 | 85.3 | 28.73 | 0.0751 | 0.57 | 13.48 | 0
May | 30 | 5AM to 6AM | 71.6 | 65.6 | 62.6 | 85.3 | 30.5 | 0.0741 | 0.57 | 13.66 | 0
May | 30 | 6AM to 7AM | 75.2 | 66.8 | 62.6 | 85.3 | 31.39 | 0.0736 | 0.57 | 13.75 | 0
May | 30 | 7AM to 8AM | 80.6 | 69.5 | 64.4 | 91 | 33.6 | 0.0728 | 0.61 | 13.91 | 0
May | 30 | 8AM to 9AM | 82.4 | 71.1 | 66.2 | 97 | 34.99 | 0.0725 | 0.65 | 13.98 | 0
May | 30 | 9AM to 10AM | 84.2 | 71.7 | 66.2 | 97 | 35.43 | 0.0723 | 0.65 | 14.02 | 0
May | 30 | 10AM to 11AM | 87.8 | 71.6 | 64.4 | 91 | 35.37 | 0.0719 | 0.61 | 14.1 | 0
May | 30 | 11AM to 12PM | 91.4 | 73.7 | 66.2 | 97 | 37.2 | 0.0714 | 0.65 | 14.21 | 0
May | 30 | 12PM to 1PM | 93.2 | 73.2 | 64.4 | 91 | 36.7 | 0.0712 | 0.61 | 14.23 | 0
May | 30 | 1PM to 2PM | 95 | 74.7 | 66.2 | 97 | 38.09 | 0.0709 | 0.65 | 14.3 | 0
May | 30 | 2PM to 3PM | 96.8 | 74.1 | 64.4 | 91 | 37.58 | 0.0707 | 0.61 | 14.33 | 0
May | 30 | 3PM to 4PM | 96.8 | 74.1 | 64.4 | 91 | 37.58 | 0.0707 | 0.61 | 14.33 | 0
May | 30 | 4PM to 5PM | 96.8 | 73.2 | 62.6 | 85.3 | 36.69 | 0.0707 | 0.57 | 14.31 | 0
May | 30 | 5PM to 6PM | 93.2 | 71.2 | 60.8 | 79.9 | 34.96 | 0.0712 | 0.54 | 14.2 | 0
May | 30 | 6PM to 7PM | 87.8 | 71.6 | 64.4 | 91 | 35.37 | 0.0719 | 0.61 | 14.1 | 0
May | 30 | 7PM to 8PM | 78.8 | 67.9 | 62.6 | 85.3 | 32.27 | 0.0731 | 0.57 | 13.85 | 0
May | 30 | 8PM to 9PM | 75.2 | 64.7 | 59 | 74.9 | 29.76 | 0.0737 | 0.5 | 13.72 | 0
May | 30 | 9PM to 10PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
May | 30 | 10PM to 11PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
May | 30 | 11PM to 12AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
May | 31 | 12AM to 1AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
May | 31 | 1AM to 2AM | 68 | 56.6 | 48.2 | 50.1 | 24.14 | 0.0748 | 0.34 | 13.46 | 0
May | 31 | 2AM to 3AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
May | 31 | 3AM to 4AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
May | 31 | 4AM to 5AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
May | 31 | 5AM to 6AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
May | 31 | 6AM to 7AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
May | 31 | 7AM to 8AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
May | 31 | 8AM to 9AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
May | 31 | 9AM to 10AM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
May | 31 | 10AM to 11AM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
May | 31 | 11AM to 12PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
May | 31 | 12PM to 1PM | 89.6 | 69.2 | 59 | 74.9 | 33.28 | 0.0717 | 0.5 | 14.09 | 0
May | 31 | 1PM to 2PM | 93.2 | 70.3 | 59 | 74.9 | 34.16 | 0.0713 | 0.5 | 14.18 | 0
May | 31 | 2PM to 3PM | 93.2 | 70.3 | 59 | 74.9 | 34.16 | 0.0713 | 0.5 | 14.18 | 0
May | 31 | 3PM to 4PM | 93.2 | 64.9 | 46.4 | 46.8 | 29.74 | 0.0714 | 0.32 | 14.09 | 0
May | 31 | 4PM to 5PM | 91.4 | 64.9 | 48.2 | 50.1 | 29.83 | 0.0716 | 0.34 | 14.06 | 0
May | 31 | 5PM to 6PM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
May | 31 | 6PM to 7PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
May | 31 | 7PM to 8PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
May | 31 | 8PM to 9PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
May | 31 | 9PM to 10PM | 63.9 | 56.8 | 52 | 57.8 | 24.32 | 0.0754 | 0.39 | 13.38 | 0
May | 31 | 10PM to 11PM | 61.5 | 55.1 | 50.5 | 54.8 | 23.28 | 0.0757 | 0.37 | 13.31 | 0
May | 31 | 11PM to 12AM | 59.2 | 53.4 | 48.9 | 51.5 | 22.21 | 0.0761 | 0.35 | 13.24 | 0
June | 1 | 12AM to 1AM | 57 | 51.7 | 47.5 | 48.8 | 21.26 | 0.0764 | 0.33 | 13.18 | 0
June | 1 | 1AM to 2AM | 54.7 | 49.9 | 45.9 | 45.9 | 20.23 | 0.0768 | 0.31 | 13.11 | 0
June | 1 | 2AM to 3AM | 52.3 | 48.2 | 44.4 | 43.4 | 19.28 | 0.0772 | 0.29 | 13.04 | 0
June | 1 | 3AM to 4AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
June | 1 | 4AM to 5AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
June | 1 | 5AM to 6AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
June | 1 | 6AM to 7AM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
June | 1 | 7AM to 8AM | 66.2 | 54.2 | 44.6 | 43.7 | 22.69 | 0.0751 | 0.3 | 13.4 | 0
June | 1 | 8AM to 9AM | 71.6 | 56.4 | 44.6 | 43.7 | 24 | 0.0744 | 0.3 | 13.53 | 0
June | 1 | 9AM to 10AM | 73.4 | 57.1 | 44.6 | 43.7 | 24.44 | 0.0741 | 0.3 | 13.58 | 0
June | 1 | 10AM to 11AM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
June | 1 | 11AM to 12PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
June | 1 | 12PM to 1PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
June | 1 | 1PM to 2PM | 86 | 62.4 | 46.4 | 46.8 | 27.99 | 0.0724 | 0.32 | 13.91 | 0
June | 1 | 2PM to 3PM | 87.8 | 62.4 | 44.6 | 43.7 | 27.94 | 0.0722 | 0.3 | 13.95 | 0
June | 1 | 3PM to 4PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
June | 1 | 4PM to 5PM | 87.8 | 60 | 37.4 | 33 | 26.25 | 0.0722 | 0.22 | 13.91 | 0
June | 1 | 5PM to 6PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
June | 1 | 6PM to 7PM | 82.4 | 60.4 | 44.6 | 43.7 | 26.63 | 0.0729 | 0.3 | 13.81 | 0
June | 1 | 7PM to 8PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
June | 1 | 8PM to 9PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
June | 1 | 9PM to 10PM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
June | 1 | 10PM to 11PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
June | 1 | 11PM to 12AM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
June | 2 | 12AM to 1AM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
June | 2 | 1AM to 2AM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
June | 2 | 2AM to 3AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
June | 2 | 3AM to 4AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
June | 2 | 4AM to 5AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
June | 2 | 5AM to 6AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
June | 2 | 6AM to 7AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
June | 2 | 7AM to 8AM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
June | 2 | 8AM to 9AM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
June | 2 | 9AM to 10AM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
June | 2 | 10AM to 11AM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
June | 2 | 11AM to 12PM | 84.2 | 61.1 | 44.6 | 43.7 | 27.06 | 0.0726 | 0.3 | 13.85 | 0
June | 2 | 12PM to 1PM | 87.8 | 61.1 | 41 | 38 | 27.04 | 0.0722 | 0.26 | 13.93 | 0
June | 2 | 1PM to 2PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
June | 2 | 2PM to 3PM | 89.6 | 63 | 44.6 | 43.7 | 28.37 | 0.0719 | 0.3 | 13.99 | 0
June | 2 | 3PM to 4PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
June | 2 | 4PM to 5PM | 87.8 | 59.4 | 35.6 | 30.7 | 25.89 | 0.0722 | 0.21 | 13.9 | 0
June | 2 | 5PM to 6PM | 82.4 | 57.9 | 37.4 | 33 | 24.95 | 0.0729 | 0.22 | 13.77 | 0
June | 2 | 6PM to 7PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
June | 2 | 7PM to 8PM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
June | 2 | 8PM to 9PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
June | 2 | 9PM to 10PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
June | 2 | 10PM to 11PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
June | 2 | 11PM to 12AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
June | 3 | 12AM to 1AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
June | 3 | 1AM to 2AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
June | 3 | 2AM to 3AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
June | 3 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
June | 3 | 4AM to 5AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
June | 3 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
June | 3 | 6AM to 7AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
June | 3 | 7AM to 8AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
June | 3 | 8AM to 9AM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
June | 3 | 9AM to 10AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
June | 3 | 10AM to 11AM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
June | 3 | 11AM to 12PM | 82.4 | 61.9 | 48.2 | 50.1 | 27.64 | 0.0728 | 0.34 | 13.83 | 0
June | 3 | 12PM to 1PM | 86 | 63.9 | 50 | 53.7 | 29.07 | 0.0723 | 0.36 | 13.93 | 0
June | 3 | 1PM to 2PM | 87.8 | 61.1 | 41 | 38 | 27.04 | 0.0722 | 0.26 | 13.93 | 0
June | 3 | 2PM to 3PM | 89.6 | 62.3 | 42.8 | 40.8 | 27.91 | 0.0719 | 0.28 | 13.98 | 0
June | 3 | 3PM to 4PM | 89.6 | 63 | 44.6 | 43.7 | 28.37 | 0.0719 | 0.3 | 13.99 | 0
June | 3 | 4PM to 5PM | 87.8 | 63.7 | 48.2 | 50.1 | 28.95 | 0.0721 | 0.34 | 13.97 | 0
June | 3 | 5PM to 6PM | 82.4 | 61.1 | 46.4 | 46.8 | 27.12 | 0.0729 | 0.32 | 13.82 | 0
June | 3 | 6PM to 7PM | 78.8 | 61.4 | 50 | 53.7 | 27.31 | 0.0733 | 0.36 | 13.75 | 0
June | 3 | 7PM to 8PM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
June | 3 | 8PM to 9PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
June | 3 | 9PM to 10PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
June | 3 | 10PM to 11PM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
June | 3 | 11PM to 12AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
June | 4 | 12AM to 1AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
June | 4 | 1AM to 2AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
June | 4 | 2AM to 3AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
June | 4 | 3AM to 4AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
June | 4 | 4AM to 5AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
June | 4 | 5AM to 6AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
June | 4 | 6AM to 7AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
June | 4 | 7AM to 8AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
June | 4 | 8AM to 9AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
June | 4 | 9AM to 10AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
June | 4 | 10AM to 11AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
June | 4 | 11AM to 12PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
June | 4 | 12PM to 1PM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
June | 4 | 1PM to 2PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
June | 4 | 2PM to 3PM | 87.8 | 61.1 | 41 | 38 | 27.04 | 0.0722 | 0.26 | 13.93 | 0
June | 4 | 3PM to 4PM | 87.8 | 60.5 | 39.2 | 35.4 | 26.64 | 0.0722 | 0.24 | 13.92 | 0
June | 4 | 4PM to 5PM | 84.2 | 61.8 | 46.4 | 46.8 | 27.55 | 0.0726 | 0.32 | 13.86 | 0
June | 4 | 5PM to 6PM | 77 | 61.6 | 51.8 | 57.4 | 27.46 | 0.0735 | 0.39 | 13.71 | 0
June | 4 | 6PM to 7PM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
June | 4 | 7PM to 8PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
June | 4 | 8PM to 9PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
June | 4 | 9PM to 10PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
June | 4 | 10PM to 11PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
June | 4 | 11PM to 12AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
June | 5 | 12AM to 1AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
June | 5 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
June | 5 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
June | 5 | 3AM to 4AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
June | 5 | 4AM to 5AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
June | 5 | 5AM to 6AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
June | 5 | 6AM to 7AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
June | 5 | 7AM to 8AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
June | 5 | 8AM to 9AM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
June | 5 | 9AM to 10AM | 68 | 54.2 | 42.8 | 40.8 | 22.67 | 0.0749 | 0.28 | 13.43 | 0
June | 5 | 10AM to 11AM | 71.6 | 54.3 | 39.2 | 35.4 | 22.71 | 0.0744 | 0.24 | 13.51 | 0
June | 5 | 11AM to 12PM | 75.2 | 57.1 | 42.8 | 40.8 | 24.42 | 0.0739 | 0.28 | 13.62 | 0
June | 5 | 12PM to 1PM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
June | 5 | 1PM to 2PM | 82.4 | 61.9 | 48.2 | 50.1 | 27.64 | 0.0728 | 0.34 | 13.83 | 0
June | 5 | 2PM to 3PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
June | 5 | 3PM to 4PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
June | 5 | 4PM to 5PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
June | 5 | 5PM to 6PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
June | 5 | 6PM to 7PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 5 | 7PM to 8PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
June | 5 | 8PM to 9PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
June | 5 | 9PM to 10PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
June | 5 | 10PM to 11PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
June | 5 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 6 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 6 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 6 | 2AM to 3AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
June | 6 | 3AM to 4AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
June | 6 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 6 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 6 | 6AM to 7AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
June | 6 | 7AM to 8AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
June | 6 | 8AM to 9AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
June | 6 | 9AM to 10AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
June | 6 | 10AM to 11AM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
June | 6 | 11AM to 12PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
June | 6 | 12PM to 1PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
June | 6 | 1PM to 2PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
June | 6 | 2PM to 3PM | 84.2 | 63.3 | 50 | 53.7 | 28.63 | 0.0726 | 0.36 | 13.89 | 0
June | 6 | 3PM to 4PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
June | 6 | 4PM to 5PM | 82.4 | 61.9 | 48.2 | 50.1 | 27.64 | 0.0728 | 0.34 | 13.83 | 0
June | 6 | 5PM to 6PM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
June | 6 | 6PM to 7PM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
June | 6 | 7PM to 8PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
June | 6 | 8PM to 9PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
June | 6 | 9PM to 10PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
June | 6 | 10PM to 11PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
June | 6 | 11PM to 12AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
June | 7 | 12AM to 1AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
June | 7 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 7 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 7 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 7 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 7 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
June | 7 | 6AM to 7AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 7 | 7AM to 8AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 7 | 8AM to 9AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
June | 7 | 9AM to 10AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
June | 7 | 10AM to 11AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
June | 7 | 11AM to 12PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
June | 7 | 12PM to 1PM | 77 | 61.6 | 51.8 | 57.4 | 27.46 | 0.0735 | 0.39 | 13.71 | 0
June | 7 | 1PM to 2PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
June | 7 | 2PM to 3PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
June | 7 | 3PM to 4PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
June | 7 | 4PM to 5PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 7 | 5PM to 6PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
June | 7 | 6PM to 7PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 7 | 7PM to 8PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 7 | 8PM to 9PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 7 | 9PM to 10PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 7 | 10PM to 11PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
June | 7 | 11PM to 12AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 8 | 12AM to 1AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 8 | 1AM to 2AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
June | 8 | 2AM to 3AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
June | 8 | 3AM to 4AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
June | 8 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
June | 8 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
June | 8 | 6AM to 7AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 8 | 7AM to 8AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 8 | 8AM to 9AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
June | 8 | 9AM to 10AM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
June | 8 | 10AM to 11AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
June | 8 | 11AM to 12PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
June | 8 | 12PM to 1PM | 68 | 56.6 | 48.2 | 50.1 | 24.14 | 0.0748 | 0.34 | 13.46 | 0
June | 8 | 1PM to 2PM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
June | 8 | 2PM to 3PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
June | 8 | 3PM to 4PM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
June | 8 | 4PM to 5PM | 72.3 | 58.5 | 48.7 | 51.2 | 25.35 | 0.0742 | 0.35 | 13.57 | 0
June | 8 | 5PM to 6PM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
June | 8 | 6PM to 7PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
June | 8 | 7PM to 8PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 8 | 8PM to 9PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 8 | 9PM to 10PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 8 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 8 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 9 | 12AM to 1AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 9 | 1AM to 2AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
June | 9 | 2AM to 3AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
June | 9 | 3AM to 4AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
June | 9 | 4AM to 5AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
June | 9 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
June | 9 | 6AM to 7AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
June | 9 | 7AM to 8AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
June | 9 | 8AM to 9AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
June | 9 | 9AM to 10AM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
June | 9 | 10AM to 11AM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
June | 9 | 11AM to 12PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
June | 9 | 12PM to 1PM | 71.8 | 58.5 | 49.3 | 52.2 | 25.38 | 0.0743 | 0.35 | 13.56 | 0
June | 9 | 1PM to 2PM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
June | 9 | 2PM to 3PM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
June | 9 | 3PM to 4PM | 77 | 60 | 48.2 | 50.1 | 26.32 | 0.0736 | 0.34 | 13.69 | 0
June | 9 | 4PM to 5PM | 77 | 60.8 | 50 | 53.7 | 26.88 | 0.0735 | 0.36 | 13.7 | 0
June | 9 | 5PM to 6PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
June | 9 | 6PM to 7PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
June | 9 | 7PM to 8PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 9 | 8PM to 9PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 9 | 9PM to 10PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 9 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 9 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 10 | 12AM to 1AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 10 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 10 | 2AM to 3AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
June | 10 | 3AM to 4AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
June | 10 | 4AM to 5AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
June | 10 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
June | 10 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 10 | 7AM to 8AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 10 | 8AM to 9AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
June | 10 | 9AM to 10AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
June | 10 | 10AM to 11AM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
June | 10 | 11AM to 12PM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
June | 10 | 12PM to 1PM | 73.4 | 57.1 | 44.6 | 43.7 | 24.44 | 0.0741 | 0.3 | 13.58 | 0
June | 10 | 1PM to 2PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
June | 10 | 2PM to 3PM | 75.2 | 56.4 | 41 | 38 | 23.99 | 0.0739 | 0.26 | 13.61 | 0
June | 10 | 3PM to 4PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
June | 10 | 4PM to 5PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
June | 10 | 5PM to 6PM | 77 | 59.2 | 46.4 | 46.8 | 25.8 | 0.0736 | 0.32 | 13.68 | 0
June | 10 | 6PM to 7PM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
June | 10 | 7PM to 8PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
June | 10 | 8PM to 9PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
June | 10 | 9PM to 10PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
June | 10 | 10PM to 11PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
June | 10 | 11PM to 12AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
June | 11 | 12AM to 1AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
June | 11 | 1AM to 2AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
June | 11 | 2AM to 3AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
June | 11 | 3AM to 4AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
June | 11 | 4AM to 5AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
June | 11 | 5AM to 6AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
June | 11 | 6AM to 7AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
June | 11 | 7AM to 8AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
June | 11 | 8AM to 9AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
June | 11 | 9AM to 10AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
June | 11 | 10AM to 11AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
June | 11 | 11AM to 12PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
June | 11 | 12PM to 1PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
June | 11 | 1PM to 2PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
June | 11 | 2PM to 3PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
June | 11 | 3PM to 4PM | 82.4 | 62.7 | 50 | 53.7 | 28.19 | 0.0728 | 0.36 | 13.84 | 0
June | 11 | 4PM to 5PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
June | 11 | 5PM to 6PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
June | 11 | 6PM to 7PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
June | 11 | 7PM to 8PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
June | 11 | 8PM to 9PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
June | 11 | 9PM to 10PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 11 | 10PM to 11PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 11 | 11PM to 12AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 12 | 12AM to 1AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 12 | 1AM to 2AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 12 | 2AM to 3AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 12 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 12 | 4AM to 5AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 12 | 5AM to 6AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 12 | 6AM to 7AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 12 | 7AM to 8AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 12 | 8AM to 9AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
June | 12 | 9AM to 10AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
June | 12 | 10AM to 11AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
June | 12 | 11AM to 12PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
June | 12 | 12PM to 1PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
June | 12 | 1PM to 2PM | 86 | 64.7 | 51.8 | 57.4 | 29.66 | 0.0723 | 0.39 | 13.94 | 0
June | 12 | 2PM to 3PM | 87.8 | 63.7 | 48.2 | 50.1 | 28.95 | 0.0721 | 0.34 | 13.97 | 0
June | 12 | 3PM to 4PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
June | 12 | 4PM to 5PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
June | 12 | 5PM to 6PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
June | 12 | 6PM to 7PM | 84.2 | 69.6 | 62.6 | 85.3 | 33.59 | 0.0724 | 0.57 | 13.99 | 0
June | 12 | 7PM to 8PM | 80.6 | 68.5 | 62.6 | 85.3 | 32.71 | 0.0729 | 0.57 | 13.89 | 0
June | 12 | 8PM to 9PM | 78.8 | 65.9 | 59 | 74.9 | 30.64 | 0.0732 | 0.5 | 13.81 | 0
June | 12 | 9PM to 10PM | 77 | 67.3 | 62.6 | 85.3 | 31.83 | 0.0733 | 0.57 | 13.8 | 0
June | 12 | 10PM to 11PM | 71.6 | 65.6 | 62.6 | 85.3 | 30.5 | 0.0741 | 0.57 | 13.66 | 0
June | 12 | 11PM to 12AM | 71.6 | 65.6 | 62.6 | 85.3 | 30.5 | 0.0741 | 0.57 | 13.66 | 0
June | 13 | 12AM to 1AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 13 | 1AM to 2AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 13 | 2AM to 3AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
June | 13 | 3AM to 4AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 13 | 4AM to 5AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
June | 13 | 5AM to 6AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
June | 13 | 6AM to 7AM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
June | 13 | 7AM to 8AM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
June | 13 | 8AM to 9AM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
June | 13 | 9AM to 10AM | 86 | 64.7 | 51.8 | 57.4 | 29.66 | 0.0723 | 0.39 | 13.94 | 0
June | 13 | 10AM to 11AM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
June | 13 | 11AM to 12PM | 93.2 | 65.5 | 48.2 | 50.1 | 30.26 | 0.0714 | 0.34 | 14.1 | 0
June | 13 | 12PM to 1PM | 96.8 | 68.1 | 51.8 | 57.4 | 32.29 | 0.0709 | 0.39 | 14.22 | 0
June | 13 | 1PM to 2PM | 98.6 | 69.4 | 53.6 | 61.4 | 33.36 | 0.0707 | 0.41 | 14.28 | 0
June | 13 | 2PM to 3PM | 98.6 | 69.4 | 53.6 | 61.4 | 33.36 | 0.0707 | 0.41 | 14.28 | 0
June | 13 | 3PM to 4PM | 100.4 | 71.5 | 57.2 | 70.1 | 35.17 | 0.0704 | 0.47 | 14.35 | 0
June | 13 | 4PM to 5PM | 98.6 | 71 | 57.2 | 70.1 | 34.73 | 0.0706 | 0.47 | 14.31 | 0
June | 13 | 5PM to 6PM | 96.8 | 70.5 | 57.2 | 70.1 | 34.29 | 0.0708 | 0.47 | 14.26 | 0
June | 13 | 6PM to 7PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
June | 13 | 7PM to 8PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
June | 13 | 8PM to 9PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
June | 13 | 9PM to 10PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
June | 13 | 10PM to 11PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
June | 13 | 11PM to 12AM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
June | 14 | 12AM to 1AM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
June | 14 | 1AM to 2AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 14 | 2AM to 3AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 14 | 3AM to 4AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 14 | 4AM to 5AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 14 | 5AM to 6AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 14 | 6AM to 7AM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
June | 14 | 7AM to 8AM | 84.2 | 69.6 | 62.6 | 85.3 | 33.59 | 0.0724 | 0.57 | 13.99 | 0
June | 14 | 8AM to 9AM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
June | 14 | 9AM to 10AM | 93.2 | 70.3 | 59 | 74.9 | 34.16 | 0.0713 | 0.5 | 14.18 | 0
June | 14 | 10AM to 11AM | 96.8 | 72.3 | 60.8 | 79.9 | 35.84 | 0.0708 | 0.54 | 14.29 | 0
June | 14 | 11AM to 12PM | 102.2 | 70.5 | 53.6 | 61.4 | 34.23 | 0.0702 | 0.41 | 14.37 | 0
June | 14 | 12PM to 1PM | 102.2 | 71.3 | 55.4 | 65.6 | 34.9 | 0.0702 | 0.44 | 14.38 | 0
June | 14 | 1PM to 2PM | 104 | 71.8 | 55.4 | 65.6 | 35.34 | 0.0699 | 0.44 | 14.43 | 0
June | 14 | 2PM to 3PM | 105.8 | 72.3 | 55.4 | 65.6 | 35.78 | 0.0697 | 0.44 | 14.48 | 0
June | 14 | 3PM to 4PM | 107.6 | 72.1 | 53.6 | 61.4 | 35.55 | 0.0695 | 0.41 | 14.51 | 0
June | 14 | 4PM to 5PM | 105.8 | 71.5 | 53.6 | 61.4 | 35.11 | 0.0698 | 0.41 | 14.46 | 0
June | 14 | 5PM to 6PM | 104 | 71.8 | 55.4 | 65.6 | 35.34 | 0.0699 | 0.44 | 14.43 | 0
June | 14 | 6PM to 7PM | 96.8 | 73.2 | 62.6 | 85.3 | 36.69 | 0.0707 | 0.57 | 14.31 | 0
June | 14 | 7PM to 8PM | 87.8 | 74.9 | 69.8 | 110.1 | 38.38 | 0.0718 | 0.73 | 14.16 | 0
June | 14 | 8PM to 9PM | 82.4 | 71.1 | 66.2 | 97 | 34.99 | 0.0725 | 0.65 | 13.98 | 0
June | 14 | 9PM to 10PM | 80.6 | 68.5 | 62.6 | 85.3 | 32.71 | 0.0729 | 0.57 | 13.89 | 0
June | 14 | 10PM to 11PM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
June | 14 | 11PM to 12AM | 87.8 | 63.7 | 48.2 | 50.1 | 28.95 | 0.0721 | 0.34 | 13.97 | 0
June | 15 | 12AM to 1AM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
June | 15 | 1AM to 2AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 15 | 2AM to 3AM | 73.4 | 65.1 | 60.8 | 79.9 | 30.11 | 0.0739 | 0.54 | 13.69 | 0
June | 15 | 3AM to 4AM | 71.6 | 65.6 | 62.6 | 85.3 | 30.5 | 0.0741 | 0.57 | 13.66 | 0
June | 15 | 4AM to 5AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
June | 15 | 5AM to 6AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
June | 15 | 6AM to 7AM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
June | 15 | 7AM to 8AM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
June | 15 | 8AM to 9AM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
June | 15 | 9AM to 10AM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
June | 15 | 10AM to 11AM | 95 | 70.8 | 59 | 74.9 | 34.6 | 0.071 | 0.5 | 14.23 | 0
June | 15 | 11AM to 12PM | 98.6 | 72.8 | 60.8 | 79.9 | 36.28 | 0.0705 | 0.54 | 14.34 | 0
June | 15 | 12PM to 1PM | 100.4 | 72.4 | 59 | 74.9 | 35.92 | 0.0703 | 0.5 | 14.37 | 0
June | 15 | 1PM to 2PM | 100.4 | 72.4 | 59 | 74.9 | 35.92 | 0.0703 | 0.5 | 14.37 | 0
June | 15 | 2PM to 3PM | 102.2 | 72.1 | 57.2 | 70.1 | 35.61 | 0.0701 | 0.47 | 14.4 | 0
June | 15 | 3PM to 4PM | 102.2 | 72.9 | 59 | 74.9 | 36.37 | 0.0701 | 0.5 | 14.41 | 0
June | 15 | 4PM to 5PM | 100.4 | 72.4 | 59 | 74.9 | 35.92 | 0.0703 | 0.5 | 14.37 | 0
June | 15 | 5PM to 6PM | 98.6 | 72.8 | 60.8 | 79.9 | 36.28 | 0.0705 | 0.54 | 14.34 | 0
June | 15 | 6PM to 7PM | 93.2 | 75.2 | 68 | 103.4 | 38.65 | 0.0711 | 0.69 | 14.27 | 0
June | 15 | 7PM to 8PM | 86 | 73.3 | 68 | 103.4 | 36.87 | 0.072 | 0.69 | 14.09 | 0
June | 15 | 8PM to 9PM | 80.6 | 72.9 | 69.8 | 110.1 | 36.6 | 0.0727 | 0.73 | 13.97 | 0
June | 15 | 9PM to 10PM | 80.6 | 72.9 | 69.8 | 110.1 | 36.6 | 0.0727 | 0.73 | 13.97 | 0
June | 15 | 10PM to 11PM | 80.1 | 67.8 | 61.7 | 82.6 | 32.15 | 0.0729 | 0.55 | 13.87 | 0
June | 15 | 11PM to 12AM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
June | 16 | 12AM to 1AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
June | 16 | 1AM to 2AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
June | 16 | 2AM to 3AM | 71.6 | 63.5 | 59 | 74.9 | 28.88 | 0.0742 | 0.5 | 13.63 | 0
June | 16 | 3AM to 4AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 16 | 4AM to 5AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
June | 16 | 5AM to 6AM | 75.2 | 60.1 | 50 | 53.7 | 26.44 | 0.0738 | 0.36 | 13.66 | 0
June | 16 | 6AM to 7AM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
June | 16 | 7AM to 8AM | 82.4 | 61.1 | 46.4 | 46.8 | 27.12 | 0.0729 | 0.32 | 13.82 | 0
June | 16 | 8AM to 9AM | 87.8 | 63 | 46.4 | 46.8 | 28.43 | 0.0721 | 0.32 | 13.96 | 0
June | 16 | 9AM to 10AM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
June | 16 | 10AM to 11AM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
June | 16 | 11AM to 12PM | 93.2 | 65.5 | 48.2 | 50.1 | 30.26 | 0.0714 | 0.34 | 14.1 | 0
June | 16 | 12PM to 1PM | 96.8 | 66.7 | 48.2 | 50.1 | 31.14 | 0.0709 | 0.34 | 14.2 | 0
June | 16 | 1PM to 2PM | 98.6 | 67.3 | 48.2 | 50.1 | 31.58 | 0.0707 | 0.34 | 14.24 | 0
June | 16 | 2PM to 3PM | 98.6 | 67.3 | 48.2 | 50.1 | 31.58 | 0.0707 | 0.34 | 14.24 | 0
June | 16 | 3PM to 4PM | 98.6 | 66.6 | 46.4 | 46.8 | 31.05 | 0.0707 | 0.32 | 14.23 | 0
June | 16 | 4PM to 5PM | 96.8 | 68.1 | 51.8 | 57.4 | 32.29 | 0.0709 | 0.39 | 14.22 | 0
June | 16 | 5PM to 6PM | 95 | 68.3 | 53.6 | 61.4 | 32.48 | 0.0711 | 0.41 | 14.19 | 0
June | 16 | 6PM to 7PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
June | 16 | 7PM to 8PM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
June | 16 | 8PM to 9PM | 79 | 64.5 | 56.3 | 67.8 | 29.58 | 0.0732 | 0.46 | 13.8 | 0
June | 16 | 9PM to 10PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
June | 16 | 10PM to 11PM | 69.8 | 62.9 | 59 | 74.9 | 28.44 | 0.0744 | 0.5 | 13.58 | 0
June | 16 | 11PM to 12AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
June | 17 | 12AM to 1AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
June | 17 | 1AM to 2AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
June | 17 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
June | 17 | 3AM to 4AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
June | 17 | 4AM to 5AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
June | 17 | 5AM to 6AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
June | 17 | 6AM to 7AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
June | 17 | 7AM to 8AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
June | 17 | 8AM to 9AM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
June | 17 | 9AM to 10AM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
June | 17 | 10AM to 11AM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
June | 17 | 11AM to 12PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
June | 17 | 12PM to 1PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
June | 17 | 1PM to 2PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
June | 17 | 2PM to 3PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
June | 17 | 3PM to 4PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
June | 17 | 4PM to 5PM | 89.6 | 69.2 | 59 | 74.9 | 33.28 | 0.0717 | 0.5 | 14.09 | 0
June | 17 | 5PM to 6PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
June | 17 | 6PM to 7PM | 78.8 | 65.9 | 59 | 74.9 | 30.64 | 0.0732 | 0.5 | 13.81 | 0
June | 17 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
June | 17 | 8PM to 9PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 17 | 9PM to 10PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 17 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
June | 17 | 11PM to 12AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
June | 18 | 12AM to 1AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 18 | 1AM to 2AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 18 | 2AM to 3AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 18 | 3AM to 4AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 18 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
June | 18 | 5AM to 6AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 18 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
June | 18 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 18 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 18 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 18 | 10AM to 11AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 18 | 11AM to 12PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
June | 18 | 12PM to 1PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
June | 18 | 1PM to 2PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
June | 18 | 2PM to 3PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
June | 18 | 3PM to 4PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
June | 18 | 4PM to 5PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
June | 18 | 5PM to 6PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
June | 18 | 6PM to 7PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 18 | 7PM to 8PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 18 | 8PM to 9PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 18 | 9PM to 10PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 18 | 10PM to 11PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 18 | 11PM to 12AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 19 | 12AM to 1AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
June | 19 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
June | 19 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
June | 19 | 3AM to 4AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
June | 19 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
June | 19 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
June | 19 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
June | 19 | 7AM to 8AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
June | 19 | 8AM to 9AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
June | 19 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
June | 19 | 10AM to 11AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
June | 19 | 11AM to 12PM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
June | 19 | 12PM to 1PM | 86 | 69.1 | 60.8 | 79.9 | 33.19 | 0.0722 | 0.54 | 14.01 | 0
June | 19 | 1PM to 2PM | 89.6 | 71.1 | 62.6 | 85.3 | 34.92 | 0.0717 | 0.57 | 14.12 | 0
June | 19 | 2PM to 3PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
June | 19 | 3PM to 4PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
June | 19 | 4PM to 5PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
June | 19 | 5PM to 6PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
June | 19 | 6PM to 7PM | 87.8 | 70.6 | 62.6 | 85.3 | 34.48 | 0.0719 | 0.57 | 14.08 | 0
June | 19 | 7PM to 8PM | 80.6 | 69.5 | 64.4 | 91 | 33.6 | 0.0728 | 0.61 | 13.91 | 0
June | 19 | 8PM to 9PM | 75.2 | 67.9 | 64.4 | 91 | 32.27 | 0.0736 | 0.61 | 13.77 | 0
June | 19 | 9PM to 10PM | 71.6 | 65.6 | 62.6 | 85.3 | 30.5 | 0.0741 | 0.57 | 13.66 | 0
June | 19 | 10PM to 11PM | 69.8 | 63.9 | 60.8 | 79.9 | 29.22 | 0.0744 | 0.54 | 13.6 | 0
June | 19 | 11PM to 12AM | 66.2 | 61.6 | 59 | 74.9 | 27.55 | 0.0749 | 0.5 | 13.49 | 0
June | 20 | 12AM to 1AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
June | 20 | 1AM to 2AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
June | 20 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
June | 20 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 20 | 4AM to 5AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 20 | 5AM to 6AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
June | 20 | 6AM to 7AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
June | 20 | 7AM to 8AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
June | 20 | 8AM to 9AM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
June | 20 | 9AM to 10AM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
June | 20 | 10AM to 11AM | 86 | 65.5 | 53.6 | 61.4 | 30.28 | 0.0723 | 0.41 | 13.96 | 0
June | 20 | 11AM to 12PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
June | 20 | 12PM to 1PM | 93.2 | 67 | 51.8 | 57.4 | 31.41 | 0.0714 | 0.39 | 14.13 | 0
June | 20 | 1PM to 2PM | 93.2 | 66.3 | 50 | 53.7 | 30.82 | 0.0714 | 0.36 | 14.12 | 0
June | 20 | 2PM to 3PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
June | 20 | 3PM to 4PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
June | 20 | 4PM to 5PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
June | 20 | 5PM to 6PM | 95 | 68.3 | 53.6 | 61.4 | 32.48 | 0.0711 | 0.41 | 14.19 | 0
June | 20 | 6PM to 7PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
June | 20 | 7PM to 8PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
June | 20 | 8PM to 9PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
June | 20 | 9PM to 10PM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
June | 20 | 10PM to 11PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 20 | 11PM to 12AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
June | 21 | 12AM to 1AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
June | 21 | 1AM to 2AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
June | 21 | 2AM to 3AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 21 | 3AM to 4AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 21 | 4AM to 5AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 21 | 5AM to 6AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 21 | 6AM to 7AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 21 | 7AM to 8AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 21 | 8AM to 9AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
June | 21 | 9AM to 10AM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
June | 21 | 10AM to 11AM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
June | 21 | 11AM to 12PM | 93.2 | 71.2 | 60.8 | 79.9 | 34.96 | 0.0712 | 0.54 | 14.2 | 0
June | 21 | 12PM to 1PM | 95 | 70.8 | 59 | 74.9 | 34.6 | 0.071 | 0.5 | 14.23 | 0
June | 21 | 1PM to 2PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
June | 21 | 2PM to 3PM | 98.6 | 68.7 | 51.8 | 57.4 | 32.73 | 0.0707 | 0.39 | 14.27 | 0
June | 21 | 3PM to 4PM | 100.4 | 70 | 53.6 | 61.4 | 33.79 | 0.0704 | 0.41 | 14.32 | 0
June | 21 | 4PM to 5PM | 98.6 | 71.9 | 59 | 74.9 | 35.48 | 0.0706 | 0.5 | 14.32 | 0
June | 21 | 5PM to 6PM | 96.8 | 72.3 | 60.8 | 79.9 | 35.84 | 0.0708 | 0.54 | 14.29 | 0
June | 21 | 6PM to 7PM | 91.4 | 71.7 | 62.6 | 85.3 | 35.36 | 0.0714 | 0.57 | 14.17 | 0
June | 21 | 7PM to 8PM | 84.2 | 69.6 | 62.6 | 85.3 | 33.59 | 0.0724 | 0.57 | 13.99 | 0
June | 21 | 8PM to 9PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
June | 21 | 9PM to 10PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
June | 21 | 10PM to 11PM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
June | 21 | 11PM to 12AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
June | 22 | 12AM to 1AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
June | 22 | 1AM to 2AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
June | 22 | 2AM to 3AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 22 | 3AM to 4AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 22 | 4AM to 5AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 22 | 5AM to 6AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 22 | 6AM to 7AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 22 | 7AM to 8AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 22 | 8AM to 9AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 22 | 9AM to 10AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
June | 22 | 10AM to 11AM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
June | 22 | 11AM to 12PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
June | 22 | 12PM to 1PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
June | 22 | 1PM to 2PM | 89.6 | 69.2 | 59 | 74.9 | 33.28 | 0.0717 | 0.5 | 14.09 | 0
June | 22 | 2PM to 3PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
June | 22 | 3PM to 4PM | 86 | 68.1 | 59 | 74.9 | 32.4 | 0.0722 | 0.5 | 14 | 0
June | 22 | 4PM to 5PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
June | 22 | 5PM to 6PM | 78.8 | 65.9 | 59 | 74.9 | 30.64 | 0.0732 | 0.5 | 13.81 | 0
June | 22 | 6PM to 7PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 22 | 7PM to 8PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
June | 22 | 8PM to 9PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
June | 22 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
June | 22 | 10PM to 11PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
June | 22 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 23 | 12AM to 1AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
June | 23 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 23 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 23 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 23 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
June | 23 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 23 | 6AM to 7AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 23 | 7AM to 8AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 23 | 8AM to 9AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 23 | 9AM to 10AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 23 | 10AM to 11AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
June | 23 | 11AM to 12PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
June | 23 | 12PM to 1PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
June | 23 | 1PM to 2PM | 84.2 | 67.6 | 59 | 74.9 | 31.96 | 0.0724 | 0.5 | 13.95 | 0
June | 23 | 2PM to 3PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
June | 23 | 3PM to 4PM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
June | 23 | 4PM to 5PM | 86 | 64.7 | 51.8 | 57.4 | 29.66 | 0.0723 | 0.39 | 13.94 | 0
June | 23 | 5PM to 6PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
June | 23 | 6PM to 7PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
June | 23 | 7PM to 8PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
June | 23 | 8PM to 9PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 23 | 9PM to 10PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
June | 23 | 10PM to 11PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
June | 23 | 11PM to 12AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
June | 24 | 12AM to 1AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
June | 24 | 1AM to 2AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
June | 24 | 2AM to 3AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
June | 24 | 3AM to 4AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 24 | 4AM to 5AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 24 | 5AM to 6AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
June | 24 | 6AM to 7AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
June | 24 | 7AM to 8AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 24 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 24 | 9AM to 10AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
June | 24 | 10AM to 11AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
June | 24 | 11AM to 12PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
June | 24 | 12PM to 1PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
June | 24 | 1PM to 2PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
June | 24 | 2PM to 3PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
June | 24 | 3PM to 4PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
June | 24 | 4PM to 5PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
June | 24 | 5PM to 6PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
June | 24 | 6PM to 7PM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
June | 24 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
June | 24 | 8PM to 9PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
June | 24 | 9PM to 10PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
June | 24 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
June | 24 | 11PM to 12AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 25 | 12AM to 1AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 25 | 1AM to 2AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 25 | 2AM to 3AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 25 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 25 | 4AM to 5AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 25 | 5AM to 6AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 25 | 6AM to 7AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 25 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 25 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 25 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
June | 25 | 10AM to 11AM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
June | 25 | 11AM to 12PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
June | 25 | 12PM to 1PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
June | 25 | 1PM to 2PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
June | 25 | 2PM to 3PM | 93.2 | 66.3 | 50 | 53.7 | 30.82 | 0.0714 | 0.36 | 14.12 | 0
June | 25 | 3PM to 4PM | 95 | 69.1 | 55.4 | 65.6 | 33.14 | 0.0711 | 0.44 | 14.2 | 0
June | 25 | 4PM to 5PM | 93.2 | 71.2 | 60.8 | 79.9 | 34.96 | 0.0712 | 0.54 | 14.2 | 0
June | 25 | 5PM to 6PM | 91.4 | 70.7 | 60.8 | 79.9 | 34.52 | 0.0715 | 0.54 | 14.15 | 0
June | 25 | 6PM to 7PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
June | 25 | 7PM to 8PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
June | 25 | 8PM to 9PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
June | 25 | 9PM to 10PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 25 | 10PM to 11PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
June | 25 | 11PM to 12AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 26 | 12AM to 1AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 26 | 1AM to 2AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 26 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
June | 26 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 26 | 4AM to 5AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 26 | 5AM to 6AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
June | 26 | 6AM to 7AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 26 | 7AM to 8AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
June | 26 | 8AM to 9AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
June | 26 | 9AM to 10AM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
June | 26 | 10AM to 11AM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
June | 26 | 11AM to 12PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
June | 26 | 12PM to 1PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
June | 26 | 1PM to 2PM | 95 | 71.7 | 60.8 | 79.9 | 35.4 | 0.071 | 0.54 | 14.25 | 0
June | 26 | 2PM to 3PM | 96.8 | 70.5 | 57.2 | 70.1 | 34.29 | 0.0708 | 0.47 | 14.26 | 0
June | 26 | 3PM to 4PM | 96.8 | 70.5 | 57.2 | 70.1 | 34.29 | 0.0708 | 0.47 | 14.26 | 0
June | 26 | 4PM to 5PM | 96.8 | 70.5 | 57.2 | 70.1 | 34.29 | 0.0708 | 0.47 | 14.26 | 0
June | 26 | 5PM to 6PM | 93.2 | 72.2 | 62.6 | 85.3 | 35.8 | 0.0712 | 0.57 | 14.22 | 0
June | 26 | 6PM to 7PM | 89.6 | 69.2 | 59 | 74.9 | 33.28 | 0.0717 | 0.5 | 14.09 | 0
June | 26 | 7PM to 8PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
June | 26 | 8PM to 9PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
June | 26 | 9PM to 10PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
June | 26 | 10PM to 11PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
June | 26 | 11PM to 12AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
June | 27 | 12AM to 1AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
June | 27 | 1AM to 2AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
June | 27 | 2AM to 3AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 27 | 3AM to 4AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 27 | 4AM to 5AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 27 | 5AM to 6AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 27 | 6AM to 7AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
June | 27 | 7AM to 8AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 27 | 8AM to 9AM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
June | 27 | 9AM to 10AM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
June | 27 | 10AM to 11AM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
June | 27 | 11AM to 12PM | 91.4 | 71.7 | 62.6 | 85.3 | 35.36 | 0.0714 | 0.57 | 14.17 | 0
June | 27 | 12PM to 1PM | 93.2 | 73.2 | 64.4 | 91 | 36.7 | 0.0712 | 0.61 | 14.23 | 0
June | 27 | 1PM to 2PM | 96.8 | 71.4 | 59 | 74.9 | 35.04 | 0.0708 | 0.5 | 14.28 | 0
June | 27 | 2PM to 3PM | 98.6 | 71 | 57.2 | 70.1 | 34.73 | 0.0706 | 0.47 | 14.31 | 0
June | 27 | 3PM to 4PM | 98.6 | 72.8 | 60.8 | 79.9 | 36.28 | 0.0705 | 0.54 | 14.34 | 0
June | 27 | 4PM to 5PM | 96.8 | 72.3 | 60.8 | 79.9 | 35.84 | 0.0708 | 0.54 | 14.29 | 0
June | 27 | 5PM to 6PM | 95 | 71.7 | 60.8 | 79.9 | 35.4 | 0.071 | 0.54 | 14.25 | 0
June | 27 | 6PM to 7PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
June | 27 | 7PM to 8PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
June | 27 | 8PM to 9PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
June | 27 | 9PM to 10PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 27 | 10PM to 11PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
June | 27 | 11PM to 12AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
June | 28 | 12AM to 1AM | 68.4 | 59.3 | 53.4 | 61 | 25.92 | 0.0747 | 0.41 | 13.5 | 0
June | 28 | 1AM to 2AM | 67.1 | 58.9 | 53.6 | 61.4 | 25.67 | 0.0749 | 0.41 | 13.47 | 0
June | 28 | 2AM to 3AM | 65.7 | 58.4 | 53.6 | 61.4 | 25.32 | 0.0751 | 0.41 | 13.44 | 0
June | 28 | 3AM to 4AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 28 | 4AM to 5AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 28 | 5AM to 6AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 28 | 6AM to 7AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
June | 28 | 7AM to 8AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 28 | 8AM to 9AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
June | 28 | 9AM to 10AM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
June | 28 | 10AM to 11AM | 84.2 | 67.6 | 59 | 74.9 | 31.96 | 0.0724 | 0.5 | 13.95 | 0
June | 28 | 11AM to 12PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
June | 28 | 12PM to 1PM | 93.2 | 71.2 | 60.8 | 79.9 | 34.96 | 0.0712 | 0.54 | 14.2 | 0
June | 28 | 1PM to 2PM | 96.8 | 73.2 | 62.6 | 85.3 | 36.69 | 0.0707 | 0.57 | 14.31 | 0
June | 28 | 2PM to 3PM | 96.8 | 73.2 | 62.6 | 85.3 | 36.69 | 0.0707 | 0.57 | 14.31 | 0
June | 28 | 3PM to 4PM | 96.8 | 71.4 | 59 | 74.9 | 35.04 | 0.0708 | 0.5 | 14.28 | 0
June | 28 | 4PM to 5PM | 95 | 71.7 | 60.8 | 79.9 | 35.4 | 0.071 | 0.54 | 14.25 | 0
June | 28 | 5PM to 6PM | 89.6 | 71.1 | 62.6 | 85.3 | 34.92 | 0.0717 | 0.57 | 14.12 | 0
June | 28 | 6PM to 7PM | 84.2 | 69.6 | 62.6 | 85.3 | 33.59 | 0.0724 | 0.57 | 13.99 | 0
June | 28 | 7PM to 8PM | 78.8 | 65.9 | 59 | 74.9 | 30.64 | 0.0732 | 0.5 | 13.81 | 0
June | 28 | 8PM to 9PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
June | 28 | 9PM to 10PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
June | 28 | 10PM to 11PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
June | 28 | 11PM to 12AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 29 | 12AM to 1AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 29 | 1AM to 2AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 29 | 2AM to 3AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
June | 29 | 3AM to 4AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
June | 29 | 4AM to 5AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 29 | 5AM to 6AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
June | 29 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
June | 29 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
June | 29 | 8AM to 9AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
June | 29 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
June | 29 | 10AM to 11AM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
June | 29 | 11AM to 12PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
June | 29 | 12PM to 1PM | 86 | 69.1 | 60.8 | 79.9 | 33.19 | 0.0722 | 0.54 | 14.01 | 0
June | 29 | 1PM to 2PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
June | 29 | 2PM to 3PM | 91.4 | 69.8 | 59 | 74.9 | 33.72 | 0.0715 | 0.5 | 14.14 | 0
June | 29 | 3PM to 4PM | 89.6 | 71.1 | 62.6 | 85.3 | 34.92 | 0.0717 | 0.57 | 14.12 | 0
June | 29 | 4PM to 5PM | 86 | 69.1 | 60.8 | 79.9 | 33.19 | 0.0722 | 0.54 | 14.01 | 0
June | 29 | 5PM to 6PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
June | 29 | 6PM to 7PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
June | 29 | 7PM to 8PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
June | 29 | 8PM to 9PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 29 | 9PM to 10PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 29 | 10PM to 11PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
June | 29 | 11PM to 12AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
June | 30 | 12AM to 1AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
June | 30 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
June | 30 | 2AM to 3AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
June | 30 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 30 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 30 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
June | 30 | 6AM to 7AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
June | 30 | 7AM to 8AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
June | 30 | 8AM to 9AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
June | 30 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
June | 30 | 10AM to 11AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
June | 30 | 11AM to 12PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
June | 30 | 12PM to 1PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
June | 30 | 1PM to 2PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
June | 30 | 2PM to 3PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
June | 30 | 3PM to 4PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
June | 30 | 4PM to 5PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
June | 30 | 5PM to 6PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
June | 30 | 6PM to 7PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
June | 30 | 7PM to 8PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
June | 30 | 8PM to 9PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
June | 30 | 9PM to 10PM | 62.6 | 56.6 | 52.5 | 59 | 24.2 | 0.0755 | 0.4 | 13.35 | 0
June | 30 | 10PM to 11PM | 62.6 | 57.1 | 53.4 | 61 | 24.51 | 0.0755 | 0.41 | 13.36 | 0
June | 30 | 11PM to 12AM | 62.6 | 57.5 | 54.1 | 62.6 | 24.77 | 0.0755 | 0.42 | 13.36 | 0
July | 1 | 12AM to 1AM | 62.6 | 57.9 | 54.9 | 64.3 | 25.03 | 0.0755 | 0.43 | 13.37 | 0
July | 1 | 1AM to 2AM | 62.6 | 58.3 | 55.6 | 66.1 | 25.3 | 0.0755 | 0.45 | 13.37 | 0
July | 1 | 2AM to 3AM | 62.6 | 58.8 | 56.5 | 68.3 | 25.65 | 0.0755 | 0.46 | 13.38 | 0
July | 1 | 3AM to 4AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
July | 1 | 4AM to 5AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
July | 1 | 5AM to 6AM | 66.2 | 62.7 | 60.8 | 79.9 | 28.34 | 0.0749 | 0.54 | 13.51 | 0
July | 1 | 6AM to 7AM | 73.4 | 65.1 | 60.8 | 79.9 | 30.11 | 0.0739 | 0.54 | 13.69 | 0
July | 1 | 7AM to 8AM | 78.8 | 69 | 64.4 | 91 | 33.16 | 0.0731 | 0.61 | 13.86 | 0
July | 1 | 8AM to 9AM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
July | 1 | 9AM to 10AM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
July | 1 | 10AM to 11AM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
July | 1 | 11AM to 12PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
July | 1 | 12PM to 1PM | 96.8 | 69.7 | 55.4 | 65.6 | 33.58 | 0.0709 | 0.44 | 14.25 | 0
July | 1 | 1PM to 2PM | 96.8 | 71.4 | 59 | 74.9 | 35.04 | 0.0708 | 0.5 | 14.28 | 0
July | 1 | 2PM to 3PM | 100.4 | 70 | 53.6 | 61.4 | 33.79 | 0.0704 | 0.41 | 14.32 | 0
July | 1 | 3PM to 4PM | 100.4 | 69.2 | 51.8 | 57.4 | 33.16 | 0.0704 | 0.39 | 14.31 | 0
July | 1 | 4PM to 5PM | 100.4 | 67.8 | 48.2 | 50.1 | 32.01 | 0.0705 | 0.34 | 14.29 | 0
July | 1 | 5PM to 6PM | 98.6 | 67.3 | 48.2 | 50.1 | 31.58 | 0.0707 | 0.34 | 14.24 | 0
July | 1 | 6PM to 7PM | 91.4 | 71.7 | 62.6 | 85.3 | 35.36 | 0.0714 | 0.57 | 14.17 | 0
July | 1 | 7PM to 8PM | 84.2 | 70.6 | 64.4 | 91 | 34.48 | 0.0723 | 0.61 | 14 | 0
July | 1 | 8PM to 9PM | 80.6 | 68.5 | 62.6 | 85.3 | 32.71 | 0.0729 | 0.57 | 13.89 | 0
July | 1 | 9PM to 10PM | 75.2 | 64.7 | 59 | 74.9 | 29.76 | 0.0737 | 0.5 | 13.72 | 0
July | 1 | 10PM to 11PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 1 | 11PM to 12AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 2 | 12AM to 1AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 2 | 1AM to 2AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 2 | 2AM to 3AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
July | 2 | 3AM to 4AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
July | 2 | 4AM to 5AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 2 | 5AM to 6AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 2 | 6AM to 7AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 2 | 7AM to 8AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
July | 2 | 8AM to 9AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
July | 2 | 9AM to 10AM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
July | 2 | 10AM to 11AM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
July | 2 | 11AM to 12PM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
July | 2 | 12PM to 1PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
July | 2 | 1PM to 2PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
July | 2 | 2PM to 3PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
July | 2 | 3PM to 4PM | 88.5 | 66.6 | 54.3 | 63.1 | 31.16 | 0.0719 | 0.43 | 14.03 | 0
July | 2 | 4PM to 5PM | 86 | 65.7 | 54 | 62.2 | 30.41 | 0.0723 | 0.42 | 13.96 | 0
July | 2 | 5PM to 6PM | 81.7 | 64.5 | 54.5 | 63.5 | 29.56 | 0.0728 | 0.43 | 13.85 | 0
July | 2 | 6PM to 7PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
July | 2 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 2 | 8PM to 9PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
July | 2 | 9PM to 10PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 2 | 10PM to 11PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 2 | 11PM to 12AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 3 | 12AM to 1AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 3 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 3 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 3 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
July | 3 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
July | 3 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
July | 3 | 6AM to 7AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 3 | 7AM to 8AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 3 | 8AM to 9AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
July | 3 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 3 | 10AM to 11AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
July | 3 | 11AM to 12PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
July | 3 | 12PM to 1PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
July | 3 | 1PM to 2PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
July | 3 | 2PM to 3PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
July | 3 | 3PM to 4PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
July | 3 | 4PM to 5PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
July | 3 | 5PM to 6PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
July | 3 | 6PM to 7PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
July | 3 | 7PM to 8PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
July | 3 | 8PM to 9PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
July | 3 | 9PM to 10PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
July | 3 | 10PM to 11PM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
July | 3 | 11PM to 12AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
July | 4 | 12AM to 1AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 4 | 1AM to 2AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
July | 4 | 2AM to 3AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
July | 4 | 3AM to 4AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
July | 4 | 4AM to 5AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
July | 4 | 5AM to 6AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
July | 4 | 6AM to 7AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
July | 4 | 7AM to 8AM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
July | 4 | 8AM to 9AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
July | 4 | 9AM to 10AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
July | 4 | 10AM to 11AM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
July | 4 | 11AM to 12PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
July | 4 | 12PM to 1PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
July | 4 | 1PM to 2PM | 86 | 64.7 | 51.8 | 57.4 | 29.66 | 0.0723 | 0.39 | 13.94 | 0
July | 4 | 2PM to 3PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
July | 4 | 3PM to 4PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
July | 4 | 4PM to 5PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
July | 4 | 5PM to 6PM | 85.3 | 66 | 55.2 | 65.2 | 30.7 | 0.0724 | 0.44 | 13.95 | 0
July | 4 | 6PM to 7PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
July | 4 | 7PM to 8PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
July | 4 | 8PM to 9PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
July | 4 | 9PM to 10PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
July | 4 | 10PM to 11PM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
July | 4 | 11PM to 12AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 5 | 12AM to 1AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 5 | 1AM to 2AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 5 | 2AM to 3AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 5 | 3AM to 4AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 5 | 4AM to 5AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
July | 5 | 5AM to 6AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 5 | 6AM to 7AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 5 | 7AM to 8AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
July | 5 | 8AM to 9AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
July | 5 | 9AM to 10AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
July | 5 | 10AM to 11AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
July | 5 | 11AM to 12PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
July | 5 | 12PM to 1PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
July | 5 | 1PM to 2PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
July | 5 | 2PM to 3PM | 89.6 | 69.2 | 59 | 74.9 | 33.28 | 0.0717 | 0.5 | 14.09 | 0
July | 5 | 3PM to 4PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
July | 5 | 4PM to 5PM | 89.6 | 69.2 | 59 | 74.9 | 33.28 | 0.0717 | 0.5 | 14.09 | 0
July | 5 | 5PM to 6PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
July | 5 | 6PM to 7PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
July | 5 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 5 | 8PM to 9PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 5 | 9PM to 10PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 5 | 10PM to 11PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
July | 5 | 11PM to 12AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
July | 6 | 12AM to 1AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 6 | 1AM to 2AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 6 | 2AM to 3AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 6 | 3AM to 4AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 6 | 4AM to 5AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 6 | 5AM to 6AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 6 | 6AM to 7AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
July | 6 | 7AM to 8AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
July | 6 | 8AM to 9AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
July | 6 | 9AM to 10AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
July | 6 | 10AM to 11AM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
July | 6 | 11AM to 12PM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
July | 6 | 12PM to 1PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
July | 6 | 1PM to 2PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
July | 6 | 2PM to 3PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
July | 6 | 3PM to 4PM | 95 | 70.8 | 59 | 74.9 | 34.6 | 0.071 | 0.5 | 14.23 | 0
July | 6 | 4PM to 5PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
July | 6 | 5PM to 6PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
July | 6 | 6PM to 7PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
July | 6 | 7PM to 8PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
July | 6 | 8PM to 9PM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
July | 6 | 9PM to 10PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
July | 6 | 10PM to 11PM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
July | 6 | 11PM to 12AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
July | 7 | 12AM to 1AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
July | 7 | 1AM to 2AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
July | 7 | 2AM to 3AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
July | 7 | 3AM to 4AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
July | 7 | 4AM to 5AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
July | 7 | 5AM to 6AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
July | 7 | 6AM to 7AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
July | 7 | 7AM to 8AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
July | 7 | 8AM to 9AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
July | 7 | 9AM to 10AM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
July | 7 | 10AM to 11AM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
July | 7 | 11AM to 12PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
July | 7 | 12PM to 1PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
July | 7 | 1PM to 2PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
July | 7 | 2PM to 3PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
July | 7 | 3PM to 4PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
July | 7 | 4PM to 5PM | 91.4 | 69.8 | 59 | 74.9 | 33.72 | 0.0715 | 0.5 | 14.14 | 0
July | 7 | 5PM to 6PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
July | 7 | 6PM to 7PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
July | 7 | 7PM to 8PM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
July | 7 | 8PM to 9PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 7 | 9PM to 10PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
July | 7 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 7 | 11PM to 12AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 8 | 12AM to 1AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 8 | 1AM to 2AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 8 | 2AM to 3AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 8 | 3AM to 4AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 8 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 8 | 5AM to 6AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 8 | 6AM to 7AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
July | 8 | 7AM to 8AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
July | 8 | 8AM to 9AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
July | 8 | 9AM to 10AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
July | 8 | 10AM to 11AM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
July | 8 | 11AM to 12PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
July | 8 | 12PM to 1PM | 89.6 | 65.1 | 50 | 53.7 | 29.94 | 0.0719 | 0.36 | 14.02 | 0
July | 8 | 1PM to 2PM | 93.2 | 64.9 | 46.4 | 46.8 | 29.74 | 0.0714 | 0.32 | 14.09 | 0
July | 8 | 2PM to 3PM | 93.2 | 63.6 | 42.8 | 40.8 | 28.79 | 0.0715 | 0.28 | 14.07 | 0
July | 8 | 3PM to 4PM | 95 | 63.6 | 41 | 38 | 28.79 | 0.0713 | 0.26 | 14.11 | 0
July | 8 | 4PM to 5PM | 95 | 63 | 39.2 | 35.4 | 28.38 | 0.0713 | 0.24 | 14.1 | 0
July | 8 | 5PM to 6PM | 93.2 | 65.5 | 48.2 | 50.1 | 30.26 | 0.0714 | 0.34 | 14.1 | 0
July | 8 | 6PM to 7PM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
July | 8 | 7PM to 8PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
July | 8 | 8PM to 9PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 8 | 9PM to 10PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
July | 8 | 10PM to 11PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
July | 8 | 11PM to 12AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
July | 9 | 12AM to 1AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
July | 9 | 1AM to 2AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
July | 9 | 2AM to 3AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 9 | 3AM to 4AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
July | 9 | 4AM to 5AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
July | 9 | 5AM to 6AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
July | 9 | 6AM to 7AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
July | 9 | 7AM to 8AM | 75.6 | 62.2 | 54.1 | 62.6 | 27.93 | 0.0737 | 0.42 | 13.69 | 0
July | 9 | 8AM to 9AM | 80.1 | 64 | 54.7 | 63.9 | 29.23 | 0.0731 | 0.43 | 13.81 | 0
July | 9 | 9AM to 10AM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
July | 9 | 10AM to 11AM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
July | 9 | 11AM to 12PM | 89.6 | 69.2 | 59 | 74.9 | 33.28 | 0.0717 | 0.5 | 14.09 | 0
July | 9 | 12PM to 1PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
July | 9 | 1PM to 2PM | 96.8 | 69.7 | 55.4 | 65.6 | 33.58 | 0.0709 | 0.44 | 14.25 | 0
July | 9 | 2PM to 3PM | 100.4 | 67.8 | 48.2 | 50.1 | 32.01 | 0.0705 | 0.34 | 14.29 | 0
July | 9 | 3PM to 4PM | 100.4 | 69.2 | 51.8 | 57.4 | 33.16 | 0.0704 | 0.39 | 14.31 | 0
July | 9 | 4PM to 5PM | 102.2 | 70.5 | 53.6 | 61.4 | 34.23 | 0.0702 | 0.41 | 14.37 | 0
July | 9 | 5PM to 6PM | 102.2 | 68.4 | 48.2 | 50.1 | 32.45 | 0.0703 | 0.34 | 14.33 | 0
July | 9 | 6PM to 7PM | 93.2 | 75.2 | 68 | 103.4 | 38.65 | 0.0711 | 0.69 | 14.27 | 0
July | 9 | 7PM to 8PM | 89.6 | 71.1 | 62.6 | 85.3 | 34.92 | 0.0717 | 0.57 | 14.12 | 0
July | 9 | 8PM to 9PM | 84.2 | 69.6 | 62.6 | 85.3 | 33.59 | 0.0724 | 0.57 | 13.99 | 0
July | 9 | 9PM to 10PM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
July | 9 | 10PM to 11PM | 73.4 | 66.2 | 62.6 | 85.3 | 30.94 | 0.0738 | 0.57 | 13.71 | 0
July | 9 | 11PM to 12AM | 73.4 | 67.3 | 64.4 | 91 | 31.83 | 0.0738 | 0.61 | 13.73 | 0
July | 10 | 12AM to 1AM | 71.6 | 64.5 | 60.8 | 79.9 | 29.67 | 0.0741 | 0.54 | 13.64 | 0
July | 10 | 1AM to 2AM | 68 | 64.4 | 62.6 | 85.3 | 29.62 | 0.0746 | 0.57 | 13.57 | 0
July | 10 | 2AM to 3AM | 68 | 63.3 | 60.8 | 79.9 | 28.78 | 0.0746 | 0.54 | 13.55 | 0
July | 10 | 3AM to 4AM | 68 | 64.4 | 62.6 | 85.3 | 29.62 | 0.0746 | 0.57 | 13.57 | 0
July | 10 | 4AM to 5AM | 66.2 | 63.8 | 62.6 | 85.3 | 29.18 | 0.0749 | 0.57 | 13.52 | 0
July | 10 | 5AM to 6AM | 68.5 | 65.8 | 64.4 | 91 | 30.64 | 0.0745 | 0.61 | 13.6 | 0
July | 10 | 6AM to 7AM | 73.4 | 68.5 | 66.2 | 97 | 32.77 | 0.0738 | 0.65 | 13.74 | 0
July | 10 | 7AM to 8AM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
July | 10 | 8AM to 9AM | 87.8 | 71.6 | 64.4 | 91 | 35.37 | 0.0719 | 0.61 | 14.1 | 0
July | 10 | 9AM to 10AM | 91.4 | 73.7 | 66.2 | 97 | 37.2 | 0.0714 | 0.65 | 14.21 | 0
July | 10 | 10AM to 11AM | 95 | 73.7 | 64.4 | 91 | 37.14 | 0.0709 | 0.61 | 14.28 | 0
July | 10 | 11AM to 12PM | 100.4 | 73.3 | 60.8 | 79.9 | 36.72 | 0.0703 | 0.54 | 14.38 | 0
July | 10 | 12PM to 1PM | 102.2 | 71.3 | 55.4 | 65.6 | 34.9 | 0.0702 | 0.44 | 14.38 | 0
July | 10 | 1PM to 2PM | 105.8 | 70.8 | 51.8 | 57.4 | 34.48 | 0.0698 | 0.39 | 14.45 | 0
July | 10 | 2PM to 3PM | 107.6 | 72.1 | 53.6 | 61.4 | 35.55 | 0.0695 | 0.41 | 14.51 | 0
July | 10 | 3PM to 4PM | 107.6 | 72.1 | 53.6 | 61.4 | 35.55 | 0.0695 | 0.41 | 14.51 | 0
July | 10 | 4PM to 5PM | 107.6 | 76.1 | 62.6 | 85.3 | 39.34 | 0.0694 | 0.57 | 14.59 | 0
July | 10 | 5PM to 6PM | 105.8 | 74.7 | 60.8 | 79.9 | 38.05 | 0.0696 | 0.54 | 14.52 | 0
July | 10 | 6PM to 7PM | 100.4 | 72.4 | 59 | 74.9 | 35.92 | 0.0703 | 0.5 | 14.37 | 0
July | 10 | 7PM to 8PM | 93.2 | 72.2 | 62.6 | 85.3 | 35.8 | 0.0712 | 0.57 | 14.22 | 0
July | 10 | 8PM to 9PM | 87.3 | 69 | 59.9 | 77.4 | 33.1 | 0.072 | 0.52 | 14.04 | 0
July | 10 | 9PM to 10PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
July | 10 | 10PM to 11PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
July | 10 | 11PM to 12AM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
July | 11 | 12AM to 1AM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
July | 11 | 1AM to 2AM | 75.2 | 60.1 | 50 | 53.7 | 26.44 | 0.0738 | 0.36 | 13.66 | 0
July | 11 | 2AM to 3AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
July | 11 | 3AM to 4AM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
July | 11 | 4AM to 5AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
July | 11 | 5AM to 6AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 11 | 6AM to 7AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 11 | 7AM to 8AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 11 | 8AM to 9AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
July | 11 | 9AM to 10AM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
July | 11 | 10AM to 11AM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
July | 11 | 11AM to 12PM | 91.4 | 71.7 | 62.6 | 85.3 | 35.36 | 0.0714 | 0.57 | 14.17 | 0
July | 11 | 12PM to 1PM | 96.8 | 71.4 | 59 | 74.9 | 35.04 | 0.0708 | 0.5 | 14.28 | 0
July | 11 | 1PM to 2PM | 100.4 | 71.5 | 57.2 | 70.1 | 35.17 | 0.0704 | 0.47 | 14.35 | 0
July | 11 | 2PM to 3PM | 100.4 | 70.7 | 55.4 | 65.6 | 34.46 | 0.0704 | 0.44 | 14.34 | 0
July | 11 | 3PM to 4PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
July | 11 | 4PM to 5PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
July | 11 | 5PM to 6PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
July | 11 | 6PM to 7PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
July | 11 | 7PM to 8PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
July | 11 | 8PM to 9PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
July | 11 | 9PM to 10PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
July | 11 | 10PM to 11PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
July | 11 | 11PM to 12AM | 78.8 | 61.4 | 50 | 53.7 | 27.31 | 0.0733 | 0.36 | 13.75 | 0
July | 12 | 12AM to 1AM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
July | 12 | 1AM to 2AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
July | 12 | 2AM to 3AM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
July | 12 | 3AM to 4AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
July | 12 | 4AM to 5AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 12 | 5AM to 6AM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
July | 12 | 6AM to 7AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
July | 12 | 7AM to 8AM | 78.6 | 63.5 | 54.5 | 63.5 | 28.81 | 0.0733 | 0.43 | 13.77 | 0
July | 12 | 8AM to 9AM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
July | 12 | 9AM to 10AM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
July | 12 | 10AM to 11AM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
July | 12 | 11AM to 12PM | 94.3 | 66.7 | 50.2 | 54 | 31.14 | 0.0712 | 0.37 | 14.14 | 0
July | 12 | 12PM to 1PM | 96.8 | 66.7 | 48.2 | 50.1 | 31.14 | 0.0709 | 0.34 | 14.2 | 0
July | 12 | 1PM to 2PM | 100.4 | 66.6 | 44.6 | 43.7 | 31 | 0.0705 | 0.3 | 14.27 | 0
July | 12 | 2PM to 3PM | 100.4 | 65.4 | 41 | 38 | 30.1 | 0.0706 | 0.26 | 14.25 | 0
July | 12 | 3PM to 4PM | 100.4 | 66.6 | 44.6 | 43.7 | 31 | 0.0705 | 0.3 | 14.27 | 0
July | 12 | 4PM to 5PM | 98.6 | 65.4 | 42.8 | 40.8 | 30.1 | 0.0708 | 0.28 | 14.21 | 0
July | 12 | 5PM to 6PM | 95 | 65.4 | 46.4 | 46.8 | 30.18 | 0.0712 | 0.32 | 14.14 | 0
July | 12 | 6PM to 7PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
July | 12 | 7PM to 8PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
July | 12 | 8PM to 9PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
July | 12 | 9PM to 10PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
July | 12 | 10PM to 11PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
July | 12 | 11PM to 12AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
July | 13 | 12AM to 1AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 13 | 1AM to 2AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 13 | 2AM to 3AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
July | 13 | 3AM to 4AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
July | 13 | 4AM to 5AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
July | 13 | 5AM to 6AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 13 | 6AM to 7AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 13 | 7AM to 8AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 13 | 8AM to 9AM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
July | 13 | 9AM to 10AM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
July | 13 | 10AM to 11AM | 87.8 | 70.6 | 62.6 | 85.3 | 34.48 | 0.0719 | 0.57 | 14.08 | 0
July | 13 | 11AM to 12PM | 93.2 | 71.2 | 60.8 | 79.9 | 34.96 | 0.0712 | 0.54 | 14.2 | 0
July | 13 | 12PM to 1PM | 96.3 | 71.7 | 60.1 | 77.9 | 35.38 | 0.0708 | 0.52 | 14.27 | 0
July | 13 | 1PM to 2PM | 98.6 | 71.9 | 59 | 74.9 | 35.48 | 0.0706 | 0.5 | 14.32 | 0
July | 13 | 2PM to 3PM | 100.4 | 70.7 | 55.4 | 65.6 | 34.46 | 0.0704 | 0.44 | 14.34 | 0
July | 13 | 3PM to 4PM | 98.6 | 71 | 57.2 | 70.1 | 34.73 | 0.0706 | 0.47 | 14.31 | 0
July | 13 | 4PM to 5PM | 98.6 | 72.8 | 60.8 | 79.9 | 36.28 | 0.0705 | 0.54 | 14.34 | 0
July | 13 | 5PM to 6PM | 91.4 | 69.8 | 59 | 74.9 | 33.72 | 0.0715 | 0.5 | 14.14 | 0
July | 13 | 6PM to 7PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
July | 13 | 7PM to 8PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
July | 13 | 8PM to 9PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
July | 13 | 9PM to 10PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
July | 13 | 10PM to 11PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 13 | 11PM to 12AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
July | 14 | 12AM to 1AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 14 | 1AM to 2AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 14 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 14 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 14 | 4AM to 5AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 14 | 5AM to 6AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 14 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 14 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 14 | 8AM to 9AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 14 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
July | 14 | 10AM to 11AM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
July | 14 | 11AM to 12PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
July | 14 | 12PM to 1PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
July | 14 | 1PM to 2PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
July | 14 | 2PM to 3PM | 91.4 | 70.7 | 60.8 | 79.9 | 34.52 | 0.0715 | 0.54 | 14.15 | 0
July | 14 | 3PM to 4PM | 91.4 | 70.7 | 60.8 | 79.9 | 34.52 | 0.0715 | 0.54 | 14.15 | 0
July | 14 | 4PM to 5PM | 91.4 | 70.7 | 60.8 | 79.9 | 34.52 | 0.0715 | 0.54 | 14.15 | 0
July | 14 | 5PM to 6PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
July | 14 | 6PM to 7PM | 82.2 | 65.6 | 56.3 | 67.8 | 30.37 | 0.0727 | 0.46 | 13.88 | 0
July | 14 | 7PM to 8PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
July | 14 | 8PM to 9PM | 71.1 | 59 | 50.9 | 55.5 | 25.72 | 0.0744 | 0.37 | 13.56 | 0
July | 14 | 9PM to 10PM | 68 | 57.4 | 50 | 53.7 | 24.69 | 0.0748 | 0.36 | 13.47 | 0
July | 14 | 10PM to 11PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
July | 14 | 11PM to 12AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 15 | 12AM to 1AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 15 | 1AM to 2AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 15 | 2AM to 3AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 15 | 3AM to 4AM | 57.9 | 54.4 | 51.8 | 57.4 | 22.81 | 0.0762 | 0.39 | 13.23 | 0
July | 15 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
July | 15 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
July | 15 | 6AM to 7AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
July | 15 | 7AM to 8AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 15 | 8AM to 9AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 15 | 9AM to 10AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
July | 15 | 10AM to 11AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
July | 15 | 11AM to 12PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
July | 15 | 12PM to 1PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
July | 15 | 1PM to 2PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
July | 15 | 2PM to 3PM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
July | 15 | 3PM to 4PM | 86 | 64.7 | 51.8 | 57.4 | 29.66 | 0.0723 | 0.39 | 13.94 | 0
July | 15 | 4PM to 5PM | 84.2 | 61.8 | 46.4 | 46.8 | 27.55 | 0.0726 | 0.32 | 13.86 | 0
July | 15 | 5PM to 6PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
July | 15 | 6PM to 7PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
July | 15 | 7PM to 8PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 15 | 8PM to 9PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 15 | 9PM to 10PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 15 | 10PM to 11PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 15 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
July | 16 | 12AM to 1AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
July | 16 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
July | 16 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
July | 16 | 3AM to 4AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
July | 16 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
July | 16 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
July | 16 | 6AM to 7AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 16 | 7AM to 8AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 16 | 8AM to 9AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 16 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 16 | 10AM to 11AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
July | 16 | 11AM to 12PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
July | 16 | 12PM to 1PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
July | 16 | 1PM to 2PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
July | 16 | 2PM to 3PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
July | 16 | 3PM to 4PM | 87.8 | 62.4 | 44.6 | 43.7 | 27.94 | 0.0722 | 0.3 | 13.95 | 0
July | 16 | 4PM to 5PM | 87.8 | 62.4 | 44.6 | 43.7 | 27.94 | 0.0722 | 0.3 | 13.95 | 0
July | 16 | 5PM to 6PM | 84.2 | 61.8 | 46.4 | 46.8 | 27.55 | 0.0726 | 0.32 | 13.86 | 0
July | 16 | 6PM to 7PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
July | 16 | 7PM to 8PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
July | 16 | 8PM to 9PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
July | 16 | 9PM to 10PM | 65.7 | 58.3 | 53.4 | 61 | 25.26 | 0.0751 | 0.41 | 13.43 | 0
July | 16 | 10PM to 11PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 16 | 11PM to 12AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 17 | 12AM to 1AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 17 | 1AM to 2AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 17 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 17 | 3AM to 4AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
July | 17 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
July | 17 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 17 | 6AM to 7AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 17 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 17 | 8AM to 9AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 17 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 17 | 10AM to 11AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
July | 17 | 11AM to 12PM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
July | 17 | 12PM to 1PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
July | 17 | 1PM to 2PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
July | 17 | 2PM to 3PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
July | 17 | 3PM to 4PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
July | 17 | 4PM to 5PM | 89.6 | 65.1 | 50 | 53.7 | 29.94 | 0.0719 | 0.36 | 14.02 | 0
July | 17 | 5PM to 6PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
July | 17 | 6PM to 7PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
July | 17 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 17 | 8PM to 9PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 17 | 9PM to 10PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 17 | 10PM to 11PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 17 | 11PM to 12AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 18 | 12AM to 1AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 18 | 1AM to 2AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 18 | 2AM to 3AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
July | 18 | 3AM to 4AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
July | 18 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 18 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 18 | 6AM to 7AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 18 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 18 | 8AM to 9AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 18 | 9AM to 10AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 18 | 10AM to 11AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
July | 18 | 11AM to 12PM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
July | 18 | 12PM to 1PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
July | 18 | 1PM to 2PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
July | 18 | 2PM to 3PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
July | 18 | 3PM to 4PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
July | 18 | 4PM to 5PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
July | 18 | 5PM to 6PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
July | 18 | 6PM to 7PM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
July | 18 | 7PM to 8PM | 71.6 | 63.5 | 59 | 74.9 | 28.88 | 0.0742 | 0.5 | 13.63 | 0
July | 18 | 8PM to 9PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
July | 18 | 9PM to 10PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 18 | 10PM to 11PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 18 | 11PM to 12AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 19 | 12AM to 1AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 19 | 1AM to 2AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 19 | 2AM to 3AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 19 | 3AM to 4AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 19 | 4AM to 5AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
July | 19 | 5AM to 6AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 19 | 6AM to 7AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
July | 19 | 7AM to 8AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
July | 19 | 8AM to 9AM | 73.4 | 64.1 | 59 | 74.9 | 29.32 | 0.0739 | 0.5 | 13.68 | 0
July | 19 | 9AM to 10AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
July | 19 | 10AM to 11AM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
July | 19 | 11AM to 12PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
July | 19 | 12PM to 1PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
July | 19 | 1PM to 2PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
July | 19 | 2PM to 3PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
July | 19 | 3PM to 4PM | 95 | 69.1 | 55.4 | 65.6 | 33.14 | 0.0711 | 0.44 | 14.2 | 0
July | 19 | 4PM to 5PM | 95 | 69.1 | 55.4 | 65.6 | 33.14 | 0.0711 | 0.44 | 14.2 | 0
July | 19 | 5PM to 6PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
July | 19 | 6PM to 7PM | 89.6 | 64.3 | 48.2 | 50.1 | 29.39 | 0.0719 | 0.34 | 14.01 | 0
July | 19 | 7PM to 8PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
July | 19 | 8PM to 9PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 19 | 9PM to 10PM | 71.6 | 63.5 | 59 | 74.9 | 28.88 | 0.0742 | 0.5 | 13.63 | 0
July | 19 | 10PM to 11PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
July | 19 | 11PM to 12AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
July | 20 | 12AM to 1AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
July | 20 | 1AM to 2AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
July | 20 | 2AM to 3AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
July | 20 | 3AM to 4AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 20 | 4AM to 5AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 20 | 5AM to 6AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 20 | 6AM to 7AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 20 | 7AM to 8AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 20 | 8AM to 9AM | 78.8 | 65.9 | 59 | 74.9 | 30.64 | 0.0732 | 0.5 | 13.81 | 0
July | 20 | 9AM to 10AM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
July | 20 | 10AM to 11AM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
July | 20 | 11AM to 12PM | 91.4 | 70.7 | 60.8 | 79.9 | 34.52 | 0.0715 | 0.54 | 14.15 | 0
July | 20 | 12PM to 1PM | 93.2 | 67 | 51.8 | 57.4 | 31.41 | 0.0714 | 0.39 | 14.13 | 0
July | 20 | 1PM to 2PM | 96.8 | 69.7 | 55.4 | 65.6 | 33.58 | 0.0709 | 0.44 | 14.25 | 0
July | 20 | 2PM to 3PM | 98.6 | 71 | 57.2 | 70.1 | 34.73 | 0.0706 | 0.47 | 14.31 | 0
July | 20 | 3PM to 4PM | 98.6 | 70.2 | 55.4 | 65.6 | 34.02 | 0.0706 | 0.44 | 14.29 | 0
July | 20 | 4PM to 5PM | 96.8 | 66.7 | 48.2 | 50.1 | 31.14 | 0.0709 | 0.34 | 14.2 | 0
July | 20 | 5PM to 6PM | 93.2 | 67 | 51.8 | 57.4 | 31.41 | 0.0714 | 0.39 | 14.13 | 0
July | 20 | 6PM to 7PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
July | 20 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 20 | 8PM to 9PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
July | 20 | 9PM to 10PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 20 | 10PM to 11PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 20 | 11PM to 12AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 21 | 12AM to 1AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 21 | 1AM to 2AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 21 | 2AM to 3AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 21 | 3AM to 4AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 21 | 4AM to 5AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 21 | 5AM to 6AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 21 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 21 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 21 | 8AM to 9AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 21 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
July | 21 | 10AM to 11AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
July | 21 | 11AM to 12PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
July | 21 | 12PM to 1PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
July | 21 | 1PM to 2PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
July | 21 | 2PM to 3PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
July | 21 | 3PM to 4PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
July | 21 | 4PM to 5PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
July | 21 | 5PM to 6PM | 78.8 | 65.9 | 59 | 74.9 | 30.64 | 0.0732 | 0.5 | 13.81 | 0
July | 21 | 6PM to 7PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 21 | 7PM to 8PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 21 | 8PM to 9PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 21 | 9PM to 10PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
July | 21 | 10PM to 11PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 21 | 11PM to 12AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 22 | 12AM to 1AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 22 | 1AM to 2AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 22 | 2AM to 3AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 22 | 3AM to 4AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 22 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 22 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 22 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 22 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 22 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 22 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 22 | 10AM to 11AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
July | 22 | 11AM to 12PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
July | 22 | 12PM to 1PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
July | 22 | 1PM to 2PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
July | 22 | 2PM to 3PM | 86 | 65.5 | 53.6 | 61.4 | 30.28 | 0.0723 | 0.41 | 13.96 | 0
July | 22 | 3PM to 4PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
July | 22 | 4PM to 5PM | 86 | 65.5 | 53.6 | 61.4 | 30.28 | 0.0723 | 0.41 | 13.96 | 0
July | 22 | 5PM to 6PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
July | 22 | 6PM to 7PM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
July | 22 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 22 | 8PM to 9PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
July | 22 | 9PM to 10PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
July | 22 | 10PM to 11PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
July | 22 | 11PM to 12AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 23 | 12AM to 1AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 23 | 1AM to 2AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 23 | 2AM to 3AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 23 | 3AM to 4AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 23 | 4AM to 5AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
July | 23 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
July | 23 | 6AM to 7AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 23 | 7AM to 8AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 23 | 8AM to 9AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
July | 23 | 9AM to 10AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
July | 23 | 10AM to 11AM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
July | 23 | 11AM to 12PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
July | 23 | 12PM to 1PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
July | 23 | 1PM to 2PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
July | 23 | 2PM to 3PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
July | 23 | 3PM to 4PM | 86 | 65.5 | 53.6 | 61.4 | 30.28 | 0.0723 | 0.41 | 13.96 | 0
July | 23 | 4PM to 5PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
July | 23 | 5PM to 6PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
July | 23 | 6PM to 7PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
July | 23 | 7PM to 8PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
July | 23 | 8PM to 9PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
July | 23 | 9PM to 10PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
July | 23 | 10PM to 11PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
July | 23 | 11PM to 12AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 24 | 12AM to 1AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 24 | 1AM to 2AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 24 | 2AM to 3AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 24 | 3AM to 4AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 24 | 4AM to 5AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
July | 24 | 5AM to 6AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 24 | 6AM to 7AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
July | 24 | 7AM to 8AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
July | 24 | 8AM to 9AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
July | 24 | 9AM to 10AM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
July | 24 | 10AM to 11AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
July | 24 | 11AM to 12PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
July | 24 | 12PM to 1PM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
July | 24 | 1PM to 2PM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
July | 24 | 2PM to 3PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
July | 24 | 3PM to 4PM | 91.4 | 63.6 | 44.6 | 43.7 | 28.81 | 0.0717 | 0.3 | 14.04 | 0
July | 24 | 4PM to 5PM | 89.6 | 63 | 44.6 | 43.7 | 28.37 | 0.0719 | 0.3 | 13.99 | 0
July | 24 | 5PM to 6PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
July | 24 | 6PM to 7PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
July | 24 | 7PM to 8PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
July | 24 | 8PM to 9PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
July | 24 | 9PM to 10PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
July | 24 | 10PM to 11PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
July | 24 | 11PM to 12AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
July | 25 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
July | 25 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 25 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 25 | 3AM to 4AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
July | 25 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
July | 25 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 25 | 6AM to 7AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 25 | 7AM to 8AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 25 | 8AM to 9AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
July | 25 | 9AM to 10AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
July | 25 | 10AM to 11AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
July | 25 | 11AM to 12PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
July | 25 | 12PM to 1PM | 84.6 | 64.3 | 52 | 57.8 | 29.37 | 0.0725 | 0.39 | 13.91 | 0
July | 25 | 1PM to 2PM | 87.8 | 63.7 | 48.2 | 50.1 | 28.95 | 0.0721 | 0.34 | 13.97 | 0
July | 25 | 2PM to 3PM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
July | 25 | 3PM to 4PM | 91.4 | 61.8 | 39.2 | 35.4 | 27.51 | 0.0717 | 0.24 | 14.01 | 0
July | 25 | 4PM to 5PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
July | 25 | 5PM to 6PM | 87.8 | 62.4 | 44.6 | 43.7 | 27.94 | 0.0722 | 0.3 | 13.95 | 0
July | 25 | 6PM to 7PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
July | 25 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 25 | 8PM to 9PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 25 | 9PM to 10PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
July | 25 | 10PM to 11PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
July | 25 | 11PM to 12AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 26 | 12AM to 1AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 26 | 1AM to 2AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
July | 26 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 26 | 3AM to 4AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
July | 26 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
July | 26 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
July | 26 | 6AM to 7AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
July | 26 | 7AM to 8AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 26 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 26 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
July | 26 | 10AM to 11AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
July | 26 | 11AM to 12PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
July | 26 | 12PM to 1PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
July | 26 | 1PM to 2PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
July | 26 | 2PM to 3PM | 93.2 | 67 | 51.8 | 57.4 | 31.41 | 0.0714 | 0.39 | 14.13 | 0
July | 26 | 3PM to 4PM | 95 | 69.1 | 55.4 | 65.6 | 33.14 | 0.0711 | 0.44 | 14.2 | 0
July | 26 | 4PM to 5PM | 94.1 | 69 | 55.8 | 66.5 | 33.06 | 0.0712 | 0.45 | 14.18 | 0
July | 26 | 5PM to 6PM | 91 | 68.7 | 57 | 69.7 | 32.81 | 0.0716 | 0.47 | 14.11 | 0
July | 26 | 6PM to 7PM | 86.2 | 68 | 58.6 | 73.9 | 32.29 | 0.0722 | 0.5 | 14 | 0
July | 26 | 7PM to 8PM | 79.5 | 65.8 | 58.5 | 73.4 | 30.59 | 0.0731 | 0.49 | 13.83 | 0
July | 26 | 8PM to 9PM | 75.2 | 64.1 | 57.9 | 72 | 29.3 | 0.0737 | 0.48 | 13.71 | 0
July | 26 | 9PM to 10PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 26 | 10PM to 11PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
July | 26 | 11PM to 12AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
July | 27 | 12AM to 1AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
July | 27 | 1AM to 2AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 27 | 2AM to 3AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 27 | 3AM to 4AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 27 | 4AM to 5AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 27 | 5AM to 6AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 27 | 6AM to 7AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
July | 27 | 7AM to 8AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
July | 27 | 8AM to 9AM | 73.4 | 64.1 | 59 | 74.9 | 29.32 | 0.0739 | 0.5 | 13.68 | 0
July | 27 | 9AM to 10AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
July | 27 | 10AM to 11AM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
July | 27 | 11AM to 12PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
July | 27 | 12PM to 1PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
July | 27 | 1PM to 2PM | 91.4 | 69.8 | 59 | 74.9 | 33.72 | 0.0715 | 0.5 | 14.14 | 0
July | 27 | 2PM to 3PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
July | 27 | 3PM to 4PM | 95 | 70.8 | 59 | 74.9 | 34.6 | 0.071 | 0.5 | 14.23 | 0
July | 27 | 4PM to 5PM | 93.2 | 72.2 | 62.6 | 85.3 | 35.8 | 0.0712 | 0.57 | 14.22 | 0
July | 27 | 5PM to 6PM | 87.8 | 71.6 | 64.4 | 91 | 35.37 | 0.0719 | 0.61 | 14.1 | 0
July | 27 | 6PM to 7PM | 80.6 | 68.5 | 62.6 | 85.3 | 32.71 | 0.0729 | 0.57 | 13.89 | 0
July | 27 | 7PM to 8PM | 73.4 | 65.1 | 60.8 | 79.9 | 30.11 | 0.0739 | 0.54 | 13.69 | 0
July | 27 | 8PM to 9PM | 71.6 | 63.5 | 59 | 74.9 | 28.88 | 0.0742 | 0.5 | 13.63 | 0
July | 27 | 9PM to 10PM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.54 | 0
July | 27 | 10PM to 11PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 27 | 11PM to 12AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 28 | 12AM to 1AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 28 | 1AM to 2AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 28 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 28 | 3AM to 4AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 28 | 4AM to 5AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 28 | 5AM to 6AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 28 | 6AM to 7AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
July | 28 | 7AM to 8AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 28 | 8AM to 9AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
July | 28 | 9AM to 10AM | 73.4 | 64.1 | 59 | 74.9 | 29.32 | 0.0739 | 0.5 | 13.68 | 0
July | 28 | 10AM to 11AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
July | 28 | 11AM to 12PM | 82.4 | 69 | 62.6 | 85.3 | 33.15 | 0.0726 | 0.57 | 13.94 | 0
July | 28 | 12PM to 1PM | 87.8 | 70.6 | 62.6 | 85.3 | 34.48 | 0.0719 | 0.57 | 14.08 | 0
July | 28 | 1PM to 2PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
July | 28 | 2PM to 3PM | 89.6 | 71.1 | 62.6 | 85.3 | 34.92 | 0.0717 | 0.57 | 14.12 | 0
July | 28 | 3PM to 4PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
July | 28 | 4PM to 5PM | 87.8 | 70.6 | 62.6 | 85.3 | 34.48 | 0.0719 | 0.57 | 14.08 | 0
July | 28 | 5PM to 6PM | 82.4 | 69 | 62.6 | 85.3 | 33.15 | 0.0726 | 0.57 | 13.94 | 0
July | 28 | 6PM to 7PM | 75.2 | 65.7 | 60.8 | 79.9 | 30.55 | 0.0736 | 0.54 | 13.74 | 0
July | 28 | 7PM to 8PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 28 | 8PM to 9PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 28 | 9PM to 10PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 28 | 10PM to 11PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 28 | 11PM to 12AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 29 | 12AM to 1AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 29 | 1AM to 2AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 29 | 2AM to 3AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 29 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
July | 29 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
July | 29 | 5AM to 6AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
July | 29 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 29 | 7AM to 8AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
July | 29 | 8AM to 9AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 29 | 9AM to 10AM | 71.6 | 63.5 | 59 | 74.9 | 28.88 | 0.0742 | 0.5 | 13.63 | 0
July | 29 | 10AM to 11AM | 75.2 | 64.7 | 59 | 74.9 | 29.76 | 0.0737 | 0.5 | 13.72 | 0
July | 29 | 11AM to 12PM | 78.8 | 67.9 | 62.6 | 85.3 | 32.27 | 0.0731 | 0.57 | 13.85 | 0
July | 29 | 12PM to 1PM | 82.4 | 69 | 62.6 | 85.3 | 33.15 | 0.0726 | 0.57 | 13.94 | 0
July | 29 | 1PM to 2PM | 86 | 71.1 | 64.4 | 91 | 34.93 | 0.0721 | 0.61 | 14.05 | 0
July | 29 | 2PM to 3PM | 89.6 | 71.1 | 62.6 | 85.3 | 34.92 | 0.0717 | 0.57 | 14.12 | 0
July | 29 | 3PM to 4PM | 89.6 | 72.1 | 64.4 | 91 | 35.81 | 0.0716 | 0.61 | 14.14 | 0
July | 29 | 4PM to 5PM | 87.8 | 70.6 | 62.6 | 85.3 | 34.48 | 0.0719 | 0.57 | 14.08 | 0
July | 29 | 5PM to 6PM | 80.6 | 68.5 | 62.6 | 85.3 | 32.71 | 0.0729 | 0.57 | 13.89 | 0
July | 29 | 6PM to 7PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
July | 29 | 7PM to 8PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
July | 29 | 8PM to 9PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 29 | 9PM to 10PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
July | 29 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 29 | 11PM to 12AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 30 | 12AM to 1AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 30 | 1AM to 2AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 30 | 2AM to 3AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 30 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
July | 30 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
July | 30 | 5AM to 6AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
July | 30 | 6AM to 7AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 30 | 7AM to 8AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
July | 30 | 8AM to 9AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
July | 30 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 30 | 10AM to 11AM | 78.8 | 65.9 | 59 | 74.9 | 30.64 | 0.0732 | 0.5 | 13.81 | 0
July | 30 | 11AM to 12PM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
July | 30 | 12PM to 1PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
July | 30 | 1PM to 2PM | 87.8 | 69.6 | 60.8 | 79.9 | 33.64 | 0.0719 | 0.54 | 14.06 | 0
July | 30 | 2PM to 3PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
July | 30 | 3PM to 4PM | 91.4 | 71.7 | 62.6 | 85.3 | 35.36 | 0.0714 | 0.57 | 14.17 | 0
July | 30 | 4PM to 5PM | 91.4 | 70.7 | 60.8 | 79.9 | 34.52 | 0.0715 | 0.54 | 14.15 | 0
July | 30 | 5PM to 6PM | 89.6 | 71.1 | 62.6 | 85.3 | 34.92 | 0.0717 | 0.57 | 14.12 | 0
July | 30 | 6PM to 7PM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
July | 30 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 30 | 8PM to 9PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
July | 30 | 9PM to 10PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
July | 30 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 30 | 11PM to 12AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 31 | 12AM to 1AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 31 | 1AM to 2AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
July | 31 | 2AM to 3AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 31 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
July | 31 | 4AM to 5AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
July | 31 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
July | 31 | 6AM to 7AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
July | 31 | 7AM to 8AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
July | 31 | 8AM to 9AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
July | 31 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
July | 31 | 10AM to 11AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
July | 31 | 11AM to 12PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
July | 31 | 12PM to 1PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
July | 31 | 1PM to 2PM | 87.8 | 70.6 | 62.6 | 85.3 | 34.48 | 0.0719 | 0.57 | 14.08 | 0
July | 31 | 2PM to 3PM | 91.4 | 71.7 | 62.6 | 85.3 | 35.36 | 0.0714 | 0.57 | 14.17 | 0
July | 31 | 3PM to 4PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
July | 31 | 4PM to 5PM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
July | 31 | 5PM to 6PM | 86 | 69.1 | 60.8 | 79.9 | 33.19 | 0.0722 | 0.54 | 14.01 | 0
July | 31 | 6PM to 7PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
July | 31 | 7PM to 8PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
July | 31 | 8PM to 9PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
July | 31 | 9PM to 10PM | 66.9 | 60.5 | 56.7 | 68.8 | 26.77 | 0.0749 | 0.46 | 13.49 | 0
July | 31 | 10PM to 11PM | 66 | 59.9 | 56.1 | 67.4 | 26.34 | 0.075 | 0.45 | 13.46 | 0
July | 31 | 11PM to 12AM | 64.9 | 59.2 | 55.6 | 66.1 | 25.87 | 0.0752 | 0.45 | 13.43 | 0
August | 1 | 12AM to 1AM | 63.9 | 58.6 | 55.2 | 65.2 | 25.47 | 0.0753 | 0.44 | 13.4 | 0
August | 1 | 1AM to 2AM | 62.8 | 57.9 | 54.7 | 63.9 | 25.01 | 0.0755 | 0.43 | 13.37 | 0
August | 1 | 2AM to 3AM | 61.9 | 57.2 | 54.1 | 62.6 | 24.59 | 0.0756 | 0.42 | 13.34 | 0
August | 1 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 1 | 4AM to 5AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 1 | 5AM to 6AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 1 | 6AM to 7AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 1 | 7AM to 8AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
August | 1 | 8AM to 9AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 1 | 9AM to 10AM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
August | 1 | 10AM to 11AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 1 | 11AM to 12PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 1 | 12PM to 1PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
August | 1 | 1PM to 2PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
August | 1 | 2PM to 3PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
August | 1 | 3PM to 4PM | 91.4 | 65.7 | 50 | 53.7 | 30.38 | 0.0716 | 0.36 | 14.07 | 0
August | 1 | 4PM to 5PM | 89.6 | 65.1 | 50 | 53.7 | 29.94 | 0.0719 | 0.36 | 14.02 | 0
August | 1 | 5PM to 6PM | 86 | 65.5 | 53.6 | 61.4 | 30.28 | 0.0723 | 0.41 | 13.96 | 0
August | 1 | 6PM to 7PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 1 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 1 | 8PM to 9PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 1 | 9PM to 10PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 1 | 10PM to 11PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 1 | 11PM to 12AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 2 | 12AM to 1AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 2 | 1AM to 2AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 2 | 2AM to 3AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 2 | 3AM to 4AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 2 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 2 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 2 | 6AM to 7AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 2 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 2 | 8AM to 9AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
August | 2 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 2 | 10AM to 11AM | 77 | 66.3 | 60.8 | 79.9 | 30.99 | 0.0734 | 0.54 | 13.78 | 0
August | 2 | 11AM to 12PM | 82.4 | 67 | 59 | 74.9 | 31.52 | 0.0727 | 0.5 | 13.91 | 0
August | 2 | 12PM to 1PM | 86 | 69.1 | 60.8 | 79.9 | 33.19 | 0.0722 | 0.54 | 14.01 | 0
August | 2 | 1PM to 2PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
August | 2 | 2PM to 3PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
August | 2 | 3PM to 4PM | 93.2 | 61.9 | 37.4 | 33 | 27.56 | 0.0715 | 0.22 | 14.05 | 0
August | 2 | 4PM to 5PM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
August | 2 | 5PM to 6PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
August | 2 | 6PM to 7PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 2 | 7PM to 8PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
August | 2 | 8PM to 9PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
August | 2 | 9PM to 10PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 2 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 2 | 11PM to 12AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 3 | 12AM to 1AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 3 | 1AM to 2AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 3 | 2AM to 3AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 3 | 3AM to 4AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 3 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 3 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 3 | 6AM to 7AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 3 | 7AM to 8AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 3 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 3 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 3 | 10AM to 11AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
August | 3 | 11AM to 12PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 3 | 12PM to 1PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 3 | 1PM to 2PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
August | 3 | 2PM to 3PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
August | 3 | 3PM to 4PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
August | 3 | 4PM to 5PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
August | 3 | 5PM to 6PM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
August | 3 | 6PM to 7PM | 73.4 | 64.1 | 59 | 74.9 | 29.32 | 0.0739 | 0.5 | 13.68 | 0
August | 3 | 7PM to 8PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
August | 3 | 8PM to 9PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
August | 3 | 9PM to 10PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
August | 3 | 10PM to 11PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
August | 3 | 11PM to 12AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
August | 4 | 12AM to 1AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
August | 4 | 1AM to 2AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
August | 4 | 2AM to 3AM | 59 | 57.9 | 57.2 | 70.1 | 25.05 | 0.076 | 0.47 | 13.29 | 0
August | 4 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 4 | 4AM to 5AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 4 | 5AM to 6AM | 59 | 57.9 | 57.2 | 70.1 | 25.05 | 0.076 | 0.47 | 13.29 | 0
August | 4 | 6AM to 7AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
August | 4 | 7AM to 8AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
August | 4 | 8AM to 9AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
August | 4 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 4 | 10AM to 11AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
August | 4 | 11AM to 12PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 4 | 12PM to 1PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 4 | 1PM to 2PM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
August | 4 | 2PM to 3PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 4 | 3PM to 4PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 4 | 4PM to 5PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 4 | 5PM to 6PM | 84.2 | 67.6 | 59 | 74.9 | 31.96 | 0.0724 | 0.5 | 13.95 | 0
August | 4 | 6PM to 7PM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
August | 4 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 4 | 8PM to 9PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
August | 4 | 9PM to 10PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
August | 4 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 4 | 11PM to 12AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 5 | 12AM to 1AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 5 | 1AM to 2AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 5 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 5 | 3AM to 4AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 5 | 4AM to 5AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 5 | 5AM to 6AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 5 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 5 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 5 | 8AM to 9AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
August | 5 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 5 | 10AM to 11AM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 5 | 11AM to 12PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
August | 5 | 12PM to 1PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 5 | 1PM to 2PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
August | 5 | 2PM to 3PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
August | 5 | 3PM to 4PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
August | 5 | 4PM to 5PM | 91.4 | 65.7 | 50 | 53.7 | 30.38 | 0.0716 | 0.36 | 14.07 | 0
August | 5 | 5PM to 6PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
August | 5 | 6PM to 7PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
August | 5 | 7PM to 8PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
August | 5 | 8PM to 9PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 5 | 9PM to 10PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 5 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 5 | 11PM to 12AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 6 | 12AM to 1AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 6 | 1AM to 2AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 6 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 6 | 3AM to 4AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 6 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 6 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 6 | 6AM to 7AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
August | 6 | 7AM to 8AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
August | 6 | 8AM to 9AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 6 | 9AM to 10AM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 6 | 10AM to 11AM | 84.2 | 67.6 | 59 | 74.9 | 31.96 | 0.0724 | 0.5 | 13.95 | 0
August | 6 | 11AM to 12PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
August | 6 | 12PM to 1PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
August | 6 | 1PM to 2PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
August | 6 | 2PM to 3PM | 95 | 70 | 57.2 | 70.1 | 33.85 | 0.0711 | 0.47 | 14.21 | 0
August | 6 | 3PM to 4PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
August | 6 | 4PM to 5PM | 96.8 | 69.7 | 55.4 | 65.6 | 33.58 | 0.0709 | 0.44 | 14.25 | 0
August | 6 | 5PM to 6PM | 93.2 | 67 | 51.8 | 57.4 | 31.41 | 0.0714 | 0.39 | 14.13 | 0
August | 6 | 6PM to 7PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 6 | 7PM to 8PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 6 | 8PM to 9PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 6 | 9PM to 10PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 6 | 10PM to 11PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 6 | 11PM to 12AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 7 | 12AM to 1AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 7 | 1AM to 2AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 7 | 2AM to 3AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 7 | 3AM to 4AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
August | 7 | 4AM to 5AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 7 | 5AM to 6AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 7 | 6AM to 7AM | 69.8 | 62.9 | 59 | 74.9 | 28.44 | 0.0744 | 0.5 | 13.58 | 0
August | 7 | 7AM to 8AM | 75.2 | 64.7 | 59 | 74.9 | 29.76 | 0.0737 | 0.5 | 13.72 | 0
August | 7 | 8AM to 9AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 7 | 9AM to 10AM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
August | 7 | 10AM to 11AM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
August | 7 | 11AM to 12PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
August | 7 | 12PM to 1PM | 95 | 69.1 | 55.4 | 65.6 | 33.14 | 0.0711 | 0.44 | 14.2 | 0
August | 7 | 1PM to 2PM | 98.6 | 68.7 | 51.8 | 57.4 | 32.73 | 0.0707 | 0.39 | 14.27 | 0
August | 7 | 2PM to 3PM | 100.4 | 70.7 | 55.4 | 65.6 | 34.46 | 0.0704 | 0.44 | 14.34 | 0
August | 7 | 3PM to 4PM | 100.4 | 70.7 | 55.4 | 65.6 | 34.46 | 0.0704 | 0.44 | 14.34 | 0
August | 7 | 4PM to 5PM | 100.4 | 70.7 | 55.4 | 65.6 | 34.46 | 0.0704 | 0.44 | 14.34 | 0
August | 7 | 5PM to 6PM | 98.6 | 70.2 | 55.4 | 65.6 | 34.02 | 0.0706 | 0.44 | 14.29 | 0
August | 7 | 6PM to 7PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
August | 7 | 7PM to 8PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
August | 7 | 8PM to 9PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
August | 7 | 9PM to 10PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
August | 7 | 10PM to 11PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
August | 7 | 11PM to 12AM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
August | 8 | 12AM to 1AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 8 | 1AM to 2AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 8 | 2AM to 3AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 8 | 3AM to 4AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 8 | 4AM to 5AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 8 | 5AM to 6AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 8 | 6AM to 7AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
August | 8 | 7AM to 8AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
August | 8 | 8AM to 9AM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
August | 8 | 9AM to 10AM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 8 | 10AM to 11AM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
August | 8 | 11AM to 12PM | 91.4 | 71.7 | 62.6 | 85.3 | 35.36 | 0.0714 | 0.57 | 14.17 | 0
August | 8 | 12PM to 1PM | 96.8 | 72.3 | 60.8 | 79.9 | 35.84 | 0.0708 | 0.54 | 14.29 | 0
August | 8 | 1PM to 2PM | 98.6 | 72.8 | 60.8 | 79.9 | 36.28 | 0.0705 | 0.54 | 14.34 | 0
August | 8 | 2PM to 3PM | 102.2 | 73.8 | 60.8 | 79.9 | 37.16 | 0.0701 | 0.54 | 14.43 | 0
August | 8 | 3PM to 4PM | 102.2 | 71.3 | 55.4 | 65.6 | 34.9 | 0.0702 | 0.44 | 14.38 | 0
August | 8 | 4PM to 5PM | 100.4 | 70 | 53.6 | 61.4 | 33.79 | 0.0704 | 0.41 | 14.32 | 0
August | 8 | 5PM to 6PM | 95 | 71.7 | 60.8 | 79.9 | 35.4 | 0.071 | 0.54 | 14.25 | 0
August | 8 | 6PM to 7PM | 88.9 | 70 | 60.8 | 79.9 | 33.9 | 0.0718 | 0.54 | 14.09 | 0
August | 8 | 7PM to 8PM | 83.1 | 67.3 | 59.2 | 75.4 | 31.77 | 0.0726 | 0.51 | 13.93 | 0
August | 8 | 8PM to 9PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 8 | 9PM to 10PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 8 | 10PM to 11PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 8 | 11PM to 12AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 9 | 12AM to 1AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 9 | 1AM to 2AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 9 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 9 | 3AM to 4AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 9 | 4AM to 5AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 9 | 5AM to 6AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 9 | 6AM to 7AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 9 | 7AM to 8AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 9 | 8AM to 9AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 9 | 9AM to 10AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 9 | 10AM to 11AM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 9 | 11AM to 12PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
August | 9 | 12PM to 1PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
August | 9 | 1PM to 2PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
August | 9 | 2PM to 3PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
August | 9 | 3PM to 4PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
August | 9 | 4PM to 5PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
August | 9 | 5PM to 6PM | 86 | 68.1 | 59 | 74.9 | 32.4 | 0.0722 | 0.5 | 14 | 0
August | 9 | 6PM to 7PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 9 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 9 | 8PM to 9PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
August | 9 | 9PM to 10PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
August | 9 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 9 | 11PM to 12AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 10 | 12AM to 1AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 10 | 1AM to 2AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 10 | 2AM to 3AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 10 | 3AM to 4AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 10 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 10 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 10 | 6AM to 7AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 10 | 7AM to 8AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 10 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 10 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 10 | 10AM to 11AM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 10 | 11AM to 12PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
August | 10 | 12PM to 1PM | 84.2 | 67.6 | 59 | 74.9 | 31.96 | 0.0724 | 0.5 | 13.95 | 0
August | 10 | 1PM to 2PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
August | 10 | 2PM to 3PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
August | 10 | 3PM to 4PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
August | 10 | 4PM to 5PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
August | 10 | 5PM to 6PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 10 | 6PM to 7PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 10 | 7PM to 8PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
August | 10 | 8PM to 9PM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
August | 10 | 9PM to 10PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
August | 10 | 10PM to 11PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
August | 10 | 11PM to 12AM | 61.7 | 55.9 | 51.8 | 57.4 | 23.74 | 0.0757 | 0.39 | 13.32 | 0
August | 11 | 12AM to 1AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
August | 11 | 1AM to 2AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
August | 11 | 2AM to 3AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
August | 11 | 3AM to 4AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 11 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 11 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
August | 11 | 6AM to 7AM | 58.5 | 55.3 | 53.1 | 60.2 | 23.38 | 0.0761 | 0.41 | 13.25 | 0
August | 11 | 7AM to 8AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 11 | 8AM to 9AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
August | 11 | 9AM to 10AM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
August | 11 | 10AM to 11AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 11 | 11AM to 12PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
August | 11 | 12PM to 1PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 11 | 1PM to 2PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
August | 11 | 2PM to 3PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
August | 11 | 3PM to 4PM | 93.2 | 67 | 51.8 | 57.4 | 31.41 | 0.0714 | 0.39 | 14.13 | 0
August | 11 | 4PM to 5PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
August | 11 | 5PM to 6PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 11 | 6PM to 7PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 11 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 11 | 8PM to 9PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
August | 11 | 9PM to 10PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
August | 11 | 10PM to 11PM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
August | 11 | 11PM to 12AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
August | 12 | 12AM to 1AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
August | 12 | 1AM to 2AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 12 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 12 | 3AM to 4AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 12 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 12 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 12 | 6AM to 7AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 12 | 7AM to 8AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 12 | 8AM to 9AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 12 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 12 | 10AM to 11AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 12 | 11AM to 12PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 12 | 12PM to 1PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
August | 12 | 1PM to 2PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
August | 12 | 2PM to 3PM | 86 | 63.9 | 50 | 53.7 | 29.07 | 0.0723 | 0.36 | 13.93 | 0
August | 12 | 3PM to 4PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
August | 12 | 4PM to 5PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
August | 12 | 5PM to 6PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
August | 12 | 6PM to 7PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
August | 12 | 7PM to 8PM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
August | 12 | 8PM to 9PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
August | 12 | 9PM to 10PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
August | 12 | 10PM to 11PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
August | 12 | 11PM to 12AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
August | 13 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 13 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 13 | 2AM to 3AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 13 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 13 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 13 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
August | 13 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 13 | 7AM to 8AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 13 | 8AM to 9AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 13 | 9AM to 10AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 13 | 10AM to 11AM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
August | 13 | 11AM to 12PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
August | 13 | 12PM to 1PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 13 | 1PM to 2PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 13 | 2PM to 3PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
August | 13 | 3PM to 4PM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
August | 13 | 4PM to 5PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
August | 13 | 5PM to 6PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
August | 13 | 6PM to 7PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
August | 13 | 7PM to 8PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
August | 13 | 8PM to 9PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
August | 13 | 9PM to 10PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
August | 13 | 10PM to 11PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 13 | 11PM to 12AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 14 | 12AM to 1AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 14 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 14 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 14 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 14 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
August | 14 | 5AM to 6AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
August | 14 | 6AM to 7AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 14 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 14 | 8AM to 9AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
August | 14 | 9AM to 10AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 14 | 10AM to 11AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 14 | 11AM to 12PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 14 | 12PM to 1PM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
August | 14 | 1PM to 2PM | 91.4 | 64.9 | 48.2 | 50.1 | 29.83 | 0.0716 | 0.34 | 14.06 | 0
August | 14 | 2PM to 3PM | 93.2 | 63.6 | 42.8 | 40.8 | 28.79 | 0.0715 | 0.28 | 14.07 | 0
August | 14 | 3PM to 4PM | 93.2 | 63.6 | 42.8 | 40.8 | 28.79 | 0.0715 | 0.28 | 14.07 | 0
August | 14 | 4PM to 5PM | 93.2 | 65.5 | 48.2 | 50.1 | 30.26 | 0.0714 | 0.34 | 14.1 | 0
August | 14 | 5PM to 6PM | 91.4 | 64.9 | 48.2 | 50.1 | 29.83 | 0.0716 | 0.34 | 14.06 | 0
August | 14 | 6PM to 7PM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
August | 14 | 7PM to 8PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
August | 14 | 8PM to 9PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
August | 14 | 9PM to 10PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 14 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 14 | 11PM to 12AM | 63.5 | 58 | 54.5 | 63.5 | 25.12 | 0.0754 | 0.43 | 13.39 | 0
August | 15 | 12AM to 1AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 15 | 1AM to 2AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 15 | 2AM to 3AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 15 | 3AM to 4AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 15 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
August | 15 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 15 | 6AM to 7AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 15 | 7AM to 8AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 15 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 15 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 15 | 10AM to 11AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 15 | 11AM to 12PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
August | 15 | 12PM to 1PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
August | 15 | 1PM to 2PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
August | 15 | 2PM to 3PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
August | 15 | 3PM to 4PM | 93.2 | 67 | 51.8 | 57.4 | 31.41 | 0.0714 | 0.39 | 14.13 | 0
August | 15 | 4PM to 5PM | 93.2 | 66.3 | 50 | 53.7 | 30.82 | 0.0714 | 0.36 | 14.12 | 0
August | 15 | 5PM to 6PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
August | 15 | 6PM to 7PM | 86 | 65.5 | 53.6 | 61.4 | 30.28 | 0.0723 | 0.41 | 13.96 | 0
August | 15 | 7PM to 8PM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
August | 15 | 8PM to 9PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
August | 15 | 9PM to 10PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
August | 15 | 10PM to 11PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 15 | 11PM to 12AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 16 | 12AM to 1AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 16 | 1AM to 2AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 16 | 2AM to 3AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 16 | 3AM to 4AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 16 | 4AM to 5AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 16 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 16 | 6AM to 7AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 16 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 16 | 8AM to 9AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 16 | 9AM to 10AM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
August | 16 | 10AM to 11AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 16 | 11AM to 12PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
August | 16 | 12PM to 1PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
August | 16 | 1PM to 2PM | 96.8 | 68.1 | 51.8 | 57.4 | 32.29 | 0.0709 | 0.39 | 14.22 | 0
August | 16 | 2PM to 3PM | 96.8 | 66.7 | 48.2 | 50.1 | 31.14 | 0.0709 | 0.34 | 14.2 | 0
August | 16 | 3PM to 4PM | 98.6 | 66 | 44.6 | 43.7 | 30.56 | 0.0708 | 0.3 | 14.22 | 0
August | 16 | 4PM to 5PM | 96.8 | 66 | 46.4 | 46.8 | 30.61 | 0.071 | 0.32 | 14.19 | 0
August | 16 | 5PM to 6PM | 96.3 | 65.8 | 46.2 | 46.5 | 30.43 | 0.071 | 0.31 | 14.17 | 0
August | 16 | 6PM to 7PM | 93.2 | 64.9 | 46.4 | 46.8 | 29.74 | 0.0714 | 0.32 | 14.09 | 0
August | 16 | 7PM to 8PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
August | 16 | 8PM to 9PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
August | 16 | 9PM to 10PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
August | 16 | 10PM to 11PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
August | 16 | 11PM to 12AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
August | 17 | 12AM to 1AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
August | 17 | 1AM to 2AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
August | 17 | 2AM to 3AM | 66.2 | 58 | 52.5 | 59 | 25.08 | 0.075 | 0.4 | 13.44 | 0
August | 17 | 3AM to 4AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
August | 17 | 4AM to 5AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
August | 17 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 17 | 6AM to 7AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 17 | 7AM to 8AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
August | 17 | 8AM to 9AM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
August | 17 | 9AM to 10AM | 86 | 63.1 | 48.2 | 50.1 | 28.51 | 0.0724 | 0.34 | 13.92 | 0
August | 17 | 10AM to 11AM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
August | 17 | 11AM to 12PM | 93.2 | 64.9 | 46.4 | 46.8 | 29.74 | 0.0714 | 0.32 | 14.09 | 0
August | 17 | 12PM to 1PM | 96.8 | 66 | 46.4 | 46.8 | 30.61 | 0.071 | 0.32 | 14.19 | 0
August | 17 | 1PM to 2PM | 98.6 | 66.6 | 46.4 | 46.8 | 31.05 | 0.0707 | 0.32 | 14.23 | 0
August | 17 | 2PM to 3PM | 100.4 | 69.2 | 51.8 | 57.4 | 33.16 | 0.0704 | 0.39 | 14.31 | 0
August | 17 | 3PM to 4PM | 99.3 | 68 | 49.5 | 52.6 | 32.14 | 0.0706 | 0.36 | 14.27 | 0
August | 17 | 4PM to 5PM | 96.8 | 66.7 | 48.2 | 50.1 | 31.14 | 0.0709 | 0.34 | 14.2 | 0
August | 17 | 5PM to 6PM | 93.2 | 67 | 51.8 | 57.4 | 31.41 | 0.0714 | 0.39 | 14.13 | 0
August | 17 | 6PM to 7PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 17 | 7PM to 8PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 17 | 8PM to 9PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
August | 17 | 9PM to 10PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
August | 17 | 10PM to 11PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
August | 17 | 11PM to 12AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 18 | 12AM to 1AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 18 | 1AM to 2AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 18 | 2AM to 3AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 18 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 18 | 4AM to 5AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 18 | 5AM to 6AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 18 | 6AM to 7AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 18 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 18 | 8AM to 9AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 18 | 9AM to 10AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 18 | 10AM to 11AM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 18 | 11AM to 12PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
August | 18 | 12PM to 1PM | 89.6 | 70.2 | 60.8 | 79.9 | 34.08 | 0.0717 | 0.54 | 14.11 | 0
August | 18 | 1PM to 2PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
August | 18 | 2PM to 3PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
August | 18 | 3PM to 4PM | 95 | 69.1 | 55.4 | 65.6 | 33.14 | 0.0711 | 0.44 | 14.2 | 0
August | 18 | 4PM to 5PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
August | 18 | 5PM to 6PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
August | 18 | 6PM to 7PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
August | 18 | 7PM to 8PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 18 | 8PM to 9PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
August | 18 | 9PM to 10PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
August | 18 | 10PM to 11PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
August | 18 | 11PM to 12AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
August | 19 | 12AM to 1AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 19 | 1AM to 2AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 19 | 2AM to 3AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 19 | 3AM to 4AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 19 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 19 | 5AM to 6AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 19 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 19 | 7AM to 8AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
August | 19 | 8AM to 9AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 19 | 9AM to 10AM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 19 | 10AM to 11AM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
August | 19 | 11AM to 12PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 19 | 12PM to 1PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
August | 19 | 1PM to 2PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
August | 19 | 2PM to 3PM | 93.2 | 65.5 | 48.2 | 50.1 | 30.26 | 0.0714 | 0.34 | 14.1 | 0
August | 19 | 3PM to 4PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
August | 19 | 4PM to 5PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
August | 19 | 5PM to 6PM | 86 | 65.5 | 53.6 | 61.4 | 30.28 | 0.0723 | 0.41 | 13.96 | 0
August | 19 | 6PM to 7PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 19 | 7PM to 8PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 19 | 8PM to 9PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 19 | 9PM to 10PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 19 | 10PM to 11PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
August | 19 | 11PM to 12AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
August | 20 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 20 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 20 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 20 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 20 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 20 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 20 | 6AM to 7AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 20 | 7AM to 8AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 20 | 8AM to 9AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 20 | 9AM to 10AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 20 | 10AM to 11AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
August | 20 | 11AM to 12PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
August | 20 | 12PM to 1PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
August | 20 | 1PM to 2PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
August | 20 | 2PM to 3PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
August | 20 | 3PM to 4PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 20 | 4PM to 5PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
August | 20 | 5PM to 6PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
August | 20 | 6PM to 7PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 20 | 7PM to 8PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 20 | 8PM to 9PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 20 | 9PM to 10PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 20 | 10PM to 11PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
August | 20 | 11PM to 12AM | 58.5 | 54.9 | 52.3 | 58.6 | 23.13 | 0.0761 | 0.4 | 13.24 | 0
August | 21 | 12AM to 1AM | 57.7 | 55 | 53.1 | 60.2 | 23.2 | 0.0762 | 0.41 | 13.23 | 0
August | 21 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 21 | 2AM to 3AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 21 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 21 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
August | 21 | 5AM to 6AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
August | 21 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 21 | 7AM to 8AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 21 | 8AM to 9AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 21 | 9AM to 10AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 21 | 10AM to 11AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 21 | 11AM to 12PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 21 | 12PM to 1PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 21 | 1PM to 2PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 21 | 2PM to 3PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
August | 21 | 3PM to 4PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
August | 21 | 4PM to 5PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
August | 21 | 5PM to 6PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 21 | 6PM to 7PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 21 | 7PM to 8PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
August | 21 | 8PM to 9PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 21 | 9PM to 10PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 21 | 10PM to 11PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 21 | 11PM to 12AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 22 | 12AM to 1AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 22 | 1AM to 2AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 22 | 2AM to 3AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 22 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 22 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 22 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 22 | 6AM to 7AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
August | 22 | 7AM to 8AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
August | 22 | 8AM to 9AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
August | 22 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 22 | 10AM to 11AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 22 | 11AM to 12PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 22 | 12PM to 1PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
August | 22 | 1PM to 2PM | 84.2 | 67.6 | 59 | 74.9 | 31.96 | 0.0724 | 0.5 | 13.95 | 0
August | 22 | 2PM to 3PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
August | 22 | 3PM to 4PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
August | 22 | 4PM to 5PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
August | 22 | 5PM to 6PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 22 | 6PM to 7PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 22 | 7PM to 8PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 22 | 8PM to 9PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 22 | 9PM to 10PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 22 | 10PM to 11PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 22 | 11PM to 12AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 23 | 12AM to 1AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 23 | 1AM to 2AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 23 | 2AM to 3AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 23 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 23 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 23 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 23 | 6AM to 7AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
August | 23 | 7AM to 8AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
August | 23 | 8AM to 9AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
August | 23 | 9AM to 10AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
August | 23 | 10AM to 11AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 23 | 11AM to 12PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 23 | 12PM to 1PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 23 | 1PM to 2PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
August | 23 | 2PM to 3PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
August | 23 | 3PM to 4PM | 84.2 | 67.6 | 59 | 74.9 | 31.96 | 0.0724 | 0.5 | 13.95 | 0
August | 23 | 4PM to 5PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
August | 23 | 5PM to 6PM | 82.4 | 69 | 62.6 | 85.3 | 33.15 | 0.0726 | 0.57 | 13.94 | 0
August | 23 | 6PM to 7PM | 78.8 | 68.3 | 63.3 | 87.5 | 32.62 | 0.0731 | 0.59 | 13.85 | 0
August | 23 | 7PM to 8PM | 75.2 | 66.8 | 62.6 | 85.3 | 31.39 | 0.0736 | 0.57 | 13.75 | 0
August | 23 | 8PM to 9PM | 73.4 | 66.2 | 62.6 | 85.3 | 30.94 | 0.0738 | 0.57 | 13.71 | 0
August | 23 | 9PM to 10PM | 69.8 | 65 | 62.6 | 85.3 | 30.06 | 0.0743 | 0.57 | 13.61 | 0
August | 23 | 10PM to 11PM | 68 | 63.3 | 60.8 | 79.9 | 28.78 | 0.0746 | 0.54 | 13.55 | 0
August | 23 | 11PM to 12AM | 68 | 63.3 | 60.8 | 79.9 | 28.78 | 0.0746 | 0.54 | 13.55 | 0
August | 24 | 12AM to 1AM | 66.2 | 62.7 | 60.8 | 79.9 | 28.34 | 0.0749 | 0.54 | 13.51 | 0
August | 24 | 1AM to 2AM | 64.4 | 62.1 | 60.8 | 79.9 | 27.9 | 0.0751 | 0.54 | 13.46 | 0
August | 24 | 2AM to 3AM | 64.4 | 62.1 | 60.8 | 79.9 | 27.9 | 0.0751 | 0.54 | 13.46 | 0
August | 24 | 3AM to 4AM | 62.6 | 60.3 | 59 | 74.9 | 26.67 | 0.0754 | 0.5 | 13.4 | 0
August | 24 | 4AM to 5AM | 62.6 | 60.3 | 59 | 74.9 | 26.67 | 0.0754 | 0.5 | 13.4 | 0
August | 24 | 5AM to 6AM | 62.6 | 60.3 | 59 | 74.9 | 26.67 | 0.0754 | 0.5 | 13.4 | 0
August | 24 | 6AM to 7AM | 64.4 | 62.1 | 60.8 | 79.9 | 27.9 | 0.0751 | 0.54 | 13.46 | 0
August | 24 | 7AM to 8AM | 68 | 63.3 | 60.8 | 79.9 | 28.78 | 0.0746 | 0.54 | 13.55 | 0
August | 24 | 8AM to 9AM | 73.4 | 65.1 | 60.8 | 79.9 | 30.11 | 0.0739 | 0.54 | 13.69 | 0
August | 24 | 9AM to 10AM | 77 | 66.3 | 60.8 | 79.9 | 30.99 | 0.0734 | 0.54 | 13.78 | 0
August | 24 | 10AM to 11AM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
August | 24 | 11AM to 12PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
August | 24 | 12PM to 1PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
August | 24 | 1PM to 2PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 24 | 2PM to 3PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
August | 24 | 3PM to 4PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
August | 24 | 4PM to 5PM | 91.4 | 65.7 | 50 | 53.7 | 30.38 | 0.0716 | 0.36 | 14.07 | 0
August | 24 | 5PM to 6PM | 87.8 | 65.3 | 51.8 | 57.4 | 30.09 | 0.0721 | 0.39 | 13.99 | 0
August | 24 | 6PM to 7PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
August | 24 | 7PM to 8PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 24 | 8PM to 9PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 24 | 9PM to 10PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
August | 24 | 10PM to 11PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 24 | 11PM to 12AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 25 | 12AM to 1AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 25 | 1AM to 2AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 25 | 2AM to 3AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 25 | 3AM to 4AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 25 | 4AM to 5AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
August | 25 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 25 | 6AM to 7AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 25 | 7AM to 8AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 25 | 8AM to 9AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 25 | 9AM to 10AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 25 | 10AM to 11AM | 84.6 | 66.9 | 57.4 | 70.6 | 31.37 | 0.0724 | 0.48 | 13.95 | 0
August | 25 | 11AM to 12PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
August | 25 | 12PM to 1PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
August | 25 | 1PM to 2PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
August | 25 | 2PM to 3PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
August | 25 | 3PM to 4PM | 95 | 68.3 | 53.6 | 61.4 | 32.48 | 0.0711 | 0.41 | 14.19 | 0
August | 25 | 4PM to 5PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
August | 25 | 5PM to 6PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
August | 25 | 6PM to 7PM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
August | 25 | 7PM to 8PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 25 | 8PM to 9PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 25 | 9PM to 10PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
August | 25 | 10PM to 11PM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
August | 25 | 11PM to 12AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
August | 26 | 12AM to 1AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 26 | 1AM to 2AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 26 | 2AM to 3AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 26 | 3AM to 4AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
August | 26 | 4AM to 5AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
August | 26 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
August | 26 | 6AM to 7AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
August | 26 | 7AM to 8AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
August | 26 | 8AM to 9AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 26 | 9AM to 10AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 26 | 10AM to 11AM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
August | 26 | 11AM to 12PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
August | 26 | 12PM to 1PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
August | 26 | 1PM to 2PM | 96.8 | 70.5 | 57.2 | 70.1 | 34.29 | 0.0708 | 0.47 | 14.26 | 0
August | 26 | 2PM to 3PM | 96.8 | 70.5 | 57.2 | 70.1 | 34.29 | 0.0708 | 0.47 | 14.26 | 0
August | 26 | 3PM to 4PM | 98.6 | 67.3 | 48.2 | 50.1 | 31.58 | 0.0707 | 0.34 | 14.24 | 0
August | 26 | 4PM to 5PM | 98.6 | 68.7 | 51.8 | 57.4 | 32.73 | 0.0707 | 0.39 | 14.27 | 0
August | 26 | 5PM to 6PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
August | 26 | 6PM to 7PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
August | 26 | 7PM to 8PM | 82.4 | 66.1 | 57.2 | 70.1 | 30.77 | 0.0727 | 0.47 | 13.89 | 0
August | 26 | 8PM to 9PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 26 | 9PM to 10PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 26 | 10PM to 11PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 26 | 11PM to 12AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 27 | 12AM to 1AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
August | 27 | 1AM to 2AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 27 | 2AM to 3AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 27 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 27 | 4AM to 5AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
August | 27 | 5AM to 6AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 27 | 6AM to 7AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 27 | 7AM to 8AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 27 | 8AM to 9AM | 79.5 | 65 | 57 | 69.7 | 30 | 0.0731 | 0.47 | 13.82 | 0
August | 27 | 9AM to 10AM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
August | 27 | 10AM to 11AM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
August | 27 | 11AM to 12PM | 95 | 69.1 | 55.4 | 65.6 | 33.14 | 0.0711 | 0.44 | 14.2 | 0
August | 27 | 12PM to 1PM | 98.6 | 71 | 57.2 | 70.1 | 34.73 | 0.0706 | 0.47 | 14.31 | 0
August | 27 | 1PM to 2PM | 100.4 | 70.7 | 55.4 | 65.6 | 34.46 | 0.0704 | 0.44 | 14.34 | 0
August | 27 | 2PM to 3PM | 102.2 | 70.5 | 53.6 | 61.4 | 34.23 | 0.0702 | 0.41 | 14.37 | 0
August | 27 | 3PM to 4PM | 102.2 | 70.5 | 53.6 | 61.4 | 34.23 | 0.0702 | 0.41 | 14.37 | 0
August | 27 | 4PM to 5PM | 100.4 | 71.5 | 57.2 | 70.1 | 35.17 | 0.0704 | 0.47 | 14.35 | 0
August | 27 | 5PM to 6PM | 96.8 | 72.3 | 60.8 | 79.9 | 35.84 | 0.0708 | 0.54 | 14.29 | 0
August | 27 | 6PM to 7PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
August | 27 | 7PM to 8PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
August | 27 | 8PM to 9PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
August | 27 | 9PM to 10PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 27 | 10PM to 11PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 27 | 11PM to 12AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 28 | 12AM to 1AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
August | 28 | 1AM to 2AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 28 | 2AM to 3AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 28 | 3AM to 4AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 28 | 4AM to 5AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
August | 28 | 5AM to 6AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 28 | 6AM to 7AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 28 | 7AM to 8AM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 28 | 8AM to 9AM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
August | 28 | 9AM to 10AM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
August | 28 | 10AM to 11AM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
August | 28 | 11AM to 12PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
August | 28 | 12PM to 1PM | 98.6 | 69.4 | 53.6 | 61.4 | 33.36 | 0.0707 | 0.41 | 14.28 | 0
August | 28 | 1PM to 2PM | 98.6 | 70.2 | 55.4 | 65.6 | 34.02 | 0.0706 | 0.44 | 14.29 | 0
August | 28 | 2PM to 3PM | 100.4 | 70.7 | 55.4 | 65.6 | 34.46 | 0.0704 | 0.44 | 14.34 | 0
August | 28 | 3PM to 4PM | 102.2 | 71.3 | 55.4 | 65.6 | 34.9 | 0.0702 | 0.44 | 14.38 | 0
August | 28 | 4PM to 5PM | 100.4 | 70 | 53.6 | 61.4 | 33.79 | 0.0704 | 0.41 | 14.32 | 0
August | 28 | 5PM to 6PM | 93.2 | 70.3 | 59 | 74.9 | 34.16 | 0.0713 | 0.5 | 14.18 | 0
August | 28 | 6PM to 7PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
August | 28 | 7PM to 8PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 28 | 8PM to 9PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
August | 28 | 9PM to 10PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 28 | 10PM to 11PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
August | 28 | 11PM to 12AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
August | 29 | 12AM to 1AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
August | 29 | 1AM to 2AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 29 | 2AM to 3AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 29 | 3AM to 4AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 29 | 4AM to 5AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 29 | 5AM to 6AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 29 | 6AM to 7AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
August | 29 | 7AM to 8AM | 68 | 60.8 | 56.5 | 68.3 | 26.97 | 0.0747 | 0.46 | 13.52 | 0
August | 29 | 8AM to 9AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
August | 29 | 9AM to 10AM | 75.2 | 64.7 | 59 | 74.9 | 29.76 | 0.0737 | 0.5 | 13.72 | 0
August | 29 | 10AM to 11AM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
August | 29 | 11AM to 12PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
August | 29 | 12PM to 1PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
August | 29 | 1PM to 2PM | 93.2 | 70.3 | 59 | 74.9 | 34.16 | 0.0713 | 0.5 | 14.18 | 0
August | 29 | 2PM to 3PM | 91.4 | 68.9 | 57.2 | 70.1 | 32.97 | 0.0715 | 0.47 | 14.12 | 0
August | 29 | 3PM to 4PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
August | 29 | 4PM to 5PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
August | 29 | 5PM to 6PM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
August | 29 | 6PM to 7PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
August | 29 | 7PM to 8PM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 29 | 8PM to 9PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 29 | 9PM to 10PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 29 | 10PM to 11PM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 29 | 11PM to 12AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 30 | 12AM to 1AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 30 | 1AM to 2AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 30 | 2AM to 3AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 30 | 3AM to 4AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 30 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 30 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 30 | 6AM to 7AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
August | 30 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 30 | 8AM to 9AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 30 | 9AM to 10AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
August | 30 | 10AM to 11AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
August | 30 | 11AM to 12PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 30 | 12PM to 1PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
August | 30 | 1PM to 2PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
August | 30 | 2PM to 3PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
August | 30 | 3PM to 4PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
August | 30 | 4PM to 5PM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
August | 30 | 5PM to 6PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 30 | 6PM to 7PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
August | 30 | 7PM to 8PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 30 | 8PM to 9PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 30 | 9PM to 10PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 30 | 10PM to 11PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 30 | 11PM to 12AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 31 | 12AM to 1AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
August | 31 | 1AM to 2AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
August | 31 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 31 | 3AM to 4AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
August | 31 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 31 | 5AM to 6AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
August | 31 | 6AM to 7AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
August | 31 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
August | 31 | 8AM to 9AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
August | 31 | 9AM to 10AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
August | 31 | 10AM to 11AM | 77 | 65.3 | 59 | 74.9 | 30.2 | 0.0734 | 0.5 | 13.77 | 0
August | 31 | 11AM to 12PM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
August | 31 | 12PM to 1PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
August | 31 | 1PM to 2PM | 86 | 69.1 | 60.8 | 79.9 | 33.19 | 0.0722 | 0.54 | 14.01 | 0
August | 31 | 2PM to 3PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
August | 31 | 3PM to 4PM | 87.8 | 68.7 | 59 | 74.9 | 32.84 | 0.072 | 0.5 | 14.04 | 0
August | 31 | 4PM to 5PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
August | 31 | 5PM to 6PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
August | 31 | 6PM to 7PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
August | 31 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
August | 31 | 8PM to 9PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
August | 31 | 9PM to 10PM | 68.2 | 61.2 | 57 | 69.7 | 27.22 | 0.0747 | 0.47 | 13.53 | 0
August | 31 | 10PM to 11PM | 66.7 | 60.4 | 56.7 | 68.8 | 26.73 | 0.0749 | 0.46 | 13.49 | 0
August | 31 | 11PM to 12AM | 65.1 | 59.8 | 56.5 | 68.3 | 26.26 | 0.0751 | 0.46 | 13.44 | 0
September | 1 | 12AM to 1AM | 63.7 | 59 | 56.1 | 67.4 | 25.77 | 0.0753 | 0.45 | 13.4 | 0
September | 1 | 1AM to 2AM | 62.1 | 58.3 | 55.9 | 67 | 25.31 | 0.0756 | 0.45 | 13.36 | 0
September | 1 | 2AM to 3AM | 60.6 | 57.5 | 55.6 | 66.1 | 24.82 | 0.0758 | 0.45 | 13.32 | 0
September | 1 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
September | 1 | 4AM to 5AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 1 | 5AM to 6AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 1 | 6AM to 7AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 1 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 1 | 8AM to 9AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 1 | 9AM to 10AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
September | 1 | 10AM to 11AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 1 | 11AM to 12PM | 59 | 57.9 | 57.2 | 70.1 | 25.05 | 0.076 | 0.47 | 13.29 | 0
September | 1 | 12PM to 1PM | 59 | 57.9 | 57.2 | 70.1 | 25.05 | 0.076 | 0.47 | 13.29 | 0
September | 1 | 1PM to 2PM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
September | 1 | 2PM to 3PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 1 | 3PM to 4PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 1 | 4PM to 5PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 1 | 5PM to 6PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 1 | 6PM to 7PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 1 | 7PM to 8PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 1 | 8PM to 9PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 1 | 9PM to 10PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 1 | 10PM to 11PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 1 | 11PM to 12AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 2 | 12AM to 1AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
September | 2 | 1AM to 2AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
September | 2 | 2AM to 3AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
September | 2 | 3AM to 4AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
September | 2 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
September | 2 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
September | 2 | 6AM to 7AM | 57.2 | 57.2 | 57.2 | 70.1 | 24.61 | 0.0763 | 0.47 | 13.25 | 0
September | 2 | 7AM to 8AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 2 | 8AM to 9AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 2 | 9AM to 10AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 2 | 10AM to 11AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
September | 2 | 11AM to 12PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
September | 2 | 12PM to 1PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
September | 2 | 1PM to 2PM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
September | 2 | 2PM to 3PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
September | 2 | 3PM to 4PM | 73.4 | 57.1 | 44.6 | 43.7 | 24.44 | 0.0741 | 0.3 | 13.58 | 0
September | 2 | 4PM to 5PM | 71.6 | 56.4 | 44.6 | 43.7 | 24 | 0.0744 | 0.3 | 13.53 | 0
September | 2 | 5PM to 6PM | 69.8 | 55.7 | 44.6 | 43.7 | 23.57 | 0.0746 | 0.3 | 13.49 | 0
September | 2 | 6PM to 7PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
September | 2 | 7PM to 8PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
September | 2 | 8PM to 9PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
September | 2 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 2 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 2 | 11PM to 12AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 3 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 3 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 3 | 2AM to 3AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 3 | 3AM to 4AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 3 | 4AM to 5AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 3 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 3 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 3 | 7AM to 8AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
September | 3 | 8AM to 9AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
September | 3 | 9AM to 10AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
September | 3 | 10AM to 11AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
September | 3 | 11AM to 12PM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
September | 3 | 12PM to 1PM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
September | 3 | 1PM to 2PM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
September | 3 | 2PM to 3PM | 75.2 | 57.8 | 44.6 | 43.7 | 24.88 | 0.0739 | 0.3 | 13.63 | 0
September | 3 | 3PM to 4PM | 75.2 | 57.1 | 42.8 | 40.8 | 24.42 | 0.0739 | 0.28 | 13.62 | 0
September | 3 | 4PM to 5PM | 75.2 | 57.1 | 42.8 | 40.8 | 24.42 | 0.0739 | 0.28 | 13.62 | 0
September | 3 | 5PM to 6PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
September | 3 | 6PM to 7PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
September | 3 | 7PM to 8PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
September | 3 | 8PM to 9PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
September | 3 | 9PM to 10PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
September | 3 | 10PM to 11PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
September | 3 | 11PM to 12AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
September | 4 | 12AM to 1AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
September | 4 | 1AM to 2AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 4 | 2AM to 3AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 4 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
September | 4 | 4AM to 5AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
September | 4 | 5AM to 6AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
September | 4 | 6AM to 7AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
September | 4 | 7AM to 8AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
September | 4 | 8AM to 9AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
September | 4 | 9AM to 10AM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
September | 4 | 10AM to 11AM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
September | 4 | 11AM to 12PM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
September | 4 | 12PM to 1PM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
September | 4 | 1PM to 2PM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
September | 4 | 2PM to 3PM | 75.2 | 57.1 | 42.8 | 40.8 | 24.42 | 0.0739 | 0.28 | 13.62 | 0
September | 4 | 3PM to 4PM | 75.2 | 57.1 | 42.8 | 40.8 | 24.42 | 0.0739 | 0.28 | 13.62 | 0
September | 4 | 4PM to 5PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
September | 4 | 5PM to 6PM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
September | 4 | 6PM to 7PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
September | 4 | 7PM to 8PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
September | 4 | 8PM to 9PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
September | 4 | 9PM to 10PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
September | 4 | 10PM to 11PM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
September | 4 | 11PM to 12AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
September | 5 | 12AM to 1AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 5 | 1AM to 2AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
September | 5 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
September | 5 | 3AM to 4AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
September | 5 | 4AM to 5AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
September | 5 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 5 | 6AM to 7AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
September | 5 | 7AM to 8AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
September | 5 | 8AM to 9AM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
September | 5 | 9AM to 10AM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
September | 5 | 10AM to 11AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
September | 5 | 11AM to 12PM | 75.2 | 57.1 | 42.8 | 40.8 | 24.42 | 0.0739 | 0.28 | 13.62 | 0
September | 5 | 12PM to 1PM | 77 | 58.5 | 44.6 | 43.7 | 25.32 | 0.0736 | 0.3 | 13.67 | 0
September | 5 | 1PM to 2PM | 78.8 | 57.8 | 41 | 38 | 24.86 | 0.0734 | 0.26 | 13.7 | 0
September | 5 | 2PM to 3PM | 80.6 | 57.8 | 39.2 | 35.4 | 24.89 | 0.0732 | 0.24 | 13.74 | 0
September | 5 | 3PM to 4PM | 80.6 | 58.5 | 41 | 38 | 25.3 | 0.0731 | 0.26 | 13.74 | 0
September | 5 | 4PM to 5PM | 80.6 | 57.8 | 39.2 | 35.4 | 24.89 | 0.0732 | 0.24 | 13.74 | 0
September | 5 | 5PM to 6PM | 75.2 | 57.8 | 44.6 | 43.7 | 24.88 | 0.0739 | 0.3 | 13.63 | 0
September | 5 | 6PM to 7PM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
September | 5 | 7PM to 8PM | 66.7 | 55.7 | 47.5 | 48.8 | 23.62 | 0.075 | 0.33 | 13.43 | 0
September | 5 | 8PM to 9PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
September | 5 | 9PM to 10PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
September | 5 | 10PM to 11PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
September | 5 | 11PM to 12AM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
September | 6 | 12AM to 1AM | 59 | 51.2 | 44.6 | 43.7 | 20.95 | 0.0762 | 0.3 | 13.21 | 0
September | 6 | 1AM to 2AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
September | 6 | 2AM to 3AM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
September | 6 | 3AM to 4AM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
September | 6 | 4AM to 5AM | 59 | 51.2 | 44.6 | 43.7 | 20.95 | 0.0762 | 0.3 | 13.21 | 0
September | 6 | 5AM to 6AM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
September | 6 | 6AM to 7AM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
September | 6 | 7AM to 8AM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
September | 6 | 8AM to 9AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
September | 6 | 9AM to 10AM | 77 | 58.5 | 44.6 | 43.7 | 25.32 | 0.0736 | 0.3 | 13.67 | 0
September | 6 | 10AM to 11AM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
September | 6 | 11AM to 12PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
September | 6 | 12PM to 1PM | 84.2 | 60.4 | 42.8 | 40.8 | 26.6 | 0.0726 | 0.28 | 13.85 | 0
September | 6 | 1PM to 2PM | 87.8 | 60.5 | 39.2 | 35.4 | 26.64 | 0.0722 | 0.24 | 13.92 | 0
September | 6 | 2PM to 3PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
September | 6 | 3PM to 4PM | 87.8 | 61.1 | 41 | 38 | 27.04 | 0.0722 | 0.26 | 13.93 | 0
September | 6 | 4PM to 5PM | 87.8 | 61.1 | 41 | 38 | 27.04 | 0.0722 | 0.26 | 13.93 | 0
September | 6 | 5PM to 6PM | 84.2 | 61.1 | 44.6 | 43.7 | 27.06 | 0.0726 | 0.3 | 13.85 | 0
September | 6 | 6PM to 7PM | 75.2 | 60.1 | 50 | 53.7 | 26.44 | 0.0738 | 0.36 | 13.66 | 0
September | 6 | 7PM to 8PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
September | 6 | 8PM to 9PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
September | 6 | 9PM to 10PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
September | 6 | 10PM to 11PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
September | 6 | 11PM to 12AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
September | 7 | 12AM to 1AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
September | 7 | 1AM to 2AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
September | 7 | 2AM to 3AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
September | 7 | 3AM to 4AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 7 | 4AM to 5AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 7 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 7 | 6AM to 7AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 7 | 7AM to 8AM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
September | 7 | 8AM to 9AM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
September | 7 | 9AM to 10AM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
September | 7 | 10AM to 11AM | 82.4 | 61.9 | 48.2 | 50.1 | 27.64 | 0.0728 | 0.34 | 13.83 | 0
September | 7 | 11AM to 12PM | 86 | 62.4 | 46.4 | 46.8 | 27.99 | 0.0724 | 0.32 | 13.91 | 0
September | 7 | 12PM to 1PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
September | 7 | 1PM to 2PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
September | 7 | 2PM to 3PM | 89.6 | 63.6 | 46.4 | 46.8 | 28.87 | 0.0719 | 0.32 | 14 | 0
September | 7 | 3PM to 4PM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
September | 7 | 4PM to 5PM | 89.6 | 61.7 | 41 | 38 | 27.48 | 0.072 | 0.26 | 13.97 | 0
September | 7 | 5PM to 6PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
September | 7 | 6PM to 7PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 7 | 7PM to 8PM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
September | 7 | 8PM to 9PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
September | 7 | 9PM to 10PM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
September | 7 | 10PM to 11PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
September | 7 | 11PM to 12AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
September | 8 | 12AM to 1AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
September | 8 | 1AM to 2AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
September | 8 | 2AM to 3AM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
September | 8 | 3AM to 4AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
September | 8 | 4AM to 5AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
September | 8 | 5AM to 6AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
September | 8 | 6AM to 7AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
September | 8 | 7AM to 8AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
September | 8 | 8AM to 9AM | 68 | 56.6 | 48.2 | 50.1 | 24.14 | 0.0748 | 0.34 | 13.46 | 0
September | 8 | 9AM to 10AM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
September | 8 | 10AM to 11AM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
September | 8 | 11AM to 12PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
September | 8 | 12PM to 1PM | 87.8 | 63.7 | 48.2 | 50.1 | 28.95 | 0.0721 | 0.34 | 13.97 | 0
September | 8 | 1PM to 2PM | 89.6 | 65.1 | 50 | 53.7 | 29.94 | 0.0719 | 0.36 | 14.02 | 0
September | 8 | 2PM to 3PM | 91.4 | 61.8 | 39.2 | 35.4 | 27.51 | 0.0717 | 0.24 | 14.01 | 0
September | 8 | 3PM to 4PM | 91.4 | 61.8 | 39.2 | 35.4 | 27.51 | 0.0717 | 0.24 | 14.01 | 0
September | 8 | 4PM to 5PM | 87.8 | 61.7 | 42.8 | 40.8 | 27.48 | 0.0722 | 0.28 | 13.94 | 0
September | 8 | 5PM to 6PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
September | 8 | 6PM to 7PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 8 | 7PM to 8PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
September | 8 | 8PM to 9PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 8 | 9PM to 10PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
September | 8 | 10PM to 11PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
September | 8 | 11PM to 12AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
September | 9 | 12AM to 1AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
September | 9 | 1AM to 2AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 9 | 2AM to 3AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
September | 9 | 3AM to 4AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
September | 9 | 4AM to 5AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 9 | 5AM to 6AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
September | 9 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 9 | 7AM to 8AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 9 | 8AM to 9AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
September | 9 | 9AM to 10AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
September | 9 | 10AM to 11AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 9 | 11AM to 12PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
September | 9 | 12PM to 1PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
September | 9 | 1PM to 2PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
September | 9 | 2PM to 3PM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
September | 9 | 3PM to 4PM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
September | 9 | 4PM to 5PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
September | 9 | 5PM to 6PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
September | 9 | 6PM to 7PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
September | 9 | 7PM to 8PM | 69.8 | 55.7 | 44.6 | 43.7 | 23.57 | 0.0746 | 0.3 | 13.49 | 0
September | 9 | 8PM to 9PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
September | 9 | 9PM to 10PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
September | 9 | 10PM to 11PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 9 | 11PM to 12AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 10 | 12AM to 1AM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
September | 10 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 10 | 2AM to 3AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
September | 10 | 3AM to 4AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
September | 10 | 4AM to 5AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
September | 10 | 5AM to 6AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
September | 10 | 6AM to 7AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
September | 10 | 7AM to 8AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 10 | 8AM to 9AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
September | 10 | 9AM to 10AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
September | 10 | 10AM to 11AM | 77 | 61.6 | 51.8 | 57.4 | 27.46 | 0.0735 | 0.39 | 13.71 | 0
September | 10 | 11AM to 12PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
September | 10 | 12PM to 1PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
September | 10 | 1PM to 2PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
September | 10 | 2PM to 3PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
September | 10 | 3PM to 4PM | 89.6 | 62.3 | 42.8 | 40.8 | 27.91 | 0.0719 | 0.28 | 13.98 | 0
September | 10 | 4PM to 5PM | 87.8 | 59.4 | 35.6 | 30.7 | 25.89 | 0.0722 | 0.21 | 13.9 | 0
September | 10 | 5PM to 6PM | 84.2 | 61.8 | 46.4 | 46.8 | 27.55 | 0.0726 | 0.32 | 13.86 | 0
September | 10 | 6PM to 7PM | 75.2 | 60.1 | 50 | 53.7 | 26.44 | 0.0738 | 0.36 | 13.66 | 0
September | 10 | 7PM to 8PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
September | 10 | 8PM to 9PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 10 | 9PM to 10PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
September | 10 | 10PM to 11PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
September | 10 | 11PM to 12AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
September | 11 | 12AM to 1AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 11 | 1AM to 2AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 11 | 2AM to 3AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
September | 11 | 3AM to 4AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
September | 11 | 4AM to 5AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
September | 11 | 5AM to 6AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
September | 11 | 6AM to 7AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
September | 11 | 7AM to 8AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
September | 11 | 8AM to 9AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
September | 11 | 9AM to 10AM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
September | 11 | 10AM to 11AM | 84.2 | 63.3 | 50 | 53.7 | 28.63 | 0.0726 | 0.36 | 13.89 | 0
September | 11 | 11AM to 12PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
September | 11 | 12PM to 1PM | 87.8 | 64.5 | 50 | 53.7 | 29.51 | 0.0721 | 0.36 | 13.98 | 0
September | 11 | 1PM to 2PM | 91.4 | 65.7 | 50 | 53.7 | 30.38 | 0.0716 | 0.36 | 14.07 | 0
September | 11 | 2PM to 3PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
September | 11 | 3PM to 4PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
September | 11 | 4PM to 5PM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
September | 11 | 5PM to 6PM | 87.8 | 63 | 46.4 | 46.8 | 28.43 | 0.0721 | 0.32 | 13.96 | 0
September | 11 | 6PM to 7PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
September | 11 | 7PM to 8PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
September | 11 | 8PM to 9PM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
September | 11 | 9PM to 10PM | 68 | 56.6 | 48.2 | 50.1 | 24.14 | 0.0748 | 0.34 | 13.46 | 0
September | 11 | 10PM to 11PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
September | 11 | 11PM to 12AM | 68 | 55 | 44.6 | 43.7 | 23.13 | 0.0749 | 0.3 | 13.44 | 0
September | 12 | 12AM to 1AM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
September | 12 | 1AM to 2AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
September | 12 | 2AM to 3AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
September | 12 | 3AM to 4AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
September | 12 | 4AM to 5AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
September | 12 | 5AM to 6AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
September | 12 | 6AM to 7AM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
September | 12 | 7AM to 8AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 12 | 8AM to 9AM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
September | 12 | 9AM to 10AM | 82.4 | 62.7 | 50 | 53.7 | 28.19 | 0.0728 | 0.36 | 13.84 | 0
September | 12 | 10AM to 11AM | 86 | 63.9 | 50 | 53.7 | 29.07 | 0.0723 | 0.36 | 13.93 | 0
September | 12 | 11AM to 12PM | 89.6 | 65.1 | 50 | 53.7 | 29.94 | 0.0719 | 0.36 | 14.02 | 0
September | 12 | 12PM to 1PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
September | 12 | 1PM to 2PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
September | 12 | 2PM to 3PM | 91.4 | 66.4 | 51.8 | 57.4 | 30.97 | 0.0716 | 0.39 | 14.08 | 0
September | 12 | 3PM to 4PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
September | 12 | 4PM to 5PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
September | 12 | 5PM to 6PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
September | 12 | 6PM to 7PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
September | 12 | 7PM to 8PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
September | 12 | 8PM to 9PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 12 | 9PM to 10PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
September | 12 | 10PM to 11PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
September | 12 | 11PM to 12AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
September | 13 | 12AM to 1AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
September | 13 | 1AM to 2AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
September | 13 | 2AM to 3AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
September | 13 | 3AM to 4AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
September | 13 | 4AM to 5AM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
September | 13 | 5AM to 6AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
September | 13 | 6AM to 7AM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
September | 13 | 7AM to 8AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
September | 13 | 8AM to 9AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
September | 13 | 9AM to 10AM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
September | 13 | 10AM to 11AM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
September | 13 | 11AM to 12PM | 82.4 | 61.9 | 48.2 | 50.1 | 27.64 | 0.0728 | 0.34 | 13.83 | 0
September | 13 | 12PM to 1PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
September | 13 | 1PM to 2PM | 87.8 | 62.4 | 44.6 | 43.7 | 27.94 | 0.0722 | 0.3 | 13.95 | 0
September | 13 | 2PM to 3PM | 91.4 | 62.4 | 41 | 38 | 27.92 | 0.0717 | 0.26 | 14.02 | 0
September | 13 | 3PM to 4PM | 93.2 | 64.9 | 46.4 | 46.8 | 29.74 | 0.0714 | 0.32 | 14.09 | 0
September | 13 | 4PM to 5PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
September | 13 | 5PM to 6PM | 80.6 | 68.5 | 62.6 | 85.3 | 32.71 | 0.0729 | 0.57 | 13.89 | 0
September | 13 | 6PM to 7PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
September | 13 | 7PM to 8PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
September | 13 | 8PM to 9PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
September | 13 | 9PM to 10PM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
September | 13 | 10PM to 11PM | 77 | 60 | 48.2 | 50.1 | 26.32 | 0.0736 | 0.34 | 13.69 | 0
September | 13 | 11PM to 12AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 14 | 12AM to 1AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
September | 14 | 1AM to 2AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
September | 14 | 2AM to 3AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
September | 14 | 3AM to 4AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
September | 14 | 4AM to 5AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
September | 14 | 5AM to 6AM | 68 | 63.3 | 60.8 | 79.9 | 28.78 | 0.0746 | 0.54 | 13.55 | 0
September | 14 | 6AM to 7AM | 69.8 | 63.9 | 60.8 | 79.9 | 29.22 | 0.0744 | 0.54 | 13.6 | 0
September | 14 | 7AM to 8AM | 71.6 | 64.5 | 60.8 | 79.9 | 29.67 | 0.0741 | 0.54 | 13.64 | 0
September | 14 | 8AM to 9AM | 73.4 | 65.1 | 60.8 | 79.9 | 30.11 | 0.0739 | 0.54 | 13.69 | 0
September | 14 | 9AM to 10AM | 77 | 66.3 | 60.8 | 79.9 | 30.99 | 0.0734 | 0.54 | 13.78 | 0
September | 14 | 10AM to 11AM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
September | 14 | 11AM to 12PM | 80.6 | 66.4 | 59 | 74.9 | 31.08 | 0.0729 | 0.5 | 13.86 | 0
September | 14 | 12PM to 1PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
September | 14 | 1PM to 2PM | 86 | 69.1 | 60.8 | 79.9 | 33.19 | 0.0722 | 0.54 | 14.01 | 0
September | 14 | 2PM to 3PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
September | 14 | 3PM to 4PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
September | 14 | 4PM to 5PM | 82.4 | 68 | 60.8 | 79.9 | 32.31 | 0.0726 | 0.54 | 13.92 | 0
September | 14 | 5PM to 6PM | 78.8 | 66.9 | 60.8 | 79.9 | 31.43 | 0.0731 | 0.54 | 13.83 | 0
September | 14 | 6PM to 7PM | 75.2 | 65.7 | 60.8 | 79.9 | 30.55 | 0.0736 | 0.54 | 13.74 | 0
September | 14 | 7PM to 8PM | 71.6 | 63.5 | 59 | 74.9 | 28.88 | 0.0742 | 0.5 | 13.63 | 0
September | 14 | 8PM to 9PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
September | 14 | 9PM to 10PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
September | 14 | 10PM to 11PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
September | 14 | 11PM to 12AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
September | 15 | 12AM to 1AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 15 | 1AM to 2AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 15 | 2AM to 3AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 15 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
September | 15 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
September | 15 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
September | 15 | 6AM to 7AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 15 | 7AM to 8AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 15 | 8AM to 9AM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
September | 15 | 9AM to 10AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
September | 15 | 10AM to 11AM | 77 | 64.3 | 57.2 | 70.1 | 29.45 | 0.0734 | 0.47 | 13.75 | 0
September | 15 | 11AM to 12PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
September | 15 | 12PM to 1PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
September | 15 | 1PM to 2PM | 84.2 | 63.3 | 50 | 53.7 | 28.63 | 0.0726 | 0.36 | 13.89 | 0
September | 15 | 2PM to 3PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
September | 15 | 3PM to 4PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
September | 15 | 4PM to 5PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
September | 15 | 5PM to 6PM | 78.8 | 64.9 | 57.2 | 70.1 | 29.89 | 0.0732 | 0.47 | 13.8 | 0
September | 15 | 6PM to 7PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
September | 15 | 7PM to 8PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
September | 15 | 8PM to 9PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
September | 15 | 9PM to 10PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
September | 15 | 10PM to 11PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 15 | 11PM to 12AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 16 | 12AM to 1AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 16 | 1AM to 2AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 16 | 2AM to 3AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 16 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
September | 16 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
September | 16 | 5AM to 6AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
September | 16 | 6AM to 7AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
September | 16 | 7AM to 8AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 16 | 8AM to 9AM | 66.2 | 61.6 | 59 | 74.9 | 27.55 | 0.0749 | 0.5 | 13.49 | 0
September | 16 | 9AM to 10AM | 71.6 | 63.5 | 59 | 74.9 | 28.88 | 0.0742 | 0.5 | 13.63 | 0
September | 16 | 10AM to 11AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
September | 16 | 11AM to 12PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
September | 16 | 12PM to 1PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
September | 16 | 1PM to 2PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
September | 16 | 2PM to 3PM | 84.2 | 66.7 | 57.2 | 70.1 | 31.21 | 0.0725 | 0.47 | 13.94 | 0
September | 16 | 3PM to 4PM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
September | 16 | 4PM to 5PM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
September | 16 | 5PM to 6PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
September | 16 | 6PM to 7PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
September | 16 | 7PM to 8PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
September | 16 | 8PM to 9PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
September | 16 | 9PM to 10PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 16 | 10PM to 11PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 16 | 11PM to 12AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 17 | 12AM to 1AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 17 | 1AM to 2AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
September | 17 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
September | 17 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
September | 17 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
September | 17 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
September | 17 | 6AM to 7AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 17 | 7AM to 8AM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
September | 17 | 8AM to 9AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 17 | 9AM to 10AM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
September | 17 | 10AM to 11AM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
September | 17 | 11AM to 12PM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
September | 17 | 12PM to 1PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
September | 17 | 1PM to 2PM | 93.2 | 68.3 | 54.7 | 63.9 | 32.43 | 0.0713 | 0.43 | 14.15 | 0
September | 17 | 2PM to 3PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
September | 17 | 3PM to 4PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
September | 17 | 4PM to 5PM | 95 | 67.6 | 51.8 | 57.4 | 31.85 | 0.0711 | 0.39 | 14.17 | 0
September | 17 | 5PM to 6PM | 91.4 | 67.2 | 53.6 | 61.4 | 31.6 | 0.0716 | 0.41 | 14.09 | 0
September | 17 | 6PM to 7PM | 78.8 | 65.9 | 59 | 74.9 | 30.64 | 0.0732 | 0.5 | 13.81 | 0
September | 17 | 7PM to 8PM | 75.2 | 65.7 | 60.8 | 79.9 | 30.55 | 0.0736 | 0.54 | 13.74 | 0
September | 17 | 8PM to 9PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
September | 17 | 9PM to 10PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
September | 17 | 10PM to 11PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
September | 17 | 11PM to 12AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
September | 18 | 12AM to 1AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 18 | 1AM to 2AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
September | 18 | 2AM to 3AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 18 | 3AM to 4AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
September | 18 | 4AM to 5AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 18 | 5AM to 6AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 18 | 6AM to 7AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 18 | 7AM to 8AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
September | 18 | 8AM to 9AM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
September | 18 | 9AM to 10AM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
September | 18 | 10AM to 11AM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
September | 18 | 11AM to 12PM | 91.4 | 65.7 | 50 | 53.7 | 30.38 | 0.0716 | 0.36 | 14.07 | 0
September | 18 | 12PM to 1PM | 96.8 | 68.1 | 51.8 | 57.4 | 32.29 | 0.0709 | 0.39 | 14.22 | 0
September | 18 | 1PM to 2PM | 98.6 | 66.6 | 46.4 | 46.8 | 31.05 | 0.0707 | 0.32 | 14.23 | 0
September | 18 | 2PM to 3PM | 100.4 | 67.2 | 46.4 | 46.8 | 31.49 | 0.0705 | 0.32 | 14.28 | 0
September | 18 | 3PM to 4PM | 100.4 | 68.5 | 50 | 53.7 | 32.57 | 0.0705 | 0.36 | 14.3 | 0
September | 18 | 4PM to 5PM | 98.6 | 68.7 | 51.8 | 57.4 | 32.73 | 0.0707 | 0.39 | 14.27 | 0
September | 18 | 5PM to 6PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
September | 18 | 6PM to 7PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
September | 18 | 7PM to 8PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
September | 18 | 8PM to 9PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 18 | 9PM to 10PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
September | 18 | 10PM to 11PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 18 | 11PM to 12AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 19 | 12AM to 1AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 19 | 1AM to 2AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 19 | 2AM to 3AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 19 | 3AM to 4AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 19 | 4AM to 5AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 19 | 5AM to 6AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
September | 19 | 6AM to 7AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
September | 19 | 7AM to 8AM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
September | 19 | 8AM to 9AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
September | 19 | 9AM to 10AM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
September | 19 | 10AM to 11AM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
September | 19 | 11AM to 12PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
September | 19 | 12PM to 1PM | 96.8 | 70.5 | 57.2 | 70.1 | 34.29 | 0.0708 | 0.47 | 14.26 | 0
September | 19 | 1PM to 2PM | 98.6 | 71 | 57.2 | 70.1 | 34.73 | 0.0706 | 0.47 | 14.31 | 0
September | 19 | 2PM to 3PM | 100.4 | 71.5 | 57.2 | 70.1 | 35.17 | 0.0704 | 0.47 | 14.35 | 0
September | 19 | 3PM to 4PM | 100.4 | 71.5 | 57.2 | 70.1 | 35.17 | 0.0704 | 0.47 | 14.35 | 0
September | 19 | 4PM to 5PM | 98.6 | 71.9 | 59 | 74.9 | 35.48 | 0.0706 | 0.5 | 14.32 | 0
September | 19 | 5PM to 6PM | 96.8 | 70.5 | 57.2 | 70.1 | 34.29 | 0.0708 | 0.47 | 14.26 | 0
September | 19 | 6PM to 7PM | 84.2 | 67.6 | 59 | 74.9 | 31.96 | 0.0724 | 0.5 | 13.95 | 0
September | 19 | 7PM to 8PM | 84.2 | 68.6 | 60.8 | 79.9 | 32.75 | 0.0724 | 0.54 | 13.97 | 0
September | 19 | 8PM to 9PM | 80.6 | 65.5 | 57.2 | 70.1 | 30.33 | 0.073 | 0.47 | 13.85 | 0
September | 19 | 9PM to 10PM | 75.2 | 63.7 | 57.2 | 70.1 | 29.01 | 0.0737 | 0.47 | 13.71 | 0
September | 19 | 10PM to 11PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 19 | 11PM to 12AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 20 | 12AM to 1AM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
September | 20 | 1AM to 2AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
September | 20 | 2AM to 3AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
September | 20 | 3AM to 4AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 20 | 4AM to 5AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 20 | 5AM to 6AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 20 | 6AM to 7AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
September | 20 | 7AM to 8AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 20 | 8AM to 9AM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
September | 20 | 9AM to 10AM | 87.8 | 66.1 | 53.6 | 61.4 | 30.72 | 0.072 | 0.41 | 14 | 0
September | 20 | 10AM to 11AM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
September | 20 | 11AM to 12PM | 93.2 | 67.8 | 53.6 | 61.4 | 32.04 | 0.0713 | 0.41 | 14.14 | 0
September | 20 | 12PM to 1PM | 96.8 | 69.7 | 55.4 | 65.6 | 33.58 | 0.0709 | 0.44 | 14.25 | 0
September | 20 | 1PM to 2PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
September | 20 | 2PM to 3PM | 96.8 | 68.9 | 53.6 | 61.4 | 32.92 | 0.0709 | 0.41 | 14.23 | 0
September | 20 | 3PM to 4PM | 98.6 | 69.4 | 53.6 | 61.4 | 33.36 | 0.0707 | 0.41 | 14.28 | 0
September | 20 | 4PM to 5PM | 98.6 | 69.4 | 53.6 | 61.4 | 33.36 | 0.0707 | 0.41 | 14.28 | 0
September | 20 | 5PM to 6PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
September | 20 | 6PM to 7PM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
September | 20 | 7PM to 8PM | 75.2 | 64.7 | 59 | 74.9 | 29.76 | 0.0737 | 0.5 | 13.72 | 0
September | 20 | 8PM to 9PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
September | 20 | 9PM to 10PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
September | 20 | 10PM to 11PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
September | 20 | 11PM to 12AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
September | 21 | 12AM to 1AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 21 | 1AM to 2AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 21 | 2AM to 3AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 21 | 3AM to 4AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 21 | 4AM to 5AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 21 | 5AM to 6AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 21 | 6AM to 7AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 21 | 7AM to 8AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
September | 21 | 8AM to 9AM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
September | 21 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 21 | 10AM to 11AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
September | 21 | 11AM to 12PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 21 | 12PM to 1PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 21 | 1PM to 2PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
September | 21 | 2PM to 3PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 21 | 3PM to 4PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 21 | 4PM to 5PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
September | 21 | 5PM to 6PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
September | 21 | 6PM to 7PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 21 | 7PM to 8PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 21 | 8PM to 9PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 21 | 9PM to 10PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 21 | 10PM to 11PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 21 | 11PM to 12AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 22 | 12AM to 1AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 22 | 1AM to 2AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 22 | 2AM to 3AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 22 | 3AM to 4AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 22 | 4AM to 5AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 22 | 5AM to 6AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 22 | 6AM to 7AM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
September | 22 | 7AM to 8AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
September | 22 | 8AM to 9AM | 62.6 | 60.3 | 59 | 74.9 | 26.67 | 0.0754 | 0.5 | 13.4 | 0
September | 22 | 9AM to 10AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
September | 22 | 10AM to 11AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
September | 22 | 11AM to 12PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
September | 22 | 12PM to 1PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
September | 22 | 1PM to 2PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
September | 22 | 2PM to 3PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 22 | 3PM to 4PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
September | 22 | 4PM to 5PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 22 | 5PM to 6PM | 69.8 | 60.8 | 55.4 | 65.6 | 26.99 | 0.0745 | 0.44 | 13.55 | 0
September | 22 | 6PM to 7PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
September | 22 | 7PM to 8PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
September | 22 | 8PM to 9PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
September | 22 | 9PM to 10PM | 59 | 56.4 | 54.7 | 63.9 | 24.09 | 0.076 | 0.43 | 13.27 | 0
September | 22 | 10PM to 11PM | 57.2 | 55.5 | 54.3 | 63.1 | 23.52 | 0.0763 | 0.43 | 13.22 | 0
September | 22 | 11PM to 12AM | 56.5 | 55 | 54 | 62.2 | 23.21 | 0.0764 | 0.42 | 13.2 | 0
September | 23 | 12AM to 1AM | 56.1 | 54.8 | 54 | 62.2 | 23.12 | 0.0765 | 0.42 | 13.19 | 0
September | 23 | 1AM to 2AM | 55.4 | 54.1 | 53.2 | 60.6 | 22.69 | 0.0766 | 0.41 | 13.17 | 0
September | 23 | 2AM to 3AM | 54.7 | 53.6 | 52.9 | 59.8 | 22.39 | 0.0767 | 0.4 | 13.15 | 0
September | 23 | 3AM to 4AM | 54 | 53 | 52.3 | 58.6 | 22.03 | 0.0768 | 0.4 | 13.13 | 0
September | 23 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
September | 23 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
September | 23 | 6AM to 7AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
September | 23 | 7AM to 8AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
September | 23 | 8AM to 9AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
September | 23 | 9AM to 10AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
September | 23 | 10AM to 11AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
September | 23 | 11AM to 12PM | 75.2 | 57.8 | 44.6 | 43.7 | 24.88 | 0.0739 | 0.3 | 13.63 | 0
September | 23 | 12PM to 1PM | 78.8 | 58.4 | 42.8 | 40.8 | 25.29 | 0.0734 | 0.28 | 13.71 | 0
September | 23 | 1PM to 2PM | 80.6 | 59.1 | 42.8 | 40.8 | 25.73 | 0.0731 | 0.28 | 13.75 | 0
September | 23 | 2PM to 3PM | 80.6 | 57.8 | 39.2 | 35.4 | 24.89 | 0.0732 | 0.24 | 13.74 | 0
September | 23 | 3PM to 4PM | 80.6 | 57.3 | 37.4 | 33 | 24.51 | 0.0732 | 0.22 | 13.73 | 0
September | 23 | 4PM to 5PM | 78.8 | 56 | 35.6 | 30.7 | 23.72 | 0.0734 | 0.21 | 13.68 | 0
September | 23 | 5PM to 6PM | 71.6 | 56.4 | 44.6 | 43.7 | 24 | 0.0744 | 0.3 | 13.53 | 0
September | 23 | 6PM to 7PM | 66.2 | 54.2 | 44.6 | 43.7 | 22.69 | 0.0751 | 0.3 | 13.4 | 0
September | 23 | 7PM to 8PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
September | 23 | 8PM to 9PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
September | 23 | 9PM to 10PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
September | 23 | 10PM to 11PM | 60.8 | 50.4 | 41 | 38 | 20.5 | 0.0759 | 0.26 | 13.24 | 0
September | 23 | 11PM to 12AM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
September | 24 | 12AM to 1AM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
September | 24 | 1AM to 2AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
September | 24 | 2AM to 3AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
September | 24 | 3AM to 4AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
September | 24 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
September | 24 | 5AM to 6AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
September | 24 | 6AM to 7AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
September | 24 | 7AM to 8AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
September | 24 | 8AM to 9AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 24 | 9AM to 10AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
September | 24 | 10AM to 11AM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
September | 24 | 11AM to 12PM | 78.8 | 58.4 | 42.8 | 40.8 | 25.29 | 0.0734 | 0.28 | 13.71 | 0
September | 24 | 12PM to 1PM | 80.6 | 57.8 | 39.2 | 35.4 | 24.89 | 0.0732 | 0.24 | 13.74 | 0
September | 24 | 1PM to 2PM | 82.4 | 59.1 | 41 | 38 | 25.73 | 0.0729 | 0.26 | 13.79 | 0
September | 24 | 2PM to 3PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
September | 24 | 3PM to 4PM | 84.2 | 60.4 | 42.8 | 40.8 | 26.6 | 0.0726 | 0.28 | 13.85 | 0
September | 24 | 4PM to 5PM | 82.4 | 59.8 | 42.8 | 40.8 | 26.17 | 0.0729 | 0.28 | 13.8 | 0
September | 24 | 5PM to 6PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
September | 24 | 6PM to 7PM | 73.4 | 57.1 | 44.6 | 43.7 | 24.44 | 0.0741 | 0.3 | 13.58 | 0
September | 24 | 7PM to 8PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
September | 24 | 8PM to 9PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
September | 24 | 9PM to 10PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
September | 24 | 10PM to 11PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
September | 24 | 11PM to 12AM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
September | 25 | 12AM to 1AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
September | 25 | 1AM to 2AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
September | 25 | 2AM to 3AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
September | 25 | 3AM to 4AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
September | 25 | 4AM to 5AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
September | 25 | 5AM to 6AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
September | 25 | 6AM to 7AM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
September | 25 | 7AM to 8AM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
September | 25 | 8AM to 9AM | 69.8 | 55.7 | 44.6 | 43.7 | 23.57 | 0.0746 | 0.3 | 13.49 | 0
September | 25 | 9AM to 10AM | 75.2 | 57.1 | 42.8 | 40.8 | 24.42 | 0.0739 | 0.28 | 13.62 | 0
September | 25 | 10AM to 11AM | 80.6 | 59.1 | 42.8 | 40.8 | 25.73 | 0.0731 | 0.28 | 13.75 | 0
September | 25 | 11AM to 12PM | 84.2 | 61.1 | 44.6 | 43.7 | 27.06 | 0.0726 | 0.3 | 13.85 | 0
September | 25 | 12PM to 1PM | 84.2 | 61.1 | 44.6 | 43.7 | 27.06 | 0.0726 | 0.3 | 13.85 | 0
September | 25 | 1PM to 2PM | 87.8 | 63.7 | 48.2 | 50.1 | 28.95 | 0.0721 | 0.34 | 13.97 | 0
September | 25 | 2PM to 3PM | 87.8 | 62.4 | 44.6 | 43.7 | 27.94 | 0.0722 | 0.3 | 13.95 | 0
September | 25 | 3PM to 4PM | 87.8 | 62.4 | 44.6 | 43.7 | 27.94 | 0.0722 | 0.3 | 13.95 | 0
September | 25 | 4PM to 5PM | 89.6 | 63 | 44.6 | 43.7 | 28.37 | 0.0719 | 0.3 | 13.99 | 0
September | 25 | 5PM to 6PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
September | 25 | 6PM to 7PM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
September | 25 | 7PM to 8PM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
September | 25 | 8PM to 9PM | 68 | 57.4 | 50 | 53.7 | 24.69 | 0.0748 | 0.36 | 13.47 | 0
September | 25 | 9PM to 10PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
September | 25 | 10PM to 11PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
September | 25 | 11PM to 12AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
September | 26 | 12AM to 1AM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
September | 26 | 1AM to 2AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
September | 26 | 2AM to 3AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
September | 26 | 3AM to 4AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
September | 26 | 4AM to 5AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
September | 26 | 5AM to 6AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
September | 26 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 26 | 7AM to 8AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
September | 26 | 8AM to 9AM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
September | 26 | 9AM to 10AM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
September | 26 | 10AM to 11AM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
September | 26 | 11AM to 12PM | 84.2 | 61.8 | 46.4 | 46.8 | 27.55 | 0.0726 | 0.32 | 13.86 | 0
September | 26 | 12PM to 1PM | 87.8 | 63 | 46.4 | 46.8 | 28.43 | 0.0721 | 0.32 | 13.96 | 0
September | 26 | 1PM to 2PM | 90 | 63.8 | 46.6 | 47.1 | 29 | 0.0718 | 0.32 | 14.01 | 0
September | 26 | 2PM to 3PM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
September | 26 | 3PM to 4PM | 91.4 | 63 | 42.8 | 40.8 | 28.35 | 0.0717 | 0.28 | 14.03 | 0
September | 26 | 4PM to 5PM | 89.6 | 62.3 | 42.8 | 40.8 | 27.91 | 0.0719 | 0.28 | 13.98 | 0
September | 26 | 5PM to 6PM | 84.2 | 61.1 | 44.6 | 43.7 | 27.06 | 0.0726 | 0.3 | 13.85 | 0
September | 26 | 6PM to 7PM | 77 | 61.6 | 51.8 | 57.4 | 27.46 | 0.0735 | 0.39 | 13.71 | 0
September | 26 | 7PM to 8PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
September | 26 | 8PM to 9PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 26 | 9PM to 10PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 26 | 10PM to 11PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 26 | 11PM to 12AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
September | 27 | 12AM to 1AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
September | 27 | 1AM to 2AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
September | 27 | 2AM to 3AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
September | 27 | 3AM to 4AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 27 | 4AM to 5AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
September | 27 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
September | 27 | 6AM to 7AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
September | 27 | 7AM to 8AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 27 | 8AM to 9AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
September | 27 | 9AM to 10AM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 27 | 10AM to 11AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 27 | 11AM to 12PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
September | 27 | 12PM to 1PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
September | 27 | 1PM to 2PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
September | 27 | 2PM to 3PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
September | 27 | 3PM to 4PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
September | 27 | 4PM to 5PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 27 | 5PM to 6PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
September | 27 | 6PM to 7PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
September | 27 | 7PM to 8PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
September | 27 | 8PM to 9PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 27 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
September | 27 | 10PM to 11PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
September | 27 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 28 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 28 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
September | 28 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
September | 28 | 3AM to 4AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
September | 28 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
September | 28 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 28 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 28 | 7AM to 8AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 28 | 8AM to 9AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
September | 28 | 9AM to 10AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 28 | 10AM to 11AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 28 | 11AM to 12PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
September | 28 | 12PM to 1PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
September | 28 | 1PM to 2PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 28 | 2PM to 3PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 28 | 3PM to 4PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 28 | 4PM to 5PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
September | 28 | 5PM to 6PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 28 | 6PM to 7PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
September | 28 | 7PM to 8PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
September | 28 | 8PM to 9PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
September | 28 | 9PM to 10PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 28 | 10PM to 11PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
September | 28 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 29 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 29 | 1AM to 2AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
September | 29 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
September | 29 | 3AM to 4AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
September | 29 | 4AM to 5AM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
September | 29 | 5AM to 6AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
September | 29 | 6AM to 7AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
September | 29 | 7AM to 8AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
September | 29 | 8AM to 9AM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
September | 29 | 9AM to 10AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
September | 29 | 10AM to 11AM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
September | 29 | 11AM to 12PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
September | 29 | 12PM to 1PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
September | 29 | 1PM to 2PM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
September | 29 | 2PM to 3PM | 87.8 | 67.8 | 57.2 | 70.1 | 32.09 | 0.072 | 0.47 | 14.03 | 0
September | 29 | 3PM to 4PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
September | 29 | 4PM to 5PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
September | 29 | 5PM to 6PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
September | 29 | 6PM to 7PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 29 | 7PM to 8PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
September | 29 | 8PM to 9PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
September | 29 | 9PM to 10PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
September | 29 | 10PM to 11PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
September | 29 | 11PM to 12AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
September | 30 | 12AM to 1AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
September | 30 | 1AM to 2AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
September | 30 | 2AM to 3AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 30 | 3AM to 4AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 30 | 4AM to 5AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
September | 30 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
September | 30 | 6AM to 7AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
September | 30 | 7AM to 8AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
September | 30 | 8AM to 9AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
September | 30 | 9AM to 10AM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
September | 30 | 10AM to 11AM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
September | 30 | 11AM to 12PM | 82.4 | 65.2 | 55.4 | 65.6 | 30.07 | 0.0727 | 0.44 | 13.88 | 0
September | 30 | 12PM to 1PM | 86 | 66.3 | 55.4 | 65.6 | 30.95 | 0.0723 | 0.44 | 13.97 | 0
September | 30 | 1PM to 2PM | 89.6 | 67.5 | 55.4 | 65.6 | 31.83 | 0.0718 | 0.44 | 14.06 | 0
September | 30 | 2PM to 3PM | 89.6 | 66.6 | 53.6 | 61.4 | 31.16 | 0.0718 | 0.41 | 14.05 | 0
September | 30 | 3PM to 4PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
September | 30 | 4PM to 5PM | 89.6 | 65.8 | 51.8 | 57.4 | 30.53 | 0.0718 | 0.39 | 14.04 | 0
September | 30 | 5PM to 6PM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
September | 30 | 6PM to 7PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
September | 30 | 7PM to 8PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
September | 30 | 8PM to 9PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
September | 30 | 9PM to 10PM | 71.4 | 60.5 | 53.6 | 61.4 | 26.73 | 0.0743 | 0.41 | 13.58 | 0
September | 30 | 10PM to 11PM | 69.3 | 59.7 | 53.6 | 61.4 | 26.2 | 0.0746 | 0.41 | 13.53 | 0
September | 30 | 11PM to 12AM | 67.3 | 59 | 53.6 | 61.4 | 25.72 | 0.0748 | 0.41 | 13.48 | 0
October | 1 | 12AM to 1AM | 65.1 | 58.2 | 53.6 | 61.4 | 25.19 | 0.0752 | 0.41 | 13.42 | 0
October | 1 | 1AM to 2AM | 63.1 | 57.4 | 53.6 | 61.4 | 24.71 | 0.0754 | 0.41 | 13.37 | 0
October | 1 | 2AM to 3AM | 61 | 56.6 | 53.6 | 61.4 | 24.18 | 0.0758 | 0.41 | 13.32 | 0
October | 1 | 3AM to 4AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
October | 1 | 4AM to 5AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
October | 1 | 5AM to 6AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 1 | 6AM to 7AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 1 | 7AM to 8AM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
October | 1 | 8AM to 9AM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
October | 1 | 9AM to 10AM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
October | 1 | 10AM to 11AM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
October | 1 | 11AM to 12PM | 87.8 | 66.9 | 55.4 | 65.6 | 31.39 | 0.072 | 0.44 | 14.02 | 0
October | 1 | 12PM to 1PM | 89.6 | 68.3 | 57.2 | 70.1 | 32.53 | 0.0718 | 0.47 | 14.08 | 0
October | 1 | 1PM to 2PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
October | 1 | 2PM to 3PM | 93.2 | 68.6 | 55.4 | 65.6 | 32.7 | 0.0713 | 0.44 | 14.15 | 0
October | 1 | 3PM to 4PM | 93.2 | 69.4 | 57.2 | 70.1 | 33.41 | 0.0713 | 0.47 | 14.17 | 0
October | 1 | 4PM to 5PM | 91.4 | 68 | 55.4 | 65.6 | 32.27 | 0.0715 | 0.44 | 14.11 | 0
October | 1 | 5PM to 6PM | 86 | 67.2 | 57.2 | 70.1 | 31.65 | 0.0722 | 0.47 | 13.98 | 0
October | 1 | 6PM to 7PM | 80.6 | 67.4 | 60.8 | 79.9 | 31.87 | 0.0729 | 0.54 | 13.88 | 0
October | 1 | 7PM to 8PM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
October | 1 | 8PM to 9PM | 71.6 | 61.5 | 55.4 | 65.6 | 27.43 | 0.0742 | 0.44 | 13.6 | 0
October | 1 | 9PM to 10PM | 68 | 61.2 | 57.2 | 70.1 | 27.25 | 0.0747 | 0.47 | 13.52 | 0
October | 1 | 10PM to 11PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
October | 1 | 11PM to 12AM | 63.3 | 59.4 | 57 | 69.7 | 26.04 | 0.0754 | 0.47 | 13.4 | 0
October | 2 | 12AM to 1AM | 62.8 | 58.9 | 56.5 | 68.3 | 25.69 | 0.0755 | 0.46 | 13.38 | 0
October | 2 | 1AM to 2AM | 61.9 | 58.3 | 56.1 | 67.4 | 25.33 | 0.0756 | 0.45 | 13.36 | 0
October | 2 | 2AM to 3AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
October | 2 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
October | 2 | 4AM to 5AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
October | 2 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 2 | 6AM to 7AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 2 | 7AM to 8AM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
October | 2 | 8AM to 9AM | 66.2 | 59.5 | 55.4 | 65.6 | 26.11 | 0.075 | 0.44 | 13.46 | 0
October | 2 | 9AM to 10AM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
October | 2 | 10AM to 11AM | 73.4 | 63.1 | 57.2 | 70.1 | 28.57 | 0.0739 | 0.47 | 13.66 | 0
October | 2 | 11AM to 12PM | 77 | 63.4 | 55.4 | 65.6 | 28.75 | 0.0735 | 0.44 | 13.74 | 0
October | 2 | 12PM to 1PM | 80.6 | 64.6 | 55.4 | 65.6 | 29.63 | 0.073 | 0.44 | 13.83 | 0
October | 2 | 1PM to 2PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
October | 2 | 2PM to 3PM | 84.2 | 64.9 | 53.6 | 61.4 | 29.84 | 0.0725 | 0.41 | 13.91 | 0
October | 2 | 3PM to 4PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
October | 2 | 4PM to 5PM | 80.6 | 62.8 | 51.8 | 57.4 | 28.34 | 0.073 | 0.39 | 13.81 | 0
October | 2 | 5PM to 6PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
October | 2 | 6PM to 7PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
October | 2 | 7PM to 8PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
October | 2 | 8PM to 9PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
October | 2 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 2 | 10PM to 11PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
October | 2 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 3 | 12AM to 1AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
October | 3 | 1AM to 2AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
October | 3 | 2AM to 3AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 3 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 3 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 3 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 3 | 6AM to 7AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 3 | 7AM to 8AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 3 | 8AM to 9AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
October | 3 | 9AM to 10AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
October | 3 | 10AM to 11AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
October | 3 | 11AM to 12PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
October | 3 | 12PM to 1PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
October | 3 | 1PM to 2PM | 82.4 | 63.5 | 51.8 | 57.4 | 28.78 | 0.0728 | 0.39 | 13.85 | 0
October | 3 | 2PM to 3PM | 84.2 | 62.5 | 48.2 | 50.1 | 28.07 | 0.0726 | 0.34 | 13.87 | 0
October | 3 | 3PM to 4PM | 84.2 | 61.1 | 44.6 | 43.7 | 27.06 | 0.0726 | 0.3 | 13.85 | 0
October | 3 | 4PM to 5PM | 82.4 | 60.4 | 44.6 | 43.7 | 26.63 | 0.0729 | 0.3 | 13.81 | 0
October | 3 | 5PM to 6PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
October | 3 | 6PM to 7PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
October | 3 | 7PM to 8PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
October | 3 | 8PM to 9PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
October | 3 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 3 | 10PM to 11PM | 58.6 | 54.4 | 51.4 | 56.6 | 22.87 | 0.0761 | 0.38 | 13.24 | 0
October | 3 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 4 | 12AM to 1AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 4 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 4 | 2AM to 3AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 4 | 3AM to 4AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 4 | 4AM to 5AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 4 | 5AM to 6AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 4 | 6AM to 7AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 4 | 7AM to 8AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 4 | 8AM to 9AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 4 | 9AM to 10AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
October | 4 | 10AM to 11AM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0746 | 0.39 | 13.51 | 0
October | 4 | 11AM to 12PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
October | 4 | 12PM to 1PM | 77 | 60.8 | 50 | 53.7 | 26.88 | 0.0735 | 0.36 | 13.7 | 0
October | 4 | 1PM to 2PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
October | 4 | 2PM to 3PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
October | 4 | 3PM to 4PM | 81.7 | 62.2 | 49.5 | 52.6 | 27.85 | 0.0729 | 0.36 | 13.82 | 0
October | 4 | 4PM to 5PM | 80.6 | 62 | 50 | 53.7 | 27.75 | 0.0731 | 0.36 | 13.79 | 0
October | 4 | 5PM to 6PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
October | 4 | 6PM to 7PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
October | 4 | 7PM to 8PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
October | 4 | 8PM to 9PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 4 | 9PM to 10PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
October | 4 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 4 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 5 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 5 | 1AM to 2AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 5 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 5 | 3AM to 4AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 5 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 5 | 5AM to 6AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 5 | 6AM to 7AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 5 | 7AM to 8AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 5 | 8AM to 9AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
October | 5 | 9AM to 10AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
October | 5 | 10AM to 11AM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
October | 5 | 11AM to 12PM | 78.8 | 64 | 55.4 | 65.6 | 29.19 | 0.0732 | 0.44 | 13.79 | 0
October | 5 | 12PM to 1PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
October | 5 | 1PM to 2PM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
October | 5 | 2PM to 3PM | 86 | 64.7 | 51.8 | 57.4 | 29.66 | 0.0723 | 0.39 | 13.94 | 0
October | 5 | 3PM to 4PM | 87.8 | 63.7 | 48.2 | 50.1 | 28.95 | 0.0721 | 0.34 | 13.97 | 0
October | 5 | 4PM to 5PM | 84.2 | 65.8 | 55.4 | 65.6 | 30.51 | 0.0725 | 0.44 | 13.92 | 0
October | 5 | 5PM to 6PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
October | 5 | 6PM to 7PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
October | 5 | 7PM to 8PM | 69.8 | 59.9 | 53.6 | 61.4 | 26.33 | 0.0745 | 0.41 | 13.54 | 0
October | 5 | 8PM to 9PM | 68 | 60.2 | 55.4 | 65.6 | 26.55 | 0.0747 | 0.44 | 13.51 | 0
October | 5 | 9PM to 10PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
October | 5 | 10PM to 11PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
October | 5 | 11PM to 12AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
October | 6 | 12AM to 1AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
October | 6 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 6 | 2AM to 3AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 6 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 6 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 6 | 5AM to 6AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 6 | 6AM to 7AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
October | 6 | 7AM to 8AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 6 | 8AM to 9AM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
October | 6 | 9AM to 10AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
October | 6 | 10AM to 11AM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
October | 6 | 11AM to 12PM | 82.4 | 64.3 | 53.6 | 61.4 | 29.4 | 0.0728 | 0.41 | 13.86 | 0
October | 6 | 12PM to 1PM | 84.2 | 64.1 | 51.8 | 57.4 | 29.22 | 0.0725 | 0.39 | 13.9 | 0
October | 6 | 1PM to 2PM | 89.6 | 63.6 | 46.4 | 46.8 | 28.87 | 0.0719 | 0.32 | 14 | 0
October | 6 | 2PM to 3PM | 91.4 | 64.3 | 46.4 | 46.8 | 29.3 | 0.0717 | 0.32 | 14.05 | 0
October | 6 | 3PM to 4PM | 91.4 | 63.6 | 44.6 | 43.7 | 28.81 | 0.0717 | 0.3 | 14.04 | 0
October | 6 | 4PM to 5PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
October | 6 | 5PM to 6PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
October | 6 | 6PM to 7PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
October | 6 | 7PM to 8PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
October | 6 | 8PM to 9PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
October | 6 | 9PM to 10PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
October | 6 | 10PM to 11PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 6 | 11PM to 12AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 7 | 12AM to 1AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 7 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 7 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 7 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 7 | 4AM to 5AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
October | 7 | 5AM to 6AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
October | 7 | 6AM to 7AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 7 | 7AM to 8AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 7 | 8AM to 9AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 7 | 9AM to 10AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
October | 7 | 10AM to 11AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
October | 7 | 11AM to 12PM | 71.6 | 60.5 | 53.6 | 61.4 | 26.77 | 0.0742 | 0.41 | 13.59 | 0
October | 7 | 12PM to 1PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
October | 7 | 1PM to 2PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
October | 7 | 2PM to 3PM | 78.8 | 62.2 | 51.8 | 57.4 | 27.9 | 0.0733 | 0.39 | 13.76 | 0
October | 7 | 3PM to 4PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
October | 7 | 4PM to 5PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
October | 7 | 5PM to 6PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
October | 7 | 6PM to 7PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
October | 7 | 7PM to 8PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 7 | 8PM to 9PM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
October | 7 | 9PM to 10PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 7 | 10PM to 11PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 7 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 8 | 12AM to 1AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 8 | 1AM to 2AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 8 | 2AM to 3AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 8 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 8 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 8 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 8 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
October | 8 | 7AM to 8AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 8 | 8AM to 9AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
October | 8 | 9AM to 10AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
October | 8 | 10AM to 11AM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
October | 8 | 11AM to 12PM | 73.4 | 60.3 | 51.8 | 57.4 | 26.59 | 0.074 | 0.39 | 13.62 | 0
October | 8 | 12PM to 1PM | 77 | 62.5 | 53.6 | 61.4 | 28.09 | 0.0735 | 0.41 | 13.73 | 0
October | 8 | 1PM to 2PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
October | 8 | 2PM to 3PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
October | 8 | 3PM to 4PM | 80.6 | 63.7 | 53.6 | 61.4 | 28.97 | 0.073 | 0.41 | 13.82 | 0
October | 8 | 4PM to 5PM | 78.8 | 63.1 | 53.6 | 61.4 | 28.53 | 0.0732 | 0.41 | 13.77 | 0
October | 8 | 5PM to 6PM | 75.2 | 62.7 | 55.4 | 65.6 | 28.31 | 0.0737 | 0.44 | 13.69 | 0
October | 8 | 6PM to 7PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
October | 8 | 7PM to 8PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
October | 8 | 8PM to 9PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
October | 8 | 9PM to 10PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 8 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 8 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 9 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 9 | 1AM to 2AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 9 | 2AM to 3AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 9 | 3AM to 4AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 9 | 4AM to 5AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 9 | 5AM to 6AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 9 | 6AM to 7AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
October | 9 | 7AM to 8AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
October | 9 | 8AM to 9AM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
October | 9 | 9AM to 10AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
October | 9 | 10AM to 11AM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
October | 9 | 11AM to 12PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
October | 9 | 12PM to 1PM | 62.6 | 61.4 | 60.8 | 79.9 | 27.46 | 0.0754 | 0.54 | 13.41 | 0
October | 9 | 1PM to 2PM | 62.6 | 60.3 | 59 | 74.9 | 26.67 | 0.0754 | 0.5 | 13.4 | 0
October | 9 | 2PM to 3PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
October | 9 | 3PM to 4PM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
October | 9 | 4PM to 5PM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
October | 9 | 5PM to 6PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
October | 9 | 6PM to 7PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 9 | 7PM to 8PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 9 | 8PM to 9PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 9 | 9PM to 10PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 9 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 9 | 11PM to 12AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 10 | 12AM to 1AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
October | 10 | 1AM to 2AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
October | 10 | 2AM to 3AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 10 | 3AM to 4AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 10 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 10 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 10 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 10 | 7AM to 8AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 10 | 8AM to 9AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 10 | 9AM to 10AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
October | 10 | 10AM to 11AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
October | 10 | 11AM to 12PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
October | 10 | 12PM to 1PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
October | 10 | 1PM to 2PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 10 | 2PM to 3PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 10 | 3PM to 4PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 10 | 4PM to 5PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
October | 10 | 5PM to 6PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
October | 10 | 6PM to 7PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 10 | 7PM to 8PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 10 | 8PM to 9PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 10 | 9PM to 10PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 10 | 10PM to 11PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 10 | 11PM to 12AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
October | 11 | 12AM to 1AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
October | 11 | 1AM to 2AM | 48.2 | 48 | 47.8 | 49.5 | 19.22 | 0.0777 | 0.33 | 12.95 | 1
October | 11 | 2AM to 3AM | 48.2 | 47.6 | 47.1 | 48.1 | 19.01 | 0.0777 | 0.33 | 12.95 | 1
October | 11 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 11 | 4AM to 5AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 11 | 5AM to 6AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 11 | 6AM to 7AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 11 | 7AM to 8AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 11 | 8AM to 9AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
October | 11 | 9AM to 10AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
October | 11 | 10AM to 11AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 11 | 11AM to 12PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 11 | 12PM to 1PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 11 | 1PM to 2PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 11 | 2PM to 3PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 11 | 3PM to 4PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 11 | 4PM to 5PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 11 | 5PM to 6PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 11 | 6PM to 7PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 11 | 7PM to 8PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 11 | 8PM to 9PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 11 | 9PM to 10PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 11 | 10PM to 11PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 11 | 11PM to 12AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
October | 12 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 12 | 1AM to 2AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
October | 12 | 2AM to 3AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 12 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 12 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 12 | 5AM to 6AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
October | 12 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
October | 12 | 7AM to 8AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 12 | 8AM to 9AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 12 | 9AM to 10AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 12 | 10AM to 11AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 12 | 11AM to 12PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
October | 12 | 12PM to 1PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
October | 12 | 1PM to 2PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
October | 12 | 2PM to 3PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
October | 12 | 3PM to 4PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
October | 12 | 4PM to 5PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
October | 12 | 5PM to 6PM | 59 | 53.8 | 50 | 53.7 | 22.5 | 0.0761 | 0.36 | 13.24 | 0
October | 12 | 6PM to 7PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
October | 12 | 7PM to 8PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 12 | 8PM to 9PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 12 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 12 | 10PM to 11PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
October | 12 | 11PM to 12AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
October | 13 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 13 | 1AM to 2AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
October | 13 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 13 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 13 | 4AM to 5AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
October | 13 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 13 | 6AM to 7AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
October | 13 | 7AM to 8AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 13 | 8AM to 9AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
October | 13 | 9AM to 10AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
October | 13 | 10AM to 11AM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
October | 13 | 11AM to 12PM | 68 | 55.7 | 46.4 | 46.8 | 23.62 | 0.0748 | 0.32 | 13.45 | 0
October | 13 | 12PM to 1PM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
October | 13 | 1PM to 2PM | 71.6 | 56.4 | 44.6 | 43.7 | 24 | 0.0744 | 0.3 | 13.53 | 0
October | 13 | 2PM to 3PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
October | 13 | 3PM to 4PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
October | 13 | 4PM to 5PM | 71.6 | 57.1 | 46.4 | 46.8 | 24.49 | 0.0743 | 0.32 | 13.54 | 0
October | 13 | 5PM to 6PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
October | 13 | 6PM to 7PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
October | 13 | 7PM to 8PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
October | 13 | 8PM to 9PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 13 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 13 | 10PM to 11PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
October | 13 | 11PM to 12AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
October | 14 | 12AM to 1AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
October | 14 | 1AM to 2AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
October | 14 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 14 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 14 | 4AM to 5AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
October | 14 | 5AM to 6AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
October | 14 | 6AM to 7AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 14 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 14 | 8AM to 9AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 14 | 9AM to 10AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
October | 14 | 10AM to 11AM | 66.2 | 56.7 | 50 | 53.7 | 24.25 | 0.0751 | 0.36 | 13.43 | 0
October | 14 | 11AM to 12PM | 69.8 | 58.1 | 50 | 53.7 | 25.12 | 0.0745 | 0.36 | 13.52 | 0
October | 14 | 12PM to 1PM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
October | 14 | 1PM to 2PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
October | 14 | 2PM to 3PM | 77 | 58.5 | 44.6 | 43.7 | 25.32 | 0.0736 | 0.3 | 13.67 | 0
October | 14 | 3PM to 4PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
October | 14 | 4PM to 5PM | 73.6 | 58 | 46.6 | 47.1 | 25.02 | 0.0741 | 0.32 | 13.59 | 0
October | 14 | 5PM to 6PM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
October | 14 | 6PM to 7PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
October | 14 | 7PM to 8PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
October | 14 | 8PM to 9PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
October | 14 | 9PM to 10PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 14 | 10PM to 11PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 14 | 11PM to 12AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
October | 15 | 12AM to 1AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 15 | 1AM to 2AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 15 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 15 | 3AM to 4AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 15 | 4AM to 5AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 15 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 15 | 6AM to 7AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 15 | 7AM to 8AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 15 | 8AM to 9AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 15 | 9AM to 10AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
October | 15 | 10AM to 11AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
October | 15 | 11AM to 12PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
October | 15 | 12PM to 1PM | 73.4 | 59.4 | 50 | 53.7 | 26 | 0.074 | 0.36 | 13.61 | 0
October | 15 | 1PM to 2PM | 75.2 | 60.1 | 50 | 53.7 | 26.44 | 0.0738 | 0.36 | 13.66 | 0
October | 15 | 2PM to 3PM | 77 | 60 | 48.2 | 50.1 | 26.32 | 0.0736 | 0.34 | 13.69 | 0
October | 15 | 3PM to 4PM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
October | 15 | 4PM to 5PM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
October | 15 | 5PM to 6PM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
October | 15 | 6PM to 7PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
October | 15 | 7PM to 8PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
October | 15 | 8PM to 9PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
October | 15 | 9PM to 10PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
October | 15 | 10PM to 11PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
October | 15 | 11PM to 12AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
October | 16 | 12AM to 1AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
October | 16 | 1AM to 2AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 16 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
October | 16 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 16 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 16 | 5AM to 6AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 16 | 6AM to 7AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 16 | 7AM to 8AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 16 | 8AM to 9AM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
October | 16 | 9AM to 10AM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
October | 16 | 10AM to 11AM | 71.6 | 58.8 | 50 | 53.7 | 25.56 | 0.0743 | 0.36 | 13.56 | 0
October | 16 | 11AM to 12PM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
October | 16 | 12PM to 1PM | 77 | 60.8 | 50 | 53.7 | 26.88 | 0.0735 | 0.36 | 13.7 | 0
October | 16 | 1PM to 2PM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
October | 16 | 2PM to 3PM | 78.8 | 60.6 | 48.2 | 50.1 | 26.76 | 0.0733 | 0.34 | 13.74 | 0
October | 16 | 3PM to 4PM | 80.6 | 61.2 | 48.2 | 50.1 | 27.2 | 0.0731 | 0.34 | 13.78 | 0
October | 16 | 4PM to 5PM | 77 | 59.2 | 46.4 | 46.8 | 25.8 | 0.0736 | 0.32 | 13.68 | 0
October | 16 | 5PM to 6PM | 69.8 | 57.3 | 48.2 | 50.1 | 24.57 | 0.0746 | 0.34 | 13.51 | 0
October | 16 | 6PM to 7PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
October | 16 | 7PM to 8PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
October | 16 | 8PM to 9PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
October | 16 | 9PM to 10PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 16 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 16 | 11PM to 12AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
October | 17 | 12AM to 1AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
October | 17 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 17 | 2AM to 3AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 17 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 17 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 17 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 17 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
October | 17 | 7AM to 8AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 17 | 8AM to 9AM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
October | 17 | 9AM to 10AM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
October | 17 | 10AM to 11AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
October | 17 | 11AM to 12PM | 75.2 | 58.5 | 46.4 | 46.8 | 25.37 | 0.0738 | 0.32 | 13.63 | 0
October | 17 | 12PM to 1PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
October | 17 | 1PM to 2PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
October | 17 | 2PM to 3PM | 82.4 | 60.4 | 44.6 | 43.7 | 26.63 | 0.0729 | 0.3 | 13.81 | 0
October | 17 | 3PM to 4PM | 82.4 | 60.4 | 44.6 | 43.7 | 26.63 | 0.0729 | 0.3 | 13.81 | 0
October | 17 | 4PM to 5PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
October | 17 | 5PM to 6PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
October | 17 | 6PM to 7PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
October | 17 | 7PM to 8PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
October | 17 | 8PM to 9PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
October | 17 | 9PM to 10PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
October | 17 | 10PM to 11PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
October | 17 | 11PM to 12AM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
October | 18 | 12AM to 1AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
October | 18 | 1AM to 2AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
October | 18 | 2AM to 3AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
October | 18 | 3AM to 4AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 18 | 4AM to 5AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 18 | 5AM to 6AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 18 | 6AM to 7AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 18 | 7AM to 8AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 18 | 8AM to 9AM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
October | 18 | 9AM to 10AM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
October | 18 | 10AM to 11AM | 73.4 | 57.8 | 46.4 | 46.8 | 24.93 | 0.0741 | 0.32 | 13.59 | 0
October | 18 | 11AM to 12PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
October | 18 | 12PM to 1PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
October | 18 | 1PM to 2PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
October | 18 | 2PM to 3PM | 82.4 | 60.4 | 44.6 | 43.7 | 26.63 | 0.0729 | 0.3 | 13.81 | 0
October | 18 | 3PM to 4PM | 80.6 | 60.5 | 46.4 | 46.8 | 26.68 | 0.0731 | 0.32 | 13.77 | 0
October | 18 | 4PM to 5PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
October | 18 | 5PM to 6PM | 73.4 | 58.6 | 48.2 | 50.1 | 25.45 | 0.0741 | 0.34 | 13.6 | 0
October | 18 | 6PM to 7PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
October | 18 | 7PM to 8PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
October | 18 | 8PM to 9PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
October | 18 | 9PM to 10PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 18 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 18 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 19 | 12AM to 1AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 19 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 19 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 19 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 19 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 19 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 19 | 6AM to 7AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 19 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 19 | 8AM to 9AM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
October | 19 | 9AM to 10AM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
October | 19 | 10AM to 11AM | 71.6 | 57.9 | 48.2 | 50.1 | 25.01 | 0.0743 | 0.34 | 13.55 | 0
October | 19 | 11AM to 12PM | 75.2 | 59.3 | 48.2 | 50.1 | 25.89 | 0.0738 | 0.34 | 13.65 | 0
October | 19 | 12PM to 1PM | 78.8 | 59.8 | 46.4 | 46.8 | 26.24 | 0.0733 | 0.32 | 13.73 | 0
October | 19 | 1PM to 2PM | 80.6 | 59.8 | 44.6 | 43.7 | 26.19 | 0.0731 | 0.3 | 13.76 | 0
October | 19 | 2PM to 3PM | 80.6 | 59.8 | 44.6 | 43.7 | 26.19 | 0.0731 | 0.3 | 13.76 | 0
October | 19 | 3PM to 4PM | 80.6 | 59.1 | 42.8 | 40.8 | 25.73 | 0.0731 | 0.28 | 13.75 | 0
October | 19 | 4PM to 5PM | 78.8 | 59.1 | 44.6 | 43.7 | 25.75 | 0.0734 | 0.3 | 13.72 | 0
October | 19 | 5PM to 6PM | 71.6 | 56.4 | 44.6 | 43.7 | 24 | 0.0744 | 0.3 | 13.53 | 0
October | 19 | 6PM to 7PM | 69.8 | 56.4 | 46.4 | 46.8 | 24.05 | 0.0746 | 0.32 | 13.5 | 0
October | 19 | 7PM to 8PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
October | 19 | 8PM to 9PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
October | 19 | 9PM to 10PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
October | 19 | 10PM to 11PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 19 | 11PM to 12AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 20 | 12AM to 1AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 20 | 1AM to 2AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 20 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 20 | 3AM to 4AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 20 | 4AM to 5AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 20 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 20 | 6AM to 7AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 20 | 7AM to 8AM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
October | 20 | 8AM to 9AM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
October | 20 | 9AM to 10AM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
October | 20 | 10AM to 11AM | 68 | 58.3 | 51.8 | 57.4 | 25.27 | 0.0748 | 0.39 | 13.48 | 0
October | 20 | 11AM to 12PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
October | 20 | 12PM to 1PM | 71.6 | 59.6 | 51.8 | 57.4 | 26.15 | 0.0743 | 0.39 | 13.58 | 0
October | 20 | 1PM to 2PM | 75.2 | 60.9 | 51.8 | 57.4 | 27.02 | 0.0738 | 0.39 | 13.67 | 0
October | 20 | 2PM to 3PM | 75.2 | 61.8 | 53.6 | 61.4 | 27.65 | 0.0737 | 0.41 | 13.68 | 0
October | 20 | 3PM to 4PM | 73.4 | 61.2 | 53.6 | 61.4 | 27.21 | 0.074 | 0.41 | 13.63 | 0
October | 20 | 4PM to 5PM | 69.8 | 61.8 | 57.2 | 70.1 | 27.69 | 0.0744 | 0.47 | 13.57 | 0
October | 20 | 5PM to 6PM | 68 | 55 | 44.6 | 43.7 | 23.13 | 0.0749 | 0.3 | 13.44 | 0
October | 20 | 6PM to 7PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
October | 20 | 7PM to 8PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
October | 20 | 8PM to 9PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
October | 20 | 9PM to 10PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
October | 20 | 10PM to 11PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
October | 20 | 11PM to 12AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
October | 21 | 12AM to 1AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
October | 21 | 1AM to 2AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
October | 21 | 2AM to 3AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
October | 21 | 3AM to 4AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
October | 21 | 4AM to 5AM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
October | 21 | 5AM to 6AM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
October | 21 | 6AM to 7AM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
October | 21 | 7AM to 8AM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
October | 21 | 8AM to 9AM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
October | 21 | 9AM to 10AM | 64.4 | 50 | 35.6 | 30.7 | 20.23 | 0.0755 | 0.21 | 13.31 | 0
October | 21 | 10AM to 11AM | 68 | 51 | 33.8 | 28.6 | 20.77 | 0.075 | 0.19 | 13.4 | 0
October | 21 | 11AM to 12PM | 69.8 | 51.7 | 33.8 | 28.6 | 21.21 | 0.0747 | 0.19 | 13.44 | 0
October | 21 | 12PM to 1PM | 71.6 | 52.5 | 33.8 | 28.6 | 21.64 | 0.0744 | 0.19 | 13.49 | 0
October | 21 | 1PM to 2PM | 71.6 | 52 | 32 | 26.6 | 21.33 | 0.0745 | 0.18 | 13.48 | 0
October | 21 | 2PM to 3PM | 71.6 | 52 | 32 | 26.6 | 21.33 | 0.0745 | 0.18 | 13.48 | 0
October | 21 | 3PM to 4PM | 69.8 | 50.6 | 30.2 | 24.4 | 20.56 | 0.0747 | 0.17 | 13.43 | 0
October | 21 | 4PM to 5PM | 66.2 | 49.6 | 32 | 26.6 | 20.02 | 0.0752 | 0.18 | 13.34 | 0
October | 21 | 5PM to 6PM | 64.4 | 48.2 | 30.2 | 24.4 | 19.26 | 0.0755 | 0.17 | 13.29 | 0
October | 21 | 6PM to 7PM | 62.6 | 48 | 32 | 26.6 | 19.15 | 0.0757 | 0.18 | 13.25 | 0
October | 21 | 7PM to 8PM | 62.6 | 46.8 | 28.4 | 22.5 | 18.52 | 0.0758 | 0.15 | 13.24 | 0
October | 21 | 8PM to 9PM | 60.8 | 46.5 | 30.2 | 24.4 | 18.39 | 0.076 | 0.17 | 13.2 | 0
October | 21 | 9PM to 10PM | 59 | 45.7 | 30.2 | 24.4 | 17.95 | 0.0763 | 0.17 | 13.15 | 0
October | 21 | 10PM to 11PM | 57.2 | 45.5 | 32 | 26.6 | 17.85 | 0.0765 | 0.18 | 13.12 | 0
October | 21 | 11PM to 12AM | 57.2 | 44.8 | 30.2 | 24.4 | 17.52 | 0.0765 | 0.17 | 13.11 | 0
October | 22 | 12AM to 1AM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
October | 22 | 1AM to 2AM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
October | 22 | 2AM to 3AM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
October | 22 | 3AM to 4AM | 55.4 | 43.3 | 28.4 | 22.5 | 16.78 | 0.0768 | 0.15 | 13.06 | 0
October | 22 | 4AM to 5AM | 55.4 | 42.7 | 26.6 | 20.7 | 16.5 | 0.0768 | 0.14 | 13.05 | 0
October | 22 | 5AM to 6AM | 55.4 | 42.7 | 26.6 | 20.7 | 16.5 | 0.0768 | 0.14 | 13.05 | 0
October | 22 | 6AM to 7AM | 55.4 | 42.2 | 24.8 | 19 | 16.24 | 0.0769 | 0.13 | 13.05 | 0
October | 22 | 7AM to 8AM | 59 | 44 | 24.8 | 19 | 17.11 | 0.0763 | 0.13 | 13.14 | 0
October | 22 | 8AM to 9AM | 62.6 | 45.7 | 24.8 | 19 | 17.98 | 0.0758 | 0.13 | 13.23 | 0
October | 22 | 9AM to 10AM | 66.2 | 46.5 | 21.2 | 16 | 18.38 | 0.0753 | 0.11 | 13.31 | 0
October | 22 | 10AM to 11AM | 68 | 47 | 19.4 | 14.7 | 18.6 | 0.075 | 0.1 | 13.35 | 0
October | 22 | 11AM to 12PM | 71.6 | 49 | 21.2 | 16 | 19.68 | 0.0745 | 0.11 | 13.45 | 0
October | 22 | 12PM to 1PM | 73.4 | 49.8 | 21.2 | 16 | 20.11 | 0.0743 | 0.11 | 13.49 | 0
October | 22 | 1PM to 2PM | 73.4 | 49.8 | 21.2 | 16 | 20.11 | 0.0743 | 0.11 | 13.49 | 0
October | 22 | 2PM to 3PM | 73.4 | 49.8 | 21.2 | 16 | 20.11 | 0.0743 | 0.11 | 13.49 | 0
October | 22 | 3PM to 4PM | 71.6 | 49 | 21.2 | 16 | 19.68 | 0.0745 | 0.11 | 13.45 | 0
October | 22 | 4PM to 5PM | 69.8 | 49.1 | 24.8 | 19 | 19.71 | 0.0748 | 0.13 | 13.41 | 0
October | 22 | 5PM to 6PM | 66.2 | 47.4 | 24.8 | 19 | 18.84 | 0.0753 | 0.13 | 13.32 | 0
October | 22 | 6PM to 7PM | 64.4 | 46.1 | 23 | 17.4 | 18.17 | 0.0755 | 0.12 | 13.27 | 0
October | 22 | 7PM to 8PM | 64.4 | 45.7 | 21.2 | 16 | 17.94 | 0.0756 | 0.11 | 13.27 | 0
October | 22 | 8PM to 9PM | 64.4 | 45.3 | 19.4 | 14.7 | 17.74 | 0.0756 | 0.1 | 13.26 | 0
October | 22 | 9PM to 10PM | 62.6 | 44.4 | 19.4 | 14.7 | 17.3 | 0.0758 | 0.1 | 13.22 | 0
October | 22 | 10PM to 11PM | 62.6 | 45.3 | 23 | 17.4 | 17.73 | 0.0758 | 0.12 | 13.22 | 0
October | 22 | 11PM to 12AM | 57.2 | 43.1 | 24.8 | 19 | 16.67 | 0.0766 | 0.13 | 13.09 | 0
October | 23 | 12AM to 1AM | 55.4 | 42.2 | 24.8 | 19 | 16.24 | 0.0769 | 0.13 | 13.05 | 0
October | 23 | 1AM to 2AM | 53.6 | 41.3 | 24.8 | 19 | 15.8 | 0.0771 | 0.13 | 13 | 0
October | 23 | 2AM to 3AM | 48.2 | 38.4 | 24.8 | 19 | 14.5 | 0.0779 | 0.13 | 12.86 | 1
October | 23 | 3AM to 4AM | 48.2 | 38.4 | 24.8 | 19 | 14.5 | 0.0779 | 0.13 | 12.86 | 1
October | 23 | 4AM to 5AM | 48.2 | 39 | 26.6 | 20.7 | 14.76 | 0.0779 | 0.14 | 12.87 | 1
October | 23 | 5AM to 6AM | 42.8 | 35.5 | 24.8 | 19 | 13.2 | 0.0788 | 0.13 | 12.73 | 1
October | 23 | 6AM to 7AM | 42.8 | 36.7 | 28.4 | 22.5 | 13.74 | 0.0788 | 0.15 | 12.74 | 1
October | 23 | 7AM to 8AM | 51.8 | 41.5 | 28.4 | 22.5 | 15.91 | 0.0774 | 0.15 | 12.97 | 1
October | 23 | 8AM to 9AM | 60.8 | 45.9 | 28.4 | 22.5 | 18.08 | 0.076 | 0.15 | 13.19 | 0
October | 23 | 9AM to 10AM | 64.4 | 47.6 | 28.4 | 22.5 | 18.95 | 0.0755 | 0.15 | 13.29 | 0
October | 23 | 10AM to 11AM | 69.8 | 50.6 | 30.2 | 24.4 | 20.56 | 0.0747 | 0.17 | 13.43 | 0
October | 23 | 11AM to 12PM | 73.4 | 52.2 | 30.2 | 24.4 | 21.43 | 0.0742 | 0.17 | 13.52 | 0
October | 23 | 12PM to 1PM | 75.2 | 52.9 | 30.2 | 24.4 | 21.87 | 0.074 | 0.17 | 13.57 | 0
October | 23 | 1PM to 2PM | 77 | 53.1 | 28.4 | 22.5 | 22 | 0.0737 | 0.15 | 13.61 | 0
October | 23 | 2PM to 3PM | 78.4 | 53.7 | 28.4 | 22.5 | 22.34 | 0.0735 | 0.15 | 13.64 | 0
October | 23 | 3PM to 4PM | 78.8 | 53.9 | 28.4 | 22.5 | 22.43 | 0.0735 | 0.15 | 13.65 | 0
October | 23 | 4PM to 5PM | 73.4 | 51.6 | 28.4 | 22.5 | 21.13 | 0.0742 | 0.15 | 13.51 | 0
October | 23 | 5PM to 6PM | 69.8 | 50.6 | 30.2 | 24.4 | 20.56 | 0.0747 | 0.17 | 13.43 | 0
October | 23 | 6PM to 7PM | 60.8 | 46.5 | 30.2 | 24.4 | 18.39 | 0.076 | 0.17 | 13.2 | 0
October | 23 | 7PM to 8PM | 62.6 | 47.4 | 30.2 | 24.4 | 18.82 | 0.0758 | 0.17 | 13.25 | 0
October | 23 | 8PM to 9PM | 57.2 | 44.8 | 30.2 | 24.4 | 17.52 | 0.0765 | 0.17 | 13.11 | 0
October | 23 | 9PM to 10PM | 55.4 | 43.9 | 30.2 | 24.4 | 17.09 | 0.0768 | 0.17 | 13.06 | 0
October | 23 | 10PM to 11PM | 53.6 | 43 | 30.2 | 24.4 | 16.65 | 0.0771 | 0.17 | 13.02 | 0
October | 23 | 11PM to 12AM | 55.4 | 43.9 | 30.2 | 24.4 | 17.09 | 0.0768 | 0.17 | 13.06 | 0
October | 24 | 12AM to 1AM | 55.4 | 43.9 | 30.2 | 24.4 | 17.09 | 0.0768 | 0.17 | 13.06 | 0
October | 24 | 1AM to 2AM | 53.6 | 43 | 30.2 | 24.4 | 16.65 | 0.0771 | 0.17 | 13.02 | 0
October | 24 | 2AM to 3AM | 51.8 | 42.1 | 30.2 | 24.4 | 16.22 | 0.0774 | 0.17 | 12.97 | 1
October | 24 | 3AM to 4AM | 51.8 | 42.1 | 30.2 | 24.4 | 16.22 | 0.0774 | 0.17 | 12.97 | 1
October | 24 | 4AM to 5AM | 46.4 | 39.3 | 30.2 | 24.4 | 14.91 | 0.0782 | 0.17 | 12.84 | 1
October | 24 | 5AM to 6AM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
October | 24 | 6AM to 7AM | 44.6 | 38.4 | 30.2 | 24.4 | 14.48 | 0.0785 | 0.17 | 12.79 | 1
October | 24 | 7AM to 8AM | 53.6 | 43 | 30.2 | 24.4 | 16.65 | 0.0771 | 0.17 | 13.02 | 0
October | 24 | 8AM to 9AM | 60.8 | 45.9 | 28.4 | 22.5 | 18.08 | 0.076 | 0.15 | 13.19 | 0
October | 24 | 9AM to 10AM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
October | 24 | 10AM to 11AM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
October | 24 | 11AM to 12PM | 73.4 | 62.1 | 55.4 | 65.6 | 27.87 | 0.074 | 0.44 | 13.65 | 0
October | 24 | 12PM to 1PM | 73.4 | 56.4 | 42.8 | 40.8 | 23.98 | 0.0741 | 0.28 | 13.57 | 0
October | 24 | 1PM to 2PM | 77 | 57.8 | 42.8 | 40.8 | 24.86 | 0.0736 | 0.28 | 13.66 | 0
October | 24 | 2PM to 3PM | 77 | 57.1 | 41 | 38 | 24.42 | 0.0736 | 0.26 | 13.65 | 0
October | 24 | 3PM to 4PM | 77 | 57.1 | 41 | 38 | 24.42 | 0.0736 | 0.26 | 13.65 | 0
October | 24 | 4PM to 5PM | 73.4 | 53.8 | 35.6 | 30.7 | 22.41 | 0.0742 | 0.21 | 13.54 | 0
October | 24 | 5PM to 6PM | 64.4 | 50 | 35.6 | 30.7 | 20.23 | 0.0755 | 0.21 | 13.31 | 0
October | 24 | 6PM to 7PM | 64.4 | 50 | 35.6 | 30.7 | 20.23 | 0.0755 | 0.21 | 13.31 | 0
October | 24 | 7PM to 8PM | 62.6 | 49.8 | 37.4 | 33 | 20.15 | 0.0757 | 0.22 | 13.27 | 0
October | 24 | 8PM to 9PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
October | 24 | 9PM to 10PM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
October | 24 | 10PM to 11PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
October | 24 | 11PM to 12AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
October | 25 | 12AM to 1AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 25 | 1AM to 2AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
October | 25 | 2AM to 3AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
October | 25 | 3AM to 4AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 25 | 4AM to 5AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 25 | 5AM to 6AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 25 | 6AM to 7AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 25 | 7AM to 8AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
October | 25 | 8AM to 9AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
October | 25 | 9AM to 10AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
October | 25 | 10AM to 11AM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
October | 25 | 11AM to 12PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 25 | 12PM to 1PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 25 | 1PM to 2PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
October | 25 | 2PM to 3PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
October | 25 | 3PM to 4PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
October | 25 | 4PM to 5PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
October | 25 | 5PM to 6PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 25 | 6PM to 7PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 25 | 7PM to 8PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 25 | 8PM to 9PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 25 | 9PM to 10PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 25 | 10PM to 11PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 25 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 26 | 12AM to 1AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 26 | 1AM to 2AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
October | 26 | 2AM to 3AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
October | 26 | 3AM to 4AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 26 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 26 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 26 | 6AM to 7AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 26 | 7AM to 8AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 26 | 8AM to 9AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 26 | 9AM to 10AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 26 | 10AM to 11AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 26 | 11AM to 12PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 26 | 12PM to 1PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 26 | 1PM to 2PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
October | 26 | 2PM to 3PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 26 | 3PM to 4PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 26 | 4PM to 5PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 26 | 5PM to 6PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 26 | 6PM to 7PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 26 | 7PM to 8PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 26 | 8PM to 9PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 26 | 9PM to 10PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 26 | 10PM to 11PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 26 | 11PM to 12AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 27 | 12AM to 1AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 27 | 1AM to 2AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 27 | 2AM to 3AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
October | 27 | 3AM to 4AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
October | 27 | 4AM to 5AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
October | 27 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 27 | 6AM to 7AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 27 | 7AM to 8AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 27 | 8AM to 9AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 27 | 9AM to 10AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 27 | 10AM to 11AM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
October | 27 | 11AM to 12PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
October | 27 | 12PM to 1PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
October | 27 | 1PM to 2PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
October | 27 | 2PM to 3PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
October | 27 | 3PM to 4PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
October | 27 | 4PM to 5PM | 66.2 | 55.8 | 48.2 | 50.1 | 23.7 | 0.0751 | 0.34 | 13.42 | 0
October | 27 | 5PM to 6PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
October | 27 | 6PM to 7PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
October | 27 | 7PM to 8PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
October | 27 | 8PM to 9PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 27 | 9PM to 10PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
October | 27 | 10PM to 11PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 27 | 11PM to 12AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 28 | 12AM to 1AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 28 | 1AM to 2AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 28 | 2AM to 3AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 28 | 3AM to 4AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 28 | 4AM to 5AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 28 | 5AM to 6AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 28 | 6AM to 7AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 28 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 28 | 8AM to 9AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 28 | 9AM to 10AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 28 | 10AM to 11AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 28 | 11AM to 12PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 28 | 12PM to 1PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 28 | 1PM to 2PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
October | 28 | 2PM to 3PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
October | 28 | 3PM to 4PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
October | 28 | 4PM to 5PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
October | 28 | 5PM to 6PM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
October | 28 | 6PM to 7PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 28 | 7PM to 8PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 28 | 8PM to 9PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
October | 28 | 9PM to 10PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 28 | 10PM to 11PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 28 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 29 | 12AM to 1AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 29 | 1AM to 2AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 29 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 29 | 3AM to 4AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 29 | 4AM to 5AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 29 | 5AM to 6AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 29 | 6AM to 7AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 29 | 7AM to 8AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 29 | 8AM to 9AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 29 | 9AM to 10AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 29 | 10AM to 11AM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
October | 29 | 11AM to 12PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
October | 29 | 12PM to 1PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
October | 29 | 1PM to 2PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
October | 29 | 2PM to 3PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
October | 29 | 3PM to 4PM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
October | 29 | 4PM to 5PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
October | 29 | 5PM to 6PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
October | 29 | 6PM to 7PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
October | 29 | 7PM to 8PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
October | 29 | 8PM to 9PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
October | 29 | 9PM to 10PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 29 | 10PM to 11PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 29 | 11PM to 12AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 30 | 12AM to 1AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 30 | 1AM to 2AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
October | 30 | 2AM to 3AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 30 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 30 | 4AM to 5AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 30 | 5AM to 6AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 30 | 6AM to 7AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 30 | 7AM to 8AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
October | 30 | 8AM to 9AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 30 | 9AM to 10AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 30 | 10AM to 11AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
October | 30 | 11AM to 12PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 30 | 12PM to 1PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
October | 30 | 1PM to 2PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 30 | 2PM to 3PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
October | 30 | 3PM to 4PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
October | 30 | 4PM to 5PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
October | 30 | 5PM to 6PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
October | 30 | 6PM to 7PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
October | 30 | 7PM to 8PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
October | 30 | 8PM to 9PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
October | 30 | 9PM to 10PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
October | 30 | 10PM to 11PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
October | 30 | 11PM to 12AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 31 | 12AM to 1AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 31 | 1AM to 2AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 31 | 2AM to 3AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
October | 31 | 3AM to 4AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
October | 31 | 4AM to 5AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
October | 31 | 5AM to 6AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
October | 31 | 6AM to 7AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
October | 31 | 7AM to 8AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
October | 31 | 8AM to 9AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
October | 31 | 9AM to 10AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
October | 31 | 10AM to 11AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
October | 31 | 11AM to 12PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
October | 31 | 12PM to 1PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
October | 31 | 1PM to 2PM | 64.4 | 52 | 41 | 38 | 21.37 | 0.0754 | 0.26 | 13.33 | 0
October | 31 | 2PM to 3PM | 66.2 | 53.5 | 42.8 | 40.8 | 22.24 | 0.0751 | 0.28 | 13.39 | 0
October | 31 | 3PM to 4PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
October | 31 | 4PM to 5PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
October | 31 | 5PM to 6PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
October | 31 | 6PM to 7PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
October | 31 | 7PM to 8PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
October | 31 | 8PM to 9PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
October | 31 | 9PM to 10PM | 50.5 | 45.5 | 40.5 | 37.2 | 17.89 | 0.0775 | 0.25 | 12.98 | 1
October | 31 | 10PM to 11PM | 49.3 | 43.1 | 36.3 | 31.6 | 16.71 | 0.0777 | 0.21 | 12.93 | 1
October | 31 | 11PM to 12AM | 48 | 40.9 | 32.2 | 26.7 | 15.66 | 0.0779 | 0.18 | 12.88 | 1
November | 1 | 12AM to 1AM | 46.6 | 38.8 | 28.4 | 22.5 | 14.65 | 0.0782 | 0.15 | 12.83 | 1
November | 1 | 1AM to 2AM | 45.3 | 36.7 | 24.3 | 18.5 | 13.73 | 0.0784 | 0.13 | 12.79 | 1
November | 1 | 2AM to 3AM | 44.1 | 34.8 | 20.1 | 15.2 | 12.92 | 0.0786 | 0.1 | 12.75 | 1
November | 1 | 3AM to 4AM | 42.8 | 33 | 15.8 | 12.3 | 12.17 | 0.0788 | 0.08 | 12.71 | 1
November | 1 | 4AM to 5AM | 42.8 | 33 | 15.8 | 12.3 | 12.17 | 0.0788 | 0.08 | 12.71 | 1
November | 1 | 5AM to 6AM | 35.6 | 28.3 | 15.8 | 12.3 | 10.44 | 0.08 | 0.08 | 12.53 | 1
November | 1 | 6AM to 7AM | 35.6 | 28.8 | 17.6 | 13.4 | 10.61 | 0.08 | 0.09 | 12.53 | 1
November | 1 | 7AM to 8AM | 46.4 | 35.1 | 15.8 | 12.3 | 13.04 | 0.0783 | 0.08 | 12.8 | 1
November | 1 | 8AM to 9AM | 51.8 | 37.4 | 12.2 | 10.3 | 14.03 | 0.0775 | 0.07 | 12.93 | 1
November | 1 | 9AM to 10AM | 57.2 | 40.6 | 14 | 11.3 | 15.47 | 0.0766 | 0.08 | 13.07 | 0
November | 1 | 10AM to 11AM | 60.8 | 41.8 | 10.4 | 9.4 | 16.05 | 0.0761 | 0.06 | 13.16 | 0
November | 1 | 11AM to 12PM | 62.6 | 42.7 | 10.4 | 9.4 | 16.49 | 0.0759 | 0.06 | 13.2 | 0
November | 1 | 12PM to 1PM | 64.4 | 43.6 | 10.4 | 9.4 | 16.92 | 0.0756 | 0.06 | 13.25 | 0
November | 1 | 1PM to 2PM | 66.2 | 44.5 | 10.4 | 9.4 | 17.35 | 0.0753 | 0.06 | 13.29 | 0
November | 1 | 2PM to 3PM | 66.2 | 44.5 | 10.4 | 9.4 | 17.35 | 0.0753 | 0.06 | 13.29 | 0
November | 1 | 3PM to 4PM | 66.2 | 44.8 | 12.2 | 10.3 | 17.49 | 0.0753 | 0.07 | 13.29 | 0
November | 1 | 4PM to 5PM | 60.8 | 42.4 | 14 | 11.3 | 16.34 | 0.0761 | 0.08 | 13.16 | 0
November | 1 | 5PM to 6PM | 55.4 | 40.4 | 17.6 | 13.4 | 15.38 | 0.0769 | 0.09 | 13.03 | 0
November | 1 | 6PM to 7PM | 51.8 | 38.5 | 17.6 | 13.4 | 14.51 | 0.0774 | 0.09 | 12.94 | 1
November | 1 | 7PM to 8PM | 50 | 37.9 | 19.4 | 14.7 | 14.27 | 0.0777 | 0.1 | 12.9 | 1
November | 1 | 8PM to 9PM | 48.2 | 37.9 | 23 | 17.4 | 14.26 | 0.078 | 0.12 | 12.86 | 1
November | 1 | 9PM to 10PM | 42.8 | 33.9 | 19.4 | 14.7 | 12.53 | 0.0788 | 0.1 | 12.72 | 1
November | 1 | 10PM to 11PM | 44.6 | 36.5 | 24.8 | 19 | 13.63 | 0.0785 | 0.13 | 12.77 | 1
November | 1 | 11PM to 12AM | 41 | 33.9 | 23 | 17.4 | 12.53 | 0.0791 | 0.12 | 12.68 | 1
November | 2 | 12AM to 1AM | 35.6 | 29.8 | 21.2 | 16 | 11 | 0.0799 | 0.11 | 12.54 | 1
November | 2 | 1AM to 2AM | 41 | 34.4 | 24.8 | 19 | 12.77 | 0.0791 | 0.13 | 12.68 | 1
November | 2 | 2AM to 3AM | 33.8 | 29.4 | 23 | 17.4 | 10.79 | 0.0802 | 0.12 | 12.5 | 1
November | 2 | 3AM to 4AM | 33.8 | 30 | 24.8 | 19 | 11.03 | 0.0802 | 0.13 | 12.5 | 1
November | 2 | 4AM to 5AM | 32 | 27.8 | 21.2 | 16 | 10.13 | 0.0805 | 0.11 | 12.45 | 1
November | 2 | 5AM to 6AM | 35.6 | 29.8 | 21.2 | 16 | 11 | 0.0799 | 0.11 | 12.54 | 1
November | 2 | 6AM to 7AM | 30.2 | 26.7 | 21.2 | 16 | 9.7 | 0.0808 | 0.11 | 12.4 | 1
November | 2 | 7AM to 8AM | 42.8 | 35.5 | 24.8 | 19 | 13.2 | 0.0788 | 0.13 | 12.73 | 1
November | 2 | 8AM to 9AM | 48.2 | 37.4 | 21.2 | 16 | 14.04 | 0.078 | 0.11 | 12.86 | 1
November | 2 | 9AM to 10AM | 55.4 | 40.8 | 19.4 | 14.7 | 15.57 | 0.0769 | 0.1 | 13.03 | 0
November | 2 | 10AM to 11AM | 60.8 | 43.5 | 19.4 | 14.7 | 16.87 | 0.0761 | 0.1 | 13.17 | 0
November | 2 | 11AM to 12PM | 61.2 | 43.8 | 19.8 | 14.9 | 17 | 0.076 | 0.1 | 13.18 | 0
November | 2 | 12PM to 1PM | 60.8 | 43.5 | 19.4 | 14.7 | 16.87 | 0.0761 | 0.1 | 13.17 | 0
November | 2 | 1PM to 2PM | 64.4 | 46.6 | 24.8 | 19 | 18.41 | 0.0755 | 0.13 | 13.28 | 0
November | 2 | 2PM to 3PM | 66.2 | 46.5 | 21.2 | 16 | 18.38 | 0.0753 | 0.11 | 13.31 | 0
November | 2 | 3PM to 4PM | 69.8 | 48.2 | 21.2 | 16 | 19.24 | 0.0748 | 0.11 | 13.4 | 0
November | 2 | 4PM to 5PM | 62.6 | 44.4 | 19.4 | 14.7 | 17.3 | 0.0758 | 0.1 | 13.22 | 0
November | 2 | 5PM to 6PM | 57.2 | 42.6 | 23 | 17.4 | 16.43 | 0.0766 | 0.12 | 13.09 | 0
November | 2 | 6PM to 7PM | 55.4 | 42.2 | 24.8 | 19 | 16.24 | 0.0769 | 0.13 | 13.05 | 0
November | 2 | 7PM to 8PM | 55.4 | 43.9 | 30.2 | 24.4 | 17.09 | 0.0768 | 0.17 | 13.06 | 0
November | 2 | 8PM to 9PM | 50 | 42.5 | 33.8 | 28.6 | 16.42 | 0.0776 | 0.19 | 12.94 | 1
November | 2 | 9PM to 10PM | 48.2 | 41.6 | 33.8 | 28.6 | 15.98 | 0.0779 | 0.19 | 12.89 | 1
November | 2 | 10PM to 11PM | 42.8 | 37.4 | 30.2 | 24.4 | 14.04 | 0.0787 | 0.17 | 12.74 | 1
November | 2 | 11PM to 12AM | 42.8 | 37.4 | 30.2 | 24.4 | 14.04 | 0.0787 | 0.17 | 12.74 | 1
November | 3 | 12AM to 1AM | 41 | 37.1 | 32 | 26.6 | 13.93 | 0.079 | 0.18 | 12.7 | 1
November | 3 | 1AM to 2AM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
November | 3 | 2AM to 3AM | 39.2 | 36.1 | 32 | 26.6 | 13.5 | 0.0793 | 0.18 | 12.66 | 1
November | 3 | 3AM to 4AM | 35.6 | 34.1 | 32 | 26.6 | 12.63 | 0.0799 | 0.18 | 12.57 | 1
November | 3 | 4AM to 5AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
November | 3 | 5AM to 6AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
November | 3 | 6AM to 7AM | 42.8 | 39.5 | 35.6 | 30.7 | 15.01 | 0.0787 | 0.21 | 12.76 | 1
November | 3 | 7AM to 8AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
November | 3 | 8AM to 9AM | 48.2 | 42.3 | 35.6 | 30.7 | 16.31 | 0.0779 | 0.21 | 12.9 | 1
November | 3 | 9AM to 10AM | 55.4 | 45.2 | 33.8 | 28.6 | 17.72 | 0.0768 | 0.19 | 13.08 | 0
November | 3 | 10AM to 11AM | 60.8 | 48.4 | 35.6 | 30.7 | 19.36 | 0.076 | 0.21 | 13.22 | 0
November | 3 | 11AM to 12PM | 62.6 | 46.2 | 26.6 | 20.7 | 18.24 | 0.0758 | 0.14 | 13.23 | 0
November | 3 | 12PM to 1PM | 66.2 | 47.9 | 26.6 | 20.7 | 19.11 | 0.0753 | 0.14 | 13.33 | 0
November | 3 | 1PM to 2PM | 68 | 48.3 | 24.8 | 19 | 19.28 | 0.075 | 0.13 | 13.37 | 0
November | 3 | 2PM to 3PM | 69.8 | 48.2 | 21.2 | 16 | 19.24 | 0.0748 | 0.11 | 13.4 | 0
November | 3 | 3PM to 4PM | 69.8 | 48.2 | 21.2 | 16 | 19.24 | 0.0748 | 0.11 | 13.4 | 0
November | 3 | 4PM to 5PM | 66.2 | 47 | 23 | 17.4 | 18.6 | 0.0753 | 0.12 | 13.32 | 0
November | 3 | 5PM to 6PM | 60.8 | 44.9 | 24.8 | 19 | 17.54 | 0.0761 | 0.13 | 13.18 | 0
November | 3 | 6PM to 7PM | 53.6 | 42.4 | 28.4 | 22.5 | 16.35 | 0.0771 | 0.15 | 13.01 | 0
November | 3 | 7PM to 8PM | 51.8 | 38.9 | 19.4 | 14.7 | 14.7 | 0.0774 | 0.1 | 12.94 | 1
November | 3 | 8PM to 9PM | 46.4 | 38 | 26.6 | 20.7 | 14.33 | 0.0782 | 0.14 | 12.82 | 1
November | 3 | 9PM to 10PM | 46.4 | 38 | 26.6 | 20.7 | 14.33 | 0.0782 | 0.14 | 12.82 | 1
November | 3 | 10PM to 11PM | 42.8 | 34.4 | 21.2 | 16 | 12.74 | 0.0788 | 0.11 | 12.72 | 1
November | 3 | 11PM to 12AM | 42.8 | 36.1 | 26.6 | 20.7 | 13.46 | 0.0788 | 0.14 | 12.73 | 1
November | 4 | 12AM to 1AM | 39.2 | 33.4 | 24.8 | 19 | 12.33 | 0.0793 | 0.13 | 12.64 | 1
November | 4 | 1AM to 2AM | 37.4 | 32.3 | 24.8 | 19 | 11.9 | 0.0796 | 0.13 | 12.59 | 1
November | 4 | 2AM to 3AM | 37.4 | 33.6 | 28.4 | 22.5 | 12.44 | 0.0796 | 0.15 | 12.6 | 1
November | 4 | 3AM to 4AM | 35.6 | 31 | 24.8 | 19 | 11.46 | 0.0799 | 0.13 | 12.55 | 1
November | 4 | 4AM to 5AM | 37.4 | 33.6 | 28.4 | 22.5 | 12.44 | 0.0796 | 0.15 | 12.6 | 1
November | 4 | 5AM to 6AM | 37.4 | 34.4 | 30.2 | 24.4 | 12.74 | 0.0796 | 0.17 | 12.61 | 1
November | 4 | 6AM to 7AM | 37.4 | 34.4 | 30.2 | 24.4 | 12.74 | 0.0796 | 0.17 | 12.61 | 1
November | 4 | 7AM to 8AM | 44.6 | 38.4 | 30.2 | 24.4 | 14.48 | 0.0785 | 0.17 | 12.79 | 1
November | 4 | 8AM to 9AM | 53.6 | 43 | 30.2 | 24.4 | 16.65 | 0.0771 | 0.17 | 13.02 | 0
November | 4 | 9AM to 10AM | 57.2 | 44.8 | 30.2 | 24.4 | 17.52 | 0.0765 | 0.17 | 13.11 | 0
November | 4 | 10AM to 11AM | 62.6 | 47.4 | 30.2 | 24.4 | 18.82 | 0.0758 | 0.17 | 13.25 | 0
November | 4 | 11AM to 12PM | 64.4 | 48.2 | 30.2 | 24.4 | 19.26 | 0.0755 | 0.17 | 13.29 | 0
November | 4 | 12PM to 1PM | 66.2 | 49 | 30.2 | 24.4 | 19.69 | 0.0752 | 0.17 | 13.34 | 0
November | 4 | 1PM to 2PM | 69.8 | 50.6 | 30.2 | 24.4 | 20.56 | 0.0747 | 0.17 | 13.43 | 0
November | 4 | 2PM to 3PM | 71.6 | 51.4 | 30.2 | 24.4 | 21 | 0.0745 | 0.17 | 13.47 | 0
November | 4 | 3PM to 4PM | 69.8 | 50.6 | 30.2 | 24.4 | 20.56 | 0.0747 | 0.17 | 13.43 | 0
November | 4 | 4PM to 5PM | 64.4 | 48.2 | 30.2 | 24.4 | 19.26 | 0.0755 | 0.17 | 13.29 | 0
November | 4 | 5PM to 6PM | 60.8 | 46.5 | 30.2 | 24.4 | 18.39 | 0.076 | 0.17 | 13.2 | 0
November | 4 | 6PM to 7PM | 55.4 | 43.9 | 30.2 | 24.4 | 17.09 | 0.0768 | 0.17 | 13.06 | 0
November | 4 | 7PM to 8PM | 55.4 | 43.9 | 30.2 | 24.4 | 17.09 | 0.0768 | 0.17 | 13.06 | 0
November | 4 | 8PM to 9PM | 51.8 | 42.1 | 30.2 | 24.4 | 16.22 | 0.0774 | 0.17 | 12.97 | 1
November | 4 | 9PM to 10PM | 44.6 | 38.4 | 30.2 | 24.4 | 14.48 | 0.0785 | 0.17 | 12.79 | 1
November | 4 | 10PM to 11PM | 50 | 41.9 | 32 | 26.6 | 16.11 | 0.0776 | 0.18 | 12.93 | 1
November | 4 | 11PM to 12AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
November | 5 | 12AM to 1AM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
November | 5 | 1AM to 2AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
November | 5 | 2AM to 3AM | 42.8 | 38.8 | 33.8 | 28.6 | 14.68 | 0.0787 | 0.19 | 12.76 | 1
November | 5 | 3AM to 4AM | 37.4 | 34.4 | 30.2 | 24.4 | 12.74 | 0.0796 | 0.17 | 12.61 | 1
November | 5 | 4AM to 5AM | 37.4 | 35.1 | 32 | 26.6 | 13.06 | 0.0796 | 0.18 | 12.61 | 1
November | 5 | 5AM to 6AM | 37.4 | 34.4 | 30.2 | 24.4 | 12.74 | 0.0796 | 0.17 | 12.61 | 1
November | 5 | 6AM to 7AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
November | 5 | 7AM to 8AM | 42.8 | 38.8 | 33.8 | 28.6 | 14.68 | 0.0787 | 0.19 | 12.76 | 1
November | 5 | 8AM to 9AM | 51.8 | 44.1 | 35.6 | 30.7 | 17.18 | 0.0773 | 0.21 | 12.99 | 1
November | 5 | 9AM to 10AM | 57.2 | 46.7 | 35.6 | 30.7 | 18.49 | 0.0765 | 0.21 | 13.13 | 0
November | 5 | 10AM to 11AM | 62.6 | 48.6 | 33.8 | 28.6 | 19.47 | 0.0757 | 0.19 | 13.26 | 0
November | 5 | 11AM to 12PM | 64.4 | 50 | 35.6 | 30.7 | 20.23 | 0.0755 | 0.21 | 13.31 | 0
November | 5 | 12PM to 1PM | 66.2 | 52 | 39.2 | 35.4 | 21.4 | 0.0752 | 0.24 | 13.37 | 0
November | 5 | 1PM to 2PM | 68 | 52.8 | 39.2 | 35.4 | 21.84 | 0.0749 | 0.24 | 13.42 | 0
November | 5 | 2PM to 3PM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
November | 5 | 3PM to 4PM | 69.8 | 52.9 | 37.4 | 33 | 21.9 | 0.0747 | 0.22 | 13.45 | 0
November | 5 | 4PM to 5PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
November | 5 | 5PM to 6PM | 59 | 48.9 | 39.2 | 35.4 | 19.66 | 0.0762 | 0.24 | 13.19 | 0
November | 5 | 6PM to 7PM | 55.4 | 45.9 | 35.6 | 30.7 | 18.06 | 0.0768 | 0.21 | 13.08 | 0
November | 5 | 7PM to 8PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
November | 5 | 8PM to 9PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
November | 5 | 9PM to 10PM | 44.6 | 38.4 | 30.2 | 24.4 | 14.48 | 0.0785 | 0.17 | 12.79 | 1
November | 5 | 10PM to 11PM | 42.8 | 37.4 | 30.2 | 24.4 | 14.04 | 0.0787 | 0.17 | 12.74 | 1
November | 5 | 11PM to 12AM | 42.8 | 37.4 | 30.2 | 24.4 | 14.04 | 0.0787 | 0.17 | 12.74 | 1
November | 6 | 12AM to 1AM | 42.8 | 38.8 | 33.8 | 28.6 | 14.68 | 0.0787 | 0.19 | 12.76 | 1
November | 6 | 1AM to 2AM | 42.8 | 39.5 | 35.6 | 30.7 | 15.01 | 0.0787 | 0.21 | 12.76 | 1
November | 6 | 2AM to 3AM | 41 | 36.4 | 30.2 | 24.4 | 13.61 | 0.079 | 0.17 | 12.7 | 1
November | 6 | 3AM to 4AM | 37.4 | 33.6 | 28.4 | 22.5 | 12.44 | 0.0796 | 0.15 | 12.6 | 1
November | 6 | 4AM to 5AM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
November | 6 | 5AM to 6AM | 37.4 | 34.4 | 30.2 | 24.4 | 12.74 | 0.0796 | 0.17 | 12.61 | 1
November | 6 | 6AM to 7AM | 37.4 | 35.1 | 32 | 26.6 | 13.06 | 0.0796 | 0.18 | 12.61 | 1
November | 6 | 7AM to 8AM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
November | 6 | 8AM to 9AM | 51.8 | 44.8 | 37.4 | 33 | 17.54 | 0.0773 | 0.22 | 13 | 1
November | 6 | 9AM to 10AM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
November | 6 | 10AM to 11AM | 59 | 48.2 | 37.4 | 33 | 19.28 | 0.0762 | 0.22 | 13.18 | 0
November | 6 | 11AM to 12PM | 62.6 | 50.5 | 39.2 | 35.4 | 20.53 | 0.0757 | 0.24 | 13.28 | 0
November | 6 | 12PM to 1PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
November | 6 | 1PM to 2PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
November | 6 | 2PM to 3PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
November | 6 | 3PM to 4PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
November | 6 | 4PM to 5PM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
November | 6 | 5PM to 6PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
November | 6 | 6PM to 7PM | 60.8 | 52 | 44.6 | 43.7 | 21.38 | 0.0759 | 0.3 | 13.26 | 0
November | 6 | 7PM to 8PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
November | 6 | 8PM to 9PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
November | 6 | 9PM to 10PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
November | 6 | 10PM to 11PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
November | 6 | 11PM to 12AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
November | 7 | 12AM to 1AM | 59 | 52.9 | 48.2 | 50.1 | 21.95 | 0.0761 | 0.34 | 13.23 | 0
November | 7 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 7 | 2AM to 3AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 7 | 3AM to 4AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 7 | 4AM to 5AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 7 | 5AM to 6AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 7 | 6AM to 7AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 7 | 7AM to 8AM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
November | 7 | 8AM to 9AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 7 | 9AM to 10AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 7 | 10AM to 11AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
November | 7 | 11AM to 12PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 7 | 12PM to 1PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
November | 7 | 1PM to 2PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 7 | 2PM to 3PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 7 | 3PM to 4PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 7 | 4PM to 5PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 7 | 5PM to 6PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
November | 7 | 6PM to 7PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
November | 7 | 7PM to 8PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
November | 7 | 8PM to 9PM | 59 | 57.9 | 57.2 | 70.1 | 25.05 | 0.076 | 0.47 | 13.29 | 0
November | 7 | 9PM to 10PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
November | 7 | 10PM to 11PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
November | 7 | 11PM to 12AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
November | 8 | 12AM to 1AM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
November | 8 | 1AM to 2AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
November | 8 | 2AM to 3AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
November | 8 | 3AM to 4AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
November | 8 | 4AM to 5AM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
November | 8 | 5AM to 6AM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
November | 8 | 6AM to 7AM | 57.2 | 57.2 | 57.2 | 70.1 | 24.61 | 0.0763 | 0.47 | 13.25 | 0
November | 8 | 7AM to 8AM | 59 | 57.9 | 57.2 | 70.1 | 25.05 | 0.076 | 0.47 | 13.29 | 0
November | 8 | 8AM to 9AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
November | 8 | 9AM to 10AM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
November | 8 | 10AM to 11AM | 62.6 | 60.3 | 59 | 74.9 | 26.67 | 0.0754 | 0.5 | 13.4 | 0
November | 8 | 11AM to 12PM | 66.2 | 62.7 | 60.8 | 79.9 | 28.34 | 0.0749 | 0.54 | 13.51 | 0
November | 8 | 12PM to 1PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
November | 8 | 1PM to 2PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
November | 8 | 2PM to 3PM | 66.2 | 60.6 | 57.2 | 70.1 | 26.81 | 0.0749 | 0.47 | 13.48 | 0
November | 8 | 3PM to 4PM | 64.4 | 59.9 | 57.2 | 70.1 | 26.37 | 0.0752 | 0.47 | 13.43 | 0
November | 8 | 4PM to 5PM | 62.6 | 59.2 | 57.2 | 70.1 | 25.93 | 0.0755 | 0.47 | 13.38 | 0
November | 8 | 5PM to 6PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
November | 8 | 6PM to 7PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
November | 8 | 7PM to 8PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
November | 8 | 8PM to 9PM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
November | 8 | 9PM to 10PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 8 | 10PM to 11PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 8 | 11PM to 12AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 9 | 12AM to 1AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 9 | 1AM to 2AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 9 | 2AM to 3AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 9 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 9 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 9 | 5AM to 6AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 9 | 6AM to 7AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 9 | 7AM to 8AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 9 | 8AM to 9AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 9 | 9AM to 10AM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
November | 9 | 10AM to 11AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 9 | 11AM to 12PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
November | 9 | 12PM to 1PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
November | 9 | 1PM to 2PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 9 | 2PM to 3PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 9 | 3PM to 4PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 9 | 4PM to 5PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
November | 9 | 5PM to 6PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 9 | 6PM to 7PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 9 | 7PM to 8PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 9 | 8PM to 9PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 9 | 9PM to 10PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 9 | 10PM to 11PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 9 | 11PM to 12AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 10 | 12AM to 1AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 10 | 1AM to 2AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 10 | 2AM to 3AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 10 | 3AM to 4AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 10 | 4AM to 5AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 10 | 5AM to 6AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 10 | 6AM to 7AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 10 | 7AM to 8AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
November | 10 | 8AM to 9AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 10 | 9AM to 10AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 10 | 10AM to 11AM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
November | 10 | 11AM to 12PM | 57.2 | 56.1 | 55.4 | 65.6 | 23.91 | 0.0763 | 0.44 | 13.23 | 0
November | 10 | 12PM to 1PM | 59 | 56.8 | 55.4 | 65.6 | 24.35 | 0.076 | 0.44 | 13.28 | 0
November | 10 | 1PM to 2PM | 60.8 | 58.6 | 57.2 | 70.1 | 25.49 | 0.0757 | 0.47 | 13.34 | 0
November | 10 | 2PM to 3PM | 62.6 | 58.2 | 55.4 | 65.6 | 25.23 | 0.0755 | 0.44 | 13.37 | 0
November | 10 | 3PM to 4PM | 60.8 | 57.5 | 55.4 | 65.6 | 24.79 | 0.0758 | 0.44 | 13.32 | 0
November | 10 | 4PM to 5PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
November | 10 | 5PM to 6PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
November | 10 | 6PM to 7PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
November | 10 | 7PM to 8PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
November | 10 | 8PM to 9PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 10 | 9PM to 10PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 10 | 10PM to 11PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 10 | 11PM to 12AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 11 | 12AM to 1AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 11 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 11 | 2AM to 3AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 11 | 3AM to 4AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 11 | 4AM to 5AM | 50 | 50 | 50 | 53.7 | 20.3 | 0.0774 | 0.36 | 13.01 | 1
November | 11 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 11 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 11 | 7AM to 8AM | 50 | 50 | 50 | 53.7 | 20.3 | 0.0774 | 0.36 | 13.01 | 1
November | 11 | 8AM to 9AM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
November | 11 | 9AM to 10AM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
November | 11 | 10AM to 11AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 11 | 11AM to 12PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 11 | 12PM to 1PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
November | 11 | 1PM to 2PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
November | 11 | 2PM to 3PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
November | 11 | 3PM to 4PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
November | 11 | 4PM to 5PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
November | 11 | 5PM to 6PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 11 | 6PM to 7PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 11 | 7PM to 8PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 11 | 8PM to 9PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 11 | 9PM to 10PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 11 | 10PM to 11PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 11 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 12 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 12 | 1AM to 2AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 12 | 2AM to 3AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 12 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 12 | 4AM to 5AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 12 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 12 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 12 | 7AM to 8AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 12 | 8AM to 9AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 12 | 9AM to 10AM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 12 | 10AM to 11AM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 12 | 11AM to 12PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
November | 12 | 12PM to 1PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
November | 12 | 1PM to 2PM | 66.2 | 58.6 | 53.6 | 61.4 | 25.45 | 0.075 | 0.41 | 13.45 | 0
November | 12 | 2PM to 3PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
November | 12 | 3PM to 4PM | 64.4 | 58.9 | 55.4 | 65.6 | 25.67 | 0.0752 | 0.44 | 13.42 | 0
November | 12 | 4PM to 5PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
November | 12 | 5PM to 6PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
November | 12 | 6PM to 7PM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 12 | 7PM to 8PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 12 | 8PM to 9PM | 53.6 | 53.6 | 53.6 | 61.4 | 22.38 | 0.0768 | 0.41 | 13.13 | 0
November | 12 | 9PM to 10PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 12 | 10PM to 11PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 12 | 11PM to 12AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 13 | 12AM to 1AM | 55.4 | 54.3 | 53.6 | 61.4 | 22.82 | 0.0766 | 0.41 | 13.17 | 0
November | 13 | 1AM to 2AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 13 | 2AM to 3AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 13 | 3AM to 4AM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 13 | 4AM to 5AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 13 | 5AM to 6AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 13 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 13 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 13 | 8AM to 9AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 13 | 9AM to 10AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 13 | 10AM to 11AM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
November | 13 | 11AM to 12PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
November | 13 | 12PM to 1PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
November | 13 | 1PM to 2PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
November | 13 | 2PM to 3PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
November | 13 | 3PM to 4PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
November | 13 | 4PM to 5PM | 60.8 | 54.6 | 50 | 53.7 | 22.93 | 0.0758 | 0.36 | 13.29 | 0
November | 13 | 5PM to 6PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 13 | 6PM to 7PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 13 | 7PM to 8PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 13 | 8PM to 9PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 13 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 13 | 10PM to 11PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 13 | 11PM to 12AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
November | 14 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
November | 14 | 1AM to 2AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
November | 14 | 2AM to 3AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
November | 14 | 3AM to 4AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
November | 14 | 4AM to 5AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
November | 14 | 5AM to 6AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
November | 14 | 6AM to 7AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
November | 14 | 7AM to 8AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
November | 14 | 8AM to 9AM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
November | 14 | 9AM to 10AM | 59 | 51.2 | 44.6 | 43.7 | 20.95 | 0.0762 | 0.3 | 13.21 | 0
November | 14 | 10AM to 11AM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
November | 14 | 11AM to 12PM | 66.2 | 54.2 | 44.6 | 43.7 | 22.69 | 0.0751 | 0.3 | 13.4 | 0
November | 14 | 12PM to 1PM | 68 | 55 | 44.6 | 43.7 | 23.13 | 0.0749 | 0.3 | 13.44 | 0
November | 14 | 1PM to 2PM | 69.8 | 55.7 | 44.6 | 43.7 | 23.57 | 0.0746 | 0.3 | 13.49 | 0
November | 14 | 2PM to 3PM | 69.8 | 55.7 | 44.6 | 43.7 | 23.57 | 0.0746 | 0.3 | 13.49 | 0
November | 14 | 3PM to 4PM | 68 | 55.7 | 46.4 | 46.8 | 23.62 | 0.0748 | 0.32 | 13.45 | 0
November | 14 | 4PM to 5PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
November | 14 | 5PM to 6PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
November | 14 | 6PM to 7PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
November | 14 | 7PM to 8PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
November | 14 | 8PM to 9PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
November | 14 | 9PM to 10PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
November | 14 | 10PM to 11PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 14 | 11PM to 12AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 15 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 15 | 1AM to 2AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 15 | 2AM to 3AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
November | 15 | 3AM to 4AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
November | 15 | 4AM to 5AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
November | 15 | 5AM to 6AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
November | 15 | 6AM to 7AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
November | 15 | 7AM to 8AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
November | 15 | 8AM to 9AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 15 | 9AM to 10AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
November | 15 | 10AM to 11AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
November | 15 | 11AM to 12PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
November | 15 | 12PM to 1PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 15 | 1PM to 2PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
November | 15 | 2PM to 3PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 15 | 3PM to 4PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 15 | 4PM to 5PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
November | 15 | 5PM to 6PM | 56.8 | 53.4 | 50.9 | 55.5 | 22.26 | 0.0764 | 0.37 | 13.19 | 0
November | 15 | 6PM to 7PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 15 | 7PM to 8PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 15 | 8PM to 9PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 15 | 9PM to 10PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 15 | 10PM to 11PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 15 | 11PM to 12AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 16 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 16 | 1AM to 2AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 16 | 2AM to 3AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 16 | 3AM to 4AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 16 | 4AM to 5AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 16 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 16 | 6AM to 7AM | 50 | 50 | 50 | 53.7 | 20.3 | 0.0774 | 0.36 | 13.01 | 1
November | 16 | 7AM to 8AM | 50 | 50 | 50 | 53.7 | 20.3 | 0.0774 | 0.36 | 13.01 | 1
November | 16 | 8AM to 9AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 16 | 9AM to 10AM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
November | 16 | 10AM to 11AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 16 | 11AM to 12PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 16 | 12PM to 1PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 16 | 1PM to 2PM | 60.8 | 55.5 | 51.8 | 57.4 | 23.52 | 0.0758 | 0.39 | 13.3 | 0
November | 16 | 2PM to 3PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 16 | 3PM to 4PM | 60.8 | 56.5 | 53.6 | 61.4 | 24.14 | 0.0758 | 0.41 | 13.31 | 0
November | 16 | 4PM to 5PM | 57.2 | 55.1 | 53.6 | 61.4 | 23.26 | 0.0763 | 0.41 | 13.22 | 0
November | 16 | 5PM to 6PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 16 | 6PM to 7PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 16 | 7PM to 8PM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
November | 16 | 8PM to 9PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 16 | 9PM to 10PM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 16 | 10PM to 11PM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 16 | 11PM to 12AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 17 | 12AM to 1AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 17 | 1AM to 2AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 17 | 2AM to 3AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 17 | 3AM to 4AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 17 | 4AM to 5AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 17 | 5AM to 6AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 17 | 6AM to 7AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 17 | 7AM to 8AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 17 | 8AM to 9AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 17 | 9AM to 10AM | 50 | 50 | 50 | 53.7 | 20.3 | 0.0774 | 0.36 | 13.01 | 1
November | 17 | 10AM to 11AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 17 | 11AM to 12PM | 62.6 | 54.4 | 48.2 | 50.1 | 22.82 | 0.0756 | 0.34 | 13.32 | 0
November | 17 | 12PM to 1PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
November | 17 | 1PM to 2PM | 64.4 | 54.3 | 46.4 | 46.8 | 22.74 | 0.0754 | 0.32 | 13.36 | 0
November | 17 | 2PM to 3PM | 66.2 | 55 | 46.4 | 46.8 | 23.18 | 0.0751 | 0.32 | 13.41 | 0
November | 17 | 3PM to 4PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
November | 17 | 4PM to 5PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
November | 17 | 5PM to 6PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
November | 17 | 6PM to 7PM | 53.2 | 48.3 | 43.9 | 42.5 | 19.36 | 0.077 | 0.29 | 13.06 | 0
November | 17 | 7PM to 8PM | 51.6 | 47.3 | 43.3 | 41.6 | 18.83 | 0.0773 | 0.28 | 13.02 | 1
November | 17 | 8PM to 9PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
November | 17 | 9PM to 10PM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
November | 17 | 10PM to 11PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
November | 17 | 11PM to 12AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
November | 18 | 12AM to 1AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
November | 18 | 1AM to 2AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
November | 18 | 2AM to 3AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
November | 18 | 3AM to 4AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
November | 18 | 4AM to 5AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
November | 18 | 5AM to 6AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
November | 18 | 6AM to 7AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
November | 18 | 7AM to 8AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
November | 18 | 8AM to 9AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 18 | 9AM to 10AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 18 | 10AM to 11AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
November | 18 | 11AM to 12PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
November | 18 | 12PM to 1PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
November | 18 | 1PM to 2PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
November | 18 | 2PM to 3PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
November | 18 | 3PM to 4PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
November | 18 | 4PM to 5PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
November | 18 | 5PM to 6PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
November | 18 | 6PM to 7PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 18 | 7PM to 8PM | 51.1 | 48.9 | 47.1 | 48.1 | 19.71 | 0.0773 | 0.33 | 13.02 | 1
November | 18 | 8PM to 9PM | 48.7 | 47.3 | 46 | 46.2 | 18.84 | 0.0777 | 0.31 | 12.96 | 1
November | 18 | 9PM to 10PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
November | 18 | 10PM to 11PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
November | 18 | 11PM to 12AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
November | 19 | 12AM to 1AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
November | 19 | 1AM to 2AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
November | 19 | 2AM to 3AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
November | 19 | 3AM to 4AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
November | 19 | 4AM to 5AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
November | 19 | 5AM to 6AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
November | 19 | 6AM to 7AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
November | 19 | 7AM to 8AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
November | 19 | 8AM to 9AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 19 | 9AM to 10AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 19 | 10AM to 11AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 19 | 11AM to 12PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
November | 19 | 12PM to 1PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
November | 19 | 1PM to 2PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
November | 19 | 2PM to 3PM | 66.2 | 53.5 | 42.8 | 40.8 | 22.24 | 0.0751 | 0.28 | 13.39 | 0
November | 19 | 3PM to 4PM | 64.4 | 53.5 | 44.6 | 43.7 | 22.26 | 0.0754 | 0.3 | 13.35 | 0
November | 19 | 4PM to 5PM | 60.8 | 53.7 | 48.2 | 50.1 | 22.38 | 0.0759 | 0.34 | 13.28 | 0
November | 19 | 5PM to 6PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
November | 19 | 6PM to 7PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
November | 19 | 7PM to 8PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 19 | 8PM to 9PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 19 | 9PM to 10PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 19 | 10PM to 11PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 19 | 11PM to 12AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 20 | 12AM to 1AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 20 | 1AM to 2AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
November | 20 | 2AM to 3AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
November | 20 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
November | 20 | 4AM to 5AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
November | 20 | 5AM to 6AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
November | 20 | 6AM to 7AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
November | 20 | 7AM to 8AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
November | 20 | 8AM to 9AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 20 | 9AM to 10AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 20 | 10AM to 11AM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
November | 20 | 11AM to 12PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 20 | 12PM to 1PM | 64.4 | 55.1 | 48.2 | 50.1 | 23.26 | 0.0753 | 0.34 | 13.37 | 0
November | 20 | 1PM to 2PM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
November | 20 | 2PM to 3PM | 68 | 57.4 | 50 | 53.7 | 24.69 | 0.0748 | 0.36 | 13.47 | 0
November | 20 | 3PM to 4PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
November | 20 | 4PM to 5PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
November | 20 | 5PM to 6PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
November | 20 | 6PM to 7PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 20 | 7PM to 8PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 20 | 8PM to 9PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 20 | 9PM to 10PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 20 | 10PM to 11PM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 20 | 11PM to 12AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 21 | 12AM to 1AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 21 | 1AM to 2AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 21 | 2AM to 3AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 21 | 3AM to 4AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 21 | 4AM to 5AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 21 | 5AM to 6AM | 45.5 | 45.4 | 45.3 | 44.9 | 17.86 | 0.0782 | 0.3 | 12.87 | 1
November | 21 | 6AM to 7AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 21 | 7AM to 8AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 21 | 8AM to 9AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
November | 21 | 9AM to 10AM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
November | 21 | 10AM to 11AM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
November | 21 | 11AM to 12PM | 64.4 | 57.9 | 53.6 | 61.4 | 25.01 | 0.0753 | 0.41 | 13.4 | 0
November | 21 | 12PM to 1PM | 66.2 | 57.6 | 51.8 | 57.4 | 24.83 | 0.075 | 0.39 | 13.44 | 0
November | 21 | 1PM to 2PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
November | 21 | 2PM to 3PM | 69.8 | 59 | 51.8 | 57.4 | 25.71 | 0.0745 | 0.39 | 13.53 | 0
November | 21 | 3PM to 4PM | 68 | 59.2 | 53.6 | 61.4 | 25.89 | 0.0747 | 0.41 | 13.5 | 0
November | 21 | 4PM to 5PM | 64.4 | 56.9 | 51.8 | 57.4 | 24.39 | 0.0753 | 0.39 | 13.39 | 0
November | 21 | 5PM to 6PM | 59 | 55.8 | 53.6 | 61.4 | 23.7 | 0.076 | 0.41 | 13.27 | 0
November | 21 | 6PM to 7PM | 59 | 54.8 | 51.8 | 57.4 | 23.08 | 0.0761 | 0.39 | 13.25 | 0
November | 21 | 7PM to 8PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 21 | 8PM to 9PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
November | 21 | 9PM to 10PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 21 | 10PM to 11PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 21 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 22 | 12AM to 1AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 22 | 1AM to 2AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 22 | 2AM to 3AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 22 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 22 | 4AM to 5AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 22 | 5AM to 6AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 22 | 6AM to 7AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 22 | 7AM to 8AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 22 | 8AM to 9AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 22 | 9AM to 10AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 22 | 10AM to 11AM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 22 | 11AM to 12PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 22 | 12PM to 1PM | 62.6 | 55.3 | 50 | 53.7 | 23.37 | 0.0756 | 0.36 | 13.33 | 0
November | 22 | 1PM to 2PM | 64.4 | 56 | 50 | 53.7 | 23.81 | 0.0753 | 0.36 | 13.38 | 0
November | 22 | 2PM to 3PM | 62.6 | 57.2 | 53.6 | 61.4 | 24.58 | 0.0755 | 0.41 | 13.36 | 0
November | 22 | 3PM to 4PM | 62.6 | 56.2 | 51.8 | 57.4 | 23.96 | 0.0755 | 0.39 | 13.35 | 0
November | 22 | 4PM to 5PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
November | 22 | 5PM to 6PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 22 | 6PM to 7PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 22 | 7PM to 8PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 22 | 8PM to 9PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
November | 22 | 9PM to 10PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 22 | 10PM to 11PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 22 | 11PM to 12AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 23 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 23 | 1AM to 2AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 23 | 2AM to 3AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 23 | 3AM to 4AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 23 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 23 | 5AM to 6AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
November | 23 | 6AM to 7AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 23 | 7AM to 8AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 23 | 8AM to 9AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 23 | 9AM to 10AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 23 | 10AM to 11AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 23 | 11AM to 12PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 23 | 12PM to 1PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 23 | 1PM to 2PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 23 | 2PM to 3PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
November | 23 | 3PM to 4PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 23 | 4PM to 5PM | 52 | 50.7 | 49.6 | 52.9 | 20.67 | 0.0771 | 0.36 | 13.06 | 0
November | 23 | 5PM to 6PM | 50.5 | 49.6 | 48.9 | 51.5 | 20.1 | 0.0774 | 0.35 | 13.02 | 1
November | 23 | 6PM to 7PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 23 | 7PM to 8PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 23 | 8PM to 9PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
November | 23 | 9PM to 10PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
November | 23 | 10PM to 11PM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
November | 23 | 11PM to 12AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
November | 24 | 12AM to 1AM | 50 | 50 | 50 | 53.7 | 20.3 | 0.0774 | 0.36 | 13.01 | 1
November | 24 | 1AM to 2AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 24 | 2AM to 3AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 24 | 3AM to 4AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 24 | 4AM to 5AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 24 | 5AM to 6AM | 51.1 | 50.3 | 49.6 | 52.9 | 20.46 | 0.0773 | 0.36 | 13.04 | 1
November | 24 | 6AM to 7AM | 50.4 | 49.9 | 49.5 | 52.6 | 20.22 | 0.0774 | 0.36 | 13.02 | 1
November | 24 | 7AM to 8AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
November | 24 | 8AM to 9AM | 53.1 | 51.6 | 50.5 | 54.8 | 21.22 | 0.077 | 0.37 | 13.09 | 0
November | 24 | 9AM to 10AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
November | 24 | 10AM to 11AM | 54 | 51.2 | 49.1 | 51.9 | 20.99 | 0.0769 | 0.35 | 13.11 | 0
November | 24 | 11AM to 12PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
November | 24 | 12PM to 1PM | 53.8 | 50 | 46.8 | 47.5 | 20.26 | 0.0769 | 0.32 | 13.09 | 0
November | 24 | 1PM to 2PM | 56.7 | 50.6 | 45.5 | 45.2 | 20.62 | 0.0765 | 0.31 | 13.16 | 0
November | 24 | 2PM to 3PM | 57 | 50.9 | 45.9 | 45.9 | 20.8 | 0.0764 | 0.31 | 13.17 | 0
November | 24 | 3PM to 4PM | 54.5 | 49.1 | 44.4 | 43.4 | 19.81 | 0.0768 | 0.29 | 13.1 | 0
November | 24 | 4PM to 5PM | 52.2 | 48.2 | 44.6 | 43.7 | 19.28 | 0.0772 | 0.3 | 13.04 | 0
November | 24 | 5PM to 6PM | 50.7 | 47.2 | 43.9 | 42.5 | 18.75 | 0.0774 | 0.29 | 13 | 1
November | 24 | 6PM to 7PM | 48.9 | 45.9 | 43 | 41 | 18.09 | 0.0777 | 0.28 | 12.95 | 1
November | 24 | 7PM to 8PM | 48.2 | 44.9 | 41.5 | 38.8 | 17.57 | 0.0778 | 0.26 | 12.92 | 1
November | 24 | 8PM to 9PM | 49.3 | 43.7 | 37.6 | 33.2 | 16.96 | 0.0777 | 0.23 | 12.93 | 1
November | 24 | 9PM to 10PM | 45 | 42 | 38.8 | 34.9 | 16.18 | 0.0783 | 0.24 | 12.83 | 1
November | 24 | 10PM to 11PM | 48.7 | 43.7 | 38.3 | 34.2 | 16.98 | 0.0778 | 0.23 | 12.92 | 1
November | 24 | 11PM to 12AM | 48.2 | 43.6 | 38.7 | 34.7 | 16.93 | 0.0778 | 0.24 | 12.91 | 1
November | 25 | 12AM to 1AM | 45.7 | 43 | 40.1 | 36.7 | 16.63 | 0.0782 | 0.25 | 12.85 | 1
November | 25 | 1AM to 2AM | 46.8 | 43.3 | 39.6 | 35.9 | 16.77 | 0.0781 | 0.24 | 12.88 | 1
November | 25 | 2AM to 3AM | 46.9 | 43.1 | 39 | 35.2 | 16.7 | 0.078 | 0.24 | 12.88 | 1
November | 25 | 3AM to 4AM | 46.4 | 43 | 39.4 | 35.7 | 16.65 | 0.0781 | 0.24 | 12.87 | 1
November | 25 | 4AM to 5AM | 44.8 | 42 | 39 | 35.2 | 16.18 | 0.0784 | 0.24 | 12.83 | 1
November | 25 | 5AM to 6AM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
November | 25 | 6AM to 7AM | 46.4 | 41.4 | 35.6 | 30.7 | 15.88 | 0.0781 | 0.21 | 12.85 | 1
November | 25 | 7AM to 8AM | 50 | 42.5 | 33.8 | 28.6 | 16.42 | 0.0776 | 0.19 | 12.94 | 1
November | 25 | 8AM to 9AM | 53.6 | 44.3 | 33.8 | 28.6 | 17.29 | 0.0771 | 0.19 | 13.03 | 0
November | 25 | 9AM to 10AM | 57.2 | 46.1 | 33.8 | 28.6 | 18.16 | 0.0765 | 0.19 | 13.12 | 0
November | 25 | 10AM to 11AM | 60.8 | 46.5 | 30.2 | 24.4 | 18.39 | 0.076 | 0.17 | 13.2 | 0
November | 25 | 11AM to 12PM | 66.2 | 49 | 30.2 | 24.4 | 19.69 | 0.0752 | 0.17 | 13.34 | 0
November | 25 | 12PM to 1PM | 66.2 | 48.4 | 28.4 | 22.5 | 19.39 | 0.0753 | 0.15 | 13.33 | 0
November | 25 | 1PM to 2PM | 69.8 | 49.5 | 26.6 | 20.7 | 19.97 | 0.0748 | 0.14 | 13.42 | 0
November | 25 | 2PM to 3PM | 69.8 | 50.1 | 28.4 | 22.5 | 20.26 | 0.0747 | 0.15 | 13.42 | 0
November | 25 | 3PM to 4PM | 66.2 | 47.9 | 26.6 | 20.7 | 19.11 | 0.0753 | 0.14 | 13.33 | 0
November | 25 | 4PM to 5PM | 62.6 | 46.8 | 28.4 | 22.5 | 18.52 | 0.0758 | 0.15 | 13.24 | 0
November | 25 | 5PM to 6PM | 60.8 | 45.9 | 28.4 | 22.5 | 18.08 | 0.076 | 0.15 | 13.19 | 0
November | 25 | 6PM to 7PM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
November | 25 | 7PM to 8PM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
November | 25 | 8PM to 9PM | 59 | 43 | 21.2 | 16 | 16.64 | 0.0763 | 0.11 | 13.13 | 0
November | 25 | 9PM to 10PM | 51.8 | 40.3 | 24.8 | 19 | 15.37 | 0.0774 | 0.13 | 12.96 | 1
November | 25 | 10PM to 11PM | 57.2 | 42.6 | 23 | 17.4 | 16.43 | 0.0766 | 0.12 | 13.09 | 0
November | 25 | 11PM to 12AM | 53.6 | 41.3 | 24.8 | 19 | 15.8 | 0.0771 | 0.13 | 13 | 0
November | 26 | 12AM to 1AM | 48.2 | 39 | 26.6 | 20.7 | 14.76 | 0.0779 | 0.14 | 12.87 | 1
November | 26 | 1AM to 2AM | 48.2 | 39 | 26.6 | 20.7 | 14.76 | 0.0779 | 0.14 | 12.87 | 1
November | 26 | 2AM to 3AM | 48.2 | 39 | 26.6 | 20.7 | 14.76 | 0.0779 | 0.14 | 12.87 | 1
November | 26 | 3AM to 4AM | 46.4 | 38.7 | 28.4 | 22.5 | 14.61 | 0.0782 | 0.15 | 12.83 | 1
November | 26 | 4AM to 5AM | 42.8 | 36.7 | 28.4 | 22.5 | 13.74 | 0.0788 | 0.15 | 12.74 | 1
November | 26 | 5AM to 6AM | 46.4 | 38 | 26.6 | 20.7 | 14.33 | 0.0782 | 0.14 | 12.82 | 1
November | 26 | 6AM to 7AM | 46.2 | 37.8 | 26.2 | 20.3 | 14.23 | 0.0782 | 0.14 | 12.82 | 1
November | 26 | 7AM to 8AM | 48.2 | 39 | 26.6 | 20.7 | 14.76 | 0.0779 | 0.14 | 12.87 | 1
November | 26 | 8AM to 9AM | 54.9 | 42.6 | 27.1 | 21.2 | 16.45 | 0.0769 | 0.14 | 13.04 | 0
November | 26 | 9AM to 10AM | 60.8 | 45.4 | 26.6 | 20.7 | 17.8 | 0.076 | 0.14 | 13.19 | 0
November | 26 | 10AM to 11AM | 65.1 | 47.5 | 26.8 | 20.8 | 18.87 | 0.0754 | 0.14 | 13.3 | 0
November | 26 | 11AM to 12PM | 68.7 | 49.2 | 27 | 21 | 19.77 | 0.0749 | 0.14 | 13.39 | 0
November | 26 | 12PM to 1PM | 71.6 | 50.3 | 26.6 | 20.7 | 20.41 | 0.0745 | 0.14 | 13.46 | 0
November | 26 | 1PM to 2PM | 73.4 | 51.1 | 26.6 | 20.7 | 20.84 | 0.0742 | 0.14 | 13.51 | 0
November | 26 | 2PM to 3PM | 71.6 | 51.4 | 30.2 | 24.4 | 21 | 0.0745 | 0.17 | 13.47 | 0
November | 26 | 3PM to 4PM | 64.4 | 48.2 | 30.2 | 24.4 | 19.26 | 0.0755 | 0.17 | 13.29 | 0
November | 26 | 4PM to 5PM | 57.2 | 44.8 | 30.2 | 24.4 | 17.52 | 0.0765 | 0.17 | 13.11 | 0
November | 26 | 5PM to 6PM | 51.8 | 42.1 | 30.2 | 24.4 | 16.22 | 0.0774 | 0.17 | 12.97 | 1
November | 26 | 6PM to 7PM | 53.6 | 43 | 30.2 | 24.4 | 16.65 | 0.0771 | 0.17 | 13.02 | 0
November | 26 | 7PM to 8PM | 46.4 | 39.3 | 30.2 | 24.4 | 14.91 | 0.0782 | 0.17 | 12.84 | 1
November | 26 | 8PM to 9PM | 46.4 | 39.3 | 30.2 | 24.4 | 14.91 | 0.0782 | 0.17 | 12.84 | 1
November | 26 | 9PM to 10PM | 42.8 | 37.4 | 30.2 | 24.4 | 14.04 | 0.0787 | 0.17 | 12.74 | 1
November | 26 | 10PM to 11PM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
November | 26 | 11PM to 12AM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
November | 27 | 12AM to 1AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
November | 27 | 1AM to 2AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 27 | 2AM to 3AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 27 | 3AM to 4AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
November | 27 | 4AM to 5AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 27 | 5AM to 6AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 27 | 6AM to 7AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 27 | 7AM to 8AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
November | 27 | 8AM to 9AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
November | 27 | 9AM to 10AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
November | 27 | 10AM to 11AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
November | 27 | 11AM to 12PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
November | 27 | 12PM to 1PM | 60.8 | 49 | 37.4 | 33 | 19.72 | 0.076 | 0.22 | 13.23 | 0
November | 27 | 1PM to 2PM | 62.6 | 51.2 | 41 | 38 | 20.93 | 0.0757 | 0.26 | 13.29 | 0
November | 27 | 2PM to 3PM | 62.6 | 51.2 | 41 | 38 | 20.93 | 0.0757 | 0.26 | 13.29 | 0
November | 27 | 3PM to 4PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
November | 27 | 4PM to 5PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
November | 27 | 5PM to 6PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
November | 27 | 6PM to 7PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
November | 27 | 7PM to 8PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
November | 27 | 8PM to 9PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
November | 27 | 9PM to 10PM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
November | 27 | 10PM to 11PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
November | 27 | 11PM to 12AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
November | 28 | 12AM to 1AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
November | 28 | 1AM to 2AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
November | 28 | 2AM to 3AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
November | 28 | 3AM to 4AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
November | 28 | 4AM to 5AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
November | 28 | 5AM to 6AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
November | 28 | 6AM to 7AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
November | 28 | 7AM to 8AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 28 | 8AM to 9AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
November | 28 | 9AM to 10AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
November | 28 | 10AM to 11AM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
November | 28 | 11AM to 12PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
November | 28 | 12PM to 1PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
November | 28 | 1PM to 2PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
November | 28 | 2PM to 3PM | 64.4 | 52.7 | 42.8 | 40.8 | 21.8 | 0.0754 | 0.28 | 13.34 | 0
November | 28 | 3PM to 4PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
November | 28 | 4PM to 5PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
November | 28 | 5PM to 6PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
November | 28 | 6PM to 7PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
November | 28 | 7PM to 8PM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
November | 28 | 8PM to 9PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
November | 28 | 9PM to 10PM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
November | 28 | 10PM to 11PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
November | 28 | 11PM to 12AM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
November | 29 | 12AM to 1AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
November | 29 | 1AM to 2AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
November | 29 | 2AM to 3AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
November | 29 | 3AM to 4AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
November | 29 | 4AM to 5AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
November | 29 | 5AM to 6AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
November | 29 | 6AM to 7AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
November | 29 | 7AM to 8AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
November | 29 | 8AM to 9AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
November | 29 | 9AM to 10AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
November | 29 | 10AM to 11AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
November | 29 | 11AM to 12PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
November | 29 | 12PM to 1PM | 60.8 | 51.2 | 42.8 | 40.8 | 20.93 | 0.0759 | 0.28 | 13.25 | 0
November | 29 | 1PM to 2PM | 62.6 | 49.8 | 37.4 | 33 | 20.15 | 0.0757 | 0.22 | 13.27 | 0
November | 29 | 2PM to 3PM | 60.8 | 49.7 | 39.2 | 35.4 | 20.09 | 0.0759 | 0.24 | 13.23 | 0
November | 29 | 3PM to 4PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
November | 29 | 4PM to 5PM | 55.4 | 48 | 41 | 38 | 19.19 | 0.0767 | 0.26 | 13.1 | 0
November | 29 | 5PM to 6PM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
November | 29 | 6PM to 7PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
November | 29 | 7PM to 8PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
November | 29 | 8PM to 9PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
November | 29 | 9PM to 10PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
November | 29 | 10PM to 11PM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
November | 29 | 11PM to 12AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
November | 30 | 12AM to 1AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 30 | 1AM to 2AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
November | 30 | 2AM to 3AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 30 | 3AM to 4AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
November | 30 | 4AM to 5AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 30 | 5AM to 6AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
November | 30 | 6AM to 7AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 30 | 7AM to 8AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
November | 30 | 8AM to 9AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
November | 30 | 9AM to 10AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
November | 30 | 10AM to 11AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
November | 30 | 11AM to 12PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
November | 30 | 12PM to 1PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
November | 30 | 1PM to 2PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
November | 30 | 2PM to 3PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
November | 30 | 3PM to 4PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
November | 30 | 4PM to 5PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
November | 30 | 5PM to 6PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
November | 30 | 6PM to 7PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
November | 30 | 7PM to 8PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
November | 30 | 8PM to 9PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
November | 30 | 9PM to 10PM | 48.4 | 45.9 | 43.5 | 41.9 | 18.09 | 0.0778 | 0.28 | 12.94 | 1
November | 30 | 10PM to 11PM | 46.9 | 44.8 | 42.6 | 40.5 | 17.52 | 0.078 | 0.27 | 12.9 | 1
November | 30 | 11PM to 12AM | 45.3 | 43.4 | 41.5 | 38.8 | 16.87 | 0.0783 | 0.26 | 12.85 | 1
December | 1 | 12AM to 1AM | 43.9 | 42.2 | 40.5 | 37.2 | 16.27 | 0.0785 | 0.25 | 12.81 | 1
December | 1 | 1AM to 2AM | 42.3 | 40.9 | 39.4 | 35.7 | 15.64 | 0.0788 | 0.24 | 12.76 | 1
December | 1 | 2AM to 3AM | 40.8 | 39.7 | 38.5 | 34.4 | 15.1 | 0.079 | 0.23 | 12.72 | 1
December | 1 | 3AM to 4AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 1 | 4AM to 5AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 1 | 5AM to 6AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 1 | 6AM to 7AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 1 | 7AM to 8AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 1 | 8AM to 9AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 1 | 9AM to 10AM | 47.5 | 45.7 | 44.1 | 42.8 | 18.01 | 0.0779 | 0.29 | 12.92 | 1
December | 1 | 10AM to 11AM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 1 | 11AM to 12PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
December | 1 | 12PM to 1PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
December | 1 | 1PM to 2PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
December | 1 | 2PM to 3PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
December | 1 | 3PM to 4PM | 55.4 | 49.6 | 44.6 | 43.7 | 20.07 | 0.0767 | 0.3 | 13.12 | 0
December | 1 | 4PM to 5PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 1 | 5PM to 6PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 1 | 6PM to 7PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
December | 1 | 7PM to 8PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 1 | 8PM to 9PM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
December | 1 | 9PM to 10PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 1 | 10PM to 11PM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 1 | 11PM to 12AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 2 | 12AM to 1AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 2 | 1AM to 2AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 2 | 2AM to 3AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 2 | 3AM to 4AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 2 | 4AM to 5AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 2 | 5AM to 6AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 2 | 6AM to 7AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 2 | 7AM to 8AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 2 | 8AM to 9AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 2 | 9AM to 10AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 2 | 10AM to 11AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 2 | 11AM to 12PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 2 | 12PM to 1PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
December | 2 | 1PM to 2PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
December | 2 | 2PM to 3PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
December | 2 | 3PM to 4PM | 57.2 | 51.3 | 46.4 | 46.8 | 20.99 | 0.0764 | 0.32 | 13.18 | 0
December | 2 | 4PM to 5PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 2 | 5PM to 6PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 2 | 6PM to 7PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 2 | 7PM to 8PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 2 | 8PM to 9PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 2 | 9PM to 10PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 2 | 10PM to 11PM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 2 | 11PM to 12AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 3 | 12AM to 1AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 3 | 1AM to 2AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 3 | 2AM to 3AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 3 | 3AM to 4AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 3 | 4AM to 5AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 3 | 5AM to 6AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 3 | 6AM to 7AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 3 | 7AM to 8AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 3 | 8AM to 9AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 3 | 9AM to 10AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 3 | 10AM to 11AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 3 | 11AM to 12PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 3 | 12PM to 1PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
December | 3 | 1PM to 2PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 3 | 2PM to 3PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
December | 3 | 3PM to 4PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
December | 3 | 4PM to 5PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 3 | 5PM to 6PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 3 | 6PM to 7PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 3 | 7PM to 8PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 3 | 8PM to 9PM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 3 | 9PM to 10PM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 3 | 10PM to 11PM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 3 | 11PM to 12AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 4 | 12AM to 1AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 1AM to 2AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 4 | 2AM to 3AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 3AM to 4AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 4AM to 5AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 5AM to 6AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 6AM to 7AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 7AM to 8AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 4 | 8AM to 9AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 4 | 9AM to 10AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 10AM to 11AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 11AM to 12PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 4 | 12PM to 1PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 4 | 1PM to 2PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 4 | 2PM to 3PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 4 | 3PM to 4PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 4 | 4PM to 5PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 4 | 5PM to 6PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 4 | 6PM to 7PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 7PM to 8PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 4 | 8PM to 9PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 4 | 9PM to 10PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 4 | 10PM to 11PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 4 | 11PM to 12AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 5 | 12AM to 1AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 5 | 1AM to 2AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 5 | 2AM to 3AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 5 | 3AM to 4AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 5 | 4AM to 5AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 5 | 5AM to 6AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 5 | 6AM to 7AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 5 | 7AM to 8AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 5 | 8AM to 9AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 5 | 9AM to 10AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 5 | 10AM to 11AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 5 | 11AM to 12PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 5 | 12PM to 1PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 5 | 1PM to 2PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 5 | 2PM to 3PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 5 | 3PM to 4PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
December | 5 | 4PM to 5PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 5 | 5PM to 6PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 5 | 6PM to 7PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 5 | 7PM to 8PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 5 | 8PM to 9PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 5 | 9PM to 10PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 5 | 10PM to 11PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 5 | 11PM to 12AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 6 | 12AM to 1AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 6 | 1AM to 2AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 6 | 2AM to 3AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 6 | 3AM to 4AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 6 | 4AM to 5AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 6 | 5AM to 6AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 6 | 6AM to 7AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 6 | 7AM to 8AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 6 | 8AM to 9AM | 41 | 41 | 41 | 38 | 15.7 | 0.0789 | 0.26 | 12.74 | 1
December | 6 | 9AM to 10AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 6 | 10AM to 11AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
December | 6 | 11AM to 12PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 6 | 12PM to 1PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 6 | 1PM to 2PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 6 | 2PM to 3PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 6 | 3PM to 4PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 6 | 4PM to 5PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 6 | 5PM to 6PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 6 | 6PM to 7PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 6 | 7PM to 8PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 6 | 8PM to 9PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 6 | 9PM to 10PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 6 | 10PM to 11PM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 6 | 11PM to 12AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 12AM to 1AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 1AM to 2AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 2AM to 3AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 3AM to 4AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 4AM to 5AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 5AM to 6AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 6AM to 7AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 7AM to 8AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 7 | 8AM to 9AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 7 | 9AM to 10AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 7 | 10AM to 11AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 7 | 11AM to 12PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 7 | 12PM to 1PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 7 | 1PM to 2PM | 53.8 | 50.2 | 47.3 | 48.4 | 20.42 | 0.0769 | 0.33 | 13.09 | 0
December | 7 | 2PM to 3PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
December | 7 | 3PM to 4PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 7 | 4PM to 5PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 7 | 5PM to 6PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 7 | 6PM to 7PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 7 | 7PM to 8PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 7 | 8PM to 9PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
December | 7 | 9PM to 10PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
December | 7 | 10PM to 11PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 7 | 11PM to 12AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 8 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 8 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 8 | 2AM to 3AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 8 | 3AM to 4AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 8 | 4AM to 5AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 8 | 5AM to 6AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 8 | 6AM to 7AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 8 | 7AM to 8AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 8 | 8AM to 9AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 8 | 9AM to 10AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 8 | 10AM to 11AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
December | 8 | 11AM to 12PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
December | 8 | 12PM to 1PM | 60.8 | 52.8 | 46.4 | 46.8 | 21.87 | 0.0759 | 0.32 | 13.27 | 0
December | 8 | 1PM to 2PM | 62.6 | 52.7 | 44.6 | 43.7 | 21.82 | 0.0756 | 0.3 | 13.3 | 0
December | 8 | 2PM to 3PM | 62.6 | 52 | 42.8 | 40.8 | 21.36 | 0.0757 | 0.28 | 13.3 | 0
December | 8 | 3PM to 4PM | 62.6 | 53.5 | 46.4 | 46.8 | 22.31 | 0.0756 | 0.32 | 13.31 | 0
December | 8 | 4PM to 5PM | 59 | 52 | 46.4 | 46.8 | 21.43 | 0.0761 | 0.32 | 13.22 | 0
December | 8 | 5PM to 6PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
December | 8 | 6PM to 7PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 8 | 7PM to 8PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 8 | 8PM to 9PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
December | 8 | 9PM to 10PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
December | 8 | 10PM to 11PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 8 | 11PM to 12AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 9 | 12AM to 1AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
December | 9 | 1AM to 2AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 9 | 2AM to 3AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 9 | 3AM to 4AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 9 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 9 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 9 | 6AM to 7AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 9 | 7AM to 8AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 9 | 8AM to 9AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 9 | 9AM to 10AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 9 | 10AM to 11AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 9 | 11AM to 12PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
December | 9 | 12PM to 1PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
December | 9 | 1PM to 2PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
December | 9 | 2PM to 3PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
December | 9 | 3PM to 4PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
December | 9 | 4PM to 5PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
December | 9 | 5PM to 6PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
December | 9 | 6PM to 7PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
December | 9 | 7PM to 8PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 9 | 8PM to 9PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 9 | 9PM to 10PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 9 | 10PM to 11PM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 9 | 11PM to 12AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 10 | 12AM to 1AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 10 | 1AM to 2AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 10 | 2AM to 3AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 10 | 3AM to 4AM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
December | 10 | 4AM to 5AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
December | 10 | 5AM to 6AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
December | 10 | 6AM to 7AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 10 | 7AM to 8AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 10 | 8AM to 9AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 10 | 9AM to 10AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 10 | 10AM to 11AM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 10 | 11AM to 12PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
December | 10 | 12PM to 1PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
December | 10 | 1PM to 2PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
December | 10 | 2PM to 3PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
December | 10 | 3PM to 4PM | 55.4 | 52.3 | 50 | 53.7 | 21.62 | 0.0766 | 0.36 | 13.15 | 0
December | 10 | 4PM to 5PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 10 | 5PM to 6PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 10 | 6PM to 7PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 10 | 7PM to 8PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 10 | 8PM to 9PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 10 | 9PM to 10PM | 53.6 | 51.6 | 50 | 53.7 | 21.18 | 0.0769 | 0.36 | 13.1 | 0
December | 10 | 10PM to 11PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 10 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 11 | 12AM to 1AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
December | 11 | 1AM to 2AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 11 | 2AM to 3AM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
December | 11 | 3AM to 4AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 11 | 4AM to 5AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 11 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 11 | 6AM to 7AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 11 | 7AM to 8AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 11 | 8AM to 9AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 11 | 9AM to 10AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 11 | 10AM to 11AM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 11 | 11AM to 12PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 11 | 12PM to 1PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 11 | 1PM to 2PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 11 | 2PM to 3PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 11 | 3PM to 4PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 11 | 4PM to 5PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 11 | 5PM to 6PM | 48.2 | 48.2 | 48.2 | 50.1 | 19.32 | 0.0777 | 0.34 | 12.96 | 1
December | 11 | 6PM to 7PM | 50 | 49 | 48.2 | 50.1 | 19.76 | 0.0775 | 0.34 | 13 | 1
December | 11 | 7PM to 8PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 11 | 8PM to 9PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 11 | 9PM to 10PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 11 | 10PM to 11PM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
December | 11 | 11PM to 12AM | 46.4 | 46.4 | 46.4 | 46.8 | 18.37 | 0.078 | 0.32 | 12.9 | 1
December | 12 | 12AM to 1AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 12 | 1AM to 2AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 12 | 2AM to 3AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 12 | 3AM to 4AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 12 | 4AM to 5AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 12 | 5AM to 6AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 12 | 6AM to 7AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 12 | 7AM to 8AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 12 | 8AM to 9AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 12 | 9AM to 10AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 12 | 10AM to 11AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 12 | 11AM to 12PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 12 | 12PM to 1PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 12 | 1PM to 2PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
December | 12 | 2PM to 3PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 12 | 3PM to 4PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 12 | 4PM to 5PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 12 | 5PM to 6PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 12 | 6PM to 7PM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 12 | 7PM to 8PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 12 | 8PM to 9PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 12 | 9PM to 10PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 12 | 10PM to 11PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 12 | 11PM to 12AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 13 | 12AM to 1AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 13 | 1AM to 2AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 13 | 2AM to 3AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 13 | 3AM to 4AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 13 | 4AM to 5AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 13 | 5AM to 6AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 13 | 6AM to 7AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 13 | 7AM to 8AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 13 | 8AM to 9AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 13 | 9AM to 10AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
December | 13 | 10AM to 11AM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
December | 13 | 11AM to 12PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 13 | 12PM to 1PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 13 | 1PM to 2PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 13 | 2PM to 3PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 13 | 3PM to 4PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 13 | 4PM to 5PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 13 | 5PM to 6PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 13 | 6PM to 7PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 13 | 7PM to 8PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 13 | 8PM to 9PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 13 | 9PM to 10PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 13 | 10PM to 11PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 13 | 11PM to 12AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 14 | 12AM to 1AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 14 | 1AM to 2AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 14 | 2AM to 3AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 14 | 3AM to 4AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 14 | 4AM to 5AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 14 | 5AM to 6AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 14 | 6AM to 7AM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 14 | 7AM to 8AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 14 | 8AM to 9AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 14 | 9AM to 10AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 14 | 10AM to 11AM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 14 | 11AM to 12PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 14 | 12PM to 1PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 14 | 1PM to 2PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
December | 14 | 2PM to 3PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 14 | 3PM to 4PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 14 | 4PM to 5PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 14 | 5PM to 6PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 14 | 6PM to 7PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 14 | 7PM to 8PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 14 | 8PM to 9PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 14 | 9PM to 10PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
December | 14 | 10PM to 11PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 14 | 11PM to 12AM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 15 | 12AM to 1AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 15 | 1AM to 2AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
December | 15 | 2AM to 3AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
December | 15 | 3AM to 4AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
December | 15 | 4AM to 5AM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
December | 15 | 5AM to 6AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 15 | 6AM to 7AM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
December | 15 | 7AM to 8AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 15 | 8AM to 9AM | 51.8 | 50.8 | 50 | 53.7 | 20.74 | 0.0772 | 0.36 | 13.06 | 1
December | 15 | 9AM to 10AM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
December | 15 | 10AM to 11AM | 51.8 | 51.8 | 51.8 | 57.4 | 21.32 | 0.0771 | 0.39 | 13.07 | 1
December | 15 | 11AM to 12PM | 53.6 | 52.6 | 51.8 | 57.4 | 21.76 | 0.0769 | 0.39 | 13.12 | 0
December | 15 | 12PM to 1PM | 55.4 | 53.3 | 51.8 | 57.4 | 22.2 | 0.0766 | 0.39 | 13.16 | 0
December | 15 | 1PM to 2PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
December | 15 | 2PM to 3PM | 57.2 | 54.1 | 51.8 | 57.4 | 22.64 | 0.0763 | 0.39 | 13.21 | 0
December | 15 | 3PM to 4PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
December | 15 | 4PM to 5PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
December | 15 | 5PM to 6PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 15 | 6PM to 7PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 15 | 7PM to 8PM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 15 | 8PM to 9PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 15 | 9PM to 10PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 15 | 10PM to 11PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
December | 15 | 11PM to 12AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
December | 16 | 12AM to 1AM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
December | 16 | 1AM to 2AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
December | 16 | 2AM to 3AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
December | 16 | 3AM to 4AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
December | 16 | 4AM to 5AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
December | 16 | 5AM to 6AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
December | 16 | 6AM to 7AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 16 | 7AM to 8AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 16 | 8AM to 9AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
December | 16 | 9AM to 10AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
December | 16 | 10AM to 11AM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
December | 16 | 11AM to 12PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 16 | 12PM to 1PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
December | 16 | 1PM to 2PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
December | 16 | 2PM to 3PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
December | 16 | 3PM to 4PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
December | 16 | 4PM to 5PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 16 | 5PM to 6PM | 50.5 | 48.3 | 46.4 | 46.8 | 19.38 | 0.0774 | 0.32 | 13.01 | 1
December | 16 | 6PM to 7PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 16 | 7PM to 8PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 16 | 8PM to 9PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 16 | 9PM to 10PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 16 | 10PM to 11PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 16 | 11PM to 12AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 17 | 12AM to 1AM | 45.9 | 44.9 | 44.1 | 42.8 | 17.62 | 0.0781 | 0.29 | 12.88 | 1
December | 17 | 1AM to 2AM | 45.5 | 44.6 | 43.7 | 42.2 | 17.44 | 0.0782 | 0.29 | 12.86 | 1
December | 17 | 2AM to 3AM | 45.1 | 44.3 | 43.5 | 41.9 | 17.31 | 0.0783 | 0.28 | 12.85 | 1
December | 17 | 3AM to 4AM | 45 | 44.1 | 43.3 | 41.6 | 17.22 | 0.0783 | 0.28 | 12.85 | 1
December | 17 | 4AM to 5AM | 44.6 | 43.8 | 43 | 41 | 17.04 | 0.0784 | 0.28 | 12.84 | 1
December | 17 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 17 | 6AM to 7AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
December | 17 | 7AM to 8AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
December | 17 | 8AM to 9AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
December | 17 | 9AM to 10AM | 51.8 | 44.8 | 37.4 | 33 | 17.54 | 0.0773 | 0.22 | 13 | 1
December | 17 | 10AM to 11AM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
December | 17 | 11AM to 12PM | 57.2 | 46.7 | 35.6 | 30.7 | 18.49 | 0.0765 | 0.21 | 13.13 | 0
December | 17 | 12PM to 1PM | 57.2 | 46.1 | 33.8 | 28.6 | 18.16 | 0.0765 | 0.19 | 13.12 | 0
December | 17 | 1PM to 2PM | 57.2 | 45.5 | 32 | 26.6 | 17.85 | 0.0765 | 0.18 | 13.12 | 0
December | 17 | 2PM to 3PM | 57.2 | 44.8 | 30.2 | 24.4 | 17.52 | 0.0765 | 0.17 | 13.11 | 0
December | 17 | 3PM to 4PM | 57.2 | 44.2 | 28.4 | 22.5 | 17.22 | 0.0766 | 0.15 | 13.1 | 0
December | 17 | 4PM to 5PM | 53.6 | 42.4 | 28.4 | 22.5 | 16.35 | 0.0771 | 0.15 | 13.01 | 0
December | 17 | 5PM to 6PM | 51.8 | 40.9 | 26.6 | 20.7 | 15.63 | 0.0774 | 0.14 | 12.96 | 1
December | 17 | 6PM to 7PM | 51.8 | 40.9 | 26.6 | 20.7 | 15.63 | 0.0774 | 0.14 | 12.96 | 1
December | 17 | 7PM to 8PM | 51.8 | 40.3 | 24.8 | 19 | 15.37 | 0.0774 | 0.13 | 12.96 | 1
December | 17 | 8PM to 9PM | 50 | 40 | 26.6 | 20.7 | 15.2 | 0.0777 | 0.14 | 12.92 | 1
December | 17 | 9PM to 10PM | 50 | 39.4 | 24.8 | 19 | 14.94 | 0.0777 | 0.13 | 12.91 | 1
December | 17 | 10PM to 11PM | 48.2 | 38.4 | 24.8 | 19 | 14.5 | 0.0779 | 0.13 | 12.86 | 1
December | 17 | 11PM to 12AM | 46.4 | 37.8 | 25.9 | 20 | 14.22 | 0.0782 | 0.14 | 12.82 | 1
December | 18 | 12AM to 1AM | 44.6 | 37.1 | 26.6 | 20.7 | 13.89 | 0.0785 | 0.14 | 12.78 | 1
December | 18 | 1AM to 2AM | 39.2 | 34 | 26.6 | 20.7 | 12.59 | 0.0793 | 0.14 | 12.64 | 1
December | 18 | 2AM to 3AM | 35.6 | 33.3 | 30.2 | 24.4 | 12.3 | 0.0799 | 0.17 | 12.56 | 1
December | 18 | 3AM to 4AM | 33.8 | 32.3 | 30.2 | 24.4 | 11.87 | 0.0802 | 0.17 | 12.52 | 1
December | 18 | 4AM to 5AM | 32 | 30.4 | 28.4 | 22.5 | 11.13 | 0.0805 | 0.15 | 12.46 | 1
December | 18 | 5AM to 6AM | 30.2 | 29.4 | 28.4 | 22.5 | 10.7 | 0.0808 | 0.15 | 12.42 | 1
December | 18 | 6AM to 7AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
December | 18 | 7AM to 8AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 18 | 8AM to 9AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 18 | 9AM to 10AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 18 | 10AM to 11AM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
December | 18 | 11AM to 12PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
December | 18 | 12PM to 1PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 18 | 1PM to 2PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
December | 18 | 2PM to 3PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
December | 18 | 3PM to 4PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
December | 18 | 4PM to 5PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
December | 18 | 5PM to 6PM | 48.2 | 44.6 | 41 | 38 | 17.44 | 0.0778 | 0.26 | 12.92 | 1
December | 18 | 6PM to 7PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
December | 18 | 7PM to 8PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 18 | 8PM to 9PM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
December | 18 | 9PM to 10PM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 18 | 10PM to 11PM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 18 | 11PM to 12AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 19 | 12AM to 1AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 19 | 1AM to 2AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
December | 19 | 2AM to 3AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
December | 19 | 3AM to 4AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 19 | 4AM to 5AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 19 | 5AM to 6AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
December | 19 | 6AM to 7AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
December | 19 | 7AM to 8AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 19 | 8AM to 9AM | 42.8 | 40.3 | 37.4 | 33 | 15.36 | 0.0787 | 0.22 | 12.77 | 1
December | 19 | 9AM to 10AM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
December | 19 | 10AM to 11AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
December | 19 | 11AM to 12PM | 55.4 | 46.5 | 37.4 | 33 | 18.41 | 0.0768 | 0.22 | 13.09 | 0
December | 19 | 12PM to 1PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
December | 19 | 1PM to 2PM | 59 | 48.9 | 39.2 | 35.4 | 19.66 | 0.0762 | 0.24 | 13.19 | 0
December | 19 | 2PM to 3PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
December | 19 | 3PM to 4PM | 57.2 | 49.6 | 42.8 | 40.8 | 20.05 | 0.0764 | 0.28 | 13.16 | 0
December | 19 | 4PM to 5PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
December | 19 | 5PM to 6PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
December | 19 | 6PM to 7PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
December | 19 | 7PM to 8PM | 46.4 | 42.1 | 37.4 | 33 | 16.23 | 0.0781 | 0.22 | 12.86 | 1
December | 19 | 8PM to 9PM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
December | 19 | 9PM to 10PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 19 | 10PM to 11PM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
December | 19 | 11PM to 12AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
December | 20 | 12AM to 1AM | 41 | 38.6 | 35.6 | 30.7 | 14.57 | 0.079 | 0.21 | 12.72 | 1
December | 20 | 1AM to 2AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 20 | 2AM to 3AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
December | 20 | 3AM to 4AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 20 | 4AM to 5AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 20 | 5AM to 6AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
December | 20 | 6AM to 7AM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
December | 20 | 7AM to 8AM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
December | 20 | 8AM to 9AM | 42.8 | 40.3 | 37.4 | 33 | 15.36 | 0.0787 | 0.22 | 12.77 | 1
December | 20 | 9AM to 10AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
December | 20 | 10AM to 11AM | 50 | 44.7 | 39.2 | 35.4 | 17.48 | 0.0776 | 0.24 | 12.96 | 1
December | 20 | 11AM to 12PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
December | 20 | 12PM to 1PM | 57.2 | 46.7 | 35.6 | 30.7 | 18.49 | 0.0765 | 0.21 | 13.13 | 0
December | 20 | 1PM to 2PM | 59 | 48.9 | 39.2 | 35.4 | 19.66 | 0.0762 | 0.24 | 13.19 | 0
December | 20 | 2PM to 3PM | 59 | 47.5 | 35.6 | 30.7 | 18.93 | 0.0762 | 0.21 | 13.17 | 0
December | 20 | 3PM to 4PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
December | 20 | 4PM to 5PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
December | 20 | 5PM to 6PM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
December | 20 | 6PM to 7PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
December | 20 | 7PM to 8PM | 50 | 45.5 | 41 | 38 | 17.88 | 0.0775 | 0.26 | 12.97 | 1
December | 20 | 8PM to 9PM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
December | 20 | 9PM to 10PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 20 | 10PM to 11PM | 44.6 | 42.8 | 41 | 38 | 16.57 | 0.0784 | 0.26 | 12.83 | 1
December | 20 | 11PM to 12AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 21 | 12AM to 1AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 21 | 1AM to 2AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 21 | 2AM to 3AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 21 | 3AM to 4AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 21 | 4AM to 5AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 21 | 5AM to 6AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 21 | 6AM to 7AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 21 | 7AM to 8AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 21 | 8AM to 9AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 21 | 9AM to 10AM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
December | 21 | 10AM to 11AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 21 | 11AM to 12PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 21 | 12PM to 1PM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
December | 21 | 1PM to 2PM | 55.4 | 51.4 | 48.2 | 50.1 | 21.07 | 0.0766 | 0.34 | 13.14 | 0
December | 21 | 2PM to 3PM | 57.2 | 53.1 | 50 | 53.7 | 22.06 | 0.0764 | 0.36 | 13.2 | 0
December | 21 | 3PM to 4PM | 57.2 | 52.2 | 48.2 | 50.1 | 21.51 | 0.0764 | 0.34 | 13.19 | 0
December | 21 | 4PM to 5PM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
December | 21 | 5PM to 6PM | 51.8 | 49.8 | 48.2 | 50.1 | 20.2 | 0.0772 | 0.34 | 13.05 | 1
December | 21 | 6PM to 7PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 21 | 7PM to 8PM | 53.6 | 49.7 | 46.4 | 46.8 | 20.12 | 0.0769 | 0.32 | 13.08 | 0
December | 21 | 8PM to 9PM | 51.8 | 48.9 | 46.4 | 46.8 | 19.68 | 0.0772 | 0.32 | 13.04 | 1
December | 21 | 9PM to 10PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 21 | 10PM to 11PM | 48.2 | 47.2 | 46.4 | 46.8 | 18.81 | 0.0778 | 0.32 | 12.95 | 1
December | 21 | 11PM to 12AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 22 | 12AM to 1AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 22 | 1AM to 2AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 22 | 2AM to 3AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 22 | 3AM to 4AM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 22 | 4AM to 5AM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 22 | 5AM to 6AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 22 | 6AM to 7AM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 22 | 7AM to 8AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 22 | 8AM to 9AM | 50 | 48.1 | 46.4 | 46.8 | 19.24 | 0.0775 | 0.32 | 12.99 | 1
December | 22 | 9AM to 10AM | 53.6 | 50.6 | 48.2 | 50.1 | 20.63 | 0.0769 | 0.34 | 13.09 | 0
December | 22 | 10AM to 11AM | 55.4 | 50.5 | 46.4 | 46.8 | 20.56 | 0.0767 | 0.32 | 13.13 | 0
December | 22 | 11AM to 12PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
December | 22 | 12PM to 1PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
December | 22 | 1PM to 2PM | 59 | 51.2 | 44.6 | 43.7 | 20.95 | 0.0762 | 0.3 | 13.21 | 0
December | 22 | 2PM to 3PM | 59 | 50.4 | 42.8 | 40.8 | 20.49 | 0.0762 | 0.28 | 13.2 | 0
December | 22 | 3PM to 4PM | 57.2 | 50.4 | 44.6 | 43.7 | 20.51 | 0.0764 | 0.3 | 13.17 | 0
December | 22 | 4PM to 5PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
December | 22 | 5PM to 6PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 22 | 6PM to 7PM | 50 | 46.3 | 42.8 | 40.8 | 18.31 | 0.0775 | 0.28 | 12.97 | 1
December | 22 | 7PM to 8PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 22 | 8PM to 9PM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 22 | 9PM to 10PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 22 | 10PM to 11PM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
December | 22 | 11PM to 12AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
December | 23 | 12AM to 1AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 23 | 1AM to 2AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 23 | 2AM to 3AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 23 | 3AM to 4AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 23 | 4AM to 5AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 23 | 5AM to 6AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 23 | 6AM to 7AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 23 | 7AM to 8AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 23 | 8AM to 9AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 23 | 9AM to 10AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 23 | 10AM to 11AM | 44.6 | 44.6 | 44.6 | 43.7 | 17.45 | 0.0783 | 0.3 | 12.85 | 1
December | 23 | 11AM to 12PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 23 | 12PM to 1PM | 50 | 47.2 | 44.6 | 43.7 | 18.76 | 0.0775 | 0.3 | 12.98 | 1
December | 23 | 1PM to 2PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 23 | 2PM to 3PM | 51.8 | 48 | 44.6 | 43.7 | 19.2 | 0.0772 | 0.3 | 13.03 | 1
December | 23 | 3PM to 4PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 23 | 4PM to 5PM | 48.2 | 46.3 | 44.6 | 43.7 | 18.32 | 0.0778 | 0.3 | 12.94 | 1
December | 23 | 5PM to 6PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 23 | 6PM to 7PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 23 | 7PM to 8PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 23 | 8PM to 9PM | 46.4 | 45.5 | 44.6 | 43.7 | 17.89 | 0.0781 | 0.3 | 12.89 | 1
December | 23 | 9PM to 10PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 23 | 10PM to 11PM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
December | 23 | 11PM to 12AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
December | 24 | 12AM to 1AM | 42.8 | 41.9 | 41 | 38 | 16.13 | 0.0787 | 0.26 | 12.78 | 1
December | 24 | 1AM to 2AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 24 | 2AM to 3AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 24 | 3AM to 4AM | 39.2 | 39.2 | 39.2 | 35.4 | 14.86 | 0.0792 | 0.24 | 12.68 | 1
December | 24 | 4AM to 5AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 24 | 5AM to 6AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 24 | 6AM to 7AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 24 | 7AM to 8AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 24 | 8AM to 9AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 24 | 9AM to 10AM | 42.8 | 42.8 | 42.8 | 40.8 | 16.56 | 0.0786 | 0.28 | 12.79 | 1
December | 24 | 10AM to 11AM | 46.4 | 44.6 | 42.8 | 40.8 | 17.43 | 0.0781 | 0.28 | 12.88 | 1
December | 24 | 11AM to 12PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 24 | 12PM to 1PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
December | 24 | 1PM to 2PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
December | 24 | 2PM to 3PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
December | 24 | 3PM to 4PM | 57.2 | 46.7 | 35.6 | 30.7 | 18.49 | 0.0765 | 0.21 | 13.13 | 0
December | 24 | 4PM to 5PM | 53.6 | 44.3 | 33.8 | 28.6 | 17.29 | 0.0771 | 0.19 | 13.03 | 0
December | 24 | 5PM to 6PM | 51.8 | 42.8 | 32 | 26.6 | 16.54 | 0.0773 | 0.18 | 12.98 | 1
December | 24 | 6PM to 7PM | 51.8 | 42.8 | 32 | 26.6 | 16.54 | 0.0773 | 0.18 | 12.98 | 1
December | 24 | 7PM to 8PM | 50 | 41.9 | 32 | 26.6 | 16.11 | 0.0776 | 0.18 | 12.93 | 1
December | 24 | 8PM to 9PM | 50 | 41.9 | 32 | 26.6 | 16.11 | 0.0776 | 0.18 | 12.93 | 1
December | 24 | 9PM to 10PM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
December | 24 | 10PM to 11PM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
December | 24 | 11PM to 12AM | 48.2 | 40.3 | 30.2 | 24.4 | 15.35 | 0.0779 | 0.17 | 12.88 | 1
December | 25 | 12AM to 1AM | 46.4 | 39.3 | 30.2 | 24.4 | 14.91 | 0.0782 | 0.17 | 12.84 | 1
December | 25 | 1AM to 2AM | 46.4 | 38.7 | 28.4 | 22.5 | 14.61 | 0.0782 | 0.15 | 12.83 | 1
December | 25 | 2AM to 3AM | 46.4 | 38.7 | 28.4 | 22.5 | 14.61 | 0.0782 | 0.15 | 12.83 | 1
December | 25 | 3AM to 4AM | 39.2 | 35.4 | 30.2 | 24.4 | 13.17 | 0.0793 | 0.17 | 12.65 | 1
December | 25 | 4AM to 5AM | 37.4 | 33.6 | 28.4 | 22.5 | 12.44 | 0.0796 | 0.15 | 12.6 | 1
December | 25 | 5AM to 6AM | 33.8 | 31.4 | 28.4 | 22.5 | 11.57 | 0.0802 | 0.15 | 12.51 | 1
December | 25 | 6AM to 7AM | 35.6 | 32.6 | 28.4 | 22.5 | 12 | 0.0799 | 0.15 | 12.56 | 1
December | 25 | 7AM to 8AM | 33.8 | 32.3 | 30.2 | 24.4 | 11.87 | 0.0802 | 0.17 | 12.52 | 1
December | 25 | 8AM to 9AM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
December | 25 | 9AM to 10AM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
December | 25 | 10AM to 11AM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
December | 25 | 11AM to 12PM | 48.2 | 42.3 | 35.6 | 30.7 | 16.31 | 0.0779 | 0.21 | 12.9 | 1
December | 25 | 12PM to 1PM | 49.8 | 43.2 | 35.8 | 30.9 | 16.74 | 0.0776 | 0.21 | 12.94 | 1
December | 25 | 1PM to 2PM | 51.1 | 43.8 | 35.6 | 30.7 | 17.01 | 0.0774 | 0.21 | 12.97 | 1
December | 25 | 2PM to 3PM | 51.8 | 44.1 | 35.6 | 30.7 | 17.18 | 0.0773 | 0.21 | 12.99 | 1
December | 25 | 3PM to 4PM | 50 | 43.2 | 35.6 | 30.7 | 16.75 | 0.0776 | 0.21 | 12.94 | 1
December | 25 | 4PM to 5PM | 46.4 | 41.4 | 35.6 | 30.7 | 15.88 | 0.0781 | 0.21 | 12.85 | 1
December | 25 | 5PM to 6PM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
December | 25 | 6PM to 7PM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
December | 25 | 7PM to 8PM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
December | 25 | 8PM to 9PM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 25 | 9PM to 10PM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 25 | 10PM to 11PM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
December | 25 | 11PM to 12AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 26 | 12AM to 1AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 26 | 1AM to 2AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 26 | 2AM to 3AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 26 | 3AM to 4AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 26 | 4AM to 5AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 26 | 5AM to 6AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 26 | 6AM to 7AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
December | 26 | 7AM to 8AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 26 | 8AM to 9AM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 26 | 9AM to 10AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 26 | 10AM to 11AM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
December | 26 | 11AM to 12PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
December | 26 | 12PM to 1PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 26 | 1PM to 2PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
December | 26 | 2PM to 3PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
December | 26 | 3PM to 4PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
December | 26 | 4PM to 5PM | 51.8 | 46.3 | 41 | 38 | 18.32 | 0.0773 | 0.26 | 13.01 | 1
December | 26 | 5PM to 6PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
December | 26 | 6PM to 7PM | 44.6 | 41.2 | 37.4 | 33 | 15.79 | 0.0784 | 0.22 | 12.81 | 1
December | 26 | 7PM to 8PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
December | 26 | 8PM to 9PM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
December | 26 | 9PM to 10PM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 26 | 10PM to 11PM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 26 | 11PM to 12AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 27 | 12AM to 1AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 27 | 1AM to 2AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 27 | 2AM to 3AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 27 | 3AM to 4AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 27 | 4AM to 5AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 27 | 5AM to 6AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 27 | 6AM to 7AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 27 | 7AM to 8AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 27 | 8AM to 9AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 27 | 9AM to 10AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 27 | 10AM to 11AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
December | 27 | 11AM to 12PM | 51.8 | 45.6 | 39.2 | 35.4 | 17.91 | 0.0773 | 0.24 | 13 | 1
December | 27 | 12PM to 1PM | 53.6 | 46.4 | 39.2 | 35.4 | 18.35 | 0.077 | 0.24 | 13.05 | 0
December | 27 | 1PM to 2PM | 57.2 | 47.4 | 37.4 | 33 | 18.85 | 0.0765 | 0.22 | 13.13 | 0
December | 27 | 2PM to 3PM | 59 | 47.5 | 35.6 | 30.7 | 18.93 | 0.0762 | 0.21 | 13.17 | 0
December | 27 | 3PM to 4PM | 57.2 | 46.1 | 33.8 | 28.6 | 18.16 | 0.0765 | 0.19 | 13.12 | 0
December | 27 | 4PM to 5PM | 53.6 | 45.7 | 37.4 | 33 | 17.97 | 0.077 | 0.22 | 13.04 | 0
December | 27 | 5PM to 6PM | 48.2 | 43 | 37.4 | 33 | 16.67 | 0.0778 | 0.22 | 12.91 | 1
December | 27 | 6PM to 7PM | 44.6 | 40.5 | 35.6 | 30.7 | 15.44 | 0.0784 | 0.21 | 12.81 | 1
December | 27 | 7PM to 8PM | 42.8 | 38.8 | 33.8 | 28.6 | 14.68 | 0.0787 | 0.19 | 12.76 | 1
December | 27 | 8PM to 9PM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
December | 27 | 9PM to 10PM | 39.2 | 36.8 | 33.8 | 28.6 | 13.81 | 0.0793 | 0.19 | 12.66 | 1
December | 27 | 10PM to 11PM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
December | 27 | 11PM to 12AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 28 | 12AM to 1AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 28 | 1AM to 2AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 28 | 2AM to 3AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
December | 28 | 3AM to 4AM | 28.4 | 28.4 | 28.4 | 22.5 | 10.26 | 0.0811 | 0.15 | 12.37 | 1
December | 28 | 4AM to 5AM | 30.2 | 29.4 | 28.4 | 22.5 | 10.7 | 0.0808 | 0.15 | 12.42 | 1
December | 28 | 5AM to 6AM | 28.4 | 28.4 | 28.4 | 22.5 | 10.26 | 0.0811 | 0.15 | 12.37 | 1
December | 28 | 6AM to 7AM | 30.2 | 29.4 | 28.4 | 22.5 | 10.7 | 0.0808 | 0.15 | 12.42 | 1
December | 28 | 7AM to 8AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 28 | 8AM to 9AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
December | 28 | 9AM to 10AM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 28 | 10AM to 11AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 28 | 11AM to 12PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
December | 28 | 12PM to 1PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 28 | 1PM to 2PM | 55.4 | 48 | 41 | 38 | 19.19 | 0.0767 | 0.26 | 13.1 | 0
December | 28 | 2PM to 3PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
December | 28 | 3PM to 4PM | 55.4 | 47.2 | 39.2 | 35.4 | 18.79 | 0.0767 | 0.24 | 13.1 | 0
December | 28 | 4PM to 5PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
December | 28 | 5PM to 6PM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
December | 28 | 6PM to 7PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
December | 28 | 7PM to 8PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 28 | 8PM to 9PM | 39.2 | 37.6 | 35.6 | 30.7 | 14.14 | 0.0793 | 0.21 | 12.67 | 1
December | 28 | 9PM to 10PM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 28 | 10PM to 11PM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 28 | 11PM to 12AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 29 | 12AM to 1AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 29 | 1AM to 2AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
December | 29 | 2AM to 3AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 29 | 3AM to 4AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 29 | 4AM to 5AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 29 | 5AM to 6AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 29 | 6AM to 7AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
December | 29 | 7AM to 8AM | 30.2 | 29.4 | 28.4 | 22.5 | 10.7 | 0.0808 | 0.15 | 12.42 | 1
December | 29 | 8AM to 9AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 29 | 9AM to 10AM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 29 | 10AM to 11AM | 48.2 | 43.8 | 39.2 | 35.4 | 17.04 | 0.0778 | 0.24 | 12.91 | 1
December | 29 | 11AM to 12PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
December | 29 | 12PM to 1PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 29 | 1PM to 2PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
December | 29 | 2PM to 3PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
December | 29 | 3PM to 4PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
December | 29 | 4PM to 5PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 29 | 5PM to 6PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
December | 29 | 6PM to 7PM | 46.4 | 43.7 | 41 | 38 | 17.01 | 0.0781 | 0.26 | 12.87 | 1
December | 29 | 7PM to 8PM | 42.8 | 41.1 | 39.2 | 35.4 | 15.73 | 0.0787 | 0.24 | 12.78 | 1
December | 29 | 8PM to 9PM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 29 | 9PM to 10PM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 29 | 10PM to 11PM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 29 | 11PM to 12AM | 32 | 32 | 32 | 26.6 | 11.76 | 0.0805 | 0.18 | 12.48 | 1
December | 30 | 12AM to 1AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 30 | 1AM to 2AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
December | 30 | 2AM to 3AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 30 | 3AM to 4AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 30 | 4AM to 5AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 30 | 5AM to 6AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 30 | 6AM to 7AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 30 | 7AM to 8AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 30 | 8AM to 9AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 30 | 9AM to 10AM | 35.6 | 35.6 | 35.6 | 30.7 | 13.27 | 0.0798 | 0.21 | 12.58 | 1
December | 30 | 10AM to 11AM | 41 | 39.3 | 37.4 | 33 | 14.92 | 0.079 | 0.22 | 12.72 | 1
December | 30 | 11AM to 12PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 30 | 12PM to 1PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
December | 30 | 1PM to 2PM | 55.4 | 48.8 | 42.8 | 40.8 | 19.62 | 0.0767 | 0.28 | 13.11 | 0
December | 30 | 2PM to 3PM | 59 | 49.6 | 41 | 38 | 20.06 | 0.0762 | 0.26 | 13.2 | 0
December | 30 | 3PM to 4PM | 57.2 | 48.8 | 41 | 38 | 19.62 | 0.0765 | 0.26 | 13.15 | 0
December | 30 | 4PM to 5PM | 53.6 | 47.2 | 41 | 38 | 18.75 | 0.077 | 0.26 | 13.06 | 0
December | 30 | 5PM to 6PM | 46.4 | 42.9 | 39.2 | 35.4 | 16.61 | 0.0781 | 0.24 | 12.87 | 1
December | 30 | 6PM to 7PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
December | 30 | 7PM to 8PM | 42.8 | 40.3 | 37.4 | 33 | 15.36 | 0.0787 | 0.22 | 12.77 | 1
December | 30 | 8PM to 9PM | 37.4 | 35.8 | 33.8 | 28.6 | 13.37 | 0.0796 | 0.19 | 12.62 | 1
December | 30 | 9PM to 10PM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 30 | 10PM to 11PM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 30 | 11PM to 12AM | 33.8 | 33.1 | 32 | 26.6 | 12.19 | 0.0802 | 0.18 | 12.52 | 1
December | 31 | 12AM to 1AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1
December | 31 | 1AM to 2AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 31 | 2AM to 3AM | 30.2 | 30.2 | 30.2 | 24.4 | 11 | 0.0808 | 0.17 | 12.42 | 1
December | 31 | 3AM to 4AM | 28.4 | 28.4 | 28.4 | 22.5 | 10.26 | 0.0811 | 0.15 | 12.37 | 1
December | 31 | 4AM to 5AM | 32 | 31.2 | 30.2 | 24.4 | 11.43 | 0.0805 | 0.17 | 12.47 | 1
December | 31 | 5AM to 6AM | 33.8 | 32.3 | 30.2 | 24.4 | 11.87 | 0.0802 | 0.17 | 12.52 | 1
December | 31 | 6AM to 7AM | 33.8 | 32.3 | 30.2 | 24.4 | 11.87 | 0.0802 | 0.17 | 12.52 | 1
December | 31 | 7AM to 8AM | 35.6 | 34.1 | 32 | 26.6 | 12.63 | 0.0799 | 0.18 | 12.57 | 1
December | 31 | 8AM to 9AM | 35.6 | 34.8 | 33.8 | 28.6 | 12.94 | 0.0799 | 0.19 | 12.57 | 1
December | 31 | 9AM to 10AM | 37.4 | 36.6 | 35.6 | 30.7 | 13.7 | 0.0796 | 0.21 | 12.62 | 1
December | 31 | 10AM to 11AM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 31 | 11AM to 12PM | 44.6 | 43.7 | 42.8 | 40.8 | 17 | 0.0784 | 0.28 | 12.84 | 1
December | 31 | 12PM to 1PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
December | 31 | 1PM to 2PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 31 | 2PM to 3PM | 53.6 | 48 | 42.8 | 40.8 | 19.18 | 0.077 | 0.28 | 13.07 | 0
December | 31 | 3PM to 4PM | 53.6 | 48.8 | 44.6 | 43.7 | 19.63 | 0.077 | 0.3 | 13.07 | 0
December | 31 | 4PM to 5PM | 51.8 | 47.1 | 42.8 | 40.8 | 18.74 | 0.0773 | 0.28 | 13.02 | 1
December | 31 | 5PM to 6PM | 48.2 | 45.4 | 42.8 | 40.8 | 17.87 | 0.0778 | 0.28 | 12.93 | 1
December | 31 | 6PM to 7PM | 44.6 | 42 | 39.2 | 35.4 | 16.17 | 0.0784 | 0.24 | 12.82 | 1
December | 31 | 7PM to 8PM | 41 | 40.1 | 39.2 | 35.4 | 15.3 | 0.079 | 0.24 | 12.73 | 1
December | 31 | 8PM to 9PM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 31 | 9PM to 10PM | 37.4 | 37.4 | 37.4 | 33 | 14.05 | 0.0795 | 0.22 | 12.63 | 1
December | 31 | 10PM to 11PM | 39.2 | 38.4 | 37.4 | 33 | 14.49 | 0.0793 | 0.22 | 12.68 | 1
December | 31 | 11PM to 12AM | 33.8 | 33.8 | 33.8 | 28.6 | 12.5 | 0.0802 | 0.19 | 12.53 | 1

## Honolulu HI TMY3 File
Country: USA | [7 empty] | OAT Flag Trigger Set Point - | 52 | °F
State: HAWAII | [8 empty] | Back to HOA kW and kWh Saving tab
City: HONOLULU_INTL_ARPT | [8 empty] | Back to Optimized kW and kWh Savings tab
Altitude: 6 ft. | [9 empty] | Number of hours less than 52.0°F in the data set - | 0
Month | Day | Hour | Dry Bulb | Wet Bulb | Dew Point | Humidity Ratio | Enthalpy | Density | Vapor Pressure | Specific Volume | 1 if the OAT is less than 52.0°F
|  |  | °F | °F | °F | gr/lb | btu/lb | lb/cu.ft. | in. HG | cu.ft./lb
January | 1 | 12AM to 1AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
January | 1 | 1AM to 2AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
January | 1 | 2AM to 3AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 1 | 3AM to 4AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
January | 1 | 4AM to 5AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
January | 1 | 5AM to 6AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
January | 1 | 6AM to 7AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
January | 1 | 7AM to 8AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
January | 1 | 8AM to 9AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
January | 1 | 9AM to 10AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
January | 1 | 10AM to 11AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
January | 1 | 11AM to 12PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
January | 1 | 12PM to 1PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
January | 1 | 1PM to 2PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
January | 1 | 2PM to 3PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
January | 1 | 3PM to 4PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
January | 1 | 4PM to 5PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
January | 1 | 5PM to 6PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
January | 1 | 6PM to 7PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
January | 1 | 7PM to 8PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
January | 1 | 8PM to 9PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
January | 1 | 9PM to 10PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
January | 1 | 10PM to 11PM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
January | 1 | 11PM to 12AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
January | 2 | 12AM to 1AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
January | 2 | 1AM to 2AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
January | 2 | 2AM to 3AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
January | 2 | 3AM to 4AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
January | 2 | 4AM to 5AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
January | 2 | 5AM to 6AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
January | 2 | 6AM to 7AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
January | 2 | 7AM to 8AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
January | 2 | 8AM to 9AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
January | 2 | 9AM to 10AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
January | 2 | 10AM to 11AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
January | 2 | 11AM to 12PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
January | 2 | 12PM to 1PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
January | 2 | 1PM to 2PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
January | 2 | 2PM to 3PM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
January | 2 | 3PM to 4PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
January | 2 | 4PM to 5PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
January | 2 | 5PM to 6PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
January | 2 | 6PM to 7PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
January | 2 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
January | 2 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
January | 2 | 9PM to 10PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
January | 2 | 10PM to 11PM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
January | 2 | 11PM to 12AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
January | 3 | 12AM to 1AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
January | 3 | 1AM to 2AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
January | 3 | 2AM to 3AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
January | 3 | 3AM to 4AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
January | 3 | 4AM to 5AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
January | 3 | 5AM to 6AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
January | 3 | 6AM to 7AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
January | 3 | 7AM to 8AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
January | 3 | 8AM to 9AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
January | 3 | 9AM to 10AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
January | 3 | 10AM to 11AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
January | 3 | 11AM to 12PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
January | 3 | 12PM to 1PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
January | 3 | 1PM to 2PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
January | 3 | 2PM to 3PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
January | 3 | 3PM to 4PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
January | 3 | 4PM to 5PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
January | 3 | 5PM to 6PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
January | 3 | 6PM to 7PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
January | 3 | 7PM to 8PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
January | 3 | 8PM to 9PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
January | 3 | 9PM to 10PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
January | 3 | 10PM to 11PM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
January | 3 | 11PM to 12AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
January | 4 | 12AM to 1AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
January | 4 | 1AM to 2AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
January | 4 | 2AM to 3AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
January | 4 | 3AM to 4AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
January | 4 | 4AM to 5AM | 66.9 | 65.6 | 64.9 | 92.7 | 30.51 | 0.0747 | 0.62 | 13.56 | 0
January | 4 | 5AM to 6AM | 68 | 66.7 | 66 | 96.3 | 31.34 | 0.0746 | 0.64 | 13.59 | 0
January | 4 | 6AM to 7AM | 66 | 65.3 | 64.9 | 92.7 | 30.28 | 0.0749 | 0.62 | 13.53 | 0
January | 4 | 7AM to 8AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
January | 4 | 8AM to 9AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
January | 4 | 9AM to 10AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
January | 4 | 10AM to 11AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
January | 4 | 11AM to 12PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
January | 4 | 12PM to 1PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
January | 4 | 1PM to 2PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
January | 4 | 2PM to 3PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
January | 4 | 3PM to 4PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
January | 4 | 4PM to 5PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
January | 4 | 5PM to 6PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
January | 4 | 6PM to 7PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
January | 4 | 7PM to 8PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
January | 4 | 8PM to 9PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
January | 4 | 9PM to 10PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
January | 4 | 10PM to 11PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
January | 4 | 11PM to 12AM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
January | 5 | 12AM to 1AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
January | 5 | 1AM to 2AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
January | 5 | 2AM to 3AM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
January | 5 | 3AM to 4AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
January | 5 | 4AM to 5AM | 64 | 62.1 | 61 | 80.4 | 27.89 | 0.0752 | 0.54 | 13.44 | 0
January | 5 | 5AM to 6AM | 64 | 63.3 | 63 | 86.4 | 28.81 | 0.0752 | 0.58 | 13.46 | 0
January | 5 | 6AM to 7AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
January | 5 | 7AM to 8AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
January | 5 | 8AM to 9AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
January | 5 | 9AM to 10AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
January | 5 | 10AM to 11AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
January | 5 | 11AM to 12PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
January | 5 | 12PM to 1PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
January | 5 | 1PM to 2PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
January | 5 | 2PM to 3PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
January | 5 | 3PM to 4PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
January | 5 | 4PM to 5PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
January | 5 | 5PM to 6PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
January | 5 | 6PM to 7PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
January | 5 | 7PM to 8PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
January | 5 | 8PM to 9PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
January | 5 | 9PM to 10PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
January | 5 | 10PM to 11PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
January | 5 | 11PM to 12AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
January | 6 | 12AM to 1AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
January | 6 | 1AM to 2AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
January | 6 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
January | 6 | 3AM to 4AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
January | 6 | 4AM to 5AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 6 | 5AM to 6AM | 64.9 | 63.6 | 63 | 86.4 | 29.03 | 0.0751 | 0.58 | 13.49 | 0
January | 6 | 6AM to 7AM | 64 | 63.3 | 63 | 86.4 | 28.81 | 0.0752 | 0.58 | 13.46 | 0
January | 6 | 7AM to 8AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
January | 6 | 8AM to 9AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
January | 6 | 9AM to 10AM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
January | 6 | 10AM to 11AM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
January | 6 | 11AM to 12PM | 84.9 | 69.5 | 62.1 | 83.6 | 33.51 | 0.0723 | 0.56 | 13.99 | 0
January | 6 | 12PM to 1PM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
January | 6 | 1PM to 2PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
January | 6 | 2PM to 3PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
January | 6 | 3PM to 4PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
January | 6 | 4PM to 5PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
January | 6 | 5PM to 6PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
January | 6 | 6PM to 7PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
January | 6 | 7PM to 8PM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
January | 6 | 8PM to 9PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
January | 6 | 9PM to 10PM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
January | 6 | 10PM to 11PM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
January | 6 | 11PM to 12AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
January | 7 | 12AM to 1AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
January | 7 | 1AM to 2AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
January | 7 | 2AM to 3AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
January | 7 | 3AM to 4AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
January | 7 | 4AM to 5AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
January | 7 | 5AM to 6AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
January | 7 | 6AM to 7AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
January | 7 | 7AM to 8AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
January | 7 | 8AM to 9AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
January | 7 | 9AM to 10AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
January | 7 | 10AM to 11AM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
January | 7 | 11AM to 12PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
January | 7 | 12PM to 1PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
January | 7 | 1PM to 2PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
January | 7 | 2PM to 3PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
January | 7 | 3PM to 4PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
January | 7 | 4PM to 5PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
January | 7 | 5PM to 6PM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
January | 7 | 6PM to 7PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
January | 7 | 7PM to 8PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
January | 7 | 8PM to 9PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
January | 7 | 9PM to 10PM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
January | 7 | 10PM to 11PM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
January | 7 | 11PM to 12AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
January | 8 | 12AM to 1AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
January | 8 | 1AM to 2AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
January | 8 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
January | 8 | 3AM to 4AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
January | 8 | 4AM to 5AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
January | 8 | 5AM to 6AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
January | 8 | 6AM to 7AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
January | 8 | 7AM to 8AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
January | 8 | 8AM to 9AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
January | 8 | 9AM to 10AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
January | 8 | 10AM to 11AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
January | 8 | 11AM to 12PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
January | 8 | 12PM to 1PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
January | 8 | 1PM to 2PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
January | 8 | 2PM to 3PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
January | 8 | 3PM to 4PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
January | 8 | 4PM to 5PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
January | 8 | 5PM to 6PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
January | 8 | 6PM to 7PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
January | 8 | 7PM to 8PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
January | 8 | 8PM to 9PM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
January | 8 | 9PM to 10PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
January | 8 | 10PM to 11PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
January | 8 | 11PM to 12AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
January | 9 | 12AM to 1AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
January | 9 | 1AM to 2AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
January | 9 | 2AM to 3AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 9 | 3AM to 4AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
January | 9 | 4AM to 5AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
January | 9 | 5AM to 6AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 9 | 6AM to 7AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
January | 9 | 7AM to 8AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
January | 9 | 8AM to 9AM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
January | 9 | 9AM to 10AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
January | 9 | 10AM to 11AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
January | 9 | 11AM to 12PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
January | 9 | 12PM to 1PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
January | 9 | 1PM to 2PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
January | 9 | 2PM to 3PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
January | 9 | 3PM to 4PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
January | 9 | 4PM to 5PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
January | 9 | 5PM to 6PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
January | 9 | 6PM to 7PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
January | 9 | 7PM to 8PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
January | 9 | 8PM to 9PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 9 | 9PM to 10PM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 9 | 10PM to 11PM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 9 | 11PM to 12AM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
January | 10 | 12AM to 1AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
January | 10 | 1AM to 2AM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
January | 10 | 2AM to 3AM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
January | 10 | 3AM to 4AM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
January | 10 | 4AM to 5AM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
January | 10 | 5AM to 6AM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
January | 10 | 6AM to 7AM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
January | 10 | 7AM to 8AM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
January | 10 | 8AM to 9AM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
January | 10 | 9AM to 10AM | 73 | 61.8 | 55 | 64.7 | 27.64 | 0.0741 | 0.44 | 13.63 | 0
January | 10 | 10AM to 11AM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
January | 10 | 11AM to 12PM | 78.1 | 63 | 54 | 62.2 | 28.47 | 0.0734 | 0.42 | 13.75 | 0
January | 10 | 12PM to 1PM | 79 | 63.9 | 55 | 64.7 | 29.09 | 0.0732 | 0.44 | 13.78 | 0
January | 10 | 1PM to 2PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
January | 10 | 2PM to 3PM | 78.1 | 63.6 | 55 | 64.7 | 28.87 | 0.0734 | 0.44 | 13.76 | 0
January | 10 | 3PM to 4PM | 77 | 63.2 | 55 | 64.7 | 28.61 | 0.0735 | 0.44 | 13.73 | 0
January | 10 | 4PM to 5PM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
January | 10 | 5PM to 6PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
January | 10 | 6PM to 7PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
January | 10 | 7PM to 8PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
January | 10 | 8PM to 9PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
January | 10 | 9PM to 10PM | 72 | 59.9 | 52 | 57.8 | 26.29 | 0.0743 | 0.39 | 13.58 | 0
January | 10 | 10PM to 11PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
January | 10 | 11PM to 12AM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
January | 11 | 12AM to 1AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
January | 11 | 1AM to 2AM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
January | 11 | 2AM to 3AM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
January | 11 | 3AM to 4AM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
January | 11 | 4AM to 5AM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
January | 11 | 5AM to 6AM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
January | 11 | 6AM to 7AM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
January | 11 | 7AM to 8AM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
January | 11 | 8AM to 9AM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
January | 11 | 9AM to 10AM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
January | 11 | 10AM to 11AM | 77 | 64.7 | 57.9 | 72 | 29.74 | 0.0735 | 0.48 | 13.75 | 0
January | 11 | 11AM to 12PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
January | 11 | 12PM to 1PM | 79 | 63.3 | 54 | 62.2 | 28.69 | 0.0733 | 0.42 | 13.77 | 0
January | 11 | 1PM to 2PM | 79 | 63.9 | 55 | 64.7 | 29.09 | 0.0732 | 0.44 | 13.78 | 0
January | 11 | 2PM to 3PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
January | 11 | 3PM to 4PM | 75 | 64.6 | 59 | 74.9 | 29.71 | 0.0737 | 0.5 | 13.71 | 0
January | 11 | 4PM to 5PM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
January | 11 | 5PM to 6PM | 73 | 62.3 | 55.9 | 66.9 | 27.98 | 0.074 | 0.45 | 13.63 | 0
January | 11 | 6PM to 7PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
January | 11 | 7PM to 8PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
January | 11 | 8PM to 9PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
January | 11 | 9PM to 10PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
January | 11 | 10PM to 11PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
January | 11 | 11PM to 12AM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
January | 12 | 12AM to 1AM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
January | 12 | 1AM to 2AM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
January | 12 | 2AM to 3AM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
January | 12 | 3AM to 4AM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
January | 12 | 4AM to 5AM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
January | 12 | 5AM to 6AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
January | 12 | 6AM to 7AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
January | 12 | 7AM to 8AM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
January | 12 | 8AM to 9AM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
January | 12 | 9AM to 10AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
January | 12 | 10AM to 11AM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
January | 12 | 11AM to 12PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
January | 12 | 12PM to 1PM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
January | 12 | 1PM to 2PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
January | 12 | 2PM to 3PM | 79 | 65.9 | 59 | 74.9 | 30.68 | 0.0732 | 0.5 | 13.81 | 0
January | 12 | 3PM to 4PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
January | 12 | 4PM to 5PM | 77 | 65.3 | 59 | 74.9 | 30.19 | 0.0735 | 0.5 | 13.76 | 0
January | 12 | 5PM to 6PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
January | 12 | 6PM to 7PM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
January | 12 | 7PM to 8PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 12 | 8PM to 9PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
January | 12 | 9PM to 10PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
January | 12 | 10PM to 11PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 12 | 11PM to 12AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 13 | 12AM to 1AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
January | 13 | 1AM to 2AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 13 | 2AM to 3AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 13 | 3AM to 4AM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
January | 13 | 4AM to 5AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 13 | 5AM to 6AM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
January | 13 | 6AM to 7AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
January | 13 | 7AM to 8AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
January | 13 | 8AM to 9AM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
January | 13 | 9AM to 10AM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
January | 13 | 10AM to 11AM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
January | 13 | 11AM to 12PM | 82 | 66.9 | 59 | 74.9 | 31.42 | 0.0728 | 0.5 | 13.89 | 0
January | 13 | 12PM to 1PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
January | 13 | 1PM to 2PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
January | 13 | 2PM to 3PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
January | 13 | 3PM to 4PM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
January | 13 | 4PM to 5PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
January | 13 | 5PM to 6PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
January | 13 | 6PM to 7PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
January | 13 | 7PM to 8PM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
January | 13 | 8PM to 9PM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
January | 13 | 9PM to 10PM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
January | 13 | 10PM to 11PM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
January | 13 | 11PM to 12AM | 66 | 62.2 | 60.1 | 77.8 | 27.97 | 0.075 | 0.52 | 13.49 | 0
January | 14 | 12AM to 1AM | 66.9 | 62.5 | 60.1 | 77.8 | 28.19 | 0.0748 | 0.52 | 13.51 | 0
January | 14 | 1AM to 2AM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
January | 14 | 2AM to 3AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
January | 14 | 3AM to 4AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
January | 14 | 4AM to 5AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
January | 14 | 5AM to 6AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
January | 14 | 6AM to 7AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
January | 14 | 7AM to 8AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
January | 14 | 8AM to 9AM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
January | 14 | 9AM to 10AM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
January | 14 | 10AM to 11AM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
January | 14 | 11AM to 12PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
January | 14 | 12PM to 1PM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
January | 14 | 1PM to 2PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
January | 14 | 2PM to 3PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
January | 14 | 3PM to 4PM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
January | 14 | 4PM to 5PM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
January | 14 | 5PM to 6PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
January | 14 | 6PM to 7PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
January | 14 | 7PM to 8PM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
January | 14 | 8PM to 9PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
January | 14 | 9PM to 10PM | 66.9 | 62.5 | 60.1 | 77.8 | 28.19 | 0.0748 | 0.52 | 13.51 | 0
January | 14 | 10PM to 11PM | 66 | 62.2 | 60.1 | 77.8 | 27.97 | 0.075 | 0.52 | 13.49 | 0
January | 14 | 11PM to 12AM | 66.9 | 61.9 | 59 | 74.9 | 27.72 | 0.0749 | 0.5 | 13.5 | 0
January | 15 | 12AM to 1AM | 66 | 62.2 | 60.1 | 77.8 | 27.97 | 0.075 | 0.52 | 13.49 | 0
January | 15 | 1AM to 2AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
January | 15 | 2AM to 3AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
January | 15 | 3AM to 4AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
January | 15 | 4AM to 5AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
January | 15 | 5AM to 6AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
January | 15 | 6AM to 7AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
January | 15 | 7AM to 8AM | 66.9 | 61.9 | 59 | 74.9 | 27.72 | 0.0749 | 0.5 | 13.5 | 0
January | 15 | 8AM to 9AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
January | 15 | 9AM to 10AM | 75 | 64.6 | 59 | 74.9 | 29.71 | 0.0737 | 0.5 | 13.71 | 0
January | 15 | 10AM to 11AM | 77 | 64.7 | 57.9 | 72 | 29.74 | 0.0735 | 0.48 | 13.75 | 0
January | 15 | 11AM to 12PM | 79 | 65.9 | 59 | 74.9 | 30.68 | 0.0732 | 0.5 | 13.81 | 0
January | 15 | 12PM to 1PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
January | 15 | 1PM to 2PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
January | 15 | 2PM to 3PM | 75 | 63.5 | 57 | 69.6 | 28.89 | 0.0738 | 0.47 | 13.69 | 0
January | 15 | 3PM to 4PM | 75.9 | 63.8 | 57 | 69.6 | 29.11 | 0.0736 | 0.47 | 13.72 | 0
January | 15 | 4PM to 5PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
January | 15 | 5PM to 6PM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
January | 15 | 6PM to 7PM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
January | 15 | 7PM to 8PM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
January | 15 | 8PM to 9PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
January | 15 | 9PM to 10PM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
January | 15 | 10PM to 11PM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
January | 15 | 11PM to 12AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
January | 16 | 12AM to 1AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
January | 16 | 1AM to 2AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
January | 16 | 2AM to 3AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
January | 16 | 3AM to 4AM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
January | 16 | 4AM to 5AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
January | 16 | 5AM to 6AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
January | 16 | 6AM to 7AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
January | 16 | 7AM to 8AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
January | 16 | 8AM to 9AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
January | 16 | 9AM to 10AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
January | 16 | 10AM to 11AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
January | 16 | 11AM to 12PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
January | 16 | 12PM to 1PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
January | 16 | 1PM to 2PM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
January | 16 | 2PM to 3PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
January | 16 | 3PM to 4PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
January | 16 | 4PM to 5PM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
January | 16 | 5PM to 6PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
January | 16 | 6PM to 7PM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
January | 16 | 7PM to 8PM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
January | 16 | 8PM to 9PM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
January | 16 | 9PM to 10PM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
January | 16 | 10PM to 11PM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
January | 16 | 11PM to 12AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
January | 17 | 12AM to 1AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
January | 17 | 1AM to 2AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
January | 17 | 2AM to 3AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
January | 17 | 3AM to 4AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
January | 17 | 4AM to 5AM | 63 | 61.7 | 61 | 80.4 | 27.62 | 0.0754 | 0.54 | 13.42 | 0
January | 17 | 5AM to 6AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
January | 17 | 6AM to 7AM | 64 | 63.3 | 63 | 86.4 | 28.81 | 0.0752 | 0.58 | 13.46 | 0
January | 17 | 7AM to 8AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
January | 17 | 8AM to 9AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
January | 17 | 9AM to 10AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
January | 17 | 10AM to 11AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
January | 17 | 11AM to 12PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
January | 17 | 12PM to 1PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
January | 17 | 1PM to 2PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
January | 17 | 2PM to 3PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
January | 17 | 3PM to 4PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
January | 17 | 4PM to 5PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
January | 17 | 5PM to 6PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
January | 17 | 6PM to 7PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
January | 17 | 7PM to 8PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
January | 17 | 8PM to 9PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 17 | 9PM to 10PM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
January | 17 | 10PM to 11PM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
January | 17 | 11PM to 12AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
January | 18 | 12AM to 1AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
January | 18 | 1AM to 2AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
January | 18 | 2AM to 3AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
January | 18 | 3AM to 4AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
January | 18 | 4AM to 5AM | 66.9 | 63.1 | 61 | 80.4 | 28.59 | 0.0748 | 0.54 | 13.52 | 0
January | 18 | 5AM to 6AM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
January | 18 | 6AM to 7AM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.53 | 0
January | 18 | 7AM to 8AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
January | 18 | 8AM to 9AM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
January | 18 | 9AM to 10AM | 78.1 | 64.6 | 57 | 69.6 | 29.64 | 0.0733 | 0.47 | 13.77 | 0
January | 18 | 10AM to 11AM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
January | 18 | 11AM to 12PM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
January | 18 | 12PM to 1PM | 81 | 65.5 | 57 | 69.6 | 30.34 | 0.0729 | 0.47 | 13.84 | 0
January | 18 | 1PM to 2PM | 81 | 66 | 57.9 | 72 | 30.71 | 0.0729 | 0.48 | 13.85 | 0
January | 18 | 2PM to 3PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
January | 18 | 3PM to 4PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
January | 18 | 4PM to 5PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
January | 18 | 5PM to 6PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
January | 18 | 6PM to 7PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
January | 18 | 7PM to 8PM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
January | 18 | 8PM to 9PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
January | 18 | 9PM to 10PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
January | 18 | 10PM to 11PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
January | 18 | 11PM to 12AM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
January | 19 | 12AM to 1AM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
January | 19 | 1AM to 2AM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
January | 19 | 2AM to 3AM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
January | 19 | 3AM to 4AM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
January | 19 | 4AM to 5AM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
January | 19 | 5AM to 6AM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
January | 19 | 6AM to 7AM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
January | 19 | 7AM to 8AM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
January | 19 | 8AM to 9AM | 70 | 57.7 | 48.9 | 51.5 | 24.83 | 0.0746 | 0.35 | 13.51 | 0
January | 19 | 9AM to 10AM | 73 | 58.8 | 48.9 | 51.5 | 25.57 | 0.0741 | 0.35 | 13.59 | 0
January | 19 | 10AM to 11AM | 73.9 | 59.6 | 50 | 53.6 | 26.13 | 0.074 | 0.36 | 13.62 | 0
January | 19 | 11AM to 12PM | 73 | 59.8 | 51.1 | 55.9 | 26.25 | 0.0741 | 0.38 | 13.6 | 0
January | 19 | 12PM to 1PM | 75 | 61 | 52 | 57.8 | 27.04 | 0.0738 | 0.39 | 13.66 | 0
January | 19 | 1PM to 2PM | 75.9 | 59.9 | 48.9 | 51.5 | 26.27 | 0.0737 | 0.35 | 13.66 | 0
January | 19 | 2PM to 3PM | 75.9 | 61.8 | 53.1 | 60.1 | 27.63 | 0.0737 | 0.41 | 13.69 | 0
January | 19 | 3PM to 4PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
January | 19 | 4PM to 5PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
January | 19 | 5PM to 6PM | 71.1 | 60.1 | 53.1 | 60.1 | 26.44 | 0.0744 | 0.41 | 13.56 | 0
January | 19 | 6PM to 7PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
January | 19 | 7PM to 8PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
January | 19 | 8PM to 9PM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
January | 19 | 9PM to 10PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
January | 19 | 10PM to 11PM | 69.1 | 57.3 | 48.9 | 51.5 | 24.61 | 0.0747 | 0.35 | 13.49 | 0
January | 19 | 11PM to 12AM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
January | 20 | 12AM to 1AM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
January | 20 | 1AM to 2AM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
January | 20 | 2AM to 3AM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
January | 20 | 3AM to 4AM | 66.9 | 56.1 | 48 | 49.8 | 23.81 | 0.075 | 0.34 | 13.42 | 0
January | 20 | 4AM to 5AM | 68 | 57.4 | 50 | 53.6 | 24.68 | 0.0748 | 0.36 | 13.46 | 0
January | 20 | 5AM to 6AM | 68 | 57.9 | 51.1 | 55.9 | 25.03 | 0.0748 | 0.38 | 13.47 | 0
January | 20 | 6AM to 7AM | 66.9 | 56.5 | 48.9 | 51.5 | 24.08 | 0.075 | 0.35 | 13.43 | 0
January | 20 | 7AM to 8AM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
January | 20 | 8AM to 9AM | 71.1 | 58.1 | 48.9 | 51.5 | 25.09 | 0.0744 | 0.35 | 13.54 | 0
January | 20 | 9AM to 10AM | 73.9 | 59.6 | 50 | 53.6 | 26.13 | 0.074 | 0.36 | 13.62 | 0
January | 20 | 10AM to 11AM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
January | 20 | 11AM to 12PM | 77 | 60.8 | 50 | 53.6 | 26.87 | 0.0736 | 0.36 | 13.69 | 0
January | 20 | 12PM to 1PM | 78.1 | 60.7 | 48.9 | 51.5 | 26.8 | 0.0735 | 0.35 | 13.71 | 0
January | 20 | 1PM to 2PM | 77 | 61.7 | 52 | 57.8 | 27.52 | 0.0736 | 0.39 | 13.71 | 0
January | 20 | 2PM to 3PM | 75.9 | 61.3 | 52 | 57.8 | 27.26 | 0.0737 | 0.39 | 13.68 | 0
January | 20 | 3PM to 4PM | 75.9 | 60.9 | 51.1 | 55.9 | 26.96 | 0.0737 | 0.38 | 13.67 | 0
January | 20 | 4PM to 5PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
January | 20 | 5PM to 6PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
January | 20 | 6PM to 7PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
January | 20 | 7PM to 8PM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
January | 20 | 8PM to 9PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
January | 20 | 9PM to 10PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
January | 20 | 10PM to 11PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
January | 20 | 11PM to 12AM | 71.1 | 59.5 | 52 | 57.8 | 26.07 | 0.0744 | 0.39 | 13.56 | 0
January | 21 | 12AM to 1AM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
January | 21 | 1AM to 2AM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
January | 21 | 2AM to 3AM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
January | 21 | 3AM to 4AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
January | 21 | 4AM to 5AM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
January | 21 | 5AM to 6AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
January | 21 | 6AM to 7AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
January | 21 | 7AM to 8AM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
January | 21 | 8AM to 9AM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
January | 21 | 9AM to 10AM | 73.9 | 60.6 | 52 | 57.8 | 26.77 | 0.074 | 0.39 | 13.63 | 0
January | 21 | 10AM to 11AM | 77 | 62.2 | 53.1 | 60.1 | 27.89 | 0.0735 | 0.41 | 13.71 | 0
January | 21 | 11AM to 12PM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
January | 21 | 12PM to 1PM | 78.1 | 62.6 | 53.1 | 60.1 | 28.15 | 0.0734 | 0.41 | 13.74 | 0
January | 21 | 1PM to 2PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
January | 21 | 2PM to 3PM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
January | 21 | 3PM to 4PM | 75 | 62.5 | 55 | 64.7 | 28.12 | 0.0738 | 0.44 | 13.68 | 0
January | 21 | 4PM to 5PM | 75 | 63 | 55.9 | 66.9 | 28.47 | 0.0738 | 0.45 | 13.68 | 0
January | 21 | 5PM to 6PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
January | 21 | 6PM to 7PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
January | 21 | 7PM to 8PM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
January | 21 | 8PM to 9PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
January | 21 | 9PM to 10PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
January | 21 | 10PM to 11PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
January | 21 | 11PM to 12AM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
January | 22 | 12AM to 1AM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
January | 22 | 1AM to 2AM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
January | 22 | 2AM to 3AM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
January | 22 | 3AM to 4AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
January | 22 | 4AM to 5AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
January | 22 | 5AM to 6AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
January | 22 | 6AM to 7AM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
January | 22 | 7AM to 8AM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
January | 22 | 8AM to 9AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
January | 22 | 9AM to 10AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
January | 22 | 10AM to 11AM | 75 | 65.2 | 60.1 | 77.8 | 30.17 | 0.0737 | 0.52 | 13.72 | 0
January | 22 | 11AM to 12PM | 78.1 | 64.6 | 57 | 69.6 | 29.64 | 0.0733 | 0.47 | 13.77 | 0
January | 22 | 12PM to 1PM | 79 | 63.9 | 55 | 64.7 | 29.09 | 0.0732 | 0.44 | 13.78 | 0
January | 22 | 1PM to 2PM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
January | 22 | 2PM to 3PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
January | 22 | 3PM to 4PM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
January | 22 | 4PM to 5PM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
January | 22 | 5PM to 6PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
January | 22 | 6PM to 7PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
January | 22 | 7PM to 8PM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
January | 22 | 8PM to 9PM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
January | 22 | 9PM to 10PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
January | 22 | 10PM to 11PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
January | 22 | 11PM to 12AM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
January | 23 | 12AM to 1AM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
January | 23 | 1AM to 2AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
January | 23 | 2AM to 3AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
January | 23 | 3AM to 4AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
January | 23 | 4AM to 5AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
January | 23 | 5AM to 6AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
January | 23 | 6AM to 7AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
January | 23 | 7AM to 8AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
January | 23 | 8AM to 9AM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
January | 23 | 9AM to 10AM | 75.9 | 64.9 | 59 | 74.9 | 29.93 | 0.0736 | 0.5 | 13.73 | 0
January | 23 | 10AM to 11AM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
January | 23 | 11AM to 12PM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
January | 23 | 12PM to 1PM | 82.9 | 66.2 | 57 | 69.6 | 30.83 | 0.0727 | 0.47 | 13.9 | 0
January | 23 | 1PM to 2PM | 82 | 64.9 | 55 | 64.7 | 29.84 | 0.0728 | 0.44 | 13.86 | 0
January | 23 | 2PM to 3PM | 81 | 65.5 | 57 | 69.6 | 30.34 | 0.0729 | 0.47 | 13.84 | 0
January | 23 | 3PM to 4PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
January | 23 | 4PM to 5PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
January | 23 | 5PM to 6PM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
January | 23 | 6PM to 7PM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
January | 23 | 7PM to 8PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
January | 23 | 8PM to 9PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
January | 23 | 9PM to 10PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
January | 23 | 10PM to 11PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
January | 23 | 11PM to 12AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 24 | 12AM to 1AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
January | 24 | 1AM to 2AM | 68 | 63.4 | 61 | 80.4 | 28.86 | 0.0747 | 0.54 | 13.55 | 0
January | 24 | 2AM to 3AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
January | 24 | 3AM to 4AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
January | 24 | 4AM to 5AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
January | 24 | 5AM to 6AM | 68 | 63.4 | 61 | 80.4 | 28.86 | 0.0747 | 0.54 | 13.55 | 0
January | 24 | 6AM to 7AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
January | 24 | 7AM to 8AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 24 | 8AM to 9AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
January | 24 | 9AM to 10AM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
January | 24 | 10AM to 11AM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
January | 24 | 11AM to 12PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
January | 24 | 12PM to 1PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
January | 24 | 1PM to 2PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
January | 24 | 2PM to 3PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
January | 24 | 3PM to 4PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
January | 24 | 4PM to 5PM | 75 | 65.2 | 60.1 | 77.8 | 30.17 | 0.0737 | 0.52 | 13.72 | 0
January | 24 | 5PM to 6PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
January | 24 | 6PM to 7PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
January | 24 | 7PM to 8PM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
January | 24 | 8PM to 9PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
January | 24 | 9PM to 10PM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
January | 24 | 10PM to 11PM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
January | 24 | 11PM to 12AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 25 | 12AM to 1AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 25 | 1AM to 2AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
January | 25 | 2AM to 3AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
January | 25 | 3AM to 4AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
January | 25 | 4AM to 5AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
January | 25 | 5AM to 6AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
January | 25 | 6AM to 7AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
January | 25 | 7AM to 8AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
January | 25 | 8AM to 9AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
January | 25 | 9AM to 10AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
January | 25 | 10AM to 11AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
January | 25 | 11AM to 12PM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
January | 25 | 12PM to 1PM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
January | 25 | 1PM to 2PM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
January | 25 | 2PM to 3PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
January | 25 | 3PM to 4PM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
January | 25 | 4PM to 5PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
January | 25 | 5PM to 6PM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
January | 25 | 6PM to 7PM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
January | 25 | 7PM to 8PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
January | 25 | 8PM to 9PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
January | 25 | 9PM to 10PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
January | 25 | 10PM to 11PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
January | 25 | 11PM to 12AM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
January | 26 | 12AM to 1AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
January | 26 | 1AM to 2AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
January | 26 | 2AM to 3AM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
January | 26 | 3AM to 4AM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
January | 26 | 4AM to 5AM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
January | 26 | 5AM to 6AM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
January | 26 | 6AM to 7AM | 66 | 57.2 | 51.1 | 55.9 | 24.55 | 0.0751 | 0.38 | 13.42 | 0
January | 26 | 7AM to 8AM | 68 | 56.9 | 48.9 | 51.5 | 24.35 | 0.0749 | 0.35 | 13.46 | 0
January | 26 | 8AM to 9AM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
January | 26 | 9AM to 10AM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
January | 26 | 10AM to 11AM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
January | 26 | 11AM to 12PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
January | 26 | 12PM to 1PM | 77 | 62.2 | 53.1 | 60.1 | 27.89 | 0.0735 | 0.41 | 13.71 | 0
January | 26 | 1PM to 2PM | 77 | 62.2 | 53.1 | 60.1 | 27.89 | 0.0735 | 0.41 | 13.71 | 0
January | 26 | 2PM to 3PM | 75.9 | 62.3 | 54 | 62.2 | 27.95 | 0.0737 | 0.42 | 13.69 | 0
January | 26 | 3PM to 4PM | 73.9 | 61.6 | 54 | 62.2 | 27.46 | 0.074 | 0.42 | 13.64 | 0
January | 26 | 4PM to 5PM | 73 | 59.8 | 51.1 | 55.9 | 26.25 | 0.0741 | 0.38 | 13.6 | 0
January | 26 | 5PM to 6PM | 71.1 | 58.6 | 50 | 53.6 | 25.43 | 0.0744 | 0.36 | 13.54 | 0
January | 26 | 6PM to 7PM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
January | 26 | 7PM to 8PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
January | 26 | 8PM to 9PM | 69.1 | 57.8 | 50 | 53.6 | 24.94 | 0.0747 | 0.36 | 13.49 | 0
January | 26 | 9PM to 10PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
January | 26 | 10PM to 11PM | 69.1 | 58.4 | 51.1 | 55.9 | 25.29 | 0.0747 | 0.38 | 13.5 | 0
January | 26 | 11PM to 12AM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
January | 27 | 12AM to 1AM | 69.1 | 58.8 | 52 | 57.8 | 25.59 | 0.0747 | 0.39 | 13.5 | 0
January | 27 | 1AM to 2AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
January | 27 | 2AM to 3AM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
January | 27 | 3AM to 4AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
January | 27 | 4AM to 5AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
January | 27 | 5AM to 6AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
January | 27 | 6AM to 7AM | 66.9 | 62.5 | 60.1 | 77.8 | 28.19 | 0.0748 | 0.52 | 13.51 | 0
January | 27 | 7AM to 8AM | 66.9 | 61.9 | 59 | 74.9 | 27.72 | 0.0749 | 0.5 | 13.5 | 0
January | 27 | 8AM to 9AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
January | 27 | 9AM to 10AM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
January | 27 | 10AM to 11AM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
January | 27 | 11AM to 12PM | 79 | 65.3 | 57.9 | 72 | 30.22 | 0.0732 | 0.48 | 13.8 | 0
January | 27 | 12PM to 1PM | 79 | 66.5 | 60.1 | 77.8 | 31.14 | 0.0732 | 0.52 | 13.82 | 0
January | 27 | 1PM to 2PM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
January | 27 | 2PM to 3PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
January | 27 | 3PM to 4PM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
January | 27 | 4PM to 5PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
January | 27 | 5PM to 6PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
January | 27 | 6PM to 7PM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
January | 27 | 7PM to 8PM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
January | 27 | 8PM to 9PM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
January | 27 | 9PM to 10PM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
January | 27 | 10PM to 11PM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
January | 27 | 11PM to 12AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
January | 28 | 12AM to 1AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
January | 28 | 1AM to 2AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 28 | 2AM to 3AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 28 | 3AM to 4AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
January | 28 | 4AM to 5AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 28 | 5AM to 6AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
January | 28 | 6AM to 7AM | 63 | 61.7 | 61 | 80.4 | 27.62 | 0.0754 | 0.54 | 13.42 | 0
January | 28 | 7AM to 8AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
January | 28 | 8AM to 9AM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
January | 28 | 9AM to 10AM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
January | 28 | 10AM to 11AM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
January | 28 | 11AM to 12PM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
January | 28 | 12PM to 1PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
January | 28 | 1PM to 2PM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
January | 28 | 2PM to 3PM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
January | 28 | 3PM to 4PM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
January | 28 | 4PM to 5PM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
January | 28 | 5PM to 6PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
January | 28 | 6PM to 7PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
January | 28 | 7PM to 8PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
January | 28 | 8PM to 9PM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
January | 28 | 9PM to 10PM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 28 | 10PM to 11PM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 28 | 11PM to 12AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 29 | 12AM to 1AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 29 | 1AM to 2AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
January | 29 | 2AM to 3AM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
January | 29 | 3AM to 4AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
January | 29 | 4AM to 5AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
January | 29 | 5AM to 6AM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
January | 29 | 6AM to 7AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
January | 29 | 7AM to 8AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
January | 29 | 8AM to 9AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
January | 29 | 9AM to 10AM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
January | 29 | 10AM to 11AM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
January | 29 | 11AM to 12PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
January | 29 | 12PM to 1PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
January | 29 | 1PM to 2PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
January | 29 | 2PM to 3PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
January | 29 | 3PM to 4PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
January | 29 | 4PM to 5PM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
January | 29 | 5PM to 6PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
January | 29 | 6PM to 7PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
January | 29 | 7PM to 8PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
January | 29 | 8PM to 9PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
January | 29 | 9PM to 10PM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
January | 29 | 10PM to 11PM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
January | 29 | 11PM to 12AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
January | 30 | 12AM to 1AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
January | 30 | 1AM to 2AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
January | 30 | 2AM to 3AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
January | 30 | 3AM to 4AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 30 | 4AM to 5AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
January | 30 | 5AM to 6AM | 64.9 | 63.6 | 63 | 86.4 | 29.03 | 0.0751 | 0.58 | 13.49 | 0
January | 30 | 6AM to 7AM | 63 | 61.7 | 61 | 80.4 | 27.62 | 0.0754 | 0.54 | 13.42 | 0
January | 30 | 7AM to 8AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
January | 30 | 8AM to 9AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
January | 30 | 9AM to 10AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
January | 30 | 10AM to 11AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
January | 30 | 11AM to 12PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
January | 30 | 12PM to 1PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
January | 30 | 1PM to 2PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
January | 30 | 2PM to 3PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
January | 30 | 3PM to 4PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
January | 30 | 4PM to 5PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
January | 30 | 5PM to 6PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
January | 30 | 6PM to 7PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
January | 30 | 7PM to 8PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
January | 30 | 8PM to 9PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
January | 30 | 9PM to 10PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
January | 30 | 10PM to 11PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
January | 30 | 11PM to 12AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
January | 31 | 12AM to 1AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
January | 31 | 1AM to 2AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
January | 31 | 2AM to 3AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
January | 31 | 3AM to 4AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
January | 31 | 4AM to 5AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
January | 31 | 5AM to 6AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
January | 31 | 6AM to 7AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
January | 31 | 7AM to 8AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
January | 31 | 8AM to 9AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
January | 31 | 9AM to 10AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
January | 31 | 10AM to 11AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
January | 31 | 11AM to 12PM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
January | 31 | 12PM to 1PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
January | 31 | 1PM to 2PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
January | 31 | 2PM to 3PM | 75 | 65.2 | 60.1 | 77.8 | 30.17 | 0.0737 | 0.52 | 13.72 | 0
January | 31 | 3PM to 4PM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
January | 31 | 4PM to 5PM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
January | 31 | 5PM to 6PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
January | 31 | 6PM to 7PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
January | 31 | 7PM to 8PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
January | 31 | 8PM to 9PM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
January | 31 | 9PM to 10PM | 69.1 | 61.9 | 57.7 | 71.5 | 27.73 | 0.0746 | 0.48 | 13.55 | 0
January | 31 | 10PM to 11PM | 69.1 | 62.3 | 58.5 | 73.4 | 28.02 | 0.0746 | 0.49 | 13.55 | 0
January | 31 | 11PM to 12AM | 69.1 | 62.7 | 59.2 | 75.3 | 28.33 | 0.0746 | 0.51 | 13.56 | 0
February | 1 | 12AM to 1AM | 69.1 | 63.1 | 59.9 | 77.3 | 28.64 | 0.0745 | 0.52 | 13.56 | 0
February | 1 | 1AM to 2AM | 69.1 | 63.6 | 60.6 | 79.4 | 28.96 | 0.0745 | 0.53 | 13.57 | 0
February | 1 | 2AM to 3AM | 69.1 | 64 | 61.3 | 81.5 | 29.29 | 0.0745 | 0.55 | 13.58 | 0
February | 1 | 3AM to 4AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
February | 1 | 4AM to 5AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
February | 1 | 5AM to 6AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
February | 1 | 6AM to 7AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
February | 1 | 7AM to 8AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
February | 1 | 8AM to 9AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
February | 1 | 9AM to 10AM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
February | 1 | 10AM to 11AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
February | 1 | 11AM to 12PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
February | 1 | 12PM to 1PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
February | 1 | 1PM to 2PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
February | 1 | 2PM to 3PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
February | 1 | 3PM to 4PM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
February | 1 | 4PM to 5PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
February | 1 | 5PM to 6PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
February | 1 | 6PM to 7PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
February | 1 | 7PM to 8PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
February | 1 | 8PM to 9PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
February | 1 | 9PM to 10PM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
February | 1 | 10PM to 11PM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
February | 1 | 11PM to 12AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
February | 2 | 12AM to 1AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
February | 2 | 1AM to 2AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 2 | 2AM to 3AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
February | 2 | 3AM to 4AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
February | 2 | 4AM to 5AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
February | 2 | 5AM to 6AM | 64.9 | 63.6 | 63 | 86.4 | 29.03 | 0.0751 | 0.58 | 13.49 | 0
February | 2 | 6AM to 7AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
February | 2 | 7AM to 8AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
February | 2 | 8AM to 9AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
February | 2 | 9AM to 10AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
February | 2 | 10AM to 11AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
February | 2 | 11AM to 12PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
February | 2 | 12PM to 1PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
February | 2 | 1PM to 2PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
February | 2 | 2PM to 3PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
February | 2 | 3PM to 4PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
February | 2 | 4PM to 5PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
February | 2 | 5PM to 6PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
February | 2 | 6PM to 7PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
February | 2 | 7PM to 8PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
February | 2 | 8PM to 9PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
February | 2 | 9PM to 10PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
February | 2 | 10PM to 11PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
February | 2 | 11PM to 12AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
February | 3 | 12AM to 1AM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
February | 3 | 1AM to 2AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
February | 3 | 2AM to 3AM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
February | 3 | 3AM to 4AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
February | 3 | 4AM to 5AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
February | 3 | 5AM to 6AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
February | 3 | 6AM to 7AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
February | 3 | 7AM to 8AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
February | 3 | 8AM to 9AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
February | 3 | 9AM to 10AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
February | 3 | 10AM to 11AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
February | 3 | 11AM to 12PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
February | 3 | 12PM to 1PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
February | 3 | 1PM to 2PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
February | 3 | 2PM to 3PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
February | 3 | 3PM to 4PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
February | 3 | 4PM to 5PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
February | 3 | 5PM to 6PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
February | 3 | 6PM to 7PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
February | 3 | 7PM to 8PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
February | 3 | 8PM to 9PM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
February | 3 | 9PM to 10PM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
February | 3 | 10PM to 11PM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
February | 3 | 11PM to 12AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
February | 4 | 12AM to 1AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
February | 4 | 1AM to 2AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 4 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 4 | 3AM to 4AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 4 | 4AM to 5AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 4 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 4 | 6AM to 7AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
February | 4 | 7AM to 8AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
February | 4 | 8AM to 9AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
February | 4 | 9AM to 10AM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
February | 4 | 10AM to 11AM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
February | 4 | 11AM to 12PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
February | 4 | 12PM to 1PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
February | 4 | 1PM to 2PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
February | 4 | 2PM to 3PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
February | 4 | 3PM to 4PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
February | 4 | 4PM to 5PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
February | 4 | 5PM to 6PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
February | 4 | 6PM to 7PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
February | 4 | 7PM to 8PM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
February | 4 | 8PM to 9PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
February | 4 | 9PM to 10PM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
February | 4 | 10PM to 11PM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
February | 4 | 11PM to 12AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
February | 5 | 12AM to 1AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
February | 5 | 1AM to 2AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
February | 5 | 2AM to 3AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
February | 5 | 3AM to 4AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
February | 5 | 4AM to 5AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
February | 5 | 5AM to 6AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
February | 5 | 6AM to 7AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
February | 5 | 7AM to 8AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
February | 5 | 8AM to 9AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
February | 5 | 9AM to 10AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
February | 5 | 10AM to 11AM | 73 | 71.6 | 71.1 | 115 | 35.5 | 0.0738 | 0.77 | 13.78 | 0
February | 5 | 11AM to 12PM | 71.1 | 70.3 | 70 | 110.8 | 34.34 | 0.0741 | 0.74 | 13.72 | 0
February | 5 | 12PM to 1PM | 72 | 70.6 | 70 | 110.8 | 34.56 | 0.0739 | 0.74 | 13.74 | 0
February | 5 | 1PM to 2PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
February | 5 | 2PM to 3PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
February | 5 | 3PM to 4PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
February | 5 | 4PM to 5PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
February | 5 | 5PM to 6PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
February | 5 | 6PM to 7PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
February | 5 | 7PM to 8PM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
February | 5 | 8PM to 9PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
February | 5 | 9PM to 10PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
February | 5 | 10PM to 11PM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
February | 5 | 11PM to 12AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
February | 6 | 12AM to 1AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
February | 6 | 1AM to 2AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
February | 6 | 2AM to 3AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
February | 6 | 3AM to 4AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
February | 6 | 4AM to 5AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
February | 6 | 5AM to 6AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
February | 6 | 6AM to 7AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
February | 6 | 7AM to 8AM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
February | 6 | 8AM to 9AM | 75.9 | 62.8 | 55 | 64.7 | 28.34 | 0.0737 | 0.44 | 13.7 | 0
February | 6 | 9AM to 10AM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
February | 6 | 10AM to 11AM | 75.9 | 63.3 | 55.9 | 66.9 | 28.69 | 0.0737 | 0.45 | 13.71 | 0
February | 6 | 11AM to 12PM | 75.9 | 61.3 | 52 | 57.8 | 27.26 | 0.0737 | 0.39 | 13.68 | 0
February | 6 | 12PM to 1PM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
February | 6 | 1PM to 2PM | 75.9 | 60.9 | 51.1 | 55.9 | 26.96 | 0.0737 | 0.38 | 13.67 | 0
February | 6 | 2PM to 3PM | 75.9 | 60.9 | 51.1 | 55.9 | 26.96 | 0.0737 | 0.38 | 13.67 | 0
February | 6 | 3PM to 4PM | 75 | 60.5 | 51.1 | 55.9 | 26.74 | 0.0738 | 0.38 | 13.65 | 0
February | 6 | 4PM to 5PM | 73 | 59.3 | 50 | 53.6 | 25.91 | 0.0741 | 0.36 | 13.59 | 0
February | 6 | 5PM to 6PM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
February | 6 | 6PM to 7PM | 69.1 | 59.4 | 53.1 | 60.1 | 25.96 | 0.0746 | 0.41 | 13.51 | 0
February | 6 | 7PM to 8PM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
February | 6 | 8PM to 9PM | 66 | 57.6 | 52 | 57.8 | 24.84 | 0.0751 | 0.39 | 13.43 | 0
February | 6 | 9PM to 10PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
February | 6 | 10PM to 11PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
February | 6 | 11PM to 12AM | 64.9 | 57.8 | 53.1 | 60.1 | 24.95 | 0.0752 | 0.41 | 13.41 | 0
February | 7 | 12AM to 1AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
February | 7 | 1AM to 2AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
February | 7 | 2AM to 3AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
February | 7 | 3AM to 4AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
February | 7 | 4AM to 5AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
February | 7 | 5AM to 6AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
February | 7 | 6AM to 7AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
February | 7 | 7AM to 8AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
February | 7 | 8AM to 9AM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
February | 7 | 9AM to 10AM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
February | 7 | 10AM to 11AM | 75 | 61 | 52 | 57.8 | 27.04 | 0.0738 | 0.39 | 13.66 | 0
February | 7 | 11AM to 12PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
February | 7 | 12PM to 1PM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
February | 7 | 1PM to 2PM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
February | 7 | 2PM to 3PM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
February | 7 | 3PM to 4PM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
February | 7 | 4PM to 5PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
February | 7 | 5PM to 6PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
February | 7 | 6PM to 7PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
February | 7 | 7PM to 8PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
February | 7 | 8PM to 9PM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
February | 7 | 9PM to 10PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
February | 7 | 10PM to 11PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
February | 7 | 11PM to 12AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
February | 8 | 12AM to 1AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
February | 8 | 1AM to 2AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
February | 8 | 2AM to 3AM | 61 | 57.9 | 55.9 | 66.9 | 25.04 | 0.0758 | 0.45 | 13.33 | 0
February | 8 | 3AM to 4AM | 60.1 | 57.6 | 55.9 | 66.9 | 24.82 | 0.0759 | 0.45 | 13.3 | 0
February | 8 | 4AM to 5AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
February | 8 | 5AM to 6AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
February | 8 | 6AM to 7AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
February | 8 | 7AM to 8AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
February | 8 | 8AM to 9AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
February | 8 | 9AM to 10AM | 73 | 62.3 | 55.9 | 66.9 | 27.98 | 0.074 | 0.45 | 13.63 | 0
February | 8 | 10AM to 11AM | 75 | 63 | 55.9 | 66.9 | 28.47 | 0.0738 | 0.45 | 13.68 | 0
February | 8 | 11AM to 12PM | 77 | 64.7 | 57.9 | 72 | 29.74 | 0.0735 | 0.48 | 13.75 | 0
February | 8 | 12PM to 1PM | 78.1 | 64 | 55.9 | 66.9 | 29.21 | 0.0734 | 0.45 | 13.76 | 0
February | 8 | 1PM to 2PM | 78.1 | 64.6 | 57 | 69.6 | 29.64 | 0.0733 | 0.47 | 13.77 | 0
February | 8 | 2PM to 3PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
February | 8 | 3PM to 4PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
February | 8 | 4PM to 5PM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
February | 8 | 5PM to 6PM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
February | 8 | 6PM to 7PM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
February | 8 | 7PM to 8PM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
February | 8 | 8PM to 9PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
February | 8 | 9PM to 10PM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
February | 8 | 10PM to 11PM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
February | 8 | 11PM to 12AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
February | 9 | 12AM to 1AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
February | 9 | 1AM to 2AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
February | 9 | 2AM to 3AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
February | 9 | 3AM to 4AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
February | 9 | 4AM to 5AM | 66 | 62.2 | 60.1 | 77.8 | 27.97 | 0.075 | 0.52 | 13.49 | 0
February | 9 | 5AM to 6AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
February | 9 | 6AM to 7AM | 66 | 62.2 | 60.1 | 77.8 | 27.97 | 0.075 | 0.52 | 13.49 | 0
February | 9 | 7AM to 8AM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
February | 9 | 8AM to 9AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
February | 9 | 9AM to 10AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
February | 9 | 10AM to 11AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
February | 9 | 11AM to 12PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
February | 9 | 12PM to 1PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
February | 9 | 1PM to 2PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
February | 9 | 2PM to 3PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
February | 9 | 3PM to 4PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
February | 9 | 4PM to 5PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
February | 9 | 5PM to 6PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
February | 9 | 6PM to 7PM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
February | 9 | 7PM to 8PM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
February | 9 | 8PM to 9PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
February | 9 | 9PM to 10PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
February | 9 | 10PM to 11PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
February | 9 | 11PM to 12AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
February | 10 | 12AM to 1AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
February | 10 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
February | 10 | 2AM to 3AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
February | 10 | 3AM to 4AM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
February | 10 | 4AM to 5AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
February | 10 | 5AM to 6AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
February | 10 | 6AM to 7AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
February | 10 | 7AM to 8AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 10 | 8AM to 9AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
February | 10 | 9AM to 10AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
February | 10 | 10AM to 11AM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
February | 10 | 11AM to 12PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
February | 10 | 12PM to 1PM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
February | 10 | 1PM to 2PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
February | 10 | 2PM to 3PM | 78.1 | 64 | 55.9 | 66.9 | 29.21 | 0.0734 | 0.45 | 13.76 | 0
February | 10 | 3PM to 4PM | 75.9 | 62.8 | 55 | 64.7 | 28.34 | 0.0737 | 0.44 | 13.7 | 0
February | 10 | 4PM to 5PM | 75 | 61 | 52 | 57.8 | 27.04 | 0.0738 | 0.39 | 13.66 | 0
February | 10 | 5PM to 6PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
February | 10 | 6PM to 7PM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
February | 10 | 7PM to 8PM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
February | 10 | 8PM to 9PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
February | 10 | 9PM to 10PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
February | 10 | 10PM to 11PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
February | 10 | 11PM to 12AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
February | 11 | 12AM to 1AM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
February | 11 | 1AM to 2AM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
February | 11 | 2AM to 3AM | 64.9 | 57.2 | 52 | 57.8 | 24.58 | 0.0752 | 0.39 | 13.4 | 0
February | 11 | 3AM to 4AM | 64 | 56.4 | 51.1 | 55.9 | 24.06 | 0.0754 | 0.38 | 13.37 | 0
February | 11 | 4AM to 5AM | 62.1 | 57.2 | 54 | 62.2 | 24.57 | 0.0756 | 0.42 | 13.34 | 0
February | 11 | 5AM to 6AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
February | 11 | 6AM to 7AM | 62.1 | 56.7 | 53.1 | 60.1 | 24.25 | 0.0757 | 0.41 | 13.33 | 0
February | 11 | 7AM to 8AM | 64 | 57.5 | 53.1 | 60.1 | 24.73 | 0.0754 | 0.41 | 13.38 | 0
February | 11 | 8AM to 9AM | 70 | 58.7 | 51.1 | 55.9 | 25.51 | 0.0745 | 0.38 | 13.52 | 0
February | 11 | 9AM to 10AM | 73 | 59.8 | 51.1 | 55.9 | 26.25 | 0.0741 | 0.38 | 13.6 | 0
February | 11 | 10AM to 11AM | 75 | 61 | 52 | 57.8 | 27.04 | 0.0738 | 0.39 | 13.66 | 0
February | 11 | 11AM to 12PM | 73 | 59.8 | 51.1 | 55.9 | 26.25 | 0.0741 | 0.38 | 13.6 | 0
February | 11 | 12PM to 1PM | 77 | 61.3 | 51.1 | 55.9 | 27.22 | 0.0736 | 0.38 | 13.7 | 0
February | 11 | 1PM to 2PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
February | 11 | 2PM to 3PM | 75 | 61 | 52 | 57.8 | 27.04 | 0.0738 | 0.39 | 13.66 | 0
February | 11 | 3PM to 4PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
February | 11 | 4PM to 5PM | 73 | 59.8 | 51.1 | 55.9 | 26.25 | 0.0741 | 0.38 | 13.6 | 0
February | 11 | 5PM to 6PM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
February | 11 | 6PM to 7PM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
February | 11 | 7PM to 8PM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
February | 11 | 8PM to 9PM | 64 | 59 | 55.9 | 66.9 | 25.78 | 0.0753 | 0.45 | 13.4 | 0
February | 11 | 9PM to 10PM | 63 | 58.1 | 55 | 64.7 | 25.18 | 0.0755 | 0.44 | 13.37 | 0
February | 11 | 10PM to 11PM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
February | 11 | 11PM to 12AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
February | 12 | 12AM to 1AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
February | 12 | 1AM to 2AM | 57 | 55.2 | 54 | 62.2 | 23.34 | 0.0764 | 0.42 | 13.21 | 0
February | 12 | 2AM to 3AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
February | 12 | 3AM to 4AM | 57.9 | 56.2 | 55 | 64.7 | 23.95 | 0.0762 | 0.44 | 13.24 | 0
February | 12 | 4AM to 5AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
February | 12 | 5AM to 6AM | 57.9 | 55.6 | 54 | 62.2 | 23.56 | 0.0762 | 0.42 | 13.23 | 0
February | 12 | 6AM to 7AM | 55.9 | 54.8 | 54 | 62.2 | 23.07 | 0.0765 | 0.42 | 13.18 | 0
February | 12 | 7AM to 8AM | 60.1 | 58.2 | 57 | 69.6 | 25.24 | 0.0759 | 0.47 | 13.31 | 0
February | 12 | 8AM to 9AM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
February | 12 | 9AM to 10AM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
February | 12 | 10AM to 11AM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
February | 12 | 11AM to 12PM | 75 | 63 | 55.9 | 66.9 | 28.47 | 0.0738 | 0.45 | 13.68 | 0
February | 12 | 12PM to 1PM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
February | 12 | 1PM to 2PM | 77 | 64.7 | 57.9 | 72 | 29.74 | 0.0735 | 0.48 | 13.75 | 0
February | 12 | 2PM to 3PM | 77 | 64.7 | 57.9 | 72 | 29.74 | 0.0735 | 0.48 | 13.75 | 0
February | 12 | 3PM to 4PM | 75.9 | 64.9 | 59 | 74.9 | 29.93 | 0.0736 | 0.5 | 13.73 | 0
February | 12 | 4PM to 5PM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
February | 12 | 5PM to 6PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
February | 12 | 6PM to 7PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
February | 12 | 7PM to 8PM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
February | 12 | 8PM to 9PM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
February | 12 | 9PM to 10PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
February | 12 | 10PM to 11PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
February | 12 | 11PM to 12AM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
February | 13 | 12AM to 1AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
February | 13 | 1AM to 2AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
February | 13 | 2AM to 3AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
February | 13 | 3AM to 4AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
February | 13 | 4AM to 5AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
February | 13 | 5AM to 6AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
February | 13 | 6AM to 7AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
February | 13 | 7AM to 8AM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
February | 13 | 8AM to 9AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
February | 13 | 9AM to 10AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
February | 13 | 10AM to 11AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
February | 13 | 11AM to 12PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
February | 13 | 12PM to 1PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
February | 13 | 1PM to 2PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
February | 13 | 2PM to 3PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
February | 13 | 3PM to 4PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
February | 13 | 4PM to 5PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 13 | 5PM to 6PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 13 | 6PM to 7PM | 71.1 | 70.3 | 70 | 110.8 | 34.34 | 0.0741 | 0.74 | 13.72 | 0
February | 13 | 7PM to 8PM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
February | 13 | 8PM to 9PM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
February | 13 | 9PM to 10PM | 69.1 | 68.3 | 68 | 103.3 | 32.69 | 0.0744 | 0.69 | 13.64 | 0
February | 13 | 10PM to 11PM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 13 | 11PM to 12AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 14 | 12AM to 1AM | 68 | 68 | 68 | 103.3 | 32.43 | 0.0745 | 0.69 | 13.62 | 0
February | 14 | 1AM to 2AM | 69.1 | 69.1 | 69.1 | 107.3 | 33.32 | 0.0744 | 0.72 | 13.66 | 0
February | 14 | 2AM to 3AM | 69.1 | 69.1 | 69.1 | 107.3 | 33.32 | 0.0744 | 0.72 | 13.66 | 0
February | 14 | 3AM to 4AM | 69.1 | 68.3 | 68 | 103.3 | 32.69 | 0.0744 | 0.69 | 13.64 | 0
February | 14 | 4AM to 5AM | 68 | 68 | 68 | 103.3 | 32.43 | 0.0745 | 0.69 | 13.62 | 0
February | 14 | 5AM to 6AM | 69.1 | 68.3 | 68 | 103.3 | 32.69 | 0.0744 | 0.69 | 13.64 | 0
February | 14 | 6AM to 7AM | 69.1 | 68.3 | 68 | 103.3 | 32.69 | 0.0744 | 0.69 | 13.64 | 0
February | 14 | 7AM to 8AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 14 | 8AM to 9AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
February | 14 | 9AM to 10AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
February | 14 | 10AM to 11AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
February | 14 | 11AM to 12PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
February | 14 | 12PM to 1PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
February | 14 | 1PM to 2PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
February | 14 | 2PM to 3PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
February | 14 | 3PM to 4PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
February | 14 | 4PM to 5PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
February | 14 | 5PM to 6PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
February | 14 | 6PM to 7PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
February | 14 | 7PM to 8PM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
February | 14 | 8PM to 9PM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
February | 14 | 9PM to 10PM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
February | 14 | 10PM to 11PM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
February | 14 | 11PM to 12AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
February | 15 | 12AM to 1AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
February | 15 | 1AM to 2AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
February | 15 | 2AM to 3AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
February | 15 | 3AM to 4AM | 63 | 62.4 | 62.1 | 83.6 | 28.12 | 0.0754 | 0.56 | 13.43 | 0
February | 15 | 4AM to 5AM | 63 | 62.4 | 62.1 | 83.6 | 28.12 | 0.0754 | 0.56 | 13.43 | 0
February | 15 | 5AM to 6AM | 62.1 | 61.4 | 61 | 80.4 | 27.4 | 0.0755 | 0.54 | 13.39 | 0
February | 15 | 6AM to 7AM | 63 | 61.7 | 61 | 80.4 | 27.62 | 0.0754 | 0.54 | 13.42 | 0
February | 15 | 7AM to 8AM | 64.9 | 63.6 | 63 | 86.4 | 29.03 | 0.0751 | 0.58 | 13.49 | 0
February | 15 | 8AM to 9AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
February | 15 | 9AM to 10AM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
February | 15 | 10AM to 11AM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
February | 15 | 11AM to 12PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
February | 15 | 12PM to 1PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
February | 15 | 1PM to 2PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
February | 15 | 2PM to 3PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
February | 15 | 3PM to 4PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
February | 15 | 4PM to 5PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
February | 15 | 5PM to 6PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
February | 15 | 6PM to 7PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
February | 15 | 7PM to 8PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
February | 15 | 8PM to 9PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
February | 15 | 9PM to 10PM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 15 | 10PM to 11PM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
February | 15 | 11PM to 12AM | 68 | 66.7 | 66 | 96.3 | 31.34 | 0.0746 | 0.64 | 13.59 | 0
February | 16 | 12AM to 1AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 16 | 1AM to 2AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 16 | 2AM to 3AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 16 | 3AM to 4AM | 68 | 68 | 68 | 103.3 | 32.43 | 0.0745 | 0.69 | 13.62 | 0
February | 16 | 4AM to 5AM | 68 | 68 | 68 | 103.3 | 32.43 | 0.0745 | 0.69 | 13.62 | 0
February | 16 | 5AM to 6AM | 69.1 | 69.1 | 69.1 | 107.3 | 33.32 | 0.0744 | 0.72 | 13.66 | 0
February | 16 | 6AM to 7AM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
February | 16 | 7AM to 8AM | 71.1 | 70.3 | 70 | 110.8 | 34.34 | 0.0741 | 0.74 | 13.72 | 0
February | 16 | 8AM to 9AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
February | 16 | 9AM to 10AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
February | 16 | 10AM to 11AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
February | 16 | 11AM to 12PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
February | 16 | 12PM to 1PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
February | 16 | 1PM to 2PM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
February | 16 | 2PM to 3PM | 82.9 | 75 | 72 | 118.7 | 38.52 | 0.0724 | 0.79 | 14.05 | 0
February | 16 | 3PM to 4PM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
February | 16 | 4PM to 5PM | 73.9 | 73.3 | 73 | 123.2 | 37 | 0.0736 | 0.82 | 13.83 | 0
February | 16 | 5PM to 6PM | 75.9 | 74.5 | 73.9 | 127.1 | 38.1 | 0.0733 | 0.85 | 13.89 | 0
February | 16 | 6PM to 7PM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 16 | 7PM to 8PM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 16 | 8PM to 9PM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 16 | 9PM to 10PM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 16 | 10PM to 11PM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
February | 16 | 11PM to 12AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 17 | 12AM to 1AM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
February | 17 | 1AM to 2AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
February | 17 | 2AM to 3AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
February | 17 | 3AM to 4AM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
February | 17 | 4AM to 5AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
February | 17 | 5AM to 6AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
February | 17 | 6AM to 7AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
February | 17 | 7AM to 8AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
February | 17 | 8AM to 9AM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
February | 17 | 9AM to 10AM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
February | 17 | 10AM to 11AM | 79 | 73.9 | 72 | 118.7 | 37.54 | 0.0729 | 0.79 | 13.95 | 0
February | 17 | 11AM to 12PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
February | 17 | 12PM to 1PM | 80.1 | 75 | 73 | 123.2 | 38.52 | 0.0727 | 0.82 | 13.99 | 0
February | 17 | 1PM to 2PM | 80.1 | 75 | 73 | 123.2 | 38.52 | 0.0727 | 0.82 | 13.99 | 0
February | 17 | 2PM to 3PM | 81 | 75.2 | 73 | 123.2 | 38.74 | 0.0726 | 0.82 | 14.01 | 0
February | 17 | 3PM to 4PM | 80.1 | 75 | 73 | 123.2 | 38.52 | 0.0727 | 0.82 | 13.99 | 0
February | 17 | 4PM to 5PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
February | 17 | 5PM to 6PM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
February | 17 | 6PM to 7PM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
February | 17 | 7PM to 8PM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
February | 17 | 8PM to 9PM | 75 | 74.2 | 73.9 | 127.1 | 37.88 | 0.0734 | 0.85 | 13.87 | 0
February | 17 | 9PM to 10PM | 75.9 | 74.5 | 73.9 | 127.1 | 38.1 | 0.0733 | 0.85 | 13.89 | 0
February | 17 | 10PM to 11PM | 75.9 | 74.5 | 73.9 | 127.1 | 38.1 | 0.0733 | 0.85 | 13.89 | 0
February | 17 | 11PM to 12AM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
February | 18 | 12AM to 1AM | 75 | 74.2 | 73.9 | 127.1 | 37.88 | 0.0734 | 0.85 | 13.87 | 0
February | 18 | 1AM to 2AM | 75 | 74.2 | 73.9 | 127.1 | 37.88 | 0.0734 | 0.85 | 13.87 | 0
February | 18 | 2AM to 3AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 18 | 3AM to 4AM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
February | 18 | 4AM to 5AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 18 | 5AM to 6AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 18 | 6AM to 7AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 18 | 7AM to 8AM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
February | 18 | 8AM to 9AM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
February | 18 | 9AM to 10AM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
February | 18 | 10AM to 11AM | 80.1 | 75.6 | 73.9 | 127.1 | 39.13 | 0.0727 | 0.85 | 14 | 0
February | 18 | 11AM to 12PM | 75.9 | 74.5 | 73.9 | 127.1 | 38.1 | 0.0733 | 0.85 | 13.89 | 0
February | 18 | 12PM to 1PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
February | 18 | 1PM to 2PM | 82 | 76.1 | 73.9 | 127.1 | 39.62 | 0.0725 | 0.85 | 14.05 | 0
February | 18 | 2PM to 3PM | 82 | 76.1 | 73.9 | 127.1 | 39.62 | 0.0725 | 0.85 | 14.05 | 0
February | 18 | 3PM to 4PM | 82 | 76.1 | 73.9 | 127.1 | 39.62 | 0.0725 | 0.85 | 14.05 | 0
February | 18 | 4PM to 5PM | 81 | 75.2 | 73 | 123.2 | 38.74 | 0.0726 | 0.82 | 14.01 | 0
February | 18 | 5PM to 6PM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
February | 18 | 6PM to 7PM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
February | 18 | 7PM to 8PM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
February | 18 | 8PM to 9PM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
February | 18 | 9PM to 10PM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
February | 18 | 10PM to 11PM | 73 | 71.6 | 71.1 | 115 | 35.5 | 0.0738 | 0.77 | 13.78 | 0
February | 18 | 11PM to 12AM | 72 | 71.3 | 71.1 | 115 | 35.23 | 0.0739 | 0.77 | 13.75 | 0
February | 19 | 12AM to 1AM | 71.1 | 70.3 | 70 | 110.8 | 34.34 | 0.0741 | 0.74 | 13.72 | 0
February | 19 | 1AM to 2AM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
February | 19 | 2AM to 3AM | 69.1 | 69.1 | 69.1 | 107.3 | 33.32 | 0.0744 | 0.72 | 13.66 | 0
February | 19 | 3AM to 4AM | 68 | 68 | 68 | 103.3 | 32.43 | 0.0745 | 0.69 | 13.62 | 0
February | 19 | 4AM to 5AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 19 | 5AM to 6AM | 66.9 | 66.3 | 66 | 96.3 | 31.07 | 0.0747 | 0.64 | 13.57 | 0
February | 19 | 6AM to 7AM | 66 | 65.3 | 64.9 | 92.7 | 30.28 | 0.0749 | 0.62 | 13.53 | 0
February | 19 | 7AM to 8AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 19 | 8AM to 9AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
February | 19 | 9AM to 10AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
February | 19 | 10AM to 11AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
February | 19 | 11AM to 12PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
February | 19 | 12PM to 1PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
February | 19 | 1PM to 2PM | 82.9 | 75 | 72 | 118.7 | 38.52 | 0.0724 | 0.79 | 14.05 | 0
February | 19 | 2PM to 3PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
February | 19 | 3PM to 4PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
February | 19 | 4PM to 5PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
February | 19 | 5PM to 6PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
February | 19 | 6PM to 7PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
February | 19 | 7PM to 8PM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
February | 19 | 8PM to 9PM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
February | 19 | 9PM to 10PM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
February | 19 | 10PM to 11PM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
February | 19 | 11PM to 12AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
February | 20 | 12AM to 1AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 20 | 1AM to 2AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 20 | 2AM to 3AM | 68 | 66.7 | 66 | 96.3 | 31.34 | 0.0746 | 0.64 | 13.59 | 0
February | 20 | 3AM to 4AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
February | 20 | 4AM to 5AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
February | 20 | 5AM to 6AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
February | 20 | 6AM to 7AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
February | 20 | 7AM to 8AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 20 | 8AM to 9AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
February | 20 | 9AM to 10AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
February | 20 | 10AM to 11AM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
February | 20 | 11AM to 12PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
February | 20 | 12PM to 1PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
February | 20 | 1PM to 2PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
February | 20 | 2PM to 3PM | 82 | 74.7 | 72 | 118.7 | 38.3 | 0.0725 | 0.79 | 14.03 | 0
February | 20 | 3PM to 4PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
February | 20 | 4PM to 5PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
February | 20 | 5PM to 6PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
February | 20 | 6PM to 7PM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
February | 20 | 7PM to 8PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
February | 20 | 8PM to 9PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
February | 20 | 9PM to 10PM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
February | 20 | 10PM to 11PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 20 | 11PM to 12AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 21 | 12AM to 1AM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
February | 21 | 1AM to 2AM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
February | 21 | 2AM to 3AM | 69.1 | 68.3 | 68 | 103.3 | 32.69 | 0.0744 | 0.69 | 13.64 | 0
February | 21 | 3AM to 4AM | 68 | 68 | 68 | 103.3 | 32.43 | 0.0745 | 0.69 | 13.62 | 0
February | 21 | 4AM to 5AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 21 | 5AM to 6AM | 66.9 | 66.9 | 66.9 | 99.5 | 31.56 | 0.0747 | 0.67 | 13.58 | 0
February | 21 | 6AM to 7AM | 66.9 | 66.9 | 66.9 | 99.5 | 31.56 | 0.0747 | 0.67 | 13.58 | 0
February | 21 | 7AM to 8AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
February | 21 | 8AM to 9AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
February | 21 | 9AM to 10AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
February | 21 | 10AM to 11AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
February | 21 | 11AM to 12PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
February | 21 | 12PM to 1PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
February | 21 | 1PM to 2PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
February | 21 | 2PM to 3PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
February | 21 | 3PM to 4PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
February | 21 | 4PM to 5PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
February | 21 | 5PM to 6PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
February | 21 | 6PM to 7PM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
February | 21 | 7PM to 8PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 21 | 8PM to 9PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 21 | 9PM to 10PM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
February | 21 | 10PM to 11PM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
February | 21 | 11PM to 12AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 22 | 12AM to 1AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 22 | 1AM to 2AM | 68 | 66.7 | 66 | 96.3 | 31.34 | 0.0746 | 0.64 | 13.59 | 0
February | 22 | 2AM to 3AM | 66.9 | 66.3 | 66 | 96.3 | 31.07 | 0.0747 | 0.64 | 13.57 | 0
February | 22 | 3AM to 4AM | 66.9 | 66.3 | 66 | 96.3 | 31.07 | 0.0747 | 0.64 | 13.57 | 0
February | 22 | 4AM to 5AM | 66.9 | 66.3 | 66 | 96.3 | 31.07 | 0.0747 | 0.64 | 13.57 | 0
February | 22 | 5AM to 6AM | 66.9 | 66.3 | 66 | 96.3 | 31.07 | 0.0747 | 0.64 | 13.57 | 0
February | 22 | 6AM to 7AM | 66.9 | 66.9 | 66.9 | 99.5 | 31.56 | 0.0747 | 0.67 | 13.58 | 0
February | 22 | 7AM to 8AM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
February | 22 | 8AM to 9AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
February | 22 | 9AM to 10AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
February | 22 | 10AM to 11AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
February | 22 | 11AM to 12PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
February | 22 | 12PM to 1PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
February | 22 | 1PM to 2PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
February | 22 | 2PM to 3PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
February | 22 | 3PM to 4PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
February | 22 | 4PM to 5PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
February | 22 | 5PM to 6PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
February | 22 | 6PM to 7PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
February | 22 | 7PM to 8PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
February | 22 | 8PM to 9PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
February | 22 | 9PM to 10PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
February | 22 | 10PM to 11PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
February | 22 | 11PM to 12AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
February | 23 | 12AM to 1AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
February | 23 | 1AM to 2AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
February | 23 | 2AM to 3AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
February | 23 | 3AM to 4AM | 68 | 66.7 | 66 | 96.3 | 31.34 | 0.0746 | 0.64 | 13.59 | 0
February | 23 | 4AM to 5AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 23 | 5AM to 6AM | 66.9 | 66.3 | 66 | 96.3 | 31.07 | 0.0747 | 0.64 | 13.57 | 0
February | 23 | 6AM to 7AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 23 | 7AM to 8AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
February | 23 | 8AM to 9AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
February | 23 | 9AM to 10AM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
February | 23 | 10AM to 11AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
February | 23 | 11AM to 12PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
February | 23 | 12PM to 1PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
February | 23 | 1PM to 2PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
February | 23 | 2PM to 3PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
February | 23 | 3PM to 4PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
February | 23 | 4PM to 5PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
February | 23 | 5PM to 6PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
February | 23 | 6PM to 7PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
February | 23 | 7PM to 8PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
February | 23 | 8PM to 9PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
February | 23 | 9PM to 10PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 23 | 10PM to 11PM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
February | 23 | 11PM to 12AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
February | 24 | 12AM to 1AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
February | 24 | 1AM to 2AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 24 | 2AM to 3AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 24 | 3AM to 4AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 24 | 4AM to 5AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 24 | 5AM to 6AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
February | 24 | 6AM to 7AM | 68 | 66.7 | 66 | 96.3 | 31.34 | 0.0746 | 0.64 | 13.59 | 0
February | 24 | 7AM to 8AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
February | 24 | 8AM to 9AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
February | 24 | 9AM to 10AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
February | 24 | 10AM to 11AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
February | 24 | 11AM to 12PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
February | 24 | 12PM to 1PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
February | 24 | 1PM to 2PM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
February | 24 | 2PM to 3PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
February | 24 | 3PM to 4PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
February | 24 | 4PM to 5PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
February | 24 | 5PM to 6PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
February | 24 | 6PM to 7PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
February | 24 | 7PM to 8PM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
February | 24 | 8PM to 9PM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
February | 24 | 9PM to 10PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 24 | 10PM to 11PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 24 | 11PM to 12AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
February | 25 | 12AM to 1AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
February | 25 | 1AM to 2AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
February | 25 | 2AM to 3AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 25 | 3AM to 4AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 25 | 4AM to 5AM | 66.9 | 66.9 | 66.9 | 99.5 | 31.56 | 0.0747 | 0.67 | 13.58 | 0
February | 25 | 5AM to 6AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 25 | 6AM to 7AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
February | 25 | 7AM to 8AM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
February | 25 | 8AM to 9AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
February | 25 | 9AM to 10AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
February | 25 | 10AM to 11AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
February | 25 | 11AM to 12PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
February | 25 | 12PM to 1PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
February | 25 | 1PM to 2PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
February | 25 | 2PM to 3PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
February | 25 | 3PM to 4PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
February | 25 | 4PM to 5PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
February | 25 | 5PM to 6PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
February | 25 | 6PM to 7PM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
February | 25 | 7PM to 8PM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
February | 25 | 8PM to 9PM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
February | 25 | 9PM to 10PM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
February | 25 | 10PM to 11PM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
February | 25 | 11PM to 12AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
February | 26 | 12AM to 1AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
February | 26 | 1AM to 2AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
February | 26 | 2AM to 3AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
February | 26 | 3AM to 4AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
February | 26 | 4AM to 5AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
February | 26 | 5AM to 6AM | 66 | 65.3 | 64.9 | 92.7 | 30.28 | 0.0749 | 0.62 | 13.53 | 0
February | 26 | 6AM to 7AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
February | 26 | 7AM to 8AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
February | 26 | 8AM to 9AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
February | 26 | 9AM to 10AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
February | 26 | 10AM to 11AM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
February | 26 | 11AM to 12PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
February | 26 | 12PM to 1PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
February | 26 | 1PM to 2PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
February | 26 | 2PM to 3PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
February | 26 | 3PM to 4PM | 82.9 | 66.2 | 57 | 69.6 | 30.83 | 0.0727 | 0.47 | 13.9 | 0
February | 26 | 4PM to 5PM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
February | 26 | 5PM to 6PM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
February | 26 | 6PM to 7PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
February | 26 | 7PM to 8PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
February | 26 | 8PM to 9PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
February | 26 | 9PM to 10PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
February | 26 | 10PM to 11PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
February | 26 | 11PM to 12AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
February | 27 | 12AM to 1AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
February | 27 | 1AM to 2AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
February | 27 | 2AM to 3AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
February | 27 | 3AM to 4AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
February | 27 | 4AM to 5AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
February | 27 | 5AM to 6AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
February | 27 | 6AM to 7AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
February | 27 | 7AM to 8AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
February | 27 | 8AM to 9AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
February | 27 | 9AM to 10AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
February | 27 | 10AM to 11AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
February | 27 | 11AM to 12PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
February | 27 | 12PM to 1PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
February | 27 | 1PM to 2PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
February | 27 | 2PM to 3PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
February | 27 | 3PM to 4PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
February | 27 | 4PM to 5PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
February | 27 | 5PM to 6PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
February | 27 | 6PM to 7PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
February | 27 | 7PM to 8PM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
February | 27 | 8PM to 9PM | 69.1 | 69.1 | 69.1 | 107.3 | 33.32 | 0.0744 | 0.72 | 13.66 | 0
February | 27 | 9PM to 10PM | 69.1 | 69.1 | 69.1 | 107.3 | 33.32 | 0.0744 | 0.72 | 13.66 | 0
February | 27 | 10PM to 11PM | 69.1 | 69.1 | 69.1 | 107.3 | 33.32 | 0.0744 | 0.72 | 13.66 | 0
February | 27 | 11PM to 12AM | 69.1 | 69.1 | 69.1 | 107.3 | 33.32 | 0.0744 | 0.72 | 13.66 | 0
February | 28 | 12AM to 1AM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
February | 28 | 1AM to 2AM | 72 | 70.6 | 70 | 110.8 | 34.56 | 0.0739 | 0.74 | 13.74 | 0
February | 28 | 2AM to 3AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 28 | 3AM to 4AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
February | 28 | 4AM to 5AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
February | 28 | 5AM to 6AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 28 | 6AM to 7AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
February | 28 | 7AM to 8AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
February | 28 | 8AM to 9AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
February | 28 | 9AM to 10AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
February | 28 | 10AM to 11AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
February | 28 | 11AM to 12PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
February | 28 | 12PM to 1PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
February | 28 | 1PM to 2PM | 82 | 74.7 | 72 | 118.7 | 38.3 | 0.0725 | 0.79 | 14.03 | 0
February | 28 | 2PM to 3PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
February | 28 | 3PM to 4PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
February | 28 | 4PM to 5PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
February | 28 | 5PM to 6PM | 73 | 71.6 | 71.1 | 115 | 35.5 | 0.0738 | 0.77 | 13.78 | 0
February | 28 | 6PM to 7PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
February | 28 | 7PM to 8PM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
February | 28 | 8PM to 9PM | 71.1 | 70.3 | 70 | 110.8 | 34.34 | 0.0741 | 0.74 | 13.72 | 0
February | 28 | 9PM to 10PM | 70.7 | 69.1 | 68.4 | 104.6 | 33.3 | 0.0741 | 0.7 | 13.69 | 0
February | 28 | 10PM to 11PM | 70.5 | 68 | 66.9 | 99.5 | 32.44 | 0.0742 | 0.67 | 13.67 | 0
February | 28 | 11PM to 12AM | 70.2 | 66.9 | 65.3 | 93.9 | 31.49 | 0.0743 | 0.63 | 13.64 | 0
March | 1 | 12AM to 1AM | 70 | 65.8 | 63.7 | 88.6 | 30.62 | 0.0743 | 0.59 | 13.62 | 0
March | 1 | 1AM to 2AM | 69.6 | 64.6 | 62.1 | 83.6 | 29.75 | 0.0744 | 0.56 | 13.6 | 0
March | 1 | 2AM to 3AM | 69.4 | 63.7 | 60.6 | 79.4 | 29.05 | 0.0745 | 0.53 | 13.58 | 0
March | 1 | 3AM to 4AM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
March | 1 | 4AM to 5AM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
March | 1 | 5AM to 6AM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
March | 1 | 6AM to 7AM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
March | 1 | 7AM to 8AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
March | 1 | 8AM to 9AM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
March | 1 | 9AM to 10AM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
March | 1 | 10AM to 11AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
March | 1 | 11AM to 12PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
March | 1 | 12PM to 1PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
March | 1 | 1PM to 2PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
March | 1 | 2PM to 3PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
March | 1 | 3PM to 4PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
March | 1 | 4PM to 5PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
March | 1 | 5PM to 6PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
March | 1 | 6PM to 7PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
March | 1 | 7PM to 8PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 1 | 8PM to 9PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
March | 1 | 9PM to 10PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
March | 1 | 10PM to 11PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
March | 1 | 11PM to 12AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
March | 2 | 12AM to 1AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
March | 2 | 1AM to 2AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
March | 2 | 2AM to 3AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
March | 2 | 3AM to 4AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
March | 2 | 4AM to 5AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
March | 2 | 5AM to 6AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 2 | 6AM to 7AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 2 | 7AM to 8AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 2 | 8AM to 9AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
March | 2 | 9AM to 10AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
March | 2 | 10AM to 11AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
March | 2 | 11AM to 12PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
March | 2 | 12PM to 1PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
March | 2 | 1PM to 2PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
March | 2 | 2PM to 3PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
March | 2 | 3PM to 4PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
March | 2 | 4PM to 5PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
March | 2 | 5PM to 6PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
March | 2 | 6PM to 7PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
March | 2 | 7PM to 8PM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
March | 2 | 8PM to 9PM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
March | 2 | 9PM to 10PM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
March | 2 | 10PM to 11PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
March | 2 | 11PM to 12AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
March | 3 | 12AM to 1AM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
March | 3 | 1AM to 2AM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
March | 3 | 2AM to 3AM | 68 | 67.3 | 66.9 | 99.5 | 31.82 | 0.0746 | 0.67 | 13.6 | 0
March | 3 | 3AM to 4AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
March | 3 | 4AM to 5AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
March | 3 | 5AM to 6AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
March | 3 | 6AM to 7AM | 70 | 69.4 | 69.1 | 107.3 | 33.54 | 0.0742 | 0.72 | 13.68 | 0
March | 3 | 7AM to 8AM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
March | 3 | 8AM to 9AM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
March | 3 | 9AM to 10AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
March | 3 | 10AM to 11AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
March | 3 | 11AM to 12PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
March | 3 | 12PM to 1PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
March | 3 | 1PM to 2PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
March | 3 | 2PM to 3PM | 72 | 70.6 | 70 | 110.8 | 34.56 | 0.0739 | 0.74 | 13.74 | 0
March | 3 | 3PM to 4PM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
March | 3 | 4PM to 5PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
March | 3 | 5PM to 6PM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
March | 3 | 6PM to 7PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
March | 3 | 7PM to 8PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
March | 3 | 8PM to 9PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
March | 3 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
March | 3 | 10PM to 11PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
March | 3 | 11PM to 12AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
March | 4 | 12AM to 1AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
March | 4 | 1AM to 2AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 4 | 2AM to 3AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
March | 4 | 3AM to 4AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
March | 4 | 4AM to 5AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
March | 4 | 5AM to 6AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
March | 4 | 6AM to 7AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
March | 4 | 7AM to 8AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
March | 4 | 8AM to 9AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
March | 4 | 9AM to 10AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
March | 4 | 10AM to 11AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
March | 4 | 11AM to 12PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
March | 4 | 12PM to 1PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
March | 4 | 1PM to 2PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
March | 4 | 2PM to 3PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
March | 4 | 3PM to 4PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
March | 4 | 4PM to 5PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
March | 4 | 5PM to 6PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
March | 4 | 6PM to 7PM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
March | 4 | 7PM to 8PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
March | 4 | 8PM to 9PM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
March | 4 | 9PM to 10PM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
March | 4 | 10PM to 11PM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
March | 4 | 11PM to 12AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
March | 5 | 12AM to 1AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
March | 5 | 1AM to 2AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
March | 5 | 2AM to 3AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
March | 5 | 3AM to 4AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
March | 5 | 4AM to 5AM | 64.9 | 63.6 | 63 | 86.4 | 29.03 | 0.0751 | 0.58 | 13.49 | 0
March | 5 | 5AM to 6AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
March | 5 | 6AM to 7AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
March | 5 | 7AM to 8AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
March | 5 | 8AM to 9AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 5 | 9AM to 10AM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
March | 5 | 10AM to 11AM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
March | 5 | 11AM to 12PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
March | 5 | 12PM to 1PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
March | 5 | 1PM to 2PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
March | 5 | 2PM to 3PM | 81 | 66.6 | 59 | 74.9 | 31.16 | 0.0729 | 0.5 | 13.86 | 0
March | 5 | 3PM to 4PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
March | 5 | 4PM to 5PM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
March | 5 | 5PM to 6PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
March | 5 | 6PM to 7PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
March | 5 | 7PM to 8PM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
March | 5 | 8PM to 9PM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
March | 5 | 9PM to 10PM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
March | 5 | 10PM to 11PM | 66.9 | 63.1 | 61 | 80.4 | 28.59 | 0.0748 | 0.54 | 13.52 | 0
March | 5 | 11PM to 12AM | 66 | 62.2 | 60.1 | 77.8 | 27.97 | 0.075 | 0.52 | 13.49 | 0
March | 6 | 12AM to 1AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
March | 6 | 1AM to 2AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
March | 6 | 2AM to 3AM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
March | 6 | 3AM to 4AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
March | 6 | 4AM to 5AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
March | 6 | 5AM to 6AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
March | 6 | 6AM to 7AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
March | 6 | 7AM to 8AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
March | 6 | 8AM to 9AM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
March | 6 | 9AM to 10AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
March | 6 | 10AM to 11AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
March | 6 | 11AM to 12PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
March | 6 | 12PM to 1PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
March | 6 | 1PM to 2PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
March | 6 | 2PM to 3PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
March | 6 | 3PM to 4PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
March | 6 | 4PM to 5PM | 78.1 | 65.1 | 57.9 | 72 | 30 | 0.0733 | 0.48 | 13.78 | 0
March | 6 | 5PM to 6PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
March | 6 | 6PM to 7PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
March | 6 | 7PM to 8PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
March | 6 | 8PM to 9PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
March | 6 | 9PM to 10PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
March | 6 | 10PM to 11PM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
March | 6 | 11PM to 12AM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
March | 7 | 12AM to 1AM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
March | 7 | 1AM to 2AM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
March | 7 | 2AM to 3AM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
March | 7 | 3AM to 4AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
March | 7 | 4AM to 5AM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
March | 7 | 5AM to 6AM | 66 | 58.7 | 54 | 62.2 | 25.53 | 0.0751 | 0.42 | 13.44 | 0
March | 7 | 6AM to 7AM | 66.9 | 58 | 52 | 57.8 | 25.06 | 0.075 | 0.39 | 13.45 | 0
March | 7 | 7AM to 8AM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
March | 7 | 8AM to 9AM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
March | 7 | 9AM to 10AM | 73.9 | 60.2 | 51.1 | 55.9 | 26.47 | 0.074 | 0.38 | 13.62 | 0
March | 7 | 10AM to 11AM | 75.9 | 62.3 | 54 | 62.2 | 27.95 | 0.0737 | 0.42 | 13.69 | 0
March | 7 | 11AM to 12PM | 75.9 | 62.8 | 55 | 64.7 | 28.34 | 0.0737 | 0.44 | 13.7 | 0
March | 7 | 12PM to 1PM | 79 | 63.9 | 55 | 64.7 | 29.09 | 0.0732 | 0.44 | 13.78 | 0
March | 7 | 1PM to 2PM | 80.1 | 64.2 | 55 | 64.7 | 29.35 | 0.0731 | 0.44 | 13.81 | 0
March | 7 | 2PM to 3PM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
March | 7 | 3PM to 4PM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
March | 7 | 4PM to 5PM | 75.9 | 62.3 | 54 | 62.2 | 27.95 | 0.0737 | 0.42 | 13.69 | 0
March | 7 | 5PM to 6PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
March | 7 | 6PM to 7PM | 71.1 | 59.5 | 52 | 57.8 | 26.07 | 0.0744 | 0.39 | 13.56 | 0
March | 7 | 7PM to 8PM | 68 | 59.4 | 54 | 62.2 | 26.02 | 0.0748 | 0.42 | 13.49 | 0
March | 7 | 8PM to 9PM | 66 | 58.2 | 53.1 | 60.1 | 25.21 | 0.0751 | 0.41 | 13.43 | 0
March | 7 | 9PM to 10PM | 64.9 | 58.3 | 54 | 62.2 | 25.27 | 0.0752 | 0.42 | 13.41 | 0
March | 7 | 10PM to 11PM | 64 | 57.9 | 54 | 62.2 | 25.05 | 0.0754 | 0.42 | 13.39 | 0
March | 7 | 11PM to 12AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
March | 8 | 12AM to 1AM | 63 | 57.5 | 54 | 62.2 | 24.79 | 0.0755 | 0.42 | 13.36 | 0
March | 8 | 1AM to 2AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
March | 8 | 2AM to 3AM | 60.1 | 56.4 | 54 | 62.2 | 24.08 | 0.0759 | 0.42 | 13.29 | 0
March | 8 | 3AM to 4AM | 59 | 56 | 54 | 62.2 | 23.82 | 0.0761 | 0.42 | 13.26 | 0
March | 8 | 4AM to 5AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
March | 8 | 5AM to 6AM | 59 | 57.1 | 55.9 | 66.9 | 24.55 | 0.0761 | 0.45 | 13.27 | 0
March | 8 | 6AM to 7AM | 59 | 56.6 | 55 | 64.7 | 24.21 | 0.0761 | 0.44 | 13.27 | 0
March | 8 | 7AM to 8AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
March | 8 | 8AM to 9AM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
March | 8 | 9AM to 10AM | 75 | 63.5 | 57 | 69.6 | 28.89 | 0.0738 | 0.47 | 13.69 | 0
March | 8 | 10AM to 11AM | 78.1 | 65.1 | 57.9 | 72 | 30 | 0.0733 | 0.48 | 13.78 | 0
March | 8 | 11AM to 12PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
March | 8 | 12PM to 1PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
March | 8 | 1PM to 2PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
March | 8 | 2PM to 3PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
March | 8 | 3PM to 4PM | 79 | 66.5 | 60.1 | 77.8 | 31.14 | 0.0732 | 0.52 | 13.82 | 0
March | 8 | 4PM to 5PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
March | 8 | 5PM to 6PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
March | 8 | 6PM to 7PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
March | 8 | 7PM to 8PM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
March | 8 | 8PM to 9PM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
March | 8 | 9PM to 10PM | 66.9 | 62.5 | 60.1 | 77.8 | 28.19 | 0.0748 | 0.52 | 13.51 | 0
March | 8 | 10PM to 11PM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
March | 8 | 11PM to 12AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
March | 9 | 12AM to 1AM | 64 | 62.1 | 61 | 80.4 | 27.89 | 0.0752 | 0.54 | 13.44 | 0
March | 9 | 1AM to 2AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
March | 9 | 2AM to 3AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
March | 9 | 3AM to 4AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
March | 9 | 4AM to 5AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
March | 9 | 5AM to 6AM | 63 | 61.1 | 60.1 | 77.8 | 27.22 | 0.0754 | 0.52 | 13.41 | 0
March | 9 | 6AM to 7AM | 62.1 | 60.1 | 59 | 74.9 | 26.53 | 0.0756 | 0.5 | 13.38 | 0
March | 9 | 7AM to 8AM | 66 | 64 | 63 | 86.4 | 29.3 | 0.0749 | 0.58 | 13.51 | 0
March | 9 | 8AM to 9AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
March | 9 | 9AM to 10AM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
March | 9 | 10AM to 11AM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
March | 9 | 11AM to 12PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
March | 9 | 12PM to 1PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
March | 9 | 1PM to 2PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
March | 9 | 2PM to 3PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
March | 9 | 3PM to 4PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
March | 9 | 4PM to 5PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
March | 9 | 5PM to 6PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
March | 9 | 6PM to 7PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
March | 9 | 7PM to 8PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
March | 9 | 8PM to 9PM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
March | 9 | 9PM to 10PM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
March | 9 | 10PM to 11PM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
March | 9 | 11PM to 12AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
March | 10 | 12AM to 1AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
March | 10 | 1AM to 2AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
March | 10 | 2AM to 3AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
March | 10 | 3AM to 4AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
March | 10 | 4AM to 5AM | 64 | 62.1 | 61 | 80.4 | 27.89 | 0.0752 | 0.54 | 13.44 | 0
March | 10 | 5AM to 6AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
March | 10 | 6AM to 7AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
March | 10 | 7AM to 8AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
March | 10 | 8AM to 9AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
March | 10 | 9AM to 10AM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
March | 10 | 10AM to 11AM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
March | 10 | 11AM to 12PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
March | 10 | 12PM to 1PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
March | 10 | 1PM to 2PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
March | 10 | 2PM to 3PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
March | 10 | 3PM to 4PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
March | 10 | 4PM to 5PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
March | 10 | 5PM to 6PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
March | 10 | 6PM to 7PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
March | 10 | 7PM to 8PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
March | 10 | 8PM to 9PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
March | 10 | 9PM to 10PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
March | 10 | 10PM to 11PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 10 | 11PM to 12AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 11 | 12AM to 1AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
March | 11 | 1AM to 2AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
March | 11 | 2AM to 3AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
March | 11 | 3AM to 4AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
March | 11 | 4AM to 5AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
March | 11 | 5AM to 6AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
March | 11 | 6AM to 7AM | 66.9 | 65.6 | 64.9 | 92.7 | 30.51 | 0.0747 | 0.62 | 13.56 | 0
March | 11 | 7AM to 8AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
March | 11 | 8AM to 9AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
March | 11 | 9AM to 10AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
March | 11 | 10AM to 11AM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
March | 11 | 11AM to 12PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
March | 11 | 12PM to 1PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
March | 11 | 1PM to 2PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
March | 11 | 2PM to 3PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
March | 11 | 3PM to 4PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
March | 11 | 4PM to 5PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
March | 11 | 5PM to 6PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
March | 11 | 6PM to 7PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
March | 11 | 7PM to 8PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
March | 11 | 8PM to 9PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
March | 11 | 9PM to 10PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
March | 11 | 10PM to 11PM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
March | 11 | 11PM to 12AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
March | 12 | 12AM to 1AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
March | 12 | 1AM to 2AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
March | 12 | 2AM to 3AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
March | 12 | 3AM to 4AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
March | 12 | 4AM to 5AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
March | 12 | 5AM to 6AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
March | 12 | 6AM to 7AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
March | 12 | 7AM to 8AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
March | 12 | 8AM to 9AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
March | 12 | 9AM to 10AM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
March | 12 | 10AM to 11AM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
March | 12 | 11AM to 12PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
March | 12 | 12PM to 1PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
March | 12 | 1PM to 2PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
March | 12 | 2PM to 3PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
March | 12 | 3PM to 4PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
March | 12 | 4PM to 5PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
March | 12 | 5PM to 6PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
March | 12 | 6PM to 7PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
March | 12 | 7PM to 8PM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
March | 12 | 8PM to 9PM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
March | 12 | 9PM to 10PM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
March | 12 | 10PM to 11PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
March | 12 | 11PM to 12AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
March | 13 | 12AM to 1AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
March | 13 | 1AM to 2AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
March | 13 | 2AM to 3AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
March | 13 | 3AM to 4AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
March | 13 | 4AM to 5AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
March | 13 | 5AM to 6AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
March | 13 | 6AM to 7AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
March | 13 | 7AM to 8AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
March | 13 | 8AM to 9AM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
March | 13 | 9AM to 10AM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
March | 13 | 10AM to 11AM | 81 | 74.5 | 72 | 118.7 | 38.03 | 0.0726 | 0.79 | 14 | 0
March | 13 | 11AM to 12PM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
March | 13 | 12PM to 1PM | 82 | 74.7 | 72 | 118.7 | 38.3 | 0.0725 | 0.79 | 14.03 | 0
March | 13 | 1PM to 2PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
March | 13 | 2PM to 3PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
March | 13 | 3PM to 4PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
March | 13 | 4PM to 5PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
March | 13 | 5PM to 6PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
March | 13 | 6PM to 7PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
March | 13 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
March | 13 | 8PM to 9PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
March | 13 | 9PM to 10PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 13 | 10PM to 11PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 13 | 11PM to 12AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 14 | 12AM to 1AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 14 | 1AM to 2AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 14 | 2AM to 3AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 14 | 3AM to 4AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 14 | 4AM to 5AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 14 | 5AM to 6AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 14 | 6AM to 7AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
March | 14 | 7AM to 8AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
March | 14 | 8AM to 9AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
March | 14 | 9AM to 10AM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
March | 14 | 10AM to 11AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
March | 14 | 11AM to 12PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
March | 14 | 12PM to 1PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
March | 14 | 1PM to 2PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
March | 14 | 2PM to 3PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
March | 14 | 3PM to 4PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
March | 14 | 4PM to 5PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
March | 14 | 5PM to 6PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
March | 14 | 6PM to 7PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
March | 14 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
March | 14 | 8PM to 9PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
March | 14 | 9PM to 10PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
March | 14 | 10PM to 11PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 14 | 11PM to 12AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
March | 15 | 12AM to 1AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
March | 15 | 1AM to 2AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 15 | 2AM to 3AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 15 | 3AM to 4AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
March | 15 | 4AM to 5AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
March | 15 | 5AM to 6AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
March | 15 | 6AM to 7AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
March | 15 | 7AM to 8AM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
March | 15 | 8AM to 9AM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
March | 15 | 9AM to 10AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
March | 15 | 10AM to 11AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
March | 15 | 11AM to 12PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
March | 15 | 12PM to 1PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
March | 15 | 1PM to 2PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
March | 15 | 2PM to 3PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
March | 15 | 3PM to 4PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
March | 15 | 4PM to 5PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
March | 15 | 5PM to 6PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
March | 15 | 6PM to 7PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
March | 15 | 7PM to 8PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
March | 15 | 8PM to 9PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
March | 15 | 9PM to 10PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 15 | 10PM to 11PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
March | 15 | 11PM to 12AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 16 | 12AM to 1AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
March | 16 | 1AM to 2AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
March | 16 | 2AM to 3AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
March | 16 | 3AM to 4AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
March | 16 | 4AM to 5AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
March | 16 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
March | 16 | 6AM to 7AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
March | 16 | 7AM to 8AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
March | 16 | 8AM to 9AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
March | 16 | 9AM to 10AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
March | 16 | 10AM to 11AM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
March | 16 | 11AM to 12PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
March | 16 | 12PM to 1PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
March | 16 | 1PM to 2PM | 84.9 | 68.4 | 60.1 | 77.8 | 32.6 | 0.0724 | 0.52 | 13.97 | 0
March | 16 | 2PM to 3PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
March | 16 | 3PM to 4PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
March | 16 | 4PM to 5PM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
March | 16 | 5PM to 6PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
March | 16 | 6PM to 7PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
March | 16 | 7PM to 8PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
March | 16 | 8PM to 9PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
March | 16 | 9PM to 10PM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
March | 16 | 10PM to 11PM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
March | 16 | 11PM to 12AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 17 | 12AM to 1AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
March | 17 | 1AM to 2AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
March | 17 | 2AM to 3AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
March | 17 | 3AM to 4AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
March | 17 | 4AM to 5AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
March | 17 | 5AM to 6AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
March | 17 | 6AM to 7AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
March | 17 | 7AM to 8AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
March | 17 | 8AM to 9AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
March | 17 | 9AM to 10AM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
March | 17 | 10AM to 11AM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
March | 17 | 11AM to 12PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
March | 17 | 12PM to 1PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
March | 17 | 1PM to 2PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
March | 17 | 2PM to 3PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
March | 17 | 3PM to 4PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
March | 17 | 4PM to 5PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
March | 17 | 5PM to 6PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
March | 17 | 6PM to 7PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
March | 17 | 7PM to 8PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
March | 17 | 8PM to 9PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
March | 17 | 9PM to 10PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
March | 17 | 10PM to 11PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
March | 17 | 11PM to 12AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
March | 18 | 12AM to 1AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 18 | 1AM to 2AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 18 | 2AM to 3AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 18 | 3AM to 4AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 18 | 4AM to 5AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
March | 18 | 5AM to 6AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
March | 18 | 6AM to 7AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
March | 18 | 7AM to 8AM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
March | 18 | 8AM to 9AM | 78.1 | 65.1 | 57.9 | 72 | 30 | 0.0733 | 0.48 | 13.78 | 0
March | 18 | 9AM to 10AM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
March | 18 | 10AM to 11AM | 82 | 66.9 | 59 | 74.9 | 31.42 | 0.0728 | 0.5 | 13.89 | 0
March | 18 | 11AM to 12PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
March | 18 | 12PM to 1PM | 81 | 68.3 | 62.1 | 83.6 | 32.53 | 0.0729 | 0.56 | 13.89 | 0
March | 18 | 1PM to 2PM | 81 | 68.3 | 62.1 | 83.6 | 32.53 | 0.0729 | 0.56 | 13.89 | 0
March | 18 | 2PM to 3PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
March | 18 | 3PM to 4PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
March | 18 | 4PM to 5PM | 79 | 66.5 | 60.1 | 77.8 | 31.14 | 0.0732 | 0.52 | 13.82 | 0
March | 18 | 5PM to 6PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
March | 18 | 6PM to 7PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
March | 18 | 7PM to 8PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
March | 18 | 8PM to 9PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
March | 18 | 9PM to 10PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
March | 18 | 10PM to 11PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
March | 18 | 11PM to 12AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
March | 19 | 12AM to 1AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
March | 19 | 1AM to 2AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
March | 19 | 2AM to 3AM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
March | 19 | 3AM to 4AM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
March | 19 | 4AM to 5AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
March | 19 | 5AM to 6AM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
March | 19 | 6AM to 7AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
March | 19 | 7AM to 8AM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
March | 19 | 8AM to 9AM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
March | 19 | 9AM to 10AM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
March | 19 | 10AM to 11AM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
March | 19 | 11AM to 12PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
March | 19 | 12PM to 1PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
March | 19 | 1PM to 2PM | 81 | 68.3 | 62.1 | 83.6 | 32.53 | 0.0729 | 0.56 | 13.89 | 0
March | 19 | 2PM to 3PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
March | 19 | 3PM to 4PM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
March | 19 | 4PM to 5PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
March | 19 | 5PM to 6PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
March | 19 | 6PM to 7PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
March | 19 | 7PM to 8PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
March | 19 | 8PM to 9PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
March | 19 | 9PM to 10PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
March | 19 | 10PM to 11PM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
March | 19 | 11PM to 12AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 20 | 12AM to 1AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
March | 20 | 1AM to 2AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
March | 20 | 2AM to 3AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
March | 20 | 3AM to 4AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
March | 20 | 4AM to 5AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
March | 20 | 5AM to 6AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
March | 20 | 6AM to 7AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
March | 20 | 7AM to 8AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
March | 20 | 8AM to 9AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
March | 20 | 9AM to 10AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
March | 20 | 10AM to 11AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
March | 20 | 11AM to 12PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
March | 20 | 12PM to 1PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
March | 20 | 1PM to 2PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
March | 20 | 2PM to 3PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
March | 20 | 3PM to 4PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
March | 20 | 4PM to 5PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
March | 20 | 5PM to 6PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
March | 20 | 6PM to 7PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
March | 20 | 7PM to 8PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
March | 20 | 8PM to 9PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
March | 20 | 9PM to 10PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
March | 20 | 10PM to 11PM | 68 | 63.4 | 61 | 80.4 | 28.86 | 0.0747 | 0.54 | 13.55 | 0
March | 20 | 11PM to 12AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
March | 21 | 12AM to 1AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
March | 21 | 1AM to 2AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
March | 21 | 2AM to 3AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
March | 21 | 3AM to 4AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
March | 21 | 4AM to 5AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
March | 21 | 5AM to 6AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
March | 21 | 6AM to 7AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
March | 21 | 7AM to 8AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
March | 21 | 8AM to 9AM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
March | 21 | 9AM to 10AM | 75.9 | 64.9 | 59 | 74.9 | 29.93 | 0.0736 | 0.5 | 13.73 | 0
March | 21 | 10AM to 11AM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
March | 21 | 11AM to 12PM | 78.1 | 64.6 | 57 | 69.6 | 29.64 | 0.0733 | 0.47 | 13.77 | 0
March | 21 | 12PM to 1PM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
March | 21 | 1PM to 2PM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
March | 21 | 2PM to 3PM | 78.1 | 63.6 | 55 | 64.7 | 28.87 | 0.0734 | 0.44 | 13.76 | 0
March | 21 | 3PM to 4PM | 78.1 | 63 | 54 | 62.2 | 28.47 | 0.0734 | 0.42 | 13.75 | 0
March | 21 | 4PM to 5PM | 75.9 | 62.8 | 55 | 64.7 | 28.34 | 0.0737 | 0.44 | 13.7 | 0
March | 21 | 5PM to 6PM | 75 | 61.5 | 53.1 | 60.1 | 27.41 | 0.0738 | 0.41 | 13.66 | 0
March | 21 | 6PM to 7PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
March | 21 | 7PM to 8PM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
March | 21 | 8PM to 9PM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
March | 21 | 9PM to 10PM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
March | 21 | 10PM to 11PM | 66 | 60.9 | 57.9 | 72 | 27.05 | 0.075 | 0.48 | 13.47 | 0
March | 21 | 11PM to 12AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 22 | 12AM to 1AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 22 | 1AM to 2AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 22 | 2AM to 3AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 22 | 3AM to 4AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
March | 22 | 4AM to 5AM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
March | 22 | 5AM to 6AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 22 | 6AM to 7AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
March | 22 | 7AM to 8AM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
March | 22 | 8AM to 9AM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
March | 22 | 9AM to 10AM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
March | 22 | 10AM to 11AM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
March | 22 | 11AM to 12PM | 79 | 64.3 | 55.9 | 66.9 | 29.43 | 0.0732 | 0.45 | 13.79 | 0
March | 22 | 12PM to 1PM | 78.1 | 65.1 | 57.9 | 72 | 30 | 0.0733 | 0.48 | 13.78 | 0
March | 22 | 1PM to 2PM | 78.1 | 65.1 | 57.9 | 72 | 30 | 0.0733 | 0.48 | 13.78 | 0
March | 22 | 2PM to 3PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
March | 22 | 3PM to 4PM | 77 | 65.3 | 59 | 74.9 | 30.19 | 0.0735 | 0.5 | 13.76 | 0
March | 22 | 4PM to 5PM | 75 | 64.6 | 59 | 74.9 | 29.71 | 0.0737 | 0.5 | 13.71 | 0
March | 22 | 5PM to 6PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
March | 22 | 6PM to 7PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
March | 22 | 7PM to 8PM | 66.9 | 63.1 | 61 | 80.4 | 28.59 | 0.0748 | 0.54 | 13.52 | 0
March | 22 | 8PM to 9PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
March | 22 | 9PM to 10PM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
March | 22 | 10PM to 11PM | 68 | 63.4 | 61 | 80.4 | 28.86 | 0.0747 | 0.54 | 13.55 | 0
March | 22 | 11PM to 12AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
March | 23 | 12AM to 1AM | 68 | 63.4 | 61 | 80.4 | 28.86 | 0.0747 | 0.54 | 13.55 | 0
March | 23 | 1AM to 2AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
March | 23 | 2AM to 3AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
March | 23 | 3AM to 4AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
March | 23 | 4AM to 5AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
March | 23 | 5AM to 6AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
March | 23 | 6AM to 7AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
March | 23 | 7AM to 8AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
March | 23 | 8AM to 9AM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
March | 23 | 9AM to 10AM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
March | 23 | 10AM to 11AM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
March | 23 | 11AM to 12PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
March | 23 | 12PM to 1PM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
March | 23 | 1PM to 2PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
March | 23 | 2PM to 3PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
March | 23 | 3PM to 4PM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
March | 23 | 4PM to 5PM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
March | 23 | 5PM to 6PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
March | 23 | 6PM to 7PM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
March | 23 | 7PM to 8PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
March | 23 | 8PM to 9PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
March | 23 | 9PM to 10PM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
March | 23 | 10PM to 11PM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
March | 23 | 11PM to 12AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
March | 24 | 12AM to 1AM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
March | 24 | 1AM to 2AM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
March | 24 | 2AM to 3AM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
March | 24 | 3AM to 4AM | 66.9 | 59 | 54 | 62.2 | 25.75 | 0.0749 | 0.42 | 13.46 | 0
March | 24 | 4AM to 5AM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
March | 24 | 5AM to 6AM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
March | 24 | 6AM to 7AM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
March | 24 | 7AM to 8AM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
March | 24 | 8AM to 9AM | 73.9 | 62.1 | 55 | 64.7 | 27.86 | 0.0739 | 0.44 | 13.65 | 0
March | 24 | 9AM to 10AM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
March | 24 | 10AM to 11AM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
March | 24 | 11AM to 12PM | 75.9 | 61.8 | 53.1 | 60.1 | 27.63 | 0.0737 | 0.41 | 13.69 | 0
March | 24 | 12PM to 1PM | 79 | 64.3 | 55.9 | 66.9 | 29.43 | 0.0732 | 0.45 | 13.79 | 0
March | 24 | 1PM to 2PM | 78.1 | 64.6 | 57 | 69.6 | 29.64 | 0.0733 | 0.47 | 13.77 | 0
March | 24 | 2PM to 3PM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
March | 24 | 3PM to 4PM | 75.9 | 63.3 | 55.9 | 66.9 | 28.69 | 0.0737 | 0.45 | 13.71 | 0
March | 24 | 4PM to 5PM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
March | 24 | 5PM to 6PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
March | 24 | 6PM to 7PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
March | 24 | 7PM to 8PM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
March | 24 | 8PM to 9PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
March | 24 | 9PM to 10PM | 66.9 | 59.6 | 55 | 64.7 | 26.15 | 0.0749 | 0.44 | 13.47 | 0
March | 24 | 10PM to 11PM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
March | 24 | 11PM to 12AM | 66 | 59.3 | 55 | 64.7 | 25.93 | 0.0751 | 0.44 | 13.45 | 0
March | 25 | 12AM to 1AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
March | 25 | 1AM to 2AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
March | 25 | 2AM to 3AM | 63 | 58.6 | 55.9 | 66.9 | 25.52 | 0.0755 | 0.45 | 13.38 | 0
March | 25 | 3AM to 4AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
March | 25 | 4AM to 5AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
March | 25 | 5AM to 6AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
March | 25 | 6AM to 7AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
March | 25 | 7AM to 8AM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
March | 25 | 8AM to 9AM | 73 | 62.3 | 55.9 | 66.9 | 27.98 | 0.074 | 0.45 | 13.63 | 0
March | 25 | 9AM to 10AM | 75.9 | 63.3 | 55.9 | 66.9 | 28.69 | 0.0737 | 0.45 | 13.71 | 0
March | 25 | 10AM to 11AM | 78.1 | 63.6 | 55 | 64.7 | 28.87 | 0.0734 | 0.44 | 13.76 | 0
March | 25 | 11AM to 12PM | 80.1 | 64.2 | 55 | 64.7 | 29.35 | 0.0731 | 0.44 | 13.81 | 0
March | 25 | 12PM to 1PM | 78.1 | 63.6 | 55 | 64.7 | 28.87 | 0.0734 | 0.44 | 13.76 | 0
March | 25 | 1PM to 2PM | 79 | 63.9 | 55 | 64.7 | 29.09 | 0.0732 | 0.44 | 13.78 | 0
March | 25 | 2PM to 3PM | 79 | 64.3 | 55.9 | 66.9 | 29.43 | 0.0732 | 0.45 | 13.79 | 0
March | 25 | 3PM to 4PM | 78.1 | 65.1 | 57.9 | 72 | 30 | 0.0733 | 0.48 | 13.78 | 0
March | 25 | 4PM to 5PM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
March | 25 | 5PM to 6PM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
March | 25 | 6PM to 7PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
March | 25 | 7PM to 8PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
March | 25 | 8PM to 9PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
March | 25 | 9PM to 10PM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
March | 25 | 10PM to 11PM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
March | 25 | 11PM to 12AM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
March | 26 | 12AM to 1AM | 66.9 | 60.1 | 55.9 | 66.9 | 26.49 | 0.0749 | 0.45 | 13.48 | 0
March | 26 | 1AM to 2AM | 66.9 | 60.7 | 57 | 69.6 | 26.91 | 0.0749 | 0.47 | 13.49 | 0
March | 26 | 2AM to 3AM | 66 | 60.4 | 57 | 69.6 | 26.69 | 0.075 | 0.47 | 13.46 | 0
March | 26 | 3AM to 4AM | 64 | 58.5 | 55 | 64.7 | 25.44 | 0.0753 | 0.44 | 13.4 | 0
March | 26 | 4AM to 5AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
March | 26 | 5AM to 6AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
March | 26 | 6AM to 7AM | 62.1 | 57.8 | 55 | 64.7 | 24.96 | 0.0756 | 0.44 | 13.35 | 0
March | 26 | 7AM to 8AM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
March | 26 | 8AM to 9AM | 75 | 63 | 55.9 | 66.9 | 28.47 | 0.0738 | 0.45 | 13.68 | 0
March | 26 | 9AM to 10AM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
March | 26 | 10AM to 11AM | 82 | 65.9 | 57 | 69.6 | 30.61 | 0.0728 | 0.47 | 13.87 | 0
March | 26 | 11AM to 12PM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
March | 26 | 12PM to 1PM | 81 | 66 | 57.9 | 72 | 30.71 | 0.0729 | 0.48 | 13.85 | 0
March | 26 | 1PM to 2PM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
March | 26 | 2PM to 3PM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
March | 26 | 3PM to 4PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
March | 26 | 4PM to 5PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
March | 26 | 5PM to 6PM | 75 | 65.2 | 60.1 | 77.8 | 30.17 | 0.0737 | 0.52 | 13.72 | 0
March | 26 | 6PM to 7PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
March | 26 | 7PM to 8PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
March | 26 | 8PM to 9PM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
March | 26 | 9PM to 10PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
March | 26 | 10PM to 11PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
March | 26 | 11PM to 12AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
March | 27 | 12AM to 1AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
March | 27 | 1AM to 2AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
March | 27 | 2AM to 3AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
March | 27 | 3AM to 4AM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
March | 27 | 4AM to 5AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
March | 27 | 5AM to 6AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
March | 27 | 6AM to 7AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
March | 27 | 7AM to 8AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
March | 27 | 8AM to 9AM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
March | 27 | 9AM to 10AM | 75.9 | 63.8 | 57 | 69.6 | 29.11 | 0.0736 | 0.47 | 13.72 | 0
March | 27 | 10AM to 11AM | 75.9 | 63.8 | 57 | 69.6 | 29.11 | 0.0736 | 0.47 | 13.72 | 0
March | 27 | 11AM to 12PM | 79 | 65.9 | 59 | 74.9 | 30.68 | 0.0732 | 0.5 | 13.81 | 0
March | 27 | 12PM to 1PM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
March | 27 | 1PM to 2PM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
March | 27 | 2PM to 3PM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
March | 27 | 3PM to 4PM | 79 | 65.9 | 59 | 74.9 | 30.68 | 0.0732 | 0.5 | 13.81 | 0
March | 27 | 4PM to 5PM | 79 | 66.5 | 60.1 | 77.8 | 31.14 | 0.0732 | 0.52 | 13.82 | 0
March | 27 | 5PM to 6PM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
March | 27 | 6PM to 7PM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
March | 27 | 7PM to 8PM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
March | 27 | 8PM to 9PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
March | 27 | 9PM to 10PM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
March | 27 | 10PM to 11PM | 66.9 | 62.5 | 60.1 | 77.8 | 28.19 | 0.0748 | 0.52 | 13.51 | 0
March | 27 | 11PM to 12AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
March | 28 | 12AM to 1AM | 64.9 | 60.5 | 57.9 | 72 | 26.79 | 0.0752 | 0.48 | 13.44 | 0
March | 28 | 1AM to 2AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
March | 28 | 2AM to 3AM | 64.9 | 60 | 57 | 69.6 | 26.43 | 0.0752 | 0.47 | 13.43 | 0
March | 28 | 3AM to 4AM | 62.1 | 58.3 | 55.9 | 66.9 | 25.3 | 0.0756 | 0.45 | 13.35 | 0
March | 28 | 4AM to 5AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 28 | 5AM to 6AM | 63 | 59.3 | 57 | 69.6 | 25.94 | 0.0755 | 0.47 | 13.38 | 0
March | 28 | 6AM to 7AM | 62.1 | 59.5 | 57.9 | 72 | 26.08 | 0.0756 | 0.48 | 13.37 | 0
March | 28 | 7AM to 8AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
March | 28 | 8AM to 9AM | 75 | 64.6 | 59 | 74.9 | 29.71 | 0.0737 | 0.5 | 13.71 | 0
March | 28 | 9AM to 10AM | 79 | 65.3 | 57.9 | 72 | 30.22 | 0.0732 | 0.48 | 13.8 | 0
March | 28 | 10AM to 11AM | 82.9 | 66.6 | 57.9 | 72 | 31.19 | 0.0727 | 0.48 | 13.9 | 0
March | 28 | 11AM to 12PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
March | 28 | 12PM to 1PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
March | 28 | 1PM to 2PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
March | 28 | 2PM to 3PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
March | 28 | 3PM to 4PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
March | 28 | 4PM to 5PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
March | 28 | 5PM to 6PM | 75.9 | 64.9 | 59 | 74.9 | 29.93 | 0.0736 | 0.5 | 13.73 | 0
March | 28 | 6PM to 7PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
March | 28 | 7PM to 8PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
March | 28 | 8PM to 9PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
March | 28 | 9PM to 10PM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
March | 28 | 10PM to 11PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
March | 28 | 11PM to 12AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
March | 29 | 12AM to 1AM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
March | 29 | 1AM to 2AM | 66.9 | 63.1 | 61 | 80.4 | 28.59 | 0.0748 | 0.54 | 13.52 | 0
March | 29 | 2AM to 3AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
March | 29 | 3AM to 4AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
March | 29 | 4AM to 5AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
March | 29 | 5AM to 6AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
March | 29 | 6AM to 7AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
March | 29 | 7AM to 8AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
March | 29 | 8AM to 9AM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
March | 29 | 9AM to 10AM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
March | 29 | 10AM to 11AM | 82.9 | 67.2 | 59 | 74.9 | 31.64 | 0.0726 | 0.5 | 13.91 | 0
March | 29 | 11AM to 12PM | 84 | 68.1 | 60.1 | 77.8 | 32.38 | 0.0725 | 0.52 | 13.95 | 0
March | 29 | 12PM to 1PM | 86 | 68.1 | 59 | 74.9 | 32.39 | 0.0722 | 0.5 | 13.99 | 0
March | 29 | 1PM to 2PM | 84.9 | 69.5 | 62.1 | 83.6 | 33.51 | 0.0723 | 0.56 | 13.99 | 0
March | 29 | 2PM to 3PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
March | 29 | 3PM to 4PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
March | 29 | 4PM to 5PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
March | 29 | 5PM to 6PM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
March | 29 | 6PM to 7PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
March | 29 | 7PM to 8PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 29 | 8PM to 9PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
March | 29 | 9PM to 10PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
March | 29 | 10PM to 11PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
March | 29 | 11PM to 12AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
March | 30 | 12AM to 1AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
March | 30 | 1AM to 2AM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
March | 30 | 2AM to 3AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
March | 30 | 3AM to 4AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
March | 30 | 4AM to 5AM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
March | 30 | 5AM to 6AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
March | 30 | 6AM to 7AM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
March | 30 | 7AM to 8AM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
March | 30 | 8AM to 9AM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
March | 30 | 9AM to 10AM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
March | 30 | 10AM to 11AM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
March | 30 | 11AM to 12PM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
March | 30 | 12PM to 1PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
March | 30 | 1PM to 2PM | 84.9 | 69.5 | 62.1 | 83.6 | 33.51 | 0.0723 | 0.56 | 13.99 | 0
March | 30 | 2PM to 3PM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
March | 30 | 3PM to 4PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
March | 30 | 4PM to 5PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
March | 30 | 5PM to 6PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
March | 30 | 6PM to 7PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
March | 30 | 7PM to 8PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
March | 30 | 8PM to 9PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
March | 30 | 9PM to 10PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
March | 30 | 10PM to 11PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
March | 30 | 11PM to 12AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
March | 31 | 12AM to 1AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
March | 31 | 1AM to 2AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
March | 31 | 2AM to 3AM | 72 | 70.6 | 70 | 110.8 | 34.56 | 0.0739 | 0.74 | 13.74 | 0
March | 31 | 3AM to 4AM | 72 | 70.6 | 70 | 110.8 | 34.56 | 0.0739 | 0.74 | 13.74 | 0
March | 31 | 4AM to 5AM | 72 | 70.6 | 70 | 110.8 | 34.56 | 0.0739 | 0.74 | 13.74 | 0
March | 31 | 5AM to 6AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
March | 31 | 6AM to 7AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
March | 31 | 7AM to 8AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
March | 31 | 8AM to 9AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
March | 31 | 9AM to 10AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
March | 31 | 10AM to 11AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
March | 31 | 11AM to 12PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
March | 31 | 12PM to 1PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
March | 31 | 1PM to 2PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
March | 31 | 2PM to 3PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
March | 31 | 3PM to 4PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
March | 31 | 4PM to 5PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
March | 31 | 5PM to 6PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
March | 31 | 6PM to 7PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
March | 31 | 7PM to 8PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
March | 31 | 8PM to 9PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
March | 31 | 9PM to 10PM | 73.9 | 68.1 | 65.3 | 93.9 | 32.42 | 0.0738 | 0.63 | 13.74 | 0
March | 31 | 10PM to 11PM | 73 | 66.6 | 63.5 | 88.1 | 31.28 | 0.0739 | 0.59 | 13.7 | 0
March | 31 | 11PM to 12AM | 72 | 65.3 | 61.9 | 83.1 | 30.24 | 0.0741 | 0.56 | 13.66 | 0
April | 1 | 12AM to 1AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
April | 1 | 1AM to 2AM | 70 | 62.6 | 58.5 | 73.4 | 28.25 | 0.0744 | 0.49 | 13.58 | 0
April | 1 | 2AM to 3AM | 69.1 | 61.3 | 56.7 | 68.7 | 27.3 | 0.0746 | 0.46 | 13.54 | 0
April | 1 | 3AM to 4AM | 68 | 60 | 55 | 64.7 | 26.41 | 0.0748 | 0.44 | 13.5 | 0
April | 1 | 4AM to 5AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
April | 1 | 5AM to 6AM | 66.9 | 57 | 50 | 53.6 | 24.42 | 0.075 | 0.36 | 13.44 | 0
April | 1 | 6AM to 7AM | 68 | 59 | 53.1 | 60.1 | 25.7 | 0.0748 | 0.41 | 13.48 | 0
April | 1 | 7AM to 8AM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
April | 1 | 8AM to 9AM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
April | 1 | 9AM to 10AM | 75.9 | 62.3 | 54 | 62.2 | 27.95 | 0.0737 | 0.42 | 13.69 | 0
April | 1 | 10AM to 11AM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
April | 1 | 11AM to 12PM | 78.1 | 62.6 | 53.1 | 60.1 | 28.15 | 0.0734 | 0.41 | 13.74 | 0
April | 1 | 12PM to 1PM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
April | 1 | 1PM to 2PM | 78.1 | 63 | 54 | 62.2 | 28.47 | 0.0734 | 0.42 | 13.75 | 0
April | 1 | 2PM to 3PM | 78.1 | 63 | 54 | 62.2 | 28.47 | 0.0734 | 0.42 | 13.75 | 0
April | 1 | 3PM to 4PM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
April | 1 | 4PM to 5PM | 75 | 62.5 | 55 | 64.7 | 28.12 | 0.0738 | 0.44 | 13.68 | 0
April | 1 | 5PM to 6PM | 73 | 61.3 | 54 | 62.2 | 27.24 | 0.0741 | 0.42 | 13.62 | 0
April | 1 | 6PM to 7PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
April | 1 | 7PM to 8PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
April | 1 | 8PM to 9PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
April | 1 | 9PM to 10PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
April | 1 | 10PM to 11PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
April | 1 | 11PM to 12AM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
April | 2 | 12AM to 1AM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
April | 2 | 1AM to 2AM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
April | 2 | 2AM to 3AM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
April | 2 | 3AM to 4AM | 69.1 | 59.8 | 54 | 62.2 | 26.28 | 0.0746 | 0.42 | 13.52 | 0
April | 2 | 4AM to 5AM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
April | 2 | 5AM to 6AM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
April | 2 | 6AM to 7AM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
April | 2 | 7AM to 8AM | 73 | 62.9 | 57 | 69.6 | 28.41 | 0.074 | 0.47 | 13.64 | 0
April | 2 | 8AM to 9AM | 73 | 62.9 | 57 | 69.6 | 28.41 | 0.074 | 0.47 | 13.64 | 0
April | 2 | 9AM to 10AM | 78.1 | 63.6 | 55 | 64.7 | 28.87 | 0.0734 | 0.44 | 13.76 | 0
April | 2 | 10AM to 11AM | 80.1 | 65.7 | 57.9 | 72 | 30.49 | 0.0731 | 0.48 | 13.83 | 0
April | 2 | 11AM to 12PM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
April | 2 | 12PM to 1PM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
April | 2 | 1PM to 2PM | 81 | 65 | 55.9 | 66.9 | 29.92 | 0.073 | 0.45 | 13.84 | 0
April | 2 | 2PM to 3PM | 80.1 | 64.2 | 55 | 64.7 | 29.35 | 0.0731 | 0.44 | 13.81 | 0
April | 2 | 3PM to 4PM | 78.1 | 64 | 55.9 | 66.9 | 29.21 | 0.0734 | 0.45 | 13.76 | 0
April | 2 | 4PM to 5PM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
April | 2 | 5PM to 6PM | 73.9 | 63.7 | 57.9 | 72 | 28.99 | 0.0739 | 0.48 | 13.67 | 0
April | 2 | 6PM to 7PM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
April | 2 | 7PM to 8PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
April | 2 | 8PM to 9PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
April | 2 | 9PM to 10PM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
April | 2 | 10PM to 11PM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
April | 2 | 11PM to 12AM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
April | 3 | 12AM to 1AM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
April | 3 | 1AM to 2AM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
April | 3 | 2AM to 3AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
April | 3 | 3AM to 4AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
April | 3 | 4AM to 5AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
April | 3 | 5AM to 6AM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
April | 3 | 6AM to 7AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
April | 3 | 7AM to 8AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 3 | 8AM to 9AM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
April | 3 | 9AM to 10AM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
April | 3 | 10AM to 11AM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
April | 3 | 11AM to 12PM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
April | 3 | 12PM to 1PM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
April | 3 | 1PM to 2PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
April | 3 | 2PM to 3PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
April | 3 | 3PM to 4PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
April | 3 | 4PM to 5PM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
April | 3 | 5PM to 6PM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
April | 3 | 6PM to 7PM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
April | 3 | 7PM to 8PM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
April | 3 | 8PM to 9PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
April | 3 | 9PM to 10PM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
April | 3 | 10PM to 11PM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
April | 3 | 11PM to 12AM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
April | 4 | 12AM to 1AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
April | 4 | 1AM to 2AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
April | 4 | 2AM to 3AM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
April | 4 | 3AM to 4AM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
April | 4 | 4AM to 5AM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
April | 4 | 5AM to 6AM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.53 | 0
April | 4 | 6AM to 7AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
April | 4 | 7AM to 8AM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
April | 4 | 8AM to 9AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 4 | 9AM to 10AM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
April | 4 | 10AM to 11AM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
April | 4 | 11AM to 12PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
April | 4 | 12PM to 1PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
April | 4 | 1PM to 2PM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
April | 4 | 2PM to 3PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
April | 4 | 3PM to 4PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
April | 4 | 4PM to 5PM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
April | 4 | 5PM to 6PM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
April | 4 | 6PM to 7PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
April | 4 | 7PM to 8PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 4 | 8PM to 9PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 4 | 9PM to 10PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 4 | 10PM to 11PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
April | 4 | 11PM to 12AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
April | 5 | 12AM to 1AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
April | 5 | 1AM to 2AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
April | 5 | 2AM to 3AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
April | 5 | 3AM to 4AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
April | 5 | 4AM to 5AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
April | 5 | 5AM to 6AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
April | 5 | 6AM to 7AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
April | 5 | 7AM to 8AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 5 | 8AM to 9AM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
April | 5 | 9AM to 10AM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
April | 5 | 10AM to 11AM | 82 | 66.3 | 57.9 | 72 | 30.97 | 0.0728 | 0.48 | 13.88 | 0
April | 5 | 11AM to 12PM | 84.9 | 65.3 | 54 | 62.2 | 30.14 | 0.0725 | 0.42 | 13.92 | 0
April | 5 | 12PM to 1PM | 84 | 65.5 | 55 | 64.7 | 30.32 | 0.0726 | 0.44 | 13.91 | 0
April | 5 | 1PM to 2PM | 84 | 66 | 55.9 | 66.9 | 30.66 | 0.0726 | 0.45 | 13.91 | 0
April | 5 | 2PM to 3PM | 84 | 68.1 | 60.1 | 77.8 | 32.38 | 0.0725 | 0.52 | 13.95 | 0
April | 5 | 3PM to 4PM | 82 | 66.9 | 59 | 74.9 | 31.42 | 0.0728 | 0.5 | 13.89 | 0
April | 5 | 4PM to 5PM | 80.1 | 64.7 | 55.9 | 66.9 | 29.7 | 0.0731 | 0.45 | 13.81 | 0
April | 5 | 5PM to 6PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
April | 5 | 6PM to 7PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 5 | 7PM to 8PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 5 | 8PM to 9PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 5 | 9PM to 10PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 5 | 10PM to 11PM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
April | 5 | 11PM to 12AM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
April | 6 | 12AM to 1AM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
April | 6 | 1AM to 2AM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
April | 6 | 2AM to 3AM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
April | 6 | 3AM to 4AM | 73 | 62.9 | 57 | 69.6 | 28.41 | 0.074 | 0.47 | 13.64 | 0
April | 6 | 4AM to 5AM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
April | 6 | 5AM to 6AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
April | 6 | 6AM to 7AM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
April | 6 | 7AM to 8AM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
April | 6 | 8AM to 9AM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
April | 6 | 9AM to 10AM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
April | 6 | 10AM to 11AM | 82.9 | 65.6 | 55.9 | 66.9 | 30.4 | 0.0727 | 0.45 | 13.89 | 0
April | 6 | 11AM to 12PM | 80.1 | 65.7 | 57.9 | 72 | 30.49 | 0.0731 | 0.48 | 13.83 | 0
April | 6 | 12PM to 1PM | 82.9 | 65.2 | 55 | 64.7 | 30.06 | 0.0727 | 0.44 | 13.88 | 0
April | 6 | 1PM to 2PM | 81 | 66 | 57.9 | 72 | 30.71 | 0.0729 | 0.48 | 13.85 | 0
April | 6 | 2PM to 3PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
April | 6 | 3PM to 4PM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
April | 6 | 4PM to 5PM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
April | 6 | 5PM to 6PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
April | 6 | 6PM to 7PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
April | 6 | 7PM to 8PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
April | 6 | 8PM to 9PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 6 | 9PM to 10PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 6 | 10PM to 11PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 6 | 11PM to 12AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
April | 7 | 12AM to 1AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
April | 7 | 1AM to 2AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 7 | 2AM to 3AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 7 | 3AM to 4AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 7 | 4AM to 5AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 7 | 5AM to 6AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
April | 7 | 6AM to 7AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 7 | 7AM to 8AM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
April | 7 | 8AM to 9AM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
April | 7 | 9AM to 10AM | 82 | 66.9 | 59 | 74.9 | 31.42 | 0.0728 | 0.5 | 13.89 | 0
April | 7 | 10AM to 11AM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
April | 7 | 11AM to 12PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
April | 7 | 12PM to 1PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
April | 7 | 1PM to 2PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
April | 7 | 2PM to 3PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
April | 7 | 3PM to 4PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
April | 7 | 4PM to 5PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
April | 7 | 5PM to 6PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
April | 7 | 6PM to 7PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
April | 7 | 7PM to 8PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
April | 7 | 8PM to 9PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
April | 7 | 9PM to 10PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 7 | 10PM to 11PM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
April | 7 | 11PM to 12AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
April | 8 | 12AM to 1AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
April | 8 | 1AM to 2AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
April | 8 | 2AM to 3AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
April | 8 | 3AM to 4AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
April | 8 | 4AM to 5AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
April | 8 | 5AM to 6AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
April | 8 | 6AM to 7AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 8 | 7AM to 8AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
April | 8 | 8AM to 9AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 8 | 9AM to 10AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
April | 8 | 10AM to 11AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
April | 8 | 11AM to 12PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
April | 8 | 12PM to 1PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
April | 8 | 1PM to 2PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
April | 8 | 2PM to 3PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
April | 8 | 3PM to 4PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
April | 8 | 4PM to 5PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
April | 8 | 5PM to 6PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
April | 8 | 6PM to 7PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 8 | 7PM to 8PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 8 | 8PM to 9PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
April | 8 | 9PM to 10PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 8 | 10PM to 11PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 8 | 11PM to 12AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
April | 9 | 12AM to 1AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
April | 9 | 1AM to 2AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
April | 9 | 2AM to 3AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
April | 9 | 3AM to 4AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 9 | 4AM to 5AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 9 | 5AM to 6AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 9 | 6AM to 7AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 9 | 7AM to 8AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
April | 9 | 8AM to 9AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
April | 9 | 9AM to 10AM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
April | 9 | 10AM to 11AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
April | 9 | 11AM to 12PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
April | 9 | 12PM to 1PM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
April | 9 | 1PM to 2PM | 86 | 68.1 | 59 | 74.9 | 32.39 | 0.0722 | 0.5 | 13.99 | 0
April | 9 | 2PM to 3PM | 84.9 | 68.4 | 60.1 | 77.8 | 32.6 | 0.0724 | 0.52 | 13.97 | 0
April | 9 | 3PM to 4PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
April | 9 | 4PM to 5PM | 81 | 68.3 | 62.1 | 83.6 | 32.53 | 0.0729 | 0.56 | 13.89 | 0
April | 9 | 5PM to 6PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
April | 9 | 6PM to 7PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
April | 9 | 7PM to 8PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
April | 9 | 8PM to 9PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
April | 9 | 9PM to 10PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
April | 9 | 10PM to 11PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 9 | 11PM to 12AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
April | 10 | 12AM to 1AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
April | 10 | 1AM to 2AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
April | 10 | 2AM to 3AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
April | 10 | 3AM to 4AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
April | 10 | 4AM to 5AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 10 | 5AM to 6AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
April | 10 | 6AM to 7AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 10 | 7AM to 8AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
April | 10 | 8AM to 9AM | 81 | 68.3 | 62.1 | 83.6 | 32.53 | 0.0729 | 0.56 | 13.89 | 0
April | 10 | 9AM to 10AM | 84.9 | 69.5 | 62.1 | 83.6 | 33.51 | 0.0723 | 0.56 | 13.99 | 0
April | 10 | 10AM to 11AM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
April | 10 | 11AM to 12PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
April | 10 | 12PM to 1PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
April | 10 | 1PM to 2PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
April | 10 | 2PM to 3PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
April | 10 | 3PM to 4PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
April | 10 | 4PM to 5PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
April | 10 | 5PM to 6PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
April | 10 | 6PM to 7PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
April | 10 | 7PM to 8PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
April | 10 | 8PM to 9PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
April | 10 | 9PM to 10PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
April | 10 | 10PM to 11PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 10 | 11PM to 12AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 11 | 12AM to 1AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
April | 11 | 1AM to 2AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
April | 11 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
April | 11 | 3AM to 4AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
April | 11 | 4AM to 5AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
April | 11 | 5AM to 6AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 11 | 6AM to 7AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
April | 11 | 7AM to 8AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
April | 11 | 8AM to 9AM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
April | 11 | 9AM to 10AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
April | 11 | 10AM to 11AM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
April | 11 | 11AM to 12PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
April | 11 | 12PM to 1PM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
April | 11 | 1PM to 2PM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
April | 11 | 2PM to 3PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
April | 11 | 3PM to 4PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
April | 11 | 4PM to 5PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
April | 11 | 5PM to 6PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
April | 11 | 6PM to 7PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
April | 11 | 7PM to 8PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
April | 11 | 8PM to 9PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
April | 11 | 9PM to 10PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
April | 11 | 10PM to 11PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
April | 11 | 11PM to 12AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
April | 12 | 12AM to 1AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 12 | 1AM to 2AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
April | 12 | 2AM to 3AM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
April | 12 | 3AM to 4AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
April | 12 | 4AM to 5AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
April | 12 | 5AM to 6AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
April | 12 | 6AM to 7AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
April | 12 | 7AM to 8AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 12 | 8AM to 9AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
April | 12 | 9AM to 10AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
April | 12 | 10AM to 11AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
April | 12 | 11AM to 12PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
April | 12 | 12PM to 1PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
April | 12 | 1PM to 2PM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
April | 12 | 2PM to 3PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
April | 12 | 3PM to 4PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
April | 12 | 4PM to 5PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
April | 12 | 5PM to 6PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
April | 12 | 6PM to 7PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 12 | 7PM to 8PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
April | 12 | 8PM to 9PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
April | 12 | 9PM to 10PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 12 | 10PM to 11PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 12 | 11PM to 12AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
April | 13 | 12AM to 1AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 13 | 1AM to 2AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 13 | 2AM to 3AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 13 | 3AM to 4AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 13 | 4AM to 5AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 13 | 5AM to 6AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
April | 13 | 6AM to 7AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
April | 13 | 7AM to 8AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
April | 13 | 8AM to 9AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
April | 13 | 9AM to 10AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
April | 13 | 10AM to 11AM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
April | 13 | 11AM to 12PM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
April | 13 | 12PM to 1PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
April | 13 | 1PM to 2PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
April | 13 | 2PM to 3PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
April | 13 | 3PM to 4PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
April | 13 | 4PM to 5PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
April | 13 | 5PM to 6PM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
April | 13 | 6PM to 7PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 13 | 7PM to 8PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
April | 13 | 8PM to 9PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 13 | 9PM to 10PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 13 | 10PM to 11PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
April | 13 | 11PM to 12AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
April | 14 | 12AM to 1AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 14 | 1AM to 2AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
April | 14 | 2AM to 3AM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
April | 14 | 3AM to 4AM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
April | 14 | 4AM to 5AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 14 | 5AM to 6AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
April | 14 | 6AM to 7AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 14 | 7AM to 8AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 14 | 8AM to 9AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
April | 14 | 9AM to 10AM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
April | 14 | 10AM to 11AM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
April | 14 | 11AM to 12PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
April | 14 | 12PM to 1PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
April | 14 | 1PM to 2PM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
April | 14 | 2PM to 3PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
April | 14 | 3PM to 4PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
April | 14 | 4PM to 5PM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
April | 14 | 5PM to 6PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
April | 14 | 6PM to 7PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 14 | 7PM to 8PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
April | 14 | 8PM to 9PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
April | 14 | 9PM to 10PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
April | 14 | 10PM to 11PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 14 | 11PM to 12AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 15 | 12AM to 1AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 15 | 1AM to 2AM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
April | 15 | 2AM to 3AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
April | 15 | 3AM to 4AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
April | 15 | 4AM to 5AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
April | 15 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
April | 15 | 6AM to 7AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
April | 15 | 7AM to 8AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
April | 15 | 8AM to 9AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 15 | 9AM to 10AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
April | 15 | 10AM to 11AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
April | 15 | 11AM to 12PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
April | 15 | 12PM to 1PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
April | 15 | 1PM to 2PM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
April | 15 | 2PM to 3PM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
April | 15 | 3PM to 4PM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
April | 15 | 4PM to 5PM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
April | 15 | 5PM to 6PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
April | 15 | 6PM to 7PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 15 | 7PM to 8PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 15 | 8PM to 9PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 15 | 9PM to 10PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 15 | 10PM to 11PM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
April | 15 | 11PM to 12AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
April | 16 | 12AM to 1AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
April | 16 | 1AM to 2AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
April | 16 | 2AM to 3AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
April | 16 | 3AM to 4AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
April | 16 | 4AM to 5AM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
April | 16 | 5AM to 6AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
April | 16 | 6AM to 7AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 16 | 7AM to 8AM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
April | 16 | 8AM to 9AM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
April | 16 | 9AM to 10AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
April | 16 | 10AM to 11AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
April | 16 | 11AM to 12PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
April | 16 | 12PM to 1PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
April | 16 | 1PM to 2PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
April | 16 | 2PM to 3PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
April | 16 | 3PM to 4PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
April | 16 | 4PM to 5PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
April | 16 | 5PM to 6PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 16 | 6PM to 7PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
April | 16 | 7PM to 8PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 16 | 8PM to 9PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
April | 16 | 9PM to 10PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 16 | 10PM to 11PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 16 | 11PM to 12AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 17 | 12AM to 1AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 17 | 1AM to 2AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 17 | 2AM to 3AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
April | 17 | 3AM to 4AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 17 | 4AM to 5AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 17 | 5AM to 6AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 17 | 6AM to 7AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 17 | 7AM to 8AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
April | 17 | 8AM to 9AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
April | 17 | 9AM to 10AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
April | 17 | 10AM to 11AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
April | 17 | 11AM to 12PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
April | 17 | 12PM to 1PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
April | 17 | 1PM to 2PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
April | 17 | 2PM to 3PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
April | 17 | 3PM to 4PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
April | 17 | 4PM to 5PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
April | 17 | 5PM to 6PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
April | 17 | 6PM to 7PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 17 | 7PM to 8PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 17 | 8PM to 9PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
April | 17 | 9PM to 10PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
April | 17 | 10PM to 11PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 17 | 11PM to 12AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
April | 18 | 12AM to 1AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
April | 18 | 1AM to 2AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 18 | 2AM to 3AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 18 | 3AM to 4AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 18 | 4AM to 5AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
April | 18 | 5AM to 6AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
April | 18 | 6AM to 7AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 18 | 7AM to 8AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
April | 18 | 8AM to 9AM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
April | 18 | 9AM to 10AM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
April | 18 | 10AM to 11AM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
April | 18 | 11AM to 12PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
April | 18 | 12PM to 1PM | 84 | 67.5 | 59 | 74.9 | 31.91 | 0.0725 | 0.5 | 13.94 | 0
April | 18 | 1PM to 2PM | 84 | 67 | 57.9 | 72 | 31.46 | 0.0725 | 0.48 | 13.93 | 0
April | 18 | 2PM to 3PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
April | 18 | 3PM to 4PM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
April | 18 | 4PM to 5PM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
April | 18 | 5PM to 6PM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
April | 18 | 6PM to 7PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
April | 18 | 7PM to 8PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 18 | 8PM to 9PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
April | 18 | 9PM to 10PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 18 | 10PM to 11PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
April | 18 | 11PM to 12AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
April | 19 | 12AM to 1AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
April | 19 | 1AM to 2AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
April | 19 | 2AM to 3AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
April | 19 | 3AM to 4AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
April | 19 | 4AM to 5AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
April | 19 | 5AM to 6AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
April | 19 | 6AM to 7AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
April | 19 | 7AM to 8AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
April | 19 | 8AM to 9AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
April | 19 | 9AM to 10AM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
April | 19 | 10AM to 11AM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
April | 19 | 11AM to 12PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
April | 19 | 12PM to 1PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
April | 19 | 1PM to 2PM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
April | 19 | 2PM to 3PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
April | 19 | 3PM to 4PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
April | 19 | 4PM to 5PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
April | 19 | 5PM to 6PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
April | 19 | 6PM to 7PM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
April | 19 | 7PM to 8PM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
April | 19 | 8PM to 9PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 19 | 9PM to 10PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
April | 19 | 10PM to 11PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
April | 19 | 11PM to 12AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
April | 20 | 12AM to 1AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
April | 20 | 1AM to 2AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
April | 20 | 2AM to 3AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
April | 20 | 3AM to 4AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
April | 20 | 4AM to 5AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
April | 20 | 5AM to 6AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
April | 20 | 6AM to 7AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
April | 20 | 7AM to 8AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
April | 20 | 8AM to 9AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
April | 20 | 9AM to 10AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
April | 20 | 10AM to 11AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
April | 20 | 11AM to 12PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
April | 20 | 12PM to 1PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
April | 20 | 1PM to 2PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
April | 20 | 2PM to 3PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
April | 20 | 3PM to 4PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
April | 20 | 4PM to 5PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
April | 20 | 5PM to 6PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
April | 20 | 6PM to 7PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
April | 20 | 7PM to 8PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
April | 20 | 8PM to 9PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 20 | 9PM to 10PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
April | 20 | 10PM to 11PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
April | 20 | 11PM to 12AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 21 | 12AM to 1AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 21 | 1AM to 2AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
April | 21 | 2AM to 3AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
April | 21 | 3AM to 4AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
April | 21 | 4AM to 5AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
April | 21 | 5AM to 6AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
April | 21 | 6AM to 7AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
April | 21 | 7AM to 8AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
April | 21 | 8AM to 9AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
April | 21 | 9AM to 10AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
April | 21 | 10AM to 11AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
April | 21 | 11AM to 12PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
April | 21 | 12PM to 1PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
April | 21 | 1PM to 2PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
April | 21 | 2PM to 3PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
April | 21 | 3PM to 4PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
April | 21 | 4PM to 5PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
April | 21 | 5PM to 6PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
April | 21 | 6PM to 7PM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
April | 21 | 7PM to 8PM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
April | 21 | 8PM to 9PM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
April | 21 | 9PM to 10PM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
April | 21 | 10PM to 11PM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
April | 21 | 11PM to 12AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
April | 22 | 12AM to 1AM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
April | 22 | 1AM to 2AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
April | 22 | 2AM to 3AM | 64 | 61.5 | 60.1 | 77.8 | 27.48 | 0.0753 | 0.52 | 13.44 | 0
April | 22 | 3AM to 4AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
April | 22 | 4AM to 5AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
April | 22 | 5AM to 6AM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
April | 22 | 6AM to 7AM | 66 | 62.8 | 61 | 80.4 | 28.37 | 0.075 | 0.54 | 13.5 | 0
April | 22 | 7AM to 8AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 22 | 8AM to 9AM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
April | 22 | 9AM to 10AM | 77 | 65.3 | 59 | 74.9 | 30.19 | 0.0735 | 0.5 | 13.76 | 0
April | 22 | 10AM to 11AM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
April | 22 | 11AM to 12PM | 82 | 66.9 | 59 | 74.9 | 31.42 | 0.0728 | 0.5 | 13.89 | 0
April | 22 | 12PM to 1PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
April | 22 | 1PM to 2PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
April | 22 | 2PM to 3PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
April | 22 | 3PM to 4PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
April | 22 | 4PM to 5PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
April | 22 | 5PM to 6PM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
April | 22 | 6PM to 7PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
April | 22 | 7PM to 8PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
April | 22 | 8PM to 9PM | 72 | 65.4 | 62.1 | 83.6 | 30.33 | 0.0741 | 0.56 | 13.66 | 0
April | 22 | 9PM to 10PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
April | 22 | 10PM to 11PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 22 | 11PM to 12AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
April | 23 | 12AM to 1AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
April | 23 | 1AM to 2AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 23 | 2AM to 3AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
April | 23 | 3AM to 4AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
April | 23 | 4AM to 5AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
April | 23 | 5AM to 6AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
April | 23 | 6AM to 7AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
April | 23 | 7AM to 8AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
April | 23 | 8AM to 9AM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
April | 23 | 9AM to 10AM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
April | 23 | 10AM to 11AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
April | 23 | 11AM to 12PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
April | 23 | 12PM to 1PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
April | 23 | 1PM to 2PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
April | 23 | 2PM to 3PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
April | 23 | 3PM to 4PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
April | 23 | 4PM to 5PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
April | 23 | 5PM to 6PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
April | 23 | 6PM to 7PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
April | 23 | 7PM to 8PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
April | 23 | 8PM to 9PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
April | 23 | 9PM to 10PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
April | 23 | 10PM to 11PM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
April | 23 | 11PM to 12AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
April | 24 | 12AM to 1AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
April | 24 | 1AM to 2AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
April | 24 | 2AM to 3AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
April | 24 | 3AM to 4AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
April | 24 | 4AM to 5AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
April | 24 | 5AM to 6AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
April | 24 | 6AM to 7AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
April | 24 | 7AM to 8AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
April | 24 | 8AM to 9AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
April | 24 | 9AM to 10AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
April | 24 | 10AM to 11AM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
April | 24 | 11AM to 12PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
April | 24 | 12PM to 1PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
April | 24 | 1PM to 2PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
April | 24 | 2PM to 3PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
April | 24 | 3PM to 4PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
April | 24 | 4PM to 5PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
April | 24 | 5PM to 6PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
April | 24 | 6PM to 7PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
April | 24 | 7PM to 8PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
April | 24 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
April | 24 | 9PM to 10PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
April | 24 | 10PM to 11PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
April | 24 | 11PM to 12AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
April | 25 | 12AM to 1AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
April | 25 | 1AM to 2AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
April | 25 | 2AM to 3AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
April | 25 | 3AM to 4AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
April | 25 | 4AM to 5AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
April | 25 | 5AM to 6AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
April | 25 | 6AM to 7AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
April | 25 | 7AM to 8AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
April | 25 | 8AM to 9AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
April | 25 | 9AM to 10AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
April | 25 | 10AM to 11AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
April | 25 | 11AM to 12PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
April | 25 | 12PM to 1PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
April | 25 | 1PM to 2PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
April | 25 | 2PM to 3PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
April | 25 | 3PM to 4PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
April | 25 | 4PM to 5PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
April | 25 | 5PM to 6PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
April | 25 | 6PM to 7PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
April | 25 | 7PM to 8PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 25 | 8PM to 9PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
April | 25 | 9PM to 10PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
April | 25 | 10PM to 11PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
April | 25 | 11PM to 12AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 26 | 12AM to 1AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
April | 26 | 1AM to 2AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 26 | 2AM to 3AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
April | 26 | 3AM to 4AM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
April | 26 | 4AM to 5AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
April | 26 | 5AM to 6AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
April | 26 | 6AM to 7AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
April | 26 | 7AM to 8AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
April | 26 | 8AM to 9AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
April | 26 | 9AM to 10AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
April | 26 | 10AM to 11AM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
April | 26 | 11AM to 12PM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
April | 26 | 12PM to 1PM | 79 | 66.5 | 60.1 | 77.8 | 31.14 | 0.0732 | 0.52 | 13.82 | 0
April | 26 | 1PM to 2PM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
April | 26 | 2PM to 3PM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
April | 26 | 3PM to 4PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
April | 26 | 4PM to 5PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
April | 26 | 5PM to 6PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
April | 26 | 6PM to 7PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
April | 26 | 7PM to 8PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
April | 26 | 8PM to 9PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
April | 26 | 9PM to 10PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
April | 26 | 10PM to 11PM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
April | 26 | 11PM to 12AM | 69.1 | 63.3 | 60.1 | 77.8 | 28.72 | 0.0745 | 0.52 | 13.57 | 0
April | 27 | 12AM to 1AM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
April | 27 | 1AM to 2AM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
April | 27 | 2AM to 3AM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.53 | 0
April | 27 | 3AM to 4AM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.53 | 0
April | 27 | 4AM to 5AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
April | 27 | 5AM to 6AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
April | 27 | 6AM to 7AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
April | 27 | 7AM to 8AM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
April | 27 | 8AM to 9AM | 75 | 62.5 | 55 | 64.7 | 28.12 | 0.0738 | 0.44 | 13.68 | 0
April | 27 | 9AM to 10AM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
April | 27 | 10AM to 11AM | 78.1 | 63 | 54 | 62.2 | 28.47 | 0.0734 | 0.42 | 13.75 | 0
April | 27 | 11AM to 12PM | 78.1 | 63.6 | 55 | 64.7 | 28.87 | 0.0734 | 0.44 | 13.76 | 0
April | 27 | 12PM to 1PM | 79 | 63.3 | 54 | 62.2 | 28.69 | 0.0733 | 0.42 | 13.77 | 0
April | 27 | 1PM to 2PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
April | 27 | 2PM to 3PM | 77 | 62.2 | 53.1 | 60.1 | 27.89 | 0.0735 | 0.41 | 13.71 | 0
April | 27 | 3PM to 4PM | 77 | 61.7 | 52 | 57.8 | 27.52 | 0.0736 | 0.39 | 13.71 | 0
April | 27 | 4PM to 5PM | 75.9 | 61.8 | 53.1 | 60.1 | 27.63 | 0.0737 | 0.41 | 13.69 | 0
April | 27 | 5PM to 6PM | 73 | 60.8 | 53.1 | 60.1 | 26.93 | 0.0741 | 0.41 | 13.61 | 0
April | 27 | 6PM to 7PM | 72 | 60.4 | 53.1 | 60.1 | 26.66 | 0.0742 | 0.41 | 13.59 | 0
April | 27 | 7PM to 8PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
April | 27 | 8PM to 9PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
April | 27 | 9PM to 10PM | 70 | 61.8 | 57 | 69.6 | 27.66 | 0.0745 | 0.47 | 13.56 | 0
April | 27 | 10PM to 11PM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
April | 27 | 11PM to 12AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
April | 28 | 12AM to 1AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
April | 28 | 1AM to 2AM | 69.1 | 62 | 57.9 | 72 | 27.8 | 0.0746 | 0.48 | 13.55 | 0
April | 28 | 2AM to 3AM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.53 | 0
April | 28 | 3AM to 4AM | 68 | 62.2 | 59 | 74.9 | 27.99 | 0.0747 | 0.5 | 13.53 | 0
April | 28 | 4AM to 5AM | 66.9 | 61.2 | 57.9 | 72 | 27.27 | 0.0749 | 0.48 | 13.49 | 0
April | 28 | 5AM to 6AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
April | 28 | 6AM to 7AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
April | 28 | 7AM to 8AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
April | 28 | 8AM to 9AM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
April | 28 | 9AM to 10AM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
April | 28 | 10AM to 11AM | 78.1 | 64.6 | 57 | 69.6 | 29.64 | 0.0733 | 0.47 | 13.77 | 0
April | 28 | 11AM to 12PM | 78.1 | 64 | 55.9 | 66.9 | 29.21 | 0.0734 | 0.45 | 13.76 | 0
April | 28 | 12PM to 1PM | 79 | 64.3 | 55.9 | 66.9 | 29.43 | 0.0732 | 0.45 | 13.79 | 0
April | 28 | 1PM to 2PM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
April | 28 | 2PM to 3PM | 77 | 63.2 | 55 | 64.7 | 28.61 | 0.0735 | 0.44 | 13.73 | 0
April | 28 | 3PM to 4PM | 77 | 63.2 | 55 | 64.7 | 28.61 | 0.0735 | 0.44 | 13.73 | 0
April | 28 | 4PM to 5PM | 75 | 63 | 55.9 | 66.9 | 28.47 | 0.0738 | 0.45 | 13.68 | 0
April | 28 | 5PM to 6PM | 73 | 61.8 | 55 | 64.7 | 27.64 | 0.0741 | 0.44 | 13.63 | 0
April | 28 | 6PM to 7PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
April | 28 | 7PM to 8PM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
April | 28 | 8PM to 9PM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
April | 28 | 9PM to 10PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
April | 28 | 10PM to 11PM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
April | 28 | 11PM to 12AM | 69.1 | 60.4 | 55 | 64.7 | 26.67 | 0.0746 | 0.44 | 13.53 | 0
April | 29 | 12AM to 1AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
April | 29 | 1AM to 2AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
April | 29 | 2AM to 3AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
April | 29 | 3AM to 4AM | 68 | 61.1 | 57 | 69.6 | 27.17 | 0.0747 | 0.47 | 13.51 | 0
April | 29 | 4AM to 5AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
April | 29 | 5AM to 6AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
April | 29 | 6AM to 7AM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
April | 29 | 7AM to 8AM | 73.9 | 63.2 | 57 | 69.6 | 28.63 | 0.0739 | 0.47 | 13.67 | 0
April | 29 | 8AM to 9AM | 75 | 63 | 55.9 | 66.9 | 28.47 | 0.0738 | 0.45 | 13.68 | 0
April | 29 | 9AM to 10AM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
April | 29 | 10AM to 11AM | 78.1 | 64 | 55.9 | 66.9 | 29.21 | 0.0734 | 0.45 | 13.76 | 0
April | 29 | 11AM to 12PM | 81 | 65.5 | 57 | 69.6 | 30.34 | 0.0729 | 0.47 | 13.84 | 0
April | 29 | 12PM to 1PM | 81 | 64.5 | 55 | 64.7 | 29.57 | 0.073 | 0.44 | 13.83 | 0
April | 29 | 1PM to 2PM | 82 | 64.9 | 55 | 64.7 | 29.84 | 0.0728 | 0.44 | 13.86 | 0
April | 29 | 2PM to 3PM | 81 | 64.5 | 55 | 64.7 | 29.57 | 0.073 | 0.44 | 13.83 | 0
April | 29 | 3PM to 4PM | 79 | 64.3 | 55.9 | 66.9 | 29.43 | 0.0732 | 0.45 | 13.79 | 0
April | 29 | 4PM to 5PM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
April | 29 | 5PM to 6PM | 75 | 63 | 55.9 | 66.9 | 28.47 | 0.0738 | 0.45 | 13.68 | 0
April | 29 | 6PM to 7PM | 73 | 62.3 | 55.9 | 66.9 | 27.98 | 0.074 | 0.45 | 13.63 | 0
April | 29 | 7PM to 8PM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
April | 29 | 8PM to 9PM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
April | 29 | 9PM to 10PM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
April | 29 | 10PM to 11PM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
April | 29 | 11PM to 12AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
April | 30 | 12AM to 1AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
April | 30 | 1AM to 2AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
April | 30 | 2AM to 3AM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
April | 30 | 3AM to 4AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
April | 30 | 4AM to 5AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
April | 30 | 5AM to 6AM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
April | 30 | 6AM to 7AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
April | 30 | 7AM to 8AM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
April | 30 | 8AM to 9AM | 78.1 | 64.6 | 57 | 69.6 | 29.64 | 0.0733 | 0.47 | 13.77 | 0
April | 30 | 9AM to 10AM | 81 | 65 | 55.9 | 66.9 | 29.92 | 0.073 | 0.45 | 13.84 | 0
April | 30 | 10AM to 11AM | 82 | 65.3 | 55.9 | 66.9 | 30.18 | 0.0728 | 0.45 | 13.86 | 0
April | 30 | 11AM to 12PM | 82 | 65.3 | 55.9 | 66.9 | 30.18 | 0.0728 | 0.45 | 13.86 | 0
April | 30 | 12PM to 1PM | 82.9 | 65.6 | 55.9 | 66.9 | 30.4 | 0.0727 | 0.45 | 13.89 | 0
April | 30 | 1PM to 2PM | 82 | 65.3 | 55.9 | 66.9 | 30.18 | 0.0728 | 0.45 | 13.86 | 0
April | 30 | 2PM to 3PM | 82 | 65.3 | 55.9 | 66.9 | 30.18 | 0.0728 | 0.45 | 13.86 | 0
April | 30 | 3PM to 4PM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
April | 30 | 4PM to 5PM | 79 | 64.9 | 57 | 69.6 | 29.86 | 0.0732 | 0.47 | 13.79 | 0
April | 30 | 5PM to 6PM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
April | 30 | 6PM to 7PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
April | 30 | 7PM to 8PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
April | 30 | 8PM to 9PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
April | 30 | 9PM to 10PM | 72.7 | 65.6 | 62.1 | 83.6 | 30.5 | 0.074 | 0.56 | 13.68 | 0
April | 30 | 10PM to 11PM | 72.1 | 65.5 | 62.1 | 83.6 | 30.37 | 0.0741 | 0.56 | 13.66 | 0
April | 30 | 11PM to 12AM | 71.8 | 65.4 | 62.1 | 83.6 | 30.28 | 0.0741 | 0.56 | 13.65 | 0
May | 1 | 12AM to 1AM | 71.2 | 65.2 | 62.1 | 83.6 | 30.15 | 0.0742 | 0.56 | 13.64 | 0
May | 1 | 1AM to 2AM | 70.9 | 65.1 | 62.1 | 83.6 | 30.06 | 0.0742 | 0.56 | 13.63 | 0
May | 1 | 2AM to 3AM | 70.3 | 64.9 | 62.1 | 83.6 | 29.93 | 0.0743 | 0.56 | 13.62 | 0
May | 1 | 3AM to 4AM | 70 | 64.8 | 62.1 | 83.6 | 29.84 | 0.0744 | 0.56 | 13.61 | 0
May | 1 | 4AM to 5AM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
May | 1 | 5AM to 6AM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
May | 1 | 6AM to 7AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
May | 1 | 7AM to 8AM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
May | 1 | 8AM to 9AM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
May | 1 | 9AM to 10AM | 81 | 68.3 | 62.1 | 83.6 | 32.53 | 0.0729 | 0.56 | 13.89 | 0
May | 1 | 10AM to 11AM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
May | 1 | 11AM to 12PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
May | 1 | 12PM to 1PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
May | 1 | 1PM to 2PM | 82.9 | 67.2 | 59 | 74.9 | 31.64 | 0.0726 | 0.5 | 13.91 | 0
May | 1 | 2PM to 3PM | 84 | 67.5 | 59 | 74.9 | 31.91 | 0.0725 | 0.5 | 13.94 | 0
May | 1 | 3PM to 4PM | 82.9 | 66.6 | 57.9 | 72 | 31.19 | 0.0727 | 0.48 | 13.9 | 0
May | 1 | 4PM to 5PM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
May | 1 | 5PM to 6PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
May | 1 | 6PM to 7PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
May | 1 | 7PM to 8PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
May | 1 | 8PM to 9PM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
May | 1 | 9PM to 10PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
May | 1 | 10PM to 11PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
May | 1 | 11PM to 12AM | 71.1 | 62.7 | 57.9 | 72 | 28.29 | 0.0743 | 0.48 | 13.6 | 0
May | 2 | 12AM to 1AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
May | 2 | 1AM to 2AM | 71.1 | 63.3 | 59 | 74.9 | 28.74 | 0.0743 | 0.5 | 13.61 | 0
May | 2 | 2AM to 3AM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
May | 2 | 3AM to 4AM | 68 | 62.9 | 60.1 | 77.8 | 28.45 | 0.0747 | 0.52 | 13.54 | 0
May | 2 | 4AM to 5AM | 68 | 63.4 | 61 | 80.4 | 28.86 | 0.0747 | 0.54 | 13.55 | 0
May | 2 | 5AM to 6AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
May | 2 | 6AM to 7AM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
May | 2 | 7AM to 8AM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
May | 2 | 8AM to 9AM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
May | 2 | 9AM to 10AM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
May | 2 | 10AM to 11AM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
May | 2 | 11AM to 12PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
May | 2 | 12PM to 1PM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
May | 2 | 1PM to 2PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
May | 2 | 2PM to 3PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
May | 2 | 3PM to 4PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
May | 2 | 4PM to 5PM | 81 | 68.3 | 62.1 | 83.6 | 32.53 | 0.0729 | 0.56 | 13.89 | 0
May | 2 | 5PM to 6PM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
May | 2 | 6PM to 7PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
May | 2 | 7PM to 8PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 2 | 8PM to 9PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 2 | 9PM to 10PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
May | 2 | 10PM to 11PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 2 | 11PM to 12AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 3 | 12AM to 1AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 3 | 1AM to 2AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
May | 3 | 2AM to 3AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 3 | 3AM to 4AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
May | 3 | 4AM to 5AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 3 | 5AM to 6AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 3 | 6AM to 7AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
May | 3 | 7AM to 8AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
May | 3 | 8AM to 9AM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
May | 3 | 9AM to 10AM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
May | 3 | 10AM to 11AM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 3 | 11AM to 12PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 3 | 12PM to 1PM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
May | 3 | 1PM to 2PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 3 | 2PM to 3PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
May | 3 | 3PM to 4PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
May | 3 | 4PM to 5PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 3 | 5PM to 6PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
May | 3 | 6PM to 7PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 3 | 7PM to 8PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
May | 3 | 8PM to 9PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
May | 3 | 9PM to 10PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
May | 3 | 10PM to 11PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
May | 3 | 11PM to 12AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
May | 4 | 12AM to 1AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
May | 4 | 1AM to 2AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
May | 4 | 2AM to 3AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
May | 4 | 3AM to 4AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
May | 4 | 4AM to 5AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
May | 4 | 5AM to 6AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
May | 4 | 6AM to 7AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
May | 4 | 7AM to 8AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
May | 4 | 8AM to 9AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
May | 4 | 9AM to 10AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
May | 4 | 10AM to 11AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
May | 4 | 11AM to 12PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
May | 4 | 12PM to 1PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
May | 4 | 1PM to 2PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
May | 4 | 2PM to 3PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
May | 4 | 3PM to 4PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
May | 4 | 4PM to 5PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
May | 4 | 5PM to 6PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
May | 4 | 6PM to 7PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 4 | 7PM to 8PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 4 | 8PM to 9PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 4 | 9PM to 10PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 4 | 10PM to 11PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 4 | 11PM to 12AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
May | 5 | 12AM to 1AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
May | 5 | 1AM to 2AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 5 | 2AM to 3AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 5 | 3AM to 4AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 5 | 4AM to 5AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
May | 5 | 5AM to 6AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
May | 5 | 6AM to 7AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 5 | 7AM to 8AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 5 | 8AM to 9AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 5 | 9AM to 10AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 5 | 10AM to 11AM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
May | 5 | 11AM to 12PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
May | 5 | 12PM to 1PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
May | 5 | 1PM to 2PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
May | 5 | 2PM to 3PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
May | 5 | 3PM to 4PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
May | 5 | 4PM to 5PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
May | 5 | 5PM to 6PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 5 | 6PM to 7PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 5 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 5 | 8PM to 9PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 5 | 9PM to 10PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
May | 5 | 10PM to 11PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
May | 5 | 11PM to 12AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
May | 6 | 12AM to 1AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
May | 6 | 1AM to 2AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 6 | 2AM to 3AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 6 | 3AM to 4AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 6 | 4AM to 5AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 6 | 5AM to 6AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 6 | 6AM to 7AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 6 | 7AM to 8AM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
May | 6 | 8AM to 9AM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
May | 6 | 9AM to 10AM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 6 | 10AM to 11AM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
May | 6 | 11AM to 12PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
May | 6 | 12PM to 1PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
May | 6 | 1PM to 2PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
May | 6 | 2PM to 3PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
May | 6 | 3PM to 4PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
May | 6 | 4PM to 5PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
May | 6 | 5PM to 6PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 6 | 6PM to 7PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 6 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 6 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 6 | 9PM to 10PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 6 | 10PM to 11PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 6 | 11PM to 12AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 7 | 12AM to 1AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 7 | 1AM to 2AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 7 | 2AM to 3AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 7 | 3AM to 4AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 7 | 4AM to 5AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
May | 7 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
May | 7 | 6AM to 7AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 7 | 7AM to 8AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
May | 7 | 8AM to 9AM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
May | 7 | 9AM to 10AM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
May | 7 | 10AM to 11AM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
May | 7 | 11AM to 12PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
May | 7 | 12PM to 1PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
May | 7 | 1PM to 2PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
May | 7 | 2PM to 3PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
May | 7 | 3PM to 4PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 7 | 4PM to 5PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 7 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
May | 7 | 6PM to 7PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
May | 7 | 7PM to 8PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
May | 7 | 8PM to 9PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 7 | 9PM to 10PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 7 | 10PM to 11PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
May | 7 | 11PM to 12AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
May | 8 | 12AM to 1AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
May | 8 | 1AM to 2AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
May | 8 | 2AM to 3AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
May | 8 | 3AM to 4AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
May | 8 | 4AM to 5AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
May | 8 | 5AM to 6AM | 68 | 66.7 | 66 | 96.3 | 31.34 | 0.0746 | 0.64 | 13.59 | 0
May | 8 | 6AM to 7AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
May | 8 | 7AM to 8AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
May | 8 | 8AM to 9AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
May | 8 | 9AM to 10AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
May | 8 | 10AM to 11AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
May | 8 | 11AM to 12PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
May | 8 | 12PM to 1PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
May | 8 | 1PM to 2PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
May | 8 | 2PM to 3PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
May | 8 | 3PM to 4PM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
May | 8 | 4PM to 5PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
May | 8 | 5PM to 6PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
May | 8 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
May | 8 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
May | 8 | 8PM to 9PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
May | 8 | 9PM to 10PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
May | 8 | 10PM to 11PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
May | 8 | 11PM to 12AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 9 | 12AM to 1AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
May | 9 | 1AM to 2AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
May | 9 | 2AM to 3AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
May | 9 | 3AM to 4AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
May | 9 | 4AM to 5AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
May | 9 | 5AM to 6AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
May | 9 | 6AM to 7AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
May | 9 | 7AM to 8AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
May | 9 | 8AM to 9AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
May | 9 | 9AM to 10AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
May | 9 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
May | 9 | 11AM to 12PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
May | 9 | 12PM to 1PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
May | 9 | 1PM to 2PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
May | 9 | 2PM to 3PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
May | 9 | 3PM to 4PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
May | 9 | 4PM to 5PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
May | 9 | 5PM to 6PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
May | 9 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
May | 9 | 7PM to 8PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
May | 9 | 8PM to 9PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
May | 9 | 9PM to 10PM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
May | 9 | 10PM to 11PM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
May | 9 | 11PM to 12AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
May | 10 | 12AM to 1AM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
May | 10 | 1AM to 2AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
May | 10 | 2AM to 3AM | 73 | 71.6 | 71.1 | 115 | 35.5 | 0.0738 | 0.77 | 13.78 | 0
May | 10 | 3AM to 4AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
May | 10 | 4AM to 5AM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
May | 10 | 5AM to 6AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
May | 10 | 6AM to 7AM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
May | 10 | 7AM to 8AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
May | 10 | 8AM to 9AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
May | 10 | 9AM to 10AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
May | 10 | 10AM to 11AM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
May | 10 | 11AM to 12PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
May | 10 | 12PM to 1PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
May | 10 | 1PM to 2PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
May | 10 | 2PM to 3PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
May | 10 | 3PM to 4PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
May | 10 | 4PM to 5PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
May | 10 | 5PM to 6PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
May | 10 | 6PM to 7PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
May | 10 | 7PM to 8PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
May | 10 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
May | 10 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
May | 10 | 10PM to 11PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 10 | 11PM to 12AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
May | 11 | 12AM to 1AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
May | 11 | 1AM to 2AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 11 | 2AM to 3AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
May | 11 | 3AM to 4AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 11 | 4AM to 5AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 11 | 5AM to 6AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 11 | 6AM to 7AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 11 | 7AM to 8AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 11 | 8AM to 9AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
May | 11 | 9AM to 10AM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
May | 11 | 10AM to 11AM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
May | 11 | 11AM to 12PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
May | 11 | 12PM to 1PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
May | 11 | 1PM to 2PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
May | 11 | 2PM to 3PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
May | 11 | 3PM to 4PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 11 | 4PM to 5PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
May | 11 | 5PM to 6PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
May | 11 | 6PM to 7PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 11 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 11 | 8PM to 9PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 11 | 9PM to 10PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 11 | 10PM to 11PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 11 | 11PM to 12AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 12 | 12AM to 1AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 12 | 1AM to 2AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 12 | 2AM to 3AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 12 | 3AM to 4AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 12 | 4AM to 5AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 12 | 5AM to 6AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 12 | 6AM to 7AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 12 | 7AM to 8AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
May | 12 | 8AM to 9AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 12 | 9AM to 10AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
May | 12 | 10AM to 11AM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
May | 12 | 11AM to 12PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
May | 12 | 12PM to 1PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 12 | 1PM to 2PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
May | 12 | 2PM to 3PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 12 | 3PM to 4PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
May | 12 | 4PM to 5PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
May | 12 | 5PM to 6PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
May | 12 | 6PM to 7PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
May | 12 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 12 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 12 | 9PM to 10PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 12 | 10PM to 11PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 12 | 11PM to 12AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 13 | 12AM to 1AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 13 | 1AM to 2AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
May | 13 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
May | 13 | 3AM to 4AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
May | 13 | 4AM to 5AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
May | 13 | 5AM to 6AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
May | 13 | 6AM to 7AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 13 | 7AM to 8AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
May | 13 | 8AM to 9AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
May | 13 | 9AM to 10AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
May | 13 | 10AM to 11AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
May | 13 | 11AM to 12PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
May | 13 | 12PM to 1PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
May | 13 | 1PM to 2PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
May | 13 | 2PM to 3PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
May | 13 | 3PM to 4PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
May | 13 | 4PM to 5PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
May | 13 | 5PM to 6PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
May | 13 | 6PM to 7PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
May | 13 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 13 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 13 | 9PM to 10PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 13 | 10PM to 11PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 13 | 11PM to 12AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 14 | 12AM to 1AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 14 | 1AM to 2AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 14 | 2AM to 3AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 14 | 3AM to 4AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 14 | 4AM to 5AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 14 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
May | 14 | 6AM to 7AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
May | 14 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
May | 14 | 8AM to 9AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
May | 14 | 9AM to 10AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
May | 14 | 10AM to 11AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
May | 14 | 11AM to 12PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
May | 14 | 12PM to 1PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
May | 14 | 1PM to 2PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
May | 14 | 2PM to 3PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
May | 14 | 3PM to 4PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
May | 14 | 4PM to 5PM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
May | 14 | 5PM to 6PM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
May | 14 | 6PM to 7PM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
May | 14 | 7PM to 8PM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
May | 14 | 8PM to 9PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
May | 14 | 9PM to 10PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
May | 14 | 10PM to 11PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
May | 14 | 11PM to 12AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
May | 15 | 12AM to 1AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
May | 15 | 1AM to 2AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
May | 15 | 2AM to 3AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
May | 15 | 3AM to 4AM | 69.1 | 67.6 | 66.9 | 99.5 | 32.09 | 0.0744 | 0.67 | 13.63 | 0
May | 15 | 4AM to 5AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
May | 15 | 5AM to 6AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
May | 15 | 6AM to 7AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
May | 15 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
May | 15 | 8AM to 9AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
May | 15 | 9AM to 10AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
May | 15 | 10AM to 11AM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
May | 15 | 11AM to 12PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
May | 15 | 12PM to 1PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
May | 15 | 1PM to 2PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
May | 15 | 2PM to 3PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
May | 15 | 3PM to 4PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
May | 15 | 4PM to 5PM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
May | 15 | 5PM to 6PM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
May | 15 | 6PM to 7PM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
May | 15 | 7PM to 8PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
May | 15 | 8PM to 9PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
May | 15 | 9PM to 10PM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
May | 15 | 10PM to 11PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
May | 15 | 11PM to 12AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
May | 16 | 12AM to 1AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 16 | 1AM to 2AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 16 | 2AM to 3AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
May | 16 | 3AM to 4AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
May | 16 | 4AM to 5AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
May | 16 | 5AM to 6AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
May | 16 | 6AM to 7AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
May | 16 | 7AM to 8AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
May | 16 | 8AM to 9AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
May | 16 | 9AM to 10AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
May | 16 | 10AM to 11AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
May | 16 | 11AM to 12PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
May | 16 | 12PM to 1PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
May | 16 | 1PM to 2PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
May | 16 | 2PM to 3PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
May | 16 | 3PM to 4PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
May | 16 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
May | 16 | 5PM to 6PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 16 | 6PM to 7PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
May | 16 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 16 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 16 | 9PM to 10PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 16 | 10PM to 11PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
May | 16 | 11PM to 12AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 17 | 12AM to 1AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
May | 17 | 1AM to 2AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 17 | 2AM to 3AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 17 | 3AM to 4AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 17 | 4AM to 5AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 17 | 5AM to 6AM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
May | 17 | 6AM to 7AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
May | 17 | 7AM to 8AM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
May | 17 | 8AM to 9AM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 17 | 9AM to 10AM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
May | 17 | 10AM to 11AM | 86 | 69.8 | 62.1 | 83.6 | 33.77 | 0.0722 | 0.56 | 14.02 | 0
May | 17 | 11AM to 12PM | 87.1 | 70.1 | 62.1 | 83.6 | 34.04 | 0.072 | 0.56 | 14.05 | 0
May | 17 | 12PM to 1PM | 88 | 70.4 | 62.1 | 83.6 | 34.26 | 0.0719 | 0.56 | 14.07 | 0
May | 17 | 1PM to 2PM | 88 | 70.4 | 62.1 | 83.6 | 34.26 | 0.0719 | 0.56 | 14.07 | 0
May | 17 | 2PM to 3PM | 87.1 | 70.6 | 63 | 86.4 | 34.47 | 0.072 | 0.58 | 14.05 | 0
May | 17 | 3PM to 4PM | 84.9 | 68.4 | 60.1 | 77.8 | 32.6 | 0.0724 | 0.52 | 13.97 | 0
May | 17 | 4PM to 5PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 17 | 5PM to 6PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
May | 17 | 6PM to 7PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
May | 17 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 17 | 8PM to 9PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 17 | 9PM to 10PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
May | 17 | 10PM to 11PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
May | 17 | 11PM to 12AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 18 | 12AM to 1AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
May | 18 | 1AM to 2AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 18 | 2AM to 3AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 18 | 3AM to 4AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 18 | 4AM to 5AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
May | 18 | 5AM to 6AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 18 | 6AM to 7AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
May | 18 | 7AM to 8AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
May | 18 | 8AM to 9AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
May | 18 | 9AM to 10AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
May | 18 | 10AM to 11AM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
May | 18 | 11AM to 12PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
May | 18 | 12PM to 1PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
May | 18 | 1PM to 2PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
May | 18 | 2PM to 3PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
May | 18 | 3PM to 4PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
May | 18 | 4PM to 5PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
May | 18 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
May | 18 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
May | 18 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 18 | 8PM to 9PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
May | 18 | 9PM to 10PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
May | 18 | 10PM to 11PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
May | 18 | 11PM to 12AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
May | 19 | 12AM to 1AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
May | 19 | 1AM to 2AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
May | 19 | 2AM to 3AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 19 | 3AM to 4AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 19 | 4AM to 5AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 19 | 5AM to 6AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 19 | 6AM to 7AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 19 | 7AM to 8AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 19 | 8AM to 9AM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
May | 19 | 9AM to 10AM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
May | 19 | 10AM to 11AM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
May | 19 | 11AM to 12PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
May | 19 | 12PM to 1PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
May | 19 | 1PM to 2PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
May | 19 | 2PM to 3PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
May | 19 | 3PM to 4PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
May | 19 | 4PM to 5PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
May | 19 | 5PM to 6PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
May | 19 | 6PM to 7PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
May | 19 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 19 | 8PM to 9PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
May | 19 | 9PM to 10PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
May | 19 | 10PM to 11PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
May | 19 | 11PM to 12AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
May | 20 | 12AM to 1AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
May | 20 | 1AM to 2AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 20 | 2AM to 3AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 20 | 3AM to 4AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 20 | 4AM to 5AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
May | 20 | 5AM to 6AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
May | 20 | 6AM to 7AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
May | 20 | 7AM to 8AM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
May | 20 | 8AM to 9AM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
May | 20 | 9AM to 10AM | 82 | 66.3 | 57.9 | 72 | 30.97 | 0.0728 | 0.48 | 13.88 | 0
May | 20 | 10AM to 11AM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
May | 20 | 11AM to 12PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
May | 20 | 12PM to 1PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
May | 20 | 1PM to 2PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
May | 20 | 2PM to 3PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
May | 20 | 3PM to 4PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
May | 20 | 4PM to 5PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
May | 20 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
May | 20 | 6PM to 7PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
May | 20 | 7PM to 8PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
May | 20 | 8PM to 9PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 20 | 9PM to 10PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
May | 20 | 10PM to 11PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 20 | 11PM to 12AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
May | 21 | 12AM to 1AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
May | 21 | 1AM to 2AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
May | 21 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
May | 21 | 3AM to 4AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
May | 21 | 4AM to 5AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
May | 21 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
May | 21 | 6AM to 7AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
May | 21 | 7AM to 8AM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
May | 21 | 8AM to 9AM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
May | 21 | 9AM to 10AM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
May | 21 | 10AM to 11AM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 21 | 11AM to 12PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
May | 21 | 12PM to 1PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
May | 21 | 1PM to 2PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
May | 21 | 2PM to 3PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
May | 21 | 3PM to 4PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 21 | 4PM to 5PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 21 | 5PM to 6PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
May | 21 | 6PM to 7PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
May | 21 | 7PM to 8PM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
May | 21 | 8PM to 9PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 21 | 9PM to 10PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 21 | 10PM to 11PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
May | 21 | 11PM to 12AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
May | 22 | 12AM to 1AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
May | 22 | 1AM to 2AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
May | 22 | 2AM to 3AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
May | 22 | 3AM to 4AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
May | 22 | 4AM to 5AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
May | 22 | 5AM to 6AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
May | 22 | 6AM to 7AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
May | 22 | 7AM to 8AM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
May | 22 | 8AM to 9AM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
May | 22 | 9AM to 10AM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
May | 22 | 10AM to 11AM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
May | 22 | 11AM to 12PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
May | 22 | 12PM to 1PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
May | 22 | 1PM to 2PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
May | 22 | 2PM to 3PM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
May | 22 | 3PM to 4PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
May | 22 | 4PM to 5PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
May | 22 | 5PM to 6PM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
May | 22 | 6PM to 7PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
May | 22 | 7PM to 8PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
May | 22 | 8PM to 9PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 22 | 9PM to 10PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 22 | 10PM to 11PM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
May | 22 | 11PM to 12AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
May | 23 | 12AM to 1AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
May | 23 | 1AM to 2AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
May | 23 | 2AM to 3AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
May | 23 | 3AM to 4AM | 66.9 | 63.1 | 61 | 80.4 | 28.59 | 0.0748 | 0.54 | 13.52 | 0
May | 23 | 4AM to 5AM | 66.9 | 63.1 | 61 | 80.4 | 28.59 | 0.0748 | 0.54 | 13.52 | 0
May | 23 | 5AM to 6AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
May | 23 | 6AM to 7AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 23 | 7AM to 8AM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
May | 23 | 8AM to 9AM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
May | 23 | 9AM to 10AM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
May | 23 | 10AM to 11AM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
May | 23 | 11AM to 12PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
May | 23 | 12PM to 1PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
May | 23 | 1PM to 2PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
May | 23 | 2PM to 3PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
May | 23 | 3PM to 4PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
May | 23 | 4PM to 5PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
May | 23 | 5PM to 6PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
May | 23 | 6PM to 7PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
May | 23 | 7PM to 8PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
May | 23 | 8PM to 9PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 23 | 9PM to 10PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 23 | 10PM to 11PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 23 | 11PM to 12AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 24 | 12AM to 1AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
May | 24 | 1AM to 2AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
May | 24 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
May | 24 | 3AM to 4AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
May | 24 | 4AM to 5AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
May | 24 | 5AM to 6AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
May | 24 | 6AM to 7AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 24 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
May | 24 | 8AM to 9AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
May | 24 | 9AM to 10AM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
May | 24 | 10AM to 11AM | 88 | 67.8 | 57 | 69.6 | 32.06 | 0.072 | 0.47 | 14.02 | 0
May | 24 | 11AM to 12PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
May | 24 | 12PM to 1PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
May | 24 | 1PM to 2PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
May | 24 | 2PM to 3PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
May | 24 | 3PM to 4PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
May | 24 | 4PM to 5PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
May | 24 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 24 | 6PM to 7PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
May | 24 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
May | 24 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
May | 24 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
May | 24 | 10PM to 11PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
May | 24 | 11PM to 12AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 25 | 12AM to 1AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 25 | 1AM to 2AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
May | 25 | 2AM to 3AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
May | 25 | 3AM to 4AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
May | 25 | 4AM to 5AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
May | 25 | 5AM to 6AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
May | 25 | 6AM to 7AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 25 | 7AM to 8AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
May | 25 | 8AM to 9AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 25 | 9AM to 10AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
May | 25 | 10AM to 11AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
May | 25 | 11AM to 12PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
May | 25 | 12PM to 1PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
May | 25 | 1PM to 2PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
May | 25 | 2PM to 3PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
May | 25 | 3PM to 4PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
May | 25 | 4PM to 5PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 25 | 5PM to 6PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 25 | 6PM to 7PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
May | 25 | 7PM to 8PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 25 | 8PM to 9PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 25 | 9PM to 10PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 25 | 10PM to 11PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
May | 25 | 11PM to 12AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 26 | 12AM to 1AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
May | 26 | 1AM to 2AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 26 | 2AM to 3AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 26 | 3AM to 4AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 26 | 4AM to 5AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
May | 26 | 5AM to 6AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
May | 26 | 6AM to 7AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 26 | 7AM to 8AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
May | 26 | 8AM to 9AM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
May | 26 | 9AM to 10AM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
May | 26 | 10AM to 11AM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
May | 26 | 11AM to 12PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
May | 26 | 12PM to 1PM | 87.1 | 70.1 | 62.1 | 83.6 | 34.04 | 0.072 | 0.56 | 14.05 | 0
May | 26 | 1PM to 2PM | 86 | 69.2 | 61 | 80.4 | 33.27 | 0.0722 | 0.54 | 14.01 | 0
May | 26 | 2PM to 3PM | 84.9 | 69.5 | 62.1 | 83.6 | 33.51 | 0.0723 | 0.56 | 13.99 | 0
May | 26 | 3PM to 4PM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
May | 26 | 4PM to 5PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
May | 26 | 5PM to 6PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
May | 26 | 6PM to 7PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
May | 26 | 7PM to 8PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
May | 26 | 8PM to 9PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 26 | 9PM to 10PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
May | 26 | 10PM to 11PM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
May | 26 | 11PM to 12AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 27 | 12AM to 1AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
May | 27 | 1AM to 2AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 27 | 2AM to 3AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
May | 27 | 3AM to 4AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
May | 27 | 4AM to 5AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
May | 27 | 5AM to 6AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
May | 27 | 6AM to 7AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 27 | 7AM to 8AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
May | 27 | 8AM to 9AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 27 | 9AM to 10AM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
May | 27 | 10AM to 11AM | 84 | 68.1 | 60.1 | 77.8 | 32.38 | 0.0725 | 0.52 | 13.95 | 0
May | 27 | 11AM to 12PM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
May | 27 | 12PM to 1PM | 87.1 | 69.5 | 61 | 80.4 | 33.53 | 0.0721 | 0.54 | 14.04 | 0
May | 27 | 1PM to 2PM | 86 | 69.2 | 61 | 80.4 | 33.27 | 0.0722 | 0.54 | 14.01 | 0
May | 27 | 2PM to 3PM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
May | 27 | 3PM to 4PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
May | 27 | 4PM to 5PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
May | 27 | 5PM to 6PM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
May | 27 | 6PM to 7PM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
May | 27 | 7PM to 8PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
May | 27 | 8PM to 9PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
May | 27 | 9PM to 10PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
May | 27 | 10PM to 11PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
May | 27 | 11PM to 12AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
May | 28 | 12AM to 1AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
May | 28 | 1AM to 2AM | 69.1 | 63.8 | 61 | 80.4 | 29.12 | 0.0745 | 0.54 | 13.57 | 0
May | 28 | 2AM to 3AM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
May | 28 | 3AM to 4AM | 68 | 64.1 | 62.1 | 83.6 | 29.35 | 0.0747 | 0.56 | 13.56 | 0
May | 28 | 4AM to 5AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
May | 28 | 5AM to 6AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
May | 28 | 6AM to 7AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
May | 28 | 7AM to 8AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
May | 28 | 8AM to 9AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
May | 28 | 9AM to 10AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
May | 28 | 10AM to 11AM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
May | 28 | 11AM to 12PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 28 | 12PM to 1PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
May | 28 | 1PM to 2PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
May | 28 | 2PM to 3PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
May | 28 | 3PM to 4PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
May | 28 | 4PM to 5PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
May | 28 | 5PM to 6PM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
May | 28 | 6PM to 7PM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
May | 28 | 7PM to 8PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
May | 28 | 8PM to 9PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
May | 28 | 9PM to 10PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
May | 28 | 10PM to 11PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
May | 28 | 11PM to 12AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
May | 29 | 12AM to 1AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 29 | 1AM to 2AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
May | 29 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
May | 29 | 3AM to 4AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
May | 29 | 4AM to 5AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
May | 29 | 5AM to 6AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
May | 29 | 6AM to 7AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
May | 29 | 7AM to 8AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
May | 29 | 8AM to 9AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
May | 29 | 9AM to 10AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
May | 29 | 10AM to 11AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
May | 29 | 11AM to 12PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
May | 29 | 12PM to 1PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
May | 29 | 1PM to 2PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
May | 29 | 2PM to 3PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 29 | 3PM to 4PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
May | 29 | 4PM to 5PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
May | 29 | 5PM to 6PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
May | 29 | 6PM to 7PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
May | 29 | 7PM to 8PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
May | 29 | 8PM to 9PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
May | 29 | 9PM to 10PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
May | 29 | 10PM to 11PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
May | 29 | 11PM to 12AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
May | 30 | 12AM to 1AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
May | 30 | 1AM to 2AM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
May | 30 | 2AM to 3AM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
May | 30 | 3AM to 4AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
May | 30 | 4AM to 5AM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
May | 30 | 5AM to 6AM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
May | 30 | 6AM to 7AM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
May | 30 | 7AM to 8AM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
May | 30 | 8AM to 9AM | 80.1 | 67.4 | 61 | 80.4 | 31.81 | 0.073 | 0.54 | 13.86 | 0
May | 30 | 9AM to 10AM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
May | 30 | 10AM to 11AM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
May | 30 | 11AM to 12PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
May | 30 | 12PM to 1PM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
May | 30 | 1PM to 2PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
May | 30 | 2PM to 3PM | 82.9 | 67.2 | 59 | 74.9 | 31.64 | 0.0726 | 0.5 | 13.91 | 0
May | 30 | 3PM to 4PM | 81 | 66 | 57.9 | 72 | 30.71 | 0.0729 | 0.48 | 13.85 | 0
May | 30 | 4PM to 5PM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
May | 30 | 5PM to 6PM | 75.9 | 64.3 | 57.9 | 72 | 29.47 | 0.0736 | 0.48 | 13.72 | 0
May | 30 | 6PM to 7PM | 75 | 63.5 | 57 | 69.6 | 28.89 | 0.0738 | 0.47 | 13.69 | 0
May | 30 | 7PM to 8PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
May | 30 | 8PM to 9PM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
May | 30 | 9PM to 10PM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
May | 30 | 10PM to 11PM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
May | 30 | 11PM to 12AM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
May | 31 | 12AM to 1AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
May | 31 | 1AM to 2AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
May | 31 | 2AM to 3AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
May | 31 | 3AM to 4AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
May | 31 | 4AM to 5AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
May | 31 | 5AM to 6AM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
May | 31 | 6AM to 7AM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
May | 31 | 7AM to 8AM | 77 | 65.3 | 59 | 74.9 | 30.19 | 0.0735 | 0.5 | 13.76 | 0
May | 31 | 8AM to 9AM | 79 | 65.3 | 57.9 | 72 | 30.22 | 0.0732 | 0.48 | 13.8 | 0
May | 31 | 9AM to 10AM | 81 | 66.6 | 59 | 74.9 | 31.16 | 0.0729 | 0.5 | 13.86 | 0
May | 31 | 10AM to 11AM | 82 | 66.3 | 57.9 | 72 | 30.97 | 0.0728 | 0.48 | 13.88 | 0
May | 31 | 11AM to 12PM | 82.9 | 66.6 | 57.9 | 72 | 31.19 | 0.0727 | 0.48 | 13.9 | 0
May | 31 | 12PM to 1PM | 82.9 | 67.2 | 59 | 74.9 | 31.64 | 0.0726 | 0.5 | 13.91 | 0
May | 31 | 1PM to 2PM | 82.9 | 67.8 | 60.1 | 77.8 | 32.11 | 0.0726 | 0.52 | 13.92 | 0
May | 31 | 2PM to 3PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
May | 31 | 3PM to 4PM | 81 | 66.6 | 59 | 74.9 | 31.16 | 0.0729 | 0.5 | 13.86 | 0
May | 31 | 4PM to 5PM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
May | 31 | 5PM to 6PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
May | 31 | 6PM to 7PM | 75 | 64 | 57.9 | 72 | 29.25 | 0.0737 | 0.48 | 13.7 | 0
May | 31 | 7PM to 8PM | 73.9 | 64.3 | 59 | 74.9 | 29.44 | 0.0739 | 0.5 | 13.68 | 0
May | 31 | 8PM to 9PM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
May | 31 | 9PM to 10PM | 73.2 | 65.7 | 61.9 | 83.1 | 30.55 | 0.0739 | 0.56 | 13.69 | 0
May | 31 | 10PM to 11PM | 73.2 | 66.1 | 62.6 | 85.3 | 30.89 | 0.0739 | 0.57 | 13.69 | 0
May | 31 | 11PM to 12AM | 73.4 | 66.8 | 63.5 | 88.1 | 31.37 | 0.0739 | 0.59 | 13.71 | 0
June | 1 | 12AM to 1AM | 73.4 | 67.2 | 64.2 | 90.4 | 31.73 | 0.0739 | 0.61 | 13.72 | 0
June | 1 | 1AM to 2AM | 73.6 | 67.8 | 65.1 | 93.3 | 32.24 | 0.0738 | 0.63 | 13.73 | 0
June | 1 | 2AM to 3AM | 73.6 | 68.3 | 65.8 | 95.7 | 32.61 | 0.0738 | 0.64 | 13.74 | 0
June | 1 | 3AM to 4AM | 73.8 | 68.9 | 66.7 | 98.8 | 33.14 | 0.0738 | 0.66 | 13.75 | 0
June | 1 | 4AM to 5AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
June | 1 | 5AM to 6AM | 73.8 | 69.2 | 67.1 | 100.1 | 33.34 | 0.0737 | 0.67 | 13.75 | 0
June | 1 | 6AM to 7AM | 74.3 | 69.4 | 67.3 | 100.7 | 33.57 | 0.0737 | 0.67 | 13.77 | 0
June | 1 | 7AM to 8AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
June | 1 | 8AM to 9AM | 77.4 | 70.6 | 67.6 | 102 | 34.53 | 0.0732 | 0.68 | 13.85 | 0
June | 1 | 9AM to 10AM | 79.7 | 71.5 | 68 | 103.3 | 35.31 | 0.0729 | 0.69 | 13.92 | 0
June | 1 | 10AM to 11AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
June | 1 | 11AM to 12PM | 81.7 | 72.3 | 68.4 | 104.6 | 36 | 0.0726 | 0.7 | 13.97 | 0
June | 1 | 12PM to 1PM | 81.3 | 72.2 | 68.4 | 104.6 | 35.92 | 0.0727 | 0.7 | 13.96 | 0
June | 1 | 1PM to 2PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
June | 1 | 2PM to 3PM | 80.2 | 71.9 | 68.4 | 104.6 | 35.65 | 0.0728 | 0.7 | 13.94 | 0
June | 1 | 3PM to 4PM | 79.7 | 71.6 | 68.2 | 104 | 35.41 | 0.0729 | 0.69 | 13.92 | 0
June | 1 | 4PM to 5PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
June | 1 | 5PM to 6PM | 77.7 | 70.9 | 68 | 103.3 | 34.82 | 0.0732 | 0.69 | 13.87 | 0
June | 1 | 6PM to 7PM | 76.3 | 70.1 | 67.5 | 101.4 | 34.16 | 0.0734 | 0.68 | 13.82 | 0
June | 1 | 7PM to 8PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
June | 1 | 8PM to 9PM | 74.7 | 69.8 | 67.6 | 102 | 33.86 | 0.0736 | 0.68 | 13.78 | 0
June | 1 | 9PM to 10PM | 74.3 | 69.9 | 68 | 103.3 | 33.98 | 0.0736 | 0.69 | 13.78 | 0
June | 1 | 10PM to 11PM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
June | 1 | 11PM to 12AM | 74.3 | 69.7 | 67.6 | 102 | 33.77 | 0.0737 | 0.68 | 13.77 | 0
June | 2 | 12AM to 1AM | 74.7 | 69.4 | 67.1 | 100.1 | 33.56 | 0.0736 | 0.67 | 13.78 | 0
June | 2 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
June | 2 | 2AM to 3AM | 74.7 | 69 | 66.4 | 97.6 | 33.17 | 0.0736 | 0.65 | 13.77 | 0
June | 2 | 3AM to 4AM | 74.3 | 68.9 | 66.4 | 97.6 | 33.08 | 0.0737 | 0.65 | 13.76 | 0
June | 2 | 4AM to 5AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
June | 2 | 5AM to 6AM | 74.3 | 68.7 | 66.2 | 96.9 | 32.98 | 0.0737 | 0.65 | 13.76 | 0
June | 2 | 6AM to 7AM | 74.7 | 69 | 66.4 | 97.6 | 33.17 | 0.0736 | 0.65 | 13.77 | 0
June | 2 | 7AM to 8AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
June | 2 | 8AM to 9AM | 76.3 | 69.5 | 66.4 | 97.6 | 33.57 | 0.0734 | 0.65 | 13.81 | 0
June | 2 | 9AM to 10AM | 77.7 | 69.9 | 66.4 | 97.6 | 33.92 | 0.0732 | 0.65 | 13.85 | 0
June | 2 | 10AM to 11AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
June | 2 | 11AM to 12PM | 80.6 | 70 | 65.1 | 93.3 | 33.96 | 0.0729 | 0.63 | 13.91 | 0
June | 2 | 12PM to 1PM | 82.4 | 69.6 | 63.7 | 88.6 | 33.67 | 0.0726 | 0.59 | 13.94 | 0
June | 2 | 1PM to 2PM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
June | 2 | 2PM to 3PM | 83.3 | 69.7 | 63.3 | 87.5 | 33.71 | 0.0725 | 0.59 | 13.96 | 0
June | 2 | 3PM to 4PM | 82.8 | 70.1 | 64.2 | 90.4 | 34.03 | 0.0726 | 0.61 | 13.96 | 0
June | 2 | 4PM to 5PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
June | 2 | 5PM to 6PM | 80.1 | 69.5 | 64.6 | 91.5 | 33.55 | 0.0729 | 0.61 | 13.89 | 0
June | 2 | 6PM to 7PM | 77.9 | 68.4 | 63.9 | 89.2 | 32.66 | 0.0732 | 0.6 | 13.83 | 0
June | 2 | 7PM to 8PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
June | 2 | 8PM to 9PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
June | 2 | 9PM to 10PM | 75.9 | 68.2 | 64.6 | 91.5 | 32.53 | 0.0735 | 0.61 | 13.78 | 0
June | 2 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 2 | 11PM to 12AM | 75.6 | 68.6 | 65.3 | 93.9 | 32.82 | 0.0735 | 0.63 | 13.78 | 0
June | 3 | 12AM to 1AM | 75.4 | 68.5 | 65.3 | 93.9 | 32.77 | 0.0736 | 0.63 | 13.78 | 0
June | 3 | 1AM to 2AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
June | 3 | 2AM to 3AM | 73.9 | 68.3 | 65.7 | 95.1 | 32.61 | 0.0737 | 0.64 | 13.74 | 0
June | 3 | 3AM to 4AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
June | 3 | 4AM to 5AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
June | 3 | 5AM to 6AM | 73.2 | 68.4 | 66.2 | 96.9 | 32.72 | 0.0738 | 0.65 | 13.73 | 0
June | 3 | 6AM to 7AM | 74.7 | 69 | 66.4 | 97.6 | 33.17 | 0.0736 | 0.65 | 13.77 | 0
June | 3 | 7AM to 8AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 3 | 8AM to 9AM | 77.9 | 69.5 | 65.7 | 95.1 | 33.58 | 0.0732 | 0.64 | 13.85 | 0
June | 3 | 9AM to 10AM | 80.1 | 69.8 | 65.1 | 93.3 | 33.83 | 0.0729 | 0.63 | 13.9 | 0
June | 3 | 10AM to 11AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
June | 3 | 11AM to 12PM | 82.8 | 69.5 | 63.3 | 87.5 | 33.58 | 0.0726 | 0.59 | 13.95 | 0
June | 3 | 12PM to 1PM | 83.3 | 69.2 | 62.4 | 84.7 | 33.28 | 0.0725 | 0.57 | 13.95 | 0
June | 3 | 1PM to 2PM | 84 | 68.6 | 61 | 80.4 | 32.78 | 0.0725 | 0.54 | 13.96 | 0
June | 3 | 2PM to 3PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
June | 3 | 3PM to 4PM | 82 | 68.9 | 62.6 | 85.3 | 33.06 | 0.0727 | 0.57 | 13.92 | 0
June | 3 | 4PM to 5PM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
June | 3 | 5PM to 6PM | 79 | 67.8 | 62.2 | 84.2 | 32.13 | 0.0731 | 0.57 | 13.84 | 0
June | 3 | 6PM to 7PM | 77 | 66.6 | 61.3 | 81.5 | 31.23 | 0.0734 | 0.55 | 13.78 | 0
June | 3 | 7PM to 8PM | 75 | 65.2 | 60.1 | 77.8 | 30.17 | 0.0737 | 0.52 | 13.72 | 0
June | 3 | 8PM to 9PM | 75 | 65.7 | 60.8 | 79.9 | 30.5 | 0.0737 | 0.54 | 13.72 | 0
June | 3 | 9PM to 10PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
June | 3 | 10PM to 11PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
June | 3 | 11PM to 12AM | 75 | 66.2 | 61.7 | 82.5 | 30.91 | 0.0737 | 0.55 | 13.73 | 0
June | 4 | 12AM to 1AM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
June | 4 | 1AM to 2AM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
June | 4 | 2AM to 3AM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
June | 4 | 3AM to 4AM | 75 | 66.2 | 61.7 | 82.5 | 30.91 | 0.0737 | 0.55 | 13.73 | 0
June | 4 | 4AM to 5AM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
June | 4 | 5AM to 6AM | 75.7 | 67.1 | 62.8 | 85.8 | 31.6 | 0.0736 | 0.58 | 13.76 | 0
June | 4 | 6AM to 7AM | 76.3 | 68.4 | 64.8 | 92.1 | 32.71 | 0.0734 | 0.62 | 13.79 | 0
June | 4 | 7AM to 8AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
June | 4 | 8AM to 9AM | 78.6 | 68.9 | 64.4 | 90.9 | 33.11 | 0.0731 | 0.61 | 13.85 | 0
June | 4 | 9AM to 10AM | 80.4 | 68.3 | 62.4 | 84.7 | 32.57 | 0.0729 | 0.57 | 13.88 | 0
June | 4 | 10AM to 11AM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
June | 4 | 11AM to 12PM | 82.4 | 68 | 60.8 | 79.9 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
June | 4 | 12PM to 1PM | 82.6 | 68.2 | 61 | 80.4 | 32.43 | 0.0727 | 0.54 | 13.92 | 0
June | 4 | 1PM to 2PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
June | 4 | 2PM to 3PM | 82.6 | 68.4 | 61.3 | 81.5 | 32.6 | 0.0727 | 0.55 | 13.92 | 0
June | 4 | 3PM to 4PM | 82.4 | 68.2 | 61.2 | 80.9 | 32.47 | 0.0727 | 0.54 | 13.92 | 0
June | 4 | 4PM to 5PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
June | 4 | 5PM to 6PM | 80.1 | 67.9 | 61.9 | 83.1 | 32.23 | 0.073 | 0.56 | 13.86 | 0
June | 4 | 6PM to 7PM | 77.9 | 67.6 | 62.6 | 85.3 | 32.04 | 0.0733 | 0.57 | 13.82 | 0
June | 4 | 7PM to 8PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
June | 4 | 8PM to 9PM | 75.9 | 67.7 | 63.7 | 88.6 | 32.08 | 0.0735 | 0.59 | 13.77 | 0
June | 4 | 9PM to 10PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
June | 4 | 10PM to 11PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
June | 4 | 11PM to 12AM | 75.6 | 68.3 | 64.9 | 92.7 | 32.63 | 0.0735 | 0.62 | 13.78 | 0
June | 5 | 12AM to 1AM | 75.4 | 68.7 | 65.7 | 95.1 | 32.96 | 0.0736 | 0.64 | 13.78 | 0
June | 5 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
June | 5 | 2AM to 3AM | 74.7 | 69 | 66.4 | 97.6 | 33.17 | 0.0736 | 0.65 | 13.77 | 0
June | 5 | 3AM to 4AM | 74.3 | 68.9 | 66.4 | 97.6 | 33.08 | 0.0737 | 0.65 | 13.76 | 0
June | 5 | 4AM to 5AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
June | 5 | 5AM to 6AM | 75 | 69 | 66.2 | 96.9 | 33.16 | 0.0736 | 0.65 | 13.78 | 0
June | 5 | 6AM to 7AM | 75.9 | 69.3 | 66.4 | 97.6 | 33.48 | 0.0735 | 0.65 | 13.8 | 0
June | 5 | 7AM to 8AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
June | 5 | 8AM to 9AM | 78.3 | 70 | 66.4 | 97.6 | 34.06 | 0.0731 | 0.65 | 13.86 | 0
June | 5 | 9AM to 10AM | 79.7 | 70.5 | 66.4 | 97.6 | 34.41 | 0.0729 | 0.65 | 13.9 | 0
June | 5 | 10AM to 11AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
June | 5 | 11AM to 12PM | 80.6 | 70.7 | 66.4 | 97.6 | 34.63 | 0.0728 | 0.65 | 13.92 | 0
June | 5 | 12PM to 1PM | 80.4 | 70.7 | 66.4 | 97.6 | 34.59 | 0.0728 | 0.65 | 13.92 | 0
June | 5 | 1PM to 2PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
June | 5 | 2PM to 3PM | 79.7 | 70 | 65.7 | 95.1 | 34.02 | 0.073 | 0.64 | 13.89 | 0
June | 5 | 3PM to 4PM | 79.3 | 69.5 | 64.9 | 92.7 | 33.56 | 0.073 | 0.62 | 13.88 | 0
June | 5 | 4PM to 5PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
June | 5 | 5PM to 6PM | 77 | 69.2 | 65.7 | 95.1 | 33.36 | 0.0733 | 0.64 | 13.82 | 0
June | 5 | 6PM to 7PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
June | 5 | 7PM to 8PM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
June | 5 | 8PM to 9PM | 73 | 69.1 | 67.3 | 100.7 | 33.26 | 0.0738 | 0.67 | 13.74 | 0
June | 5 | 9PM to 10PM | 73 | 68.5 | 66.4 | 97.6 | 32.77 | 0.0739 | 0.65 | 13.73 | 0
June | 5 | 10PM to 11PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
June | 5 | 11PM to 12AM | 72.3 | 67.8 | 65.7 | 95.1 | 32.21 | 0.074 | 0.64 | 13.7 | 0
June | 6 | 12AM to 1AM | 71.8 | 67.8 | 66 | 96.3 | 32.27 | 0.074 | 0.64 | 13.69 | 0
June | 6 | 1AM to 2AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
June | 6 | 2AM to 3AM | 70.7 | 67.5 | 66 | 96.3 | 32 | 0.0742 | 0.64 | 13.66 | 0
June | 6 | 3AM to 4AM | 70.3 | 67.2 | 65.7 | 95.1 | 31.72 | 0.0742 | 0.64 | 13.65 | 0
June | 6 | 4AM to 5AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
June | 6 | 5AM to 6AM | 72.3 | 67 | 64.4 | 90.9 | 31.56 | 0.074 | 0.61 | 13.69 | 0
June | 6 | 6AM to 7AM | 74.7 | 67.5 | 64 | 89.8 | 31.95 | 0.0737 | 0.6 | 13.75 | 0
June | 6 | 7AM to 8AM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
June | 6 | 8AM to 9AM | 78.3 | 68.2 | 63.3 | 87.5 | 32.48 | 0.0732 | 0.59 | 13.83 | 0
June | 6 | 9AM to 10AM | 79.7 | 68.6 | 63.3 | 87.5 | 32.83 | 0.073 | 0.59 | 13.87 | 0
June | 6 | 10AM to 11AM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
June | 6 | 11AM to 12PM | 81 | 69 | 63.3 | 87.5 | 33.14 | 0.0728 | 0.59 | 13.9 | 0
June | 6 | 12PM to 1PM | 81 | 69 | 63.3 | 87.5 | 33.14 | 0.0728 | 0.59 | 13.9 | 0
June | 6 | 1PM to 2PM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
June | 6 | 2PM to 3PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
June | 6 | 3PM to 4PM | 79 | 68 | 62.6 | 85.3 | 32.3 | 0.0731 | 0.57 | 13.84 | 0
June | 6 | 4PM to 5PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
June | 6 | 5PM to 6PM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
June | 6 | 6PM to 7PM | 76.1 | 67.7 | 63.7 | 88.6 | 32.12 | 0.0735 | 0.59 | 13.78 | 0
June | 6 | 7PM to 8PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
June | 6 | 8PM to 9PM | 74.7 | 67.7 | 64.4 | 90.9 | 32.13 | 0.0737 | 0.61 | 13.75 | 0
June | 6 | 9PM to 10PM | 74.3 | 67.6 | 64.4 | 90.9 | 32.04 | 0.0737 | 0.61 | 13.74 | 0
June | 6 | 10PM to 11PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
June | 6 | 11PM to 12AM | 73.6 | 67.4 | 64.4 | 90.9 | 31.87 | 0.0738 | 0.61 | 13.72 | 0
June | 7 | 12AM to 1AM | 73.4 | 67.3 | 64.4 | 90.9 | 31.82 | 0.0738 | 0.61 | 13.72 | 0
June | 7 | 1AM to 2AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
June | 7 | 2AM to 3AM | 72.7 | 67.3 | 64.8 | 92.1 | 31.83 | 0.0739 | 0.62 | 13.7 | 0
June | 7 | 3AM to 4AM | 72.3 | 67.4 | 65.1 | 93.3 | 31.93 | 0.074 | 0.63 | 13.7 | 0
June | 7 | 4AM to 5AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
June | 7 | 5AM to 6AM | 73.6 | 67.8 | 65.1 | 93.3 | 32.24 | 0.0738 | 0.63 | 13.73 | 0
June | 7 | 6AM to 7AM | 75.4 | 68.5 | 65.3 | 93.9 | 32.77 | 0.0736 | 0.63 | 13.78 | 0
June | 7 | 7AM to 8AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 7 | 8AM to 9AM | 78.6 | 69.3 | 64.9 | 92.7 | 33.38 | 0.0731 | 0.62 | 13.86 | 0
June | 7 | 9AM to 10AM | 80.4 | 69.7 | 64.8 | 92.1 | 33.73 | 0.0729 | 0.62 | 13.9 | 0
June | 7 | 10AM to 11AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
June | 7 | 11AM to 12PM | 81.3 | 69.7 | 64.4 | 90.9 | 33.77 | 0.0728 | 0.61 | 13.92 | 0
June | 7 | 12PM to 1PM | 80.8 | 69.6 | 64.4 | 90.9 | 33.64 | 0.0728 | 0.61 | 13.91 | 0
June | 7 | 1PM to 2PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
June | 7 | 2PM to 3PM | 80.1 | 69.4 | 64.4 | 90.9 | 33.46 | 0.0729 | 0.61 | 13.89 | 0
June | 7 | 3PM to 4PM | 80.1 | 69.3 | 64.2 | 90.4 | 33.37 | 0.0729 | 0.61 | 13.89 | 0
June | 7 | 4PM to 5PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
June | 7 | 5PM to 6PM | 78.4 | 69 | 64.6 | 91.5 | 33.15 | 0.0732 | 0.61 | 13.85 | 0
June | 7 | 6PM to 7PM | 76.6 | 68.7 | 64.9 | 92.7 | 32.89 | 0.0734 | 0.62 | 13.81 | 0
June | 7 | 7PM to 8PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
June | 7 | 8PM to 9PM | 75 | 68.6 | 65.7 | 95.1 | 32.87 | 0.0736 | 0.64 | 13.77 | 0
June | 7 | 9PM to 10PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
June | 7 | 10PM to 11PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
June | 7 | 11PM to 12AM | 74.3 | 68.9 | 66.4 | 97.6 | 33.08 | 0.0737 | 0.65 | 13.76 | 0
June | 8 | 12AM to 1AM | 73.8 | 68.7 | 66.4 | 97.6 | 32.95 | 0.0738 | 0.65 | 13.75 | 0
June | 8 | 1AM to 2AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
June | 8 | 2AM to 3AM | 72 | 68.1 | 66.4 | 97.6 | 32.5 | 0.074 | 0.65 | 13.7 | 0
June | 8 | 3AM to 4AM | 71.1 | 67.9 | 66.4 | 97.6 | 32.28 | 0.0741 | 0.65 | 13.68 | 0
June | 8 | 4AM to 5AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
June | 8 | 5AM to 6AM | 73 | 68.5 | 66.4 | 97.6 | 32.77 | 0.0739 | 0.65 | 13.73 | 0
June | 8 | 6AM to 7AM | 75.9 | 69.8 | 67.1 | 100.1 | 33.87 | 0.0734 | 0.67 | 13.81 | 0
June | 8 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
June | 8 | 8AM to 9AM | 80.1 | 70.7 | 66.6 | 98.2 | 34.6 | 0.0729 | 0.66 | 13.91 | 0
June | 8 | 9AM to 10AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
June | 8 | 10AM to 11AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
June | 8 | 11AM to 12PM | 82 | 71.2 | 66.4 | 97.6 | 34.99 | 0.0726 | 0.65 | 13.96 | 0
June | 8 | 12PM to 1PM | 82 | 71.7 | 67.3 | 100.7 | 35.48 | 0.0726 | 0.67 | 13.97 | 0
June | 8 | 1PM to 2PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
June | 8 | 2PM to 3PM | 80.8 | 71.8 | 68 | 103.3 | 35.58 | 0.0728 | 0.69 | 13.95 | 0
June | 8 | 3PM to 4PM | 79.3 | 71 | 67.5 | 101.4 | 34.92 | 0.073 | 0.68 | 13.9 | 0
June | 8 | 4PM to 5PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
June | 8 | 5PM to 6PM | 76.5 | 70.3 | 67.6 | 102 | 34.31 | 0.0734 | 0.68 | 13.83 | 0
June | 8 | 6PM to 7PM | 74.7 | 69.9 | 67.8 | 102.7 | 33.97 | 0.0736 | 0.69 | 13.79 | 0
June | 8 | 7PM to 8PM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
June | 8 | 8PM to 9PM | 72.3 | 69.8 | 68.7 | 106 | 33.9 | 0.0739 | 0.71 | 13.74 | 0
June | 8 | 9PM to 10PM | 71.8 | 69.9 | 69.1 | 107.3 | 33.98 | 0.074 | 0.72 | 13.73 | 0
June | 8 | 10PM to 11PM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
June | 8 | 11PM to 12AM | 71.8 | 70.1 | 69.4 | 108.7 | 34.19 | 0.074 | 0.73 | 13.73 | 0
June | 9 | 12AM to 1AM | 72.3 | 70.3 | 69.4 | 108.7 | 34.33 | 0.0739 | 0.73 | 13.74 | 0
June | 9 | 1AM to 2AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
June | 9 | 2AM to 3AM | 72 | 69.7 | 68.7 | 106 | 33.82 | 0.074 | 0.71 | 13.73 | 0
June | 9 | 3AM to 4AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
June | 9 | 4AM to 5AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
June | 9 | 5AM to 6AM | 72.3 | 69 | 67.5 | 101.4 | 33.19 | 0.0739 | 0.68 | 13.72 | 0
June | 9 | 6AM to 7AM | 74.7 | 70 | 68 | 103.3 | 34.07 | 0.0736 | 0.69 | 13.79 | 0
June | 9 | 7AM to 8AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
June | 9 | 8AM to 9AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
June | 9 | 9AM to 10AM | 81 | 71.6 | 67.6 | 102 | 35.42 | 0.0727 | 0.68 | 13.95 | 0
June | 9 | 10AM to 11AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
June | 9 | 11AM to 12PM | 82.9 | 71.4 | 66.4 | 97.6 | 35.21 | 0.0725 | 0.65 | 13.98 | 0
June | 9 | 12PM to 1PM | 82.9 | 70.8 | 65.3 | 93.9 | 34.63 | 0.0725 | 0.63 | 13.97 | 0
June | 9 | 1PM to 2PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
June | 9 | 2PM to 3PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
June | 9 | 3PM to 4PM | 82.9 | 69.7 | 63.5 | 88.1 | 33.72 | 0.0726 | 0.59 | 13.95 | 0
June | 9 | 4PM to 5PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
June | 9 | 5PM to 6PM | 80.6 | 69.2 | 63.9 | 89.2 | 33.32 | 0.0729 | 0.6 | 13.9 | 0
June | 9 | 6PM to 7PM | 78.3 | 68.9 | 64.6 | 91.5 | 33.11 | 0.0732 | 0.61 | 13.84 | 0
June | 9 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 9 | 8PM to 9PM | 75.6 | 68.6 | 65.3 | 93.9 | 32.82 | 0.0735 | 0.63 | 13.78 | 0
June | 9 | 9PM to 10PM | 75.4 | 68.5 | 65.3 | 93.9 | 32.77 | 0.0736 | 0.63 | 13.78 | 0
June | 9 | 10PM to 11PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
June | 9 | 11PM to 12AM | 74.7 | 68.3 | 65.3 | 93.9 | 32.6 | 0.0737 | 0.63 | 13.76 | 0
June | 10 | 12AM to 1AM | 74.3 | 68.2 | 65.3 | 93.9 | 32.51 | 0.0737 | 0.63 | 13.75 | 0
June | 10 | 1AM to 2AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
June | 10 | 2AM to 3AM | 73.6 | 67.7 | 64.9 | 92.7 | 32.14 | 0.0738 | 0.62 | 13.73 | 0
June | 10 | 3AM to 4AM | 73.4 | 67.5 | 64.8 | 92.1 | 32.01 | 0.0738 | 0.62 | 13.72 | 0
June | 10 | 4AM to 5AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
June | 10 | 5AM to 6AM | 75 | 67.8 | 64.4 | 90.9 | 32.22 | 0.0736 | 0.61 | 13.76 | 0
June | 10 | 6AM to 7AM | 77 | 68.9 | 65.1 | 93.3 | 33.08 | 0.0733 | 0.63 | 13.82 | 0
June | 10 | 7AM to 8AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
June | 10 | 8AM to 9AM | 81 | 69.6 | 64.4 | 90.9 | 33.68 | 0.0728 | 0.61 | 13.91 | 0
June | 10 | 9AM to 10AM | 82.9 | 69.6 | 63.3 | 87.5 | 33.63 | 0.0726 | 0.59 | 13.95 | 0
June | 10 | 10AM to 11AM | 84.9 | 69.5 | 62.1 | 83.6 | 33.51 | 0.0723 | 0.56 | 13.99 | 0
June | 10 | 11AM to 12PM | 84.9 | 69.9 | 62.8 | 85.8 | 33.85 | 0.0723 | 0.58 | 14 | 0
June | 10 | 12PM to 1PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
June | 10 | 1PM to 2PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
June | 10 | 2PM to 3PM | 84 | 70.1 | 63.7 | 88.6 | 34.07 | 0.0724 | 0.59 | 13.98 | 0
June | 10 | 3PM to 4PM | 82.9 | 69.9 | 63.9 | 89.2 | 33.89 | 0.0726 | 0.6 | 13.96 | 0
June | 10 | 4PM to 5PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
June | 10 | 5PM to 6PM | 80.4 | 69.5 | 64.4 | 90.9 | 33.55 | 0.0729 | 0.61 | 13.9 | 0
June | 10 | 6PM to 7PM | 78.6 | 68.8 | 64.2 | 90.4 | 33.01 | 0.0731 | 0.61 | 13.85 | 0
June | 10 | 7PM to 8PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
June | 10 | 8PM to 9PM | 76.6 | 68.5 | 64.8 | 92.1 | 32.8 | 0.0734 | 0.62 | 13.8 | 0
June | 10 | 9PM to 10PM | 76.3 | 68.5 | 64.9 | 92.7 | 32.81 | 0.0734 | 0.62 | 13.8 | 0
June | 10 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 10 | 11PM to 12AM | 75.6 | 68.1 | 64.6 | 91.5 | 32.44 | 0.0735 | 0.61 | 13.77 | 0
June | 11 | 12AM to 1AM | 75.4 | 67.7 | 64 | 89.8 | 32.13 | 0.0736 | 0.6 | 13.76 | 0
June | 11 | 1AM to 2AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
June | 11 | 2AM to 3AM | 75 | 67.4 | 63.7 | 88.6 | 31.86 | 0.0736 | 0.59 | 13.75 | 0
June | 11 | 3AM to 4AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
June | 11 | 4AM to 5AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
June | 11 | 5AM to 6AM | 76.1 | 67.8 | 63.9 | 89.2 | 32.21 | 0.0735 | 0.6 | 13.78 | 0
June | 11 | 6AM to 7AM | 77 | 68 | 63.7 | 88.6 | 32.35 | 0.0734 | 0.59 | 13.8 | 0
June | 11 | 7AM to 8AM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
June | 11 | 8AM to 9AM | 79.3 | 68.9 | 64 | 89.8 | 33.1 | 0.073 | 0.6 | 13.87 | 0
June | 11 | 9AM to 10AM | 80.8 | 69.7 | 64.6 | 91.5 | 33.73 | 0.0728 | 0.61 | 13.91 | 0
June | 11 | 10AM to 11AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
June | 11 | 11AM to 12PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
June | 11 | 12PM to 1PM | 84 | 70.8 | 64.8 | 92.1 | 34.62 | 0.0724 | 0.62 | 13.99 | 0
June | 11 | 1PM to 2PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
June | 11 | 2PM to 3PM | 83.7 | 70.6 | 64.8 | 92.1 | 34.53 | 0.0724 | 0.62 | 13.98 | 0
June | 11 | 3PM to 4PM | 82.2 | 70.3 | 64.9 | 92.7 | 34.27 | 0.0726 | 0.62 | 13.95 | 0
June | 11 | 4PM to 5PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
June | 11 | 5PM to 6PM | 79.7 | 69.6 | 64.9 | 92.7 | 33.65 | 0.073 | 0.62 | 13.88 | 0
June | 11 | 6PM to 7PM | 78.3 | 68.9 | 64.6 | 91.5 | 33.11 | 0.0732 | 0.61 | 13.84 | 0
June | 11 | 7PM to 8PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
June | 11 | 8PM to 9PM | 76.6 | 68.3 | 64.4 | 90.9 | 32.62 | 0.0734 | 0.61 | 13.8 | 0
June | 11 | 9PM to 10PM | 76.3 | 68.2 | 64.4 | 90.9 | 32.53 | 0.0735 | 0.61 | 13.79 | 0
June | 11 | 10PM to 11PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
June | 11 | 11PM to 12AM | 75.2 | 68.2 | 64.9 | 92.7 | 32.54 | 0.0736 | 0.62 | 13.77 | 0
June | 12 | 12AM to 1AM | 74.7 | 68.5 | 65.7 | 95.1 | 32.78 | 0.0736 | 0.64 | 13.76 | 0
June | 12 | 1AM to 2AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
June | 12 | 2AM to 3AM | 74.3 | 68.6 | 66 | 96.3 | 32.89 | 0.0737 | 0.64 | 13.76 | 0
June | 12 | 3AM to 4AM | 74.7 | 68.5 | 65.7 | 95.1 | 32.78 | 0.0736 | 0.64 | 13.76 | 0
June | 12 | 4AM to 5AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
June | 12 | 5AM to 6AM | 76.1 | 68.6 | 65.1 | 93.3 | 32.86 | 0.0735 | 0.63 | 13.79 | 0
June | 12 | 6AM to 7AM | 77 | 69 | 65.3 | 93.9 | 33.17 | 0.0733 | 0.63 | 13.82 | 0
June | 12 | 7AM to 8AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
June | 12 | 8AM to 9AM | 80.1 | 69.5 | 64.6 | 91.5 | 33.55 | 0.0729 | 0.61 | 13.89 | 0
June | 12 | 9AM to 10AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
June | 12 | 10AM to 11AM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
June | 12 | 11AM to 12PM | 84.4 | 70.4 | 64 | 89.8 | 34.34 | 0.0724 | 0.6 | 14 | 0
June | 12 | 12PM to 1PM | 84.6 | 70.8 | 64.6 | 91.5 | 34.66 | 0.0723 | 0.61 | 14.01 | 0
June | 12 | 1PM to 2PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
June | 12 | 2PM to 3PM | 83.3 | 71.1 | 65.7 | 95.1 | 34.91 | 0.0725 | 0.64 | 13.98 | 0
June | 12 | 3PM to 4PM | 81.7 | 70.7 | 65.8 | 95.7 | 34.61 | 0.0727 | 0.64 | 13.94 | 0
June | 12 | 4PM to 5PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
June | 12 | 5PM to 6PM | 78.6 | 70.2 | 66.4 | 97.6 | 34.14 | 0.0731 | 0.65 | 13.87 | 0
June | 12 | 6PM to 7PM | 77.4 | 69.7 | 66.2 | 96.9 | 33.74 | 0.0733 | 0.65 | 13.84 | 0
June | 12 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 12 | 8PM to 9PM | 75.9 | 68.9 | 65.7 | 95.1 | 33.09 | 0.0735 | 0.64 | 13.79 | 0
June | 12 | 9PM to 10PM | 75.9 | 68.5 | 65.1 | 93.3 | 32.81 | 0.0735 | 0.63 | 13.79 | 0
June | 12 | 10PM to 11PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
June | 12 | 11PM to 12AM | 75.6 | 68.1 | 64.6 | 91.5 | 32.44 | 0.0735 | 0.61 | 13.77 | 0
June | 13 | 12AM to 1AM | 75.4 | 68.3 | 64.9 | 92.7 | 32.59 | 0.0736 | 0.62 | 13.77 | 0
June | 13 | 1AM to 2AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
June | 13 | 2AM to 3AM | 74.3 | 68.4 | 65.7 | 95.1 | 32.7 | 0.0737 | 0.64 | 13.75 | 0
June | 13 | 3AM to 4AM | 73.8 | 68.5 | 66 | 96.3 | 32.75 | 0.0738 | 0.64 | 13.74 | 0
June | 13 | 4AM to 5AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
June | 13 | 5AM to 6AM | 73.9 | 68.7 | 66.4 | 97.6 | 32.99 | 0.0737 | 0.65 | 13.75 | 0
June | 13 | 6AM to 7AM | 75 | 69.5 | 67.1 | 100.1 | 33.65 | 0.0736 | 0.67 | 13.79 | 0
June | 13 | 7AM to 8AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
June | 13 | 8AM to 9AM | 77.9 | 70.3 | 66.9 | 99.5 | 34.26 | 0.0732 | 0.67 | 13.86 | 0
June | 13 | 9AM to 10AM | 80.1 | 70.8 | 66.7 | 98.8 | 34.69 | 0.0729 | 0.66 | 13.91 | 0
June | 13 | 10AM to 11AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
June | 13 | 11AM to 12PM | 82.9 | 71 | 65.7 | 95.1 | 34.82 | 0.0725 | 0.64 | 13.98 | 0
June | 13 | 12PM to 1PM | 84 | 71 | 65.1 | 93.3 | 34.8 | 0.0724 | 0.63 | 14 | 0
June | 13 | 1PM to 2PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
June | 13 | 2PM to 3PM | 84 | 70.5 | 64.4 | 90.9 | 34.43 | 0.0724 | 0.61 | 13.99 | 0
June | 13 | 3PM to 4PM | 82.9 | 70.1 | 64.2 | 90.4 | 34.08 | 0.0726 | 0.61 | 13.96 | 0
June | 13 | 4PM to 5PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
June | 13 | 5PM to 6PM | 80.4 | 69.8 | 64.9 | 92.7 | 33.82 | 0.0729 | 0.62 | 13.9 | 0
June | 13 | 6PM to 7PM | 78.6 | 69.7 | 65.7 | 95.1 | 33.76 | 0.0731 | 0.64 | 13.86 | 0
June | 13 | 7PM to 8PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
June | 13 | 8PM to 9PM | 77 | 69.7 | 66.4 | 97.6 | 33.74 | 0.0733 | 0.65 | 13.83 | 0
June | 13 | 9PM to 10PM | 77 | 69.7 | 66.4 | 97.6 | 33.74 | 0.0733 | 0.65 | 13.83 | 0
June | 13 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
June | 13 | 11PM to 12AM | 76.6 | 69.6 | 66.4 | 97.6 | 33.66 | 0.0734 | 0.65 | 13.82 | 0
June | 14 | 12AM to 1AM | 76.3 | 69.5 | 66.4 | 97.6 | 33.57 | 0.0734 | 0.65 | 13.81 | 0
June | 14 | 1AM to 2AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 14 | 2AM to 3AM | 75.2 | 69.6 | 67.1 | 100.1 | 33.7 | 0.0735 | 0.67 | 13.79 | 0
June | 14 | 3AM to 4AM | 74.7 | 69.9 | 67.8 | 102.7 | 33.97 | 0.0736 | 0.69 | 13.79 | 0
June | 14 | 4AM to 5AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
June | 14 | 5AM to 6AM | 75.4 | 70.6 | 68.5 | 105.3 | 34.56 | 0.0735 | 0.7 | 13.81 | 0
June | 14 | 6AM to 7AM | 76.6 | 71.3 | 69.1 | 107.3 | 35.18 | 0.0733 | 0.72 | 13.85 | 0
June | 14 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
June | 14 | 8AM to 9AM | 80.1 | 72.1 | 68.7 | 106 | 35.81 | 0.0728 | 0.71 | 13.94 | 0
June | 14 | 9AM to 10AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
June | 14 | 10AM to 11AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
June | 14 | 11AM to 12PM | 84 | 72.3 | 67.3 | 100.7 | 35.97 | 0.0723 | 0.67 | 14.02 | 0
June | 14 | 12PM to 1PM | 84 | 72.3 | 67.3 | 100.7 | 35.97 | 0.0723 | 0.67 | 14.02 | 0
June | 14 | 1PM to 2PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
June | 14 | 2PM to 3PM | 83.7 | 72.2 | 67.3 | 100.7 | 35.88 | 0.0724 | 0.67 | 14.01 | 0
June | 14 | 3PM to 4PM | 83.3 | 72 | 67.1 | 100.1 | 35.69 | 0.0724 | 0.67 | 14 | 0
June | 14 | 4PM to 5PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
June | 14 | 5PM to 6PM | 80.6 | 71.5 | 67.6 | 102 | 35.33 | 0.0728 | 0.68 | 13.94 | 0
June | 14 | 6PM to 7PM | 78.3 | 71 | 67.8 | 102.7 | 34.85 | 0.0731 | 0.69 | 13.88 | 0
June | 14 | 7PM to 8PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
June | 14 | 8PM to 9PM | 75.9 | 70.6 | 68.4 | 104.6 | 34.58 | 0.0734 | 0.7 | 13.82 | 0
June | 14 | 9PM to 10PM | 75.9 | 70.6 | 68.4 | 104.6 | 34.58 | 0.0734 | 0.7 | 13.82 | 0
June | 14 | 10PM to 11PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
June | 14 | 11PM to 12AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
June | 15 | 12AM to 1AM | 75.9 | 68.9 | 65.7 | 95.1 | 33.09 | 0.0735 | 0.64 | 13.79 | 0
June | 15 | 1AM to 2AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
June | 15 | 2AM to 3AM | 75.9 | 68.5 | 65.1 | 93.3 | 32.81 | 0.0735 | 0.63 | 13.79 | 0
June | 15 | 3AM to 4AM | 75.9 | 69 | 65.8 | 95.7 | 33.19 | 0.0735 | 0.64 | 13.8 | 0
June | 15 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 15 | 5AM to 6AM | 77 | 69.7 | 66.4 | 97.6 | 33.74 | 0.0733 | 0.65 | 13.83 | 0
June | 15 | 6AM to 7AM | 77.9 | 70.4 | 67.1 | 100.1 | 34.36 | 0.0732 | 0.67 | 13.86 | 0
June | 15 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
June | 15 | 8AM to 9AM | 80.6 | 71.1 | 66.9 | 99.5 | 34.93 | 0.0728 | 0.67 | 13.93 | 0
June | 15 | 9AM to 10AM | 82.4 | 71.5 | 66.7 | 98.8 | 35.27 | 0.0726 | 0.66 | 13.97 | 0
June | 15 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
June | 15 | 11AM to 12PM | 84.4 | 71.2 | 65.3 | 93.9 | 34.99 | 0.0723 | 0.63 | 14.01 | 0
June | 15 | 12PM to 1PM | 84.6 | 70.7 | 64.4 | 90.9 | 34.56 | 0.0723 | 0.61 | 14 | 0
June | 15 | 1PM to 2PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
June | 15 | 2PM to 3PM | 84.6 | 70.3 | 63.7 | 88.6 | 34.2 | 0.0723 | 0.59 | 14 | 0
June | 15 | 3PM to 4PM | 84.4 | 70.3 | 63.9 | 89.2 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
June | 15 | 4PM to 5PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
June | 15 | 5PM to 6PM | 81.7 | 70 | 64.6 | 91.5 | 33.95 | 0.0727 | 0.61 | 13.93 | 0
June | 15 | 6PM to 7PM | 79.3 | 69.5 | 64.9 | 92.7 | 33.56 | 0.073 | 0.62 | 13.88 | 0
June | 15 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 15 | 8PM to 9PM | 77 | 69 | 65.3 | 93.9 | 33.17 | 0.0733 | 0.63 | 13.82 | 0
June | 15 | 9PM to 10PM | 77 | 69 | 65.3 | 93.9 | 33.17 | 0.0733 | 0.63 | 13.82 | 0
June | 15 | 10PM to 11PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 15 | 11PM to 12AM | 76.6 | 68.4 | 64.6 | 91.5 | 32.71 | 0.0734 | 0.61 | 13.8 | 0
June | 16 | 12AM to 1AM | 76.3 | 68 | 64 | 89.8 | 32.35 | 0.0735 | 0.6 | 13.79 | 0
June | 16 | 1AM to 2AM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
June | 16 | 2AM to 3AM | 75.6 | 67.8 | 64 | 89.8 | 32.17 | 0.0736 | 0.6 | 13.77 | 0
June | 16 | 3AM to 4AM | 75.4 | 68.2 | 64.8 | 92.1 | 32.49 | 0.0736 | 0.62 | 13.77 | 0
June | 16 | 4AM to 5AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
June | 16 | 5AM to 6AM | 76.1 | 68.8 | 65.5 | 94.5 | 33.04 | 0.0735 | 0.63 | 13.8 | 0
June | 16 | 6AM to 7AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
June | 16 | 7AM to 8AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
June | 16 | 8AM to 9AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
June | 16 | 9AM to 10AM | 82 | 70.7 | 65.7 | 95.1 | 34.6 | 0.0726 | 0.64 | 13.95 | 0
June | 16 | 10AM to 11AM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
June | 16 | 11AM to 12PM | 84.7 | 71.3 | 65.3 | 93.9 | 35.07 | 0.0723 | 0.63 | 14.02 | 0
June | 16 | 12PM to 1PM | 85.3 | 71.4 | 65.3 | 93.9 | 35.21 | 0.0722 | 0.63 | 14.03 | 0
June | 16 | 1PM to 2PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
June | 16 | 2PM to 3PM | 84.7 | 71.3 | 65.3 | 93.9 | 35.07 | 0.0723 | 0.63 | 14.02 | 0
June | 16 | 3PM to 4PM | 83.3 | 70.8 | 65.1 | 93.3 | 34.63 | 0.0725 | 0.63 | 13.98 | 0
June | 16 | 4PM to 5PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
June | 16 | 5PM to 6PM | 80.8 | 70.1 | 65.3 | 93.9 | 34.1 | 0.0728 | 0.63 | 13.92 | 0
June | 16 | 6PM to 7PM | 79.3 | 69.6 | 65.1 | 93.3 | 33.65 | 0.073 | 0.63 | 13.88 | 0
June | 16 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
June | 16 | 8PM to 9PM | 77.7 | 69.2 | 65.3 | 93.9 | 33.35 | 0.0732 | 0.63 | 13.84 | 0
June | 16 | 9PM to 10PM | 77.4 | 69.1 | 65.3 | 93.9 | 33.26 | 0.0733 | 0.63 | 13.83 | 0
June | 16 | 10PM to 11PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 16 | 11PM to 12AM | 77 | 69 | 65.3 | 93.9 | 33.17 | 0.0733 | 0.63 | 13.82 | 0
June | 17 | 12AM to 1AM | 77 | 69 | 65.3 | 93.9 | 33.17 | 0.0733 | 0.63 | 13.82 | 0
June | 17 | 1AM to 2AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 17 | 2AM to 3AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 17 | 3AM to 4AM | 75 | 69.3 | 66.7 | 98.8 | 33.45 | 0.0736 | 0.66 | 13.78 | 0
June | 17 | 4AM to 5AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
June | 17 | 5AM to 6AM | 75.4 | 69.6 | 67.1 | 100.1 | 33.74 | 0.0735 | 0.67 | 13.8 | 0
June | 17 | 6AM to 7AM | 76.6 | 70.1 | 67.3 | 100.7 | 34.15 | 0.0733 | 0.67 | 13.83 | 0
June | 17 | 7AM to 8AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
June | 17 | 8AM to 9AM | 80.1 | 71.1 | 67.3 | 100.7 | 34.99 | 0.0729 | 0.67 | 13.92 | 0
June | 17 | 9AM to 10AM | 82 | 71.7 | 67.3 | 100.7 | 35.48 | 0.0726 | 0.67 | 13.97 | 0
June | 17 | 10AM to 11AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
June | 17 | 11AM to 12PM | 84.4 | 72.2 | 66.9 | 99.5 | 35.86 | 0.0723 | 0.67 | 14.03 | 0
June | 17 | 12PM to 1PM | 84.6 | 72.1 | 66.7 | 98.8 | 35.8 | 0.0723 | 0.66 | 14.03 | 0
June | 17 | 1PM to 2PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
June | 17 | 2PM to 3PM | 84 | 71.9 | 66.7 | 98.8 | 35.67 | 0.0724 | 0.66 | 14.02 | 0
June | 17 | 3PM to 4PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
June | 17 | 4PM to 5PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
June | 17 | 5PM to 6PM | 80.4 | 71.5 | 67.6 | 102 | 35.28 | 0.0728 | 0.68 | 13.93 | 0
June | 17 | 6PM to 7PM | 78.6 | 71.1 | 67.8 | 102.7 | 34.94 | 0.0731 | 0.69 | 13.89 | 0
June | 17 | 7PM to 8PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
June | 17 | 8PM to 9PM | 77.4 | 70.6 | 67.6 | 102 | 34.53 | 0.0732 | 0.68 | 13.85 | 0
June | 17 | 9PM to 10PM | 77.7 | 70.3 | 67.1 | 100.1 | 34.32 | 0.0732 | 0.67 | 13.86 | 0
June | 17 | 10PM to 11PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
June | 17 | 11PM to 12AM | 78.1 | 70 | 66.4 | 97.6 | 34.01 | 0.0732 | 0.65 | 13.86 | 0
June | 18 | 12AM to 1AM | 78.1 | 70 | 66.4 | 97.6 | 34.01 | 0.0732 | 0.65 | 13.86 | 0
June | 18 | 1AM to 2AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
June | 18 | 2AM to 3AM | 77.4 | 69.8 | 66.4 | 97.6 | 33.83 | 0.0733 | 0.65 | 13.84 | 0
June | 18 | 3AM to 4AM | 76.6 | 69.6 | 66.4 | 97.6 | 33.66 | 0.0734 | 0.65 | 13.82 | 0
June | 18 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 18 | 5AM to 6AM | 77.4 | 69.7 | 66.2 | 96.9 | 33.74 | 0.0733 | 0.65 | 13.84 | 0
June | 18 | 6AM to 7AM | 78.6 | 70.2 | 66.4 | 97.6 | 34.14 | 0.0731 | 0.65 | 13.87 | 0
June | 18 | 7AM to 8AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
June | 18 | 8AM to 9AM | 81.7 | 70.6 | 65.7 | 95.1 | 34.51 | 0.0727 | 0.64 | 13.94 | 0
June | 18 | 9AM to 10AM | 83.3 | 70.8 | 65.1 | 93.3 | 34.63 | 0.0725 | 0.63 | 13.98 | 0
June | 18 | 10AM to 11AM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
June | 18 | 11AM to 12PM | 85.3 | 70.9 | 64.4 | 90.9 | 34.74 | 0.0722 | 0.61 | 14.02 | 0
June | 18 | 12PM to 1PM | 85.6 | 71 | 64.4 | 90.9 | 34.83 | 0.0722 | 0.61 | 14.03 | 0
June | 18 | 1PM to 2PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
June | 18 | 2PM to 3PM | 85.3 | 71.1 | 64.8 | 92.1 | 34.93 | 0.0722 | 0.62 | 14.03 | 0
June | 18 | 3PM to 4PM | 84.7 | 71.1 | 64.9 | 92.7 | 34.89 | 0.0723 | 0.62 | 14.01 | 0
June | 18 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
June | 18 | 5PM to 6PM | 81.7 | 70.4 | 65.3 | 93.9 | 34.32 | 0.0727 | 0.63 | 13.94 | 0
June | 18 | 6PM to 7PM | 79.3 | 69.6 | 65.1 | 93.3 | 33.65 | 0.073 | 0.63 | 13.88 | 0
June | 18 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 18 | 8PM to 9PM | 77 | 69.2 | 65.7 | 95.1 | 33.36 | 0.0733 | 0.64 | 13.82 | 0
June | 18 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
June | 18 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
June | 18 | 11PM to 12AM | 76.6 | 69.3 | 66 | 96.3 | 33.46 | 0.0734 | 0.64 | 13.82 | 0
June | 19 | 12AM to 1AM | 76.3 | 69 | 65.7 | 95.1 | 33.18 | 0.0734 | 0.64 | 13.8 | 0
June | 19 | 1AM to 2AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 19 | 2AM to 3AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 19 | 3AM to 4AM | 75.9 | 68.3 | 64.8 | 92.1 | 32.63 | 0.0735 | 0.62 | 13.79 | 0
June | 19 | 4AM to 5AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
June | 19 | 5AM to 6AM | 76.6 | 68.3 | 64.4 | 90.9 | 32.62 | 0.0734 | 0.61 | 13.8 | 0
June | 19 | 6AM to 7AM | 77.4 | 69 | 65.1 | 93.3 | 33.17 | 0.0733 | 0.63 | 13.83 | 0
June | 19 | 7AM to 8AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
June | 19 | 8AM to 9AM | 80.1 | 69.4 | 64.4 | 90.9 | 33.46 | 0.0729 | 0.61 | 13.89 | 0
June | 19 | 9AM to 10AM | 82 | 69.3 | 63.3 | 87.5 | 33.41 | 0.0727 | 0.59 | 13.93 | 0
June | 19 | 10AM to 11AM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
June | 19 | 11AM to 12PM | 84.4 | 69.7 | 62.8 | 85.8 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
June | 19 | 12PM to 1PM | 84.6 | 69.9 | 63 | 86.4 | 33.85 | 0.0724 | 0.58 | 13.99 | 0
June | 19 | 1PM to 2PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
June | 19 | 2PM to 3PM | 84.2 | 70.4 | 64 | 89.8 | 34.29 | 0.0724 | 0.6 | 13.99 | 0
June | 19 | 3PM to 4PM | 83.7 | 70.5 | 64.6 | 91.5 | 34.44 | 0.0725 | 0.61 | 13.98 | 0
June | 19 | 4PM to 5PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
June | 19 | 5PM to 6PM | 80.6 | 70.3 | 65.7 | 95.1 | 34.25 | 0.0728 | 0.64 | 13.92 | 0
June | 19 | 6PM to 7PM | 78.3 | 69.7 | 65.8 | 95.7 | 33.77 | 0.0732 | 0.64 | 13.86 | 0
June | 19 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 19 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 19 | 9PM to 10PM | 75.9 | 68.9 | 65.7 | 95.1 | 33.09 | 0.0735 | 0.64 | 13.79 | 0
June | 19 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 19 | 11PM to 12AM | 75.9 | 68.7 | 65.3 | 93.9 | 32.9 | 0.0735 | 0.63 | 13.79 | 0
June | 20 | 12AM to 1AM | 75.9 | 68.7 | 65.3 | 93.9 | 32.9 | 0.0735 | 0.63 | 13.79 | 0
June | 20 | 1AM to 2AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 20 | 2AM to 3AM | 75.6 | 68.8 | 65.7 | 95.1 | 33.01 | 0.0735 | 0.64 | 13.79 | 0
June | 20 | 3AM to 4AM | 75.4 | 69 | 66 | 96.3 | 33.15 | 0.0735 | 0.64 | 13.78 | 0
June | 20 | 4AM to 5AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
June | 20 | 5AM to 6AM | 76.3 | 69.3 | 66.2 | 96.9 | 33.47 | 0.0734 | 0.65 | 13.81 | 0
June | 20 | 6AM to 7AM | 77.7 | 69.9 | 66.4 | 97.6 | 33.92 | 0.0732 | 0.65 | 13.85 | 0
June | 20 | 7AM to 8AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
June | 20 | 8AM to 9AM | 80.6 | 71.2 | 67.1 | 100.1 | 35.03 | 0.0728 | 0.67 | 13.93 | 0
June | 20 | 9AM to 10AM | 82.4 | 72 | 67.6 | 102 | 35.77 | 0.0726 | 0.68 | 13.98 | 0
June | 20 | 10AM to 11AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
June | 20 | 11AM to 12PM | 84 | 73.2 | 68.7 | 106 | 36.79 | 0.0723 | 0.71 | 14.04 | 0
June | 20 | 12PM to 1PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
June | 20 | 1PM to 2PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
June | 20 | 2PM to 3PM | 84 | 73.2 | 68.7 | 106 | 36.79 | 0.0723 | 0.71 | 14.04 | 0
June | 20 | 3PM to 4PM | 84 | 72.6 | 67.8 | 102.7 | 36.27 | 0.0723 | 0.69 | 14.03 | 0
June | 20 | 4PM to 5PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
June | 20 | 5PM to 6PM | 82.4 | 72 | 67.6 | 102 | 35.77 | 0.0726 | 0.68 | 13.98 | 0
June | 20 | 6PM to 7PM | 80.6 | 71.6 | 67.8 | 102.7 | 35.43 | 0.0728 | 0.69 | 13.94 | 0
June | 20 | 7PM to 8PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
June | 20 | 8PM to 9PM | 78.6 | 71.4 | 68.4 | 104.6 | 35.25 | 0.073 | 0.7 | 13.89 | 0
June | 20 | 9PM to 10PM | 78.4 | 71.4 | 68.4 | 104.6 | 35.21 | 0.0731 | 0.7 | 13.89 | 0
June | 20 | 10PM to 11PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
June | 20 | 11PM to 12AM | 77.7 | 70.9 | 68 | 103.3 | 34.82 | 0.0732 | 0.69 | 13.87 | 0
June | 21 | 12AM to 1AM | 77.4 | 70.6 | 67.6 | 102 | 34.53 | 0.0732 | 0.68 | 13.85 | 0
June | 21 | 1AM to 2AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
June | 21 | 2AM to 3AM | 77.4 | 70.1 | 66.9 | 99.5 | 34.13 | 0.0733 | 0.67 | 13.85 | 0
June | 21 | 3AM to 4AM | 77.7 | 70.1 | 66.7 | 98.8 | 34.12 | 0.0732 | 0.66 | 13.85 | 0
June | 21 | 4AM to 5AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
June | 21 | 5AM to 6AM | 79 | 69.5 | 65.1 | 93.3 | 33.56 | 0.0731 | 0.63 | 13.87 | 0
June | 21 | 6AM to 7AM | 80.1 | 69.4 | 64.4 | 90.9 | 33.46 | 0.0729 | 0.61 | 13.89 | 0
June | 21 | 7AM to 8AM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
June | 21 | 8AM to 9AM | 82.2 | 69.8 | 64 | 89.8 | 33.81 | 0.0727 | 0.6 | 13.94 | 0
June | 21 | 9AM to 10AM | 83.7 | 70.5 | 64.6 | 91.5 | 34.44 | 0.0725 | 0.61 | 13.98 | 0
June | 21 | 10AM to 11AM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
June | 21 | 11AM to 12PM | 85.3 | 71.4 | 65.3 | 93.9 | 35.21 | 0.0722 | 0.63 | 14.03 | 0
June | 21 | 12PM to 1PM | 85.6 | 71.5 | 65.3 | 93.9 | 35.3 | 0.0722 | 0.63 | 14.04 | 0
June | 21 | 1PM to 2PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
June | 21 | 2PM to 3PM | 84.9 | 71.3 | 65.3 | 93.9 | 35.12 | 0.0723 | 0.63 | 14.02 | 0
June | 21 | 3PM to 4PM | 84 | 71 | 65.1 | 93.3 | 34.8 | 0.0724 | 0.63 | 14 | 0
June | 21 | 4PM to 5PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
June | 21 | 5PM to 6PM | 81.3 | 70.5 | 65.7 | 95.1 | 34.42 | 0.0727 | 0.64 | 13.93 | 0
June | 21 | 6PM to 7PM | 79.7 | 70.1 | 65.8 | 95.7 | 34.12 | 0.073 | 0.64 | 13.89 | 0
June | 21 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
June | 21 | 8PM to 9PM | 77.7 | 69.7 | 66 | 96.3 | 33.73 | 0.0732 | 0.64 | 13.84 | 0
June | 21 | 9PM to 10PM | 77.4 | 69.3 | 65.7 | 95.1 | 33.45 | 0.0733 | 0.64 | 13.83 | 0
June | 21 | 10PM to 11PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 21 | 11PM to 12AM | 76.6 | 68.9 | 65.3 | 93.9 | 33.08 | 0.0734 | 0.63 | 13.81 | 0
June | 22 | 12AM to 1AM | 76.3 | 68.8 | 65.3 | 93.9 | 32.99 | 0.0734 | 0.63 | 13.8 | 0
June | 22 | 1AM to 2AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 22 | 2AM to 3AM | 76.3 | 69.2 | 66 | 96.3 | 33.37 | 0.0734 | 0.64 | 13.81 | 0
June | 22 | 3AM to 4AM | 76.6 | 69.8 | 66.7 | 98.8 | 33.85 | 0.0734 | 0.66 | 13.82 | 0
June | 22 | 4AM to 5AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
June | 22 | 5AM to 6AM | 77.7 | 70.8 | 67.8 | 102.7 | 34.72 | 0.0732 | 0.69 | 13.86 | 0
June | 22 | 6AM to 7AM | 78.3 | 71.5 | 68.7 | 106 | 35.37 | 0.0731 | 0.71 | 13.89 | 0
June | 22 | 7AM to 8AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
June | 22 | 8AM to 9AM | 80.2 | 72.3 | 69.1 | 107.3 | 36.07 | 0.0728 | 0.72 | 13.94 | 0
June | 22 | 9AM to 10AM | 81.7 | 72.5 | 68.7 | 106 | 36.21 | 0.0726 | 0.71 | 13.98 | 0
June | 22 | 10AM to 11AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
June | 22 | 11AM to 12PM | 83.7 | 72.8 | 68.4 | 104.6 | 36.49 | 0.0724 | 0.7 | 14.02 | 0
June | 22 | 12PM to 1PM | 84.2 | 73 | 68.4 | 104.6 | 36.63 | 0.0723 | 0.7 | 14.04 | 0
June | 22 | 1PM to 2PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
June | 22 | 2PM to 3PM | 84 | 72.3 | 67.3 | 100.7 | 35.97 | 0.0723 | 0.67 | 14.02 | 0
June | 22 | 3PM to 4PM | 82.9 | 71.3 | 66.2 | 96.9 | 35.11 | 0.0725 | 0.65 | 13.98 | 0
June | 22 | 4PM to 5PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
June | 22 | 5PM to 6PM | 80.4 | 70.2 | 65.7 | 95.1 | 34.2 | 0.0729 | 0.64 | 13.91 | 0
June | 22 | 6PM to 7PM | 78.6 | 69.8 | 65.8 | 95.7 | 33.85 | 0.0731 | 0.64 | 13.87 | 0
June | 22 | 7PM to 8PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
June | 22 | 8PM to 9PM | 76.6 | 69.3 | 66 | 96.3 | 33.46 | 0.0734 | 0.64 | 13.82 | 0
June | 22 | 9PM to 10PM | 76.3 | 69 | 65.7 | 95.1 | 33.18 | 0.0734 | 0.64 | 13.8 | 0
June | 22 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 22 | 11PM to 12AM | 75.9 | 68.7 | 65.3 | 93.9 | 32.9 | 0.0735 | 0.63 | 13.79 | 0
June | 23 | 12AM to 1AM | 75.9 | 68.7 | 65.3 | 93.9 | 32.9 | 0.0735 | 0.63 | 13.79 | 0
June | 23 | 1AM to 2AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 23 | 2AM to 3AM | 75.6 | 68.6 | 65.3 | 93.9 | 32.82 | 0.0735 | 0.63 | 13.78 | 0
June | 23 | 3AM to 4AM | 75.4 | 68.5 | 65.3 | 93.9 | 32.77 | 0.0736 | 0.63 | 13.78 | 0
June | 23 | 4AM to 5AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
June | 23 | 5AM to 6AM | 76.1 | 68.6 | 65.1 | 93.3 | 32.86 | 0.0735 | 0.63 | 13.79 | 0
June | 23 | 6AM to 7AM | 77 | 69 | 65.3 | 93.9 | 33.17 | 0.0733 | 0.63 | 13.82 | 0
June | 23 | 7AM to 8AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
June | 23 | 8AM to 9AM | 79.7 | 69.4 | 64.6 | 91.5 | 33.46 | 0.073 | 0.61 | 13.88 | 0
June | 23 | 9AM to 10AM | 81.3 | 69.5 | 64 | 89.8 | 33.59 | 0.0728 | 0.6 | 13.92 | 0
June | 23 | 10AM to 11AM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
June | 23 | 11AM to 12PM | 82.9 | 69.6 | 63.3 | 87.5 | 33.63 | 0.0726 | 0.59 | 13.95 | 0
June | 23 | 12PM to 1PM | 82.9 | 69.6 | 63.3 | 87.5 | 33.63 | 0.0726 | 0.59 | 13.95 | 0
June | 23 | 1PM to 2PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
June | 23 | 2PM to 3PM | 82.2 | 70 | 64.4 | 90.9 | 33.99 | 0.0726 | 0.61 | 13.94 | 0
June | 23 | 3PM to 4PM | 81.7 | 70.4 | 65.3 | 93.9 | 34.32 | 0.0727 | 0.63 | 13.94 | 0
June | 23 | 4PM to 5PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
June | 23 | 5PM to 6PM | 79.7 | 70.2 | 66 | 96.3 | 34.22 | 0.073 | 0.64 | 13.9 | 0
June | 23 | 6PM to 7PM | 78.3 | 69.5 | 65.5 | 94.5 | 33.57 | 0.0732 | 0.63 | 13.85 | 0
June | 23 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 23 | 8PM to 9PM | 76.6 | 68.7 | 64.9 | 92.7 | 32.89 | 0.0734 | 0.62 | 13.81 | 0
June | 23 | 9PM to 10PM | 76.3 | 68.4 | 64.8 | 92.1 | 32.71 | 0.0734 | 0.62 | 13.79 | 0
June | 23 | 10PM to 11PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
June | 23 | 11PM to 12AM | 75.6 | 68 | 64.4 | 90.9 | 32.35 | 0.0736 | 0.61 | 13.77 | 0
June | 24 | 12AM to 1AM | 75.4 | 67.9 | 64.4 | 90.9 | 32.31 | 0.0736 | 0.61 | 13.77 | 0
June | 24 | 1AM to 2AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
June | 24 | 2AM to 3AM | 75 | 67.8 | 64.4 | 90.9 | 32.22 | 0.0736 | 0.61 | 13.76 | 0
June | 24 | 3AM to 4AM | 75 | 67.8 | 64.4 | 90.9 | 32.22 | 0.0736 | 0.61 | 13.76 | 0
June | 24 | 4AM to 5AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
June | 24 | 5AM to 6AM | 76.3 | 68.7 | 65.1 | 93.3 | 32.9 | 0.0734 | 0.63 | 13.8 | 0
June | 24 | 6AM to 7AM | 77.7 | 69.9 | 66.4 | 97.6 | 33.92 | 0.0732 | 0.65 | 13.85 | 0
June | 24 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
June | 24 | 8AM to 9AM | 80.2 | 71.4 | 67.6 | 102 | 35.24 | 0.0728 | 0.68 | 13.93 | 0
June | 24 | 9AM to 10AM | 81.7 | 72.1 | 68 | 103.3 | 35.8 | 0.0726 | 0.69 | 13.97 | 0
June | 24 | 10AM to 11AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
June | 24 | 11AM to 12PM | 83.3 | 72.5 | 68 | 103.3 | 36.2 | 0.0724 | 0.69 | 14.01 | 0
June | 24 | 12PM to 1PM | 83.7 | 72.4 | 67.6 | 102 | 36.08 | 0.0724 | 0.68 | 14.02 | 0
June | 24 | 1PM to 2PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
June | 24 | 2PM to 3PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
June | 24 | 3PM to 4PM | 84 | 71.8 | 66.6 | 98.2 | 35.57 | 0.0724 | 0.66 | 14.01 | 0
June | 24 | 4PM to 5PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
June | 24 | 5PM to 6PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
June | 24 | 6PM to 7PM | 80.1 | 70 | 65.5 | 94.5 | 34.02 | 0.0729 | 0.63 | 13.9 | 0
June | 24 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
June | 24 | 8PM to 9PM | 77.7 | 69.2 | 65.3 | 93.9 | 33.35 | 0.0732 | 0.63 | 13.84 | 0
June | 24 | 9PM to 10PM | 77.4 | 69.1 | 65.3 | 93.9 | 33.26 | 0.0733 | 0.63 | 13.83 | 0
June | 24 | 10PM to 11PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 24 | 11PM to 12AM | 76.3 | 68.5 | 64.9 | 92.7 | 32.81 | 0.0734 | 0.62 | 13.8 | 0
June | 25 | 12AM to 1AM | 75.7 | 68.3 | 64.8 | 92.1 | 32.58 | 0.0735 | 0.62 | 13.78 | 0
June | 25 | 1AM to 2AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
June | 25 | 2AM to 3AM | 75.4 | 68.2 | 64.8 | 92.1 | 32.49 | 0.0736 | 0.62 | 13.77 | 0
June | 25 | 3AM to 4AM | 75.6 | 68.4 | 65.1 | 93.3 | 32.72 | 0.0735 | 0.63 | 13.78 | 0
June | 25 | 4AM to 5AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 25 | 5AM to 6AM | 76.3 | 69.2 | 66 | 96.3 | 33.37 | 0.0734 | 0.64 | 13.81 | 0
June | 25 | 6AM to 7AM | 76.6 | 70.3 | 67.5 | 101.4 | 34.25 | 0.0733 | 0.68 | 13.83 | 0
June | 25 | 7AM to 8AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
June | 25 | 8AM to 9AM | 79.7 | 70.9 | 67.1 | 100.1 | 34.8 | 0.0729 | 0.67 | 13.91 | 0
June | 25 | 9AM to 10AM | 82.2 | 70.8 | 65.7 | 95.1 | 34.64 | 0.0726 | 0.64 | 13.96 | 0
June | 25 | 10AM to 11AM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
June | 25 | 11AM to 12PM | 85.3 | 71.1 | 64.8 | 92.1 | 34.93 | 0.0722 | 0.62 | 14.03 | 0
June | 25 | 12PM to 1PM | 85.6 | 71.3 | 64.9 | 92.7 | 35.11 | 0.0722 | 0.62 | 14.04 | 0
June | 25 | 1PM to 2PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
June | 25 | 2PM to 3PM | 84.4 | 70.8 | 64.6 | 91.5 | 34.61 | 0.0724 | 0.61 | 14 | 0
June | 25 | 3PM to 4PM | 82.6 | 69.8 | 63.9 | 89.2 | 33.81 | 0.0726 | 0.6 | 13.95 | 0
June | 25 | 4PM to 5PM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
June | 25 | 5PM to 6PM | 79.7 | 68.9 | 63.9 | 89.2 | 33.1 | 0.073 | 0.6 | 13.87 | 0
June | 25 | 6PM to 7PM | 78.3 | 68.9 | 64.6 | 91.5 | 33.11 | 0.0732 | 0.61 | 13.84 | 0
June | 25 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 25 | 8PM to 9PM | 76.6 | 68.9 | 65.3 | 93.9 | 33.08 | 0.0734 | 0.63 | 13.81 | 0
June | 25 | 9PM to 10PM | 76.3 | 68.8 | 65.3 | 93.9 | 32.99 | 0.0734 | 0.63 | 13.8 | 0
June | 25 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 25 | 11PM to 12AM | 75.6 | 68.8 | 65.7 | 95.1 | 33.01 | 0.0735 | 0.64 | 13.79 | 0
June | 26 | 12AM to 1AM | 75.4 | 69 | 66 | 96.3 | 33.15 | 0.0735 | 0.64 | 13.78 | 0
June | 26 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
June | 26 | 2AM to 3AM | 74.7 | 69 | 66.4 | 97.6 | 33.17 | 0.0736 | 0.65 | 13.77 | 0
June | 26 | 3AM to 4AM | 74.3 | 68.9 | 66.4 | 97.6 | 33.08 | 0.0737 | 0.65 | 13.76 | 0
June | 26 | 4AM to 5AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
June | 26 | 5AM to 6AM | 75.4 | 69.2 | 66.4 | 97.6 | 33.35 | 0.0735 | 0.65 | 13.79 | 0
June | 26 | 6AM to 7AM | 76.6 | 70 | 67.1 | 100.1 | 34.05 | 0.0733 | 0.67 | 13.83 | 0
June | 26 | 7AM to 8AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
June | 26 | 8AM to 9AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
June | 26 | 9AM to 10AM | 82 | 71.4 | 66.7 | 98.8 | 35.18 | 0.0726 | 0.66 | 13.96 | 0
June | 26 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
June | 26 | 11AM to 12PM | 85.1 | 71.6 | 65.7 | 95.1 | 35.35 | 0.0722 | 0.64 | 14.03 | 0
June | 26 | 12PM to 1PM | 86 | 71.5 | 65.1 | 93.3 | 35.29 | 0.0721 | 0.63 | 14.05 | 0
June | 26 | 1PM to 2PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
June | 26 | 2PM to 3PM | 86.4 | 71.6 | 65.1 | 93.3 | 35.38 | 0.0721 | 0.63 | 14.06 | 0
June | 26 | 3PM to 4PM | 85.6 | 71.8 | 65.7 | 95.1 | 35.49 | 0.0722 | 0.64 | 14.05 | 0
June | 26 | 4PM to 5PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
June | 26 | 5PM to 6PM | 82.2 | 71 | 66 | 96.3 | 34.84 | 0.0726 | 0.64 | 13.96 | 0
June | 26 | 6PM to 7PM | 79.7 | 69.9 | 65.5 | 94.5 | 33.93 | 0.073 | 0.63 | 13.89 | 0
June | 26 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 26 | 8PM to 9PM | 76.6 | 68.9 | 65.3 | 93.9 | 33.08 | 0.0734 | 0.63 | 13.81 | 0
June | 26 | 9PM to 10PM | 76.3 | 68.8 | 65.3 | 93.9 | 32.99 | 0.0734 | 0.63 | 13.8 | 0
June | 26 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
June | 26 | 11PM to 12AM | 75.6 | 68.8 | 65.7 | 95.1 | 33.01 | 0.0735 | 0.64 | 13.79 | 0
June | 27 | 12AM to 1AM | 75.4 | 69 | 66 | 96.3 | 33.15 | 0.0735 | 0.64 | 13.78 | 0
June | 27 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
June | 27 | 2AM to 3AM | 74.7 | 69 | 66.4 | 97.6 | 33.17 | 0.0736 | 0.65 | 13.77 | 0
June | 27 | 3AM to 4AM | 74.3 | 68.9 | 66.4 | 97.6 | 33.08 | 0.0737 | 0.65 | 13.76 | 0
June | 27 | 4AM to 5AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
June | 27 | 5AM to 6AM | 75.4 | 69.2 | 66.4 | 97.6 | 33.35 | 0.0735 | 0.65 | 13.79 | 0
June | 27 | 6AM to 7AM | 76.6 | 70 | 67.1 | 100.1 | 34.05 | 0.0733 | 0.67 | 13.83 | 0
June | 27 | 7AM to 8AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
June | 27 | 8AM to 9AM | 79.7 | 71.5 | 68 | 103.3 | 35.31 | 0.0729 | 0.69 | 13.92 | 0
June | 27 | 9AM to 10AM | 81.3 | 72.4 | 68.7 | 106 | 36.13 | 0.0727 | 0.71 | 13.97 | 0
June | 27 | 10AM to 11AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
June | 27 | 11AM to 12PM | 82.9 | 73.3 | 69.4 | 108.7 | 36.95 | 0.0724 | 0.73 | 14.02 | 0
June | 27 | 12PM to 1PM | 82.9 | 73.3 | 69.4 | 108.7 | 36.95 | 0.0724 | 0.73 | 14.02 | 0
June | 27 | 1PM to 2PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
June | 27 | 2PM to 3PM | 82.6 | 72.8 | 68.7 | 106 | 36.44 | 0.0725 | 0.71 | 14 | 0
June | 27 | 3PM to 4PM | 82.4 | 72.2 | 67.8 | 102.7 | 35.87 | 0.0726 | 0.69 | 13.99 | 0
June | 27 | 4PM to 5PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
June | 27 | 5PM to 6PM | 80.8 | 71.3 | 67.3 | 100.7 | 35.17 | 0.0728 | 0.67 | 13.94 | 0
June | 27 | 6PM to 7PM | 79.3 | 70.8 | 67.1 | 100.1 | 34.72 | 0.073 | 0.67 | 13.9 | 0
June | 27 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
June | 27 | 8PM to 9PM | 77.7 | 70.5 | 67.3 | 100.7 | 34.42 | 0.0732 | 0.67 | 13.86 | 0
June | 27 | 9PM to 10PM | 77.4 | 70.4 | 67.3 | 100.7 | 34.33 | 0.0732 | 0.67 | 13.85 | 0
June | 27 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
June | 27 | 11PM to 12AM | 76.3 | 70 | 67.3 | 100.7 | 34.06 | 0.0734 | 0.67 | 13.82 | 0
June | 28 | 12AM to 1AM | 75.7 | 69.9 | 67.3 | 100.7 | 33.93 | 0.0735 | 0.67 | 13.81 | 0
June | 28 | 1AM to 2AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
June | 28 | 2AM to 3AM | 73.8 | 69 | 66.9 | 99.5 | 33.24 | 0.0737 | 0.67 | 13.75 | 0
June | 28 | 3AM to 4AM | 72.3 | 68.5 | 66.7 | 98.8 | 32.79 | 0.074 | 0.66 | 13.71 | 0
June | 28 | 4AM to 5AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
June | 28 | 5AM to 6AM | 74.1 | 69 | 66.7 | 98.8 | 33.23 | 0.0737 | 0.66 | 13.76 | 0
June | 28 | 6AM to 7AM | 77 | 70.6 | 67.8 | 102.7 | 34.54 | 0.0733 | 0.69 | 13.85 | 0
June | 28 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
June | 28 | 8AM to 9AM | 81.7 | 72.1 | 68 | 103.3 | 35.8 | 0.0726 | 0.69 | 13.97 | 0
June | 28 | 9AM to 10AM | 83.3 | 72.3 | 67.6 | 102 | 35.99 | 0.0724 | 0.68 | 14.01 | 0
June | 28 | 10AM to 11AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
June | 28 | 11AM to 12PM | 84 | 72.5 | 67.6 | 102 | 36.17 | 0.0723 | 0.68 | 14.03 | 0
June | 28 | 12PM to 1PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
June | 28 | 1PM to 2PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
June | 28 | 2PM to 3PM | 81.7 | 72.1 | 68 | 103.3 | 35.8 | 0.0726 | 0.69 | 13.97 | 0
June | 28 | 3PM to 4PM | 81.3 | 71.6 | 67.5 | 101.4 | 35.4 | 0.0727 | 0.68 | 13.95 | 0
June | 28 | 4PM to 5PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
June | 28 | 5PM to 6PM | 80.1 | 71.4 | 67.6 | 102 | 35.19 | 0.0729 | 0.68 | 13.92 | 0
June | 28 | 6PM to 7PM | 79 | 71.2 | 67.8 | 102.7 | 35.03 | 0.073 | 0.69 | 13.9 | 0
June | 28 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
June | 28 | 8PM to 9PM | 77.4 | 71.1 | 68.4 | 104.6 | 34.94 | 0.0732 | 0.7 | 13.86 | 0
June | 28 | 9PM to 10PM | 76.6 | 70.8 | 68.4 | 104.6 | 34.76 | 0.0733 | 0.7 | 13.84 | 0
June | 28 | 10PM to 11PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
June | 28 | 11PM to 12AM | 75.2 | 70.2 | 68 | 103.3 | 34.2 | 0.0735 | 0.69 | 13.8 | 0
June | 29 | 12AM to 1AM | 74.7 | 69.8 | 67.6 | 102 | 33.86 | 0.0736 | 0.68 | 13.78 | 0
June | 29 | 1AM to 2AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
June | 29 | 2AM to 3AM | 72.7 | 68.9 | 67.3 | 100.7 | 33.17 | 0.0739 | 0.67 | 13.73 | 0
June | 29 | 3AM to 4AM | 71.2 | 68.5 | 67.3 | 100.7 | 32.82 | 0.0741 | 0.67 | 13.69 | 0
June | 29 | 4AM to 5AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
June | 29 | 5AM to 6AM | 73 | 68.9 | 67.1 | 100.1 | 33.16 | 0.0738 | 0.67 | 13.74 | 0
June | 29 | 6AM to 7AM | 75.9 | 69.9 | 67.3 | 100.7 | 33.97 | 0.0734 | 0.67 | 13.81 | 0
June | 29 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
June | 29 | 8AM to 9AM | 81.7 | 71.6 | 67.3 | 100.7 | 35.39 | 0.0727 | 0.67 | 13.96 | 0
June | 29 | 9AM to 10AM | 84.4 | 72.4 | 67.3 | 100.7 | 36.06 | 0.0723 | 0.67 | 14.03 | 0
June | 29 | 10AM to 11AM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
June | 29 | 11AM to 12PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
June | 29 | 12PM to 1PM | 87.1 | 72.8 | 66.7 | 98.8 | 36.42 | 0.072 | 0.66 | 14.09 | 0
June | 29 | 1PM to 2PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
June | 29 | 2PM to 3PM | 85.5 | 72.1 | 66.4 | 97.6 | 35.83 | 0.0722 | 0.65 | 14.05 | 0
June | 29 | 3PM to 4PM | 83.7 | 71.5 | 66.2 | 96.9 | 35.29 | 0.0724 | 0.65 | 14 | 0
June | 29 | 4PM to 5PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
June | 29 | 5PM to 6PM | 80.8 | 71.1 | 66.9 | 99.5 | 34.97 | 0.0728 | 0.67 | 13.93 | 0
June | 29 | 6PM to 7PM | 79.3 | 71.2 | 67.6 | 102 | 35.02 | 0.073 | 0.68 | 13.9 | 0
June | 29 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
June | 29 | 8PM to 9PM | 77.7 | 70.9 | 68 | 103.3 | 34.82 | 0.0732 | 0.69 | 13.87 | 0
June | 29 | 9PM to 10PM | 77.4 | 70.6 | 67.6 | 102 | 34.53 | 0.0732 | 0.68 | 13.85 | 0
June | 29 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
June | 29 | 11PM to 12AM | 76.6 | 70.4 | 67.6 | 102 | 34.35 | 0.0733 | 0.68 | 13.83 | 0
June | 30 | 12AM to 1AM | 76.3 | 70.5 | 68 | 103.3 | 34.47 | 0.0734 | 0.69 | 13.83 | 0
June | 30 | 1AM to 2AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
June | 30 | 2AM to 3AM | 75.9 | 70.2 | 67.6 | 102 | 34.17 | 0.0734 | 0.68 | 13.82 | 0
June | 30 | 3AM to 4AM | 75.9 | 69.8 | 67.1 | 100.1 | 33.87 | 0.0734 | 0.67 | 13.81 | 0
June | 30 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
June | 30 | 5AM to 6AM | 77 | 69.6 | 66.2 | 96.9 | 33.65 | 0.0733 | 0.65 | 13.83 | 0
June | 30 | 6AM to 7AM | 77.9 | 69.9 | 66.4 | 97.6 | 33.97 | 0.0732 | 0.65 | 13.85 | 0
June | 30 | 7AM to 8AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
June | 30 | 8AM to 9AM | 81.3 | 70.5 | 65.7 | 95.1 | 34.42 | 0.0727 | 0.64 | 13.93 | 0
June | 30 | 9AM to 10AM | 83.7 | 70.9 | 65.1 | 93.3 | 34.71 | 0.0724 | 0.63 | 13.99 | 0
June | 30 | 10AM to 11AM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
June | 30 | 11AM to 12PM | 85.6 | 70.8 | 64 | 89.8 | 34.65 | 0.0722 | 0.6 | 14.03 | 0
June | 30 | 12PM to 1PM | 85.3 | 70.5 | 63.7 | 88.6 | 34.38 | 0.0723 | 0.59 | 14.02 | 0
June | 30 | 1PM to 2PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
June | 30 | 2PM to 3PM | 84.6 | 70.5 | 64 | 89.8 | 34.38 | 0.0723 | 0.6 | 14 | 0
June | 30 | 3PM to 4PM | 84.4 | 70.8 | 64.6 | 91.5 | 34.61 | 0.0724 | 0.61 | 14 | 0
June | 30 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
June | 30 | 5PM to 6PM | 81.7 | 70.4 | 65.3 | 93.9 | 34.32 | 0.0727 | 0.63 | 13.94 | 0
June | 30 | 6PM to 7PM | 79.3 | 69.6 | 65.1 | 93.3 | 33.65 | 0.073 | 0.63 | 13.88 | 0
June | 30 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
June | 30 | 8PM to 9PM | 76.6 | 68.9 | 65.3 | 93.9 | 33.08 | 0.0734 | 0.63 | 13.81 | 0
June | 30 | 9PM to 10PM | 76.5 | 68.8 | 65.3 | 93.9 | 33.04 | 0.0734 | 0.63 | 13.8 | 0
June | 30 | 10PM to 11PM | 76.1 | 68.6 | 65.1 | 93.3 | 32.86 | 0.0735 | 0.63 | 13.79 | 0
June | 30 | 11PM to 12AM | 75.9 | 68.5 | 65.1 | 93.3 | 32.81 | 0.0735 | 0.63 | 13.79 | 0
July | 1 | 12AM to 1AM | 75.7 | 68.5 | 65.1 | 93.3 | 32.77 | 0.0735 | 0.63 | 13.78 | 0
July | 1 | 1AM to 2AM | 75.6 | 68.4 | 65.1 | 93.3 | 32.72 | 0.0735 | 0.63 | 13.78 | 0
July | 1 | 2AM to 3AM | 75.2 | 68.2 | 64.9 | 92.7 | 32.54 | 0.0736 | 0.62 | 13.77 | 0
July | 1 | 3AM to 4AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 1 | 4AM to 5AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
July | 1 | 5AM to 6AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
July | 1 | 6AM to 7AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 1 | 7AM to 8AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
July | 1 | 8AM to 9AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
July | 1 | 9AM to 10AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
July | 1 | 10AM to 11AM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
July | 1 | 11AM to 12PM | 89.1 | 71.2 | 63 | 86.4 | 34.95 | 0.0718 | 0.58 | 14.11 | 0
July | 1 | 12PM to 1PM | 89.1 | 70.7 | 62.1 | 83.6 | 34.52 | 0.0718 | 0.56 | 14.1 | 0
July | 1 | 1PM to 2PM | 89.1 | 70.7 | 62.1 | 83.6 | 34.52 | 0.0718 | 0.56 | 14.1 | 0
July | 1 | 2PM to 3PM | 88 | 70.9 | 63 | 86.4 | 34.69 | 0.0719 | 0.58 | 14.08 | 0
July | 1 | 3PM to 4PM | 87.1 | 70.1 | 62.1 | 83.6 | 34.04 | 0.072 | 0.56 | 14.05 | 0
July | 1 | 4PM to 5PM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
July | 1 | 5PM to 6PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
July | 1 | 6PM to 7PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
July | 1 | 7PM to 8PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
July | 1 | 8PM to 9PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 1 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 1 | 10PM to 11PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 1 | 11PM to 12AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 2 | 12AM to 1AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 2 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 2 | 2AM to 3AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 2 | 3AM to 4AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 2 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 2 | 5AM to 6AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 2 | 6AM to 7AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 2 | 7AM to 8AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 2 | 8AM to 9AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
July | 2 | 9AM to 10AM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
July | 2 | 10AM to 11AM | 87.1 | 70.6 | 63 | 86.4 | 34.47 | 0.072 | 0.58 | 14.05 | 0
July | 2 | 11AM to 12PM | 88 | 70.9 | 63 | 86.4 | 34.69 | 0.0719 | 0.58 | 14.08 | 0
July | 2 | 12PM to 1PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
July | 2 | 1PM to 2PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
July | 2 | 2PM to 3PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
July | 2 | 3PM to 4PM | 87.1 | 70.6 | 63 | 86.4 | 34.47 | 0.072 | 0.58 | 14.05 | 0
July | 2 | 4PM to 5PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
July | 2 | 5PM to 6PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
July | 2 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 2 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 2 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 2 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 2 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 2 | 11PM to 12AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 3 | 12AM to 1AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 3 | 1AM to 2AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
July | 3 | 2AM to 3AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
July | 3 | 3AM to 4AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 3 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 3 | 5AM to 6AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 3 | 6AM to 7AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
July | 3 | 7AM to 8AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
July | 3 | 8AM to 9AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
July | 3 | 9AM to 10AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
July | 3 | 10AM to 11AM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
July | 3 | 11AM to 12PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
July | 3 | 12PM to 1PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
July | 3 | 1PM to 2PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
July | 3 | 2PM to 3PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
July | 3 | 3PM to 4PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
July | 3 | 4PM to 5PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
July | 3 | 5PM to 6PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
July | 3 | 6PM to 7PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
July | 3 | 7PM to 8PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
July | 3 | 8PM to 9PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
July | 3 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 3 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 3 | 11PM to 12AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 4 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 4 | 1AM to 2AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
July | 4 | 2AM to 3AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 4 | 3AM to 4AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
July | 4 | 4AM to 5AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
July | 4 | 5AM to 6AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 4 | 6AM to 7AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 4 | 7AM to 8AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
July | 4 | 8AM to 9AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
July | 4 | 9AM to 10AM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
July | 4 | 10AM to 11AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
July | 4 | 11AM to 12PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
July | 4 | 12PM to 1PM | 87.1 | 70.6 | 63 | 86.4 | 34.47 | 0.072 | 0.58 | 14.05 | 0
July | 4 | 1PM to 2PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
July | 4 | 2PM to 3PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
July | 4 | 3PM to 4PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 4 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
July | 4 | 5PM to 6PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
July | 4 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 4 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 4 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 4 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 4 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 4 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 5 | 12AM to 1AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 5 | 1AM to 2AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 5 | 2AM to 3AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 5 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 5 | 4AM to 5AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 5 | 5AM to 6AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 5 | 6AM to 7AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 5 | 7AM to 8AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 5 | 8AM to 9AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
July | 5 | 9AM to 10AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
July | 5 | 10AM to 11AM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
July | 5 | 11AM to 12PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
July | 5 | 12PM to 1PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
July | 5 | 1PM to 2PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
July | 5 | 2PM to 3PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 5 | 3PM to 4PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
July | 5 | 4PM to 5PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
July | 5 | 5PM to 6PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
July | 5 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
July | 5 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 5 | 8PM to 9PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 5 | 9PM to 10PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 5 | 10PM to 11PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 5 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 6 | 12AM to 1AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 6 | 1AM to 2AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 6 | 2AM to 3AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 6 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 6 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 6 | 5AM to 6AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 6 | 6AM to 7AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
July | 6 | 7AM to 8AM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
July | 6 | 8AM to 9AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
July | 6 | 9AM to 10AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
July | 6 | 10AM to 11AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
July | 6 | 11AM to 12PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 6 | 12PM to 1PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
July | 6 | 1PM to 2PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
July | 6 | 2PM to 3PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
July | 6 | 3PM to 4PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 6 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
July | 6 | 5PM to 6PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
July | 6 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
July | 6 | 7PM to 8PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 6 | 8PM to 9PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 6 | 9PM to 10PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 6 | 10PM to 11PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 6 | 11PM to 12AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 7 | 12AM to 1AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 7 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 7 | 2AM to 3AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 7 | 3AM to 4AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 7 | 4AM to 5AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 7 | 5AM to 6AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 7 | 6AM to 7AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 7 | 7AM to 8AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 7 | 8AM to 9AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
July | 7 | 9AM to 10AM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
July | 7 | 10AM to 11AM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
July | 7 | 11AM to 12PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
July | 7 | 12PM to 1PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
July | 7 | 1PM to 2PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 7 | 2PM to 3PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 7 | 3PM to 4PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
July | 7 | 4PM to 5PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
July | 7 | 5PM to 6PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
July | 7 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 7 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 7 | 8PM to 9PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
July | 7 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 7 | 10PM to 11PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 7 | 11PM to 12AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
July | 8 | 12AM to 1AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 8 | 1AM to 2AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 8 | 2AM to 3AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 8 | 3AM to 4AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 8 | 4AM to 5AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
July | 8 | 5AM to 6AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
July | 8 | 6AM to 7AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 8 | 7AM to 8AM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
July | 8 | 8AM to 9AM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
July | 8 | 9AM to 10AM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
July | 8 | 10AM to 11AM | 87.1 | 70.6 | 63 | 86.4 | 34.47 | 0.072 | 0.58 | 14.05 | 0
July | 8 | 11AM to 12PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
July | 8 | 12PM to 1PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
July | 8 | 1PM to 2PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
July | 8 | 2PM to 3PM | 88 | 70.9 | 63 | 86.4 | 34.69 | 0.0719 | 0.58 | 14.08 | 0
July | 8 | 3PM to 4PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 8 | 4PM to 5PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
July | 8 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
July | 8 | 6PM to 7PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
July | 8 | 7PM to 8PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 8 | 8PM to 9PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 8 | 9PM to 10PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
July | 8 | 10PM to 11PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
July | 8 | 11PM to 12AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 9 | 12AM to 1AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 9 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 9 | 2AM to 3AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
July | 9 | 3AM to 4AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
July | 9 | 4AM to 5AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
July | 9 | 5AM to 6AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 9 | 6AM to 7AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 9 | 7AM to 8AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
July | 9 | 8AM to 9AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
July | 9 | 9AM to 10AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
July | 9 | 10AM to 11AM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
July | 9 | 11AM to 12PM | 90 | 74.4 | 68 | 103.3 | 37.84 | 0.0716 | 0.69 | 14.18 | 0
July | 9 | 12PM to 1PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
July | 9 | 1PM to 2PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
July | 9 | 2PM to 3PM | 89.1 | 72.9 | 66 | 96.3 | 36.52 | 0.0717 | 0.64 | 14.14 | 0
July | 9 | 3PM to 4PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 9 | 4PM to 5PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
July | 9 | 5PM to 6PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
July | 9 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 9 | 7PM to 8PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
July | 9 | 8PM to 9PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 9 | 9PM to 10PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 9 | 10PM to 11PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 9 | 11PM to 12AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 10 | 12AM to 1AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 10 | 1AM to 2AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 10 | 2AM to 3AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 10 | 3AM to 4AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 10 | 4AM to 5AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 10 | 5AM to 6AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
July | 10 | 6AM to 7AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 10 | 7AM to 8AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 10 | 8AM to 9AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
July | 10 | 9AM to 10AM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
July | 10 | 10AM to 11AM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
July | 10 | 11AM to 12PM | 89.1 | 74.1 | 68 | 103.3 | 37.62 | 0.0717 | 0.69 | 14.16 | 0
July | 10 | 12PM to 1PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
July | 10 | 1PM to 2PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
July | 10 | 2PM to 3PM | 89.1 | 74.8 | 69.1 | 107.3 | 38.25 | 0.0716 | 0.72 | 14.17 | 0
July | 10 | 3PM to 4PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
July | 10 | 4PM to 5PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
July | 10 | 5PM to 6PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
July | 10 | 6PM to 7PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 10 | 7PM to 8PM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
July | 10 | 8PM to 9PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 10 | 9PM to 10PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
July | 10 | 10PM to 11PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 10 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 11 | 12AM to 1AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 11 | 1AM to 2AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 11 | 2AM to 3AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
July | 11 | 3AM to 4AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
July | 11 | 4AM to 5AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
July | 11 | 5AM to 6AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 11 | 6AM to 7AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 11 | 7AM to 8AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
July | 11 | 8AM to 9AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
July | 11 | 9AM to 10AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
July | 11 | 10AM to 11AM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 11 | 11AM to 12PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
July | 11 | 12PM to 1PM | 89.1 | 74.1 | 68 | 103.3 | 37.62 | 0.0717 | 0.69 | 14.16 | 0
July | 11 | 1PM to 2PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
July | 11 | 2PM to 3PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
July | 11 | 3PM to 4PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
July | 11 | 4PM to 5PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
July | 11 | 5PM to 6PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
July | 11 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
July | 11 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 11 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 11 | 9PM to 10PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 11 | 10PM to 11PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 11 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 12 | 12AM to 1AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 12 | 1AM to 2AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 12 | 2AM to 3AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 12 | 3AM to 4AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
July | 12 | 4AM to 5AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 12 | 5AM to 6AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 12 | 6AM to 7AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
July | 12 | 7AM to 8AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
July | 12 | 8AM to 9AM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
July | 12 | 9AM to 10AM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 12 | 10AM to 11AM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 12 | 11AM to 12PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
July | 12 | 12PM to 1PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
July | 12 | 1PM to 2PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
July | 12 | 2PM to 3PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
July | 12 | 3PM to 4PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 12 | 4PM to 5PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
July | 12 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
July | 12 | 6PM to 7PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
July | 12 | 7PM to 8PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
July | 12 | 8PM to 9PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 12 | 9PM to 10PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 12 | 10PM to 11PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 12 | 11PM to 12AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 13 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 13 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 13 | 2AM to 3AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
July | 13 | 3AM to 4AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
July | 13 | 4AM to 5AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 13 | 5AM to 6AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
July | 13 | 6AM to 7AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 13 | 7AM to 8AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 13 | 8AM to 9AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
July | 13 | 9AM to 10AM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
July | 13 | 10AM to 11AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
July | 13 | 11AM to 12PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 13 | 12PM to 1PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
July | 13 | 1PM to 2PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
July | 13 | 2PM to 3PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 13 | 3PM to 4PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 13 | 4PM to 5PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
July | 13 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
July | 13 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 13 | 7PM to 8PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 13 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 13 | 9PM to 10PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 13 | 10PM to 11PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 13 | 11PM to 12AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 14 | 12AM to 1AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 14 | 1AM to 2AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
July | 14 | 2AM to 3AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 14 | 3AM to 4AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 14 | 4AM to 5AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 14 | 5AM to 6AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 14 | 6AM to 7AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 14 | 7AM to 8AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
July | 14 | 8AM to 9AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
July | 14 | 9AM to 10AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
July | 14 | 10AM to 11AM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
July | 14 | 11AM to 12PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
July | 14 | 12PM to 1PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
July | 14 | 1PM to 2PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
July | 14 | 2PM to 3PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
July | 14 | 3PM to 4PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
July | 14 | 4PM to 5PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
July | 14 | 5PM to 6PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
July | 14 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
July | 14 | 7PM to 8PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
July | 14 | 8PM to 9PM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
July | 14 | 9PM to 10PM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
July | 14 | 10PM to 11PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
July | 14 | 11PM to 12AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
July | 15 | 12AM to 1AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 15 | 1AM to 2AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 15 | 2AM to 3AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
July | 15 | 3AM to 4AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 15 | 4AM to 5AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 15 | 5AM to 6AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 15 | 6AM to 7AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 15 | 7AM to 8AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
July | 15 | 8AM to 9AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
July | 15 | 9AM to 10AM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
July | 15 | 10AM to 11AM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
July | 15 | 11AM to 12PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
July | 15 | 12PM to 1PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
July | 15 | 1PM to 2PM | 89.1 | 74.8 | 69.1 | 107.3 | 38.25 | 0.0716 | 0.72 | 14.17 | 0
July | 15 | 2PM to 3PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
July | 15 | 3PM to 4PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
July | 15 | 4PM to 5PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
July | 15 | 5PM to 6PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
July | 15 | 6PM to 7PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
July | 15 | 7PM to 8PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
July | 15 | 8PM to 9PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
July | 15 | 9PM to 10PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 15 | 10PM to 11PM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
July | 15 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 16 | 12AM to 1AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
July | 16 | 1AM to 2AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 16 | 2AM to 3AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 16 | 3AM to 4AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 16 | 4AM to 5AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 16 | 5AM to 6AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 16 | 6AM to 7AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 16 | 7AM to 8AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 16 | 8AM to 9AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
July | 16 | 9AM to 10AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
July | 16 | 10AM to 11AM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 16 | 11AM to 12PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 16 | 12PM to 1PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
July | 16 | 1PM to 2PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 16 | 2PM to 3PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
July | 16 | 3PM to 4PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
July | 16 | 4PM to 5PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
July | 16 | 5PM to 6PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
July | 16 | 6PM to 7PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
July | 16 | 7PM to 8PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
July | 16 | 8PM to 9PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 16 | 9PM to 10PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 16 | 10PM to 11PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 16 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 17 | 12AM to 1AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 17 | 1AM to 2AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 17 | 2AM to 3AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 17 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
July | 17 | 4AM to 5AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 17 | 5AM to 6AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 17 | 6AM to 7AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 17 | 7AM to 8AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
July | 17 | 8AM to 9AM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
July | 17 | 9AM to 10AM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
July | 17 | 10AM to 11AM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
July | 17 | 11AM to 12PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
July | 17 | 12PM to 1PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
July | 17 | 1PM to 2PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
July | 17 | 2PM to 3PM | 88 | 75 | 70 | 110.8 | 38.52 | 0.0718 | 0.74 | 14.15 | 0
July | 17 | 3PM to 4PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
July | 17 | 4PM to 5PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
July | 17 | 5PM to 6PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
July | 17 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 17 | 7PM to 8PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 17 | 8PM to 9PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
July | 17 | 9PM to 10PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
July | 17 | 10PM to 11PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 17 | 11PM to 12AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 18 | 12AM to 1AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 18 | 1AM to 2AM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
July | 18 | 2AM to 3AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 18 | 3AM to 4AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 18 | 4AM to 5AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 18 | 5AM to 6AM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
July | 18 | 6AM to 7AM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
July | 18 | 7AM to 8AM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
July | 18 | 8AM to 9AM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
July | 18 | 9AM to 10AM | 86 | 68.7 | 60.1 | 77.8 | 32.86 | 0.0722 | 0.52 | 14 | 0
July | 18 | 10AM to 11AM | 87.1 | 70.1 | 62.1 | 83.6 | 34.04 | 0.072 | 0.56 | 14.05 | 0
July | 18 | 11AM to 12PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
July | 18 | 12PM to 1PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
July | 18 | 1PM to 2PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
July | 18 | 2PM to 3PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
July | 18 | 3PM to 4PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
July | 18 | 4PM to 5PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
July | 18 | 5PM to 6PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
July | 18 | 6PM to 7PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
July | 18 | 7PM to 8PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
July | 18 | 8PM to 9PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
July | 18 | 9PM to 10PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
July | 18 | 10PM to 11PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 18 | 11PM to 12AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 19 | 12AM to 1AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
July | 19 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 19 | 2AM to 3AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 19 | 3AM to 4AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 19 | 4AM to 5AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 19 | 5AM to 6AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
July | 19 | 6AM to 7AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 19 | 7AM to 8AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 19 | 8AM to 9AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
July | 19 | 9AM to 10AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
July | 19 | 10AM to 11AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 19 | 11AM to 12PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 19 | 12PM to 1PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
July | 19 | 1PM to 2PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
July | 19 | 2PM to 3PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
July | 19 | 3PM to 4PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
July | 19 | 4PM to 5PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
July | 19 | 5PM to 6PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
July | 19 | 6PM to 7PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
July | 19 | 7PM to 8PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
July | 19 | 8PM to 9PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 19 | 9PM to 10PM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
July | 19 | 10PM to 11PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 19 | 11PM to 12AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 20 | 12AM to 1AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
July | 20 | 1AM to 2AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 20 | 2AM to 3AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
July | 20 | 3AM to 4AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
July | 20 | 4AM to 5AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
July | 20 | 5AM to 6AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
July | 20 | 6AM to 7AM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
July | 20 | 7AM to 8AM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
July | 20 | 8AM to 9AM | 84 | 75.3 | 72 | 118.7 | 38.79 | 0.0722 | 0.79 | 14.08 | 0
July | 20 | 9AM to 10AM | 78.1 | 75.1 | 73.9 | 127.1 | 38.63 | 0.073 | 0.85 | 13.95 | 0
July | 20 | 10AM to 11AM | 82 | 75.5 | 73 | 123.2 | 39.01 | 0.0725 | 0.82 | 14.04 | 0
July | 20 | 11AM to 12PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
July | 20 | 12PM to 1PM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
July | 20 | 1PM to 2PM | 80.1 | 76.3 | 75 | 131.9 | 39.88 | 0.0727 | 0.88 | 14.02 | 0
July | 20 | 2PM to 3PM | 80.1 | 75 | 73 | 123.2 | 38.52 | 0.0727 | 0.82 | 13.99 | 0
July | 20 | 3PM to 4PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
July | 20 | 4PM to 5PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
July | 20 | 5PM to 6PM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
July | 20 | 6PM to 7PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 20 | 7PM to 8PM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
July | 20 | 8PM to 9PM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
July | 20 | 9PM to 10PM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
July | 20 | 10PM to 11PM | 73.9 | 73.3 | 73 | 123.2 | 37 | 0.0736 | 0.82 | 13.83 | 0
July | 20 | 11PM to 12AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
July | 21 | 12AM to 1AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
July | 21 | 1AM to 2AM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
July | 21 | 2AM to 3AM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
July | 21 | 3AM to 4AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
July | 21 | 4AM to 5AM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
July | 21 | 5AM to 6AM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
July | 21 | 6AM to 7AM | 77 | 74.1 | 73 | 123.2 | 37.76 | 0.0732 | 0.82 | 13.91 | 0
July | 21 | 7AM to 8AM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
July | 21 | 8AM to 9AM | 80.1 | 75 | 73 | 123.2 | 38.52 | 0.0727 | 0.82 | 13.99 | 0
July | 21 | 9AM to 10AM | 80.1 | 75 | 73 | 123.2 | 38.52 | 0.0727 | 0.82 | 13.99 | 0
July | 21 | 10AM to 11AM | 82 | 75.5 | 73 | 123.2 | 39.01 | 0.0725 | 0.82 | 14.04 | 0
July | 21 | 11AM to 12PM | 84 | 76 | 73 | 123.2 | 39.5 | 0.0722 | 0.82 | 14.09 | 0
July | 21 | 12PM to 1PM | 84.9 | 75.5 | 72 | 118.7 | 39.01 | 0.0721 | 0.79 | 14.1 | 0
July | 21 | 1PM to 2PM | 86 | 75.8 | 72 | 118.7 | 39.28 | 0.072 | 0.79 | 14.13 | 0
July | 21 | 2PM to 3PM | 84.9 | 75.5 | 72 | 118.7 | 39.01 | 0.0721 | 0.79 | 14.1 | 0
July | 21 | 3PM to 4PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
July | 21 | 4PM to 5PM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
July | 21 | 5PM to 6PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
July | 21 | 6PM to 7PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
July | 21 | 7PM to 8PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
July | 21 | 8PM to 9PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
July | 21 | 9PM to 10PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
July | 21 | 10PM to 11PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
July | 21 | 11PM to 12AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
July | 22 | 12AM to 1AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 22 | 1AM to 2AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 22 | 2AM to 3AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 22 | 3AM to 4AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 22 | 4AM to 5AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 22 | 5AM to 6AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 22 | 6AM to 7AM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
July | 22 | 7AM to 8AM | 79 | 66.5 | 60.1 | 77.8 | 31.14 | 0.0732 | 0.52 | 13.82 | 0
July | 22 | 8AM to 9AM | 82 | 75.5 | 73 | 123.2 | 39.01 | 0.0725 | 0.82 | 14.04 | 0
July | 22 | 9AM to 10AM | 79 | 76.1 | 75 | 131.9 | 39.61 | 0.0728 | 0.88 | 13.99 | 0
July | 22 | 10AM to 11AM | 84 | 76 | 73 | 123.2 | 39.5 | 0.0722 | 0.82 | 14.09 | 0
July | 22 | 11AM to 12PM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
July | 22 | 12PM to 1PM | 84.9 | 75.5 | 72 | 118.7 | 39.01 | 0.0721 | 0.79 | 14.1 | 0
July | 22 | 1PM to 2PM | 82.9 | 75 | 72 | 118.7 | 38.52 | 0.0724 | 0.79 | 14.05 | 0
July | 22 | 2PM to 3PM | 82 | 74.7 | 72 | 118.7 | 38.3 | 0.0725 | 0.79 | 14.03 | 0
July | 22 | 3PM to 4PM | 84.9 | 76.2 | 73 | 123.2 | 39.72 | 0.0721 | 0.82 | 14.12 | 0
July | 22 | 4PM to 5PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
July | 22 | 5PM to 6PM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
July | 22 | 6PM to 7PM | 78.1 | 75.1 | 73.9 | 127.1 | 38.63 | 0.073 | 0.85 | 13.95 | 0
July | 22 | 7PM to 8PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
July | 22 | 8PM to 9PM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
July | 22 | 9PM to 10PM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
July | 22 | 10PM to 11PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 22 | 11PM to 12AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
July | 23 | 12AM to 1AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 23 | 1AM to 2AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 23 | 2AM to 3AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 23 | 3AM to 4AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
July | 23 | 4AM to 5AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
July | 23 | 5AM to 6AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
July | 23 | 6AM to 7AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
July | 23 | 7AM to 8AM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
July | 23 | 8AM to 9AM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
July | 23 | 9AM to 10AM | 84.9 | 74.9 | 71.1 | 115 | 38.43 | 0.0721 | 0.77 | 14.09 | 0
July | 23 | 10AM to 11AM | 87.1 | 75.5 | 71.1 | 115 | 38.97 | 0.0719 | 0.77 | 14.15 | 0
July | 23 | 11AM to 12PM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
July | 23 | 12PM to 1PM | 84.9 | 74.9 | 71.1 | 115 | 38.43 | 0.0721 | 0.77 | 14.09 | 0
July | 23 | 1PM to 2PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
July | 23 | 2PM to 3PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
July | 23 | 3PM to 4PM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
July | 23 | 4PM to 5PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
July | 23 | 5PM to 6PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
July | 23 | 6PM to 7PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
July | 23 | 7PM to 8PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
July | 23 | 8PM to 9PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 23 | 9PM to 10PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
July | 23 | 10PM to 11PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
July | 23 | 11PM to 12AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
July | 24 | 12AM to 1AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
July | 24 | 1AM to 2AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 24 | 2AM to 3AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 24 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 24 | 4AM to 5AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 24 | 5AM to 6AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 24 | 6AM to 7AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
July | 24 | 7AM to 8AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
July | 24 | 8AM to 9AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
July | 24 | 9AM to 10AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
July | 24 | 10AM to 11AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 24 | 11AM to 12PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 24 | 12PM to 1PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
July | 24 | 1PM to 2PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
July | 24 | 2PM to 3PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
July | 24 | 3PM to 4PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
July | 24 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
July | 24 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
July | 24 | 6PM to 7PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
July | 24 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
July | 24 | 8PM to 9PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 24 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 24 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 24 | 11PM to 12AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 25 | 12AM to 1AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 25 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 25 | 2AM to 3AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 25 | 3AM to 4AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 25 | 4AM to 5AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 25 | 5AM to 6AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
July | 25 | 6AM to 7AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 25 | 7AM to 8AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 25 | 8AM to 9AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
July | 25 | 9AM to 10AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
July | 25 | 10AM to 11AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
July | 25 | 11AM to 12PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 25 | 12PM to 1PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
July | 25 | 1PM to 2PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 25 | 2PM to 3PM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
July | 25 | 3PM to 4PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
July | 25 | 4PM to 5PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
July | 25 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
July | 25 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
July | 25 | 7PM to 8PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 25 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 25 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 25 | 10PM to 11PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 25 | 11PM to 12AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
July | 26 | 12AM to 1AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
July | 26 | 1AM to 2AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
July | 26 | 2AM to 3AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
July | 26 | 3AM to 4AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
July | 26 | 4AM to 5AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
July | 26 | 5AM to 6AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
July | 26 | 6AM to 7AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 26 | 7AM to 8AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
July | 26 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
July | 26 | 9AM to 10AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
July | 26 | 10AM to 11AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 26 | 11AM to 12PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 26 | 12PM to 1PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 26 | 1PM to 2PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
July | 26 | 2PM to 3PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 26 | 3PM to 4PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
July | 26 | 4PM to 5PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
July | 26 | 5PM to 6PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
July | 26 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 26 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 26 | 8PM to 9PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 26 | 9PM to 10PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 26 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 26 | 11PM to 12AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 27 | 12AM to 1AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 27 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 27 | 2AM to 3AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 27 | 3AM to 4AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 27 | 4AM to 5AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 27 | 5AM to 6AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 27 | 6AM to 7AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 27 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
July | 27 | 8AM to 9AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
July | 27 | 9AM to 10AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 27 | 10AM to 11AM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
July | 27 | 11AM to 12PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 27 | 12PM to 1PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
July | 27 | 1PM to 2PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 27 | 2PM to 3PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
July | 27 | 3PM to 4PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
July | 27 | 4PM to 5PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
July | 27 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
July | 27 | 6PM to 7PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
July | 27 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 27 | 8PM to 9PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 27 | 9PM to 10PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 27 | 10PM to 11PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 27 | 11PM to 12AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
July | 28 | 12AM to 1AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 28 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 28 | 2AM to 3AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 28 | 3AM to 4AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 28 | 4AM to 5AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
July | 28 | 5AM to 6AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 28 | 6AM to 7AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 28 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
July | 28 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
July | 28 | 9AM to 10AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
July | 28 | 10AM to 11AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
July | 28 | 11AM to 12PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
July | 28 | 12PM to 1PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
July | 28 | 1PM to 2PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
July | 28 | 2PM to 3PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
July | 28 | 3PM to 4PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
July | 28 | 4PM to 5PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
July | 28 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
July | 28 | 6PM to 7PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
July | 28 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
July | 28 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 28 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 28 | 10PM to 11PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 28 | 11PM to 12AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 29 | 12AM to 1AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
July | 29 | 1AM to 2AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 29 | 2AM to 3AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 29 | 3AM to 4AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 29 | 4AM to 5AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 29 | 5AM to 6AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
July | 29 | 6AM to 7AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
July | 29 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
July | 29 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
July | 29 | 9AM to 10AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
July | 29 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
July | 29 | 11AM to 12PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 29 | 12PM to 1PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 29 | 1PM to 2PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
July | 29 | 2PM to 3PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 29 | 3PM to 4PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
July | 29 | 4PM to 5PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
July | 29 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
July | 29 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 29 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
July | 29 | 8PM to 9PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 29 | 9PM to 10PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 29 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 29 | 11PM to 12AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 30 | 12AM to 1AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
July | 30 | 1AM to 2AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
July | 30 | 2AM to 3AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 30 | 3AM to 4AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 30 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 30 | 5AM to 6AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
July | 30 | 6AM to 7AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 30 | 7AM to 8AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
July | 30 | 8AM to 9AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
July | 30 | 9AM to 10AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
July | 30 | 10AM to 11AM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
July | 30 | 11AM to 12PM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
July | 30 | 12PM to 1PM | 88 | 70.4 | 62.1 | 83.6 | 34.26 | 0.0719 | 0.56 | 14.07 | 0
July | 30 | 1PM to 2PM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
July | 30 | 2PM to 3PM | 86 | 69.8 | 62.1 | 83.6 | 33.77 | 0.0722 | 0.56 | 14.02 | 0
July | 30 | 3PM to 4PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
July | 30 | 4PM to 5PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
July | 30 | 5PM to 6PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
July | 30 | 6PM to 7PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
July | 30 | 7PM to 8PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
July | 30 | 8PM to 9PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
July | 30 | 9PM to 10PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 30 | 10PM to 11PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 30 | 11PM to 12AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
July | 31 | 12AM to 1AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 31 | 1AM to 2AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
July | 31 | 2AM to 3AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
July | 31 | 3AM to 4AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 31 | 4AM to 5AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
July | 31 | 5AM to 6AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
July | 31 | 6AM to 7AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
July | 31 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 31 | 8AM to 9AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
July | 31 | 9AM to 10AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
July | 31 | 10AM to 11AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
July | 31 | 11AM to 12PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
July | 31 | 12PM to 1PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
July | 31 | 1PM to 2PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
July | 31 | 2PM to 3PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
July | 31 | 3PM to 4PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
July | 31 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
July | 31 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
July | 31 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
July | 31 | 7PM to 8PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
July | 31 | 8PM to 9PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
July | 31 | 9PM to 10PM | 76.8 | 70.2 | 67.3 | 100.7 | 34.19 | 0.0733 | 0.67 | 13.84 | 0
July | 31 | 10PM to 11PM | 76.6 | 70.3 | 67.5 | 101.4 | 34.25 | 0.0733 | 0.68 | 13.83 | 0
July | 31 | 11PM to 12AM | 76.5 | 70.4 | 67.8 | 102.7 | 34.41 | 0.0734 | 0.69 | 13.83 | 0
August | 1 | 12AM to 1AM | 76.5 | 70.7 | 68.2 | 104 | 34.61 | 0.0733 | 0.69 | 13.84 | 0
August | 1 | 1AM to 2AM | 76.3 | 70.9 | 68.5 | 105.3 | 34.78 | 0.0734 | 0.7 | 13.84 | 0
August | 1 | 2AM to 3AM | 76.1 | 70.9 | 68.7 | 106 | 34.84 | 0.0734 | 0.71 | 13.83 | 0
August | 1 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
August | 1 | 4AM to 5AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
August | 1 | 5AM to 6AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 1 | 6AM to 7AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 1 | 7AM to 8AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
August | 1 | 8AM to 9AM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
August | 1 | 9AM to 10AM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
August | 1 | 10AM to 11AM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
August | 1 | 11AM to 12PM | 89.1 | 74.8 | 69.1 | 107.3 | 38.25 | 0.0716 | 0.72 | 14.17 | 0
August | 1 | 12PM to 1PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
August | 1 | 1PM to 2PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
August | 1 | 2PM to 3PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
August | 1 | 3PM to 4PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
August | 1 | 4PM to 5PM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
August | 1 | 5PM to 6PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
August | 1 | 6PM to 7PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
August | 1 | 7PM to 8PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
August | 1 | 8PM to 9PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
August | 1 | 9PM to 10PM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
August | 1 | 10PM to 11PM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
August | 1 | 11PM to 12AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
August | 2 | 12AM to 1AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 2 | 1AM to 2AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 2 | 2AM to 3AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 2 | 3AM to 4AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 2 | 4AM to 5AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 2 | 5AM to 6AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 2 | 6AM to 7AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 2 | 7AM to 8AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
August | 2 | 8AM to 9AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
August | 2 | 9AM to 10AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 2 | 10AM to 11AM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
August | 2 | 11AM to 12PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
August | 2 | 12PM to 1PM | 88 | 70.9 | 63 | 86.4 | 34.69 | 0.0719 | 0.58 | 14.08 | 0
August | 2 | 1PM to 2PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 2 | 2PM to 3PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
August | 2 | 3PM to 4PM | 87.1 | 70.1 | 62.1 | 83.6 | 34.04 | 0.072 | 0.56 | 14.05 | 0
August | 2 | 4PM to 5PM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
August | 2 | 5PM to 6PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
August | 2 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
August | 2 | 7PM to 8PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
August | 2 | 8PM to 9PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
August | 2 | 9PM to 10PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
August | 2 | 10PM to 11PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
August | 2 | 11PM to 12AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 3 | 12AM to 1AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
August | 3 | 1AM to 2AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
August | 3 | 2AM to 3AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 3 | 3AM to 4AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
August | 3 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 3 | 5AM to 6AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
August | 3 | 6AM to 7AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 3 | 7AM to 8AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 3 | 8AM to 9AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
August | 3 | 9AM to 10AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 3 | 10AM to 11AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
August | 3 | 11AM to 12PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
August | 3 | 12PM to 1PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
August | 3 | 1PM to 2PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
August | 3 | 2PM to 3PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 3 | 3PM to 4PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
August | 3 | 4PM to 5PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
August | 3 | 5PM to 6PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
August | 3 | 6PM to 7PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 3 | 7PM to 8PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 3 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 3 | 9PM to 10PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 3 | 10PM to 11PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
August | 3 | 11PM to 12AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 4 | 12AM to 1AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 4 | 1AM to 2AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 4 | 2AM to 3AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
August | 4 | 3AM to 4AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
August | 4 | 4AM to 5AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
August | 4 | 5AM to 6AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 4 | 6AM to 7AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 4 | 7AM to 8AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 4 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
August | 4 | 9AM to 10AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 4 | 10AM to 11AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 4 | 11AM to 12PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
August | 4 | 12PM to 1PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
August | 4 | 1PM to 2PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
August | 4 | 2PM to 3PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
August | 4 | 3PM to 4PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 4 | 4PM to 5PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
August | 4 | 5PM to 6PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
August | 4 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 4 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 4 | 8PM to 9PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 4 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 4 | 10PM to 11PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 4 | 11PM to 12AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 5 | 12AM to 1AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 5 | 1AM to 2AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
August | 5 | 2AM to 3AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 5 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
August | 5 | 4AM to 5AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 5 | 5AM to 6AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 5 | 6AM to 7AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 5 | 7AM to 8AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 5 | 8AM to 9AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
August | 5 | 9AM to 10AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
August | 5 | 10AM to 11AM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
August | 5 | 11AM to 12PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
August | 5 | 12PM to 1PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
August | 5 | 1PM to 2PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 5 | 2PM to 3PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
August | 5 | 3PM to 4PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 5 | 4PM to 5PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
August | 5 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
August | 5 | 6PM to 7PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
August | 5 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 5 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 5 | 9PM to 10PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 5 | 10PM to 11PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
August | 5 | 11PM to 12AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
August | 6 | 12AM to 1AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 6 | 1AM to 2AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 6 | 2AM to 3AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 6 | 3AM to 4AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 6 | 4AM to 5AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 6 | 5AM to 6AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
August | 6 | 6AM to 7AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
August | 6 | 7AM to 8AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
August | 6 | 8AM to 9AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 6 | 9AM to 10AM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
August | 6 | 10AM to 11AM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
August | 6 | 11AM to 12PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
August | 6 | 12PM to 1PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
August | 6 | 1PM to 2PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
August | 6 | 2PM to 3PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
August | 6 | 3PM to 4PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 6 | 4PM to 5PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
August | 6 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
August | 6 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
August | 6 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 6 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 6 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 6 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 6 | 11PM to 12AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
August | 7 | 12AM to 1AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 7 | 1AM to 2AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 7 | 2AM to 3AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 7 | 3AM to 4AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 7 | 4AM to 5AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 7 | 5AM to 6AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
August | 7 | 6AM to 7AM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
August | 7 | 7AM to 8AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
August | 7 | 8AM to 9AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
August | 7 | 9AM to 10AM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
August | 7 | 10AM to 11AM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
August | 7 | 11AM to 12PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
August | 7 | 12PM to 1PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
August | 7 | 1PM to 2PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 7 | 2PM to 3PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
August | 7 | 3PM to 4PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
August | 7 | 4PM to 5PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
August | 7 | 5PM to 6PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
August | 7 | 6PM to 7PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
August | 7 | 7PM to 8PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
August | 7 | 8PM to 9PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 7 | 9PM to 10PM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
August | 7 | 10PM to 11PM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
August | 7 | 11PM to 12AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 8 | 12AM to 1AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 8 | 1AM to 2AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
August | 8 | 2AM to 3AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 8 | 3AM to 4AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 8 | 4AM to 5AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 8 | 5AM to 6AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 8 | 6AM to 7AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 8 | 7AM to 8AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 8 | 8AM to 9AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
August | 8 | 9AM to 10AM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
August | 8 | 10AM to 11AM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
August | 8 | 11AM to 12PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
August | 8 | 12PM to 1PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
August | 8 | 1PM to 2PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
August | 8 | 2PM to 3PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
August | 8 | 3PM to 4PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
August | 8 | 4PM to 5PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 8 | 5PM to 6PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
August | 8 | 6PM to 7PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
August | 8 | 7PM to 8PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 8 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 8 | 9PM to 10PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 8 | 10PM to 11PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 8 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 9 | 12AM to 1AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
August | 9 | 1AM to 2AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
August | 9 | 2AM to 3AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
August | 9 | 3AM to 4AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 9 | 4AM to 5AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 9 | 5AM to 6AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 9 | 6AM to 7AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 9 | 7AM to 8AM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
August | 9 | 8AM to 9AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
August | 9 | 9AM to 10AM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
August | 9 | 10AM to 11AM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
August | 9 | 11AM to 12PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
August | 9 | 12PM to 1PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
August | 9 | 1PM to 2PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
August | 9 | 2PM to 3PM | 90 | 73.7 | 66.9 | 99.5 | 37.23 | 0.0716 | 0.67 | 14.17 | 0
August | 9 | 3PM to 4PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
August | 9 | 4PM to 5PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
August | 9 | 5PM to 6PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
August | 9 | 6PM to 7PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
August | 9 | 7PM to 8PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 9 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 9 | 9PM to 10PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 9 | 10PM to 11PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 9 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 10 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 10 | 1AM to 2AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 10 | 2AM to 3AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 10 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 10 | 4AM to 5AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 10 | 5AM to 6AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 10 | 6AM to 7AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 10 | 7AM to 8AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 10 | 8AM to 9AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
August | 10 | 9AM to 10AM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
August | 10 | 10AM to 11AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 10 | 11AM to 12PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 10 | 12PM to 1PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
August | 10 | 1PM to 2PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
August | 10 | 2PM to 3PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 10 | 3PM to 4PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
August | 10 | 4PM to 5PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
August | 10 | 5PM to 6PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
August | 10 | 6PM to 7PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
August | 10 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 10 | 8PM to 9PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 10 | 9PM to 10PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 10 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 10 | 11PM to 12AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 11 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 11 | 1AM to 2AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 11 | 2AM to 3AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 11 | 3AM to 4AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
August | 11 | 4AM to 5AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
August | 11 | 5AM to 6AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
August | 11 | 6AM to 7AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
August | 11 | 7AM to 8AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
August | 11 | 8AM to 9AM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
August | 11 | 9AM to 10AM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
August | 11 | 10AM to 11AM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
August | 11 | 11AM to 12PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
August | 11 | 12PM to 1PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
August | 11 | 1PM to 2PM | 91 | 74 | 66.9 | 99.5 | 37.5 | 0.0714 | 0.67 | 14.2 | 0
August | 11 | 2PM to 3PM | 89.1 | 74.1 | 68 | 103.3 | 37.62 | 0.0717 | 0.69 | 14.16 | 0
August | 11 | 3PM to 4PM | 89.1 | 74.8 | 69.1 | 107.3 | 38.25 | 0.0716 | 0.72 | 14.17 | 0
August | 11 | 4PM to 5PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
August | 11 | 5PM to 6PM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
August | 11 | 6PM to 7PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
August | 11 | 7PM to 8PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
August | 11 | 8PM to 9PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
August | 11 | 9PM to 10PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
August | 11 | 10PM to 11PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 11 | 11PM to 12AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 12 | 12AM to 1AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 12 | 1AM to 2AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 12 | 2AM to 3AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 12 | 3AM to 4AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 12 | 4AM to 5AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 12 | 5AM to 6AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 12 | 6AM to 7AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 12 | 7AM to 8AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
August | 12 | 8AM to 9AM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
August | 12 | 9AM to 10AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
August | 12 | 10AM to 11AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
August | 12 | 11AM to 12PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 12 | 12PM to 1PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 12 | 1PM to 2PM | 89.1 | 72.9 | 66 | 96.3 | 36.52 | 0.0717 | 0.64 | 14.14 | 0
August | 12 | 2PM to 3PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
August | 12 | 3PM to 4PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
August | 12 | 4PM to 5PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 12 | 5PM to 6PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
August | 12 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
August | 12 | 7PM to 8PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 12 | 8PM to 9PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 12 | 9PM to 10PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 12 | 10PM to 11PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 12 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 13 | 12AM to 1AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 13 | 1AM to 2AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
August | 13 | 2AM to 3AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
August | 13 | 3AM to 4AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
August | 13 | 4AM to 5AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
August | 13 | 5AM to 6AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
August | 13 | 6AM to 7AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
August | 13 | 7AM to 8AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 13 | 8AM to 9AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
August | 13 | 9AM to 10AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 13 | 10AM to 11AM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
August | 13 | 11AM to 12PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 13 | 12PM to 1PM | 90 | 73.2 | 66 | 96.3 | 36.74 | 0.0716 | 0.64 | 14.16 | 0
August | 13 | 1PM to 2PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 13 | 2PM to 3PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
August | 13 | 3PM to 4PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
August | 13 | 4PM to 5PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 13 | 5PM to 6PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
August | 13 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 13 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 13 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 13 | 9PM to 10PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 13 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 13 | 11PM to 12AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 14 | 12AM to 1AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 14 | 1AM to 2AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 14 | 2AM to 3AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 14 | 3AM to 4AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
August | 14 | 4AM to 5AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
August | 14 | 5AM to 6AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
August | 14 | 6AM to 7AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
August | 14 | 7AM to 8AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
August | 14 | 8AM to 9AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
August | 14 | 9AM to 10AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 14 | 10AM to 11AM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
August | 14 | 11AM to 12PM | 90 | 72.6 | 64.9 | 92.7 | 36.17 | 0.0716 | 0.62 | 14.15 | 0
August | 14 | 12PM to 1PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
August | 14 | 1PM to 2PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 14 | 2PM to 3PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 14 | 3PM to 4PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
August | 14 | 4PM to 5PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
August | 14 | 5PM to 6PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
August | 14 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
August | 14 | 7PM to 8PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 14 | 8PM to 9PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 14 | 9PM to 10PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 14 | 10PM to 11PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 14 | 11PM to 12AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 15 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 15 | 1AM to 2AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 15 | 2AM to 3AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 15 | 3AM to 4AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 15 | 4AM to 5AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 15 | 5AM to 6AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 15 | 6AM to 7AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 15 | 7AM to 8AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
August | 15 | 8AM to 9AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 15 | 9AM to 10AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
August | 15 | 10AM to 11AM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
August | 15 | 11AM to 12PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 15 | 12PM to 1PM | 90 | 72 | 64 | 89.8 | 35.71 | 0.0716 | 0.6 | 14.14 | 0
August | 15 | 1PM to 2PM | 91 | 72.4 | 64 | 89.8 | 35.97 | 0.0715 | 0.6 | 14.17 | 0
August | 15 | 2PM to 3PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
August | 15 | 3PM to 4PM | 88 | 70.9 | 63 | 86.4 | 34.69 | 0.0719 | 0.58 | 14.08 | 0
August | 15 | 4PM to 5PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
August | 15 | 5PM to 6PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
August | 15 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 15 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 15 | 8PM to 9PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 15 | 9PM to 10PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 15 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 15 | 11PM to 12AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 16 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 16 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 16 | 2AM to 3AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 16 | 3AM to 4AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 16 | 4AM to 5AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
August | 16 | 5AM to 6AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
August | 16 | 6AM to 7AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
August | 16 | 7AM to 8AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 16 | 8AM to 9AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
August | 16 | 9AM to 10AM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
August | 16 | 10AM to 11AM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
August | 16 | 11AM to 12PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
August | 16 | 12PM to 1PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 16 | 1PM to 2PM | 90 | 73.2 | 66 | 96.3 | 36.74 | 0.0716 | 0.64 | 14.16 | 0
August | 16 | 2PM to 3PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
August | 16 | 3PM to 4PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
August | 16 | 4PM to 5PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
August | 16 | 5PM to 6PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
August | 16 | 6PM to 7PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
August | 16 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 16 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 16 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 16 | 10PM to 11PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 16 | 11PM to 12AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 17 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 17 | 1AM to 2AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 17 | 2AM to 3AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 17 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 17 | 4AM to 5AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
August | 17 | 5AM to 6AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
August | 17 | 6AM to 7AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
August | 17 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
August | 17 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
August | 17 | 9AM to 10AM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
August | 17 | 10AM to 11AM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
August | 17 | 11AM to 12PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
August | 17 | 12PM to 1PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
August | 17 | 1PM to 2PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
August | 17 | 2PM to 3PM | 89.1 | 75.3 | 70 | 110.8 | 38.79 | 0.0716 | 0.74 | 14.18 | 0
August | 17 | 3PM to 4PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
August | 17 | 4PM to 5PM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
August | 17 | 5PM to 6PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
August | 17 | 6PM to 7PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
August | 17 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 17 | 8PM to 9PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 17 | 9PM to 10PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 17 | 10PM to 11PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
August | 17 | 11PM to 12AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
August | 18 | 12AM to 1AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
August | 18 | 1AM to 2AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
August | 18 | 2AM to 3AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
August | 18 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
August | 18 | 4AM to 5AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
August | 18 | 5AM to 6AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
August | 18 | 6AM to 7AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
August | 18 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
August | 18 | 8AM to 9AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
August | 18 | 9AM to 10AM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
August | 18 | 10AM to 11AM | 88 | 75.7 | 71.1 | 115 | 39.19 | 0.0717 | 0.77 | 14.17 | 0
August | 18 | 11AM to 12PM | 88 | 75 | 70 | 110.8 | 38.52 | 0.0718 | 0.74 | 14.15 | 0
August | 18 | 12PM to 1PM | 88 | 75.7 | 71.1 | 115 | 39.19 | 0.0717 | 0.77 | 14.17 | 0
August | 18 | 1PM to 2PM | 89.1 | 76 | 71.1 | 115 | 39.46 | 0.0716 | 0.77 | 14.2 | 0
August | 18 | 2PM to 3PM | 88 | 75 | 70 | 110.8 | 38.52 | 0.0718 | 0.74 | 14.15 | 0
August | 18 | 3PM to 4PM | 87.1 | 74.8 | 70 | 110.8 | 38.3 | 0.0719 | 0.74 | 14.13 | 0
August | 18 | 4PM to 5PM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
August | 18 | 5PM to 6PM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
August | 18 | 6PM to 7PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
August | 18 | 7PM to 8PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
August | 18 | 8PM to 9PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 18 | 9PM to 10PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 18 | 10PM to 11PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 18 | 11PM to 12AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 19 | 12AM to 1AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
August | 19 | 1AM to 2AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
August | 19 | 2AM to 3AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
August | 19 | 3AM to 4AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
August | 19 | 4AM to 5AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
August | 19 | 5AM to 6AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
August | 19 | 6AM to 7AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
August | 19 | 7AM to 8AM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
August | 19 | 8AM to 9AM | 84 | 75.3 | 72 | 118.7 | 38.79 | 0.0722 | 0.79 | 14.08 | 0
August | 19 | 9AM to 10AM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
August | 19 | 10AM to 11AM | 86 | 76.5 | 73 | 123.2 | 39.99 | 0.072 | 0.82 | 14.14 | 0
August | 19 | 11AM to 12PM | 87.1 | 76.8 | 73 | 123.2 | 40.25 | 0.0718 | 0.82 | 14.17 | 0
August | 19 | 12PM to 1PM | 89.1 | 77.3 | 73 | 123.2 | 40.75 | 0.0715 | 0.82 | 14.22 | 0
August | 19 | 1PM to 2PM | 89.1 | 77.3 | 73 | 123.2 | 40.75 | 0.0715 | 0.82 | 14.22 | 0
August | 19 | 2PM to 3PM | 89.1 | 77.9 | 73.9 | 127.1 | 41.36 | 0.0715 | 0.85 | 14.23 | 0
August | 19 | 3PM to 4PM | 87.1 | 76.1 | 72 | 118.7 | 39.54 | 0.0718 | 0.79 | 14.16 | 0
August | 19 | 4PM to 5PM | 86 | 76.5 | 73 | 123.2 | 39.99 | 0.072 | 0.82 | 14.14 | 0
August | 19 | 5PM to 6PM | 86 | 75.8 | 72 | 118.7 | 39.28 | 0.072 | 0.79 | 14.13 | 0
August | 19 | 6PM to 7PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
August | 19 | 7PM to 8PM | 81 | 74.5 | 72 | 118.7 | 38.03 | 0.0726 | 0.79 | 14 | 0
August | 19 | 8PM to 9PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
August | 19 | 9PM to 10PM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
August | 19 | 10PM to 11PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
August | 19 | 11PM to 12AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
August | 20 | 12AM to 1AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
August | 20 | 1AM to 2AM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
August | 20 | 2AM to 3AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 20 | 3AM to 4AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
August | 20 | 4AM to 5AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
August | 20 | 5AM to 6AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 20 | 6AM to 7AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 20 | 7AM to 8AM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
August | 20 | 8AM to 9AM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
August | 20 | 9AM to 10AM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
August | 20 | 10AM to 11AM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
August | 20 | 11AM to 12PM | 90 | 74.4 | 68 | 103.3 | 37.84 | 0.0716 | 0.69 | 14.18 | 0
August | 20 | 12PM to 1PM | 90 | 73.7 | 66.9 | 99.5 | 37.23 | 0.0716 | 0.67 | 14.17 | 0
August | 20 | 1PM to 2PM | 90 | 74.4 | 68 | 103.3 | 37.84 | 0.0716 | 0.69 | 14.18 | 0
August | 20 | 2PM to 3PM | 90 | 73.2 | 66 | 96.3 | 36.74 | 0.0716 | 0.64 | 14.16 | 0
August | 20 | 3PM to 4PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
August | 20 | 4PM to 5PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
August | 20 | 5PM to 6PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
August | 20 | 6PM to 7PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
August | 20 | 7PM to 8PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 20 | 8PM to 9PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 20 | 9PM to 10PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 20 | 10PM to 11PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 20 | 11PM to 12AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 21 | 12AM to 1AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 21 | 1AM to 2AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 21 | 2AM to 3AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 21 | 3AM to 4AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 21 | 4AM to 5AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 21 | 5AM to 6AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 21 | 6AM to 7AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 21 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 21 | 8AM to 9AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 21 | 9AM to 10AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 21 | 10AM to 11AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
August | 21 | 11AM to 12PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
August | 21 | 12PM to 1PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
August | 21 | 1PM to 2PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
August | 21 | 2PM to 3PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
August | 21 | 3PM to 4PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
August | 21 | 4PM to 5PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
August | 21 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
August | 21 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
August | 21 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 21 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 21 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 21 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 21 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 22 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 22 | 1AM to 2AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 22 | 2AM to 3AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 22 | 3AM to 4AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 22 | 4AM to 5AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 22 | 5AM to 6AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 22 | 6AM to 7AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 22 | 7AM to 8AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 22 | 8AM to 9AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
August | 22 | 9AM to 10AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 22 | 10AM to 11AM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
August | 22 | 11AM to 12PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
August | 22 | 12PM to 1PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
August | 22 | 1PM to 2PM | 90 | 71.4 | 63 | 86.4 | 35.17 | 0.0717 | 0.58 | 14.13 | 0
August | 22 | 2PM to 3PM | 88 | 69.8 | 61 | 80.4 | 33.75 | 0.0719 | 0.54 | 14.06 | 0
August | 22 | 3PM to 4PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
August | 22 | 4PM to 5PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
August | 22 | 5PM to 6PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
August | 22 | 6PM to 7PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
August | 22 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 22 | 8PM to 9PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 22 | 9PM to 10PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
August | 22 | 10PM to 11PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 22 | 11PM to 12AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 23 | 12AM to 1AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
August | 23 | 1AM to 2AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 23 | 2AM to 3AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
August | 23 | 3AM to 4AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
August | 23 | 4AM to 5AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
August | 23 | 5AM to 6AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 23 | 6AM to 7AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
August | 23 | 7AM to 8AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
August | 23 | 8AM to 9AM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
August | 23 | 9AM to 10AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
August | 23 | 10AM to 11AM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
August | 23 | 11AM to 12PM | 90 | 71 | 62.1 | 83.6 | 34.74 | 0.0717 | 0.56 | 14.12 | 0
August | 23 | 12PM to 1PM | 89.1 | 70.7 | 62.1 | 83.6 | 34.52 | 0.0718 | 0.56 | 14.1 | 0
August | 23 | 1PM to 2PM | 90 | 70.4 | 61 | 80.4 | 34.24 | 0.0717 | 0.54 | 14.11 | 0
August | 23 | 2PM to 3PM | 89.1 | 71.2 | 63 | 86.4 | 34.95 | 0.0718 | 0.58 | 14.11 | 0
August | 23 | 3PM to 4PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
August | 23 | 4PM to 5PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
August | 23 | 5PM to 6PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
August | 23 | 6PM to 7PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
August | 23 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 23 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 23 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 23 | 10PM to 11PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 23 | 11PM to 12AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 24 | 12AM to 1AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 24 | 1AM to 2AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
August | 24 | 2AM to 3AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
August | 24 | 3AM to 4AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
August | 24 | 4AM to 5AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
August | 24 | 5AM to 6AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
August | 24 | 6AM to 7AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
August | 24 | 7AM to 8AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 24 | 8AM to 9AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
August | 24 | 9AM to 10AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
August | 24 | 10AM to 11AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
August | 24 | 11AM to 12PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
August | 24 | 12PM to 1PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
August | 24 | 1PM to 2PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
August | 24 | 2PM to 3PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
August | 24 | 3PM to 4PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
August | 24 | 4PM to 5PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
August | 24 | 5PM to 6PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
August | 24 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 24 | 7PM to 8PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 24 | 8PM to 9PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
August | 24 | 9PM to 10PM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
August | 24 | 10PM to 11PM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
August | 24 | 11PM to 12AM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
August | 25 | 12AM to 1AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
August | 25 | 1AM to 2AM | 73.9 | 72.5 | 72 | 118.7 | 36.29 | 0.0736 | 0.79 | 13.82 | 0
August | 25 | 2AM to 3AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
August | 25 | 3AM to 4AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
August | 25 | 4AM to 5AM | 72 | 70.6 | 70 | 110.8 | 34.56 | 0.0739 | 0.74 | 13.74 | 0
August | 25 | 5AM to 6AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
August | 25 | 6AM to 7AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
August | 25 | 7AM to 8AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
August | 25 | 8AM to 9AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 25 | 9AM to 10AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 25 | 10AM to 11AM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
August | 25 | 11AM to 12PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
August | 25 | 12PM to 1PM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
August | 25 | 1PM to 2PM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
August | 25 | 2PM to 3PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
August | 25 | 3PM to 4PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
August | 25 | 4PM to 5PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
August | 25 | 5PM to 6PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 25 | 6PM to 7PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
August | 25 | 7PM to 8PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
August | 25 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 25 | 9PM to 10PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
August | 25 | 10PM to 11PM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
August | 25 | 11PM to 12AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
August | 26 | 12AM to 1AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
August | 26 | 1AM to 2AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
August | 26 | 2AM to 3AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
August | 26 | 3AM to 4AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
August | 26 | 4AM to 5AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
August | 26 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
August | 26 | 6AM to 7AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
August | 26 | 7AM to 8AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 26 | 8AM to 9AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
August | 26 | 9AM to 10AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
August | 26 | 10AM to 11AM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
August | 26 | 11AM to 12PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
August | 26 | 12PM to 1PM | 90 | 74.4 | 68 | 103.3 | 37.84 | 0.0716 | 0.69 | 14.18 | 0
August | 26 | 1PM to 2PM | 90 | 75 | 69.1 | 107.3 | 38.47 | 0.0715 | 0.72 | 14.2 | 0
August | 26 | 2PM to 3PM | 88 | 75 | 70 | 110.8 | 38.52 | 0.0718 | 0.74 | 14.15 | 0
August | 26 | 3PM to 4PM | 87.1 | 74.8 | 70 | 110.8 | 38.3 | 0.0719 | 0.74 | 14.13 | 0
August | 26 | 4PM to 5PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
August | 26 | 5PM to 6PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
August | 26 | 6PM to 7PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
August | 26 | 7PM to 8PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
August | 26 | 8PM to 9PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 26 | 9PM to 10PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 26 | 10PM to 11PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 26 | 11PM to 12AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 27 | 12AM to 1AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 27 | 1AM to 2AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 27 | 2AM to 3AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 27 | 3AM to 4AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 27 | 4AM to 5AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 27 | 5AM to 6AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 27 | 6AM to 7AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 27 | 7AM to 8AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
August | 27 | 8AM to 9AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
August | 27 | 9AM to 10AM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
August | 27 | 10AM to 11AM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
August | 27 | 11AM to 12PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 27 | 12PM to 1PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 27 | 1PM to 2PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 27 | 2PM to 3PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
August | 27 | 3PM to 4PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
August | 27 | 4PM to 5PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
August | 27 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 27 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 27 | 7PM to 8PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
August | 27 | 8PM to 9PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 27 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 27 | 10PM to 11PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 27 | 11PM to 12AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
August | 28 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 28 | 1AM to 2AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 28 | 2AM to 3AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 28 | 3AM to 4AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
August | 28 | 4AM to 5AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 28 | 5AM to 6AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
August | 28 | 6AM to 7AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
August | 28 | 7AM to 8AM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
August | 28 | 8AM to 9AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
August | 28 | 9AM to 10AM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
August | 28 | 10AM to 11AM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
August | 28 | 11AM to 12PM | 89.1 | 74.1 | 68 | 103.3 | 37.62 | 0.0717 | 0.69 | 14.16 | 0
August | 28 | 12PM to 1PM | 90 | 73.2 | 66 | 96.3 | 36.74 | 0.0716 | 0.64 | 14.16 | 0
August | 28 | 1PM to 2PM | 90 | 73.2 | 66 | 96.3 | 36.74 | 0.0716 | 0.64 | 14.16 | 0
August | 28 | 2PM to 3PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
August | 28 | 3PM to 4PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
August | 28 | 4PM to 5PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
August | 28 | 5PM to 6PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
August | 28 | 6PM to 7PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
August | 28 | 7PM to 8PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
August | 28 | 8PM to 9PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 28 | 9PM to 10PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
August | 28 | 10PM to 11PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
August | 28 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 29 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 29 | 1AM to 2AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 29 | 2AM to 3AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 29 | 3AM to 4AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 29 | 4AM to 5AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 29 | 5AM to 6AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 29 | 6AM to 7AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 29 | 7AM to 8AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
August | 29 | 8AM to 9AM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
August | 29 | 9AM to 10AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
August | 29 | 10AM to 11AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
August | 29 | 11AM to 12PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
August | 29 | 12PM to 1PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
August | 29 | 1PM to 2PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
August | 29 | 2PM to 3PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
August | 29 | 3PM to 4PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
August | 29 | 4PM to 5PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
August | 29 | 5PM to 6PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
August | 29 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
August | 29 | 7PM to 8PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 29 | 8PM to 9PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 29 | 9PM to 10PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 29 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 29 | 11PM to 12AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 30 | 12AM to 1AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 30 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 30 | 2AM to 3AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
August | 30 | 3AM to 4AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
August | 30 | 4AM to 5AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
August | 30 | 5AM to 6AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
August | 30 | 6AM to 7AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
August | 30 | 7AM to 8AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
August | 30 | 8AM to 9AM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
August | 30 | 9AM to 10AM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
August | 30 | 10AM to 11AM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
August | 30 | 11AM to 12PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 30 | 12PM to 1PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
August | 30 | 1PM to 2PM | 90 | 72.6 | 64.9 | 92.7 | 36.17 | 0.0716 | 0.62 | 14.15 | 0
August | 30 | 2PM to 3PM | 89.1 | 72.9 | 66 | 96.3 | 36.52 | 0.0717 | 0.64 | 14.14 | 0
August | 30 | 3PM to 4PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 30 | 4PM to 5PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
August | 30 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
August | 30 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
August | 30 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
August | 30 | 8PM to 9PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
August | 30 | 9PM to 10PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 30 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 30 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
August | 31 | 12AM to 1AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
August | 31 | 1AM to 2AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 31 | 2AM to 3AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
August | 31 | 3AM to 4AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 31 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 31 | 5AM to 6AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
August | 31 | 6AM to 7AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
August | 31 | 7AM to 8AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
August | 31 | 8AM to 9AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
August | 31 | 9AM to 10AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
August | 31 | 10AM to 11AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
August | 31 | 11AM to 12PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
August | 31 | 12PM to 1PM | 90 | 72 | 64 | 89.8 | 35.71 | 0.0716 | 0.6 | 14.14 | 0
August | 31 | 1PM to 2PM | 89.1 | 71.8 | 64 | 89.8 | 35.49 | 0.0717 | 0.6 | 14.12 | 0
August | 31 | 2PM to 3PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
August | 31 | 3PM to 4PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
August | 31 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
August | 31 | 5PM to 6PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
August | 31 | 6PM to 7PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
August | 31 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 31 | 8PM to 9PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
August | 31 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
August | 31 | 10PM to 11PM | 78.1 | 70.6 | 67.3 | 100.7 | 34.5 | 0.0731 | 0.67 | 13.87 | 0
August | 31 | 11PM to 12AM | 78.1 | 71.3 | 68.4 | 104.6 | 35.12 | 0.0731 | 0.7 | 13.88 | 0
September | 1 | 12AM to 1AM | 78.1 | 72.1 | 69.6 | 109.4 | 35.86 | 0.0731 | 0.73 | 13.89 | 0
September | 1 | 1AM to 2AM | 78.1 | 72.8 | 70.7 | 113.6 | 36.52 | 0.0731 | 0.76 | 13.91 | 0
September | 1 | 2AM to 3AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
September | 1 | 3AM to 4AM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
September | 1 | 4AM to 5AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
September | 1 | 5AM to 6AM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
September | 1 | 6AM to 7AM | 79 | 73.9 | 72 | 118.7 | 37.54 | 0.0729 | 0.79 | 13.95 | 0
September | 1 | 7AM to 8AM | 80.1 | 75 | 73 | 123.2 | 38.52 | 0.0727 | 0.82 | 13.99 | 0
September | 1 | 8AM to 9AM | 82 | 74.7 | 72 | 118.7 | 38.3 | 0.0725 | 0.79 | 14.03 | 0
September | 1 | 9AM to 10AM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
September | 1 | 10AM to 11AM | 81 | 75.8 | 73.9 | 127.1 | 39.35 | 0.0726 | 0.85 | 14.02 | 0
September | 1 | 11AM to 12PM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
September | 1 | 12PM to 1PM | 88 | 75 | 70 | 110.8 | 38.52 | 0.0718 | 0.74 | 14.15 | 0
September | 1 | 1PM to 2PM | 90 | 75 | 69.1 | 107.3 | 38.47 | 0.0715 | 0.72 | 14.2 | 0
September | 1 | 2PM to 3PM | 87.1 | 75.5 | 71.1 | 115 | 38.97 | 0.0719 | 0.77 | 14.15 | 0
September | 1 | 3PM to 4PM | 89.1 | 74.8 | 69.1 | 107.3 | 38.25 | 0.0716 | 0.72 | 14.17 | 0
September | 1 | 4PM to 5PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
September | 1 | 5PM to 6PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
September | 1 | 6PM to 7PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
September | 1 | 7PM to 8PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
September | 1 | 8PM to 9PM | 81 | 74.5 | 72 | 118.7 | 38.03 | 0.0726 | 0.79 | 14 | 0
September | 1 | 9PM to 10PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
September | 1 | 10PM to 11PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 1 | 11PM to 12AM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
September | 2 | 12AM to 1AM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 2 | 1AM to 2AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 2 | 2AM to 3AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 2 | 3AM to 4AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
September | 2 | 4AM to 5AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
September | 2 | 5AM to 6AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
September | 2 | 6AM to 7AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 2 | 7AM to 8AM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
September | 2 | 8AM to 9AM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
September | 2 | 9AM to 10AM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
September | 2 | 10AM to 11AM | 90 | 74.4 | 68 | 103.3 | 37.84 | 0.0716 | 0.69 | 14.18 | 0
September | 2 | 11AM to 12PM | 91 | 73.5 | 66 | 96.3 | 37.01 | 0.0715 | 0.64 | 14.19 | 0
September | 2 | 12PM to 1PM | 91.9 | 74.3 | 66.9 | 99.5 | 37.72 | 0.0713 | 0.67 | 14.22 | 0
September | 2 | 1PM to 2PM | 91 | 74.6 | 68 | 103.3 | 38.11 | 0.0714 | 0.69 | 14.21 | 0
September | 2 | 2PM to 3PM | 91 | 74 | 66.9 | 99.5 | 37.5 | 0.0714 | 0.67 | 14.2 | 0
September | 2 | 3PM to 4PM | 90 | 75 | 69.1 | 107.3 | 38.47 | 0.0715 | 0.72 | 14.2 | 0
September | 2 | 4PM to 5PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
September | 2 | 5PM to 6PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
September | 2 | 6PM to 7PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
September | 2 | 7PM to 8PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
September | 2 | 8PM to 9PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
September | 2 | 9PM to 10PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
September | 2 | 10PM to 11PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
September | 2 | 11PM to 12AM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
September | 3 | 12AM to 1AM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
September | 3 | 1AM to 2AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
September | 3 | 2AM to 3AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
September | 3 | 3AM to 4AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
September | 3 | 4AM to 5AM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
September | 3 | 5AM to 6AM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
September | 3 | 6AM to 7AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
September | 3 | 7AM to 8AM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
September | 3 | 8AM to 9AM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
September | 3 | 9AM to 10AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
September | 3 | 10AM to 11AM | 89.1 | 74.8 | 69.1 | 107.3 | 38.25 | 0.0716 | 0.72 | 14.17 | 0
September | 3 | 11AM to 12PM | 89.1 | 74.1 | 68 | 103.3 | 37.62 | 0.0717 | 0.69 | 14.16 | 0
September | 3 | 12PM to 1PM | 91.9 | 75.5 | 69.1 | 107.3 | 38.96 | 0.0713 | 0.72 | 14.25 | 0
September | 3 | 1PM to 2PM | 91.9 | 74.9 | 68 | 103.3 | 38.33 | 0.0713 | 0.69 | 14.23 | 0
September | 3 | 2PM to 3PM | 91 | 74.6 | 68 | 103.3 | 38.11 | 0.0714 | 0.69 | 14.21 | 0
September | 3 | 3PM to 4PM | 91 | 74.6 | 68 | 103.3 | 38.11 | 0.0714 | 0.69 | 14.21 | 0
September | 3 | 4PM to 5PM | 89.1 | 74.1 | 68 | 103.3 | 37.62 | 0.0717 | 0.69 | 14.16 | 0
September | 3 | 5PM to 6PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
September | 3 | 6PM to 7PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
September | 3 | 7PM to 8PM | 79.7 | 71.7 | 68.4 | 104.6 | 35.52 | 0.0729 | 0.7 | 13.92 | 0
September | 3 | 8PM to 9PM | 78.8 | 73 | 70.7 | 113.6 | 36.7 | 0.073 | 0.76 | 13.93 | 0
September | 3 | 9PM to 10PM | 78.1 | 73.8 | 72.1 | 119.4 | 37.43 | 0.073 | 0.8 | 13.93 | 0
September | 3 | 10PM to 11PM | 77.4 | 71.2 | 68.5 | 105.3 | 35.04 | 0.0732 | 0.7 | 13.86 | 0
September | 3 | 11PM to 12AM | 77.7 | 72.7 | 70.7 | 113.6 | 36.43 | 0.0731 | 0.76 | 13.9 | 0
September | 4 | 12AM to 1AM | 76.8 | 71.1 | 68.7 | 106 | 35.01 | 0.0733 | 0.71 | 13.85 | 0
September | 4 | 1AM to 2AM | 76.3 | 71.6 | 69.6 | 109.4 | 35.41 | 0.0733 | 0.73 | 13.85 | 0
September | 4 | 2AM to 3AM | 76.3 | 72.4 | 70.9 | 114.3 | 36.18 | 0.0733 | 0.76 | 13.86 | 0
September | 4 | 3AM to 4AM | 75.4 | 72.4 | 71.2 | 115.7 | 36.19 | 0.0734 | 0.77 | 13.84 | 0
September | 4 | 4AM to 5AM | 75.7 | 71.5 | 69.8 | 110.1 | 35.39 | 0.0734 | 0.73 | 13.84 | 0
September | 4 | 5AM to 6AM | 77 | 73.1 | 71.6 | 117.2 | 36.82 | 0.0732 | 0.78 | 13.89 | 0
September | 4 | 6AM to 7AM | 78.1 | 72.1 | 69.6 | 109.4 | 35.86 | 0.0731 | 0.73 | 13.89 | 0
September | 4 | 7AM to 8AM | 80.2 | 72.8 | 69.8 | 110.1 | 36.5 | 0.0728 | 0.73 | 13.95 | 0
September | 4 | 8AM to 9AM | 82.4 | 73.5 | 70 | 110.8 | 37.14 | 0.0725 | 0.74 | 14.01 | 0
September | 4 | 9AM to 10AM | 84.2 | 73.9 | 69.8 | 110.1 | 37.48 | 0.0723 | 0.73 | 14.06 | 0
September | 4 | 10AM to 11AM | 86.7 | 75.2 | 70.7 | 113.6 | 38.65 | 0.0719 | 0.76 | 14.13 | 0
September | 4 | 11AM to 12PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
September | 4 | 12PM to 1PM | 87.3 | 73.6 | 68 | 103.3 | 37.17 | 0.0719 | 0.69 | 14.11 | 0
September | 4 | 1PM to 2PM | 89.1 | 74.6 | 68.7 | 106 | 38.03 | 0.0717 | 0.71 | 14.17 | 0
September | 4 | 2PM to 3PM | 87.6 | 74.6 | 69.4 | 108.7 | 38.11 | 0.0718 | 0.73 | 14.14 | 0
September | 4 | 3PM to 4PM | 87.3 | 74.1 | 68.7 | 106 | 37.59 | 0.0719 | 0.71 | 14.12 | 0
September | 4 | 4PM to 5PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
September | 4 | 5PM to 6PM | 87.4 | 74.1 | 68.7 | 106 | 37.64 | 0.0719 | 0.71 | 14.13 | 0
September | 4 | 6PM to 7PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
September | 4 | 7PM to 8PM | 83.1 | 73.5 | 69.6 | 109.4 | 37.1 | 0.0724 | 0.73 | 14.02 | 0
September | 4 | 8PM to 9PM | 83.1 | 74.6 | 71.2 | 115.7 | 38.1 | 0.0724 | 0.77 | 14.04 | 0
September | 4 | 9PM to 10PM | 80.2 | 72.5 | 69.3 | 108 | 36.18 | 0.0728 | 0.72 | 13.95 | 0
September | 4 | 10PM to 11PM | 78.3 | 73 | 70.9 | 114.3 | 36.67 | 0.073 | 0.76 | 13.91 | 0
September | 4 | 11PM to 12AM | 77.5 | 72.5 | 70.5 | 112.9 | 36.27 | 0.0731 | 0.75 | 13.89 | 0
September | 5 | 12AM to 1AM | 77.2 | 73.1 | 71.4 | 116.5 | 36.75 | 0.0732 | 0.78 | 13.89 | 0
September | 5 | 1AM to 2AM | 77.2 | 72.8 | 71.1 | 115 | 36.52 | 0.0732 | 0.77 | 13.89 | 0
September | 5 | 2AM to 3AM | 76.3 | 72.6 | 71.1 | 115 | 36.3 | 0.0733 | 0.77 | 13.87 | 0
September | 5 | 3AM to 4AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
September | 5 | 4AM to 5AM | 76.5 | 71.9 | 70 | 110.8 | 35.68 | 0.0733 | 0.74 | 13.86 | 0
September | 5 | 5AM to 6AM | 76.5 | 71.3 | 69.1 | 107.3 | 35.14 | 0.0733 | 0.72 | 13.85 | 0
September | 5 | 6AM to 7AM | 77.9 | 72.8 | 70.7 | 113.6 | 36.47 | 0.0731 | 0.76 | 13.9 | 0
September | 5 | 7AM to 8AM | 80.6 | 74 | 71.4 | 116.5 | 37.59 | 0.0727 | 0.78 | 13.98 | 0
September | 5 | 8AM to 9AM | 83.1 | 74.4 | 71.1 | 115 | 37.99 | 0.0724 | 0.77 | 14.04 | 0
September | 5 | 9AM to 10AM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
September | 5 | 10AM to 11AM | 86.7 | 74 | 68.9 | 106.6 | 37.56 | 0.072 | 0.71 | 14.11 | 0
September | 5 | 11AM to 12PM | 88.9 | 75.5 | 70.3 | 112.2 | 38.96 | 0.0716 | 0.75 | 14.18 | 0
September | 5 | 12PM to 1PM | 88.5 | 76.3 | 71.8 | 117.9 | 39.78 | 0.0717 | 0.79 | 14.19 | 0
September | 5 | 1PM to 2PM | 88 | 75.2 | 70.2 | 111.5 | 38.63 | 0.0718 | 0.74 | 14.16 | 0
September | 5 | 2PM to 3PM | 88.7 | 74.7 | 69.1 | 107.3 | 38.16 | 0.0717 | 0.72 | 14.16 | 0
September | 5 | 3PM to 4PM | 88.5 | 74.9 | 69.4 | 108.7 | 38.33 | 0.0717 | 0.73 | 14.16 | 0
September | 5 | 4PM to 5PM | 88 | 73.4 | 67.3 | 100.7 | 36.94 | 0.0718 | 0.67 | 14.12 | 0
September | 5 | 5PM to 6PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
September | 5 | 6PM to 7PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
September | 5 | 7PM to 8PM | 79.9 | 71.5 | 68 | 103.3 | 35.35 | 0.0729 | 0.69 | 13.92 | 0
September | 5 | 8PM to 9PM | 79.9 | 71.1 | 67.3 | 100.7 | 34.95 | 0.0729 | 0.67 | 13.91 | 0
September | 5 | 9PM to 10PM | 79.2 | 71.5 | 68.2 | 104 | 35.28 | 0.073 | 0.69 | 13.91 | 0
September | 5 | 10PM to 11PM | 79.2 | 71.3 | 68 | 103.3 | 35.18 | 0.073 | 0.69 | 13.9 | 0
September | 5 | 11PM to 12AM | 78.4 | 71.8 | 69.1 | 107.3 | 35.63 | 0.0731 | 0.72 | 13.9 | 0
September | 6 | 12AM to 1AM | 77.7 | 72.2 | 70 | 110.8 | 35.99 | 0.0731 | 0.74 | 13.89 | 0
September | 6 | 1AM to 2AM | 77.7 | 71.6 | 69.1 | 107.3 | 35.45 | 0.0732 | 0.72 | 13.88 | 0
September | 6 | 2AM to 3AM | 77.7 | 70.9 | 68 | 103.3 | 34.82 | 0.0732 | 0.69 | 13.87 | 0
September | 6 | 3AM to 4AM | 76.5 | 71.3 | 69.1 | 107.3 | 35.14 | 0.0733 | 0.72 | 13.85 | 0
September | 6 | 4AM to 5AM | 76.5 | 70.6 | 68 | 103.3 | 34.51 | 0.0734 | 0.69 | 13.83 | 0
September | 6 | 5AM to 6AM | 77.5 | 70.9 | 68 | 103.3 | 34.78 | 0.0732 | 0.69 | 13.86 | 0
September | 6 | 6AM to 7AM | 77.7 | 70.7 | 67.6 | 102 | 34.62 | 0.0732 | 0.68 | 13.86 | 0
September | 6 | 7AM to 8AM | 80.8 | 72 | 68.4 | 104.6 | 35.78 | 0.0728 | 0.7 | 13.95 | 0
September | 6 | 8AM to 9AM | 82.8 | 72.8 | 68.7 | 106 | 36.48 | 0.0725 | 0.71 | 14 | 0
September | 6 | 9AM to 10AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
September | 6 | 10AM to 11AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
September | 6 | 11AM to 12PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
September | 6 | 12PM to 1PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
September | 6 | 1PM to 2PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
September | 6 | 2PM to 3PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
September | 6 | 3PM to 4PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
September | 6 | 4PM to 5PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
September | 6 | 5PM to 6PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
September | 6 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
September | 6 | 7PM to 8PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
September | 6 | 8PM to 9PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
September | 6 | 9PM to 10PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 6 | 10PM to 11PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
September | 6 | 11PM to 12AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
September | 7 | 12AM to 1AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
September | 7 | 1AM to 2AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
September | 7 | 2AM to 3AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
September | 7 | 3AM to 4AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 7 | 4AM to 5AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
September | 7 | 5AM to 6AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
September | 7 | 6AM to 7AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
September | 7 | 7AM to 8AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
September | 7 | 8AM to 9AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
September | 7 | 9AM to 10AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
September | 7 | 10AM to 11AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
September | 7 | 11AM to 12PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
September | 7 | 12PM to 1PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
September | 7 | 1PM to 2PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
September | 7 | 2PM to 3PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
September | 7 | 3PM to 4PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
September | 7 | 4PM to 5PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
September | 7 | 5PM to 6PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
September | 7 | 6PM to 7PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
September | 7 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 7 | 8PM to 9PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 7 | 9PM to 10PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 7 | 10PM to 11PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
September | 7 | 11PM to 12AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 8 | 12AM to 1AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 8 | 1AM to 2AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 8 | 2AM to 3AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 8 | 3AM to 4AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 8 | 4AM to 5AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 8 | 5AM to 6AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
September | 8 | 6AM to 7AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
September | 8 | 7AM to 8AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
September | 8 | 8AM to 9AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 8 | 9AM to 10AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
September | 8 | 10AM to 11AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
September | 8 | 11AM to 12PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
September | 8 | 12PM to 1PM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
September | 8 | 1PM to 2PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
September | 8 | 2PM to 3PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
September | 8 | 3PM to 4PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
September | 8 | 4PM to 5PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
September | 8 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
September | 8 | 6PM to 7PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
September | 8 | 7PM to 8PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 8 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 8 | 9PM to 10PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 8 | 10PM to 11PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 8 | 11PM to 12AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
September | 9 | 12AM to 1AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
September | 9 | 1AM to 2AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
September | 9 | 2AM to 3AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
September | 9 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
September | 9 | 4AM to 5AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
September | 9 | 5AM to 6AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
September | 9 | 6AM to 7AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 9 | 7AM to 8AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
September | 9 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
September | 9 | 9AM to 10AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
September | 9 | 10AM to 11AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
September | 9 | 11AM to 12PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
September | 9 | 12PM to 1PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
September | 9 | 1PM to 2PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
September | 9 | 2PM to 3PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
September | 9 | 3PM to 4PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
September | 9 | 4PM to 5PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
September | 9 | 5PM to 6PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
September | 9 | 6PM to 7PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
September | 9 | 7PM to 8PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 9 | 8PM to 9PM | 79 | 73.9 | 72 | 118.7 | 37.54 | 0.0729 | 0.79 | 13.95 | 0
September | 9 | 9PM to 10PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
September | 9 | 10PM to 11PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
September | 9 | 11PM to 12AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 10 | 12AM to 1AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 10 | 1AM to 2AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 10 | 2AM to 3AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 10 | 3AM to 4AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
September | 10 | 4AM to 5AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
September | 10 | 5AM to 6AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
September | 10 | 6AM to 7AM | 75 | 73.6 | 73 | 123.2 | 37.27 | 0.0734 | 0.82 | 13.86 | 0
September | 10 | 7AM to 8AM | 79 | 73.9 | 72 | 118.7 | 37.54 | 0.0729 | 0.79 | 13.95 | 0
September | 10 | 8AM to 9AM | 81 | 74.5 | 72 | 118.7 | 38.03 | 0.0726 | 0.79 | 14 | 0
September | 10 | 9AM to 10AM | 84.9 | 74.9 | 71.1 | 115 | 38.43 | 0.0721 | 0.77 | 14.09 | 0
September | 10 | 10AM to 11AM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
September | 10 | 11AM to 12PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
September | 10 | 12PM to 1PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
September | 10 | 1PM to 2PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
September | 10 | 2PM to 3PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
September | 10 | 3PM to 4PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
September | 10 | 4PM to 5PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
September | 10 | 5PM to 6PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
September | 10 | 6PM to 7PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 10 | 7PM to 8PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 10 | 8PM to 9PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
September | 10 | 9PM to 10PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 10 | 10PM to 11PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 10 | 11PM to 12AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 11 | 12AM to 1AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 11 | 1AM to 2AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
September | 11 | 2AM to 3AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 11 | 3AM to 4AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 11 | 4AM to 5AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 11 | 5AM to 6AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 11 | 6AM to 7AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 11 | 7AM to 8AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
September | 11 | 8AM to 9AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
September | 11 | 9AM to 10AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
September | 11 | 10AM to 11AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
September | 11 | 11AM to 12PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
September | 11 | 12PM to 1PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
September | 11 | 1PM to 2PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
September | 11 | 2PM to 3PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
September | 11 | 3PM to 4PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
September | 11 | 4PM to 5PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
September | 11 | 5PM to 6PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
September | 11 | 6PM to 7PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
September | 11 | 7PM to 8PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 11 | 8PM to 9PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
September | 11 | 9PM to 10PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 11 | 10PM to 11PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
September | 11 | 11PM to 12AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 12 | 12AM to 1AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 12 | 1AM to 2AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 12 | 2AM to 3AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
September | 12 | 3AM to 4AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 12 | 4AM to 5AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 12 | 5AM to 6AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 12 | 6AM to 7AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 12 | 7AM to 8AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
September | 12 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
September | 12 | 9AM to 10AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
September | 12 | 10AM to 11AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
September | 12 | 11AM to 12PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
September | 12 | 12PM to 1PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
September | 12 | 1PM to 2PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
September | 12 | 2PM to 3PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
September | 12 | 3PM to 4PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
September | 12 | 4PM to 5PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
September | 12 | 5PM to 6PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
September | 12 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 12 | 7PM to 8PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 12 | 8PM to 9PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 12 | 9PM to 10PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 12 | 10PM to 11PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 12 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 13 | 12AM to 1AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 13 | 1AM to 2AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 13 | 2AM to 3AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 13 | 3AM to 4AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 13 | 4AM to 5AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 13 | 5AM to 6AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 13 | 6AM to 7AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 13 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
September | 13 | 8AM to 9AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
September | 13 | 9AM to 10AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
September | 13 | 10AM to 11AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
September | 13 | 11AM to 12PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
September | 13 | 12PM to 1PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
September | 13 | 1PM to 2PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
September | 13 | 2PM to 3PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
September | 13 | 3PM to 4PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
September | 13 | 4PM to 5PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
September | 13 | 5PM to 6PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
September | 13 | 6PM to 7PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 13 | 7PM to 8PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
September | 13 | 8PM to 9PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 13 | 9PM to 10PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
September | 13 | 10PM to 11PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 13 | 11PM to 12AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 14 | 12AM to 1AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 14 | 1AM to 2AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 14 | 2AM to 3AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 14 | 3AM to 4AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 14 | 4AM to 5AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 14 | 5AM to 6AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 14 | 6AM to 7AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 14 | 7AM to 8AM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 14 | 8AM to 9AM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
September | 14 | 9AM to 10AM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
September | 14 | 10AM to 11AM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
September | 14 | 11AM to 12PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
September | 14 | 12PM to 1PM | 87.1 | 74.8 | 70 | 110.8 | 38.3 | 0.0719 | 0.74 | 14.13 | 0
September | 14 | 1PM to 2PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
September | 14 | 2PM to 3PM | 87.1 | 75.5 | 71.1 | 115 | 38.97 | 0.0719 | 0.77 | 14.15 | 0
September | 14 | 3PM to 4PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
September | 14 | 4PM to 5PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
September | 14 | 5PM to 6PM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
September | 14 | 6PM to 7PM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
September | 14 | 7PM to 8PM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
September | 14 | 8PM to 9PM | 79 | 73.9 | 72 | 118.7 | 37.54 | 0.0729 | 0.79 | 13.95 | 0
September | 14 | 9PM to 10PM | 78.1 | 74.4 | 73 | 123.2 | 38.02 | 0.073 | 0.82 | 13.94 | 0
September | 14 | 10PM to 11PM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
September | 14 | 11PM to 12AM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
September | 15 | 12AM to 1AM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
September | 15 | 1AM to 2AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
September | 15 | 2AM to 3AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
September | 15 | 3AM to 4AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
September | 15 | 4AM to 5AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 15 | 5AM to 6AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 15 | 6AM to 7AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 15 | 7AM to 8AM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
September | 15 | 8AM to 9AM | 82 | 74.7 | 72 | 118.7 | 38.3 | 0.0725 | 0.79 | 14.03 | 0
September | 15 | 9AM to 10AM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
September | 15 | 10AM to 11AM | 84 | 75.3 | 72 | 118.7 | 38.79 | 0.0722 | 0.79 | 14.08 | 0
September | 15 | 11AM to 12PM | 87.1 | 75.5 | 71.1 | 115 | 38.97 | 0.0719 | 0.77 | 14.15 | 0
September | 15 | 12PM to 1PM | 86 | 75.8 | 72 | 118.7 | 39.28 | 0.072 | 0.79 | 14.13 | 0
September | 15 | 1PM to 2PM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
September | 15 | 2PM to 3PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
September | 15 | 3PM to 4PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
September | 15 | 4PM to 5PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
September | 15 | 5PM to 6PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 15 | 6PM to 7PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
September | 15 | 7PM to 8PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 15 | 8PM to 9PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 15 | 9PM to 10PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 15 | 10PM to 11PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 15 | 11PM to 12AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 16 | 12AM to 1AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 16 | 1AM to 2AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 16 | 2AM to 3AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 16 | 3AM to 4AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
September | 16 | 4AM to 5AM | 73.4 | 72.1 | 71.6 | 117.2 | 35.93 | 0.0737 | 0.78 | 13.8 | 0
September | 16 | 5AM to 6AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
September | 16 | 6AM to 7AM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
September | 16 | 7AM to 8AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 16 | 8AM to 9AM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 16 | 9AM to 10AM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
September | 16 | 10AM to 11AM | 81 | 74.5 | 72 | 118.7 | 38.03 | 0.0726 | 0.79 | 14 | 0
September | 16 | 11AM to 12PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
September | 16 | 12PM to 1PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
September | 16 | 1PM to 2PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
September | 16 | 2PM to 3PM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
September | 16 | 3PM to 4PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 16 | 4PM to 5PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
September | 16 | 5PM to 6PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
September | 16 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 16 | 7PM to 8PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 16 | 8PM to 9PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
September | 16 | 9PM to 10PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 16 | 10PM to 11PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 16 | 11PM to 12AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 17 | 12AM to 1AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 17 | 1AM to 2AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
September | 17 | 2AM to 3AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
September | 17 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
September | 17 | 4AM to 5AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
September | 17 | 5AM to 6AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 17 | 6AM to 7AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 17 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 17 | 8AM to 9AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
September | 17 | 9AM to 10AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
September | 17 | 10AM to 11AM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
September | 17 | 11AM to 12PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
September | 17 | 12PM to 1PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
September | 17 | 1PM to 2PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
September | 17 | 2PM to 3PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
September | 17 | 3PM to 4PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
September | 17 | 4PM to 5PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
September | 17 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
September | 17 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
September | 17 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
September | 17 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
September | 17 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
September | 17 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 17 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 18 | 12AM to 1AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
September | 18 | 1AM to 2AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
September | 18 | 2AM to 3AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
September | 18 | 3AM to 4AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
September | 18 | 4AM to 5AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
September | 18 | 5AM to 6AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
September | 18 | 6AM to 7AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
September | 18 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 18 | 8AM to 9AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
September | 18 | 9AM to 10AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
September | 18 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
September | 18 | 11AM to 12PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
September | 18 | 12PM to 1PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
September | 18 | 1PM to 2PM | 84.9 | 69.5 | 62.1 | 83.6 | 33.51 | 0.0723 | 0.56 | 13.99 | 0
September | 18 | 2PM to 3PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
September | 18 | 3PM to 4PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
September | 18 | 4PM to 5PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
September | 18 | 5PM to 6PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
September | 18 | 6PM to 7PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
September | 18 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
September | 18 | 8PM to 9PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
September | 18 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
September | 18 | 10PM to 11PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
September | 18 | 11PM to 12AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
September | 19 | 12AM to 1AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
September | 19 | 1AM to 2AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
September | 19 | 2AM to 3AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
September | 19 | 3AM to 4AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
September | 19 | 4AM to 5AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
September | 19 | 5AM to 6AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
September | 19 | 6AM to 7AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
September | 19 | 7AM to 8AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
September | 19 | 8AM to 9AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 19 | 9AM to 10AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
September | 19 | 10AM to 11AM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
September | 19 | 11AM to 12PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
September | 19 | 12PM to 1PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
September | 19 | 1PM to 2PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
September | 19 | 2PM to 3PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
September | 19 | 3PM to 4PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
September | 19 | 4PM to 5PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
September | 19 | 5PM to 6PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
September | 19 | 6PM to 7PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
September | 19 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
September | 19 | 8PM to 9PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 19 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
September | 19 | 10PM to 11PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
September | 19 | 11PM to 12AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
September | 20 | 12AM to 1AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
September | 20 | 1AM to 2AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
September | 20 | 2AM to 3AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
September | 20 | 3AM to 4AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
September | 20 | 4AM to 5AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
September | 20 | 5AM to 6AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
September | 20 | 6AM to 7AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
September | 20 | 7AM to 8AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
September | 20 | 8AM to 9AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
September | 20 | 9AM to 10AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
September | 20 | 10AM to 11AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
September | 20 | 11AM to 12PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
September | 20 | 12PM to 1PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
September | 20 | 1PM to 2PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
September | 20 | 2PM to 3PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
September | 20 | 3PM to 4PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
September | 20 | 4PM to 5PM | 82.4 | 71.1 | 66.2 | 96.9 | 34.98 | 0.0726 | 0.65 | 13.97 | 0
September | 20 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
September | 20 | 6PM to 7PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 20 | 7PM to 8PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 20 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
September | 20 | 9PM to 10PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 20 | 10PM to 11PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 20 | 11PM to 12AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
September | 21 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
September | 21 | 1AM to 2AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
September | 21 | 2AM to 3AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
September | 21 | 3AM to 4AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
September | 21 | 4AM to 5AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
September | 21 | 5AM to 6AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
September | 21 | 6AM to 7AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
September | 21 | 7AM to 8AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
September | 21 | 8AM to 9AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
September | 21 | 9AM to 10AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
September | 21 | 10AM to 11AM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
September | 21 | 11AM to 12PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
September | 21 | 12PM to 1PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
September | 21 | 1PM to 2PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
September | 21 | 2PM to 3PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
September | 21 | 3PM to 4PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
September | 21 | 4PM to 5PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
September | 21 | 5PM to 6PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
September | 21 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 21 | 7PM to 8PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 21 | 8PM to 9PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
September | 21 | 9PM to 10PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
September | 21 | 10PM to 11PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 21 | 11PM to 12AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
September | 22 | 12AM to 1AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
September | 22 | 1AM to 2AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
September | 22 | 2AM to 3AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
September | 22 | 3AM to 4AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
September | 22 | 4AM to 5AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
September | 22 | 5AM to 6AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
September | 22 | 6AM to 7AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
September | 22 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
September | 22 | 8AM to 9AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
September | 22 | 9AM to 10AM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
September | 22 | 10AM to 11AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
September | 22 | 11AM to 12PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
September | 22 | 12PM to 1PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
September | 22 | 1PM to 2PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
September | 22 | 2PM to 3PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
September | 22 | 3PM to 4PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
September | 22 | 4PM to 5PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
September | 22 | 5PM to 6PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
September | 22 | 6PM to 7PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
September | 22 | 7PM to 8PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
September | 22 | 8PM to 9PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 22 | 9PM to 10PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 22 | 10PM to 11PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 22 | 11PM to 12AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 23 | 12AM to 1AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 23 | 1AM to 2AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
September | 23 | 2AM to 3AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
September | 23 | 3AM to 4AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
September | 23 | 4AM to 5AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
September | 23 | 5AM to 6AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
September | 23 | 6AM to 7AM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
September | 23 | 7AM to 8AM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
September | 23 | 8AM to 9AM | 82 | 74.1 | 71.1 | 115 | 37.72 | 0.0725 | 0.77 | 14.01 | 0
September | 23 | 9AM to 10AM | 82 | 76.1 | 73.9 | 127.1 | 39.62 | 0.0725 | 0.85 | 14.05 | 0
September | 23 | 10AM to 11AM | 82.9 | 76.3 | 73.9 | 127.1 | 39.84 | 0.0723 | 0.85 | 14.08 | 0
September | 23 | 11AM to 12PM | 84.9 | 76.2 | 73 | 123.2 | 39.72 | 0.0721 | 0.82 | 14.12 | 0
September | 23 | 12PM to 1PM | 82.9 | 75.7 | 73 | 123.2 | 39.23 | 0.0724 | 0.82 | 14.06 | 0
September | 23 | 1PM to 2PM | 81 | 75.8 | 73.9 | 127.1 | 39.35 | 0.0726 | 0.85 | 14.02 | 0
September | 23 | 2PM to 3PM | 81 | 77.2 | 75.9 | 136.1 | 40.75 | 0.0725 | 0.9 | 14.05 | 0
September | 23 | 3PM to 4PM | 82 | 75.5 | 73 | 123.2 | 39.01 | 0.0725 | 0.82 | 14.04 | 0
September | 23 | 4PM to 5PM | 81 | 76.6 | 75 | 131.9 | 40.1 | 0.0726 | 0.88 | 14.04 | 0
September | 23 | 5PM to 6PM | 81 | 74.5 | 72 | 118.7 | 38.03 | 0.0726 | 0.79 | 14 | 0
September | 23 | 6PM to 7PM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
September | 23 | 7PM to 8PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 23 | 8PM to 9PM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
September | 23 | 9PM to 10PM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
September | 23 | 10PM to 11PM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
September | 23 | 11PM to 12AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
September | 24 | 12AM to 1AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
September | 24 | 1AM to 2AM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
September | 24 | 2AM to 3AM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
September | 24 | 3AM to 4AM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
September | 24 | 4AM to 5AM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
September | 24 | 5AM to 6AM | 73.9 | 71.9 | 71.1 | 115 | 35.72 | 0.0736 | 0.77 | 13.81 | 0
September | 24 | 6AM to 7AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
September | 24 | 7AM to 8AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
September | 24 | 8AM to 9AM | 82 | 74.7 | 72 | 118.7 | 38.3 | 0.0725 | 0.79 | 14.03 | 0
September | 24 | 9AM to 10AM | 82.9 | 75.7 | 73 | 123.2 | 39.23 | 0.0724 | 0.82 | 14.06 | 0
September | 24 | 10AM to 11AM | 84 | 75.3 | 72 | 118.7 | 38.79 | 0.0722 | 0.79 | 14.08 | 0
September | 24 | 11AM to 12PM | 84.9 | 76.2 | 73 | 123.2 | 39.72 | 0.0721 | 0.82 | 14.12 | 0
September | 24 | 12PM to 1PM | 86 | 77.1 | 73.9 | 127.1 | 40.6 | 0.0719 | 0.85 | 14.16 | 0
September | 24 | 1PM to 2PM | 84 | 76.6 | 73.9 | 127.1 | 40.11 | 0.0722 | 0.85 | 14.1 | 0
September | 24 | 2PM to 3PM | 84.9 | 76.2 | 73 | 123.2 | 39.72 | 0.0721 | 0.82 | 14.12 | 0
September | 24 | 3PM to 4PM | 84 | 76.6 | 73.9 | 127.1 | 40.11 | 0.0722 | 0.85 | 14.1 | 0
September | 24 | 4PM to 5PM | 82 | 76.1 | 73.9 | 127.1 | 39.62 | 0.0725 | 0.85 | 14.05 | 0
September | 24 | 5PM to 6PM | 80.6 | 75.3 | 73.4 | 124.8 | 38.89 | 0.0727 | 0.83 | 14.01 | 0
September | 24 | 6PM to 7PM | 81 | 75.8 | 73.9 | 127.1 | 39.35 | 0.0726 | 0.85 | 14.02 | 0
September | 24 | 7PM to 8PM | 81 | 75.8 | 73.9 | 127.1 | 39.35 | 0.0726 | 0.85 | 14.02 | 0
September | 24 | 8PM to 9PM | 80.1 | 74.2 | 72 | 118.7 | 37.81 | 0.0728 | 0.79 | 13.97 | 0
September | 24 | 9PM to 10PM | 79 | 73.9 | 72 | 118.7 | 37.54 | 0.0729 | 0.79 | 13.95 | 0
September | 24 | 10PM to 11PM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
September | 24 | 11PM to 12AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
September | 25 | 12AM to 1AM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
September | 25 | 1AM to 2AM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
September | 25 | 2AM to 3AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
September | 25 | 3AM to 4AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
September | 25 | 4AM to 5AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
September | 25 | 5AM to 6AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
September | 25 | 6AM to 7AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
September | 25 | 7AM to 8AM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 25 | 8AM to 9AM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
September | 25 | 9AM to 10AM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
September | 25 | 10AM to 11AM | 84.9 | 76.2 | 73 | 123.2 | 39.72 | 0.0721 | 0.82 | 14.12 | 0
September | 25 | 11AM to 12PM | 86 | 76.5 | 73 | 123.2 | 39.99 | 0.072 | 0.82 | 14.14 | 0
September | 25 | 12PM to 1PM | 86 | 75.8 | 72 | 118.7 | 39.28 | 0.072 | 0.79 | 14.13 | 0
September | 25 | 1PM to 2PM | 86 | 75.8 | 72 | 118.7 | 39.28 | 0.072 | 0.79 | 14.13 | 0
September | 25 | 2PM to 3PM | 84.9 | 76.8 | 73.9 | 127.1 | 40.33 | 0.0721 | 0.85 | 14.13 | 0
September | 25 | 3PM to 4PM | 86 | 75.8 | 72 | 118.7 | 39.28 | 0.072 | 0.79 | 14.13 | 0
September | 25 | 4PM to 5PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
September | 25 | 5PM to 6PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
September | 25 | 6PM to 7PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
September | 25 | 7PM to 8PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 25 | 8PM to 9PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
September | 25 | 9PM to 10PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 25 | 10PM to 11PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 25 | 11PM to 12AM | 79 | 73.9 | 72 | 118.7 | 37.54 | 0.0729 | 0.79 | 13.95 | 0
September | 26 | 12AM to 1AM | 78.1 | 73.7 | 72 | 118.7 | 37.32 | 0.073 | 0.79 | 13.92 | 0
September | 26 | 1AM to 2AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 26 | 2AM to 3AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 26 | 3AM to 4AM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 26 | 4AM to 5AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 26 | 5AM to 6AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 26 | 6AM to 7AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 26 | 7AM to 8AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 26 | 8AM to 9AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
September | 26 | 9AM to 10AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
September | 26 | 10AM to 11AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
September | 26 | 11AM to 12PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
September | 26 | 12PM to 1PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
September | 26 | 1PM to 2PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
September | 26 | 2PM to 3PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
September | 26 | 3PM to 4PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
September | 26 | 4PM to 5PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
September | 26 | 5PM to 6PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
September | 26 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
September | 26 | 7PM to 8PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 26 | 8PM to 9PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
September | 26 | 9PM to 10PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
September | 26 | 10PM to 11PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 26 | 11PM to 12AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
September | 27 | 12AM to 1AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
September | 27 | 1AM to 2AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
September | 27 | 2AM to 3AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
September | 27 | 3AM to 4AM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
September | 27 | 4AM to 5AM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
September | 27 | 5AM to 6AM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
September | 27 | 6AM to 7AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
September | 27 | 7AM to 8AM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
September | 27 | 8AM to 9AM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
September | 27 | 9AM to 10AM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
September | 27 | 10AM to 11AM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
September | 27 | 11AM to 12PM | 84 | 69.2 | 62.1 | 83.6 | 33.28 | 0.0725 | 0.56 | 13.97 | 0
September | 27 | 12PM to 1PM | 84.9 | 68.9 | 61 | 80.4 | 33 | 0.0724 | 0.54 | 13.98 | 0
September | 27 | 1PM to 2PM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
September | 27 | 2PM to 3PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
September | 27 | 3PM to 4PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
September | 27 | 4PM to 5PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
September | 27 | 5PM to 6PM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
September | 27 | 6PM to 7PM | 79 | 68.2 | 63 | 86.4 | 32.48 | 0.0731 | 0.58 | 13.85 | 0
September | 27 | 7PM to 8PM | 78.1 | 68.5 | 64 | 89.8 | 32.79 | 0.0732 | 0.6 | 13.83 | 0
September | 27 | 8PM to 9PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
September | 27 | 9PM to 10PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
September | 27 | 10PM to 11PM | 77 | 67.6 | 63 | 86.4 | 31.99 | 0.0734 | 0.58 | 13.8 | 0
September | 27 | 11PM to 12AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
September | 28 | 12AM to 1AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
September | 28 | 1AM to 2AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
September | 28 | 2AM to 3AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
September | 28 | 3AM to 4AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
September | 28 | 4AM to 5AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
September | 28 | 5AM to 6AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
September | 28 | 6AM to 7AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
September | 28 | 7AM to 8AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
September | 28 | 8AM to 9AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
September | 28 | 9AM to 10AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
September | 28 | 10AM to 11AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
September | 28 | 11AM to 12PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
September | 28 | 12PM to 1PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
September | 28 | 1PM to 2PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
September | 28 | 2PM to 3PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
September | 28 | 3PM to 4PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
September | 28 | 4PM to 5PM | 82.4 | 70.1 | 64.4 | 90.9 | 34.03 | 0.0726 | 0.61 | 13.95 | 0
September | 28 | 5PM to 6PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
September | 28 | 6PM to 7PM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
September | 28 | 7PM to 8PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
September | 28 | 8PM to 9PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
September | 28 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
September | 28 | 10PM to 11PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
September | 28 | 11PM to 12AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
September | 29 | 12AM to 1AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
September | 29 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
September | 29 | 2AM to 3AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
September | 29 | 3AM to 4AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
September | 29 | 4AM to 5AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
September | 29 | 5AM to 6AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
September | 29 | 6AM to 7AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
September | 29 | 7AM to 8AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
September | 29 | 8AM to 9AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
September | 29 | 9AM to 10AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
September | 29 | 10AM to 11AM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
September | 29 | 11AM to 12PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
September | 29 | 12PM to 1PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
September | 29 | 1PM to 2PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
September | 29 | 2PM to 3PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
September | 29 | 3PM to 4PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
September | 29 | 4PM to 5PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 29 | 5PM to 6PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 29 | 6PM to 7PM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
September | 29 | 7PM to 8PM | 73 | 71.6 | 71.1 | 115 | 35.5 | 0.0738 | 0.77 | 13.78 | 0
September | 29 | 8PM to 9PM | 73.9 | 72.5 | 72 | 118.7 | 36.29 | 0.0736 | 0.79 | 13.82 | 0
September | 29 | 9PM to 10PM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
September | 29 | 10PM to 11PM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
September | 29 | 11PM to 12AM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
September | 30 | 12AM to 1AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
September | 30 | 1AM to 2AM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
September | 30 | 2AM to 3AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
September | 30 | 3AM to 4AM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
September | 30 | 4AM to 5AM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
September | 30 | 5AM to 6AM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
September | 30 | 6AM to 7AM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
September | 30 | 7AM to 8AM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
September | 30 | 8AM to 9AM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
September | 30 | 9AM to 10AM | 75.9 | 73.8 | 73 | 123.2 | 37.49 | 0.0733 | 0.82 | 13.88 | 0
September | 30 | 10AM to 11AM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
September | 30 | 11AM to 12PM | 81 | 74.5 | 72 | 118.7 | 38.03 | 0.0726 | 0.79 | 14 | 0
September | 30 | 12PM to 1PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
September | 30 | 1PM to 2PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
September | 30 | 2PM to 3PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
September | 30 | 3PM to 4PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
September | 30 | 4PM to 5PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
September | 30 | 5PM to 6PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
September | 30 | 6PM to 7PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 30 | 7PM to 8PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
September | 30 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
September | 30 | 9PM to 10PM | 77.9 | 71.6 | 68.9 | 106.6 | 35.39 | 0.0731 | 0.71 | 13.88 | 0
September | 30 | 10PM to 11PM | 77.7 | 71.4 | 68.7 | 106 | 35.24 | 0.0732 | 0.71 | 13.87 | 0
September | 30 | 11PM to 12AM | 77.5 | 71.2 | 68.5 | 105.3 | 35.09 | 0.0732 | 0.7 | 13.87 | 0
October | 1 | 12AM to 1AM | 77.5 | 71.2 | 68.5 | 105.3 | 35.09 | 0.0732 | 0.7 | 13.87 | 0
October | 1 | 1AM to 2AM | 77.4 | 71.1 | 68.4 | 104.6 | 34.94 | 0.0732 | 0.7 | 13.86 | 0
October | 1 | 2AM to 3AM | 77.2 | 70.9 | 68.2 | 104 | 34.79 | 0.0732 | 0.69 | 13.85 | 0
October | 1 | 3AM to 4AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 1 | 4AM to 5AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 1 | 5AM to 6AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 1 | 6AM to 7AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 1 | 7AM to 8AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 1 | 8AM to 9AM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
October | 1 | 9AM to 10AM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
October | 1 | 10AM to 11AM | 89.1 | 72.9 | 66 | 96.3 | 36.52 | 0.0717 | 0.64 | 14.14 | 0
October | 1 | 11AM to 12PM | 90 | 72.6 | 64.9 | 92.7 | 36.17 | 0.0716 | 0.62 | 14.15 | 0
October | 1 | 12PM to 1PM | 91.9 | 73.7 | 66 | 96.3 | 37.23 | 0.0713 | 0.64 | 14.21 | 0
October | 1 | 1PM to 2PM | 91 | 72.4 | 64 | 89.8 | 35.97 | 0.0715 | 0.6 | 14.17 | 0
October | 1 | 2PM to 3PM | 91 | 73.5 | 66 | 96.3 | 37.01 | 0.0715 | 0.64 | 14.19 | 0
October | 1 | 3PM to 4PM | 90 | 73.7 | 66.9 | 99.5 | 37.23 | 0.0716 | 0.67 | 14.17 | 0
October | 1 | 4PM to 5PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
October | 1 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
October | 1 | 6PM to 7PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
October | 1 | 7PM to 8PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
October | 1 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 1 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 1 | 10PM to 11PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
October | 1 | 11PM to 12AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
October | 2 | 12AM to 1AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
October | 2 | 1AM to 2AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 2 | 2AM to 3AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
October | 2 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 2 | 4AM to 5AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 2 | 5AM to 6AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
October | 2 | 6AM to 7AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 2 | 7AM to 8AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 2 | 8AM to 9AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
October | 2 | 9AM to 10AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
October | 2 | 10AM to 11AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 2 | 11AM to 12PM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
October | 2 | 12PM to 1PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
October | 2 | 1PM to 2PM | 90 | 73.7 | 66.9 | 99.5 | 37.23 | 0.0716 | 0.67 | 14.17 | 0
October | 2 | 2PM to 3PM | 89.1 | 73.5 | 66.9 | 99.5 | 37.01 | 0.0717 | 0.67 | 14.15 | 0
October | 2 | 3PM to 4PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
October | 2 | 4PM to 5PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
October | 2 | 5PM to 6PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
October | 2 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 2 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 2 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 2 | 9PM to 10PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 2 | 10PM to 11PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 2 | 11PM to 12AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 3 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 3 | 1AM to 2AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
October | 3 | 2AM to 3AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
October | 3 | 3AM to 4AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
October | 3 | 4AM to 5AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
October | 3 | 5AM to 6AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
October | 3 | 6AM to 7AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
October | 3 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
October | 3 | 8AM to 9AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
October | 3 | 9AM to 10AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
October | 3 | 10AM to 11AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 3 | 11AM to 12PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
October | 3 | 12PM to 1PM | 90 | 71.4 | 63 | 86.4 | 35.17 | 0.0717 | 0.58 | 14.13 | 0
October | 3 | 1PM to 2PM | 90 | 71 | 62.1 | 83.6 | 34.74 | 0.0717 | 0.56 | 14.12 | 0
October | 3 | 2PM to 3PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
October | 3 | 3PM to 4PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
October | 3 | 4PM to 5PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
October | 3 | 5PM to 6PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
October | 3 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 3 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 3 | 8PM to 9PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 3 | 9PM to 10PM | 76.1 | 70.3 | 67.8 | 102.7 | 34.32 | 0.0734 | 0.69 | 13.82 | 0
October | 3 | 10PM to 11PM | 75 | 69.7 | 67.3 | 100.7 | 33.75 | 0.0736 | 0.67 | 13.79 | 0
October | 3 | 11PM to 12AM | 74.1 | 69.4 | 67.3 | 100.7 | 33.53 | 0.0737 | 0.67 | 13.77 | 0
October | 4 | 12AM to 1AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
October | 4 | 1AM to 2AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
October | 4 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 4 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 4 | 4AM to 5AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 4 | 5AM to 6AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
October | 4 | 6AM to 7AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 4 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 4 | 8AM to 9AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
October | 4 | 9AM to 10AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
October | 4 | 10AM to 11AM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
October | 4 | 11AM to 12PM | 88 | 75 | 70 | 110.8 | 38.52 | 0.0718 | 0.74 | 14.15 | 0
October | 4 | 12PM to 1PM | 88 | 75 | 70 | 110.8 | 38.52 | 0.0718 | 0.74 | 14.15 | 0
October | 4 | 1PM to 2PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
October | 4 | 2PM to 3PM | 90 | 73.7 | 66.9 | 99.5 | 37.23 | 0.0716 | 0.67 | 14.17 | 0
October | 4 | 3PM to 4PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
October | 4 | 4PM to 5PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
October | 4 | 5PM to 6PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
October | 4 | 6PM to 7PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
October | 4 | 7PM to 8PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 4 | 8PM to 9PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 4 | 9PM to 10PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 4 | 10PM to 11PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 4 | 11PM to 12AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 5 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 5 | 1AM to 2AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 5 | 2AM to 3AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 5 | 3AM to 4AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 5 | 4AM to 5AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 5 | 5AM to 6AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 5 | 6AM to 7AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 5 | 7AM to 8AM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
October | 5 | 8AM to 9AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
October | 5 | 9AM to 10AM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
October | 5 | 10AM to 11AM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
October | 5 | 11AM to 12PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
October | 5 | 12PM to 1PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
October | 5 | 1PM to 2PM | 90 | 72.6 | 64.9 | 92.7 | 36.17 | 0.0716 | 0.62 | 14.15 | 0
October | 5 | 2PM to 3PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
October | 5 | 3PM to 4PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
October | 5 | 4PM to 5PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
October | 5 | 5PM to 6PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
October | 5 | 6PM to 7PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 5 | 7PM to 8PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 5 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 5 | 9PM to 10PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 5 | 10PM to 11PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 5 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 6 | 12AM to 1AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 6 | 1AM to 2AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 6 | 2AM to 3AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 6 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 6 | 4AM to 5AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 6 | 5AM to 6AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 6 | 6AM to 7AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 6 | 7AM to 8AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
October | 6 | 8AM to 9AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
October | 6 | 9AM to 10AM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
October | 6 | 10AM to 11AM | 87.1 | 74.8 | 70 | 110.8 | 38.3 | 0.0719 | 0.74 | 14.13 | 0
October | 6 | 11AM to 12PM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
October | 6 | 12PM to 1PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
October | 6 | 1PM to 2PM | 88 | 73.8 | 68 | 103.3 | 37.35 | 0.0718 | 0.69 | 14.13 | 0
October | 6 | 2PM to 3PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 6 | 3PM to 4PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
October | 6 | 4PM to 5PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
October | 6 | 5PM to 6PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
October | 6 | 6PM to 7PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 6 | 7PM to 8PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
October | 6 | 8PM to 9PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
October | 6 | 9PM to 10PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 6 | 10PM to 11PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 6 | 11PM to 12AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 7 | 12AM to 1AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 7 | 1AM to 2AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 7 | 2AM to 3AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 7 | 3AM to 4AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
October | 7 | 4AM to 5AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 7 | 5AM to 6AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 7 | 6AM to 7AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 7 | 7AM to 8AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 7 | 8AM to 9AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
October | 7 | 9AM to 10AM | 77 | 73.4 | 72 | 118.7 | 37.05 | 0.0732 | 0.79 | 13.9 | 0
October | 7 | 10AM to 11AM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
October | 7 | 11AM to 12PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
October | 7 | 12PM to 1PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 7 | 1PM to 2PM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
October | 7 | 2PM to 3PM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
October | 7 | 3PM to 4PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 7 | 4PM to 5PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 7 | 5PM to 6PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
October | 7 | 6PM to 7PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
October | 7 | 7PM to 8PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 7 | 8PM to 9PM | 75.9 | 72.5 | 71.1 | 115 | 36.21 | 0.0734 | 0.77 | 13.86 | 0
October | 7 | 9PM to 10PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
October | 7 | 10PM to 11PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
October | 7 | 11PM to 12AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 8 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 8 | 1AM to 2AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 8 | 2AM to 3AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
October | 8 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 8 | 4AM to 5AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 8 | 5AM to 6AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 8 | 6AM to 7AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 8 | 7AM to 8AM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
October | 8 | 8AM to 9AM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
October | 8 | 9AM to 10AM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
October | 8 | 10AM to 11AM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
October | 8 | 11AM to 12PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
October | 8 | 12PM to 1PM | 91 | 72.4 | 64 | 89.8 | 35.97 | 0.0715 | 0.6 | 14.17 | 0
October | 8 | 1PM to 2PM | 90 | 72.6 | 64.9 | 92.7 | 36.17 | 0.0716 | 0.62 | 14.15 | 0
October | 8 | 2PM to 3PM | 89.1 | 71.2 | 63 | 86.4 | 34.95 | 0.0718 | 0.58 | 14.11 | 0
October | 8 | 3PM to 4PM | 87.1 | 70.6 | 63 | 86.4 | 34.47 | 0.072 | 0.58 | 14.05 | 0
October | 8 | 4PM to 5PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
October | 8 | 5PM to 6PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
October | 8 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
October | 8 | 7PM to 8PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
October | 8 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 8 | 9PM to 10PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 8 | 10PM to 11PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 8 | 11PM to 12AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
October | 9 | 12AM to 1AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 9 | 1AM to 2AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 9 | 2AM to 3AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 9 | 3AM to 4AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 9 | 4AM to 5AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 9 | 5AM to 6AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 9 | 6AM to 7AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
October | 9 | 7AM to 8AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 9 | 8AM to 9AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 9 | 9AM to 10AM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
October | 9 | 10AM to 11AM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
October | 9 | 11AM to 12PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
October | 9 | 12PM to 1PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
October | 9 | 1PM to 2PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
October | 9 | 2PM to 3PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
October | 9 | 3PM to 4PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 9 | 4PM to 5PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
October | 9 | 5PM to 6PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
October | 9 | 6PM to 7PM | 75 | 72.8 | 72 | 118.7 | 36.56 | 0.0735 | 0.79 | 13.84 | 0
October | 9 | 7PM to 8PM | 73.9 | 72.5 | 72 | 118.7 | 36.29 | 0.0736 | 0.79 | 13.82 | 0
October | 9 | 8PM to 9PM | 75 | 72.2 | 71.1 | 115 | 35.99 | 0.0735 | 0.77 | 13.83 | 0
October | 9 | 9PM to 10PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
October | 9 | 10PM to 11PM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
October | 9 | 11PM to 12AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
October | 10 | 12AM to 1AM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
October | 10 | 1AM to 2AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 10 | 2AM to 3AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 10 | 3AM to 4AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 10 | 4AM to 5AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 10 | 5AM to 6AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 10 | 6AM to 7AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 10 | 7AM to 8AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
October | 10 | 8AM to 9AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
October | 10 | 9AM to 10AM | 86 | 74.5 | 70 | 110.8 | 38.03 | 0.072 | 0.74 | 14.1 | 0
October | 10 | 10AM to 11AM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
October | 10 | 11AM to 12PM | 86 | 75.8 | 72 | 118.7 | 39.28 | 0.072 | 0.79 | 14.13 | 0
October | 10 | 12PM to 1PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
October | 10 | 1PM to 2PM | 84.9 | 74.9 | 71.1 | 115 | 38.43 | 0.0721 | 0.77 | 14.09 | 0
October | 10 | 2PM to 3PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
October | 10 | 3PM to 4PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
October | 10 | 4PM to 5PM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
October | 10 | 5PM to 6PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
October | 10 | 6PM to 7PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
October | 10 | 7PM to 8PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
October | 10 | 8PM to 9PM | 78.1 | 73.1 | 71.1 | 115 | 36.74 | 0.0731 | 0.77 | 13.91 | 0
October | 10 | 9PM to 10PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
October | 10 | 10PM to 11PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
October | 10 | 11PM to 12AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
October | 11 | 12AM to 1AM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
October | 11 | 1AM to 2AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
October | 11 | 2AM to 3AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
October | 11 | 3AM to 4AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 11 | 4AM to 5AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 11 | 5AM to 6AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 11 | 6AM to 7AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 11 | 7AM to 8AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 11 | 8AM to 9AM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
October | 11 | 9AM to 10AM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
October | 11 | 10AM to 11AM | 89.1 | 72.9 | 66 | 96.3 | 36.52 | 0.0717 | 0.64 | 14.14 | 0
October | 11 | 11AM to 12PM | 90 | 73.2 | 66 | 96.3 | 36.74 | 0.0716 | 0.64 | 14.16 | 0
October | 11 | 12PM to 1PM | 91.9 | 73.7 | 66 | 96.3 | 37.23 | 0.0713 | 0.64 | 14.21 | 0
October | 11 | 1PM to 2PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
October | 11 | 2PM to 3PM | 89.1 | 74.1 | 68 | 103.3 | 37.62 | 0.0717 | 0.69 | 14.16 | 0
October | 11 | 3PM to 4PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
October | 11 | 4PM to 5PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
October | 11 | 5PM to 6PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
October | 11 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
October | 11 | 7PM to 8PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 11 | 8PM to 9PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 11 | 9PM to 10PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 11 | 10PM to 11PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 11 | 11PM to 12AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 12 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 12 | 1AM to 2AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 12 | 2AM to 3AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 12 | 3AM to 4AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 12 | 4AM to 5AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 12 | 5AM to 6AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 12 | 6AM to 7AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 12 | 7AM to 8AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
October | 12 | 8AM to 9AM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
October | 12 | 9AM to 10AM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
October | 12 | 10AM to 11AM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
October | 12 | 11AM to 12PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
October | 12 | 12PM to 1PM | 86 | 75.2 | 71.1 | 115 | 38.7 | 0.072 | 0.77 | 14.12 | 0
October | 12 | 1PM to 2PM | 84 | 74.7 | 71.1 | 115 | 38.21 | 0.0723 | 0.77 | 14.07 | 0
October | 12 | 2PM to 3PM | 84 | 75.3 | 72 | 118.7 | 38.79 | 0.0722 | 0.79 | 14.08 | 0
October | 12 | 3PM to 4PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
October | 12 | 4PM to 5PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
October | 12 | 5PM to 6PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
October | 12 | 6PM to 7PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 12 | 7PM to 8PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 12 | 8PM to 9PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 12 | 9PM to 10PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 12 | 10PM to 11PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 12 | 11PM to 12AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 13 | 12AM to 1AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 13 | 1AM to 2AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 13 | 2AM to 3AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 13 | 3AM to 4AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
October | 13 | 4AM to 5AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
October | 13 | 5AM to 6AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
October | 13 | 6AM to 7AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 13 | 7AM to 8AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
October | 13 | 8AM to 9AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 13 | 9AM to 10AM | 82.9 | 74.4 | 71.1 | 115 | 37.94 | 0.0724 | 0.77 | 14.04 | 0
October | 13 | 10AM to 11AM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
October | 13 | 11AM to 12PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 13 | 12PM to 1PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
October | 13 | 1PM to 2PM | 89.1 | 72.9 | 66 | 96.3 | 36.52 | 0.0717 | 0.64 | 14.14 | 0
October | 13 | 2PM to 3PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
October | 13 | 3PM to 4PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 13 | 4PM to 5PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
October | 13 | 5PM to 6PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
October | 13 | 6PM to 7PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
October | 13 | 7PM to 8PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 13 | 8PM to 9PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 13 | 9PM to 10PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
October | 13 | 10PM to 11PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 13 | 11PM to 12AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 14 | 12AM to 1AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 14 | 1AM to 2AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 14 | 2AM to 3AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 14 | 3AM to 4AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
October | 14 | 4AM to 5AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 14 | 5AM to 6AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
October | 14 | 6AM to 7AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
October | 14 | 7AM to 8AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
October | 14 | 8AM to 9AM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
October | 14 | 9AM to 10AM | 87.1 | 75.5 | 71.1 | 115 | 38.97 | 0.0719 | 0.77 | 14.15 | 0
October | 14 | 10AM to 11AM | 88 | 75.7 | 71.1 | 115 | 39.19 | 0.0717 | 0.77 | 14.17 | 0
October | 14 | 11AM to 12PM | 88 | 75.7 | 71.1 | 115 | 39.19 | 0.0717 | 0.77 | 14.17 | 0
October | 14 | 12PM to 1PM | 89.1 | 75.3 | 70 | 110.8 | 38.79 | 0.0716 | 0.74 | 14.18 | 0
October | 14 | 1PM to 2PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
October | 14 | 2PM to 3PM | 87.1 | 74.8 | 70 | 110.8 | 38.3 | 0.0719 | 0.74 | 14.13 | 0
October | 14 | 3PM to 4PM | 87.1 | 74.8 | 70 | 110.8 | 38.3 | 0.0719 | 0.74 | 14.13 | 0
October | 14 | 4PM to 5PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
October | 14 | 5PM to 6PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
October | 14 | 6PM to 7PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
October | 14 | 7PM to 8PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 14 | 8PM to 9PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 14 | 9PM to 10PM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
October | 14 | 10PM to 11PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
October | 14 | 11PM to 12AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
October | 15 | 12AM to 1AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 15 | 1AM to 2AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 15 | 2AM to 3AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 15 | 3AM to 4AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 15 | 4AM to 5AM | 71.1 | 69.7 | 69.1 | 107.3 | 33.8 | 0.0741 | 0.72 | 13.71 | 0
October | 15 | 5AM to 6AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 15 | 6AM to 7AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 15 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
October | 15 | 8AM to 9AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 15 | 9AM to 10AM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
October | 15 | 10AM to 11AM | 87.1 | 75.5 | 71.1 | 115 | 38.97 | 0.0719 | 0.77 | 14.15 | 0
October | 15 | 11AM to 12PM | 87.1 | 75.5 | 71.1 | 115 | 38.97 | 0.0719 | 0.77 | 14.15 | 0
October | 15 | 12PM to 1PM | 90 | 75.6 | 70 | 110.8 | 39.01 | 0.0715 | 0.74 | 14.21 | 0
October | 15 | 1PM to 2PM | 89.1 | 76.6 | 72 | 118.7 | 40.03 | 0.0716 | 0.79 | 14.21 | 0
October | 15 | 2PM to 3PM | 88 | 76.3 | 72 | 118.7 | 39.77 | 0.0717 | 0.79 | 14.18 | 0
October | 15 | 3PM to 4PM | 88 | 75.7 | 71.1 | 115 | 39.19 | 0.0717 | 0.77 | 14.17 | 0
October | 15 | 4PM to 5PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
October | 15 | 5PM to 6PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
October | 15 | 6PM to 7PM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
October | 15 | 7PM to 8PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 15 | 8PM to 9PM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
October | 15 | 9PM to 10PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 15 | 10PM to 11PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
October | 15 | 11PM to 12AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 16 | 12AM to 1AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 16 | 1AM to 2AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 16 | 2AM to 3AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 16 | 3AM to 4AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 16 | 4AM to 5AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 16 | 5AM to 6AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 16 | 6AM to 7AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 16 | 7AM to 8AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 16 | 8AM to 9AM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 16 | 9AM to 10AM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
October | 16 | 10AM to 11AM | 87.1 | 74.8 | 70 | 110.8 | 38.3 | 0.0719 | 0.74 | 14.13 | 0
October | 16 | 11AM to 12PM | 88 | 75.7 | 71.1 | 115 | 39.19 | 0.0717 | 0.77 | 14.17 | 0
October | 16 | 12PM to 1PM | 77 | 72.8 | 71.1 | 115 | 36.47 | 0.0732 | 0.77 | 13.88 | 0
October | 16 | 1PM to 2PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
October | 16 | 2PM to 3PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
October | 16 | 3PM to 4PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
October | 16 | 4PM to 5PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
October | 16 | 5PM to 6PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 16 | 6PM to 7PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 16 | 7PM to 8PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 16 | 8PM to 9PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 16 | 9PM to 10PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 16 | 10PM to 11PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 16 | 11PM to 12AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 17 | 12AM to 1AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
October | 17 | 1AM to 2AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
October | 17 | 2AM to 3AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
October | 17 | 3AM to 4AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
October | 17 | 4AM to 5AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
October | 17 | 5AM to 6AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
October | 17 | 6AM to 7AM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
October | 17 | 7AM to 8AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
October | 17 | 8AM to 9AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
October | 17 | 9AM to 10AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
October | 17 | 10AM to 11AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
October | 17 | 11AM to 12PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
October | 17 | 12PM to 1PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
October | 17 | 1PM to 2PM | 82.9 | 69.4 | 63 | 86.4 | 33.45 | 0.0726 | 0.58 | 13.95 | 0
October | 17 | 2PM to 3PM | 82.9 | 68.3 | 61 | 80.4 | 32.52 | 0.0726 | 0.54 | 13.93 | 0
October | 17 | 3PM to 4PM | 82 | 69.1 | 63 | 86.4 | 33.23 | 0.0727 | 0.58 | 13.92 | 0
October | 17 | 4PM to 5PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
October | 17 | 5PM to 6PM | 78.1 | 67.9 | 63 | 86.4 | 32.26 | 0.0732 | 0.58 | 13.82 | 0
October | 17 | 6PM to 7PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
October | 17 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
October | 17 | 8PM to 9PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
October | 17 | 9PM to 10PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
October | 17 | 10PM to 11PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
October | 17 | 11PM to 12AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 18 | 12AM to 1AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 18 | 1AM to 2AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 18 | 2AM to 3AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 18 | 3AM to 4AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
October | 18 | 4AM to 5AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
October | 18 | 5AM to 6AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
October | 18 | 6AM to 7AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
October | 18 | 7AM to 8AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
October | 18 | 8AM to 9AM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
October | 18 | 9AM to 10AM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
October | 18 | 10AM to 11AM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
October | 18 | 11AM to 12PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
October | 18 | 12PM to 1PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
October | 18 | 1PM to 2PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
October | 18 | 2PM to 3PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
October | 18 | 3PM to 4PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
October | 18 | 4PM to 5PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
October | 18 | 5PM to 6PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
October | 18 | 6PM to 7PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
October | 18 | 7PM to 8PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
October | 18 | 8PM to 9PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
October | 18 | 9PM to 10PM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
October | 18 | 10PM to 11PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
October | 18 | 11PM to 12AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
October | 19 | 12AM to 1AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
October | 19 | 1AM to 2AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
October | 19 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
October | 19 | 3AM to 4AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
October | 19 | 4AM to 5AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
October | 19 | 5AM to 6AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
October | 19 | 6AM to 7AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
October | 19 | 7AM to 8AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
October | 19 | 8AM to 9AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
October | 19 | 9AM to 10AM | 84.9 | 69.5 | 62.1 | 83.6 | 33.51 | 0.0723 | 0.56 | 13.99 | 0
October | 19 | 10AM to 11AM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
October | 19 | 11AM to 12PM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
October | 19 | 12PM to 1PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
October | 19 | 1PM to 2PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
October | 19 | 2PM to 3PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
October | 19 | 3PM to 4PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
October | 19 | 4PM to 5PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
October | 19 | 5PM to 6PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
October | 19 | 6PM to 7PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
October | 19 | 7PM to 8PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
October | 19 | 8PM to 9PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
October | 19 | 9PM to 10PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
October | 19 | 10PM to 11PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 19 | 11PM to 12AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
October | 20 | 12AM to 1AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
October | 20 | 1AM to 2AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
October | 20 | 2AM to 3AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
October | 20 | 3AM to 4AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
October | 20 | 4AM to 5AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
October | 20 | 5AM to 6AM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
October | 20 | 6AM to 7AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
October | 20 | 7AM to 8AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
October | 20 | 8AM to 9AM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
October | 20 | 9AM to 10AM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
October | 20 | 10AM to 11AM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
October | 20 | 11AM to 12PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
October | 20 | 12PM to 1PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
October | 20 | 1PM to 2PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
October | 20 | 2PM to 3PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
October | 20 | 3PM to 4PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
October | 20 | 4PM to 5PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
October | 20 | 5PM to 6PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
October | 20 | 6PM to 7PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
October | 20 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
October | 20 | 8PM to 9PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
October | 20 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 20 | 10PM to 11PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
October | 20 | 11PM to 12AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
October | 21 | 12AM to 1AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
October | 21 | 1AM to 2AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 21 | 2AM to 3AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
October | 21 | 3AM to 4AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
October | 21 | 4AM to 5AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 21 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 21 | 6AM to 7AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 21 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 21 | 8AM to 9AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
October | 21 | 9AM to 10AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 21 | 10AM to 11AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 21 | 11AM to 12PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
October | 21 | 12PM to 1PM | 89.1 | 74.1 | 68 | 103.3 | 37.62 | 0.0717 | 0.69 | 14.16 | 0
October | 21 | 1PM to 2PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 21 | 2PM to 3PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
October | 21 | 3PM to 4PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
October | 21 | 4PM to 5PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
October | 21 | 5PM to 6PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
October | 21 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 21 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
October | 21 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 21 | 9PM to 10PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 21 | 10PM to 11PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 21 | 11PM to 12AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
October | 22 | 12AM to 1AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 22 | 1AM to 2AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 22 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 22 | 3AM to 4AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 22 | 4AM to 5AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
October | 22 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
October | 22 | 6AM to 7AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 22 | 7AM to 8AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
October | 22 | 8AM to 9AM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
October | 22 | 9AM to 10AM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
October | 22 | 10AM to 11AM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
October | 22 | 11AM to 12PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
October | 22 | 12PM to 1PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
October | 22 | 1PM to 2PM | 84.9 | 74.9 | 71.1 | 115 | 38.43 | 0.0721 | 0.77 | 14.09 | 0
October | 22 | 2PM to 3PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
October | 22 | 3PM to 4PM | 80.1 | 73.6 | 71.1 | 115 | 37.23 | 0.0728 | 0.77 | 13.96 | 0
October | 22 | 4PM to 5PM | 75.9 | 73.1 | 72 | 118.7 | 36.78 | 0.0733 | 0.79 | 13.87 | 0
October | 22 | 5PM to 6PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 22 | 6PM to 7PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 22 | 7PM to 8PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
October | 22 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 22 | 9PM to 10PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 22 | 10PM to 11PM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 22 | 11PM to 12AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 23 | 12AM to 1AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 23 | 1AM to 2AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 23 | 2AM to 3AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 23 | 3AM to 4AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
October | 23 | 4AM to 5AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
October | 23 | 5AM to 6AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
October | 23 | 6AM to 7AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
October | 23 | 7AM to 8AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
October | 23 | 8AM to 9AM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
October | 23 | 9AM to 10AM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
October | 23 | 10AM to 11AM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
October | 23 | 11AM to 12PM | 88 | 74.5 | 69.1 | 107.3 | 37.98 | 0.0718 | 0.72 | 14.14 | 0
October | 23 | 12PM to 1PM | 88 | 73.2 | 66.9 | 99.5 | 36.74 | 0.0718 | 0.67 | 14.12 | 0
October | 23 | 1PM to 2PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 23 | 2PM to 3PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
October | 23 | 3PM to 4PM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
October | 23 | 4PM to 5PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
October | 23 | 5PM to 6PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
October | 23 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 23 | 7PM to 8PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 23 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
October | 23 | 9PM to 10PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 23 | 10PM to 11PM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
October | 23 | 11PM to 12AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
October | 24 | 12AM to 1AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
October | 24 | 1AM to 2AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
October | 24 | 2AM to 3AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 24 | 3AM to 4AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 24 | 4AM to 5AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 24 | 5AM to 6AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 24 | 6AM to 7AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
October | 24 | 7AM to 8AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
October | 24 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
October | 24 | 9AM to 10AM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
October | 24 | 10AM to 11AM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
October | 24 | 11AM to 12PM | 82.9 | 73.7 | 70 | 110.8 | 37.28 | 0.0724 | 0.74 | 14.02 | 0
October | 24 | 12PM to 1PM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
October | 24 | 1PM to 2PM | 81 | 73.9 | 71.1 | 115 | 37.45 | 0.0727 | 0.77 | 13.99 | 0
October | 24 | 2PM to 3PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
October | 24 | 3PM to 4PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
October | 24 | 4PM to 5PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
October | 24 | 5PM to 6PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
October | 24 | 6PM to 7PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 24 | 7PM to 8PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 24 | 8PM to 9PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 24 | 9PM to 10PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 24 | 10PM to 11PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
October | 24 | 11PM to 12AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
October | 25 | 12AM to 1AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 25 | 1AM to 2AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 25 | 2AM to 3AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 25 | 3AM to 4AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
October | 25 | 4AM to 5AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
October | 25 | 5AM to 6AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 25 | 6AM to 7AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
October | 25 | 7AM to 8AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
October | 25 | 8AM to 9AM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
October | 25 | 9AM to 10AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
October | 25 | 10AM to 11AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
October | 25 | 11AM to 12PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
October | 25 | 12PM to 1PM | 89.1 | 72.3 | 64.9 | 92.7 | 35.95 | 0.0717 | 0.62 | 14.13 | 0
October | 25 | 1PM to 2PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
October | 25 | 2PM to 3PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
October | 25 | 3PM to 4PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
October | 25 | 4PM to 5PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
October | 25 | 5PM to 6PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
October | 25 | 6PM to 7PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
October | 25 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
October | 25 | 8PM to 9PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
October | 25 | 9PM to 10PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
October | 25 | 10PM to 11PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
October | 25 | 11PM to 12AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
October | 26 | 12AM to 1AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
October | 26 | 1AM to 2AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
October | 26 | 2AM to 3AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
October | 26 | 3AM to 4AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
October | 26 | 4AM to 5AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
October | 26 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
October | 26 | 6AM to 7AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
October | 26 | 7AM to 8AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 26 | 8AM to 9AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
October | 26 | 9AM to 10AM | 84.9 | 70 | 63 | 86.4 | 33.94 | 0.0723 | 0.58 | 14 | 0
October | 26 | 10AM to 11AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
October | 26 | 11AM to 12PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
October | 26 | 12PM to 1PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
October | 26 | 1PM to 2PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
October | 26 | 2PM to 3PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
October | 26 | 3PM to 4PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
October | 26 | 4PM to 5PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
October | 26 | 5PM to 6PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
October | 26 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
October | 26 | 7PM to 8PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
October | 26 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 26 | 9PM to 10PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
October | 26 | 10PM to 11PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 26 | 11PM to 12AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 27 | 12AM to 1AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
October | 27 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
October | 27 | 2AM to 3AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
October | 27 | 3AM to 4AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
October | 27 | 4AM to 5AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
October | 27 | 5AM to 6AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 27 | 6AM to 7AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 27 | 7AM to 8AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
October | 27 | 8AM to 9AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
October | 27 | 9AM to 10AM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
October | 27 | 10AM to 11AM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
October | 27 | 11AM to 12PM | 86 | 69.8 | 62.1 | 83.6 | 33.77 | 0.0722 | 0.56 | 14.02 | 0
October | 27 | 12PM to 1PM | 86 | 69.8 | 62.1 | 83.6 | 33.77 | 0.0722 | 0.56 | 14.02 | 0
October | 27 | 1PM to 2PM | 86 | 70.3 | 63 | 86.4 | 34.2 | 0.0722 | 0.58 | 14.03 | 0
October | 27 | 2PM to 3PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
October | 27 | 3PM to 4PM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
October | 27 | 4PM to 5PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
October | 27 | 5PM to 6PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
October | 27 | 6PM to 7PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
October | 27 | 7PM to 8PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
October | 27 | 8PM to 9PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
October | 27 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
October | 27 | 10PM to 11PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
October | 27 | 11PM to 12AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
October | 28 | 12AM to 1AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
October | 28 | 1AM to 2AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
October | 28 | 2AM to 3AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 28 | 3AM to 4AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
October | 28 | 4AM to 5AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
October | 28 | 5AM to 6AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 28 | 6AM to 7AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
October | 28 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
October | 28 | 8AM to 9AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
October | 28 | 9AM to 10AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
October | 28 | 10AM to 11AM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
October | 28 | 11AM to 12PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
October | 28 | 12PM to 1PM | 88 | 72 | 64.9 | 92.7 | 35.68 | 0.0719 | 0.62 | 14.1 | 0
October | 28 | 1PM to 2PM | 88 | 72.6 | 66 | 96.3 | 36.25 | 0.0719 | 0.64 | 14.11 | 0
October | 28 | 2PM to 3PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
October | 28 | 3PM to 4PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
October | 28 | 4PM to 5PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
October | 28 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
October | 28 | 6PM to 7PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
October | 28 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
October | 28 | 8PM to 9PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
October | 28 | 9PM to 10PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 28 | 10PM to 11PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 28 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
October | 29 | 12AM to 1AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
October | 29 | 1AM to 2AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
October | 29 | 2AM to 3AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
October | 29 | 3AM to 4AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
October | 29 | 4AM to 5AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
October | 29 | 5AM to 6AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
October | 29 | 6AM to 7AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
October | 29 | 7AM to 8AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
October | 29 | 8AM to 9AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
October | 29 | 9AM to 10AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
October | 29 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
October | 29 | 11AM to 12PM | 87.1 | 70.6 | 63 | 86.4 | 34.47 | 0.072 | 0.58 | 14.05 | 0
October | 29 | 12PM to 1PM | 86 | 70.9 | 64 | 89.8 | 34.74 | 0.0722 | 0.6 | 14.04 | 0
October | 29 | 1PM to 2PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
October | 29 | 2PM to 3PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
October | 29 | 3PM to 4PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
October | 29 | 4PM to 5PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
October | 29 | 5PM to 6PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
October | 29 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
October | 29 | 7PM to 8PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
October | 29 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
October | 29 | 9PM to 10PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 29 | 10PM to 11PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 29 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
October | 30 | 12AM to 1AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
October | 30 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 30 | 2AM to 3AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 30 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
October | 30 | 4AM to 5AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 30 | 5AM to 6AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
October | 30 | 6AM to 7AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
October | 30 | 7AM to 8AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
October | 30 | 8AM to 9AM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
October | 30 | 9AM to 10AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
October | 30 | 10AM to 11AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
October | 30 | 11AM to 12PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
October | 30 | 12PM to 1PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
October | 30 | 1PM to 2PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
October | 30 | 2PM to 3PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
October | 30 | 3PM to 4PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
October | 30 | 4PM to 5PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
October | 30 | 5PM to 6PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
October | 30 | 6PM to 7PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 30 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 30 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 30 | 9PM to 10PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
October | 30 | 10PM to 11PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
October | 30 | 11PM to 12AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
October | 31 | 12AM to 1AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
October | 31 | 1AM to 2AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
October | 31 | 2AM to 3AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
October | 31 | 3AM to 4AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
October | 31 | 4AM to 5AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
October | 31 | 5AM to 6AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
October | 31 | 6AM to 7AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
October | 31 | 7AM to 8AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
October | 31 | 8AM to 9AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
October | 31 | 9AM to 10AM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
October | 31 | 10AM to 11AM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
October | 31 | 11AM to 12PM | 88 | 71.5 | 64 | 89.8 | 35.22 | 0.0719 | 0.6 | 14.09 | 0
October | 31 | 12PM to 1PM | 87.1 | 70.6 | 63 | 86.4 | 34.47 | 0.072 | 0.58 | 14.05 | 0
October | 31 | 1PM to 2PM | 87.1 | 71.2 | 64 | 89.8 | 35 | 0.072 | 0.6 | 14.07 | 0
October | 31 | 2PM to 3PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
October | 31 | 3PM to 4PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
October | 31 | 4PM to 5PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
October | 31 | 5PM to 6PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
October | 31 | 6PM to 7PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
October | 31 | 7PM to 8PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
October | 31 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
October | 31 | 9PM to 10PM | 75.7 | 69.3 | 66.4 | 97.6 | 33.43 | 0.0735 | 0.65 | 13.8 | 0
October | 31 | 10PM to 11PM | 75.7 | 69.4 | 66.6 | 98.2 | 33.53 | 0.0735 | 0.66 | 13.8 | 0
October | 31 | 11PM to 12AM | 75.6 | 69.6 | 66.9 | 99.5 | 33.68 | 0.0735 | 0.67 | 13.8 | 0
November | 1 | 12AM to 1AM | 75.4 | 69.6 | 67.1 | 100.1 | 33.74 | 0.0735 | 0.67 | 13.8 | 0
November | 1 | 1AM to 2AM | 75.2 | 69.8 | 67.5 | 101.4 | 33.9 | 0.0735 | 0.68 | 13.8 | 0
November | 1 | 2AM to 3AM | 75.2 | 69.9 | 67.6 | 102 | 34 | 0.0735 | 0.68 | 13.8 | 0
November | 1 | 3AM to 4AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
November | 1 | 4AM to 5AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 1 | 5AM to 6AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 1 | 6AM to 7AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 1 | 7AM to 8AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
November | 1 | 8AM to 9AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
November | 1 | 9AM to 10AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
November | 1 | 10AM to 11AM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
November | 1 | 11AM to 12PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
November | 1 | 12PM to 1PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
November | 1 | 1PM to 2PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
November | 1 | 2PM to 3PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
November | 1 | 3PM to 4PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
November | 1 | 4PM to 5PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
November | 1 | 5PM to 6PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 1 | 6PM to 7PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
November | 1 | 7PM to 8PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 1 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 1 | 9PM to 10PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 1 | 10PM to 11PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 1 | 11PM to 12AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 2 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 2 | 1AM to 2AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 2 | 2AM to 3AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 2 | 3AM to 4AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
November | 2 | 4AM to 5AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
November | 2 | 5AM to 6AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
November | 2 | 6AM to 7AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
November | 2 | 7AM to 8AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
November | 2 | 8AM to 9AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
November | 2 | 9AM to 10AM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
November | 2 | 10AM to 11AM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
November | 2 | 11AM to 12PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
November | 2 | 12PM to 1PM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
November | 2 | 1PM to 2PM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
November | 2 | 2PM to 3PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
November | 2 | 3PM to 4PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
November | 2 | 4PM to 5PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
November | 2 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
November | 2 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 2 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
November | 2 | 8PM to 9PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 2 | 9PM to 10PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 2 | 10PM to 11PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 2 | 11PM to 12AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 3 | 12AM to 1AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 3 | 1AM to 2AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 3 | 2AM to 3AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 3 | 3AM to 4AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 3 | 4AM to 5AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
November | 3 | 5AM to 6AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
November | 3 | 6AM to 7AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 3 | 7AM to 8AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
November | 3 | 8AM to 9AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
November | 3 | 9AM to 10AM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
November | 3 | 10AM to 11AM | 84.9 | 73.6 | 69.1 | 107.3 | 37.22 | 0.0722 | 0.72 | 14.06 | 0
November | 3 | 11AM to 12PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
November | 3 | 12PM to 1PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
November | 3 | 1PM to 2PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
November | 3 | 2PM to 3PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
November | 3 | 3PM to 4PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
November | 3 | 4PM to 5PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
November | 3 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
November | 3 | 6PM to 7PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
November | 3 | 7PM to 8PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 3 | 8PM to 9PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
November | 3 | 9PM to 10PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
November | 3 | 10PM to 11PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 3 | 11PM to 12AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
November | 4 | 12AM to 1AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 4 | 1AM to 2AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 4 | 2AM to 3AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 4 | 3AM to 4AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 4 | 4AM to 5AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 4 | 5AM to 6AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 4 | 6AM to 7AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 4 | 7AM to 8AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
November | 4 | 8AM to 9AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
November | 4 | 9AM to 10AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
November | 4 | 10AM to 11AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
November | 4 | 11AM to 12PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
November | 4 | 12PM to 1PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
November | 4 | 1PM to 2PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
November | 4 | 2PM to 3PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
November | 4 | 3PM to 4PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
November | 4 | 4PM to 5PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
November | 4 | 5PM to 6PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
November | 4 | 6PM to 7PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
November | 4 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
November | 4 | 8PM to 9PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
November | 4 | 9PM to 10PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 4 | 10PM to 11PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 4 | 11PM to 12AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 5 | 12AM to 1AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
November | 5 | 1AM to 2AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 5 | 2AM to 3AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
November | 5 | 3AM to 4AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
November | 5 | 4AM to 5AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 5 | 5AM to 6AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 5 | 6AM to 7AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 5 | 7AM to 8AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
November | 5 | 8AM to 9AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
November | 5 | 9AM to 10AM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
November | 5 | 10AM to 11AM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
November | 5 | 11AM to 12PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
November | 5 | 12PM to 1PM | 87.1 | 72.4 | 66 | 96.3 | 36.03 | 0.072 | 0.64 | 14.09 | 0
November | 5 | 1PM to 2PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
November | 5 | 2PM to 3PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
November | 5 | 3PM to 4PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
November | 5 | 4PM to 5PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
November | 5 | 5PM to 6PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
November | 5 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 5 | 7PM to 8PM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
November | 5 | 8PM to 9PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
November | 5 | 9PM to 10PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
November | 5 | 10PM to 11PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
November | 5 | 11PM to 12AM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
November | 6 | 12AM to 1AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 6 | 1AM to 2AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 6 | 2AM to 3AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 6 | 3AM to 4AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
November | 6 | 4AM to 5AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 6 | 5AM to 6AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 6 | 6AM to 7AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 6 | 7AM to 8AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 6 | 8AM to 9AM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
November | 6 | 9AM to 10AM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
November | 6 | 10AM to 11AM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
November | 6 | 11AM to 12PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
November | 6 | 12PM to 1PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
November | 6 | 1PM to 2PM | 87.1 | 72.9 | 66.9 | 99.5 | 36.52 | 0.072 | 0.67 | 14.1 | 0
November | 6 | 2PM to 3PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
November | 6 | 3PM to 4PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
November | 6 | 4PM to 5PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
November | 6 | 5PM to 6PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
November | 6 | 6PM to 7PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
November | 6 | 7PM to 8PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 6 | 8PM to 9PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
November | 6 | 9PM to 10PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 6 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 6 | 11PM to 12AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
November | 7 | 12AM to 1AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 7 | 1AM to 2AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 7 | 2AM to 3AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 7 | 3AM to 4AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
November | 7 | 4AM to 5AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 7 | 5AM to 6AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 7 | 6AM to 7AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 7 | 7AM to 8AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
November | 7 | 8AM to 9AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
November | 7 | 9AM to 10AM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
November | 7 | 10AM to 11AM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
November | 7 | 11AM to 12PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
November | 7 | 12PM to 1PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
November | 7 | 1PM to 2PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
November | 7 | 2PM to 3PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
November | 7 | 3PM to 4PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
November | 7 | 4PM to 5PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
November | 7 | 5PM to 6PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
November | 7 | 6PM to 7PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
November | 7 | 7PM to 8PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
November | 7 | 8PM to 9PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
November | 7 | 9PM to 10PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 7 | 10PM to 11PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
November | 7 | 11PM to 12AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 8 | 12AM to 1AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
November | 8 | 1AM to 2AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
November | 8 | 2AM to 3AM | 73 | 70.3 | 69.1 | 107.3 | 34.29 | 0.0738 | 0.72 | 13.76 | 0
November | 8 | 3AM to 4AM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
November | 8 | 4AM to 5AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
November | 8 | 5AM to 6AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
November | 8 | 6AM to 7AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
November | 8 | 7AM to 8AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 8 | 8AM to 9AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 8 | 9AM to 10AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
November | 8 | 10AM to 11AM | 79 | 68.8 | 64 | 89.8 | 33.01 | 0.0731 | 0.6 | 13.86 | 0
November | 8 | 11AM to 12PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
November | 8 | 12PM to 1PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
November | 8 | 1PM to 2PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
November | 8 | 2PM to 3PM | 82.9 | 67.2 | 59 | 74.9 | 31.64 | 0.0726 | 0.5 | 13.91 | 0
November | 8 | 3PM to 4PM | 80.1 | 66.9 | 60.1 | 77.8 | 31.41 | 0.073 | 0.52 | 13.85 | 0
November | 8 | 4PM to 5PM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
November | 8 | 5PM to 6PM | 75 | 64.6 | 59 | 74.9 | 29.71 | 0.0737 | 0.5 | 13.71 | 0
November | 8 | 6PM to 7PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
November | 8 | 7PM to 8PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
November | 8 | 8PM to 9PM | 73 | 64.6 | 60.1 | 77.8 | 29.69 | 0.074 | 0.52 | 13.67 | 0
November | 8 | 9PM to 10PM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
November | 8 | 10PM to 11PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
November | 8 | 11PM to 12AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
November | 9 | 12AM to 1AM | 68 | 63.4 | 61 | 80.4 | 28.86 | 0.0747 | 0.54 | 13.55 | 0
November | 9 | 1AM to 2AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
November | 9 | 2AM to 3AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
November | 9 | 3AM to 4AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
November | 9 | 4AM to 5AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
November | 9 | 5AM to 6AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
November | 9 | 6AM to 7AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
November | 9 | 7AM to 8AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
November | 9 | 8AM to 9AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
November | 9 | 9AM to 10AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 9 | 10AM to 11AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
November | 9 | 11AM to 12PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 9 | 12PM to 1PM | 80.1 | 69.1 | 64 | 89.8 | 33.28 | 0.0729 | 0.6 | 13.88 | 0
November | 9 | 1PM to 2PM | 81 | 68.3 | 62.1 | 83.6 | 32.53 | 0.0729 | 0.56 | 13.89 | 0
November | 9 | 2PM to 3PM | 81 | 67.7 | 61 | 80.4 | 32.03 | 0.0729 | 0.54 | 13.88 | 0
November | 9 | 3PM to 4PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
November | 9 | 4PM to 5PM | 78.1 | 67.4 | 62.1 | 83.6 | 31.83 | 0.0733 | 0.56 | 13.81 | 0
November | 9 | 5PM to 6PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
November | 9 | 6PM to 7PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
November | 9 | 7PM to 8PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
November | 9 | 8PM to 9PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
November | 9 | 9PM to 10PM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
November | 9 | 10PM to 11PM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
November | 9 | 11PM to 12AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
November | 10 | 12AM to 1AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
November | 10 | 1AM to 2AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
November | 10 | 2AM to 3AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
November | 10 | 3AM to 4AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
November | 10 | 4AM to 5AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
November | 10 | 5AM to 6AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
November | 10 | 6AM to 7AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
November | 10 | 7AM to 8AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
November | 10 | 8AM to 9AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
November | 10 | 9AM to 10AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 10 | 10AM to 11AM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 10 | 11AM to 12PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
November | 10 | 12PM to 1PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
November | 10 | 1PM to 2PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
November | 10 | 2PM to 3PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
November | 10 | 3PM to 4PM | 75.9 | 71.7 | 70 | 110.8 | 35.54 | 0.0734 | 0.74 | 13.84 | 0
November | 10 | 4PM to 5PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 10 | 5PM to 6PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 10 | 6PM to 7PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 10 | 7PM to 8PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 10 | 8PM to 9PM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
November | 10 | 9PM to 10PM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
November | 10 | 10PM to 11PM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
November | 10 | 11PM to 12AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
November | 11 | 12AM to 1AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
November | 11 | 1AM to 2AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
November | 11 | 2AM to 3AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
November | 11 | 3AM to 4AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
November | 11 | 4AM to 5AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
November | 11 | 5AM to 6AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
November | 11 | 6AM to 7AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
November | 11 | 7AM to 8AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
November | 11 | 8AM to 9AM | 72 | 69.9 | 69.1 | 107.3 | 34.03 | 0.0739 | 0.72 | 13.73 | 0
November | 11 | 9AM to 10AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 11 | 10AM to 11AM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 11 | 11AM to 12PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
November | 11 | 12PM to 1PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
November | 11 | 1PM to 2PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
November | 11 | 2PM to 3PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
November | 11 | 3PM to 4PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
November | 11 | 4PM to 5PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
November | 11 | 5PM to 6PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
November | 11 | 6PM to 7PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
November | 11 | 7PM to 8PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
November | 11 | 8PM to 9PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
November | 11 | 9PM to 10PM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
November | 11 | 10PM to 11PM | 69.1 | 65.7 | 64 | 89.8 | 30.58 | 0.0745 | 0.6 | 13.6 | 0
November | 11 | 11PM to 12AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
November | 12 | 12AM to 1AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
November | 12 | 1AM to 2AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
November | 12 | 2AM to 3AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
November | 12 | 3AM to 4AM | 66.9 | 64.3 | 63 | 86.4 | 29.52 | 0.0748 | 0.58 | 13.54 | 0
November | 12 | 4AM to 5AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
November | 12 | 5AM to 6AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
November | 12 | 6AM to 7AM | 66 | 64.7 | 64 | 89.8 | 29.83 | 0.0749 | 0.6 | 13.52 | 0
November | 12 | 7AM to 8AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
November | 12 | 8AM to 9AM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
November | 12 | 9AM to 10AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
November | 12 | 10AM to 11AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
November | 12 | 11AM to 12PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
November | 12 | 12PM to 1PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
November | 12 | 1PM to 2PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
November | 12 | 2PM to 3PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
November | 12 | 3PM to 4PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
November | 12 | 4PM to 5PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
November | 12 | 5PM to 6PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
November | 12 | 6PM to 7PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
November | 12 | 7PM to 8PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
November | 12 | 8PM to 9PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
November | 12 | 9PM to 10PM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
November | 12 | 10PM to 11PM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
November | 12 | 11PM to 12AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
November | 13 | 12AM to 1AM | 69.1 | 65 | 63 | 86.4 | 30.05 | 0.0745 | 0.58 | 13.59 | 0
November | 13 | 1AM to 2AM | 68 | 64.7 | 63 | 86.4 | 29.78 | 0.0746 | 0.58 | 13.56 | 0
November | 13 | 2AM to 3AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
November | 13 | 3AM to 4AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
November | 13 | 4AM to 5AM | 70 | 66 | 64 | 89.8 | 30.8 | 0.0743 | 0.6 | 13.63 | 0
November | 13 | 5AM to 6AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
November | 13 | 6AM to 7AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
November | 13 | 7AM to 8AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
November | 13 | 8AM to 9AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 13 | 9AM to 10AM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
November | 13 | 10AM to 11AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
November | 13 | 11AM to 12PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
November | 13 | 12PM to 1PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
November | 13 | 1PM to 2PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
November | 13 | 2PM to 3PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
November | 13 | 3PM to 4PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
November | 13 | 4PM to 5PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 13 | 5PM to 6PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
November | 13 | 6PM to 7PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
November | 13 | 7PM to 8PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 13 | 8PM to 9PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
November | 13 | 9PM to 10PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
November | 13 | 10PM to 11PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
November | 13 | 11PM to 12AM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
November | 14 | 12AM to 1AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
November | 14 | 1AM to 2AM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
November | 14 | 2AM to 3AM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
November | 14 | 3AM to 4AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
November | 14 | 4AM to 5AM | 71.1 | 65.7 | 63 | 86.4 | 30.53 | 0.0742 | 0.58 | 13.64 | 0
November | 14 | 5AM to 6AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
November | 14 | 6AM to 7AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
November | 14 | 7AM to 8AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 14 | 8AM to 9AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
November | 14 | 9AM to 10AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
November | 14 | 10AM to 11AM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 14 | 11AM to 12PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 14 | 12PM to 1PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 14 | 1PM to 2PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 14 | 2PM to 3PM | 77 | 68.8 | 64.9 | 92.7 | 32.98 | 0.0733 | 0.62 | 13.82 | 0
November | 14 | 3PM to 4PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 14 | 4PM to 5PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
November | 14 | 5PM to 6PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
November | 14 | 6PM to 7PM | 73.9 | 66.6 | 63 | 86.4 | 31.24 | 0.0738 | 0.58 | 13.72 | 0
November | 14 | 7PM to 8PM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
November | 14 | 8PM to 9PM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 14 | 9PM to 10PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
November | 14 | 10PM to 11PM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
November | 14 | 11PM to 12AM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
November | 15 | 12AM to 1AM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
November | 15 | 1AM to 2AM | 73 | 65.1 | 61 | 80.4 | 30.09 | 0.074 | 0.54 | 13.68 | 0
November | 15 | 2AM to 3AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 15 | 3AM to 4AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 15 | 4AM to 5AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 15 | 5AM to 6AM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
November | 15 | 6AM to 7AM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
November | 15 | 7AM to 8AM | 75 | 65.2 | 60.1 | 77.8 | 30.17 | 0.0737 | 0.52 | 13.72 | 0
November | 15 | 8AM to 9AM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
November | 15 | 9AM to 10AM | 79 | 66.5 | 60.1 | 77.8 | 31.14 | 0.0732 | 0.52 | 13.82 | 0
November | 15 | 10AM to 11AM | 80.1 | 66.3 | 59 | 74.9 | 30.94 | 0.073 | 0.5 | 13.84 | 0
November | 15 | 11AM to 12PM | 82 | 68 | 61 | 80.4 | 32.3 | 0.0727 | 0.54 | 13.91 | 0
November | 15 | 12PM to 1PM | 82 | 67.5 | 60.1 | 77.8 | 31.89 | 0.0728 | 0.52 | 13.9 | 0
November | 15 | 1PM to 2PM | 81 | 67.2 | 60.1 | 77.8 | 31.63 | 0.0729 | 0.52 | 13.87 | 0
November | 15 | 2PM to 3PM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
November | 15 | 3PM to 4PM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
November | 15 | 4PM to 5PM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
November | 15 | 5PM to 6PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
November | 15 | 6PM to 7PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
November | 15 | 7PM to 8PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
November | 15 | 8PM to 9PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
November | 15 | 9PM to 10PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
November | 15 | 10PM to 11PM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
November | 15 | 11PM to 12AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
November | 16 | 12AM to 1AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
November | 16 | 1AM to 2AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 16 | 2AM to 3AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 16 | 3AM to 4AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 16 | 4AM to 5AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 16 | 5AM to 6AM | 72 | 64.8 | 61 | 80.4 | 29.83 | 0.0741 | 0.54 | 13.65 | 0
November | 16 | 6AM to 7AM | 73.9 | 65.4 | 61 | 80.4 | 30.31 | 0.0738 | 0.54 | 13.7 | 0
November | 16 | 7AM to 8AM | 75.9 | 66.1 | 61 | 80.4 | 30.8 | 0.0736 | 0.54 | 13.75 | 0
November | 16 | 8AM to 9AM | 78.1 | 66.7 | 61 | 80.4 | 31.33 | 0.0733 | 0.54 | 13.8 | 0
November | 16 | 9AM to 10AM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
November | 16 | 10AM to 11AM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
November | 16 | 11AM to 12PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
November | 16 | 12PM to 1PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
November | 16 | 1PM to 2PM | 82.9 | 68.9 | 62.1 | 83.6 | 33.02 | 0.0726 | 0.56 | 13.94 | 0
November | 16 | 2PM to 3PM | 82 | 68.6 | 62.1 | 83.6 | 32.8 | 0.0727 | 0.56 | 13.92 | 0
November | 16 | 3PM to 4PM | 80.1 | 68 | 62.1 | 83.6 | 32.31 | 0.073 | 0.56 | 13.87 | 0
November | 16 | 4PM to 5PM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
November | 16 | 5PM to 6PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
November | 16 | 6PM to 7PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
November | 16 | 7PM to 8PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
November | 16 | 8PM to 9PM | 75.9 | 67.2 | 63 | 86.4 | 31.73 | 0.0735 | 0.58 | 13.77 | 0
November | 16 | 9PM to 10PM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
November | 16 | 10PM to 11PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
November | 16 | 11PM to 12AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
November | 17 | 12AM to 1AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
November | 17 | 1AM to 2AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
November | 17 | 2AM to 3AM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
November | 17 | 3AM to 4AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
November | 17 | 4AM to 5AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
November | 17 | 5AM to 6AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
November | 17 | 6AM to 7AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
November | 17 | 7AM to 8AM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 17 | 8AM to 9AM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
November | 17 | 9AM to 10AM | 80.1 | 68.5 | 63 | 86.4 | 32.74 | 0.073 | 0.58 | 13.87 | 0
November | 17 | 10AM to 11AM | 81 | 68.8 | 63 | 86.4 | 32.96 | 0.0728 | 0.58 | 13.9 | 0
November | 17 | 11AM to 12PM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
November | 17 | 12PM to 1PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
November | 17 | 1PM to 2PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
November | 17 | 2PM to 3PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
November | 17 | 3PM to 4PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 17 | 4PM to 5PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 17 | 5PM to 6PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 17 | 6PM to 7PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 17 | 7PM to 8PM | 73.9 | 71.1 | 70 | 110.8 | 35.05 | 0.0737 | 0.74 | 13.79 | 0
November | 17 | 8PM to 9PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 17 | 9PM to 10PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 17 | 10PM to 11PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 17 | 11PM to 12AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 18 | 12AM to 1AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 18 | 1AM to 2AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 18 | 2AM to 3AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 18 | 3AM to 4AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 18 | 4AM to 5AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 18 | 5AM to 6AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 18 | 6AM to 7AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 18 | 7AM to 8AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 18 | 8AM to 9AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
November | 18 | 9AM to 10AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
November | 18 | 10AM to 11AM | 80.1 | 72.9 | 70 | 110.8 | 36.56 | 0.0728 | 0.74 | 13.95 | 0
November | 18 | 11AM to 12PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
November | 18 | 12PM to 1PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
November | 18 | 1PM to 2PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
November | 18 | 2PM to 3PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
November | 18 | 3PM to 4PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
November | 18 | 4PM to 5PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
November | 18 | 5PM to 6PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
November | 18 | 6PM to 7PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 18 | 7PM to 8PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 18 | 8PM to 9PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 18 | 9PM to 10PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 18 | 10PM to 11PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
November | 18 | 11PM to 12AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 19 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 19 | 1AM to 2AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 19 | 2AM to 3AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 19 | 3AM to 4AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 19 | 4AM to 5AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 19 | 5AM to 6AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 19 | 6AM to 7AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 19 | 7AM to 8AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 19 | 8AM to 9AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
November | 19 | 9AM to 10AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
November | 19 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
November | 19 | 11AM to 12PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
November | 19 | 12PM to 1PM | 84.9 | 71.1 | 64.9 | 92.7 | 34.93 | 0.0723 | 0.62 | 14.02 | 0
November | 19 | 1PM to 2PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
November | 19 | 2PM to 3PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
November | 19 | 3PM to 4PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
November | 19 | 4PM to 5PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
November | 19 | 5PM to 6PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
November | 19 | 6PM to 7PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 19 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 19 | 8PM to 9PM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 19 | 9PM to 10PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
November | 19 | 10PM to 11PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 19 | 11PM to 12AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 20 | 12AM to 1AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 20 | 1AM to 2AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 20 | 2AM to 3AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 20 | 3AM to 4AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 20 | 4AM to 5AM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
November | 20 | 5AM to 6AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
November | 20 | 6AM to 7AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
November | 20 | 7AM to 8AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 20 | 8AM to 9AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
November | 20 | 9AM to 10AM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
November | 20 | 10AM to 11AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
November | 20 | 11AM to 12PM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
November | 20 | 12PM to 1PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
November | 20 | 1PM to 2PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
November | 20 | 2PM to 3PM | 82.9 | 71.7 | 66.9 | 99.5 | 35.5 | 0.0725 | 0.67 | 13.99 | 0
November | 20 | 3PM to 4PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
November | 20 | 4PM to 5PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
November | 20 | 5PM to 6PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 20 | 6PM to 7PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 20 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 20 | 8PM to 9PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 20 | 9PM to 10PM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
November | 20 | 10PM to 11PM | 75 | 67.6 | 64 | 89.8 | 32.04 | 0.0736 | 0.6 | 13.76 | 0
November | 20 | 11PM to 12AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
November | 21 | 12AM to 1AM | 73.9 | 66.1 | 62.1 | 83.6 | 30.81 | 0.0738 | 0.56 | 13.71 | 0
November | 21 | 1AM to 2AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
November | 21 | 2AM to 3AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
November | 21 | 3AM to 4AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
November | 21 | 4AM to 5AM | 73 | 66.3 | 63 | 86.4 | 31.02 | 0.0739 | 0.58 | 13.69 | 0
November | 21 | 5AM to 6AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
November | 21 | 6AM to 7AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
November | 21 | 7AM to 8AM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
November | 21 | 8AM to 9AM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
November | 21 | 9AM to 10AM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
November | 21 | 10AM to 11AM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
November | 21 | 11AM to 12PM | 84.9 | 70.6 | 64 | 89.8 | 34.47 | 0.0723 | 0.6 | 14.01 | 0
November | 21 | 12PM to 1PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
November | 21 | 1PM to 2PM | 86 | 72.1 | 66 | 96.3 | 35.77 | 0.0721 | 0.64 | 14.06 | 0
November | 21 | 2PM to 3PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
November | 21 | 3PM to 4PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
November | 21 | 4PM to 5PM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
November | 21 | 5PM to 6PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
November | 21 | 6PM to 7PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 21 | 7PM to 8PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 21 | 8PM to 9PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 21 | 9PM to 10PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 21 | 10PM to 11PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 21 | 11PM to 12AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 22 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 22 | 1AM to 2AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 22 | 2AM to 3AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 22 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 22 | 4AM to 5AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 22 | 5AM to 6AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 22 | 6AM to 7AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 22 | 7AM to 8AM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
November | 22 | 8AM to 9AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
November | 22 | 9AM to 10AM | 84 | 74 | 70 | 110.8 | 37.54 | 0.0723 | 0.74 | 14.05 | 0
November | 22 | 10AM to 11AM | 86 | 73.9 | 69.1 | 107.3 | 37.49 | 0.072 | 0.72 | 14.09 | 0
November | 22 | 11AM to 12PM | 87.1 | 73.6 | 68 | 103.3 | 37.13 | 0.0719 | 0.69 | 14.11 | 0
November | 22 | 12PM to 1PM | 87.1 | 74.2 | 69.1 | 107.3 | 37.76 | 0.0719 | 0.72 | 14.12 | 0
November | 22 | 1PM to 2PM | 86 | 73.3 | 68 | 103.3 | 36.86 | 0.0721 | 0.69 | 14.08 | 0
November | 22 | 2PM to 3PM | 86 | 72.6 | 66.9 | 99.5 | 36.26 | 0.0721 | 0.67 | 14.07 | 0
November | 22 | 3PM to 4PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
November | 22 | 4PM to 5PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
November | 22 | 5PM to 6PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 22 | 6PM to 7PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
November | 22 | 7PM to 8PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
November | 22 | 8PM to 9PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
November | 22 | 9PM to 10PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 22 | 10PM to 11PM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 22 | 11PM to 12AM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
November | 23 | 12AM to 1AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 23 | 1AM to 2AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
November | 23 | 2AM to 3AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
November | 23 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 23 | 4AM to 5AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
November | 23 | 5AM to 6AM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
November | 23 | 6AM to 7AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
November | 23 | 7AM to 8AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
November | 23 | 8AM to 9AM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
November | 23 | 9AM to 10AM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
November | 23 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
November | 23 | 11AM to 12PM | 84.9 | 71.8 | 66 | 96.3 | 35.5 | 0.0723 | 0.64 | 14.03 | 0
November | 23 | 12PM to 1PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
November | 23 | 1PM to 2PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
November | 23 | 2PM to 3PM | 84.9 | 72.3 | 66.9 | 99.5 | 35.99 | 0.0722 | 0.67 | 14.04 | 0
November | 23 | 3PM to 4PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
November | 23 | 4PM to 5PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
November | 23 | 5PM to 6PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 23 | 6PM to 7PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 23 | 7PM to 8PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
November | 23 | 8PM to 9PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
November | 23 | 9PM to 10PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 23 | 10PM to 11PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 23 | 11PM to 12AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 24 | 12AM to 1AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 24 | 1AM to 2AM | 75 | 70.8 | 69.1 | 107.3 | 34.78 | 0.0735 | 0.72 | 13.81 | 0
November | 24 | 2AM to 3AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
November | 24 | 3AM to 4AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
November | 24 | 4AM to 5AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
November | 24 | 5AM to 6AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
November | 24 | 6AM to 7AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
November | 24 | 7AM to 8AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 24 | 8AM to 9AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
November | 24 | 9AM to 10AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
November | 24 | 10AM to 11AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
November | 24 | 11AM to 12PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
November | 24 | 12PM to 1PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
November | 24 | 1PM to 2PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
November | 24 | 2PM to 3PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
November | 24 | 3PM to 4PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
November | 24 | 4PM to 5PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
November | 24 | 5PM to 6PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
November | 24 | 6PM to 7PM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 24 | 7PM to 8PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
November | 24 | 8PM to 9PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
November | 24 | 9PM to 10PM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
November | 24 | 10PM to 11PM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
November | 24 | 11PM to 12AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
November | 25 | 12AM to 1AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
November | 25 | 1AM to 2AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
November | 25 | 2AM to 3AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
November | 25 | 3AM to 4AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
November | 25 | 4AM to 5AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
November | 25 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
November | 25 | 6AM to 7AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
November | 25 | 7AM to 8AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
November | 25 | 8AM to 9AM | 77 | 72 | 70 | 110.8 | 35.81 | 0.0732 | 0.74 | 13.87 | 0
November | 25 | 9AM to 10AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
November | 25 | 10AM to 11AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
November | 25 | 11AM to 12PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
November | 25 | 12PM to 1PM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
November | 25 | 1PM to 2PM | 82.9 | 71.2 | 66 | 96.3 | 35.01 | 0.0725 | 0.64 | 13.98 | 0
November | 25 | 2PM to 3PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
November | 25 | 3PM to 4PM | 79 | 69.4 | 64.9 | 92.7 | 33.47 | 0.0731 | 0.62 | 13.87 | 0
November | 25 | 4PM to 5PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
November | 25 | 5PM to 6PM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
November | 25 | 6PM to 7PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
November | 25 | 7PM to 8PM | 70 | 62.9 | 59 | 74.9 | 28.47 | 0.0744 | 0.5 | 13.58 | 0
November | 25 | 8PM to 9PM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
November | 25 | 9PM to 10PM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
November | 25 | 10PM to 11PM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
November | 25 | 11PM to 12AM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
November | 26 | 12AM to 1AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
November | 26 | 1AM to 2AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
November | 26 | 2AM to 3AM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
November | 26 | 3AM to 4AM | 68 | 60.5 | 55.9 | 66.9 | 26.75 | 0.0748 | 0.45 | 13.5 | 0
November | 26 | 4AM to 5AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
November | 26 | 5AM to 6AM | 66 | 61.5 | 59 | 74.9 | 27.5 | 0.075 | 0.5 | 13.48 | 0
November | 26 | 6AM to 7AM | 64 | 60.8 | 59 | 74.9 | 27.02 | 0.0753 | 0.5 | 13.43 | 0
November | 26 | 7AM to 8AM | 70 | 64.1 | 61 | 80.4 | 29.34 | 0.0744 | 0.54 | 13.6 | 0
November | 26 | 8AM to 9AM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
November | 26 | 9AM to 10AM | 75 | 65.8 | 61 | 80.4 | 30.58 | 0.0737 | 0.54 | 13.73 | 0
November | 26 | 10AM to 11AM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
November | 26 | 11AM to 12PM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
November | 26 | 12PM to 1PM | 73.9 | 67.8 | 64.9 | 92.7 | 32.23 | 0.0738 | 0.62 | 13.74 | 0
November | 26 | 1PM to 2PM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
November | 26 | 2PM to 3PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
November | 26 | 3PM to 4PM | 75.9 | 66.7 | 62.1 | 83.6 | 31.3 | 0.0735 | 0.56 | 13.76 | 0
November | 26 | 4PM to 5PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
November | 26 | 5PM to 6PM | 73 | 64 | 59 | 74.9 | 29.22 | 0.074 | 0.5 | 13.66 | 0
November | 26 | 6PM to 7PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
November | 26 | 7PM to 8PM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
November | 26 | 8PM to 9PM | 71.1 | 63.9 | 60.1 | 77.8 | 29.2 | 0.0743 | 0.52 | 13.62 | 0
November | 26 | 9PM to 10PM | 72 | 64.2 | 60.1 | 77.8 | 29.42 | 0.0741 | 0.52 | 13.64 | 0
November | 26 | 10PM to 11PM | 68 | 63.4 | 61 | 80.4 | 28.86 | 0.0747 | 0.54 | 13.55 | 0
November | 26 | 11PM to 12AM | 66 | 62.2 | 60.1 | 77.8 | 27.97 | 0.075 | 0.52 | 13.49 | 0
November | 27 | 12AM to 1AM | 64.9 | 61.8 | 60.1 | 77.8 | 27.71 | 0.0751 | 0.52 | 13.46 | 0
November | 27 | 1AM to 2AM | 64 | 62.1 | 61 | 80.4 | 27.89 | 0.0752 | 0.54 | 13.44 | 0
November | 27 | 2AM to 3AM | 62.1 | 60.8 | 60.1 | 77.8 | 27 | 0.0755 | 0.52 | 13.39 | 0
November | 27 | 3AM to 4AM | 62.1 | 60.8 | 60.1 | 77.8 | 27 | 0.0755 | 0.52 | 13.39 | 0
November | 27 | 4AM to 5AM | 66.9 | 63.7 | 62.1 | 83.6 | 29.09 | 0.0748 | 0.56 | 13.53 | 0
November | 27 | 5AM to 6AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
November | 27 | 6AM to 7AM | 61 | 59.7 | 59 | 74.9 | 26.27 | 0.0757 | 0.5 | 13.35 | 0
November | 27 | 7AM to 8AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
November | 27 | 8AM to 9AM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
November | 27 | 9AM to 10AM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
November | 27 | 10AM to 11AM | 79 | 65.9 | 59 | 74.9 | 30.68 | 0.0732 | 0.5 | 13.81 | 0
November | 27 | 11AM to 12PM | 77 | 65.3 | 59 | 74.9 | 30.19 | 0.0735 | 0.5 | 13.76 | 0
November | 27 | 12PM to 1PM | 80.1 | 64.7 | 55.9 | 66.9 | 29.7 | 0.0731 | 0.45 | 13.81 | 0
November | 27 | 1PM to 2PM | 80.1 | 65.2 | 57 | 69.6 | 30.12 | 0.0731 | 0.47 | 13.82 | 0
November | 27 | 2PM to 3PM | 79 | 65.9 | 59 | 74.9 | 30.68 | 0.0732 | 0.5 | 13.81 | 0
November | 27 | 3PM to 4PM | 77 | 65.9 | 60.1 | 77.8 | 30.66 | 0.0734 | 0.52 | 13.77 | 0
November | 27 | 4PM to 5PM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
November | 27 | 5PM to 6PM | 73.9 | 64.9 | 60.1 | 77.8 | 29.91 | 0.0739 | 0.52 | 13.69 | 0
November | 27 | 6PM to 7PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
November | 27 | 7PM to 8PM | 71.1 | 65.1 | 62.1 | 83.6 | 30.11 | 0.0742 | 0.56 | 13.63 | 0
November | 27 | 8PM to 9PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
November | 27 | 9PM to 10PM | 69.1 | 64.5 | 62.1 | 83.6 | 29.62 | 0.0745 | 0.56 | 13.58 | 0
November | 27 | 10PM to 11PM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
November | 27 | 11PM to 12AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
November | 28 | 12AM to 1AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
November | 28 | 1AM to 2AM | 64 | 62.7 | 62.1 | 83.6 | 28.38 | 0.0752 | 0.56 | 13.45 | 0
November | 28 | 2AM to 3AM | 64 | 62.1 | 61 | 80.4 | 27.89 | 0.0752 | 0.54 | 13.44 | 0
November | 28 | 3AM to 4AM | 63 | 61.7 | 61 | 80.4 | 27.62 | 0.0754 | 0.54 | 13.42 | 0
November | 28 | 4AM to 5AM | 64.9 | 63.6 | 63 | 86.4 | 29.03 | 0.0751 | 0.58 | 13.49 | 0
November | 28 | 5AM to 6AM | 64.9 | 63.1 | 62.1 | 83.6 | 28.6 | 0.0751 | 0.56 | 13.48 | 0
November | 28 | 6AM to 7AM | 66 | 63.4 | 62.1 | 83.6 | 28.87 | 0.0749 | 0.56 | 13.5 | 0
November | 28 | 7AM to 8AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
November | 28 | 8AM to 9AM | 75.9 | 67.9 | 64 | 89.8 | 32.26 | 0.0735 | 0.6 | 13.78 | 0
November | 28 | 9AM to 10AM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
November | 28 | 10AM to 11AM | 82 | 69.7 | 64 | 89.8 | 33.76 | 0.0727 | 0.6 | 13.94 | 0
November | 28 | 11AM to 12PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
November | 28 | 12PM to 1PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
November | 28 | 1PM to 2PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
November | 28 | 2PM to 3PM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
November | 28 | 3PM to 4PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
November | 28 | 4PM to 5PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
November | 28 | 5PM to 6PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 28 | 6PM to 7PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 28 | 7PM to 8PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 28 | 8PM to 9PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 28 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 28 | 10PM to 11PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 28 | 11PM to 12AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 29 | 12AM to 1AM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
November | 29 | 1AM to 2AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 29 | 2AM to 3AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
November | 29 | 3AM to 4AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 29 | 4AM to 5AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
November | 29 | 5AM to 6AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 29 | 6AM to 7AM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
November | 29 | 7AM to 8AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
November | 29 | 8AM to 9AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
November | 29 | 9AM to 10AM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
November | 29 | 10AM to 11AM | 84 | 71.5 | 66 | 96.3 | 35.28 | 0.0724 | 0.64 | 14.01 | 0
November | 29 | 11AM to 12PM | 84.9 | 74.2 | 70 | 110.8 | 37.76 | 0.0722 | 0.74 | 14.08 | 0
November | 29 | 12PM to 1PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
November | 29 | 1PM to 2PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
November | 29 | 2PM to 3PM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
November | 29 | 3PM to 4PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
November | 29 | 4PM to 5PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
November | 29 | 5PM to 6PM | 79 | 73.3 | 71.1 | 115 | 36.96 | 0.0729 | 0.77 | 13.94 | 0
November | 29 | 6PM to 7PM | 78.1 | 72.3 | 70 | 110.8 | 36.08 | 0.0731 | 0.74 | 13.9 | 0
November | 29 | 7PM to 8PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
November | 29 | 8PM to 9PM | 73 | 69.5 | 68 | 103.3 | 33.67 | 0.0738 | 0.69 | 13.75 | 0
November | 29 | 9PM to 10PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
November | 29 | 10PM to 11PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
November | 29 | 11PM to 12AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
November | 30 | 12AM to 1AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
November | 30 | 1AM to 2AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
November | 30 | 2AM to 3AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
November | 30 | 3AM to 4AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
November | 30 | 4AM to 5AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
November | 30 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
November | 30 | 6AM to 7AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
November | 30 | 7AM to 8AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
November | 30 | 8AM to 9AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
November | 30 | 9AM to 10AM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
November | 30 | 10AM to 11AM | 81 | 73.1 | 70 | 110.8 | 36.79 | 0.0727 | 0.74 | 13.97 | 0
November | 30 | 11AM to 12PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
November | 30 | 12PM to 1PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
November | 30 | 1PM to 2PM | 84 | 72.7 | 68 | 103.3 | 36.38 | 0.0723 | 0.69 | 14.03 | 0
November | 30 | 2PM to 3PM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
November | 30 | 3PM to 4PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
November | 30 | 4PM to 5PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
November | 30 | 5PM to 6PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
November | 30 | 6PM to 7PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
November | 30 | 7PM to 8PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 30 | 8PM to 9PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
November | 30 | 9PM to 10PM | 76.1 | 69.9 | 67.1 | 100.1 | 33.92 | 0.0734 | 0.67 | 13.81 | 0
November | 30 | 10PM to 11PM | 76.3 | 70.1 | 67.5 | 101.4 | 34.16 | 0.0734 | 0.68 | 13.82 | 0
November | 30 | 11PM to 12AM | 76.5 | 70.3 | 67.6 | 102 | 34.31 | 0.0734 | 0.68 | 13.83 | 0
December | 1 | 12AM to 1AM | 76.5 | 70.4 | 67.8 | 102.7 | 34.41 | 0.0734 | 0.69 | 13.83 | 0
December | 1 | 1AM to 2AM | 76.6 | 70.6 | 68 | 103.3 | 34.56 | 0.0733 | 0.69 | 13.84 | 0
December | 1 | 2AM to 3AM | 76.8 | 70.9 | 68.4 | 104.6 | 34.81 | 0.0733 | 0.7 | 13.85 | 0
December | 1 | 3AM to 4AM | 77 | 71.1 | 68.5 | 105.3 | 34.95 | 0.0733 | 0.7 | 13.85 | 0
December | 1 | 4AM to 5AM | 77 | 70.7 | 68 | 103.3 | 34.64 | 0.0733 | 0.69 | 13.85 | 0
December | 1 | 5AM to 6AM | 77.4 | 71.1 | 68.4 | 104.6 | 34.94 | 0.0732 | 0.7 | 13.86 | 0
December | 1 | 6AM to 7AM | 77.7 | 71.2 | 68.4 | 104.6 | 35.03 | 0.0732 | 0.7 | 13.87 | 0
December | 1 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 1 | 8AM to 9AM | 79.3 | 72.9 | 70.3 | 112.2 | 36.61 | 0.0729 | 0.75 | 13.94 | 0
December | 1 | 9AM to 10AM | 80.8 | 73.3 | 70.3 | 112.2 | 36.96 | 0.0727 | 0.75 | 13.97 | 0
December | 1 | 10AM to 11AM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
December | 1 | 11AM to 12PM | 82.4 | 73.7 | 70.2 | 111.5 | 37.25 | 0.0725 | 0.74 | 14.01 | 0
December | 1 | 12PM to 1PM | 82.6 | 73.5 | 69.8 | 110.1 | 37.08 | 0.0725 | 0.73 | 14.01 | 0
December | 1 | 1PM to 2PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
December | 1 | 2PM to 3PM | 82.2 | 73.1 | 69.4 | 108.7 | 36.77 | 0.0725 | 0.73 | 14 | 0
December | 1 | 3PM to 4PM | 81.7 | 73.1 | 69.6 | 109.4 | 36.75 | 0.0726 | 0.73 | 13.99 | 0
December | 1 | 4PM to 5PM | 81 | 72.5 | 69.1 | 107.3 | 36.25 | 0.0727 | 0.72 | 13.96 | 0
December | 1 | 5PM to 6PM | 80.1 | 72.5 | 69.4 | 108.7 | 36.24 | 0.0728 | 0.73 | 13.94 | 0
December | 1 | 6PM to 7PM | 79 | 72.2 | 69.4 | 108.7 | 35.97 | 0.073 | 0.73 | 13.92 | 0
December | 1 | 7PM to 8PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 1 | 8PM to 9PM | 77 | 71.3 | 68.9 | 106.6 | 35.16 | 0.0733 | 0.71 | 13.86 | 0
December | 1 | 9PM to 10PM | 76.1 | 70.8 | 68.5 | 105.3 | 34.73 | 0.0734 | 0.7 | 13.83 | 0
December | 1 | 10PM to 11PM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
December | 1 | 11PM to 12AM | 75 | 70.2 | 68.2 | 104 | 34.26 | 0.0735 | 0.69 | 13.8 | 0
December | 2 | 12AM to 1AM | 75 | 70.2 | 68.2 | 104 | 34.26 | 0.0735 | 0.69 | 13.8 | 0
December | 2 | 1AM to 2AM | 75 | 70.1 | 68 | 103.3 | 34.16 | 0.0735 | 0.69 | 13.8 | 0
December | 2 | 2AM to 3AM | 74.7 | 70.1 | 68.2 | 104 | 34.17 | 0.0736 | 0.69 | 13.79 | 0
December | 2 | 3AM to 4AM | 74.3 | 70 | 68.2 | 104 | 34.08 | 0.0736 | 0.69 | 13.78 | 0
December | 2 | 4AM to 5AM | 73.9 | 69.8 | 68 | 103.3 | 33.89 | 0.0737 | 0.69 | 13.77 | 0
December | 2 | 5AM to 6AM | 75.4 | 70.5 | 68.4 | 104.6 | 34.45 | 0.0735 | 0.7 | 13.81 | 0
December | 2 | 6AM to 7AM | 76.6 | 70.8 | 68.4 | 104.6 | 34.76 | 0.0733 | 0.7 | 13.84 | 0
December | 2 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 2 | 8AM to 9AM | 79 | 72.3 | 69.6 | 109.4 | 36.08 | 0.073 | 0.73 | 13.92 | 0
December | 2 | 9AM to 10AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
December | 2 | 10AM to 11AM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
December | 2 | 11AM to 12PM | 81.7 | 72.6 | 68.9 | 106.6 | 36.32 | 0.0726 | 0.71 | 13.98 | 0
December | 2 | 12PM to 1PM | 82.2 | 73 | 69.3 | 108 | 36.67 | 0.0725 | 0.72 | 14 | 0
December | 2 | 1PM to 2PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
December | 2 | 2PM to 3PM | 82.2 | 72.9 | 69.1 | 107.3 | 36.56 | 0.0725 | 0.72 | 14 | 0
December | 2 | 3PM to 4PM | 81.7 | 72.6 | 68.9 | 106.6 | 36.32 | 0.0726 | 0.71 | 13.98 | 0
December | 2 | 4PM to 5PM | 81 | 71.9 | 68 | 103.3 | 35.62 | 0.0727 | 0.69 | 13.95 | 0
December | 2 | 5PM to 6PM | 80.1 | 72.1 | 68.7 | 106 | 35.81 | 0.0728 | 0.71 | 13.94 | 0
December | 2 | 6PM to 7PM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
December | 2 | 7PM to 8PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 2 | 8PM to 9PM | 78.1 | 71.8 | 69.3 | 108 | 35.64 | 0.0731 | 0.72 | 13.89 | 0
December | 2 | 9PM to 10PM | 78.1 | 71.8 | 69.3 | 108 | 35.64 | 0.0731 | 0.72 | 13.89 | 0
December | 2 | 10PM to 11PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 2 | 11PM to 12AM | 78.1 | 71.8 | 69.3 | 108 | 35.64 | 0.0731 | 0.72 | 13.89 | 0
December | 3 | 12AM to 1AM | 78.1 | 71.8 | 69.3 | 108 | 35.64 | 0.0731 | 0.72 | 13.89 | 0
December | 3 | 1AM to 2AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 3 | 2AM to 3AM | 78.1 | 71.6 | 68.9 | 106.6 | 35.43 | 0.0731 | 0.71 | 13.89 | 0
December | 3 | 3AM to 4AM | 78.1 | 71.4 | 68.5 | 105.3 | 35.22 | 0.0731 | 0.7 | 13.88 | 0
December | 3 | 4AM to 5AM | 78.1 | 71 | 68 | 103.3 | 34.91 | 0.0731 | 0.69 | 13.88 | 0
December | 3 | 5AM to 6AM | 78.4 | 71.4 | 68.4 | 104.6 | 35.21 | 0.0731 | 0.7 | 13.89 | 0
December | 3 | 6AM to 7AM | 78.6 | 71.4 | 68.4 | 104.6 | 35.25 | 0.073 | 0.7 | 13.89 | 0
December | 3 | 7AM to 8AM | 79 | 72 | 69.1 | 107.3 | 35.76 | 0.073 | 0.72 | 13.91 | 0
December | 3 | 8AM to 9AM | 79 | 73.4 | 71.2 | 115.7 | 37.08 | 0.0729 | 0.77 | 13.94 | 0
December | 3 | 9AM to 10AM | 79 | 74.2 | 72.3 | 120.2 | 37.77 | 0.0729 | 0.8 | 13.95 | 0
December | 3 | 10AM to 11AM | 79 | 74.7 | 73 | 123.2 | 38.25 | 0.0729 | 0.82 | 13.96 | 0
December | 3 | 11AM to 12PM | 77.7 | 73.9 | 72.5 | 120.9 | 37.58 | 0.0731 | 0.81 | 13.92 | 0
December | 3 | 12PM to 1PM | 76.3 | 72.8 | 71.4 | 116.5 | 36.52 | 0.0733 | 0.78 | 13.87 | 0
December | 3 | 1PM to 2PM | 75 | 71.5 | 70 | 110.8 | 35.32 | 0.0735 | 0.74 | 13.82 | 0
December | 3 | 2PM to 3PM | 75 | 71.1 | 69.4 | 108.7 | 34.99 | 0.0735 | 0.73 | 13.81 | 0
December | 3 | 3PM to 4PM | 75 | 70.4 | 68.4 | 104.6 | 34.36 | 0.0735 | 0.7 | 13.8 | 0
December | 3 | 4PM to 5PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
December | 3 | 5PM to 6PM | 73.9 | 68.4 | 65.8 | 95.7 | 32.7 | 0.0737 | 0.64 | 13.75 | 0
December | 3 | 6PM to 7PM | 73 | 67.3 | 64.6 | 91.5 | 31.83 | 0.0739 | 0.61 | 13.71 | 0
December | 3 | 7PM to 8PM | 72 | 66 | 63 | 86.4 | 30.76 | 0.0741 | 0.58 | 13.67 | 0
December | 3 | 8PM to 9PM | 71.2 | 65.3 | 62.2 | 84.2 | 30.23 | 0.0742 | 0.57 | 13.64 | 0
December | 3 | 9PM to 10PM | 70.7 | 64.6 | 61.3 | 81.5 | 29.68 | 0.0743 | 0.55 | 13.62 | 0
December | 3 | 10PM to 11PM | 70 | 63.6 | 60.1 | 77.8 | 28.94 | 0.0744 | 0.52 | 13.59 | 0
December | 3 | 11PM to 12AM | 69.6 | 63.3 | 59.9 | 77.3 | 28.77 | 0.0745 | 0.52 | 13.58 | 0
December | 4 | 12AM to 1AM | 69.4 | 63.1 | 59.5 | 76.3 | 28.57 | 0.0745 | 0.51 | 13.57 | 0
December | 4 | 1AM to 2AM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
December | 4 | 2AM to 3AM | 68.7 | 62.4 | 58.8 | 74.4 | 28.09 | 0.0746 | 0.5 | 13.55 | 0
December | 4 | 3AM to 4AM | 68.4 | 62.1 | 58.5 | 73.4 | 27.85 | 0.0747 | 0.49 | 13.53 | 0
December | 4 | 4AM to 5AM | 68 | 61.6 | 57.9 | 72 | 27.54 | 0.0747 | 0.48 | 13.52 | 0
December | 4 | 5AM to 6AM | 69.3 | 62.1 | 57.9 | 72 | 27.85 | 0.0745 | 0.48 | 13.55 | 0
December | 4 | 6AM to 7AM | 70.7 | 62.4 | 57.6 | 71 | 28.05 | 0.0743 | 0.48 | 13.59 | 0
December | 4 | 7AM to 8AM | 72 | 63 | 57.9 | 72 | 28.51 | 0.0742 | 0.48 | 13.62 | 0
December | 4 | 8AM to 9AM | 74.3 | 64.3 | 58.8 | 74.4 | 29.45 | 0.0738 | 0.5 | 13.69 | 0
December | 4 | 9AM to 10AM | 76.6 | 65 | 58.6 | 73.9 | 29.95 | 0.0735 | 0.5 | 13.75 | 0
December | 4 | 10AM to 11AM | 79 | 65.3 | 57.9 | 72 | 30.22 | 0.0732 | 0.48 | 13.8 | 0
December | 4 | 11AM to 12PM | 79.7 | 66.1 | 58.8 | 74.4 | 30.77 | 0.0731 | 0.5 | 13.83 | 0
December | 4 | 12PM to 1PM | 80.2 | 66.4 | 59.2 | 75.3 | 31.06 | 0.073 | 0.51 | 13.84 | 0
December | 4 | 1PM to 2PM | 81 | 66.6 | 59 | 74.9 | 31.16 | 0.0729 | 0.5 | 13.86 | 0
December | 4 | 2PM to 3PM | 80.1 | 66.7 | 59.7 | 76.8 | 31.25 | 0.073 | 0.52 | 13.84 | 0
December | 4 | 3PM to 4PM | 79 | 66.6 | 60.3 | 78.4 | 31.22 | 0.0732 | 0.53 | 13.82 | 0
December | 4 | 4PM to 5PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
December | 4 | 5PM to 6PM | 77 | 66.4 | 61 | 80.4 | 31.06 | 0.0734 | 0.54 | 13.78 | 0
December | 4 | 6PM to 7PM | 76.1 | 66.5 | 61.7 | 82.5 | 31.17 | 0.0735 | 0.55 | 13.76 | 0
December | 4 | 7PM to 8PM | 75 | 66.4 | 62.1 | 83.6 | 31.08 | 0.0737 | 0.56 | 13.74 | 0
December | 4 | 8PM to 9PM | 74.7 | 66.8 | 63 | 86.4 | 31.42 | 0.0737 | 0.58 | 13.74 | 0
December | 4 | 9PM to 10PM | 74.3 | 67.2 | 63.7 | 88.6 | 31.68 | 0.0737 | 0.59 | 13.73 | 0
December | 4 | 10PM to 11PM | 73.9 | 67.3 | 64 | 89.8 | 31.77 | 0.0738 | 0.6 | 13.73 | 0
December | 4 | 11PM to 12AM | 73 | 67.3 | 64.6 | 91.5 | 31.83 | 0.0739 | 0.61 | 13.71 | 0
December | 5 | 12AM to 1AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
December | 5 | 1AM to 2AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
December | 5 | 2AM to 3AM | 71.1 | 67 | 65.1 | 93.3 | 31.62 | 0.0742 | 0.63 | 13.66 | 0
December | 5 | 3AM to 4AM | 71.1 | 67 | 65.1 | 93.3 | 31.62 | 0.0742 | 0.63 | 13.66 | 0
December | 5 | 4AM to 5AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
December | 5 | 5AM to 6AM | 72.3 | 67.5 | 65.3 | 93.9 | 32.02 | 0.074 | 0.63 | 13.7 | 0
December | 5 | 6AM to 7AM | 73.8 | 68 | 65.3 | 93.9 | 32.37 | 0.0738 | 0.63 | 13.74 | 0
December | 5 | 7AM to 8AM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
December | 5 | 8AM to 9AM | 76.6 | 69.9 | 66.9 | 99.5 | 33.95 | 0.0734 | 0.67 | 13.83 | 0
December | 5 | 9AM to 10AM | 78.4 | 70.3 | 66.7 | 98.8 | 34.3 | 0.0731 | 0.66 | 13.87 | 0
December | 5 | 10AM to 11AM | 80.1 | 70.4 | 66 | 96.3 | 34.3 | 0.0729 | 0.64 | 13.91 | 0
December | 5 | 11AM to 12PM | 80.1 | 71 | 67.1 | 100.1 | 34.89 | 0.0729 | 0.67 | 13.92 | 0
December | 5 | 12PM to 1PM | 80.1 | 71.5 | 67.8 | 102.7 | 35.3 | 0.0729 | 0.69 | 13.92 | 0
December | 5 | 1PM to 2PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
December | 5 | 2PM to 3PM | 80.1 | 71.8 | 68.4 | 104.6 | 35.61 | 0.0729 | 0.7 | 13.93 | 0
December | 5 | 3PM to 4PM | 80.1 | 71.9 | 68.5 | 105.3 | 35.71 | 0.0729 | 0.7 | 13.93 | 0
December | 5 | 4PM to 5PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
December | 5 | 5PM to 6PM | 79 | 71.8 | 68.7 | 106 | 35.55 | 0.073 | 0.71 | 13.91 | 0
December | 5 | 6PM to 7PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 5 | 7PM to 8PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
December | 5 | 8PM to 9PM | 76.6 | 71.4 | 69.3 | 108 | 35.29 | 0.0733 | 0.72 | 13.85 | 0
December | 5 | 9PM to 10PM | 76.3 | 71.3 | 69.3 | 108 | 35.2 | 0.0733 | 0.72 | 13.84 | 0
December | 5 | 10PM to 11PM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
December | 5 | 11PM to 12AM | 74.3 | 70.2 | 68.4 | 104.6 | 34.18 | 0.0736 | 0.7 | 13.78 | 0
December | 6 | 12AM to 1AM | 72.7 | 68.9 | 67.3 | 100.7 | 33.17 | 0.0739 | 0.67 | 13.73 | 0
December | 6 | 1AM to 2AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
December | 6 | 2AM to 3AM | 72.7 | 68.9 | 67.3 | 100.7 | 33.17 | 0.0739 | 0.67 | 13.73 | 0
December | 6 | 3AM to 4AM | 74.3 | 70.2 | 68.4 | 104.6 | 34.18 | 0.0736 | 0.7 | 13.78 | 0
December | 6 | 4AM to 5AM | 75.9 | 71.1 | 69.1 | 107.3 | 35 | 0.0734 | 0.72 | 13.83 | 0
December | 6 | 5AM to 6AM | 76.6 | 71.3 | 69.1 | 107.3 | 35.18 | 0.0733 | 0.72 | 13.85 | 0
December | 6 | 6AM to 7AM | 77.4 | 71.3 | 68.7 | 106 | 35.15 | 0.0732 | 0.71 | 13.87 | 0
December | 6 | 7AM to 8AM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 6 | 8AM to 9AM | 79.3 | 72.7 | 70 | 110.8 | 36.39 | 0.0729 | 0.74 | 13.93 | 0
December | 6 | 9AM to 10AM | 80.8 | 73 | 69.8 | 110.1 | 36.63 | 0.0727 | 0.73 | 13.97 | 0
December | 6 | 10AM to 11AM | 82 | 72.9 | 69.1 | 107.3 | 36.51 | 0.0726 | 0.72 | 13.99 | 0
December | 6 | 11AM to 12PM | 82.8 | 73.4 | 69.6 | 109.4 | 37.01 | 0.0725 | 0.73 | 14.02 | 0
December | 6 | 12PM to 1PM | 83.3 | 73.5 | 69.6 | 109.4 | 37.15 | 0.0724 | 0.73 | 14.03 | 0
December | 6 | 1PM to 2PM | 84 | 73.4 | 69.1 | 107.3 | 37 | 0.0723 | 0.72 | 14.04 | 0
December | 6 | 2PM to 3PM | 82.8 | 73.3 | 69.4 | 108.7 | 36.91 | 0.0725 | 0.73 | 14.01 | 0
December | 6 | 3PM to 4PM | 81.3 | 73 | 69.6 | 109.4 | 36.66 | 0.0727 | 0.73 | 13.98 | 0
December | 6 | 4PM to 5PM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
December | 6 | 5PM to 6PM | 77 | 71.4 | 69.1 | 107.3 | 35.27 | 0.0733 | 0.72 | 13.86 | 0
December | 6 | 6PM to 7PM | 74.1 | 70.3 | 68.7 | 106 | 34.35 | 0.0737 | 0.71 | 13.78 | 0
December | 6 | 7PM to 8PM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
December | 6 | 8PM to 9PM | 71.4 | 68.8 | 67.6 | 102 | 33.07 | 0.0741 | 0.68 | 13.7 | 0
December | 6 | 9PM to 10PM | 71.6 | 68.4 | 66.9 | 99.5 | 32.71 | 0.074 | 0.67 | 13.7 | 0
December | 6 | 10PM to 11PM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
December | 6 | 11PM to 12AM | 71.6 | 67.9 | 66.2 | 96.9 | 32.32 | 0.0741 | 0.65 | 13.69 | 0
December | 7 | 12AM to 1AM | 71.4 | 67.9 | 66.2 | 96.9 | 32.27 | 0.0741 | 0.65 | 13.68 | 0
December | 7 | 1AM to 2AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
December | 7 | 2AM to 3AM | 70.7 | 67.4 | 65.8 | 95.7 | 31.91 | 0.0742 | 0.64 | 13.66 | 0
December | 7 | 3AM to 4AM | 70.3 | 67 | 65.5 | 94.5 | 31.63 | 0.0743 | 0.63 | 13.65 | 0
December | 7 | 4AM to 5AM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
December | 7 | 5AM to 6AM | 69.6 | 66.5 | 64.9 | 92.7 | 31.17 | 0.0744 | 0.62 | 13.63 | 0
December | 7 | 6AM to 7AM | 69.4 | 66.2 | 64.6 | 91.5 | 30.94 | 0.0744 | 0.61 | 13.62 | 0
December | 7 | 7AM to 8AM | 69.1 | 66.3 | 64.9 | 92.7 | 31.04 | 0.0744 | 0.62 | 13.61 | 0
December | 7 | 8AM to 9AM | 72.1 | 68.1 | 66.2 | 96.9 | 32.45 | 0.074 | 0.65 | 13.7 | 0
December | 7 | 9AM to 10AM | 75 | 69.1 | 66.4 | 97.6 | 33.26 | 0.0736 | 0.65 | 13.78 | 0
December | 7 | 10AM to 11AM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
December | 7 | 11AM to 12PM | 78.8 | 70.4 | 66.7 | 98.8 | 34.38 | 0.0731 | 0.66 | 13.88 | 0
December | 7 | 12PM to 1PM | 79.3 | 70.8 | 67.1 | 100.1 | 34.72 | 0.073 | 0.67 | 13.9 | 0
December | 7 | 1PM to 2PM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
December | 7 | 2PM to 3PM | 79.7 | 70.9 | 67.1 | 100.1 | 34.8 | 0.0729 | 0.67 | 13.91 | 0
December | 7 | 3PM to 4PM | 79.3 | 70.6 | 66.7 | 98.8 | 34.52 | 0.073 | 0.66 | 13.89 | 0
December | 7 | 4PM to 5PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
December | 7 | 5PM to 6PM | 77.7 | 69.9 | 66.4 | 97.6 | 33.92 | 0.0732 | 0.65 | 13.85 | 0
December | 7 | 6PM to 7PM | 76.3 | 69.5 | 66.4 | 97.6 | 33.57 | 0.0734 | 0.65 | 13.81 | 0
December | 7 | 7PM to 8PM | 75 | 68.8 | 66 | 96.3 | 33.06 | 0.0736 | 0.64 | 13.78 | 0
December | 7 | 8PM to 9PM | 73.9 | 68.4 | 65.8 | 95.7 | 32.7 | 0.0737 | 0.64 | 13.75 | 0
December | 7 | 9PM to 10PM | 73 | 67.9 | 65.5 | 94.5 | 32.29 | 0.0739 | 0.63 | 13.72 | 0
December | 7 | 10PM to 11PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
December | 7 | 11PM to 12AM | 71.1 | 67.3 | 65.5 | 94.5 | 31.8 | 0.0742 | 0.63 | 13.67 | 0
December | 8 | 12AM to 1AM | 70 | 67.2 | 65.8 | 95.7 | 31.73 | 0.0743 | 0.64 | 13.64 | 0
December | 8 | 1AM to 2AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
December | 8 | 2AM to 3AM | 68.7 | 66.8 | 65.8 | 95.7 | 31.42 | 0.0745 | 0.64 | 13.61 | 0
December | 8 | 3AM to 4AM | 68.4 | 66.4 | 65.5 | 94.5 | 31.14 | 0.0745 | 0.63 | 13.6 | 0
December | 8 | 4AM to 5AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
December | 8 | 5AM to 6AM | 68.7 | 66.4 | 65.3 | 93.9 | 31.13 | 0.0745 | 0.63 | 13.61 | 0
December | 8 | 6AM to 7AM | 69.3 | 66.6 | 65.3 | 93.9 | 31.27 | 0.0744 | 0.63 | 13.62 | 0
December | 8 | 7AM to 8AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
December | 8 | 8AM to 9AM | 73.4 | 69.6 | 68 | 103.3 | 33.76 | 0.0738 | 0.69 | 13.76 | 0
December | 8 | 9AM to 10AM | 76.6 | 71.1 | 68.7 | 106 | 34.97 | 0.0733 | 0.71 | 13.85 | 0
December | 8 | 10AM to 11AM | 80.1 | 72.3 | 69.1 | 107.3 | 36.03 | 0.0728 | 0.72 | 13.94 | 0
December | 8 | 11AM to 12PM | 80.8 | 72.4 | 68.9 | 106.6 | 36.1 | 0.0727 | 0.71 | 13.96 | 0
December | 8 | 12PM to 1PM | 81.3 | 72.1 | 68.2 | 104 | 35.81 | 0.0727 | 0.69 | 13.96 | 0
December | 8 | 1PM to 2PM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
December | 8 | 2PM to 3PM | 81.3 | 71.7 | 67.6 | 102 | 35.51 | 0.0727 | 0.68 | 13.96 | 0
December | 8 | 3PM to 4PM | 80.8 | 71.9 | 68.2 | 104 | 35.68 | 0.0728 | 0.69 | 13.95 | 0
December | 8 | 4PM to 5PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
December | 8 | 5PM to 6PM | 78.6 | 71.4 | 68.4 | 104.6 | 35.25 | 0.073 | 0.7 | 13.89 | 0
December | 8 | 6PM to 7PM | 77.4 | 71.1 | 68.4 | 104.6 | 34.94 | 0.0732 | 0.7 | 13.86 | 0
December | 8 | 7PM to 8PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
December | 8 | 8PM to 9PM | 75 | 70 | 67.8 | 102.7 | 34.05 | 0.0736 | 0.69 | 13.79 | 0
December | 8 | 9PM to 10PM | 73.9 | 69.4 | 67.5 | 101.4 | 33.59 | 0.0737 | 0.68 | 13.76 | 0
December | 8 | 10PM to 11PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
December | 8 | 11PM to 12AM | 72.3 | 68.7 | 67.1 | 100.1 | 32.99 | 0.0739 | 0.67 | 13.72 | 0
December | 9 | 12AM to 1AM | 71.8 | 68.6 | 67.1 | 100.1 | 32.85 | 0.074 | 0.67 | 13.7 | 0
December | 9 | 1AM to 2AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
December | 9 | 2AM to 3AM | 70.3 | 67.9 | 66.7 | 98.8 | 32.3 | 0.0742 | 0.66 | 13.66 | 0
December | 9 | 3AM to 4AM | 69.8 | 67.6 | 66.6 | 98.2 | 32.07 | 0.0743 | 0.66 | 13.65 | 0
December | 9 | 4AM to 5AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
December | 9 | 5AM to 6AM | 69.8 | 67.6 | 66.6 | 98.2 | 32.07 | 0.0743 | 0.66 | 13.65 | 0
December | 9 | 6AM to 7AM | 70.3 | 68 | 66.9 | 99.5 | 32.4 | 0.0742 | 0.67 | 13.66 | 0
December | 9 | 7AM to 8AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
December | 9 | 8AM to 9AM | 75 | 70.7 | 68.9 | 106.6 | 34.68 | 0.0735 | 0.71 | 13.81 | 0
December | 9 | 9AM to 10AM | 79 | 71.8 | 68.7 | 106 | 35.55 | 0.073 | 0.71 | 13.91 | 0
December | 9 | 10AM to 11AM | 82.9 | 72.4 | 68 | 103.3 | 36.11 | 0.0725 | 0.69 | 14 | 0
December | 9 | 11AM to 12PM | 82.6 | 73 | 69.1 | 107.3 | 36.65 | 0.0725 | 0.72 | 14 | 0
December | 9 | 12PM to 1PM | 82.4 | 73.4 | 69.8 | 110.1 | 37.03 | 0.0725 | 0.73 | 14.01 | 0
December | 9 | 1PM to 2PM | 82 | 73.4 | 70 | 110.8 | 37.05 | 0.0726 | 0.74 | 14 | 0
December | 9 | 2PM to 3PM | 81 | 73.4 | 70.3 | 112.2 | 37.01 | 0.0727 | 0.75 | 13.98 | 0
December | 9 | 3PM to 4PM | 80.1 | 73.2 | 70.5 | 112.9 | 36.9 | 0.0728 | 0.75 | 13.96 | 0
December | 9 | 4PM to 5PM | 79 | 72.6 | 70 | 110.8 | 36.3 | 0.073 | 0.74 | 13.92 | 0
December | 9 | 5PM to 6PM | 77 | 72.3 | 70.3 | 112.2 | 36.03 | 0.0732 | 0.75 | 13.88 | 0
December | 9 | 6PM to 7PM | 75 | 71.7 | 70.3 | 112.2 | 35.54 | 0.0735 | 0.75 | 13.82 | 0
December | 9 | 7PM to 8PM | 73 | 70.9 | 70 | 110.8 | 34.83 | 0.0738 | 0.74 | 13.77 | 0
December | 9 | 8PM to 9PM | 73.4 | 71 | 70 | 110.8 | 34.92 | 0.0737 | 0.74 | 13.78 | 0
December | 9 | 9PM to 10PM | 73.6 | 70.8 | 69.6 | 109.4 | 34.75 | 0.0737 | 0.73 | 13.78 | 0
December | 9 | 10PM to 11PM | 73.9 | 70.5 | 69.1 | 107.3 | 34.52 | 0.0737 | 0.72 | 13.78 | 0
December | 9 | 11PM to 12AM | 73.2 | 70 | 68.5 | 105.3 | 34.02 | 0.0738 | 0.7 | 13.76 | 0
December | 10 | 12AM to 1AM | 72.7 | 69.3 | 67.8 | 102.7 | 33.48 | 0.0739 | 0.69 | 13.73 | 0
December | 10 | 1AM to 2AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
December | 10 | 2AM to 3AM | 71.2 | 68.4 | 67.1 | 100.1 | 32.72 | 0.0741 | 0.67 | 13.69 | 0
December | 10 | 3AM to 4AM | 70.7 | 68.2 | 67.1 | 100.1 | 32.59 | 0.0742 | 0.67 | 13.68 | 0
December | 10 | 4AM to 5AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
December | 10 | 5AM to 6AM | 70.3 | 68.2 | 67.3 | 100.7 | 32.6 | 0.0742 | 0.67 | 13.67 | 0
December | 10 | 6AM to 7AM | 70.7 | 68.3 | 67.3 | 100.7 | 32.69 | 0.0742 | 0.67 | 13.68 | 0
December | 10 | 7AM to 8AM | 71.1 | 68.9 | 68 | 103.3 | 33.18 | 0.0741 | 0.69 | 13.69 | 0
December | 10 | 8AM to 9AM | 74.7 | 70.1 | 68.2 | 104 | 34.17 | 0.0736 | 0.69 | 13.79 | 0
December | 10 | 9AM to 10AM | 78.4 | 70.7 | 67.3 | 100.7 | 34.59 | 0.0731 | 0.67 | 13.88 | 0
December | 10 | 10AM to 11AM | 82 | 70.9 | 66 | 96.3 | 34.79 | 0.0726 | 0.64 | 13.96 | 0
December | 10 | 11AM to 12PM | 83.3 | 71.4 | 66.2 | 96.9 | 35.2 | 0.0725 | 0.65 | 13.99 | 0
December | 10 | 12PM to 1PM | 84.7 | 71.6 | 65.8 | 95.7 | 35.36 | 0.0723 | 0.64 | 14.02 | 0
December | 10 | 1PM to 2PM | 86 | 71.4 | 64.9 | 92.7 | 35.2 | 0.0721 | 0.62 | 14.05 | 0
December | 10 | 2PM to 3PM | 84.4 | 71.4 | 65.7 | 95.1 | 35.18 | 0.0723 | 0.64 | 14.01 | 0
December | 10 | 3PM to 4PM | 82.6 | 71.2 | 66.2 | 96.9 | 35.02 | 0.0726 | 0.65 | 13.97 | 0
December | 10 | 4PM to 5PM | 81 | 70.6 | 66 | 96.3 | 34.53 | 0.0728 | 0.64 | 13.93 | 0
December | 10 | 5PM to 6PM | 79.3 | 70.5 | 66.6 | 98.2 | 34.42 | 0.073 | 0.66 | 13.89 | 0
December | 10 | 6PM to 7PM | 77.5 | 70.2 | 66.9 | 99.5 | 34.17 | 0.0732 | 0.67 | 13.85 | 0
December | 10 | 7PM to 8PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
December | 10 | 8PM to 9PM | 74.7 | 69.3 | 66.9 | 99.5 | 33.46 | 0.0736 | 0.67 | 13.78 | 0
December | 10 | 9PM to 10PM | 73.2 | 68.6 | 66.6 | 98.2 | 32.91 | 0.0738 | 0.66 | 13.73 | 0
December | 10 | 10PM to 11PM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
December | 10 | 11PM to 12AM | 71.2 | 67.8 | 66.2 | 96.9 | 32.23 | 0.0741 | 0.65 | 13.68 | 0
December | 11 | 12AM to 1AM | 70.7 | 67.6 | 66.2 | 96.9 | 32.1 | 0.0742 | 0.65 | 13.67 | 0
December | 11 | 1AM to 2AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
December | 11 | 2AM to 3AM | 69.3 | 66.9 | 65.8 | 95.7 | 31.55 | 0.0744 | 0.64 | 13.63 | 0
December | 11 | 3AM to 4AM | 68.7 | 66.5 | 65.5 | 94.5 | 31.23 | 0.0745 | 0.63 | 13.61 | 0
December | 11 | 4AM to 5AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
December | 11 | 5AM to 6AM | 69.1 | 66.6 | 65.5 | 94.5 | 31.32 | 0.0744 | 0.63 | 13.62 | 0
December | 11 | 6AM to 7AM | 70 | 67.2 | 65.8 | 95.7 | 31.73 | 0.0743 | 0.64 | 13.64 | 0
December | 11 | 7AM to 8AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
December | 11 | 8AM to 9AM | 74.7 | 69.9 | 67.8 | 102.7 | 33.97 | 0.0736 | 0.69 | 13.79 | 0
December | 11 | 9AM to 10AM | 78.4 | 70.9 | 67.6 | 102 | 34.8 | 0.0731 | 0.68 | 13.88 | 0
December | 11 | 10AM to 11AM | 82 | 71.5 | 66.9 | 99.5 | 35.28 | 0.0726 | 0.67 | 13.97 | 0
December | 11 | 11AM to 12PM | 82.8 | 72 | 67.5 | 101.4 | 35.76 | 0.0725 | 0.68 | 13.99 | 0
December | 11 | 12PM to 1PM | 83.3 | 72.2 | 67.5 | 101.4 | 35.89 | 0.0724 | 0.68 | 14 | 0
December | 11 | 1PM to 2PM | 84 | 72.1 | 66.9 | 99.5 | 35.77 | 0.0724 | 0.67 | 14.02 | 0
December | 11 | 2PM to 3PM | 83.3 | 72.3 | 67.6 | 102 | 35.99 | 0.0724 | 0.68 | 14.01 | 0
December | 11 | 3PM to 4PM | 82.8 | 72.5 | 68.2 | 104 | 36.17 | 0.0725 | 0.69 | 14 | 0
December | 11 | 4PM to 5PM | 82 | 72.2 | 68 | 103.3 | 35.89 | 0.0726 | 0.69 | 13.98 | 0
December | 11 | 5PM to 6PM | 80.1 | 71.8 | 68.4 | 104.6 | 35.61 | 0.0729 | 0.7 | 13.93 | 0
December | 11 | 6PM to 7PM | 77.9 | 71.2 | 68.4 | 104.6 | 35.07 | 0.0731 | 0.7 | 13.88 | 0
December | 11 | 7PM to 8PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
December | 11 | 8PM to 9PM | 75 | 70 | 67.8 | 102.7 | 34.05 | 0.0736 | 0.69 | 13.79 | 0
December | 11 | 9PM to 10PM | 73.9 | 69.4 | 67.5 | 101.4 | 33.59 | 0.0737 | 0.68 | 13.76 | 0
December | 11 | 10PM to 11PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
December | 11 | 11PM to 12AM | 72 | 68.5 | 66.9 | 99.5 | 32.8 | 0.074 | 0.67 | 13.71 | 0
December | 12 | 12AM to 1AM | 71.1 | 68 | 66.6 | 98.2 | 32.38 | 0.0741 | 0.66 | 13.68 | 0
December | 12 | 1AM to 2AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
December | 12 | 2AM to 3AM | 69.6 | 67.3 | 66.2 | 96.9 | 31.83 | 0.0743 | 0.65 | 13.64 | 0
December | 12 | 3AM to 4AM | 69.4 | 67.2 | 66.2 | 96.9 | 31.79 | 0.0744 | 0.65 | 13.63 | 0
December | 12 | 4AM to 5AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
December | 12 | 5AM to 6AM | 69.8 | 67.2 | 66 | 96.3 | 31.78 | 0.0743 | 0.64 | 13.64 | 0
December | 12 | 6AM to 7AM | 70.3 | 67.2 | 65.7 | 95.1 | 31.72 | 0.0742 | 0.64 | 13.65 | 0
December | 12 | 7AM to 8AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
December | 12 | 8AM to 9AM | 74.3 | 69.4 | 67.3 | 100.7 | 33.57 | 0.0737 | 0.67 | 13.77 | 0
December | 12 | 9AM to 10AM | 77.7 | 70.5 | 67.3 | 100.7 | 34.42 | 0.0732 | 0.67 | 13.86 | 0
December | 12 | 10AM to 11AM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
December | 12 | 11AM to 12PM | 82.2 | 72.1 | 67.8 | 102.7 | 35.83 | 0.0726 | 0.69 | 13.98 | 0
December | 12 | 12PM to 1PM | 83.7 | 72.7 | 68.2 | 104 | 36.39 | 0.0724 | 0.69 | 14.02 | 0
December | 12 | 1PM to 2PM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
December | 12 | 2PM to 3PM | 84.2 | 73.2 | 68.7 | 106 | 36.84 | 0.0723 | 0.71 | 14.04 | 0
December | 12 | 3PM to 4PM | 83.7 | 73.4 | 69.3 | 108 | 37.02 | 0.0724 | 0.72 | 14.03 | 0
December | 12 | 4PM to 5PM | 82.9 | 73.1 | 69.1 | 107.3 | 36.74 | 0.0725 | 0.72 | 14.01 | 0
December | 12 | 5PM to 6PM | 81 | 72.3 | 68.7 | 106 | 36.04 | 0.0727 | 0.71 | 13.96 | 0
December | 12 | 6PM to 7PM | 79 | 71.3 | 68 | 103.3 | 35.13 | 0.073 | 0.69 | 13.9 | 0
December | 12 | 7PM to 8PM | 77 | 70 | 66.9 | 99.5 | 34.04 | 0.0733 | 0.67 | 13.84 | 0
December | 12 | 8PM to 9PM | 75.7 | 69.6 | 66.9 | 99.5 | 33.73 | 0.0735 | 0.67 | 13.8 | 0
December | 12 | 9PM to 10PM | 74.3 | 69 | 66.6 | 98.2 | 33.18 | 0.0737 | 0.66 | 13.76 | 0
December | 12 | 10PM to 11PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
December | 12 | 11PM to 12AM | 72 | 68 | 66.2 | 96.9 | 32.41 | 0.074 | 0.65 | 13.7 | 0
December | 13 | 12AM to 1AM | 71.1 | 67.7 | 66.2 | 96.9 | 32.19 | 0.0741 | 0.65 | 13.68 | 0
December | 13 | 1AM to 2AM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
December | 13 | 2AM to 3AM | 69.6 | 67.3 | 66.2 | 96.9 | 31.83 | 0.0743 | 0.65 | 13.64 | 0
December | 13 | 3AM to 4AM | 69.4 | 67.2 | 66.2 | 96.9 | 31.79 | 0.0744 | 0.65 | 13.63 | 0
December | 13 | 4AM to 5AM | 69.1 | 67 | 66 | 96.3 | 31.6 | 0.0744 | 0.64 | 13.62 | 0
December | 13 | 5AM to 6AM | 70 | 67.6 | 66.6 | 98.2 | 32.11 | 0.0743 | 0.66 | 13.65 | 0
December | 13 | 6AM to 7AM | 71.1 | 68.2 | 66.9 | 99.5 | 32.58 | 0.0741 | 0.67 | 13.68 | 0
December | 13 | 7AM to 8AM | 72 | 69.2 | 68 | 103.3 | 33.4 | 0.074 | 0.69 | 13.72 | 0
December | 13 | 8AM to 9AM | 76.3 | 71.1 | 68.9 | 106.6 | 34.99 | 0.0734 | 0.71 | 13.84 | 0
December | 13 | 9AM to 10AM | 80.6 | 72.2 | 68.7 | 106 | 35.95 | 0.0728 | 0.71 | 13.95 | 0
December | 13 | 10AM to 11AM | 84.9 | 73 | 68 | 103.3 | 36.6 | 0.0722 | 0.69 | 14.05 | 0
December | 13 | 11AM to 12PM | 85.6 | 72.8 | 67.5 | 101.4 | 36.47 | 0.0721 | 0.68 | 14.06 | 0
December | 13 | 12PM to 1PM | 86.4 | 72.4 | 66.4 | 97.6 | 36.05 | 0.0721 | 0.65 | 14.07 | 0
December | 13 | 1PM to 2PM | 87.1 | 71.7 | 64.9 | 92.7 | 35.46 | 0.072 | 0.62 | 14.07 | 0
December | 13 | 2PM to 3PM | 85.6 | 71.4 | 65.1 | 93.3 | 35.2 | 0.0722 | 0.63 | 14.04 | 0
December | 13 | 3PM to 4PM | 84.4 | 70.9 | 64.8 | 92.1 | 34.71 | 0.0724 | 0.62 | 14 | 0
December | 13 | 4PM to 5PM | 82.9 | 70 | 64 | 89.8 | 33.98 | 0.0726 | 0.6 | 13.96 | 0
December | 13 | 5PM to 6PM | 81.3 | 70.1 | 64.9 | 92.7 | 34.05 | 0.0728 | 0.62 | 13.93 | 0
December | 13 | 6PM to 7PM | 79.7 | 70 | 65.7 | 95.1 | 34.02 | 0.073 | 0.64 | 13.89 | 0
December | 13 | 7PM to 8PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
December | 13 | 8PM to 9PM | 77.7 | 69.8 | 66.2 | 96.9 | 33.83 | 0.0732 | 0.65 | 13.85 | 0
December | 13 | 9PM to 10PM | 77.4 | 69.7 | 66.2 | 96.9 | 33.74 | 0.0733 | 0.65 | 13.84 | 0
December | 13 | 10PM to 11PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
December | 13 | 11PM to 12AM | 75.4 | 69.1 | 66.2 | 96.9 | 33.25 | 0.0735 | 0.65 | 13.79 | 0
December | 14 | 12AM to 1AM | 73.6 | 68.5 | 66.2 | 96.9 | 32.81 | 0.0738 | 0.65 | 13.74 | 0
December | 14 | 1AM to 2AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
December | 14 | 2AM to 3AM | 72.3 | 68.4 | 66.6 | 98.2 | 32.69 | 0.074 | 0.66 | 13.71 | 0
December | 14 | 3AM to 4AM | 72.7 | 68.7 | 66.9 | 99.5 | 32.98 | 0.0739 | 0.67 | 13.72 | 0
December | 14 | 4AM to 5AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
December | 14 | 5AM to 6AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
December | 14 | 6AM to 7AM | 75 | 69.2 | 66.6 | 98.2 | 33.36 | 0.0736 | 0.66 | 13.78 | 0
December | 14 | 7AM to 8AM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
December | 14 | 8AM to 9AM | 78.3 | 70.5 | 67.1 | 100.1 | 34.45 | 0.0731 | 0.67 | 13.87 | 0
December | 14 | 9AM to 10AM | 80.6 | 70.6 | 66.2 | 96.9 | 34.53 | 0.0728 | 0.65 | 13.92 | 0
December | 14 | 10AM to 11AM | 82.9 | 70.5 | 64.9 | 92.7 | 34.44 | 0.0725 | 0.62 | 13.97 | 0
December | 14 | 11AM to 12PM | 82.6 | 70.8 | 65.5 | 94.5 | 34.64 | 0.0726 | 0.63 | 13.96 | 0
December | 14 | 12PM to 1PM | 82.4 | 70.7 | 65.5 | 94.5 | 34.59 | 0.0726 | 0.63 | 13.96 | 0
December | 14 | 1PM to 2PM | 82 | 70.3 | 64.9 | 92.7 | 34.22 | 0.0727 | 0.62 | 13.94 | 0
December | 14 | 2PM to 3PM | 81.7 | 70.3 | 65.1 | 93.3 | 34.23 | 0.0727 | 0.63 | 13.94 | 0
December | 14 | 3PM to 4PM | 81.3 | 70 | 64.8 | 92.1 | 33.95 | 0.0728 | 0.62 | 13.92 | 0
December | 14 | 4PM to 5PM | 81 | 69.4 | 64 | 89.8 | 33.5 | 0.0728 | 0.6 | 13.91 | 0
December | 14 | 5PM to 6PM | 79.3 | 69.5 | 64.9 | 92.7 | 33.56 | 0.073 | 0.62 | 13.88 | 0
December | 14 | 6PM to 7PM | 77.5 | 69.4 | 65.7 | 95.1 | 33.49 | 0.0733 | 0.64 | 13.84 | 0
December | 14 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
December | 14 | 8PM to 9PM | 75.9 | 69.5 | 66.6 | 98.2 | 33.58 | 0.0735 | 0.66 | 13.8 | 0
December | 14 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
December | 14 | 10PM to 11PM | 75.9 | 69.7 | 66.9 | 99.5 | 33.77 | 0.0734 | 0.67 | 13.81 | 0
December | 14 | 11PM to 12AM | 75.6 | 69.4 | 66.6 | 98.2 | 33.49 | 0.0735 | 0.66 | 13.8 | 0
December | 15 | 12AM to 1AM | 75.4 | 68.8 | 65.8 | 95.7 | 33.06 | 0.0735 | 0.64 | 13.78 | 0
December | 15 | 1AM to 2AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
December | 15 | 2AM to 3AM | 75 | 67.8 | 64.4 | 90.9 | 32.22 | 0.0736 | 0.61 | 13.76 | 0
December | 15 | 3AM to 4AM | 75 | 67.5 | 63.9 | 89.2 | 31.95 | 0.0736 | 0.6 | 13.75 | 0
December | 15 | 4AM to 5AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
December | 15 | 5AM to 6AM | 75.7 | 67.4 | 63.3 | 87.5 | 31.86 | 0.0735 | 0.59 | 13.77 | 0
December | 15 | 6AM to 7AM | 76.3 | 67.6 | 63.3 | 87.5 | 31.99 | 0.0735 | 0.59 | 13.78 | 0
December | 15 | 7AM to 8AM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
December | 15 | 8AM to 9AM | 79.3 | 69.3 | 64.6 | 91.5 | 33.37 | 0.073 | 0.61 | 13.87 | 0
December | 15 | 9AM to 10AM | 81.7 | 69.6 | 64 | 89.8 | 33.68 | 0.0727 | 0.6 | 13.93 | 0
December | 15 | 10AM to 11AM | 84 | 69.7 | 63 | 86.4 | 33.72 | 0.0724 | 0.58 | 13.98 | 0
December | 15 | 11AM to 12PM | 84 | 70.3 | 64 | 89.8 | 34.25 | 0.0724 | 0.6 | 13.99 | 0
December | 15 | 12PM to 1PM | 84 | 70.8 | 64.8 | 92.1 | 34.62 | 0.0724 | 0.62 | 13.99 | 0
December | 15 | 1PM to 2PM | 84 | 70.9 | 64.9 | 92.7 | 34.71 | 0.0724 | 0.62 | 14 | 0
December | 15 | 2PM to 3PM | 82.8 | 70.7 | 65.3 | 93.9 | 34.59 | 0.0726 | 0.63 | 13.97 | 0
December | 15 | 3PM to 4PM | 81.3 | 70.4 | 65.5 | 94.5 | 34.33 | 0.0727 | 0.63 | 13.93 | 0
December | 15 | 4PM to 5PM | 80.1 | 69.7 | 64.9 | 92.7 | 33.74 | 0.0729 | 0.62 | 13.89 | 0
December | 15 | 5PM to 6PM | 78.6 | 69.7 | 65.7 | 95.1 | 33.76 | 0.0731 | 0.64 | 13.86 | 0
December | 15 | 6PM to 7PM | 77.4 | 69.5 | 66 | 96.3 | 33.64 | 0.0733 | 0.64 | 13.84 | 0
December | 15 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
December | 15 | 8PM to 9PM | 76.3 | 69 | 65.7 | 95.1 | 33.18 | 0.0734 | 0.64 | 13.8 | 0
December | 15 | 9PM to 10PM | 76.6 | 68.7 | 64.9 | 92.7 | 32.89 | 0.0734 | 0.62 | 13.81 | 0
December | 15 | 10PM to 11PM | 77 | 68.2 | 64 | 89.8 | 32.53 | 0.0734 | 0.6 | 13.81 | 0
December | 15 | 11PM to 12AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
December | 16 | 12AM to 1AM | 73 | 68 | 65.7 | 95.1 | 32.39 | 0.0739 | 0.64 | 13.72 | 0
December | 16 | 1AM to 2AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
December | 16 | 2AM to 3AM | 71.4 | 67.9 | 66.2 | 96.9 | 32.27 | 0.0741 | 0.65 | 13.68 | 0
December | 16 | 3AM to 4AM | 71.6 | 67.9 | 66.2 | 96.9 | 32.32 | 0.0741 | 0.65 | 13.69 | 0
December | 16 | 4AM to 5AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
December | 16 | 5AM to 6AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
December | 16 | 6AM to 7AM | 73.9 | 67 | 63.7 | 88.6 | 31.59 | 0.0738 | 0.59 | 13.72 | 0
December | 16 | 7AM to 8AM | 75 | 66.9 | 63 | 86.4 | 31.51 | 0.0737 | 0.58 | 13.74 | 0
December | 16 | 8AM to 9AM | 75.4 | 68.6 | 65.5 | 94.5 | 32.87 | 0.0736 | 0.63 | 13.78 | 0
December | 16 | 9AM to 10AM | 75.6 | 69.6 | 66.9 | 99.5 | 33.68 | 0.0735 | 0.67 | 13.8 | 0
December | 16 | 10AM to 11AM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
December | 16 | 11AM to 12PM | 77.5 | 70.5 | 67.5 | 101.4 | 34.47 | 0.0732 | 0.68 | 13.86 | 0
December | 16 | 12PM to 1PM | 79.3 | 70.4 | 66.4 | 97.6 | 34.32 | 0.073 | 0.65 | 13.89 | 0
December | 16 | 1PM to 2PM | 81 | 70 | 64.9 | 92.7 | 33.96 | 0.0728 | 0.62 | 13.92 | 0
December | 16 | 2PM to 3PM | 80.1 | 69.9 | 65.3 | 93.9 | 33.92 | 0.0729 | 0.63 | 13.9 | 0
December | 16 | 3PM to 4PM | 79 | 69.7 | 65.5 | 94.5 | 33.75 | 0.0731 | 0.63 | 13.87 | 0
December | 16 | 4PM to 5PM | 78.1 | 69.1 | 64.9 | 92.7 | 33.25 | 0.0732 | 0.62 | 13.84 | 0
December | 16 | 5PM to 6PM | 77 | 69.3 | 65.8 | 95.7 | 33.46 | 0.0733 | 0.64 | 13.82 | 0
December | 16 | 6PM to 7PM | 76.1 | 69.5 | 66.6 | 98.2 | 33.62 | 0.0734 | 0.66 | 13.81 | 0
December | 16 | 7PM to 8PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
December | 16 | 8PM to 9PM | 74.7 | 69.3 | 66.9 | 99.5 | 33.46 | 0.0736 | 0.67 | 13.78 | 0
December | 16 | 9PM to 10PM | 74.3 | 69 | 66.6 | 98.2 | 33.18 | 0.0737 | 0.66 | 13.76 | 0
December | 16 | 10PM to 11PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
December | 16 | 11PM to 12AM | 73.6 | 68.5 | 66.2 | 96.9 | 32.81 | 0.0738 | 0.65 | 13.74 | 0
December | 17 | 12AM to 1AM | 73.4 | 68.5 | 66.2 | 96.9 | 32.76 | 0.0738 | 0.65 | 13.74 | 0
December | 17 | 1AM to 2AM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
December | 17 | 2AM to 3AM | 72.3 | 68.1 | 66.2 | 96.9 | 32.5 | 0.074 | 0.65 | 13.71 | 0
December | 17 | 3AM to 4AM | 71.8 | 68 | 66.2 | 96.9 | 32.36 | 0.074 | 0.65 | 13.69 | 0
December | 17 | 4AM to 5AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
December | 17 | 5AM to 6AM | 71.4 | 67.7 | 66 | 96.3 | 32.18 | 0.0741 | 0.64 | 13.68 | 0
December | 17 | 6AM to 7AM | 71.6 | 67.6 | 65.7 | 95.1 | 32.03 | 0.0741 | 0.64 | 13.68 | 0
December | 17 | 7AM to 8AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
December | 17 | 8AM to 9AM | 72.7 | 68.9 | 67.3 | 100.7 | 33.17 | 0.0739 | 0.67 | 13.73 | 0
December | 17 | 9AM to 10AM | 73.2 | 69.1 | 67.3 | 100.7 | 33.31 | 0.0738 | 0.67 | 13.74 | 0
December | 17 | 10AM to 11AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
December | 17 | 11AM to 12PM | 74.7 | 69.9 | 67.8 | 102.7 | 33.97 | 0.0736 | 0.69 | 13.79 | 0
December | 17 | 12PM to 1PM | 75.2 | 70.3 | 68.2 | 104 | 34.3 | 0.0735 | 0.69 | 13.8 | 0
December | 17 | 1PM to 2PM | 75.9 | 70.4 | 68 | 103.3 | 34.38 | 0.0734 | 0.69 | 13.82 | 0
December | 17 | 2PM to 3PM | 75.2 | 70.1 | 67.8 | 102.7 | 34.1 | 0.0735 | 0.69 | 13.8 | 0
December | 17 | 3PM to 4PM | 74.7 | 69.4 | 67.1 | 100.1 | 33.56 | 0.0736 | 0.67 | 13.78 | 0
December | 17 | 4PM to 5PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
December | 17 | 5PM to 6PM | 73.2 | 68.5 | 66.4 | 97.6 | 32.81 | 0.0738 | 0.65 | 13.73 | 0
December | 17 | 6PM to 7PM | 72.7 | 68.4 | 66.4 | 97.6 | 32.68 | 0.0739 | 0.65 | 13.72 | 0
December | 17 | 7PM to 8PM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0
December | 17 | 8PM to 9PM | 72 | 67.8 | 65.8 | 95.7 | 32.22 | 0.074 | 0.64 | 13.69 | 0
December | 17 | 9PM to 10PM | 72 | 67.6 | 65.5 | 94.5 | 32.03 | 0.074 | 0.63 | 13.69 | 0
December | 17 | 10PM to 11PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
December | 17 | 11PM to 12AM | 71.6 | 67.2 | 65.1 | 93.3 | 31.75 | 0.0741 | 0.63 | 13.68 | 0
December | 18 | 12AM to 1AM | 71.4 | 67.1 | 65.1 | 93.3 | 31.7 | 0.0741 | 0.63 | 13.67 | 0
December | 18 | 1AM to 2AM | 71.1 | 66.9 | 64.9 | 92.7 | 31.52 | 0.0742 | 0.62 | 13.66 | 0
December | 18 | 2AM to 3AM | 71.1 | 67.3 | 65.5 | 94.5 | 31.8 | 0.0742 | 0.63 | 13.67 | 0
December | 18 | 3AM to 4AM | 71.1 | 67.5 | 65.8 | 95.7 | 31.99 | 0.0741 | 0.64 | 13.67 | 0
December | 18 | 4AM to 5AM | 71.1 | 67.6 | 66 | 96.3 | 32.09 | 0.0741 | 0.64 | 13.67 | 0
December | 18 | 5AM to 6AM | 71.4 | 67.3 | 65.3 | 93.9 | 31.8 | 0.0741 | 0.63 | 13.68 | 0
December | 18 | 6AM to 7AM | 71.6 | 66.7 | 64.4 | 90.9 | 31.38 | 0.0741 | 0.61 | 13.67 | 0
December | 18 | 7AM to 8AM | 72 | 66.6 | 64 | 89.8 | 31.29 | 0.0741 | 0.6 | 13.68 | 0
December | 18 | 8AM to 9AM | 74.3 | 67.5 | 64.2 | 90.4 | 31.95 | 0.0737 | 0.61 | 13.74 | 0
December | 18 | 9AM to 10AM | 76.6 | 67.7 | 63.3 | 87.5 | 32.08 | 0.0734 | 0.59 | 13.79 | 0
December | 18 | 10AM to 11AM | 79 | 67.7 | 62.1 | 83.6 | 32.05 | 0.0731 | 0.56 | 13.84 | 0
December | 18 | 11AM to 12PM | 79 | 67.8 | 62.2 | 84.2 | 32.13 | 0.0731 | 0.57 | 13.84 | 0
December | 18 | 12PM to 1PM | 79 | 67.5 | 61.9 | 83.1 | 31.96 | 0.0731 | 0.56 | 13.84 | 0
December | 18 | 1PM to 2PM | 79 | 67 | 61 | 80.4 | 31.55 | 0.0731 | 0.54 | 13.83 | 0
December | 18 | 2PM to 3PM | 77.4 | 67.8 | 63.1 | 86.9 | 32.17 | 0.0733 | 0.58 | 13.81 | 0
December | 18 | 3PM to 4PM | 75.6 | 68.2 | 64.8 | 92.1 | 32.54 | 0.0735 | 0.62 | 13.78 | 0
December | 18 | 4PM to 5PM | 73.9 | 68.5 | 66 | 96.3 | 32.8 | 0.0737 | 0.64 | 13.75 | 0
December | 18 | 5PM to 6PM | 73.6 | 67.7 | 64.9 | 92.7 | 32.14 | 0.0738 | 0.62 | 13.73 | 0
December | 18 | 6PM to 7PM | 73.4 | 66.9 | 63.7 | 88.6 | 31.46 | 0.0739 | 0.59 | 13.71 | 0
December | 18 | 7PM to 8PM | 73 | 65.8 | 62.1 | 83.6 | 30.59 | 0.0739 | 0.56 | 13.69 | 0
December | 18 | 8PM to 9PM | 72.3 | 65.4 | 61.9 | 83.1 | 30.33 | 0.074 | 0.56 | 13.67 | 0
December | 18 | 9PM to 10PM | 71.8 | 65 | 61.5 | 82 | 30.03 | 0.0741 | 0.55 | 13.65 | 0
December | 18 | 10PM to 11PM | 71.1 | 64.5 | 61 | 80.4 | 29.61 | 0.0742 | 0.54 | 13.62 | 0
December | 18 | 11PM to 12AM | 71.4 | 64.4 | 60.6 | 79.4 | 29.53 | 0.0742 | 0.53 | 13.63 | 0
December | 19 | 12AM to 1AM | 71.6 | 64 | 59.9 | 77.3 | 29.26 | 0.0742 | 0.52 | 13.63 | 0
December | 19 | 1AM to 2AM | 72 | 63.6 | 59 | 74.9 | 28.96 | 0.0741 | 0.5 | 13.63 | 0
December | 19 | 2AM to 3AM | 71.6 | 62.7 | 57.6 | 71 | 28.27 | 0.0742 | 0.48 | 13.61 | 0
December | 19 | 3AM to 4AM | 71.4 | 61.7 | 55.9 | 66.9 | 27.59 | 0.0743 | 0.45 | 13.59 | 0
December | 19 | 4AM to 5AM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
December | 19 | 5AM to 6AM | 71.4 | 60.7 | 54 | 62.2 | 26.85 | 0.0743 | 0.42 | 13.58 | 0
December | 19 | 6AM to 7AM | 71.6 | 60.5 | 53.6 | 61.4 | 26.76 | 0.0743 | 0.41 | 13.58 | 0
December | 19 | 7AM to 8AM | 72 | 60.9 | 54 | 62.2 | 26.98 | 0.0742 | 0.42 | 13.59 | 0
December | 19 | 8AM to 9AM | 73.6 | 62.3 | 55.6 | 66 | 27.98 | 0.074 | 0.45 | 13.64 | 0
December | 19 | 9AM to 10AM | 75.4 | 63.1 | 55.9 | 66.9 | 28.55 | 0.0737 | 0.45 | 13.69 | 0
December | 19 | 10AM to 11AM | 77 | 63.6 | 55.9 | 66.9 | 28.95 | 0.0735 | 0.45 | 13.74 | 0
December | 19 | 11AM to 12PM | 77 | 63.6 | 55.8 | 66.5 | 28.88 | 0.0735 | 0.45 | 13.73 | 0
December | 19 | 12PM to 1PM | 77 | 63.2 | 55 | 64.7 | 28.61 | 0.0735 | 0.44 | 13.73 | 0
December | 19 | 1PM to 2PM | 77 | 62.6 | 54 | 62.2 | 28.21 | 0.0735 | 0.42 | 13.72 | 0
December | 19 | 2PM to 3PM | 75.9 | 62.4 | 54.1 | 62.6 | 28.01 | 0.0737 | 0.42 | 13.69 | 0
December | 19 | 3PM to 4PM | 75 | 61.9 | 53.8 | 61.8 | 27.66 | 0.0738 | 0.42 | 13.67 | 0
December | 19 | 4PM to 5PM | 73.9 | 61.1 | 53.1 | 60.1 | 27.14 | 0.074 | 0.41 | 13.64 | 0
December | 19 | 5PM to 6PM | 73 | 60.6 | 52.7 | 59.3 | 26.8 | 0.0741 | 0.4 | 13.61 | 0
December | 19 | 6PM to 7PM | 72 | 60 | 52.2 | 58.2 | 26.35 | 0.0743 | 0.39 | 13.58 | 0
December | 19 | 7PM to 8PM | 71.1 | 59.1 | 51.1 | 55.9 | 25.77 | 0.0744 | 0.38 | 13.55 | 0
December | 19 | 8PM to 9PM | 71.1 | 59.7 | 52.3 | 58.6 | 26.19 | 0.0744 | 0.4 | 13.56 | 0
December | 19 | 9PM to 10PM | 71.1 | 60.2 | 53.2 | 60.6 | 26.51 | 0.0744 | 0.41 | 13.56 | 0
December | 19 | 10PM to 11PM | 71.1 | 60.5 | 54 | 62.2 | 26.76 | 0.0744 | 0.42 | 13.57 | 0
December | 19 | 11PM to 12AM | 70.7 | 60.7 | 54.5 | 63.5 | 26.87 | 0.0744 | 0.43 | 13.56 | 0
December | 20 | 12AM to 1AM | 70.3 | 60.8 | 54.9 | 64.3 | 26.91 | 0.0744 | 0.43 | 13.56 | 0
December | 20 | 1AM to 2AM | 70 | 60.7 | 55 | 64.7 | 26.89 | 0.0745 | 0.44 | 13.55 | 0
December | 20 | 2AM to 3AM | 70 | 60.2 | 54.1 | 62.6 | 26.56 | 0.0745 | 0.42 | 13.54 | 0
December | 20 | 3AM to 4AM | 70 | 59.8 | 53.2 | 60.6 | 26.24 | 0.0745 | 0.41 | 13.54 | 0
December | 20 | 4AM to 5AM | 70 | 59.1 | 52 | 57.8 | 25.81 | 0.0745 | 0.39 | 13.53 | 0
December | 20 | 5AM to 6AM | 70 | 59.8 | 53.2 | 60.6 | 26.24 | 0.0745 | 0.41 | 13.54 | 0
December | 20 | 6AM to 7AM | 70 | 60.3 | 54.3 | 63 | 26.63 | 0.0745 | 0.43 | 13.54 | 0
December | 20 | 7AM to 8AM | 70 | 61.2 | 55.9 | 66.9 | 27.23 | 0.0745 | 0.45 | 13.56 | 0
December | 20 | 8AM to 9AM | 72 | 62.2 | 56.5 | 68.3 | 27.93 | 0.0742 | 0.46 | 13.61 | 0
December | 20 | 9AM to 10AM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
December | 20 | 10AM to 11AM | 75.9 | 62.8 | 55 | 64.7 | 28.34 | 0.0737 | 0.44 | 13.7 | 0
December | 20 | 11AM to 12PM | 75.9 | 63.1 | 55.6 | 66 | 28.55 | 0.0737 | 0.45 | 13.7 | 0
December | 20 | 12PM to 1PM | 75.9 | 63.1 | 55.6 | 66 | 28.55 | 0.0737 | 0.45 | 13.7 | 0
December | 20 | 1PM to 2PM | 75.9 | 62.8 | 55 | 64.7 | 28.34 | 0.0737 | 0.44 | 13.7 | 0
December | 20 | 2PM to 3PM | 75.2 | 62.9 | 55.8 | 66.5 | 28.44 | 0.0738 | 0.45 | 13.69 | 0
December | 20 | 3PM to 4PM | 74.7 | 62.9 | 56.1 | 67.4 | 28.45 | 0.0738 | 0.45 | 13.68 | 0
December | 20 | 4PM to 5PM | 73.9 | 62.6 | 55.9 | 66.9 | 28.2 | 0.0739 | 0.45 | 13.66 | 0
December | 20 | 5PM to 6PM | 73.2 | 62.3 | 55.9 | 66.9 | 28.03 | 0.074 | 0.45 | 13.64 | 0
December | 20 | 6PM to 7PM | 72.7 | 62.1 | 55.8 | 66.5 | 27.83 | 0.0741 | 0.45 | 13.62 | 0
December | 20 | 7PM to 8PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
December | 20 | 8PM to 9PM | 71.6 | 61.6 | 55.6 | 66 | 27.49 | 0.0743 | 0.45 | 13.59 | 0
December | 20 | 9PM to 10PM | 71.4 | 61.7 | 55.9 | 66.9 | 27.59 | 0.0743 | 0.45 | 13.59 | 0
December | 20 | 10PM to 11PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
December | 20 | 11PM to 12AM | 70.3 | 61.6 | 56.5 | 68.3 | 27.53 | 0.0744 | 0.46 | 13.57 | 0
December | 21 | 12AM to 1AM | 69.8 | 61.6 | 56.8 | 69.2 | 27.54 | 0.0745 | 0.47 | 13.56 | 0
December | 21 | 1AM to 2AM | 69.1 | 61.5 | 57 | 69.6 | 27.44 | 0.0746 | 0.47 | 13.54 | 0
December | 21 | 2AM to 3AM | 67.1 | 61.3 | 57.9 | 72 | 27.32 | 0.0749 | 0.48 | 13.5 | 0
December | 21 | 3AM to 4AM | 64.9 | 60.9 | 58.6 | 73.9 | 27.09 | 0.0751 | 0.5 | 13.45 | 0
December | 21 | 4AM to 5AM | 63 | 60.5 | 59 | 74.9 | 26.75 | 0.0754 | 0.5 | 13.4 | 0
December | 21 | 5AM to 6AM | 63.7 | 61 | 59.5 | 76.3 | 27.16 | 0.0753 | 0.51 | 13.42 | 0
December | 21 | 6AM to 7AM | 64.2 | 61.5 | 59.9 | 77.3 | 27.45 | 0.0752 | 0.52 | 13.44 | 0
December | 21 | 7AM to 8AM | 64.9 | 62.4 | 61 | 80.4 | 28.11 | 0.0751 | 0.54 | 13.47 | 0
December | 21 | 8AM to 9AM | 68.5 | 63.4 | 60.6 | 79.4 | 28.83 | 0.0746 | 0.53 | 13.56 | 0
December | 21 | 9AM to 10AM | 72.3 | 63.7 | 59 | 74.9 | 29.05 | 0.0741 | 0.5 | 13.64 | 0
December | 21 | 10AM to 11AM | 75.9 | 63.8 | 57 | 69.6 | 29.11 | 0.0736 | 0.47 | 13.72 | 0
December | 21 | 11AM to 12PM | 76.3 | 64.4 | 57.7 | 71.5 | 29.49 | 0.0736 | 0.48 | 13.73 | 0
December | 21 | 12PM to 1PM | 76.6 | 64.7 | 58.1 | 72.4 | 29.72 | 0.0735 | 0.49 | 13.74 | 0
December | 21 | 1PM to 2PM | 77 | 64.7 | 57.9 | 72 | 29.74 | 0.0735 | 0.48 | 13.75 | 0
December | 21 | 2PM to 3PM | 76.3 | 64.2 | 57.4 | 70.6 | 29.34 | 0.0736 | 0.48 | 13.73 | 0
December | 21 | 3PM to 4PM | 75.7 | 63.5 | 56.5 | 68.3 | 28.85 | 0.0737 | 0.46 | 13.71 | 0
December | 21 | 4PM to 5PM | 75 | 62.5 | 55 | 64.7 | 28.12 | 0.0738 | 0.44 | 13.68 | 0
December | 21 | 5PM to 6PM | 73.8 | 62.2 | 55.4 | 65.6 | 27.95 | 0.074 | 0.44 | 13.65 | 0
December | 21 | 6PM to 7PM | 72.3 | 61.7 | 55.4 | 65.6 | 27.6 | 0.0742 | 0.44 | 13.61 | 0
December | 21 | 7PM to 8PM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
December | 21 | 8PM to 9PM | 69.6 | 61.5 | 56.7 | 68.7 | 27.43 | 0.0745 | 0.46 | 13.55 | 0
December | 21 | 9PM to 10PM | 68.4 | 61.7 | 57.9 | 72 | 27.63 | 0.0747 | 0.48 | 13.53 | 0
December | 21 | 10PM to 11PM | 66.9 | 61.9 | 59 | 74.9 | 27.72 | 0.0749 | 0.5 | 13.5 | 0
December | 21 | 11PM to 12AM | 65.7 | 61.3 | 58.8 | 74.4 | 27.34 | 0.075 | 0.5 | 13.47 | 0
December | 22 | 12AM to 1AM | 64.2 | 60.6 | 58.5 | 73.4 | 26.84 | 0.0753 | 0.49 | 13.43 | 0
December | 22 | 1AM to 2AM | 63 | 59.8 | 57.9 | 72 | 26.3 | 0.0754 | 0.48 | 13.39 | 0
December | 22 | 2AM to 3AM | 63.3 | 60 | 58.1 | 72.4 | 26.47 | 0.0754 | 0.49 | 13.4 | 0
December | 22 | 3AM to 4AM | 63.7 | 60.2 | 58.1 | 72.4 | 26.55 | 0.0753 | 0.49 | 13.41 | 0
December | 22 | 4AM to 5AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
December | 22 | 5AM to 6AM | 64.4 | 60.5 | 58.3 | 72.9 | 26.81 | 0.0752 | 0.49 | 13.43 | 0
December | 22 | 6AM to 7AM | 64.6 | 60.6 | 58.3 | 72.9 | 26.85 | 0.0752 | 0.49 | 13.44 | 0
December | 22 | 7AM to 8AM | 64.9 | 61.2 | 59 | 74.9 | 27.24 | 0.0751 | 0.5 | 13.45 | 0
December | 22 | 8AM to 9AM | 68.9 | 62.3 | 58.6 | 73.9 | 28.06 | 0.0746 | 0.5 | 13.55 | 0
December | 22 | 9AM to 10AM | 73 | 62.9 | 57 | 69.6 | 28.41 | 0.074 | 0.47 | 13.64 | 0
December | 22 | 10AM to 11AM | 77 | 63.2 | 55 | 64.7 | 28.61 | 0.0735 | 0.44 | 13.73 | 0
December | 22 | 11AM to 12PM | 77.7 | 63.3 | 54.9 | 64.3 | 28.72 | 0.0734 | 0.43 | 13.75 | 0
December | 22 | 12PM to 1PM | 78.3 | 63.2 | 54.1 | 62.6 | 28.58 | 0.0734 | 0.42 | 13.75 | 0
December | 22 | 1PM to 2PM | 79 | 62.9 | 53.1 | 60.1 | 28.37 | 0.0733 | 0.41 | 13.76 | 0
December | 22 | 2PM to 3PM | 77.9 | 63 | 54.1 | 62.6 | 28.5 | 0.0734 | 0.42 | 13.74 | 0
December | 22 | 3PM to 4PM | 77 | 63.1 | 54.9 | 64.3 | 28.54 | 0.0735 | 0.43 | 13.73 | 0
December | 22 | 4PM to 5PM | 75.9 | 62.8 | 55 | 64.7 | 28.34 | 0.0737 | 0.44 | 13.7 | 0
December | 22 | 5PM to 6PM | 75 | 63.2 | 56.3 | 67.8 | 28.61 | 0.0738 | 0.46 | 13.69 | 0
December | 22 | 6PM to 7PM | 73.9 | 63.4 | 57.4 | 70.6 | 28.77 | 0.0739 | 0.48 | 13.67 | 0
December | 22 | 7PM to 8PM | 73 | 63.4 | 57.9 | 72 | 28.77 | 0.074 | 0.48 | 13.65 | 0
December | 22 | 8PM to 9PM | 72.7 | 62.8 | 57.2 | 70.1 | 28.39 | 0.0741 | 0.47 | 13.63 | 0
December | 22 | 9PM to 10PM | 72.3 | 62.2 | 56.3 | 67.8 | 27.95 | 0.0741 | 0.46 | 13.62 | 0
December | 22 | 10PM to 11PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
December | 22 | 11PM to 12AM | 71.2 | 61 | 54.7 | 63.9 | 27.07 | 0.0743 | 0.43 | 13.58 | 0
December | 23 | 12AM to 1AM | 70.7 | 60.4 | 54 | 62.2 | 26.67 | 0.0744 | 0.42 | 13.56 | 0
December | 23 | 1AM to 2AM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
December | 23 | 2AM to 3AM | 68 | 59.7 | 54.5 | 63.5 | 26.21 | 0.0748 | 0.43 | 13.49 | 0
December | 23 | 3AM to 4AM | 66 | 59.8 | 55.9 | 66.9 | 26.27 | 0.075 | 0.45 | 13.45 | 0
December | 23 | 4AM to 5AM | 64 | 59.7 | 57 | 69.6 | 26.21 | 0.0753 | 0.47 | 13.41 | 0
December | 23 | 5AM to 6AM | 64.8 | 60.5 | 57.9 | 72 | 26.74 | 0.0752 | 0.48 | 13.44 | 0
December | 23 | 6AM to 7AM | 65.3 | 61.1 | 58.6 | 73.9 | 27.18 | 0.0751 | 0.5 | 13.46 | 0
December | 23 | 7AM to 8AM | 66 | 62.2 | 60.1 | 77.8 | 27.97 | 0.075 | 0.52 | 13.49 | 0
December | 23 | 8AM to 9AM | 69.6 | 63.3 | 59.9 | 77.3 | 28.77 | 0.0745 | 0.52 | 13.58 | 0
December | 23 | 9AM to 10AM | 73.4 | 63.9 | 58.6 | 73.9 | 29.16 | 0.074 | 0.5 | 13.66 | 0
December | 23 | 10AM to 11AM | 77 | 64.2 | 57 | 69.6 | 29.37 | 0.0735 | 0.47 | 13.74 | 0
December | 23 | 11AM to 12PM | 77.7 | 64.4 | 56.8 | 69.2 | 29.48 | 0.0734 | 0.47 | 13.76 | 0
December | 23 | 12PM to 1PM | 78.3 | 64.2 | 56.1 | 67.4 | 29.33 | 0.0733 | 0.45 | 13.77 | 0
December | 23 | 1PM to 2PM | 79 | 63.9 | 55 | 64.7 | 29.09 | 0.0732 | 0.44 | 13.78 | 0
December | 23 | 2PM to 3PM | 77.7 | 63.6 | 55.4 | 65.6 | 28.92 | 0.0734 | 0.44 | 13.75 | 0
December | 23 | 3PM to 4PM | 76.3 | 63.2 | 55.6 | 66 | 28.64 | 0.0736 | 0.45 | 13.71 | 0
December | 23 | 4PM to 5PM | 75 | 62.5 | 55 | 64.7 | 28.12 | 0.0738 | 0.44 | 13.68 | 0
December | 23 | 5PM to 6PM | 73.8 | 62.5 | 55.9 | 66.9 | 28.16 | 0.0739 | 0.45 | 13.65 | 0
December | 23 | 6PM to 7PM | 72.3 | 62.4 | 56.7 | 68.7 | 28.09 | 0.0741 | 0.46 | 13.62 | 0
December | 23 | 7PM to 8PM | 71.1 | 62.2 | 57 | 69.6 | 27.92 | 0.0743 | 0.47 | 13.59 | 0
December | 23 | 8PM to 9PM | 71.4 | 62.4 | 57.2 | 70.1 | 28.08 | 0.0743 | 0.47 | 13.6 | 0
December | 23 | 9PM to 10PM | 71.6 | 62.5 | 57.2 | 70.1 | 28.13 | 0.0742 | 0.47 | 13.61 | 0
December | 23 | 10PM to 11PM | 72 | 62.5 | 57 | 69.6 | 28.14 | 0.0742 | 0.47 | 13.61 | 0
December | 23 | 11PM to 12AM | 71.2 | 61.7 | 55.9 | 66.9 | 27.54 | 0.0743 | 0.45 | 13.59 | 0
December | 24 | 12AM to 1AM | 70.7 | 60.8 | 54.7 | 63.9 | 26.94 | 0.0744 | 0.43 | 13.56 | 0
December | 24 | 1AM to 2AM | 70 | 59.7 | 53.1 | 60.1 | 26.18 | 0.0745 | 0.41 | 13.53 | 0
December | 24 | 2AM to 3AM | 70 | 60.6 | 54.9 | 64.3 | 26.83 | 0.0745 | 0.43 | 13.55 | 0
December | 24 | 3AM to 4AM | 70 | 61.5 | 56.5 | 68.3 | 27.44 | 0.0745 | 0.46 | 13.56 | 0
December | 24 | 4AM to 5AM | 70 | 62.3 | 57.9 | 72 | 28.02 | 0.0744 | 0.48 | 13.57 | 0
December | 24 | 5AM to 6AM | 70.7 | 62.2 | 57.2 | 70.1 | 27.91 | 0.0744 | 0.47 | 13.58 | 0
December | 24 | 6AM to 7AM | 71.2 | 61.8 | 56.3 | 67.8 | 27.68 | 0.0743 | 0.46 | 13.59 | 0
December | 24 | 7AM to 8AM | 72 | 61.9 | 55.9 | 66.9 | 27.72 | 0.0742 | 0.45 | 13.61 | 0
December | 24 | 8AM to 9AM | 73.9 | 63.3 | 57.2 | 70.1 | 28.7 | 0.0739 | 0.47 | 13.67 | 0
December | 24 | 9AM to 10AM | 76.1 | 64.1 | 57.4 | 70.6 | 29.3 | 0.0736 | 0.48 | 13.72 | 0
December | 24 | 10AM to 11AM | 78.1 | 64.6 | 57 | 69.6 | 29.64 | 0.0733 | 0.47 | 13.77 | 0
December | 24 | 11AM to 12PM | 78.1 | 64.7 | 57.2 | 70.1 | 29.71 | 0.0733 | 0.47 | 13.77 | 0
December | 24 | 12PM to 1PM | 78.1 | 64.5 | 56.8 | 69.2 | 29.57 | 0.0733 | 0.47 | 13.77 | 0
December | 24 | 1PM to 2PM | 78.1 | 64 | 55.9 | 66.9 | 29.21 | 0.0734 | 0.45 | 13.76 | 0
December | 24 | 2PM to 3PM | 77 | 63.6 | 55.8 | 66.5 | 28.88 | 0.0735 | 0.45 | 13.73 | 0
December | 24 | 3PM to 4PM | 76.1 | 62.9 | 55 | 64.7 | 28.39 | 0.0736 | 0.44 | 13.71 | 0
December | 24 | 4PM to 5PM | 75 | 61.9 | 54 | 62.2 | 27.73 | 0.0738 | 0.42 | 13.67 | 0
December | 24 | 5PM to 6PM | 73.9 | 61.9 | 54.7 | 63.9 | 27.73 | 0.0739 | 0.43 | 13.65 | 0
December | 24 | 6PM to 7PM | 73 | 61.8 | 55 | 64.7 | 27.64 | 0.0741 | 0.44 | 13.63 | 0
December | 24 | 7PM to 8PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
December | 24 | 8PM to 9PM | 72 | 61.5 | 55.2 | 65.2 | 27.44 | 0.0742 | 0.44 | 13.6 | 0
December | 24 | 9PM to 10PM | 72 | 61.5 | 55.2 | 65.2 | 27.44 | 0.0742 | 0.44 | 13.6 | 0
December | 24 | 10PM to 11PM | 72 | 61.4 | 55 | 64.7 | 27.38 | 0.0742 | 0.44 | 13.6 | 0
December | 24 | 11PM to 12AM | 71.2 | 61.1 | 54.9 | 64.3 | 27.13 | 0.0743 | 0.43 | 13.58 | 0
December | 25 | 12AM to 1AM | 70.7 | 60.7 | 54.5 | 63.5 | 26.87 | 0.0744 | 0.43 | 13.56 | 0
December | 25 | 1AM to 2AM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
December | 25 | 2AM to 3AM | 70 | 60.2 | 54.1 | 62.6 | 26.56 | 0.0745 | 0.42 | 13.54 | 0
December | 25 | 3AM to 4AM | 70 | 60.2 | 54.1 | 62.6 | 26.56 | 0.0745 | 0.42 | 13.54 | 0
December | 25 | 4AM to 5AM | 70 | 60.1 | 54 | 62.2 | 26.5 | 0.0745 | 0.42 | 13.54 | 0
December | 25 | 5AM to 6AM | 70.3 | 60.5 | 54.3 | 63 | 26.72 | 0.0745 | 0.43 | 13.55 | 0
December | 25 | 6AM to 7AM | 70.7 | 60.6 | 54.3 | 63 | 26.8 | 0.0744 | 0.43 | 13.56 | 0
December | 25 | 7AM to 8AM | 71.1 | 61.1 | 55 | 64.7 | 27.16 | 0.0743 | 0.44 | 13.58 | 0
December | 25 | 8AM to 9AM | 72.7 | 62.5 | 56.7 | 68.7 | 28.17 | 0.0741 | 0.46 | 13.63 | 0
December | 25 | 9AM to 10AM | 74.3 | 63.3 | 57 | 69.6 | 28.71 | 0.0739 | 0.47 | 13.67 | 0
December | 25 | 10AM to 11AM | 75.9 | 63.8 | 57 | 69.6 | 29.11 | 0.0736 | 0.47 | 13.72 | 0
December | 25 | 11AM to 12PM | 77.4 | 64.2 | 56.8 | 69.2 | 29.39 | 0.0734 | 0.47 | 13.75 | 0
December | 25 | 12PM to 1PM | 78.6 | 64.3 | 56.1 | 67.4 | 29.41 | 0.0733 | 0.45 | 13.78 | 0
December | 25 | 1PM to 2PM | 80.1 | 64.2 | 55 | 64.7 | 29.35 | 0.0731 | 0.44 | 13.81 | 0
December | 25 | 2PM to 3PM | 78.6 | 64.1 | 55.8 | 66.5 | 29.28 | 0.0733 | 0.45 | 13.78 | 0
December | 25 | 3PM to 4PM | 77.4 | 63.9 | 56.1 | 67.4 | 29.11 | 0.0735 | 0.45 | 13.75 | 0
December | 25 | 4PM to 5PM | 75.9 | 63.3 | 55.9 | 66.9 | 28.69 | 0.0737 | 0.45 | 13.71 | 0
December | 25 | 5PM to 6PM | 74.3 | 62.9 | 56.3 | 67.8 | 28.43 | 0.0739 | 0.46 | 13.67 | 0
December | 25 | 6PM to 7PM | 72.7 | 62.4 | 56.3 | 67.8 | 28.03 | 0.0741 | 0.46 | 13.63 | 0
December | 25 | 7PM to 8PM | 71.1 | 61.6 | 55.9 | 66.9 | 27.5 | 0.0743 | 0.45 | 13.58 | 0
December | 25 | 8PM to 9PM | 70.3 | 61.4 | 56.1 | 67.4 | 27.39 | 0.0744 | 0.45 | 13.57 | 0
December | 25 | 9PM to 10PM | 69.8 | 61.2 | 56.1 | 67.4 | 27.26 | 0.0745 | 0.45 | 13.55 | 0
December | 25 | 10PM to 11PM | 69.1 | 60.9 | 55.9 | 66.9 | 27.02 | 0.0746 | 0.45 | 13.53 | 0
December | 25 | 11PM to 12AM | 66.7 | 60.3 | 56.5 | 68.3 | 26.65 | 0.0749 | 0.46 | 13.48 | 0
December | 26 | 12AM to 1AM | 64.4 | 59.7 | 56.8 | 69.2 | 26.22 | 0.0753 | 0.47 | 13.42 | 0
December | 26 | 1AM to 2AM | 62.1 | 58.9 | 57 | 69.6 | 25.72 | 0.0756 | 0.47 | 13.36 | 0
December | 26 | 2AM to 3AM | 62.8 | 59.5 | 57.6 | 71 | 26.11 | 0.0755 | 0.48 | 13.38 | 0
December | 26 | 3AM to 4AM | 63.3 | 59.9 | 57.9 | 72 | 26.39 | 0.0754 | 0.48 | 13.4 | 0
December | 26 | 4AM to 5AM | 64 | 60.2 | 57.9 | 72 | 26.57 | 0.0753 | 0.48 | 13.42 | 0
December | 26 | 5AM to 6AM | 65.7 | 61 | 58.3 | 72.9 | 27.11 | 0.0751 | 0.49 | 13.46 | 0
December | 26 | 6AM to 7AM | 67.5 | 61.6 | 58.3 | 72.9 | 27.55 | 0.0748 | 0.49 | 13.51 | 0
December | 26 | 7AM to 8AM | 69.1 | 62.6 | 59 | 74.9 | 28.25 | 0.0746 | 0.5 | 13.56 | 0
December | 26 | 8AM to 9AM | 72.1 | 64.2 | 59.9 | 77.3 | 29.39 | 0.0741 | 0.52 | 13.64 | 0
December | 26 | 9AM to 10AM | 75 | 65 | 59.7 | 76.8 | 30.02 | 0.0737 | 0.52 | 13.72 | 0
December | 26 | 10AM to 11AM | 78.1 | 65.6 | 59 | 74.9 | 30.46 | 0.0733 | 0.5 | 13.79 | 0
December | 26 | 11AM to 12PM | 78.1 | 66.1 | 59.9 | 77.3 | 30.84 | 0.0733 | 0.52 | 13.8 | 0
December | 26 | 12PM to 1PM | 78.1 | 66.3 | 60.3 | 78.4 | 31 | 0.0733 | 0.53 | 13.8 | 0
December | 26 | 1PM to 2PM | 78.1 | 66.2 | 60.1 | 77.8 | 30.92 | 0.0733 | 0.52 | 13.8 | 0
December | 26 | 2PM to 3PM | 77.4 | 66 | 60.1 | 77.8 | 30.75 | 0.0734 | 0.52 | 13.78 | 0
December | 26 | 3PM to 4PM | 76.6 | 65.7 | 59.9 | 77.3 | 30.49 | 0.0735 | 0.52 | 13.76 | 0
December | 26 | 4PM to 5PM | 75.9 | 64.9 | 59 | 74.9 | 29.93 | 0.0736 | 0.5 | 13.73 | 0
December | 26 | 5PM to 6PM | 74.3 | 65.5 | 61 | 80.4 | 30.4 | 0.0738 | 0.54 | 13.71 | 0
December | 26 | 6PM to 7PM | 72.7 | 66.1 | 62.8 | 85.8 | 30.85 | 0.074 | 0.58 | 13.68 | 0
December | 26 | 7PM to 8PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
December | 26 | 8PM to 9PM | 70.7 | 66.6 | 64.6 | 91.5 | 31.25 | 0.0742 | 0.61 | 13.65 | 0
December | 26 | 9PM to 10PM | 70.3 | 66.7 | 64.9 | 92.7 | 31.35 | 0.0743 | 0.62 | 13.64 | 0
December | 26 | 10PM to 11PM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
December | 26 | 11PM to 12AM | 70 | 66.3 | 64.6 | 91.5 | 31.07 | 0.0743 | 0.61 | 13.63 | 0
December | 27 | 12AM to 1AM | 70 | 65.9 | 63.9 | 89.2 | 30.71 | 0.0743 | 0.6 | 13.62 | 0
December | 27 | 1AM to 2AM | 70 | 65.3 | 63 | 86.4 | 30.27 | 0.0744 | 0.58 | 13.61 | 0
December | 27 | 2AM to 3AM | 71.1 | 66.2 | 63.9 | 89.2 | 30.98 | 0.0742 | 0.6 | 13.65 | 0
December | 27 | 3AM to 4AM | 72 | 67 | 64.6 | 91.5 | 31.56 | 0.074 | 0.61 | 13.68 | 0
December | 27 | 4AM to 5AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
December | 27 | 5AM to 6AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
December | 27 | 6AM to 7AM | 73 | 67.3 | 64.6 | 91.5 | 31.83 | 0.0739 | 0.61 | 13.71 | 0
December | 27 | 7AM to 8AM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
December | 27 | 8AM to 9AM | 74.3 | 67.9 | 64.9 | 92.7 | 32.32 | 0.0737 | 0.62 | 13.75 | 0
December | 27 | 9AM to 10AM | 75.7 | 67.6 | 63.7 | 88.6 | 32.04 | 0.0735 | 0.59 | 13.77 | 0
December | 27 | 10AM to 11AM | 77 | 67 | 62.1 | 83.6 | 31.56 | 0.0734 | 0.56 | 13.79 | 0
December | 27 | 11AM to 12PM | 76.6 | 66.8 | 61.9 | 83.1 | 31.39 | 0.0735 | 0.56 | 13.78 | 0
December | 27 | 12PM to 1PM | 76.3 | 66.3 | 61.2 | 80.9 | 30.97 | 0.0735 | 0.54 | 13.76 | 0
December | 27 | 1PM to 2PM | 75.9 | 65.5 | 60.1 | 77.8 | 30.39 | 0.0736 | 0.52 | 13.74 | 0
December | 27 | 2PM to 3PM | 76.3 | 67 | 62.4 | 84.7 | 31.56 | 0.0735 | 0.57 | 13.77 | 0
December | 27 | 3PM to 4PM | 76.6 | 68.4 | 64.6 | 91.5 | 32.71 | 0.0734 | 0.61 | 13.8 | 0
December | 27 | 4PM to 5PM | 77 | 69.4 | 66 | 96.3 | 33.55 | 0.0733 | 0.64 | 13.83 | 0
December | 27 | 5PM to 6PM | 76.6 | 69.6 | 66.4 | 97.6 | 33.66 | 0.0734 | 0.65 | 13.82 | 0
December | 27 | 6PM to 7PM | 76.3 | 69.5 | 66.4 | 97.6 | 33.57 | 0.0734 | 0.65 | 13.81 | 0
December | 27 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
December | 27 | 8PM to 9PM | 75.9 | 69 | 65.8 | 95.7 | 33.19 | 0.0735 | 0.64 | 13.8 | 0
December | 27 | 9PM to 10PM | 75.9 | 68.8 | 65.5 | 94.5 | 33 | 0.0735 | 0.63 | 13.79 | 0
December | 27 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 92.7 | 32.72 | 0.0735 | 0.62 | 13.79 | 0
December | 27 | 11PM to 12AM | 75 | 68.2 | 64.9 | 92.7 | 32.5 | 0.0736 | 0.62 | 13.76 | 0
December | 28 | 12AM to 1AM | 73.9 | 67.6 | 64.6 | 91.5 | 32.05 | 0.0738 | 0.61 | 13.73 | 0
December | 28 | 1AM to 2AM | 73 | 67 | 64 | 89.8 | 31.55 | 0.0739 | 0.6 | 13.7 | 0
December | 28 | 2AM to 3AM | 72.3 | 66.9 | 64.2 | 90.4 | 31.47 | 0.074 | 0.61 | 13.69 | 0
December | 28 | 3AM to 4AM | 71.8 | 66.7 | 64.2 | 90.4 | 31.33 | 0.0741 | 0.61 | 13.67 | 0
December | 28 | 4AM to 5AM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
December | 28 | 5AM to 6AM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
December | 28 | 6AM to 7AM | 73 | 68 | 65.7 | 95.1 | 32.39 | 0.0739 | 0.64 | 13.72 | 0
December | 28 | 7AM to 8AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
December | 28 | 8AM to 9AM | 75.9 | 70.3 | 67.8 | 102.7 | 34.28 | 0.0734 | 0.69 | 13.82 | 0
December | 28 | 9AM to 10AM | 78.1 | 70.8 | 67.6 | 102 | 34.71 | 0.0731 | 0.68 | 13.87 | 0
December | 28 | 10AM to 11AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
December | 28 | 11AM to 12PM | 80.4 | 71.4 | 67.5 | 101.4 | 35.18 | 0.0728 | 0.68 | 13.93 | 0
December | 28 | 12PM to 1PM | 80.6 | 71.4 | 67.5 | 101.4 | 35.23 | 0.0728 | 0.68 | 13.93 | 0
December | 28 | 1PM to 2PM | 81 | 71.2 | 66.9 | 99.5 | 35.01 | 0.0728 | 0.67 | 13.94 | 0
December | 28 | 2PM to 3PM | 80.2 | 71.1 | 67.1 | 100.1 | 34.94 | 0.0729 | 0.67 | 13.92 | 0
December | 28 | 3PM to 4PM | 79.7 | 70.7 | 66.7 | 98.8 | 34.61 | 0.0729 | 0.66 | 13.9 | 0
December | 28 | 4PM to 5PM | 79 | 70 | 66 | 96.3 | 34.04 | 0.0731 | 0.64 | 13.88 | 0
December | 28 | 5PM to 6PM | 77 | 69.7 | 66.4 | 97.6 | 33.74 | 0.0733 | 0.65 | 13.83 | 0
December | 28 | 6PM to 7PM | 75 | 69.1 | 66.4 | 97.6 | 33.26 | 0.0736 | 0.65 | 13.78 | 0
December | 28 | 7PM to 8PM | 73 | 68.2 | 66 | 96.3 | 32.58 | 0.0739 | 0.64 | 13.72 | 0
December | 28 | 8PM to 9PM | 72 | 67.8 | 65.8 | 95.7 | 32.22 | 0.074 | 0.64 | 13.69 | 0
December | 28 | 9PM to 10PM | 71.1 | 67.3 | 65.5 | 94.5 | 31.8 | 0.0742 | 0.63 | 13.67 | 0
December | 28 | 10PM to 11PM | 70 | 66.6 | 64.9 | 92.7 | 31.26 | 0.0743 | 0.62 | 13.63 | 0
December | 28 | 11PM to 12AM | 69.3 | 66.5 | 65.1 | 93.3 | 31.17 | 0.0744 | 0.63 | 13.62 | 0
December | 29 | 12AM to 1AM | 68.7 | 66.3 | 65.1 | 93.3 | 31.04 | 0.0745 | 0.63 | 13.6 | 0
December | 29 | 1AM to 2AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
December | 29 | 2AM to 3AM | 67.6 | 65.9 | 65.1 | 93.3 | 30.77 | 0.0746 | 0.63 | 13.58 | 0
December | 29 | 3AM to 4AM | 67.3 | 65.8 | 65.1 | 93.3 | 30.69 | 0.0747 | 0.63 | 13.57 | 0
December | 29 | 4AM to 5AM | 66.9 | 65.6 | 64.9 | 92.7 | 30.51 | 0.0747 | 0.62 | 13.56 | 0
December | 29 | 5AM to 6AM | 66.9 | 65.6 | 64.9 | 92.7 | 30.51 | 0.0747 | 0.62 | 13.56 | 0
December | 29 | 6AM to 7AM | 66.9 | 65.4 | 64.6 | 91.5 | 30.32 | 0.0748 | 0.61 | 13.55 | 0
December | 29 | 7AM to 8AM | 66.9 | 65.6 | 64.9 | 92.7 | 30.51 | 0.0747 | 0.62 | 13.56 | 0
December | 29 | 8AM to 9AM | 71.2 | 68 | 66.6 | 98.2 | 32.42 | 0.0741 | 0.66 | 13.68 | 0
December | 29 | 9AM to 10AM | 75.7 | 69.6 | 66.9 | 99.5 | 33.73 | 0.0735 | 0.67 | 13.8 | 0
December | 29 | 10AM to 11AM | 80.1 | 70.9 | 66.9 | 99.5 | 34.79 | 0.0729 | 0.67 | 13.91 | 0
December | 29 | 11AM to 12PM | 79.7 | 71.1 | 67.5 | 101.4 | 35 | 0.0729 | 0.68 | 13.91 | 0
December | 29 | 12PM to 1PM | 79.3 | 71 | 67.5 | 101.4 | 34.92 | 0.073 | 0.68 | 13.9 | 0
December | 29 | 1PM to 2PM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
December | 29 | 2PM to 3PM | 78.6 | 71.2 | 68 | 103.3 | 35.04 | 0.0731 | 0.69 | 13.89 | 0
December | 29 | 3PM to 4PM | 78.4 | 71.7 | 68.9 | 106.6 | 35.52 | 0.0731 | 0.71 | 13.9 | 0
December | 29 | 4PM to 5PM | 78.1 | 71.7 | 69.1 | 107.3 | 35.54 | 0.0731 | 0.72 | 13.89 | 0
December | 29 | 5PM to 6PM | 77.4 | 71.1 | 68.4 | 104.6 | 34.94 | 0.0732 | 0.7 | 13.86 | 0
December | 29 | 6PM to 7PM | 76.6 | 70.3 | 67.5 | 101.4 | 34.25 | 0.0733 | 0.68 | 13.83 | 0
December | 29 | 7PM to 8PM | 75.9 | 69.1 | 66 | 96.3 | 33.29 | 0.0735 | 0.64 | 13.8 | 0
December | 29 | 8PM to 9PM | 75 | 68.7 | 65.8 | 95.7 | 32.97 | 0.0736 | 0.64 | 13.77 | 0
December | 29 | 9PM to 10PM | 73.9 | 68.2 | 65.5 | 94.5 | 32.51 | 0.0738 | 0.63 | 13.74 | 0
December | 29 | 10PM to 11PM | 73 | 67.5 | 64.9 | 92.7 | 32.01 | 0.0739 | 0.62 | 13.71 | 0
December | 29 | 11PM to 12AM | 71.4 | 67 | 64.9 | 92.7 | 31.61 | 0.0741 | 0.62 | 13.67 | 0
December | 30 | 12AM to 1AM | 69.6 | 66.2 | 64.6 | 91.5 | 30.98 | 0.0744 | 0.61 | 13.62 | 0
December | 30 | 1AM to 2AM | 68 | 65.4 | 64 | 89.8 | 30.31 | 0.0746 | 0.6 | 13.57 | 0
December | 30 | 2AM to 3AM | 67.6 | 65.4 | 64.2 | 90.4 | 30.32 | 0.0747 | 0.61 | 13.57 | 0
December | 30 | 3AM to 4AM | 67.3 | 65.2 | 64.2 | 90.4 | 30.23 | 0.0747 | 0.61 | 13.56 | 0
December | 30 | 4AM to 5AM | 66.9 | 65 | 64 | 89.8 | 30.05 | 0.0748 | 0.6 | 13.55 | 0
December | 30 | 5AM to 6AM | 67.3 | 65.2 | 64.2 | 90.4 | 30.23 | 0.0747 | 0.61 | 13.56 | 0
December | 30 | 6AM to 7AM | 67.6 | 65.4 | 64.2 | 90.4 | 30.32 | 0.0747 | 0.61 | 13.57 | 0
December | 30 | 7AM to 8AM | 68 | 65.9 | 64.9 | 92.7 | 30.77 | 0.0746 | 0.62 | 13.58 | 0
December | 30 | 8AM to 9AM | 71.6 | 68.1 | 66.6 | 98.2 | 32.51 | 0.0741 | 0.66 | 13.69 | 0
December | 30 | 9AM to 10AM | 75.4 | 69.5 | 66.9 | 99.5 | 33.64 | 0.0735 | 0.67 | 13.79 | 0
December | 30 | 10AM to 11AM | 79 | 70.6 | 66.9 | 99.5 | 34.53 | 0.073 | 0.67 | 13.89 | 0
December | 30 | 11AM to 12PM | 79.3 | 71.3 | 67.8 | 102.7 | 35.12 | 0.073 | 0.69 | 13.91 | 0
December | 30 | 12PM to 1PM | 79.7 | 71.6 | 68.2 | 104 | 35.41 | 0.0729 | 0.69 | 13.92 | 0
December | 30 | 1PM to 2PM | 80.1 | 71.6 | 68 | 103.3 | 35.4 | 0.0729 | 0.69 | 13.93 | 0
December | 30 | 2PM to 3PM | 79.3 | 71.4 | 68 | 103.3 | 35.22 | 0.073 | 0.69 | 13.91 | 0
December | 30 | 3PM to 4PM | 78.8 | 71.1 | 67.8 | 102.7 | 34.99 | 0.073 | 0.69 | 13.89 | 0
December | 30 | 4PM to 5PM | 78.1 | 70.3 | 66.9 | 99.5 | 34.31 | 0.0732 | 0.67 | 13.86 | 0
December | 30 | 5PM to 6PM | 77 | 70.2 | 67.3 | 100.7 | 34.24 | 0.0733 | 0.67 | 13.84 | 0
December | 30 | 6PM to 7PM | 76.1 | 70 | 67.3 | 100.7 | 34.02 | 0.0734 | 0.67 | 13.82 | 0
December | 30 | 7PM to 8PM | 75 | 69.4 | 66.9 | 99.5 | 33.55 | 0.0736 | 0.67 | 13.78 | 0
December | 30 | 8PM to 9PM | 74.3 | 69.3 | 67.1 | 100.1 | 33.47 | 0.0737 | 0.67 | 13.77 | 0
December | 30 | 9PM to 10PM | 73.8 | 69.2 | 67.1 | 100.1 | 33.34 | 0.0737 | 0.67 | 13.75 | 0
December | 30 | 10PM to 11PM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
December | 30 | 11PM to 12AM | 73 | 68.9 | 67.1 | 100.1 | 33.16 | 0.0738 | 0.67 | 13.74 | 0
December | 31 | 12AM to 1AM | 73 | 68.9 | 67.1 | 100.1 | 33.16 | 0.0738 | 0.67 | 13.74 | 0
December | 31 | 1AM to 2AM | 73 | 68.8 | 66.9 | 99.5 | 33.06 | 0.0738 | 0.67 | 13.73 | 0
December | 31 | 2AM to 3AM | 72 | 68.9 | 67.5 | 101.4 | 33.1 | 0.074 | 0.68 | 13.71 | 0
December | 31 | 3AM to 4AM | 71.1 | 68.8 | 67.8 | 102.7 | 33.08 | 0.0741 | 0.69 | 13.69 | 0
December | 31 | 4AM to 5AM | 70 | 68.6 | 68 | 103.3 | 32.91 | 0.0742 | 0.69 | 13.67 | 0
December | 31 | 5AM to 6AM | 70 | 68.4 | 67.6 | 102 | 32.71 | 0.0743 | 0.68 | 13.66 | 0
December | 31 | 6AM to 7AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
December | 31 | 7AM to 8AM | 70 | 67.9 | 66.9 | 99.5 | 32.31 | 0.0743 | 0.67 | 13.66 | 0
December | 31 | 8AM to 9AM | 71.2 | 68.9 | 67.8 | 102.7 | 33.12 | 0.0741 | 0.69 | 13.7 | 0
December | 31 | 9AM to 10AM | 72.7 | 69.2 | 67.6 | 102 | 33.38 | 0.0739 | 0.68 | 13.73 | 0
December | 31 | 10AM to 11AM | 73.9 | 69.1 | 66.9 | 99.5 | 33.29 | 0.0737 | 0.67 | 13.76 | 0
December | 31 | 11AM to 12PM | 75.4 | 69.6 | 67.1 | 100.1 | 33.74 | 0.0735 | 0.67 | 13.8 | 0
December | 31 | 12PM to 1PM | 76.6 | 69.8 | 66.7 | 98.8 | 33.85 | 0.0734 | 0.66 | 13.82 | 0
December | 31 | 1PM to 2PM | 78.1 | 69.8 | 66 | 96.3 | 33.82 | 0.0732 | 0.64 | 13.85 | 0
December | 31 | 2PM to 3PM | 76.1 | 69.2 | 66 | 96.3 | 33.33 | 0.0734 | 0.64 | 13.8 | 0
December | 31 | 3PM to 4PM | 73.9 | 68.4 | 65.8 | 95.7 | 32.7 | 0.0737 | 0.64 | 13.75 | 0
December | 31 | 4PM to 5PM | 72 | 67.2 | 64.9 | 92.7 | 31.74 | 0.074 | 0.62 | 13.69 | 0
December | 31 | 5PM to 6PM | 71.2 | 67.4 | 65.7 | 95.1 | 31.94 | 0.0741 | 0.64 | 13.67 | 0
December | 31 | 6PM to 7PM | 70.7 | 67.5 | 66 | 96.3 | 32 | 0.0742 | 0.64 | 13.66 | 0
December | 31 | 7PM to 8PM | 70 | 67.3 | 66 | 96.3 | 31.82 | 0.0743 | 0.64 | 13.65 | 0
December | 31 | 8PM to 9PM | 70.3 | 67.2 | 65.7 | 95.1 | 31.72 | 0.0742 | 0.64 | 13.65 | 0
December | 31 | 9PM to 10PM | 70.7 | 66.8 | 64.9 | 92.7 | 31.43 | 0.0742 | 0.62 | 13.65 | 0
December | 31 | 10PM to 11PM | 71.1 | 66.3 | 64 | 89.8 | 31.07 | 0.0742 | 0.6 | 13.65 | 0
December | 31 | 11PM to 12AM | 72 | 67.9 | 66 | 96.3 | 32.31 | 0.074 | 0.64 | 13.7 | 0

## St. Louis MO TMY3 Weather
Country: USA | [7 empty] | OAT Flag Trigger Set Point - | 52 | °F
State: MISSOURI | [8 empty] | Back to HOA kW and kWh Saving tab
City: ST_LOUIS_LAMBERT_INT'L_ARPT | [8 empty] | Back to Optimized kW and kWh Savings tab
Altitude: 567 ft. | [9 empty] | Number of hours less than 52.0°F in the data set - | 3617
Month | Day | Hour | Dry Bulb | Wet Bulb | Dew Point | Humidity Ratio | Enthalpy | Density | Vapor Pressure | Specific Volume | 1 if the OAT is less than 52.0°F
|  |  | °F | °F | °F | gr/lb | btu/lb | lb/cu.ft. | in. HG | cu.ft./lb
January | 1 | 12AM to 1AM | 23 | 20.1 | 14 | 11.5 | 7.28 | 0.0805 | 0.08 | 12.45 | 1
January | 1 | 1AM to 2AM | 21.9 | 19.4 | 14 | 11.5 | 7.02 | 0.0806 | 0.08 | 12.42 | 1
January | 1 | 2AM to 3AM | 21 | 18.8 | 14 | 11.5 | 6.8 | 0.0808 | 0.08 | 12.4 | 1
January | 1 | 3AM to 4AM | 21 | 18.5 | 12.9 | 10.9 | 6.71 | 0.0808 | 0.07 | 12.4 | 1
January | 1 | 4AM to 5AM | 19 | 17 | 12 | 10.4 | 6.16 | 0.0811 | 0.07 | 12.34 | 1
January | 1 | 5AM to 6AM | 18 | 15.7 | 10 | 9.4 | 5.75 | 0.0813 | 0.06 | 12.31 | 1
January | 1 | 6AM to 7AM | 16 | 14.3 | 10 | 9.4 | 5.27 | 0.0817 | 0.06 | 12.26 | 1
January | 1 | 7AM to 8AM | 16 | 14.1 | 9 | 8.9 | 5.2 | 0.0817 | 0.06 | 12.26 | 1
January | 1 | 8AM to 9AM | 18 | 15.5 | 9 | 8.9 | 5.68 | 0.0813 | 0.06 | 12.31 | 1
January | 1 | 9AM to 10AM | 19.9 | 16.8 | 9 | 8.9 | 6.15 | 0.081 | 0.06 | 12.36 | 1
January | 1 | 10AM to 11AM | 21 | 17.4 | 8.1 | 8.5 | 6.35 | 0.0808 | 0.06 | 12.39 | 1
January | 1 | 11AM to 12PM | 23 | 18.5 | 7 | 8.1 | 6.76 | 0.0805 | 0.05 | 12.44 | 1
January | 1 | 12PM to 1PM | 25 | 19.8 | 7 | 8.1 | 7.23 | 0.0802 | 0.05 | 12.49 | 1
January | 1 | 1PM to 2PM | 26.1 | 20.1 | 5 | 7.3 | 7.37 | 0.08 | 0.05 | 12.52 | 1
January | 1 | 2PM to 3PM | 27 | 20.7 | 5 | 7.3 | 7.59 | 0.0798 | 0.05 | 12.54 | 1
January | 1 | 3PM to 4PM | 26.1 | 19.9 | 3.9 | 6.9 | 7.31 | 0.08 | 0.05 | 12.51 | 1
January | 1 | 4PM to 5PM | 24.1 | 18.5 | 3 | 6.6 | 6.79 | 0.0803 | 0.04 | 12.46 | 1
January | 1 | 5PM to 6PM | 21.9 | 17.4 | 5 | 7.3 | 6.38 | 0.0807 | 0.05 | 12.41 | 1
January | 1 | 6PM to 7PM | 21 | 16.8 | 5 | 7.3 | 6.16 | 0.0808 | 0.05 | 12.39 | 1
January | 1 | 7PM to 8PM | 19.9 | 16 | 5 | 7.3 | 5.9 | 0.081 | 0.05 | 12.36 | 1
January | 1 | 8PM to 9PM | 19.9 | 16.2 | 6.1 | 7.7 | 5.97 | 0.081 | 0.05 | 12.36 | 1
January | 1 | 9PM to 10PM | 19.9 | 16.2 | 6.1 | 7.7 | 5.97 | 0.081 | 0.05 | 12.36 | 1
January | 1 | 10PM to 11PM | 19 | 15.6 | 6.1 | 7.7 | 5.75 | 0.0812 | 0.05 | 12.34 | 1
January | 1 | 11PM to 12AM | 16 | 14.1 | 9 | 8.9 | 5.2 | 0.0817 | 0.06 | 12.26 | 1
January | 2 | 12AM to 1AM | 16 | 14.1 | 9 | 8.9 | 5.2 | 0.0817 | 0.06 | 12.26 | 1
January | 2 | 1AM to 2AM | 18 | 15.5 | 9 | 8.9 | 5.68 | 0.0813 | 0.06 | 12.31 | 1
January | 2 | 2AM to 3AM | 18 | 15.3 | 8.1 | 8.5 | 5.61 | 0.0813 | 0.06 | 12.31 | 1
January | 2 | 3AM to 4AM | 17.1 | 14.6 | 8.1 | 8.5 | 5.4 | 0.0815 | 0.06 | 12.29 | 1
January | 2 | 4AM to 5AM | 17.1 | 14.4 | 7 | 8.1 | 5.33 | 0.0815 | 0.05 | 12.29 | 1
January | 2 | 5AM to 6AM | 18 | 15 | 7 | 8.1 | 5.55 | 0.0813 | 0.05 | 12.31 | 1
January | 2 | 6AM to 7AM | 17.1 | 14.4 | 7 | 8.1 | 5.33 | 0.0815 | 0.05 | 12.29 | 1
January | 2 | 7AM to 8AM | 16 | 13.6 | 7 | 8.1 | 5.07 | 0.0817 | 0.05 | 12.26 | 1
January | 2 | 8AM to 9AM | 19.9 | 16.8 | 9 | 8.9 | 6.15 | 0.081 | 0.06 | 12.36 | 1
January | 2 | 9AM to 10AM | 24.1 | 19.4 | 8.1 | 8.5 | 7.09 | 0.0803 | 0.06 | 12.47 | 1
January | 2 | 10AM to 11AM | 27 | 21.7 | 10 | 9.4 | 7.92 | 0.0798 | 0.06 | 12.54 | 1
January | 2 | 11AM to 12PM | 28.9 | 22.7 | 9 | 8.9 | 8.32 | 0.0795 | 0.06 | 12.59 | 1
January | 2 | 12PM to 1PM | 32 | 24.4 | 8.1 | 8.5 | 8.99 | 0.079 | 0.06 | 12.67 | 1
January | 2 | 1PM to 2PM | 33.1 | 24.9 | 7 | 8.1 | 9.18 | 0.0788 | 0.05 | 12.7 | 1
January | 2 | 2PM to 3PM | 34 | 25.4 | 7 | 8.1 | 9.4 | 0.0787 | 0.05 | 12.72 | 1
January | 2 | 3PM to 4PM | 34 | 25.2 | 6.1 | 7.7 | 9.34 | 0.0787 | 0.05 | 12.72 | 1
January | 2 | 4PM to 5PM | 32 | 23.9 | 5 | 7.3 | 8.8 | 0.079 | 0.05 | 12.67 | 1
January | 2 | 5PM to 6PM | 30.9 | 23.4 | 6.1 | 7.7 | 8.61 | 0.0792 | 0.05 | 12.64 | 1
January | 2 | 6PM to 7PM | 30 | 23.4 | 9 | 8.9 | 8.58 | 0.0793 | 0.06 | 12.62 | 1
January | 2 | 7PM to 8PM | 28.9 | 22.7 | 9 | 8.9 | 8.32 | 0.0795 | 0.06 | 12.59 | 1
January | 2 | 8PM to 9PM | 28 | 22.6 | 10.9 | 9.9 | 8.24 | 0.0796 | 0.07 | 12.57 | 1
January | 2 | 9PM to 10PM | 27 | 22.1 | 12 | 10.4 | 8.07 | 0.0798 | 0.07 | 12.55 | 1
January | 2 | 10PM to 11PM | 26.1 | 21.6 | 12 | 10.4 | 7.85 | 0.08 | 0.07 | 12.52 | 1
January | 2 | 11PM to 12AM | 25 | 20.6 | 10.9 | 9.9 | 7.51 | 0.0801 | 0.07 | 12.5 | 1
January | 3 | 12AM to 1AM | 24.1 | 19.8 | 10 | 9.4 | 7.22 | 0.0803 | 0.06 | 12.47 | 1
January | 3 | 1AM to 2AM | 24.1 | 19.4 | 8.1 | 8.5 | 7.09 | 0.0803 | 0.06 | 12.47 | 1
January | 3 | 2AM to 3AM | 23 | 18.9 | 9 | 8.9 | 6.89 | 0.0805 | 0.06 | 12.44 | 1
January | 3 | 3AM to 4AM | 23 | 19.1 | 10 | 9.4 | 6.96 | 0.0805 | 0.06 | 12.44 | 1
January | 3 | 4AM to 5AM | 24.1 | 20 | 10.9 | 9.9 | 7.29 | 0.0803 | 0.07 | 12.47 | 1
January | 3 | 5AM to 6AM | 24.1 | 20.3 | 12 | 10.4 | 7.37 | 0.0803 | 0.07 | 12.47 | 1
January | 3 | 6AM to 7AM | 24.1 | 20.5 | 12.9 | 10.9 | 7.45 | 0.0803 | 0.07 | 12.47 | 1
January | 3 | 7AM to 8AM | 25 | 21.1 | 12.9 | 10.9 | 7.66 | 0.0801 | 0.07 | 12.5 | 1
January | 3 | 8AM to 9AM | 27 | 22.4 | 12.9 | 10.9 | 8.14 | 0.0798 | 0.07 | 12.55 | 1
January | 3 | 9AM to 10AM | 28.9 | 23.4 | 12 | 10.4 | 8.54 | 0.0795 | 0.07 | 12.6 | 1
January | 3 | 10AM to 11AM | 33.1 | 26.3 | 14 | 11.5 | 9.71 | 0.0788 | 0.08 | 12.71 | 1
January | 3 | 11AM to 12PM | 34 | 26.8 | 14 | 11.5 | 9.92 | 0.0787 | 0.08 | 12.73 | 1
January | 3 | 12PM to 1PM | 36 | 28.2 | 15.1 | 12.1 | 10.5 | 0.0784 | 0.08 | 12.78 | 1
January | 3 | 1PM to 2PM | 37.9 | 30.9 | 21 | 16.2 | 11.6 | 0.078 | 0.11 | 12.85 | 1
January | 3 | 2PM to 3PM | 37.9 | 30.9 | 21 | 16.2 | 11.6 | 0.078 | 0.11 | 12.85 | 1
January | 3 | 3PM to 4PM | 37 | 32.5 | 26.1 | 20.5 | 12.05 | 0.0781 | 0.14 | 12.84 | 1
January | 3 | 4PM to 5PM | 36 | 32.6 | 28 | 22.5 | 12.1 | 0.0783 | 0.15 | 12.82 | 1
January | 3 | 5PM to 6PM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
January | 3 | 6PM to 7PM | 33.1 | 32.1 | 30.9 | 25.8 | 11.9 | 0.0787 | 0.17 | 12.75 | 1
January | 3 | 7PM to 8PM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
January | 3 | 8PM to 9PM | 33.1 | 32.1 | 30.9 | 25.8 | 11.9 | 0.0787 | 0.17 | 12.75 | 1
January | 3 | 9PM to 10PM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
January | 3 | 10PM to 11PM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
January | 3 | 11PM to 12AM | 28 | 24.7 | 19 | 14.7 | 8.98 | 0.0796 | 0.1 | 12.59 | 1
January | 4 | 12AM to 1AM | 25 | 22.5 | 18 | 13.9 | 8.13 | 0.0801 | 0.09 | 12.51 | 1
January | 4 | 1AM to 2AM | 23 | 21 | 17.1 | 13.3 | 7.56 | 0.0804 | 0.09 | 12.45 | 1
January | 4 | 2AM to 3AM | 23 | 21 | 17.1 | 13.3 | 7.56 | 0.0804 | 0.09 | 12.45 | 1
January | 4 | 3AM to 4AM | 19.9 | 18.4 | 15.1 | 12.1 | 6.64 | 0.081 | 0.08 | 12.37 | 1
January | 4 | 4AM to 5AM | 19 | 17.8 | 15.1 | 12.1 | 6.42 | 0.0811 | 0.08 | 12.35 | 1
January | 4 | 5AM to 6AM | 21 | 19.1 | 15.1 | 12.1 | 6.9 | 0.0808 | 0.08 | 12.4 | 1
January | 4 | 6AM to 7AM | 19.9 | 17.8 | 12.9 | 10.9 | 6.45 | 0.081 | 0.07 | 12.37 | 1
January | 4 | 7AM to 8AM | 19.9 | 17.1 | 10 | 9.4 | 6.23 | 0.081 | 0.06 | 12.36 | 1
January | 4 | 8AM to 9AM | 23 | 18.7 | 8.1 | 8.5 | 6.83 | 0.0805 | 0.06 | 12.44 | 1
January | 4 | 9AM to 10AM | 25 | 19.6 | 6.1 | 7.7 | 7.18 | 0.0802 | 0.05 | 12.49 | 1
January | 4 | 10AM to 11AM | 27 | 20.7 | 5 | 7.3 | 7.59 | 0.0798 | 0.05 | 12.54 | 1
January | 4 | 11AM to 12PM | 28 | 21.2 | 3.9 | 6.9 | 7.79 | 0.0797 | 0.05 | 12.57 | 1
January | 4 | 12PM to 1PM | 26.1 | 19.5 | 1 | 5.9 | 7.17 | 0.08 | 0.04 | 12.51 | 1
January | 4 | 1PM to 2PM | 24.1 | 18.2 | 1 | 5.9 | 6.69 | 0.0803 | 0.04 | 12.46 | 1
January | 4 | 2PM to 3PM | 21.9 | 16.2 | -2.9 | 4.8 | 6 | 0.0807 | 0.03 | 12.4 | 1
January | 4 | 3PM to 4PM | 19.9 | 14.8 | -2.9 | 4.8 | 5.53 | 0.081 | 0.03 | 12.35 | 1
January | 4 | 4PM to 5PM | 16 | 11.3 | -8 | 3.7 | 4.4 | 0.0817 | 0.02 | 12.25 | 1
January | 4 | 5PM to 6PM | 15.1 | 11 | -5.1 | 4.3 | 4.28 | 0.0819 | 0.03 | 12.22 | 1
January | 4 | 6PM to 7PM | 14 | 10.5 | -2.9 | 4.8 | 4.1 | 0.082 | 0.03 | 12.2 | 1
January | 4 | 7PM to 8PM | 12.9 | 9.4 | -5.1 | 4.3 | 3.76 | 0.0822 | 0.03 | 12.17 | 1
January | 4 | 8PM to 9PM | 12 | 8.6 | -6 | 4.1 | 3.51 | 0.0824 | 0.03 | 12.15 | 1
January | 4 | 9PM to 10PM | 10.9 | 7.7 | -7.1 | 3.9 | 3.22 | 0.0826 | 0.03 | 12.12 | 1
January | 4 | 10PM to 11PM | 10 | 7.1 | -6 | 4.1 | 3.04 | 0.0827 | 0.03 | 12.09 | 1
January | 4 | 11PM to 12AM | 10 | 7 | -7.1 | 3.9 | 3 | 0.0827 | 0.03 | 12.09 | 1
January | 5 | 12AM to 1AM | 9 | 6.1 | -7.1 | 3.9 | 2.74 | 0.0829 | 0.03 | 12.07 | 1
January | 5 | 1AM to 2AM | 8.1 | 5.4 | -7.1 | 3.9 | 2.52 | 0.0831 | 0.03 | 12.04 | 1
January | 5 | 2AM to 3AM | 8.1 | 5.4 | -7.1 | 3.9 | 2.52 | 0.0831 | 0.03 | 12.04 | 1
January | 5 | 3AM to 4AM | 7 | 4.6 | -7.1 | 3.9 | 2.26 | 0.0833 | 0.03 | 12.01 | 1
January | 5 | 4AM to 5AM | 6.1 | 3.9 | -7.1 | 3.9 | 2.05 | 0.0834 | 0.03 | 11.99 | 1
January | 5 | 5AM to 6AM | 6.1 | 3.9 | -7.1 | 3.9 | 2.05 | 0.0834 | 0.03 | 11.99 | 1
January | 5 | 6AM to 7AM | 6.1 | 3.9 | -7.1 | 3.9 | 2.05 | 0.0834 | 0.03 | 11.99 | 1
January | 5 | 7AM to 8AM | 6.1 | 3.9 | -7.1 | 3.9 | 2.05 | 0.0834 | 0.03 | 11.99 | 1
January | 5 | 8AM to 9AM | 7 | 4.5 | -8 | 3.7 | 2.24 | 0.0833 | 0.02 | 12.01 | 1
January | 5 | 9AM to 10AM | 8.1 | 5.7 | -5.1 | 4.3 | 2.59 | 0.0831 | 0.03 | 12.04 | 1
January | 5 | 10AM to 11AM | 10 | 7.1 | -6 | 4.1 | 3.04 | 0.0827 | 0.03 | 12.09 | 1
January | 5 | 11AM to 12PM | 10 | 7 | -7.1 | 3.9 | 3 | 0.0827 | 0.03 | 12.09 | 1
January | 5 | 12PM to 1PM | 10.9 | 7.8 | -6 | 4.1 | 3.25 | 0.0826 | 0.03 | 12.12 | 1
January | 5 | 1PM to 2PM | 12 | 8.6 | -6 | 4.1 | 3.51 | 0.0824 | 0.03 | 12.15 | 1
January | 5 | 2PM to 3PM | 14 | 10.2 | -5.1 | 4.3 | 4.02 | 0.082 | 0.03 | 12.2 | 1
January | 5 | 3PM to 4PM | 12.9 | 9.3 | -6 | 4.1 | 3.73 | 0.0822 | 0.03 | 12.17 | 1
January | 5 | 4PM to 5PM | 10.9 | 7.9 | -5.1 | 4.3 | 3.28 | 0.0826 | 0.03 | 12.12 | 1
January | 5 | 5PM to 6PM | 10.9 | 7.9 | -5.1 | 4.3 | 3.28 | 0.0826 | 0.03 | 12.12 | 1
January | 5 | 6PM to 7PM | 10 | 7.4 | -4 | 4.6 | 3.1 | 0.0827 | 0.03 | 12.1 | 1
January | 5 | 7PM to 8PM | 10.9 | 7.9 | -5.1 | 4.3 | 3.28 | 0.0826 | 0.03 | 12.12 | 1
January | 5 | 8PM to 9PM | 10 | 7.2 | -5.1 | 4.3 | 3.07 | 0.0827 | 0.03 | 12.09 | 1
January | 5 | 9PM to 10PM | 9 | 6.1 | -7.1 | 3.9 | 2.74 | 0.0829 | 0.03 | 12.07 | 1
January | 5 | 10PM to 11PM | 9 | 6.3 | -6 | 4.1 | 2.78 | 0.0829 | 0.03 | 12.07 | 1
January | 5 | 11PM to 12AM | 8.1 | 5.4 | -7.1 | 3.9 | 2.52 | 0.0831 | 0.03 | 12.04 | 1
January | 6 | 12AM to 1AM | 7 | 4.5 | -8 | 3.7 | 2.24 | 0.0833 | 0.02 | 12.01 | 1
January | 6 | 1AM to 2AM | 6.1 | 3.8 | -8 | 3.7 | 2.02 | 0.0834 | 0.02 | 11.99 | 1
January | 6 | 2AM to 3AM | 5 | 3.3 | -5.1 | 4.3 | 1.86 | 0.0836 | 0.03 | 11.96 | 1
January | 6 | 3AM to 4AM | 5 | 3.2 | -6 | 4.1 | 1.82 | 0.0836 | 0.03 | 11.96 | 1
January | 6 | 4AM to 5AM | 3.9 | 2.3 | -6 | 4.1 | 1.56 | 0.0838 | 0.03 | 11.94 | 1
January | 6 | 5AM to 6AM | 3 | 1.6 | -6 | 4.1 | 1.35 | 0.084 | 0.03 | 11.91 | 1
January | 6 | 6AM to 7AM | 1.9 | 0.8 | -5.1 | 4.3 | 1.12 | 0.0842 | 0.03 | 11.89 | 1
January | 6 | 7AM to 8AM | 1.9 | 0.5 | -7.1 | 3.9 | 1.05 | 0.0842 | 0.03 | 11.88 | 1
January | 6 | 8AM to 9AM | 3 | 1.2 | -9 | 3.5 | 1.25 | 0.084 | 0.02 | 11.91 | 1
January | 6 | 9AM to 10AM | 3.9 | 2.2 | -7.1 | 3.9 | 1.53 | 0.0838 | 0.03 | 11.94 | 1
January | 6 | 10AM to 11AM | 6.1 | 3.8 | -8 | 3.7 | 2.02 | 0.0834 | 0.02 | 11.99 | 1
January | 6 | 11AM to 12PM | 7 | 4.5 | -8 | 3.7 | 2.24 | 0.0833 | 0.02 | 12.01 | 1
January | 6 | 12PM to 1PM | 8.1 | 5.3 | -8 | 3.7 | 2.5 | 0.0831 | 0.02 | 12.04 | 1
January | 6 | 1PM to 2PM | 9 | 5.9 | -9 | 3.5 | 2.68 | 0.0829 | 0.02 | 12.06 | 1
January | 6 | 2PM to 3PM | 10 | 6.8 | -9 | 3.5 | 2.94 | 0.0827 | 0.02 | 12.09 | 1
January | 6 | 3PM to 4PM | 9 | 5.9 | -9 | 3.5 | 2.68 | 0.0829 | 0.02 | 12.06 | 1
January | 6 | 4PM to 5PM | 9 | 6.1 | -7.1 | 3.9 | 2.74 | 0.0829 | 0.03 | 12.07 | 1
January | 6 | 5PM to 6PM | 10 | 7 | -7.1 | 3.9 | 3 | 0.0827 | 0.03 | 12.09 | 1
January | 6 | 6PM to 7PM | 10 | 7 | -7.1 | 3.9 | 3 | 0.0827 | 0.03 | 12.09 | 1
January | 6 | 7PM to 8PM | 10 | 7.2 | -5.1 | 4.3 | 3.07 | 0.0827 | 0.03 | 12.09 | 1
January | 6 | 8PM to 9PM | 10 | 7.2 | -5.1 | 4.3 | 3.07 | 0.0827 | 0.03 | 12.09 | 1
January | 6 | 9PM to 10PM | 10.9 | 7.9 | -5.1 | 4.3 | 3.28 | 0.0826 | 0.03 | 12.12 | 1
January | 6 | 10PM to 11PM | 10.9 | 8.1 | -4 | 4.6 | 3.32 | 0.0826 | 0.03 | 12.12 | 1
January | 6 | 11PM to 12AM | 12 | 9 | -2.9 | 4.8 | 3.62 | 0.0824 | 0.03 | 12.15 | 1
January | 7 | 12AM to 1AM | 12 | 9.2 | -2 | 5.1 | 3.66 | 0.0824 | 0.03 | 12.15 | 1
January | 7 | 1AM to 2AM | 12 | 9.3 | -0.9 | 5.4 | 3.7 | 0.0824 | 0.04 | 12.15 | 1
January | 7 | 2AM to 3AM | 12 | 9.3 | -0.9 | 5.4 | 3.7 | 0.0824 | 0.04 | 12.15 | 1
January | 7 | 3AM to 4AM | 12 | 9.3 | -0.9 | 5.4 | 3.7 | 0.0824 | 0.04 | 12.15 | 1
January | 7 | 4AM to 5AM | 10.9 | 9.3 | 3.9 | 6.9 | 3.68 | 0.0826 | 0.05 | 12.13 | 1
January | 7 | 5AM to 6AM | 10 | 8.9 | 5 | 7.3 | 3.52 | 0.0827 | 0.05 | 12.1 | 1
January | 7 | 6AM to 7AM | 10.9 | 9.8 | 6.1 | 7.7 | 3.8 | 0.0825 | 0.05 | 12.13 | 1
January | 7 | 7AM to 8AM | 10.9 | 10 | 7 | 8.1 | 3.86 | 0.0825 | 0.05 | 12.13 | 1
January | 7 | 8AM to 9AM | 10.9 | 10.2 | 8.1 | 8.5 | 3.93 | 0.0825 | 0.06 | 12.13 | 1
January | 7 | 9AM to 10AM | 12 | 11 | 8.1 | 8.5 | 4.19 | 0.0824 | 0.06 | 12.16 | 1
January | 7 | 10AM to 11AM | 12.9 | 11.7 | 8.1 | 8.5 | 4.4 | 0.0822 | 0.06 | 12.18 | 1
January | 7 | 11AM to 12PM | 14 | 12.2 | 7 | 8.1 | 4.59 | 0.082 | 0.05 | 12.21 | 1
January | 7 | 12PM to 1PM | 16 | 13.9 | 8.1 | 8.5 | 5.14 | 0.0817 | 0.06 | 12.26 | 1
January | 7 | 1PM to 2PM | 17.1 | 14.8 | 9 | 8.9 | 5.46 | 0.0815 | 0.06 | 12.29 | 1
January | 7 | 2PM to 3PM | 17.1 | 14.6 | 8.1 | 8.5 | 5.4 | 0.0815 | 0.06 | 12.29 | 1
January | 7 | 3PM to 4PM | 16 | 13.9 | 8.1 | 8.5 | 5.14 | 0.0817 | 0.06 | 12.26 | 1
January | 7 | 4PM to 5PM | 16 | 13.6 | 7 | 8.1 | 5.07 | 0.0817 | 0.05 | 12.26 | 1
January | 7 | 5PM to 6PM | 14 | 12.5 | 8.1 | 8.5 | 4.66 | 0.082 | 0.06 | 12.21 | 1
January | 7 | 6PM to 7PM | 12.9 | 11.2 | 6.1 | 7.7 | 4.28 | 0.0822 | 0.05 | 12.18 | 1
January | 7 | 7PM to 8PM | 10 | 8.9 | 5 | 7.3 | 3.52 | 0.0827 | 0.05 | 12.1 | 1
January | 7 | 8PM to 9PM | 10 | 9.1 | 6.1 | 7.7 | 3.59 | 0.0827 | 0.05 | 12.1 | 1
January | 7 | 9PM to 10PM | 9 | 8.3 | 6.1 | 7.7 | 3.33 | 0.0829 | 0.05 | 12.08 | 1
January | 7 | 10PM to 11PM | 7 | 6.3 | 3.9 | 6.9 | 2.73 | 0.0833 | 0.05 | 12.02 | 1
January | 7 | 11PM to 12AM | 8.1 | 7.4 | 5 | 7.3 | 3.05 | 0.0831 | 0.05 | 12.05 | 1
January | 8 | 12AM to 1AM | 7 | 6.5 | 5 | 7.3 | 2.79 | 0.0833 | 0.05 | 12.02 | 1
January | 8 | 1AM to 2AM | 5 | 4.6 | 3 | 6.6 | 2.2 | 0.0836 | 0.04 | 11.97 | 1
January | 8 | 2AM to 3AM | 6.1 | 5.4 | 3 | 6.6 | 2.46 | 0.0834 | 0.04 | 12 | 1
January | 8 | 3AM to 4AM | 3.9 | 3.5 | 1.9 | 6.2 | 1.89 | 0.0838 | 0.04 | 11.94 | 1
January | 8 | 4AM to 5AM | 5 | 4.4 | 1.9 | 6.2 | 2.15 | 0.0836 | 0.04 | 11.97 | 1
January | 8 | 5AM to 6AM | 3.9 | 3.4 | 1 | 5.9 | 1.85 | 0.0838 | 0.04 | 11.94 | 1
January | 8 | 6AM to 7AM | 3.9 | 3.5 | 1.9 | 6.2 | 1.89 | 0.0838 | 0.04 | 11.94 | 1
January | 8 | 7AM to 8AM | 5 | 4.4 | 1.9 | 6.2 | 2.15 | 0.0836 | 0.04 | 11.97 | 1
January | 8 | 8AM to 9AM | 9 | 8.5 | 7 | 8.1 | 3.38 | 0.0829 | 0.05 | 12.08 | 1
January | 8 | 9AM to 10AM | 12 | 11.5 | 10 | 9.4 | 4.32 | 0.0823 | 0.06 | 12.16 | 1
January | 8 | 10AM to 11AM | 16 | 14.6 | 10.9 | 9.9 | 5.34 | 0.0817 | 0.07 | 12.26 | 1
January | 8 | 11AM to 12PM | 19 | 17 | 12 | 10.4 | 6.16 | 0.0811 | 0.07 | 12.34 | 1
January | 8 | 12PM to 1PM | 19.9 | 17.6 | 12 | 10.4 | 6.38 | 0.081 | 0.07 | 12.37 | 1
January | 8 | 1PM to 2PM | 21 | 18 | 10.9 | 9.9 | 6.55 | 0.0808 | 0.07 | 12.39 | 1
January | 8 | 2PM to 3PM | 21.9 | 18.9 | 12 | 10.4 | 6.85 | 0.0806 | 0.07 | 12.42 | 1
January | 8 | 3PM to 4PM | 21.9 | 18.9 | 12 | 10.4 | 6.85 | 0.0806 | 0.07 | 12.42 | 1
January | 8 | 4PM to 5PM | 19 | 16.7 | 10.9 | 9.9 | 6.08 | 0.0811 | 0.07 | 12.34 | 1
January | 8 | 5PM to 6PM | 19.9 | 17.3 | 10.9 | 9.9 | 6.29 | 0.081 | 0.07 | 12.37 | 1
January | 8 | 6PM to 7PM | 17.1 | 15.1 | 10 | 9.4 | 5.53 | 0.0815 | 0.06 | 12.29 | 1
January | 8 | 7PM to 8PM | 21 | 18.3 | 12 | 10.4 | 6.64 | 0.0808 | 0.07 | 12.39 | 1
January | 8 | 8PM to 9PM | 21 | 18.5 | 12.9 | 10.9 | 6.71 | 0.0808 | 0.07 | 12.4 | 1
January | 8 | 9PM to 10PM | 19.9 | 17.6 | 12 | 10.4 | 6.38 | 0.081 | 0.07 | 12.37 | 1
January | 8 | 10PM to 11PM | 19 | 17 | 12 | 10.4 | 6.16 | 0.0811 | 0.07 | 12.34 | 1
January | 8 | 11PM to 12AM | 16 | 13.9 | 8.1 | 8.5 | 5.14 | 0.0817 | 0.06 | 12.26 | 1
January | 9 | 12AM to 1AM | 14 | 11.8 | 5 | 7.3 | 4.47 | 0.082 | 0.05 | 12.2 | 1
January | 9 | 1AM to 2AM | 12 | 10.2 | 3.9 | 6.9 | 3.94 | 0.0824 | 0.05 | 12.15 | 1
January | 9 | 2AM to 3AM | 12 | 10.2 | 3.9 | 6.9 | 3.94 | 0.0824 | 0.05 | 12.15 | 1
January | 9 | 3AM to 4AM | 9 | 7.7 | 3 | 6.6 | 3.15 | 0.0829 | 0.04 | 12.07 | 1
January | 9 | 4AM to 5AM | 9 | 7.7 | 3 | 6.6 | 3.15 | 0.0829 | 0.04 | 12.07 | 1
January | 9 | 5AM to 6AM | 8.1 | 6.8 | 1.9 | 6.2 | 2.88 | 0.0831 | 0.04 | 12.05 | 1
January | 9 | 6AM to 7AM | 9 | 7.7 | 3 | 6.6 | 3.15 | 0.0829 | 0.04 | 12.07 | 1
January | 9 | 7AM to 8AM | 9 | 7.7 | 3 | 6.6 | 3.15 | 0.0829 | 0.04 | 12.07 | 1
January | 9 | 8AM to 9AM | 10 | 8.5 | 3 | 6.6 | 3.41 | 0.0827 | 0.04 | 12.1 | 1
January | 9 | 9AM to 10AM | 10.9 | 9.3 | 3.9 | 6.9 | 3.68 | 0.0826 | 0.05 | 12.13 | 1
January | 9 | 10AM to 11AM | 12.9 | 10.6 | 3 | 6.6 | 4.11 | 0.0822 | 0.04 | 12.18 | 1
January | 9 | 11AM to 12PM | 14 | 11.6 | 3.9 | 6.9 | 4.41 | 0.082 | 0.05 | 12.2 | 1
January | 9 | 12PM to 1PM | 15.1 | 12 | 1.9 | 6.2 | 4.57 | 0.0818 | 0.04 | 12.23 | 1
January | 9 | 1PM to 2PM | 16 | 13 | 3.9 | 6.9 | 4.89 | 0.0817 | 0.05 | 12.25 | 1
January | 9 | 2PM to 3PM | 17.1 | 13.8 | 3.9 | 6.9 | 5.15 | 0.0815 | 0.05 | 12.28 | 1
January | 9 | 3PM to 4PM | 17.1 | 13.8 | 3.9 | 6.9 | 5.15 | 0.0815 | 0.05 | 12.28 | 1
January | 9 | 4PM to 5PM | 15.1 | 12.2 | 3 | 6.6 | 4.63 | 0.0818 | 0.04 | 12.23 | 1
January | 9 | 5PM to 6PM | 12.9 | 10.5 | 1.9 | 6.2 | 4.05 | 0.0822 | 0.04 | 12.17 | 1
January | 9 | 6PM to 7PM | 12 | 9.8 | 1.9 | 6.2 | 3.84 | 0.0824 | 0.04 | 12.15 | 1
January | 9 | 7PM to 8PM | 12 | 10 | 3 | 6.6 | 3.89 | 0.0824 | 0.04 | 12.15 | 1
January | 9 | 8PM to 9PM | 10.9 | 9.3 | 3.9 | 6.9 | 3.68 | 0.0826 | 0.05 | 12.13 | 1
January | 9 | 9PM to 10PM | 10 | 8.7 | 3.9 | 6.9 | 3.46 | 0.0827 | 0.05 | 12.1 | 1
January | 9 | 10PM to 11PM | 10 | 8.7 | 3.9 | 6.9 | 3.46 | 0.0827 | 0.05 | 12.1 | 1
January | 9 | 11PM to 12AM | 10 | 8.9 | 5 | 7.3 | 3.52 | 0.0827 | 0.05 | 12.1 | 1
January | 10 | 12AM to 1AM | 9 | 7.5 | 1.9 | 6.2 | 3.1 | 0.0829 | 0.04 | 12.07 | 1
January | 10 | 1AM to 2AM | 7 | 5.6 | 0 | 5.6 | 2.53 | 0.0833 | 0.04 | 12.02 | 1
January | 10 | 2AM to 3AM | 7 | 5.6 | 0 | 5.6 | 2.53 | 0.0833 | 0.04 | 12.02 | 1
January | 10 | 3AM to 4AM | 6.1 | 4.7 | -0.9 | 5.4 | 2.28 | 0.0834 | 0.04 | 12 | 1
January | 10 | 4AM to 5AM | 6.1 | 4.7 | -0.9 | 5.4 | 2.28 | 0.0834 | 0.04 | 12 | 1
January | 10 | 5AM to 6AM | 5 | 3.9 | -0.9 | 5.4 | 2.02 | 0.0836 | 0.04 | 11.97 | 1
January | 10 | 6AM to 7AM | 3.9 | 3 | -0.9 | 5.4 | 1.76 | 0.0838 | 0.04 | 11.94 | 1
January | 10 | 7AM to 8AM | 6.1 | 4.9 | 0 | 5.6 | 2.31 | 0.0834 | 0.04 | 12 | 1
January | 10 | 8AM to 9AM | 9 | 7.5 | 1.9 | 6.2 | 3.1 | 0.0829 | 0.04 | 12.07 | 1
January | 10 | 9AM to 10AM | 14 | 11.3 | 1.9 | 6.2 | 4.31 | 0.082 | 0.04 | 12.2 | 1
January | 10 | 10AM to 11AM | 16 | 12.9 | 3 | 6.6 | 4.84 | 0.0817 | 0.04 | 12.25 | 1
January | 10 | 11AM to 12PM | 19 | 15.4 | 5 | 7.3 | 5.69 | 0.0812 | 0.05 | 12.33 | 1
January | 10 | 12PM to 1PM | 19.9 | 16.2 | 6.1 | 7.7 | 5.97 | 0.081 | 0.05 | 12.36 | 1
January | 10 | 1PM to 2PM | 21.9 | 17.8 | 7 | 8.1 | 6.5 | 0.0807 | 0.05 | 12.41 | 1
January | 10 | 2PM to 3PM | 23 | 18.7 | 8.1 | 8.5 | 6.83 | 0.0805 | 0.06 | 12.44 | 1
January | 10 | 3PM to 4PM | 23 | 18.7 | 8.1 | 8.5 | 6.83 | 0.0805 | 0.06 | 12.44 | 1
January | 10 | 4PM to 5PM | 21.9 | 18 | 8.1 | 8.5 | 6.57 | 0.0807 | 0.06 | 12.41 | 1
January | 10 | 5PM to 6PM | 19.9 | 16.8 | 9 | 8.9 | 6.15 | 0.081 | 0.06 | 12.36 | 1
January | 10 | 6PM to 7PM | 19.9 | 16.8 | 9 | 8.9 | 6.15 | 0.081 | 0.06 | 12.36 | 1
January | 10 | 7PM to 8PM | 19.9 | 16.8 | 9 | 8.9 | 6.15 | 0.081 | 0.06 | 12.36 | 1
January | 10 | 8PM to 9PM | 19.9 | 16.8 | 9 | 8.9 | 6.15 | 0.081 | 0.06 | 12.36 | 1
January | 10 | 9PM to 10PM | 19.9 | 16.8 | 9 | 8.9 | 6.15 | 0.081 | 0.06 | 12.36 | 1
January | 10 | 10PM to 11PM | 19.9 | 17.1 | 10 | 9.4 | 6.23 | 0.081 | 0.06 | 12.36 | 1
January | 10 | 11PM to 12AM | 19 | 16.5 | 10 | 9.4 | 6.01 | 0.0811 | 0.06 | 12.34 | 1
January | 11 | 12AM to 1AM | 19 | 16.7 | 10.9 | 9.9 | 6.08 | 0.0811 | 0.07 | 12.34 | 1
January | 11 | 1AM to 2AM | 19 | 16.7 | 10.9 | 9.9 | 6.08 | 0.0811 | 0.07 | 12.34 | 1
January | 11 | 2AM to 3AM | 18 | 15.9 | 10.9 | 9.9 | 5.82 | 0.0813 | 0.07 | 12.31 | 1
January | 11 | 3AM to 4AM | 18 | 15.9 | 10.9 | 9.9 | 5.82 | 0.0813 | 0.07 | 12.31 | 1
January | 11 | 4AM to 5AM | 18 | 16.2 | 12 | 10.4 | 5.9 | 0.0813 | 0.07 | 12.32 | 1
January | 11 | 5AM to 6AM | 18 | 16.2 | 12 | 10.4 | 5.9 | 0.0813 | 0.07 | 12.32 | 1
January | 11 | 6AM to 7AM | 19 | 17.5 | 14 | 11.5 | 6.33 | 0.0811 | 0.08 | 12.35 | 1
January | 11 | 7AM to 8AM | 19.9 | 18.4 | 15.1 | 12.1 | 6.64 | 0.081 | 0.08 | 12.37 | 1
January | 11 | 8AM to 9AM | 26.1 | 22.9 | 17.1 | 13.3 | 8.3 | 0.0799 | 0.09 | 12.53 | 1
January | 11 | 9AM to 10AM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
January | 11 | 10AM to 11AM | 33.1 | 27.9 | 19.9 | 15.3 | 10.3 | 0.0788 | 0.1 | 12.72 | 1
January | 11 | 11AM to 12PM | 37 | 30.5 | 21 | 16.2 | 11.38 | 0.0782 | 0.11 | 12.82 | 1
January | 11 | 12PM to 1PM | 41 | 33.5 | 21.9 | 16.9 | 12.44 | 0.0775 | 0.11 | 12.93 | 1
January | 11 | 1PM to 2PM | 43 | 34.6 | 21.9 | 16.9 | 12.92 | 0.0772 | 0.11 | 12.98 | 1
January | 11 | 2PM to 3PM | 44.1 | 34.9 | 21 | 16.2 | 13.07 | 0.0771 | 0.11 | 13.01 | 1
January | 11 | 3PM to 4PM | 43 | 34.3 | 21 | 16.2 | 12.81 | 0.0772 | 0.11 | 12.98 | 1
January | 11 | 4PM to 5PM | 39.9 | 32.6 | 21 | 16.2 | 12.07 | 0.0777 | 0.11 | 12.9 | 1
January | 11 | 5PM to 6PM | 39 | 32.3 | 21.9 | 16.9 | 11.97 | 0.0778 | 0.11 | 12.88 | 1
January | 11 | 6PM to 7PM | 37.9 | 30.6 | 19.9 | 15.3 | 11.47 | 0.078 | 0.1 | 12.85 | 1
January | 11 | 7PM to 8PM | 37 | 29.6 | 18 | 13.9 | 11.04 | 0.0782 | 0.09 | 12.82 | 1
January | 11 | 8PM to 9PM | 36 | 29 | 18 | 13.9 | 10.78 | 0.0783 | 0.09 | 12.79 | 1
January | 11 | 9PM to 10PM | 35.1 | 28.5 | 18 | 13.9 | 10.56 | 0.0785 | 0.09 | 12.77 | 1
January | 11 | 10PM to 11PM | 35.1 | 28.5 | 18 | 13.9 | 10.56 | 0.0785 | 0.09 | 12.77 | 1
January | 11 | 11PM to 12AM | 37 | 29.3 | 17.1 | 13.3 | 10.95 | 0.0782 | 0.09 | 12.82 | 1
January | 12 | 12AM to 1AM | 37.9 | 29.6 | 16 | 12.7 | 11.06 | 0.078 | 0.08 | 12.84 | 1
January | 12 | 1AM to 2AM | 37.9 | 29.6 | 16 | 12.7 | 11.06 | 0.078 | 0.08 | 12.84 | 1
January | 12 | 2AM to 3AM | 39 | 30.4 | 17.1 | 13.3 | 11.42 | 0.0779 | 0.09 | 12.87 | 1
January | 12 | 3AM to 4AM | 41 | 32.9 | 19.9 | 15.3 | 12.21 | 0.0775 | 0.1 | 12.92 | 1
January | 12 | 4AM to 5AM | 41 | 33.2 | 21 | 16.2 | 12.33 | 0.0775 | 0.11 | 12.93 | 1
January | 12 | 5AM to 6AM | 39.9 | 33.2 | 23 | 17.8 | 12.32 | 0.0777 | 0.12 | 12.9 | 1
January | 12 | 6AM to 7AM | 41 | 34.8 | 26.1 | 20.5 | 13.01 | 0.0775 | 0.14 | 12.94 | 1
January | 12 | 7AM to 8AM | 42.1 | 36.4 | 28.9 | 23.5 | 13.73 | 0.0773 | 0.16 | 12.98 | 1
January | 12 | 8AM to 9AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
January | 12 | 9AM to 10AM | 45 | 39.2 | 32 | 27.1 | 14.98 | 0.0769 | 0.18 | 13.06 | 1
January | 12 | 10AM to 11AM | 45 | 39.2 | 32 | 27.1 | 14.98 | 0.0769 | 0.18 | 13.06 | 1
January | 12 | 11AM to 12PM | 46 | 39.8 | 32 | 27.1 | 15.24 | 0.0767 | 0.18 | 13.09 | 1
January | 12 | 12PM to 1PM | 48 | 40.8 | 32 | 27.1 | 15.71 | 0.0764 | 0.18 | 13.14 | 1
January | 12 | 1PM to 2PM | 50 | 41.8 | 32 | 27.1 | 16.19 | 0.0761 | 0.18 | 13.19 | 1
January | 12 | 2PM to 3PM | 50 | 41.1 | 30 | 24.7 | 15.83 | 0.0761 | 0.16 | 13.18 | 1
January | 12 | 3PM to 4PM | 50 | 40.3 | 28 | 22.5 | 15.49 | 0.0761 | 0.15 | 13.18 | 1
January | 12 | 4PM to 5PM | 42.1 | 35 | 25 | 19.5 | 13.11 | 0.0773 | 0.13 | 12.96 | 1
January | 12 | 5PM to 6PM | 36 | 29.3 | 19 | 14.7 | 10.89 | 0.0783 | 0.1 | 12.79 | 1
January | 12 | 6PM to 7PM | 28.9 | 22.2 | 6.1 | 7.7 | 8.13 | 0.0795 | 0.05 | 12.59 | 1
January | 12 | 7PM to 8PM | 26.1 | 20.5 | 7 | 8.1 | 7.49 | 0.08 | 0.05 | 12.52 | 1
January | 12 | 8PM to 9PM | 23 | 18.1 | 5 | 7.3 | 6.64 | 0.0805 | 0.05 | 12.44 | 1
January | 12 | 9PM to 10PM | 19.9 | 15.8 | 3.9 | 6.9 | 5.84 | 0.081 | 0.05 | 12.36 | 1
January | 12 | 10PM to 11PM | 19 | 15.4 | 5 | 7.3 | 5.69 | 0.0812 | 0.05 | 12.33 | 1
January | 12 | 11PM to 12AM | 18 | 14.4 | 3.9 | 6.9 | 5.37 | 0.0813 | 0.05 | 12.31 | 1
January | 13 | 12AM to 1AM | 16 | 13 | 3.9 | 6.9 | 4.89 | 0.0817 | 0.05 | 12.25 | 1
January | 13 | 1AM to 2AM | 16 | 13.2 | 5 | 7.3 | 4.95 | 0.0817 | 0.05 | 12.26 | 1
January | 13 | 2AM to 3AM | 15.1 | 12.8 | 6.1 | 7.7 | 4.8 | 0.0818 | 0.05 | 12.23 | 1
January | 13 | 3AM to 4AM | 15.1 | 12.8 | 6.1 | 7.7 | 4.8 | 0.0818 | 0.05 | 12.23 | 1
January | 13 | 4AM to 5AM | 14 | 12 | 6.1 | 7.7 | 4.54 | 0.082 | 0.05 | 12.21 | 1
January | 13 | 5AM to 6AM | 12.9 | 11 | 5 | 7.3 | 4.21 | 0.0822 | 0.05 | 12.18 | 1
January | 13 | 6AM to 7AM | 12 | 10.4 | 5 | 7.3 | 4 | 0.0824 | 0.05 | 12.15 | 1
January | 13 | 7AM to 8AM | 12 | 10.4 | 5 | 7.3 | 4 | 0.0824 | 0.05 | 12.15 | 1
January | 13 | 8AM to 9AM | 14 | 11.6 | 3.9 | 6.9 | 4.41 | 0.082 | 0.05 | 12.2 | 1
January | 13 | 9AM to 10AM | 16 | 13 | 3.9 | 6.9 | 4.89 | 0.0817 | 0.05 | 12.25 | 1
January | 13 | 10AM to 11AM | 18 | 14.3 | 3 | 6.6 | 5.32 | 0.0813 | 0.04 | 12.3 | 1
January | 13 | 11AM to 12PM | 21 | 16.6 | 3.9 | 6.9 | 6.1 | 0.0808 | 0.05 | 12.38 | 1
January | 13 | 12PM to 1PM | 24.1 | 18.6 | 3.9 | 6.9 | 6.84 | 0.0803 | 0.05 | 12.46 | 1
January | 13 | 1PM to 2PM | 26.1 | 19.9 | 3.9 | 6.9 | 7.31 | 0.08 | 0.05 | 12.51 | 1
January | 13 | 2PM to 3PM | 26.1 | 19.2 | -0.9 | 5.4 | 7.08 | 0.08 | 0.04 | 12.51 | 1
January | 13 | 3PM to 4PM | 26.1 | 19.2 | -0.9 | 5.4 | 7.08 | 0.08 | 0.04 | 12.51 | 1
January | 13 | 4PM to 5PM | 24.1 | 17.9 | -0.9 | 5.4 | 6.6 | 0.0803 | 0.04 | 12.46 | 1
January | 13 | 5PM to 6PM | 21.9 | 16.6 | 0 | 5.6 | 6.12 | 0.0807 | 0.04 | 12.4 | 1
January | 13 | 6PM to 7PM | 21.9 | 16.6 | 0 | 5.6 | 6.12 | 0.0807 | 0.04 | 12.4 | 1
January | 13 | 7PM to 8PM | 23 | 17.6 | 1.9 | 6.2 | 6.48 | 0.0805 | 0.04 | 12.43 | 1
January | 13 | 8PM to 9PM | 19.9 | 15.5 | 1.9 | 6.2 | 5.74 | 0.081 | 0.04 | 12.35 | 1
January | 13 | 9PM to 10PM | 21 | 16.6 | 3.9 | 6.9 | 6.1 | 0.0808 | 0.05 | 12.38 | 1
January | 13 | 10PM to 11PM | 19.9 | 15.5 | 1.9 | 6.2 | 5.74 | 0.081 | 0.04 | 12.35 | 1
January | 13 | 11PM to 12AM | 19 | 14.6 | 0 | 5.6 | 5.43 | 0.0812 | 0.04 | 12.33 | 1
January | 14 | 12AM to 1AM | 17.1 | 13.3 | 1 | 5.9 | 5 | 0.0815 | 0.04 | 12.28 | 1
January | 14 | 1AM to 2AM | 17.1 | 13.1 | 0 | 5.6 | 4.95 | 0.0815 | 0.04 | 12.28 | 1
January | 14 | 2AM to 3AM | 17.1 | 13.1 | 0 | 5.6 | 4.95 | 0.0815 | 0.04 | 12.28 | 1
January | 14 | 3AM to 4AM | 16 | 12.5 | 1 | 5.9 | 4.74 | 0.0817 | 0.04 | 12.25 | 1
January | 14 | 4AM to 5AM | 16 | 12.5 | 1 | 5.9 | 4.74 | 0.0817 | 0.04 | 12.25 | 1
January | 14 | 5AM to 6AM | 17.1 | 13.5 | 1.9 | 6.2 | 5.05 | 0.0815 | 0.04 | 12.28 | 1
January | 14 | 6AM to 7AM | 18 | 14 | 1 | 5.9 | 5.22 | 0.0813 | 0.04 | 12.3 | 1
January | 14 | 7AM to 8AM | 18 | 14.1 | 1.9 | 6.2 | 5.26 | 0.0813 | 0.04 | 12.3 | 1
January | 14 | 8AM to 9AM | 19 | 15.2 | 3.9 | 6.9 | 5.63 | 0.0812 | 0.05 | 12.33 | 1
January | 14 | 9AM to 10AM | 21 | 16.6 | 3.9 | 6.9 | 6.1 | 0.0808 | 0.05 | 12.38 | 1
January | 14 | 10AM to 11AM | 26.1 | 20.1 | 5 | 7.3 | 7.37 | 0.08 | 0.05 | 12.52 | 1
January | 14 | 11AM to 12PM | 27 | 20.7 | 5 | 7.3 | 7.59 | 0.0798 | 0.05 | 12.54 | 1
January | 14 | 12PM to 1PM | 28 | 21.6 | 6.1 | 7.7 | 7.91 | 0.0797 | 0.05 | 12.57 | 1
January | 14 | 1PM to 2PM | 28 | 21.8 | 7 | 8.1 | 7.97 | 0.0797 | 0.05 | 12.57 | 1
January | 14 | 2PM to 3PM | 28 | 22.1 | 9 | 8.9 | 8.1 | 0.0796 | 0.06 | 12.57 | 1
January | 14 | 3PM to 4PM | 28 | 23.8 | 16 | 12.7 | 8.67 | 0.0796 | 0.08 | 12.58 | 1
January | 14 | 4PM to 5PM | 27 | 22.6 | 14 | 11.5 | 8.23 | 0.0798 | 0.08 | 12.55 | 1
January | 14 | 5PM to 6PM | 27 | 22.4 | 12.9 | 10.9 | 8.14 | 0.0798 | 0.07 | 12.55 | 1
January | 14 | 6PM to 7PM | 27 | 21.5 | 9 | 8.9 | 7.84 | 0.0798 | 0.06 | 12.54 | 1
January | 14 | 7PM to 8PM | 26.1 | 21.1 | 10 | 9.4 | 7.7 | 0.08 | 0.06 | 12.52 | 1
January | 14 | 8PM to 9PM | 26.1 | 21.1 | 10 | 9.4 | 7.7 | 0.08 | 0.06 | 12.52 | 1
January | 14 | 9PM to 10PM | 26.1 | 21.1 | 10 | 9.4 | 7.7 | 0.08 | 0.06 | 12.52 | 1
January | 14 | 10PM to 11PM | 26.1 | 21.1 | 10 | 9.4 | 7.7 | 0.08 | 0.06 | 12.52 | 1
January | 14 | 11PM to 12AM | 25 | 20.4 | 10 | 9.4 | 7.44 | 0.0801 | 0.06 | 12.49 | 1
January | 15 | 12AM to 1AM | 26.1 | 21.1 | 10 | 9.4 | 7.7 | 0.08 | 0.06 | 12.52 | 1
January | 15 | 1AM to 2AM | 25 | 20.6 | 10.9 | 9.9 | 7.51 | 0.0801 | 0.07 | 12.5 | 1
January | 15 | 2AM to 3AM | 24.1 | 20 | 10.9 | 9.9 | 7.29 | 0.0803 | 0.07 | 12.47 | 1
January | 15 | 3AM to 4AM | 24.1 | 20 | 10.9 | 9.9 | 7.29 | 0.0803 | 0.07 | 12.47 | 1
January | 15 | 4AM to 5AM | 24.1 | 20 | 10.9 | 9.9 | 7.29 | 0.0803 | 0.07 | 12.47 | 1
January | 15 | 5AM to 6AM | 24.1 | 20 | 10.9 | 9.9 | 7.29 | 0.0803 | 0.07 | 12.47 | 1
January | 15 | 6AM to 7AM | 24.1 | 20 | 10.9 | 9.9 | 7.29 | 0.0803 | 0.07 | 12.47 | 1
January | 15 | 7AM to 8AM | 25 | 20.9 | 12 | 10.4 | 7.59 | 0.0801 | 0.07 | 12.5 | 1
January | 15 | 8AM to 9AM | 28 | 23 | 12.9 | 10.9 | 8.4 | 0.0796 | 0.07 | 12.58 | 1
January | 15 | 9AM to 10AM | 34 | 27.1 | 15.1 | 12.1 | 10.02 | 0.0787 | 0.08 | 12.73 | 1
January | 15 | 10AM to 11AM | 37.9 | 29.6 | 16 | 12.7 | 11.06 | 0.078 | 0.08 | 12.84 | 1
January | 15 | 11AM to 12PM | 43 | 33.5 | 18 | 13.9 | 12.47 | 0.0772 | 0.09 | 12.97 | 1
January | 15 | 12PM to 1PM | 46.9 | 35.8 | 18 | 13.9 | 13.42 | 0.0766 | 0.09 | 13.07 | 1
January | 15 | 1PM to 2PM | 48 | 36.4 | 18 | 13.9 | 13.68 | 0.0765 | 0.09 | 13.1 | 1
January | 15 | 2PM to 3PM | 50 | 37.4 | 18 | 13.9 | 14.16 | 0.0762 | 0.09 | 13.15 | 1
January | 15 | 3PM to 4PM | 51.1 | 38 | 18 | 13.9 | 14.42 | 0.076 | 0.09 | 13.18 | 1
January | 15 | 4PM to 5PM | 48 | 36.6 | 19 | 14.7 | 13.8 | 0.0765 | 0.1 | 13.1 | 1
January | 15 | 5PM to 6PM | 46 | 35.5 | 19 | 14.7 | 13.32 | 0.0768 | 0.1 | 13.05 | 1
January | 15 | 6PM to 7PM | 45 | 35.1 | 19.9 | 15.3 | 13.16 | 0.0769 | 0.1 | 13.03 | 1
January | 15 | 7PM to 8PM | 43 | 34 | 19.9 | 15.3 | 12.68 | 0.0772 | 0.1 | 12.98 | 1
January | 15 | 8PM to 9PM | 41 | 32.9 | 19.9 | 15.3 | 12.21 | 0.0775 | 0.1 | 12.92 | 1
January | 15 | 9PM to 10PM | 39 | 31.2 | 19.9 | 15.3 | 11.73 | 0.0779 | 0.1 | 12.87 | 1
January | 15 | 10PM to 11PM | 37 | 30.5 | 21 | 16.2 | 11.38 | 0.0782 | 0.11 | 12.82 | 1
January | 15 | 11PM to 12AM | 37 | 30.5 | 21 | 16.2 | 11.38 | 0.0782 | 0.11 | 12.82 | 1
January | 16 | 12AM to 1AM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
January | 16 | 1AM to 2AM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
January | 16 | 2AM to 3AM | 36 | 30.2 | 21.9 | 16.9 | 11.23 | 0.0783 | 0.11 | 12.8 | 1
January | 16 | 3AM to 4AM | 35.1 | 29.7 | 21.9 | 16.9 | 11.01 | 0.0785 | 0.11 | 12.78 | 1
January | 16 | 4AM to 5AM | 35.1 | 30 | 23 | 17.8 | 11.15 | 0.0785 | 0.12 | 12.78 | 1
January | 16 | 5AM to 6AM | 37 | 31.1 | 23 | 17.8 | 11.63 | 0.0781 | 0.12 | 12.83 | 1
January | 16 | 6AM to 7AM | 37.9 | 31.9 | 24.1 | 18.7 | 11.99 | 0.078 | 0.12 | 12.86 | 1
January | 16 | 7AM to 8AM | 37.9 | 33 | 26.1 | 20.5 | 12.27 | 0.078 | 0.14 | 12.86 | 1
January | 16 | 8AM to 9AM | 41 | 35.5 | 28 | 22.5 | 13.32 | 0.0775 | 0.15 | 12.95 | 1
January | 16 | 9AM to 10AM | 48.9 | 41.3 | 32 | 27.1 | 15.93 | 0.0763 | 0.18 | 13.16 | 1
January | 16 | 10AM to 11AM | 52 | 42.8 | 32 | 27.1 | 16.67 | 0.0758 | 0.18 | 13.24 | 0
January | 16 | 11AM to 12PM | 52 | 42.8 | 32 | 27.1 | 16.67 | 0.0758 | 0.18 | 13.24 | 0
January | 16 | 12PM to 1PM | 51.1 | 42.4 | 32 | 27.1 | 16.45 | 0.0759 | 0.18 | 13.22 | 1
January | 16 | 1PM to 2PM | 51.1 | 41.9 | 30.9 | 25.8 | 16.25 | 0.0759 | 0.17 | 13.22 | 1
January | 16 | 2PM to 3PM | 51.1 | 42.4 | 32 | 27.1 | 16.45 | 0.0759 | 0.18 | 13.22 | 1
January | 16 | 3PM to 4PM | 51.1 | 41.6 | 30 | 24.7 | 16.09 | 0.076 | 0.16 | 13.21 | 1
January | 16 | 4PM to 5PM | 48.9 | 40.5 | 30 | 24.7 | 15.57 | 0.0763 | 0.16 | 13.16 | 1
January | 16 | 5PM to 6PM | 46.9 | 38.7 | 28 | 22.5 | 14.75 | 0.0766 | 0.15 | 13.1 | 1
January | 16 | 6PM to 7PM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
January | 16 | 7PM to 8PM | 43 | 36.6 | 28 | 22.5 | 13.79 | 0.0772 | 0.15 | 13 | 1
January | 16 | 8PM to 9PM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
January | 16 | 9PM to 10PM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
January | 16 | 10PM to 11PM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
January | 16 | 11PM to 12AM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
January | 17 | 12AM to 1AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
January | 17 | 1AM to 2AM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
January | 17 | 2AM to 3AM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
January | 17 | 3AM to 4AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
January | 17 | 4AM to 5AM | 43 | 42.5 | 42.1 | 40.4 | 16.55 | 0.0771 | 0.27 | 13.05 | 1
January | 17 | 5AM to 6AM | 43 | 42.5 | 42.1 | 40.4 | 16.55 | 0.0771 | 0.27 | 13.05 | 1
January | 17 | 6AM to 7AM | 43 | 42 | 41 | 38.8 | 16.3 | 0.0771 | 0.26 | 13.04 | 1
January | 17 | 7AM to 8AM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
January | 17 | 8AM to 9AM | 41 | 40.5 | 39.9 | 37.2 | 15.57 | 0.0774 | 0.25 | 12.99 | 1
January | 17 | 9AM to 10AM | 41 | 40.1 | 39 | 35.9 | 15.37 | 0.0774 | 0.24 | 12.98 | 1
January | 17 | 10AM to 11AM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
January | 17 | 11AM to 12PM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
January | 17 | 12PM to 1PM | 46 | 44.5 | 43 | 41.9 | 17.52 | 0.0766 | 0.28 | 13.13 | 1
January | 17 | 1PM to 2PM | 48.9 | 46.8 | 45 | 45.2 | 18.73 | 0.0761 | 0.3 | 13.22 | 1
January | 17 | 2PM to 3PM | 50 | 47.9 | 46 | 47.1 | 19.29 | 0.076 | 0.31 | 13.25 | 1
January | 17 | 3PM to 4PM | 51.1 | 48.8 | 46.9 | 48.8 | 19.81 | 0.0758 | 0.32 | 13.29 | 1
January | 17 | 4PM to 5PM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
January | 17 | 5PM to 6PM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
January | 17 | 6PM to 7PM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
January | 17 | 7PM to 8PM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
January | 17 | 8PM to 9PM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
January | 17 | 9PM to 10PM | 41 | 40.1 | 39 | 35.9 | 15.37 | 0.0774 | 0.24 | 12.98 | 1
January | 17 | 10PM to 11PM | 37.9 | 37 | 36 | 31.8 | 14 | 0.0779 | 0.21 | 12.89 | 1
January | 17 | 11PM to 12AM | 37 | 36.6 | 36 | 31.8 | 13.78 | 0.0781 | 0.21 | 12.87 | 1
January | 18 | 12AM to 1AM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 1AM to 2AM | 35.1 | 34.6 | 34 | 29.3 | 12.93 | 0.0784 | 0.2 | 12.81 | 1
January | 18 | 2AM to 3AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
January | 18 | 3AM to 4AM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 4AM to 5AM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 5AM to 6AM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
January | 18 | 6AM to 7AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
January | 18 | 7AM to 8AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
January | 18 | 8AM to 9AM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 9AM to 10AM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 10AM to 11AM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 11AM to 12PM | 37 | 35.7 | 34 | 29.3 | 13.41 | 0.0781 | 0.2 | 12.86 | 1
January | 18 | 12PM to 1PM | 37 | 36.2 | 35.1 | 30.6 | 13.61 | 0.0781 | 0.2 | 12.87 | 1
January | 18 | 1PM to 2PM | 37.9 | 37 | 36 | 31.8 | 14 | 0.0779 | 0.21 | 12.89 | 1
January | 18 | 2PM to 3PM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
January | 18 | 3PM to 4PM | 39 | 37.6 | 36 | 31.8 | 14.26 | 0.0777 | 0.21 | 12.92 | 1
January | 18 | 4PM to 5PM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
January | 18 | 5PM to 6PM | 37.9 | 37 | 36 | 31.8 | 14 | 0.0779 | 0.21 | 12.89 | 1
January | 18 | 6PM to 7PM | 37 | 36.2 | 35.1 | 30.6 | 13.61 | 0.0781 | 0.2 | 12.87 | 1
January | 18 | 7PM to 8PM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 8PM to 9PM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 9PM to 10PM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 10PM to 11PM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
January | 18 | 11PM to 12AM | 37 | 37 | 37 | 33.2 | 14 | 0.078 | 0.22 | 12.87 | 1
January | 19 | 12AM to 1AM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
January | 19 | 1AM to 2AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
January | 19 | 2AM to 3AM | 37.9 | 37 | 36 | 31.8 | 14 | 0.0779 | 0.21 | 12.89 | 1
January | 19 | 3AM to 4AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
January | 19 | 4AM to 5AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
January | 19 | 5AM to 6AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
January | 19 | 6AM to 7AM | 39 | 38.5 | 37.9 | 34.4 | 14.66 | 0.0777 | 0.23 | 12.93 | 1
January | 19 | 7AM to 8AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
January | 19 | 8AM to 9AM | 41 | 40.5 | 39.9 | 37.2 | 15.57 | 0.0774 | 0.25 | 12.99 | 1
January | 19 | 9AM to 10AM | 41 | 41 | 41 | 38.8 | 15.82 | 0.0774 | 0.26 | 12.99 | 1
January | 19 | 10AM to 11AM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
January | 19 | 11AM to 12PM | 43 | 42.5 | 42.1 | 40.4 | 16.55 | 0.0771 | 0.27 | 13.05 | 1
January | 19 | 12PM to 1PM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
January | 19 | 1PM to 2PM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
January | 19 | 2PM to 3PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
January | 19 | 3PM to 4PM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
January | 19 | 4PM to 5PM | 43 | 42.5 | 42.1 | 40.4 | 16.55 | 0.0771 | 0.27 | 13.05 | 1
January | 19 | 5PM to 6PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
January | 19 | 6PM to 7PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
January | 19 | 7PM to 8PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
January | 19 | 8PM to 9PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
January | 19 | 9PM to 10PM | 43 | 42.5 | 42.1 | 40.4 | 16.55 | 0.0771 | 0.27 | 13.05 | 1
January | 19 | 10PM to 11PM | 44.1 | 43.5 | 43 | 41.9 | 17.04 | 0.0769 | 0.28 | 13.08 | 1
January | 19 | 11PM to 12AM | 45 | 44.5 | 44.1 | 43.6 | 17.53 | 0.0767 | 0.29 | 13.11 | 1
January | 20 | 12AM to 1AM | 45 | 44.5 | 44.1 | 43.6 | 17.53 | 0.0767 | 0.29 | 13.11 | 1
January | 20 | 1AM to 2AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
January | 20 | 2AM to 3AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
January | 20 | 3AM to 4AM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
January | 20 | 4AM to 5AM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
January | 20 | 5AM to 6AM | 42.1 | 39.3 | 36 | 31.8 | 15 | 0.0773 | 0.21 | 13 | 1
January | 20 | 6AM to 7AM | 42.1 | 38.9 | 35.1 | 30.6 | 14.83 | 0.0773 | 0.2 | 13 | 1
January | 20 | 7AM to 8AM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
January | 20 | 8AM to 9AM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
January | 20 | 9AM to 10AM | 37 | 35.3 | 33.1 | 28.3 | 13.25 | 0.0781 | 0.19 | 12.86 | 1
January | 20 | 10AM to 11AM | 37 | 35.7 | 34 | 29.3 | 13.41 | 0.0781 | 0.2 | 12.86 | 1
January | 20 | 11AM to 12PM | 37 | 35.7 | 34 | 29.3 | 13.41 | 0.0781 | 0.2 | 12.86 | 1
January | 20 | 12PM to 1PM | 36 | 34.7 | 33.1 | 28.3 | 12.99 | 0.0782 | 0.19 | 12.83 | 1
January | 20 | 1PM to 2PM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
January | 20 | 2PM to 3PM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
January | 20 | 3PM to 4PM | 35.1 | 33.3 | 30.9 | 25.8 | 12.38 | 0.0784 | 0.17 | 12.8 | 1
January | 20 | 4PM to 5PM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
January | 20 | 5PM to 6PM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
January | 20 | 6PM to 7PM | 33.1 | 31.2 | 28.9 | 23.5 | 11.55 | 0.0787 | 0.16 | 12.74 | 1
January | 20 | 7PM to 8PM | 33.1 | 30.4 | 27 | 21.4 | 11.23 | 0.0787 | 0.14 | 12.74 | 1
January | 20 | 8PM to 9PM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
January | 20 | 9PM to 10PM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
January | 20 | 10PM to 11PM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
January | 20 | 11PM to 12AM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
January | 21 | 12AM to 1AM | 30.9 | 29.2 | 27 | 21.4 | 10.71 | 0.0791 | 0.14 | 12.68 | 1
January | 21 | 1AM to 2AM | 30.9 | 28.8 | 26.1 | 20.5 | 10.58 | 0.0791 | 0.14 | 12.68 | 1
January | 21 | 2AM to 3AM | 30 | 27.9 | 25 | 19.5 | 10.2 | 0.0793 | 0.13 | 12.65 | 1
January | 21 | 3AM to 4AM | 30 | 27.9 | 25 | 19.5 | 10.2 | 0.0793 | 0.13 | 12.65 | 1
January | 21 | 4AM to 5AM | 30 | 27.9 | 25 | 19.5 | 10.2 | 0.0793 | 0.13 | 12.65 | 1
January | 21 | 5AM to 6AM | 30 | 27.9 | 25 | 19.5 | 10.2 | 0.0793 | 0.13 | 12.65 | 1
January | 21 | 6AM to 7AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 7AM to 8AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 8AM to 9AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 9AM to 10AM | 28.9 | 27.3 | 25 | 19.5 | 9.94 | 0.0794 | 0.13 | 12.63 | 1
January | 21 | 10AM to 11AM | 28.9 | 27.3 | 25 | 19.5 | 9.94 | 0.0794 | 0.13 | 12.63 | 1
January | 21 | 11AM to 12PM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 12PM to 1PM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
January | 21 | 1PM to 2PM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
January | 21 | 2PM to 3PM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
January | 21 | 3PM to 4PM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
January | 21 | 4PM to 5PM | 28.9 | 26.6 | 23 | 17.8 | 9.67 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 5PM to 6PM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 6PM to 7PM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 7PM to 8PM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 8PM to 9PM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 9PM to 10PM | 28.9 | 26.6 | 23 | 17.8 | 9.67 | 0.0794 | 0.12 | 12.62 | 1
January | 21 | 10PM to 11PM | 28 | 26.4 | 24.1 | 18.7 | 9.6 | 0.0796 | 0.12 | 12.6 | 1
January | 21 | 11PM to 12AM | 28 | 26.4 | 24.1 | 18.7 | 9.6 | 0.0796 | 0.12 | 12.6 | 1
January | 22 | 12AM to 1AM | 28 | 26 | 23 | 17.8 | 9.46 | 0.0796 | 0.12 | 12.6 | 1
January | 22 | 1AM to 2AM | 28 | 26.4 | 24.1 | 18.7 | 9.6 | 0.0796 | 0.12 | 12.6 | 1
January | 22 | 2AM to 3AM | 28 | 26 | 23 | 17.8 | 9.46 | 0.0796 | 0.12 | 12.6 | 1
January | 22 | 3AM to 4AM | 28 | 26 | 23 | 17.8 | 9.46 | 0.0796 | 0.12 | 12.6 | 1
January | 22 | 4AM to 5AM | 28 | 25.7 | 21.9 | 16.9 | 9.32 | 0.0796 | 0.11 | 12.59 | 1
January | 22 | 5AM to 6AM | 27 | 25 | 21.9 | 16.9 | 9.06 | 0.0798 | 0.11 | 12.57 | 1
January | 22 | 6AM to 7AM | 27 | 25 | 21.9 | 16.9 | 9.06 | 0.0798 | 0.11 | 12.57 | 1
January | 22 | 7AM to 8AM | 27 | 24.7 | 21 | 16.2 | 8.95 | 0.0798 | 0.11 | 12.56 | 1
January | 22 | 8AM to 9AM | 26.1 | 24.2 | 21 | 16.2 | 8.73 | 0.0799 | 0.11 | 12.54 | 1
January | 22 | 9AM to 10AM | 26.1 | 24.2 | 21 | 16.2 | 8.73 | 0.0799 | 0.11 | 12.54 | 1
January | 22 | 10AM to 11AM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
January | 22 | 11AM to 12PM | 28.9 | 25.3 | 19 | 14.7 | 9.2 | 0.0795 | 0.1 | 12.61 | 1
January | 22 | 12PM to 1PM | 30.9 | 26.1 | 18 | 13.9 | 9.56 | 0.0791 | 0.09 | 12.66 | 1
January | 22 | 1PM to 2PM | 34 | 28.2 | 19 | 14.7 | 10.42 | 0.0786 | 0.1 | 12.74 | 1
January | 22 | 2PM to 3PM | 33.1 | 27.4 | 18 | 13.9 | 10.08 | 0.0788 | 0.09 | 12.72 | 1
January | 22 | 3PM to 4PM | 32 | 27.7 | 21 | 16.2 | 10.16 | 0.079 | 0.11 | 12.69 | 1
January | 22 | 4PM to 5PM | 32 | 28.3 | 23 | 17.8 | 10.41 | 0.0789 | 0.12 | 12.7 | 1
January | 22 | 5PM to 6PM | 30.9 | 27.7 | 23 | 17.8 | 10.15 | 0.0791 | 0.12 | 12.67 | 1
January | 22 | 6PM to 7PM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
January | 22 | 7PM to 8PM | 32 | 28.7 | 24.1 | 18.7 | 10.55 | 0.0789 | 0.12 | 12.7 | 1
January | 22 | 8PM to 9PM | 32 | 29 | 25 | 19.5 | 10.68 | 0.0789 | 0.13 | 12.7 | 1
January | 22 | 9PM to 10PM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
January | 22 | 10PM to 11PM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
January | 22 | 11PM to 12AM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
January | 23 | 12AM to 1AM | 32 | 28.7 | 24.1 | 18.7 | 10.55 | 0.0789 | 0.12 | 12.7 | 1
January | 23 | 1AM to 2AM | 32 | 27 | 19 | 14.7 | 9.94 | 0.079 | 0.1 | 12.69 | 1
January | 23 | 2AM to 3AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
January | 23 | 3AM to 4AM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
January | 23 | 4AM to 5AM | 28.9 | 24.4 | 16 | 12.7 | 8.89 | 0.0795 | 0.08 | 12.61 | 1
January | 23 | 5AM to 6AM | 28.9 | 24.9 | 18 | 13.9 | 9.09 | 0.0795 | 0.09 | 12.61 | 1
January | 23 | 6AM to 7AM | 28.9 | 24.9 | 18 | 13.9 | 9.09 | 0.0795 | 0.09 | 12.61 | 1
January | 23 | 7AM to 8AM | 28.9 | 25.3 | 19 | 14.7 | 9.2 | 0.0795 | 0.1 | 12.61 | 1
January | 23 | 8AM to 9AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
January | 23 | 9AM to 10AM | 33.1 | 28.3 | 21 | 16.2 | 10.42 | 0.0788 | 0.11 | 12.72 | 1
January | 23 | 10AM to 11AM | 34 | 28.8 | 21 | 16.2 | 10.64 | 0.0786 | 0.11 | 12.75 | 1
January | 23 | 11AM to 12PM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
January | 23 | 12PM to 1PM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
January | 23 | 1PM to 2PM | 37.9 | 31.2 | 21.9 | 16.9 | 11.71 | 0.078 | 0.11 | 12.85 | 1
January | 23 | 2PM to 3PM | 41 | 33.8 | 23 | 17.8 | 12.58 | 0.0775 | 0.12 | 12.93 | 1
January | 23 | 3PM to 4PM | 43 | 35.2 | 24.1 | 18.7 | 13.2 | 0.0772 | 0.12 | 12.99 | 1
January | 23 | 4PM to 5PM | 44.1 | 35.8 | 24.1 | 18.7 | 13.46 | 0.077 | 0.12 | 13.01 | 1
January | 23 | 5PM to 6PM | 44.1 | 36.1 | 25 | 19.5 | 13.59 | 0.077 | 0.13 | 13.02 | 1
January | 23 | 6PM to 7PM | 46 | 36.9 | 24.1 | 18.7 | 13.94 | 0.0767 | 0.12 | 13.06 | 1
January | 23 | 7PM to 8PM | 46 | 36.9 | 24.1 | 18.7 | 13.94 | 0.0767 | 0.12 | 13.06 | 1
January | 23 | 8PM to 9PM | 44.1 | 36.8 | 27 | 21.4 | 13.88 | 0.077 | 0.14 | 13.02 | 1
January | 23 | 9PM to 10PM | 43 | 36.9 | 28.9 | 23.5 | 13.94 | 0.0772 | 0.16 | 13 | 1
January | 23 | 10PM to 11PM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
January | 23 | 11PM to 12AM | 41 | 36.6 | 30.9 | 25.8 | 13.81 | 0.0775 | 0.17 | 12.96 | 1
January | 24 | 12AM to 1AM | 41 | 36.6 | 30.9 | 25.8 | 13.81 | 0.0775 | 0.17 | 12.96 | 1
January | 24 | 1AM to 2AM | 34 | 29.8 | 24.1 | 18.7 | 11.03 | 0.0786 | 0.12 | 12.75 | 1
January | 24 | 2AM to 3AM | 28 | 23.8 | 16 | 12.7 | 8.67 | 0.0796 | 0.08 | 12.58 | 1
January | 24 | 3AM to 4AM | 24.1 | 20.8 | 14 | 11.5 | 7.54 | 0.0803 | 0.08 | 12.48 | 1
January | 24 | 4AM to 5AM | 21 | 18.5 | 12.9 | 10.9 | 6.71 | 0.0808 | 0.07 | 12.4 | 1
January | 24 | 5AM to 6AM | 19 | 17 | 12 | 10.4 | 6.16 | 0.0811 | 0.07 | 12.34 | 1
January | 24 | 6AM to 7AM | 18 | 15.9 | 10.9 | 9.9 | 5.82 | 0.0813 | 0.07 | 12.31 | 1
January | 24 | 7AM to 8AM | 18 | 16.2 | 12 | 10.4 | 5.9 | 0.0813 | 0.07 | 12.32 | 1
January | 24 | 8AM to 9AM | 19.9 | 17.8 | 12.9 | 10.9 | 6.45 | 0.081 | 0.07 | 12.37 | 1
January | 24 | 9AM to 10AM | 23 | 19.8 | 12.9 | 10.9 | 7.19 | 0.0805 | 0.07 | 12.45 | 1
January | 24 | 10AM to 11AM | 25 | 21.1 | 12.9 | 10.9 | 7.66 | 0.0801 | 0.07 | 12.5 | 1
January | 24 | 11AM to 12PM | 28 | 23.3 | 14 | 11.5 | 8.49 | 0.0796 | 0.08 | 12.58 | 1
January | 24 | 12PM to 1PM | 32 | 26.2 | 16 | 12.7 | 9.63 | 0.079 | 0.08 | 12.68 | 1
January | 24 | 1PM to 2PM | 34 | 27.6 | 17.1 | 13.3 | 10.21 | 0.0787 | 0.09 | 12.74 | 1
January | 24 | 2PM to 3PM | 36 | 29 | 18 | 13.9 | 10.78 | 0.0783 | 0.09 | 12.79 | 1
January | 24 | 3PM to 4PM | 37 | 29.9 | 19 | 14.7 | 11.15 | 0.0782 | 0.1 | 12.82 | 1
January | 24 | 4PM to 5PM | 36 | 29.5 | 19.9 | 15.3 | 10.99 | 0.0783 | 0.1 | 12.79 | 1
January | 24 | 5PM to 6PM | 35.1 | 29.4 | 21 | 16.2 | 10.9 | 0.0785 | 0.11 | 12.77 | 1
January | 24 | 6PM to 7PM | 37 | 30.1 | 19.9 | 15.3 | 11.25 | 0.0782 | 0.1 | 12.82 | 1
January | 24 | 7PM to 8PM | 37 | 30.5 | 21 | 16.2 | 11.38 | 0.0782 | 0.11 | 12.82 | 1
January | 24 | 8PM to 9PM | 37 | 30.5 | 21 | 16.2 | 11.38 | 0.0782 | 0.11 | 12.82 | 1
January | 24 | 9PM to 10PM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
January | 24 | 10PM to 11PM | 36 | 30.2 | 21.9 | 16.9 | 11.23 | 0.0783 | 0.11 | 12.8 | 1
January | 24 | 11PM to 12AM | 35.1 | 30 | 23 | 17.8 | 11.15 | 0.0785 | 0.12 | 12.78 | 1
January | 25 | 12AM to 1AM | 34 | 29.4 | 23 | 17.8 | 10.89 | 0.0786 | 0.12 | 12.75 | 1
January | 25 | 1AM to 2AM | 34 | 30.1 | 25 | 19.5 | 11.16 | 0.0786 | 0.13 | 12.76 | 1
January | 25 | 2AM to 3AM | 28 | 26 | 23 | 17.8 | 9.46 | 0.0796 | 0.12 | 12.6 | 1
January | 25 | 3AM to 4AM | 25 | 22.8 | 19 | 14.7 | 8.25 | 0.0801 | 0.1 | 12.51 | 1
January | 25 | 4AM to 5AM | 19 | 16 | 8.1 | 8.5 | 5.87 | 0.0811 | 0.06 | 12.34 | 1
January | 25 | 5AM to 6AM | 16 | 13.6 | 7 | 8.1 | 5.07 | 0.0817 | 0.05 | 12.26 | 1
January | 25 | 6AM to 7AM | 10.9 | 8.8 | 1 | 5.9 | 3.53 | 0.0826 | 0.04 | 12.12 | 1
January | 25 | 7AM to 8AM | 10.9 | 9 | 1.9 | 6.2 | 3.58 | 0.0826 | 0.04 | 12.12 | 1
January | 25 | 8AM to 9AM | 10 | 8.1 | 1 | 5.9 | 3.32 | 0.0827 | 0.04 | 12.1 | 1
January | 25 | 9AM to 10AM | 10.9 | 9.2 | 3 | 6.6 | 3.63 | 0.0826 | 0.04 | 12.12 | 1
January | 25 | 10AM to 11AM | 12.9 | 10.8 | 3.9 | 6.9 | 4.15 | 0.0822 | 0.05 | 12.18 | 1
January | 25 | 11AM to 12PM | 12.9 | 10.8 | 3.9 | 6.9 | 4.15 | 0.0822 | 0.05 | 12.18 | 1
January | 25 | 12PM to 1PM | 15.1 | 12.2 | 3 | 6.6 | 4.63 | 0.0818 | 0.04 | 12.23 | 1
January | 25 | 1PM to 2PM | 16 | 13 | 3.9 | 6.9 | 4.89 | 0.0817 | 0.05 | 12.25 | 1
January | 25 | 2PM to 3PM | 16 | 12.7 | 1.9 | 6.2 | 4.79 | 0.0817 | 0.04 | 12.25 | 1
January | 25 | 3PM to 4PM | 16 | 12.7 | 1.9 | 6.2 | 4.79 | 0.0817 | 0.04 | 12.25 | 1
January | 25 | 4PM to 5PM | 15.1 | 12 | 1.9 | 6.2 | 4.57 | 0.0818 | 0.04 | 12.23 | 1
January | 25 | 5PM to 6PM | 16 | 12.5 | 1 | 5.9 | 4.74 | 0.0817 | 0.04 | 12.25 | 1
January | 25 | 6PM to 7PM | 15.1 | 11.9 | 1 | 5.9 | 4.53 | 0.0818 | 0.04 | 12.23 | 1
January | 25 | 7PM to 8PM | 15.1 | 11.9 | 1 | 5.9 | 4.53 | 0.0818 | 0.04 | 12.23 | 1
January | 25 | 8PM to 9PM | 14 | 11.1 | 1 | 5.9 | 4.27 | 0.082 | 0.04 | 12.2 | 1
January | 25 | 9PM to 10PM | 14 | 10.8 | -0.9 | 5.4 | 4.18 | 0.082 | 0.04 | 12.2 | 1
January | 25 | 10PM to 11PM | 12.9 | 10 | -0.9 | 5.4 | 3.92 | 0.0822 | 0.04 | 12.17 | 1
January | 25 | 11PM to 12AM | 12 | 9.5 | 0 | 5.6 | 3.74 | 0.0824 | 0.04 | 12.15 | 1
January | 26 | 12AM to 1AM | 10.9 | 8.6 | 0 | 5.6 | 3.48 | 0.0826 | 0.04 | 12.12 | 1
January | 26 | 1AM to 2AM | 10 | 8 | 0 | 5.6 | 3.27 | 0.0827 | 0.04 | 12.1 | 1
January | 26 | 2AM to 3AM | 9 | 7.1 | 0 | 5.6 | 3.01 | 0.0829 | 0.04 | 12.07 | 1
January | 26 | 3AM to 4AM | 8.1 | 6.6 | 1 | 5.9 | 2.84 | 0.0831 | 0.04 | 12.05 | 1
January | 26 | 4AM to 5AM | 8.1 | 6.4 | 0 | 5.6 | 2.79 | 0.0831 | 0.04 | 12.05 | 1
January | 26 | 5AM to 6AM | 7 | 5.6 | 0 | 5.6 | 2.53 | 0.0833 | 0.04 | 12.02 | 1
January | 26 | 6AM to 7AM | 6.1 | 4.9 | 0 | 5.6 | 2.31 | 0.0834 | 0.04 | 12 | 1
January | 26 | 7AM to 8AM | 6.1 | 4.9 | 0 | 5.6 | 2.31 | 0.0834 | 0.04 | 12 | 1
January | 26 | 8AM to 9AM | 9 | 7.3 | 1 | 5.9 | 3.06 | 0.0829 | 0.04 | 12.07 | 1
January | 26 | 9AM to 10AM | 10.9 | 9 | 1.9 | 6.2 | 3.58 | 0.0826 | 0.04 | 12.12 | 1
January | 26 | 10AM to 11AM | 14 | 11.6 | 3.9 | 6.9 | 4.41 | 0.082 | 0.05 | 12.2 | 1
January | 26 | 11AM to 12PM | 18 | 14.7 | 5 | 7.3 | 5.43 | 0.0813 | 0.05 | 12.31 | 1
January | 26 | 12PM to 1PM | 21 | 17 | 6.1 | 7.7 | 6.23 | 0.0808 | 0.05 | 12.39 | 1
January | 26 | 1PM to 2PM | 23 | 18.3 | 6.1 | 7.7 | 6.7 | 0.0805 | 0.05 | 12.44 | 1
January | 26 | 2PM to 3PM | 24.1 | 19 | 6.1 | 7.7 | 6.96 | 0.0803 | 0.05 | 12.47 | 1
January | 26 | 3PM to 4PM | 24.1 | 18.6 | 3.9 | 6.9 | 6.84 | 0.0803 | 0.05 | 12.46 | 1
January | 26 | 4PM to 5PM | 23 | 17.9 | 3.9 | 6.9 | 6.58 | 0.0805 | 0.05 | 12.44 | 1
January | 26 | 5PM to 6PM | 19.9 | 15.8 | 3.9 | 6.9 | 5.84 | 0.081 | 0.05 | 12.36 | 1
January | 26 | 6PM to 7PM | 19 | 15.4 | 5 | 7.3 | 5.69 | 0.0812 | 0.05 | 12.33 | 1
January | 26 | 7PM to 8PM | 17.1 | 14 | 5 | 7.3 | 5.21 | 0.0815 | 0.05 | 12.28 | 1
January | 26 | 8PM to 9PM | 17.1 | 14.2 | 6.1 | 7.7 | 5.27 | 0.0815 | 0.05 | 12.28 | 1
January | 26 | 9PM to 10PM | 19 | 15.6 | 6.1 | 7.7 | 5.75 | 0.0812 | 0.05 | 12.34 | 1
January | 26 | 10PM to 11PM | 19 | 16.2 | 9 | 8.9 | 5.94 | 0.0811 | 0.06 | 12.34 | 1
January | 26 | 11PM to 12AM | 19 | 16 | 8.1 | 8.5 | 5.87 | 0.0811 | 0.06 | 12.34 | 1
January | 27 | 12AM to 1AM | 19.9 | 16.4 | 7 | 8.1 | 6.02 | 0.081 | 0.05 | 12.36 | 1
January | 27 | 1AM to 2AM | 21 | 17.4 | 8.1 | 8.5 | 6.35 | 0.0808 | 0.06 | 12.39 | 1
January | 27 | 2AM to 3AM | 19.9 | 16.4 | 7 | 8.1 | 6.02 | 0.081 | 0.05 | 12.36 | 1
January | 27 | 3AM to 4AM | 19.9 | 16.8 | 9 | 8.9 | 6.15 | 0.081 | 0.06 | 12.36 | 1
January | 27 | 4AM to 5AM | 21.9 | 17.6 | 6.1 | 7.7 | 6.44 | 0.0807 | 0.05 | 12.41 | 1
January | 27 | 5AM to 6AM | 21.9 | 18 | 8.1 | 8.5 | 6.57 | 0.0807 | 0.06 | 12.41 | 1
January | 27 | 6AM to 7AM | 23 | 18.7 | 8.1 | 8.5 | 6.83 | 0.0805 | 0.06 | 12.44 | 1
January | 27 | 7AM to 8AM | 24.1 | 19.6 | 9 | 8.9 | 7.15 | 0.0803 | 0.06 | 12.47 | 1
January | 27 | 8AM to 9AM | 25 | 20.4 | 10 | 9.4 | 7.44 | 0.0801 | 0.06 | 12.49 | 1
January | 27 | 9AM to 10AM | 26.1 | 20.9 | 9 | 8.9 | 7.62 | 0.08 | 0.06 | 12.52 | 1
January | 27 | 10AM to 11AM | 28.9 | 23.1 | 10.9 | 9.9 | 8.46 | 0.0795 | 0.07 | 12.6 | 1
January | 27 | 11AM to 12PM | 30.9 | 24.6 | 12 | 10.4 | 9.02 | 0.0792 | 0.07 | 12.65 | 1
January | 27 | 12PM to 1PM | 34 | 27.6 | 17.1 | 13.3 | 10.21 | 0.0787 | 0.09 | 12.74 | 1
January | 27 | 1PM to 2PM | 36 | 29 | 18 | 13.9 | 10.78 | 0.0783 | 0.09 | 12.79 | 1
January | 27 | 2PM to 3PM | 37 | 29.9 | 19 | 14.7 | 11.15 | 0.0782 | 0.1 | 12.82 | 1
January | 27 | 3PM to 4PM | 39 | 31.2 | 19.9 | 15.3 | 11.73 | 0.0779 | 0.1 | 12.87 | 1
January | 27 | 4PM to 5PM | 35.1 | 29.4 | 21 | 16.2 | 10.9 | 0.0785 | 0.11 | 12.77 | 1
January | 27 | 5PM to 6PM | 34 | 28.8 | 21 | 16.2 | 10.64 | 0.0786 | 0.11 | 12.75 | 1
January | 27 | 6PM to 7PM | 33.1 | 28.6 | 21.9 | 16.9 | 10.53 | 0.0788 | 0.11 | 12.72 | 1
January | 27 | 7PM to 8PM | 35.1 | 29.7 | 21.9 | 16.9 | 11.01 | 0.0785 | 0.11 | 12.78 | 1
January | 27 | 8PM to 9PM | 34 | 29.8 | 24.1 | 18.7 | 11.03 | 0.0786 | 0.12 | 12.75 | 1
January | 27 | 9PM to 10PM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
January | 27 | 10PM to 11PM | 30.9 | 27.7 | 23 | 17.8 | 10.15 | 0.0791 | 0.12 | 12.67 | 1
January | 27 | 11PM to 12AM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
January | 28 | 12AM to 1AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 28 | 1AM to 2AM | 28 | 26 | 23 | 17.8 | 9.46 | 0.0796 | 0.12 | 12.6 | 1
January | 28 | 2AM to 3AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 28 | 3AM to 4AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
January | 28 | 4AM to 5AM | 28 | 26 | 23 | 17.8 | 9.46 | 0.0796 | 0.12 | 12.6 | 1
January | 28 | 5AM to 6AM | 28 | 26 | 23 | 17.8 | 9.46 | 0.0796 | 0.12 | 12.6 | 1
January | 28 | 6AM to 7AM | 28 | 26.4 | 24.1 | 18.7 | 9.6 | 0.0796 | 0.12 | 12.6 | 1
January | 28 | 7AM to 8AM | 28.9 | 27.3 | 25 | 19.5 | 9.94 | 0.0794 | 0.13 | 12.63 | 1
January | 28 | 8AM to 9AM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
January | 28 | 9AM to 10AM | 36 | 32.6 | 28 | 22.5 | 12.1 | 0.0783 | 0.15 | 12.82 | 1
January | 28 | 10AM to 11AM | 39.9 | 35.2 | 28.9 | 23.5 | 13.21 | 0.0777 | 0.16 | 12.92 | 1
January | 28 | 11AM to 12PM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
January | 28 | 12PM to 1PM | 46 | 39 | 30 | 24.7 | 14.87 | 0.0767 | 0.16 | 13.08 | 1
January | 28 | 1PM to 2PM | 48 | 40.4 | 30.9 | 25.8 | 15.51 | 0.0764 | 0.17 | 13.14 | 1
January | 28 | 2PM to 3PM | 50 | 41.4 | 30.9 | 25.8 | 15.99 | 0.0761 | 0.17 | 13.19 | 1
January | 28 | 3PM to 4PM | 50 | 41.8 | 32 | 27.1 | 16.19 | 0.0761 | 0.18 | 13.19 | 1
January | 28 | 4PM to 5PM | 48.9 | 40.8 | 30.9 | 25.8 | 15.73 | 0.0763 | 0.17 | 13.16 | 1
January | 28 | 5PM to 6PM | 46 | 39 | 30 | 24.7 | 14.87 | 0.0767 | 0.16 | 13.08 | 1
January | 28 | 6PM to 7PM | 45 | 38.8 | 30.9 | 25.8 | 14.77 | 0.0769 | 0.17 | 13.06 | 1
January | 28 | 7PM to 8PM | 43 | 37.7 | 30.9 | 25.8 | 14.29 | 0.0772 | 0.17 | 13.01 | 1
January | 28 | 8PM to 9PM | 41 | 37.1 | 32 | 27.1 | 14.02 | 0.0775 | 0.18 | 12.96 | 1
January | 28 | 9PM to 10PM | 42.1 | 37.7 | 32 | 27.1 | 14.28 | 0.0773 | 0.18 | 12.99 | 1
January | 28 | 10PM to 11PM | 41 | 37.1 | 32 | 27.1 | 14.02 | 0.0775 | 0.18 | 12.96 | 1
January | 28 | 11PM to 12AM | 42.1 | 37.7 | 32 | 27.1 | 14.28 | 0.0773 | 0.18 | 12.99 | 1
January | 29 | 12AM to 1AM | 42.1 | 37.7 | 32 | 27.1 | 14.28 | 0.0773 | 0.18 | 12.99 | 1
January | 29 | 1AM to 2AM | 43 | 38.2 | 32 | 27.1 | 14.5 | 0.0772 | 0.18 | 13.01 | 1
January | 29 | 2AM to 3AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
January | 29 | 3AM to 4AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
January | 29 | 4AM to 5AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
January | 29 | 5AM to 6AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
January | 29 | 6AM to 7AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
January | 29 | 7AM to 8AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
January | 29 | 8AM to 9AM | 46.9 | 40.3 | 32 | 27.1 | 15.45 | 0.0766 | 0.18 | 13.11 | 1
January | 29 | 9AM to 10AM | 54 | 45.2 | 36 | 31.8 | 17.88 | 0.0755 | 0.21 | 13.31 | 0
January | 29 | 10AM to 11AM | 57.9 | 48.2 | 39 | 35.9 | 19.47 | 0.0749 | 0.24 | 13.42 | 0
January | 29 | 11AM to 12PM | 61 | 50 | 39.9 | 37.2 | 20.41 | 0.0744 | 0.25 | 13.51 | 0
January | 29 | 12PM to 1PM | 63 | 51.3 | 41 | 38.8 | 21.14 | 0.0741 | 0.26 | 13.56 | 0
January | 29 | 1PM to 2PM | 66 | 53 | 42.1 | 40.4 | 22.14 | 0.0737 | 0.27 | 13.65 | 0
January | 29 | 2PM to 3PM | 64.9 | 52.5 | 42.1 | 40.4 | 21.88 | 0.0738 | 0.27 | 13.62 | 0
January | 29 | 3PM to 4PM | 66 | 53.8 | 44.1 | 43.6 | 22.65 | 0.0737 | 0.29 | 13.66 | 0
January | 29 | 4PM to 5PM | 64.9 | 50.9 | 37.9 | 34.4 | 20.94 | 0.0739 | 0.23 | 13.6 | 0
January | 29 | 5PM to 6PM | 62.1 | 49.3 | 37 | 33.2 | 20.05 | 0.0743 | 0.22 | 13.52 | 0
January | 29 | 6PM to 7PM | 60.1 | 47.4 | 34 | 29.3 | 18.98 | 0.0746 | 0.2 | 13.46 | 0
January | 29 | 7PM to 8PM | 57 | 46.3 | 35.1 | 30.6 | 18.44 | 0.075 | 0.2 | 13.38 | 0
January | 29 | 8PM to 9PM | 54 | 47.8 | 42.1 | 40.4 | 19.22 | 0.0754 | 0.27 | 13.33 | 0
January | 29 | 9PM to 10PM | 55 | 47.8 | 41 | 38.8 | 19.22 | 0.0753 | 0.26 | 13.36 | 0
January | 29 | 10PM to 11PM | 54 | 48.2 | 43 | 41.9 | 19.44 | 0.0754 | 0.28 | 13.34 | 0
January | 29 | 11PM to 12AM | 54 | 48.2 | 43 | 41.9 | 19.44 | 0.0754 | 0.28 | 13.34 | 0
January | 30 | 12AM to 1AM | 54 | 48.2 | 43 | 41.9 | 19.44 | 0.0754 | 0.28 | 13.34 | 0
January | 30 | 1AM to 2AM | 54 | 48.7 | 44.1 | 43.6 | 19.72 | 0.0754 | 0.29 | 13.34 | 0
January | 30 | 2AM to 3AM | 53.1 | 47.8 | 43 | 41.9 | 19.22 | 0.0755 | 0.28 | 13.32 | 0
January | 30 | 3AM to 4AM | 54 | 48.2 | 43 | 41.9 | 19.44 | 0.0754 | 0.28 | 13.34 | 0
January | 30 | 4AM to 5AM | 53.1 | 48.3 | 44.1 | 43.6 | 19.5 | 0.0755 | 0.29 | 13.32 | 0
January | 30 | 5AM to 6AM | 53.1 | 48.3 | 44.1 | 43.6 | 19.5 | 0.0755 | 0.29 | 13.32 | 0
January | 30 | 6AM to 7AM | 54 | 49.6 | 46 | 47.1 | 20.25 | 0.0754 | 0.31 | 13.36 | 0
January | 30 | 7AM to 8AM | 54 | 49.1 | 45 | 45.2 | 19.96 | 0.0754 | 0.3 | 13.35 | 0
January | 30 | 8AM to 9AM | 55.9 | 49.6 | 44.1 | 43.6 | 20.2 | 0.0751 | 0.29 | 13.4 | 0
January | 30 | 9AM to 10AM | 57 | 50.4 | 45 | 45.2 | 20.7 | 0.0749 | 0.3 | 13.43 | 0
January | 30 | 10AM to 11AM | 59 | 51.8 | 46 | 47.1 | 21.48 | 0.0746 | 0.31 | 13.49 | 0
January | 30 | 11AM to 12PM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
January | 30 | 12PM to 1PM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
January | 30 | 1PM to 2PM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
January | 30 | 2PM to 3PM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
January | 30 | 3PM to 4PM | 60.1 | 53.2 | 48 | 50.8 | 22.31 | 0.0745 | 0.34 | 13.53 | 0
January | 30 | 4PM to 5PM | 59 | 52.8 | 48 | 50.8 | 22.05 | 0.0746 | 0.34 | 13.5 | 0
January | 30 | 5PM to 6PM | 60.1 | 54.2 | 50 | 54.7 | 22.93 | 0.0744 | 0.36 | 13.54 | 0
January | 30 | 6PM to 7PM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
January | 30 | 7PM to 8PM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
January | 30 | 8PM to 9PM | 60.1 | 53.7 | 48.9 | 52.6 | 22.59 | 0.0745 | 0.35 | 13.53 | 0
January | 30 | 9PM to 10PM | 60.1 | 53.7 | 48.9 | 52.6 | 22.59 | 0.0745 | 0.35 | 13.53 | 0
January | 30 | 10PM to 11PM | 59 | 53.2 | 48.9 | 52.6 | 22.33 | 0.0746 | 0.35 | 13.5 | 0
January | 30 | 11PM to 12AM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
January | 31 | 12AM to 1AM | 60.1 | 53.7 | 48.9 | 52.6 | 22.59 | 0.0745 | 0.35 | 13.53 | 0
January | 31 | 1AM to 2AM | 60.1 | 53.7 | 48.9 | 52.6 | 22.59 | 0.0745 | 0.35 | 13.53 | 0
January | 31 | 2AM to 3AM | 61 | 54 | 48.9 | 52.6 | 22.81 | 0.0743 | 0.35 | 13.55 | 0
January | 31 | 3AM to 4AM | 60.1 | 54.2 | 50 | 54.7 | 22.93 | 0.0744 | 0.36 | 13.54 | 0
January | 31 | 4AM to 5AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
January | 31 | 5AM to 6AM | 55.9 | 53.1 | 51.1 | 57 | 22.27 | 0.075 | 0.38 | 13.44 | 0
January | 31 | 6AM to 7AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
January | 31 | 7AM to 8AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
January | 31 | 8AM to 9AM | 55.9 | 52 | 48.9 | 52.6 | 21.58 | 0.0751 | 0.35 | 13.42 | 0
January | 31 | 9AM to 10AM | 53.1 | 50.7 | 48.9 | 52.6 | 20.88 | 0.0755 | 0.35 | 13.35 | 0
January | 31 | 10AM to 11AM | 52 | 51.5 | 51.1 | 57 | 21.31 | 0.0756 | 0.38 | 13.33 | 0
January | 31 | 11AM to 12PM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
January | 31 | 12PM to 1PM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
January | 31 | 1PM to 2PM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
January | 31 | 2PM to 3PM | 51.1 | 51.1 | 51.1 | 57 | 21.09 | 0.0757 | 0.38 | 13.31 | 1
January | 31 | 3PM to 4PM | 52 | 52 | 52 | 59 | 21.61 | 0.0756 | 0.39 | 13.34 | 0
January | 31 | 4PM to 5PM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
January | 31 | 5PM to 6PM | 41 | 40.5 | 39.9 | 37.2 | 15.57 | 0.0774 | 0.25 | 12.99 | 1
January | 31 | 6PM to 7PM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
January | 31 | 7PM to 8PM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
January | 31 | 8PM to 9PM | 37.9 | 37 | 36 | 31.8 | 14 | 0.0779 | 0.21 | 12.89 | 1
January | 31 | 9PM to 10PM | 34.9 | 33.6 | 31.8 | 26.9 | 12.5 | 0.0784 | 0.18 | 12.8 | 1
January | 31 | 10PM to 11PM | 32 | 30.1 | 27.7 | 22.2 | 11.09 | 0.0789 | 0.15 | 12.71 | 1
January | 31 | 11PM to 12AM | 29.1 | 26.8 | 23.4 | 18.1 | 9.76 | 0.0794 | 0.12 | 12.63 | 1
February | 1 | 12AM to 1AM | 26.2 | 23.6 | 19 | 14.7 | 8.55 | 0.0799 | 0.1 | 12.54 | 1
February | 1 | 1AM to 2AM | 23.2 | 20.4 | 14.7 | 11.9 | 7.39 | 0.0804 | 0.08 | 12.45 | 1
February | 1 | 2AM to 3AM | 20.3 | 17.5 | 10.6 | 9.7 | 6.35 | 0.0809 | 0.06 | 12.37 | 1
February | 1 | 3AM to 4AM | 17.1 | 14.2 | 6.1 | 7.7 | 5.27 | 0.0815 | 0.05 | 12.28 | 1
February | 1 | 4AM to 5AM | 17.1 | 14.6 | 8.1 | 8.5 | 5.4 | 0.0815 | 0.06 | 12.29 | 1
February | 1 | 5AM to 6AM | 16 | 13.9 | 8.1 | 8.5 | 5.14 | 0.0817 | 0.06 | 12.26 | 1
February | 1 | 6AM to 7AM | 14 | 12.7 | 9 | 8.9 | 4.72 | 0.082 | 0.06 | 12.21 | 1
February | 1 | 7AM to 8AM | 15.1 | 13.4 | 9 | 8.9 | 4.98 | 0.0818 | 0.06 | 12.24 | 1
February | 1 | 8AM to 9AM | 18 | 15.5 | 9 | 8.9 | 5.68 | 0.0813 | 0.06 | 12.31 | 1
February | 1 | 9AM to 10AM | 19 | 16 | 8.1 | 8.5 | 5.87 | 0.0811 | 0.06 | 12.34 | 1
February | 1 | 10AM to 11AM | 23 | 18.5 | 7 | 8.1 | 6.76 | 0.0805 | 0.05 | 12.44 | 1
February | 1 | 11AM to 12PM | 25 | 19.6 | 6.1 | 7.7 | 7.18 | 0.0802 | 0.05 | 12.49 | 1
February | 1 | 12PM to 1PM | 28 | 22 | 8.1 | 8.5 | 8.04 | 0.0796 | 0.06 | 12.57 | 1
February | 1 | 1PM to 2PM | 28.9 | 22.7 | 9 | 8.9 | 8.32 | 0.0795 | 0.06 | 12.59 | 1
February | 1 | 2PM to 3PM | 30 | 23.6 | 10 | 9.4 | 8.65 | 0.0793 | 0.06 | 12.62 | 1
February | 1 | 3PM to 4PM | 28.9 | 23.1 | 10.9 | 9.9 | 8.46 | 0.0795 | 0.07 | 12.6 | 1
February | 1 | 4PM to 5PM | 28.9 | 23.1 | 10.9 | 9.9 | 8.46 | 0.0795 | 0.07 | 12.6 | 1
February | 1 | 5PM to 6PM | 28.9 | 23.1 | 10.9 | 9.9 | 8.46 | 0.0795 | 0.07 | 12.6 | 1
February | 1 | 6PM to 7PM | 28 | 23 | 12.9 | 10.9 | 8.4 | 0.0796 | 0.07 | 12.58 | 1
February | 1 | 7PM to 8PM | 27 | 22.4 | 12.9 | 10.9 | 8.14 | 0.0798 | 0.07 | 12.55 | 1
February | 1 | 8PM to 9PM | 27 | 22.4 | 12.9 | 10.9 | 8.14 | 0.0798 | 0.07 | 12.55 | 1
February | 1 | 9PM to 10PM | 26.1 | 22.3 | 15.1 | 12.1 | 8.11 | 0.0799 | 0.08 | 12.53 | 1
February | 1 | 10PM to 11PM | 26.1 | 22.6 | 16 | 12.7 | 8.2 | 0.0799 | 0.08 | 12.53 | 1
February | 1 | 11PM to 12AM | 26.1 | 22.9 | 17.1 | 13.3 | 8.3 | 0.0799 | 0.09 | 12.53 | 1
February | 2 | 12AM to 1AM | 27 | 23.7 | 18 | 13.9 | 8.61 | 0.0798 | 0.09 | 12.56 | 1
February | 2 | 1AM to 2AM | 27 | 23.7 | 18 | 13.9 | 8.61 | 0.0798 | 0.09 | 12.56 | 1
February | 2 | 2AM to 3AM | 27 | 23.5 | 17.1 | 13.3 | 8.52 | 0.0798 | 0.09 | 12.56 | 1
February | 2 | 3AM to 4AM | 25 | 22.2 | 17.1 | 13.3 | 8.04 | 0.0801 | 0.09 | 12.51 | 1
February | 2 | 4AM to 5AM | 25 | 22.5 | 18 | 13.9 | 8.13 | 0.0801 | 0.09 | 12.51 | 1
February | 2 | 5AM to 6AM | 25 | 22.5 | 18 | 13.9 | 8.13 | 0.0801 | 0.09 | 12.51 | 1
February | 2 | 6AM to 7AM | 25 | 23.1 | 19.9 | 15.3 | 8.35 | 0.0801 | 0.1 | 12.51 | 1
February | 2 | 7AM to 8AM | 25 | 23.1 | 19.9 | 15.3 | 8.35 | 0.0801 | 0.1 | 12.51 | 1
February | 2 | 8AM to 9AM | 27 | 24.3 | 19.9 | 15.3 | 8.82 | 0.0798 | 0.1 | 12.56 | 1
February | 2 | 9AM to 10AM | 28.9 | 24.9 | 18 | 13.9 | 9.09 | 0.0795 | 0.09 | 12.61 | 1
February | 2 | 10AM to 11AM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
February | 2 | 11AM to 12PM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
February | 2 | 12PM to 1PM | 34 | 27.1 | 15.1 | 12.1 | 10.02 | 0.0787 | 0.08 | 12.73 | 1
February | 2 | 1PM to 2PM | 36 | 27.5 | 12 | 10.4 | 10.23 | 0.0784 | 0.07 | 12.78 | 1
February | 2 | 2PM to 3PM | 37 | 27.7 | 10 | 9.4 | 10.34 | 0.0782 | 0.06 | 12.8 | 1
February | 2 | 3PM to 4PM | 37.9 | 28.4 | 10.9 | 9.9 | 10.63 | 0.0781 | 0.07 | 12.83 | 1
February | 2 | 4PM to 5PM | 37 | 28.6 | 14 | 11.5 | 10.66 | 0.0782 | 0.08 | 12.81 | 1
February | 2 | 5PM to 6PM | 37 | 29.1 | 16 | 12.7 | 10.84 | 0.0782 | 0.08 | 12.81 | 1
February | 2 | 6PM to 7PM | 36 | 29.3 | 19 | 14.7 | 10.89 | 0.0783 | 0.1 | 12.79 | 1
February | 2 | 7PM to 8PM | 33.1 | 27.9 | 19.9 | 15.3 | 10.3 | 0.0788 | 0.1 | 12.72 | 1
February | 2 | 8PM to 9PM | 33.1 | 27.4 | 18 | 13.9 | 10.08 | 0.0788 | 0.09 | 12.72 | 1
February | 2 | 9PM to 10PM | 33.1 | 26.8 | 16 | 12.7 | 9.89 | 0.0788 | 0.08 | 12.71 | 1
February | 2 | 10PM to 11PM | 32 | 25.2 | 12 | 10.4 | 9.28 | 0.079 | 0.07 | 12.68 | 1
February | 2 | 11PM to 12AM | 28.9 | 24.1 | 15.1 | 12.1 | 8.8 | 0.0795 | 0.08 | 12.6 | 1
February | 3 | 12AM to 1AM | 25 | 23.8 | 21.9 | 16.9 | 8.58 | 0.0801 | 0.11 | 12.52 | 1
February | 3 | 1AM to 2AM | 25 | 23.8 | 21.9 | 16.9 | 8.58 | 0.0801 | 0.11 | 12.52 | 1
February | 3 | 2AM to 3AM | 25 | 23.8 | 21.9 | 16.9 | 8.58 | 0.0801 | 0.11 | 12.52 | 1
February | 3 | 3AM to 4AM | 23 | 20.1 | 14 | 11.5 | 7.28 | 0.0805 | 0.08 | 12.45 | 1
February | 3 | 4AM to 5AM | 23 | 19.8 | 12.9 | 10.9 | 7.19 | 0.0805 | 0.07 | 12.45 | 1
February | 3 | 5AM to 6AM | 21.9 | 19.1 | 12.9 | 10.9 | 6.93 | 0.0806 | 0.07 | 12.42 | 1
February | 3 | 6AM to 7AM | 19.9 | 17.3 | 10.9 | 9.9 | 6.29 | 0.081 | 0.07 | 12.37 | 1
February | 3 | 7AM to 8AM | 19.9 | 17.3 | 10.9 | 9.9 | 6.29 | 0.081 | 0.07 | 12.37 | 1
February | 3 | 8AM to 9AM | 24.1 | 20.8 | 14 | 11.5 | 7.54 | 0.0803 | 0.08 | 12.48 | 1
February | 3 | 9AM to 10AM | 27 | 22.9 | 15.1 | 12.1 | 8.33 | 0.0798 | 0.08 | 12.55 | 1
February | 3 | 10AM to 11AM | 28.9 | 23.6 | 12.9 | 10.9 | 8.62 | 0.0795 | 0.07 | 12.6 | 1
February | 3 | 11AM to 12PM | 30.9 | 24.6 | 12 | 10.4 | 9.02 | 0.0792 | 0.07 | 12.65 | 1
February | 3 | 12PM to 1PM | 35.1 | 27.5 | 14 | 11.5 | 10.18 | 0.0785 | 0.08 | 12.76 | 1
February | 3 | 1PM to 2PM | 37 | 28.2 | 12 | 10.4 | 10.49 | 0.0782 | 0.07 | 12.81 | 1
February | 3 | 2PM to 3PM | 37.9 | 28.4 | 10.9 | 9.9 | 10.63 | 0.0781 | 0.07 | 12.83 | 1
February | 3 | 3PM to 4PM | 39 | 29 | 10.9 | 9.9 | 10.89 | 0.0779 | 0.07 | 12.86 | 1
February | 3 | 4PM to 5PM | 37 | 28.6 | 14 | 11.5 | 10.66 | 0.0782 | 0.08 | 12.81 | 1
February | 3 | 5PM to 6PM | 36 | 28.2 | 15.1 | 12.1 | 10.5 | 0.0784 | 0.08 | 12.78 | 1
February | 3 | 6PM to 7PM | 35.1 | 28.2 | 17.1 | 13.3 | 10.47 | 0.0785 | 0.09 | 12.77 | 1
February | 3 | 7PM to 8PM | 34 | 28.2 | 19 | 14.7 | 10.42 | 0.0786 | 0.1 | 12.74 | 1
February | 3 | 8PM to 9PM | 35.1 | 29.7 | 21.9 | 16.9 | 11.01 | 0.0785 | 0.11 | 12.78 | 1
February | 3 | 9PM to 10PM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
February | 3 | 10PM to 11PM | 35.1 | 30.7 | 25 | 19.5 | 11.42 | 0.0784 | 0.13 | 12.78 | 1
February | 3 | 11PM to 12AM | 35.1 | 30.7 | 25 | 19.5 | 11.42 | 0.0784 | 0.13 | 12.78 | 1
February | 4 | 12AM to 1AM | 35.1 | 30.7 | 25 | 19.5 | 11.42 | 0.0784 | 0.13 | 12.78 | 1
February | 4 | 1AM to 2AM | 37 | 32.1 | 25 | 19.5 | 11.9 | 0.0781 | 0.13 | 12.83 | 1
February | 4 | 2AM to 3AM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
February | 4 | 3AM to 4AM | 32 | 29 | 25 | 19.5 | 10.68 | 0.0789 | 0.13 | 12.7 | 1
February | 4 | 4AM to 5AM | 28.9 | 27.3 | 25 | 19.5 | 9.94 | 0.0794 | 0.13 | 12.63 | 1
February | 4 | 5AM to 6AM | 28 | 26 | 23 | 17.8 | 9.46 | 0.0796 | 0.12 | 12.6 | 1
February | 4 | 6AM to 7AM | 27 | 24.7 | 21 | 16.2 | 8.95 | 0.0798 | 0.11 | 12.56 | 1
February | 4 | 7AM to 8AM | 27 | 24.3 | 19.9 | 15.3 | 8.82 | 0.0798 | 0.1 | 12.56 | 1
February | 4 | 8AM to 9AM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
February | 4 | 9AM to 10AM | 30 | 26.5 | 21 | 16.2 | 9.69 | 0.0793 | 0.11 | 12.64 | 1
February | 4 | 10AM to 11AM | 32 | 27.7 | 21 | 16.2 | 10.16 | 0.079 | 0.11 | 12.69 | 1
February | 4 | 11AM to 12PM | 32 | 28 | 21.9 | 16.9 | 10.27 | 0.079 | 0.11 | 12.7 | 1
February | 4 | 12PM to 1PM | 35.1 | 29.7 | 21.9 | 16.9 | 11.01 | 0.0785 | 0.11 | 12.78 | 1
February | 4 | 1PM to 2PM | 36 | 30.2 | 21.9 | 16.9 | 11.23 | 0.0783 | 0.11 | 12.8 | 1
February | 4 | 2PM to 3PM | 37 | 30.7 | 21.9 | 16.9 | 11.49 | 0.0782 | 0.11 | 12.83 | 1
February | 4 | 3PM to 4PM | 37 | 30.1 | 19.9 | 15.3 | 11.25 | 0.0782 | 0.1 | 12.82 | 1
February | 4 | 4PM to 5PM | 36 | 29.5 | 19.9 | 15.3 | 10.99 | 0.0783 | 0.1 | 12.79 | 1
February | 4 | 5PM to 6PM | 34 | 28.4 | 19.9 | 15.3 | 10.52 | 0.0786 | 0.1 | 12.74 | 1
February | 4 | 6PM to 7PM | 34 | 28.8 | 21 | 16.2 | 10.64 | 0.0786 | 0.11 | 12.75 | 1
February | 4 | 7PM to 8PM | 33.1 | 27.9 | 19.9 | 15.3 | 10.3 | 0.0788 | 0.1 | 12.72 | 1
February | 4 | 8PM to 9PM | 33.1 | 27.9 | 19.9 | 15.3 | 10.3 | 0.0788 | 0.1 | 12.72 | 1
February | 4 | 9PM to 10PM | 32 | 27.7 | 21 | 16.2 | 10.16 | 0.079 | 0.11 | 12.69 | 1
February | 4 | 10PM to 11PM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
February | 4 | 11PM to 12AM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
February | 5 | 12AM to 1AM | 30 | 26.5 | 21 | 16.2 | 9.69 | 0.0793 | 0.11 | 12.64 | 1
February | 5 | 1AM to 2AM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
February | 5 | 2AM to 3AM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
February | 5 | 3AM to 4AM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
February | 5 | 4AM to 5AM | 32 | 28.3 | 23 | 17.8 | 10.41 | 0.0789 | 0.12 | 12.7 | 1
February | 5 | 5AM to 6AM | 32 | 28.3 | 23 | 17.8 | 10.41 | 0.0789 | 0.12 | 12.7 | 1
February | 5 | 6AM to 7AM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
February | 5 | 7AM to 8AM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
February | 5 | 8AM to 9AM | 33.1 | 29.3 | 24.1 | 18.7 | 10.82 | 0.0788 | 0.12 | 12.73 | 1
February | 5 | 9AM to 10AM | 36 | 30.9 | 24.1 | 18.7 | 11.51 | 0.0783 | 0.12 | 12.8 | 1
February | 5 | 10AM to 11AM | 37.9 | 29.8 | 17.1 | 13.3 | 11.16 | 0.078 | 0.09 | 12.84 | 1
February | 5 | 11AM to 12PM | 41 | 31.7 | 18 | 13.9 | 11.99 | 0.0776 | 0.09 | 12.92 | 1
February | 5 | 12PM to 1PM | 43 | 33.5 | 18 | 13.9 | 12.47 | 0.0772 | 0.09 | 12.97 | 1
February | 5 | 1PM to 2PM | 45 | 34.2 | 16 | 12.7 | 12.75 | 0.077 | 0.08 | 13.02 | 1
February | 5 | 2PM to 3PM | 45 | 33.7 | 14 | 11.5 | 12.57 | 0.077 | 0.08 | 13.02 | 1
February | 5 | 3PM to 4PM | 45 | 34.2 | 16 | 12.7 | 12.75 | 0.077 | 0.08 | 13.02 | 1
February | 5 | 4PM to 5PM | 43 | 32.8 | 15.1 | 12.1 | 12.19 | 0.0773 | 0.08 | 12.97 | 1
February | 5 | 5PM to 6PM | 39 | 30.2 | 16 | 12.7 | 11.32 | 0.0779 | 0.08 | 12.87 | 1
February | 5 | 6PM to 7PM | 36 | 28.2 | 15.1 | 12.1 | 10.5 | 0.0784 | 0.08 | 12.78 | 1
February | 5 | 7PM to 8PM | 34 | 27.1 | 15.1 | 12.1 | 10.02 | 0.0787 | 0.08 | 12.73 | 1
February | 5 | 8PM to 9PM | 32 | 25.7 | 14 | 11.5 | 9.45 | 0.079 | 0.08 | 12.68 | 1
February | 5 | 9PM to 10PM | 30.9 | 24.8 | 12.9 | 10.9 | 9.09 | 0.0792 | 0.07 | 12.65 | 1
February | 5 | 10PM to 11PM | 32 | 24.8 | 10 | 9.4 | 9.13 | 0.079 | 0.06 | 12.67 | 1
February | 5 | 11PM to 12AM | 30.9 | 24.3 | 10.9 | 9.9 | 8.94 | 0.0792 | 0.07 | 12.65 | 1
February | 6 | 12AM to 1AM | 26.1 | 22.3 | 15.1 | 12.1 | 8.11 | 0.0799 | 0.08 | 12.53 | 1
February | 6 | 1AM to 2AM | 30 | 24 | 12 | 10.4 | 8.8 | 0.0793 | 0.07 | 12.63 | 1
February | 6 | 2AM to 3AM | 30 | 24 | 12 | 10.4 | 8.8 | 0.0793 | 0.07 | 12.63 | 1
February | 6 | 3AM to 4AM | 30.9 | 24.6 | 12 | 10.4 | 9.02 | 0.0792 | 0.07 | 12.65 | 1
February | 6 | 4AM to 5AM | 32 | 25 | 10.9 | 9.9 | 9.2 | 0.079 | 0.07 | 12.68 | 1
February | 6 | 5AM to 6AM | 30.9 | 24.6 | 12 | 10.4 | 9.02 | 0.0792 | 0.07 | 12.65 | 1
February | 6 | 6AM to 7AM | 34 | 26.8 | 14 | 11.5 | 9.92 | 0.0787 | 0.08 | 12.73 | 1
February | 6 | 7AM to 8AM | 36 | 28.2 | 15.1 | 12.1 | 10.5 | 0.0784 | 0.08 | 12.78 | 1
February | 6 | 8AM to 9AM | 39.9 | 30.4 | 15.1 | 12.1 | 11.45 | 0.0777 | 0.08 | 12.89 | 1
February | 6 | 9AM to 10AM | 42.1 | 32.8 | 17.1 | 13.3 | 12.16 | 0.0774 | 0.09 | 12.95 | 1
February | 6 | 10AM to 11AM | 48 | 36.1 | 17.1 | 13.3 | 13.59 | 0.0765 | 0.09 | 13.1 | 1
February | 6 | 11AM to 12PM | 50 | 37.4 | 18 | 13.9 | 14.16 | 0.0762 | 0.09 | 13.15 | 1
February | 6 | 12PM to 1PM | 53.1 | 39.5 | 19.9 | 15.3 | 15.11 | 0.0757 | 0.1 | 13.24 | 0
February | 6 | 1PM to 2PM | 54 | 40.8 | 23 | 17.8 | 15.71 | 0.0756 | 0.12 | 13.27 | 0
February | 6 | 2PM to 3PM | 53.1 | 40.7 | 24.1 | 18.7 | 15.63 | 0.0757 | 0.12 | 13.25 | 0
February | 6 | 3PM to 4PM | 53.1 | 40.9 | 25 | 19.5 | 15.76 | 0.0757 | 0.13 | 13.25 | 0
February | 6 | 4PM to 5PM | 50 | 39.3 | 25 | 19.5 | 15.02 | 0.0761 | 0.13 | 13.17 | 1
February | 6 | 5PM to 6PM | 48 | 38.3 | 25 | 19.5 | 14.54 | 0.0764 | 0.13 | 13.12 | 1
February | 6 | 6PM to 7PM | 45 | 36.6 | 25 | 19.5 | 13.81 | 0.0769 | 0.13 | 13.04 | 1
February | 6 | 7PM to 8PM | 43 | 35.2 | 24.1 | 18.7 | 13.2 | 0.0772 | 0.12 | 12.99 | 1
February | 6 | 8PM to 9PM | 39.9 | 33.5 | 24.1 | 18.7 | 12.47 | 0.0777 | 0.12 | 12.91 | 1
February | 6 | 9PM to 10PM | 39 | 33.3 | 25 | 19.5 | 12.37 | 0.0778 | 0.13 | 12.89 | 1
February | 6 | 10PM to 11PM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
February | 6 | 11PM to 12AM | 33.1 | 29.6 | 25 | 19.5 | 10.94 | 0.0788 | 0.13 | 12.73 | 1
February | 7 | 12AM to 1AM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
February | 7 | 1AM to 2AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
February | 7 | 2AM to 3AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
February | 7 | 3AM to 4AM | 27 | 24.3 | 19.9 | 15.3 | 8.82 | 0.0798 | 0.1 | 12.56 | 1
February | 7 | 4AM to 5AM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
February | 7 | 5AM to 6AM | 25 | 22.2 | 17.1 | 13.3 | 8.04 | 0.0801 | 0.09 | 12.51 | 1
February | 7 | 6AM to 7AM | 24.1 | 21.7 | 17.1 | 13.3 | 7.82 | 0.0803 | 0.09 | 12.48 | 1
February | 7 | 7AM to 8AM | 24.1 | 21.3 | 16 | 12.7 | 7.72 | 0.0803 | 0.08 | 12.48 | 1
February | 7 | 8AM to 9AM | 25 | 21.7 | 15.1 | 12.1 | 7.85 | 0.0801 | 0.08 | 12.5 | 1
February | 7 | 9AM to 10AM | 26.1 | 22.1 | 14 | 11.5 | 8.02 | 0.08 | 0.08 | 12.53 | 1
February | 7 | 10AM to 11AM | 27 | 22.6 | 14 | 11.5 | 8.23 | 0.0798 | 0.08 | 12.55 | 1
February | 7 | 11AM to 12PM | 28.9 | 24.1 | 15.1 | 12.1 | 8.8 | 0.0795 | 0.08 | 12.6 | 1
February | 7 | 12PM to 1PM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
February | 7 | 1PM to 2PM | 30.9 | 25.6 | 16 | 12.7 | 9.37 | 0.0792 | 0.08 | 12.66 | 1
February | 7 | 2PM to 3PM | 30.9 | 25.8 | 17.1 | 13.3 | 9.47 | 0.0791 | 0.09 | 12.66 | 1
February | 7 | 3PM to 4PM | 30.9 | 26.1 | 18 | 13.9 | 9.56 | 0.0791 | 0.09 | 12.66 | 1
February | 7 | 4PM to 5PM | 30.9 | 26.1 | 18 | 13.9 | 9.56 | 0.0791 | 0.09 | 12.66 | 1
February | 7 | 5PM to 6PM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
February | 7 | 6PM to 7PM | 30 | 26.2 | 19.9 | 15.3 | 9.56 | 0.0793 | 0.1 | 12.64 | 1
February | 7 | 7PM to 8PM | 30 | 26.2 | 19.9 | 15.3 | 9.56 | 0.0793 | 0.1 | 12.64 | 1
February | 7 | 8PM to 9PM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
February | 7 | 9PM to 10PM | 28.9 | 25.5 | 19.9 | 15.3 | 9.3 | 0.0795 | 0.1 | 12.61 | 1
February | 7 | 10PM to 11PM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
February | 7 | 11PM to 12AM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
February | 8 | 12AM to 1AM | 28 | 24.7 | 19 | 14.7 | 8.98 | 0.0796 | 0.1 | 12.59 | 1
February | 8 | 1AM to 2AM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
February | 8 | 2AM to 3AM | 26.1 | 23.8 | 19.9 | 15.3 | 8.61 | 0.0799 | 0.1 | 12.54 | 1
February | 8 | 3AM to 4AM | 24.1 | 22.6 | 19.9 | 15.3 | 8.13 | 0.0803 | 0.1 | 12.49 | 1
February | 8 | 4AM to 5AM | 24.1 | 22.6 | 19.9 | 15.3 | 8.13 | 0.0803 | 0.1 | 12.49 | 1
February | 8 | 5AM to 6AM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
February | 8 | 6AM to 7AM | 25 | 24.2 | 23 | 17.8 | 8.72 | 0.0801 | 0.12 | 12.52 | 1
February | 8 | 7AM to 8AM | 26.1 | 24.9 | 23 | 17.8 | 8.98 | 0.0799 | 0.12 | 12.55 | 1
February | 8 | 8AM to 9AM | 26.1 | 25.6 | 25 | 19.5 | 9.25 | 0.0799 | 0.13 | 12.55 | 1
February | 8 | 9AM to 10AM | 27 | 26.6 | 26.1 | 20.5 | 9.62 | 0.0797 | 0.14 | 12.58 | 1
February | 8 | 10AM to 11AM | 28 | 27.2 | 26.1 | 20.5 | 9.88 | 0.0796 | 0.14 | 12.6 | 1
February | 8 | 11AM to 12PM | 28 | 27.6 | 27 | 21.4 | 10.02 | 0.0796 | 0.14 | 12.61 | 1
February | 8 | 12PM to 1PM | 27 | 26.6 | 26.1 | 20.5 | 9.62 | 0.0797 | 0.14 | 12.58 | 1
February | 8 | 1PM to 2PM | 28 | 27.2 | 26.1 | 20.5 | 9.88 | 0.0796 | 0.14 | 12.6 | 1
February | 8 | 2PM to 3PM | 27 | 26.2 | 25 | 19.5 | 9.46 | 0.0798 | 0.13 | 12.57 | 1
February | 8 | 3PM to 4PM | 25 | 24.6 | 24.1 | 18.7 | 8.86 | 0.0801 | 0.12 | 12.52 | 1
February | 8 | 4PM to 5PM | 25 | 24.2 | 23 | 17.8 | 8.72 | 0.0801 | 0.12 | 12.52 | 1
February | 8 | 5PM to 6PM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
February | 8 | 6PM to 7PM | 23 | 22.3 | 21 | 16.2 | 8 | 0.0804 | 0.11 | 12.46 | 1
February | 8 | 7PM to 8PM | 23 | 22.3 | 21 | 16.2 | 8 | 0.0804 | 0.11 | 12.46 | 1
February | 8 | 8PM to 9PM | 23 | 21.6 | 19 | 14.7 | 7.77 | 0.0804 | 0.1 | 12.46 | 1
February | 8 | 9PM to 10PM | 23 | 21.9 | 19.9 | 15.3 | 7.87 | 0.0804 | 0.1 | 12.46 | 1
February | 8 | 10PM to 11PM | 21.9 | 21.2 | 19.9 | 15.3 | 7.61 | 0.0806 | 0.1 | 12.43 | 1
February | 8 | 11PM to 12AM | 21 | 20 | 18 | 13.9 | 7.18 | 0.0808 | 0.09 | 12.4 | 1
February | 9 | 12AM to 1AM | 19.9 | 19 | 17.1 | 13.3 | 6.83 | 0.081 | 0.09 | 12.38 | 1
February | 9 | 1AM to 2AM | 19.9 | 18.7 | 16 | 12.7 | 6.72 | 0.081 | 0.08 | 12.37 | 1
February | 9 | 2AM to 3AM | 19 | 17.8 | 15.1 | 12.1 | 6.42 | 0.0811 | 0.08 | 12.35 | 1
February | 9 | 3AM to 4AM | 19 | 17.5 | 14 | 11.5 | 6.33 | 0.0811 | 0.08 | 12.35 | 1
February | 9 | 4AM to 5AM | 18 | 16.8 | 14 | 11.5 | 6.07 | 0.0813 | 0.08 | 12.32 | 1
February | 9 | 5AM to 6AM | 18 | 16.5 | 12.9 | 10.9 | 5.97 | 0.0813 | 0.07 | 12.32 | 1
February | 9 | 6AM to 7AM | 17.1 | 15.6 | 12 | 10.4 | 5.68 | 0.0815 | 0.07 | 12.29 | 1
February | 9 | 7AM to 8AM | 17.1 | 15.6 | 12 | 10.4 | 5.68 | 0.0815 | 0.07 | 12.29 | 1
February | 9 | 8AM to 9AM | 17.1 | 15.6 | 12 | 10.4 | 5.68 | 0.0815 | 0.07 | 12.29 | 1
February | 9 | 9AM to 10AM | 17.1 | 15.3 | 10.9 | 9.9 | 5.6 | 0.0815 | 0.07 | 12.29 | 1
February | 9 | 10AM to 11AM | 17.1 | 14.8 | 9 | 8.9 | 5.46 | 0.0815 | 0.06 | 12.29 | 1
February | 9 | 11AM to 12PM | 18 | 15.7 | 10 | 9.4 | 5.75 | 0.0813 | 0.06 | 12.31 | 1
February | 9 | 12PM to 1PM | 18 | 15.5 | 9 | 8.9 | 5.68 | 0.0813 | 0.06 | 12.31 | 1
February | 9 | 1PM to 2PM | 18 | 15.7 | 10 | 9.4 | 5.75 | 0.0813 | 0.06 | 12.31 | 1
February | 9 | 2PM to 3PM | 18 | 15.9 | 10.9 | 9.9 | 5.82 | 0.0813 | 0.07 | 12.31 | 1
February | 9 | 3PM to 4PM | 17.1 | 15.3 | 10.9 | 9.9 | 5.6 | 0.0815 | 0.07 | 12.29 | 1
February | 9 | 4PM to 5PM | 17.1 | 15.1 | 10 | 9.4 | 5.53 | 0.0815 | 0.06 | 12.29 | 1
February | 9 | 5PM to 6PM | 17.1 | 15.1 | 10 | 9.4 | 5.53 | 0.0815 | 0.06 | 12.29 | 1
February | 9 | 6PM to 7PM | 17.1 | 15.3 | 10.9 | 9.9 | 5.6 | 0.0815 | 0.07 | 12.29 | 1
February | 9 | 7PM to 8PM | 17.1 | 14.8 | 9 | 8.9 | 5.46 | 0.0815 | 0.06 | 12.29 | 1
February | 9 | 8PM to 9PM | 17.1 | 14.6 | 8.1 | 8.5 | 5.4 | 0.0815 | 0.06 | 12.29 | 1
February | 9 | 9PM to 10PM | 16 | 13.9 | 8.1 | 8.5 | 5.14 | 0.0817 | 0.06 | 12.26 | 1
February | 9 | 10PM to 11PM | 15.1 | 13.4 | 9 | 8.9 | 4.98 | 0.0818 | 0.06 | 12.24 | 1
February | 9 | 11PM to 12AM | 15.1 | 13.2 | 8.1 | 8.5 | 4.92 | 0.0818 | 0.06 | 12.24 | 1
February | 10 | 12AM to 1AM | 14 | 12.5 | 8.1 | 8.5 | 4.66 | 0.082 | 0.06 | 12.21 | 1
February | 10 | 1AM to 2AM | 12.9 | 11.9 | 9 | 8.9 | 4.46 | 0.0822 | 0.06 | 12.18 | 1
February | 10 | 2AM to 3AM | 12.9 | 11.7 | 8.1 | 8.5 | 4.4 | 0.0822 | 0.06 | 12.18 | 1
February | 10 | 3AM to 4AM | 12 | 11 | 8.1 | 8.5 | 4.19 | 0.0824 | 0.06 | 12.16 | 1
February | 10 | 4AM to 5AM | 12 | 11 | 8.1 | 8.5 | 4.19 | 0.0824 | 0.06 | 12.16 | 1
February | 10 | 5AM to 6AM | 12 | 10.8 | 7 | 8.1 | 4.12 | 0.0824 | 0.05 | 12.16 | 1
February | 10 | 6AM to 7AM | 10.9 | 10 | 7 | 8.1 | 3.86 | 0.0825 | 0.05 | 12.13 | 1
February | 10 | 7AM to 8AM | 14 | 12.7 | 9 | 8.9 | 4.72 | 0.082 | 0.06 | 12.21 | 1
February | 10 | 8AM to 9AM | 17.1 | 14.6 | 8.1 | 8.5 | 5.4 | 0.0815 | 0.06 | 12.29 | 1
February | 10 | 9AM to 10AM | 19 | 16.2 | 9 | 8.9 | 5.94 | 0.0811 | 0.06 | 12.34 | 1
February | 10 | 10AM to 11AM | 21.9 | 18.9 | 12 | 10.4 | 6.85 | 0.0806 | 0.07 | 12.42 | 1
February | 10 | 11AM to 12PM | 23 | 20.1 | 14 | 11.5 | 7.28 | 0.0805 | 0.08 | 12.45 | 1
February | 10 | 12PM to 1PM | 27 | 23.2 | 16 | 12.7 | 8.41 | 0.0798 | 0.08 | 12.55 | 1
February | 10 | 1PM to 2PM | 27 | 23.2 | 16 | 12.7 | 8.41 | 0.0798 | 0.08 | 12.55 | 1
February | 10 | 2PM to 3PM | 27 | 22.9 | 15.1 | 12.1 | 8.33 | 0.0798 | 0.08 | 12.55 | 1
February | 10 | 3PM to 4PM | 27 | 23.2 | 16 | 12.7 | 8.41 | 0.0798 | 0.08 | 12.55 | 1
February | 10 | 4PM to 5PM | 27 | 23.5 | 17.1 | 13.3 | 8.52 | 0.0798 | 0.09 | 12.56 | 1
February | 10 | 5PM to 6PM | 27 | 23.7 | 18 | 13.9 | 8.61 | 0.0798 | 0.09 | 12.56 | 1
February | 10 | 6PM to 7PM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
February | 10 | 7PM to 8PM | 25 | 22.5 | 18 | 13.9 | 8.13 | 0.0801 | 0.09 | 12.51 | 1
February | 10 | 8PM to 9PM | 24.1 | 21.9 | 18 | 13.9 | 7.92 | 0.0803 | 0.09 | 12.48 | 1
February | 10 | 9PM to 10PM | 24.1 | 21.9 | 18 | 13.9 | 7.92 | 0.0803 | 0.09 | 12.48 | 1
February | 10 | 10PM to 11PM | 23 | 21.3 | 18 | 13.9 | 7.66 | 0.0804 | 0.09 | 12.46 | 1
February | 10 | 11PM to 12AM | 23 | 21.3 | 18 | 13.9 | 7.66 | 0.0804 | 0.09 | 12.46 | 1
February | 11 | 12AM to 1AM | 21 | 19.7 | 17.1 | 13.3 | 7.09 | 0.0808 | 0.09 | 12.4 | 1
February | 11 | 1AM to 2AM | 21 | 19.7 | 17.1 | 13.3 | 7.09 | 0.0808 | 0.09 | 12.4 | 1
February | 11 | 2AM to 3AM | 21 | 19.1 | 15.1 | 12.1 | 6.9 | 0.0808 | 0.08 | 12.4 | 1
February | 11 | 3AM to 4AM | 19.9 | 18.4 | 15.1 | 12.1 | 6.64 | 0.081 | 0.08 | 12.37 | 1
February | 11 | 4AM to 5AM | 19.9 | 18.4 | 15.1 | 12.1 | 6.64 | 0.081 | 0.08 | 12.37 | 1
February | 11 | 5AM to 6AM | 19 | 17.8 | 15.1 | 12.1 | 6.42 | 0.0811 | 0.08 | 12.35 | 1
February | 11 | 6AM to 7AM | 19 | 17.5 | 14 | 11.5 | 6.33 | 0.0811 | 0.08 | 12.35 | 1
February | 11 | 7AM to 8AM | 19.9 | 18.1 | 14 | 11.5 | 6.54 | 0.081 | 0.08 | 12.37 | 1
February | 11 | 8AM to 9AM | 23 | 20.1 | 14 | 11.5 | 7.28 | 0.0805 | 0.08 | 12.45 | 1
February | 11 | 9AM to 10AM | 28 | 22.8 | 12 | 10.4 | 8.33 | 0.0796 | 0.07 | 12.58 | 1
February | 11 | 10AM to 11AM | 33.1 | 25.9 | 12 | 10.4 | 9.54 | 0.0788 | 0.07 | 12.71 | 1
February | 11 | 11AM to 12PM | 36 | 27.7 | 12.9 | 10.9 | 10.31 | 0.0784 | 0.07 | 12.78 | 1
February | 11 | 12PM to 1PM | 37 | 28.6 | 14 | 11.5 | 10.66 | 0.0782 | 0.08 | 12.81 | 1
February | 11 | 1PM to 2PM | 39 | 29.5 | 12.9 | 10.9 | 11.04 | 0.0779 | 0.07 | 12.86 | 1
February | 11 | 2PM to 3PM | 39.9 | 30.4 | 15.1 | 12.1 | 11.45 | 0.0777 | 0.08 | 12.89 | 1
February | 11 | 3PM to 4PM | 39.9 | 31.1 | 18 | 13.9 | 11.73 | 0.0777 | 0.09 | 12.89 | 1
February | 11 | 4PM to 5PM | 37 | 29.6 | 18 | 13.9 | 11.04 | 0.0782 | 0.09 | 12.82 | 1
February | 11 | 5PM to 6PM | 36 | 29.3 | 19 | 14.7 | 10.89 | 0.0783 | 0.1 | 12.79 | 1
February | 11 | 6PM to 7PM | 34 | 28.4 | 19.9 | 15.3 | 10.52 | 0.0786 | 0.1 | 12.74 | 1
February | 11 | 7PM to 8PM | 33.1 | 28.3 | 21 | 16.2 | 10.42 | 0.0788 | 0.11 | 12.72 | 1
February | 11 | 8PM to 9PM | 32 | 27.7 | 21 | 16.2 | 10.16 | 0.079 | 0.11 | 12.69 | 1
February | 11 | 9PM to 10PM | 32 | 27.7 | 21 | 16.2 | 10.16 | 0.079 | 0.11 | 12.69 | 1
February | 11 | 10PM to 11PM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
February | 11 | 11PM to 12AM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
February | 12 | 12AM to 1AM | 32 | 28.7 | 24.1 | 18.7 | 10.55 | 0.0789 | 0.12 | 12.7 | 1
February | 12 | 1AM to 2AM | 33.1 | 30 | 26.1 | 20.5 | 11.1 | 0.0788 | 0.14 | 12.74 | 1
February | 12 | 2AM to 3AM | 34 | 31.3 | 28 | 22.5 | 11.62 | 0.0786 | 0.15 | 12.76 | 1
February | 12 | 3AM to 4AM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
February | 12 | 4AM to 5AM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
February | 12 | 5AM to 6AM | 34 | 33.2 | 32 | 27.1 | 12.32 | 0.0786 | 0.18 | 12.78 | 1
February | 12 | 6AM to 7AM | 34 | 33.2 | 32 | 27.1 | 12.32 | 0.0786 | 0.18 | 12.78 | 1
February | 12 | 7AM to 8AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
February | 12 | 8AM to 9AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
February | 12 | 9AM to 10AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
February | 12 | 10AM to 11AM | 36 | 34.3 | 32 | 27.1 | 12.8 | 0.0783 | 0.18 | 12.83 | 1
February | 12 | 11AM to 12PM | 37.9 | 35.4 | 32 | 27.1 | 13.28 | 0.0779 | 0.18 | 12.88 | 1
February | 12 | 12PM to 1PM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
February | 12 | 1PM to 2PM | 42.1 | 38.5 | 34 | 29.3 | 14.63 | 0.0773 | 0.2 | 12.99 | 1
February | 12 | 2PM to 3PM | 42.1 | 38.5 | 34 | 29.3 | 14.63 | 0.0773 | 0.2 | 12.99 | 1
February | 12 | 3PM to 4PM | 41 | 35.5 | 28 | 22.5 | 13.32 | 0.0775 | 0.15 | 12.95 | 1
February | 12 | 4PM to 5PM | 39.9 | 34.9 | 28 | 22.5 | 13.06 | 0.0777 | 0.15 | 12.92 | 1
February | 12 | 5PM to 6PM | 36 | 34.3 | 32 | 27.1 | 12.8 | 0.0783 | 0.18 | 12.83 | 1
February | 12 | 6PM to 7PM | 33.1 | 32.1 | 30.9 | 25.8 | 11.9 | 0.0787 | 0.17 | 12.75 | 1
February | 12 | 7PM to 8PM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
February | 12 | 8PM to 9PM | 30.9 | 28.4 | 25 | 19.5 | 10.42 | 0.0791 | 0.13 | 12.68 | 1
February | 12 | 9PM to 10PM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
February | 12 | 10PM to 11PM | 28.9 | 25.9 | 21 | 16.2 | 9.43 | 0.0795 | 0.11 | 12.62 | 1
February | 12 | 11PM to 12AM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
February | 13 | 12AM to 1AM | 27 | 23.5 | 17.1 | 13.3 | 8.52 | 0.0798 | 0.09 | 12.56 | 1
February | 13 | 1AM to 2AM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
February | 13 | 2AM to 3AM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
February | 13 | 3AM to 4AM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
February | 13 | 4AM to 5AM | 26.1 | 22.9 | 17.1 | 13.3 | 8.3 | 0.0799 | 0.09 | 12.53 | 1
February | 13 | 5AM to 6AM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
February | 13 | 6AM to 7AM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
February | 13 | 7AM to 8AM | 25 | 22.5 | 18 | 13.9 | 8.13 | 0.0801 | 0.09 | 12.51 | 1
February | 13 | 8AM to 9AM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
February | 13 | 9AM to 10AM | 28 | 24.7 | 19 | 14.7 | 8.98 | 0.0796 | 0.1 | 12.59 | 1
February | 13 | 10AM to 11AM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
February | 13 | 11AM to 12PM | 35.1 | 29.4 | 21 | 16.2 | 10.9 | 0.0785 | 0.11 | 12.77 | 1
February | 13 | 12PM to 1PM | 39.9 | 32.6 | 21 | 16.2 | 12.07 | 0.0777 | 0.11 | 12.9 | 1
February | 13 | 1PM to 2PM | 43 | 33.8 | 19 | 14.7 | 12.58 | 0.0772 | 0.1 | 12.97 | 1
February | 13 | 2PM to 3PM | 44.1 | 34.6 | 19.9 | 15.3 | 12.94 | 0.0771 | 0.1 | 13 | 1
February | 13 | 3PM to 4PM | 45 | 34.9 | 19 | 14.7 | 13.06 | 0.0769 | 0.1 | 13.02 | 1
February | 13 | 4PM to 5PM | 44.1 | 34.1 | 18 | 13.9 | 12.73 | 0.0771 | 0.09 | 13 | 1
February | 13 | 5PM to 6PM | 42.1 | 32.5 | 16 | 12.7 | 12.05 | 0.0774 | 0.08 | 12.94 | 1
February | 13 | 6PM to 7PM | 39.9 | 30.4 | 15.1 | 12.1 | 11.45 | 0.0777 | 0.08 | 12.89 | 1
February | 13 | 7PM to 8PM | 39 | 29.9 | 15.1 | 12.1 | 11.23 | 0.0779 | 0.08 | 12.86 | 1
February | 13 | 8PM to 9PM | 39 | 30.2 | 16 | 12.7 | 11.32 | 0.0779 | 0.08 | 12.87 | 1
February | 13 | 9PM to 10PM | 37 | 28.8 | 15.1 | 12.1 | 10.76 | 0.0782 | 0.08 | 12.81 | 1
February | 13 | 10PM to 11PM | 35.1 | 27.7 | 15.1 | 12.1 | 10.28 | 0.0785 | 0.08 | 12.76 | 1
February | 13 | 11PM to 12AM | 33.1 | 26.6 | 15.1 | 12.1 | 9.8 | 0.0788 | 0.08 | 12.71 | 1
February | 14 | 12AM to 1AM | 36 | 28.5 | 16 | 12.7 | 10.58 | 0.0783 | 0.08 | 12.79 | 1
February | 14 | 1AM to 2AM | 35.1 | 27.7 | 15.1 | 12.1 | 10.28 | 0.0785 | 0.08 | 12.76 | 1
February | 14 | 2AM to 3AM | 34 | 26.8 | 14 | 11.5 | 9.92 | 0.0787 | 0.08 | 12.73 | 1
February | 14 | 3AM to 4AM | 35.1 | 27.5 | 14 | 11.5 | 10.18 | 0.0785 | 0.08 | 12.76 | 1
February | 14 | 4AM to 5AM | 36 | 28 | 14 | 11.5 | 10.4 | 0.0784 | 0.08 | 12.78 | 1
February | 14 | 5AM to 6AM | 36 | 28 | 14 | 11.5 | 10.4 | 0.0784 | 0.08 | 12.78 | 1
February | 14 | 6AM to 7AM | 35.1 | 27.5 | 14 | 11.5 | 10.18 | 0.0785 | 0.08 | 12.76 | 1
February | 14 | 7AM to 8AM | 37.9 | 29.3 | 15.1 | 12.1 | 10.97 | 0.078 | 0.08 | 12.84 | 1
February | 14 | 8AM to 9AM | 43 | 31.8 | 14 | 11.5 | 12.09 | 0.0773 | 0.08 | 12.96 | 1
February | 14 | 9AM to 10AM | 46 | 34.6 | 15.1 | 12.1 | 12.92 | 0.0768 | 0.08 | 13.04 | 1
February | 14 | 10AM to 11AM | 51.1 | 37.6 | 16 | 12.7 | 14.22 | 0.076 | 0.08 | 13.18 | 1
February | 14 | 11AM to 12PM | 54 | 38.9 | 15.1 | 12.1 | 14.83 | 0.0756 | 0.08 | 13.25 | 0
February | 14 | 12PM to 1PM | 59 | 41.7 | 16 | 12.7 | 16.13 | 0.0749 | 0.08 | 13.38 | 0
February | 14 | 1PM to 2PM | 60.1 | 42.1 | 15.1 | 12.1 | 16.3 | 0.0747 | 0.08 | 13.41 | 0
February | 14 | 2PM to 3PM | 61 | 42.3 | 14 | 11.5 | 16.42 | 0.0746 | 0.08 | 13.43 | 0
February | 14 | 3PM to 4PM | 61 | 42.3 | 14 | 11.5 | 16.42 | 0.0746 | 0.08 | 13.43 | 0
February | 14 | 4PM to 5PM | 60.1 | 41.5 | 12 | 10.4 | 16.04 | 0.0747 | 0.07 | 13.4 | 0
February | 14 | 5PM to 6PM | 57 | 40.1 | 12.9 | 10.9 | 15.38 | 0.0752 | 0.07 | 13.32 | 0
February | 14 | 6PM to 7PM | 54 | 38.7 | 14 | 11.5 | 14.73 | 0.0756 | 0.08 | 13.25 | 0
February | 14 | 7PM to 8PM | 53.1 | 38 | 12.9 | 10.9 | 14.42 | 0.0757 | 0.07 | 13.22 | 0
February | 14 | 8PM to 9PM | 50 | 36.6 | 14 | 11.5 | 13.78 | 0.0762 | 0.08 | 13.15 | 1
February | 14 | 9PM to 10PM | 50 | 36.6 | 14 | 11.5 | 13.78 | 0.0762 | 0.08 | 13.15 | 1
February | 14 | 10PM to 11PM | 50 | 36 | 10.9 | 9.9 | 13.53 | 0.0762 | 0.07 | 13.14 | 1
February | 14 | 11PM to 12AM | 48.9 | 35.4 | 10.9 | 9.9 | 13.27 | 0.0764 | 0.07 | 13.11 | 1
February | 15 | 12AM to 1AM | 48.9 | 35.6 | 12 | 10.4 | 13.35 | 0.0764 | 0.07 | 13.11 | 1
February | 15 | 1AM to 2AM | 48 | 35.5 | 14 | 11.5 | 13.3 | 0.0765 | 0.08 | 13.09 | 1
February | 15 | 2AM to 3AM | 46 | 34.4 | 14 | 11.5 | 12.82 | 0.0768 | 0.08 | 13.04 | 1
February | 15 | 3AM to 4AM | 42.1 | 32.5 | 16 | 12.7 | 12.05 | 0.0774 | 0.08 | 12.94 | 1
February | 15 | 4AM to 5AM | 39 | 30.2 | 16 | 12.7 | 11.32 | 0.0779 | 0.08 | 12.87 | 1
February | 15 | 5AM to 6AM | 37.9 | 30.1 | 18 | 13.9 | 11.25 | 0.078 | 0.09 | 12.84 | 1
February | 15 | 6AM to 7AM | 37.9 | 30.1 | 18 | 13.9 | 11.25 | 0.078 | 0.09 | 12.84 | 1
February | 15 | 7AM to 8AM | 36 | 29 | 18 | 13.9 | 10.78 | 0.0783 | 0.09 | 12.79 | 1
February | 15 | 8AM to 9AM | 43 | 34.6 | 21.9 | 16.9 | 12.92 | 0.0772 | 0.11 | 12.98 | 1
February | 15 | 9AM to 10AM | 44.1 | 35.5 | 23 | 17.8 | 13.32 | 0.0771 | 0.12 | 13.01 | 1
February | 15 | 10AM to 11AM | 46.9 | 37.4 | 24.1 | 18.7 | 14.16 | 0.0766 | 0.12 | 13.09 | 1
February | 15 | 11AM to 12PM | 50 | 39.3 | 25 | 19.5 | 15.02 | 0.0761 | 0.13 | 13.17 | 1
February | 15 | 12PM to 1PM | 52 | 40.4 | 25 | 19.5 | 15.5 | 0.0759 | 0.13 | 13.22 | 0
February | 15 | 1PM to 2PM | 53.1 | 41.3 | 26.1 | 20.5 | 15.92 | 0.0757 | 0.14 | 13.25 | 0
February | 15 | 2PM to 3PM | 54 | 41.4 | 25 | 19.5 | 15.98 | 0.0756 | 0.13 | 13.27 | 0
February | 15 | 3PM to 4PM | 54 | 41.4 | 25 | 19.5 | 15.98 | 0.0756 | 0.13 | 13.27 | 0
February | 15 | 4PM to 5PM | 53.1 | 40.9 | 25 | 19.5 | 15.76 | 0.0757 | 0.13 | 13.25 | 0
February | 15 | 5PM to 6PM | 50 | 39.1 | 24.1 | 18.7 | 14.9 | 0.0762 | 0.12 | 13.17 | 1
February | 15 | 6PM to 7PM | 46.9 | 37.7 | 25 | 19.5 | 14.28 | 0.0766 | 0.13 | 13.09 | 1
February | 15 | 7PM to 8PM | 46 | 36.9 | 24.1 | 18.7 | 13.94 | 0.0767 | 0.12 | 13.06 | 1
February | 15 | 8PM to 9PM | 43 | 35.9 | 26.1 | 20.5 | 13.49 | 0.0772 | 0.14 | 12.99 | 1
February | 15 | 9PM to 10PM | 41 | 34.8 | 26.1 | 20.5 | 13.01 | 0.0775 | 0.14 | 12.94 | 1
February | 15 | 10PM to 11PM | 39.9 | 34.2 | 26.1 | 20.5 | 12.75 | 0.0777 | 0.14 | 12.91 | 1
February | 15 | 11PM to 12AM | 36 | 31.6 | 26.1 | 20.5 | 11.79 | 0.0783 | 0.14 | 12.81 | 1
February | 16 | 12AM to 1AM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
February | 16 | 1AM to 2AM | 32 | 29 | 25 | 19.5 | 10.68 | 0.0789 | 0.13 | 12.7 | 1
February | 16 | 2AM to 3AM | 30.9 | 28.4 | 25 | 19.5 | 10.42 | 0.0791 | 0.13 | 12.68 | 1
February | 16 | 3AM to 4AM | 30 | 27.9 | 25 | 19.5 | 10.2 | 0.0793 | 0.13 | 12.65 | 1
February | 16 | 4AM to 5AM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
February | 16 | 5AM to 6AM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
February | 16 | 6AM to 7AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
February | 16 | 7AM to 8AM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
February | 16 | 8AM to 9AM | 39.9 | 36 | 30.9 | 25.8 | 13.55 | 0.0776 | 0.17 | 12.93 | 1
February | 16 | 9AM to 10AM | 45 | 39.6 | 33.1 | 28.3 | 15.16 | 0.0768 | 0.19 | 13.07 | 1
February | 16 | 10AM to 11AM | 46.9 | 39.8 | 30.9 | 25.8 | 15.25 | 0.0766 | 0.17 | 13.11 | 1
February | 16 | 11AM to 12PM | 51.1 | 42.4 | 32 | 27.1 | 16.45 | 0.0759 | 0.18 | 13.22 | 1
February | 16 | 12PM to 1PM | 53.1 | 43.7 | 33.1 | 28.3 | 17.12 | 0.0756 | 0.19 | 13.27 | 0
February | 16 | 1PM to 2PM | 55.9 | 44.7 | 32 | 27.1 | 17.63 | 0.0752 | 0.18 | 13.35 | 0
February | 16 | 2PM to 3PM | 57 | 45.3 | 32 | 27.1 | 17.89 | 0.0751 | 0.18 | 13.37 | 0
February | 16 | 3PM to 4PM | 57.9 | 45.7 | 32 | 27.1 | 18.11 | 0.0749 | 0.18 | 13.4 | 0
February | 16 | 4PM to 5PM | 57 | 45.6 | 33.1 | 28.3 | 18.08 | 0.0751 | 0.19 | 13.38 | 0
February | 16 | 5PM to 6PM | 54 | 43.8 | 32 | 27.1 | 17.15 | 0.0755 | 0.18 | 13.29 | 0
February | 16 | 6PM to 7PM | 53.1 | 43.7 | 33.1 | 28.3 | 17.12 | 0.0756 | 0.19 | 13.27 | 0
February | 16 | 7PM to 8PM | 52 | 42.8 | 32 | 27.1 | 16.67 | 0.0758 | 0.18 | 13.24 | 0
February | 16 | 8PM to 9PM | 51.1 | 41.2 | 28.9 | 23.5 | 15.9 | 0.076 | 0.16 | 13.21 | 1
February | 16 | 9PM to 10PM | 51.1 | 41.9 | 30.9 | 25.8 | 16.25 | 0.0759 | 0.17 | 13.22 | 1
February | 16 | 10PM to 11PM | 50 | 41.8 | 32 | 27.1 | 16.19 | 0.0761 | 0.18 | 13.19 | 1
February | 16 | 11PM to 12AM | 48.9 | 41.3 | 32 | 27.1 | 15.93 | 0.0763 | 0.18 | 13.16 | 1
February | 17 | 12AM to 1AM | 48 | 40.4 | 30.9 | 25.8 | 15.51 | 0.0764 | 0.17 | 13.14 | 1
February | 17 | 1AM to 2AM | 46.9 | 39.8 | 30.9 | 25.8 | 15.25 | 0.0766 | 0.17 | 13.11 | 1
February | 17 | 2AM to 3AM | 46 | 39.8 | 32 | 27.1 | 15.24 | 0.0767 | 0.18 | 13.09 | 1
February | 17 | 3AM to 4AM | 46 | 39.8 | 32 | 27.1 | 15.24 | 0.0767 | 0.18 | 13.09 | 1
February | 17 | 4AM to 5AM | 45 | 39.2 | 32 | 27.1 | 14.98 | 0.0769 | 0.18 | 13.06 | 1
February | 17 | 5AM to 6AM | 43 | 38.2 | 32 | 27.1 | 14.5 | 0.0772 | 0.18 | 13.01 | 1
February | 17 | 6AM to 7AM | 44.1 | 39.2 | 33.1 | 28.3 | 14.94 | 0.077 | 0.19 | 13.04 | 1
February | 17 | 7AM to 8AM | 46 | 40.5 | 34 | 29.3 | 15.58 | 0.0767 | 0.2 | 13.1 | 1
February | 17 | 8AM to 9AM | 48.9 | 41.7 | 33.1 | 28.3 | 16.12 | 0.0763 | 0.19 | 13.17 | 1
February | 17 | 9AM to 10AM | 55 | 45 | 34 | 29.3 | 17.76 | 0.0753 | 0.2 | 13.33 | 0
February | 17 | 10AM to 11AM | 59 | 46.6 | 33.1 | 28.3 | 18.56 | 0.0748 | 0.19 | 13.43 | 0
February | 17 | 11AM to 12PM | 62.1 | 47.6 | 32 | 27.1 | 19.11 | 0.0743 | 0.18 | 13.5 | 0
February | 17 | 12PM to 1PM | 64 | 48.8 | 33.1 | 28.3 | 19.77 | 0.074 | 0.19 | 13.56 | 0
February | 17 | 1PM to 2PM | 66 | 48.7 | 30 | 24.7 | 19.7 | 0.0738 | 0.16 | 13.6 | 0
February | 17 | 2PM to 3PM | 66 | 48.7 | 30 | 24.7 | 19.7 | 0.0738 | 0.16 | 13.6 | 0
February | 17 | 3PM to 4PM | 66 | 48.4 | 28.9 | 23.5 | 19.51 | 0.0738 | 0.16 | 13.6 | 0
February | 17 | 4PM to 5PM | 64 | 47.8 | 30 | 24.7 | 19.22 | 0.0741 | 0.16 | 13.55 | 0
February | 17 | 5PM to 6PM | 61 | 46.7 | 30.9 | 25.8 | 18.64 | 0.0745 | 0.17 | 13.47 | 0
February | 17 | 6PM to 7PM | 57 | 45.9 | 34 | 29.3 | 18.24 | 0.075 | 0.2 | 13.38 | 0
February | 17 | 7PM to 8PM | 55.9 | 44.7 | 32 | 27.1 | 17.63 | 0.0752 | 0.18 | 13.35 | 0
February | 17 | 8PM to 9PM | 54 | 43.8 | 32 | 27.1 | 17.15 | 0.0755 | 0.18 | 13.29 | 0
February | 17 | 9PM to 10PM | 52 | 42.8 | 32 | 27.1 | 16.67 | 0.0758 | 0.18 | 13.24 | 0
February | 17 | 10PM to 11PM | 51.1 | 42.7 | 33.1 | 28.3 | 16.64 | 0.0759 | 0.19 | 13.22 | 1
February | 17 | 11PM to 12AM | 51.1 | 43.1 | 34 | 29.3 | 16.8 | 0.0759 | 0.2 | 13.23 | 1
February | 18 | 12AM to 1AM | 48.9 | 42.4 | 35.1 | 30.6 | 16.48 | 0.0762 | 0.2 | 13.17 | 1
February | 18 | 1AM to 2AM | 48 | 42 | 35.1 | 30.6 | 16.26 | 0.0764 | 0.2 | 13.15 | 1
February | 18 | 2AM to 3AM | 46 | 41 | 35.1 | 30.6 | 15.79 | 0.0767 | 0.2 | 13.1 | 1
February | 18 | 3AM to 4AM | 45 | 40.4 | 35.1 | 30.6 | 15.52 | 0.0768 | 0.2 | 13.07 | 1
February | 18 | 4AM to 5AM | 45 | 40.4 | 35.1 | 30.6 | 15.52 | 0.0768 | 0.2 | 13.07 | 1
February | 18 | 5AM to 6AM | 45 | 40.4 | 35.1 | 30.6 | 15.52 | 0.0768 | 0.2 | 13.07 | 1
February | 18 | 6AM to 7AM | 45 | 40.4 | 35.1 | 30.6 | 15.52 | 0.0768 | 0.2 | 13.07 | 1
February | 18 | 7AM to 8AM | 46 | 41 | 35.1 | 30.6 | 15.79 | 0.0767 | 0.2 | 13.1 | 1
February | 18 | 8AM to 9AM | 53.1 | 44 | 34 | 29.3 | 17.28 | 0.0756 | 0.2 | 13.28 | 0
February | 18 | 9AM to 10AM | 55 | 45.4 | 35.1 | 30.6 | 17.96 | 0.0753 | 0.2 | 13.33 | 0
February | 18 | 10AM to 11AM | 60.1 | 47.4 | 34 | 29.3 | 18.98 | 0.0746 | 0.2 | 13.46 | 0
February | 18 | 11AM to 12PM | 62.1 | 48.3 | 34 | 29.3 | 19.46 | 0.0743 | 0.2 | 13.51 | 0
February | 18 | 12PM to 1PM | 66 | 50 | 34 | 29.3 | 20.42 | 0.0738 | 0.2 | 13.61 | 0
February | 18 | 1PM to 2PM | 68 | 50.9 | 34 | 29.3 | 20.9 | 0.0735 | 0.2 | 13.66 | 0
February | 18 | 2PM to 3PM | 66 | 50.4 | 35.1 | 30.6 | 20.62 | 0.0738 | 0.2 | 13.62 | 0
February | 18 | 3PM to 4PM | 68 | 50.9 | 34 | 29.3 | 20.9 | 0.0735 | 0.2 | 13.66 | 0
February | 18 | 4PM to 5PM | 66 | 51.1 | 37 | 33.2 | 21.01 | 0.0737 | 0.22 | 13.63 | 0
February | 18 | 5PM to 6PM | 64 | 50.9 | 39 | 35.9 | 20.95 | 0.074 | 0.24 | 13.58 | 0
February | 18 | 6PM to 7PM | 62.1 | 51.7 | 43 | 41.9 | 21.41 | 0.0742 | 0.28 | 13.55 | 0
February | 18 | 7PM to 8PM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
February | 18 | 8PM to 9PM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
February | 18 | 9PM to 10PM | 59 | 52.2 | 46.9 | 48.8 | 21.73 | 0.0746 | 0.32 | 13.49 | 0
February | 18 | 10PM to 11PM | 57.9 | 52.3 | 48 | 50.8 | 21.79 | 0.0748 | 0.34 | 13.47 | 0
February | 18 | 11PM to 12AM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
February | 19 | 12AM to 1AM | 57.9 | 52.8 | 48.9 | 52.6 | 22.06 | 0.0748 | 0.35 | 13.47 | 0
February | 19 | 1AM to 2AM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
February | 19 | 2AM to 3AM | 60.1 | 54.2 | 50 | 54.7 | 22.93 | 0.0744 | 0.36 | 13.54 | 0
February | 19 | 3AM to 4AM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
February | 19 | 4AM to 5AM | 57.9 | 53.4 | 50 | 54.7 | 22.4 | 0.0748 | 0.36 | 13.48 | 0
February | 19 | 5AM to 6AM | 57.9 | 53.4 | 50 | 54.7 | 22.4 | 0.0748 | 0.36 | 13.48 | 0
February | 19 | 6AM to 7AM | 57 | 53 | 50 | 54.7 | 22.18 | 0.0749 | 0.36 | 13.46 | 0
February | 19 | 7AM to 8AM | 59 | 54.4 | 51.1 | 57 | 23.02 | 0.0746 | 0.38 | 13.52 | 0
February | 19 | 8AM to 9AM | 61 | 55.6 | 52 | 59 | 23.8 | 0.0743 | 0.39 | 13.57 | 0
February | 19 | 9AM to 10AM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
February | 19 | 10AM to 11AM | 68 | 58.3 | 52 | 59 | 25.52 | 0.0733 | 0.39 | 13.76 | 0
February | 19 | 11AM to 12PM | 68 | 58.9 | 53.1 | 61.4 | 25.89 | 0.0733 | 0.41 | 13.76 | 0
February | 19 | 12PM to 1PM | 64.9 | 58.2 | 54 | 63.5 | 25.47 | 0.0737 | 0.42 | 13.69 | 0
February | 19 | 1PM to 2PM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
February | 19 | 2PM to 3PM | 64 | 57.4 | 53.1 | 61.4 | 24.93 | 0.0738 | 0.41 | 13.66 | 0
February | 19 | 3PM to 4PM | 63 | 57.5 | 54 | 63.5 | 24.99 | 0.074 | 0.42 | 13.64 | 0
February | 19 | 4PM to 5PM | 62.1 | 57.1 | 54 | 63.5 | 24.77 | 0.0741 | 0.42 | 13.62 | 0
February | 19 | 5PM to 6PM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
February | 19 | 6PM to 7PM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
February | 19 | 7PM to 8PM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
February | 19 | 8PM to 9PM | 63 | 57.5 | 54 | 63.5 | 24.99 | 0.074 | 0.42 | 13.64 | 0
February | 19 | 9PM to 10PM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
February | 19 | 10PM to 11PM | 62.1 | 58.3 | 55.9 | 68.3 | 25.52 | 0.0741 | 0.45 | 13.63 | 0
February | 19 | 11PM to 12AM | 61 | 58.5 | 57 | 71.1 | 25.69 | 0.0742 | 0.47 | 13.61 | 0
February | 20 | 12AM to 1AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
February | 20 | 1AM to 2AM | 55.9 | 54.2 | 53.1 | 61.4 | 22.95 | 0.075 | 0.41 | 13.45 | 0
February | 20 | 2AM to 3AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
February | 20 | 3AM to 4AM | 55.9 | 53.6 | 52 | 59 | 22.58 | 0.075 | 0.39 | 13.44 | 0
February | 20 | 4AM to 5AM | 55.9 | 53.6 | 52 | 59 | 22.58 | 0.075 | 0.39 | 13.44 | 0
February | 20 | 5AM to 6AM | 55 | 53.3 | 52 | 59 | 22.36 | 0.0751 | 0.39 | 13.42 | 0
February | 20 | 6AM to 7AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
February | 20 | 7AM to 8AM | 53.1 | 52.4 | 52 | 59 | 21.87 | 0.0754 | 0.39 | 13.37 | 0
February | 20 | 8AM to 9AM | 53.1 | 50.7 | 48.9 | 52.6 | 20.88 | 0.0755 | 0.35 | 13.35 | 0
February | 20 | 9AM to 10AM | 52 | 49.8 | 48 | 50.8 | 20.34 | 0.0756 | 0.34 | 13.31 | 0
February | 20 | 10AM to 11AM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
February | 20 | 11AM to 12PM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
February | 20 | 12PM to 1PM | 48 | 46.4 | 45 | 45.2 | 18.51 | 0.0763 | 0.3 | 13.19 | 1
February | 20 | 1PM to 2PM | 48 | 46 | 44.1 | 43.6 | 18.28 | 0.0763 | 0.29 | 13.19 | 1
February | 20 | 2PM to 3PM | 48 | 46 | 44.1 | 43.6 | 18.28 | 0.0763 | 0.29 | 13.19 | 1
February | 20 | 3PM to 4PM | 48 | 46 | 44.1 | 43.6 | 18.28 | 0.0763 | 0.29 | 13.19 | 1
February | 20 | 4PM to 5PM | 46.9 | 44.9 | 43 | 41.9 | 17.74 | 0.0765 | 0.28 | 13.16 | 1
February | 20 | 5PM to 6PM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
February | 20 | 6PM to 7PM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
February | 20 | 7PM to 8PM | 44.1 | 41.6 | 39 | 35.9 | 16.11 | 0.0769 | 0.24 | 13.06 | 1
February | 20 | 8PM to 9PM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
February | 20 | 9PM to 10PM | 42.1 | 40.6 | 39 | 35.9 | 15.63 | 0.0772 | 0.24 | 13.01 | 1
February | 20 | 10PM to 11PM | 41 | 39.6 | 37.9 | 34.4 | 15.14 | 0.0774 | 0.23 | 12.98 | 1
February | 20 | 11PM to 12AM | 39 | 38.5 | 37.9 | 34.4 | 14.66 | 0.0777 | 0.23 | 12.93 | 1
February | 21 | 12AM to 1AM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
February | 21 | 1AM to 2AM | 37 | 36.6 | 36 | 31.8 | 13.78 | 0.0781 | 0.21 | 12.87 | 1
February | 21 | 2AM to 3AM | 37 | 36.2 | 35.1 | 30.6 | 13.61 | 0.0781 | 0.2 | 12.87 | 1
February | 21 | 3AM to 4AM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 21 | 4AM to 5AM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 21 | 5AM to 6AM | 34 | 33.2 | 32 | 27.1 | 12.32 | 0.0786 | 0.18 | 12.78 | 1
February | 21 | 6AM to 7AM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
February | 21 | 7AM to 8AM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
February | 21 | 8AM to 9AM | 34 | 30.5 | 26.1 | 20.5 | 11.31 | 0.0786 | 0.14 | 12.76 | 1
February | 21 | 9AM to 10AM | 36 | 32.6 | 28 | 22.5 | 12.1 | 0.0783 | 0.15 | 12.82 | 1
February | 21 | 10AM to 11AM | 37.9 | 33.8 | 28 | 22.5 | 12.58 | 0.078 | 0.15 | 12.87 | 1
February | 21 | 11AM to 12PM | 41 | 35.8 | 28.9 | 23.5 | 13.47 | 0.0775 | 0.16 | 12.95 | 1
February | 21 | 12PM to 1PM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
February | 21 | 1PM to 2PM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
February | 21 | 2PM to 3PM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
February | 21 | 3PM to 4PM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
February | 21 | 4PM to 5PM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
February | 21 | 5PM to 6PM | 39.9 | 35.7 | 30 | 24.7 | 13.39 | 0.0776 | 0.16 | 12.92 | 1
February | 21 | 6PM to 7PM | 39 | 35.2 | 30 | 24.7 | 13.17 | 0.0778 | 0.16 | 12.9 | 1
February | 21 | 7PM to 8PM | 37.9 | 34.6 | 30 | 24.7 | 12.91 | 0.078 | 0.16 | 12.87 | 1
February | 21 | 8PM to 9PM | 37.9 | 34.6 | 30 | 24.7 | 12.91 | 0.078 | 0.16 | 12.87 | 1
February | 21 | 9PM to 10PM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
February | 21 | 10PM to 11PM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
February | 21 | 11PM to 12AM | 37 | 34.4 | 30.9 | 25.8 | 12.86 | 0.0781 | 0.17 | 12.85 | 1
February | 22 | 12AM to 1AM | 37 | 34.4 | 30.9 | 25.8 | 12.86 | 0.0781 | 0.17 | 12.85 | 1
February | 22 | 1AM to 2AM | 37.9 | 35.4 | 32 | 27.1 | 13.28 | 0.0779 | 0.18 | 12.88 | 1
February | 22 | 2AM to 3AM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
February | 22 | 3AM to 4AM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
February | 22 | 4AM to 5AM | 36 | 34.3 | 32 | 27.1 | 12.8 | 0.0783 | 0.18 | 12.83 | 1
February | 22 | 5AM to 6AM | 35.1 | 33.3 | 30.9 | 25.8 | 12.38 | 0.0784 | 0.17 | 12.8 | 1
February | 22 | 6AM to 7AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
February | 22 | 7AM to 8AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
February | 22 | 8AM to 9AM | 35.1 | 34.2 | 33.1 | 28.3 | 12.77 | 0.0784 | 0.19 | 12.81 | 1
February | 22 | 9AM to 10AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
February | 22 | 10AM to 11AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
February | 22 | 11AM to 12PM | 35.1 | 34.2 | 33.1 | 28.3 | 12.77 | 0.0784 | 0.19 | 12.81 | 1
February | 22 | 12PM to 1PM | 35.1 | 34.2 | 33.1 | 28.3 | 12.77 | 0.0784 | 0.19 | 12.81 | 1
February | 22 | 1PM to 2PM | 36 | 34.7 | 33.1 | 28.3 | 12.99 | 0.0782 | 0.19 | 12.83 | 1
February | 22 | 2PM to 3PM | 36 | 34.3 | 32 | 27.1 | 12.8 | 0.0783 | 0.18 | 12.83 | 1
February | 22 | 3PM to 4PM | 36 | 34.3 | 32 | 27.1 | 12.8 | 0.0783 | 0.18 | 12.83 | 1
February | 22 | 4PM to 5PM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 22 | 5PM to 6PM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 22 | 6PM to 7PM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 22 | 7PM to 8PM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 22 | 8PM to 9PM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 22 | 9PM to 10PM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 22 | 10PM to 11PM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
February | 22 | 11PM to 12AM | 35.1 | 34.6 | 34 | 29.3 | 12.93 | 0.0784 | 0.2 | 12.81 | 1
February | 23 | 12AM to 1AM | 35.1 | 34.6 | 34 | 29.3 | 12.93 | 0.0784 | 0.2 | 12.81 | 1
February | 23 | 1AM to 2AM | 34 | 33.6 | 33.1 | 28.3 | 12.51 | 0.0786 | 0.19 | 12.78 | 1
February | 23 | 2AM to 3AM | 34 | 33.6 | 33.1 | 28.3 | 12.51 | 0.0786 | 0.19 | 12.78 | 1
February | 23 | 3AM to 4AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
February | 23 | 4AM to 5AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
February | 23 | 5AM to 6AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
February | 23 | 6AM to 7AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
February | 23 | 7AM to 8AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
February | 23 | 8AM to 9AM | 34 | 33.2 | 32 | 27.1 | 12.32 | 0.0786 | 0.18 | 12.78 | 1
February | 23 | 9AM to 10AM | 33.1 | 32.1 | 30.9 | 25.8 | 11.9 | 0.0787 | 0.17 | 12.75 | 1
February | 23 | 10AM to 11AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
February | 23 | 11AM to 12PM | 33.1 | 30.8 | 28 | 22.5 | 11.4 | 0.0787 | 0.15 | 12.74 | 1
February | 23 | 12PM to 1PM | 33.1 | 30 | 26.1 | 20.5 | 11.1 | 0.0788 | 0.14 | 12.74 | 1
February | 23 | 1PM to 2PM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
February | 23 | 2PM to 3PM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
February | 23 | 3PM to 4PM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
February | 23 | 4PM to 5PM | 28.9 | 26.2 | 21.9 | 16.9 | 9.54 | 0.0794 | 0.11 | 12.62 | 1
February | 23 | 5PM to 6PM | 28 | 26.4 | 24.1 | 18.7 | 9.6 | 0.0796 | 0.12 | 12.6 | 1
February | 23 | 6PM to 7PM | 27 | 25.8 | 24.1 | 18.7 | 9.34 | 0.0798 | 0.12 | 12.57 | 1
February | 23 | 7PM to 8PM | 25 | 23.1 | 19.9 | 15.3 | 8.35 | 0.0801 | 0.1 | 12.51 | 1
February | 23 | 8PM to 9PM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
February | 23 | 9PM to 10PM | 23 | 21.3 | 18 | 13.9 | 7.66 | 0.0804 | 0.09 | 12.46 | 1
February | 23 | 10PM to 11PM | 21.9 | 20 | 16 | 12.7 | 7.2 | 0.0806 | 0.08 | 12.42 | 1
February | 23 | 11PM to 12AM | 21 | 19.1 | 15.1 | 12.1 | 6.9 | 0.0808 | 0.08 | 12.4 | 1
February | 24 | 12AM to 1AM | 21 | 19.4 | 16 | 12.7 | 6.98 | 0.0808 | 0.08 | 12.4 | 1
February | 24 | 1AM to 2AM | 19.9 | 17.6 | 12 | 10.4 | 6.38 | 0.081 | 0.07 | 12.37 | 1
February | 24 | 2AM to 3AM | 19 | 17.2 | 12.9 | 10.9 | 6.23 | 0.0811 | 0.07 | 12.34 | 1
February | 24 | 3AM to 4AM | 18 | 16.2 | 12 | 10.4 | 5.9 | 0.0813 | 0.07 | 12.32 | 1
February | 24 | 4AM to 5AM | 18 | 15.9 | 10.9 | 9.9 | 5.82 | 0.0813 | 0.07 | 12.31 | 1
February | 24 | 5AM to 6AM | 17.1 | 14.8 | 9 | 8.9 | 5.46 | 0.0815 | 0.06 | 12.29 | 1
February | 24 | 6AM to 7AM | 16 | 14.3 | 10 | 9.4 | 5.27 | 0.0817 | 0.06 | 12.26 | 1
February | 24 | 7AM to 8AM | 18 | 16.2 | 12 | 10.4 | 5.9 | 0.0813 | 0.07 | 12.32 | 1
February | 24 | 8AM to 9AM | 19.9 | 17.3 | 10.9 | 9.9 | 6.29 | 0.081 | 0.07 | 12.37 | 1
February | 24 | 9AM to 10AM | 21.9 | 18.9 | 12 | 10.4 | 6.85 | 0.0806 | 0.07 | 12.42 | 1
February | 24 | 10AM to 11AM | 24.1 | 20.8 | 14 | 11.5 | 7.54 | 0.0803 | 0.08 | 12.48 | 1
February | 24 | 11AM to 12PM | 25 | 21.7 | 15.1 | 12.1 | 7.85 | 0.0801 | 0.08 | 12.5 | 1
February | 24 | 12PM to 1PM | 28 | 23.8 | 16 | 12.7 | 8.67 | 0.0796 | 0.08 | 12.58 | 1
February | 24 | 1PM to 2PM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
February | 24 | 2PM to 3PM | 30 | 25.3 | 17.1 | 13.3 | 9.25 | 0.0793 | 0.09 | 12.64 | 1
February | 24 | 3PM to 4PM | 30.9 | 26.1 | 18 | 13.9 | 9.56 | 0.0791 | 0.09 | 12.66 | 1
February | 24 | 4PM to 5PM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
February | 24 | 5PM to 6PM | 30.9 | 26.7 | 19.9 | 15.3 | 9.78 | 0.0791 | 0.1 | 12.66 | 1
February | 24 | 6PM to 7PM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
February | 24 | 7PM to 8PM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
February | 24 | 8PM to 9PM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
February | 24 | 9PM to 10PM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
February | 24 | 10PM to 11PM | 30 | 27.9 | 25 | 19.5 | 10.2 | 0.0793 | 0.13 | 12.65 | 1
February | 24 | 11PM to 12AM | 30 | 28.3 | 26.1 | 20.5 | 10.36 | 0.0792 | 0.14 | 12.66 | 1
February | 25 | 12AM to 1AM | 30.9 | 29.2 | 27 | 21.4 | 10.71 | 0.0791 | 0.14 | 12.68 | 1
February | 25 | 1AM to 2AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
February | 25 | 2AM to 3AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
February | 25 | 3AM to 4AM | 33.1 | 31.2 | 28.9 | 23.5 | 11.55 | 0.0787 | 0.16 | 12.74 | 1
February | 25 | 4AM to 5AM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
February | 25 | 5AM to 6AM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
February | 25 | 6AM to 7AM | 35.1 | 33.3 | 30.9 | 25.8 | 12.38 | 0.0784 | 0.17 | 12.8 | 1
February | 25 | 7AM to 8AM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
February | 25 | 8AM to 9AM | 37.9 | 34.9 | 30.9 | 25.8 | 13.08 | 0.0779 | 0.17 | 12.88 | 1
February | 25 | 9AM to 10AM | 34 | 31.3 | 28 | 22.5 | 11.62 | 0.0786 | 0.15 | 12.76 | 1
February | 25 | 10AM to 11AM | 28.9 | 25.5 | 19.9 | 15.3 | 9.3 | 0.0795 | 0.1 | 12.61 | 1
February | 25 | 11AM to 12PM | 30 | 26.2 | 19.9 | 15.3 | 9.56 | 0.0793 | 0.1 | 12.64 | 1
February | 25 | 12PM to 1PM | 24.1 | 21.1 | 15.1 | 12.1 | 7.63 | 0.0803 | 0.08 | 12.48 | 1
February | 25 | 1PM to 2PM | 24.1 | 19.6 | 9 | 8.9 | 7.15 | 0.0803 | 0.06 | 12.47 | 1
February | 25 | 2PM to 3PM | 23 | 18.3 | 6.1 | 7.7 | 6.7 | 0.0805 | 0.05 | 12.44 | 1
February | 25 | 3PM to 4PM | 19.9 | 15.5 | 1.9 | 6.2 | 5.74 | 0.081 | 0.04 | 12.35 | 1
February | 25 | 4PM to 5PM | 18 | 14.1 | 1.9 | 6.2 | 5.26 | 0.0813 | 0.04 | 12.3 | 1
February | 25 | 5PM to 6PM | 17.1 | 13.5 | 1.9 | 6.2 | 5.05 | 0.0815 | 0.04 | 12.28 | 1
February | 25 | 6PM to 7PM | 16 | 12.7 | 1.9 | 6.2 | 4.79 | 0.0817 | 0.04 | 12.25 | 1
February | 25 | 7PM to 8PM | 16 | 12.9 | 3 | 6.6 | 4.84 | 0.0817 | 0.04 | 12.25 | 1
February | 25 | 8PM to 9PM | 16 | 13 | 3.9 | 6.9 | 4.89 | 0.0817 | 0.05 | 12.25 | 1
February | 25 | 9PM to 10PM | 16 | 13.2 | 5 | 7.3 | 4.95 | 0.0817 | 0.05 | 12.26 | 1
February | 25 | 10PM to 11PM | 16 | 13.2 | 5 | 7.3 | 4.95 | 0.0817 | 0.05 | 12.26 | 1
February | 25 | 11PM to 12AM | 16 | 13.5 | 6.1 | 7.7 | 5.01 | 0.0817 | 0.05 | 12.26 | 1
February | 26 | 12AM to 1AM | 15.1 | 13 | 7 | 8.1 | 4.85 | 0.0818 | 0.05 | 12.23 | 1
February | 26 | 1AM to 2AM | 16 | 13.9 | 8.1 | 8.5 | 5.14 | 0.0817 | 0.06 | 12.26 | 1
February | 26 | 2AM to 3AM | 16 | 13.9 | 8.1 | 8.5 | 5.14 | 0.0817 | 0.06 | 12.26 | 1
February | 26 | 3AM to 4AM | 15.1 | 13.2 | 8.1 | 8.5 | 4.92 | 0.0818 | 0.06 | 12.24 | 1
February | 26 | 4AM to 5AM | 15.1 | 13.4 | 9 | 8.9 | 4.98 | 0.0818 | 0.06 | 12.24 | 1
February | 26 | 5AM to 6AM | 14 | 12.7 | 9 | 8.9 | 4.72 | 0.082 | 0.06 | 12.21 | 1
February | 26 | 6AM to 7AM | 15.1 | 13.7 | 10 | 9.4 | 5.06 | 0.0818 | 0.06 | 12.24 | 1
February | 26 | 7AM to 8AM | 16 | 14.6 | 10.9 | 9.9 | 5.34 | 0.0817 | 0.07 | 12.26 | 1
February | 26 | 8AM to 9AM | 17.1 | 15.1 | 10 | 9.4 | 5.53 | 0.0815 | 0.06 | 12.29 | 1
February | 26 | 9AM to 10AM | 19.9 | 17.3 | 10.9 | 9.9 | 6.29 | 0.081 | 0.07 | 12.37 | 1
February | 26 | 10AM to 11AM | 23 | 19.3 | 10.9 | 9.9 | 7.03 | 0.0805 | 0.07 | 12.44 | 1
February | 26 | 11AM to 12PM | 25 | 20.9 | 12 | 10.4 | 7.59 | 0.0801 | 0.07 | 12.5 | 1
February | 26 | 12PM to 1PM | 27 | 22.1 | 12 | 10.4 | 8.07 | 0.0798 | 0.07 | 12.55 | 1
February | 26 | 1PM to 2PM | 27 | 22.1 | 12 | 10.4 | 8.07 | 0.0798 | 0.07 | 12.55 | 1
February | 26 | 2PM to 3PM | 28.9 | 23.6 | 12.9 | 10.9 | 8.62 | 0.0795 | 0.07 | 12.6 | 1
February | 26 | 3PM to 4PM | 28 | 23 | 12.9 | 10.9 | 8.4 | 0.0796 | 0.07 | 12.58 | 1
February | 26 | 4PM to 5PM | 28 | 23 | 12.9 | 10.9 | 8.4 | 0.0796 | 0.07 | 12.58 | 1
February | 26 | 5PM to 6PM | 26.1 | 21.8 | 12.9 | 10.9 | 7.92 | 0.08 | 0.07 | 12.53 | 1
February | 26 | 6PM to 7PM | 24.1 | 20.8 | 14 | 11.5 | 7.54 | 0.0803 | 0.08 | 12.48 | 1
February | 26 | 7PM to 8PM | 23 | 20.1 | 14 | 11.5 | 7.28 | 0.0805 | 0.08 | 12.45 | 1
February | 26 | 8PM to 9PM | 21.9 | 19.4 | 14 | 11.5 | 7.02 | 0.0806 | 0.08 | 12.42 | 1
February | 26 | 9PM to 10PM | 21 | 18.8 | 14 | 11.5 | 6.8 | 0.0808 | 0.08 | 12.4 | 1
February | 26 | 10PM to 11PM | 21 | 18.8 | 14 | 11.5 | 6.8 | 0.0808 | 0.08 | 12.4 | 1
February | 26 | 11PM to 12AM | 19.9 | 18.1 | 14 | 11.5 | 6.54 | 0.081 | 0.08 | 12.37 | 1
February | 27 | 12AM to 1AM | 19 | 17.5 | 14 | 11.5 | 6.33 | 0.0811 | 0.08 | 12.35 | 1
February | 27 | 1AM to 2AM | 19 | 17.5 | 14 | 11.5 | 6.33 | 0.0811 | 0.08 | 12.35 | 1
February | 27 | 2AM to 3AM | 18 | 16.8 | 14 | 11.5 | 6.07 | 0.0813 | 0.08 | 12.32 | 1
February | 27 | 3AM to 4AM | 18 | 16.8 | 14 | 11.5 | 6.07 | 0.0813 | 0.08 | 12.32 | 1
February | 27 | 4AM to 5AM | 18 | 16.8 | 14 | 11.5 | 6.07 | 0.0813 | 0.08 | 12.32 | 1
February | 27 | 5AM to 6AM | 17.1 | 16.1 | 14 | 11.5 | 5.85 | 0.0815 | 0.08 | 12.3 | 1
February | 27 | 6AM to 7AM | 17.1 | 15.6 | 12 | 10.4 | 5.68 | 0.0815 | 0.07 | 12.29 | 1
February | 27 | 7AM to 8AM | 19 | 16.5 | 10 | 9.4 | 6.01 | 0.0811 | 0.06 | 12.34 | 1
February | 27 | 8AM to 9AM | 21.9 | 19.1 | 12.9 | 10.9 | 6.93 | 0.0806 | 0.07 | 12.42 | 1
February | 27 | 9AM to 10AM | 25 | 21.4 | 14 | 11.5 | 7.76 | 0.0801 | 0.08 | 12.5 | 1
February | 27 | 10AM to 11AM | 28 | 23.6 | 15.1 | 12.1 | 8.59 | 0.0796 | 0.08 | 12.58 | 1
February | 27 | 11AM to 12PM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
February | 27 | 12PM to 1PM | 32 | 26.2 | 16 | 12.7 | 9.63 | 0.079 | 0.08 | 12.68 | 1
February | 27 | 1PM to 2PM | 32 | 26.5 | 17.1 | 13.3 | 9.73 | 0.079 | 0.09 | 12.69 | 1
February | 27 | 2PM to 3PM | 34 | 27.6 | 17.1 | 13.3 | 10.21 | 0.0787 | 0.09 | 12.74 | 1
February | 27 | 3PM to 4PM | 33.1 | 27.1 | 17.1 | 13.3 | 9.99 | 0.0788 | 0.09 | 12.71 | 1
February | 27 | 4PM to 5PM | 33.1 | 27.1 | 17.1 | 13.3 | 9.99 | 0.0788 | 0.09 | 12.71 | 1
February | 27 | 5PM to 6PM | 32 | 26.5 | 17.1 | 13.3 | 9.73 | 0.079 | 0.09 | 12.69 | 1
February | 27 | 6PM to 7PM | 30.9 | 26.1 | 18 | 13.9 | 9.56 | 0.0791 | 0.09 | 12.66 | 1
February | 27 | 7PM to 8PM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
February | 27 | 8PM to 9PM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
February | 27 | 9PM to 10PM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
February | 27 | 10PM to 11PM | 28.9 | 24.9 | 18 | 13.9 | 9.09 | 0.0795 | 0.09 | 12.61 | 1
February | 27 | 11PM to 12AM | 28.9 | 25.3 | 19 | 14.7 | 9.2 | 0.0795 | 0.1 | 12.61 | 1
February | 28 | 12AM to 1AM | 28 | 24.7 | 19 | 14.7 | 8.98 | 0.0796 | 0.1 | 12.59 | 1
February | 28 | 1AM to 2AM | 28 | 24.7 | 19 | 14.7 | 8.98 | 0.0796 | 0.1 | 12.59 | 1
February | 28 | 2AM to 3AM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
February | 28 | 3AM to 4AM | 28 | 24.7 | 19 | 14.7 | 8.98 | 0.0796 | 0.1 | 12.59 | 1
February | 28 | 4AM to 5AM | 28.9 | 25.3 | 19 | 14.7 | 9.2 | 0.0795 | 0.1 | 12.61 | 1
February | 28 | 5AM to 6AM | 28.9 | 25.3 | 19 | 14.7 | 9.2 | 0.0795 | 0.1 | 12.61 | 1
February | 28 | 6AM to 7AM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
February | 28 | 7AM to 8AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
February | 28 | 8AM to 9AM | 32 | 26.7 | 18 | 13.9 | 9.82 | 0.079 | 0.09 | 12.69 | 1
February | 28 | 9AM to 10AM | 33.1 | 27.4 | 18 | 13.9 | 10.08 | 0.0788 | 0.09 | 12.72 | 1
February | 28 | 10AM to 11AM | 34 | 28.2 | 19 | 14.7 | 10.42 | 0.0786 | 0.1 | 12.74 | 1
February | 28 | 11AM to 12PM | 35.1 | 28.8 | 19 | 14.7 | 10.68 | 0.0785 | 0.1 | 12.77 | 1
February | 28 | 12PM to 1PM | 36 | 29.5 | 19.9 | 15.3 | 10.99 | 0.0783 | 0.1 | 12.79 | 1
February | 28 | 1PM to 2PM | 37.9 | 31.2 | 21.9 | 16.9 | 11.71 | 0.078 | 0.11 | 12.85 | 1
February | 28 | 2PM to 3PM | 39 | 32.6 | 23 | 17.8 | 12.1 | 0.0778 | 0.12 | 12.88 | 1
February | 28 | 3PM to 4PM | 37.9 | 31.6 | 23 | 17.8 | 11.84 | 0.078 | 0.12 | 12.85 | 1
February | 28 | 4PM to 5PM | 37.9 | 31.9 | 24.1 | 18.7 | 11.99 | 0.078 | 0.12 | 12.86 | 1
February | 28 | 5PM to 6PM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
February | 28 | 6PM to 7PM | 35.1 | 31.4 | 27 | 21.4 | 11.71 | 0.0784 | 0.14 | 12.79 | 1
February | 28 | 7PM to 8PM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
February | 28 | 8PM to 9PM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
February | 28 | 9PM to 10PM | 32.2 | 30.6 | 28.6 | 23.1 | 11.28 | 0.0789 | 0.15 | 12.72 | 1
February | 28 | 10PM to 11PM | 31.5 | 29.6 | 27.1 | 21.6 | 10.87 | 0.079 | 0.14 | 12.7 | 1
February | 28 | 11PM to 12AM | 30.6 | 28.4 | 25.5 | 20 | 10.41 | 0.0792 | 0.13 | 12.67 | 1
March | 1 | 12AM to 1AM | 29.8 | 27.4 | 23.9 | 18.5 | 10.01 | 0.0793 | 0.12 | 12.65 | 1
March | 1 | 1AM to 2AM | 28.9 | 26.3 | 22.3 | 17.2 | 9.58 | 0.0794 | 0.11 | 12.62 | 1
March | 1 | 2AM to 3AM | 28 | 25.3 | 20.8 | 16 | 9.19 | 0.0796 | 0.11 | 12.59 | 1
March | 1 | 3AM to 4AM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
March | 1 | 4AM to 5AM | 26.1 | 23.5 | 19 | 14.7 | 8.51 | 0.0799 | 0.1 | 12.54 | 1
March | 1 | 5AM to 6AM | 26.1 | 23.5 | 19 | 14.7 | 8.51 | 0.0799 | 0.1 | 12.54 | 1
March | 1 | 6AM to 7AM | 26.1 | 23.5 | 19 | 14.7 | 8.51 | 0.0799 | 0.1 | 12.54 | 1
March | 1 | 7AM to 8AM | 28.9 | 25.3 | 19 | 14.7 | 9.2 | 0.0795 | 0.1 | 12.61 | 1
March | 1 | 8AM to 9AM | 34 | 28.4 | 19.9 | 15.3 | 10.52 | 0.0786 | 0.1 | 12.74 | 1
March | 1 | 9AM to 10AM | 36 | 29.3 | 19 | 14.7 | 10.89 | 0.0783 | 0.1 | 12.79 | 1
March | 1 | 10AM to 11AM | 37.9 | 30.1 | 18 | 13.9 | 11.25 | 0.078 | 0.09 | 12.84 | 1
March | 1 | 11AM to 12PM | 43 | 33.5 | 18 | 13.9 | 12.47 | 0.0772 | 0.09 | 12.97 | 1
March | 1 | 12PM to 1PM | 44.1 | 33.9 | 17.1 | 13.3 | 12.64 | 0.0771 | 0.09 | 13 | 1
March | 1 | 1PM to 2PM | 48 | 36.4 | 18 | 13.9 | 13.68 | 0.0765 | 0.09 | 13.1 | 1
March | 1 | 2PM to 3PM | 48.9 | 37.1 | 19 | 14.7 | 14.01 | 0.0763 | 0.1 | 13.13 | 1
March | 1 | 3PM to 4PM | 48 | 36.4 | 18 | 13.9 | 13.68 | 0.0765 | 0.09 | 13.1 | 1
March | 1 | 4PM to 5PM | 46.9 | 35.1 | 15.1 | 12.1 | 13.14 | 0.0767 | 0.08 | 13.07 | 1
March | 1 | 5PM to 6PM | 45 | 34 | 15.1 | 12.1 | 12.66 | 0.077 | 0.08 | 13.02 | 1
March | 1 | 6PM to 7PM | 42.1 | 32.8 | 17.1 | 13.3 | 12.16 | 0.0774 | 0.09 | 12.95 | 1
March | 1 | 7PM to 8PM | 41 | 31.2 | 16 | 12.7 | 11.79 | 0.0776 | 0.08 | 12.92 | 1
March | 1 | 8PM to 9PM | 37.9 | 30.1 | 18 | 13.9 | 11.25 | 0.078 | 0.09 | 12.84 | 1
March | 1 | 9PM to 10PM | 35.1 | 28.5 | 18 | 13.9 | 10.56 | 0.0785 | 0.09 | 12.77 | 1
March | 1 | 10PM to 11PM | 35.1 | 28.5 | 18 | 13.9 | 10.56 | 0.0785 | 0.09 | 12.77 | 1
March | 1 | 11PM to 12AM | 33.1 | 27.4 | 18 | 13.9 | 10.08 | 0.0788 | 0.09 | 12.72 | 1
March | 2 | 12AM to 1AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
March | 2 | 1AM to 2AM | 34 | 27.9 | 18 | 13.9 | 10.3 | 0.0787 | 0.09 | 12.74 | 1
March | 2 | 2AM to 3AM | 34 | 28.2 | 19 | 14.7 | 10.42 | 0.0786 | 0.1 | 12.74 | 1
March | 2 | 3AM to 4AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
March | 2 | 4AM to 5AM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
March | 2 | 5AM to 6AM | 28.9 | 24.9 | 18 | 13.9 | 9.09 | 0.0795 | 0.09 | 12.61 | 1
March | 2 | 6AM to 7AM | 28.9 | 24.9 | 18 | 13.9 | 9.09 | 0.0795 | 0.09 | 12.61 | 1
March | 2 | 7AM to 8AM | 33.1 | 27.9 | 19.9 | 15.3 | 10.3 | 0.0788 | 0.1 | 12.72 | 1
March | 2 | 8AM to 9AM | 39 | 32.3 | 21.9 | 16.9 | 11.97 | 0.0778 | 0.11 | 12.88 | 1
March | 2 | 9AM to 10AM | 44.1 | 35.2 | 21.9 | 16.9 | 13.18 | 0.0771 | 0.11 | 13.01 | 1
March | 2 | 10AM to 11AM | 48 | 37.1 | 21 | 16.2 | 14.03 | 0.0765 | 0.11 | 13.11 | 1
March | 2 | 11AM to 12PM | 53.1 | 40.1 | 21.9 | 16.9 | 15.35 | 0.0757 | 0.11 | 13.24 | 0
March | 2 | 12PM to 1PM | 55.9 | 41.3 | 21 | 16.2 | 15.93 | 0.0753 | 0.11 | 13.31 | 0
March | 2 | 1PM to 2PM | 57.9 | 42 | 19.9 | 15.3 | 16.28 | 0.075 | 0.1 | 13.36 | 0
March | 2 | 2PM to 3PM | 59 | 42.6 | 19.9 | 15.3 | 16.54 | 0.0749 | 0.1 | 13.39 | 0
March | 2 | 3PM to 4PM | 60.1 | 43.4 | 21 | 16.2 | 16.93 | 0.0747 | 0.11 | 13.42 | 0
March | 2 | 4PM to 5PM | 59 | 43.1 | 21.9 | 16.9 | 16.78 | 0.0748 | 0.11 | 13.39 | 0
March | 2 | 5PM to 6PM | 55.9 | 42.1 | 24.1 | 18.7 | 16.33 | 0.0753 | 0.12 | 13.32 | 0
March | 2 | 6PM to 7PM | 52 | 41 | 27 | 21.4 | 15.8 | 0.0758 | 0.14 | 13.23 | 0
March | 2 | 7PM to 8PM | 50 | 40.3 | 28 | 22.5 | 15.49 | 0.0761 | 0.15 | 13.18 | 1
March | 2 | 8PM to 9PM | 46.9 | 38.7 | 28 | 22.5 | 14.75 | 0.0766 | 0.15 | 13.1 | 1
March | 2 | 9PM to 10PM | 46 | 38.3 | 28 | 22.5 | 14.53 | 0.0767 | 0.15 | 13.08 | 1
March | 2 | 10PM to 11PM | 43 | 36.6 | 28 | 22.5 | 13.79 | 0.0772 | 0.15 | 13 | 1
March | 2 | 11PM to 12AM | 45 | 38.4 | 30 | 24.7 | 14.61 | 0.0769 | 0.16 | 13.05 | 1
March | 3 | 12AM to 1AM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
March | 3 | 1AM to 2AM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
March | 3 | 2AM to 3AM | 41 | 35.1 | 27 | 21.4 | 13.15 | 0.0775 | 0.14 | 12.94 | 1
March | 3 | 3AM to 4AM | 37.9 | 32.7 | 25 | 19.5 | 12.11 | 0.078 | 0.13 | 12.86 | 1
March | 3 | 4AM to 5AM | 37 | 31.5 | 24.1 | 18.7 | 11.77 | 0.0781 | 0.12 | 12.83 | 1
March | 3 | 5AM to 6AM | 35.1 | 30 | 23 | 17.8 | 11.15 | 0.0785 | 0.12 | 12.78 | 1
March | 3 | 6AM to 7AM | 34 | 29.1 | 21.9 | 16.9 | 10.75 | 0.0786 | 0.11 | 12.75 | 1
March | 3 | 7AM to 8AM | 36 | 30.2 | 21.9 | 16.9 | 11.23 | 0.0783 | 0.11 | 12.8 | 1
March | 3 | 8AM to 9AM | 37.9 | 30.6 | 19.9 | 15.3 | 11.47 | 0.078 | 0.1 | 12.85 | 1
March | 3 | 9AM to 10AM | 39.9 | 30.9 | 17.1 | 13.3 | 11.64 | 0.0777 | 0.09 | 12.89 | 1
March | 3 | 10AM to 11AM | 41 | 31.7 | 18 | 13.9 | 11.99 | 0.0776 | 0.09 | 12.92 | 1
March | 3 | 11AM to 12PM | 43 | 33.5 | 18 | 13.9 | 12.47 | 0.0772 | 0.09 | 12.97 | 1
March | 3 | 12PM to 1PM | 45 | 34.4 | 17.1 | 13.3 | 12.85 | 0.0769 | 0.09 | 13.02 | 1
March | 3 | 1PM to 2PM | 48 | 35.5 | 14 | 11.5 | 13.3 | 0.0765 | 0.08 | 13.09 | 1
March | 3 | 2PM to 3PM | 48 | 35.7 | 15.1 | 12.1 | 13.4 | 0.0765 | 0.08 | 13.1 | 1
March | 3 | 3PM to 4PM | 48 | 35.7 | 15.1 | 12.1 | 13.4 | 0.0765 | 0.08 | 13.1 | 1
March | 3 | 4PM to 5PM | 46 | 34 | 12 | 10.4 | 12.66 | 0.0768 | 0.07 | 13.04 | 1
March | 3 | 5PM to 6PM | 44.1 | 32.6 | 10.9 | 9.9 | 12.1 | 0.0771 | 0.07 | 12.99 | 1
March | 3 | 6PM to 7PM | 39.9 | 29.8 | 12 | 10.4 | 11.19 | 0.0777 | 0.07 | 12.88 | 1
March | 3 | 7PM to 8PM | 39 | 29.7 | 14 | 11.5 | 11.14 | 0.0779 | 0.08 | 12.86 | 1
March | 3 | 8PM to 9PM | 37.9 | 29.6 | 16 | 12.7 | 11.06 | 0.078 | 0.08 | 12.84 | 1
March | 3 | 9PM to 10PM | 37 | 28.3 | 12.9 | 10.9 | 10.57 | 0.0782 | 0.07 | 12.81 | 1
March | 3 | 10PM to 11PM | 35.1 | 27.5 | 14 | 11.5 | 10.18 | 0.0785 | 0.08 | 12.76 | 1
March | 3 | 11PM to 12AM | 33.1 | 26.6 | 15.1 | 12.1 | 9.8 | 0.0788 | 0.08 | 12.71 | 1
March | 4 | 12AM to 1AM | 33.1 | 26.8 | 16 | 12.7 | 9.89 | 0.0788 | 0.08 | 12.71 | 1
March | 4 | 1AM to 2AM | 32 | 26.2 | 16 | 12.7 | 9.63 | 0.079 | 0.08 | 12.68 | 1
March | 4 | 2AM to 3AM | 30.9 | 25.8 | 17.1 | 13.3 | 9.47 | 0.0791 | 0.09 | 12.66 | 1
March | 4 | 3AM to 4AM | 30 | 25.3 | 17.1 | 13.3 | 9.25 | 0.0793 | 0.09 | 12.64 | 1
March | 4 | 4AM to 5AM | 30 | 25.3 | 17.1 | 13.3 | 9.25 | 0.0793 | 0.09 | 12.64 | 1
March | 4 | 5AM to 6AM | 30 | 25.3 | 17.1 | 13.3 | 9.25 | 0.0793 | 0.09 | 12.64 | 1
March | 4 | 6AM to 7AM | 30 | 25.3 | 17.1 | 13.3 | 9.25 | 0.0793 | 0.09 | 12.64 | 1
March | 4 | 7AM to 8AM | 33.1 | 27.4 | 18 | 13.9 | 10.08 | 0.0788 | 0.09 | 12.72 | 1
March | 4 | 8AM to 9AM | 36 | 28.7 | 17.1 | 13.3 | 10.68 | 0.0783 | 0.09 | 12.79 | 1
March | 4 | 9AM to 10AM | 39.9 | 30.9 | 17.1 | 13.3 | 11.64 | 0.0777 | 0.09 | 12.89 | 1
March | 4 | 10AM to 11AM | 43 | 33.3 | 17.1 | 13.3 | 12.38 | 0.0773 | 0.09 | 12.97 | 1
March | 4 | 11AM to 12PM | 46 | 35.3 | 18 | 13.9 | 13.21 | 0.0768 | 0.09 | 13.05 | 1
March | 4 | 12PM to 1PM | 48.9 | 37.1 | 19 | 14.7 | 14.01 | 0.0763 | 0.1 | 13.13 | 1
March | 4 | 1PM to 2PM | 52 | 39 | 19.9 | 15.3 | 14.85 | 0.0759 | 0.1 | 13.21 | 0
March | 4 | 2PM to 3PM | 54 | 40.3 | 21 | 16.2 | 15.46 | 0.0756 | 0.11 | 13.26 | 0
March | 4 | 3PM to 4PM | 57 | 42.4 | 23 | 17.8 | 16.44 | 0.0751 | 0.12 | 13.35 | 0
March | 4 | 4PM to 5PM | 57 | 42.1 | 21.9 | 16.9 | 16.31 | 0.0751 | 0.11 | 13.34 | 0
March | 4 | 5PM to 6PM | 55 | 41.7 | 24.1 | 18.7 | 16.11 | 0.0754 | 0.12 | 13.3 | 0
March | 4 | 6PM to 7PM | 51.1 | 39.9 | 25 | 19.5 | 15.28 | 0.076 | 0.13 | 13.2 | 1
March | 4 | 7PM to 8PM | 50 | 39.7 | 26.1 | 20.5 | 15.18 | 0.0761 | 0.14 | 13.17 | 1
March | 4 | 8PM to 9PM | 48 | 38.6 | 26.1 | 20.5 | 14.7 | 0.0764 | 0.14 | 13.12 | 1
March | 4 | 9PM to 10PM | 48.9 | 39.1 | 26.1 | 20.5 | 14.92 | 0.0763 | 0.14 | 13.14 | 1
March | 4 | 10PM to 11PM | 48.9 | 39.4 | 27 | 21.4 | 15.06 | 0.0763 | 0.14 | 13.15 | 1
March | 4 | 11PM to 12AM | 48 | 39.3 | 28 | 22.5 | 15.01 | 0.0764 | 0.15 | 13.13 | 1
March | 5 | 12AM to 1AM | 48 | 39.6 | 28.9 | 23.5 | 15.16 | 0.0764 | 0.16 | 13.13 | 1
March | 5 | 1AM to 2AM | 46 | 39 | 30 | 24.7 | 14.87 | 0.0767 | 0.16 | 13.08 | 1
March | 5 | 2AM to 3AM | 45 | 38.8 | 30.9 | 25.8 | 14.77 | 0.0769 | 0.17 | 13.06 | 1
March | 5 | 3AM to 4AM | 45 | 39.2 | 32 | 27.1 | 14.98 | 0.0769 | 0.18 | 13.06 | 1
March | 5 | 4AM to 5AM | 46 | 40.2 | 33.1 | 28.3 | 15.42 | 0.0767 | 0.19 | 13.09 | 1
March | 5 | 5AM to 6AM | 45 | 39.6 | 33.1 | 28.3 | 15.16 | 0.0768 | 0.19 | 13.07 | 1
March | 5 | 6AM to 7AM | 46 | 40.2 | 33.1 | 28.3 | 15.42 | 0.0767 | 0.19 | 13.09 | 1
March | 5 | 7AM to 8AM | 50 | 42.5 | 34 | 29.3 | 16.54 | 0.0761 | 0.2 | 13.2 | 1
March | 5 | 8AM to 9AM | 55.9 | 45.4 | 34 | 29.3 | 17.98 | 0.0752 | 0.2 | 13.35 | 0
March | 5 | 9AM to 10AM | 61 | 48.1 | 35.1 | 30.6 | 19.4 | 0.0745 | 0.2 | 13.49 | 0
March | 5 | 10AM to 11AM | 61 | 48.9 | 37 | 33.2 | 19.79 | 0.0745 | 0.22 | 13.49 | 0
March | 5 | 11AM to 12PM | 64 | 50.5 | 37.9 | 34.4 | 20.72 | 0.074 | 0.23 | 13.58 | 0
March | 5 | 12PM to 1PM | 62.1 | 50.4 | 39.9 | 37.2 | 20.67 | 0.0743 | 0.25 | 13.54 | 0
March | 5 | 1PM to 2PM | 62.1 | 50.9 | 41 | 38.8 | 20.92 | 0.0743 | 0.26 | 13.54 | 0
March | 5 | 2PM to 3PM | 60.1 | 50.5 | 42.1 | 40.4 | 20.7 | 0.0745 | 0.27 | 13.49 | 0
March | 5 | 3PM to 4PM | 59 | 49.1 | 39.9 | 37.2 | 19.93 | 0.0747 | 0.25 | 13.46 | 0
March | 5 | 4PM to 5PM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
March | 5 | 5PM to 6PM | 57 | 50 | 44.1 | 43.6 | 20.46 | 0.075 | 0.29 | 13.42 | 0
March | 5 | 6PM to 7PM | 54 | 50.1 | 46.9 | 48.8 | 20.51 | 0.0754 | 0.32 | 13.36 | 0
March | 5 | 7PM to 8PM | 54 | 49.1 | 45 | 45.2 | 19.96 | 0.0754 | 0.3 | 13.35 | 0
March | 5 | 8PM to 9PM | 55 | 49.2 | 44.1 | 43.6 | 19.98 | 0.0752 | 0.29 | 13.37 | 0
March | 5 | 9PM to 10PM | 53.1 | 48.3 | 44.1 | 43.6 | 19.5 | 0.0755 | 0.29 | 13.32 | 0
March | 5 | 10PM to 11PM | 53.1 | 48.3 | 44.1 | 43.6 | 19.5 | 0.0755 | 0.29 | 13.32 | 0
March | 5 | 11PM to 12AM | 51.1 | 47.8 | 45 | 45.2 | 19.26 | 0.0758 | 0.3 | 13.27 | 1
March | 6 | 12AM to 1AM | 50 | 47.9 | 46 | 47.1 | 19.29 | 0.076 | 0.31 | 13.25 | 1
March | 6 | 1AM to 2AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
March | 6 | 2AM to 3AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 6 | 3AM to 4AM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
March | 6 | 4AM to 5AM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
March | 6 | 5AM to 6AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
March | 6 | 6AM to 7AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
March | 6 | 7AM to 8AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
March | 6 | 8AM to 9AM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
March | 6 | 9AM to 10AM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
March | 6 | 10AM to 11AM | 48.9 | 45.8 | 43 | 41.9 | 18.22 | 0.0762 | 0.28 | 13.21 | 1
March | 6 | 11AM to 12PM | 50 | 46.4 | 43 | 41.9 | 18.48 | 0.076 | 0.28 | 13.24 | 1
March | 6 | 12PM to 1PM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
March | 6 | 1PM to 2PM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
March | 6 | 2PM to 3PM | 50 | 45.4 | 41 | 38.8 | 18 | 0.076 | 0.26 | 13.23 | 1
March | 6 | 3PM to 4PM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
March | 6 | 4PM to 5PM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
March | 6 | 5PM to 6PM | 46.9 | 43.1 | 39 | 35.9 | 16.81 | 0.0765 | 0.24 | 13.14 | 1
March | 6 | 6PM to 7PM | 45 | 41.2 | 37 | 33.2 | 15.91 | 0.0768 | 0.22 | 13.08 | 1
March | 6 | 7PM to 8PM | 45 | 40.8 | 36 | 31.8 | 15.7 | 0.0768 | 0.21 | 13.08 | 1
March | 6 | 8PM to 9PM | 44.1 | 40.3 | 36 | 31.8 | 15.48 | 0.077 | 0.21 | 13.05 | 1
March | 6 | 9PM to 10PM | 44.1 | 40.3 | 36 | 31.8 | 15.48 | 0.077 | 0.21 | 13.05 | 1
March | 6 | 10PM to 11PM | 43 | 39.4 | 35.1 | 30.6 | 15.04 | 0.0771 | 0.2 | 13.02 | 1
March | 6 | 11PM to 12AM | 43 | 39.4 | 35.1 | 30.6 | 15.04 | 0.0771 | 0.2 | 13.02 | 1
March | 7 | 12AM to 1AM | 42.1 | 38.9 | 35.1 | 30.6 | 14.83 | 0.0773 | 0.2 | 13 | 1
March | 7 | 1AM to 2AM | 42.1 | 38.9 | 35.1 | 30.6 | 14.83 | 0.0773 | 0.2 | 13 | 1
March | 7 | 2AM to 3AM | 41 | 38.3 | 35.1 | 30.6 | 14.57 | 0.0774 | 0.2 | 12.97 | 1
March | 7 | 3AM to 4AM | 39.9 | 37.7 | 35.1 | 30.6 | 14.3 | 0.0776 | 0.2 | 12.94 | 1
March | 7 | 4AM to 5AM | 39.9 | 37.7 | 35.1 | 30.6 | 14.3 | 0.0776 | 0.2 | 12.94 | 1
March | 7 | 5AM to 6AM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
March | 7 | 6AM to 7AM | 39 | 36.8 | 34 | 29.3 | 13.89 | 0.0778 | 0.2 | 12.91 | 1
March | 7 | 7AM to 8AM | 39.9 | 36.9 | 33.1 | 28.3 | 13.94 | 0.0776 | 0.19 | 12.93 | 1
March | 7 | 8AM to 9AM | 39.9 | 36.9 | 33.1 | 28.3 | 13.94 | 0.0776 | 0.19 | 12.93 | 1
March | 7 | 9AM to 10AM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
March | 7 | 10AM to 11AM | 42.1 | 38.5 | 34 | 29.3 | 14.63 | 0.0773 | 0.2 | 12.99 | 1
March | 7 | 11AM to 12PM | 43 | 38.9 | 34 | 29.3 | 14.84 | 0.0771 | 0.2 | 13.02 | 1
March | 7 | 12PM to 1PM | 43 | 38.6 | 33.1 | 28.3 | 14.68 | 0.0772 | 0.19 | 13.01 | 1
March | 7 | 1PM to 2PM | 44.1 | 39.2 | 33.1 | 28.3 | 14.94 | 0.077 | 0.19 | 13.04 | 1
March | 7 | 2PM to 3PM | 44.1 | 39.5 | 34 | 29.3 | 15.11 | 0.077 | 0.2 | 13.04 | 1
March | 7 | 3PM to 4PM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
March | 7 | 4PM to 5PM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
March | 7 | 5PM to 6PM | 42.1 | 40.1 | 37.9 | 34.4 | 15.4 | 0.0772 | 0.23 | 13.01 | 1
March | 7 | 6PM to 7PM | 42.1 | 40.1 | 37.9 | 34.4 | 15.4 | 0.0772 | 0.23 | 13.01 | 1
March | 7 | 7PM to 8PM | 42.1 | 40.1 | 37.9 | 34.4 | 15.4 | 0.0772 | 0.23 | 13.01 | 1
March | 7 | 8PM to 9PM | 44.1 | 40.8 | 37 | 33.2 | 15.69 | 0.077 | 0.22 | 13.06 | 1
March | 7 | 9PM to 10PM | 44.1 | 41.6 | 39 | 35.9 | 16.11 | 0.0769 | 0.24 | 13.06 | 1
March | 7 | 10PM to 11PM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
March | 7 | 11PM to 12AM | 46 | 43.5 | 41 | 38.8 | 17.04 | 0.0766 | 0.26 | 13.12 | 1
March | 8 | 12AM to 1AM | 46 | 44 | 42.1 | 40.4 | 17.3 | 0.0766 | 0.27 | 13.13 | 1
March | 8 | 1AM to 2AM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
March | 8 | 2AM to 3AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 8 | 3AM to 4AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
March | 8 | 4AM to 5AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
March | 8 | 5AM to 6AM | 51.1 | 49.4 | 48 | 50.8 | 20.13 | 0.0758 | 0.34 | 13.29 | 1
March | 8 | 6AM to 7AM | 52 | 50.3 | 48.9 | 52.6 | 20.62 | 0.0756 | 0.35 | 13.32 | 0
March | 8 | 7AM to 8AM | 53.1 | 51.9 | 51.1 | 57 | 21.57 | 0.0755 | 0.38 | 13.36 | 0
March | 8 | 8AM to 9AM | 55 | 53.3 | 52 | 59 | 22.36 | 0.0751 | 0.39 | 13.42 | 0
March | 8 | 9AM to 10AM | 57 | 54.7 | 53.1 | 61.4 | 23.22 | 0.0748 | 0.41 | 13.48 | 0
March | 8 | 10AM to 11AM | 59 | 56 | 54 | 63.5 | 24.02 | 0.0745 | 0.42 | 13.54 | 0
March | 8 | 11AM to 12PM | 62.1 | 57.1 | 54 | 63.5 | 24.77 | 0.0741 | 0.42 | 13.62 | 0
March | 8 | 12PM to 1PM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
March | 8 | 1PM to 2PM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
March | 8 | 2PM to 3PM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
March | 8 | 3PM to 4PM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
March | 8 | 4PM to 5PM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
March | 8 | 5PM to 6PM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
March | 8 | 6PM to 7PM | 61 | 55.6 | 52 | 59 | 23.8 | 0.0743 | 0.39 | 13.57 | 0
March | 8 | 7PM to 8PM | 61 | 55.6 | 52 | 59 | 23.8 | 0.0743 | 0.39 | 13.57 | 0
March | 8 | 8PM to 9PM | 60.1 | 55.9 | 53.1 | 61.4 | 23.96 | 0.0744 | 0.41 | 13.56 | 0
March | 8 | 9PM to 10PM | 60.1 | 55.9 | 53.1 | 61.4 | 23.96 | 0.0744 | 0.41 | 13.56 | 0
March | 8 | 10PM to 11PM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
March | 8 | 11PM to 12AM | 57.9 | 55 | 53.1 | 61.4 | 23.44 | 0.0747 | 0.41 | 13.5 | 0
March | 9 | 12AM to 1AM | 55.9 | 54.2 | 53.1 | 61.4 | 22.95 | 0.075 | 0.41 | 13.45 | 0
March | 9 | 1AM to 2AM | 57 | 54.7 | 53.1 | 61.4 | 23.22 | 0.0748 | 0.41 | 13.48 | 0
March | 9 | 2AM to 3AM | 55 | 52.2 | 50 | 54.7 | 21.7 | 0.0752 | 0.36 | 13.41 | 0
March | 9 | 3AM to 4AM | 51.1 | 48.8 | 46.9 | 48.8 | 19.81 | 0.0758 | 0.32 | 13.29 | 1
March | 9 | 4AM to 5AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
March | 9 | 5AM to 6AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
March | 9 | 6AM to 7AM | 48 | 46.4 | 45 | 45.2 | 18.51 | 0.0763 | 0.3 | 13.19 | 1
March | 9 | 7AM to 8AM | 51.1 | 48.8 | 46.9 | 48.8 | 19.81 | 0.0758 | 0.32 | 13.29 | 1
March | 9 | 8AM to 9AM | 54 | 51.7 | 50 | 54.7 | 21.44 | 0.0753 | 0.36 | 13.38 | 0
March | 9 | 9AM to 10AM | 55.9 | 54.2 | 53.1 | 61.4 | 22.95 | 0.075 | 0.41 | 13.45 | 0
March | 9 | 10AM to 11AM | 60.1 | 55.3 | 52 | 59 | 23.59 | 0.0744 | 0.39 | 13.55 | 0
March | 9 | 11AM to 12PM | 64.9 | 58.8 | 55 | 66.1 | 25.88 | 0.0737 | 0.44 | 13.7 | 0
March | 9 | 12PM to 1PM | 71.1 | 62.1 | 57 | 71.1 | 28.15 | 0.0728 | 0.47 | 13.87 | 0
March | 9 | 1PM to 2PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
March | 9 | 2PM to 3PM | 75.9 | 63.8 | 57 | 71.1 | 29.34 | 0.0721 | 0.47 | 14 | 0
March | 9 | 3PM to 4PM | 79 | 64.2 | 55.9 | 68.3 | 29.65 | 0.0718 | 0.45 | 14.07 | 0
March | 9 | 4PM to 5PM | 79 | 63.8 | 55 | 66.1 | 29.3 | 0.0718 | 0.44 | 14.07 | 0
March | 9 | 5PM to 6PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
March | 9 | 6PM to 7PM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
March | 9 | 7PM to 8PM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
March | 9 | 8PM to 9PM | 66 | 62.2 | 60.1 | 79.5 | 28.23 | 0.0735 | 0.52 | 13.77 | 0
March | 9 | 9PM to 10PM | 64.9 | 61.8 | 60.1 | 79.5 | 27.96 | 0.0736 | 0.52 | 13.74 | 0
March | 9 | 10PM to 11PM | 64 | 61.5 | 60.1 | 79.5 | 27.74 | 0.0737 | 0.52 | 13.72 | 0
March | 9 | 11PM to 12AM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
March | 10 | 12AM to 1AM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
March | 10 | 1AM to 2AM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
March | 10 | 2AM to 3AM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
March | 10 | 3AM to 4AM | 63 | 61.7 | 61 | 82.1 | 27.89 | 0.0739 | 0.54 | 13.7 | 0
March | 10 | 4AM to 5AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
March | 10 | 5AM to 6AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
March | 10 | 6AM to 7AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
March | 10 | 7AM to 8AM | 68 | 64.1 | 62.1 | 85.4 | 29.63 | 0.0731 | 0.56 | 13.84 | 0
March | 10 | 8AM to 9AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
March | 10 | 9AM to 10AM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
March | 10 | 10AM to 11AM | 79 | 67 | 61 | 82.1 | 31.81 | 0.0717 | 0.54 | 14.12 | 0
March | 10 | 11AM to 12PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
March | 10 | 12PM to 1PM | 82.9 | 66.5 | 57.9 | 73.5 | 31.43 | 0.0712 | 0.48 | 14.19 | 0
March | 10 | 1PM to 2PM | 82.9 | 66.1 | 57 | 71.1 | 31.06 | 0.0712 | 0.47 | 14.19 | 0
March | 10 | 2PM to 3PM | 82 | 65.8 | 57 | 71.1 | 30.84 | 0.0713 | 0.47 | 14.16 | 0
March | 10 | 3PM to 4PM | 82.9 | 65.5 | 55.9 | 68.3 | 30.62 | 0.0712 | 0.45 | 14.18 | 0
March | 10 | 4PM to 5PM | 80.1 | 65.6 | 57.9 | 73.5 | 30.72 | 0.0716 | 0.48 | 14.12 | 0
March | 10 | 5PM to 6PM | 79 | 65.3 | 57.9 | 73.5 | 30.46 | 0.0717 | 0.48 | 14.09 | 0
March | 10 | 6PM to 7PM | 75.9 | 65.5 | 60.1 | 79.5 | 30.65 | 0.0721 | 0.52 | 14.03 | 0
March | 10 | 7PM to 8PM | 75 | 64 | 57.9 | 73.5 | 29.49 | 0.0723 | 0.48 | 13.99 | 0
March | 10 | 8PM to 9PM | 73.9 | 63.1 | 57 | 71.1 | 28.85 | 0.0724 | 0.47 | 13.95 | 0
March | 10 | 9PM to 10PM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
March | 10 | 10PM to 11PM | 71.1 | 63.2 | 59 | 76.4 | 28.98 | 0.0728 | 0.5 | 13.89 | 0
March | 10 | 11PM to 12AM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
March | 11 | 12AM to 1AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
March | 11 | 1AM to 2AM | 68 | 64.1 | 62.1 | 85.4 | 29.63 | 0.0731 | 0.56 | 13.84 | 0
March | 11 | 2AM to 3AM | 66.9 | 63.7 | 62.1 | 85.4 | 29.36 | 0.0733 | 0.56 | 13.81 | 0
March | 11 | 3AM to 4AM | 66.9 | 63.7 | 62.1 | 85.4 | 29.36 | 0.0733 | 0.56 | 13.81 | 0
March | 11 | 4AM to 5AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
March | 11 | 5AM to 6AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
March | 11 | 6AM to 7AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
March | 11 | 7AM to 8AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
March | 11 | 8AM to 9AM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
March | 11 | 9AM to 10AM | 73 | 63.9 | 59 | 76.4 | 29.47 | 0.0725 | 0.5 | 13.94 | 0
March | 11 | 10AM to 11AM | 75 | 64 | 57.9 | 73.5 | 29.49 | 0.0723 | 0.48 | 13.99 | 0
March | 11 | 11AM to 12PM | 78.1 | 63.9 | 55.9 | 68.3 | 29.43 | 0.0719 | 0.45 | 14.05 | 0
March | 11 | 12PM to 1PM | 79 | 64.2 | 55.9 | 68.3 | 29.65 | 0.0718 | 0.45 | 14.07 | 0
March | 11 | 1PM to 2PM | 77 | 64.1 | 57 | 71.1 | 29.6 | 0.072 | 0.47 | 14.03 | 0
March | 11 | 2PM to 3PM | 75.9 | 63.8 | 57 | 71.1 | 29.34 | 0.0721 | 0.47 | 14 | 0
March | 11 | 3PM to 4PM | 75.9 | 63.8 | 57 | 71.1 | 29.34 | 0.0721 | 0.47 | 14 | 0
March | 11 | 4PM to 5PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
March | 11 | 5PM to 6PM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
March | 11 | 6PM to 7PM | 70 | 63.5 | 60.1 | 79.5 | 29.2 | 0.0729 | 0.52 | 13.87 | 0
March | 11 | 7PM to 8PM | 69.1 | 62.6 | 59 | 76.4 | 28.5 | 0.073 | 0.5 | 13.84 | 0
March | 11 | 8PM to 9PM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
March | 11 | 9PM to 10PM | 69.1 | 63.2 | 60.1 | 79.5 | 28.98 | 0.073 | 0.52 | 13.85 | 0
March | 11 | 10PM to 11PM | 61 | 59.7 | 59 | 76.4 | 26.52 | 0.0742 | 0.5 | 13.63 | 0
March | 11 | 11PM to 12AM | 62.1 | 59.5 | 57.9 | 73.5 | 26.32 | 0.074 | 0.48 | 13.65 | 0
March | 12 | 12AM to 1AM | 62.1 | 60.1 | 59 | 76.4 | 26.78 | 0.074 | 0.5 | 13.66 | 0
March | 12 | 1AM to 2AM | 63 | 59.8 | 57.9 | 73.5 | 26.54 | 0.0739 | 0.48 | 13.67 | 0
March | 12 | 2AM to 3AM | 64.9 | 61.1 | 59 | 76.4 | 27.48 | 0.0736 | 0.5 | 13.73 | 0
March | 12 | 3AM to 4AM | 64 | 60.8 | 59 | 76.4 | 27.26 | 0.0737 | 0.5 | 13.71 | 0
March | 12 | 4AM to 5AM | 64 | 60.8 | 59 | 76.4 | 27.26 | 0.0737 | 0.5 | 13.71 | 0
March | 12 | 5AM to 6AM | 64 | 61.5 | 60.1 | 79.5 | 27.74 | 0.0737 | 0.52 | 13.72 | 0
March | 12 | 6AM to 7AM | 64 | 61.5 | 60.1 | 79.5 | 27.74 | 0.0737 | 0.52 | 13.72 | 0
March | 12 | 7AM to 8AM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
March | 12 | 8AM to 9AM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
March | 12 | 9AM to 10AM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
March | 12 | 10AM to 11AM | 77 | 67 | 62.1 | 85.4 | 31.84 | 0.0719 | 0.56 | 14.08 | 0
March | 12 | 11AM to 12PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
March | 12 | 12PM to 1PM | 81 | 66.5 | 59 | 76.4 | 31.41 | 0.0714 | 0.5 | 14.15 | 0
March | 12 | 1PM to 2PM | 82.9 | 66.5 | 57.9 | 73.5 | 31.43 | 0.0712 | 0.48 | 14.19 | 0
March | 12 | 2PM to 3PM | 82.9 | 66.1 | 57 | 71.1 | 31.06 | 0.0712 | 0.47 | 14.19 | 0
March | 12 | 3PM to 4PM | 82.9 | 65.5 | 55.9 | 68.3 | 30.62 | 0.0712 | 0.45 | 14.18 | 0
March | 12 | 4PM to 5PM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
March | 12 | 5PM to 6PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
March | 12 | 6PM to 7PM | 75 | 65.7 | 61 | 82.1 | 30.84 | 0.0722 | 0.54 | 14.01 | 0
March | 12 | 7PM to 8PM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
March | 12 | 8PM to 9PM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
March | 12 | 9PM to 10PM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
March | 12 | 10PM to 11PM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
March | 12 | 11PM to 12AM | 68 | 64.1 | 62.1 | 85.4 | 29.63 | 0.0731 | 0.56 | 13.84 | 0
March | 13 | 12AM to 1AM | 66.9 | 63.7 | 62.1 | 85.4 | 29.36 | 0.0733 | 0.56 | 13.81 | 0
March | 13 | 1AM to 2AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
March | 13 | 2AM to 3AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
March | 13 | 3AM to 4AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
March | 13 | 4AM to 5AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
March | 13 | 5AM to 6AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
March | 13 | 6AM to 7AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
March | 13 | 7AM to 8AM | 66.9 | 63.7 | 62.1 | 85.4 | 29.36 | 0.0733 | 0.56 | 13.81 | 0
March | 13 | 8AM to 9AM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
March | 13 | 9AM to 10AM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
March | 13 | 10AM to 11AM | 75.9 | 66 | 61 | 82.1 | 31.06 | 0.0721 | 0.54 | 14.04 | 0
March | 13 | 11AM to 12PM | 78.1 | 65.6 | 59 | 76.4 | 30.7 | 0.0718 | 0.5 | 14.08 | 0
March | 13 | 12PM to 1PM | 77 | 65.2 | 59 | 76.4 | 30.44 | 0.072 | 0.5 | 14.05 | 0
March | 13 | 1PM to 2PM | 78.1 | 64.5 | 57 | 71.1 | 29.87 | 0.0719 | 0.47 | 14.06 | 0
March | 13 | 2PM to 3PM | 78.1 | 64.5 | 57 | 71.1 | 29.87 | 0.0719 | 0.47 | 14.06 | 0
March | 13 | 3PM to 4PM | 78.1 | 64.5 | 57 | 71.1 | 29.87 | 0.0719 | 0.47 | 14.06 | 0
March | 13 | 4PM to 5PM | 75.9 | 63.8 | 57 | 71.1 | 29.34 | 0.0721 | 0.47 | 14 | 0
March | 13 | 5PM to 6PM | 75 | 62.9 | 55.9 | 68.3 | 28.69 | 0.0723 | 0.45 | 13.97 | 0
March | 13 | 6PM to 7PM | 73 | 62.8 | 57 | 71.1 | 28.63 | 0.0725 | 0.47 | 13.93 | 0
March | 13 | 7PM to 8PM | 72 | 62.4 | 57 | 71.1 | 28.37 | 0.0727 | 0.47 | 13.9 | 0
March | 13 | 8PM to 9PM | 71.1 | 63.2 | 59 | 76.4 | 28.98 | 0.0728 | 0.5 | 13.89 | 0
March | 13 | 9PM to 10PM | 71.1 | 63.2 | 59 | 76.4 | 28.98 | 0.0728 | 0.5 | 13.89 | 0
March | 13 | 10PM to 11PM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
March | 13 | 11PM to 12AM | 70 | 62.3 | 57.9 | 73.5 | 28.26 | 0.0729 | 0.48 | 13.85 | 0
March | 14 | 12AM to 1AM | 69.1 | 61.9 | 57.9 | 73.5 | 28.04 | 0.0731 | 0.48 | 13.83 | 0
March | 14 | 1AM to 2AM | 69.1 | 61.4 | 57 | 71.1 | 27.67 | 0.0731 | 0.47 | 13.82 | 0
March | 14 | 2AM to 3AM | 69.1 | 61.4 | 57 | 71.1 | 27.67 | 0.0731 | 0.47 | 13.82 | 0
March | 14 | 3AM to 4AM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
March | 14 | 4AM to 5AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
March | 14 | 5AM to 6AM | 63 | 59.2 | 57 | 71.1 | 26.17 | 0.0739 | 0.47 | 13.66 | 0
March | 14 | 6AM to 7AM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
March | 14 | 7AM to 8AM | 64 | 61.5 | 60.1 | 79.5 | 27.74 | 0.0737 | 0.52 | 13.72 | 0
March | 14 | 8AM to 9AM | 64.9 | 61.8 | 60.1 | 79.5 | 27.96 | 0.0736 | 0.52 | 13.74 | 0
March | 14 | 9AM to 10AM | 64.9 | 61.8 | 60.1 | 79.5 | 27.96 | 0.0736 | 0.52 | 13.74 | 0
March | 14 | 10AM to 11AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
March | 14 | 11AM to 12PM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
March | 14 | 12PM to 1PM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
March | 14 | 1PM to 2PM | 69.1 | 62.6 | 59 | 76.4 | 28.5 | 0.073 | 0.5 | 13.84 | 0
March | 14 | 2PM to 3PM | 66.9 | 62.5 | 60.1 | 79.5 | 28.45 | 0.0733 | 0.52 | 13.79 | 0
March | 14 | 3PM to 4PM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
March | 14 | 4PM to 5PM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
March | 14 | 5PM to 6PM | 66.9 | 61.2 | 57.9 | 73.5 | 27.51 | 0.0734 | 0.48 | 13.77 | 0
March | 14 | 6PM to 7PM | 66.9 | 60.7 | 57 | 71.1 | 27.14 | 0.0734 | 0.47 | 13.77 | 0
March | 14 | 7PM to 8PM | 66.9 | 60.7 | 57 | 71.1 | 27.14 | 0.0734 | 0.47 | 13.77 | 0
March | 14 | 8PM to 9PM | 66 | 59.7 | 55.9 | 68.3 | 26.49 | 0.0735 | 0.45 | 13.73 | 0
March | 14 | 9PM to 10PM | 66.9 | 60.1 | 55.9 | 68.3 | 26.71 | 0.0734 | 0.45 | 13.76 | 0
March | 14 | 10PM to 11PM | 64.9 | 61.1 | 59 | 76.4 | 27.48 | 0.0736 | 0.5 | 13.73 | 0
March | 14 | 11PM to 12AM | 62.1 | 60.8 | 60.1 | 79.5 | 27.26 | 0.074 | 0.52 | 13.67 | 0
March | 15 | 12AM to 1AM | 63 | 60.4 | 59 | 76.4 | 27 | 0.0739 | 0.5 | 13.68 | 0
March | 15 | 1AM to 2AM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
March | 15 | 2AM to 3AM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
March | 15 | 3AM to 4AM | 64.9 | 60 | 57 | 71.1 | 26.65 | 0.0737 | 0.47 | 13.71 | 0
March | 15 | 4AM to 5AM | 64.9 | 58.8 | 55 | 66.1 | 25.88 | 0.0737 | 0.44 | 13.7 | 0
March | 15 | 5AM to 6AM | 60.1 | 47.7 | 35.1 | 30.6 | 19.18 | 0.0746 | 0.2 | 13.46 | 0
March | 15 | 6AM to 7AM | 57 | 46.3 | 35.1 | 30.6 | 18.44 | 0.075 | 0.2 | 13.38 | 0
March | 15 | 7AM to 8AM | 55 | 46.5 | 37.9 | 34.4 | 18.54 | 0.0753 | 0.23 | 13.34 | 0
March | 15 | 8AM to 9AM | 54 | 46 | 37.9 | 34.4 | 18.28 | 0.0755 | 0.23 | 13.32 | 0
March | 15 | 9AM to 10AM | 53.1 | 45.6 | 37.9 | 34.4 | 18.06 | 0.0756 | 0.23 | 13.29 | 0
March | 15 | 10AM to 11AM | 53.1 | 45.2 | 37 | 33.2 | 17.87 | 0.0756 | 0.22 | 13.29 | 0
March | 15 | 11AM to 12PM | 55 | 46.1 | 37 | 33.2 | 18.35 | 0.0753 | 0.22 | 13.34 | 0
March | 15 | 12PM to 1PM | 57.9 | 47.8 | 37.9 | 34.4 | 19.24 | 0.0749 | 0.23 | 13.42 | 0
March | 15 | 1PM to 2PM | 60.1 | 48.5 | 37 | 33.2 | 19.57 | 0.0746 | 0.22 | 13.47 | 0
March | 15 | 2PM to 3PM | 61 | 48.5 | 36 | 31.8 | 19.57 | 0.0745 | 0.21 | 13.49 | 0
March | 15 | 3PM to 4PM | 61 | 48.1 | 35.1 | 30.6 | 19.4 | 0.0745 | 0.2 | 13.49 | 0
March | 15 | 4PM to 5PM | 62.1 | 48.3 | 34 | 29.3 | 19.46 | 0.0743 | 0.2 | 13.51 | 0
March | 15 | 5PM to 6PM | 60.1 | 47.7 | 35.1 | 30.6 | 19.18 | 0.0746 | 0.2 | 13.46 | 0
March | 15 | 6PM to 7PM | 55.9 | 46.1 | 36 | 31.8 | 18.35 | 0.0752 | 0.21 | 13.36 | 0
March | 15 | 7PM to 8PM | 55 | 45.4 | 35.1 | 30.6 | 17.96 | 0.0753 | 0.2 | 13.33 | 0
March | 15 | 8PM to 9PM | 55 | 45.4 | 35.1 | 30.6 | 17.96 | 0.0753 | 0.2 | 13.33 | 0
March | 15 | 9PM to 10PM | 52 | 44.7 | 37 | 33.2 | 17.61 | 0.0758 | 0.22 | 13.26 | 0
March | 15 | 10PM to 11PM | 50 | 43.3 | 36 | 31.8 | 16.92 | 0.0761 | 0.21 | 13.21 | 1
March | 15 | 11PM to 12AM | 48.9 | 43.2 | 37 | 33.2 | 16.87 | 0.0762 | 0.22 | 13.18 | 1
March | 16 | 12AM to 1AM | 48 | 42.3 | 36 | 31.8 | 16.44 | 0.0764 | 0.21 | 13.15 | 1
March | 16 | 1AM to 2AM | 48.9 | 42.8 | 36 | 31.8 | 16.66 | 0.0762 | 0.21 | 13.18 | 1
March | 16 | 2AM to 3AM | 46.9 | 41.8 | 36 | 31.8 | 16.18 | 0.0765 | 0.21 | 13.13 | 1
March | 16 | 3AM to 4AM | 46 | 41.3 | 36 | 31.8 | 15.96 | 0.0767 | 0.21 | 13.1 | 1
March | 16 | 4AM to 5AM | 45 | 40.8 | 36 | 31.8 | 15.7 | 0.0768 | 0.21 | 13.08 | 1
March | 16 | 5AM to 6AM | 44.1 | 40.3 | 36 | 31.8 | 15.48 | 0.077 | 0.21 | 13.05 | 1
March | 16 | 6AM to 7AM | 46 | 41.8 | 37 | 33.2 | 16.17 | 0.0767 | 0.22 | 13.11 | 1
March | 16 | 7AM to 8AM | 51.1 | 43.8 | 36 | 31.8 | 17.18 | 0.0759 | 0.21 | 13.23 | 1
March | 16 | 8AM to 9AM | 55 | 45 | 34 | 29.3 | 17.76 | 0.0753 | 0.2 | 13.33 | 0
March | 16 | 9AM to 10AM | 59 | 46.9 | 34 | 29.3 | 18.72 | 0.0748 | 0.2 | 13.43 | 0
March | 16 | 10AM to 11AM | 61 | 48.1 | 35.1 | 30.6 | 19.4 | 0.0745 | 0.2 | 13.49 | 0
March | 16 | 11AM to 12PM | 64 | 48.1 | 30.9 | 25.8 | 19.38 | 0.0741 | 0.17 | 13.55 | 0
March | 16 | 12PM to 1PM | 66 | 48.7 | 30 | 24.7 | 19.7 | 0.0738 | 0.16 | 13.6 | 0
March | 16 | 1PM to 2PM | 66.9 | 48.8 | 28.9 | 23.5 | 19.73 | 0.0737 | 0.16 | 13.62 | 0
March | 16 | 2PM to 3PM | 66.9 | 48.8 | 28.9 | 23.5 | 19.73 | 0.0737 | 0.16 | 13.62 | 0
March | 16 | 3PM to 4PM | 64.9 | 47.6 | 28 | 22.5 | 19.1 | 0.074 | 0.15 | 13.56 | 0
March | 16 | 4PM to 5PM | 64.9 | 47.9 | 28.9 | 23.5 | 19.25 | 0.074 | 0.16 | 13.57 | 0
March | 16 | 5PM to 6PM | 62.1 | 46.9 | 30 | 24.7 | 18.74 | 0.0744 | 0.16 | 13.5 | 0
March | 16 | 6PM to 7PM | 57 | 45.6 | 33.1 | 28.3 | 18.08 | 0.0751 | 0.19 | 13.38 | 0
March | 16 | 7PM to 8PM | 55 | 44.3 | 32 | 27.1 | 17.41 | 0.0754 | 0.18 | 13.32 | 0
March | 16 | 8PM to 9PM | 53.1 | 43.7 | 33.1 | 28.3 | 17.12 | 0.0756 | 0.19 | 13.27 | 0
March | 16 | 9PM to 10PM | 51.1 | 43.5 | 35.1 | 30.6 | 17 | 0.0759 | 0.2 | 13.23 | 1
March | 16 | 10PM to 11PM | 48.9 | 42.4 | 35.1 | 30.6 | 16.48 | 0.0762 | 0.2 | 13.17 | 1
March | 16 | 11PM to 12AM | 48 | 42 | 35.1 | 30.6 | 16.26 | 0.0764 | 0.2 | 13.15 | 1
March | 17 | 12AM to 1AM | 46.9 | 41.4 | 35.1 | 30.6 | 16 | 0.0765 | 0.2 | 13.12 | 1
March | 17 | 1AM to 2AM | 46 | 41.3 | 36 | 31.8 | 15.96 | 0.0767 | 0.21 | 13.1 | 1
March | 17 | 2AM to 3AM | 44.1 | 40.3 | 36 | 31.8 | 15.48 | 0.077 | 0.21 | 13.05 | 1
March | 17 | 3AM to 4AM | 45 | 40.4 | 35.1 | 30.6 | 15.52 | 0.0768 | 0.2 | 13.07 | 1
March | 17 | 4AM to 5AM | 44.1 | 40.3 | 36 | 31.8 | 15.48 | 0.077 | 0.21 | 13.05 | 1
March | 17 | 5AM to 6AM | 44.1 | 40.8 | 37 | 33.2 | 15.69 | 0.077 | 0.22 | 13.06 | 1
March | 17 | 6AM to 7AM | 44.1 | 40.8 | 37 | 33.2 | 15.69 | 0.077 | 0.22 | 13.06 | 1
March | 17 | 7AM to 8AM | 46.9 | 42.6 | 37.9 | 34.4 | 16.58 | 0.0765 | 0.23 | 13.13 | 1
March | 17 | 8AM to 9AM | 51.1 | 44.3 | 37 | 33.2 | 17.39 | 0.0759 | 0.22 | 13.24 | 1
March | 17 | 9AM to 10AM | 54 | 44.5 | 34 | 29.3 | 17.5 | 0.0755 | 0.2 | 13.3 | 0
March | 17 | 10AM to 11AM | 55.9 | 45.1 | 33.1 | 28.3 | 17.82 | 0.0752 | 0.19 | 13.35 | 0
March | 17 | 11AM to 12PM | 57 | 43.9 | 28 | 22.5 | 17.18 | 0.0751 | 0.15 | 13.36 | 0
March | 17 | 12PM to 1PM | 59 | 44.8 | 28 | 22.5 | 17.66 | 0.0748 | 0.15 | 13.41 | 0
March | 17 | 1PM to 2PM | 59 | 43.9 | 25 | 19.5 | 17.19 | 0.0748 | 0.13 | 13.4 | 0
March | 17 | 2PM to 3PM | 59 | 44.2 | 26.1 | 20.5 | 17.35 | 0.0748 | 0.14 | 13.4 | 0
March | 17 | 3PM to 4PM | 57.9 | 44.3 | 28 | 22.5 | 17.4 | 0.075 | 0.15 | 13.38 | 0
March | 17 | 4PM to 5PM | 55 | 42.3 | 26.1 | 20.5 | 16.4 | 0.0754 | 0.14 | 13.3 | 0
March | 17 | 5PM to 6PM | 53.1 | 41.3 | 26.1 | 20.5 | 15.92 | 0.0757 | 0.14 | 13.25 | 0
March | 17 | 6PM to 7PM | 51.1 | 40.5 | 27 | 21.4 | 15.58 | 0.076 | 0.14 | 13.2 | 1
March | 17 | 7PM to 8PM | 50 | 40 | 27 | 21.4 | 15.32 | 0.0761 | 0.14 | 13.17 | 1
March | 17 | 8PM to 9PM | 48 | 39.3 | 28 | 22.5 | 15.01 | 0.0764 | 0.15 | 13.13 | 1
March | 17 | 9PM to 10PM | 46 | 38.6 | 28.9 | 23.5 | 14.68 | 0.0767 | 0.16 | 13.08 | 1
March | 17 | 10PM to 11PM | 45 | 37.7 | 28 | 22.5 | 14.27 | 0.0769 | 0.15 | 13.05 | 1
March | 17 | 11PM to 12AM | 45 | 38 | 28.9 | 23.5 | 14.42 | 0.0769 | 0.16 | 13.05 | 1
March | 18 | 12AM to 1AM | 43 | 36.6 | 28 | 22.5 | 13.79 | 0.0772 | 0.15 | 13 | 1
March | 18 | 1AM to 2AM | 41 | 34.1 | 24.1 | 18.7 | 12.73 | 0.0775 | 0.12 | 12.93 | 1
March | 18 | 2AM to 3AM | 37.9 | 32.7 | 25 | 19.5 | 12.11 | 0.078 | 0.13 | 12.86 | 1
March | 18 | 3AM to 4AM | 37 | 31.5 | 24.1 | 18.7 | 11.77 | 0.0781 | 0.12 | 12.83 | 1
March | 18 | 4AM to 5AM | 36 | 30.9 | 24.1 | 18.7 | 11.51 | 0.0783 | 0.12 | 12.8 | 1
March | 18 | 5AM to 6AM | 36 | 31.9 | 27 | 21.4 | 11.93 | 0.0783 | 0.14 | 12.81 | 1
March | 18 | 6AM to 7AM | 37 | 32.8 | 27 | 21.4 | 12.19 | 0.0781 | 0.14 | 12.84 | 1
March | 18 | 7AM to 8AM | 41 | 35.1 | 27 | 21.4 | 13.15 | 0.0775 | 0.14 | 12.94 | 1
March | 18 | 8AM to 9AM | 45 | 36.6 | 25 | 19.5 | 13.81 | 0.0769 | 0.13 | 13.04 | 1
March | 18 | 9AM to 10AM | 46.9 | 37.7 | 25 | 19.5 | 14.28 | 0.0766 | 0.13 | 13.09 | 1
March | 18 | 10AM to 11AM | 48.9 | 39.4 | 27 | 21.4 | 15.06 | 0.0763 | 0.14 | 13.15 | 1
March | 18 | 11AM to 12PM | 48.9 | 40.5 | 30 | 24.7 | 15.57 | 0.0763 | 0.16 | 13.16 | 1
March | 18 | 12PM to 1PM | 48.9 | 41.3 | 32 | 27.1 | 15.93 | 0.0763 | 0.18 | 13.16 | 1
March | 18 | 1PM to 2PM | 48.9 | 41.7 | 33.1 | 28.3 | 16.12 | 0.0763 | 0.19 | 13.17 | 1
March | 18 | 2PM to 3PM | 48.9 | 40.5 | 30 | 24.7 | 15.57 | 0.0763 | 0.16 | 13.16 | 1
March | 18 | 3PM to 4PM | 48 | 40.4 | 30.9 | 25.8 | 15.51 | 0.0764 | 0.17 | 13.14 | 1
March | 18 | 4PM to 5PM | 46 | 40.5 | 34 | 29.3 | 15.58 | 0.0767 | 0.2 | 13.1 | 1
March | 18 | 5PM to 6PM | 45 | 40.4 | 35.1 | 30.6 | 15.52 | 0.0768 | 0.2 | 13.07 | 1
March | 18 | 6PM to 7PM | 44.1 | 39.9 | 35.1 | 30.6 | 15.31 | 0.077 | 0.2 | 13.05 | 1
March | 18 | 7PM to 8PM | 45 | 40.8 | 36 | 31.8 | 15.7 | 0.0768 | 0.21 | 13.08 | 1
March | 18 | 8PM to 9PM | 39.9 | 36 | 30.9 | 25.8 | 13.55 | 0.0776 | 0.17 | 12.93 | 1
March | 18 | 9PM to 10PM | 37.9 | 33 | 26.1 | 20.5 | 12.27 | 0.078 | 0.14 | 12.86 | 1
March | 18 | 10PM to 11PM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
March | 18 | 11PM to 12AM | 33.1 | 27.7 | 19 | 14.7 | 10.2 | 0.0788 | 0.1 | 12.72 | 1
March | 19 | 12AM to 1AM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
March | 19 | 1AM to 2AM | 30 | 23.8 | 10.9 | 9.9 | 8.72 | 0.0793 | 0.07 | 12.63 | 1
March | 19 | 2AM to 3AM | 28.9 | 23.4 | 12 | 10.4 | 8.54 | 0.0795 | 0.07 | 12.6 | 1
March | 19 | 3AM to 4AM | 28 | 23 | 12.9 | 10.9 | 8.4 | 0.0796 | 0.07 | 12.58 | 1
March | 19 | 4AM to 5AM | 28 | 23.3 | 14 | 11.5 | 8.49 | 0.0796 | 0.08 | 12.58 | 1
March | 19 | 5AM to 6AM | 27 | 23.2 | 16 | 12.7 | 8.41 | 0.0798 | 0.08 | 12.55 | 1
March | 19 | 6AM to 7AM | 28 | 24.4 | 18 | 13.9 | 8.87 | 0.0796 | 0.09 | 12.59 | 1
March | 19 | 7AM to 8AM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
March | 19 | 8AM to 9AM | 32 | 25.7 | 14 | 11.5 | 9.45 | 0.079 | 0.08 | 12.68 | 1
March | 19 | 9AM to 10AM | 33.1 | 26.3 | 14 | 11.5 | 9.71 | 0.0788 | 0.08 | 12.71 | 1
March | 19 | 10AM to 11AM | 35.1 | 27.2 | 12.9 | 10.9 | 10.09 | 0.0785 | 0.07 | 12.76 | 1
March | 19 | 11AM to 12PM | 37 | 28.6 | 14 | 11.5 | 10.66 | 0.0782 | 0.08 | 12.81 | 1
March | 19 | 12PM to 1PM | 36 | 28.5 | 16 | 12.7 | 10.58 | 0.0783 | 0.08 | 12.79 | 1
March | 19 | 1PM to 2PM | 36 | 28.7 | 17.1 | 13.3 | 10.68 | 0.0783 | 0.09 | 12.79 | 1
March | 19 | 2PM to 3PM | 36 | 28.5 | 16 | 12.7 | 10.58 | 0.0783 | 0.08 | 12.79 | 1
March | 19 | 3PM to 4PM | 37 | 29.1 | 16 | 12.7 | 10.84 | 0.0782 | 0.08 | 12.81 | 1
March | 19 | 4PM to 5PM | 35.1 | 27.5 | 14 | 11.5 | 10.18 | 0.0785 | 0.08 | 12.76 | 1
March | 19 | 5PM to 6PM | 35.1 | 27.2 | 12.9 | 10.9 | 10.09 | 0.0785 | 0.07 | 12.76 | 1
March | 19 | 6PM to 7PM | 33.1 | 26.1 | 12.9 | 10.9 | 9.61 | 0.0788 | 0.07 | 12.71 | 1
March | 19 | 7PM to 8PM | 32 | 25.7 | 14 | 11.5 | 9.45 | 0.079 | 0.08 | 12.68 | 1
March | 19 | 8PM to 9PM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
March | 19 | 9PM to 10PM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
March | 19 | 10PM to 11PM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
March | 19 | 11PM to 12AM | 28.9 | 24.1 | 15.1 | 12.1 | 8.8 | 0.0795 | 0.08 | 12.6 | 1
March | 20 | 12AM to 1AM | 28.9 | 24.1 | 15.1 | 12.1 | 8.8 | 0.0795 | 0.08 | 12.6 | 1
March | 20 | 1AM to 2AM | 28 | 24.1 | 17.1 | 13.3 | 8.78 | 0.0796 | 0.09 | 12.58 | 1
March | 20 | 2AM to 3AM | 26.1 | 22.9 | 17.1 | 13.3 | 8.3 | 0.0799 | 0.09 | 12.53 | 1
March | 20 | 3AM to 4AM | 26.1 | 22.9 | 17.1 | 13.3 | 8.3 | 0.0799 | 0.09 | 12.53 | 1
March | 20 | 4AM to 5AM | 27 | 23.7 | 18 | 13.9 | 8.61 | 0.0798 | 0.09 | 12.56 | 1
March | 20 | 5AM to 6AM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
March | 20 | 6AM to 7AM | 27 | 23.5 | 17.1 | 13.3 | 8.52 | 0.0798 | 0.09 | 12.56 | 1
March | 20 | 7AM to 8AM | 33.1 | 27.4 | 18 | 13.9 | 10.08 | 0.0788 | 0.09 | 12.72 | 1
March | 20 | 8AM to 9AM | 35.1 | 28 | 16 | 12.7 | 10.36 | 0.0785 | 0.08 | 12.76 | 1
March | 20 | 9AM to 10AM | 37.9 | 29.8 | 17.1 | 13.3 | 11.16 | 0.078 | 0.09 | 12.84 | 1
March | 20 | 10AM to 11AM | 41 | 31.7 | 18 | 13.9 | 11.99 | 0.0776 | 0.09 | 12.92 | 1
March | 20 | 11AM to 12PM | 42.1 | 32.8 | 17.1 | 13.3 | 12.16 | 0.0774 | 0.09 | 12.95 | 1
March | 20 | 12PM to 1PM | 46 | 34.8 | 16 | 12.7 | 13.01 | 0.0768 | 0.08 | 13.05 | 1
March | 20 | 1PM to 2PM | 48.9 | 36.4 | 16 | 12.7 | 13.7 | 0.0764 | 0.08 | 13.12 | 1
March | 20 | 2PM to 3PM | 51.1 | 37.8 | 17.1 | 13.3 | 14.33 | 0.076 | 0.09 | 13.18 | 1
March | 20 | 3PM to 4PM | 52 | 38.1 | 16 | 12.7 | 14.44 | 0.0759 | 0.08 | 13.2 | 0
March | 20 | 4PM to 5PM | 52 | 37.7 | 14 | 11.5 | 14.25 | 0.0759 | 0.08 | 13.2 | 0
March | 20 | 5PM to 6PM | 52 | 37.7 | 14 | 11.5 | 14.25 | 0.0759 | 0.08 | 13.2 | 0
March | 20 | 6PM to 7PM | 48.9 | 36.8 | 18 | 13.9 | 13.9 | 0.0763 | 0.09 | 13.12 | 1
March | 20 | 7PM to 8PM | 46.9 | 36.3 | 19.9 | 15.3 | 13.64 | 0.0766 | 0.1 | 13.08 | 1
March | 20 | 8PM to 9PM | 44.1 | 35.8 | 24.1 | 18.7 | 13.46 | 0.077 | 0.12 | 13.01 | 1
March | 20 | 9PM to 10PM | 43 | 35.5 | 25 | 19.5 | 13.33 | 0.0772 | 0.13 | 12.99 | 1
March | 20 | 10PM to 11PM | 43 | 35.2 | 24.1 | 18.7 | 13.2 | 0.0772 | 0.12 | 12.99 | 1
March | 20 | 11PM to 12AM | 42.1 | 34.7 | 24.1 | 18.7 | 12.99 | 0.0774 | 0.12 | 12.96 | 1
March | 21 | 12AM to 1AM | 41 | 34.1 | 24.1 | 18.7 | 12.73 | 0.0775 | 0.12 | 12.93 | 1
March | 21 | 1AM to 2AM | 39.9 | 33.5 | 24.1 | 18.7 | 12.47 | 0.0777 | 0.12 | 12.91 | 1
March | 21 | 2AM to 3AM | 39 | 33.3 | 25 | 19.5 | 12.37 | 0.0778 | 0.13 | 12.89 | 1
March | 21 | 3AM to 4AM | 39 | 33.3 | 25 | 19.5 | 12.37 | 0.0778 | 0.13 | 12.89 | 1
March | 21 | 4AM to 5AM | 39 | 33.7 | 26.1 | 20.5 | 12.53 | 0.0778 | 0.14 | 12.89 | 1
March | 21 | 5AM to 6AM | 37.9 | 33.4 | 27 | 21.4 | 12.41 | 0.078 | 0.14 | 12.86 | 1
March | 21 | 6AM to 7AM | 39.9 | 34.5 | 27 | 21.4 | 12.88 | 0.0777 | 0.14 | 12.91 | 1
March | 21 | 7AM to 8AM | 45 | 37.3 | 27 | 21.4 | 14.1 | 0.0769 | 0.14 | 13.04 | 1
March | 21 | 8AM to 9AM | 51.1 | 40.5 | 27 | 21.4 | 15.58 | 0.076 | 0.14 | 13.2 | 1
March | 21 | 9AM to 10AM | 57 | 43.9 | 28 | 22.5 | 17.18 | 0.0751 | 0.15 | 13.36 | 0
March | 21 | 10AM to 11AM | 61 | 46.1 | 28.9 | 23.5 | 18.29 | 0.0745 | 0.16 | 13.47 | 0
March | 21 | 11AM to 12PM | 64 | 47.2 | 28 | 22.5 | 18.88 | 0.0741 | 0.15 | 13.54 | 0
March | 21 | 12PM to 1PM | 66.9 | 48.2 | 27 | 21.4 | 19.4 | 0.0737 | 0.14 | 13.61 | 0
March | 21 | 1PM to 2PM | 68 | 48.4 | 26.1 | 20.5 | 19.52 | 0.0735 | 0.14 | 13.64 | 0
March | 21 | 2PM to 3PM | 70 | 50.1 | 28.9 | 23.5 | 20.46 | 0.0732 | 0.16 | 13.7 | 0
March | 21 | 3PM to 4PM | 70 | 50.1 | 28.9 | 23.5 | 20.46 | 0.0732 | 0.16 | 13.7 | 0
March | 21 | 4PM to 5PM | 69.1 | 50.1 | 30 | 24.7 | 20.44 | 0.0734 | 0.16 | 13.68 | 0
March | 21 | 5PM to 6PM | 66 | 49.4 | 32 | 27.1 | 20.07 | 0.0738 | 0.18 | 13.61 | 0
March | 21 | 6PM to 7PM | 63 | 48.7 | 34 | 29.3 | 19.68 | 0.0742 | 0.2 | 13.53 | 0
March | 21 | 7PM to 8PM | 61 | 48.1 | 35.1 | 30.6 | 19.4 | 0.0745 | 0.2 | 13.49 | 0
March | 21 | 8PM to 9PM | 59 | 48 | 37 | 33.2 | 19.31 | 0.0747 | 0.22 | 13.44 | 0
March | 21 | 9PM to 10PM | 57.9 | 47.5 | 37 | 33.2 | 19.05 | 0.0749 | 0.22 | 13.42 | 0
March | 21 | 10PM to 11PM | 57 | 47.1 | 37 | 33.2 | 18.83 | 0.075 | 0.22 | 13.39 | 0
March | 21 | 11PM to 12AM | 57 | 47.4 | 37.9 | 34.4 | 19.02 | 0.075 | 0.23 | 13.4 | 0
March | 22 | 12AM to 1AM | 57 | 47.4 | 37.9 | 34.4 | 19.02 | 0.075 | 0.23 | 13.4 | 0
March | 22 | 1AM to 2AM | 57 | 47.4 | 37.9 | 34.4 | 19.02 | 0.075 | 0.23 | 13.4 | 0
March | 22 | 2AM to 3AM | 57 | 47.4 | 37.9 | 34.4 | 19.02 | 0.075 | 0.23 | 13.4 | 0
March | 22 | 3AM to 4AM | 57 | 47.1 | 37 | 33.2 | 18.83 | 0.075 | 0.22 | 13.39 | 0
March | 22 | 4AM to 5AM | 57 | 47.1 | 37 | 33.2 | 18.83 | 0.075 | 0.22 | 13.39 | 0
March | 22 | 5AM to 6AM | 55.9 | 47.7 | 39.9 | 37.2 | 19.19 | 0.0752 | 0.25 | 13.38 | 0
March | 22 | 6AM to 7AM | 52 | 48.2 | 45 | 45.2 | 19.48 | 0.0757 | 0.3 | 13.3 | 0
March | 22 | 7AM to 8AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
March | 22 | 8AM to 9AM | 54 | 50.6 | 48 | 50.8 | 20.83 | 0.0754 | 0.34 | 13.37 | 0
March | 22 | 9AM to 10AM | 57.9 | 51.8 | 46.9 | 48.8 | 21.47 | 0.0748 | 0.32 | 13.46 | 0
March | 22 | 10AM to 11AM | 64.9 | 55.6 | 48.9 | 52.6 | 23.77 | 0.0738 | 0.35 | 13.66 | 0
March | 22 | 11AM to 12PM | 66.9 | 56.4 | 48.9 | 52.6 | 24.25 | 0.0735 | 0.35 | 13.71 | 0
March | 22 | 12PM to 1PM | 64 | 54.8 | 48 | 50.8 | 23.28 | 0.0739 | 0.34 | 13.63 | 0
March | 22 | 1PM to 2PM | 60.1 | 52.3 | 46 | 47.1 | 21.74 | 0.0745 | 0.31 | 13.51 | 0
March | 22 | 2PM to 3PM | 60.1 | 51.3 | 44.1 | 43.6 | 21.2 | 0.0745 | 0.29 | 13.5 | 0
March | 22 | 3PM to 4PM | 57.9 | 49.9 | 43 | 41.9 | 20.4 | 0.0748 | 0.28 | 13.44 | 0
March | 22 | 4PM to 5PM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
March | 22 | 5PM to 6PM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
March | 22 | 6PM to 7PM | 55 | 48.7 | 43 | 41.9 | 19.7 | 0.0753 | 0.28 | 13.37 | 0
March | 22 | 7PM to 8PM | 54 | 47.3 | 41 | 38.8 | 18.96 | 0.0754 | 0.26 | 13.33 | 0
March | 22 | 8PM to 9PM | 50 | 44.9 | 39.9 | 37.2 | 17.75 | 0.076 | 0.25 | 13.22 | 1
March | 22 | 9PM to 10PM | 45 | 41.6 | 37.9 | 34.4 | 16.1 | 0.0768 | 0.23 | 13.08 | 1
March | 22 | 10PM to 11PM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
March | 22 | 11PM to 12AM | 42.1 | 38.1 | 33.1 | 28.3 | 14.47 | 0.0773 | 0.19 | 12.99 | 1
March | 23 | 12AM to 1AM | 41 | 37.1 | 32 | 27.1 | 14.02 | 0.0775 | 0.18 | 12.96 | 1
March | 23 | 1AM to 2AM | 39 | 35.2 | 30 | 24.7 | 13.17 | 0.0778 | 0.16 | 12.9 | 1
March | 23 | 2AM to 3AM | 37 | 33.3 | 28 | 22.5 | 12.36 | 0.0781 | 0.15 | 12.84 | 1
March | 23 | 3AM to 4AM | 35.1 | 30.7 | 25 | 19.5 | 11.42 | 0.0784 | 0.13 | 12.78 | 1
March | 23 | 4AM to 5AM | 33.1 | 28.3 | 21 | 16.2 | 10.42 | 0.0788 | 0.11 | 12.72 | 1
March | 23 | 5AM to 6AM | 32 | 28 | 21.9 | 16.9 | 10.27 | 0.079 | 0.11 | 12.7 | 1
March | 23 | 6AM to 7AM | 33.1 | 27.9 | 19.9 | 15.3 | 10.3 | 0.0788 | 0.1 | 12.72 | 1
March | 23 | 7AM to 8AM | 34 | 26.8 | 14 | 11.5 | 9.92 | 0.0787 | 0.08 | 12.73 | 1
March | 23 | 8AM to 9AM | 36 | 27.5 | 12 | 10.4 | 10.23 | 0.0784 | 0.07 | 12.78 | 1
March | 23 | 9AM to 10AM | 36 | 27.7 | 12.9 | 10.9 | 10.31 | 0.0784 | 0.07 | 12.78 | 1
March | 23 | 10AM to 11AM | 36 | 27.7 | 12.9 | 10.9 | 10.31 | 0.0784 | 0.07 | 12.78 | 1
March | 23 | 11AM to 12PM | 36 | 27.5 | 12 | 10.4 | 10.23 | 0.0784 | 0.07 | 12.78 | 1
March | 23 | 12PM to 1PM | 34 | 26.8 | 14 | 11.5 | 9.92 | 0.0787 | 0.08 | 12.73 | 1
March | 23 | 1PM to 2PM | 30.9 | 26.1 | 18 | 13.9 | 9.56 | 0.0791 | 0.09 | 12.66 | 1
March | 23 | 2PM to 3PM | 28 | 24.4 | 18 | 13.9 | 8.87 | 0.0796 | 0.09 | 12.59 | 1
March | 23 | 3PM to 4PM | 26.1 | 23.5 | 19 | 14.7 | 8.51 | 0.0799 | 0.1 | 12.54 | 1
March | 23 | 4PM to 5PM | 25 | 22.8 | 19 | 14.7 | 8.25 | 0.0801 | 0.1 | 12.51 | 1
March | 23 | 5PM to 6PM | 24.1 | 22.6 | 19.9 | 15.3 | 8.13 | 0.0803 | 0.1 | 12.49 | 1
March | 23 | 6PM to 7PM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
March | 23 | 7PM to 8PM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
March | 23 | 8PM to 9PM | 23 | 22.3 | 21 | 16.2 | 8 | 0.0804 | 0.11 | 12.46 | 1
March | 23 | 9PM to 10PM | 23 | 22.3 | 21 | 16.2 | 8 | 0.0804 | 0.11 | 12.46 | 1
March | 23 | 10PM to 11PM | 23 | 21.9 | 19.9 | 15.3 | 7.87 | 0.0804 | 0.1 | 12.46 | 1
March | 23 | 11PM to 12AM | 24.1 | 22.6 | 19.9 | 15.3 | 8.13 | 0.0803 | 0.1 | 12.49 | 1
March | 24 | 12AM to 1AM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
March | 24 | 1AM to 2AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
March | 24 | 2AM to 3AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
March | 24 | 3AM to 4AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
March | 24 | 4AM to 5AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
March | 24 | 5AM to 6AM | 25 | 23.8 | 21.9 | 16.9 | 8.58 | 0.0801 | 0.11 | 12.52 | 1
March | 24 | 6AM to 7AM | 25 | 23.5 | 21 | 16.2 | 8.47 | 0.0801 | 0.11 | 12.51 | 1
March | 24 | 7AM to 8AM | 27 | 24.7 | 21 | 16.2 | 8.95 | 0.0798 | 0.11 | 12.56 | 1
March | 24 | 8AM to 9AM | 28 | 25.4 | 21 | 16.2 | 9.21 | 0.0796 | 0.11 | 12.59 | 1
March | 24 | 9AM to 10AM | 30.9 | 26.7 | 19.9 | 15.3 | 9.78 | 0.0791 | 0.1 | 12.66 | 1
March | 24 | 10AM to 11AM | 32 | 27.3 | 19.9 | 15.3 | 10.04 | 0.079 | 0.1 | 12.69 | 1
March | 24 | 11AM to 12PM | 32 | 27 | 19 | 14.7 | 9.94 | 0.079 | 0.1 | 12.69 | 1
March | 24 | 12PM to 1PM | 34 | 27.9 | 18 | 13.9 | 10.3 | 0.0787 | 0.09 | 12.74 | 1
March | 24 | 1PM to 2PM | 34 | 28.2 | 19 | 14.7 | 10.42 | 0.0786 | 0.1 | 12.74 | 1
March | 24 | 2PM to 3PM | 33.1 | 27.4 | 18 | 13.9 | 10.08 | 0.0788 | 0.09 | 12.72 | 1
March | 24 | 3PM to 4PM | 34 | 27.1 | 15.1 | 12.1 | 10.02 | 0.0787 | 0.08 | 12.73 | 1
March | 24 | 4PM to 5PM | 34 | 27.6 | 17.1 | 13.3 | 10.21 | 0.0787 | 0.09 | 12.74 | 1
March | 24 | 5PM to 6PM | 33.1 | 27.1 | 17.1 | 13.3 | 9.99 | 0.0788 | 0.09 | 12.71 | 1
March | 24 | 6PM to 7PM | 33.1 | 26.8 | 16 | 12.7 | 9.89 | 0.0788 | 0.08 | 12.71 | 1
March | 24 | 7PM to 8PM | 33.1 | 27.4 | 18 | 13.9 | 10.08 | 0.0788 | 0.09 | 12.72 | 1
March | 24 | 8PM to 9PM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
March | 24 | 9PM to 10PM | 30 | 26.2 | 19.9 | 15.3 | 9.56 | 0.0793 | 0.1 | 12.64 | 1
March | 24 | 10PM to 11PM | 28.9 | 24.1 | 15.1 | 12.1 | 8.8 | 0.0795 | 0.08 | 12.6 | 1
March | 24 | 11PM to 12AM | 28.9 | 24.1 | 15.1 | 12.1 | 8.8 | 0.0795 | 0.08 | 12.6 | 1
March | 25 | 12AM to 1AM | 26.1 | 22.6 | 16 | 12.7 | 8.2 | 0.0799 | 0.08 | 12.53 | 1
March | 25 | 1AM to 2AM | 25 | 21.7 | 15.1 | 12.1 | 7.85 | 0.0801 | 0.08 | 12.5 | 1
March | 25 | 2AM to 3AM | 24.1 | 21.1 | 15.1 | 12.1 | 7.63 | 0.0803 | 0.08 | 12.48 | 1
March | 25 | 3AM to 4AM | 25 | 21.7 | 15.1 | 12.1 | 7.85 | 0.0801 | 0.08 | 12.5 | 1
March | 25 | 4AM to 5AM | 24.1 | 20.8 | 14 | 11.5 | 7.54 | 0.0803 | 0.08 | 12.48 | 1
March | 25 | 5AM to 6AM | 23 | 20.4 | 15.1 | 12.1 | 7.37 | 0.0805 | 0.08 | 12.45 | 1
March | 25 | 6AM to 7AM | 21.9 | 19.4 | 14 | 11.5 | 7.02 | 0.0806 | 0.08 | 12.42 | 1
March | 25 | 7AM to 8AM | 28.9 | 24.1 | 15.1 | 12.1 | 8.8 | 0.0795 | 0.08 | 12.6 | 1
March | 25 | 8AM to 9AM | 33.1 | 27.1 | 17.1 | 13.3 | 9.99 | 0.0788 | 0.09 | 12.71 | 1
March | 25 | 9AM to 10AM | 36 | 29 | 18 | 13.9 | 10.78 | 0.0783 | 0.09 | 12.79 | 1
March | 25 | 10AM to 11AM | 39 | 31 | 19 | 14.7 | 11.63 | 0.0779 | 0.1 | 12.87 | 1
March | 25 | 11AM to 12PM | 42.1 | 33 | 18 | 13.9 | 12.25 | 0.0774 | 0.09 | 12.95 | 1
March | 25 | 12PM to 1PM | 42.1 | 33 | 18 | 13.9 | 12.25 | 0.0774 | 0.09 | 12.95 | 1
March | 25 | 1PM to 2PM | 44.1 | 34.1 | 18 | 13.9 | 12.73 | 0.0771 | 0.09 | 13 | 1
March | 25 | 2PM to 3PM | 42.1 | 33.3 | 19 | 14.7 | 12.37 | 0.0774 | 0.1 | 12.95 | 1
March | 25 | 3PM to 4PM | 44.1 | 34.1 | 18 | 13.9 | 12.73 | 0.0771 | 0.09 | 13 | 1
March | 25 | 4PM to 5PM | 42.1 | 33.5 | 19.9 | 15.3 | 12.47 | 0.0774 | 0.1 | 12.95 | 1
March | 25 | 5PM to 6PM | 39.9 | 31.7 | 19.9 | 15.3 | 11.95 | 0.0777 | 0.1 | 12.9 | 1
March | 25 | 6PM to 7PM | 39 | 32 | 21 | 16.2 | 11.86 | 0.0778 | 0.11 | 12.88 | 1
March | 25 | 7PM to 8PM | 37 | 30.5 | 21 | 16.2 | 11.38 | 0.0782 | 0.11 | 12.82 | 1
March | 25 | 8PM to 9PM | 35.1 | 29.4 | 21 | 16.2 | 10.9 | 0.0785 | 0.11 | 12.77 | 1
March | 25 | 9PM to 10PM | 33.1 | 27.9 | 19.9 | 15.3 | 10.3 | 0.0788 | 0.1 | 12.72 | 1
March | 25 | 10PM to 11PM | 34 | 27.9 | 18 | 13.9 | 10.3 | 0.0787 | 0.09 | 12.74 | 1
March | 25 | 11PM to 12AM | 32 | 27 | 19 | 14.7 | 9.94 | 0.079 | 0.1 | 12.69 | 1
March | 26 | 12AM to 1AM | 30.9 | 26.1 | 18 | 13.9 | 9.56 | 0.0791 | 0.09 | 12.66 | 1
March | 26 | 1AM to 2AM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
March | 26 | 2AM to 3AM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
March | 26 | 3AM to 4AM | 28.9 | 25.5 | 19.9 | 15.3 | 9.3 | 0.0795 | 0.1 | 12.61 | 1
March | 26 | 4AM to 5AM | 28.9 | 25.5 | 19.9 | 15.3 | 9.3 | 0.0795 | 0.1 | 12.61 | 1
March | 26 | 5AM to 6AM | 30 | 26.5 | 21 | 16.2 | 9.69 | 0.0793 | 0.11 | 12.64 | 1
March | 26 | 6AM to 7AM | 32 | 28 | 21.9 | 16.9 | 10.27 | 0.079 | 0.11 | 12.7 | 1
March | 26 | 7AM to 8AM | 34 | 29.4 | 23 | 17.8 | 10.89 | 0.0786 | 0.12 | 12.75 | 1
March | 26 | 8AM to 9AM | 37 | 31.5 | 24.1 | 18.7 | 11.77 | 0.0781 | 0.12 | 12.83 | 1
March | 26 | 9AM to 10AM | 41 | 34.8 | 26.1 | 20.5 | 13.01 | 0.0775 | 0.14 | 12.94 | 1
March | 26 | 10AM to 11AM | 44.1 | 35.8 | 24.1 | 18.7 | 13.46 | 0.077 | 0.12 | 13.01 | 1
March | 26 | 11AM to 12PM | 46 | 36.9 | 24.1 | 18.7 | 13.94 | 0.0767 | 0.12 | 13.06 | 1
March | 26 | 12PM to 1PM | 48 | 37.4 | 21.9 | 16.9 | 14.14 | 0.0765 | 0.11 | 13.11 | 1
March | 26 | 1PM to 2PM | 48 | 37.7 | 23 | 17.8 | 14.27 | 0.0765 | 0.12 | 13.11 | 1
March | 26 | 2PM to 3PM | 48.9 | 38.2 | 23 | 17.8 | 14.49 | 0.0763 | 0.12 | 13.14 | 1
March | 26 | 3PM to 4PM | 50 | 38.4 | 21.9 | 16.9 | 14.61 | 0.0762 | 0.11 | 13.16 | 1
March | 26 | 4PM to 5PM | 50 | 39.1 | 24.1 | 18.7 | 14.9 | 0.0762 | 0.12 | 13.17 | 1
March | 26 | 5PM to 6PM | 46.9 | 37.1 | 23 | 17.8 | 14.01 | 0.0766 | 0.12 | 13.08 | 1
March | 26 | 6PM to 7PM | 45 | 35.7 | 21.9 | 16.9 | 13.4 | 0.0769 | 0.11 | 13.03 | 1
March | 26 | 7PM to 8PM | 45 | 35.7 | 21.9 | 16.9 | 13.4 | 0.0769 | 0.11 | 13.03 | 1
March | 26 | 8PM to 9PM | 44.1 | 35.5 | 23 | 17.8 | 13.32 | 0.0771 | 0.12 | 13.01 | 1
March | 26 | 9PM to 10PM | 41 | 33.8 | 23 | 17.8 | 12.58 | 0.0775 | 0.12 | 12.93 | 1
March | 26 | 10PM to 11PM | 39 | 32.3 | 21.9 | 16.9 | 11.97 | 0.0778 | 0.11 | 12.88 | 1
March | 26 | 11PM to 12AM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
March | 27 | 12AM to 1AM | 36 | 30.9 | 24.1 | 18.7 | 11.51 | 0.0783 | 0.12 | 12.8 | 1
March | 27 | 1AM to 2AM | 34 | 29.8 | 24.1 | 18.7 | 11.03 | 0.0786 | 0.12 | 12.75 | 1
March | 27 | 2AM to 3AM | 32 | 28.3 | 23 | 17.8 | 10.41 | 0.0789 | 0.12 | 12.7 | 1
March | 27 | 3AM to 4AM | 34 | 29.8 | 24.1 | 18.7 | 11.03 | 0.0786 | 0.12 | 12.75 | 1
March | 27 | 4AM to 5AM | 33.1 | 29.3 | 24.1 | 18.7 | 10.82 | 0.0788 | 0.12 | 12.73 | 1
March | 27 | 5AM to 6AM | 33.1 | 28.6 | 21.9 | 16.9 | 10.53 | 0.0788 | 0.11 | 12.72 | 1
March | 27 | 6AM to 7AM | 33.1 | 28.9 | 23 | 17.8 | 10.67 | 0.0788 | 0.12 | 12.73 | 1
March | 27 | 7AM to 8AM | 41 | 33.2 | 21 | 16.2 | 12.33 | 0.0775 | 0.11 | 12.93 | 1
March | 27 | 8AM to 9AM | 46 | 36.6 | 23 | 17.8 | 13.8 | 0.0768 | 0.12 | 13.06 | 1
March | 27 | 9AM to 10AM | 48 | 36.4 | 18 | 13.9 | 13.68 | 0.0765 | 0.09 | 13.1 | 1
March | 27 | 10AM to 11AM | 50 | 37.7 | 19 | 14.7 | 14.28 | 0.0762 | 0.1 | 13.15 | 1
March | 27 | 11AM to 12PM | 52 | 39 | 19.9 | 15.3 | 14.85 | 0.0759 | 0.1 | 13.21 | 0
March | 27 | 12PM to 1PM | 53.1 | 39.3 | 19 | 14.7 | 15.01 | 0.0757 | 0.1 | 13.23 | 0
March | 27 | 1PM to 2PM | 54 | 39.8 | 19 | 14.7 | 15.23 | 0.0756 | 0.1 | 13.26 | 0
March | 27 | 2PM to 3PM | 55 | 40.6 | 19.9 | 15.3 | 15.59 | 0.0754 | 0.1 | 13.29 | 0
March | 27 | 3PM to 4PM | 55 | 41.4 | 23 | 17.8 | 15.97 | 0.0754 | 0.12 | 13.29 | 0
March | 27 | 4PM to 5PM | 54 | 40.8 | 23 | 17.8 | 15.71 | 0.0756 | 0.12 | 13.27 | 0
March | 27 | 5PM to 6PM | 52 | 40.1 | 24.1 | 18.7 | 15.37 | 0.0759 | 0.12 | 13.22 | 0
March | 27 | 6PM to 7PM | 51.1 | 39.6 | 24.1 | 18.7 | 15.16 | 0.076 | 0.12 | 13.19 | 1
March | 27 | 7PM to 8PM | 50 | 39.1 | 24.1 | 18.7 | 14.9 | 0.0762 | 0.12 | 13.17 | 1
March | 27 | 8PM to 9PM | 48 | 38.6 | 26.1 | 20.5 | 14.7 | 0.0764 | 0.14 | 13.12 | 1
March | 27 | 9PM to 10PM | 46.9 | 38.7 | 28 | 22.5 | 14.75 | 0.0766 | 0.15 | 13.1 | 1
March | 27 | 10PM to 11PM | 46 | 38.3 | 28 | 22.5 | 14.53 | 0.0767 | 0.15 | 13.08 | 1
March | 27 | 11PM to 12AM | 45 | 37.7 | 28 | 22.5 | 14.27 | 0.0769 | 0.15 | 13.05 | 1
March | 28 | 12AM to 1AM | 45 | 37.7 | 28 | 22.5 | 14.27 | 0.0769 | 0.15 | 13.05 | 1
March | 28 | 1AM to 2AM | 44.1 | 37.2 | 28 | 22.5 | 14.06 | 0.077 | 0.15 | 13.02 | 1
March | 28 | 2AM to 3AM | 43 | 36.2 | 27 | 21.4 | 13.62 | 0.0772 | 0.14 | 12.99 | 1
March | 28 | 3AM to 4AM | 43 | 35.9 | 26.1 | 20.5 | 13.49 | 0.0772 | 0.14 | 12.99 | 1
March | 28 | 4AM to 5AM | 43 | 35.5 | 25 | 19.5 | 13.33 | 0.0772 | 0.13 | 12.99 | 1
March | 28 | 5AM to 6AM | 43 | 35.9 | 26.1 | 20.5 | 13.49 | 0.0772 | 0.14 | 12.99 | 1
March | 28 | 6AM to 7AM | 44.1 | 36.5 | 26.1 | 20.5 | 13.75 | 0.077 | 0.14 | 13.02 | 1
March | 28 | 7AM to 8AM | 42.1 | 37.7 | 32 | 27.1 | 14.28 | 0.0773 | 0.18 | 12.99 | 1
March | 28 | 8AM to 9AM | 42.1 | 39.3 | 36 | 31.8 | 15 | 0.0773 | 0.21 | 13 | 1
March | 28 | 9AM to 10AM | 46 | 41.3 | 36 | 31.8 | 15.96 | 0.0767 | 0.21 | 13.1 | 1
March | 28 | 10AM to 11AM | 46.9 | 40.7 | 33.1 | 28.3 | 15.64 | 0.0765 | 0.19 | 13.12 | 1
March | 28 | 11AM to 12PM | 48.9 | 41.7 | 33.1 | 28.3 | 16.12 | 0.0763 | 0.19 | 13.17 | 1
March | 28 | 12PM to 1PM | 50 | 42.5 | 34 | 29.3 | 16.54 | 0.0761 | 0.2 | 13.2 | 1
March | 28 | 1PM to 2PM | 50 | 44.1 | 37.9 | 34.4 | 17.32 | 0.076 | 0.23 | 13.21 | 1
March | 28 | 2PM to 3PM | 51.1 | 45.1 | 39 | 35.9 | 17.81 | 0.0759 | 0.24 | 13.25 | 1
March | 28 | 3PM to 4PM | 50 | 44.1 | 37.9 | 34.4 | 17.32 | 0.076 | 0.23 | 13.21 | 1
March | 28 | 4PM to 5PM | 46.9 | 44 | 41 | 38.8 | 17.26 | 0.0765 | 0.26 | 13.15 | 1
March | 28 | 5PM to 6PM | 46.9 | 44.5 | 42.1 | 40.4 | 17.52 | 0.0765 | 0.27 | 13.15 | 1
March | 28 | 6PM to 7PM | 46 | 43.5 | 41 | 38.8 | 17.04 | 0.0766 | 0.26 | 13.12 | 1
March | 28 | 7PM to 8PM | 45 | 43.5 | 42.1 | 40.4 | 17.04 | 0.0768 | 0.27 | 13.1 | 1
March | 28 | 8PM to 9PM | 45 | 43.5 | 42.1 | 40.4 | 17.04 | 0.0768 | 0.27 | 13.1 | 1
March | 28 | 9PM to 10PM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
March | 28 | 10PM to 11PM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
March | 28 | 11PM to 12AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
March | 29 | 12AM to 1AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
March | 29 | 1AM to 2AM | 45 | 44.5 | 44.1 | 43.6 | 17.53 | 0.0767 | 0.29 | 13.11 | 1
March | 29 | 2AM to 3AM | 45 | 44.5 | 44.1 | 43.6 | 17.53 | 0.0767 | 0.29 | 13.11 | 1
March | 29 | 3AM to 4AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 29 | 4AM to 5AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 29 | 5AM to 6AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 29 | 6AM to 7AM | 46.9 | 46.5 | 46 | 47.1 | 18.55 | 0.0764 | 0.31 | 13.17 | 1
March | 29 | 7AM to 8AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
March | 29 | 8AM to 9AM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
March | 29 | 9AM to 10AM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
March | 29 | 10AM to 11AM | 51.1 | 49.9 | 48.9 | 52.6 | 20.4 | 0.0758 | 0.35 | 13.3 | 1
March | 29 | 11AM to 12PM | 50 | 49.4 | 48.9 | 52.6 | 20.14 | 0.0759 | 0.35 | 13.27 | 1
March | 29 | 12PM to 1PM | 52 | 50.3 | 48.9 | 52.6 | 20.62 | 0.0756 | 0.35 | 13.32 | 0
March | 29 | 1PM to 2PM | 53.1 | 50.7 | 48.9 | 52.6 | 20.88 | 0.0755 | 0.35 | 13.35 | 0
March | 29 | 2PM to 3PM | 51.1 | 49.9 | 48.9 | 52.6 | 20.4 | 0.0758 | 0.35 | 13.3 | 1
March | 29 | 3PM to 4PM | 51.1 | 49.4 | 48 | 50.8 | 20.13 | 0.0758 | 0.34 | 13.29 | 1
March | 29 | 4PM to 5PM | 52 | 49.8 | 48 | 50.8 | 20.34 | 0.0756 | 0.34 | 13.31 | 0
March | 29 | 5PM to 6PM | 51.1 | 49.4 | 48 | 50.8 | 20.13 | 0.0758 | 0.34 | 13.29 | 1
March | 29 | 6PM to 7PM | 51.1 | 49.4 | 48 | 50.8 | 20.13 | 0.0758 | 0.34 | 13.29 | 1
March | 29 | 7PM to 8PM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
March | 29 | 8PM to 9PM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
March | 29 | 9PM to 10PM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
March | 29 | 10PM to 11PM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
March | 29 | 11PM to 12AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
March | 30 | 12AM to 1AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 30 | 1AM to 2AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 30 | 2AM to 3AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 30 | 3AM to 4AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 30 | 4AM to 5AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 30 | 5AM to 6AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 30 | 6AM to 7AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 30 | 7AM to 8AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 30 | 8AM to 9AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 30 | 9AM to 10AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
March | 30 | 10AM to 11AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
March | 30 | 11AM to 12PM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
March | 30 | 12PM to 1PM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
March | 30 | 1PM to 2PM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
March | 30 | 2PM to 3PM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
March | 30 | 3PM to 4PM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
March | 30 | 4PM to 5PM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
March | 30 | 5PM to 6PM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
March | 30 | 6PM to 7PM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
March | 30 | 7PM to 8PM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
March | 30 | 8PM to 9PM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
March | 30 | 9PM to 10PM | 48 | 46.4 | 45 | 45.2 | 18.51 | 0.0763 | 0.3 | 13.19 | 1
March | 30 | 10PM to 11PM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 30 | 11PM to 12AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 31 | 12AM to 1AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 31 | 1AM to 2AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 31 | 2AM to 3AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 31 | 3AM to 4AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 31 | 4AM to 5AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 31 | 5AM to 6AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
March | 31 | 6AM to 7AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 31 | 7AM to 8AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 31 | 8AM to 9AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
March | 31 | 9AM to 10AM | 50 | 47.3 | 45 | 45.2 | 19 | 0.076 | 0.3 | 13.25 | 1
March | 31 | 10AM to 11AM | 52 | 48.8 | 46 | 47.1 | 19.77 | 0.0757 | 0.31 | 13.3 | 0
March | 31 | 11AM to 12PM | 53.1 | 49.7 | 46.9 | 48.8 | 20.29 | 0.0755 | 0.32 | 13.34 | 0
March | 31 | 12PM to 1PM | 55.9 | 50.9 | 46.9 | 48.8 | 20.99 | 0.0751 | 0.32 | 13.41 | 0
March | 31 | 1PM to 2PM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
March | 31 | 2PM to 3PM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
March | 31 | 3PM to 4PM | 57 | 52.4 | 48.9 | 52.6 | 21.84 | 0.0749 | 0.35 | 13.45 | 0
March | 31 | 4PM to 5PM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
March | 31 | 5PM to 6PM | 55.9 | 51.5 | 48 | 50.8 | 21.31 | 0.0751 | 0.34 | 13.42 | 0
March | 31 | 6PM to 7PM | 55 | 51.1 | 48 | 50.8 | 21.09 | 0.0752 | 0.34 | 13.39 | 0
March | 31 | 7PM to 8PM | 54 | 51.1 | 48.9 | 52.6 | 21.1 | 0.0753 | 0.35 | 13.37 | 0
March | 31 | 8PM to 9PM | 54 | 51.1 | 48.9 | 52.6 | 21.1 | 0.0753 | 0.35 | 13.37 | 0
March | 31 | 9PM to 10PM | 52.3 | 48.6 | 45.5 | 46.1 | 19.71 | 0.0756 | 0.31 | 13.31 | 0
March | 31 | 10PM to 11PM | 50.5 | 46.2 | 42.1 | 40.4 | 18.39 | 0.0759 | 0.27 | 13.25 | 1
March | 31 | 11PM to 12AM | 48.9 | 43.9 | 38.7 | 35.4 | 17.21 | 0.0762 | 0.24 | 13.19 | 1
April | 1 | 12AM to 1AM | 47.1 | 41.6 | 35.2 | 30.9 | 16.08 | 0.0765 | 0.21 | 13.13 | 1
April | 1 | 1AM to 2AM | 45.5 | 39.5 | 32 | 27.1 | 15.11 | 0.0768 | 0.18 | 13.08 | 1
April | 1 | 2AM to 3AM | 43.7 | 37.2 | 28.6 | 23.1 | 14.06 | 0.0771 | 0.15 | 13.02 | 1
April | 1 | 3AM to 4AM | 42.1 | 35 | 25 | 19.5 | 13.11 | 0.0773 | 0.13 | 12.96 | 1
April | 1 | 4AM to 5AM | 42.1 | 35.4 | 26.1 | 20.5 | 13.27 | 0.0773 | 0.14 | 12.97 | 1
April | 1 | 5AM to 6AM | 41 | 35.1 | 27 | 21.4 | 13.15 | 0.0775 | 0.14 | 12.94 | 1
April | 1 | 6AM to 7AM | 43 | 36.9 | 28.9 | 23.5 | 13.94 | 0.0772 | 0.16 | 13 | 1
April | 1 | 7AM to 8AM | 51.1 | 41.9 | 30.9 | 25.8 | 16.25 | 0.0759 | 0.17 | 13.22 | 1
April | 1 | 8AM to 9AM | 55.9 | 45.4 | 34 | 29.3 | 17.98 | 0.0752 | 0.2 | 13.35 | 0
April | 1 | 9AM to 10AM | 60.1 | 47.7 | 35.1 | 30.6 | 19.18 | 0.0746 | 0.2 | 13.46 | 0
April | 1 | 10AM to 11AM | 63 | 49.3 | 36 | 31.8 | 20.05 | 0.0742 | 0.21 | 13.54 | 0
April | 1 | 11AM to 12PM | 66.9 | 51.4 | 37 | 33.2 | 21.23 | 0.0736 | 0.22 | 13.65 | 0
April | 1 | 12PM to 1PM | 68 | 52.2 | 37.9 | 34.4 | 21.68 | 0.0735 | 0.23 | 13.68 | 0
April | 1 | 1PM to 2PM | 71.1 | 53.5 | 37.9 | 34.4 | 22.42 | 0.073 | 0.23 | 13.76 | 0
April | 1 | 2PM to 3PM | 73 | 54.7 | 39 | 35.9 | 23.13 | 0.0728 | 0.24 | 13.82 | 0
April | 1 | 3PM to 4PM | 72 | 53.5 | 37 | 33.2 | 22.45 | 0.0729 | 0.22 | 13.78 | 0
April | 1 | 4PM to 5PM | 72 | 52 | 32 | 27.1 | 21.5 | 0.073 | 0.18 | 13.76 | 0
April | 1 | 5PM to 6PM | 70 | 51.1 | 32 | 27.1 | 21.02 | 0.0732 | 0.18 | 13.71 | 0
April | 1 | 6PM to 7PM | 66.9 | 49.8 | 32 | 27.1 | 20.28 | 0.0737 | 0.18 | 13.63 | 0
April | 1 | 7PM to 8PM | 64 | 51.3 | 39.9 | 37.2 | 21.15 | 0.074 | 0.25 | 13.59 | 0
April | 1 | 8PM to 9PM | 63 | 51.7 | 42.1 | 40.4 | 21.4 | 0.0741 | 0.27 | 13.57 | 0
April | 1 | 9PM to 10PM | 61 | 51.3 | 43 | 41.9 | 21.14 | 0.0744 | 0.28 | 13.52 | 0
April | 1 | 10PM to 11PM | 57.9 | 49.9 | 43 | 41.9 | 20.4 | 0.0748 | 0.28 | 13.44 | 0
April | 1 | 11PM to 12AM | 57 | 49.5 | 43 | 41.9 | 20.18 | 0.075 | 0.28 | 13.42 | 0
April | 2 | 12AM to 1AM | 55 | 48.7 | 43 | 41.9 | 19.7 | 0.0753 | 0.28 | 13.37 | 0
April | 2 | 1AM to 2AM | 54 | 48.2 | 43 | 41.9 | 19.44 | 0.0754 | 0.28 | 13.34 | 0
April | 2 | 2AM to 3AM | 54 | 47.8 | 42.1 | 40.4 | 19.22 | 0.0754 | 0.27 | 13.33 | 0
April | 2 | 3AM to 4AM | 53.1 | 46.4 | 39.9 | 37.2 | 18.49 | 0.0756 | 0.25 | 13.3 | 0
April | 2 | 4AM to 5AM | 53.1 | 45.6 | 37.9 | 34.4 | 18.06 | 0.0756 | 0.23 | 13.29 | 0
April | 2 | 5AM to 6AM | 53.1 | 43.7 | 33.1 | 28.3 | 17.12 | 0.0756 | 0.19 | 13.27 | 0
April | 2 | 6AM to 7AM | 54 | 44.2 | 33.1 | 28.3 | 17.34 | 0.0755 | 0.19 | 13.3 | 0
April | 2 | 7AM to 8AM | 59 | 48.3 | 37.9 | 34.4 | 19.5 | 0.0747 | 0.23 | 13.45 | 0
April | 2 | 8AM to 9AM | 63 | 52.1 | 43 | 41.9 | 21.63 | 0.0741 | 0.28 | 13.57 | 0
April | 2 | 9AM to 10AM | 64 | 53 | 44.1 | 43.6 | 22.17 | 0.074 | 0.29 | 13.61 | 0
April | 2 | 10AM to 11AM | 64.9 | 54.3 | 46 | 47.1 | 22.92 | 0.0738 | 0.31 | 13.64 | 0
April | 2 | 11AM to 12PM | 64 | 53.9 | 46 | 47.1 | 22.7 | 0.0739 | 0.31 | 13.62 | 0
April | 2 | 12PM to 1PM | 64.9 | 54.7 | 46.9 | 48.8 | 23.18 | 0.0738 | 0.32 | 13.65 | 0
April | 2 | 1PM to 2PM | 64 | 54.3 | 46.9 | 48.8 | 22.96 | 0.0739 | 0.32 | 13.62 | 0
April | 2 | 2PM to 3PM | 62.1 | 54.5 | 48.9 | 52.6 | 23.07 | 0.0742 | 0.35 | 13.58 | 0
April | 2 | 3PM to 4PM | 62.1 | 54 | 48 | 50.8 | 22.8 | 0.0742 | 0.34 | 13.58 | 0
April | 2 | 4PM to 5PM | 61 | 54.6 | 50 | 54.7 | 23.15 | 0.0743 | 0.36 | 13.56 | 0
April | 2 | 5PM to 6PM | 60.1 | 53.7 | 48.9 | 52.6 | 22.59 | 0.0745 | 0.35 | 13.53 | 0
April | 2 | 6PM to 7PM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
April | 2 | 7PM to 8PM | 50 | 47.3 | 45 | 45.2 | 19 | 0.076 | 0.3 | 13.25 | 1
April | 2 | 8PM to 9PM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
April | 2 | 9PM to 10PM | 44.1 | 41.6 | 39 | 35.9 | 16.11 | 0.0769 | 0.24 | 13.06 | 1
April | 2 | 10PM to 11PM | 43 | 40.6 | 37.9 | 34.4 | 15.62 | 0.0771 | 0.23 | 13.03 | 1
April | 2 | 11PM to 12AM | 41 | 39.6 | 37.9 | 34.4 | 15.14 | 0.0774 | 0.23 | 12.98 | 1
April | 3 | 12AM to 1AM | 39.9 | 38.6 | 37 | 33.2 | 14.69 | 0.0776 | 0.22 | 12.95 | 1
April | 3 | 1AM to 2AM | 39.6 | 38.2 | 36.7 | 32.7 | 14.53 | 0.0777 | 0.22 | 12.94 | 1
April | 3 | 2AM to 3AM | 39 | 37.6 | 36 | 31.8 | 14.26 | 0.0777 | 0.21 | 12.92 | 1
April | 3 | 3AM to 4AM | 37.9 | 35.8 | 33.1 | 28.3 | 13.46 | 0.0779 | 0.19 | 12.88 | 1
April | 3 | 4AM to 5AM | 36 | 33 | 28.9 | 23.5 | 12.25 | 0.0783 | 0.16 | 12.82 | 1
April | 3 | 5AM to 6AM | 34 | 31.3 | 28 | 22.5 | 11.62 | 0.0786 | 0.15 | 12.76 | 1
April | 3 | 6AM to 7AM | 35.1 | 32.1 | 28 | 22.5 | 11.88 | 0.0784 | 0.15 | 12.79 | 1
April | 3 | 7AM to 8AM | 36 | 31.9 | 27 | 21.4 | 11.93 | 0.0783 | 0.14 | 12.81 | 1
April | 3 | 8AM to 9AM | 39.9 | 34.5 | 27 | 21.4 | 12.88 | 0.0777 | 0.14 | 12.91 | 1
April | 3 | 9AM to 10AM | 41 | 35.1 | 27 | 21.4 | 13.15 | 0.0775 | 0.14 | 12.94 | 1
April | 3 | 10AM to 11AM | 42.1 | 36.1 | 28 | 22.5 | 13.58 | 0.0773 | 0.15 | 12.97 | 1
April | 3 | 11AM to 12PM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
April | 3 | 12PM to 1PM | 45 | 38.4 | 30 | 24.7 | 14.61 | 0.0769 | 0.16 | 13.05 | 1
April | 3 | 1PM to 2PM | 48 | 40.4 | 30.9 | 25.8 | 15.51 | 0.0764 | 0.17 | 13.14 | 1
April | 3 | 2PM to 3PM | 48.9 | 40.5 | 30 | 24.7 | 15.57 | 0.0763 | 0.16 | 13.16 | 1
April | 3 | 3PM to 4PM | 50 | 40.3 | 28 | 22.5 | 15.49 | 0.0761 | 0.15 | 13.18 | 1
April | 3 | 4PM to 5PM | 50 | 39.7 | 26.1 | 20.5 | 15.18 | 0.0761 | 0.14 | 13.17 | 1
April | 3 | 5PM to 6PM | 48.9 | 39.4 | 27 | 21.4 | 15.06 | 0.0763 | 0.14 | 13.15 | 1
April | 3 | 6PM to 7PM | 46.9 | 38.4 | 27 | 21.4 | 14.58 | 0.0766 | 0.14 | 13.1 | 1
April | 3 | 7PM to 8PM | 46 | 37.9 | 27 | 21.4 | 14.36 | 0.0767 | 0.14 | 13.07 | 1
April | 3 | 8PM to 9PM | 44.1 | 37.2 | 28 | 22.5 | 14.06 | 0.077 | 0.15 | 13.02 | 1
April | 3 | 9PM to 10PM | 43 | 36.6 | 28 | 22.5 | 13.79 | 0.0772 | 0.15 | 13 | 1
April | 3 | 10PM to 11PM | 43 | 36.6 | 28 | 22.5 | 13.79 | 0.0772 | 0.15 | 13 | 1
April | 3 | 11PM to 12AM | 41 | 35.5 | 28 | 22.5 | 13.32 | 0.0775 | 0.15 | 12.95 | 1
April | 4 | 12AM to 1AM | 41 | 35.5 | 28 | 22.5 | 13.32 | 0.0775 | 0.15 | 12.95 | 1
April | 4 | 1AM to 2AM | 39.9 | 35.2 | 28.9 | 23.5 | 13.21 | 0.0777 | 0.16 | 12.92 | 1
April | 4 | 2AM to 3AM | 39.9 | 35.2 | 28.9 | 23.5 | 13.21 | 0.0777 | 0.16 | 12.92 | 1
April | 4 | 3AM to 4AM | 39 | 34.4 | 28 | 22.5 | 12.84 | 0.0778 | 0.15 | 12.89 | 1
April | 4 | 4AM to 5AM | 37.9 | 34.1 | 28.9 | 23.5 | 12.73 | 0.078 | 0.16 | 12.87 | 1
April | 4 | 5AM to 6AM | 37.9 | 34.6 | 30 | 24.7 | 12.91 | 0.078 | 0.16 | 12.87 | 1
April | 4 | 6AM to 7AM | 39.9 | 36 | 30.9 | 25.8 | 13.55 | 0.0776 | 0.17 | 12.93 | 1
April | 4 | 7AM to 8AM | 44.1 | 39.5 | 34 | 29.3 | 15.11 | 0.077 | 0.2 | 13.04 | 1
April | 4 | 8AM to 9AM | 48 | 41.5 | 34 | 29.3 | 16.06 | 0.0764 | 0.2 | 13.15 | 1
April | 4 | 9AM to 10AM | 52 | 43.9 | 35.1 | 30.6 | 17.22 | 0.0758 | 0.2 | 13.25 | 0
April | 4 | 10AM to 11AM | 55 | 45.7 | 36 | 31.8 | 18.14 | 0.0753 | 0.21 | 13.34 | 0
April | 4 | 11AM to 12PM | 59 | 48 | 37 | 33.2 | 19.31 | 0.0747 | 0.22 | 13.44 | 0
April | 4 | 12PM to 1PM | 61 | 48.5 | 36 | 31.8 | 19.57 | 0.0745 | 0.21 | 13.49 | 0
April | 4 | 1PM to 2PM | 63 | 49 | 35.1 | 30.6 | 19.88 | 0.0742 | 0.2 | 13.54 | 0
April | 4 | 2PM to 3PM | 64 | 49.8 | 36 | 31.8 | 20.31 | 0.074 | 0.21 | 13.57 | 0
April | 4 | 3PM to 4PM | 64 | 50.2 | 37 | 33.2 | 20.53 | 0.074 | 0.22 | 13.57 | 0
April | 4 | 4PM to 5PM | 63 | 49.7 | 37 | 33.2 | 20.27 | 0.0742 | 0.22 | 13.55 | 0
April | 4 | 5PM to 6PM | 60.1 | 49.2 | 39 | 35.9 | 19.99 | 0.0746 | 0.24 | 13.48 | 0
April | 4 | 6PM to 7PM | 59 | 48.7 | 39 | 35.9 | 19.73 | 0.0747 | 0.24 | 13.45 | 0
April | 4 | 7PM to 8PM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
April | 4 | 8PM to 9PM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
April | 4 | 9PM to 10PM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
April | 4 | 10PM to 11PM | 57 | 48.7 | 41 | 38.8 | 19.7 | 0.075 | 0.26 | 13.41 | 0
April | 4 | 11PM to 12AM | 57 | 48.7 | 41 | 38.8 | 19.7 | 0.075 | 0.26 | 13.41 | 0
April | 5 | 12AM to 1AM | 57 | 47.8 | 39 | 35.9 | 19.25 | 0.075 | 0.24 | 13.4 | 0
April | 5 | 1AM to 2AM | 57 | 49.1 | 42.1 | 40.4 | 19.96 | 0.075 | 0.27 | 13.41 | 0
April | 5 | 2AM to 3AM | 57.9 | 49.1 | 41 | 38.8 | 19.92 | 0.0749 | 0.26 | 13.43 | 0
April | 5 | 3AM to 4AM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
April | 5 | 4AM to 5AM | 55.9 | 48.7 | 42.1 | 40.4 | 19.7 | 0.0751 | 0.27 | 13.39 | 0
April | 5 | 5AM to 6AM | 55.9 | 49.1 | 43 | 41.9 | 19.92 | 0.0751 | 0.28 | 13.39 | 0
April | 5 | 6AM to 7AM | 55 | 49.2 | 44.1 | 43.6 | 19.98 | 0.0752 | 0.29 | 13.37 | 0
April | 5 | 7AM to 8AM | 45 | 43.5 | 42.1 | 40.4 | 17.04 | 0.0768 | 0.27 | 13.1 | 1
April | 5 | 8AM to 9AM | 43 | 42 | 41 | 38.8 | 16.3 | 0.0771 | 0.26 | 13.04 | 1
April | 5 | 9AM to 10AM | 43 | 42 | 41 | 38.8 | 16.3 | 0.0771 | 0.26 | 13.04 | 1
April | 5 | 10AM to 11AM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
April | 5 | 11AM to 12PM | 44.1 | 41.6 | 39 | 35.9 | 16.11 | 0.0769 | 0.24 | 13.06 | 1
April | 5 | 12PM to 1PM | 44.1 | 41.1 | 37.9 | 34.4 | 15.88 | 0.0769 | 0.23 | 13.06 | 1
April | 5 | 1PM to 2PM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
April | 5 | 2PM to 3PM | 41 | 39.2 | 37 | 33.2 | 14.95 | 0.0774 | 0.22 | 12.98 | 1
April | 5 | 3PM to 4PM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
April | 5 | 4PM to 5PM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
April | 5 | 5PM to 6PM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
April | 5 | 6PM to 7PM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
April | 5 | 7PM to 8PM | 37 | 36.2 | 35.1 | 30.6 | 13.61 | 0.0781 | 0.2 | 12.87 | 1
April | 5 | 8PM to 9PM | 37 | 36.2 | 35.1 | 30.6 | 13.61 | 0.0781 | 0.2 | 12.87 | 1
April | 5 | 9PM to 10PM | 36 | 34.7 | 33.1 | 28.3 | 12.99 | 0.0782 | 0.19 | 12.83 | 1
April | 5 | 10PM to 11PM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
April | 5 | 11PM to 12AM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
April | 6 | 12AM to 1AM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
April | 6 | 1AM to 2AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
April | 6 | 2AM to 3AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
April | 6 | 3AM to 4AM | 30.9 | 29.6 | 28 | 22.5 | 10.88 | 0.0791 | 0.15 | 12.69 | 1
April | 6 | 4AM to 5AM | 30.9 | 29.2 | 27 | 21.4 | 10.71 | 0.0791 | 0.14 | 12.68 | 1
April | 6 | 5AM to 6AM | 32 | 30.6 | 28.9 | 23.5 | 11.29 | 0.0789 | 0.16 | 12.72 | 1
April | 6 | 6AM to 7AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
April | 6 | 7AM to 8AM | 30.9 | 30.5 | 30 | 24.7 | 11.22 | 0.0791 | 0.16 | 12.69 | 1
April | 6 | 8AM to 9AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
April | 6 | 9AM to 10AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
April | 6 | 10AM to 11AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
April | 6 | 11AM to 12PM | 32 | 30.6 | 28.9 | 23.5 | 11.29 | 0.0789 | 0.16 | 12.72 | 1
April | 6 | 12PM to 1PM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
April | 6 | 1PM to 2PM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
April | 6 | 2PM to 3PM | 37.9 | 34.1 | 28.9 | 23.5 | 12.73 | 0.078 | 0.16 | 12.87 | 1
April | 6 | 3PM to 4PM | 42.1 | 36.4 | 28.9 | 23.5 | 13.73 | 0.0773 | 0.16 | 12.98 | 1
April | 6 | 4PM to 5PM | 42.1 | 36.1 | 28 | 22.5 | 13.58 | 0.0773 | 0.15 | 12.97 | 1
April | 6 | 5PM to 6PM | 42.1 | 35.7 | 27 | 21.4 | 13.41 | 0.0773 | 0.14 | 12.97 | 1
April | 6 | 6PM to 7PM | 41 | 34.4 | 25 | 19.5 | 12.85 | 0.0775 | 0.13 | 12.94 | 1
April | 6 | 7PM to 8PM | 39 | 32.6 | 23 | 17.8 | 12.1 | 0.0778 | 0.12 | 12.88 | 1
April | 6 | 8PM to 9PM | 36 | 30.9 | 24.1 | 18.7 | 11.51 | 0.0783 | 0.12 | 12.8 | 1
April | 6 | 9PM to 10PM | 34 | 30.9 | 27 | 21.4 | 11.45 | 0.0786 | 0.14 | 12.76 | 1
April | 6 | 10PM to 11PM | 35.1 | 31.4 | 27 | 21.4 | 11.71 | 0.0784 | 0.14 | 12.79 | 1
April | 6 | 11PM to 12AM | 34 | 30.9 | 27 | 21.4 | 11.45 | 0.0786 | 0.14 | 12.76 | 1
April | 7 | 12AM to 1AM | 33.1 | 30.4 | 27 | 21.4 | 11.23 | 0.0787 | 0.14 | 12.74 | 1
April | 7 | 1AM to 2AM | 33.1 | 30 | 26.1 | 20.5 | 11.1 | 0.0788 | 0.14 | 12.74 | 1
April | 7 | 2AM to 3AM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
April | 7 | 3AM to 4AM | 30.9 | 29.2 | 27 | 21.4 | 10.71 | 0.0791 | 0.14 | 12.68 | 1
April | 7 | 4AM to 5AM | 30 | 28.7 | 27 | 21.4 | 10.5 | 0.0792 | 0.14 | 12.66 | 1
April | 7 | 5AM to 6AM | 28.9 | 28.1 | 27 | 21.4 | 10.23 | 0.0794 | 0.14 | 12.63 | 1
April | 7 | 6AM to 7AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
April | 7 | 7AM to 8AM | 39.9 | 36 | 30.9 | 25.8 | 13.55 | 0.0776 | 0.17 | 12.93 | 1
April | 7 | 8AM to 9AM | 44.1 | 36.8 | 27 | 21.4 | 13.88 | 0.077 | 0.14 | 13.02 | 1
April | 7 | 9AM to 10AM | 46.9 | 37.4 | 24.1 | 18.7 | 14.16 | 0.0766 | 0.12 | 13.09 | 1
April | 7 | 10AM to 11AM | 48.9 | 37.9 | 21.9 | 16.9 | 14.35 | 0.0763 | 0.11 | 13.13 | 1
April | 7 | 11AM to 12PM | 50 | 37.7 | 19 | 14.7 | 14.28 | 0.0762 | 0.1 | 13.15 | 1
April | 7 | 12PM to 1PM | 52 | 39 | 19.9 | 15.3 | 14.85 | 0.0759 | 0.1 | 13.21 | 0
April | 7 | 1PM to 2PM | 53.1 | 40.4 | 23 | 17.8 | 15.49 | 0.0757 | 0.12 | 13.24 | 0
April | 7 | 2PM to 3PM | 54 | 41.1 | 24.1 | 18.7 | 15.85 | 0.0756 | 0.12 | 13.27 | 0
April | 7 | 3PM to 4PM | 54 | 41.4 | 25 | 19.5 | 15.98 | 0.0756 | 0.13 | 13.27 | 0
April | 7 | 4PM to 5PM | 53.1 | 41.5 | 27 | 21.4 | 16.06 | 0.0757 | 0.14 | 13.25 | 0
April | 7 | 5PM to 6PM | 52 | 41.4 | 28 | 22.5 | 15.97 | 0.0758 | 0.15 | 13.23 | 0
April | 7 | 6PM to 7PM | 50 | 40.3 | 28 | 22.5 | 15.49 | 0.0761 | 0.15 | 13.18 | 1
April | 7 | 7PM to 8PM | 48.9 | 39.8 | 28 | 22.5 | 15.23 | 0.0763 | 0.15 | 13.15 | 1
April | 7 | 8PM to 9PM | 46.9 | 39.5 | 30 | 24.7 | 15.09 | 0.0766 | 0.16 | 13.11 | 1
April | 7 | 9PM to 10PM | 46.9 | 39.5 | 30 | 24.7 | 15.09 | 0.0766 | 0.16 | 13.11 | 1
April | 7 | 10PM to 11PM | 46.9 | 39.5 | 30 | 24.7 | 15.09 | 0.0766 | 0.16 | 13.11 | 1
April | 7 | 11PM to 12AM | 46 | 39 | 30 | 24.7 | 14.87 | 0.0767 | 0.16 | 13.08 | 1
April | 8 | 12AM to 1AM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
April | 8 | 1AM to 2AM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
April | 8 | 2AM to 3AM | 43 | 36.9 | 28.9 | 23.5 | 13.94 | 0.0772 | 0.16 | 13 | 1
April | 8 | 3AM to 4AM | 42.1 | 36.4 | 28.9 | 23.5 | 13.73 | 0.0773 | 0.16 | 12.98 | 1
April | 8 | 4AM to 5AM | 42.1 | 36.9 | 30 | 24.7 | 13.91 | 0.0773 | 0.16 | 12.98 | 1
April | 8 | 5AM to 6AM | 42.1 | 37.2 | 30.9 | 25.8 | 14.08 | 0.0773 | 0.17 | 12.98 | 1
April | 8 | 6AM to 7AM | 43 | 38.2 | 32 | 27.1 | 14.5 | 0.0772 | 0.18 | 13.01 | 1
April | 8 | 7AM to 8AM | 45 | 39.6 | 33.1 | 28.3 | 15.16 | 0.0768 | 0.19 | 13.07 | 1
April | 8 | 8AM to 9AM | 48.9 | 41.3 | 32 | 27.1 | 15.93 | 0.0763 | 0.18 | 13.16 | 1
April | 8 | 9AM to 10AM | 53.1 | 44 | 34 | 29.3 | 17.28 | 0.0756 | 0.2 | 13.28 | 0
April | 8 | 10AM to 11AM | 57 | 45.9 | 34 | 29.3 | 18.24 | 0.075 | 0.2 | 13.38 | 0
April | 8 | 11AM to 12PM | 61 | 48.5 | 36 | 31.8 | 19.57 | 0.0745 | 0.21 | 13.49 | 0
April | 8 | 12PM to 1PM | 64 | 49.5 | 35.1 | 30.6 | 20.14 | 0.074 | 0.2 | 13.57 | 0
April | 8 | 1PM to 2PM | 66.9 | 49.8 | 32 | 27.1 | 20.28 | 0.0737 | 0.18 | 13.63 | 0
April | 8 | 2PM to 3PM | 69.1 | 50.4 | 30.9 | 25.8 | 20.6 | 0.0734 | 0.17 | 13.68 | 0
April | 8 | 3PM to 4PM | 71.1 | 50.9 | 30 | 24.7 | 20.91 | 0.0731 | 0.16 | 13.73 | 0
April | 8 | 4PM to 5PM | 71.1 | 51.2 | 30.9 | 25.8 | 21.08 | 0.0731 | 0.17 | 13.73 | 0
April | 8 | 5PM to 6PM | 68 | 50.3 | 32 | 27.1 | 20.54 | 0.0735 | 0.18 | 13.66 | 0
April | 8 | 6PM to 7PM | 64.9 | 49.2 | 33.1 | 28.3 | 19.99 | 0.0739 | 0.19 | 13.58 | 0
April | 8 | 7PM to 8PM | 64 | 48.5 | 32 | 27.1 | 19.59 | 0.0741 | 0.18 | 13.56 | 0
April | 8 | 8PM to 9PM | 63 | 48.7 | 34 | 29.3 | 19.68 | 0.0742 | 0.2 | 13.53 | 0
April | 8 | 9PM to 10PM | 62.1 | 48.6 | 35.1 | 30.6 | 19.66 | 0.0743 | 0.2 | 13.52 | 0
April | 8 | 10PM to 11PM | 62.1 | 49.3 | 37 | 33.2 | 20.05 | 0.0743 | 0.22 | 13.52 | 0
April | 8 | 11PM to 12AM | 61 | 49.6 | 39 | 35.9 | 20.21 | 0.0744 | 0.24 | 13.5 | 0
April | 9 | 12AM to 1AM | 60.1 | 49.6 | 39.9 | 37.2 | 20.19 | 0.0746 | 0.25 | 13.48 | 0
April | 9 | 1AM to 2AM | 60.1 | 50 | 41 | 38.8 | 20.44 | 0.0745 | 0.26 | 13.49 | 0
April | 9 | 2AM to 3AM | 59 | 49.5 | 41 | 38.8 | 20.18 | 0.0747 | 0.26 | 13.46 | 0
April | 9 | 3AM to 4AM | 59 | 50 | 42.1 | 40.4 | 20.44 | 0.0747 | 0.27 | 13.47 | 0
April | 9 | 4AM to 5AM | 60.1 | 50.9 | 43 | 41.9 | 20.93 | 0.0745 | 0.28 | 13.5 | 0
April | 9 | 5AM to 6AM | 57.9 | 49.9 | 43 | 41.9 | 20.4 | 0.0748 | 0.28 | 13.44 | 0
April | 9 | 6AM to 7AM | 57.9 | 49.9 | 43 | 41.9 | 20.4 | 0.0748 | 0.28 | 13.44 | 0
April | 9 | 7AM to 8AM | 61 | 51.7 | 44.1 | 43.6 | 21.42 | 0.0744 | 0.29 | 13.53 | 0
April | 9 | 8AM to 9AM | 62.1 | 52.2 | 44.1 | 43.6 | 21.68 | 0.0742 | 0.29 | 13.56 | 0
April | 9 | 9AM to 10AM | 61 | 53.6 | 48 | 50.8 | 22.53 | 0.0743 | 0.34 | 13.55 | 0
April | 9 | 10AM to 11AM | 60.1 | 54.2 | 50 | 54.7 | 22.93 | 0.0744 | 0.36 | 13.54 | 0
April | 9 | 11AM to 12PM | 60.1 | 50.5 | 42.1 | 40.4 | 20.7 | 0.0745 | 0.27 | 13.49 | 0
April | 9 | 12PM to 1PM | 62.1 | 55 | 50 | 54.7 | 23.41 | 0.0742 | 0.36 | 13.59 | 0
April | 9 | 1PM to 2PM | 61 | 54.6 | 50 | 54.7 | 23.15 | 0.0743 | 0.36 | 13.56 | 0
April | 9 | 2PM to 3PM | 61 | 54.6 | 50 | 54.7 | 23.15 | 0.0743 | 0.36 | 13.56 | 0
April | 9 | 3PM to 4PM | 60.1 | 54.8 | 51.1 | 57 | 23.28 | 0.0744 | 0.38 | 13.54 | 0
April | 9 | 4PM to 5PM | 59 | 53.2 | 48.9 | 52.6 | 22.33 | 0.0746 | 0.35 | 13.5 | 0
April | 9 | 5PM to 6PM | 57 | 53 | 50 | 54.7 | 22.18 | 0.0749 | 0.36 | 13.46 | 0
April | 9 | 6PM to 7PM | 55 | 53.3 | 52 | 59 | 22.36 | 0.0751 | 0.39 | 13.42 | 0
April | 9 | 7PM to 8PM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
April | 9 | 8PM to 9PM | 53.1 | 52.4 | 52 | 59 | 21.87 | 0.0754 | 0.39 | 13.37 | 0
April | 9 | 9PM to 10PM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
April | 9 | 10PM to 11PM | 50 | 49.4 | 48.9 | 52.6 | 20.14 | 0.0759 | 0.35 | 13.27 | 1
April | 9 | 11PM to 12AM | 50 | 49.4 | 48.9 | 52.6 | 20.14 | 0.0759 | 0.35 | 13.27 | 1
April | 10 | 12AM to 1AM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
April | 10 | 1AM to 2AM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
April | 10 | 2AM to 3AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 10 | 3AM to 4AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 10 | 4AM to 5AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
April | 10 | 5AM to 6AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
April | 10 | 6AM to 7AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
April | 10 | 7AM to 8AM | 50 | 47.9 | 46 | 47.1 | 19.29 | 0.076 | 0.31 | 13.25 | 1
April | 10 | 8AM to 9AM | 51.1 | 48.4 | 46 | 47.1 | 19.55 | 0.0758 | 0.31 | 13.28 | 1
April | 10 | 9AM to 10AM | 52 | 48.8 | 46 | 47.1 | 19.77 | 0.0757 | 0.31 | 13.3 | 0
April | 10 | 10AM to 11AM | 53.1 | 49.7 | 46.9 | 48.8 | 20.29 | 0.0755 | 0.32 | 13.34 | 0
April | 10 | 11AM to 12PM | 52 | 48.8 | 46 | 47.1 | 19.77 | 0.0757 | 0.31 | 13.3 | 0
April | 10 | 12PM to 1PM | 54 | 49.1 | 45 | 45.2 | 19.96 | 0.0754 | 0.3 | 13.35 | 0
April | 10 | 1PM to 2PM | 55.9 | 50 | 45 | 45.2 | 20.44 | 0.0751 | 0.3 | 13.4 | 0
April | 10 | 2PM to 3PM | 55 | 49.6 | 45 | 45.2 | 20.22 | 0.0752 | 0.3 | 13.38 | 0
April | 10 | 3PM to 4PM | 54 | 49.6 | 46 | 47.1 | 20.25 | 0.0754 | 0.31 | 13.36 | 0
April | 10 | 4PM to 5PM | 54 | 49.6 | 46 | 47.1 | 20.25 | 0.0754 | 0.31 | 13.36 | 0
April | 10 | 5PM to 6PM | 53.1 | 49.7 | 46.9 | 48.8 | 20.29 | 0.0755 | 0.32 | 13.34 | 0
April | 10 | 6PM to 7PM | 52 | 48.8 | 46 | 47.1 | 19.77 | 0.0757 | 0.31 | 13.3 | 0
April | 10 | 7PM to 8PM | 51.1 | 47.8 | 45 | 45.2 | 19.26 | 0.0758 | 0.3 | 13.27 | 1
April | 10 | 8PM to 9PM | 50 | 47.9 | 46 | 47.1 | 19.29 | 0.076 | 0.31 | 13.25 | 1
April | 10 | 9PM to 10PM | 50 | 47.9 | 46 | 47.1 | 19.29 | 0.076 | 0.31 | 13.25 | 1
April | 10 | 10PM to 11PM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
April | 10 | 11PM to 12AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
April | 11 | 12AM to 1AM | 48 | 46.4 | 45 | 45.2 | 18.51 | 0.0763 | 0.3 | 13.19 | 1
April | 11 | 1AM to 2AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 11 | 2AM to 3AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 11 | 3AM to 4AM | 46.9 | 46.5 | 46 | 47.1 | 18.55 | 0.0764 | 0.31 | 13.17 | 1
April | 11 | 4AM to 5AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
April | 11 | 5AM to 6AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
April | 11 | 6AM to 7AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 11 | 7AM to 8AM | 48 | 46.4 | 45 | 45.2 | 18.51 | 0.0763 | 0.3 | 13.19 | 1
April | 11 | 8AM to 9AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 11 | 9AM to 10AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 11 | 10AM to 11AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
April | 11 | 11AM to 12PM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 11 | 12PM to 1PM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
April | 11 | 1PM to 2PM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
April | 11 | 2PM to 3PM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
April | 11 | 3PM to 4PM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
April | 11 | 4PM to 5PM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 11 | 5PM to 6PM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
April | 11 | 6PM to 7PM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
April | 11 | 7PM to 8PM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
April | 11 | 8PM to 9PM | 50 | 49.4 | 48.9 | 52.6 | 20.14 | 0.0759 | 0.35 | 13.27 | 1
April | 11 | 9PM to 10PM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
April | 11 | 10PM to 11PM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 11 | 11PM to 12AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 12 | 12AM to 1AM | 48 | 48 | 48 | 50.8 | 19.38 | 0.0762 | 0.34 | 13.21 | 1
April | 12 | 1AM to 2AM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
April | 12 | 2AM to 3AM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
April | 12 | 3AM to 4AM | 52 | 51.5 | 51.1 | 57 | 21.31 | 0.0756 | 0.38 | 13.33 | 0
April | 12 | 4AM to 5AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
April | 12 | 5AM to 6AM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
April | 12 | 6AM to 7AM | 59 | 58.3 | 57.9 | 73.5 | 25.57 | 0.0745 | 0.48 | 13.57 | 0
April | 12 | 7AM to 8AM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
April | 12 | 8AM to 9AM | 59 | 56.6 | 55 | 66.1 | 24.43 | 0.0745 | 0.44 | 13.54 | 0
April | 12 | 9AM to 10AM | 62.1 | 55 | 50 | 54.7 | 23.41 | 0.0742 | 0.36 | 13.59 | 0
April | 12 | 10AM to 11AM | 62.1 | 52.2 | 44.1 | 43.6 | 21.68 | 0.0742 | 0.29 | 13.56 | 0
April | 12 | 11AM to 12PM | 63 | 51.3 | 41 | 38.8 | 21.14 | 0.0741 | 0.26 | 13.56 | 0
April | 12 | 12PM to 1PM | 64 | 51.3 | 39.9 | 37.2 | 21.15 | 0.074 | 0.25 | 13.59 | 0
April | 12 | 1PM to 2PM | 64 | 50.9 | 39 | 35.9 | 20.95 | 0.074 | 0.24 | 13.58 | 0
April | 12 | 2PM to 3PM | 63 | 50.5 | 39 | 35.9 | 20.69 | 0.0742 | 0.24 | 13.55 | 0
April | 12 | 3PM to 4PM | 61 | 49.6 | 39 | 35.9 | 20.21 | 0.0744 | 0.24 | 13.5 | 0
April | 12 | 4PM to 5PM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
April | 12 | 5PM to 6PM | 54 | 45.2 | 36 | 31.8 | 17.88 | 0.0755 | 0.21 | 13.31 | 0
April | 12 | 6PM to 7PM | 53.1 | 44.8 | 36 | 31.8 | 17.66 | 0.0756 | 0.21 | 13.29 | 0
April | 12 | 7PM to 8PM | 53.1 | 45.2 | 37 | 33.2 | 17.87 | 0.0756 | 0.22 | 13.29 | 0
April | 12 | 8PM to 9PM | 53.1 | 44.8 | 36 | 31.8 | 17.66 | 0.0756 | 0.21 | 13.29 | 0
April | 12 | 9PM to 10PM | 52 | 44.3 | 36 | 31.8 | 17.4 | 0.0758 | 0.21 | 13.26 | 0
April | 12 | 10PM to 11PM | 51.1 | 43.5 | 35.1 | 30.6 | 17 | 0.0759 | 0.2 | 13.23 | 1
April | 12 | 11PM to 12AM | 51.1 | 43.8 | 36 | 31.8 | 17.18 | 0.0759 | 0.21 | 13.23 | 1
April | 13 | 12AM to 1AM | 48.9 | 43.2 | 37 | 33.2 | 16.87 | 0.0762 | 0.22 | 13.18 | 1
April | 13 | 1AM to 2AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
April | 13 | 2AM to 3AM | 46 | 43 | 39.9 | 37.2 | 16.79 | 0.0766 | 0.25 | 13.12 | 1
April | 13 | 3AM to 4AM | 46 | 42.1 | 37.9 | 34.4 | 16.36 | 0.0766 | 0.23 | 13.11 | 1
April | 13 | 4AM to 5AM | 46 | 42.1 | 37.9 | 34.4 | 16.36 | 0.0766 | 0.23 | 13.11 | 1
April | 13 | 5AM to 6AM | 46 | 41.8 | 37 | 33.2 | 16.17 | 0.0767 | 0.22 | 13.11 | 1
April | 13 | 6AM to 7AM | 46.9 | 42.6 | 37.9 | 34.4 | 16.58 | 0.0765 | 0.23 | 13.13 | 1
April | 13 | 7AM to 8AM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
April | 13 | 8AM to 9AM | 46.9 | 42.6 | 37.9 | 34.4 | 16.58 | 0.0765 | 0.23 | 13.13 | 1
April | 13 | 9AM to 10AM | 48 | 43.1 | 37.9 | 34.4 | 16.84 | 0.0763 | 0.23 | 13.16 | 1
April | 13 | 10AM to 11AM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
April | 13 | 11AM to 12PM | 50 | 44.6 | 39 | 35.9 | 17.55 | 0.076 | 0.24 | 13.22 | 1
April | 13 | 12PM to 1PM | 55.9 | 47.7 | 39.9 | 37.2 | 19.19 | 0.0752 | 0.25 | 13.38 | 0
April | 13 | 1PM to 2PM | 60.1 | 50.5 | 42.1 | 40.4 | 20.7 | 0.0745 | 0.27 | 13.49 | 0
April | 13 | 2PM to 3PM | 62.1 | 50.1 | 39 | 35.9 | 20.47 | 0.0743 | 0.24 | 13.53 | 0
April | 13 | 3PM to 4PM | 64 | 50.2 | 37 | 33.2 | 20.53 | 0.074 | 0.22 | 13.57 | 0
April | 13 | 4PM to 5PM | 64.9 | 50.9 | 37.9 | 34.4 | 20.94 | 0.0739 | 0.23 | 13.6 | 0
April | 13 | 5PM to 6PM | 64.9 | 50.6 | 37 | 33.2 | 20.75 | 0.0739 | 0.22 | 13.6 | 0
April | 13 | 6PM to 7PM | 62.1 | 50.4 | 39.9 | 37.2 | 20.67 | 0.0743 | 0.25 | 13.54 | 0
April | 13 | 7PM to 8PM | 61 | 49.2 | 37.9 | 34.4 | 19.98 | 0.0744 | 0.23 | 13.5 | 0
April | 13 | 8PM to 9PM | 59 | 48.7 | 39 | 35.9 | 19.73 | 0.0747 | 0.24 | 13.45 | 0
April | 13 | 9PM to 10PM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
April | 13 | 10PM to 11PM | 55.9 | 47.7 | 39.9 | 37.2 | 19.19 | 0.0752 | 0.25 | 13.38 | 0
April | 13 | 11PM to 12AM | 55.9 | 47.7 | 39.9 | 37.2 | 19.19 | 0.0752 | 0.25 | 13.38 | 0
April | 14 | 12AM to 1AM | 57 | 47.8 | 39 | 35.9 | 19.25 | 0.075 | 0.24 | 13.4 | 0
April | 14 | 1AM to 2AM | 61 | 49.2 | 37.9 | 34.4 | 19.98 | 0.0744 | 0.23 | 13.5 | 0
April | 14 | 2AM to 3AM | 63 | 50.5 | 39 | 35.9 | 20.69 | 0.0742 | 0.24 | 13.55 | 0
April | 14 | 3AM to 4AM | 62.1 | 50.4 | 39.9 | 37.2 | 20.67 | 0.0743 | 0.25 | 13.54 | 0
April | 14 | 4AM to 5AM | 57.9 | 49.1 | 41 | 38.8 | 19.92 | 0.0749 | 0.26 | 13.43 | 0
April | 14 | 5AM to 6AM | 61 | 50.4 | 41 | 38.8 | 20.66 | 0.0744 | 0.26 | 13.51 | 0
April | 14 | 6AM to 7AM | 64.9 | 52.9 | 43 | 41.9 | 22.11 | 0.0738 | 0.28 | 13.62 | 0
April | 14 | 7AM to 8AM | 68 | 55 | 45 | 45.2 | 23.37 | 0.0734 | 0.3 | 13.71 | 0
April | 14 | 8AM to 9AM | 71.1 | 56.7 | 46 | 47.1 | 24.41 | 0.073 | 0.31 | 13.8 | 0
April | 14 | 9AM to 10AM | 73.9 | 58.2 | 46.9 | 48.8 | 25.37 | 0.0725 | 0.32 | 13.88 | 0
April | 14 | 10AM to 11AM | 75.9 | 59.8 | 48.9 | 52.6 | 26.44 | 0.0723 | 0.35 | 13.94 | 0
April | 14 | 11AM to 12PM | 79 | 61.3 | 50 | 54.7 | 27.53 | 0.0718 | 0.36 | 14.03 | 0
April | 14 | 12PM to 1PM | 82 | 63.8 | 53.1 | 61.4 | 29.32 | 0.0714 | 0.41 | 14.13 | 0
April | 14 | 1PM to 2PM | 84.9 | 63.4 | 50 | 54.7 | 28.98 | 0.071 | 0.36 | 14.18 | 0
April | 14 | 2PM to 3PM | 86 | 62.5 | 46.9 | 48.8 | 28.3 | 0.0709 | 0.32 | 14.19 | 0
April | 14 | 3PM to 4PM | 84 | 61.8 | 46.9 | 48.8 | 27.82 | 0.0712 | 0.32 | 14.14 | 0
April | 14 | 4PM to 5PM | 82.9 | 61.4 | 46.9 | 48.8 | 27.55 | 0.0713 | 0.32 | 14.11 | 0
April | 14 | 5PM to 6PM | 81 | 61.2 | 48 | 50.8 | 27.39 | 0.0716 | 0.34 | 14.07 | 0
April | 14 | 6PM to 7PM | 78.1 | 61.5 | 51.1 | 57 | 27.67 | 0.0719 | 0.38 | 14.01 | 0
April | 14 | 7PM to 8PM | 75.9 | 64.9 | 59 | 76.4 | 30.17 | 0.0721 | 0.5 | 14.02 | 0
April | 14 | 8PM to 9PM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
April | 14 | 9PM to 10PM | 73.9 | 66.5 | 63 | 88.2 | 31.53 | 0.0723 | 0.58 | 14 | 0
April | 14 | 10PM to 11PM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
April | 14 | 11PM to 12AM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
April | 15 | 12AM to 1AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
April | 15 | 1AM to 2AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
April | 15 | 2AM to 3AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
April | 15 | 3AM to 4AM | 66.9 | 56.9 | 50 | 54.7 | 24.59 | 0.0735 | 0.36 | 13.72 | 0
April | 15 | 4AM to 5AM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
April | 15 | 5AM to 6AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
April | 15 | 6AM to 7AM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
April | 15 | 7AM to 8AM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
April | 15 | 8AM to 9AM | 57.9 | 56.2 | 55 | 66.1 | 24.16 | 0.0747 | 0.44 | 13.52 | 0
April | 15 | 9AM to 10AM | 55.9 | 52 | 48.9 | 52.6 | 21.58 | 0.0751 | 0.35 | 13.42 | 0
April | 15 | 10AM to 11AM | 57.9 | 51.3 | 46 | 47.1 | 21.22 | 0.0748 | 0.31 | 13.46 | 0
April | 15 | 11AM to 12PM | 57 | 50 | 44.1 | 43.6 | 20.46 | 0.075 | 0.29 | 13.42 | 0
April | 15 | 12PM to 1PM | 59 | 50.9 | 44.1 | 43.6 | 20.94 | 0.0747 | 0.29 | 13.48 | 0
April | 15 | 1PM to 2PM | 63 | 50.8 | 39.9 | 37.2 | 20.89 | 0.0741 | 0.25 | 13.56 | 0
April | 15 | 2PM to 3PM | 63 | 50.1 | 37.9 | 34.4 | 20.46 | 0.0742 | 0.23 | 13.55 | 0
April | 15 | 3PM to 4PM | 59 | 47.6 | 36 | 31.8 | 19.1 | 0.0747 | 0.21 | 13.44 | 0
April | 15 | 4PM to 5PM | 60.1 | 47.7 | 35.1 | 30.6 | 19.18 | 0.0746 | 0.2 | 13.46 | 0
April | 15 | 5PM to 6PM | 57.9 | 45.3 | 30.9 | 25.8 | 17.9 | 0.0749 | 0.17 | 13.39 | 0
April | 15 | 6PM to 7PM | 55 | 44.3 | 32 | 27.1 | 17.41 | 0.0754 | 0.18 | 13.32 | 0
April | 15 | 7PM to 8PM | 55 | 43.9 | 30.9 | 25.8 | 17.21 | 0.0754 | 0.17 | 13.32 | 0
April | 15 | 8PM to 9PM | 53.1 | 42.9 | 30.9 | 25.8 | 16.73 | 0.0757 | 0.17 | 13.27 | 0
April | 15 | 9PM to 10PM | 51.1 | 42.4 | 32 | 27.1 | 16.45 | 0.0759 | 0.18 | 13.22 | 1
April | 15 | 10PM to 11PM | 50 | 41.4 | 30.9 | 25.8 | 15.99 | 0.0761 | 0.17 | 13.19 | 1
April | 15 | 11PM to 12AM | 50 | 41.1 | 30 | 24.7 | 15.83 | 0.0761 | 0.16 | 13.18 | 1
April | 16 | 12AM to 1AM | 48 | 40.4 | 30.9 | 25.8 | 15.51 | 0.0764 | 0.17 | 13.14 | 1
April | 16 | 1AM to 2AM | 48.9 | 40.1 | 28.9 | 23.5 | 15.38 | 0.0763 | 0.16 | 13.15 | 1
April | 16 | 2AM to 3AM | 48.9 | 40.5 | 30 | 24.7 | 15.57 | 0.0763 | 0.16 | 13.16 | 1
April | 16 | 3AM to 4AM | 46.9 | 40.3 | 32 | 27.1 | 15.45 | 0.0766 | 0.18 | 13.11 | 1
April | 16 | 4AM to 5AM | 48 | 40.4 | 30.9 | 25.8 | 15.51 | 0.0764 | 0.17 | 13.14 | 1
April | 16 | 5AM to 6AM | 46.9 | 40.3 | 32 | 27.1 | 15.45 | 0.0766 | 0.18 | 13.11 | 1
April | 16 | 6AM to 7AM | 50 | 41.4 | 30.9 | 25.8 | 15.99 | 0.0761 | 0.17 | 13.19 | 1
April | 16 | 7AM to 8AM | 55 | 44.3 | 32 | 27.1 | 17.41 | 0.0754 | 0.18 | 13.32 | 0
April | 16 | 8AM to 9AM | 60.1 | 46.3 | 30.9 | 25.8 | 18.42 | 0.0746 | 0.17 | 13.45 | 0
April | 16 | 9AM to 10AM | 62.1 | 48 | 33.1 | 28.3 | 19.3 | 0.0743 | 0.19 | 13.51 | 0
April | 16 | 10AM to 11AM | 66 | 49.7 | 33.1 | 28.3 | 20.25 | 0.0738 | 0.19 | 13.61 | 0
April | 16 | 11AM to 12PM | 69.1 | 51.1 | 33.1 | 28.3 | 20.99 | 0.0733 | 0.19 | 13.69 | 0
April | 16 | 12PM to 1PM | 71.1 | 51.9 | 33.1 | 28.3 | 21.47 | 0.0731 | 0.19 | 13.74 | 0
April | 16 | 1PM to 2PM | 73 | 52.7 | 33.1 | 28.3 | 21.95 | 0.0728 | 0.19 | 13.79 | 0
April | 16 | 2PM to 3PM | 73.9 | 52.8 | 32 | 27.1 | 21.98 | 0.0727 | 0.18 | 13.81 | 0
April | 16 | 3PM to 4PM | 75 | 53.5 | 33.1 | 28.3 | 22.43 | 0.0725 | 0.19 | 13.84 | 0
April | 16 | 4PM to 5PM | 73.9 | 53.1 | 33.1 | 28.3 | 22.17 | 0.0727 | 0.19 | 13.82 | 0
April | 16 | 5PM to 6PM | 73 | 53.6 | 36 | 31.8 | 22.49 | 0.0728 | 0.21 | 13.8 | 0
April | 16 | 6PM to 7PM | 71.1 | 53.2 | 37 | 33.2 | 22.23 | 0.073 | 0.22 | 13.76 | 0
April | 16 | 7PM to 8PM | 66 | 50 | 34 | 29.3 | 20.42 | 0.0738 | 0.2 | 13.61 | 0
April | 16 | 8PM to 9PM | 63 | 49 | 35.1 | 30.6 | 19.88 | 0.0742 | 0.2 | 13.54 | 0
April | 16 | 9PM to 10PM | 61 | 47.8 | 34 | 29.3 | 19.2 | 0.0745 | 0.2 | 13.48 | 0
April | 16 | 10PM to 11PM | 57 | 46.3 | 35.1 | 30.6 | 18.44 | 0.075 | 0.2 | 13.38 | 0
April | 16 | 11PM to 12AM | 57 | 46.3 | 35.1 | 30.6 | 18.44 | 0.075 | 0.2 | 13.38 | 0
April | 17 | 12AM to 1AM | 54 | 45.6 | 37 | 33.2 | 18.09 | 0.0755 | 0.22 | 13.31 | 0
April | 17 | 1AM to 2AM | 52 | 44.7 | 37 | 33.2 | 17.61 | 0.0758 | 0.22 | 13.26 | 0
April | 17 | 2AM to 3AM | 52 | 44.7 | 37 | 33.2 | 17.61 | 0.0758 | 0.22 | 13.26 | 0
April | 17 | 3AM to 4AM | 52 | 44.7 | 37 | 33.2 | 17.61 | 0.0758 | 0.22 | 13.26 | 0
April | 17 | 4AM to 5AM | 51.1 | 44.3 | 37 | 33.2 | 17.39 | 0.0759 | 0.22 | 13.24 | 1
April | 17 | 5AM to 6AM | 48 | 43.1 | 37.9 | 34.4 | 16.84 | 0.0763 | 0.23 | 13.16 | 1
April | 17 | 6AM to 7AM | 54 | 46.8 | 39.9 | 37.2 | 18.71 | 0.0754 | 0.25 | 13.33 | 0
April | 17 | 7AM to 8AM | 61 | 49.2 | 37.9 | 34.4 | 19.98 | 0.0744 | 0.23 | 13.5 | 0
April | 17 | 8AM to 9AM | 63 | 47.3 | 30 | 24.7 | 18.96 | 0.0742 | 0.16 | 13.52 | 0
April | 17 | 9AM to 10AM | 64 | 47.5 | 28.9 | 23.5 | 19.03 | 0.0741 | 0.16 | 13.54 | 0
April | 17 | 10AM to 11AM | 66 | 47 | 24.1 | 18.7 | 18.76 | 0.0738 | 0.12 | 13.58 | 0
April | 17 | 11AM to 12PM | 69.1 | 49.7 | 28.9 | 23.5 | 20.25 | 0.0734 | 0.16 | 13.67 | 0
April | 17 | 12PM to 1PM | 71.1 | 50.9 | 30 | 24.7 | 20.91 | 0.0731 | 0.16 | 13.73 | 0
April | 17 | 1PM to 2PM | 72 | 51.3 | 30 | 24.7 | 21.13 | 0.073 | 0.16 | 13.75 | 0
April | 17 | 2PM to 3PM | 73.9 | 52.8 | 32 | 27.1 | 21.98 | 0.0727 | 0.18 | 13.81 | 0
April | 17 | 3PM to 4PM | 75 | 52.9 | 30.9 | 25.8 | 22.03 | 0.0725 | 0.17 | 13.84 | 0
April | 17 | 4PM to 5PM | 73.9 | 53.1 | 33.1 | 28.3 | 22.17 | 0.0727 | 0.19 | 13.82 | 0
April | 17 | 5PM to 6PM | 73 | 53.3 | 35.1 | 30.6 | 22.32 | 0.0728 | 0.2 | 13.8 | 0
April | 17 | 6PM to 7PM | 69.1 | 53.4 | 39.9 | 37.2 | 22.38 | 0.0733 | 0.25 | 13.72 | 0
April | 17 | 7PM to 8PM | 66.9 | 51.8 | 37.9 | 34.4 | 21.42 | 0.0736 | 0.23 | 13.65 | 0
April | 17 | 8PM to 9PM | 66 | 51.4 | 37.9 | 34.4 | 21.2 | 0.0737 | 0.23 | 13.63 | 0
April | 17 | 9PM to 10PM | 66 | 53 | 42.1 | 40.4 | 22.14 | 0.0737 | 0.27 | 13.65 | 0
April | 17 | 10PM to 11PM | 64 | 53 | 44.1 | 43.6 | 22.17 | 0.074 | 0.29 | 13.61 | 0
April | 17 | 11PM to 12AM | 64 | 53.4 | 45 | 45.2 | 22.4 | 0.0739 | 0.3 | 13.61 | 0
April | 18 | 12AM to 1AM | 62.1 | 53.1 | 46 | 47.1 | 22.22 | 0.0742 | 0.31 | 13.57 | 0
April | 18 | 1AM to 2AM | 63 | 53 | 45 | 45.2 | 22.14 | 0.0741 | 0.3 | 13.58 | 0
April | 18 | 2AM to 3AM | 63 | 52.6 | 44.1 | 43.6 | 21.9 | 0.0741 | 0.29 | 13.58 | 0
April | 18 | 3AM to 4AM | 62.1 | 52.2 | 44.1 | 43.6 | 21.68 | 0.0742 | 0.29 | 13.56 | 0
April | 18 | 4AM to 5AM | 66 | 53 | 42.1 | 40.4 | 22.14 | 0.0737 | 0.27 | 13.65 | 0
April | 18 | 5AM to 6AM | 64.9 | 52.5 | 42.1 | 40.4 | 21.88 | 0.0738 | 0.27 | 13.62 | 0
April | 18 | 6AM to 7AM | 66 | 53.4 | 43 | 41.9 | 22.37 | 0.0737 | 0.28 | 13.65 | 0
April | 18 | 7AM to 8AM | 70 | 55.4 | 44.1 | 43.6 | 23.61 | 0.0731 | 0.29 | 13.76 | 0
April | 18 | 8AM to 9AM | 73 | 56.6 | 44.1 | 43.6 | 24.35 | 0.0727 | 0.29 | 13.84 | 0
April | 18 | 9AM to 10AM | 75.9 | 58.1 | 45 | 45.2 | 25.29 | 0.0723 | 0.3 | 13.92 | 0
April | 18 | 10AM to 11AM | 79 | 57.7 | 41 | 38.8 | 25.03 | 0.0719 | 0.26 | 13.98 | 0
April | 18 | 11AM to 12PM | 82 | 57.8 | 37.9 | 34.4 | 25.08 | 0.0716 | 0.23 | 14.04 | 0
April | 18 | 12PM to 1PM | 84.9 | 58.6 | 37 | 33.2 | 25.59 | 0.0712 | 0.22 | 14.12 | 0
April | 18 | 1PM to 2PM | 86 | 58.4 | 35.1 | 30.6 | 25.45 | 0.0711 | 0.2 | 14.14 | 0
April | 18 | 2PM to 3PM | 86 | 57.8 | 33.1 | 28.3 | 25.08 | 0.0711 | 0.19 | 14.13 | 0
April | 18 | 3PM to 4PM | 87.1 | 58.2 | 33.1 | 28.3 | 25.35 | 0.0709 | 0.19 | 14.16 | 0
April | 18 | 4PM to 5PM | 86 | 58.4 | 35.1 | 30.6 | 25.45 | 0.0711 | 0.2 | 14.14 | 0
April | 18 | 5PM to 6PM | 84 | 58.5 | 37.9 | 34.4 | 25.56 | 0.0713 | 0.23 | 14.1 | 0
April | 18 | 6PM to 7PM | 81 | 57.4 | 37.9 | 34.4 | 24.82 | 0.0717 | 0.23 | 14.02 | 0
April | 18 | 7PM to 8PM | 79 | 57 | 39 | 35.9 | 24.57 | 0.0719 | 0.24 | 13.97 | 0
April | 18 | 8PM to 9PM | 75 | 55.5 | 39 | 35.9 | 23.61 | 0.0725 | 0.24 | 13.87 | 0
April | 18 | 9PM to 10PM | 73.9 | 55 | 39 | 35.9 | 23.35 | 0.0726 | 0.24 | 13.84 | 0
April | 18 | 10PM to 11PM | 73 | 54.3 | 37.9 | 34.4 | 22.9 | 0.0728 | 0.23 | 13.81 | 0
April | 18 | 11PM to 12AM | 70 | 53.4 | 39 | 35.9 | 22.39 | 0.0732 | 0.24 | 13.74 | 0
April | 19 | 12AM to 1AM | 68 | 53 | 39.9 | 37.2 | 22.11 | 0.0734 | 0.25 | 13.69 | 0
April | 19 | 1AM to 2AM | 68 | 53.8 | 42.1 | 40.4 | 22.62 | 0.0734 | 0.27 | 13.7 | 0
April | 19 | 2AM to 3AM | 66 | 53.8 | 44.1 | 43.6 | 22.65 | 0.0737 | 0.29 | 13.66 | 0
April | 19 | 3AM to 4AM | 64.9 | 54.3 | 46 | 47.1 | 22.92 | 0.0738 | 0.31 | 13.64 | 0
April | 19 | 4AM to 5AM | 66.9 | 56 | 48 | 50.8 | 23.98 | 0.0735 | 0.34 | 13.7 | 0
April | 19 | 5AM to 6AM | 64.9 | 55.2 | 48 | 50.8 | 23.5 | 0.0738 | 0.34 | 13.65 | 0
April | 19 | 6AM to 7AM | 66 | 53.8 | 44.1 | 43.6 | 22.65 | 0.0737 | 0.29 | 13.66 | 0
April | 19 | 7AM to 8AM | 66.9 | 54.6 | 45 | 45.2 | 23.1 | 0.0735 | 0.3 | 13.69 | 0
April | 19 | 8AM to 9AM | 68 | 54.2 | 43 | 41.9 | 22.85 | 0.0734 | 0.28 | 13.7 | 0
April | 19 | 9AM to 10AM | 70 | 55 | 43 | 41.9 | 23.33 | 0.0731 | 0.28 | 13.76 | 0
April | 19 | 10AM to 11AM | 72 | 56.2 | 44.1 | 43.6 | 24.09 | 0.0729 | 0.29 | 13.81 | 0
April | 19 | 11AM to 12PM | 73 | 56.6 | 44.1 | 43.6 | 24.35 | 0.0727 | 0.29 | 13.84 | 0
April | 19 | 12PM to 1PM | 73.9 | 56.9 | 44.1 | 43.6 | 24.57 | 0.0726 | 0.29 | 13.86 | 0
April | 19 | 1PM to 2PM | 75 | 57.7 | 45 | 45.2 | 25.07 | 0.0724 | 0.3 | 13.9 | 0
April | 19 | 2PM to 3PM | 75.9 | 58.5 | 46 | 47.1 | 25.59 | 0.0723 | 0.31 | 13.93 | 0
April | 19 | 3PM to 4PM | 75 | 57.7 | 45 | 45.2 | 25.07 | 0.0724 | 0.3 | 13.9 | 0
April | 19 | 4PM to 5PM | 75 | 57.7 | 45 | 45.2 | 25.07 | 0.0724 | 0.3 | 13.9 | 0
April | 19 | 5PM to 6PM | 73 | 57 | 45 | 45.2 | 24.59 | 0.0727 | 0.3 | 13.85 | 0
April | 19 | 6PM to 7PM | 70 | 55.4 | 44.1 | 43.6 | 23.61 | 0.0731 | 0.29 | 13.76 | 0
April | 19 | 7PM to 8PM | 66.9 | 53.4 | 42.1 | 40.4 | 22.36 | 0.0736 | 0.27 | 13.67 | 0
April | 19 | 8PM to 9PM | 64.9 | 52.9 | 43 | 41.9 | 22.11 | 0.0738 | 0.28 | 13.62 | 0
April | 19 | 9PM to 10PM | 63 | 49.7 | 37 | 33.2 | 20.27 | 0.0742 | 0.22 | 13.55 | 0
April | 19 | 10PM to 11PM | 63 | 49 | 35.1 | 30.6 | 19.88 | 0.0742 | 0.2 | 13.54 | 0
April | 19 | 11PM to 12AM | 62.1 | 48.6 | 35.1 | 30.6 | 19.66 | 0.0743 | 0.2 | 13.52 | 0
April | 20 | 12AM to 1AM | 60.1 | 48.5 | 37 | 33.2 | 19.57 | 0.0746 | 0.22 | 13.47 | 0
April | 20 | 1AM to 2AM | 60.1 | 48.1 | 36 | 31.8 | 19.36 | 0.0746 | 0.21 | 13.47 | 0
April | 20 | 2AM to 3AM | 59 | 46.2 | 32 | 27.1 | 18.37 | 0.0748 | 0.18 | 13.42 | 0
April | 20 | 3AM to 4AM | 57 | 44.2 | 28.9 | 23.5 | 17.33 | 0.0751 | 0.16 | 13.36 | 0
April | 20 | 4AM to 5AM | 55.9 | 43.6 | 28.9 | 23.5 | 17.07 | 0.0752 | 0.16 | 13.33 | 0
April | 20 | 5AM to 6AM | 54 | 43 | 30 | 24.7 | 16.78 | 0.0755 | 0.16 | 13.29 | 0
April | 20 | 6AM to 7AM | 57 | 44.2 | 28.9 | 23.5 | 17.33 | 0.0751 | 0.16 | 13.36 | 0
April | 20 | 7AM to 8AM | 60.1 | 45.3 | 28 | 22.5 | 17.92 | 0.0747 | 0.15 | 13.44 | 0
April | 20 | 8AM to 9AM | 62.1 | 46.3 | 28 | 22.5 | 18.4 | 0.0744 | 0.15 | 13.49 | 0
April | 20 | 9AM to 10AM | 64 | 46.6 | 26.1 | 20.5 | 18.57 | 0.0741 | 0.14 | 13.54 | 0
April | 20 | 10AM to 11AM | 66 | 48.1 | 28 | 22.5 | 19.36 | 0.0738 | 0.15 | 13.59 | 0
April | 20 | 11AM to 12PM | 68 | 49.6 | 30 | 24.7 | 20.17 | 0.0735 | 0.16 | 13.65 | 0
April | 20 | 12PM to 1PM | 70 | 49.9 | 28 | 22.5 | 20.31 | 0.0733 | 0.15 | 13.69 | 0
April | 20 | 1PM to 2PM | 70 | 50.5 | 30 | 24.7 | 20.65 | 0.0732 | 0.16 | 13.7 | 0
April | 20 | 2PM to 3PM | 72 | 51.6 | 30.9 | 25.8 | 21.3 | 0.073 | 0.17 | 13.76 | 0
April | 20 | 3PM to 4PM | 71.1 | 50.9 | 30 | 24.7 | 20.91 | 0.0731 | 0.16 | 13.73 | 0
April | 20 | 4PM to 5PM | 71.1 | 51.2 | 30.9 | 25.8 | 21.08 | 0.0731 | 0.17 | 13.73 | 0
April | 20 | 5PM to 6PM | 70 | 51.1 | 32 | 27.1 | 21.02 | 0.0732 | 0.18 | 13.71 | 0
April | 20 | 6PM to 7PM | 66.9 | 50.1 | 33.1 | 28.3 | 20.47 | 0.0736 | 0.19 | 13.63 | 0
April | 20 | 7PM to 8PM | 64.9 | 49.5 | 34 | 29.3 | 20.16 | 0.0739 | 0.2 | 13.59 | 0
April | 20 | 8PM to 9PM | 64 | 49.5 | 35.1 | 30.6 | 20.14 | 0.074 | 0.2 | 13.57 | 0
April | 20 | 9PM to 10PM | 63 | 49.3 | 36 | 31.8 | 20.05 | 0.0742 | 0.21 | 13.54 | 0
April | 20 | 10PM to 11PM | 62.1 | 48.9 | 36 | 31.8 | 19.84 | 0.0743 | 0.21 | 13.52 | 0
April | 20 | 11PM to 12AM | 62.1 | 48.9 | 36 | 31.8 | 19.84 | 0.0743 | 0.21 | 13.52 | 0
April | 21 | 12AM to 1AM | 60.1 | 48.1 | 36 | 31.8 | 19.36 | 0.0746 | 0.21 | 13.47 | 0
April | 21 | 1AM to 2AM | 59 | 47.2 | 35.1 | 30.6 | 18.92 | 0.0748 | 0.2 | 13.44 | 0
April | 21 | 2AM to 3AM | 57 | 47.8 | 39 | 35.9 | 19.25 | 0.075 | 0.24 | 13.4 | 0
April | 21 | 3AM to 4AM | 55 | 46.9 | 39 | 35.9 | 18.77 | 0.0753 | 0.24 | 13.35 | 0
April | 21 | 4AM to 5AM | 54 | 46.8 | 39.9 | 37.2 | 18.71 | 0.0754 | 0.25 | 13.33 | 0
April | 21 | 5AM to 6AM | 54 | 46.4 | 39 | 35.9 | 18.51 | 0.0755 | 0.24 | 13.32 | 0
April | 21 | 6AM to 7AM | 55 | 46.9 | 39 | 35.9 | 18.77 | 0.0753 | 0.24 | 13.35 | 0
April | 21 | 7AM to 8AM | 55 | 47.8 | 41 | 38.8 | 19.22 | 0.0753 | 0.26 | 13.36 | 0
April | 21 | 8AM to 9AM | 52 | 48.8 | 46 | 47.1 | 19.77 | 0.0757 | 0.31 | 13.3 | 0
April | 21 | 9AM to 10AM | 54 | 50.1 | 46.9 | 48.8 | 20.51 | 0.0754 | 0.32 | 13.36 | 0
April | 21 | 10AM to 11AM | 53.1 | 48.7 | 45 | 45.2 | 19.74 | 0.0755 | 0.3 | 13.33 | 0
April | 21 | 11AM to 12PM | 53.1 | 49.2 | 46 | 47.1 | 20.03 | 0.0755 | 0.31 | 13.33 | 0
April | 21 | 12PM to 1PM | 55 | 51.1 | 48 | 50.8 | 21.09 | 0.0752 | 0.34 | 13.39 | 0
April | 21 | 1PM to 2PM | 53.1 | 51.3 | 50 | 54.7 | 21.22 | 0.0755 | 0.36 | 13.35 | 0
April | 21 | 2PM to 3PM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
April | 21 | 3PM to 4PM | 55 | 51.1 | 48 | 50.8 | 21.09 | 0.0752 | 0.34 | 13.39 | 0
April | 21 | 4PM to 5PM | 55 | 51.1 | 48 | 50.8 | 21.09 | 0.0752 | 0.34 | 13.39 | 0
April | 21 | 5PM to 6PM | 53.1 | 48.7 | 45 | 45.2 | 19.74 | 0.0755 | 0.3 | 13.33 | 0
April | 21 | 6PM to 7PM | 53.1 | 49.2 | 46 | 47.1 | 20.03 | 0.0755 | 0.31 | 13.33 | 0
April | 21 | 7PM to 8PM | 53.1 | 48.7 | 45 | 45.2 | 19.74 | 0.0755 | 0.3 | 13.33 | 0
April | 21 | 8PM to 9PM | 52 | 48.8 | 46 | 47.1 | 19.77 | 0.0757 | 0.31 | 13.3 | 0
April | 21 | 9PM to 10PM | 52 | 48.8 | 46 | 47.1 | 19.77 | 0.0757 | 0.31 | 13.3 | 0
April | 21 | 10PM to 11PM | 51.1 | 48.4 | 46 | 47.1 | 19.55 | 0.0758 | 0.31 | 13.28 | 1
April | 21 | 11PM to 12AM | 50 | 47.9 | 46 | 47.1 | 19.29 | 0.076 | 0.31 | 13.25 | 1
April | 22 | 12AM to 1AM | 48.9 | 46.8 | 45 | 45.2 | 18.73 | 0.0761 | 0.3 | 13.22 | 1
April | 22 | 1AM to 2AM | 48.9 | 46.4 | 44.1 | 43.6 | 18.49 | 0.0762 | 0.29 | 13.21 | 1
April | 22 | 2AM to 3AM | 48 | 45 | 42.1 | 40.4 | 17.78 | 0.0763 | 0.27 | 13.18 | 1
April | 22 | 3AM to 4AM | 46.9 | 41.4 | 35.1 | 30.6 | 16 | 0.0765 | 0.2 | 13.12 | 1
April | 22 | 4AM to 5AM | 46 | 37.9 | 27 | 21.4 | 14.36 | 0.0767 | 0.14 | 13.07 | 1
April | 22 | 5AM to 6AM | 45 | 37.7 | 28 | 22.5 | 14.27 | 0.0769 | 0.15 | 13.05 | 1
April | 22 | 6AM to 7AM | 46.9 | 39.5 | 30 | 24.7 | 15.09 | 0.0766 | 0.16 | 13.11 | 1
April | 22 | 7AM to 8AM | 50 | 41.4 | 30.9 | 25.8 | 15.99 | 0.0761 | 0.17 | 13.19 | 1
April | 22 | 8AM to 9AM | 53.1 | 44 | 34 | 29.3 | 17.28 | 0.0756 | 0.2 | 13.28 | 0
April | 22 | 9AM to 10AM | 57 | 45.6 | 33.1 | 28.3 | 18.08 | 0.0751 | 0.19 | 13.38 | 0
April | 22 | 10AM to 11AM | 61 | 47.5 | 33.1 | 28.3 | 19.03 | 0.0745 | 0.19 | 13.48 | 0
April | 22 | 11AM to 12PM | 63 | 48.7 | 34 | 29.3 | 19.68 | 0.0742 | 0.2 | 13.53 | 0
April | 22 | 12PM to 1PM | 64 | 48.1 | 30.9 | 25.8 | 19.38 | 0.0741 | 0.17 | 13.55 | 0
April | 22 | 1PM to 2PM | 64.9 | 48.9 | 32 | 27.1 | 19.8 | 0.0739 | 0.18 | 13.58 | 0
April | 22 | 2PM to 3PM | 64.9 | 48.9 | 32 | 27.1 | 19.8 | 0.0739 | 0.18 | 13.58 | 0
April | 22 | 3PM to 4PM | 64.9 | 48.2 | 30 | 24.7 | 19.44 | 0.0739 | 0.16 | 13.57 | 0
April | 22 | 4PM to 5PM | 64 | 48.5 | 32 | 27.1 | 19.59 | 0.0741 | 0.18 | 13.56 | 0
April | 22 | 5PM to 6PM | 62.1 | 48.3 | 34 | 29.3 | 19.46 | 0.0743 | 0.2 | 13.51 | 0
April | 22 | 6PM to 7PM | 60.1 | 47.4 | 34 | 29.3 | 18.98 | 0.0746 | 0.2 | 13.46 | 0
April | 22 | 7PM to 8PM | 57.9 | 46 | 33.1 | 28.3 | 18.3 | 0.0749 | 0.19 | 13.4 | 0
April | 22 | 8PM to 9PM | 55 | 44.7 | 33.1 | 28.3 | 17.6 | 0.0753 | 0.19 | 13.33 | 0
April | 22 | 9PM to 10PM | 53.1 | 43.3 | 32 | 27.1 | 16.93 | 0.0756 | 0.18 | 13.27 | 0
April | 22 | 10PM to 11PM | 52 | 42.4 | 30.9 | 25.8 | 16.47 | 0.0758 | 0.17 | 13.24 | 0
April | 22 | 11PM to 12AM | 51.1 | 41.9 | 30.9 | 25.8 | 16.25 | 0.0759 | 0.17 | 13.22 | 1
April | 23 | 12AM to 1AM | 50 | 41.4 | 30.9 | 25.8 | 15.99 | 0.0761 | 0.17 | 13.19 | 1
April | 23 | 1AM to 2AM | 48.9 | 40.5 | 30 | 24.7 | 15.57 | 0.0763 | 0.16 | 13.16 | 1
April | 23 | 2AM to 3AM | 46.9 | 39.5 | 30 | 24.7 | 15.09 | 0.0766 | 0.16 | 13.11 | 1
April | 23 | 3AM to 4AM | 46 | 39.8 | 32 | 27.1 | 15.24 | 0.0767 | 0.18 | 13.09 | 1
April | 23 | 4AM to 5AM | 48 | 40 | 30 | 24.7 | 15.35 | 0.0764 | 0.16 | 13.13 | 1
April | 23 | 5AM to 6AM | 46.9 | 39.8 | 30.9 | 25.8 | 15.25 | 0.0766 | 0.17 | 13.11 | 1
April | 23 | 6AM to 7AM | 50 | 41.8 | 32 | 27.1 | 16.19 | 0.0761 | 0.18 | 13.19 | 1
April | 23 | 7AM to 8AM | 55 | 43.2 | 28.9 | 23.5 | 16.86 | 0.0754 | 0.16 | 13.31 | 0
April | 23 | 8AM to 9AM | 57.9 | 45 | 30 | 24.7 | 17.74 | 0.0749 | 0.16 | 13.39 | 0
April | 23 | 9AM to 10AM | 62.1 | 47.6 | 32 | 27.1 | 19.11 | 0.0743 | 0.18 | 13.5 | 0
April | 23 | 10AM to 11AM | 64 | 48.1 | 30.9 | 25.8 | 19.38 | 0.0741 | 0.17 | 13.55 | 0
April | 23 | 11AM to 12PM | 66 | 50 | 34 | 29.3 | 20.42 | 0.0738 | 0.2 | 13.61 | 0
April | 23 | 12PM to 1PM | 68 | 49.6 | 30 | 24.7 | 20.17 | 0.0735 | 0.16 | 13.65 | 0
April | 23 | 1PM to 2PM | 70 | 50.5 | 30 | 24.7 | 20.65 | 0.0732 | 0.16 | 13.7 | 0
April | 23 | 2PM to 3PM | 70 | 51.4 | 33.1 | 28.3 | 21.21 | 0.0732 | 0.19 | 13.71 | 0
April | 23 | 3PM to 4PM | 72 | 52.9 | 35.1 | 30.6 | 22.06 | 0.0729 | 0.2 | 13.77 | 0
April | 23 | 4PM to 5PM | 72 | 52.5 | 34 | 29.3 | 21.85 | 0.0729 | 0.2 | 13.77 | 0
April | 23 | 5PM to 6PM | 70 | 52.1 | 35.1 | 30.6 | 21.58 | 0.0732 | 0.2 | 13.72 | 0
April | 23 | 6PM to 7PM | 66.9 | 51.4 | 37 | 33.2 | 21.23 | 0.0736 | 0.22 | 13.65 | 0
April | 23 | 7PM to 8PM | 64.9 | 49.9 | 35.1 | 30.6 | 20.36 | 0.0739 | 0.2 | 13.59 | 0
April | 23 | 8PM to 9PM | 64 | 49.1 | 34 | 29.3 | 19.94 | 0.074 | 0.2 | 13.56 | 0
April | 23 | 9PM to 10PM | 62.1 | 48.3 | 34 | 29.3 | 19.46 | 0.0743 | 0.2 | 13.51 | 0
April | 23 | 10PM to 11PM | 61 | 47.8 | 34 | 29.3 | 19.2 | 0.0745 | 0.2 | 13.48 | 0
April | 23 | 11PM to 12AM | 60.1 | 47.4 | 34 | 29.3 | 18.98 | 0.0746 | 0.2 | 13.46 | 0
April | 24 | 12AM to 1AM | 57.9 | 46.4 | 34 | 29.3 | 18.46 | 0.0749 | 0.2 | 13.4 | 0
April | 24 | 1AM to 2AM | 57 | 45.9 | 34 | 29.3 | 18.24 | 0.075 | 0.2 | 13.38 | 0
April | 24 | 2AM to 3AM | 55 | 45 | 34 | 29.3 | 17.76 | 0.0753 | 0.2 | 13.33 | 0
April | 24 | 3AM to 4AM | 55 | 45 | 34 | 29.3 | 17.76 | 0.0753 | 0.2 | 13.33 | 0
April | 24 | 4AM to 5AM | 55.9 | 45.4 | 34 | 29.3 | 17.98 | 0.0752 | 0.2 | 13.35 | 0
April | 24 | 5AM to 6AM | 55.9 | 45.8 | 35.1 | 30.6 | 18.18 | 0.0752 | 0.2 | 13.36 | 0
April | 24 | 6AM to 7AM | 62.1 | 48.6 | 35.1 | 30.6 | 19.66 | 0.0743 | 0.2 | 13.52 | 0
April | 24 | 7AM to 8AM | 68 | 53 | 39.9 | 37.2 | 22.11 | 0.0734 | 0.25 | 13.69 | 0
April | 24 | 8AM to 9AM | 71.1 | 56.7 | 46 | 47.1 | 24.41 | 0.073 | 0.31 | 13.8 | 0
April | 24 | 9AM to 10AM | 75 | 59.9 | 50 | 54.7 | 26.57 | 0.0724 | 0.36 | 13.93 | 0
April | 24 | 10AM to 11AM | 78.1 | 62.5 | 53.1 | 61.4 | 28.35 | 0.0719 | 0.41 | 14.03 | 0
April | 24 | 11AM to 12PM | 81 | 64.9 | 55.9 | 68.3 | 30.14 | 0.0715 | 0.45 | 14.12 | 0
April | 24 | 12PM to 1PM | 82.9 | 65.1 | 55 | 66.1 | 30.27 | 0.0712 | 0.44 | 14.17 | 0
April | 24 | 1PM to 2PM | 84 | 65.4 | 55 | 66.1 | 30.54 | 0.0711 | 0.44 | 14.2 | 0
April | 24 | 2PM to 3PM | 84 | 64 | 52 | 59 | 29.42 | 0.0711 | 0.39 | 14.17 | 0
April | 24 | 3PM to 4PM | 86 | 64.6 | 52 | 59 | 29.9 | 0.0709 | 0.39 | 14.23 | 0
April | 24 | 4PM to 5PM | 84.9 | 63.8 | 51.1 | 57 | 29.33 | 0.071 | 0.38 | 14.19 | 0
April | 24 | 5PM to 6PM | 84 | 63.5 | 51.1 | 57 | 29.11 | 0.0712 | 0.38 | 14.17 | 0
April | 24 | 6PM to 7PM | 81 | 62.9 | 52 | 59 | 28.67 | 0.0715 | 0.39 | 14.1 | 0
April | 24 | 7PM to 8PM | 79 | 61.8 | 51.1 | 57 | 27.89 | 0.0718 | 0.38 | 14.04 | 0
April | 24 | 8PM to 9PM | 77 | 61.1 | 51.1 | 57 | 27.4 | 0.0721 | 0.38 | 13.99 | 0
April | 24 | 9PM to 10PM | 75.9 | 60.8 | 51.1 | 57 | 27.14 | 0.0722 | 0.38 | 13.96 | 0
April | 24 | 10PM to 11PM | 73.9 | 61 | 53.1 | 61.4 | 27.34 | 0.0725 | 0.41 | 13.92 | 0
April | 24 | 11PM to 12AM | 73.9 | 61.5 | 54 | 63.5 | 27.67 | 0.0725 | 0.42 | 13.93 | 0
April | 25 | 12AM to 1AM | 72 | 61.8 | 55.9 | 68.3 | 27.94 | 0.0727 | 0.45 | 13.89 | 0
April | 25 | 1AM to 2AM | 70 | 61.7 | 57 | 71.1 | 27.89 | 0.073 | 0.47 | 13.85 | 0
April | 25 | 2AM to 3AM | 68 | 61 | 57 | 71.1 | 27.4 | 0.0732 | 0.47 | 13.79 | 0
April | 25 | 3AM to 4AM | 69.1 | 63.2 | 60.1 | 79.5 | 28.98 | 0.073 | 0.52 | 13.85 | 0
April | 25 | 4AM to 5AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
April | 25 | 5AM to 6AM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
April | 25 | 6AM to 7AM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
April | 25 | 7AM to 8AM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
April | 25 | 8AM to 9AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
April | 25 | 9AM to 10AM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
April | 25 | 10AM to 11AM | 81 | 68.2 | 62.1 | 85.4 | 32.81 | 0.0714 | 0.56 | 14.18 | 0
April | 25 | 11AM to 12PM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
April | 25 | 12PM to 1PM | 84.9 | 68.8 | 61 | 82.1 | 33.27 | 0.0709 | 0.54 | 14.27 | 0
April | 25 | 1PM to 2PM | 84.9 | 67.7 | 59 | 76.4 | 32.38 | 0.0709 | 0.5 | 14.25 | 0
April | 25 | 2PM to 3PM | 84 | 69.1 | 62.1 | 85.4 | 33.56 | 0.071 | 0.56 | 14.26 | 0
April | 25 | 3PM to 4PM | 82.9 | 67.7 | 60.1 | 79.5 | 32.37 | 0.0712 | 0.52 | 14.21 | 0
April | 25 | 4PM to 5PM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
April | 25 | 5PM to 6PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
April | 25 | 6PM to 7PM | 79 | 65.8 | 59 | 76.4 | 30.92 | 0.0717 | 0.5 | 14.1 | 0
April | 25 | 7PM to 8PM | 78.1 | 66.2 | 60.1 | 79.5 | 31.18 | 0.0718 | 0.52 | 14.08 | 0
April | 25 | 8PM to 9PM | 75.9 | 66.6 | 62.1 | 85.4 | 31.57 | 0.0721 | 0.56 | 14.05 | 0
April | 25 | 9PM to 10PM | 73.9 | 66.5 | 63 | 88.2 | 31.53 | 0.0723 | 0.58 | 14 | 0
April | 25 | 10PM to 11PM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
April | 25 | 11PM to 12AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
April | 26 | 12AM to 1AM | 71.1 | 65.6 | 63 | 88.2 | 30.82 | 0.0727 | 0.58 | 13.93 | 0
April | 26 | 1AM to 2AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
April | 26 | 2AM to 3AM | 70 | 65.3 | 63 | 88.2 | 30.55 | 0.0728 | 0.58 | 13.9 | 0
April | 26 | 3AM to 4AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
April | 26 | 4AM to 5AM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
April | 26 | 5AM to 6AM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
April | 26 | 6AM to 7AM | 68 | 64.1 | 62.1 | 85.4 | 29.63 | 0.0731 | 0.56 | 13.84 | 0
April | 26 | 7AM to 8AM | 70 | 65.3 | 63 | 88.2 | 30.55 | 0.0728 | 0.58 | 13.9 | 0
April | 26 | 8AM to 9AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
April | 26 | 9AM to 10AM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
April | 26 | 10AM to 11AM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
April | 26 | 11AM to 12PM | 82 | 69 | 63 | 88.2 | 33.52 | 0.0712 | 0.58 | 14.22 | 0
April | 26 | 12PM to 1PM | 84 | 69.6 | 63 | 88.2 | 34 | 0.071 | 0.58 | 14.27 | 0
April | 26 | 1PM to 2PM | 84.9 | 69.9 | 63 | 88.2 | 34.22 | 0.0709 | 0.58 | 14.29 | 0
April | 26 | 2PM to 3PM | 84.9 | 68.8 | 61 | 82.1 | 33.27 | 0.0709 | 0.54 | 14.27 | 0
April | 26 | 3PM to 4PM | 86 | 67.5 | 57.9 | 73.5 | 32.18 | 0.0708 | 0.48 | 14.27 | 0
April | 26 | 4PM to 5PM | 86 | 67.5 | 57.9 | 73.5 | 32.18 | 0.0708 | 0.48 | 14.27 | 0
April | 26 | 5PM to 6PM | 84.9 | 67.1 | 57.9 | 73.5 | 31.91 | 0.0709 | 0.48 | 14.24 | 0
April | 26 | 6PM to 7PM | 82.9 | 66.5 | 57.9 | 73.5 | 31.43 | 0.0712 | 0.48 | 14.19 | 0
April | 26 | 7PM to 8PM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
April | 26 | 8PM to 9PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
April | 26 | 9PM to 10PM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
April | 26 | 10PM to 11PM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
April | 26 | 11PM to 12AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
April | 27 | 12AM to 1AM | 64 | 62.7 | 62.1 | 85.4 | 28.66 | 0.0737 | 0.56 | 13.74 | 0
April | 27 | 1AM to 2AM | 64 | 62.7 | 62.1 | 85.4 | 28.66 | 0.0737 | 0.56 | 13.74 | 0
April | 27 | 2AM to 3AM | 64 | 60.8 | 59 | 76.4 | 27.26 | 0.0737 | 0.5 | 13.71 | 0
April | 27 | 3AM to 4AM | 62.1 | 56.1 | 52 | 59 | 24.07 | 0.0741 | 0.39 | 13.6 | 0
April | 27 | 4AM to 5AM | 60.1 | 53.2 | 48 | 50.8 | 22.31 | 0.0745 | 0.34 | 13.53 | 0
April | 27 | 5AM to 6AM | 57.9 | 51.8 | 46.9 | 48.8 | 21.47 | 0.0748 | 0.32 | 13.46 | 0
April | 27 | 6AM to 7AM | 55.9 | 49.1 | 43 | 41.9 | 19.92 | 0.0751 | 0.28 | 13.39 | 0
April | 27 | 7AM to 8AM | 55.9 | 48.2 | 41 | 38.8 | 19.44 | 0.0751 | 0.26 | 13.38 | 0
April | 27 | 8AM to 9AM | 57.9 | 49.1 | 41 | 38.8 | 19.92 | 0.0749 | 0.26 | 13.43 | 0
April | 27 | 9AM to 10AM | 59 | 49.5 | 41 | 38.8 | 20.18 | 0.0747 | 0.26 | 13.46 | 0
April | 27 | 10AM to 11AM | 62.1 | 52.2 | 44.1 | 43.6 | 21.68 | 0.0742 | 0.29 | 13.56 | 0
April | 27 | 11AM to 12PM | 64 | 52.2 | 42.1 | 40.4 | 21.66 | 0.074 | 0.27 | 13.6 | 0
April | 27 | 12PM to 1PM | 64.9 | 53.4 | 44.1 | 43.6 | 22.38 | 0.0738 | 0.29 | 13.63 | 0
April | 27 | 1PM to 2PM | 66 | 54.7 | 46 | 47.1 | 23.18 | 0.0737 | 0.31 | 13.67 | 0
April | 27 | 2PM to 3PM | 69.1 | 56.3 | 46.9 | 48.8 | 24.18 | 0.0732 | 0.32 | 13.75 | 0
April | 27 | 3PM to 4PM | 69.1 | 56.8 | 48 | 50.8 | 24.5 | 0.0732 | 0.34 | 13.76 | 0
April | 27 | 4PM to 5PM | 66.9 | 55.5 | 46.9 | 48.8 | 23.66 | 0.0735 | 0.32 | 13.7 | 0
April | 27 | 5PM to 6PM | 61 | 54 | 48.9 | 52.6 | 22.81 | 0.0743 | 0.35 | 13.55 | 0
April | 27 | 6PM to 7PM | 59 | 54.4 | 51.1 | 57 | 23.02 | 0.0746 | 0.38 | 13.52 | 0
April | 27 | 7PM to 8PM | 55.9 | 53.1 | 51.1 | 57 | 22.27 | 0.075 | 0.38 | 13.44 | 0
April | 27 | 8PM to 9PM | 55 | 52.2 | 50 | 54.7 | 21.7 | 0.0752 | 0.36 | 13.41 | 0
April | 27 | 9PM to 10PM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
April | 27 | 10PM to 11PM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
April | 27 | 11PM to 12AM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
April | 28 | 12AM to 1AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
April | 28 | 1AM to 2AM | 53.1 | 53.1 | 53.1 | 61.4 | 22.25 | 0.0754 | 0.41 | 13.38 | 0
April | 28 | 2AM to 3AM | 54 | 53.4 | 53.1 | 61.4 | 22.47 | 0.0753 | 0.41 | 13.4 | 0
April | 28 | 3AM to 4AM | 54 | 53.4 | 53.1 | 61.4 | 22.47 | 0.0753 | 0.41 | 13.4 | 0
April | 28 | 4AM to 5AM | 55 | 54.4 | 54 | 63.5 | 23.06 | 0.0751 | 0.42 | 13.43 | 0
April | 28 | 5AM to 6AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
April | 28 | 6AM to 7AM | 52 | 51.5 | 51.1 | 57 | 21.31 | 0.0756 | 0.38 | 13.33 | 0
April | 28 | 7AM to 8AM | 52 | 51.5 | 51.1 | 57 | 21.31 | 0.0756 | 0.38 | 13.33 | 0
April | 28 | 8AM to 9AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
April | 28 | 9AM to 10AM | 57 | 56.4 | 55.9 | 68.3 | 24.29 | 0.0748 | 0.45 | 13.5 | 0
April | 28 | 10AM to 11AM | 57.9 | 57.4 | 57 | 71.1 | 24.94 | 0.0747 | 0.47 | 13.53 | 0
April | 28 | 11AM to 12PM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
April | 28 | 12PM to 1PM | 63 | 62.4 | 62.1 | 85.4 | 28.39 | 0.0738 | 0.56 | 13.71 | 0
April | 28 | 1PM to 2PM | 64.9 | 61.8 | 60.1 | 79.5 | 27.96 | 0.0736 | 0.52 | 13.74 | 0
April | 28 | 2PM to 3PM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
April | 28 | 3PM to 4PM | 73.9 | 64.2 | 59 | 76.4 | 29.69 | 0.0724 | 0.5 | 13.97 | 0
April | 28 | 4PM to 5PM | 75.9 | 66 | 61 | 82.1 | 31.06 | 0.0721 | 0.54 | 14.04 | 0
April | 28 | 5PM to 6PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
April | 28 | 6PM to 7PM | 73.9 | 64.8 | 60.1 | 79.5 | 30.17 | 0.0724 | 0.52 | 13.98 | 0
April | 28 | 7PM to 8PM | 71.1 | 60.5 | 54 | 63.5 | 26.97 | 0.0729 | 0.42 | 13.85 | 0
April | 28 | 8PM to 9PM | 64 | 57.4 | 53.1 | 61.4 | 24.93 | 0.0738 | 0.41 | 13.66 | 0
April | 28 | 9PM to 10PM | 61 | 54.6 | 50 | 54.7 | 23.15 | 0.0743 | 0.36 | 13.56 | 0
April | 28 | 10PM to 11PM | 57.9 | 53.4 | 50 | 54.7 | 22.4 | 0.0748 | 0.36 | 13.48 | 0
April | 28 | 11PM to 12AM | 55.9 | 51.5 | 48 | 50.8 | 21.31 | 0.0751 | 0.34 | 13.42 | 0
April | 29 | 12AM to 1AM | 54 | 49.1 | 45 | 45.2 | 19.96 | 0.0754 | 0.3 | 13.35 | 0
April | 29 | 1AM to 2AM | 52 | 47.8 | 44.1 | 43.6 | 19.24 | 0.0757 | 0.29 | 13.29 | 0
April | 29 | 2AM to 3AM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
April | 29 | 3AM to 4AM | 48 | 43.1 | 37.9 | 34.4 | 16.84 | 0.0763 | 0.23 | 13.16 | 1
April | 29 | 4AM to 5AM | 46.9 | 42.6 | 37.9 | 34.4 | 16.58 | 0.0765 | 0.23 | 13.13 | 1
April | 29 | 5AM to 6AM | 46 | 41.8 | 37 | 33.2 | 16.17 | 0.0767 | 0.22 | 13.11 | 1
April | 29 | 6AM to 7AM | 46 | 42.1 | 37.9 | 34.4 | 16.36 | 0.0766 | 0.23 | 13.11 | 1
April | 29 | 7AM to 8AM | 44.1 | 40.8 | 37 | 33.2 | 15.69 | 0.077 | 0.22 | 13.06 | 1
April | 29 | 8AM to 9AM | 44.1 | 41.1 | 37.9 | 34.4 | 15.88 | 0.0769 | 0.23 | 13.06 | 1
April | 29 | 9AM to 10AM | 43 | 40.6 | 37.9 | 34.4 | 15.62 | 0.0771 | 0.23 | 13.03 | 1
April | 29 | 10AM to 11AM | 45 | 41.2 | 37 | 33.2 | 15.91 | 0.0768 | 0.22 | 13.08 | 1
April | 29 | 11AM to 12PM | 46.9 | 41 | 34 | 29.3 | 15.8 | 0.0765 | 0.2 | 13.12 | 1
April | 29 | 12PM to 1PM | 48 | 42.8 | 37 | 33.2 | 16.65 | 0.0764 | 0.22 | 13.16 | 1
April | 29 | 1PM to 2PM | 51.1 | 45.1 | 39 | 35.9 | 17.81 | 0.0759 | 0.24 | 13.25 | 1
April | 29 | 2PM to 3PM | 52 | 45.5 | 39 | 35.9 | 18.03 | 0.0757 | 0.24 | 13.27 | 0
April | 29 | 3PM to 4PM | 53.1 | 46 | 39 | 35.9 | 18.29 | 0.0756 | 0.24 | 13.3 | 0
April | 29 | 4PM to 5PM | 52 | 44.7 | 37 | 33.2 | 17.61 | 0.0758 | 0.22 | 13.26 | 0
April | 29 | 5PM to 6PM | 53.1 | 45.2 | 37 | 33.2 | 17.87 | 0.0756 | 0.22 | 13.29 | 0
April | 29 | 6PM to 7PM | 51.1 | 45.9 | 41 | 38.8 | 18.26 | 0.0759 | 0.26 | 13.26 | 1
April | 29 | 7PM to 8PM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
April | 29 | 8PM to 9PM | 48.9 | 45.8 | 43 | 41.9 | 18.22 | 0.0762 | 0.28 | 13.21 | 1
April | 29 | 9PM to 10PM | 48 | 45.4 | 43 | 41.9 | 18 | 0.0763 | 0.28 | 13.19 | 1
April | 29 | 10PM to 11PM | 48 | 45.4 | 43 | 41.9 | 18 | 0.0763 | 0.28 | 13.19 | 1
April | 29 | 11PM to 12AM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
April | 30 | 12AM to 1AM | 46.9 | 44.9 | 43 | 41.9 | 17.74 | 0.0765 | 0.28 | 13.16 | 1
April | 30 | 1AM to 2AM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
April | 30 | 2AM to 3AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
April | 30 | 3AM to 4AM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
April | 30 | 4AM to 5AM | 46 | 44.5 | 43 | 41.9 | 17.52 | 0.0766 | 0.28 | 13.13 | 1
April | 30 | 5AM to 6AM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
April | 30 | 6AM to 7AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
April | 30 | 7AM to 8AM | 46.9 | 46.5 | 46 | 47.1 | 18.55 | 0.0764 | 0.31 | 13.17 | 1
April | 30 | 8AM to 9AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
April | 30 | 9AM to 10AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
April | 30 | 10AM to 11AM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
April | 30 | 11AM to 12PM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
April | 30 | 12PM to 1PM | 46.9 | 46.9 | 46.9 | 48.8 | 18.8 | 0.0764 | 0.32 | 13.18 | 1
April | 30 | 1PM to 2PM | 46.9 | 46.5 | 46 | 47.1 | 18.55 | 0.0764 | 0.31 | 13.17 | 1
April | 30 | 2PM to 3PM | 45 | 44.5 | 44.1 | 43.6 | 17.53 | 0.0767 | 0.29 | 13.11 | 1
April | 30 | 3PM to 4PM | 46 | 43.5 | 41 | 38.8 | 17.04 | 0.0766 | 0.26 | 13.12 | 1
April | 30 | 4PM to 5PM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
April | 30 | 5PM to 6PM | 44.1 | 41.6 | 39 | 35.9 | 16.11 | 0.0769 | 0.24 | 13.06 | 1
April | 30 | 6PM to 7PM | 44.1 | 41.1 | 37.9 | 34.4 | 15.88 | 0.0769 | 0.23 | 13.06 | 1
April | 30 | 7PM to 8PM | 42.1 | 40.1 | 37.9 | 34.4 | 15.4 | 0.0772 | 0.23 | 13.01 | 1
April | 30 | 8PM to 9PM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
April | 30 | 9PM to 10PM | 45.5 | 43 | 40.5 | 37.9 | 16.78 | 0.0767 | 0.25 | 13.11 | 1
April | 30 | 10PM to 11PM | 48 | 45.9 | 43.9 | 43.3 | 18.23 | 0.0763 | 0.29 | 13.19 | 1
April | 30 | 11PM to 12AM | 50.5 | 48.8 | 47.3 | 49.4 | 19.78 | 0.0759 | 0.33 | 13.27 | 1
May | 1 | 12AM to 1AM | 53.2 | 51.7 | 50.5 | 55.9 | 21.44 | 0.0754 | 0.37 | 13.36 | 0
May | 1 | 1AM to 2AM | 55.8 | 54.7 | 54 | 63.5 | 23.23 | 0.075 | 0.42 | 13.45 | 0
May | 1 | 2AM to 3AM | 58.3 | 57.7 | 57.4 | 72 | 25.17 | 0.0746 | 0.48 | 13.54 | 0
May | 1 | 3AM to 4AM | 60.8 | 60.8 | 60.8 | 81.6 | 27.27 | 0.0742 | 0.54 | 13.64 | 0
May | 1 | 4AM to 5AM | 60.1 | 60.1 | 60.1 | 79.5 | 26.77 | 0.0743 | 0.52 | 13.61 | 0
May | 1 | 5AM to 6AM | 61 | 60.4 | 60.1 | 79.5 | 26.99 | 0.0742 | 0.52 | 13.64 | 0
May | 1 | 6AM to 7AM | 62.1 | 60.8 | 60.1 | 79.5 | 27.26 | 0.074 | 0.52 | 13.67 | 0
May | 1 | 7AM to 8AM | 64 | 62.7 | 62.1 | 85.4 | 28.66 | 0.0737 | 0.56 | 13.74 | 0
May | 1 | 8AM to 9AM | 64 | 63.3 | 63 | 88.2 | 29.09 | 0.0737 | 0.58 | 13.74 | 0
May | 1 | 9AM to 10AM | 64.9 | 64.3 | 64 | 91.7 | 29.86 | 0.0735 | 0.6 | 13.78 | 0
May | 1 | 10AM to 11AM | 64.9 | 64.9 | 64.9 | 94.6 | 30.32 | 0.0735 | 0.62 | 13.79 | 0
May | 1 | 11AM to 12PM | 66 | 66 | 66 | 98.4 | 31.17 | 0.0733 | 0.64 | 13.83 | 0
May | 1 | 12PM to 1PM | 66 | 66 | 66 | 98.4 | 31.17 | 0.0733 | 0.64 | 13.83 | 0
May | 1 | 1PM to 2PM | 66.9 | 66.9 | 66.9 | 101.5 | 31.88 | 0.0732 | 0.67 | 13.86 | 0
May | 1 | 2PM to 3PM | 68 | 68 | 68 | 105.5 | 32.77 | 0.073 | 0.69 | 13.9 | 0
May | 1 | 3PM to 4PM | 69.1 | 69.1 | 69.1 | 109.6 | 33.67 | 0.0728 | 0.72 | 13.94 | 0
May | 1 | 4PM to 5PM | 70 | 70 | 70 | 113.1 | 34.44 | 0.0727 | 0.74 | 13.98 | 0
May | 1 | 5PM to 6PM | 70 | 70 | 70 | 113.1 | 34.44 | 0.0727 | 0.74 | 13.98 | 0
May | 1 | 6PM to 7PM | 70 | 70 | 70 | 113.1 | 34.44 | 0.0727 | 0.74 | 13.98 | 0
May | 1 | 7PM to 8PM | 69.8 | 69.8 | 69.8 | 112.4 | 34.28 | 0.0727 | 0.73 | 13.97 | 0
May | 1 | 8PM to 9PM | 66 | 66 | 66 | 98.4 | 31.17 | 0.0733 | 0.64 | 13.83 | 0
May | 1 | 9PM to 10PM | 64.9 | 64.3 | 64 | 91.7 | 29.86 | 0.0735 | 0.6 | 13.78 | 0
May | 1 | 10PM to 11PM | 62.1 | 60.8 | 60.1 | 79.5 | 27.26 | 0.074 | 0.52 | 13.67 | 0
May | 1 | 11PM to 12AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
May | 2 | 12AM to 1AM | 53.1 | 51.3 | 50 | 54.7 | 21.22 | 0.0755 | 0.36 | 13.35 | 0
May | 2 | 1AM to 2AM | 53.1 | 51.3 | 50 | 54.7 | 21.22 | 0.0755 | 0.36 | 13.35 | 0
May | 2 | 2AM to 3AM | 53.1 | 50.7 | 48.9 | 52.6 | 20.88 | 0.0755 | 0.35 | 13.35 | 0
May | 2 | 3AM to 4AM | 52 | 50.3 | 48.9 | 52.6 | 20.62 | 0.0756 | 0.35 | 13.32 | 0
May | 2 | 4AM to 5AM | 52 | 49.8 | 48 | 50.8 | 20.34 | 0.0756 | 0.34 | 13.31 | 0
May | 2 | 5AM to 6AM | 51.1 | 48.8 | 46.9 | 48.8 | 19.81 | 0.0758 | 0.32 | 13.29 | 1
May | 2 | 6AM to 7AM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
May | 2 | 7AM to 8AM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
May | 2 | 8AM to 9AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
May | 2 | 9AM to 10AM | 51.1 | 47.8 | 45 | 45.2 | 19.26 | 0.0758 | 0.3 | 13.27 | 1
May | 2 | 10AM to 11AM | 55 | 50.1 | 46 | 47.1 | 20.52 | 0.0752 | 0.31 | 13.38 | 0
May | 2 | 11AM to 12PM | 55.9 | 49.6 | 44.1 | 43.6 | 20.2 | 0.0751 | 0.29 | 13.4 | 0
May | 2 | 12PM to 1PM | 57 | 49.5 | 43 | 41.9 | 20.18 | 0.075 | 0.28 | 13.42 | 0
May | 2 | 1PM to 2PM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
May | 2 | 2PM to 3PM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
May | 2 | 3PM to 4PM | 57.9 | 48.6 | 39.9 | 37.2 | 19.67 | 0.0749 | 0.25 | 13.43 | 0
May | 2 | 4PM to 5PM | 57.9 | 48.2 | 39 | 35.9 | 19.47 | 0.0749 | 0.24 | 13.42 | 0
May | 2 | 5PM to 6PM | 57 | 46.7 | 36 | 31.8 | 18.62 | 0.075 | 0.21 | 13.39 | 0
May | 2 | 6PM to 7PM | 55 | 45.4 | 35.1 | 30.6 | 17.96 | 0.0753 | 0.2 | 13.33 | 0
May | 2 | 7PM to 8PM | 52 | 43.5 | 34 | 29.3 | 17.02 | 0.0758 | 0.2 | 13.25 | 0
May | 2 | 8PM to 9PM | 51.1 | 43.5 | 35.1 | 30.6 | 17 | 0.0759 | 0.2 | 13.23 | 1
May | 2 | 9PM to 10PM | 48 | 43.1 | 37.9 | 34.4 | 16.84 | 0.0763 | 0.23 | 13.16 | 1
May | 2 | 10PM to 11PM | 46 | 43 | 39.9 | 37.2 | 16.79 | 0.0766 | 0.25 | 13.12 | 1
May | 2 | 11PM to 12AM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
May | 3 | 12AM to 1AM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
May | 3 | 1AM to 2AM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
May | 3 | 2AM to 3AM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
May | 3 | 3AM to 4AM | 41 | 40.1 | 39 | 35.9 | 15.37 | 0.0774 | 0.24 | 12.98 | 1
May | 3 | 4AM to 5AM | 42.1 | 40.6 | 39 | 35.9 | 15.63 | 0.0772 | 0.24 | 13.01 | 1
May | 3 | 5AM to 6AM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
May | 3 | 6AM to 7AM | 50 | 45.4 | 41 | 38.8 | 18 | 0.076 | 0.26 | 13.23 | 1
May | 3 | 7AM to 8AM | 55 | 46.9 | 39 | 35.9 | 18.77 | 0.0753 | 0.24 | 13.35 | 0
May | 3 | 8AM to 9AM | 60.1 | 47.4 | 34 | 29.3 | 18.98 | 0.0746 | 0.2 | 13.46 | 0
May | 3 | 9AM to 10AM | 62.1 | 48.9 | 36 | 31.8 | 19.84 | 0.0743 | 0.21 | 13.52 | 0
May | 3 | 10AM to 11AM | 63 | 50.5 | 39 | 35.9 | 20.69 | 0.0742 | 0.24 | 13.55 | 0
May | 3 | 11AM to 12PM | 64 | 51.3 | 39.9 | 37.2 | 21.15 | 0.074 | 0.25 | 13.59 | 0
May | 3 | 12PM to 1PM | 66 | 52.6 | 41 | 38.8 | 21.88 | 0.0737 | 0.26 | 13.64 | 0
May | 3 | 1PM to 2PM | 68 | 54.2 | 43 | 41.9 | 22.85 | 0.0734 | 0.28 | 13.7 | 0
May | 3 | 2PM to 3PM | 68 | 54.2 | 43 | 41.9 | 22.85 | 0.0734 | 0.28 | 13.7 | 0
May | 3 | 3PM to 4PM | 66.9 | 53.4 | 42.1 | 40.4 | 22.36 | 0.0736 | 0.27 | 13.67 | 0
May | 3 | 4PM to 5PM | 64.9 | 52.1 | 41 | 38.8 | 21.62 | 0.0739 | 0.26 | 13.61 | 0
May | 3 | 5PM to 6PM | 64 | 52.2 | 42.1 | 40.4 | 21.66 | 0.074 | 0.27 | 13.6 | 0
May | 3 | 6PM to 7PM | 63 | 52.1 | 43 | 41.9 | 21.63 | 0.0741 | 0.28 | 13.57 | 0
May | 3 | 7PM to 8PM | 62.1 | 51.3 | 42.1 | 40.4 | 21.18 | 0.0743 | 0.27 | 13.55 | 0
May | 3 | 8PM to 9PM | 61 | 51.3 | 43 | 41.9 | 21.14 | 0.0744 | 0.28 | 13.52 | 0
May | 3 | 9PM to 10PM | 61 | 51.3 | 43 | 41.9 | 21.14 | 0.0744 | 0.28 | 13.52 | 0
May | 3 | 10PM to 11PM | 57.9 | 50.4 | 44.1 | 43.6 | 20.68 | 0.0748 | 0.29 | 13.45 | 0
May | 3 | 11PM to 12AM | 57.9 | 51.3 | 46 | 47.1 | 21.22 | 0.0748 | 0.31 | 13.46 | 0
May | 4 | 12AM to 1AM | 55 | 52.2 | 50 | 54.7 | 21.7 | 0.0752 | 0.36 | 13.41 | 0
May | 4 | 1AM to 2AM | 54 | 51.7 | 50 | 54.7 | 21.44 | 0.0753 | 0.36 | 13.38 | 0
May | 4 | 2AM to 3AM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
May | 4 | 3AM to 4AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
May | 4 | 4AM to 5AM | 51.1 | 49.9 | 48.9 | 52.6 | 20.4 | 0.0758 | 0.35 | 13.3 | 1
May | 4 | 5AM to 6AM | 52 | 50.3 | 48.9 | 52.6 | 20.62 | 0.0756 | 0.35 | 13.32 | 0
May | 4 | 6AM to 7AM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
May | 4 | 7AM to 8AM | 59 | 52.2 | 46.9 | 48.8 | 21.73 | 0.0746 | 0.32 | 13.49 | 0
May | 4 | 8AM to 9AM | 62.1 | 53.5 | 46.9 | 48.8 | 22.48 | 0.0742 | 0.32 | 13.57 | 0
May | 4 | 9AM to 10AM | 64 | 53.4 | 45 | 45.2 | 22.4 | 0.0739 | 0.3 | 13.61 | 0
May | 4 | 10AM to 11AM | 66 | 54.2 | 45 | 45.2 | 22.89 | 0.0737 | 0.3 | 13.66 | 0
May | 4 | 11AM to 12PM | 68 | 55 | 45 | 45.2 | 23.37 | 0.0734 | 0.3 | 13.71 | 0
May | 4 | 12PM to 1PM | 69.1 | 55.4 | 45 | 45.2 | 23.63 | 0.0732 | 0.3 | 13.74 | 0
May | 4 | 1PM to 2PM | 71.1 | 58 | 48.9 | 52.6 | 25.26 | 0.0729 | 0.35 | 13.82 | 0
May | 4 | 2PM to 3PM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
May | 4 | 3PM to 4PM | 73 | 58.3 | 48 | 50.8 | 25.47 | 0.0727 | 0.34 | 13.86 | 0
May | 4 | 4PM to 5PM | 73 | 58.7 | 48.9 | 52.6 | 25.74 | 0.0726 | 0.35 | 13.87 | 0
May | 4 | 5PM to 6PM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
May | 4 | 6PM to 7PM | 69.1 | 57.7 | 50 | 54.7 | 25.12 | 0.0732 | 0.36 | 13.77 | 0
May | 4 | 7PM to 8PM | 68 | 57.3 | 50 | 54.7 | 24.86 | 0.0733 | 0.36 | 13.74 | 0
May | 4 | 8PM to 9PM | 64 | 56.8 | 52 | 59 | 24.55 | 0.0739 | 0.39 | 13.65 | 0
May | 4 | 9PM to 10PM | 61 | 55.2 | 51.1 | 57 | 23.5 | 0.0743 | 0.38 | 13.57 | 0
May | 4 | 10PM to 11PM | 62.1 | 55 | 50 | 54.7 | 23.41 | 0.0742 | 0.36 | 13.59 | 0
May | 4 | 11PM to 12AM | 61 | 55.2 | 51.1 | 57 | 23.5 | 0.0743 | 0.38 | 13.57 | 0
May | 5 | 12AM to 1AM | 62.1 | 55.6 | 51.1 | 57 | 23.76 | 0.0741 | 0.38 | 13.6 | 0
May | 5 | 1AM to 2AM | 61 | 55.6 | 52 | 59 | 23.8 | 0.0743 | 0.39 | 13.57 | 0
May | 5 | 2AM to 3AM | 59 | 54.9 | 52 | 59 | 23.32 | 0.0746 | 0.39 | 13.52 | 0
May | 5 | 3AM to 4AM | 59 | 56.6 | 55 | 66.1 | 24.43 | 0.0745 | 0.44 | 13.54 | 0
May | 5 | 4AM to 5AM | 59 | 56.6 | 55 | 66.1 | 24.43 | 0.0745 | 0.44 | 13.54 | 0
May | 5 | 5AM to 6AM | 59 | 57.1 | 55.9 | 68.3 | 24.77 | 0.0745 | 0.45 | 13.55 | 0
May | 5 | 6AM to 7AM | 63 | 59.2 | 57 | 71.1 | 26.17 | 0.0739 | 0.47 | 13.66 | 0
May | 5 | 7AM to 8AM | 66.9 | 61.2 | 57.9 | 73.5 | 27.51 | 0.0734 | 0.48 | 13.77 | 0
May | 5 | 8AM to 9AM | 71.1 | 62.1 | 57 | 71.1 | 28.15 | 0.0728 | 0.47 | 13.87 | 0
May | 5 | 9AM to 10AM | 73.9 | 61.5 | 54 | 63.5 | 27.67 | 0.0725 | 0.42 | 13.93 | 0
May | 5 | 10AM to 11AM | 75 | 63.5 | 57 | 71.1 | 29.12 | 0.0723 | 0.47 | 13.98 | 0
May | 5 | 11AM to 12PM | 77 | 64.1 | 57 | 71.1 | 29.6 | 0.072 | 0.47 | 14.03 | 0
May | 5 | 12PM to 1PM | 80.1 | 64.6 | 55.9 | 68.3 | 29.92 | 0.0716 | 0.45 | 14.1 | 0
May | 5 | 1PM to 2PM | 81 | 64.9 | 55.9 | 68.3 | 30.14 | 0.0715 | 0.45 | 14.12 | 0
May | 5 | 2PM to 3PM | 82 | 65.2 | 55.9 | 68.3 | 30.4 | 0.0713 | 0.45 | 14.15 | 0
May | 5 | 3PM to 4PM | 82 | 66.2 | 57.9 | 73.5 | 31.21 | 0.0713 | 0.48 | 14.17 | 0
May | 5 | 4PM to 5PM | 82 | 65.8 | 57 | 71.1 | 30.84 | 0.0713 | 0.47 | 14.16 | 0
May | 5 | 5PM to 6PM | 80.1 | 65.6 | 57.9 | 73.5 | 30.72 | 0.0716 | 0.48 | 14.12 | 0
May | 5 | 6PM to 7PM | 77 | 65.8 | 60.1 | 79.5 | 30.92 | 0.0719 | 0.52 | 14.06 | 0
May | 5 | 7PM to 8PM | 75 | 65.7 | 61 | 82.1 | 30.84 | 0.0722 | 0.54 | 14.01 | 0
May | 5 | 8PM to 9PM | 73 | 63.9 | 59 | 76.4 | 29.47 | 0.0725 | 0.5 | 13.94 | 0
May | 5 | 9PM to 10PM | 72 | 63.5 | 59 | 76.4 | 29.2 | 0.0726 | 0.5 | 13.92 | 0
May | 5 | 10PM to 11PM | 71.1 | 63.2 | 59 | 76.4 | 28.98 | 0.0728 | 0.5 | 13.89 | 0
May | 5 | 11PM to 12AM | 70 | 62.3 | 57.9 | 73.5 | 28.26 | 0.0729 | 0.48 | 13.85 | 0
May | 6 | 12AM to 1AM | 70 | 61.1 | 55.9 | 68.3 | 27.45 | 0.073 | 0.45 | 13.84 | 0
May | 6 | 1AM to 2AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
May | 6 | 2AM to 3AM | 64.9 | 64.3 | 64 | 91.7 | 29.86 | 0.0735 | 0.6 | 13.78 | 0
May | 6 | 3AM to 4AM | 64.9 | 64.9 | 64.9 | 94.6 | 30.32 | 0.0735 | 0.62 | 13.79 | 0
May | 6 | 4AM to 5AM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
May | 6 | 5AM to 6AM | 64.9 | 64.9 | 64.9 | 94.6 | 30.32 | 0.0735 | 0.62 | 13.79 | 0
May | 6 | 6AM to 7AM | 64.9 | 64.9 | 64.9 | 94.6 | 30.32 | 0.0735 | 0.62 | 13.79 | 0
May | 6 | 7AM to 8AM | 68 | 67.3 | 66.9 | 101.5 | 32.15 | 0.073 | 0.67 | 13.89 | 0
May | 6 | 8AM to 9AM | 71.1 | 69.7 | 69.1 | 109.6 | 34.16 | 0.0726 | 0.72 | 14 | 0
May | 6 | 9AM to 10AM | 64.4 | 64.4 | 64.4 | 92.8 | 29.91 | 0.0736 | 0.61 | 13.77 | 0
May | 6 | 10AM to 11AM | 64.9 | 63.6 | 63 | 88.2 | 29.32 | 0.0735 | 0.58 | 13.77 | 0
May | 6 | 11AM to 12PM | 66.9 | 66.3 | 66 | 98.4 | 31.39 | 0.0732 | 0.64 | 13.85 | 0
May | 6 | 12PM to 1PM | 71.1 | 66.9 | 64.9 | 94.6 | 31.83 | 0.0727 | 0.62 | 13.95 | 0
May | 6 | 1PM to 2PM | 71.1 | 66.9 | 64.9 | 94.6 | 31.83 | 0.0727 | 0.62 | 13.95 | 0
May | 6 | 2PM to 3PM | 73 | 68.8 | 66.9 | 101.5 | 33.39 | 0.0723 | 0.67 | 14.02 | 0
May | 6 | 3PM to 4PM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
May | 6 | 4PM to 5PM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
May | 6 | 5PM to 6PM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
May | 6 | 6PM to 7PM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
May | 6 | 7PM to 8PM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
May | 6 | 8PM to 9PM | 75.9 | 73.1 | 72 | 121.2 | 37.17 | 0.0718 | 0.79 | 14.16 | 0
May | 6 | 9PM to 10PM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
May | 6 | 10PM to 11PM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
May | 6 | 11PM to 12AM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
May | 7 | 12AM to 1AM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
May | 7 | 1AM to 2AM | 68 | 66.6 | 66 | 98.4 | 31.65 | 0.0731 | 0.64 | 13.88 | 0
May | 7 | 2AM to 3AM | 64.4 | 64.4 | 64.4 | 92.8 | 29.91 | 0.0736 | 0.61 | 13.77 | 0
May | 7 | 3AM to 4AM | 64 | 64 | 64 | 91.7 | 29.64 | 0.0737 | 0.6 | 13.75 | 0
May | 7 | 4AM to 5AM | 64 | 64 | 64 | 91.7 | 29.64 | 0.0737 | 0.6 | 13.75 | 0
May | 7 | 5AM to 6AM | 64.9 | 64.3 | 64 | 91.7 | 29.86 | 0.0735 | 0.6 | 13.78 | 0
May | 7 | 6AM to 7AM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
May | 7 | 7AM to 8AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
May | 7 | 8AM to 9AM | 72 | 67.2 | 64.9 | 94.6 | 32.05 | 0.0725 | 0.62 | 13.97 | 0
May | 7 | 9AM to 10AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
May | 7 | 10AM to 11AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
May | 7 | 11AM to 12PM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
May | 7 | 12PM to 1PM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
May | 7 | 1PM to 2PM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
May | 7 | 2PM to 3PM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
May | 7 | 3PM to 4PM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
May | 7 | 4PM to 5PM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
May | 7 | 5PM to 6PM | 71.1 | 67.6 | 66 | 98.4 | 32.41 | 0.0726 | 0.64 | 13.96 | 0
May | 7 | 6PM to 7PM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
May | 7 | 7PM to 8PM | 71.1 | 66.3 | 64 | 91.7 | 31.36 | 0.0727 | 0.6 | 13.94 | 0
May | 7 | 8PM to 9PM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
May | 7 | 9PM to 10PM | 64.9 | 64.3 | 64 | 91.7 | 29.86 | 0.0735 | 0.6 | 13.78 | 0
May | 7 | 10PM to 11PM | 64 | 64 | 64 | 91.7 | 29.64 | 0.0737 | 0.6 | 13.75 | 0
May | 7 | 11PM to 12AM | 64 | 63.3 | 63 | 88.2 | 29.09 | 0.0737 | 0.58 | 13.74 | 0
May | 8 | 12AM to 1AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 8 | 1AM to 2AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 8 | 2AM to 3AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 8 | 3AM to 4AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 8 | 4AM to 5AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 8 | 5AM to 6AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 8 | 6AM to 7AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 8 | 7AM to 8AM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
May | 8 | 8AM to 9AM | 70 | 67.3 | 66 | 98.4 | 32.14 | 0.0728 | 0.64 | 13.93 | 0
May | 8 | 9AM to 10AM | 73.9 | 69.1 | 66.9 | 101.5 | 33.61 | 0.0722 | 0.67 | 14.05 | 0
May | 8 | 10AM to 11AM | 78.1 | 72.3 | 70 | 113.1 | 36.44 | 0.0716 | 0.74 | 14.19 | 0
May | 8 | 11AM to 12PM | 81 | 73.1 | 70 | 113.1 | 37.15 | 0.0712 | 0.74 | 14.27 | 0
May | 8 | 12PM to 1PM | 82 | 74.1 | 71.1 | 117.4 | 38.1 | 0.0711 | 0.77 | 14.31 | 0
May | 8 | 1PM to 2PM | 81 | 72.5 | 69.1 | 109.6 | 36.6 | 0.0712 | 0.72 | 14.26 | 0
May | 8 | 2PM to 3PM | 80.1 | 72.8 | 70 | 113.1 | 36.93 | 0.0713 | 0.74 | 14.24 | 0
May | 8 | 3PM to 4PM | 79 | 72.5 | 70 | 113.1 | 36.66 | 0.0715 | 0.74 | 14.22 | 0
May | 8 | 4PM to 5PM | 78.1 | 71.7 | 69.1 | 109.6 | 35.89 | 0.0716 | 0.72 | 14.18 | 0
May | 8 | 5PM to 6PM | 78.1 | 71 | 68 | 105.5 | 35.25 | 0.0716 | 0.69 | 14.17 | 0
May | 8 | 6PM to 7PM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
May | 8 | 7PM to 8PM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
May | 8 | 8PM to 9PM | 75 | 71.4 | 70 | 113.1 | 35.69 | 0.072 | 0.74 | 14.11 | 0
May | 8 | 9PM to 10PM | 75 | 71.4 | 70 | 113.1 | 35.69 | 0.072 | 0.74 | 14.11 | 0
May | 8 | 10PM to 11PM | 69.8 | 65 | 62.6 | 87 | 30.33 | 0.0729 | 0.57 | 13.89 | 0
May | 8 | 11PM to 12AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 9 | 12AM to 1AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 9 | 1AM to 2AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
May | 9 | 2AM to 3AM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
May | 9 | 3AM to 4AM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
May | 9 | 4AM to 5AM | 57.2 | 57.2 | 57.2 | 71.5 | 24.83 | 0.0748 | 0.47 | 13.51 | 0
May | 9 | 5AM to 6AM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
May | 9 | 6AM to 7AM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
May | 9 | 7AM to 8AM | 55 | 51.1 | 48 | 50.8 | 21.09 | 0.0752 | 0.34 | 13.39 | 0
May | 9 | 8AM to 9AM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
May | 9 | 9AM to 10AM | 60.1 | 53.2 | 48 | 50.8 | 22.31 | 0.0745 | 0.34 | 13.53 | 0
May | 9 | 10AM to 11AM | 61 | 53.1 | 46.9 | 48.8 | 22.22 | 0.0744 | 0.32 | 13.54 | 0
May | 9 | 11AM to 12PM | 63 | 52.1 | 43 | 41.9 | 21.63 | 0.0741 | 0.28 | 13.57 | 0
May | 9 | 12PM to 1PM | 64.9 | 52.9 | 43 | 41.9 | 22.11 | 0.0738 | 0.28 | 13.62 | 0
May | 9 | 1PM to 2PM | 66 | 54.2 | 45 | 45.2 | 22.89 | 0.0737 | 0.3 | 13.66 | 0
May | 9 | 2PM to 3PM | 66 | 53.4 | 43 | 41.9 | 22.37 | 0.0737 | 0.28 | 13.65 | 0
May | 9 | 3PM to 4PM | 64.9 | 52.9 | 43 | 41.9 | 22.11 | 0.0738 | 0.28 | 13.62 | 0
May | 9 | 4PM to 5PM | 64.9 | 52.1 | 41 | 38.8 | 21.62 | 0.0739 | 0.26 | 13.61 | 0
May | 9 | 5PM to 6PM | 63 | 50.5 | 39 | 35.9 | 20.69 | 0.0742 | 0.24 | 13.55 | 0
May | 9 | 6PM to 7PM | 60.1 | 50.9 | 43 | 41.9 | 20.93 | 0.0745 | 0.28 | 13.5 | 0
May | 9 | 7PM to 8PM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
May | 9 | 8PM to 9PM | 57 | 48.7 | 41 | 38.8 | 19.7 | 0.075 | 0.26 | 13.41 | 0
May | 9 | 9PM to 10PM | 54 | 47.8 | 42.1 | 40.4 | 19.22 | 0.0754 | 0.27 | 13.33 | 0
May | 9 | 10PM to 11PM | 53.1 | 47.3 | 42.1 | 40.4 | 19 | 0.0756 | 0.27 | 13.31 | 0
May | 9 | 11PM to 12AM | 53.1 | 47.3 | 42.1 | 40.4 | 19 | 0.0756 | 0.27 | 13.31 | 0
May | 10 | 12AM to 1AM | 52 | 47.3 | 43 | 41.9 | 18.96 | 0.0757 | 0.28 | 13.29 | 0
May | 10 | 1AM to 2AM | 48.9 | 46.4 | 44.1 | 43.6 | 18.49 | 0.0762 | 0.29 | 13.21 | 1
May | 10 | 2AM to 3AM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
May | 10 | 3AM to 4AM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
May | 10 | 4AM to 5AM | 48.9 | 45.8 | 43 | 41.9 | 18.22 | 0.0762 | 0.28 | 13.21 | 1
May | 10 | 5AM to 6AM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
May | 10 | 6AM to 7AM | 55 | 49.2 | 44.1 | 43.6 | 19.98 | 0.0752 | 0.29 | 13.37 | 0
May | 10 | 7AM to 8AM | 59 | 48.3 | 37.9 | 34.4 | 19.5 | 0.0747 | 0.23 | 13.45 | 0
May | 10 | 8AM to 9AM | 61 | 47.5 | 33.1 | 28.3 | 19.03 | 0.0745 | 0.19 | 13.48 | 0
May | 10 | 9AM to 10AM | 64 | 49.8 | 36 | 31.8 | 20.31 | 0.074 | 0.21 | 13.57 | 0
May | 10 | 10AM to 11AM | 64 | 49.1 | 34 | 29.3 | 19.94 | 0.074 | 0.2 | 13.56 | 0
May | 10 | 11AM to 12PM | 64.9 | 50.2 | 36 | 31.8 | 20.53 | 0.0739 | 0.21 | 13.59 | 0
May | 10 | 12PM to 1PM | 66 | 52.1 | 39.9 | 37.2 | 21.63 | 0.0737 | 0.25 | 13.64 | 0
May | 10 | 1PM to 2PM | 68 | 53 | 39.9 | 37.2 | 22.11 | 0.0734 | 0.25 | 13.69 | 0
May | 10 | 2PM to 3PM | 66.9 | 52.5 | 39.9 | 37.2 | 21.85 | 0.0736 | 0.25 | 13.66 | 0
May | 10 | 3PM to 4PM | 68 | 54.6 | 44.1 | 43.6 | 23.13 | 0.0734 | 0.29 | 13.71 | 0
May | 10 | 4PM to 5PM | 66.9 | 54.2 | 44.1 | 43.6 | 22.86 | 0.0735 | 0.29 | 13.68 | 0
May | 10 | 5PM to 6PM | 64.9 | 52.9 | 43 | 41.9 | 22.11 | 0.0738 | 0.28 | 13.62 | 0
May | 10 | 6PM to 7PM | 64 | 52.2 | 42.1 | 40.4 | 21.66 | 0.074 | 0.27 | 13.6 | 0
May | 10 | 7PM to 8PM | 64 | 52.6 | 43.2 | 42.2 | 21.93 | 0.074 | 0.28 | 13.6 | 0
May | 10 | 8PM to 9PM | 63 | 52.6 | 44.1 | 43.6 | 21.9 | 0.0741 | 0.29 | 13.58 | 0
May | 10 | 9PM to 10PM | 62.1 | 54 | 48 | 50.8 | 22.8 | 0.0742 | 0.34 | 13.58 | 0
May | 10 | 10PM to 11PM | 62.1 | 54.7 | 49.5 | 53.6 | 23.24 | 0.0742 | 0.36 | 13.59 | 0
May | 10 | 11PM to 12AM | 61.3 | 55.1 | 50.7 | 56.3 | 23.47 | 0.0743 | 0.37 | 13.58 | 0
May | 11 | 12AM to 1AM | 60.1 | 50.5 | 42.1 | 40.4 | 20.7 | 0.0745 | 0.27 | 13.49 | 0
May | 11 | 1AM to 2AM | 60.1 | 51.3 | 44.1 | 43.6 | 21.2 | 0.0745 | 0.29 | 13.5 | 0
May | 11 | 2AM to 3AM | 60.1 | 52.3 | 46 | 47.1 | 21.74 | 0.0745 | 0.31 | 13.51 | 0
May | 11 | 3AM to 4AM | 60.1 | 51.8 | 45 | 45.2 | 21.44 | 0.0745 | 0.3 | 13.51 | 0
May | 11 | 4AM to 5AM | 57.9 | 52.8 | 48.9 | 52.6 | 22.06 | 0.0748 | 0.35 | 13.47 | 0
May | 11 | 5AM to 6AM | 57.9 | 52.8 | 48.9 | 52.6 | 22.06 | 0.0748 | 0.35 | 13.47 | 0
May | 11 | 6AM to 7AM | 59 | 52.8 | 48 | 50.8 | 22.05 | 0.0746 | 0.34 | 13.5 | 0
May | 11 | 7AM to 8AM | 60.1 | 53.2 | 48 | 50.8 | 22.31 | 0.0745 | 0.34 | 13.53 | 0
May | 11 | 8AM to 9AM | 62.1 | 55.6 | 51.1 | 57 | 23.76 | 0.0741 | 0.38 | 13.6 | 0
May | 11 | 9AM to 10AM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
May | 11 | 10AM to 11AM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
May | 11 | 11AM to 12PM | 68 | 64.1 | 62.1 | 85.4 | 29.63 | 0.0731 | 0.56 | 13.84 | 0
May | 11 | 12PM to 1PM | 71.6 | 66.7 | 64.4 | 92.8 | 31.68 | 0.0726 | 0.61 | 13.96 | 0
May | 11 | 1PM to 2PM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
May | 11 | 2PM to 3PM | 77 | 70.7 | 68 | 105.5 | 34.99 | 0.0718 | 0.69 | 14.14 | 0
May | 11 | 3PM to 4PM | 79 | 71.2 | 68 | 105.5 | 35.47 | 0.0715 | 0.69 | 14.19 | 0
May | 11 | 4PM to 5PM | 80.1 | 70.3 | 66 | 98.4 | 34.62 | 0.0714 | 0.64 | 14.2 | 0
May | 11 | 5PM to 6PM | 78.1 | 69.7 | 66 | 98.4 | 34.14 | 0.0717 | 0.64 | 14.14 | 0
May | 11 | 6PM to 7PM | 75.9 | 67.8 | 64 | 91.7 | 32.56 | 0.072 | 0.6 | 14.07 | 0
May | 11 | 7PM to 8PM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
May | 11 | 8PM to 9PM | 75 | 70.1 | 68 | 105.5 | 34.5 | 0.0721 | 0.69 | 14.09 | 0
May | 11 | 9PM to 10PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
May | 11 | 10PM to 11PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
May | 11 | 11PM to 12AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
May | 12 | 12AM to 1AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
May | 12 | 1AM to 2AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
May | 12 | 2AM to 3AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
May | 12 | 3AM to 4AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
May | 12 | 4AM to 5AM | 71.1 | 71.1 | 71.1 | 117.4 | 35.39 | 0.0725 | 0.77 | 14.02 | 0
May | 12 | 5AM to 6AM | 72 | 72 | 72 | 121.2 | 36.19 | 0.0724 | 0.79 | 14.06 | 0
May | 12 | 6AM to 7AM | 72 | 72 | 72 | 121.2 | 36.19 | 0.0724 | 0.79 | 14.06 | 0
May | 12 | 7AM to 8AM | 71.6 | 71.6 | 71.6 | 119.7 | 35.87 | 0.0724 | 0.78 | 14.04 | 0
May | 12 | 8AM to 9AM | 72 | 71.3 | 71.1 | 117.4 | 35.61 | 0.0724 | 0.77 | 14.04 | 0
May | 12 | 9AM to 10AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
May | 12 | 10AM to 11AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
May | 12 | 11AM to 12PM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
May | 12 | 12PM to 1PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
May | 12 | 1PM to 2PM | 71.6 | 71.6 | 71.6 | 119.7 | 35.87 | 0.0724 | 0.78 | 14.04 | 0
May | 12 | 2PM to 3PM | 70 | 70 | 70 | 113.1 | 34.44 | 0.0727 | 0.74 | 13.98 | 0
May | 12 | 3PM to 4PM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
May | 12 | 4PM to 5PM | 60.1 | 60.1 | 60.1 | 79.5 | 26.77 | 0.0743 | 0.52 | 13.61 | 0
May | 12 | 5PM to 6PM | 57.9 | 57.9 | 57.9 | 73.5 | 25.31 | 0.0746 | 0.48 | 13.54 | 0
May | 12 | 6PM to 7PM | 57.9 | 57.9 | 57.9 | 73.5 | 25.31 | 0.0746 | 0.48 | 13.54 | 0
May | 12 | 7PM to 8PM | 55.9 | 55.9 | 55.9 | 68.3 | 24.02 | 0.075 | 0.45 | 13.47 | 0
May | 12 | 8PM to 9PM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
May | 12 | 9PM to 10PM | 55 | 55 | 55 | 66.1 | 23.46 | 0.0751 | 0.44 | 13.44 | 0
May | 12 | 10PM to 11PM | 54 | 54 | 54 | 63.5 | 22.79 | 0.0753 | 0.42 | 13.4 | 0
May | 12 | 11PM to 12AM | 53.1 | 53.1 | 53.1 | 61.4 | 22.25 | 0.0754 | 0.41 | 13.38 | 0
May | 13 | 12AM to 1AM | 51.1 | 51.1 | 51.1 | 57 | 21.09 | 0.0757 | 0.38 | 13.31 | 1
May | 13 | 1AM to 2AM | 51.1 | 51.1 | 51.1 | 57 | 21.09 | 0.0757 | 0.38 | 13.31 | 1
May | 13 | 2AM to 3AM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
May | 13 | 3AM to 4AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
May | 13 | 4AM to 5AM | 48.2 | 48.2 | 48.2 | 51.1 | 19.48 | 0.0762 | 0.34 | 13.22 | 1
May | 13 | 5AM to 6AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
May | 13 | 6AM to 7AM | 50 | 47.9 | 46 | 47.1 | 19.29 | 0.076 | 0.31 | 13.25 | 1
May | 13 | 7AM to 8AM | 50 | 47.3 | 45 | 45.2 | 19 | 0.076 | 0.3 | 13.25 | 1
May | 13 | 8AM to 9AM | 51.1 | 47.8 | 45 | 45.2 | 19.26 | 0.0758 | 0.3 | 13.27 | 1
May | 13 | 9AM to 10AM | 53.1 | 48.7 | 45 | 45.2 | 19.74 | 0.0755 | 0.3 | 13.33 | 0
May | 13 | 10AM to 11AM | 55 | 49.2 | 44.1 | 43.6 | 19.98 | 0.0752 | 0.29 | 13.37 | 0
May | 13 | 11AM to 12PM | 57.9 | 51.3 | 46 | 47.1 | 21.22 | 0.0748 | 0.31 | 13.46 | 0
May | 13 | 12PM to 1PM | 60.1 | 51.8 | 45 | 45.2 | 21.44 | 0.0745 | 0.3 | 13.51 | 0
May | 13 | 1PM to 2PM | 61 | 52.6 | 46 | 47.1 | 21.96 | 0.0744 | 0.31 | 13.54 | 0
May | 13 | 2PM to 3PM | 63 | 53.9 | 46.9 | 48.8 | 22.7 | 0.0741 | 0.32 | 13.59 | 0
May | 13 | 3PM to 4PM | 64 | 55.3 | 48.9 | 52.6 | 23.55 | 0.0739 | 0.35 | 13.63 | 0
May | 13 | 4PM to 5PM | 64 | 54.8 | 48 | 50.8 | 23.28 | 0.0739 | 0.34 | 13.63 | 0
May | 13 | 5PM to 6PM | 64 | 55.3 | 48.9 | 52.6 | 23.55 | 0.0739 | 0.35 | 13.63 | 0
May | 13 | 6PM to 7PM | 63 | 54.8 | 48.9 | 52.6 | 23.29 | 0.074 | 0.35 | 13.61 | 0
May | 13 | 7PM to 8PM | 59 | 54.4 | 51.1 | 57 | 23.02 | 0.0746 | 0.38 | 13.52 | 0
May | 13 | 8PM to 9PM | 59 | 54.4 | 51.1 | 57 | 23.02 | 0.0746 | 0.38 | 13.52 | 0
May | 13 | 9PM to 10PM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
May | 13 | 10PM to 11PM | 57.9 | 53.4 | 50 | 54.7 | 22.4 | 0.0748 | 0.36 | 13.48 | 0
May | 13 | 11PM to 12AM | 57 | 52.4 | 48.9 | 52.6 | 21.84 | 0.0749 | 0.35 | 13.45 | 0
May | 14 | 12AM to 1AM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
May | 14 | 1AM to 2AM | 53.1 | 50.7 | 48.9 | 52.6 | 20.88 | 0.0755 | 0.35 | 13.35 | 0
May | 14 | 2AM to 3AM | 51.1 | 49.9 | 48.9 | 52.6 | 20.4 | 0.0758 | 0.35 | 13.3 | 1
May | 14 | 3AM to 4AM | 52 | 49.8 | 48 | 50.8 | 20.34 | 0.0756 | 0.34 | 13.31 | 0
May | 14 | 4AM to 5AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
May | 14 | 5AM to 6AM | 52 | 50.3 | 48.9 | 52.6 | 20.62 | 0.0756 | 0.35 | 13.32 | 0
May | 14 | 6AM to 7AM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
May | 14 | 7AM to 8AM | 61 | 53.6 | 48 | 50.8 | 22.53 | 0.0743 | 0.34 | 13.55 | 0
May | 14 | 8AM to 9AM | 62.1 | 53.5 | 46.9 | 48.8 | 22.48 | 0.0742 | 0.32 | 13.57 | 0
May | 14 | 9AM to 10AM | 64 | 53.4 | 45 | 45.2 | 22.4 | 0.0739 | 0.3 | 13.61 | 0
May | 14 | 10AM to 11AM | 66 | 53.4 | 43 | 41.9 | 22.37 | 0.0737 | 0.28 | 13.65 | 0
May | 14 | 11AM to 12PM | 66 | 54.2 | 45 | 45.2 | 22.89 | 0.0737 | 0.3 | 13.66 | 0
May | 14 | 12PM to 1PM | 66.9 | 55.5 | 46.9 | 48.8 | 23.66 | 0.0735 | 0.32 | 13.7 | 0
May | 14 | 1PM to 2PM | 69.1 | 55.9 | 46 | 47.1 | 23.93 | 0.0732 | 0.31 | 13.75 | 0
May | 14 | 2PM to 3PM | 69.1 | 55 | 44.1 | 43.6 | 23.39 | 0.0732 | 0.29 | 13.74 | 0
May | 14 | 3PM to 4PM | 70 | 55.8 | 45 | 45.2 | 23.85 | 0.0731 | 0.3 | 13.77 | 0
May | 14 | 4PM to 5PM | 70 | 56.3 | 46 | 47.1 | 24.15 | 0.0731 | 0.31 | 13.77 | 0
May | 14 | 5PM to 6PM | 68 | 54.6 | 44.1 | 43.6 | 23.13 | 0.0734 | 0.29 | 13.71 | 0
May | 14 | 6PM to 7PM | 66 | 53.8 | 44.1 | 43.6 | 22.65 | 0.0737 | 0.29 | 13.66 | 0
May | 14 | 7PM to 8PM | 63 | 54.8 | 48.9 | 52.6 | 23.29 | 0.074 | 0.35 | 13.61 | 0
May | 14 | 8PM to 9PM | 59 | 53.2 | 48.9 | 52.6 | 22.33 | 0.0746 | 0.35 | 13.5 | 0
May | 14 | 9PM to 10PM | 57 | 53 | 50 | 54.7 | 22.18 | 0.0749 | 0.36 | 13.46 | 0
May | 14 | 10PM to 11PM | 57.9 | 52.3 | 48 | 50.8 | 21.79 | 0.0748 | 0.34 | 13.47 | 0
May | 14 | 11PM to 12AM | 57 | 51.4 | 46.9 | 48.8 | 21.25 | 0.0749 | 0.32 | 13.44 | 0
May | 15 | 12AM to 1AM | 60.1 | 52.3 | 46 | 47.1 | 21.74 | 0.0745 | 0.31 | 13.51 | 0
May | 15 | 1AM to 2AM | 54 | 50.1 | 46.9 | 48.8 | 20.51 | 0.0754 | 0.32 | 13.36 | 0
May | 15 | 2AM to 3AM | 57 | 51.4 | 46.9 | 48.8 | 21.25 | 0.0749 | 0.32 | 13.44 | 0
May | 15 | 3AM to 4AM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
May | 15 | 4AM to 5AM | 57.9 | 51.8 | 46.9 | 48.8 | 21.47 | 0.0748 | 0.32 | 13.46 | 0
May | 15 | 5AM to 6AM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
May | 15 | 6AM to 7AM | 60.1 | 54.8 | 51.1 | 57 | 23.28 | 0.0744 | 0.38 | 13.54 | 0
May | 15 | 7AM to 8AM | 64.9 | 58.2 | 54 | 63.5 | 25.47 | 0.0737 | 0.42 | 13.69 | 0
May | 15 | 8AM to 9AM | 68 | 57.3 | 50 | 54.7 | 24.86 | 0.0733 | 0.36 | 13.74 | 0
May | 15 | 9AM to 10AM | 72 | 59.3 | 51.1 | 57 | 26.18 | 0.0728 | 0.38 | 13.85 | 0
May | 15 | 10AM to 11AM | 75 | 60.4 | 51.1 | 57 | 26.92 | 0.0724 | 0.38 | 13.93 | 0
May | 15 | 11AM to 12PM | 77 | 59.3 | 46.9 | 48.8 | 26.11 | 0.0721 | 0.32 | 13.96 | 0
May | 15 | 12PM to 1PM | 78.1 | 59.7 | 46.9 | 48.8 | 26.37 | 0.072 | 0.32 | 13.99 | 0
May | 15 | 1PM to 2PM | 78.1 | 58.9 | 45 | 45.2 | 25.81 | 0.072 | 0.3 | 13.98 | 0
May | 15 | 2PM to 3PM | 79 | 60 | 46.9 | 48.8 | 26.59 | 0.0719 | 0.32 | 14.01 | 0
May | 15 | 3PM to 4PM | 77 | 58.9 | 46 | 47.1 | 25.85 | 0.0721 | 0.31 | 13.95 | 0
May | 15 | 4PM to 5PM | 75.9 | 59.4 | 48 | 50.8 | 26.17 | 0.0723 | 0.34 | 13.94 | 0
May | 15 | 5PM to 6PM | 73.9 | 59.5 | 50 | 54.7 | 26.3 | 0.0725 | 0.36 | 13.9 | 0
May | 15 | 6PM to 7PM | 72 | 59.3 | 51.1 | 57 | 26.18 | 0.0728 | 0.38 | 13.85 | 0
May | 15 | 7PM to 8PM | 71.1 | 58.5 | 50 | 54.7 | 25.6 | 0.0729 | 0.36 | 13.82 | 0
May | 15 | 8PM to 9PM | 69.1 | 57.7 | 50 | 54.7 | 25.12 | 0.0732 | 0.36 | 13.77 | 0
May | 15 | 9PM to 10PM | 69.1 | 58.7 | 52 | 59 | 25.78 | 0.0732 | 0.39 | 13.79 | 0
May | 15 | 10PM to 11PM | 68 | 58.3 | 52 | 59 | 25.52 | 0.0733 | 0.39 | 13.76 | 0
May | 15 | 11PM to 12AM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
May | 16 | 12AM to 1AM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
May | 16 | 1AM to 2AM | 64 | 59.6 | 57 | 71.1 | 26.43 | 0.0738 | 0.47 | 13.69 | 0
May | 16 | 2AM to 3AM | 62.1 | 57.8 | 55 | 66.1 | 25.17 | 0.0741 | 0.44 | 13.62 | 0
May | 16 | 3AM to 4AM | 63 | 57.5 | 54 | 63.5 | 24.99 | 0.074 | 0.42 | 13.64 | 0
May | 16 | 4AM to 5AM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
May | 16 | 5AM to 6AM | 66 | 58.1 | 53.1 | 61.4 | 25.41 | 0.0736 | 0.41 | 13.71 | 0
May | 16 | 6AM to 7AM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
May | 16 | 7AM to 8AM | 68 | 59.4 | 54 | 63.5 | 26.22 | 0.0733 | 0.42 | 13.77 | 0
May | 16 | 8AM to 9AM | 64 | 60.2 | 57.9 | 73.5 | 26.8 | 0.0738 | 0.48 | 13.7 | 0
May | 16 | 9AM to 10AM | 63 | 60.4 | 59 | 76.4 | 27 | 0.0739 | 0.5 | 13.68 | 0
May | 16 | 10AM to 11AM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
May | 16 | 11AM to 12PM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
May | 16 | 12PM to 1PM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
May | 16 | 1PM to 2PM | 68 | 64.1 | 62.1 | 85.4 | 29.63 | 0.0731 | 0.56 | 13.84 | 0
May | 16 | 2PM to 3PM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
May | 16 | 3PM to 4PM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
May | 16 | 4PM to 5PM | 66.9 | 62.5 | 60.1 | 79.5 | 28.45 | 0.0733 | 0.52 | 13.79 | 0
May | 16 | 5PM to 6PM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
May | 16 | 6PM to 7PM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
May | 16 | 7PM to 8PM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
May | 16 | 8PM to 9PM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
May | 16 | 9PM to 10PM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
May | 16 | 10PM to 11PM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
May | 16 | 11PM to 12AM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
May | 17 | 12AM to 1AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
May | 17 | 1AM to 2AM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
May | 17 | 2AM to 3AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
May | 17 | 3AM to 4AM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
May | 17 | 4AM to 5AM | 63 | 60.4 | 59 | 76.4 | 27 | 0.0739 | 0.5 | 13.68 | 0
May | 17 | 5AM to 6AM | 62.1 | 60.1 | 59 | 76.4 | 26.78 | 0.074 | 0.5 | 13.66 | 0
May | 17 | 6AM to 7AM | 57.9 | 56.2 | 55 | 66.1 | 24.16 | 0.0747 | 0.44 | 13.52 | 0
May | 17 | 7AM to 8AM | 53.6 | 50.6 | 48.2 | 51.1 | 20.79 | 0.0754 | 0.34 | 13.36 | 0
May | 17 | 8AM to 9AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
May | 17 | 9AM to 10AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
May | 17 | 10AM to 11AM | 48 | 46.4 | 45 | 45.2 | 18.51 | 0.0763 | 0.3 | 13.19 | 1
May | 17 | 11AM to 12PM | 48 | 46.4 | 45 | 45.2 | 18.51 | 0.0763 | 0.3 | 13.19 | 1
May | 17 | 12PM to 1PM | 46 | 44.5 | 43 | 41.9 | 17.52 | 0.0766 | 0.28 | 13.13 | 1
May | 17 | 1PM to 2PM | 48.2 | 46.3 | 44.6 | 44.6 | 18.46 | 0.0763 | 0.3 | 13.2 | 1
May | 17 | 2PM to 3PM | 48 | 45.4 | 43 | 41.9 | 18 | 0.0763 | 0.28 | 13.19 | 1
May | 17 | 3PM to 4PM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
May | 17 | 4PM to 5PM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
May | 17 | 5PM to 6PM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
May | 17 | 6PM to 7PM | 45 | 43.5 | 42.1 | 40.4 | 17.04 | 0.0768 | 0.27 | 13.1 | 1
May | 17 | 7PM to 8PM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
May | 17 | 8PM to 9PM | 44.1 | 41.6 | 39 | 35.9 | 16.11 | 0.0769 | 0.24 | 13.06 | 1
May | 17 | 9PM to 10PM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
May | 17 | 10PM to 11PM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
May | 17 | 11PM to 12AM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
May | 18 | 12AM to 1AM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
May | 18 | 1AM to 2AM | 41 | 40.1 | 39 | 35.9 | 15.37 | 0.0774 | 0.24 | 12.98 | 1
May | 18 | 2AM to 3AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
May | 18 | 3AM to 4AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
May | 18 | 4AM to 5AM | 39 | 38.5 | 37.9 | 34.4 | 14.66 | 0.0777 | 0.23 | 12.93 | 1
May | 18 | 5AM to 6AM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
May | 18 | 6AM to 7AM | 46 | 44 | 42.1 | 40.4 | 17.3 | 0.0766 | 0.27 | 13.13 | 1
May | 18 | 7AM to 8AM | 48.9 | 43.6 | 37.9 | 34.4 | 17.06 | 0.0762 | 0.23 | 13.19 | 1
May | 18 | 8AM to 9AM | 51.1 | 43.8 | 36 | 31.8 | 17.18 | 0.0759 | 0.21 | 13.23 | 1
May | 18 | 9AM to 10AM | 53.1 | 45.6 | 37.9 | 34.4 | 18.06 | 0.0756 | 0.23 | 13.29 | 0
May | 18 | 10AM to 11AM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
May | 18 | 11AM to 12PM | 57.9 | 47.8 | 37.9 | 34.4 | 19.24 | 0.0749 | 0.23 | 13.42 | 0
May | 18 | 12PM to 1PM | 59 | 48.3 | 37.9 | 34.4 | 19.5 | 0.0747 | 0.23 | 13.45 | 0
May | 18 | 1PM to 2PM | 60.1 | 48.8 | 37.9 | 34.4 | 19.76 | 0.0746 | 0.23 | 13.48 | 0
May | 18 | 2PM to 3PM | 61 | 48.9 | 37 | 33.2 | 19.79 | 0.0745 | 0.22 | 13.49 | 0
May | 18 | 3PM to 4PM | 62.1 | 49.7 | 37.9 | 34.4 | 20.24 | 0.0743 | 0.23 | 13.53 | 0
May | 18 | 4PM to 5PM | 61 | 48.9 | 37 | 33.2 | 19.79 | 0.0745 | 0.22 | 13.49 | 0
May | 18 | 5PM to 6PM | 60.1 | 47.4 | 34 | 29.3 | 18.98 | 0.0746 | 0.2 | 13.46 | 0
May | 18 | 6PM to 7PM | 57 | 45.9 | 34 | 29.3 | 18.24 | 0.075 | 0.2 | 13.38 | 0
May | 18 | 7PM to 8PM | 55.9 | 45.8 | 35.1 | 30.6 | 18.18 | 0.0752 | 0.2 | 13.36 | 0
May | 18 | 8PM to 9PM | 52 | 45.5 | 39 | 35.9 | 18.03 | 0.0757 | 0.24 | 13.27 | 0
May | 18 | 9PM to 10PM | 50 | 44.9 | 39.9 | 37.2 | 17.75 | 0.076 | 0.25 | 13.22 | 1
May | 18 | 10PM to 11PM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
May | 18 | 11PM to 12AM | 48 | 43.6 | 39 | 35.9 | 17.07 | 0.0763 | 0.24 | 13.17 | 1
May | 19 | 12AM to 1AM | 46.9 | 43.1 | 39 | 35.9 | 16.81 | 0.0765 | 0.24 | 13.14 | 1
May | 19 | 1AM to 2AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
May | 19 | 2AM to 3AM | 48.9 | 43.6 | 37.9 | 34.4 | 17.06 | 0.0762 | 0.23 | 13.19 | 1
May | 19 | 3AM to 4AM | 46.9 | 43.1 | 39 | 35.9 | 16.81 | 0.0765 | 0.24 | 13.14 | 1
May | 19 | 4AM to 5AM | 46.9 | 43.1 | 39 | 35.9 | 16.81 | 0.0765 | 0.24 | 13.14 | 1
May | 19 | 5AM to 6AM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
May | 19 | 6AM to 7AM | 51.1 | 45.9 | 41 | 38.8 | 18.26 | 0.0759 | 0.26 | 13.26 | 1
May | 19 | 7AM to 8AM | 57 | 49.1 | 42.1 | 40.4 | 19.96 | 0.075 | 0.27 | 13.41 | 0
May | 19 | 8AM to 9AM | 61 | 51.3 | 43 | 41.9 | 21.14 | 0.0744 | 0.28 | 13.52 | 0
May | 19 | 9AM to 10AM | 64 | 51.3 | 39.9 | 37.2 | 21.15 | 0.074 | 0.25 | 13.59 | 0
May | 19 | 10AM to 11AM | 64.9 | 49.2 | 33.1 | 28.3 | 19.99 | 0.0739 | 0.19 | 13.58 | 0
May | 19 | 11AM to 12PM | 63 | 48.7 | 34 | 29.3 | 19.68 | 0.0742 | 0.2 | 13.53 | 0
May | 19 | 12PM to 1PM | 64.9 | 50.2 | 36 | 31.8 | 20.53 | 0.0739 | 0.21 | 13.59 | 0
May | 19 | 1PM to 2PM | 64.9 | 49.5 | 34 | 29.3 | 20.16 | 0.0739 | 0.2 | 13.59 | 0
May | 19 | 2PM to 3PM | 66 | 50.4 | 35.1 | 30.6 | 20.62 | 0.0738 | 0.2 | 13.62 | 0
May | 19 | 3PM to 4PM | 64.9 | 49.5 | 34 | 29.3 | 20.16 | 0.0739 | 0.2 | 13.59 | 0
May | 19 | 4PM to 5PM | 64.9 | 49.2 | 33.1 | 28.3 | 19.99 | 0.0739 | 0.19 | 13.58 | 0
May | 19 | 5PM to 6PM | 63 | 48 | 32 | 27.1 | 19.33 | 0.0742 | 0.18 | 13.53 | 0
May | 19 | 6PM to 7PM | 62.1 | 48 | 33.1 | 28.3 | 19.3 | 0.0743 | 0.19 | 13.51 | 0
May | 19 | 7PM to 8PM | 60.1 | 47.1 | 33.1 | 28.3 | 18.82 | 0.0746 | 0.19 | 13.46 | 0
May | 19 | 8PM to 9PM | 57.9 | 46.4 | 34 | 29.3 | 18.46 | 0.0749 | 0.2 | 13.4 | 0
May | 19 | 9PM to 10PM | 55 | 45.7 | 36 | 31.8 | 18.14 | 0.0753 | 0.21 | 13.34 | 0
May | 19 | 10PM to 11PM | 52 | 45.5 | 39 | 35.9 | 18.03 | 0.0757 | 0.24 | 13.27 | 0
May | 19 | 11PM to 12AM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
May | 20 | 12AM to 1AM | 46 | 43.5 | 41 | 38.8 | 17.04 | 0.0766 | 0.26 | 13.12 | 1
May | 20 | 1AM to 2AM | 45 | 42.5 | 39.9 | 37.2 | 16.53 | 0.0768 | 0.25 | 13.09 | 1
May | 20 | 2AM to 3AM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
May | 20 | 3AM to 4AM | 46 | 43 | 39.9 | 37.2 | 16.79 | 0.0766 | 0.25 | 13.12 | 1
May | 20 | 4AM to 5AM | 46 | 44 | 42.1 | 40.4 | 17.3 | 0.0766 | 0.27 | 13.13 | 1
May | 20 | 5AM to 6AM | 48 | 45 | 42.1 | 40.4 | 17.78 | 0.0763 | 0.27 | 13.18 | 1
May | 20 | 6AM to 7AM | 55 | 47.3 | 39.9 | 37.2 | 18.97 | 0.0753 | 0.25 | 13.35 | 0
May | 20 | 7AM to 8AM | 59 | 48.3 | 37.9 | 34.4 | 19.5 | 0.0747 | 0.23 | 13.45 | 0
May | 20 | 8AM to 9AM | 60.1 | 51.3 | 44.1 | 43.6 | 21.2 | 0.0745 | 0.29 | 13.5 | 0
May | 20 | 9AM to 10AM | 61 | 50.4 | 41 | 38.8 | 20.66 | 0.0744 | 0.26 | 13.51 | 0
May | 20 | 10AM to 11AM | 63 | 49 | 35.1 | 30.6 | 19.88 | 0.0742 | 0.2 | 13.54 | 0
May | 20 | 11AM to 12PM | 63 | 50.5 | 39 | 35.9 | 20.69 | 0.0742 | 0.24 | 13.55 | 0
May | 20 | 12PM to 1PM | 62.1 | 49.7 | 37.9 | 34.4 | 20.24 | 0.0743 | 0.23 | 13.53 | 0
May | 20 | 1PM to 2PM | 60.1 | 49.2 | 39 | 35.9 | 19.99 | 0.0746 | 0.24 | 13.48 | 0
May | 20 | 2PM to 3PM | 61 | 49.2 | 37.9 | 34.4 | 19.98 | 0.0744 | 0.23 | 13.5 | 0
May | 20 | 3PM to 4PM | 60.1 | 49.2 | 39 | 35.9 | 19.99 | 0.0746 | 0.24 | 13.48 | 0
May | 20 | 4PM to 5PM | 60.1 | 48.1 | 36 | 31.8 | 19.36 | 0.0746 | 0.21 | 13.47 | 0
May | 20 | 5PM to 6PM | 57.9 | 47.8 | 37.9 | 34.4 | 19.24 | 0.0749 | 0.23 | 13.42 | 0
May | 20 | 6PM to 7PM | 57 | 47.1 | 37 | 33.2 | 18.83 | 0.075 | 0.22 | 13.39 | 0
May | 20 | 7PM to 8PM | 55 | 46.1 | 37 | 33.2 | 18.35 | 0.0753 | 0.22 | 13.34 | 0
May | 20 | 8PM to 9PM | 53.1 | 45.2 | 37 | 33.2 | 17.87 | 0.0756 | 0.22 | 13.29 | 0
May | 20 | 9PM to 10PM | 51.1 | 44.3 | 37 | 33.2 | 17.39 | 0.0759 | 0.22 | 13.24 | 1
May | 20 | 10PM to 11PM | 48.9 | 43.2 | 37 | 33.2 | 16.87 | 0.0762 | 0.22 | 13.18 | 1
May | 20 | 11PM to 12AM | 48 | 42.3 | 36 | 31.8 | 16.44 | 0.0764 | 0.21 | 13.15 | 1
May | 21 | 12AM to 1AM | 46 | 41.8 | 37 | 33.2 | 16.17 | 0.0767 | 0.22 | 13.11 | 1
May | 21 | 1AM to 2AM | 46 | 41.3 | 36 | 31.8 | 15.96 | 0.0767 | 0.21 | 13.1 | 1
May | 21 | 2AM to 3AM | 45 | 40.4 | 35.1 | 30.6 | 15.52 | 0.0768 | 0.2 | 13.07 | 1
May | 21 | 3AM to 4AM | 43 | 39.4 | 35.1 | 30.6 | 15.04 | 0.0771 | 0.2 | 13.02 | 1
May | 21 | 4AM to 5AM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
May | 21 | 5AM to 6AM | 46 | 41.3 | 36 | 31.8 | 15.96 | 0.0767 | 0.21 | 13.1 | 1
May | 21 | 6AM to 7AM | 48.9 | 40.8 | 30.9 | 25.8 | 15.73 | 0.0763 | 0.17 | 13.16 | 1
May | 21 | 7AM to 8AM | 51.1 | 40.2 | 26.1 | 20.5 | 15.44 | 0.076 | 0.14 | 13.2 | 1
May | 21 | 8AM to 9AM | 53.1 | 42.2 | 28.9 | 23.5 | 16.38 | 0.0757 | 0.16 | 13.26 | 0
May | 21 | 9AM to 10AM | 54 | 43.4 | 30.9 | 25.8 | 16.95 | 0.0755 | 0.17 | 13.29 | 0
May | 21 | 10AM to 11AM | 55 | 44.3 | 32 | 27.1 | 17.41 | 0.0754 | 0.18 | 13.32 | 0
May | 21 | 11AM to 12PM | 57 | 45.9 | 34 | 29.3 | 18.24 | 0.075 | 0.2 | 13.38 | 0
May | 21 | 12PM to 1PM | 57.9 | 46 | 33.1 | 28.3 | 18.3 | 0.0749 | 0.19 | 13.4 | 0
May | 21 | 1PM to 2PM | 59 | 46.2 | 32 | 27.1 | 18.37 | 0.0748 | 0.18 | 13.42 | 0
May | 21 | 2PM to 3PM | 60.1 | 47.1 | 33.1 | 28.3 | 18.82 | 0.0746 | 0.19 | 13.46 | 0
May | 21 | 3PM to 4PM | 61 | 48.1 | 35.1 | 30.6 | 19.4 | 0.0745 | 0.2 | 13.49 | 0
May | 21 | 4PM to 5PM | 61 | 47.8 | 34 | 29.3 | 19.2 | 0.0745 | 0.2 | 13.48 | 0
May | 21 | 5PM to 6PM | 60.1 | 48.1 | 36 | 31.8 | 19.36 | 0.0746 | 0.21 | 13.47 | 0
May | 21 | 6PM to 7PM | 57.9 | 47.5 | 37 | 33.2 | 19.05 | 0.0749 | 0.22 | 13.42 | 0
May | 21 | 7PM to 8PM | 55.9 | 46.1 | 36 | 31.8 | 18.35 | 0.0752 | 0.21 | 13.36 | 0
May | 21 | 8PM to 9PM | 54 | 45.6 | 37 | 33.2 | 18.09 | 0.0755 | 0.22 | 13.31 | 0
May | 21 | 9PM to 10PM | 53.1 | 45.6 | 37.9 | 34.4 | 18.06 | 0.0756 | 0.23 | 13.29 | 0
May | 21 | 10PM to 11PM | 53.1 | 45.2 | 37 | 33.2 | 17.87 | 0.0756 | 0.22 | 13.29 | 0
May | 21 | 11PM to 12AM | 52 | 45.1 | 37.9 | 34.4 | 17.8 | 0.0758 | 0.23 | 13.27 | 0
May | 22 | 12AM to 1AM | 52 | 44.7 | 37 | 33.2 | 17.61 | 0.0758 | 0.22 | 13.26 | 0
May | 22 | 1AM to 2AM | 51.1 | 44.6 | 37.9 | 34.4 | 17.58 | 0.0759 | 0.23 | 13.24 | 1
May | 22 | 2AM to 3AM | 48.9 | 43.6 | 37.9 | 34.4 | 17.06 | 0.0762 | 0.23 | 13.19 | 1
May | 22 | 3AM to 4AM | 50 | 43.7 | 37 | 33.2 | 17.13 | 0.0761 | 0.22 | 13.21 | 1
May | 22 | 4AM to 5AM | 50 | 44.1 | 37.9 | 34.4 | 17.32 | 0.076 | 0.23 | 13.21 | 1
May | 22 | 5AM to 6AM | 51.1 | 45.1 | 39 | 35.9 | 17.81 | 0.0759 | 0.24 | 13.25 | 1
May | 22 | 6AM to 7AM | 55 | 47.3 | 39.9 | 37.2 | 18.97 | 0.0753 | 0.25 | 13.35 | 0
May | 22 | 7AM to 8AM | 57 | 48.7 | 41 | 38.8 | 19.7 | 0.075 | 0.26 | 13.41 | 0
May | 22 | 8AM to 9AM | 60.1 | 50.5 | 42.1 | 40.4 | 20.7 | 0.0745 | 0.27 | 13.49 | 0
May | 22 | 9AM to 10AM | 63 | 52.6 | 44.1 | 43.6 | 21.9 | 0.0741 | 0.29 | 13.58 | 0
May | 22 | 10AM to 11AM | 64.9 | 54.3 | 46 | 47.1 | 22.92 | 0.0738 | 0.31 | 13.64 | 0
May | 22 | 11AM to 12PM | 66.9 | 55.5 | 46.9 | 48.8 | 23.66 | 0.0735 | 0.32 | 13.7 | 0
May | 22 | 12PM to 1PM | 69.1 | 56.8 | 48 | 50.8 | 24.5 | 0.0732 | 0.34 | 13.76 | 0
May | 22 | 1PM to 2PM | 70 | 57.1 | 48 | 50.8 | 24.72 | 0.0731 | 0.34 | 13.78 | 0
May | 22 | 2PM to 3PM | 71.1 | 58 | 48.9 | 52.6 | 25.26 | 0.0729 | 0.35 | 13.82 | 0
May | 22 | 3PM to 4PM | 70 | 57.1 | 48 | 50.8 | 24.72 | 0.0731 | 0.34 | 13.78 | 0
May | 22 | 4PM to 5PM | 71.1 | 57.6 | 48 | 50.8 | 24.98 | 0.0729 | 0.34 | 13.81 | 0
May | 22 | 5PM to 6PM | 70 | 57.1 | 48 | 50.8 | 24.72 | 0.0731 | 0.34 | 13.78 | 0
May | 22 | 6PM to 7PM | 66.9 | 55.1 | 46 | 47.1 | 23.4 | 0.0735 | 0.31 | 13.69 | 0
May | 22 | 7PM to 8PM | 66 | 54.2 | 45 | 45.2 | 22.89 | 0.0737 | 0.3 | 13.66 | 0
May | 22 | 8PM to 9PM | 64 | 52.5 | 43 | 41.9 | 21.89 | 0.074 | 0.28 | 13.6 | 0
May | 22 | 9PM to 10PM | 63 | 52.1 | 43 | 41.9 | 21.63 | 0.0741 | 0.28 | 13.57 | 0
May | 22 | 10PM to 11PM | 62.1 | 51.7 | 43 | 41.9 | 21.41 | 0.0742 | 0.28 | 13.55 | 0
May | 22 | 11PM to 12AM | 60.1 | 50.9 | 43 | 41.9 | 20.93 | 0.0745 | 0.28 | 13.5 | 0
May | 23 | 12AM to 1AM | 59 | 50.4 | 43 | 41.9 | 20.66 | 0.0747 | 0.28 | 13.47 | 0
May | 23 | 1AM to 2AM | 59 | 50.4 | 43 | 41.9 | 20.66 | 0.0747 | 0.28 | 13.47 | 0
May | 23 | 2AM to 3AM | 59 | 50.9 | 44.1 | 43.6 | 20.94 | 0.0747 | 0.29 | 13.48 | 0
May | 23 | 3AM to 4AM | 59 | 50.9 | 44.1 | 43.6 | 20.94 | 0.0747 | 0.29 | 13.48 | 0
May | 23 | 4AM to 5AM | 57.9 | 50.8 | 45 | 45.2 | 20.92 | 0.0748 | 0.3 | 13.45 | 0
May | 23 | 5AM to 6AM | 59 | 51.3 | 45 | 45.2 | 21.18 | 0.0747 | 0.3 | 13.48 | 0
May | 23 | 6AM to 7AM | 62.1 | 53.5 | 46.9 | 48.8 | 22.48 | 0.0742 | 0.32 | 13.57 | 0
May | 23 | 7AM to 8AM | 66 | 55.6 | 48 | 50.8 | 23.76 | 0.0736 | 0.34 | 13.68 | 0
May | 23 | 8AM to 9AM | 69.1 | 57.2 | 48.9 | 52.6 | 24.78 | 0.0732 | 0.35 | 13.77 | 0
May | 23 | 9AM to 10AM | 73.9 | 61.5 | 54 | 63.5 | 27.67 | 0.0725 | 0.42 | 13.93 | 0
May | 23 | 10AM to 11AM | 77 | 63.1 | 55 | 66.1 | 28.82 | 0.072 | 0.44 | 14.01 | 0
May | 23 | 11AM to 12PM | 78.1 | 63.9 | 55.9 | 68.3 | 29.43 | 0.0719 | 0.45 | 14.05 | 0
May | 23 | 12PM to 1PM | 80.1 | 64.6 | 55.9 | 68.3 | 29.92 | 0.0716 | 0.45 | 14.1 | 0
May | 23 | 1PM to 2PM | 82 | 65.8 | 57 | 71.1 | 30.84 | 0.0713 | 0.47 | 14.16 | 0
May | 23 | 2PM to 3PM | 80.1 | 65.1 | 57 | 71.1 | 30.35 | 0.0716 | 0.47 | 14.11 | 0
May | 23 | 3PM to 4PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
May | 23 | 4PM to 5PM | 79 | 65.3 | 57.9 | 73.5 | 30.46 | 0.0717 | 0.48 | 14.09 | 0
May | 23 | 5PM to 6PM | 78.1 | 65.6 | 59 | 76.4 | 30.7 | 0.0718 | 0.5 | 14.08 | 0
May | 23 | 6PM to 7PM | 75.9 | 65.5 | 60.1 | 79.5 | 30.65 | 0.0721 | 0.52 | 14.03 | 0
May | 23 | 7PM to 8PM | 75 | 65.7 | 61 | 82.1 | 30.84 | 0.0722 | 0.54 | 14.01 | 0
May | 23 | 8PM to 9PM | 73 | 64.5 | 60.1 | 79.5 | 29.95 | 0.0725 | 0.52 | 13.95 | 0
May | 23 | 9PM to 10PM | 73 | 64.5 | 60.1 | 79.5 | 29.95 | 0.0725 | 0.52 | 13.95 | 0
May | 23 | 10PM to 11PM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
May | 23 | 11PM to 12AM | 72 | 64.7 | 61 | 82.1 | 30.09 | 0.0726 | 0.54 | 13.93 | 0
May | 24 | 12AM to 1AM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
May | 24 | 1AM to 2AM | 66.9 | 65 | 64 | 91.7 | 30.34 | 0.0733 | 0.6 | 13.83 | 0
May | 24 | 2AM to 3AM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
May | 24 | 3AM to 4AM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
May | 24 | 4AM to 5AM | 66.2 | 63.8 | 62.6 | 87 | 29.45 | 0.0734 | 0.57 | 13.8 | 0
May | 24 | 5AM to 6AM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
May | 24 | 6AM to 7AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
May | 24 | 7AM to 8AM | 68 | 64.6 | 63 | 88.2 | 30.07 | 0.0731 | 0.58 | 13.85 | 0
May | 24 | 8AM to 9AM | 66.2 | 65 | 64.4 | 92.8 | 30.35 | 0.0733 | 0.61 | 13.82 | 0
May | 24 | 9AM to 10AM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
May | 24 | 10AM to 11AM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
May | 24 | 11AM to 12PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
May | 24 | 12PM to 1PM | 68 | 65.6 | 64.4 | 92.8 | 30.79 | 0.0731 | 0.61 | 13.86 | 0
May | 24 | 1PM to 2PM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
May | 24 | 2PM to 3PM | 70 | 67.3 | 66 | 98.4 | 32.14 | 0.0728 | 0.64 | 13.93 | 0
May | 24 | 3PM to 4PM | 68 | 66.6 | 66 | 98.4 | 31.65 | 0.0731 | 0.64 | 13.88 | 0
May | 24 | 4PM to 5PM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
May | 24 | 5PM to 6PM | 68 | 65.3 | 64 | 91.7 | 30.61 | 0.0731 | 0.6 | 13.86 | 0
May | 24 | 6PM to 7PM | 66.9 | 65 | 64 | 91.7 | 30.34 | 0.0733 | 0.6 | 13.83 | 0
May | 24 | 7PM to 8PM | 66 | 64.7 | 64 | 91.7 | 30.12 | 0.0734 | 0.6 | 13.81 | 0
May | 24 | 8PM to 9PM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
May | 24 | 9PM to 10PM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
May | 24 | 10PM to 11PM | 64.9 | 63.6 | 63 | 88.2 | 29.32 | 0.0735 | 0.58 | 13.77 | 0
May | 24 | 11PM to 12AM | 64 | 62.7 | 62.1 | 85.4 | 28.66 | 0.0737 | 0.56 | 13.74 | 0
May | 25 | 12AM to 1AM | 64.4 | 63.2 | 62.6 | 87 | 29.01 | 0.0736 | 0.57 | 13.75 | 0
May | 25 | 1AM to 2AM | 64.9 | 63.6 | 63 | 88.2 | 29.32 | 0.0735 | 0.58 | 13.77 | 0
May | 25 | 2AM to 3AM | 64.9 | 63.6 | 63 | 88.2 | 29.32 | 0.0735 | 0.58 | 13.77 | 0
May | 25 | 3AM to 4AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
May | 25 | 4AM to 5AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
May | 25 | 5AM to 6AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
May | 25 | 6AM to 7AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
May | 25 | 7AM to 8AM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
May | 25 | 8AM to 9AM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
May | 25 | 9AM to 10AM | 70 | 65.3 | 63 | 88.2 | 30.55 | 0.0728 | 0.58 | 13.9 | 0
May | 25 | 10AM to 11AM | 66.9 | 61.8 | 59 | 76.4 | 27.97 | 0.0733 | 0.5 | 13.78 | 0
May | 25 | 11AM to 12PM | 69.1 | 61.9 | 57.9 | 73.5 | 28.04 | 0.0731 | 0.48 | 13.83 | 0
May | 25 | 12PM to 1PM | 70 | 62.3 | 57.9 | 73.5 | 28.26 | 0.0729 | 0.48 | 13.85 | 0
May | 25 | 1PM to 2PM | 69.1 | 60.3 | 55 | 66.1 | 26.89 | 0.0731 | 0.44 | 13.81 | 0
May | 25 | 2PM to 3PM | 69.1 | 60.8 | 55.9 | 68.3 | 27.23 | 0.0731 | 0.45 | 13.81 | 0
May | 25 | 3PM to 4PM | 68 | 59.9 | 55 | 66.1 | 26.62 | 0.0733 | 0.44 | 13.78 | 0
May | 25 | 4PM to 5PM | 68 | 59.4 | 54 | 63.5 | 26.22 | 0.0733 | 0.42 | 13.77 | 0
May | 25 | 5PM to 6PM | 66 | 58.6 | 54 | 63.5 | 25.74 | 0.0735 | 0.42 | 13.72 | 0
May | 25 | 6PM to 7PM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
May | 25 | 7PM to 8PM | 62.1 | 57.1 | 54 | 63.5 | 24.77 | 0.0741 | 0.42 | 13.62 | 0
May | 25 | 8PM to 9PM | 60.1 | 55.3 | 52 | 59 | 23.59 | 0.0744 | 0.39 | 13.55 | 0
May | 25 | 9PM to 10PM | 57.9 | 54.4 | 52 | 59 | 23.06 | 0.0747 | 0.39 | 13.49 | 0
May | 25 | 10PM to 11PM | 57 | 53.6 | 51.1 | 57 | 22.54 | 0.0749 | 0.38 | 13.46 | 0
May | 25 | 11PM to 12AM | 57 | 53.6 | 51.1 | 57 | 22.54 | 0.0749 | 0.38 | 13.46 | 0
May | 26 | 12AM to 1AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
May | 26 | 1AM to 2AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
May | 26 | 2AM to 3AM | 53.1 | 51.3 | 50 | 54.7 | 21.22 | 0.0755 | 0.36 | 13.35 | 0
May | 26 | 3AM to 4AM | 52 | 50.3 | 48.9 | 52.6 | 20.62 | 0.0756 | 0.35 | 13.32 | 0
May | 26 | 4AM to 5AM | 53.1 | 50.7 | 48.9 | 52.6 | 20.88 | 0.0755 | 0.35 | 13.35 | 0
May | 26 | 5AM to 6AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
May | 26 | 6AM to 7AM | 57.9 | 53.9 | 51.1 | 57 | 22.75 | 0.0747 | 0.38 | 13.49 | 0
May | 26 | 7AM to 8AM | 62.1 | 55 | 50 | 54.7 | 23.41 | 0.0742 | 0.36 | 13.59 | 0
May | 26 | 8AM to 9AM | 64 | 55.3 | 48.9 | 52.6 | 23.55 | 0.0739 | 0.35 | 13.63 | 0
May | 26 | 9AM to 10AM | 66 | 57.1 | 51.1 | 57 | 24.73 | 0.0736 | 0.38 | 13.7 | 0
May | 26 | 10AM to 11AM | 69.1 | 59.3 | 53.1 | 61.4 | 26.16 | 0.0731 | 0.41 | 13.79 | 0
May | 26 | 11AM to 12PM | 71.1 | 60 | 53.1 | 61.4 | 26.64 | 0.0729 | 0.41 | 13.84 | 0
May | 26 | 12PM to 1PM | 73 | 60.2 | 52 | 59 | 26.74 | 0.0726 | 0.39 | 13.89 | 0
May | 26 | 1PM to 2PM | 73.9 | 60.5 | 52 | 59 | 26.96 | 0.0725 | 0.39 | 13.91 | 0
May | 26 | 2PM to 3PM | 75.9 | 61.7 | 53.1 | 61.4 | 27.83 | 0.0722 | 0.41 | 13.97 | 0
May | 26 | 3PM to 4PM | 75.9 | 59.8 | 48.9 | 52.6 | 26.44 | 0.0723 | 0.35 | 13.94 | 0
May | 26 | 4PM to 5PM | 75.9 | 60.3 | 50 | 54.7 | 26.79 | 0.0722 | 0.36 | 13.95 | 0
May | 26 | 5PM to 6PM | 75 | 59.9 | 50 | 54.7 | 26.57 | 0.0724 | 0.36 | 13.93 | 0
May | 26 | 6PM to 7PM | 72 | 59.3 | 51.1 | 57 | 26.18 | 0.0728 | 0.38 | 13.85 | 0
May | 26 | 7PM to 8PM | 70 | 58.6 | 51.1 | 57 | 25.69 | 0.073 | 0.38 | 13.8 | 0
May | 26 | 8PM to 9PM | 69.1 | 58.3 | 51.1 | 57 | 25.47 | 0.0732 | 0.38 | 13.78 | 0
May | 26 | 9PM to 10PM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
May | 26 | 10PM to 11PM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
May | 26 | 11PM to 12AM | 66.9 | 59.6 | 55 | 66.1 | 26.36 | 0.0734 | 0.44 | 13.75 | 0
May | 27 | 12AM to 1AM | 66.9 | 60.1 | 55.9 | 68.3 | 26.71 | 0.0734 | 0.45 | 13.76 | 0
May | 27 | 1AM to 2AM | 63 | 59.2 | 57 | 71.1 | 26.17 | 0.0739 | 0.47 | 13.66 | 0
May | 27 | 2AM to 3AM | 60.1 | 58.2 | 57 | 71.1 | 25.47 | 0.0743 | 0.47 | 13.59 | 0
May | 27 | 3AM to 4AM | 61 | 58.5 | 57 | 71.1 | 25.69 | 0.0742 | 0.47 | 13.61 | 0
May | 27 | 4AM to 5AM | 64 | 60.8 | 59 | 76.4 | 27.26 | 0.0737 | 0.5 | 13.71 | 0
May | 27 | 5AM to 6AM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
May | 27 | 6AM to 7AM | 66.9 | 63.7 | 62.1 | 85.4 | 29.36 | 0.0733 | 0.56 | 13.81 | 0
May | 27 | 7AM to 8AM | 70 | 66 | 64 | 91.7 | 31.1 | 0.0728 | 0.6 | 13.91 | 0
May | 27 | 8AM to 9AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
May | 27 | 9AM to 10AM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
May | 27 | 10AM to 11AM | 78.1 | 69 | 64.9 | 94.6 | 33.56 | 0.0717 | 0.62 | 14.13 | 0
May | 27 | 11AM to 12PM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
May | 27 | 12PM to 1PM | 80.1 | 68.4 | 63 | 88.2 | 33.03 | 0.0715 | 0.58 | 14.16 | 0
May | 27 | 1PM to 2PM | 80.1 | 69.1 | 64 | 91.7 | 33.57 | 0.0715 | 0.6 | 14.18 | 0
May | 27 | 2PM to 3PM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
May | 27 | 3PM to 4PM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
May | 27 | 4PM to 5PM | 77 | 69.4 | 66 | 98.4 | 33.87 | 0.0718 | 0.64 | 14.12 | 0
May | 27 | 5PM to 6PM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
May | 27 | 6PM to 7PM | 77 | 70 | 66.9 | 101.5 | 34.37 | 0.0718 | 0.67 | 14.13 | 0
May | 27 | 7PM to 8PM | 75.9 | 68.4 | 64.9 | 94.6 | 33.02 | 0.072 | 0.62 | 14.08 | 0
May | 27 | 8PM to 9PM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
May | 27 | 9PM to 10PM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
May | 27 | 10PM to 11PM | 70 | 66 | 64 | 91.7 | 31.1 | 0.0728 | 0.6 | 13.91 | 0
May | 27 | 11PM to 12AM | 70 | 65.3 | 63 | 88.2 | 30.55 | 0.0728 | 0.58 | 13.9 | 0
May | 28 | 12AM to 1AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
May | 28 | 1AM to 2AM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
May | 28 | 2AM to 3AM | 64.9 | 63.6 | 63 | 88.2 | 29.32 | 0.0735 | 0.58 | 13.77 | 0
May | 28 | 3AM to 4AM | 64 | 62.7 | 62.1 | 85.4 | 28.66 | 0.0737 | 0.56 | 13.74 | 0
May | 28 | 4AM to 5AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
May | 28 | 5AM to 6AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
May | 28 | 6AM to 7AM | 70 | 65.3 | 63 | 88.2 | 30.55 | 0.0728 | 0.58 | 13.9 | 0
May | 28 | 7AM to 8AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
May | 28 | 8AM to 9AM | 75.9 | 69.7 | 66.9 | 101.5 | 34.1 | 0.072 | 0.67 | 14.1 | 0
May | 28 | 9AM to 10AM | 78.1 | 69.7 | 66 | 98.4 | 34.14 | 0.0717 | 0.64 | 14.14 | 0
May | 28 | 10AM to 11AM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
May | 28 | 11AM to 12PM | 78.1 | 69.7 | 66 | 98.4 | 34.14 | 0.0717 | 0.64 | 14.14 | 0
May | 28 | 12PM to 1PM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
May | 28 | 1PM to 2PM | 79 | 70 | 66 | 98.4 | 34.36 | 0.0716 | 0.64 | 14.17 | 0
May | 28 | 2PM to 3PM | 71.6 | 66.7 | 64.4 | 92.8 | 31.68 | 0.0726 | 0.61 | 13.96 | 0
May | 28 | 3PM to 4PM | 68 | 66.6 | 66 | 98.4 | 31.65 | 0.0731 | 0.64 | 13.88 | 0
May | 28 | 4PM to 5PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
May | 28 | 5PM to 6PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
May | 28 | 6PM to 7PM | 68 | 65.3 | 64 | 91.7 | 30.61 | 0.0731 | 0.6 | 13.86 | 0
May | 28 | 7PM to 8PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
May | 28 | 8PM to 9PM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
May | 28 | 9PM to 10PM | 66.2 | 65 | 64.4 | 92.8 | 30.35 | 0.0733 | 0.61 | 13.82 | 0
May | 28 | 10PM to 11PM | 66.9 | 65 | 64 | 91.7 | 30.34 | 0.0733 | 0.6 | 13.83 | 0
May | 28 | 11PM to 12AM | 66.9 | 65 | 64 | 91.7 | 30.34 | 0.0733 | 0.6 | 13.83 | 0
May | 29 | 12AM to 1AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
May | 29 | 1AM to 2AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
May | 29 | 2AM to 3AM | 66 | 64.7 | 64 | 91.7 | 30.12 | 0.0734 | 0.6 | 13.81 | 0
May | 29 | 3AM to 4AM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
May | 29 | 4AM to 5AM | 66.2 | 65 | 64.4 | 92.8 | 30.35 | 0.0733 | 0.61 | 13.82 | 0
May | 29 | 5AM to 6AM | 66 | 64.7 | 64 | 91.7 | 30.12 | 0.0734 | 0.6 | 13.81 | 0
May | 29 | 6AM to 7AM | 66.9 | 65 | 64 | 91.7 | 30.34 | 0.0733 | 0.6 | 13.83 | 0
May | 29 | 7AM to 8AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
May | 29 | 8AM to 9AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
May | 29 | 9AM to 10AM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
May | 29 | 10AM to 11AM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
May | 29 | 11AM to 12PM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
May | 29 | 12PM to 1PM | 75.9 | 69.1 | 66 | 98.4 | 33.6 | 0.072 | 0.64 | 14.09 | 0
May | 29 | 1PM to 2PM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
May | 29 | 2PM to 3PM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
May | 29 | 3PM to 4PM | 78.1 | 68.5 | 64 | 91.7 | 33.09 | 0.0717 | 0.6 | 14.12 | 0
May | 29 | 4PM to 5PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
May | 29 | 5PM to 6PM | 75.9 | 66.6 | 62.1 | 85.4 | 31.57 | 0.0721 | 0.56 | 14.05 | 0
May | 29 | 6PM to 7PM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
May | 29 | 7PM to 8PM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
May | 29 | 8PM to 9PM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
May | 29 | 9PM to 10PM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
May | 29 | 10PM to 11PM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
May | 29 | 11PM to 12AM | 68 | 64.6 | 63 | 88.2 | 30.07 | 0.0731 | 0.58 | 13.85 | 0
May | 30 | 12AM to 1AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
May | 30 | 1AM to 2AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
May | 30 | 2AM to 3AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
May | 30 | 3AM to 4AM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
May | 30 | 4AM to 5AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
May | 30 | 5AM to 6AM | 69.1 | 65.7 | 64 | 91.7 | 30.87 | 0.073 | 0.6 | 13.89 | 0
May | 30 | 6AM to 7AM | 71.1 | 67.6 | 66 | 98.4 | 32.41 | 0.0726 | 0.64 | 13.96 | 0
May | 30 | 7AM to 8AM | 75.9 | 69.7 | 66.9 | 101.5 | 34.1 | 0.072 | 0.67 | 14.1 | 0
May | 30 | 8AM to 9AM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
May | 30 | 9AM to 10AM | 79 | 68.1 | 63 | 88.2 | 32.76 | 0.0716 | 0.58 | 14.14 | 0
May | 30 | 10AM to 11AM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
May | 30 | 11AM to 12PM | 81 | 68.7 | 63 | 88.2 | 33.25 | 0.0714 | 0.58 | 14.19 | 0
May | 30 | 12PM to 1PM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
May | 30 | 1PM to 2PM | 79 | 70 | 66 | 98.4 | 34.36 | 0.0716 | 0.64 | 14.17 | 0
May | 30 | 2PM to 3PM | 81 | 69.9 | 64.9 | 94.6 | 34.26 | 0.0713 | 0.62 | 14.21 | 0
May | 30 | 3PM to 4PM | 82.9 | 70.5 | 64.9 | 94.6 | 34.75 | 0.0711 | 0.62 | 14.26 | 0
May | 30 | 4PM to 5PM | 82 | 69.7 | 64 | 91.7 | 34.06 | 0.0712 | 0.6 | 14.23 | 0
May | 30 | 5PM to 6PM | 82 | 70.2 | 64.9 | 94.6 | 34.53 | 0.0712 | 0.62 | 14.24 | 0
May | 30 | 6PM to 7PM | 80.1 | 69.1 | 64 | 91.7 | 33.57 | 0.0715 | 0.6 | 14.18 | 0
May | 30 | 7PM to 8PM | 77 | 69.4 | 66 | 98.4 | 33.87 | 0.0718 | 0.64 | 14.12 | 0
May | 30 | 8PM to 9PM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
May | 30 | 9PM to 10PM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
May | 30 | 10PM to 11PM | 72 | 67.2 | 64.9 | 94.6 | 32.05 | 0.0725 | 0.62 | 13.97 | 0
May | 30 | 11PM to 12AM | 71.1 | 66.9 | 64.9 | 94.6 | 31.83 | 0.0727 | 0.62 | 13.95 | 0
May | 31 | 12AM to 1AM | 71.1 | 66.9 | 64.9 | 94.6 | 31.83 | 0.0727 | 0.62 | 13.95 | 0
May | 31 | 1AM to 2AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
May | 31 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
May | 31 | 3AM to 4AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
May | 31 | 4AM to 5AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
May | 31 | 5AM to 6AM | 70 | 67.3 | 66 | 98.4 | 32.14 | 0.0728 | 0.64 | 13.93 | 0
May | 31 | 6AM to 7AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
May | 31 | 7AM to 8AM | 78.1 | 69.7 | 66 | 98.4 | 34.14 | 0.0717 | 0.64 | 14.14 | 0
May | 31 | 8AM to 9AM | 81 | 71.1 | 66.9 | 101.5 | 35.34 | 0.0713 | 0.67 | 14.23 | 0
May | 31 | 9AM to 10AM | 82.9 | 72.4 | 68 | 105.5 | 36.45 | 0.071 | 0.69 | 14.3 | 0
May | 31 | 10AM to 11AM | 86 | 72.5 | 66.9 | 101.5 | 36.59 | 0.0706 | 0.67 | 14.36 | 0
May | 31 | 11AM to 12PM | 88 | 74.4 | 69.1 | 109.6 | 38.34 | 0.0703 | 0.72 | 14.44 | 0
May | 31 | 12PM to 1PM | 88 | 75 | 70 | 113.1 | 38.89 | 0.0703 | 0.74 | 14.45 | 0
May | 31 | 1PM to 2PM | 90 | 74.9 | 69.1 | 109.6 | 38.83 | 0.0701 | 0.72 | 14.49 | 0
May | 31 | 2PM to 3PM | 90 | 75.5 | 70 | 113.1 | 39.38 | 0.0701 | 0.74 | 14.51 | 0
May | 31 | 3PM to 4PM | 89.1 | 75.3 | 70 | 113.1 | 39.16 | 0.0702 | 0.74 | 14.48 | 0
May | 31 | 4PM to 5PM | 88 | 75 | 70 | 113.1 | 38.89 | 0.0703 | 0.74 | 14.45 | 0
May | 31 | 5PM to 6PM | 87.1 | 74.2 | 69.1 | 109.6 | 38.11 | 0.0704 | 0.72 | 14.42 | 0
May | 31 | 6PM to 7PM | 84.9 | 73.6 | 69.1 | 109.6 | 37.58 | 0.0707 | 0.72 | 14.36 | 0
May | 31 | 7PM to 8PM | 82.9 | 72.4 | 68 | 105.5 | 36.45 | 0.071 | 0.69 | 14.3 | 0
May | 31 | 8PM to 9PM | 81 | 71.8 | 68 | 105.5 | 35.96 | 0.0713 | 0.69 | 14.24 | 0
May | 31 | 9PM to 10PM | 78.6 | 70.3 | 66.7 | 100.9 | 34.67 | 0.0716 | 0.66 | 14.17 | 0
May | 31 | 10PM to 11PM | 76.1 | 68.8 | 65.5 | 96.5 | 33.36 | 0.072 | 0.63 | 14.09 | 0
May | 31 | 11PM to 12AM | 73.8 | 67.3 | 64.2 | 92.2 | 32.12 | 0.0723 | 0.61 | 14.01 | 0
June | 1 | 12AM to 1AM | 71.2 | 65.6 | 62.8 | 87.6 | 30.77 | 0.0727 | 0.58 | 13.93 | 0
June | 1 | 1AM to 2AM | 68.9 | 64 | 61.5 | 83.7 | 29.59 | 0.073 | 0.55 | 13.86 | 0
June | 1 | 2AM to 3AM | 66.4 | 62.4 | 60.3 | 80 | 28.39 | 0.0734 | 0.53 | 13.78 | 0
June | 1 | 3AM to 4AM | 64 | 60.8 | 59 | 76.4 | 27.26 | 0.0737 | 0.5 | 13.71 | 0
June | 1 | 4AM to 5AM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
June | 1 | 5AM to 6AM | 61 | 56.2 | 53.1 | 61.4 | 24.18 | 0.0743 | 0.41 | 13.58 | 0
June | 1 | 6AM to 7AM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
June | 1 | 7AM to 8AM | 64 | 55.8 | 50 | 54.7 | 23.89 | 0.0739 | 0.36 | 13.64 | 0
June | 1 | 8AM to 9AM | 66.9 | 57.5 | 51.1 | 57 | 24.95 | 0.0735 | 0.38 | 13.72 | 0
June | 1 | 9AM to 10AM | 69.1 | 58.3 | 51.1 | 57 | 25.47 | 0.0732 | 0.38 | 13.78 | 0
June | 1 | 10AM to 11AM | 70 | 59.1 | 52 | 59 | 26 | 0.073 | 0.39 | 13.81 | 0
June | 1 | 11AM to 12PM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
June | 1 | 12PM to 1PM | 73 | 58.7 | 48.9 | 52.6 | 25.74 | 0.0726 | 0.35 | 13.87 | 0
June | 1 | 1PM to 2PM | 75 | 59.9 | 50 | 54.7 | 26.57 | 0.0724 | 0.36 | 13.93 | 0
June | 1 | 2PM to 3PM | 75 | 60.4 | 51.1 | 57 | 26.92 | 0.0724 | 0.38 | 13.93 | 0
June | 1 | 3PM to 4PM | 75 | 59.9 | 50 | 54.7 | 26.57 | 0.0724 | 0.36 | 13.93 | 0
June | 1 | 4PM to 5PM | 78.1 | 60.5 | 48.9 | 52.6 | 26.97 | 0.072 | 0.35 | 14 | 0
June | 1 | 5PM to 6PM | 77 | 58.9 | 46 | 47.1 | 25.85 | 0.0721 | 0.31 | 13.95 | 0
June | 1 | 6PM to 7PM | 75 | 58.6 | 46.9 | 48.8 | 25.63 | 0.0724 | 0.32 | 13.91 | 0
June | 1 | 7PM to 8PM | 71.1 | 58 | 48.9 | 52.6 | 25.26 | 0.0729 | 0.35 | 13.82 | 0
June | 1 | 8PM to 9PM | 66.9 | 57.5 | 51.1 | 57 | 24.95 | 0.0735 | 0.38 | 13.72 | 0
June | 1 | 9PM to 10PM | 64 | 56.8 | 52 | 59 | 24.55 | 0.0739 | 0.39 | 13.65 | 0
June | 1 | 10PM to 11PM | 66 | 57.1 | 51.1 | 57 | 24.73 | 0.0736 | 0.38 | 13.7 | 0
June | 1 | 11PM to 12AM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
June | 2 | 12AM to 1AM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
June | 2 | 1AM to 2AM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
June | 2 | 2AM to 3AM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
June | 2 | 3AM to 4AM | 61 | 56.2 | 53.1 | 61.4 | 24.18 | 0.0743 | 0.41 | 13.58 | 0
June | 2 | 4AM to 5AM | 60.1 | 56.4 | 54 | 63.5 | 24.29 | 0.0744 | 0.42 | 13.56 | 0
June | 2 | 5AM to 6AM | 62.1 | 57.8 | 55 | 66.1 | 25.17 | 0.0741 | 0.44 | 13.62 | 0
June | 2 | 6AM to 7AM | 64 | 56.4 | 51.1 | 57 | 24.25 | 0.0739 | 0.38 | 13.65 | 0
June | 2 | 7AM to 8AM | 69.1 | 58.7 | 52 | 59 | 25.78 | 0.0732 | 0.39 | 13.79 | 0
June | 2 | 8AM to 9AM | 69.1 | 57.7 | 50 | 54.7 | 25.12 | 0.0732 | 0.36 | 13.77 | 0
June | 2 | 9AM to 10AM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
June | 2 | 10AM to 11AM | 73 | 58.7 | 48.9 | 52.6 | 25.74 | 0.0726 | 0.35 | 13.87 | 0
June | 2 | 11AM to 12PM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
June | 2 | 12PM to 1PM | 73 | 59.2 | 50 | 54.7 | 26.08 | 0.0726 | 0.36 | 13.88 | 0
June | 2 | 1PM to 2PM | 73.9 | 59.5 | 50 | 54.7 | 26.3 | 0.0725 | 0.36 | 13.9 | 0
June | 2 | 2PM to 3PM | 73.9 | 59.5 | 50 | 54.7 | 26.3 | 0.0725 | 0.36 | 13.9 | 0
June | 2 | 3PM to 4PM | 73.9 | 59.5 | 50 | 54.7 | 26.3 | 0.0725 | 0.36 | 13.9 | 0
June | 2 | 4PM to 5PM | 73.9 | 59 | 48.9 | 52.6 | 25.96 | 0.0725 | 0.35 | 13.89 | 0
June | 2 | 5PM to 6PM | 72 | 62.4 | 57 | 71.1 | 28.37 | 0.0727 | 0.47 | 13.9 | 0
June | 2 | 6PM to 7PM | 70 | 58.6 | 51.1 | 57 | 25.69 | 0.073 | 0.38 | 13.8 | 0
June | 2 | 7PM to 8PM | 68 | 56.8 | 48.9 | 52.6 | 24.52 | 0.0733 | 0.35 | 13.74 | 0
June | 2 | 8PM to 9PM | 64 | 56.8 | 52 | 59 | 24.55 | 0.0739 | 0.39 | 13.65 | 0
June | 2 | 9PM to 10PM | 64 | 57.4 | 53.1 | 61.4 | 24.93 | 0.0738 | 0.41 | 13.66 | 0
June | 2 | 10PM to 11PM | 64 | 55.8 | 50 | 54.7 | 23.89 | 0.0739 | 0.36 | 13.64 | 0
June | 2 | 11PM to 12AM | 62.1 | 56.1 | 52 | 59 | 24.07 | 0.0741 | 0.39 | 13.6 | 0
June | 3 | 12AM to 1AM | 60.1 | 55.9 | 53.1 | 61.4 | 23.96 | 0.0744 | 0.41 | 13.56 | 0
June | 3 | 1AM to 2AM | 59 | 54.9 | 52 | 59 | 23.32 | 0.0746 | 0.39 | 13.52 | 0
June | 3 | 2AM to 3AM | 57.9 | 54.4 | 52 | 59 | 23.06 | 0.0747 | 0.39 | 13.49 | 0
June | 3 | 3AM to 4AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
June | 3 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 61.4 | 22.95 | 0.075 | 0.41 | 13.45 | 0
June | 3 | 5AM to 6AM | 57 | 55.2 | 54 | 63.5 | 23.54 | 0.0748 | 0.42 | 13.48 | 0
June | 3 | 6AM to 7AM | 60.1 | 57 | 55 | 66.1 | 24.69 | 0.0744 | 0.44 | 13.57 | 0
June | 3 | 7AM to 8AM | 66 | 59.2 | 55 | 66.1 | 26.14 | 0.0735 | 0.44 | 13.73 | 0
June | 3 | 8AM to 9AM | 70 | 61.1 | 55.9 | 68.3 | 27.45 | 0.073 | 0.45 | 13.84 | 0
June | 3 | 9AM to 10AM | 73.9 | 62 | 55 | 66.1 | 28.07 | 0.0724 | 0.44 | 13.93 | 0
June | 3 | 10AM to 11AM | 78.1 | 61.9 | 52 | 59 | 27.97 | 0.0719 | 0.39 | 14.02 | 0
June | 3 | 11AM to 12PM | 80.1 | 63.1 | 53.1 | 61.4 | 28.83 | 0.0716 | 0.41 | 14.08 | 0
June | 3 | 12PM to 1PM | 81 | 62 | 50 | 54.7 | 28.01 | 0.0716 | 0.36 | 14.08 | 0
June | 3 | 1PM to 2PM | 82 | 61.9 | 48.9 | 52.6 | 27.93 | 0.0714 | 0.35 | 14.1 | 0
June | 3 | 2PM to 3PM | 84.9 | 62.9 | 48.9 | 52.6 | 28.63 | 0.0711 | 0.35 | 14.18 | 0
June | 3 | 3PM to 4PM | 84 | 60.3 | 43 | 41.9 | 26.74 | 0.0712 | 0.28 | 14.12 | 0
June | 3 | 4PM to 5PM | 84 | 60.7 | 44.1 | 43.6 | 27.02 | 0.0712 | 0.29 | 14.13 | 0
June | 3 | 5PM to 6PM | 82 | 62.4 | 50 | 54.7 | 28.28 | 0.0714 | 0.36 | 14.11 | 0
June | 3 | 6PM to 7PM | 79 | 61.3 | 50 | 54.7 | 27.53 | 0.0718 | 0.36 | 14.03 | 0
June | 3 | 7PM to 8PM | 75 | 59.9 | 50 | 54.7 | 26.57 | 0.0724 | 0.36 | 13.93 | 0
June | 3 | 8PM to 9PM | 73.9 | 59 | 48.9 | 52.6 | 25.96 | 0.0725 | 0.35 | 13.89 | 0
June | 3 | 9PM to 10PM | 72 | 59.3 | 51.1 | 57 | 26.18 | 0.0728 | 0.38 | 13.85 | 0
June | 3 | 10PM to 11PM | 71.1 | 60 | 53.1 | 61.4 | 26.64 | 0.0729 | 0.41 | 13.84 | 0
June | 3 | 11PM to 12AM | 69.1 | 59.8 | 54 | 63.5 | 26.48 | 0.0731 | 0.42 | 13.8 | 0
June | 4 | 12AM to 1AM | 68 | 59.9 | 55 | 66.1 | 26.62 | 0.0733 | 0.44 | 13.78 | 0
June | 4 | 1AM to 2AM | 64.9 | 60 | 57 | 71.1 | 26.65 | 0.0737 | 0.47 | 13.71 | 0
June | 4 | 2AM to 3AM | 64.9 | 61.1 | 59 | 76.4 | 27.48 | 0.0736 | 0.5 | 13.73 | 0
June | 4 | 3AM to 4AM | 63 | 60.4 | 59 | 76.4 | 27 | 0.0739 | 0.5 | 13.68 | 0
June | 4 | 4AM to 5AM | 62.1 | 60.1 | 59 | 76.4 | 26.78 | 0.074 | 0.5 | 13.66 | 0
June | 4 | 5AM to 6AM | 64 | 60.8 | 59 | 76.4 | 27.26 | 0.0737 | 0.5 | 13.71 | 0
June | 4 | 6AM to 7AM | 69.1 | 63.2 | 60.1 | 79.5 | 28.98 | 0.073 | 0.52 | 13.85 | 0
June | 4 | 7AM to 8AM | 73 | 64.5 | 60.1 | 79.5 | 29.95 | 0.0725 | 0.52 | 13.95 | 0
June | 4 | 8AM to 9AM | 75.9 | 65.5 | 60.1 | 79.5 | 30.65 | 0.0721 | 0.52 | 14.03 | 0
June | 4 | 9AM to 10AM | 78.1 | 64.5 | 57 | 71.1 | 29.87 | 0.0719 | 0.47 | 14.06 | 0
June | 4 | 10AM to 11AM | 79 | 64.8 | 57 | 71.1 | 30.09 | 0.0717 | 0.47 | 14.08 | 0
June | 4 | 11AM to 12PM | 80.1 | 65.6 | 57.9 | 73.5 | 30.72 | 0.0716 | 0.48 | 14.12 | 0
June | 4 | 12PM to 1PM | 80.1 | 65.1 | 57 | 71.1 | 30.35 | 0.0716 | 0.47 | 14.11 | 0
June | 4 | 1PM to 2PM | 82.9 | 65.5 | 55.9 | 68.3 | 30.62 | 0.0712 | 0.45 | 14.18 | 0
June | 4 | 2PM to 3PM | 84 | 65.8 | 55.9 | 68.3 | 30.89 | 0.0711 | 0.45 | 14.2 | 0
June | 4 | 3PM to 4PM | 84.9 | 66.1 | 55.9 | 68.3 | 31.11 | 0.071 | 0.45 | 14.23 | 0
June | 4 | 4PM to 5PM | 84 | 65.8 | 55.9 | 68.3 | 30.89 | 0.0711 | 0.45 | 14.2 | 0
June | 4 | 5PM to 6PM | 82 | 65.2 | 55.9 | 68.3 | 30.4 | 0.0713 | 0.45 | 14.15 | 0
June | 4 | 6PM to 7PM | 80.1 | 65.1 | 57 | 71.1 | 30.35 | 0.0716 | 0.47 | 14.11 | 0
June | 4 | 7PM to 8PM | 78.1 | 64.5 | 57 | 71.1 | 29.87 | 0.0719 | 0.47 | 14.06 | 0
June | 4 | 8PM to 9PM | 77 | 65.2 | 59 | 76.4 | 30.44 | 0.072 | 0.5 | 14.05 | 0
June | 4 | 9PM to 10PM | 77 | 65.2 | 59 | 76.4 | 30.44 | 0.072 | 0.5 | 14.05 | 0
June | 4 | 10PM to 11PM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
June | 4 | 11PM to 12AM | 73.9 | 64.2 | 59 | 76.4 | 29.69 | 0.0724 | 0.5 | 13.97 | 0
June | 5 | 12AM to 1AM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
June | 5 | 1AM to 2AM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
June | 5 | 2AM to 3AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
June | 5 | 3AM to 4AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
June | 5 | 4AM to 5AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
June | 5 | 5AM to 6AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
June | 5 | 6AM to 7AM | 73 | 64.5 | 60.1 | 79.5 | 29.95 | 0.0725 | 0.52 | 13.95 | 0
June | 5 | 7AM to 8AM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
June | 5 | 8AM to 9AM | 77 | 65.8 | 60.1 | 79.5 | 30.92 | 0.0719 | 0.52 | 14.06 | 0
June | 5 | 9AM to 10AM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
June | 5 | 10AM to 11AM | 82.9 | 68.8 | 62.1 | 85.4 | 33.3 | 0.0711 | 0.56 | 14.23 | 0
June | 5 | 11AM to 12PM | 84.9 | 68.8 | 61 | 82.1 | 33.27 | 0.0709 | 0.54 | 14.27 | 0
June | 5 | 12PM to 1PM | 87.1 | 69.4 | 61 | 82.1 | 33.8 | 0.0706 | 0.54 | 14.33 | 0
June | 5 | 1PM to 2PM | 89.1 | 69.5 | 60.1 | 79.5 | 33.87 | 0.0704 | 0.52 | 14.37 | 0
June | 5 | 2PM to 3PM | 89.1 | 70 | 61 | 82.1 | 34.29 | 0.0704 | 0.54 | 14.38 | 0
June | 5 | 3PM to 4PM | 91 | 71.2 | 62.1 | 85.4 | 35.28 | 0.0701 | 0.56 | 14.44 | 0
June | 5 | 4PM to 5PM | 89.1 | 71.1 | 63 | 88.2 | 35.24 | 0.0703 | 0.58 | 14.4 | 0
June | 5 | 5PM to 6PM | 87.1 | 70.5 | 63 | 88.2 | 34.75 | 0.0706 | 0.58 | 14.35 | 0
June | 5 | 6PM to 7PM | 84.9 | 70.5 | 64 | 91.7 | 34.77 | 0.0708 | 0.6 | 14.3 | 0
June | 5 | 7PM to 8PM | 82 | 69.7 | 64 | 91.7 | 34.06 | 0.0712 | 0.6 | 14.23 | 0
June | 5 | 8PM to 9PM | 79 | 69.3 | 64.9 | 94.6 | 33.78 | 0.0716 | 0.62 | 14.16 | 0
June | 5 | 9PM to 10PM | 79 | 69.3 | 64.9 | 94.6 | 33.78 | 0.0716 | 0.62 | 14.16 | 0
June | 5 | 10PM to 11PM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
June | 5 | 11PM to 12AM | 75.9 | 68.4 | 64.9 | 94.6 | 33.02 | 0.072 | 0.62 | 14.08 | 0
June | 6 | 12AM to 1AM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
June | 6 | 1AM to 2AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
June | 6 | 2AM to 3AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
June | 6 | 3AM to 4AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
June | 6 | 4AM to 5AM | 71.1 | 67.6 | 66 | 98.4 | 32.41 | 0.0726 | 0.64 | 13.96 | 0
June | 6 | 5AM to 6AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
June | 6 | 6AM to 7AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
June | 6 | 7AM to 8AM | 77 | 70 | 66.9 | 101.5 | 34.37 | 0.0718 | 0.67 | 14.13 | 0
June | 6 | 8AM to 9AM | 78.1 | 70.3 | 66.9 | 101.5 | 34.63 | 0.0717 | 0.67 | 14.15 | 0
June | 6 | 9AM to 10AM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
June | 6 | 10AM to 11AM | 82.9 | 72.4 | 68 | 105.5 | 36.45 | 0.071 | 0.69 | 14.3 | 0
June | 6 | 11AM to 12PM | 84.9 | 71 | 64.9 | 94.6 | 35.24 | 0.0708 | 0.62 | 14.31 | 0
June | 6 | 12PM to 1PM | 86 | 71 | 64.4 | 92.8 | 35.22 | 0.0707 | 0.61 | 14.34 | 0
June | 6 | 1PM to 2PM | 84 | 70.4 | 64.2 | 92.2 | 34.64 | 0.0709 | 0.61 | 14.28 | 0
June | 6 | 2PM to 3PM | 84 | 70.6 | 64.6 | 93.4 | 34.83 | 0.0709 | 0.61 | 14.29 | 0
June | 6 | 3PM to 4PM | 84 | 70.2 | 64 | 91.7 | 34.55 | 0.0709 | 0.6 | 14.28 | 0
June | 6 | 4PM to 5PM | 84 | 70.2 | 64 | 91.7 | 34.55 | 0.0709 | 0.6 | 14.28 | 0
June | 6 | 5PM to 6PM | 82 | 70.9 | 66 | 98.4 | 35.11 | 0.0712 | 0.64 | 14.25 | 0
June | 6 | 6PM to 7PM | 81 | 69.9 | 64.9 | 94.6 | 34.26 | 0.0713 | 0.62 | 14.21 | 0
June | 6 | 7PM to 8PM | 79 | 69.3 | 64.9 | 94.6 | 33.78 | 0.0716 | 0.62 | 14.16 | 0
June | 6 | 8PM to 9PM | 77 | 69.4 | 66 | 98.4 | 33.87 | 0.0718 | 0.64 | 14.12 | 0
June | 6 | 9PM to 10PM | 75.9 | 69.1 | 66 | 98.4 | 33.6 | 0.072 | 0.64 | 14.09 | 0
June | 6 | 10PM to 11PM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
June | 6 | 11PM to 12AM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
June | 7 | 12AM to 1AM | 75 | 70.1 | 68 | 105.5 | 34.5 | 0.0721 | 0.69 | 14.09 | 0
June | 7 | 1AM to 2AM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
June | 7 | 2AM to 3AM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
June | 7 | 3AM to 4AM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
June | 7 | 4AM to 5AM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
June | 7 | 5AM to 6AM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
June | 7 | 6AM to 7AM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
June | 7 | 7AM to 8AM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
June | 7 | 8AM to 9AM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
June | 7 | 9AM to 10AM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
June | 7 | 10AM to 11AM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
June | 7 | 11AM to 12PM | 81 | 69.9 | 64.9 | 94.6 | 34.26 | 0.0713 | 0.62 | 14.21 | 0
June | 7 | 12PM to 1PM | 84 | 71.4 | 66 | 98.4 | 35.6 | 0.0709 | 0.64 | 14.3 | 0
June | 7 | 1PM to 2PM | 84 | 70.8 | 64.9 | 94.6 | 35.02 | 0.0709 | 0.62 | 14.29 | 0
June | 7 | 2PM to 3PM | 86 | 72 | 66 | 98.4 | 36.09 | 0.0706 | 0.64 | 14.35 | 0
June | 7 | 3PM to 4PM | 86 | 72 | 66 | 98.4 | 36.09 | 0.0706 | 0.64 | 14.35 | 0
June | 7 | 4PM to 5PM | 84.9 | 71.7 | 66 | 98.4 | 35.82 | 0.0708 | 0.64 | 14.32 | 0
June | 7 | 5PM to 6PM | 82.9 | 71.1 | 66 | 98.4 | 35.33 | 0.071 | 0.64 | 14.27 | 0
June | 7 | 6PM to 7PM | 82 | 70.9 | 66 | 98.4 | 35.11 | 0.0712 | 0.64 | 14.25 | 0
June | 7 | 7PM to 8PM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
June | 7 | 8PM to 9PM | 79 | 70.5 | 66.9 | 101.5 | 34.86 | 0.0716 | 0.67 | 14.18 | 0
June | 7 | 9PM to 10PM | 75.9 | 69.7 | 66.9 | 101.5 | 34.1 | 0.072 | 0.67 | 14.1 | 0
June | 7 | 10PM to 11PM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
June | 7 | 11PM to 12AM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
June | 8 | 12AM to 1AM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
June | 8 | 1AM to 2AM | 77 | 72 | 70 | 113.1 | 36.18 | 0.0717 | 0.74 | 14.16 | 0
June | 8 | 2AM to 3AM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
June | 8 | 3AM to 4AM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
June | 8 | 4AM to 5AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
June | 8 | 5AM to 6AM | 77 | 72.7 | 71.1 | 117.4 | 36.86 | 0.0717 | 0.77 | 14.18 | 0
June | 8 | 6AM to 7AM | 80.1 | 74.2 | 72 | 121.2 | 38.2 | 0.0713 | 0.79 | 14.27 | 0
June | 8 | 7AM to 8AM | 81 | 74.4 | 72 | 121.2 | 38.42 | 0.0712 | 0.79 | 14.29 | 0
June | 8 | 8AM to 9AM | 82.9 | 74.9 | 72 | 121.2 | 38.91 | 0.0709 | 0.79 | 14.35 | 0
June | 8 | 9AM to 10AM | 84 | 75.2 | 72 | 121.2 | 39.18 | 0.0708 | 0.79 | 14.37 | 0
June | 8 | 10AM to 11AM | 88 | 76.3 | 72 | 121.2 | 40.16 | 0.0703 | 0.79 | 14.48 | 0
June | 8 | 11AM to 12PM | 86 | 75.7 | 72 | 121.2 | 39.67 | 0.0705 | 0.79 | 14.43 | 0
June | 8 | 12PM to 1PM | 80.1 | 73.6 | 71.1 | 117.4 | 37.61 | 0.0713 | 0.77 | 14.26 | 0
June | 8 | 1PM to 2PM | 84 | 76 | 73 | 125.8 | 39.91 | 0.0707 | 0.82 | 14.39 | 0
June | 8 | 2PM to 3PM | 79 | 73.3 | 71.1 | 117.4 | 37.35 | 0.0715 | 0.77 | 14.23 | 0
June | 8 | 3PM to 4PM | 80.1 | 72.8 | 70 | 113.1 | 36.93 | 0.0713 | 0.74 | 14.24 | 0
June | 8 | 4PM to 5PM | 82.9 | 73.6 | 70 | 113.1 | 37.64 | 0.071 | 0.74 | 14.32 | 0
June | 8 | 5PM to 6PM | 84 | 73.9 | 70 | 113.1 | 37.91 | 0.0708 | 0.74 | 14.35 | 0
June | 8 | 6PM to 7PM | 82 | 73.4 | 70 | 113.1 | 37.42 | 0.0711 | 0.74 | 14.3 | 0
June | 8 | 7PM to 8PM | 80.1 | 73.6 | 71.1 | 117.4 | 37.61 | 0.0713 | 0.77 | 14.26 | 0
June | 8 | 8PM to 9PM | 77 | 72.7 | 71.1 | 117.4 | 36.86 | 0.0717 | 0.77 | 14.18 | 0
June | 8 | 9PM to 10PM | 78.1 | 73 | 71.1 | 117.4 | 37.12 | 0.0716 | 0.77 | 14.21 | 0
June | 8 | 10PM to 11PM | 79 | 73.3 | 71.1 | 117.4 | 37.35 | 0.0715 | 0.77 | 14.23 | 0
June | 8 | 11PM to 12AM | 78.1 | 73 | 71.1 | 117.4 | 37.12 | 0.0716 | 0.77 | 14.21 | 0
June | 9 | 12AM to 1AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
June | 9 | 1AM to 2AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
June | 9 | 2AM to 3AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
June | 9 | 3AM to 4AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
June | 9 | 4AM to 5AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
June | 9 | 5AM to 6AM | 77 | 72 | 70 | 113.1 | 36.18 | 0.0717 | 0.74 | 14.16 | 0
June | 9 | 6AM to 7AM | 78.1 | 72.3 | 70 | 113.1 | 36.44 | 0.0716 | 0.74 | 14.19 | 0
June | 9 | 7AM to 8AM | 81 | 73.1 | 70 | 113.1 | 37.15 | 0.0712 | 0.74 | 14.27 | 0
June | 9 | 8AM to 9AM | 84.9 | 74.2 | 70 | 113.1 | 38.13 | 0.0707 | 0.74 | 14.37 | 0
June | 9 | 9AM to 10AM | 87.1 | 74.7 | 70 | 113.1 | 38.67 | 0.0704 | 0.74 | 14.43 | 0
June | 9 | 10AM to 11AM | 88 | 75 | 70 | 113.1 | 38.89 | 0.0703 | 0.74 | 14.45 | 0
June | 9 | 11AM to 12PM | 88 | 75 | 70 | 113.1 | 38.89 | 0.0703 | 0.74 | 14.45 | 0
June | 9 | 12PM to 1PM | 89.1 | 75.3 | 70 | 113.1 | 39.16 | 0.0702 | 0.74 | 14.48 | 0
June | 9 | 1PM to 2PM | 91 | 75.2 | 69.1 | 109.6 | 39.09 | 0.0699 | 0.72 | 14.52 | 0
June | 9 | 2PM to 3PM | 91.9 | 75.4 | 69.1 | 109.6 | 39.32 | 0.0698 | 0.72 | 14.55 | 0
June | 9 | 3PM to 4PM | 91.9 | 75.4 | 69.1 | 109.6 | 39.32 | 0.0698 | 0.72 | 14.55 | 0
June | 9 | 4PM to 5PM | 91.9 | 73.6 | 66 | 98.4 | 37.55 | 0.0699 | 0.64 | 14.51 | 0
June | 9 | 5PM to 6PM | 90 | 73.1 | 66 | 98.4 | 37.06 | 0.0701 | 0.64 | 14.46 | 0
June | 9 | 6PM to 7PM | 88 | 73.7 | 68 | 105.5 | 37.69 | 0.0704 | 0.69 | 14.43 | 0
June | 9 | 7PM to 8PM | 86 | 73.9 | 69.1 | 109.6 | 37.85 | 0.0706 | 0.72 | 14.39 | 0
June | 9 | 8PM to 9PM | 84 | 73.3 | 69.1 | 109.6 | 37.36 | 0.0708 | 0.72 | 14.34 | 0
June | 9 | 9PM to 10PM | 82.9 | 73 | 69.1 | 109.6 | 37.09 | 0.071 | 0.72 | 14.31 | 0
June | 9 | 10PM to 11PM | 82 | 72.1 | 68 | 105.5 | 36.23 | 0.0711 | 0.69 | 14.27 | 0
June | 9 | 11PM to 12AM | 81 | 71.8 | 68 | 105.5 | 35.96 | 0.0713 | 0.69 | 14.24 | 0
June | 10 | 12AM to 1AM | 80.1 | 71.5 | 68 | 105.5 | 35.74 | 0.0714 | 0.69 | 14.22 | 0
June | 10 | 1AM to 2AM | 78.1 | 71 | 68 | 105.5 | 35.25 | 0.0716 | 0.69 | 14.17 | 0
June | 10 | 2AM to 3AM | 78.1 | 71 | 68 | 105.5 | 35.25 | 0.0716 | 0.69 | 14.17 | 0
June | 10 | 3AM to 4AM | 77 | 70.7 | 68 | 105.5 | 34.99 | 0.0718 | 0.69 | 14.14 | 0
June | 10 | 4AM to 5AM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
June | 10 | 5AM to 6AM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
June | 10 | 6AM to 7AM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
June | 10 | 7AM to 8AM | 61 | 59.7 | 59 | 76.4 | 26.52 | 0.0742 | 0.5 | 13.63 | 0
June | 10 | 8AM to 9AM | 60.1 | 57 | 55 | 66.1 | 24.69 | 0.0744 | 0.44 | 13.57 | 0
June | 10 | 9AM to 10AM | 63 | 57.5 | 54 | 63.5 | 24.99 | 0.074 | 0.42 | 13.64 | 0
June | 10 | 10AM to 11AM | 66.9 | 59 | 54 | 63.5 | 25.96 | 0.0734 | 0.42 | 13.74 | 0
June | 10 | 11AM to 12PM | 68 | 58.3 | 52 | 59 | 25.52 | 0.0733 | 0.39 | 13.76 | 0
June | 10 | 12PM to 1PM | 70 | 58.1 | 50 | 54.7 | 25.34 | 0.0731 | 0.36 | 13.8 | 0
June | 10 | 1PM to 2PM | 72 | 58.8 | 50 | 54.7 | 25.82 | 0.0728 | 0.36 | 13.85 | 0
June | 10 | 2PM to 3PM | 73.9 | 59.5 | 50 | 54.7 | 26.3 | 0.0725 | 0.36 | 13.9 | 0
June | 10 | 3PM to 4PM | 73 | 58.3 | 48 | 50.8 | 25.47 | 0.0727 | 0.34 | 13.86 | 0
June | 10 | 4PM to 5PM | 75 | 59.4 | 48.9 | 52.6 | 26.22 | 0.0724 | 0.35 | 13.92 | 0
June | 10 | 5PM to 6PM | 73.9 | 59 | 48.9 | 52.6 | 25.96 | 0.0725 | 0.35 | 13.89 | 0
June | 10 | 6PM to 7PM | 72 | 58.8 | 50 | 54.7 | 25.82 | 0.0728 | 0.36 | 13.85 | 0
June | 10 | 7PM to 8PM | 69.1 | 57.7 | 50 | 54.7 | 25.12 | 0.0732 | 0.36 | 13.77 | 0
June | 10 | 8PM to 9PM | 66 | 57.1 | 51.1 | 57 | 24.73 | 0.0736 | 0.38 | 13.7 | 0
June | 10 | 9PM to 10PM | 64 | 56.8 | 52 | 59 | 24.55 | 0.0739 | 0.39 | 13.65 | 0
June | 10 | 10PM to 11PM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
June | 10 | 11PM to 12AM | 60.1 | 55.9 | 53.1 | 61.4 | 23.96 | 0.0744 | 0.41 | 13.56 | 0
June | 11 | 12AM to 1AM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
June | 11 | 1AM to 2AM | 57.9 | 55 | 53.1 | 61.4 | 23.44 | 0.0747 | 0.41 | 13.5 | 0
June | 11 | 2AM to 3AM | 57 | 55.2 | 54 | 63.5 | 23.54 | 0.0748 | 0.42 | 13.48 | 0
June | 11 | 3AM to 4AM | 57 | 54.7 | 53.1 | 61.4 | 23.22 | 0.0748 | 0.41 | 13.48 | 0
June | 11 | 4AM to 5AM | 55.9 | 54.2 | 53.1 | 61.4 | 22.95 | 0.075 | 0.41 | 13.45 | 0
June | 11 | 5AM to 6AM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
June | 11 | 6AM to 7AM | 62.1 | 56.2 | 52.2 | 59.4 | 24.13 | 0.0741 | 0.39 | 13.6 | 0
June | 11 | 7AM to 8AM | 66.9 | 57.6 | 51.4 | 57.8 | 25.07 | 0.0735 | 0.38 | 13.73 | 0
June | 11 | 8AM to 9AM | 72 | 58.4 | 49.1 | 52.9 | 25.54 | 0.0728 | 0.35 | 13.84 | 0
June | 11 | 9AM to 10AM | 75 | 59.3 | 48.6 | 51.8 | 26.11 | 0.0724 | 0.34 | 13.92 | 0
June | 11 | 10AM to 11AM | 79 | 60.5 | 48 | 50.8 | 26.91 | 0.0719 | 0.34 | 14.02 | 0
June | 11 | 11AM to 12PM | 80.1 | 60.4 | 46.9 | 48.8 | 26.85 | 0.0717 | 0.32 | 14.04 | 0
June | 11 | 12PM to 1PM | 80.1 | 59.7 | 45.1 | 45.5 | 26.34 | 0.0717 | 0.3 | 14.03 | 0
June | 11 | 1PM to 2PM | 81 | 60 | 45.1 | 45.5 | 26.56 | 0.0716 | 0.3 | 14.05 | 0
June | 11 | 2PM to 3PM | 82.9 | 61 | 46 | 47.1 | 27.29 | 0.0714 | 0.31 | 14.11 | 0
June | 11 | 3PM to 4PM | 82 | 60.2 | 44.6 | 44.6 | 26.68 | 0.0715 | 0.3 | 14.08 | 0
June | 11 | 4PM to 5PM | 82.9 | 61 | 46 | 47.1 | 27.29 | 0.0714 | 0.31 | 14.11 | 0
June | 11 | 5PM to 6PM | 81 | 61.2 | 48 | 50.8 | 27.39 | 0.0716 | 0.34 | 14.07 | 0
June | 11 | 6PM to 7PM | 80.1 | 61.7 | 50 | 54.7 | 27.79 | 0.0717 | 0.36 | 14.06 | 0
June | 11 | 7PM to 8PM | 75 | 60.9 | 52 | 59 | 27.23 | 0.0723 | 0.39 | 13.94 | 0
June | 11 | 8PM to 9PM | 72 | 60.3 | 53.1 | 61.4 | 26.86 | 0.0727 | 0.41 | 13.87 | 0
June | 11 | 9PM to 10PM | 70 | 60.1 | 54 | 63.5 | 26.7 | 0.073 | 0.42 | 13.82 | 0
June | 11 | 10PM to 11PM | 69.1 | 59.8 | 54 | 63.5 | 26.48 | 0.0731 | 0.42 | 13.8 | 0
June | 11 | 11PM to 12AM | 68 | 59.9 | 55 | 66.1 | 26.62 | 0.0733 | 0.44 | 13.78 | 0
June | 12 | 12AM to 1AM | 66 | 59.2 | 55 | 66.1 | 26.14 | 0.0735 | 0.44 | 13.73 | 0
June | 12 | 1AM to 2AM | 64 | 58.5 | 55 | 66.1 | 25.66 | 0.0738 | 0.44 | 13.68 | 0
June | 12 | 2AM to 3AM | 63 | 58.1 | 55 | 66.1 | 25.39 | 0.074 | 0.44 | 13.65 | 0
June | 12 | 3AM to 4AM | 63 | 58.1 | 55 | 66.1 | 25.39 | 0.074 | 0.44 | 13.65 | 0
June | 12 | 4AM to 5AM | 61 | 57.3 | 55 | 66.1 | 24.91 | 0.0742 | 0.44 | 13.6 | 0
June | 12 | 5AM to 6AM | 64 | 58.5 | 55 | 66.1 | 25.66 | 0.0738 | 0.44 | 13.68 | 0
June | 12 | 6AM to 7AM | 68 | 59.9 | 55 | 66.1 | 26.62 | 0.0733 | 0.44 | 13.78 | 0
June | 12 | 7AM to 8AM | 73 | 62.2 | 55.9 | 68.3 | 28.2 | 0.0726 | 0.45 | 13.92 | 0
June | 12 | 8AM to 9AM | 77 | 63.1 | 55 | 66.1 | 28.82 | 0.072 | 0.44 | 14.01 | 0
June | 12 | 9AM to 10AM | 80.1 | 64.1 | 55 | 66.1 | 29.57 | 0.0716 | 0.44 | 14.09 | 0
June | 12 | 10AM to 11AM | 82 | 64.2 | 54 | 63.5 | 29.65 | 0.0714 | 0.42 | 14.14 | 0
June | 12 | 11AM to 12PM | 82 | 64.2 | 54 | 63.5 | 29.65 | 0.0714 | 0.42 | 14.14 | 0
June | 12 | 12PM to 1PM | 84 | 64 | 52 | 59 | 29.42 | 0.0711 | 0.39 | 14.17 | 0
June | 12 | 1PM to 2PM | 84.9 | 64.3 | 52 | 59 | 29.64 | 0.071 | 0.39 | 14.2 | 0
June | 12 | 2PM to 3PM | 86 | 65.5 | 54 | 63.5 | 30.61 | 0.0709 | 0.42 | 14.24 | 0
June | 12 | 3PM to 4PM | 86 | 65.1 | 53.1 | 61.4 | 30.28 | 0.0709 | 0.41 | 14.23 | 0
June | 12 | 4PM to 5PM | 84.9 | 65.7 | 55 | 66.1 | 30.75 | 0.071 | 0.44 | 14.22 | 0
June | 12 | 5PM to 6PM | 84 | 65.4 | 55 | 66.1 | 30.54 | 0.0711 | 0.44 | 14.2 | 0
June | 12 | 6PM to 7PM | 82 | 64.8 | 55 | 66.1 | 30.05 | 0.0714 | 0.44 | 14.15 | 0
June | 12 | 7PM to 8PM | 79 | 64.2 | 55.9 | 68.3 | 29.65 | 0.0718 | 0.45 | 14.07 | 0
June | 12 | 8PM to 9PM | 77 | 64.1 | 57 | 71.1 | 29.6 | 0.072 | 0.47 | 14.03 | 0
June | 12 | 9PM to 10PM | 75.9 | 64.3 | 57.9 | 73.5 | 29.71 | 0.0721 | 0.48 | 14.01 | 0
June | 12 | 10PM to 11PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
June | 12 | 11PM to 12AM | 73 | 63.3 | 57.9 | 73.5 | 29.01 | 0.0725 | 0.48 | 13.93 | 0
June | 13 | 12AM to 1AM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
June | 13 | 1AM to 2AM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
June | 13 | 2AM to 3AM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
June | 13 | 3AM to 4AM | 69.1 | 62.6 | 59 | 76.4 | 28.5 | 0.073 | 0.5 | 13.84 | 0
June | 13 | 4AM to 5AM | 70 | 62.3 | 57.9 | 73.5 | 28.26 | 0.0729 | 0.48 | 13.85 | 0
June | 13 | 5AM to 6AM | 70 | 62.3 | 57.9 | 73.5 | 28.26 | 0.0729 | 0.48 | 13.85 | 0
June | 13 | 6AM to 7AM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
June | 13 | 7AM to 8AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
June | 13 | 8AM to 9AM | 72 | 65.4 | 62.1 | 85.4 | 30.6 | 0.0726 | 0.56 | 13.94 | 0
June | 13 | 9AM to 10AM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
June | 13 | 10AM to 11AM | 80.1 | 65.6 | 57.9 | 73.5 | 30.72 | 0.0716 | 0.48 | 14.12 | 0
June | 13 | 11AM to 12PM | 82 | 66.8 | 59 | 76.4 | 31.67 | 0.0713 | 0.5 | 14.18 | 0
June | 13 | 12PM to 1PM | 84 | 67.4 | 59 | 76.4 | 32.16 | 0.071 | 0.5 | 14.23 | 0
June | 13 | 1PM to 2PM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
June | 13 | 2PM to 3PM | 84 | 68.5 | 61 | 82.1 | 33.05 | 0.071 | 0.54 | 14.25 | 0
June | 13 | 3PM to 4PM | 82.9 | 68.2 | 61 | 82.1 | 32.78 | 0.0711 | 0.54 | 14.22 | 0
June | 13 | 4PM to 5PM | 82.9 | 68.8 | 62.1 | 85.4 | 33.3 | 0.0711 | 0.56 | 14.23 | 0
June | 13 | 5PM to 6PM | 82.9 | 69.3 | 63 | 88.2 | 33.74 | 0.0711 | 0.58 | 14.24 | 0
June | 13 | 6PM to 7PM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
June | 13 | 7PM to 8PM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
June | 13 | 8PM to 9PM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
June | 13 | 9PM to 10PM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
June | 13 | 10PM to 11PM | 73.9 | 65.4 | 61 | 82.1 | 30.58 | 0.0723 | 0.54 | 13.98 | 0
June | 13 | 11PM to 12AM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
June | 14 | 12AM to 1AM | 71.1 | 64.4 | 61 | 82.1 | 29.87 | 0.0727 | 0.54 | 13.91 | 0
June | 14 | 1AM to 2AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
June | 14 | 2AM to 3AM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
June | 14 | 3AM to 4AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
June | 14 | 4AM to 5AM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
June | 14 | 5AM to 6AM | 70 | 63.5 | 60.1 | 79.5 | 29.2 | 0.0729 | 0.52 | 13.87 | 0
June | 14 | 6AM to 7AM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
June | 14 | 7AM to 8AM | 77 | 65.8 | 60.1 | 79.5 | 30.92 | 0.0719 | 0.52 | 14.06 | 0
June | 14 | 8AM to 9AM | 80.1 | 66.8 | 60.1 | 79.5 | 31.67 | 0.0715 | 0.52 | 14.14 | 0
June | 14 | 9AM to 10AM | 84 | 68 | 60.1 | 79.5 | 32.64 | 0.071 | 0.52 | 14.24 | 0
June | 14 | 10AM to 11AM | 84.9 | 67.7 | 59 | 76.4 | 32.38 | 0.0709 | 0.5 | 14.25 | 0
June | 14 | 11AM to 12PM | 87.1 | 68.4 | 59 | 76.4 | 32.91 | 0.0706 | 0.5 | 14.31 | 0
June | 14 | 12PM to 1PM | 88 | 68.6 | 59 | 76.4 | 33.13 | 0.0705 | 0.5 | 14.33 | 0
June | 14 | 1PM to 2PM | 89.1 | 68.4 | 57.9 | 73.5 | 32.93 | 0.0704 | 0.48 | 14.35 | 0
June | 14 | 2PM to 3PM | 89.1 | 69 | 59 | 76.4 | 33.39 | 0.0704 | 0.5 | 14.36 | 0
June | 14 | 3PM to 4PM | 88 | 68.1 | 57.9 | 73.5 | 32.66 | 0.0705 | 0.48 | 14.32 | 0
June | 14 | 4PM to 5PM | 88 | 68.1 | 57.9 | 73.5 | 32.66 | 0.0705 | 0.48 | 14.32 | 0
June | 14 | 5PM to 6PM | 86 | 68 | 59 | 76.4 | 32.64 | 0.0708 | 0.5 | 14.28 | 0
June | 14 | 6PM to 7PM | 84.9 | 67.7 | 59 | 76.4 | 32.38 | 0.0709 | 0.5 | 14.25 | 0
June | 14 | 7PM to 8PM | 82 | 67.4 | 60.1 | 79.5 | 32.15 | 0.0713 | 0.52 | 14.19 | 0
June | 14 | 8PM to 9PM | 81 | 67.6 | 61 | 82.1 | 32.3 | 0.0714 | 0.54 | 14.17 | 0
June | 14 | 9PM to 10PM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
June | 14 | 10PM to 11PM | 78.1 | 67.3 | 62.1 | 85.4 | 32.1 | 0.0718 | 0.56 | 14.1 | 0
June | 14 | 11PM to 12AM | 75.9 | 66.6 | 62.1 | 85.4 | 31.57 | 0.0721 | 0.56 | 14.05 | 0
June | 15 | 12AM to 1AM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
June | 15 | 1AM to 2AM | 73.9 | 64.8 | 60.1 | 79.5 | 30.17 | 0.0724 | 0.52 | 13.98 | 0
June | 15 | 2AM to 3AM | 73.9 | 64.2 | 59 | 76.4 | 29.69 | 0.0724 | 0.5 | 13.97 | 0
June | 15 | 3AM to 4AM | 73 | 63.3 | 57.9 | 73.5 | 29.01 | 0.0725 | 0.48 | 13.93 | 0
June | 15 | 4AM to 5AM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
June | 15 | 5AM to 6AM | 73 | 63.9 | 59 | 76.4 | 29.47 | 0.0725 | 0.5 | 13.94 | 0
June | 15 | 6AM to 7AM | 75 | 64 | 57.9 | 73.5 | 29.49 | 0.0723 | 0.48 | 13.99 | 0
June | 15 | 7AM to 8AM | 78.1 | 63.4 | 55 | 66.1 | 29.08 | 0.0719 | 0.44 | 14.04 | 0
June | 15 | 8AM to 9AM | 79 | 63.2 | 54 | 63.5 | 28.9 | 0.0718 | 0.42 | 14.06 | 0
June | 15 | 9AM to 10AM | 82.9 | 66.1 | 57 | 71.1 | 31.06 | 0.0712 | 0.47 | 14.19 | 0
June | 15 | 10AM to 11AM | 84.9 | 67.1 | 57.9 | 73.5 | 31.91 | 0.0709 | 0.48 | 14.24 | 0
June | 15 | 11AM to 12PM | 86 | 67 | 57 | 71.1 | 31.8 | 0.0708 | 0.47 | 14.27 | 0
June | 15 | 12PM to 1PM | 88 | 68.1 | 57.9 | 73.5 | 32.66 | 0.0705 | 0.48 | 14.32 | 0
June | 15 | 1PM to 2PM | 89.1 | 68 | 57 | 71.1 | 32.55 | 0.0704 | 0.47 | 14.35 | 0
June | 15 | 2PM to 3PM | 89.1 | 68 | 57 | 71.1 | 32.55 | 0.0704 | 0.47 | 14.35 | 0
June | 15 | 3PM to 4PM | 88 | 67.6 | 57 | 71.1 | 32.29 | 0.0706 | 0.47 | 14.32 | 0
June | 15 | 4PM to 5PM | 87.1 | 67.3 | 57 | 71.1 | 32.07 | 0.0707 | 0.47 | 14.29 | 0
June | 15 | 5PM to 6PM | 86 | 67.5 | 57.9 | 73.5 | 32.18 | 0.0708 | 0.48 | 14.27 | 0
June | 15 | 6PM to 7PM | 84 | 66.9 | 57.9 | 73.5 | 31.69 | 0.0711 | 0.48 | 14.22 | 0
June | 15 | 7PM to 8PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
June | 15 | 8PM to 9PM | 79 | 65.8 | 59 | 76.4 | 30.92 | 0.0717 | 0.5 | 14.1 | 0
June | 15 | 9PM to 10PM | 78.1 | 65.6 | 59 | 76.4 | 30.7 | 0.0718 | 0.5 | 14.08 | 0
June | 15 | 10PM to 11PM | 77 | 65.2 | 59 | 76.4 | 30.44 | 0.072 | 0.5 | 14.05 | 0
June | 15 | 11PM to 12AM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
June | 16 | 12AM to 1AM | 73 | 64.5 | 60.1 | 79.5 | 29.95 | 0.0725 | 0.52 | 13.95 | 0
June | 16 | 1AM to 2AM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
June | 16 | 2AM to 3AM | 72 | 64.7 | 61 | 82.1 | 30.09 | 0.0726 | 0.54 | 13.93 | 0
June | 16 | 3AM to 4AM | 71.1 | 64.4 | 61 | 82.1 | 29.87 | 0.0727 | 0.54 | 13.91 | 0
June | 16 | 4AM to 5AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
June | 16 | 5AM to 6AM | 71.1 | 64.4 | 61 | 82.1 | 29.87 | 0.0727 | 0.54 | 13.91 | 0
June | 16 | 6AM to 7AM | 73.9 | 64.8 | 60.1 | 79.5 | 30.17 | 0.0724 | 0.52 | 13.98 | 0
June | 16 | 7AM to 8AM | 78.1 | 66.2 | 60.1 | 79.5 | 31.18 | 0.0718 | 0.52 | 14.08 | 0
June | 16 | 8AM to 9AM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
June | 16 | 9AM to 10AM | 82.9 | 68.2 | 61 | 82.1 | 32.78 | 0.0711 | 0.54 | 14.22 | 0
June | 16 | 10AM to 11AM | 84.9 | 68.8 | 61 | 82.1 | 33.27 | 0.0709 | 0.54 | 14.27 | 0
June | 16 | 11AM to 12PM | 86 | 69.1 | 61 | 82.1 | 33.53 | 0.0707 | 0.54 | 14.3 | 0
June | 16 | 12PM to 1PM | 88 | 69.7 | 61 | 82.1 | 34.02 | 0.0705 | 0.54 | 14.35 | 0
June | 16 | 1PM to 2PM | 89.1 | 70 | 61 | 82.1 | 34.29 | 0.0704 | 0.54 | 14.38 | 0
June | 16 | 2PM to 3PM | 89.1 | 69.5 | 60.1 | 79.5 | 33.87 | 0.0704 | 0.52 | 14.37 | 0
June | 16 | 3PM to 4PM | 89.1 | 70 | 61 | 82.1 | 34.29 | 0.0704 | 0.54 | 14.38 | 0
June | 16 | 4PM to 5PM | 88 | 69.7 | 61 | 82.1 | 34.02 | 0.0705 | 0.54 | 14.35 | 0
June | 16 | 5PM to 6PM | 86 | 69.7 | 62.1 | 85.4 | 34.05 | 0.0707 | 0.56 | 14.31 | 0
June | 16 | 6PM to 7PM | 84.9 | 69.4 | 62.1 | 85.4 | 33.78 | 0.0709 | 0.56 | 14.28 | 0
June | 16 | 7PM to 8PM | 82.9 | 68.8 | 62.1 | 85.4 | 33.3 | 0.0711 | 0.56 | 14.23 | 0
June | 16 | 8PM to 9PM | 82 | 68.5 | 62.1 | 85.4 | 33.08 | 0.0712 | 0.56 | 14.21 | 0
June | 16 | 9PM to 10PM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
June | 16 | 10PM to 11PM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
June | 16 | 11PM to 12AM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
June | 17 | 12AM to 1AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
June | 17 | 1AM to 2AM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
June | 17 | 2AM to 3AM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
June | 17 | 3AM to 4AM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
June | 17 | 4AM to 5AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
June | 17 | 5AM to 6AM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
June | 17 | 6AM to 7AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
June | 17 | 7AM to 8AM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
June | 17 | 8AM to 9AM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
June | 17 | 9AM to 10AM | 86 | 71.3 | 64.9 | 94.6 | 35.5 | 0.0707 | 0.62 | 14.34 | 0
June | 17 | 10AM to 11AM | 88 | 70.8 | 63 | 88.2 | 34.97 | 0.0705 | 0.58 | 14.37 | 0
June | 17 | 11AM to 12PM | 90 | 71.9 | 64 | 91.7 | 36.01 | 0.0702 | 0.6 | 14.44 | 0
June | 17 | 12PM to 1PM | 91.9 | 71.4 | 62.1 | 85.4 | 35.5 | 0.07 | 0.56 | 14.47 | 0
June | 17 | 1PM to 2PM | 91.9 | 69.8 | 59 | 76.4 | 34.1 | 0.07 | 0.5 | 14.44 | 0
June | 17 | 2PM to 3PM | 91.9 | 70.8 | 61 | 82.1 | 34.99 | 0.07 | 0.54 | 14.46 | 0
June | 17 | 3PM to 4PM | 91.9 | 70.4 | 60.1 | 79.5 | 34.58 | 0.07 | 0.52 | 14.45 | 0
June | 17 | 4PM to 5PM | 90 | 70.8 | 62.1 | 85.4 | 35.02 | 0.0702 | 0.56 | 14.42 | 0
June | 17 | 5PM to 6PM | 89.1 | 71.7 | 64 | 91.7 | 35.79 | 0.0703 | 0.6 | 14.41 | 0
June | 17 | 6PM to 7PM | 88 | 71.9 | 64.9 | 94.6 | 35.99 | 0.0704 | 0.62 | 14.39 | 0
June | 17 | 7PM to 8PM | 86 | 71.3 | 64.9 | 94.6 | 35.5 | 0.0707 | 0.62 | 14.34 | 0
June | 17 | 8PM to 9PM | 84 | 70.8 | 64.9 | 94.6 | 35.02 | 0.0709 | 0.62 | 14.29 | 0
June | 17 | 9PM to 10PM | 82.9 | 70.5 | 64.9 | 94.6 | 34.75 | 0.0711 | 0.62 | 14.26 | 0
June | 17 | 10PM to 11PM | 82 | 70.2 | 64.9 | 94.6 | 34.53 | 0.0712 | 0.62 | 14.24 | 0
June | 17 | 11PM to 12AM | 81 | 69.9 | 64.9 | 94.6 | 34.26 | 0.0713 | 0.62 | 14.21 | 0
June | 18 | 12AM to 1AM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
June | 18 | 1AM to 2AM | 79 | 69.3 | 64.9 | 94.6 | 33.78 | 0.0716 | 0.62 | 14.16 | 0
June | 18 | 2AM to 3AM | 78.1 | 69 | 64.9 | 94.6 | 33.56 | 0.0717 | 0.62 | 14.13 | 0
June | 18 | 3AM to 4AM | 75.9 | 69.1 | 66 | 98.4 | 33.6 | 0.072 | 0.64 | 14.09 | 0
June | 18 | 4AM to 5AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
June | 18 | 5AM to 6AM | 75.9 | 68.4 | 64.9 | 94.6 | 33.02 | 0.072 | 0.62 | 14.08 | 0
June | 18 | 6AM to 7AM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
June | 18 | 7AM to 8AM | 82 | 70.2 | 64.9 | 94.6 | 34.53 | 0.0712 | 0.62 | 14.24 | 0
June | 18 | 8AM to 9AM | 84 | 70.8 | 64.9 | 94.6 | 35.02 | 0.0709 | 0.62 | 14.29 | 0
June | 18 | 9AM to 10AM | 86 | 71.3 | 64.9 | 94.6 | 35.5 | 0.0707 | 0.62 | 14.34 | 0
June | 18 | 10AM to 11AM | 86 | 71.3 | 64.9 | 94.6 | 35.5 | 0.0707 | 0.62 | 14.34 | 0
June | 18 | 11AM to 12PM | 88 | 71.9 | 64.9 | 94.6 | 35.99 | 0.0704 | 0.62 | 14.39 | 0
June | 18 | 12PM to 1PM | 89.1 | 71.7 | 64 | 91.7 | 35.79 | 0.0703 | 0.6 | 14.41 | 0
June | 18 | 1PM to 2PM | 90 | 71.9 | 64 | 91.7 | 36.01 | 0.0702 | 0.6 | 14.44 | 0
June | 18 | 2PM to 3PM | 91.9 | 73 | 64.9 | 94.6 | 36.97 | 0.0699 | 0.62 | 14.5 | 0
June | 18 | 3PM to 4PM | 91.9 | 71.9 | 63 | 88.2 | 35.95 | 0.0699 | 0.58 | 14.48 | 0
June | 18 | 4PM to 5PM | 91 | 72.2 | 64 | 91.7 | 36.27 | 0.07 | 0.6 | 14.46 | 0
June | 18 | 5PM to 6PM | 90 | 71.9 | 64 | 91.7 | 36.01 | 0.0702 | 0.6 | 14.44 | 0
June | 18 | 6PM to 7PM | 88 | 71.9 | 64.9 | 94.6 | 35.99 | 0.0704 | 0.62 | 14.39 | 0
June | 18 | 7PM to 8PM | 87.1 | 70.5 | 63 | 88.2 | 34.75 | 0.0706 | 0.58 | 14.35 | 0
June | 18 | 8PM to 9PM | 84.9 | 69.4 | 62.1 | 85.4 | 33.78 | 0.0709 | 0.56 | 14.28 | 0
June | 18 | 9PM to 10PM | 82.9 | 68.8 | 62.1 | 85.4 | 33.3 | 0.0711 | 0.56 | 14.23 | 0
June | 18 | 10PM to 11PM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
June | 18 | 11PM to 12AM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
June | 19 | 12AM to 1AM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
June | 19 | 1AM to 2AM | 78.1 | 67.8 | 63 | 88.2 | 32.54 | 0.0718 | 0.58 | 14.11 | 0
June | 19 | 2AM to 3AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
June | 19 | 3AM to 4AM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
June | 19 | 4AM to 5AM | 73.9 | 66.5 | 63 | 88.2 | 31.53 | 0.0723 | 0.58 | 14 | 0
June | 19 | 5AM to 6AM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
June | 19 | 6AM to 7AM | 78.1 | 68.5 | 64 | 91.7 | 33.09 | 0.0717 | 0.6 | 14.12 | 0
June | 19 | 7AM to 8AM | 82 | 70.2 | 64.9 | 94.6 | 34.53 | 0.0712 | 0.62 | 14.24 | 0
June | 19 | 8AM to 9AM | 84.9 | 72.2 | 66.9 | 101.5 | 36.32 | 0.0708 | 0.67 | 14.34 | 0
June | 19 | 9AM to 10AM | 88 | 73.7 | 68 | 105.5 | 37.69 | 0.0704 | 0.69 | 14.43 | 0
June | 19 | 10AM to 11AM | 90 | 73.6 | 66.9 | 101.5 | 37.56 | 0.0701 | 0.67 | 14.47 | 0
June | 19 | 11AM to 12PM | 93 | 72.8 | 64 | 91.7 | 36.76 | 0.0698 | 0.6 | 14.52 | 0
June | 19 | 12PM to 1PM | 93.9 | 74.2 | 66 | 98.4 | 38.04 | 0.0696 | 0.64 | 14.56 | 0
June | 19 | 1PM to 2PM | 93.9 | 73.5 | 64.9 | 94.6 | 37.45 | 0.0697 | 0.62 | 14.55 | 0
June | 19 | 2PM to 3PM | 93 | 73.9 | 66 | 98.4 | 37.81 | 0.0698 | 0.64 | 14.54 | 0
June | 19 | 3PM to 4PM | 93 | 74.4 | 66.9 | 101.5 | 38.32 | 0.0697 | 0.67 | 14.55 | 0
June | 19 | 4PM to 5PM | 91.9 | 74.2 | 66.9 | 101.5 | 38.05 | 0.0699 | 0.67 | 14.52 | 0
June | 19 | 5PM to 6PM | 91.9 | 73.6 | 66 | 98.4 | 37.55 | 0.0699 | 0.64 | 14.51 | 0
June | 19 | 6PM to 7PM | 90 | 73.6 | 66.9 | 101.5 | 37.56 | 0.0701 | 0.67 | 14.47 | 0
June | 19 | 7PM to 8PM | 89.1 | 73.4 | 66.9 | 101.5 | 37.34 | 0.0702 | 0.67 | 14.44 | 0
June | 19 | 8PM to 9PM | 87.1 | 72.8 | 66.9 | 101.5 | 36.85 | 0.0705 | 0.67 | 14.39 | 0
June | 19 | 9PM to 10PM | 86 | 73.2 | 68 | 105.5 | 37.21 | 0.0706 | 0.69 | 14.38 | 0
June | 19 | 10PM to 11PM | 84.9 | 72.9 | 68 | 105.5 | 36.94 | 0.0707 | 0.69 | 14.35 | 0
June | 19 | 11PM to 12AM | 84.9 | 72.9 | 68 | 105.5 | 36.94 | 0.0707 | 0.69 | 14.35 | 0
June | 20 | 12AM to 1AM | 84 | 72.7 | 68 | 105.5 | 36.72 | 0.0709 | 0.69 | 14.32 | 0
June | 20 | 1AM to 2AM | 82.9 | 73 | 69.1 | 109.6 | 37.09 | 0.071 | 0.72 | 14.31 | 0
June | 20 | 2AM to 3AM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
June | 20 | 3AM to 4AM | 81 | 71.8 | 68 | 105.5 | 35.96 | 0.0713 | 0.69 | 14.24 | 0
June | 20 | 4AM to 5AM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
June | 20 | 5AM to 6AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
June | 20 | 6AM to 7AM | 77 | 70.7 | 68 | 105.5 | 34.99 | 0.0718 | 0.69 | 14.14 | 0
June | 20 | 7AM to 8AM | 82.9 | 73 | 69.1 | 109.6 | 37.09 | 0.071 | 0.72 | 14.31 | 0
June | 20 | 8AM to 9AM | 84.9 | 72.9 | 68 | 105.5 | 36.94 | 0.0707 | 0.69 | 14.35 | 0
June | 20 | 9AM to 10AM | 89.1 | 73.4 | 66.9 | 101.5 | 37.34 | 0.0702 | 0.67 | 14.44 | 0
June | 20 | 10AM to 11AM | 91 | 73.9 | 66.9 | 101.5 | 37.83 | 0.07 | 0.67 | 14.5 | 0
June | 20 | 11AM to 12PM | 91.9 | 74.8 | 68 | 105.5 | 38.67 | 0.0698 | 0.69 | 14.53 | 0
June | 20 | 12PM to 1PM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
June | 20 | 1PM to 2PM | 93.9 | 75.3 | 68 | 105.5 | 39.16 | 0.0696 | 0.69 | 14.58 | 0
June | 20 | 2PM to 3PM | 95 | 75.6 | 68 | 105.5 | 39.43 | 0.0695 | 0.69 | 14.61 | 0
June | 20 | 3PM to 4PM | 96.1 | 75.2 | 66.9 | 101.5 | 39.07 | 0.0694 | 0.67 | 14.63 | 0
June | 20 | 4PM to 5PM | 96.1 | 74.1 | 64.9 | 94.6 | 37.98 | 0.0694 | 0.62 | 14.61 | 0
June | 20 | 5PM to 6PM | 93.9 | 72.5 | 63 | 88.2 | 36.43 | 0.0697 | 0.58 | 14.53 | 0
June | 20 | 6PM to 7PM | 91.9 | 70.8 | 61 | 82.1 | 34.99 | 0.07 | 0.54 | 14.46 | 0
June | 20 | 7PM to 8PM | 87.1 | 74.7 | 70 | 113.1 | 38.67 | 0.0704 | 0.74 | 14.43 | 0
June | 20 | 8PM to 9PM | 84.9 | 72.9 | 68 | 105.5 | 36.94 | 0.0707 | 0.69 | 14.35 | 0
June | 20 | 9PM to 10PM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
June | 20 | 10PM to 11PM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
June | 20 | 11PM to 12AM | 79 | 72.5 | 70 | 113.1 | 36.66 | 0.0715 | 0.74 | 14.22 | 0
June | 21 | 12AM to 1AM | 77 | 71.4 | 69.1 | 109.6 | 35.63 | 0.0718 | 0.72 | 14.15 | 0
June | 21 | 1AM to 2AM | 80.1 | 72.2 | 69.1 | 109.6 | 36.38 | 0.0714 | 0.72 | 14.23 | 0
June | 21 | 2AM to 3AM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
June | 21 | 3AM to 4AM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
June | 21 | 4AM to 5AM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
June | 21 | 5AM to 6AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
June | 21 | 6AM to 7AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
June | 21 | 7AM to 8AM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
June | 21 | 8AM to 9AM | 84 | 68 | 60.1 | 79.5 | 32.64 | 0.071 | 0.52 | 14.24 | 0
June | 21 | 9AM to 10AM | 87.1 | 67.8 | 57.9 | 73.5 | 32.44 | 0.0707 | 0.48 | 14.3 | 0
June | 21 | 10AM to 11AM | 90 | 67.3 | 55 | 66.1 | 31.99 | 0.0703 | 0.44 | 14.35 | 0
June | 21 | 11AM to 12PM | 91.9 | 67.4 | 54 | 63.5 | 32.06 | 0.0701 | 0.42 | 14.4 | 0
June | 21 | 12PM to 1PM | 93.9 | 68.5 | 55 | 66.1 | 32.95 | 0.0698 | 0.44 | 14.46 | 0
June | 21 | 1PM to 2PM | 96.1 | 67.8 | 52 | 59 | 32.36 | 0.0696 | 0.39 | 14.49 | 0
June | 21 | 2PM to 3PM | 95 | 67.9 | 53.1 | 61.4 | 32.48 | 0.0697 | 0.41 | 14.47 | 0
June | 21 | 3PM to 4PM | 95 | 68.3 | 54 | 63.5 | 32.81 | 0.0697 | 0.42 | 14.48 | 0
June | 21 | 4PM to 5PM | 96.1 | 68.7 | 54 | 63.5 | 33.07 | 0.0696 | 0.42 | 14.5 | 0
June | 21 | 5PM to 6PM | 93 | 67.3 | 53.1 | 61.4 | 32 | 0.07 | 0.41 | 14.42 | 0
June | 21 | 6PM to 7PM | 93 | 67.7 | 54 | 63.5 | 32.32 | 0.07 | 0.42 | 14.42 | 0
June | 21 | 7PM to 8PM | 88 | 66.7 | 55 | 66.1 | 31.5 | 0.0706 | 0.44 | 14.3 | 0
June | 21 | 8PM to 9PM | 84.9 | 66.1 | 55.9 | 68.3 | 31.11 | 0.071 | 0.45 | 14.23 | 0
June | 21 | 9PM to 10PM | 82.9 | 66.5 | 57.9 | 73.5 | 31.43 | 0.0712 | 0.48 | 14.19 | 0
June | 21 | 10PM to 11PM | 78.1 | 66.2 | 60.1 | 79.5 | 31.18 | 0.0718 | 0.52 | 14.08 | 0
June | 21 | 11PM to 12AM | 81 | 66.5 | 59 | 76.4 | 31.41 | 0.0714 | 0.5 | 14.15 | 0
June | 22 | 12AM to 1AM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
June | 22 | 1AM to 2AM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
June | 22 | 2AM to 3AM | 78.1 | 68.5 | 64 | 91.7 | 33.09 | 0.0717 | 0.6 | 14.12 | 0
June | 22 | 3AM to 4AM | 77 | 68.2 | 64 | 91.7 | 32.82 | 0.0719 | 0.6 | 14.1 | 0
June | 22 | 4AM to 5AM | 75.9 | 67.8 | 64 | 91.7 | 32.56 | 0.072 | 0.6 | 14.07 | 0
June | 22 | 5AM to 6AM | 77 | 68.2 | 64 | 91.7 | 32.82 | 0.0719 | 0.6 | 14.1 | 0
June | 22 | 6AM to 7AM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
June | 22 | 7AM to 8AM | 77 | 69.4 | 66 | 98.4 | 33.87 | 0.0718 | 0.64 | 14.12 | 0
June | 22 | 8AM to 9AM | 78.1 | 69 | 64.9 | 94.6 | 33.56 | 0.0717 | 0.62 | 14.13 | 0
June | 22 | 9AM to 10AM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
June | 22 | 10AM to 11AM | 82 | 69.7 | 64 | 91.7 | 34.06 | 0.0712 | 0.6 | 14.23 | 0
June | 22 | 11AM to 12PM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
June | 22 | 12PM to 1PM | 86 | 70.2 | 63 | 88.2 | 34.49 | 0.0707 | 0.58 | 14.32 | 0
June | 22 | 1PM to 2PM | 88 | 69.7 | 61 | 82.1 | 34.02 | 0.0705 | 0.54 | 14.35 | 0
June | 22 | 2PM to 3PM | 91.9 | 70.4 | 60.1 | 79.5 | 34.58 | 0.07 | 0.52 | 14.45 | 0
June | 22 | 3PM to 4PM | 91.9 | 70.8 | 61 | 82.1 | 34.99 | 0.07 | 0.54 | 14.46 | 0
June | 22 | 4PM to 5PM | 90 | 70.3 | 61 | 82.1 | 34.51 | 0.0702 | 0.54 | 14.4 | 0
June | 22 | 5PM to 6PM | 91 | 70.1 | 60.1 | 79.5 | 34.36 | 0.0701 | 0.52 | 14.42 | 0
June | 22 | 6PM to 7PM | 89.1 | 70 | 61 | 82.1 | 34.29 | 0.0704 | 0.54 | 14.38 | 0
June | 22 | 7PM to 8PM | 84 | 69.6 | 63 | 88.2 | 34 | 0.071 | 0.58 | 14.27 | 0
June | 22 | 8PM to 9PM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
June | 22 | 9PM to 10PM | 82 | 69.7 | 64 | 91.7 | 34.06 | 0.0712 | 0.6 | 14.23 | 0
June | 22 | 10PM to 11PM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
June | 22 | 11PM to 12AM | 80.1 | 69.1 | 64 | 91.7 | 33.57 | 0.0715 | 0.6 | 14.18 | 0
June | 23 | 12AM to 1AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
June | 23 | 1AM to 2AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
June | 23 | 2AM to 3AM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
June | 23 | 3AM to 4AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
June | 23 | 4AM to 5AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
June | 23 | 5AM to 6AM | 72 | 67.2 | 64.9 | 94.6 | 32.05 | 0.0725 | 0.62 | 13.97 | 0
June | 23 | 6AM to 7AM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
June | 23 | 7AM to 8AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
June | 23 | 8AM to 9AM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
June | 23 | 9AM to 10AM | 75 | 65.7 | 61 | 82.1 | 30.84 | 0.0722 | 0.54 | 14.01 | 0
June | 23 | 10AM to 11AM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
June | 23 | 11AM to 12PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
June | 23 | 12PM to 1PM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
June | 23 | 1PM to 2PM | 81 | 67.6 | 61 | 82.1 | 32.3 | 0.0714 | 0.54 | 14.17 | 0
June | 23 | 2PM to 3PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
June | 23 | 3PM to 4PM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
June | 23 | 4PM to 5PM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
June | 23 | 5PM to 6PM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
June | 23 | 6PM to 7PM | 66 | 64 | 63 | 88.2 | 29.58 | 0.0734 | 0.58 | 13.8 | 0
June | 23 | 7PM to 8PM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
June | 23 | 8PM to 9PM | 64 | 60.8 | 59 | 76.4 | 27.26 | 0.0737 | 0.5 | 13.71 | 0
June | 23 | 9PM to 10PM | 61 | 58.5 | 57 | 71.1 | 25.69 | 0.0742 | 0.47 | 13.61 | 0
June | 23 | 10PM to 11PM | 59 | 57.1 | 55.9 | 68.3 | 24.77 | 0.0745 | 0.45 | 13.55 | 0
June | 23 | 11PM to 12AM | 55.9 | 55.9 | 55.9 | 68.3 | 24.02 | 0.075 | 0.45 | 13.47 | 0
June | 24 | 12AM to 1AM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
June | 24 | 1AM to 2AM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
June | 24 | 2AM to 3AM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
June | 24 | 3AM to 4AM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
June | 24 | 4AM to 5AM | 55 | 53.3 | 52 | 59 | 22.36 | 0.0751 | 0.39 | 13.42 | 0
June | 24 | 5AM to 6AM | 55 | 52.2 | 50 | 54.7 | 21.7 | 0.0752 | 0.36 | 13.41 | 0
June | 24 | 6AM to 7AM | 57 | 53 | 50 | 54.7 | 22.18 | 0.0749 | 0.36 | 13.46 | 0
June | 24 | 7AM to 8AM | 60.1 | 54.8 | 51.1 | 57 | 23.28 | 0.0744 | 0.38 | 13.54 | 0
June | 24 | 8AM to 9AM | 62.1 | 56.1 | 52 | 59 | 24.07 | 0.0741 | 0.39 | 13.6 | 0
June | 24 | 9AM to 10AM | 64.9 | 58.2 | 54 | 63.5 | 25.47 | 0.0737 | 0.42 | 13.69 | 0
June | 24 | 10AM to 11AM | 68 | 59.4 | 54 | 63.5 | 26.22 | 0.0733 | 0.42 | 13.77 | 0
June | 24 | 11AM to 12PM | 72 | 60.8 | 54 | 63.5 | 27.19 | 0.0727 | 0.42 | 13.87 | 0
June | 24 | 12PM to 1PM | 73.9 | 62 | 55 | 66.1 | 28.07 | 0.0724 | 0.44 | 13.93 | 0
June | 24 | 1PM to 2PM | 75 | 62.4 | 55 | 66.1 | 28.34 | 0.0723 | 0.44 | 13.96 | 0
June | 24 | 2PM to 3PM | 75 | 61.9 | 54 | 63.5 | 27.93 | 0.0723 | 0.42 | 13.95 | 0
June | 24 | 3PM to 4PM | 78.1 | 62.9 | 54 | 63.5 | 28.68 | 0.0719 | 0.42 | 14.03 | 0
June | 24 | 4PM to 5PM | 77 | 61.6 | 52 | 59 | 27.71 | 0.0721 | 0.39 | 13.99 | 0
June | 24 | 5PM to 6PM | 77 | 61.1 | 51.1 | 57 | 27.4 | 0.0721 | 0.38 | 13.99 | 0
June | 24 | 6PM to 7PM | 75 | 60.4 | 51.1 | 57 | 26.92 | 0.0724 | 0.38 | 13.93 | 0
June | 24 | 7PM to 8PM | 72 | 59.8 | 52 | 59 | 26.48 | 0.0728 | 0.39 | 13.86 | 0
June | 24 | 8PM to 9PM | 70 | 59.6 | 53.1 | 61.4 | 26.38 | 0.073 | 0.41 | 13.82 | 0
June | 24 | 9PM to 10PM | 66 | 59.7 | 55.9 | 68.3 | 26.49 | 0.0735 | 0.45 | 13.73 | 0
June | 24 | 10PM to 11PM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
June | 24 | 11PM to 12AM | 63 | 58.1 | 55 | 66.1 | 25.39 | 0.074 | 0.44 | 13.65 | 0
June | 25 | 12AM to 1AM | 61 | 57.3 | 55 | 66.1 | 24.91 | 0.0742 | 0.44 | 13.6 | 0
June | 25 | 1AM to 2AM | 60.1 | 57 | 55 | 66.1 | 24.69 | 0.0744 | 0.44 | 13.57 | 0
June | 25 | 2AM to 3AM | 60.1 | 56.4 | 54 | 63.5 | 24.29 | 0.0744 | 0.42 | 13.56 | 0
June | 25 | 3AM to 4AM | 57.9 | 55.5 | 54 | 63.5 | 23.76 | 0.0747 | 0.42 | 13.51 | 0
June | 25 | 4AM to 5AM | 57.9 | 55.5 | 54 | 63.5 | 23.76 | 0.0747 | 0.42 | 13.51 | 0
June | 25 | 5AM to 6AM | 60.1 | 57 | 55 | 66.1 | 24.69 | 0.0744 | 0.44 | 13.57 | 0
June | 25 | 6AM to 7AM | 66 | 60.3 | 57 | 71.1 | 26.92 | 0.0735 | 0.47 | 13.74 | 0
June | 25 | 7AM to 8AM | 71.1 | 61.5 | 55.9 | 68.3 | 27.72 | 0.0728 | 0.45 | 13.87 | 0
June | 25 | 8AM to 9AM | 73 | 60.7 | 53.1 | 61.4 | 27.12 | 0.0726 | 0.41 | 13.9 | 0
June | 25 | 9AM to 10AM | 73.9 | 60 | 51.1 | 57 | 26.66 | 0.0725 | 0.38 | 13.91 | 0
June | 25 | 10AM to 11AM | 75 | 59.4 | 48.9 | 52.6 | 26.22 | 0.0724 | 0.35 | 13.92 | 0
June | 25 | 11AM to 12PM | 75.9 | 59.8 | 48.9 | 52.6 | 26.44 | 0.0723 | 0.35 | 13.94 | 0
June | 25 | 12PM to 1PM | 78.1 | 60.5 | 48.9 | 52.6 | 26.97 | 0.072 | 0.35 | 14 | 0
June | 25 | 1PM to 2PM | 79 | 60.9 | 48.9 | 52.6 | 27.19 | 0.0718 | 0.35 | 14.02 | 0
June | 25 | 2PM to 3PM | 79 | 60.5 | 48 | 50.8 | 26.91 | 0.0719 | 0.34 | 14.02 | 0
June | 25 | 3PM to 4PM | 77 | 59.3 | 46.9 | 48.8 | 26.11 | 0.0721 | 0.32 | 13.96 | 0
June | 25 | 4PM to 5PM | 78.1 | 58.5 | 44.1 | 43.6 | 25.57 | 0.072 | 0.29 | 13.97 | 0
June | 25 | 5PM to 6PM | 77 | 58.5 | 45 | 45.2 | 25.55 | 0.0722 | 0.3 | 13.95 | 0
June | 25 | 6PM to 7PM | 75.9 | 60.3 | 50 | 54.7 | 26.79 | 0.0722 | 0.36 | 13.95 | 0
June | 25 | 7PM to 8PM | 73 | 59.2 | 50 | 54.7 | 26.08 | 0.0726 | 0.36 | 13.88 | 0
June | 25 | 8PM to 9PM | 69.1 | 58.7 | 52 | 59 | 25.78 | 0.0732 | 0.39 | 13.79 | 0
June | 25 | 9PM to 10PM | 66 | 58.1 | 53.1 | 61.4 | 25.41 | 0.0736 | 0.41 | 13.71 | 0
June | 25 | 10PM to 11PM | 64 | 57.4 | 53.1 | 61.4 | 24.93 | 0.0738 | 0.41 | 13.66 | 0
June | 25 | 11PM to 12AM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
June | 26 | 12AM to 1AM | 61 | 56.2 | 53.1 | 61.4 | 24.18 | 0.0743 | 0.41 | 13.58 | 0
June | 26 | 1AM to 2AM | 60.1 | 55.9 | 53.1 | 61.4 | 23.96 | 0.0744 | 0.41 | 13.56 | 0
June | 26 | 2AM to 3AM | 61 | 56.2 | 53.1 | 61.4 | 24.18 | 0.0743 | 0.41 | 13.58 | 0
June | 26 | 3AM to 4AM | 60.1 | 55.3 | 52 | 59 | 23.59 | 0.0744 | 0.39 | 13.55 | 0
June | 26 | 4AM to 5AM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
June | 26 | 5AM to 6AM | 60.1 | 56.4 | 54 | 63.5 | 24.29 | 0.0744 | 0.42 | 13.56 | 0
June | 26 | 6AM to 7AM | 68 | 58.9 | 53.1 | 61.4 | 25.89 | 0.0733 | 0.41 | 13.76 | 0
June | 26 | 7AM to 8AM | 72 | 59.3 | 51.1 | 57 | 26.18 | 0.0728 | 0.38 | 13.85 | 0
June | 26 | 8AM to 9AM | 75 | 60.4 | 51.1 | 57 | 26.92 | 0.0724 | 0.38 | 13.93 | 0
June | 26 | 9AM to 10AM | 78.1 | 61 | 50 | 54.7 | 27.31 | 0.072 | 0.36 | 14.01 | 0
June | 26 | 10AM to 11AM | 79 | 60.9 | 48.9 | 52.6 | 27.19 | 0.0718 | 0.35 | 14.02 | 0
June | 26 | 11AM to 12PM | 81 | 60.7 | 46.9 | 48.8 | 27.07 | 0.0716 | 0.32 | 14.06 | 0
June | 26 | 12PM to 1PM | 82 | 61.1 | 46.9 | 48.8 | 27.33 | 0.0715 | 0.32 | 14.09 | 0
June | 26 | 1PM to 2PM | 84 | 61.4 | 46 | 47.1 | 27.56 | 0.0712 | 0.31 | 14.14 | 0
June | 26 | 2PM to 3PM | 84.9 | 62.1 | 46.9 | 48.8 | 28.03 | 0.0711 | 0.32 | 14.17 | 0
June | 26 | 3PM to 4PM | 84.9 | 62.1 | 46.9 | 48.8 | 28.03 | 0.0711 | 0.32 | 14.17 | 0
June | 26 | 4PM to 5PM | 84.9 | 62.1 | 46.9 | 48.8 | 28.03 | 0.0711 | 0.32 | 14.17 | 0
June | 26 | 5PM to 6PM | 84 | 62.2 | 48 | 50.8 | 28.14 | 0.0712 | 0.34 | 14.15 | 0
June | 26 | 6PM to 7PM | 82 | 61.1 | 46.9 | 48.8 | 27.33 | 0.0715 | 0.32 | 14.09 | 0
June | 26 | 7PM to 8PM | 80.1 | 60.8 | 48 | 50.8 | 27.17 | 0.0717 | 0.34 | 14.05 | 0
June | 26 | 8PM to 9PM | 78.1 | 59.7 | 46.9 | 48.8 | 26.37 | 0.072 | 0.32 | 13.99 | 0
June | 26 | 9PM to 10PM | 75.9 | 59.8 | 48.9 | 52.6 | 26.44 | 0.0723 | 0.35 | 13.94 | 0
June | 26 | 10PM to 11PM | 73.9 | 59 | 48.9 | 52.6 | 25.96 | 0.0725 | 0.35 | 13.89 | 0
June | 26 | 11PM to 12AM | 72 | 59.8 | 52 | 59 | 26.48 | 0.0728 | 0.39 | 13.86 | 0
June | 27 | 12AM to 1AM | 70 | 59.6 | 53.1 | 61.4 | 26.38 | 0.073 | 0.41 | 13.82 | 0
June | 27 | 1AM to 2AM | 69.1 | 59.8 | 54 | 63.5 | 26.48 | 0.0731 | 0.42 | 13.8 | 0
June | 27 | 2AM to 3AM | 69.1 | 59.8 | 54 | 63.5 | 26.48 | 0.0731 | 0.42 | 13.8 | 0
June | 27 | 3AM to 4AM | 68 | 59.4 | 54 | 63.5 | 26.22 | 0.0733 | 0.42 | 13.77 | 0
June | 27 | 4AM to 5AM | 66.9 | 59 | 54 | 63.5 | 25.96 | 0.0734 | 0.42 | 13.74 | 0
June | 27 | 5AM to 6AM | 69.1 | 59.8 | 54 | 63.5 | 26.48 | 0.0731 | 0.42 | 13.8 | 0
June | 27 | 6AM to 7AM | 71.1 | 61 | 55 | 66.1 | 27.37 | 0.0728 | 0.44 | 13.86 | 0
June | 27 | 7AM to 8AM | 73 | 62.2 | 55.9 | 68.3 | 28.2 | 0.0726 | 0.45 | 13.92 | 0
June | 27 | 8AM to 9AM | 75.9 | 63.2 | 55.9 | 68.3 | 28.91 | 0.0722 | 0.45 | 13.99 | 0
June | 27 | 9AM to 10AM | 79 | 64.2 | 55.9 | 68.3 | 29.65 | 0.0718 | 0.45 | 14.07 | 0
June | 27 | 10AM to 11AM | 81 | 65.4 | 57 | 71.1 | 30.57 | 0.0715 | 0.47 | 14.13 | 0
June | 27 | 11AM to 12PM | 82.9 | 66.5 | 57.9 | 73.5 | 31.43 | 0.0712 | 0.48 | 14.19 | 0
June | 27 | 12PM to 1PM | 84 | 65.8 | 55.9 | 68.3 | 30.89 | 0.0711 | 0.45 | 14.2 | 0
June | 27 | 1PM to 2PM | 86 | 66.5 | 55.9 | 68.3 | 31.37 | 0.0708 | 0.45 | 14.26 | 0
June | 27 | 2PM to 3PM | 86 | 66.5 | 55.9 | 68.3 | 31.37 | 0.0708 | 0.45 | 14.26 | 0
June | 27 | 3PM to 4PM | 84.9 | 66.7 | 57 | 71.1 | 31.54 | 0.071 | 0.47 | 14.24 | 0
June | 27 | 4PM to 5PM | 82.9 | 67.1 | 59 | 76.4 | 31.89 | 0.0712 | 0.5 | 14.2 | 0
June | 27 | 5PM to 6PM | 82 | 66.2 | 57.9 | 73.5 | 31.21 | 0.0713 | 0.48 | 14.17 | 0
June | 27 | 6PM to 7PM | 80.1 | 66.2 | 59 | 76.4 | 31.19 | 0.0716 | 0.5 | 14.13 | 0
June | 27 | 7PM to 8PM | 80.1 | 66.2 | 59 | 76.4 | 31.19 | 0.0716 | 0.5 | 14.13 | 0
June | 27 | 8PM to 9PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
June | 27 | 9PM to 10PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
June | 27 | 10PM to 11PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
June | 27 | 11PM to 12AM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
June | 28 | 12AM to 1AM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
June | 28 | 1AM to 2AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
June | 28 | 2AM to 3AM | 72 | 65.4 | 62.1 | 85.4 | 30.6 | 0.0726 | 0.56 | 13.94 | 0
June | 28 | 3AM to 4AM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
June | 28 | 4AM to 5AM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
June | 28 | 5AM to 6AM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
June | 28 | 6AM to 7AM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
June | 28 | 7AM to 8AM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
June | 28 | 8AM to 9AM | 79 | 68.1 | 63 | 88.2 | 32.76 | 0.0716 | 0.58 | 14.14 | 0
June | 28 | 9AM to 10AM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
June | 28 | 10AM to 11AM | 79 | 69.3 | 64.9 | 94.6 | 33.78 | 0.0716 | 0.62 | 14.16 | 0
June | 28 | 11AM to 12PM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
June | 28 | 12PM to 1PM | 72 | 69.9 | 69.1 | 109.6 | 34.38 | 0.0724 | 0.72 | 14.02 | 0
June | 28 | 1PM to 2PM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
June | 28 | 2PM to 3PM | 72 | 68.5 | 66.9 | 101.5 | 33.13 | 0.0725 | 0.67 | 13.99 | 0
June | 28 | 3PM to 4PM | 72 | 69.2 | 68 | 105.5 | 33.74 | 0.0725 | 0.69 | 14.01 | 0
June | 28 | 4PM to 5PM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
June | 28 | 5PM to 6PM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
June | 28 | 6PM to 7PM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
June | 28 | 7PM to 8PM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
June | 28 | 8PM to 9PM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
June | 28 | 9PM to 10PM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
June | 28 | 10PM to 11PM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
June | 28 | 11PM to 12AM | 69.1 | 67.6 | 66.9 | 101.5 | 32.42 | 0.0729 | 0.67 | 13.92 | 0
June | 29 | 12AM to 1AM | 68 | 66.6 | 66 | 98.4 | 31.65 | 0.0731 | 0.64 | 13.88 | 0
June | 29 | 1AM to 2AM | 68 | 66.6 | 66 | 98.4 | 31.65 | 0.0731 | 0.64 | 13.88 | 0
June | 29 | 2AM to 3AM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
June | 29 | 3AM to 4AM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
June | 29 | 4AM to 5AM | 64.9 | 64.3 | 64 | 91.7 | 29.86 | 0.0735 | 0.6 | 13.78 | 0
June | 29 | 5AM to 6AM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
June | 29 | 6AM to 7AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
June | 29 | 7AM to 8AM | 71.1 | 67.6 | 66 | 98.4 | 32.41 | 0.0726 | 0.64 | 13.96 | 0
June | 29 | 8AM to 9AM | 73 | 68.8 | 66.9 | 101.5 | 33.39 | 0.0723 | 0.67 | 14.02 | 0
June | 29 | 9AM to 10AM | 73.9 | 69.1 | 66.9 | 101.5 | 33.61 | 0.0722 | 0.67 | 14.05 | 0
June | 29 | 10AM to 11AM | 78.1 | 71 | 68 | 105.5 | 35.25 | 0.0716 | 0.69 | 14.17 | 0
June | 29 | 11AM to 12PM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
June | 29 | 12PM to 1PM | 84 | 72 | 66.9 | 101.5 | 36.1 | 0.0709 | 0.67 | 14.31 | 0
June | 29 | 1PM to 2PM | 86 | 68.6 | 60.1 | 79.5 | 33.12 | 0.0708 | 0.52 | 14.29 | 0
June | 29 | 2PM to 3PM | 84.9 | 68.8 | 61 | 82.1 | 33.27 | 0.0709 | 0.54 | 14.27 | 0
June | 29 | 3PM to 4PM | 82.9 | 68.2 | 61 | 82.1 | 32.78 | 0.0711 | 0.54 | 14.22 | 0
June | 29 | 4PM to 5PM | 81 | 68.2 | 62.1 | 85.4 | 32.81 | 0.0714 | 0.56 | 14.18 | 0
June | 29 | 5PM to 6PM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
June | 29 | 6PM to 7PM | 79 | 67 | 61 | 82.1 | 31.81 | 0.0717 | 0.54 | 14.12 | 0
June | 29 | 7PM to 8PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
June | 29 | 8PM to 9PM | 73.9 | 65.4 | 61 | 82.1 | 30.58 | 0.0723 | 0.54 | 13.98 | 0
June | 29 | 9PM to 10PM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
June | 29 | 10PM to 11PM | 71.1 | 64.4 | 61 | 82.1 | 29.87 | 0.0727 | 0.54 | 13.91 | 0
June | 29 | 11PM to 12AM | 70 | 63.5 | 60.1 | 79.5 | 29.2 | 0.0729 | 0.52 | 13.87 | 0
June | 30 | 12AM to 1AM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
June | 30 | 1AM to 2AM | 66 | 62.2 | 60.1 | 79.5 | 28.23 | 0.0735 | 0.52 | 13.77 | 0
June | 30 | 2AM to 3AM | 64.9 | 61.8 | 60.1 | 79.5 | 27.96 | 0.0736 | 0.52 | 13.74 | 0
June | 30 | 3AM to 4AM | 64 | 61.5 | 60.1 | 79.5 | 27.74 | 0.0737 | 0.52 | 13.72 | 0
June | 30 | 4AM to 5AM | 64 | 61.5 | 60.1 | 79.5 | 27.74 | 0.0737 | 0.52 | 13.72 | 0
June | 30 | 5AM to 6AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
June | 30 | 6AM to 7AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
June | 30 | 7AM to 8AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
June | 30 | 8AM to 9AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
June | 30 | 9AM to 10AM | 78.1 | 67.8 | 63 | 88.2 | 32.54 | 0.0718 | 0.58 | 14.11 | 0
June | 30 | 10AM to 11AM | 81 | 67.6 | 61 | 82.1 | 32.3 | 0.0714 | 0.54 | 14.17 | 0
June | 30 | 11AM to 12PM | 82.9 | 67.7 | 60.1 | 79.5 | 32.37 | 0.0712 | 0.52 | 14.21 | 0
June | 30 | 12PM to 1PM | 84.9 | 68.3 | 60.1 | 79.5 | 32.86 | 0.0709 | 0.52 | 14.26 | 0
June | 30 | 1PM to 2PM | 86 | 68.6 | 60.1 | 79.5 | 33.12 | 0.0708 | 0.52 | 14.29 | 0
June | 30 | 2PM to 3PM | 87.1 | 68.4 | 59 | 76.4 | 32.91 | 0.0706 | 0.5 | 14.31 | 0
June | 30 | 3PM to 4PM | 87.1 | 68.4 | 59 | 76.4 | 32.91 | 0.0706 | 0.5 | 14.31 | 0
June | 30 | 4PM to 5PM | 87.1 | 67.8 | 57.9 | 73.5 | 32.44 | 0.0707 | 0.48 | 14.3 | 0
June | 30 | 5PM to 6PM | 86 | 68 | 59 | 76.4 | 32.64 | 0.0708 | 0.5 | 14.28 | 0
June | 30 | 6PM to 7PM | 84 | 67.4 | 59 | 76.4 | 32.16 | 0.071 | 0.5 | 14.23 | 0
June | 30 | 7PM to 8PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
June | 30 | 8PM to 9PM | 78.1 | 66.2 | 60.1 | 79.5 | 31.18 | 0.0718 | 0.52 | 14.08 | 0
June | 30 | 9PM to 10PM | 78.4 | 66.9 | 61.2 | 82.6 | 31.76 | 0.0717 | 0.54 | 14.1 | 0
June | 30 | 10PM to 11PM | 78.6 | 67.7 | 62.4 | 86.5 | 32.41 | 0.0717 | 0.57 | 14.12 | 0
June | 30 | 11PM to 12AM | 79 | 68.4 | 63.5 | 89.9 | 33.03 | 0.0716 | 0.59 | 14.14 | 0
July | 1 | 12AM to 1AM | 79.2 | 69.1 | 64.6 | 93.4 | 33.63 | 0.0716 | 0.61 | 14.16 | 0
July | 1 | 1AM to 2AM | 79.5 | 69.9 | 65.7 | 97.1 | 34.29 | 0.0715 | 0.64 | 14.18 | 0
July | 1 | 2AM to 3AM | 79.7 | 70.8 | 66.9 | 101.5 | 35.03 | 0.0715 | 0.67 | 14.2 | 0
July | 1 | 3AM to 4AM | 80.1 | 71.5 | 68 | 105.5 | 35.74 | 0.0714 | 0.69 | 14.22 | 0
July | 1 | 4AM to 5AM | 80.1 | 71.5 | 68 | 105.5 | 35.74 | 0.0714 | 0.69 | 14.22 | 0
July | 1 | 5AM to 6AM | 82 | 72.1 | 68 | 105.5 | 36.23 | 0.0711 | 0.69 | 14.27 | 0
July | 1 | 6AM to 7AM | 84 | 72.7 | 68 | 105.5 | 36.72 | 0.0709 | 0.69 | 14.32 | 0
July | 1 | 7AM to 8AM | 84.9 | 72.9 | 68 | 105.5 | 36.94 | 0.0707 | 0.69 | 14.35 | 0
July | 1 | 8AM to 9AM | 87.1 | 74.2 | 69.1 | 109.6 | 38.11 | 0.0704 | 0.72 | 14.42 | 0
July | 1 | 9AM to 10AM | 90 | 74.9 | 69.1 | 109.6 | 38.83 | 0.0701 | 0.72 | 14.49 | 0
July | 1 | 10AM to 11AM | 91.9 | 76 | 70 | 113.1 | 39.87 | 0.0698 | 0.74 | 14.56 | 0
July | 1 | 11AM to 12PM | 95 | 75.6 | 68 | 105.5 | 39.43 | 0.0695 | 0.69 | 14.61 | 0
July | 1 | 12PM to 1PM | 98.1 | 76.4 | 68 | 105.5 | 40.18 | 0.0691 | 0.69 | 14.69 | 0
July | 1 | 1PM to 2PM | 99 | 76.6 | 68 | 105.5 | 40.4 | 0.069 | 0.69 | 14.72 | 0
July | 1 | 2PM to 3PM | 99 | 76 | 66.9 | 101.5 | 39.78 | 0.069 | 0.67 | 14.7 | 0
July | 1 | 3PM to 4PM | 99 | 76 | 66.9 | 101.5 | 39.78 | 0.069 | 0.67 | 14.7 | 0
July | 1 | 4PM to 5PM | 97 | 75.5 | 66.9 | 101.5 | 39.29 | 0.0692 | 0.67 | 14.65 | 0
July | 1 | 5PM to 6PM | 96.1 | 75.9 | 68 | 105.5 | 39.69 | 0.0693 | 0.69 | 14.64 | 0
July | 1 | 6PM to 7PM | 93.9 | 76.5 | 70 | 113.1 | 40.36 | 0.0696 | 0.74 | 14.61 | 0
July | 1 | 7PM to 8PM | 91 | 76.5 | 71.1 | 117.4 | 40.33 | 0.0699 | 0.77 | 14.55 | 0
July | 1 | 8PM to 9PM | 89.1 | 75.9 | 71.1 | 117.4 | 39.84 | 0.0701 | 0.77 | 14.5 | 0
July | 1 | 9PM to 10PM | 88 | 75.7 | 71.1 | 117.4 | 39.57 | 0.0703 | 0.77 | 14.47 | 0
July | 1 | 10PM to 11PM | 86 | 75.2 | 71.1 | 117.4 | 39.08 | 0.0705 | 0.77 | 14.41 | 0
July | 1 | 11PM to 12AM | 84.9 | 74.9 | 71.1 | 117.4 | 38.82 | 0.0707 | 0.77 | 14.39 | 0
July | 2 | 12AM to 1AM | 82.9 | 74.3 | 71.1 | 117.4 | 38.33 | 0.0709 | 0.77 | 14.33 | 0
July | 2 | 1AM to 2AM | 82.9 | 74.3 | 71.1 | 117.4 | 38.33 | 0.0709 | 0.77 | 14.33 | 0
July | 2 | 2AM to 3AM | 82.9 | 74.3 | 71.1 | 117.4 | 38.33 | 0.0709 | 0.77 | 14.33 | 0
July | 2 | 3AM to 4AM | 81 | 73.8 | 71.1 | 117.4 | 37.84 | 0.0712 | 0.77 | 14.28 | 0
July | 2 | 4AM to 5AM | 80.1 | 73.6 | 71.1 | 117.4 | 37.61 | 0.0713 | 0.77 | 14.26 | 0
July | 2 | 5AM to 6AM | 81 | 73.8 | 71.1 | 117.4 | 37.84 | 0.0712 | 0.77 | 14.28 | 0
July | 2 | 6AM to 7AM | 78.1 | 75 | 73.9 | 129.8 | 39.06 | 0.0715 | 0.85 | 14.24 | 0
July | 2 | 7AM to 8AM | 79 | 71.9 | 69.1 | 109.6 | 36.11 | 0.0715 | 0.72 | 14.2 | 0
July | 2 | 8AM to 9AM | 73 | 72.3 | 72 | 121.2 | 36.46 | 0.0722 | 0.79 | 14.08 | 0
July | 2 | 9AM to 10AM | 72 | 69.9 | 69.1 | 109.6 | 34.38 | 0.0724 | 0.72 | 14.02 | 0
July | 2 | 10AM to 11AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
July | 2 | 11AM to 12PM | 80.1 | 74.2 | 72 | 121.2 | 38.2 | 0.0713 | 0.79 | 14.27 | 0
July | 2 | 12PM to 1PM | 82 | 73.4 | 70 | 113.1 | 37.42 | 0.0711 | 0.74 | 14.3 | 0
July | 2 | 1PM to 2PM | 86 | 73.9 | 69.1 | 109.6 | 37.85 | 0.0706 | 0.72 | 14.39 | 0
July | 2 | 2PM to 3PM | 89.1 | 75.3 | 70 | 113.1 | 39.16 | 0.0702 | 0.74 | 14.48 | 0
July | 2 | 3PM to 4PM | 89.1 | 74 | 68 | 105.5 | 37.96 | 0.0702 | 0.69 | 14.46 | 0
July | 2 | 4PM to 5PM | 89.1 | 74 | 68 | 105.5 | 37.96 | 0.0702 | 0.69 | 14.46 | 0
July | 2 | 5PM to 6PM | 89.1 | 74.7 | 69.1 | 109.6 | 38.6 | 0.0702 | 0.72 | 14.47 | 0
July | 2 | 6PM to 7PM | 87.1 | 74.2 | 69.1 | 109.6 | 38.11 | 0.0704 | 0.72 | 14.42 | 0
July | 2 | 7PM to 8PM | 84.9 | 72.2 | 66.9 | 101.5 | 36.32 | 0.0708 | 0.67 | 14.34 | 0
July | 2 | 8PM to 9PM | 84 | 73.3 | 69.1 | 109.6 | 37.36 | 0.0708 | 0.72 | 14.34 | 0
July | 2 | 9PM to 10PM | 80.1 | 73.6 | 71.1 | 117.4 | 37.61 | 0.0713 | 0.77 | 14.26 | 0
July | 2 | 10PM to 11PM | 79 | 73.3 | 71.1 | 117.4 | 37.35 | 0.0715 | 0.77 | 14.23 | 0
July | 2 | 11PM to 12AM | 78.1 | 73.6 | 72 | 121.2 | 37.71 | 0.0716 | 0.79 | 14.22 | 0
July | 3 | 12AM to 1AM | 78.1 | 73.6 | 72 | 121.2 | 37.71 | 0.0716 | 0.79 | 14.22 | 0
July | 3 | 1AM to 2AM | 77 | 73.4 | 72 | 121.2 | 37.44 | 0.0717 | 0.79 | 14.19 | 0
July | 3 | 2AM to 3AM | 75.9 | 73.1 | 72 | 121.2 | 37.17 | 0.0718 | 0.79 | 14.16 | 0
July | 3 | 3AM to 4AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
July | 3 | 4AM to 5AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
July | 3 | 5AM to 6AM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
July | 3 | 6AM to 7AM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
July | 3 | 7AM to 8AM | 84.9 | 71.7 | 66 | 98.4 | 35.82 | 0.0708 | 0.64 | 14.32 | 0
July | 3 | 8AM to 9AM | 88 | 68.6 | 59 | 76.4 | 33.13 | 0.0705 | 0.5 | 14.33 | 0
July | 3 | 9AM to 10AM | 90 | 68.7 | 57.9 | 73.5 | 33.15 | 0.0703 | 0.48 | 14.38 | 0
July | 3 | 10AM to 11AM | 91.9 | 68.3 | 55.9 | 68.3 | 32.82 | 0.0701 | 0.45 | 14.41 | 0
July | 3 | 11AM to 12PM | 91.9 | 68.8 | 57 | 71.1 | 33.26 | 0.07 | 0.47 | 14.42 | 0
July | 3 | 12PM to 1PM | 93 | 68.6 | 55.9 | 68.3 | 33.08 | 0.0699 | 0.45 | 14.44 | 0
July | 3 | 1PM to 2PM | 93 | 69.2 | 57 | 71.1 | 33.52 | 0.0699 | 0.47 | 14.45 | 0
July | 3 | 2PM to 3PM | 91 | 69 | 57.9 | 73.5 | 33.41 | 0.0701 | 0.48 | 14.4 | 0
July | 3 | 3PM to 4PM | 72 | 69.2 | 68 | 105.5 | 33.74 | 0.0725 | 0.69 | 14.01 | 0
July | 3 | 4PM to 5PM | 73 | 68.8 | 66.9 | 101.5 | 33.39 | 0.0723 | 0.67 | 14.02 | 0
July | 3 | 5PM to 6PM | 77 | 70 | 66.9 | 101.5 | 34.37 | 0.0718 | 0.67 | 14.13 | 0
July | 3 | 6PM to 7PM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
July | 3 | 7PM to 8PM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
July | 3 | 8PM to 9PM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
July | 3 | 9PM to 10PM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
July | 3 | 10PM to 11PM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
July | 3 | 11PM to 12AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
July | 4 | 12AM to 1AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
July | 4 | 1AM to 2AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
July | 4 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
July | 4 | 3AM to 4AM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
July | 4 | 4AM to 5AM | 66.9 | 65 | 64 | 91.7 | 30.34 | 0.0733 | 0.6 | 13.83 | 0
July | 4 | 5AM to 6AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
July | 4 | 6AM to 7AM | 72 | 67.2 | 64.9 | 94.6 | 32.05 | 0.0725 | 0.62 | 13.97 | 0
July | 4 | 7AM to 8AM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
July | 4 | 8AM to 9AM | 80.1 | 70.3 | 66 | 98.4 | 34.62 | 0.0714 | 0.64 | 14.2 | 0
July | 4 | 9AM to 10AM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
July | 4 | 10AM to 11AM | 84 | 68.5 | 61 | 82.1 | 33.05 | 0.071 | 0.54 | 14.25 | 0
July | 4 | 11AM to 12PM | 87.1 | 71.1 | 64 | 91.7 | 35.3 | 0.0705 | 0.6 | 14.36 | 0
July | 4 | 12PM to 1PM | 84 | 70.2 | 64 | 91.7 | 34.55 | 0.0709 | 0.6 | 14.28 | 0
July | 4 | 1PM to 2PM | 88 | 69.2 | 60.1 | 79.5 | 33.61 | 0.0705 | 0.52 | 14.34 | 0
July | 4 | 2PM to 3PM | 90 | 69.2 | 59 | 76.4 | 33.61 | 0.0703 | 0.5 | 14.39 | 0
July | 4 | 3PM to 4PM | 90 | 68.7 | 57.9 | 73.5 | 33.15 | 0.0703 | 0.48 | 14.38 | 0
July | 4 | 4PM to 5PM | 88 | 68.6 | 59 | 76.4 | 33.13 | 0.0705 | 0.5 | 14.33 | 0
July | 4 | 5PM to 6PM | 87.1 | 67.8 | 57.9 | 73.5 | 32.44 | 0.0707 | 0.48 | 14.3 | 0
July | 4 | 6PM to 7PM | 86 | 68 | 59 | 76.4 | 32.64 | 0.0708 | 0.5 | 14.28 | 0
July | 4 | 7PM to 8PM | 82 | 67.4 | 60.1 | 79.5 | 32.15 | 0.0713 | 0.52 | 14.19 | 0
July | 4 | 8PM to 9PM | 81 | 67.6 | 61 | 82.1 | 32.3 | 0.0714 | 0.54 | 14.17 | 0
July | 4 | 9PM to 10PM | 79 | 67 | 61 | 82.1 | 31.81 | 0.0717 | 0.54 | 14.12 | 0
July | 4 | 10PM to 11PM | 77 | 65.8 | 60.1 | 79.5 | 30.92 | 0.0719 | 0.52 | 14.06 | 0
July | 4 | 11PM to 12AM | 75.9 | 65.5 | 60.1 | 79.5 | 30.65 | 0.0721 | 0.52 | 14.03 | 0
July | 5 | 12AM to 1AM | 75.9 | 65.5 | 60.1 | 79.5 | 30.65 | 0.0721 | 0.52 | 14.03 | 0
July | 5 | 1AM to 2AM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
July | 5 | 2AM to 3AM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
July | 5 | 3AM to 4AM | 75.9 | 65.5 | 60.1 | 79.5 | 30.65 | 0.0721 | 0.52 | 14.03 | 0
July | 5 | 4AM to 5AM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
July | 5 | 5AM to 6AM | 75.9 | 66.6 | 62.1 | 85.4 | 31.57 | 0.0721 | 0.56 | 14.05 | 0
July | 5 | 6AM to 7AM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
July | 5 | 7AM to 8AM | 82 | 70.2 | 64.9 | 94.6 | 34.53 | 0.0712 | 0.62 | 14.24 | 0
July | 5 | 8AM to 9AM | 84 | 72 | 66.9 | 101.5 | 36.1 | 0.0709 | 0.67 | 14.31 | 0
July | 5 | 9AM to 10AM | 87.1 | 73.5 | 68 | 105.5 | 37.47 | 0.0705 | 0.69 | 14.4 | 0
July | 5 | 10AM to 11AM | 89.1 | 74 | 68 | 105.5 | 37.96 | 0.0702 | 0.69 | 14.46 | 0
July | 5 | 11AM to 12PM | 91.9 | 74.8 | 68 | 105.5 | 38.67 | 0.0698 | 0.69 | 14.53 | 0
July | 5 | 12PM to 1PM | 93 | 75.1 | 68 | 105.5 | 38.94 | 0.0697 | 0.69 | 14.56 | 0
July | 5 | 1PM to 2PM | 93.9 | 74.2 | 66 | 98.4 | 38.04 | 0.0696 | 0.64 | 14.56 | 0
July | 5 | 2PM to 3PM | 93.9 | 73.5 | 64.9 | 94.6 | 37.45 | 0.0697 | 0.62 | 14.55 | 0
July | 5 | 3PM to 4PM | 95 | 74.4 | 66 | 98.4 | 38.3 | 0.0695 | 0.64 | 14.59 | 0
July | 5 | 4PM to 5PM | 93.9 | 73.5 | 64.9 | 94.6 | 37.45 | 0.0697 | 0.62 | 14.55 | 0
July | 5 | 5PM to 6PM | 93.9 | 74.2 | 66 | 98.4 | 38.04 | 0.0696 | 0.64 | 14.56 | 0
July | 5 | 6PM to 7PM | 93 | 73.9 | 66 | 98.4 | 37.81 | 0.0698 | 0.64 | 14.54 | 0
July | 5 | 7PM to 8PM | 91 | 72.8 | 64.9 | 94.6 | 36.74 | 0.07 | 0.62 | 14.47 | 0
July | 5 | 8PM to 9PM | 89.1 | 72.8 | 66 | 98.4 | 36.84 | 0.0703 | 0.64 | 14.43 | 0
July | 5 | 9PM to 10PM | 87.1 | 72.8 | 66.9 | 101.5 | 36.85 | 0.0705 | 0.67 | 14.39 | 0
July | 5 | 10PM to 11PM | 84.9 | 71 | 64.9 | 94.6 | 35.24 | 0.0708 | 0.62 | 14.31 | 0
July | 5 | 11PM to 12AM | 84 | 70.8 | 64.9 | 94.6 | 35.02 | 0.0709 | 0.62 | 14.29 | 0
July | 6 | 12AM to 1AM | 82 | 70.9 | 66 | 98.4 | 35.11 | 0.0712 | 0.64 | 14.25 | 0
July | 6 | 1AM to 2AM | 81 | 70.6 | 66 | 98.4 | 34.84 | 0.0713 | 0.64 | 14.22 | 0
July | 6 | 2AM to 3AM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
July | 6 | 3AM to 4AM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
July | 6 | 4AM to 5AM | 79 | 70.5 | 66.9 | 101.5 | 34.86 | 0.0716 | 0.67 | 14.18 | 0
July | 6 | 5AM to 6AM | 79 | 70.5 | 66.9 | 101.5 | 34.86 | 0.0716 | 0.67 | 14.18 | 0
July | 6 | 6AM to 7AM | 82 | 72.1 | 68 | 105.5 | 36.23 | 0.0711 | 0.69 | 14.27 | 0
July | 6 | 7AM to 8AM | 84.9 | 72.9 | 68 | 105.5 | 36.94 | 0.0707 | 0.69 | 14.35 | 0
July | 6 | 8AM to 9AM | 87.1 | 74.2 | 69.1 | 109.6 | 38.11 | 0.0704 | 0.72 | 14.42 | 0
July | 6 | 9AM to 10AM | 90 | 74.9 | 69.1 | 109.6 | 38.83 | 0.0701 | 0.72 | 14.49 | 0
July | 6 | 10AM to 11AM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
July | 6 | 11AM to 12PM | 95 | 74.4 | 66 | 98.4 | 38.3 | 0.0695 | 0.64 | 14.59 | 0
July | 6 | 12PM to 1PM | 97 | 76.1 | 68 | 105.5 | 39.92 | 0.0692 | 0.69 | 14.67 | 0
July | 6 | 1PM to 2PM | 98.1 | 74.7 | 64.9 | 94.6 | 38.47 | 0.0691 | 0.62 | 14.66 | 0
July | 6 | 2PM to 3PM | 99 | 73.8 | 63 | 88.2 | 37.67 | 0.0691 | 0.58 | 14.66 | 0
July | 6 | 3PM to 4PM | 100 | 73.1 | 61 | 82.1 | 36.98 | 0.069 | 0.54 | 14.67 | 0
July | 6 | 4PM to 5PM | 98.1 | 73.1 | 62.1 | 85.4 | 37.01 | 0.0692 | 0.56 | 14.63 | 0
July | 6 | 5PM to 6PM | 97 | 71.8 | 60.1 | 79.5 | 35.81 | 0.0694 | 0.52 | 14.58 | 0
July | 6 | 6PM to 7PM | 93.9 | 70.9 | 60.1 | 79.5 | 35.06 | 0.0697 | 0.52 | 14.5 | 0
July | 6 | 7PM to 8PM | 91.9 | 71.4 | 62.1 | 85.4 | 35.5 | 0.07 | 0.56 | 14.47 | 0
July | 6 | 8PM to 9PM | 90 | 71.3 | 63 | 88.2 | 35.46 | 0.0702 | 0.58 | 14.42 | 0
July | 6 | 9PM to 10PM | 88 | 71.4 | 64 | 91.7 | 35.52 | 0.0704 | 0.6 | 14.38 | 0
July | 6 | 10PM to 11PM | 86 | 72 | 66 | 98.4 | 36.09 | 0.0706 | 0.64 | 14.35 | 0
July | 6 | 11PM to 12AM | 84 | 72.7 | 68 | 105.5 | 36.72 | 0.0709 | 0.69 | 14.32 | 0
July | 7 | 12AM to 1AM | 82 | 72.1 | 68 | 105.5 | 36.23 | 0.0711 | 0.69 | 14.27 | 0
July | 7 | 1AM to 2AM | 81 | 71.8 | 68 | 105.5 | 35.96 | 0.0713 | 0.69 | 14.24 | 0
July | 7 | 2AM to 3AM | 81 | 72.5 | 69.1 | 109.6 | 36.6 | 0.0712 | 0.72 | 14.26 | 0
July | 7 | 3AM to 4AM | 79 | 71.9 | 69.1 | 109.6 | 36.11 | 0.0715 | 0.72 | 14.2 | 0
July | 7 | 4AM to 5AM | 79 | 71.9 | 69.1 | 109.6 | 36.11 | 0.0715 | 0.72 | 14.2 | 0
July | 7 | 5AM to 6AM | 79 | 71.9 | 69.1 | 109.6 | 36.11 | 0.0715 | 0.72 | 14.2 | 0
July | 7 | 6AM to 7AM | 82 | 73.4 | 70 | 113.1 | 37.42 | 0.0711 | 0.74 | 14.3 | 0
July | 7 | 7AM to 8AM | 84.9 | 74.2 | 70 | 113.1 | 38.13 | 0.0707 | 0.74 | 14.37 | 0
July | 7 | 8AM to 9AM | 88 | 75.7 | 71.1 | 117.4 | 39.57 | 0.0703 | 0.77 | 14.47 | 0
July | 7 | 9AM to 10AM | 90 | 76.2 | 71.1 | 117.4 | 40.06 | 0.07 | 0.77 | 14.52 | 0
July | 7 | 10AM to 11AM | 91.9 | 76.7 | 71.1 | 117.4 | 40.55 | 0.0698 | 0.77 | 14.57 | 0
July | 7 | 11AM to 12PM | 95 | 76.2 | 69.1 | 109.6 | 40.07 | 0.0694 | 0.72 | 14.63 | 0
July | 7 | 12PM to 1PM | 97 | 73.9 | 64 | 91.7 | 37.73 | 0.0693 | 0.6 | 14.62 | 0
July | 7 | 1PM to 2PM | 96.1 | 74.1 | 64.9 | 94.6 | 37.98 | 0.0694 | 0.62 | 14.61 | 0
July | 7 | 2PM to 3PM | 99 | 75.5 | 66 | 98.4 | 39.28 | 0.069 | 0.64 | 14.69 | 0
July | 7 | 3PM to 4PM | 99 | 76 | 66.9 | 101.5 | 39.78 | 0.069 | 0.67 | 14.7 | 0
July | 7 | 4PM to 5PM | 97 | 75.5 | 66.9 | 101.5 | 39.29 | 0.0692 | 0.67 | 14.65 | 0
July | 7 | 5PM to 6PM | 97 | 75.5 | 66.9 | 101.5 | 39.29 | 0.0692 | 0.67 | 14.65 | 0
July | 7 | 6PM to 7PM | 93.9 | 75.3 | 68 | 105.5 | 39.16 | 0.0696 | 0.69 | 14.58 | 0
July | 7 | 7PM to 8PM | 91.9 | 74.8 | 68 | 105.5 | 38.67 | 0.0698 | 0.69 | 14.53 | 0
July | 7 | 8PM to 9PM | 90 | 74.3 | 68 | 105.5 | 38.18 | 0.0701 | 0.69 | 14.48 | 0
July | 7 | 9PM to 10PM | 89.1 | 73.4 | 66.9 | 101.5 | 37.34 | 0.0702 | 0.67 | 14.44 | 0
July | 7 | 10PM to 11PM | 88 | 73.1 | 66.9 | 101.5 | 37.07 | 0.0704 | 0.67 | 14.42 | 0
July | 7 | 11PM to 12AM | 86 | 73.2 | 68 | 105.5 | 37.21 | 0.0706 | 0.69 | 14.38 | 0
July | 8 | 12AM to 1AM | 84 | 73.3 | 69.1 | 109.6 | 37.36 | 0.0708 | 0.72 | 14.34 | 0
July | 8 | 1AM to 2AM | 82.9 | 73.6 | 70 | 113.1 | 37.64 | 0.071 | 0.74 | 14.32 | 0
July | 8 | 2AM to 3AM | 82 | 74.1 | 71.1 | 117.4 | 38.1 | 0.0711 | 0.77 | 14.31 | 0
July | 8 | 3AM to 4AM | 81 | 74.4 | 72 | 121.2 | 38.42 | 0.0712 | 0.79 | 14.29 | 0
July | 8 | 4AM to 5AM | 80.1 | 74.2 | 72 | 121.2 | 38.2 | 0.0713 | 0.79 | 14.27 | 0
July | 8 | 5AM to 6AM | 80.1 | 73.6 | 71.1 | 117.4 | 37.61 | 0.0713 | 0.77 | 14.26 | 0
July | 8 | 6AM to 7AM | 79 | 71.2 | 68 | 105.5 | 35.47 | 0.0715 | 0.69 | 14.19 | 0
July | 8 | 7AM to 8AM | 82 | 72.1 | 68 | 105.5 | 36.23 | 0.0711 | 0.69 | 14.27 | 0
July | 8 | 8AM to 9AM | 82 | 72.1 | 68 | 105.5 | 36.23 | 0.0711 | 0.69 | 14.27 | 0
July | 8 | 9AM to 10AM | 84.9 | 73.6 | 69.1 | 109.6 | 37.58 | 0.0707 | 0.72 | 14.36 | 0
July | 8 | 10AM to 11AM | 87.1 | 73.5 | 68 | 105.5 | 37.47 | 0.0705 | 0.69 | 14.4 | 0
July | 8 | 11AM to 12PM | 88 | 73.7 | 68 | 105.5 | 37.69 | 0.0704 | 0.69 | 14.43 | 0
July | 8 | 12PM to 1PM | 91 | 74.6 | 68 | 105.5 | 38.45 | 0.07 | 0.69 | 14.51 | 0
July | 8 | 1PM to 2PM | 91 | 73.9 | 66.9 | 101.5 | 37.83 | 0.07 | 0.67 | 14.5 | 0
July | 8 | 2PM to 3PM | 91.9 | 74.8 | 68 | 105.5 | 38.67 | 0.0698 | 0.69 | 14.53 | 0
July | 8 | 3PM to 4PM | 91.9 | 73.6 | 66 | 98.4 | 37.55 | 0.0699 | 0.64 | 14.51 | 0
July | 8 | 4PM to 5PM | 91 | 72.8 | 64.9 | 94.6 | 36.74 | 0.07 | 0.62 | 14.47 | 0
July | 8 | 5PM to 6PM | 90 | 71.9 | 64 | 91.7 | 36.01 | 0.0702 | 0.6 | 14.44 | 0
July | 8 | 6PM to 7PM | 86 | 72 | 66 | 98.4 | 36.09 | 0.0706 | 0.64 | 14.35 | 0
July | 8 | 7PM to 8PM | 84 | 70.8 | 64.9 | 94.6 | 35.02 | 0.0709 | 0.62 | 14.29 | 0
July | 8 | 8PM to 9PM | 82.9 | 69.9 | 64 | 91.7 | 34.28 | 0.0711 | 0.6 | 14.25 | 0
July | 8 | 9PM to 10PM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
July | 8 | 10PM to 11PM | 80.1 | 68.4 | 63 | 88.2 | 33.03 | 0.0715 | 0.58 | 14.16 | 0
July | 8 | 11PM to 12AM | 79 | 69.3 | 64.9 | 94.6 | 33.78 | 0.0716 | 0.62 | 14.16 | 0
July | 9 | 12AM to 1AM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
July | 9 | 1AM to 2AM | 77 | 69.4 | 66 | 98.4 | 33.87 | 0.0718 | 0.64 | 14.12 | 0
July | 9 | 2AM to 3AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
July | 9 | 3AM to 4AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
July | 9 | 4AM to 5AM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
July | 9 | 5AM to 6AM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
July | 9 | 6AM to 7AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
July | 9 | 7AM to 8AM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
July | 9 | 8AM to 9AM | 71.1 | 68.9 | 68 | 105.5 | 33.52 | 0.0726 | 0.69 | 13.98 | 0
July | 9 | 9AM to 10AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
July | 9 | 10AM to 11AM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
July | 9 | 11AM to 12PM | 81 | 70.6 | 66 | 98.4 | 34.84 | 0.0713 | 0.64 | 14.22 | 0
July | 9 | 12PM to 1PM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
July | 9 | 1PM to 2PM | 84.9 | 69.9 | 63 | 88.2 | 34.22 | 0.0709 | 0.58 | 14.29 | 0
July | 9 | 2PM to 3PM | 86 | 71.3 | 64.9 | 94.6 | 35.5 | 0.0707 | 0.62 | 14.34 | 0
July | 9 | 3PM to 4PM | 86 | 72.5 | 66.9 | 101.5 | 36.59 | 0.0706 | 0.67 | 14.36 | 0
July | 9 | 4PM to 5PM | 84.9 | 73.6 | 69.1 | 109.6 | 37.58 | 0.0707 | 0.72 | 14.36 | 0
July | 9 | 5PM to 6PM | 84 | 75.2 | 72 | 121.2 | 39.18 | 0.0708 | 0.79 | 14.37 | 0
July | 9 | 6PM to 7PM | 82.9 | 75.7 | 73 | 125.8 | 39.64 | 0.0709 | 0.82 | 14.36 | 0
July | 9 | 7PM to 8PM | 77 | 74.1 | 73 | 125.8 | 38.17 | 0.0717 | 0.82 | 14.2 | 0
July | 9 | 8PM to 9PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
July | 9 | 9PM to 10PM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
July | 9 | 10PM to 11PM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
July | 9 | 11PM to 12AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
July | 10 | 12AM to 1AM | 71.1 | 69.7 | 69.1 | 109.6 | 34.16 | 0.0726 | 0.72 | 14 | 0
July | 10 | 1AM to 2AM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
July | 10 | 2AM to 3AM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
July | 10 | 3AM to 4AM | 71.1 | 68.9 | 68 | 105.5 | 33.52 | 0.0726 | 0.69 | 13.98 | 0
July | 10 | 4AM to 5AM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
July | 10 | 5AM to 6AM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
July | 10 | 6AM to 7AM | 69.1 | 68.3 | 68 | 105.5 | 33.03 | 0.0729 | 0.69 | 13.93 | 0
July | 10 | 7AM to 8AM | 69.1 | 69.1 | 69.1 | 109.6 | 33.67 | 0.0728 | 0.72 | 13.94 | 0
July | 10 | 8AM to 9AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
July | 10 | 9AM to 10AM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
July | 10 | 10AM to 11AM | 77 | 72 | 70 | 113.1 | 36.18 | 0.0717 | 0.74 | 14.16 | 0
July | 10 | 11AM to 12PM | 80.1 | 72.8 | 70 | 113.1 | 36.93 | 0.0713 | 0.74 | 14.24 | 0
July | 10 | 12PM to 1PM | 81 | 73.8 | 71.1 | 117.4 | 37.84 | 0.0712 | 0.77 | 14.28 | 0
July | 10 | 1PM to 2PM | 82 | 74.7 | 72 | 121.2 | 38.69 | 0.071 | 0.79 | 14.32 | 0
July | 10 | 2PM to 3PM | 84 | 75.2 | 72 | 121.2 | 39.18 | 0.0708 | 0.79 | 14.37 | 0
July | 10 | 3PM to 4PM | 84.9 | 74.9 | 71.1 | 117.4 | 38.82 | 0.0707 | 0.77 | 14.39 | 0
July | 10 | 4PM to 5PM | 84 | 73.9 | 70 | 113.1 | 37.91 | 0.0708 | 0.74 | 14.35 | 0
July | 10 | 5PM to 6PM | 84 | 74.6 | 71.1 | 117.4 | 38.59 | 0.0708 | 0.77 | 14.36 | 0
July | 10 | 6PM to 7PM | 82.9 | 73.6 | 70 | 113.1 | 37.64 | 0.071 | 0.74 | 14.32 | 0
July | 10 | 7PM to 8PM | 81 | 73.8 | 71.1 | 117.4 | 37.84 | 0.0712 | 0.77 | 14.28 | 0
July | 10 | 8PM to 9PM | 79 | 74.6 | 73 | 125.8 | 38.66 | 0.0714 | 0.82 | 14.26 | 0
July | 10 | 9PM to 10PM | 79 | 73.9 | 72 | 121.2 | 37.93 | 0.0714 | 0.79 | 14.24 | 0
July | 10 | 10PM to 11PM | 78.1 | 73.6 | 72 | 121.2 | 37.71 | 0.0716 | 0.79 | 14.22 | 0
July | 10 | 11PM to 12AM | 78.1 | 73.6 | 72 | 121.2 | 37.71 | 0.0716 | 0.79 | 14.22 | 0
July | 11 | 12AM to 1AM | 77 | 74.1 | 73 | 125.8 | 38.17 | 0.0717 | 0.82 | 14.2 | 0
July | 11 | 1AM to 2AM | 73.9 | 73.3 | 73 | 125.8 | 37.41 | 0.0721 | 0.82 | 14.12 | 0
July | 11 | 2AM to 3AM | 73.9 | 73.3 | 73 | 125.8 | 37.41 | 0.0721 | 0.82 | 14.12 | 0
July | 11 | 3AM to 4AM | 72 | 71.3 | 71.1 | 117.4 | 35.61 | 0.0724 | 0.77 | 14.04 | 0
July | 11 | 4AM to 5AM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
July | 11 | 5AM to 6AM | 70 | 69.3 | 69.1 | 109.6 | 33.89 | 0.0727 | 0.72 | 13.97 | 0
July | 11 | 6AM to 7AM | 71.1 | 69.7 | 69.1 | 109.6 | 34.16 | 0.0726 | 0.72 | 14 | 0
July | 11 | 7AM to 8AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
July | 11 | 8AM to 9AM | 77 | 71.4 | 69.1 | 109.6 | 35.63 | 0.0718 | 0.72 | 14.15 | 0
July | 11 | 9AM to 10AM | 80.1 | 72.8 | 70 | 113.1 | 36.93 | 0.0713 | 0.74 | 14.24 | 0
July | 11 | 10AM to 11AM | 82.9 | 74.3 | 71.1 | 117.4 | 38.33 | 0.0709 | 0.77 | 14.33 | 0
July | 11 | 11AM to 12PM | 84.9 | 75.5 | 72 | 121.2 | 39.4 | 0.0707 | 0.79 | 14.4 | 0
July | 11 | 12PM to 1PM | 87.1 | 76.7 | 73 | 125.8 | 40.67 | 0.0703 | 0.82 | 14.47 | 0
July | 11 | 1PM to 2PM | 89.1 | 77.8 | 73.9 | 129.8 | 41.78 | 0.0701 | 0.85 | 14.54 | 0
July | 11 | 2PM to 3PM | 91.9 | 78 | 73 | 125.8 | 41.87 | 0.0697 | 0.82 | 14.6 | 0
July | 11 | 3PM to 4PM | 91.9 | 78 | 73 | 125.8 | 41.87 | 0.0697 | 0.82 | 14.6 | 0
July | 11 | 4PM to 5PM | 91.9 | 79.3 | 75 | 134.7 | 43.27 | 0.0697 | 0.88 | 14.63 | 0
July | 11 | 5PM to 6PM | 91 | 77.7 | 73 | 125.8 | 41.65 | 0.0698 | 0.82 | 14.57 | 0
July | 11 | 6PM to 7PM | 89.1 | 77.2 | 73 | 125.8 | 41.16 | 0.0701 | 0.82 | 14.52 | 0
July | 11 | 7PM to 8PM | 87.1 | 77.3 | 73.9 | 129.8 | 41.29 | 0.0703 | 0.85 | 14.48 | 0
July | 11 | 8PM to 9PM | 78.1 | 73 | 71.1 | 117.4 | 37.12 | 0.0716 | 0.77 | 14.21 | 0
July | 11 | 9PM to 10PM | 78.1 | 73 | 71.1 | 117.4 | 37.12 | 0.0716 | 0.77 | 14.21 | 0
July | 11 | 10PM to 11PM | 73.9 | 72.5 | 72 | 121.2 | 36.68 | 0.0721 | 0.79 | 14.11 | 0
July | 11 | 11PM to 12AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
July | 12 | 12AM to 1AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
July | 12 | 1AM to 2AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
July | 12 | 2AM to 3AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
July | 12 | 3AM to 4AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
July | 12 | 4AM to 5AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
July | 12 | 5AM to 6AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
July | 12 | 6AM to 7AM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
July | 12 | 7AM to 8AM | 77 | 73.4 | 72 | 121.2 | 37.44 | 0.0717 | 0.79 | 14.19 | 0
July | 12 | 8AM to 9AM | 80.1 | 74.9 | 73 | 125.8 | 38.93 | 0.0713 | 0.82 | 14.28 | 0
July | 12 | 9AM to 10AM | 82.9 | 74.9 | 72 | 121.2 | 38.91 | 0.0709 | 0.79 | 14.35 | 0
July | 12 | 10AM to 11AM | 84.9 | 75.5 | 72 | 121.2 | 39.4 | 0.0707 | 0.79 | 14.4 | 0
July | 12 | 11AM to 12PM | 88 | 75 | 70 | 113.1 | 38.89 | 0.0703 | 0.74 | 14.45 | 0
July | 12 | 12PM to 1PM | 91 | 75.2 | 69.1 | 109.6 | 39.09 | 0.0699 | 0.72 | 14.52 | 0
July | 12 | 1PM to 2PM | 91.9 | 73 | 64.9 | 94.6 | 36.97 | 0.0699 | 0.62 | 14.5 | 0
July | 12 | 2PM to 3PM | 93 | 73.3 | 64.9 | 94.6 | 37.23 | 0.0698 | 0.62 | 14.53 | 0
July | 12 | 3PM to 4PM | 93.9 | 73 | 64 | 91.7 | 36.98 | 0.0697 | 0.6 | 14.54 | 0
July | 12 | 4PM to 5PM | 91.9 | 72.5 | 64 | 91.7 | 36.49 | 0.0699 | 0.6 | 14.49 | 0
July | 12 | 5PM to 6PM | 91 | 71.6 | 63 | 88.2 | 35.73 | 0.0701 | 0.58 | 14.45 | 0
July | 12 | 6PM to 7PM | 87.1 | 72.8 | 66.9 | 101.5 | 36.85 | 0.0705 | 0.67 | 14.39 | 0
July | 12 | 7PM to 8PM | 84 | 73.3 | 69.1 | 109.6 | 37.36 | 0.0708 | 0.72 | 14.34 | 0
July | 12 | 8PM to 9PM | 84 | 73.3 | 69.1 | 109.6 | 37.36 | 0.0708 | 0.72 | 14.34 | 0
July | 12 | 9PM to 10PM | 82.9 | 72.4 | 68 | 105.5 | 36.45 | 0.071 | 0.69 | 14.3 | 0
July | 12 | 10PM to 11PM | 81 | 72.5 | 69.1 | 109.6 | 36.6 | 0.0712 | 0.72 | 14.26 | 0
July | 12 | 11PM to 12AM | 80.1 | 71.5 | 68 | 105.5 | 35.74 | 0.0714 | 0.69 | 14.22 | 0
July | 13 | 12AM to 1AM | 78.1 | 71.7 | 69.1 | 109.6 | 35.89 | 0.0716 | 0.72 | 14.18 | 0
July | 13 | 1AM to 2AM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
July | 13 | 2AM to 3AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
July | 13 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
July | 13 | 4AM to 5AM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
July | 13 | 5AM to 6AM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
July | 13 | 6AM to 7AM | 77 | 70 | 66.9 | 101.5 | 34.37 | 0.0718 | 0.67 | 14.13 | 0
July | 13 | 7AM to 8AM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
July | 13 | 8AM to 9AM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
July | 13 | 9AM to 10AM | 82.9 | 68.2 | 61 | 82.1 | 32.78 | 0.0711 | 0.54 | 14.22 | 0
July | 13 | 10AM to 11AM | 84 | 68 | 60.1 | 79.5 | 32.64 | 0.071 | 0.52 | 14.24 | 0
July | 13 | 11AM to 12PM | 86 | 69.7 | 62.1 | 85.4 | 34.05 | 0.0707 | 0.56 | 14.31 | 0
July | 13 | 12PM to 1PM | 86 | 69.7 | 62.1 | 85.4 | 34.05 | 0.0707 | 0.56 | 14.31 | 0
July | 13 | 1PM to 2PM | 86 | 69.7 | 62.1 | 85.4 | 34.05 | 0.0707 | 0.56 | 14.31 | 0
July | 13 | 2PM to 3PM | 84.9 | 70.5 | 64 | 91.7 | 34.77 | 0.0708 | 0.6 | 14.3 | 0
July | 13 | 3PM to 4PM | 84.9 | 70.5 | 64 | 91.7 | 34.77 | 0.0708 | 0.6 | 14.3 | 0
July | 13 | 4PM to 5PM | 84 | 70.8 | 64.9 | 94.6 | 35.02 | 0.0709 | 0.62 | 14.29 | 0
July | 13 | 5PM to 6PM | 81 | 70.6 | 66 | 98.4 | 34.84 | 0.0713 | 0.64 | 14.22 | 0
July | 13 | 6PM to 7PM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
July | 13 | 7PM to 8PM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
July | 13 | 8PM to 9PM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
July | 13 | 9PM to 10PM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
July | 13 | 10PM to 11PM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
July | 13 | 11PM to 12AM | 72 | 67.2 | 64.9 | 94.6 | 32.05 | 0.0725 | 0.62 | 13.97 | 0
July | 14 | 12AM to 1AM | 71.1 | 66.9 | 64.9 | 94.6 | 31.83 | 0.0727 | 0.62 | 13.95 | 0
July | 14 | 1AM to 2AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
July | 14 | 2AM to 3AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
July | 14 | 3AM to 4AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
July | 14 | 4AM to 5AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
July | 14 | 5AM to 6AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
July | 14 | 6AM to 7AM | 73.9 | 64.8 | 60.1 | 79.5 | 30.17 | 0.0724 | 0.52 | 13.98 | 0
July | 14 | 7AM to 8AM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
July | 14 | 8AM to 9AM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
July | 14 | 9AM to 10AM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
July | 14 | 10AM to 11AM | 80.1 | 66.8 | 60.1 | 79.5 | 31.67 | 0.0715 | 0.52 | 14.14 | 0
July | 14 | 11AM to 12PM | 82 | 68.5 | 62.1 | 85.4 | 33.08 | 0.0712 | 0.56 | 14.21 | 0
July | 14 | 12PM to 1PM | 82.9 | 68.2 | 61 | 82.1 | 32.78 | 0.0711 | 0.54 | 14.22 | 0
July | 14 | 1PM to 2PM | 84 | 68.5 | 61 | 82.1 | 33.05 | 0.071 | 0.54 | 14.25 | 0
July | 14 | 2PM to 3PM | 82.9 | 67.7 | 60.1 | 79.5 | 32.37 | 0.0712 | 0.52 | 14.21 | 0
July | 14 | 3PM to 4PM | 84 | 68.5 | 61 | 82.1 | 33.05 | 0.071 | 0.54 | 14.25 | 0
July | 14 | 4PM to 5PM | 84 | 69.1 | 62.1 | 85.4 | 33.56 | 0.071 | 0.56 | 14.26 | 0
July | 14 | 5PM to 6PM | 82.9 | 68.8 | 62.1 | 85.4 | 33.3 | 0.0711 | 0.56 | 14.23 | 0
July | 14 | 6PM to 7PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
July | 14 | 7PM to 8PM | 78.1 | 67.3 | 62.1 | 85.4 | 32.1 | 0.0718 | 0.56 | 14.1 | 0
July | 14 | 8PM to 9PM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
July | 14 | 9PM to 10PM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
July | 14 | 10PM to 11PM | 73.9 | 66.5 | 63 | 88.2 | 31.53 | 0.0723 | 0.58 | 14 | 0
July | 14 | 11PM to 12AM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
July | 15 | 12AM to 1AM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
July | 15 | 1AM to 2AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
July | 15 | 2AM to 3AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
July | 15 | 3AM to 4AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
July | 15 | 4AM to 5AM | 68 | 64.1 | 62.1 | 85.4 | 29.63 | 0.0731 | 0.56 | 13.84 | 0
July | 15 | 5AM to 6AM | 69.1 | 63.2 | 60.1 | 79.5 | 28.98 | 0.073 | 0.52 | 13.85 | 0
July | 15 | 6AM to 7AM | 73.9 | 64.2 | 59 | 76.4 | 29.69 | 0.0724 | 0.5 | 13.97 | 0
July | 15 | 7AM to 8AM | 79 | 65.3 | 57.9 | 73.5 | 30.46 | 0.0717 | 0.48 | 14.09 | 0
July | 15 | 8AM to 9AM | 80.1 | 65.1 | 57 | 71.1 | 30.35 | 0.0716 | 0.47 | 14.11 | 0
July | 15 | 9AM to 10AM | 82.9 | 65.5 | 55.9 | 68.3 | 30.62 | 0.0712 | 0.45 | 14.18 | 0
July | 15 | 10AM to 11AM | 84 | 64.9 | 54 | 63.5 | 30.13 | 0.0711 | 0.42 | 14.19 | 0
July | 15 | 11AM to 12PM | 84.9 | 65.7 | 55 | 66.1 | 30.75 | 0.071 | 0.44 | 14.22 | 0
July | 15 | 12PM to 1PM | 86 | 65.1 | 53.1 | 61.4 | 30.28 | 0.0709 | 0.41 | 14.23 | 0
July | 15 | 1PM to 2PM | 84.9 | 64.3 | 52 | 59 | 29.64 | 0.071 | 0.39 | 14.2 | 0
July | 15 | 2PM to 3PM | 87.1 | 65.4 | 53.1 | 61.4 | 30.55 | 0.0707 | 0.41 | 14.26 | 0
July | 15 | 3PM to 4PM | 87.1 | 65.9 | 54 | 63.5 | 30.88 | 0.0707 | 0.42 | 14.27 | 0
July | 15 | 4PM to 5PM | 87.1 | 66.8 | 55.9 | 68.3 | 31.63 | 0.0707 | 0.45 | 14.28 | 0
July | 15 | 5PM to 6PM | 84.9 | 66.7 | 57 | 71.1 | 31.54 | 0.071 | 0.47 | 14.24 | 0
July | 15 | 6PM to 7PM | 82.9 | 66.1 | 57 | 71.1 | 31.06 | 0.0712 | 0.47 | 14.19 | 0
July | 15 | 7PM to 8PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
July | 15 | 8PM to 9PM | 79 | 68.1 | 63 | 88.2 | 32.76 | 0.0716 | 0.58 | 14.14 | 0
July | 15 | 9PM to 10PM | 78.1 | 67.8 | 63 | 88.2 | 32.54 | 0.0718 | 0.58 | 14.11 | 0
July | 15 | 10PM to 11PM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
July | 15 | 11PM to 12AM | 75.9 | 67.8 | 64 | 91.7 | 32.56 | 0.072 | 0.6 | 14.07 | 0
July | 16 | 12AM to 1AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
July | 16 | 1AM to 2AM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
July | 16 | 2AM to 3AM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
July | 16 | 3AM to 4AM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
July | 16 | 4AM to 5AM | 71.1 | 66.3 | 64 | 91.7 | 31.36 | 0.0727 | 0.6 | 13.94 | 0
July | 16 | 5AM to 6AM | 71.1 | 66.3 | 64 | 91.7 | 31.36 | 0.0727 | 0.6 | 13.94 | 0
July | 16 | 6AM to 7AM | 77 | 68.2 | 64 | 91.7 | 32.82 | 0.0719 | 0.6 | 14.1 | 0
July | 16 | 7AM to 8AM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
July | 16 | 8AM to 9AM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
July | 16 | 9AM to 10AM | 82.9 | 65.5 | 55.9 | 68.3 | 30.62 | 0.0712 | 0.45 | 14.18 | 0
July | 16 | 10AM to 11AM | 88 | 68.1 | 57.9 | 73.5 | 32.66 | 0.0705 | 0.48 | 14.32 | 0
July | 16 | 11AM to 12PM | 87.1 | 67.3 | 57 | 71.1 | 32.07 | 0.0707 | 0.47 | 14.29 | 0
July | 16 | 12PM to 1PM | 87.1 | 67.8 | 57.9 | 73.5 | 32.44 | 0.0707 | 0.48 | 14.3 | 0
July | 16 | 1PM to 2PM | 89.1 | 69 | 59 | 76.4 | 33.39 | 0.0704 | 0.5 | 14.36 | 0
July | 16 | 2PM to 3PM | 89.1 | 69 | 59 | 76.4 | 33.39 | 0.0704 | 0.5 | 14.36 | 0
July | 16 | 3PM to 4PM | 89.1 | 69.5 | 60.1 | 79.5 | 33.87 | 0.0704 | 0.52 | 14.37 | 0
July | 16 | 4PM to 5PM | 88 | 69.7 | 61 | 82.1 | 34.02 | 0.0705 | 0.54 | 14.35 | 0
July | 16 | 5PM to 6PM | 86 | 69.1 | 61 | 82.1 | 33.53 | 0.0707 | 0.54 | 14.3 | 0
July | 16 | 6PM to 7PM | 84.9 | 68.3 | 60.1 | 79.5 | 32.86 | 0.0709 | 0.52 | 14.26 | 0
July | 16 | 7PM to 8PM | 82.9 | 66.5 | 57.9 | 73.5 | 31.43 | 0.0712 | 0.48 | 14.19 | 0
July | 16 | 8PM to 9PM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
July | 16 | 9PM to 10PM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
July | 16 | 10PM to 11PM | 78.1 | 67.8 | 63 | 88.2 | 32.54 | 0.0718 | 0.58 | 14.11 | 0
July | 16 | 11PM to 12AM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
July | 17 | 12AM to 1AM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
July | 17 | 1AM to 2AM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
July | 17 | 2AM to 3AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
July | 17 | 3AM to 4AM | 71.1 | 66.3 | 64 | 91.7 | 31.36 | 0.0727 | 0.6 | 13.94 | 0
July | 17 | 4AM to 5AM | 71.1 | 66.3 | 64 | 91.7 | 31.36 | 0.0727 | 0.6 | 13.94 | 0
July | 17 | 5AM to 6AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
July | 17 | 6AM to 7AM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
July | 17 | 7AM to 8AM | 81 | 68.2 | 62.1 | 85.4 | 32.81 | 0.0714 | 0.56 | 14.18 | 0
July | 17 | 8AM to 9AM | 82.9 | 69.3 | 63 | 88.2 | 33.74 | 0.0711 | 0.58 | 14.24 | 0
July | 17 | 9AM to 10AM | 86 | 71.3 | 64.9 | 94.6 | 35.5 | 0.0707 | 0.62 | 14.34 | 0
July | 17 | 10AM to 11AM | 89.1 | 72.2 | 64.9 | 94.6 | 36.26 | 0.0703 | 0.62 | 14.42 | 0
July | 17 | 11AM to 12PM | 90 | 68.7 | 57.9 | 73.5 | 33.15 | 0.0703 | 0.48 | 14.38 | 0
July | 17 | 12PM to 1PM | 91 | 71.2 | 62.1 | 85.4 | 35.28 | 0.0701 | 0.56 | 14.44 | 0
July | 17 | 1PM to 2PM | 91.9 | 70.4 | 60.1 | 79.5 | 34.58 | 0.07 | 0.52 | 14.45 | 0
July | 17 | 2PM to 3PM | 91.9 | 69.8 | 59 | 76.4 | 34.1 | 0.07 | 0.5 | 14.44 | 0
July | 17 | 3PM to 4PM | 91.9 | 70.4 | 60.1 | 79.5 | 34.58 | 0.07 | 0.52 | 14.45 | 0
July | 17 | 4PM to 5PM | 91 | 70.6 | 61 | 82.1 | 34.77 | 0.0701 | 0.54 | 14.43 | 0
July | 17 | 5PM to 6PM | 90 | 70.8 | 62.1 | 85.4 | 35.02 | 0.0702 | 0.56 | 14.42 | 0
July | 17 | 6PM to 7PM | 86 | 70.2 | 63 | 88.2 | 34.49 | 0.0707 | 0.58 | 14.32 | 0
July | 17 | 7PM to 8PM | 84 | 71.4 | 66 | 98.4 | 35.6 | 0.0709 | 0.64 | 14.3 | 0
July | 17 | 8PM to 9PM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
July | 17 | 9PM to 10PM | 81 | 71.8 | 68 | 105.5 | 35.96 | 0.0713 | 0.69 | 14.24 | 0
July | 17 | 10PM to 11PM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
July | 17 | 11PM to 12AM | 79 | 70 | 66 | 98.4 | 34.36 | 0.0716 | 0.64 | 14.17 | 0
July | 18 | 12AM to 1AM | 78.1 | 69.7 | 66 | 98.4 | 34.14 | 0.0717 | 0.64 | 14.14 | 0
July | 18 | 1AM to 2AM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
July | 18 | 2AM to 3AM | 75.9 | 68.4 | 64.9 | 94.6 | 33.02 | 0.072 | 0.62 | 14.08 | 0
July | 18 | 3AM to 4AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
July | 18 | 4AM to 5AM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
July | 18 | 5AM to 6AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
July | 18 | 6AM to 7AM | 78.1 | 69 | 64.9 | 94.6 | 33.56 | 0.0717 | 0.62 | 14.13 | 0
July | 18 | 7AM to 8AM | 81 | 69.9 | 64.9 | 94.6 | 34.26 | 0.0713 | 0.62 | 14.21 | 0
July | 18 | 8AM to 9AM | 86 | 72 | 66 | 98.4 | 36.09 | 0.0706 | 0.64 | 14.35 | 0
July | 18 | 9AM to 10AM | 88 | 73.1 | 66.9 | 101.5 | 37.07 | 0.0704 | 0.67 | 14.42 | 0
July | 18 | 10AM to 11AM | 91.9 | 73 | 64.9 | 94.6 | 36.97 | 0.0699 | 0.62 | 14.5 | 0
July | 18 | 11AM to 12PM | 91 | 72.8 | 64.9 | 94.6 | 36.74 | 0.07 | 0.62 | 14.47 | 0
July | 18 | 12PM to 1PM | 93 | 72.8 | 64 | 91.7 | 36.76 | 0.0698 | 0.6 | 14.52 | 0
July | 18 | 1PM to 2PM | 93.9 | 74.7 | 66.9 | 101.5 | 38.54 | 0.0696 | 0.67 | 14.57 | 0
July | 18 | 2PM to 3PM | 91.9 | 71.9 | 63 | 88.2 | 35.95 | 0.0699 | 0.58 | 14.48 | 0
July | 18 | 3PM to 4PM | 93 | 72.2 | 63 | 88.2 | 36.21 | 0.0698 | 0.58 | 14.5 | 0
July | 18 | 4PM to 5PM | 93 | 72.2 | 63 | 88.2 | 36.21 | 0.0698 | 0.58 | 14.5 | 0
July | 18 | 5PM to 6PM | 91 | 72.2 | 64 | 91.7 | 36.27 | 0.07 | 0.6 | 14.46 | 0
July | 18 | 6PM to 7PM | 89.1 | 73.4 | 66.9 | 101.5 | 37.34 | 0.0702 | 0.67 | 14.44 | 0
July | 18 | 7PM to 8PM | 87.1 | 72.8 | 66.9 | 101.5 | 36.85 | 0.0705 | 0.67 | 14.39 | 0
July | 18 | 8PM to 9PM | 84.9 | 72.2 | 66.9 | 101.5 | 36.32 | 0.0708 | 0.67 | 14.34 | 0
July | 18 | 9PM to 10PM | 84 | 72 | 66.9 | 101.5 | 36.1 | 0.0709 | 0.67 | 14.31 | 0
July | 18 | 10PM to 11PM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
July | 18 | 11PM to 12AM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
July | 19 | 12AM to 1AM | 81 | 71.1 | 66.9 | 101.5 | 35.34 | 0.0713 | 0.67 | 14.23 | 0
July | 19 | 1AM to 2AM | 79 | 70.5 | 66.9 | 101.5 | 34.86 | 0.0716 | 0.67 | 14.18 | 0
July | 19 | 2AM to 3AM | 78.1 | 70.3 | 66.9 | 101.5 | 34.63 | 0.0717 | 0.67 | 14.15 | 0
July | 19 | 3AM to 4AM | 78.1 | 69.7 | 66 | 98.4 | 34.14 | 0.0717 | 0.64 | 14.14 | 0
July | 19 | 4AM to 5AM | 77 | 69.4 | 66 | 98.4 | 33.87 | 0.0718 | 0.64 | 14.12 | 0
July | 19 | 5AM to 6AM | 78.1 | 70.3 | 66.9 | 101.5 | 34.63 | 0.0717 | 0.67 | 14.15 | 0
July | 19 | 6AM to 7AM | 81 | 71.1 | 66.9 | 101.5 | 35.34 | 0.0713 | 0.67 | 14.23 | 0
July | 19 | 7AM to 8AM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
July | 19 | 8AM to 9AM | 86 | 72.5 | 66.9 | 101.5 | 36.59 | 0.0706 | 0.67 | 14.36 | 0
July | 19 | 9AM to 10AM | 89.1 | 74 | 68 | 105.5 | 37.96 | 0.0702 | 0.69 | 14.46 | 0
July | 19 | 10AM to 11AM | 90 | 73.1 | 66 | 98.4 | 37.06 | 0.0701 | 0.64 | 14.46 | 0
July | 19 | 11AM to 12PM | 91 | 74.6 | 68 | 105.5 | 38.45 | 0.07 | 0.69 | 14.51 | 0
July | 19 | 12PM to 1PM | 91 | 74.6 | 68 | 105.5 | 38.45 | 0.07 | 0.69 | 14.51 | 0
July | 19 | 1PM to 2PM | 93 | 73.9 | 66 | 98.4 | 37.81 | 0.0698 | 0.64 | 14.54 | 0
July | 19 | 2PM to 3PM | 93 | 73.9 | 66 | 98.4 | 37.81 | 0.0698 | 0.64 | 14.54 | 0
July | 19 | 3PM to 4PM | 91.9 | 73.6 | 66 | 98.4 | 37.55 | 0.0699 | 0.64 | 14.51 | 0
July | 19 | 4PM to 5PM | 91.9 | 73.6 | 66 | 98.4 | 37.55 | 0.0699 | 0.64 | 14.51 | 0
July | 19 | 5PM to 6PM | 90 | 73.6 | 66.9 | 101.5 | 37.56 | 0.0701 | 0.67 | 14.47 | 0
July | 19 | 6PM to 7PM | 89.1 | 72.2 | 64.9 | 94.6 | 36.26 | 0.0703 | 0.62 | 14.42 | 0
July | 19 | 7PM to 8PM | 87.1 | 72.3 | 66 | 98.4 | 36.35 | 0.0705 | 0.64 | 14.38 | 0
July | 19 | 8PM to 9PM | 86 | 73.9 | 69.1 | 109.6 | 37.85 | 0.0706 | 0.72 | 14.39 | 0
July | 19 | 9PM to 10PM | 84.9 | 72.9 | 68 | 105.5 | 36.94 | 0.0707 | 0.69 | 14.35 | 0
July | 19 | 10PM to 11PM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
July | 19 | 11PM to 12AM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
July | 20 | 12AM to 1AM | 81 | 71.1 | 66.9 | 101.5 | 35.34 | 0.0713 | 0.67 | 14.23 | 0
July | 20 | 1AM to 2AM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
July | 20 | 2AM to 3AM | 78.1 | 71 | 68 | 105.5 | 35.25 | 0.0716 | 0.69 | 14.17 | 0
July | 20 | 3AM to 4AM | 78.1 | 71 | 68 | 105.5 | 35.25 | 0.0716 | 0.69 | 14.17 | 0
July | 20 | 4AM to 5AM | 77 | 70.7 | 68 | 105.5 | 34.99 | 0.0718 | 0.69 | 14.14 | 0
July | 20 | 5AM to 6AM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
July | 20 | 6AM to 7AM | 80.1 | 71.5 | 68 | 105.5 | 35.74 | 0.0714 | 0.69 | 14.22 | 0
July | 20 | 7AM to 8AM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
July | 20 | 8AM to 9AM | 84.9 | 72.2 | 66.9 | 101.5 | 36.32 | 0.0708 | 0.67 | 14.34 | 0
July | 20 | 9AM to 10AM | 87.1 | 72.8 | 66.9 | 101.5 | 36.85 | 0.0705 | 0.67 | 14.39 | 0
July | 20 | 10AM to 11AM | 89.1 | 73.4 | 66.9 | 101.5 | 37.34 | 0.0702 | 0.67 | 14.44 | 0
July | 20 | 11AM to 12PM | 91 | 74.6 | 68 | 105.5 | 38.45 | 0.07 | 0.69 | 14.51 | 0
July | 20 | 12PM to 1PM | 91.9 | 75.4 | 69.1 | 109.6 | 39.32 | 0.0698 | 0.72 | 14.55 | 0
July | 20 | 1PM to 2PM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
July | 20 | 2PM to 3PM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
July | 20 | 3PM to 4PM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
July | 20 | 4PM to 5PM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
July | 20 | 5PM to 6PM | 91.9 | 75.4 | 69.1 | 109.6 | 39.32 | 0.0698 | 0.72 | 14.55 | 0
July | 20 | 6PM to 7PM | 90 | 74.3 | 68 | 105.5 | 38.18 | 0.0701 | 0.69 | 14.48 | 0
July | 20 | 7PM to 8PM | 88 | 75 | 70 | 113.1 | 38.89 | 0.0703 | 0.74 | 14.45 | 0
July | 20 | 8PM to 9PM | 86 | 74.5 | 70 | 113.1 | 38.4 | 0.0706 | 0.74 | 14.4 | 0
July | 20 | 9PM to 10PM | 84.9 | 73.6 | 69.1 | 109.6 | 37.58 | 0.0707 | 0.72 | 14.36 | 0
July | 20 | 10PM to 11PM | 84 | 73.3 | 69.1 | 109.6 | 37.36 | 0.0708 | 0.72 | 14.34 | 0
July | 20 | 11PM to 12AM | 82.9 | 73.6 | 70 | 113.1 | 37.64 | 0.071 | 0.74 | 14.32 | 0
July | 21 | 12AM to 1AM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
July | 21 | 1AM to 2AM | 81 | 71.8 | 68 | 105.5 | 35.96 | 0.0713 | 0.69 | 14.24 | 0
July | 21 | 2AM to 3AM | 80.1 | 71.5 | 68 | 105.5 | 35.74 | 0.0714 | 0.69 | 14.22 | 0
July | 21 | 3AM to 4AM | 79 | 71.2 | 68 | 105.5 | 35.47 | 0.0715 | 0.69 | 14.19 | 0
July | 21 | 4AM to 5AM | 79 | 71.2 | 68 | 105.5 | 35.47 | 0.0715 | 0.69 | 14.19 | 0
July | 21 | 5AM to 6AM | 79 | 71.9 | 69.1 | 109.6 | 36.11 | 0.0715 | 0.72 | 14.2 | 0
July | 21 | 6AM to 7AM | 81 | 72.5 | 69.1 | 109.6 | 36.6 | 0.0712 | 0.72 | 14.26 | 0
July | 21 | 7AM to 8AM | 84 | 73.3 | 69.1 | 109.6 | 37.36 | 0.0708 | 0.72 | 14.34 | 0
July | 21 | 8AM to 9AM | 86 | 74.5 | 70 | 113.1 | 38.4 | 0.0706 | 0.74 | 14.4 | 0
July | 21 | 9AM to 10AM | 90 | 75.5 | 70 | 113.1 | 39.38 | 0.0701 | 0.74 | 14.51 | 0
July | 21 | 10AM to 11AM | 91.9 | 76 | 70 | 113.1 | 39.87 | 0.0698 | 0.74 | 14.56 | 0
July | 21 | 11AM to 12PM | 93 | 77 | 71.1 | 117.4 | 40.82 | 0.0696 | 0.77 | 14.6 | 0
July | 21 | 12PM to 1PM | 96.1 | 76.5 | 69.1 | 109.6 | 40.34 | 0.0693 | 0.72 | 14.66 | 0
July | 21 | 1PM to 2PM | 97 | 76.1 | 68 | 105.5 | 39.92 | 0.0692 | 0.69 | 14.67 | 0
July | 21 | 2PM to 3PM | 96.1 | 75.9 | 68 | 105.5 | 39.69 | 0.0693 | 0.69 | 14.64 | 0
July | 21 | 3PM to 4PM | 97 | 76.1 | 68 | 105.5 | 39.92 | 0.0692 | 0.69 | 14.67 | 0
July | 21 | 4PM to 5PM | 97 | 76.7 | 69.1 | 109.6 | 40.56 | 0.0692 | 0.72 | 14.68 | 0
July | 21 | 5PM to 6PM | 96.1 | 75.9 | 68 | 105.5 | 39.69 | 0.0693 | 0.69 | 14.64 | 0
July | 21 | 6PM to 7PM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
July | 21 | 7PM to 8PM | 91 | 75.8 | 70 | 113.1 | 39.65 | 0.0699 | 0.74 | 14.53 | 0
July | 21 | 8PM to 9PM | 88 | 77 | 73 | 125.8 | 40.89 | 0.0702 | 0.82 | 14.49 | 0
July | 21 | 9PM to 10PM | 87.1 | 76.7 | 73 | 125.8 | 40.67 | 0.0703 | 0.82 | 14.47 | 0
July | 21 | 10PM to 11PM | 86 | 75.7 | 72 | 121.2 | 39.67 | 0.0705 | 0.79 | 14.43 | 0
July | 21 | 11PM to 12AM | 84.9 | 74.9 | 71.1 | 117.4 | 38.82 | 0.0707 | 0.77 | 14.39 | 0
July | 22 | 12AM to 1AM | 84 | 73.3 | 69.1 | 109.6 | 37.36 | 0.0708 | 0.72 | 14.34 | 0
July | 22 | 1AM to 2AM | 82.9 | 72.4 | 68 | 105.5 | 36.45 | 0.071 | 0.69 | 14.3 | 0
July | 22 | 2AM to 3AM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
July | 22 | 3AM to 4AM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
July | 22 | 4AM to 5AM | 81 | 71.1 | 66.9 | 101.5 | 35.34 | 0.0713 | 0.67 | 14.23 | 0
July | 22 | 5AM to 6AM | 81 | 71.1 | 66.9 | 101.5 | 35.34 | 0.0713 | 0.67 | 14.23 | 0
July | 22 | 6AM to 7AM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
July | 22 | 7AM to 8AM | 86 | 73.2 | 68 | 105.5 | 37.21 | 0.0706 | 0.69 | 14.38 | 0
July | 22 | 8AM to 9AM | 88 | 74.4 | 69.1 | 109.6 | 38.34 | 0.0703 | 0.72 | 14.44 | 0
July | 22 | 9AM to 10AM | 90 | 75.5 | 70 | 113.1 | 39.38 | 0.0701 | 0.74 | 14.51 | 0
July | 22 | 10AM to 11AM | 93 | 76.3 | 70 | 113.1 | 40.14 | 0.0697 | 0.74 | 14.59 | 0
July | 22 | 11AM to 12PM | 95 | 76.2 | 69.1 | 109.6 | 40.07 | 0.0694 | 0.72 | 14.63 | 0
July | 22 | 12PM to 1PM | 97 | 76.1 | 68 | 105.5 | 39.92 | 0.0692 | 0.69 | 14.67 | 0
July | 22 | 1PM to 2PM | 97 | 75.5 | 66.9 | 101.5 | 39.29 | 0.0692 | 0.67 | 14.65 | 0
July | 22 | 2PM to 3PM | 97 | 75.5 | 66.9 | 101.5 | 39.29 | 0.0692 | 0.67 | 14.65 | 0
July | 22 | 3PM to 4PM | 98.1 | 75.8 | 66.9 | 101.5 | 39.56 | 0.0691 | 0.67 | 14.68 | 0
July | 22 | 4PM to 5PM | 97 | 74.4 | 64.9 | 94.6 | 38.2 | 0.0693 | 0.62 | 14.63 | 0
July | 22 | 5PM to 6PM | 96.1 | 74.1 | 64.9 | 94.6 | 37.98 | 0.0694 | 0.62 | 14.61 | 0
July | 22 | 6PM to 7PM | 93 | 73.9 | 66 | 98.4 | 37.81 | 0.0698 | 0.64 | 14.54 | 0
July | 22 | 7PM to 8PM | 91 | 74.6 | 68 | 105.5 | 38.45 | 0.07 | 0.69 | 14.51 | 0
July | 22 | 8PM to 9PM | 91 | 74.6 | 68 | 105.5 | 38.45 | 0.07 | 0.69 | 14.51 | 0
July | 22 | 9PM to 10PM | 90 | 74.3 | 68 | 105.5 | 38.18 | 0.0701 | 0.69 | 14.48 | 0
July | 22 | 10PM to 11PM | 89.1 | 74 | 68 | 105.5 | 37.96 | 0.0702 | 0.69 | 14.46 | 0
July | 22 | 11PM to 12AM | 86 | 74.5 | 70 | 113.1 | 38.4 | 0.0706 | 0.74 | 14.4 | 0
July | 23 | 12AM to 1AM | 82.9 | 73.6 | 70 | 113.1 | 37.64 | 0.071 | 0.74 | 14.32 | 0
July | 23 | 1AM to 2AM | 81 | 73.1 | 70 | 113.1 | 37.15 | 0.0712 | 0.74 | 14.27 | 0
July | 23 | 2AM to 3AM | 81 | 73.1 | 70 | 113.1 | 37.15 | 0.0712 | 0.74 | 14.27 | 0
July | 23 | 3AM to 4AM | 79 | 73.3 | 71.1 | 117.4 | 37.35 | 0.0715 | 0.77 | 14.23 | 0
July | 23 | 4AM to 5AM | 78.1 | 72.3 | 70 | 113.1 | 36.44 | 0.0716 | 0.74 | 14.19 | 0
July | 23 | 5AM to 6AM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
July | 23 | 6AM to 7AM | 75.9 | 72.4 | 71.1 | 117.4 | 36.59 | 0.0719 | 0.77 | 14.15 | 0
July | 23 | 7AM to 8AM | 78.1 | 73.6 | 72 | 121.2 | 37.71 | 0.0716 | 0.79 | 14.22 | 0
July | 23 | 8AM to 9AM | 80.1 | 74.2 | 72 | 121.2 | 38.2 | 0.0713 | 0.79 | 14.27 | 0
July | 23 | 9AM to 10AM | 82 | 74.7 | 72 | 121.2 | 38.69 | 0.071 | 0.79 | 14.32 | 0
July | 23 | 10AM to 11AM | 84 | 75.2 | 72 | 121.2 | 39.18 | 0.0708 | 0.79 | 14.37 | 0
July | 23 | 11AM to 12PM | 84 | 75.2 | 72 | 121.2 | 39.18 | 0.0708 | 0.79 | 14.37 | 0
July | 23 | 12PM to 1PM | 86 | 75.7 | 72 | 121.2 | 39.67 | 0.0705 | 0.79 | 14.43 | 0
July | 23 | 1PM to 2PM | 87.1 | 74.7 | 70 | 113.1 | 38.67 | 0.0704 | 0.74 | 14.43 | 0
July | 23 | 2PM to 3PM | 87.1 | 75.4 | 71.1 | 117.4 | 39.35 | 0.0704 | 0.77 | 14.44 | 0
July | 23 | 3PM to 4PM | 86 | 75.2 | 71.1 | 117.4 | 39.08 | 0.0705 | 0.77 | 14.41 | 0
July | 23 | 4PM to 5PM | 84.9 | 73.6 | 69.1 | 109.6 | 37.58 | 0.0707 | 0.72 | 14.36 | 0
July | 23 | 5PM to 6PM | 82.9 | 71.1 | 66 | 98.4 | 35.33 | 0.071 | 0.64 | 14.27 | 0
July | 23 | 6PM to 7PM | 81 | 70.6 | 66 | 98.4 | 34.84 | 0.0713 | 0.64 | 14.22 | 0
July | 23 | 7PM to 8PM | 80.1 | 69.1 | 64 | 91.7 | 33.57 | 0.0715 | 0.6 | 14.18 | 0
July | 23 | 8PM to 9PM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
July | 23 | 9PM to 10PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
July | 23 | 10PM to 11PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
July | 23 | 11PM to 12AM | 75.9 | 66 | 61 | 82.1 | 31.06 | 0.0721 | 0.54 | 14.04 | 0
July | 24 | 12AM to 1AM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
July | 24 | 1AM to 2AM | 73 | 63.9 | 59 | 76.4 | 29.47 | 0.0725 | 0.5 | 13.94 | 0
July | 24 | 2AM to 3AM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
July | 24 | 3AM to 4AM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
July | 24 | 4AM to 5AM | 71.1 | 62.6 | 57.9 | 73.5 | 28.52 | 0.0728 | 0.48 | 13.88 | 0
July | 24 | 5AM to 6AM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
July | 24 | 6AM to 7AM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
July | 24 | 7AM to 8AM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
July | 24 | 8AM to 9AM | 72 | 63.5 | 59 | 76.4 | 29.2 | 0.0726 | 0.5 | 13.92 | 0
July | 24 | 9AM to 10AM | 73 | 63.9 | 59 | 76.4 | 29.47 | 0.0725 | 0.5 | 13.94 | 0
July | 24 | 10AM to 11AM | 73.9 | 64.2 | 59 | 76.4 | 29.69 | 0.0724 | 0.5 | 13.97 | 0
July | 24 | 11AM to 12PM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
July | 24 | 12PM to 1PM | 75.9 | 64.9 | 59 | 76.4 | 30.17 | 0.0721 | 0.5 | 14.02 | 0
July | 24 | 1PM to 2PM | 75 | 65.7 | 61 | 82.1 | 30.84 | 0.0722 | 0.54 | 14.01 | 0
July | 24 | 2PM to 3PM | 73.9 | 64.8 | 60.1 | 79.5 | 30.17 | 0.0724 | 0.52 | 13.98 | 0
July | 24 | 3PM to 4PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
July | 24 | 4PM to 5PM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
July | 24 | 5PM to 6PM | 73 | 63.3 | 57.9 | 73.5 | 29.01 | 0.0725 | 0.48 | 13.93 | 0
July | 24 | 6PM to 7PM | 72 | 63.5 | 59 | 76.4 | 29.2 | 0.0726 | 0.5 | 13.92 | 0
July | 24 | 7PM to 8PM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
July | 24 | 8PM to 9PM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
July | 24 | 9PM to 10PM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
July | 24 | 10PM to 11PM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
July | 24 | 11PM to 12AM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
July | 25 | 12AM to 1AM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
July | 25 | 1AM to 2AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
July | 25 | 2AM to 3AM | 64.9 | 61.8 | 60.1 | 79.5 | 27.96 | 0.0736 | 0.52 | 13.74 | 0
July | 25 | 3AM to 4AM | 63 | 60.4 | 59 | 76.4 | 27 | 0.0739 | 0.5 | 13.68 | 0
July | 25 | 4AM to 5AM | 62.1 | 59.5 | 57.9 | 73.5 | 26.32 | 0.074 | 0.48 | 13.65 | 0
July | 25 | 5AM to 6AM | 63 | 59.8 | 57.9 | 73.5 | 26.54 | 0.0739 | 0.48 | 13.67 | 0
July | 25 | 6AM to 7AM | 69.1 | 62.6 | 59 | 76.4 | 28.5 | 0.073 | 0.5 | 13.84 | 0
July | 25 | 7AM to 8AM | 72 | 63.5 | 59 | 76.4 | 29.2 | 0.0726 | 0.5 | 13.92 | 0
July | 25 | 8AM to 9AM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
July | 25 | 9AM to 10AM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
July | 25 | 10AM to 11AM | 82 | 67.4 | 60.1 | 79.5 | 32.15 | 0.0713 | 0.52 | 14.19 | 0
July | 25 | 11AM to 12PM | 82.9 | 66.1 | 57 | 71.1 | 31.06 | 0.0712 | 0.47 | 14.19 | 0
July | 25 | 12PM to 1PM | 86 | 66 | 55 | 66.1 | 31.02 | 0.0708 | 0.44 | 14.25 | 0
July | 25 | 1PM to 2PM | 87.1 | 65.4 | 53.1 | 61.4 | 30.55 | 0.0707 | 0.41 | 14.26 | 0
July | 25 | 2PM to 3PM | 84 | 66.4 | 57 | 71.1 | 31.32 | 0.0711 | 0.47 | 14.21 | 0
July | 25 | 3PM to 4PM | 86 | 68 | 59 | 76.4 | 32.64 | 0.0708 | 0.5 | 14.28 | 0
July | 25 | 4PM to 5PM | 82 | 67.4 | 60.1 | 79.5 | 32.15 | 0.0713 | 0.52 | 14.19 | 0
July | 25 | 5PM to 6PM | 81 | 65.4 | 57 | 71.1 | 30.57 | 0.0715 | 0.47 | 14.13 | 0
July | 25 | 6PM to 7PM | 79 | 64.2 | 55.9 | 68.3 | 29.65 | 0.0718 | 0.45 | 14.07 | 0
July | 25 | 7PM to 8PM | 77 | 63.6 | 55.9 | 68.3 | 29.17 | 0.072 | 0.45 | 14.02 | 0
July | 25 | 8PM to 9PM | 75 | 63.5 | 57 | 71.1 | 29.12 | 0.0723 | 0.47 | 13.98 | 0
July | 25 | 9PM to 10PM | 73.9 | 62.5 | 55.9 | 68.3 | 28.42 | 0.0724 | 0.45 | 13.94 | 0
July | 25 | 10PM to 11PM | 72 | 60.8 | 54 | 63.5 | 27.19 | 0.0727 | 0.42 | 13.87 | 0
July | 25 | 11PM to 12AM | 70 | 60.7 | 55 | 66.1 | 27.11 | 0.073 | 0.44 | 13.83 | 0
July | 26 | 12AM to 1AM | 69.1 | 59.8 | 54 | 63.5 | 26.48 | 0.0731 | 0.42 | 13.8 | 0
July | 26 | 1AM to 2AM | 68 | 58.9 | 53.1 | 61.4 | 25.89 | 0.0733 | 0.41 | 13.76 | 0
July | 26 | 2AM to 3AM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
July | 26 | 3AM to 4AM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
July | 26 | 4AM to 5AM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
July | 26 | 5AM to 6AM | 64.9 | 58.2 | 54 | 63.5 | 25.47 | 0.0737 | 0.42 | 13.69 | 0
July | 26 | 6AM to 7AM | 70 | 60.1 | 54 | 63.5 | 26.7 | 0.073 | 0.42 | 13.82 | 0
July | 26 | 7AM to 8AM | 73.9 | 61 | 53.1 | 61.4 | 27.34 | 0.0725 | 0.41 | 13.92 | 0
July | 26 | 8AM to 9AM | 77 | 62.1 | 53.1 | 61.4 | 28.09 | 0.0721 | 0.41 | 14 | 0
July | 26 | 9AM to 10AM | 79 | 62.3 | 52 | 59 | 28.19 | 0.0718 | 0.39 | 14.04 | 0
July | 26 | 10AM to 11AM | 79 | 62.3 | 52 | 59 | 28.19 | 0.0718 | 0.39 | 14.04 | 0
July | 26 | 11AM to 12PM | 82 | 63.3 | 52 | 59 | 28.94 | 0.0714 | 0.39 | 14.12 | 0
July | 26 | 12PM to 1PM | 82 | 63.3 | 52 | 59 | 28.94 | 0.0714 | 0.39 | 14.12 | 0
July | 26 | 1PM to 2PM | 82 | 63.3 | 52 | 59 | 28.94 | 0.0714 | 0.39 | 14.12 | 0
July | 26 | 2PM to 3PM | 82 | 63.3 | 52 | 59 | 28.94 | 0.0714 | 0.39 | 14.12 | 0
July | 26 | 3PM to 4PM | 80.1 | 62.6 | 52 | 59 | 28.45 | 0.0717 | 0.39 | 14.07 | 0
July | 26 | 4PM to 5PM | 81 | 63.4 | 53.1 | 61.4 | 29.05 | 0.0715 | 0.41 | 14.1 | 0
July | 26 | 5PM to 6PM | 79 | 62.8 | 53.1 | 61.4 | 28.57 | 0.0718 | 0.41 | 14.05 | 0
July | 26 | 6PM to 7PM | 78.1 | 62.9 | 54 | 63.5 | 28.68 | 0.0719 | 0.42 | 14.03 | 0
July | 26 | 7PM to 8PM | 75 | 62.4 | 55 | 66.1 | 28.34 | 0.0723 | 0.44 | 13.96 | 0
July | 26 | 8PM to 9PM | 73.9 | 62 | 55 | 66.1 | 28.07 | 0.0724 | 0.44 | 13.93 | 0
July | 26 | 9PM to 10PM | 73 | 61.7 | 55 | 66.1 | 27.85 | 0.0726 | 0.44 | 13.91 | 0
July | 26 | 10PM to 11PM | 70 | 60.7 | 55 | 66.1 | 27.11 | 0.073 | 0.44 | 13.83 | 0
July | 26 | 11PM to 12AM | 69.1 | 60.8 | 55.9 | 68.3 | 27.23 | 0.0731 | 0.45 | 13.81 | 0
July | 27 | 12AM to 1AM | 68 | 59.9 | 55 | 66.1 | 26.62 | 0.0733 | 0.44 | 13.78 | 0
July | 27 | 1AM to 2AM | 66.9 | 59.6 | 55 | 66.1 | 26.36 | 0.0734 | 0.44 | 13.75 | 0
July | 27 | 2AM to 3AM | 66.9 | 59 | 54 | 63.5 | 25.96 | 0.0734 | 0.42 | 13.74 | 0
July | 27 | 3AM to 4AM | 64 | 57.4 | 53.1 | 61.4 | 24.93 | 0.0738 | 0.41 | 13.66 | 0
July | 27 | 4AM to 5AM | 64 | 57.4 | 53.1 | 61.4 | 24.93 | 0.0738 | 0.41 | 13.66 | 0
July | 27 | 5AM to 6AM | 64 | 57.4 | 53.1 | 61.4 | 24.93 | 0.0738 | 0.41 | 13.66 | 0
July | 27 | 6AM to 7AM | 68 | 58.9 | 53.1 | 61.4 | 25.89 | 0.0733 | 0.41 | 13.76 | 0
July | 27 | 7AM to 8AM | 72 | 60.3 | 53.1 | 61.4 | 26.86 | 0.0727 | 0.41 | 13.87 | 0
July | 27 | 8AM to 9AM | 75 | 61.9 | 54 | 63.5 | 27.93 | 0.0723 | 0.42 | 13.95 | 0
July | 27 | 9AM to 10AM | 79 | 63.8 | 55 | 66.1 | 29.3 | 0.0718 | 0.44 | 14.07 | 0
July | 27 | 10AM to 11AM | 81 | 63.4 | 53.1 | 61.4 | 29.05 | 0.0715 | 0.41 | 14.1 | 0
July | 27 | 11AM to 12PM | 82.9 | 63.6 | 52 | 59 | 29.16 | 0.0713 | 0.39 | 14.15 | 0
July | 27 | 12PM to 1PM | 84 | 64 | 52 | 59 | 29.42 | 0.0711 | 0.39 | 14.17 | 0
July | 27 | 1PM to 2PM | 84.9 | 64.3 | 52 | 59 | 29.64 | 0.071 | 0.39 | 14.2 | 0
July | 27 | 2PM to 3PM | 84 | 63.1 | 50 | 54.7 | 28.76 | 0.0712 | 0.36 | 14.16 | 0
July | 27 | 3PM to 4PM | 84 | 63.5 | 51.1 | 57 | 29.11 | 0.0712 | 0.38 | 14.17 | 0
July | 27 | 4PM to 5PM | 82.9 | 64.1 | 53.1 | 61.4 | 29.54 | 0.0713 | 0.41 | 14.15 | 0
July | 27 | 5PM to 6PM | 82 | 64.8 | 55 | 66.1 | 30.05 | 0.0714 | 0.44 | 14.15 | 0
July | 27 | 6PM to 7PM | 80.1 | 64.6 | 55.9 | 68.3 | 29.92 | 0.0716 | 0.45 | 14.1 | 0
July | 27 | 7PM to 8PM | 78.1 | 64.5 | 57 | 71.1 | 29.87 | 0.0719 | 0.47 | 14.06 | 0
July | 27 | 8PM to 9PM | 75 | 64 | 57.9 | 73.5 | 29.49 | 0.0723 | 0.48 | 13.99 | 0
July | 27 | 9PM to 10PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
July | 27 | 10PM to 11PM | 73 | 63.3 | 57.9 | 73.5 | 29.01 | 0.0725 | 0.48 | 13.93 | 0
July | 27 | 11PM to 12AM | 72 | 62.4 | 57 | 71.1 | 28.37 | 0.0727 | 0.47 | 13.9 | 0
July | 28 | 12AM to 1AM | 72 | 61.8 | 55.9 | 68.3 | 27.94 | 0.0727 | 0.45 | 13.89 | 0
July | 28 | 1AM to 2AM | 71.1 | 61.5 | 55.9 | 68.3 | 27.72 | 0.0728 | 0.45 | 13.87 | 0
July | 28 | 2AM to 3AM | 71.1 | 61.5 | 55.9 | 68.3 | 27.72 | 0.0728 | 0.45 | 13.87 | 0
July | 28 | 3AM to 4AM | 70 | 61.7 | 57 | 71.1 | 27.89 | 0.073 | 0.47 | 13.85 | 0
July | 28 | 4AM to 5AM | 70 | 61.7 | 57 | 71.1 | 27.89 | 0.073 | 0.47 | 13.85 | 0
July | 28 | 5AM to 6AM | 70 | 62.3 | 57.9 | 73.5 | 28.26 | 0.0729 | 0.48 | 13.85 | 0
July | 28 | 6AM to 7AM | 70 | 62.3 | 57.9 | 73.5 | 28.26 | 0.0729 | 0.48 | 13.85 | 0
July | 28 | 7AM to 8AM | 70 | 63.5 | 60.1 | 79.5 | 29.2 | 0.0729 | 0.52 | 13.87 | 0
July | 28 | 8AM to 9AM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
July | 28 | 9AM to 10AM | 77 | 68.2 | 64 | 91.7 | 32.82 | 0.0719 | 0.6 | 14.1 | 0
July | 28 | 10AM to 11AM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
July | 28 | 11AM to 12PM | 81 | 68.2 | 62.1 | 85.4 | 32.81 | 0.0714 | 0.56 | 14.18 | 0
July | 28 | 12PM to 1PM | 82 | 67.4 | 60.1 | 79.5 | 32.15 | 0.0713 | 0.52 | 14.19 | 0
July | 28 | 1PM to 2PM | 82 | 66.8 | 59 | 76.4 | 31.67 | 0.0713 | 0.5 | 14.18 | 0
July | 28 | 2PM to 3PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
July | 28 | 3PM to 4PM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
July | 28 | 4PM to 5PM | 82 | 67.4 | 60.1 | 79.5 | 32.15 | 0.0713 | 0.52 | 14.19 | 0
July | 28 | 5PM to 6PM | 82 | 66.8 | 59 | 76.4 | 31.67 | 0.0713 | 0.5 | 14.18 | 0
July | 28 | 6PM to 7PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
July | 28 | 7PM to 8PM | 80.1 | 66.8 | 60.1 | 79.5 | 31.67 | 0.0715 | 0.52 | 14.14 | 0
July | 28 | 8PM to 9PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
July | 28 | 9PM to 10PM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
July | 28 | 10PM to 11PM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
July | 28 | 11PM to 12AM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
July | 29 | 12AM to 1AM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
July | 29 | 1AM to 2AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
July | 29 | 2AM to 3AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
July | 29 | 3AM to 4AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
July | 29 | 4AM to 5AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
July | 29 | 5AM to 6AM | 73 | 68.8 | 66.9 | 101.5 | 33.39 | 0.0723 | 0.67 | 14.02 | 0
July | 29 | 6AM to 7AM | 71.1 | 69.7 | 69.1 | 109.6 | 34.16 | 0.0726 | 0.72 | 14 | 0
July | 29 | 7AM to 8AM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
July | 29 | 8AM to 9AM | 71.1 | 67.6 | 66 | 98.4 | 32.41 | 0.0726 | 0.64 | 13.96 | 0
July | 29 | 9AM to 10AM | 69.1 | 67 | 66 | 98.4 | 31.92 | 0.0729 | 0.64 | 13.91 | 0
July | 29 | 10AM to 11AM | 72 | 66.6 | 64 | 91.7 | 31.58 | 0.0726 | 0.6 | 13.96 | 0
July | 29 | 11AM to 12PM | 71.1 | 65.6 | 63 | 88.2 | 30.82 | 0.0727 | 0.58 | 13.93 | 0
July | 29 | 12PM to 1PM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
July | 29 | 1PM to 2PM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
July | 29 | 2PM to 3PM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
July | 29 | 3PM to 4PM | 75 | 63.5 | 57 | 71.1 | 29.12 | 0.0723 | 0.47 | 13.98 | 0
July | 29 | 4PM to 5PM | 75.9 | 65.5 | 60.1 | 79.5 | 30.65 | 0.0721 | 0.52 | 14.03 | 0
July | 29 | 5PM to 6PM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
July | 29 | 6PM to 7PM | 73.9 | 64.8 | 60.1 | 79.5 | 30.17 | 0.0724 | 0.52 | 13.98 | 0
July | 29 | 7PM to 8PM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
July | 29 | 8PM to 9PM | 70 | 63.5 | 60.1 | 79.5 | 29.2 | 0.0729 | 0.52 | 13.87 | 0
July | 29 | 9PM to 10PM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
July | 29 | 10PM to 11PM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
July | 29 | 11PM to 12AM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
July | 30 | 12AM to 1AM | 64 | 60.8 | 59 | 76.4 | 27.26 | 0.0737 | 0.5 | 13.71 | 0
July | 30 | 1AM to 2AM | 63 | 60.4 | 59 | 76.4 | 27 | 0.0739 | 0.5 | 13.68 | 0
July | 30 | 2AM to 3AM | 62.1 | 60.8 | 60.1 | 79.5 | 27.26 | 0.074 | 0.52 | 13.67 | 0
July | 30 | 3AM to 4AM | 62.1 | 60.8 | 60.1 | 79.5 | 27.26 | 0.074 | 0.52 | 13.67 | 0
July | 30 | 4AM to 5AM | 61 | 59.1 | 57.9 | 73.5 | 26.06 | 0.0742 | 0.48 | 13.62 | 0
July | 30 | 5AM to 6AM | 62.1 | 60.1 | 59 | 76.4 | 26.78 | 0.074 | 0.5 | 13.66 | 0
July | 30 | 6AM to 7AM | 69.1 | 63.2 | 60.1 | 79.5 | 28.98 | 0.073 | 0.52 | 13.85 | 0
July | 30 | 7AM to 8AM | 71.1 | 62.6 | 57.9 | 73.5 | 28.52 | 0.0728 | 0.48 | 13.88 | 0
July | 30 | 8AM to 9AM | 75 | 63.5 | 57 | 71.1 | 29.12 | 0.0723 | 0.47 | 13.98 | 0
July | 30 | 9AM to 10AM | 77 | 64.1 | 57 | 71.1 | 29.6 | 0.072 | 0.47 | 14.03 | 0
July | 30 | 10AM to 11AM | 77 | 63.6 | 55.9 | 68.3 | 29.17 | 0.072 | 0.45 | 14.02 | 0
July | 30 | 11AM to 12PM | 80.1 | 65.6 | 57.9 | 73.5 | 30.72 | 0.0716 | 0.48 | 14.12 | 0
July | 30 | 12PM to 1PM | 81 | 66.5 | 59 | 76.4 | 31.41 | 0.0714 | 0.5 | 14.15 | 0
July | 30 | 1PM to 2PM | 82.9 | 67.1 | 59 | 76.4 | 31.89 | 0.0712 | 0.5 | 14.2 | 0
July | 30 | 2PM to 3PM | 82.9 | 67.1 | 59 | 76.4 | 31.89 | 0.0712 | 0.5 | 14.2 | 0
July | 30 | 3PM to 4PM | 84 | 67.4 | 59 | 76.4 | 32.16 | 0.071 | 0.5 | 14.23 | 0
July | 30 | 4PM to 5PM | 82.9 | 66.5 | 57.9 | 73.5 | 31.43 | 0.0712 | 0.48 | 14.19 | 0
July | 30 | 5PM to 6PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
July | 30 | 6PM to 7PM | 80.1 | 65.1 | 57 | 71.1 | 30.35 | 0.0716 | 0.47 | 14.11 | 0
July | 30 | 7PM to 8PM | 78.1 | 65.6 | 59 | 76.4 | 30.7 | 0.0718 | 0.5 | 14.08 | 0
July | 30 | 8PM to 9PM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
July | 30 | 9PM to 10PM | 73.9 | 64.2 | 59 | 76.4 | 29.69 | 0.0724 | 0.5 | 13.97 | 0
July | 30 | 10PM to 11PM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
July | 30 | 11PM to 12AM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
July | 31 | 12AM to 1AM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
July | 31 | 1AM to 2AM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
July | 31 | 2AM to 3AM | 68 | 62.2 | 59 | 76.4 | 28.23 | 0.0732 | 0.5 | 13.81 | 0
July | 31 | 3AM to 4AM | 66.9 | 61.8 | 59 | 76.4 | 27.97 | 0.0733 | 0.5 | 13.78 | 0
July | 31 | 4AM to 5AM | 66.9 | 61.8 | 59 | 76.4 | 27.97 | 0.0733 | 0.5 | 13.78 | 0
July | 31 | 5AM to 6AM | 66.9 | 61.8 | 59 | 76.4 | 27.97 | 0.0733 | 0.5 | 13.78 | 0
July | 31 | 6AM to 7AM | 73 | 63.9 | 59 | 76.4 | 29.47 | 0.0725 | 0.5 | 13.94 | 0
July | 31 | 7AM to 8AM | 77 | 64.6 | 57.9 | 73.5 | 29.98 | 0.072 | 0.48 | 14.04 | 0
July | 31 | 8AM to 9AM | 79 | 65.3 | 57.9 | 73.5 | 30.46 | 0.0717 | 0.48 | 14.09 | 0
July | 31 | 9AM to 10AM | 82 | 66.8 | 59 | 76.4 | 31.67 | 0.0713 | 0.5 | 14.18 | 0
July | 31 | 10AM to 11AM | 84.9 | 68.3 | 60.1 | 79.5 | 32.86 | 0.0709 | 0.52 | 14.26 | 0
July | 31 | 11AM to 12PM | 84 | 68.5 | 61 | 82.1 | 33.05 | 0.071 | 0.54 | 14.25 | 0
July | 31 | 12PM to 1PM | 86 | 69.1 | 61 | 82.1 | 33.53 | 0.0707 | 0.54 | 14.3 | 0
July | 31 | 1PM to 2PM | 90 | 69.8 | 60.1 | 79.5 | 34.09 | 0.0703 | 0.52 | 14.4 | 0
July | 31 | 2PM to 3PM | 90 | 69.8 | 60.1 | 79.5 | 34.09 | 0.0703 | 0.52 | 14.4 | 0
July | 31 | 3PM to 4PM | 91 | 70.6 | 61 | 82.1 | 34.77 | 0.0701 | 0.54 | 14.43 | 0
July | 31 | 4PM to 5PM | 89.1 | 70.6 | 62.1 | 85.4 | 34.8 | 0.0703 | 0.56 | 14.39 | 0
July | 31 | 5PM to 6PM | 84.9 | 69.4 | 62.1 | 85.4 | 33.78 | 0.0709 | 0.56 | 14.28 | 0
July | 31 | 6PM to 7PM | 84.9 | 69.4 | 62.1 | 85.4 | 33.78 | 0.0709 | 0.56 | 14.28 | 0
July | 31 | 7PM to 8PM | 82.9 | 68.8 | 62.1 | 85.4 | 33.3 | 0.0711 | 0.56 | 14.23 | 0
July | 31 | 8PM to 9PM | 82.9 | 67.7 | 60.1 | 79.5 | 32.37 | 0.0712 | 0.52 | 14.21 | 0
July | 31 | 9PM to 10PM | 80.4 | 66.6 | 59.5 | 77.9 | 31.51 | 0.0715 | 0.51 | 14.14 | 0
July | 31 | 10PM to 11PM | 77.7 | 65.3 | 58.8 | 75.9 | 30.54 | 0.0719 | 0.5 | 14.06 | 0
July | 31 | 11PM to 12AM | 75.2 | 64.2 | 58.3 | 74.4 | 29.69 | 0.0722 | 0.49 | 13.99 | 0
August | 1 | 12AM to 1AM | 72.7 | 63.1 | 57.7 | 73 | 28.84 | 0.0726 | 0.48 | 13.92 | 0
August | 1 | 1AM to 2AM | 70.2 | 61.9 | 57.2 | 71.5 | 28 | 0.0729 | 0.47 | 13.85 | 0
August | 1 | 2AM to 3AM | 67.5 | 60.6 | 56.5 | 69.7 | 27.05 | 0.0733 | 0.46 | 13.78 | 0
August | 1 | 3AM to 4AM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
August | 1 | 4AM to 5AM | 63 | 58.6 | 55.9 | 68.3 | 25.74 | 0.074 | 0.45 | 13.65 | 0
August | 1 | 5AM to 6AM | 64 | 59.6 | 57 | 71.1 | 26.43 | 0.0738 | 0.47 | 13.69 | 0
August | 1 | 6AM to 7AM | 66.9 | 60.7 | 57 | 71.1 | 27.14 | 0.0734 | 0.47 | 13.77 | 0
August | 1 | 7AM to 8AM | 70 | 61.7 | 57 | 71.1 | 27.89 | 0.073 | 0.47 | 13.85 | 0
August | 1 | 8AM to 9AM | 73 | 63.3 | 57.9 | 73.5 | 29.01 | 0.0725 | 0.48 | 13.93 | 0
August | 1 | 9AM to 10AM | 75.9 | 63.2 | 55.9 | 68.3 | 28.91 | 0.0722 | 0.45 | 13.99 | 0
August | 1 | 10AM to 11AM | 77 | 62.5 | 54 | 63.5 | 28.42 | 0.072 | 0.42 | 14.01 | 0
August | 1 | 11AM to 12PM | 80.1 | 64.6 | 55.9 | 68.3 | 29.92 | 0.0716 | 0.45 | 14.1 | 0
August | 1 | 12PM to 1PM | 80.1 | 63.6 | 54 | 63.5 | 29.16 | 0.0716 | 0.42 | 14.09 | 0
August | 1 | 1PM to 2PM | 81 | 63.9 | 54 | 63.5 | 29.38 | 0.0715 | 0.42 | 14.11 | 0
August | 1 | 2PM to 3PM | 82 | 63.8 | 53.1 | 61.4 | 29.32 | 0.0714 | 0.41 | 14.13 | 0
August | 1 | 3PM to 4PM | 82 | 64.8 | 55 | 66.1 | 30.05 | 0.0714 | 0.44 | 14.15 | 0
August | 1 | 4PM to 5PM | 81 | 64.9 | 55.9 | 68.3 | 30.14 | 0.0715 | 0.45 | 14.12 | 0
August | 1 | 5PM to 6PM | 80.1 | 64.1 | 55 | 66.1 | 29.57 | 0.0716 | 0.44 | 14.09 | 0
August | 1 | 6PM to 7PM | 78.1 | 63.4 | 55 | 66.1 | 29.08 | 0.0719 | 0.44 | 14.04 | 0
August | 1 | 7PM to 8PM | 75.9 | 62.7 | 55 | 66.1 | 28.56 | 0.0722 | 0.44 | 13.99 | 0
August | 1 | 8PM to 9PM | 73.9 | 62 | 55 | 66.1 | 28.07 | 0.0724 | 0.44 | 13.93 | 0
August | 1 | 9PM to 10PM | 72 | 61.4 | 55 | 66.1 | 27.59 | 0.0727 | 0.44 | 13.88 | 0
August | 1 | 10PM to 11PM | 71.1 | 61 | 55 | 66.1 | 27.37 | 0.0728 | 0.44 | 13.86 | 0
August | 1 | 11PM to 12AM | 70 | 61.1 | 55.9 | 68.3 | 27.45 | 0.073 | 0.45 | 13.84 | 0
August | 2 | 12AM to 1AM | 70 | 60.1 | 54 | 63.5 | 26.7 | 0.073 | 0.42 | 13.82 | 0
August | 2 | 1AM to 2AM | 68 | 61 | 57 | 71.1 | 27.4 | 0.0732 | 0.47 | 13.79 | 0
August | 2 | 2AM to 3AM | 68 | 59.9 | 55 | 66.1 | 26.62 | 0.0733 | 0.44 | 13.78 | 0
August | 2 | 3AM to 4AM | 66.9 | 60.1 | 55.9 | 68.3 | 26.71 | 0.0734 | 0.45 | 13.76 | 0
August | 2 | 4AM to 5AM | 66.9 | 60.7 | 57 | 71.1 | 27.14 | 0.0734 | 0.47 | 13.77 | 0
August | 2 | 5AM to 6AM | 68 | 61 | 57 | 71.1 | 27.4 | 0.0732 | 0.47 | 13.79 | 0
August | 2 | 6AM to 7AM | 70 | 61.7 | 57 | 71.1 | 27.89 | 0.073 | 0.47 | 13.85 | 0
August | 2 | 7AM to 8AM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
August | 2 | 8AM to 9AM | 78.1 | 65.6 | 59 | 76.4 | 30.7 | 0.0718 | 0.5 | 14.08 | 0
August | 2 | 9AM to 10AM | 79 | 64.2 | 55.9 | 68.3 | 29.65 | 0.0718 | 0.45 | 14.07 | 0
August | 2 | 10AM to 11AM | 82 | 66.2 | 57.9 | 73.5 | 31.21 | 0.0713 | 0.48 | 14.17 | 0
August | 2 | 11AM to 12PM | 84 | 67.4 | 59 | 76.4 | 32.16 | 0.071 | 0.5 | 14.23 | 0
August | 2 | 12PM to 1PM | 86 | 69.1 | 61 | 82.1 | 33.53 | 0.0707 | 0.54 | 14.3 | 0
August | 2 | 1PM to 2PM | 87.1 | 70 | 62.1 | 85.4 | 34.31 | 0.0706 | 0.56 | 14.34 | 0
August | 2 | 2PM to 3PM | 87.1 | 70 | 62.1 | 85.4 | 34.31 | 0.0706 | 0.56 | 14.34 | 0
August | 2 | 3PM to 4PM | 86 | 69.7 | 62.1 | 85.4 | 34.05 | 0.0707 | 0.56 | 14.31 | 0
August | 2 | 4PM to 5PM | 87.1 | 70 | 62.1 | 85.4 | 34.31 | 0.0706 | 0.56 | 14.34 | 0
August | 2 | 5PM to 6PM | 84.9 | 69.9 | 63 | 88.2 | 34.22 | 0.0709 | 0.58 | 14.29 | 0
August | 2 | 6PM to 7PM | 82.9 | 69.3 | 63 | 88.2 | 33.74 | 0.0711 | 0.58 | 14.24 | 0
August | 2 | 7PM to 8PM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
August | 2 | 8PM to 9PM | 80.1 | 69.1 | 64 | 91.7 | 33.57 | 0.0715 | 0.6 | 14.18 | 0
August | 2 | 9PM to 10PM | 78.1 | 69 | 64.9 | 94.6 | 33.56 | 0.0717 | 0.62 | 14.13 | 0
August | 2 | 10PM to 11PM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
August | 2 | 11PM to 12AM | 75.9 | 68.4 | 64.9 | 94.6 | 33.02 | 0.072 | 0.62 | 14.08 | 0
August | 3 | 12AM to 1AM | 75.9 | 68.4 | 64.9 | 94.6 | 33.02 | 0.072 | 0.62 | 14.08 | 0
August | 3 | 1AM to 2AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
August | 3 | 2AM to 3AM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
August | 3 | 3AM to 4AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
August | 3 | 4AM to 5AM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
August | 3 | 5AM to 6AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
August | 3 | 6AM to 7AM | 75.9 | 67.8 | 64 | 91.7 | 32.56 | 0.072 | 0.6 | 14.07 | 0
August | 3 | 7AM to 8AM | 79 | 70.5 | 66.9 | 101.5 | 34.86 | 0.0716 | 0.67 | 14.18 | 0
August | 3 | 8AM to 9AM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
August | 3 | 9AM to 10AM | 84.9 | 73.6 | 69.1 | 109.6 | 37.58 | 0.0707 | 0.72 | 14.36 | 0
August | 3 | 10AM to 11AM | 86 | 74.5 | 70 | 113.1 | 38.4 | 0.0706 | 0.74 | 14.4 | 0
August | 3 | 11AM to 12PM | 82 | 75.4 | 73 | 125.8 | 39.42 | 0.071 | 0.82 | 14.34 | 0
August | 3 | 12PM to 1PM | 82.9 | 76.3 | 73.9 | 129.8 | 40.26 | 0.0709 | 0.85 | 14.37 | 0
August | 3 | 1PM to 2PM | 86 | 76.5 | 73 | 125.8 | 40.4 | 0.0705 | 0.82 | 14.44 | 0
August | 3 | 2PM to 3PM | 86 | 76.5 | 73 | 125.8 | 40.4 | 0.0705 | 0.82 | 14.44 | 0
August | 3 | 3PM to 4PM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 3 | 4PM to 5PM | 72 | 71.3 | 71.1 | 117.4 | 35.61 | 0.0724 | 0.77 | 14.04 | 0
August | 3 | 5PM to 6PM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 3 | 6PM to 7PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 3 | 7PM to 8PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 3 | 8PM to 9PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 3 | 9PM to 10PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 3 | 10PM to 11PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 3 | 11PM to 12AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 4 | 12AM to 1AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 4 | 1AM to 2AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
August | 4 | 2AM to 3AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
August | 4 | 3AM to 4AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
August | 4 | 4AM to 5AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
August | 4 | 5AM to 6AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
August | 4 | 6AM to 7AM | 73 | 72.3 | 72 | 121.2 | 36.46 | 0.0722 | 0.79 | 14.08 | 0
August | 4 | 7AM to 8AM | 75 | 72.8 | 72 | 121.2 | 36.95 | 0.072 | 0.79 | 14.14 | 0
August | 4 | 8AM to 9AM | 75.9 | 73.8 | 73 | 125.8 | 37.9 | 0.0718 | 0.82 | 14.17 | 0
August | 4 | 9AM to 10AM | 75.9 | 73.8 | 73 | 125.8 | 37.9 | 0.0718 | 0.82 | 14.17 | 0
August | 4 | 10AM to 11AM | 75.9 | 73.8 | 73 | 125.8 | 37.9 | 0.0718 | 0.82 | 14.17 | 0
August | 4 | 11AM to 12PM | 78.1 | 73.6 | 72 | 121.2 | 37.71 | 0.0716 | 0.79 | 14.22 | 0
August | 4 | 12PM to 1PM | 80.1 | 74.9 | 73 | 125.8 | 38.93 | 0.0713 | 0.82 | 14.28 | 0
August | 4 | 1PM to 2PM | 79 | 75.3 | 73.9 | 129.8 | 39.28 | 0.0714 | 0.85 | 14.27 | 0
August | 4 | 2PM to 3PM | 79 | 74.6 | 73 | 125.8 | 38.66 | 0.0714 | 0.82 | 14.26 | 0
August | 4 | 3PM to 4PM | 81 | 74.4 | 72 | 121.2 | 38.42 | 0.0712 | 0.79 | 14.29 | 0
August | 4 | 4PM to 5PM | 80.1 | 74.2 | 72 | 121.2 | 38.2 | 0.0713 | 0.79 | 14.27 | 0
August | 4 | 5PM to 6PM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
August | 4 | 6PM to 7PM | 80.1 | 72.2 | 69.1 | 109.6 | 36.38 | 0.0714 | 0.72 | 14.23 | 0
August | 4 | 7PM to 8PM | 79 | 72.5 | 70 | 113.1 | 36.66 | 0.0715 | 0.74 | 14.22 | 0
August | 4 | 8PM to 9PM | 77 | 71.4 | 69.1 | 109.6 | 35.63 | 0.0718 | 0.72 | 14.15 | 0
August | 4 | 9PM to 10PM | 75 | 71.4 | 70 | 113.1 | 35.69 | 0.072 | 0.74 | 14.11 | 0
August | 4 | 10PM to 11PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
August | 4 | 11PM to 12AM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
August | 5 | 12AM to 1AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 5 | 1AM to 2AM | 72 | 69.2 | 68 | 105.5 | 33.74 | 0.0725 | 0.69 | 14.01 | 0
August | 5 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
August | 5 | 3AM to 4AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
August | 5 | 4AM to 5AM | 69.1 | 65.7 | 64 | 91.7 | 30.87 | 0.073 | 0.6 | 13.89 | 0
August | 5 | 5AM to 6AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
August | 5 | 6AM to 7AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
August | 5 | 7AM to 8AM | 71.1 | 66.3 | 64 | 91.7 | 31.36 | 0.0727 | 0.6 | 13.94 | 0
August | 5 | 8AM to 9AM | 73 | 61.2 | 54 | 63.5 | 27.45 | 0.0726 | 0.42 | 13.9 | 0
August | 5 | 9AM to 10AM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
August | 5 | 10AM to 11AM | 78.1 | 69 | 64.9 | 94.6 | 33.56 | 0.0717 | 0.62 | 14.13 | 0
August | 5 | 11AM to 12PM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
August | 5 | 12PM to 1PM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
August | 5 | 1PM to 2PM | 81 | 68.7 | 63 | 88.2 | 33.25 | 0.0714 | 0.58 | 14.19 | 0
August | 5 | 2PM to 3PM | 81 | 68.7 | 63 | 88.2 | 33.25 | 0.0714 | 0.58 | 14.19 | 0
August | 5 | 3PM to 4PM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
August | 5 | 4PM to 5PM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
August | 5 | 5PM to 6PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
August | 5 | 6PM to 7PM | 75.9 | 66 | 61 | 82.1 | 31.06 | 0.0721 | 0.54 | 14.04 | 0
August | 5 | 7PM to 8PM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
August | 5 | 8PM to 9PM | 71.1 | 64.4 | 61 | 82.1 | 29.87 | 0.0727 | 0.54 | 13.91 | 0
August | 5 | 9PM to 10PM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
August | 5 | 10PM to 11PM | 69.1 | 62.6 | 59 | 76.4 | 28.5 | 0.073 | 0.5 | 13.84 | 0
August | 5 | 11PM to 12AM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
August | 6 | 12AM to 1AM | 66.9 | 61.8 | 59 | 76.4 | 27.97 | 0.0733 | 0.5 | 13.78 | 0
August | 6 | 1AM to 2AM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
August | 6 | 2AM to 3AM | 64.9 | 60.5 | 57.9 | 73.5 | 27.02 | 0.0736 | 0.48 | 13.72 | 0
August | 6 | 3AM to 4AM | 64 | 60.2 | 57.9 | 73.5 | 26.8 | 0.0738 | 0.48 | 13.7 | 0
August | 6 | 4AM to 5AM | 62.1 | 60.1 | 59 | 76.4 | 26.78 | 0.074 | 0.5 | 13.66 | 0
August | 6 | 5AM to 6AM | 62.1 | 59.5 | 57.9 | 73.5 | 26.32 | 0.074 | 0.48 | 13.65 | 0
August | 6 | 6AM to 7AM | 64 | 60.2 | 57.9 | 73.5 | 26.8 | 0.0738 | 0.48 | 13.7 | 0
August | 6 | 7AM to 8AM | 66.9 | 61.8 | 59 | 76.4 | 27.97 | 0.0733 | 0.5 | 13.78 | 0
August | 6 | 8AM to 9AM | 69.1 | 61.9 | 57.9 | 73.5 | 28.04 | 0.0731 | 0.48 | 13.83 | 0
August | 6 | 9AM to 10AM | 71.1 | 62.1 | 57 | 71.1 | 28.15 | 0.0728 | 0.47 | 13.87 | 0
August | 6 | 10AM to 11AM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
August | 6 | 11AM to 12PM | 75 | 64 | 57.9 | 73.5 | 29.49 | 0.0723 | 0.48 | 13.99 | 0
August | 6 | 12PM to 1PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
August | 6 | 1PM to 2PM | 75 | 63.5 | 57 | 71.1 | 29.12 | 0.0723 | 0.47 | 13.98 | 0
August | 6 | 2PM to 3PM | 77 | 64.1 | 57 | 71.1 | 29.6 | 0.072 | 0.47 | 14.03 | 0
August | 6 | 3PM to 4PM | 75 | 62.9 | 55.9 | 68.3 | 28.69 | 0.0723 | 0.45 | 13.97 | 0
August | 6 | 4PM to 5PM | 73.9 | 62 | 55 | 66.1 | 28.07 | 0.0724 | 0.44 | 13.93 | 0
August | 6 | 5PM to 6PM | 73.9 | 61.5 | 54 | 63.5 | 27.67 | 0.0725 | 0.42 | 13.93 | 0
August | 6 | 6PM to 7PM | 71.1 | 58.5 | 50 | 54.7 | 25.6 | 0.0729 | 0.36 | 13.82 | 0
August | 6 | 7PM to 8PM | 68 | 56.8 | 48.9 | 52.6 | 24.52 | 0.0733 | 0.35 | 13.74 | 0
August | 6 | 8PM to 9PM | 66 | 56 | 48.9 | 52.6 | 24.03 | 0.0736 | 0.35 | 13.69 | 0
August | 6 | 9PM to 10PM | 64.9 | 55.6 | 48.9 | 52.6 | 23.77 | 0.0738 | 0.35 | 13.66 | 0
August | 6 | 10PM to 11PM | 64 | 55.8 | 50 | 54.7 | 23.89 | 0.0739 | 0.36 | 13.64 | 0
August | 6 | 11PM to 12AM | 63 | 55.9 | 51.1 | 57 | 23.98 | 0.074 | 0.38 | 13.62 | 0
August | 7 | 12AM to 1AM | 60.1 | 55.3 | 52 | 59 | 23.59 | 0.0744 | 0.39 | 13.55 | 0
August | 7 | 1AM to 2AM | 60.1 | 55.3 | 52 | 59 | 23.59 | 0.0744 | 0.39 | 13.55 | 0
August | 7 | 2AM to 3AM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
August | 7 | 3AM to 4AM | 57.9 | 55 | 53.1 | 61.4 | 23.44 | 0.0747 | 0.41 | 13.5 | 0
August | 7 | 4AM to 5AM | 57 | 54.7 | 53.1 | 61.4 | 23.22 | 0.0748 | 0.41 | 13.48 | 0
August | 7 | 5AM to 6AM | 57.9 | 55.5 | 54 | 63.5 | 23.76 | 0.0747 | 0.42 | 13.51 | 0
August | 7 | 6AM to 7AM | 63 | 58.1 | 55 | 66.1 | 25.39 | 0.074 | 0.44 | 13.65 | 0
August | 7 | 7AM to 8AM | 66.9 | 59.6 | 55 | 66.1 | 26.36 | 0.0734 | 0.44 | 13.75 | 0
August | 7 | 8AM to 9AM | 71.1 | 58.5 | 50 | 54.7 | 25.6 | 0.0729 | 0.36 | 13.82 | 0
August | 7 | 9AM to 10AM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
August | 7 | 10AM to 11AM | 73 | 58.7 | 48.9 | 52.6 | 25.74 | 0.0726 | 0.35 | 13.87 | 0
August | 7 | 11AM to 12PM | 73.9 | 60 | 51.1 | 57 | 26.66 | 0.0725 | 0.38 | 13.91 | 0
August | 7 | 12PM to 1PM | 75 | 60.4 | 51.1 | 57 | 26.92 | 0.0724 | 0.38 | 13.93 | 0
August | 7 | 1PM to 2PM | 75 | 59.9 | 50 | 54.7 | 26.57 | 0.0724 | 0.36 | 13.93 | 0
August | 7 | 2PM to 3PM | 75.9 | 60.8 | 51.1 | 57 | 27.14 | 0.0722 | 0.38 | 13.96 | 0
August | 7 | 3PM to 4PM | 75.9 | 60.8 | 51.1 | 57 | 27.14 | 0.0722 | 0.38 | 13.96 | 0
August | 7 | 4PM to 5PM | 75 | 60.4 | 51.1 | 57 | 26.92 | 0.0724 | 0.38 | 13.93 | 0
August | 7 | 5PM to 6PM | 75 | 60.9 | 52 | 59 | 27.23 | 0.0723 | 0.39 | 13.94 | 0
August | 7 | 6PM to 7PM | 73 | 60.2 | 52 | 59 | 26.74 | 0.0726 | 0.39 | 13.89 | 0
August | 7 | 7PM to 8PM | 71.1 | 60 | 53.1 | 61.4 | 26.64 | 0.0729 | 0.41 | 13.84 | 0
August | 7 | 8PM to 9PM | 70 | 60.1 | 54 | 63.5 | 26.7 | 0.073 | 0.42 | 13.82 | 0
August | 7 | 9PM to 10PM | 69.1 | 59.3 | 53.1 | 61.4 | 26.16 | 0.0731 | 0.41 | 13.79 | 0
August | 7 | 10PM to 11PM | 68 | 58.9 | 53.1 | 61.4 | 25.89 | 0.0733 | 0.41 | 13.76 | 0
August | 7 | 11PM to 12AM | 66.9 | 59.6 | 55 | 66.1 | 26.36 | 0.0734 | 0.44 | 13.75 | 0
August | 8 | 12AM to 1AM | 66 | 59.2 | 55 | 66.1 | 26.14 | 0.0735 | 0.44 | 13.73 | 0
August | 8 | 1AM to 2AM | 64.9 | 58.8 | 55 | 66.1 | 25.88 | 0.0737 | 0.44 | 13.7 | 0
August | 8 | 2AM to 3AM | 64 | 59 | 55.9 | 68.3 | 26 | 0.0738 | 0.45 | 13.68 | 0
August | 8 | 3AM to 4AM | 62.1 | 57.8 | 55 | 66.1 | 25.17 | 0.0741 | 0.44 | 13.62 | 0
August | 8 | 4AM to 5AM | 62.1 | 57.1 | 54 | 63.5 | 24.77 | 0.0741 | 0.42 | 13.62 | 0
August | 8 | 5AM to 6AM | 63 | 58.1 | 55 | 66.1 | 25.39 | 0.074 | 0.44 | 13.65 | 0
August | 8 | 6AM to 7AM | 66 | 59.2 | 55 | 66.1 | 26.14 | 0.0735 | 0.44 | 13.73 | 0
August | 8 | 7AM to 8AM | 71.1 | 61.5 | 55.9 | 68.3 | 27.72 | 0.0728 | 0.45 | 13.87 | 0
August | 8 | 8AM to 9AM | 72 | 60.8 | 54 | 63.5 | 27.19 | 0.0727 | 0.42 | 13.87 | 0
August | 8 | 9AM to 10AM | 73.9 | 61 | 53.1 | 61.4 | 27.34 | 0.0725 | 0.41 | 13.92 | 0
August | 8 | 10AM to 11AM | 75 | 61.9 | 54 | 63.5 | 27.93 | 0.0723 | 0.42 | 13.95 | 0
August | 8 | 11AM to 12PM | 75.9 | 61.2 | 52 | 59 | 27.45 | 0.0722 | 0.39 | 13.96 | 0
August | 8 | 12PM to 1PM | 78.1 | 61.9 | 52 | 59 | 27.97 | 0.0719 | 0.39 | 14.02 | 0
August | 8 | 1PM to 2PM | 78.1 | 61.5 | 51.1 | 57 | 27.67 | 0.0719 | 0.38 | 14.01 | 0
August | 8 | 2PM to 3PM | 79 | 61.8 | 51.1 | 57 | 27.89 | 0.0718 | 0.38 | 14.04 | 0
August | 8 | 3PM to 4PM | 79 | 62.3 | 52 | 59 | 28.19 | 0.0718 | 0.39 | 14.04 | 0
August | 8 | 4PM to 5PM | 79 | 62.8 | 53.1 | 61.4 | 28.57 | 0.0718 | 0.41 | 14.05 | 0
August | 8 | 5PM to 6PM | 78.1 | 61.9 | 52 | 59 | 27.97 | 0.0719 | 0.39 | 14.02 | 0
August | 8 | 6PM to 7PM | 75.9 | 61.2 | 52 | 59 | 27.45 | 0.0722 | 0.39 | 13.96 | 0
August | 8 | 7PM to 8PM | 73.9 | 61 | 53.1 | 61.4 | 27.34 | 0.0725 | 0.41 | 13.92 | 0
August | 8 | 8PM to 9PM | 72 | 61.8 | 55.9 | 68.3 | 27.94 | 0.0727 | 0.45 | 13.89 | 0
August | 8 | 9PM to 10PM | 70 | 61.7 | 57 | 71.1 | 27.89 | 0.073 | 0.47 | 13.85 | 0
August | 8 | 10PM to 11PM | 69.1 | 61.4 | 57 | 71.1 | 27.67 | 0.0731 | 0.47 | 13.82 | 0
August | 8 | 11PM to 12AM | 68 | 60.4 | 55.9 | 68.3 | 26.97 | 0.0732 | 0.45 | 13.79 | 0
August | 9 | 12AM to 1AM | 66 | 59.7 | 55.9 | 68.3 | 26.49 | 0.0735 | 0.45 | 13.73 | 0
August | 9 | 1AM to 2AM | 64.9 | 60 | 57 | 71.1 | 26.65 | 0.0737 | 0.47 | 13.71 | 0
August | 9 | 2AM to 3AM | 64 | 59.6 | 57 | 71.1 | 26.43 | 0.0738 | 0.47 | 13.69 | 0
August | 9 | 3AM to 4AM | 63 | 59.2 | 57 | 71.1 | 26.17 | 0.0739 | 0.47 | 13.66 | 0
August | 9 | 4AM to 5AM | 61 | 58.5 | 57 | 71.1 | 25.69 | 0.0742 | 0.47 | 13.61 | 0
August | 9 | 5AM to 6AM | 62.1 | 58.9 | 57 | 71.1 | 25.95 | 0.0741 | 0.47 | 13.64 | 0
August | 9 | 6AM to 7AM | 68 | 61 | 57 | 71.1 | 27.4 | 0.0732 | 0.47 | 13.79 | 0
August | 9 | 7AM to 8AM | 73 | 62.2 | 55.9 | 68.3 | 28.2 | 0.0726 | 0.45 | 13.92 | 0
August | 9 | 8AM to 9AM | 75.9 | 63.2 | 55.9 | 68.3 | 28.91 | 0.0722 | 0.45 | 13.99 | 0
August | 9 | 9AM to 10AM | 77 | 62.5 | 54 | 63.5 | 28.42 | 0.072 | 0.42 | 14.01 | 0
August | 9 | 10AM to 11AM | 79 | 63.2 | 54 | 63.5 | 28.9 | 0.0718 | 0.42 | 14.06 | 0
August | 9 | 11AM to 12PM | 78.1 | 62.9 | 54 | 63.5 | 28.68 | 0.0719 | 0.42 | 14.03 | 0
August | 9 | 12PM to 1PM | 82 | 65.2 | 55.9 | 68.3 | 30.4 | 0.0713 | 0.45 | 14.15 | 0
August | 9 | 1PM to 2PM | 81 | 64.4 | 55 | 66.1 | 29.79 | 0.0715 | 0.44 | 14.12 | 0
August | 9 | 2PM to 3PM | 82.9 | 65.1 | 55 | 66.1 | 30.27 | 0.0712 | 0.44 | 14.17 | 0
August | 9 | 3PM to 4PM | 81 | 64.9 | 55.9 | 68.3 | 30.14 | 0.0715 | 0.45 | 14.12 | 0
August | 9 | 4PM to 5PM | 81 | 64.9 | 55.9 | 68.3 | 30.14 | 0.0715 | 0.45 | 14.12 | 0
August | 9 | 5PM to 6PM | 80.1 | 64.6 | 55.9 | 68.3 | 29.92 | 0.0716 | 0.45 | 14.1 | 0
August | 9 | 6PM to 7PM | 78.1 | 63.9 | 55.9 | 68.3 | 29.43 | 0.0719 | 0.45 | 14.05 | 0
August | 9 | 7PM to 8PM | 75.9 | 64.3 | 57.9 | 73.5 | 29.71 | 0.0721 | 0.48 | 14.01 | 0
August | 9 | 8PM to 9PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
August | 9 | 9PM to 10PM | 73 | 63.3 | 57.9 | 73.5 | 29.01 | 0.0725 | 0.48 | 13.93 | 0
August | 9 | 10PM to 11PM | 71.1 | 62.6 | 57.9 | 73.5 | 28.52 | 0.0728 | 0.48 | 13.88 | 0
August | 9 | 11PM to 12AM | 70 | 62.3 | 57.9 | 73.5 | 28.26 | 0.0729 | 0.48 | 13.85 | 0
August | 10 | 12AM to 1AM | 69.1 | 62.6 | 59 | 76.4 | 28.5 | 0.073 | 0.5 | 13.84 | 0
August | 10 | 1AM to 2AM | 68 | 62.2 | 59 | 76.4 | 28.23 | 0.0732 | 0.5 | 13.81 | 0
August | 10 | 2AM to 3AM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
August | 10 | 3AM to 4AM | 66.9 | 61.8 | 59 | 76.4 | 27.97 | 0.0733 | 0.5 | 13.78 | 0
August | 10 | 4AM to 5AM | 66.9 | 61.2 | 57.9 | 73.5 | 27.51 | 0.0734 | 0.48 | 13.77 | 0
August | 10 | 5AM to 6AM | 66 | 60.9 | 57.9 | 73.5 | 27.29 | 0.0735 | 0.48 | 13.75 | 0
August | 10 | 6AM to 7AM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
August | 10 | 7AM to 8AM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
August | 10 | 8AM to 9AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
August | 10 | 9AM to 10AM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
August | 10 | 10AM to 11AM | 73 | 63.9 | 59 | 76.4 | 29.47 | 0.0725 | 0.5 | 13.94 | 0
August | 10 | 11AM to 12PM | 75 | 65.7 | 61 | 82.1 | 30.84 | 0.0722 | 0.54 | 14.01 | 0
August | 10 | 12PM to 1PM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
August | 10 | 1PM to 2PM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
August | 10 | 2PM to 3PM | 84 | 68.5 | 61 | 82.1 | 33.05 | 0.071 | 0.54 | 14.25 | 0
August | 10 | 3PM to 4PM | 84 | 69.1 | 62.1 | 85.4 | 33.56 | 0.071 | 0.56 | 14.26 | 0
August | 10 | 4PM to 5PM | 82.9 | 67.7 | 60.1 | 79.5 | 32.37 | 0.0712 | 0.52 | 14.21 | 0
August | 10 | 5PM to 6PM | 81 | 68.2 | 62.1 | 85.4 | 32.81 | 0.0714 | 0.56 | 14.18 | 0
August | 10 | 6PM to 7PM | 79 | 66.4 | 60.1 | 79.5 | 31.4 | 0.0717 | 0.52 | 14.11 | 0
August | 10 | 7PM to 8PM | 79 | 65.8 | 59 | 76.4 | 30.92 | 0.0717 | 0.5 | 14.1 | 0
August | 10 | 8PM to 9PM | 75.9 | 66.6 | 62.1 | 85.4 | 31.57 | 0.0721 | 0.56 | 14.05 | 0
August | 10 | 9PM to 10PM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
August | 10 | 10PM to 11PM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
August | 10 | 11PM to 12AM | 72 | 65.4 | 62.1 | 85.4 | 30.6 | 0.0726 | 0.56 | 13.94 | 0
August | 11 | 12AM to 1AM | 72 | 65.4 | 62.1 | 85.4 | 30.6 | 0.0726 | 0.56 | 13.94 | 0
August | 11 | 1AM to 2AM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
August | 11 | 2AM to 3AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
August | 11 | 3AM to 4AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
August | 11 | 4AM to 5AM | 68 | 64.1 | 62.1 | 85.4 | 29.63 | 0.0731 | 0.56 | 13.84 | 0
August | 11 | 5AM to 6AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
August | 11 | 6AM to 7AM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
August | 11 | 7AM to 8AM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
August | 11 | 8AM to 9AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
August | 11 | 9AM to 10AM | 80.1 | 68.4 | 63 | 88.2 | 33.03 | 0.0715 | 0.58 | 14.16 | 0
August | 11 | 10AM to 11AM | 82.9 | 70.5 | 64.9 | 94.6 | 34.75 | 0.0711 | 0.62 | 14.26 | 0
August | 11 | 11AM to 12PM | 84 | 69.1 | 62.1 | 85.4 | 33.56 | 0.071 | 0.56 | 14.26 | 0
August | 11 | 12PM to 1PM | 84.9 | 69.9 | 63 | 88.2 | 34.22 | 0.0709 | 0.58 | 14.29 | 0
August | 11 | 1PM to 2PM | 84.9 | 69.9 | 63 | 88.2 | 34.22 | 0.0709 | 0.58 | 14.29 | 0
August | 11 | 2PM to 3PM | 86 | 69.7 | 62.1 | 85.4 | 34.05 | 0.0707 | 0.56 | 14.31 | 0
August | 11 | 3PM to 4PM | 87.1 | 69.4 | 61 | 82.1 | 33.8 | 0.0706 | 0.54 | 14.33 | 0
August | 11 | 4PM to 5PM | 84 | 69.6 | 63 | 88.2 | 34 | 0.071 | 0.58 | 14.27 | 0
August | 11 | 5PM to 6PM | 82.9 | 68.8 | 62.1 | 85.4 | 33.3 | 0.0711 | 0.56 | 14.23 | 0
August | 11 | 6PM to 7PM | 82 | 69 | 63 | 88.2 | 33.52 | 0.0712 | 0.58 | 14.22 | 0
August | 11 | 7PM to 8PM | 81 | 70.6 | 66 | 98.4 | 34.84 | 0.0713 | 0.64 | 14.22 | 0
August | 11 | 8PM to 9PM | 79 | 70 | 66 | 98.4 | 34.36 | 0.0716 | 0.64 | 14.17 | 0
August | 11 | 9PM to 10PM | 78.1 | 69.7 | 66 | 98.4 | 34.14 | 0.0717 | 0.64 | 14.14 | 0
August | 11 | 10PM to 11PM | 78.1 | 70.3 | 66.9 | 101.5 | 34.63 | 0.0717 | 0.67 | 14.15 | 0
August | 11 | 11PM to 12AM | 77 | 70 | 66.9 | 101.5 | 34.37 | 0.0718 | 0.67 | 14.13 | 0
August | 12 | 12AM to 1AM | 75.9 | 69.7 | 66.9 | 101.5 | 34.1 | 0.072 | 0.67 | 14.1 | 0
August | 12 | 1AM to 2AM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
August | 12 | 2AM to 3AM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
August | 12 | 3AM to 4AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 12 | 4AM to 5AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 12 | 5AM to 6AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 12 | 6AM to 7AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 12 | 7AM to 8AM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 12 | 8AM to 9AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
August | 12 | 9AM to 10AM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
August | 12 | 10AM to 11AM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
August | 12 | 11AM to 12PM | 80.1 | 72.8 | 70 | 113.1 | 36.93 | 0.0713 | 0.74 | 14.24 | 0
August | 12 | 12PM to 1PM | 81 | 73.1 | 70 | 113.1 | 37.15 | 0.0712 | 0.74 | 14.27 | 0
August | 12 | 1PM to 2PM | 82.9 | 73 | 69.1 | 109.6 | 37.09 | 0.071 | 0.72 | 14.31 | 0
August | 12 | 2PM to 3PM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
August | 12 | 3PM to 4PM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
August | 12 | 4PM to 5PM | 79 | 73.9 | 72 | 121.2 | 37.93 | 0.0714 | 0.79 | 14.24 | 0
August | 12 | 5PM to 6PM | 77 | 74.1 | 73 | 125.8 | 38.17 | 0.0717 | 0.82 | 14.2 | 0
August | 12 | 6PM to 7PM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
August | 12 | 7PM to 8PM | 72 | 69.9 | 69.1 | 109.6 | 34.38 | 0.0724 | 0.72 | 14.02 | 0
August | 12 | 8PM to 9PM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 12 | 9PM to 10PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 12 | 10PM to 11PM | 71.1 | 69.7 | 69.1 | 109.6 | 34.16 | 0.0726 | 0.72 | 14 | 0
August | 12 | 11PM to 12AM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
August | 13 | 12AM to 1AM | 69.1 | 67 | 66 | 98.4 | 31.92 | 0.0729 | 0.64 | 13.91 | 0
August | 13 | 1AM to 2AM | 69.1 | 67 | 66 | 98.4 | 31.92 | 0.0729 | 0.64 | 13.91 | 0
August | 13 | 2AM to 3AM | 69.1 | 67 | 66 | 98.4 | 31.92 | 0.0729 | 0.64 | 13.91 | 0
August | 13 | 3AM to 4AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
August | 13 | 4AM to 5AM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
August | 13 | 5AM to 6AM | 68 | 65.3 | 64 | 91.7 | 30.61 | 0.0731 | 0.6 | 13.86 | 0
August | 13 | 6AM to 7AM | 68 | 65.3 | 64 | 91.7 | 30.61 | 0.0731 | 0.6 | 13.86 | 0
August | 13 | 7AM to 8AM | 69.1 | 65.7 | 64 | 91.7 | 30.87 | 0.073 | 0.6 | 13.89 | 0
August | 13 | 8AM to 9AM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
August | 13 | 9AM to 10AM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
August | 13 | 10AM to 11AM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
August | 13 | 11AM to 12PM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
August | 13 | 12PM to 1PM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
August | 13 | 1PM to 2PM | 77 | 67 | 62.1 | 85.4 | 31.84 | 0.0719 | 0.56 | 14.08 | 0
August | 13 | 2PM to 3PM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
August | 13 | 3PM to 4PM | 81 | 68.7 | 63 | 88.2 | 33.25 | 0.0714 | 0.58 | 14.19 | 0
August | 13 | 4PM to 5PM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
August | 13 | 5PM to 6PM | 78.1 | 67.3 | 62.1 | 85.4 | 32.1 | 0.0718 | 0.56 | 14.1 | 0
August | 13 | 6PM to 7PM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
August | 13 | 7PM to 8PM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
August | 13 | 8PM to 9PM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
August | 13 | 9PM to 10PM | 71.1 | 66.3 | 64 | 91.7 | 31.36 | 0.0727 | 0.6 | 13.94 | 0
August | 13 | 10PM to 11PM | 70 | 65.3 | 63 | 88.2 | 30.55 | 0.0728 | 0.58 | 13.9 | 0
August | 13 | 11PM to 12AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
August | 14 | 12AM to 1AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
August | 14 | 1AM to 2AM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
August | 14 | 2AM to 3AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
August | 14 | 3AM to 4AM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
August | 14 | 4AM to 5AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
August | 14 | 5AM to 6AM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
August | 14 | 6AM to 7AM | 66.9 | 63 | 61 | 82.1 | 28.86 | 0.0733 | 0.54 | 13.8 | 0
August | 14 | 7AM to 8AM | 71.1 | 64.4 | 61 | 82.1 | 29.87 | 0.0727 | 0.54 | 13.91 | 0
August | 14 | 8AM to 9AM | 73.9 | 65.4 | 61 | 82.1 | 30.58 | 0.0723 | 0.54 | 13.98 | 0
August | 14 | 9AM to 10AM | 77 | 67 | 62.1 | 85.4 | 31.84 | 0.0719 | 0.56 | 14.08 | 0
August | 14 | 10AM to 11AM | 79 | 67 | 61 | 82.1 | 31.81 | 0.0717 | 0.54 | 14.12 | 0
August | 14 | 11AM to 12PM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
August | 14 | 12PM to 1PM | 82.9 | 68.2 | 61 | 82.1 | 32.78 | 0.0711 | 0.54 | 14.22 | 0
August | 14 | 1PM to 2PM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
August | 14 | 2PM to 3PM | 82 | 68.5 | 62.1 | 85.4 | 33.08 | 0.0712 | 0.56 | 14.21 | 0
August | 14 | 3PM to 4PM | 82.9 | 68.2 | 61 | 82.1 | 32.78 | 0.0711 | 0.54 | 14.22 | 0
August | 14 | 4PM to 5PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
August | 14 | 5PM to 6PM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
August | 14 | 6PM to 7PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
August | 14 | 7PM to 8PM | 75.9 | 66 | 61 | 82.1 | 31.06 | 0.0721 | 0.54 | 14.04 | 0
August | 14 | 8PM to 9PM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
August | 14 | 9PM to 10PM | 73.9 | 64.8 | 60.1 | 79.5 | 30.17 | 0.0724 | 0.52 | 13.98 | 0
August | 14 | 10PM to 11PM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
August | 14 | 11PM to 12AM | 72 | 64.7 | 61 | 82.1 | 30.09 | 0.0726 | 0.54 | 13.93 | 0
August | 15 | 12AM to 1AM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
August | 15 | 1AM to 2AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
August | 15 | 2AM to 3AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
August | 15 | 3AM to 4AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
August | 15 | 4AM to 5AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
August | 15 | 5AM to 6AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
August | 15 | 6AM to 7AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
August | 15 | 7AM to 8AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
August | 15 | 8AM to 9AM | 75.9 | 67.8 | 64 | 91.7 | 32.56 | 0.072 | 0.6 | 14.07 | 0
August | 15 | 9AM to 10AM | 75.9 | 69.1 | 66 | 98.4 | 33.6 | 0.072 | 0.64 | 14.09 | 0
August | 15 | 10AM to 11AM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
August | 15 | 11AM to 12PM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
August | 15 | 12PM to 1PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 15 | 1PM to 2PM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 15 | 2PM to 3PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
August | 15 | 3PM to 4PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
August | 15 | 4PM to 5PM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
August | 15 | 5PM to 6PM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
August | 15 | 6PM to 7PM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
August | 15 | 7PM to 8PM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
August | 15 | 8PM to 9PM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
August | 15 | 9PM to 10PM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
August | 15 | 10PM to 11PM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
August | 15 | 11PM to 12AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
August | 16 | 12AM to 1AM | 72 | 71.3 | 71.1 | 117.4 | 35.61 | 0.0724 | 0.77 | 14.04 | 0
August | 16 | 1AM to 2AM | 72 | 71.3 | 71.1 | 117.4 | 35.61 | 0.0724 | 0.77 | 14.04 | 0
August | 16 | 2AM to 3AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 16 | 3AM to 4AM | 71.1 | 69.7 | 69.1 | 109.6 | 34.16 | 0.0726 | 0.72 | 14 | 0
August | 16 | 4AM to 5AM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 16 | 5AM to 6AM | 71.1 | 69.7 | 69.1 | 109.6 | 34.16 | 0.0726 | 0.72 | 14 | 0
August | 16 | 6AM to 7AM | 72 | 69.9 | 69.1 | 109.6 | 34.38 | 0.0724 | 0.72 | 14.02 | 0
August | 16 | 7AM to 8AM | 72 | 69.9 | 69.1 | 109.6 | 34.38 | 0.0724 | 0.72 | 14.02 | 0
August | 16 | 8AM to 9AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 16 | 9AM to 10AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 16 | 10AM to 11AM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 16 | 11AM to 12PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 16 | 12PM to 1PM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 16 | 1PM to 2PM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 16 | 2PM to 3PM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
August | 16 | 3PM to 4PM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
August | 16 | 4PM to 5PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
August | 16 | 5PM to 6PM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
August | 16 | 6PM to 7PM | 73.9 | 71.9 | 71.1 | 117.4 | 36.1 | 0.0721 | 0.77 | 14.1 | 0
August | 16 | 7PM to 8PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
August | 16 | 8PM to 9PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 16 | 9PM to 10PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 16 | 10PM to 11PM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 16 | 11PM to 12AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 17 | 12AM to 1AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 17 | 1AM to 2AM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 17 | 2AM to 3AM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 17 | 3AM to 4AM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 17 | 4AM to 5AM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 17 | 5AM to 6AM | 71.1 | 70.3 | 70 | 113.1 | 34.71 | 0.0725 | 0.74 | 14.01 | 0
August | 17 | 6AM to 7AM | 73 | 71.6 | 71.1 | 117.4 | 35.88 | 0.0723 | 0.77 | 14.07 | 0
August | 17 | 7AM to 8AM | 77 | 73.4 | 72 | 121.2 | 37.44 | 0.0717 | 0.79 | 14.19 | 0
August | 17 | 8AM to 9AM | 82 | 74.7 | 72 | 121.2 | 38.69 | 0.071 | 0.79 | 14.32 | 0
August | 17 | 9AM to 10AM | 87.1 | 76.7 | 73 | 125.8 | 40.67 | 0.0703 | 0.82 | 14.47 | 0
August | 17 | 10AM to 11AM | 89.1 | 77.8 | 73.9 | 129.8 | 41.78 | 0.0701 | 0.85 | 14.54 | 0
August | 17 | 11AM to 12PM | 91.9 | 78 | 73 | 125.8 | 41.87 | 0.0697 | 0.82 | 14.6 | 0
August | 17 | 12PM to 1PM | 91.9 | 78.5 | 73.9 | 129.8 | 42.5 | 0.0697 | 0.85 | 14.61 | 0
August | 17 | 1PM to 2PM | 93 | 78.8 | 73.9 | 129.8 | 42.77 | 0.0696 | 0.85 | 14.64 | 0
August | 17 | 2PM to 3PM | 93 | 77 | 71.1 | 117.4 | 40.82 | 0.0696 | 0.77 | 14.6 | 0
August | 17 | 3PM to 4PM | 93 | 77 | 71.1 | 117.4 | 40.82 | 0.0696 | 0.77 | 14.6 | 0
August | 17 | 4PM to 5PM | 93 | 76.3 | 70 | 113.1 | 40.14 | 0.0697 | 0.74 | 14.59 | 0
August | 17 | 5PM to 6PM | 91 | 77 | 72 | 121.2 | 40.92 | 0.0699 | 0.79 | 14.56 | 0
August | 17 | 6PM to 7PM | 88 | 77 | 73 | 125.8 | 40.89 | 0.0702 | 0.82 | 14.49 | 0
August | 17 | 7PM to 8PM | 87.1 | 76 | 72 | 121.2 | 39.94 | 0.0704 | 0.79 | 14.46 | 0
August | 17 | 8PM to 9PM | 84.9 | 75.5 | 72 | 121.2 | 39.4 | 0.0707 | 0.79 | 14.4 | 0
August | 17 | 9PM to 10PM | 82.9 | 74.9 | 72 | 121.2 | 38.91 | 0.0709 | 0.79 | 14.35 | 0
August | 17 | 10PM to 11PM | 82 | 74.7 | 72 | 121.2 | 38.69 | 0.071 | 0.79 | 14.32 | 0
August | 17 | 11PM to 12AM | 81 | 74.4 | 72 | 121.2 | 38.42 | 0.0712 | 0.79 | 14.29 | 0
August | 18 | 12AM to 1AM | 81 | 73.8 | 71.1 | 117.4 | 37.84 | 0.0712 | 0.77 | 14.28 | 0
August | 18 | 1AM to 2AM | 80.1 | 73.6 | 71.1 | 117.4 | 37.61 | 0.0713 | 0.77 | 14.26 | 0
August | 18 | 2AM to 3AM | 80.1 | 73.6 | 71.1 | 117.4 | 37.61 | 0.0713 | 0.77 | 14.26 | 0
August | 18 | 3AM to 4AM | 79 | 73.3 | 71.1 | 117.4 | 37.35 | 0.0715 | 0.77 | 14.23 | 0
August | 18 | 4AM to 5AM | 78.1 | 72.3 | 70 | 113.1 | 36.44 | 0.0716 | 0.74 | 14.19 | 0
August | 18 | 5AM to 6AM | 78.1 | 72.3 | 70 | 113.1 | 36.44 | 0.0716 | 0.74 | 14.19 | 0
August | 18 | 6AM to 7AM | 80.1 | 72.8 | 70 | 113.1 | 36.93 | 0.0713 | 0.74 | 14.24 | 0
August | 18 | 7AM to 8AM | 82.9 | 74.3 | 71.1 | 117.4 | 38.33 | 0.0709 | 0.77 | 14.33 | 0
August | 18 | 8AM to 9AM | 87.1 | 76 | 72 | 121.2 | 39.94 | 0.0704 | 0.79 | 14.46 | 0
August | 18 | 9AM to 10AM | 90 | 76.8 | 72 | 121.2 | 40.65 | 0.07 | 0.79 | 14.53 | 0
August | 18 | 10AM to 11AM | 91 | 77 | 72 | 121.2 | 40.92 | 0.0699 | 0.79 | 14.56 | 0
August | 18 | 11AM to 12PM | 91.9 | 76 | 70 | 113.1 | 39.87 | 0.0698 | 0.74 | 14.56 | 0
August | 18 | 12PM to 1PM | 93 | 74.4 | 66.9 | 101.5 | 38.32 | 0.0697 | 0.67 | 14.55 | 0
August | 18 | 1PM to 2PM | 93.9 | 75.3 | 68 | 105.5 | 39.16 | 0.0696 | 0.69 | 14.58 | 0
August | 18 | 2PM to 3PM | 93.9 | 76 | 69.1 | 109.6 | 39.8 | 0.0696 | 0.72 | 14.6 | 0
August | 18 | 3PM to 4PM | 93 | 75.1 | 68 | 105.5 | 38.94 | 0.0697 | 0.69 | 14.56 | 0
August | 18 | 4PM to 5PM | 91.9 | 75.4 | 69.1 | 109.6 | 39.32 | 0.0698 | 0.72 | 14.55 | 0
August | 18 | 5PM to 6PM | 91 | 75.2 | 69.1 | 109.6 | 39.09 | 0.0699 | 0.72 | 14.52 | 0
August | 18 | 6PM to 7PM | 89.1 | 75.3 | 70 | 113.1 | 39.16 | 0.0702 | 0.74 | 14.48 | 0
August | 18 | 7PM to 8PM | 87.1 | 75.4 | 71.1 | 117.4 | 39.35 | 0.0704 | 0.77 | 14.44 | 0
August | 18 | 8PM to 9PM | 84.9 | 74.9 | 71.1 | 117.4 | 38.82 | 0.0707 | 0.77 | 14.39 | 0
August | 18 | 9PM to 10PM | 84 | 75.2 | 72 | 121.2 | 39.18 | 0.0708 | 0.79 | 14.37 | 0
August | 18 | 10PM to 11PM | 82.9 | 74.9 | 72 | 121.2 | 38.91 | 0.0709 | 0.79 | 14.35 | 0
August | 18 | 11PM to 12AM | 82 | 74.7 | 72 | 121.2 | 38.69 | 0.071 | 0.79 | 14.32 | 0
August | 19 | 12AM to 1AM | 81 | 74.4 | 72 | 121.2 | 38.42 | 0.0712 | 0.79 | 14.29 | 0
August | 19 | 1AM to 2AM | 79 | 73.9 | 72 | 121.2 | 37.93 | 0.0714 | 0.79 | 14.24 | 0
August | 19 | 2AM to 3AM | 80.1 | 72.8 | 70 | 113.1 | 36.93 | 0.0713 | 0.74 | 14.24 | 0
August | 19 | 3AM to 4AM | 79 | 72.5 | 70 | 113.1 | 36.66 | 0.0715 | 0.74 | 14.22 | 0
August | 19 | 4AM to 5AM | 78.1 | 71.7 | 69.1 | 109.6 | 35.89 | 0.0716 | 0.72 | 14.18 | 0
August | 19 | 5AM to 6AM | 78.1 | 71.7 | 69.1 | 109.6 | 35.89 | 0.0716 | 0.72 | 14.18 | 0
August | 19 | 6AM to 7AM | 80.1 | 72.2 | 69.1 | 109.6 | 36.38 | 0.0714 | 0.72 | 14.23 | 0
August | 19 | 7AM to 8AM | 84 | 73.9 | 70 | 113.1 | 37.91 | 0.0708 | 0.74 | 14.35 | 0
August | 19 | 8AM to 9AM | 87.1 | 75.4 | 71.1 | 117.4 | 39.35 | 0.0704 | 0.77 | 14.44 | 0
August | 19 | 9AM to 10AM | 90 | 75.5 | 70 | 113.1 | 39.38 | 0.0701 | 0.74 | 14.51 | 0
August | 19 | 10AM to 11AM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
August | 19 | 11AM to 12PM | 93 | 75.7 | 69.1 | 109.6 | 39.58 | 0.0697 | 0.72 | 14.57 | 0
August | 19 | 12PM to 1PM | 95 | 75.6 | 68 | 105.5 | 39.43 | 0.0695 | 0.69 | 14.61 | 0
August | 19 | 1PM to 2PM | 95 | 75 | 66.9 | 101.5 | 38.8 | 0.0695 | 0.67 | 14.6 | 0
August | 19 | 2PM to 3PM | 95 | 75.6 | 68 | 105.5 | 39.43 | 0.0695 | 0.69 | 14.61 | 0
August | 19 | 3PM to 4PM | 93.9 | 76.5 | 70 | 113.1 | 40.36 | 0.0696 | 0.74 | 14.61 | 0
August | 19 | 4PM to 5PM | 93.9 | 76 | 69.1 | 109.6 | 39.8 | 0.0696 | 0.72 | 14.6 | 0
August | 19 | 5PM to 6PM | 91.9 | 74.8 | 68 | 105.5 | 38.67 | 0.0698 | 0.69 | 14.53 | 0
August | 19 | 6PM to 7PM | 89.1 | 75.3 | 70 | 113.1 | 39.16 | 0.0702 | 0.74 | 14.48 | 0
August | 19 | 7PM to 8PM | 88 | 75.7 | 71.1 | 117.4 | 39.57 | 0.0703 | 0.77 | 14.47 | 0
August | 19 | 8PM to 9PM | 86 | 75.7 | 72 | 121.2 | 39.67 | 0.0705 | 0.79 | 14.43 | 0
August | 19 | 9PM to 10PM | 84.9 | 75.5 | 72 | 121.2 | 39.4 | 0.0707 | 0.79 | 14.4 | 0
August | 19 | 10PM to 11PM | 84 | 74.6 | 71.1 | 117.4 | 38.59 | 0.0708 | 0.77 | 14.36 | 0
August | 19 | 11PM to 12AM | 82.9 | 74.3 | 71.1 | 117.4 | 38.33 | 0.0709 | 0.77 | 14.33 | 0
August | 20 | 12AM to 1AM | 82 | 73.4 | 70 | 113.1 | 37.42 | 0.0711 | 0.74 | 14.3 | 0
August | 20 | 1AM to 2AM | 80.1 | 74.2 | 72 | 121.2 | 38.2 | 0.0713 | 0.79 | 14.27 | 0
August | 20 | 2AM to 3AM | 78.1 | 73.6 | 72 | 121.2 | 37.71 | 0.0716 | 0.79 | 14.22 | 0
August | 20 | 3AM to 4AM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
August | 20 | 4AM to 5AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 20 | 5AM to 6AM | 72 | 70.6 | 70 | 113.1 | 34.93 | 0.0724 | 0.74 | 14.03 | 0
August | 20 | 6AM to 7AM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
August | 20 | 7AM to 8AM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
August | 20 | 8AM to 9AM | 80.1 | 73.6 | 71.1 | 117.4 | 37.61 | 0.0713 | 0.77 | 14.26 | 0
August | 20 | 9AM to 10AM | 82 | 74.7 | 72 | 121.2 | 38.69 | 0.071 | 0.79 | 14.32 | 0
August | 20 | 10AM to 11AM | 84.9 | 76.2 | 73 | 125.8 | 40.13 | 0.0706 | 0.82 | 14.41 | 0
August | 20 | 11AM to 12PM | 88 | 77 | 73 | 125.8 | 40.89 | 0.0702 | 0.82 | 14.49 | 0
August | 20 | 12PM to 1PM | 89.1 | 77.8 | 73.9 | 129.8 | 41.78 | 0.0701 | 0.85 | 14.54 | 0
August | 20 | 1PM to 2PM | 90 | 77.5 | 73 | 125.8 | 41.38 | 0.07 | 0.82 | 14.55 | 0
August | 20 | 2PM to 3PM | 91 | 77.7 | 73 | 125.8 | 41.65 | 0.0698 | 0.82 | 14.57 | 0
August | 20 | 3PM to 4PM | 91 | 76.5 | 71.1 | 117.4 | 40.33 | 0.0699 | 0.77 | 14.55 | 0
August | 20 | 4PM to 5PM | 90 | 76.8 | 72 | 121.2 | 40.65 | 0.07 | 0.79 | 14.53 | 0
August | 20 | 5PM to 6PM | 88 | 75.7 | 71.1 | 117.4 | 39.57 | 0.0703 | 0.77 | 14.47 | 0
August | 20 | 6PM to 7PM | 84.9 | 74.2 | 70 | 113.1 | 38.13 | 0.0707 | 0.74 | 14.37 | 0
August | 20 | 7PM to 8PM | 82.9 | 73.6 | 70 | 113.1 | 37.64 | 0.071 | 0.74 | 14.32 | 0
August | 20 | 8PM to 9PM | 81 | 73.1 | 70 | 113.1 | 37.15 | 0.0712 | 0.74 | 14.27 | 0
August | 20 | 9PM to 10PM | 78.1 | 71.7 | 69.1 | 109.6 | 35.89 | 0.0716 | 0.72 | 14.18 | 0
August | 20 | 10PM to 11PM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
August | 20 | 11PM to 12AM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
August | 21 | 12AM to 1AM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
August | 21 | 1AM to 2AM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
August | 21 | 2AM to 3AM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
August | 21 | 3AM to 4AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 21 | 4AM to 5AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 21 | 5AM to 6AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 21 | 6AM to 7AM | 73.9 | 72.5 | 72 | 121.2 | 36.68 | 0.0721 | 0.79 | 14.11 | 0
August | 21 | 7AM to 8AM | 75 | 72.2 | 71.1 | 117.4 | 36.37 | 0.072 | 0.77 | 14.12 | 0
August | 21 | 8AM to 9AM | 73.9 | 72.5 | 72 | 121.2 | 36.68 | 0.0721 | 0.79 | 14.11 | 0
August | 21 | 9AM to 10AM | 75 | 72.8 | 72 | 121.2 | 36.95 | 0.072 | 0.79 | 14.14 | 0
August | 21 | 10AM to 11AM | 77 | 72.7 | 71.1 | 117.4 | 36.86 | 0.0717 | 0.77 | 14.18 | 0
August | 21 | 11AM to 12PM | 78.1 | 72.3 | 70 | 113.1 | 36.44 | 0.0716 | 0.74 | 14.19 | 0
August | 21 | 12PM to 1PM | 78.1 | 72.3 | 70 | 113.1 | 36.44 | 0.0716 | 0.74 | 14.19 | 0
August | 21 | 1PM to 2PM | 78.1 | 72.3 | 70 | 113.1 | 36.44 | 0.0716 | 0.74 | 14.19 | 0
August | 21 | 2PM to 3PM | 77 | 72 | 70 | 113.1 | 36.18 | 0.0717 | 0.74 | 14.16 | 0
August | 21 | 3PM to 4PM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
August | 21 | 4PM to 5PM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
August | 21 | 5PM to 6PM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
August | 21 | 6PM to 7PM | 75 | 70.1 | 68 | 105.5 | 34.5 | 0.0721 | 0.69 | 14.09 | 0
August | 21 | 7PM to 8PM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
August | 21 | 8PM to 9PM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
August | 21 | 9PM to 10PM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 21 | 10PM to 11PM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 21 | 11PM to 12AM | 72 | 69.2 | 68 | 105.5 | 33.74 | 0.0725 | 0.69 | 14.01 | 0
August | 22 | 12AM to 1AM | 72 | 69.2 | 68 | 105.5 | 33.74 | 0.0725 | 0.69 | 14.01 | 0
August | 22 | 1AM to 2AM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
August | 22 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
August | 22 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
August | 22 | 4AM to 5AM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
August | 22 | 5AM to 6AM | 70 | 67.3 | 66 | 98.4 | 32.14 | 0.0728 | 0.64 | 13.93 | 0
August | 22 | 6AM to 7AM | 69.1 | 67.6 | 66.9 | 101.5 | 32.42 | 0.0729 | 0.67 | 13.92 | 0
August | 22 | 7AM to 8AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
August | 22 | 8AM to 9AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
August | 22 | 9AM to 10AM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
August | 22 | 10AM to 11AM | 73.9 | 69.1 | 66.9 | 101.5 | 33.61 | 0.0722 | 0.67 | 14.05 | 0
August | 22 | 11AM to 12PM | 73.9 | 69.1 | 66.9 | 101.5 | 33.61 | 0.0722 | 0.67 | 14.05 | 0
August | 22 | 12PM to 1PM | 73.9 | 69.1 | 66.9 | 101.5 | 33.61 | 0.0722 | 0.67 | 14.05 | 0
August | 22 | 1PM to 2PM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
August | 22 | 2PM to 3PM | 75 | 70.1 | 68 | 105.5 | 34.5 | 0.0721 | 0.69 | 14.09 | 0
August | 22 | 3PM to 4PM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
August | 22 | 4PM to 5PM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
August | 22 | 5PM to 6PM | 75 | 70.1 | 68 | 105.5 | 34.5 | 0.0721 | 0.69 | 14.09 | 0
August | 22 | 6PM to 7PM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
August | 22 | 7PM to 8PM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
August | 22 | 8PM to 9PM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 22 | 9PM to 10PM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 22 | 10PM to 11PM | 73.9 | 71.1 | 70 | 113.1 | 35.42 | 0.0722 | 0.74 | 14.08 | 0
August | 22 | 11PM to 12AM | 73 | 70.9 | 70 | 113.1 | 35.2 | 0.0723 | 0.74 | 14.06 | 0
August | 23 | 12AM to 1AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 23 | 1AM to 2AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 23 | 2AM to 3AM | 73 | 70.2 | 69.1 | 109.6 | 34.65 | 0.0723 | 0.72 | 14.05 | 0
August | 23 | 3AM to 4AM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
August | 23 | 4AM to 5AM | 72 | 69.2 | 68 | 105.5 | 33.74 | 0.0725 | 0.69 | 14.01 | 0
August | 23 | 5AM to 6AM | 72 | 69.2 | 68 | 105.5 | 33.74 | 0.0725 | 0.69 | 14.01 | 0
August | 23 | 6AM to 7AM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
August | 23 | 7AM to 8AM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
August | 23 | 8AM to 9AM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
August | 23 | 9AM to 10AM | 78.1 | 71.7 | 69.1 | 109.6 | 35.89 | 0.0716 | 0.72 | 14.18 | 0
August | 23 | 10AM to 11AM | 81 | 72.5 | 69.1 | 109.6 | 36.6 | 0.0712 | 0.72 | 14.26 | 0
August | 23 | 11AM to 12PM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
August | 23 | 12PM to 1PM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
August | 23 | 1PM to 2PM | 84.9 | 72.2 | 66.9 | 101.5 | 36.32 | 0.0708 | 0.67 | 14.34 | 0
August | 23 | 2PM to 3PM | 84.9 | 71 | 64.9 | 94.6 | 35.24 | 0.0708 | 0.62 | 14.31 | 0
August | 23 | 3PM to 4PM | 84 | 71.4 | 66 | 98.4 | 35.6 | 0.0709 | 0.64 | 14.3 | 0
August | 23 | 4PM to 5PM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
August | 23 | 5PM to 6PM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
August | 23 | 6PM to 7PM | 79 | 71.2 | 68 | 105.5 | 35.47 | 0.0715 | 0.69 | 14.19 | 0
August | 23 | 7PM to 8PM | 77 | 70.7 | 68 | 105.5 | 34.99 | 0.0718 | 0.69 | 14.14 | 0
August | 23 | 8PM to 9PM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
August | 23 | 9PM to 10PM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
August | 23 | 10PM to 11PM | 73.9 | 69.1 | 66.9 | 101.5 | 33.61 | 0.0722 | 0.67 | 14.05 | 0
August | 23 | 11PM to 12AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
August | 24 | 12AM to 1AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
August | 24 | 1AM to 2AM | 72 | 68.5 | 66.9 | 101.5 | 33.13 | 0.0725 | 0.67 | 13.99 | 0
August | 24 | 2AM to 3AM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
August | 24 | 3AM to 4AM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
August | 24 | 4AM to 5AM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
August | 24 | 5AM to 6AM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
August | 24 | 6AM to 7AM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
August | 24 | 7AM to 8AM | 77 | 70 | 66.9 | 101.5 | 34.37 | 0.0718 | 0.67 | 14.13 | 0
August | 24 | 8AM to 9AM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
August | 24 | 9AM to 10AM | 82 | 71.4 | 66.9 | 101.5 | 35.61 | 0.0711 | 0.67 | 14.26 | 0
August | 24 | 10AM to 11AM | 84 | 72 | 66.9 | 101.5 | 36.1 | 0.0709 | 0.67 | 14.31 | 0
August | 24 | 11AM to 12PM | 86 | 73.9 | 69.1 | 109.6 | 37.85 | 0.0706 | 0.72 | 14.39 | 0
August | 24 | 12PM to 1PM | 87.1 | 74.2 | 69.1 | 109.6 | 38.11 | 0.0704 | 0.72 | 14.42 | 0
August | 24 | 1PM to 2PM | 88 | 74.4 | 69.1 | 109.6 | 38.34 | 0.0703 | 0.72 | 14.44 | 0
August | 24 | 2PM to 3PM | 87.1 | 74.2 | 69.1 | 109.6 | 38.11 | 0.0704 | 0.72 | 14.42 | 0
August | 24 | 3PM to 4PM | 87.1 | 74.2 | 69.1 | 109.6 | 38.11 | 0.0704 | 0.72 | 14.42 | 0
August | 24 | 4PM to 5PM | 87.1 | 73.5 | 68 | 105.5 | 37.47 | 0.0705 | 0.69 | 14.4 | 0
August | 24 | 5PM to 6PM | 84 | 72.7 | 68 | 105.5 | 36.72 | 0.0709 | 0.69 | 14.32 | 0
August | 24 | 6PM to 7PM | 82 | 72.1 | 68 | 105.5 | 36.23 | 0.0711 | 0.69 | 14.27 | 0
August | 24 | 7PM to 8PM | 80.1 | 71.5 | 68 | 105.5 | 35.74 | 0.0714 | 0.69 | 14.22 | 0
August | 24 | 8PM to 9PM | 78.1 | 71 | 68 | 105.5 | 35.25 | 0.0716 | 0.69 | 14.17 | 0
August | 24 | 9PM to 10PM | 77 | 70.7 | 68 | 105.5 | 34.99 | 0.0718 | 0.69 | 14.14 | 0
August | 24 | 10PM to 11PM | 75.9 | 70.4 | 68 | 105.5 | 34.72 | 0.0719 | 0.69 | 14.11 | 0
August | 24 | 11PM to 12AM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
August | 25 | 12AM to 1AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
August | 25 | 1AM to 2AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
August | 25 | 2AM to 3AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
August | 25 | 3AM to 4AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
August | 25 | 4AM to 5AM | 72 | 68.5 | 66.9 | 101.5 | 33.13 | 0.0725 | 0.67 | 13.99 | 0
August | 25 | 5AM to 6AM | 72 | 68.5 | 66.9 | 101.5 | 33.13 | 0.0725 | 0.67 | 13.99 | 0
August | 25 | 6AM to 7AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
August | 25 | 7AM to 8AM | 78.1 | 69.7 | 66 | 98.4 | 34.14 | 0.0717 | 0.64 | 14.14 | 0
August | 25 | 8AM to 9AM | 81 | 71.1 | 66.9 | 101.5 | 35.34 | 0.0713 | 0.67 | 14.23 | 0
August | 25 | 9AM to 10AM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
August | 25 | 10AM to 11AM | 86 | 73.9 | 69.1 | 109.6 | 37.85 | 0.0706 | 0.72 | 14.39 | 0
August | 25 | 11AM to 12PM | 87.1 | 74.7 | 70 | 113.1 | 38.67 | 0.0704 | 0.74 | 14.43 | 0
August | 25 | 12PM to 1PM | 89.1 | 75.9 | 71.1 | 117.4 | 39.84 | 0.0701 | 0.77 | 14.5 | 0
August | 25 | 1PM to 2PM | 89.1 | 75.9 | 71.1 | 117.4 | 39.84 | 0.0701 | 0.77 | 14.5 | 0
August | 25 | 2PM to 3PM | 89.1 | 75.9 | 71.1 | 117.4 | 39.84 | 0.0701 | 0.77 | 14.5 | 0
August | 25 | 3PM to 4PM | 89.1 | 76.5 | 72 | 121.2 | 40.43 | 0.0701 | 0.79 | 14.51 | 0
August | 25 | 4PM to 5PM | 87.1 | 76 | 72 | 121.2 | 39.94 | 0.0704 | 0.79 | 14.46 | 0
August | 25 | 5PM to 6PM | 86 | 75.7 | 72 | 121.2 | 39.67 | 0.0705 | 0.79 | 14.43 | 0
August | 25 | 6PM to 7PM | 84 | 75.2 | 72 | 121.2 | 39.18 | 0.0708 | 0.79 | 14.37 | 0
August | 25 | 7PM to 8PM | 82.9 | 74.9 | 72 | 121.2 | 38.91 | 0.0709 | 0.79 | 14.35 | 0
August | 25 | 8PM to 9PM | 82 | 74.7 | 72 | 121.2 | 38.69 | 0.071 | 0.79 | 14.32 | 0
August | 25 | 9PM to 10PM | 81 | 74.4 | 72 | 121.2 | 38.42 | 0.0712 | 0.79 | 14.29 | 0
August | 25 | 10PM to 11PM | 80.1 | 74.2 | 72 | 121.2 | 38.2 | 0.0713 | 0.79 | 14.27 | 0
August | 25 | 11PM to 12AM | 79 | 73.3 | 71.1 | 117.4 | 37.35 | 0.0715 | 0.77 | 14.23 | 0
August | 26 | 12AM to 1AM | 78.1 | 71.7 | 69.1 | 109.6 | 35.89 | 0.0716 | 0.72 | 14.18 | 0
August | 26 | 1AM to 2AM | 77 | 71.4 | 69.1 | 109.6 | 35.63 | 0.0718 | 0.72 | 14.15 | 0
August | 26 | 2AM to 3AM | 77 | 71.4 | 69.1 | 109.6 | 35.63 | 0.0718 | 0.72 | 14.15 | 0
August | 26 | 3AM to 4AM | 75.9 | 71.1 | 69.1 | 109.6 | 35.36 | 0.0719 | 0.72 | 14.12 | 0
August | 26 | 4AM to 5AM | 75 | 70.8 | 69.1 | 109.6 | 35.14 | 0.072 | 0.72 | 14.1 | 0
August | 26 | 5AM to 6AM | 73.9 | 70.5 | 69.1 | 109.6 | 34.87 | 0.0722 | 0.72 | 14.07 | 0
August | 26 | 6AM to 7AM | 75.9 | 71.7 | 70 | 113.1 | 35.91 | 0.0719 | 0.74 | 14.13 | 0
August | 26 | 7AM to 8AM | 80.1 | 72.2 | 69.1 | 109.6 | 36.38 | 0.0714 | 0.72 | 14.23 | 0
August | 26 | 8AM to 9AM | 82.9 | 73.6 | 70 | 113.1 | 37.64 | 0.071 | 0.74 | 14.32 | 0
August | 26 | 9AM to 10AM | 86 | 75.2 | 71.1 | 117.4 | 39.08 | 0.0705 | 0.77 | 14.41 | 0
August | 26 | 10AM to 11AM | 89.1 | 76.5 | 72 | 121.2 | 40.43 | 0.0701 | 0.79 | 14.51 | 0
August | 26 | 11AM to 12PM | 91 | 77.7 | 73 | 125.8 | 41.65 | 0.0698 | 0.82 | 14.57 | 0
August | 26 | 12PM to 1PM | 93 | 78.2 | 73 | 125.8 | 42.14 | 0.0696 | 0.82 | 14.63 | 0
August | 26 | 1PM to 2PM | 93.9 | 79 | 73.9 | 129.8 | 42.99 | 0.0695 | 0.85 | 14.66 | 0
August | 26 | 2PM to 3PM | 93.9 | 79 | 73.9 | 129.8 | 42.99 | 0.0695 | 0.85 | 14.66 | 0
August | 26 | 3PM to 4PM | 93.9 | 79 | 73.9 | 129.8 | 42.99 | 0.0695 | 0.85 | 14.66 | 0
August | 26 | 4PM to 5PM | 93 | 78.2 | 73 | 125.8 | 42.14 | 0.0696 | 0.82 | 14.63 | 0
August | 26 | 5PM to 6PM | 91 | 78.3 | 73.9 | 129.8 | 42.27 | 0.0698 | 0.85 | 14.59 | 0
August | 26 | 6PM to 7PM | 89.1 | 77.8 | 73.9 | 129.8 | 41.78 | 0.0701 | 0.85 | 14.54 | 0
August | 26 | 7PM to 8PM | 87.1 | 77.3 | 73.9 | 129.8 | 41.29 | 0.0703 | 0.85 | 14.48 | 0
August | 26 | 8PM to 9PM | 86 | 77.1 | 73.9 | 129.8 | 41.02 | 0.0705 | 0.85 | 14.45 | 0
August | 26 | 9PM to 10PM | 84 | 76.6 | 73.9 | 129.8 | 40.53 | 0.0707 | 0.85 | 14.4 | 0
August | 26 | 10PM to 11PM | 82.9 | 76.3 | 73.9 | 129.8 | 40.26 | 0.0709 | 0.85 | 14.37 | 0
August | 26 | 11PM to 12AM | 81 | 75.8 | 73.9 | 129.8 | 39.77 | 0.0711 | 0.85 | 14.32 | 0
August | 27 | 12AM to 1AM | 80.1 | 74.9 | 73 | 125.8 | 38.93 | 0.0713 | 0.82 | 14.28 | 0
August | 27 | 1AM to 2AM | 80.1 | 75.6 | 73.9 | 129.8 | 39.55 | 0.0712 | 0.85 | 14.3 | 0
August | 27 | 2AM to 3AM | 79 | 74.6 | 73 | 125.8 | 38.66 | 0.0714 | 0.82 | 14.26 | 0
August | 27 | 3AM to 4AM | 79 | 74.6 | 73 | 125.8 | 38.66 | 0.0714 | 0.82 | 14.26 | 0
August | 27 | 4AM to 5AM | 79 | 74.6 | 73 | 125.8 | 38.66 | 0.0714 | 0.82 | 14.26 | 0
August | 27 | 5AM to 6AM | 78.1 | 74.4 | 73 | 125.8 | 38.43 | 0.0715 | 0.82 | 14.23 | 0
August | 27 | 6AM to 7AM | 79 | 75.3 | 73.9 | 129.8 | 39.28 | 0.0714 | 0.85 | 14.27 | 0
August | 27 | 7AM to 8AM | 84.9 | 76.8 | 73.9 | 129.8 | 40.76 | 0.0706 | 0.85 | 14.43 | 0
August | 27 | 8AM to 9AM | 88 | 77.6 | 73.9 | 129.8 | 41.51 | 0.0702 | 0.85 | 14.51 | 0
August | 27 | 9AM to 10AM | 91.9 | 79.3 | 75 | 134.7 | 43.27 | 0.0697 | 0.88 | 14.63 | 0
August | 27 | 10AM to 11AM | 93 | 79.5 | 75 | 134.7 | 43.54 | 0.0695 | 0.88 | 14.66 | 0
August | 27 | 11AM to 12PM | 95 | 79.3 | 73.9 | 129.8 | 43.26 | 0.0693 | 0.85 | 14.69 | 0
August | 27 | 12PM to 1PM | 97 | 80.5 | 75 | 134.7 | 44.53 | 0.069 | 0.88 | 14.76 | 0
August | 27 | 1PM to 2PM | 98.1 | 80 | 73.9 | 129.8 | 44.02 | 0.0689 | 0.85 | 14.77 | 0
August | 27 | 2PM to 3PM | 96.1 | 79 | 73 | 125.8 | 42.9 | 0.0692 | 0.82 | 14.71 | 0
August | 27 | 3PM to 4PM | 98.1 | 78.8 | 72 | 121.2 | 42.66 | 0.069 | 0.79 | 14.75 | 0
August | 27 | 4PM to 5PM | 96.1 | 77.7 | 71.1 | 117.4 | 41.58 | 0.0693 | 0.77 | 14.68 | 0
August | 27 | 5PM to 6PM | 93.9 | 78.4 | 73 | 125.8 | 42.36 | 0.0695 | 0.82 | 14.65 | 0
August | 27 | 6PM to 7PM | 91.9 | 78 | 73 | 125.8 | 41.87 | 0.0697 | 0.82 | 14.6 | 0
August | 27 | 7PM to 8PM | 89.1 | 78.6 | 75 | 134.7 | 42.56 | 0.07 | 0.88 | 14.55 | 0
August | 27 | 8PM to 9PM | 88 | 77.6 | 73.9 | 129.8 | 41.51 | 0.0702 | 0.85 | 14.51 | 0
August | 27 | 9PM to 10PM | 86 | 77.8 | 75 | 134.7 | 41.8 | 0.0704 | 0.88 | 14.47 | 0
August | 27 | 10PM to 11PM | 84 | 77.3 | 75 | 134.7 | 41.3 | 0.0707 | 0.88 | 14.42 | 0
August | 27 | 11PM to 12AM | 82.9 | 77.1 | 75 | 134.7 | 41.04 | 0.0708 | 0.88 | 14.39 | 0
August | 28 | 12AM to 1AM | 82.9 | 76.3 | 73.9 | 129.8 | 40.26 | 0.0709 | 0.85 | 14.37 | 0
August | 28 | 1AM to 2AM | 82 | 75.4 | 73 | 125.8 | 39.42 | 0.071 | 0.82 | 14.34 | 0
August | 28 | 2AM to 3AM | 82 | 74.7 | 72 | 121.2 | 38.69 | 0.071 | 0.79 | 14.32 | 0
August | 28 | 3AM to 4AM | 81 | 74.4 | 72 | 121.2 | 38.42 | 0.0712 | 0.79 | 14.29 | 0
August | 28 | 4AM to 5AM | 81 | 73.8 | 71.1 | 117.4 | 37.84 | 0.0712 | 0.77 | 14.28 | 0
August | 28 | 5AM to 6AM | 80.1 | 72.8 | 70 | 113.1 | 36.93 | 0.0713 | 0.74 | 14.24 | 0
August | 28 | 6AM to 7AM | 82.9 | 74.3 | 71.1 | 117.4 | 38.33 | 0.0709 | 0.77 | 14.33 | 0
August | 28 | 7AM to 8AM | 86 | 75.2 | 71.1 | 117.4 | 39.08 | 0.0705 | 0.77 | 14.41 | 0
August | 28 | 8AM to 9AM | 91 | 77 | 72 | 121.2 | 40.92 | 0.0699 | 0.79 | 14.56 | 0
August | 28 | 9AM to 10AM | 93 | 78.2 | 73 | 125.8 | 42.14 | 0.0696 | 0.82 | 14.63 | 0
August | 28 | 10AM to 11AM | 96.1 | 79 | 73 | 125.8 | 42.9 | 0.0692 | 0.82 | 14.71 | 0
August | 28 | 11AM to 12PM | 99 | 79.6 | 73 | 125.8 | 43.61 | 0.0689 | 0.82 | 14.78 | 0
August | 28 | 12PM to 1PM | 100 | 79.2 | 72 | 121.2 | 43.15 | 0.0687 | 0.79 | 14.8 | 0
August | 28 | 1PM to 2PM | 100.9 | 78.9 | 71.1 | 117.4 | 42.78 | 0.0687 | 0.77 | 14.81 | 0
August | 28 | 2PM to 3PM | 100 | 78 | 70 | 113.1 | 41.87 | 0.0688 | 0.74 | 14.77 | 0
August | 28 | 3PM to 4PM | 98.1 | 77.5 | 70 | 113.1 | 41.38 | 0.069 | 0.74 | 14.72 | 0
August | 28 | 4PM to 5PM | 97 | 77.3 | 70 | 113.1 | 41.11 | 0.0692 | 0.74 | 14.69 | 0
August | 28 | 5PM to 6PM | 96.1 | 77.1 | 70 | 113.1 | 40.89 | 0.0693 | 0.74 | 14.67 | 0
August | 28 | 6PM to 7PM | 93.9 | 77.2 | 71.1 | 117.4 | 41.04 | 0.0695 | 0.77 | 14.62 | 0
August | 28 | 7PM to 8PM | 91 | 77 | 72 | 121.2 | 40.92 | 0.0699 | 0.79 | 14.56 | 0
August | 28 | 8PM to 9PM | 89.1 | 76.5 | 72 | 121.2 | 40.43 | 0.0701 | 0.79 | 14.51 | 0
August | 28 | 9PM to 10PM | 88 | 76.3 | 72 | 121.2 | 40.16 | 0.0703 | 0.79 | 14.48 | 0
August | 28 | 10PM to 11PM | 86 | 76.5 | 73 | 125.8 | 40.4 | 0.0705 | 0.82 | 14.44 | 0
August | 28 | 11PM to 12AM | 84.9 | 76.8 | 73.9 | 129.8 | 40.76 | 0.0706 | 0.85 | 14.43 | 0
August | 29 | 12AM to 1AM | 84.9 | 76.2 | 73 | 125.8 | 40.13 | 0.0706 | 0.82 | 14.41 | 0
August | 29 | 1AM to 2AM | 84 | 76 | 73 | 125.8 | 39.91 | 0.0707 | 0.82 | 14.39 | 0
August | 29 | 2AM to 3AM | 82.9 | 74.9 | 72 | 121.2 | 38.91 | 0.0709 | 0.79 | 14.35 | 0
August | 29 | 3AM to 4AM | 82.9 | 74.9 | 72 | 121.2 | 38.91 | 0.0709 | 0.79 | 14.35 | 0
August | 29 | 4AM to 5AM | 82.9 | 75.7 | 73 | 125.8 | 39.64 | 0.0709 | 0.82 | 14.36 | 0
August | 29 | 5AM to 6AM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
August | 29 | 6AM to 7AM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
August | 29 | 7AM to 8AM | 79 | 70 | 66 | 98.4 | 34.36 | 0.0716 | 0.64 | 14.17 | 0
August | 29 | 8AM to 9AM | 79 | 70.5 | 66.9 | 101.5 | 34.86 | 0.0716 | 0.67 | 14.18 | 0
August | 29 | 9AM to 10AM | 77 | 71.4 | 69.1 | 109.6 | 35.63 | 0.0718 | 0.72 | 14.15 | 0
August | 29 | 10AM to 11AM | 79 | 72.5 | 70 | 113.1 | 36.66 | 0.0715 | 0.74 | 14.22 | 0
August | 29 | 11AM to 12PM | 82 | 72.8 | 69.1 | 109.6 | 36.87 | 0.0711 | 0.72 | 14.28 | 0
August | 29 | 12PM to 1PM | 84 | 73.9 | 70 | 113.1 | 37.91 | 0.0708 | 0.74 | 14.35 | 0
August | 29 | 1PM to 2PM | 86 | 72.5 | 66.9 | 101.5 | 36.59 | 0.0706 | 0.67 | 14.36 | 0
August | 29 | 2PM to 3PM | 87.1 | 71.1 | 64 | 91.7 | 35.3 | 0.0705 | 0.6 | 14.36 | 0
August | 29 | 3PM to 4PM | 88 | 70.3 | 62.1 | 85.4 | 34.53 | 0.0705 | 0.56 | 14.36 | 0
August | 29 | 4PM to 5PM | 87.1 | 70 | 62.1 | 85.4 | 34.31 | 0.0706 | 0.56 | 14.34 | 0
August | 29 | 5PM to 6PM | 86 | 68 | 59 | 76.4 | 32.64 | 0.0708 | 0.5 | 14.28 | 0
August | 29 | 6PM to 7PM | 82.9 | 68.2 | 61 | 82.1 | 32.78 | 0.0711 | 0.54 | 14.22 | 0
August | 29 | 7PM to 8PM | 81 | 68.7 | 63 | 88.2 | 33.25 | 0.0714 | 0.58 | 14.19 | 0
August | 29 | 8PM to 9PM | 79 | 68.8 | 64 | 91.7 | 33.31 | 0.0716 | 0.6 | 14.15 | 0
August | 29 | 9PM to 10PM | 78.1 | 67.3 | 62.1 | 85.4 | 32.1 | 0.0718 | 0.56 | 14.1 | 0
August | 29 | 10PM to 11PM | 75.9 | 68.4 | 64.9 | 94.6 | 33.02 | 0.072 | 0.62 | 14.08 | 0
August | 29 | 11PM to 12AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
August | 30 | 12AM to 1AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
August | 30 | 1AM to 2AM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
August | 30 | 2AM to 3AM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
August | 30 | 3AM to 4AM | 71.1 | 66.9 | 64.9 | 94.6 | 31.83 | 0.0727 | 0.62 | 13.95 | 0
August | 30 | 4AM to 5AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
August | 30 | 5AM to 6AM | 71.1 | 66.9 | 64.9 | 94.6 | 31.83 | 0.0727 | 0.62 | 13.95 | 0
August | 30 | 6AM to 7AM | 71.1 | 67.6 | 66 | 98.4 | 32.41 | 0.0726 | 0.64 | 13.96 | 0
August | 30 | 7AM to 8AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
August | 30 | 8AM to 9AM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
August | 30 | 9AM to 10AM | 82 | 69.7 | 64 | 91.7 | 34.06 | 0.0712 | 0.6 | 14.23 | 0
August | 30 | 10AM to 11AM | 84 | 70.2 | 64 | 91.7 | 34.55 | 0.0709 | 0.6 | 14.28 | 0
August | 30 | 11AM to 12PM | 84.9 | 69.9 | 63 | 88.2 | 34.22 | 0.0709 | 0.58 | 14.29 | 0
August | 30 | 12PM to 1PM | 87.1 | 70.5 | 63 | 88.2 | 34.75 | 0.0706 | 0.58 | 14.35 | 0
August | 30 | 1PM to 2PM | 86 | 70.8 | 64 | 91.7 | 35.03 | 0.0707 | 0.6 | 14.33 | 0
August | 30 | 2PM to 3PM | 87.1 | 70.5 | 63 | 88.2 | 34.75 | 0.0706 | 0.58 | 14.35 | 0
August | 30 | 3PM to 4PM | 88 | 68.6 | 59 | 76.4 | 33.13 | 0.0705 | 0.5 | 14.33 | 0
August | 30 | 4PM to 5PM | 84.9 | 69.9 | 63 | 88.2 | 34.22 | 0.0709 | 0.58 | 14.29 | 0
August | 30 | 5PM to 6PM | 82.9 | 69.3 | 63 | 88.2 | 33.74 | 0.0711 | 0.58 | 14.24 | 0
August | 30 | 6PM to 7PM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
August | 30 | 7PM to 8PM | 79 | 69.3 | 64.9 | 94.6 | 33.78 | 0.0716 | 0.62 | 14.16 | 0
August | 30 | 8PM to 9PM | 77 | 68.7 | 64.9 | 94.6 | 33.29 | 0.0719 | 0.62 | 14.1 | 0
August | 30 | 9PM to 10PM | 75.9 | 67.8 | 64 | 91.7 | 32.56 | 0.072 | 0.6 | 14.07 | 0
August | 30 | 10PM to 11PM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
August | 30 | 11PM to 12AM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
August | 31 | 12AM to 1AM | 72 | 65.4 | 62.1 | 85.4 | 30.6 | 0.0726 | 0.56 | 13.94 | 0
August | 31 | 1AM to 2AM | 70 | 64.1 | 61 | 82.1 | 29.61 | 0.0729 | 0.54 | 13.88 | 0
August | 31 | 2AM to 3AM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
August | 31 | 3AM to 4AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
August | 31 | 4AM to 5AM | 66.9 | 62.5 | 60.1 | 79.5 | 28.45 | 0.0733 | 0.52 | 13.79 | 0
August | 31 | 5AM to 6AM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
August | 31 | 6AM to 7AM | 71.1 | 63.2 | 59 | 76.4 | 28.98 | 0.0728 | 0.5 | 13.89 | 0
August | 31 | 7AM to 8AM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
August | 31 | 8AM to 9AM | 78.1 | 67.8 | 63 | 88.2 | 32.54 | 0.0718 | 0.58 | 14.11 | 0
August | 31 | 9AM to 10AM | 82 | 70.2 | 64.9 | 94.6 | 34.53 | 0.0712 | 0.62 | 14.24 | 0
August | 31 | 10AM to 11AM | 84 | 70.2 | 64 | 91.7 | 34.55 | 0.0709 | 0.6 | 14.28 | 0
August | 31 | 11AM to 12PM | 86 | 70.8 | 64 | 91.7 | 35.03 | 0.0707 | 0.6 | 14.33 | 0
August | 31 | 12PM to 1PM | 87.1 | 70 | 62.1 | 85.4 | 34.31 | 0.0706 | 0.56 | 14.34 | 0
August | 31 | 1PM to 2PM | 88 | 69.7 | 61 | 82.1 | 34.02 | 0.0705 | 0.54 | 14.35 | 0
August | 31 | 2PM to 3PM | 89.1 | 70 | 61 | 82.1 | 34.29 | 0.0704 | 0.54 | 14.38 | 0
August | 31 | 3PM to 4PM | 89.1 | 70.6 | 62.1 | 85.4 | 34.8 | 0.0703 | 0.56 | 14.39 | 0
August | 31 | 4PM to 5PM | 89.1 | 69.5 | 60.1 | 79.5 | 33.87 | 0.0704 | 0.52 | 14.37 | 0
August | 31 | 5PM to 6PM | 87.1 | 68.9 | 60.1 | 79.5 | 33.39 | 0.0706 | 0.52 | 14.32 | 0
August | 31 | 6PM to 7PM | 84 | 69.1 | 62.1 | 85.4 | 33.56 | 0.071 | 0.56 | 14.26 | 0
August | 31 | 7PM to 8PM | 82.9 | 69.3 | 63 | 88.2 | 33.74 | 0.0711 | 0.58 | 14.24 | 0
August | 31 | 8PM to 9PM | 81 | 69.3 | 64 | 91.7 | 33.8 | 0.0713 | 0.6 | 14.2 | 0
August | 31 | 9PM to 10PM | 77.4 | 67.2 | 62.2 | 85.9 | 32.01 | 0.0719 | 0.57 | 14.09 | 0
August | 31 | 10PM to 11PM | 73.8 | 65.1 | 60.6 | 81 | 30.37 | 0.0724 | 0.53 | 13.98 | 0
August | 31 | 11PM to 12AM | 70.2 | 62.8 | 58.8 | 75.9 | 28.68 | 0.0729 | 0.5 | 13.87 | 0
September | 1 | 12AM to 1AM | 66.7 | 60.7 | 57.2 | 71.5 | 27.17 | 0.0734 | 0.47 | 13.76 | 0
September | 1 | 1AM to 2AM | 63.1 | 58.4 | 55.4 | 67 | 25.57 | 0.0739 | 0.44 | 13.66 | 0
September | 1 | 2AM to 3AM | 59.5 | 56.1 | 53.8 | 63.1 | 24.09 | 0.0745 | 0.42 | 13.55 | 0
September | 1 | 3AM to 4AM | 55.9 | 53.6 | 52 | 59 | 22.58 | 0.075 | 0.39 | 13.44 | 0
September | 1 | 4AM to 5AM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
September | 1 | 5AM to 6AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
September | 1 | 6AM to 7AM | 57.9 | 55.5 | 54 | 63.5 | 23.76 | 0.0747 | 0.42 | 13.51 | 0
September | 1 | 7AM to 8AM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
September | 1 | 8AM to 9AM | 68 | 57.3 | 50 | 54.7 | 24.86 | 0.0733 | 0.36 | 13.74 | 0
September | 1 | 9AM to 10AM | 71.1 | 56.2 | 45 | 45.2 | 24.11 | 0.073 | 0.3 | 13.79 | 0
September | 1 | 10AM to 11AM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
September | 1 | 11AM to 12PM | 73 | 57.4 | 46 | 47.1 | 24.89 | 0.0727 | 0.31 | 13.85 | 0
September | 1 | 12PM to 1PM | 73.9 | 57.3 | 45 | 45.2 | 24.81 | 0.0726 | 0.3 | 13.87 | 0
September | 1 | 1PM to 2PM | 77 | 58.9 | 46 | 47.1 | 25.85 | 0.0721 | 0.31 | 13.95 | 0
September | 1 | 2PM to 3PM | 77 | 58.1 | 44.1 | 43.6 | 25.31 | 0.0722 | 0.29 | 13.94 | 0
September | 1 | 3PM to 4PM | 77 | 58.5 | 45 | 45.2 | 25.55 | 0.0722 | 0.3 | 13.95 | 0
September | 1 | 4PM to 5PM | 77 | 58.9 | 46 | 47.1 | 25.85 | 0.0721 | 0.31 | 13.95 | 0
September | 1 | 5PM to 6PM | 75 | 58.2 | 46 | 47.1 | 25.37 | 0.0724 | 0.31 | 13.9 | 0
September | 1 | 6PM to 7PM | 73.9 | 57.8 | 46 | 47.1 | 25.11 | 0.0726 | 0.31 | 13.87 | 0
September | 1 | 7PM to 8PM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
September | 1 | 8PM to 9PM | 71.1 | 58 | 48.9 | 52.6 | 25.26 | 0.0729 | 0.35 | 13.82 | 0
September | 1 | 9PM to 10PM | 71.1 | 56.7 | 46 | 47.1 | 24.41 | 0.073 | 0.31 | 13.8 | 0
September | 1 | 10PM to 11PM | 69.1 | 56.3 | 46.9 | 48.8 | 24.18 | 0.0732 | 0.32 | 13.75 | 0
September | 1 | 11PM to 12AM | 68 | 56.8 | 48.9 | 52.6 | 24.52 | 0.0733 | 0.35 | 13.74 | 0
September | 2 | 12AM to 1AM | 66 | 58.1 | 53.1 | 61.4 | 25.41 | 0.0736 | 0.41 | 13.71 | 0
September | 2 | 1AM to 2AM | 66.9 | 57.9 | 52 | 59 | 25.25 | 0.0735 | 0.39 | 13.73 | 0
September | 2 | 2AM to 3AM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
September | 2 | 3AM to 4AM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
September | 2 | 4AM to 5AM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
September | 2 | 5AM to 6AM | 63 | 58.1 | 55 | 66.1 | 25.39 | 0.074 | 0.44 | 13.65 | 0
September | 2 | 6AM to 7AM | 66.9 | 60.7 | 57 | 71.1 | 27.14 | 0.0734 | 0.47 | 13.77 | 0
September | 2 | 7AM to 8AM | 70 | 63.5 | 60.1 | 79.5 | 29.2 | 0.0729 | 0.52 | 13.87 | 0
September | 2 | 8AM to 9AM | 72 | 65.4 | 62.1 | 85.4 | 30.6 | 0.0726 | 0.56 | 13.94 | 0
September | 2 | 9AM to 10AM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
September | 2 | 10AM to 11AM | 77 | 67.5 | 63 | 88.2 | 32.28 | 0.0719 | 0.58 | 14.08 | 0
September | 2 | 11AM to 12PM | 80.1 | 66.8 | 60.1 | 79.5 | 31.67 | 0.0715 | 0.52 | 14.14 | 0
September | 2 | 12PM to 1PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
September | 2 | 1PM to 2PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
September | 2 | 2PM to 3PM | 82 | 65.8 | 57 | 71.1 | 30.84 | 0.0713 | 0.47 | 14.16 | 0
September | 2 | 3PM to 4PM | 81 | 65.4 | 57 | 71.1 | 30.57 | 0.0715 | 0.47 | 14.13 | 0
September | 2 | 4PM to 5PM | 79 | 64.2 | 55.9 | 68.3 | 29.65 | 0.0718 | 0.45 | 14.07 | 0
September | 2 | 5PM to 6PM | 77 | 62.5 | 54 | 63.5 | 28.42 | 0.072 | 0.42 | 14.01 | 0
September | 2 | 6PM to 7PM | 73.9 | 62 | 55 | 66.1 | 28.07 | 0.0724 | 0.44 | 13.93 | 0
September | 2 | 7PM to 8PM | 71.1 | 61 | 55 | 66.1 | 27.37 | 0.0728 | 0.44 | 13.86 | 0
September | 2 | 8PM to 9PM | 69.1 | 60.8 | 55.9 | 68.3 | 27.23 | 0.0731 | 0.45 | 13.81 | 0
September | 2 | 9PM to 10PM | 66.9 | 60.1 | 55.9 | 68.3 | 26.71 | 0.0734 | 0.45 | 13.76 | 0
September | 2 | 10PM to 11PM | 64.9 | 58.8 | 55 | 66.1 | 25.88 | 0.0737 | 0.44 | 13.7 | 0
September | 2 | 11PM to 12AM | 64 | 58.5 | 55 | 66.1 | 25.66 | 0.0738 | 0.44 | 13.68 | 0
September | 3 | 12AM to 1AM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
September | 3 | 1AM to 2AM | 61 | 56.2 | 53.1 | 61.4 | 24.18 | 0.0743 | 0.41 | 13.58 | 0
September | 3 | 2AM to 3AM | 60.1 | 55.9 | 53.1 | 61.4 | 23.96 | 0.0744 | 0.41 | 13.56 | 0
September | 3 | 3AM to 4AM | 59 | 54.9 | 52 | 59 | 23.32 | 0.0746 | 0.39 | 13.52 | 0
September | 3 | 4AM to 5AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
September | 3 | 5AM to 6AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
September | 3 | 6AM to 7AM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
September | 3 | 7AM to 8AM | 64 | 58.5 | 55 | 66.1 | 25.66 | 0.0738 | 0.44 | 13.68 | 0
September | 3 | 8AM to 9AM | 69.1 | 61.9 | 57.9 | 73.5 | 28.04 | 0.0731 | 0.48 | 13.83 | 0
September | 3 | 9AM to 10AM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
September | 3 | 10AM to 11AM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
September | 3 | 11AM to 12PM | 75.9 | 64.9 | 59 | 76.4 | 30.17 | 0.0721 | 0.5 | 14.02 | 0
September | 3 | 12PM to 1PM | 79 | 64.8 | 57 | 71.1 | 30.09 | 0.0717 | 0.47 | 14.08 | 0
September | 3 | 1PM to 2PM | 80.1 | 65.1 | 57 | 71.1 | 30.35 | 0.0716 | 0.47 | 14.11 | 0
September | 3 | 2PM to 3PM | 79 | 62.8 | 53.1 | 61.4 | 28.57 | 0.0718 | 0.41 | 14.05 | 0
September | 3 | 3PM to 4PM | 81 | 63.9 | 54 | 63.5 | 29.38 | 0.0715 | 0.42 | 14.11 | 0
September | 3 | 4PM to 5PM | 79 | 62.3 | 52 | 59 | 28.19 | 0.0718 | 0.39 | 14.04 | 0
September | 3 | 5PM to 6PM | 79 | 62.3 | 52 | 59 | 28.19 | 0.0718 | 0.39 | 14.04 | 0
September | 3 | 6PM to 7PM | 75 | 61.4 | 53.1 | 61.4 | 27.61 | 0.0723 | 0.41 | 13.95 | 0
September | 3 | 7PM to 8PM | 72 | 60.3 | 53.1 | 61.4 | 26.86 | 0.0727 | 0.41 | 13.87 | 0
September | 3 | 8PM to 9PM | 71.1 | 61 | 55 | 66.1 | 27.37 | 0.0728 | 0.44 | 13.86 | 0
September | 3 | 9PM to 10PM | 64.9 | 60 | 57 | 71.1 | 26.65 | 0.0737 | 0.47 | 13.71 | 0
September | 3 | 10PM to 11PM | 66.9 | 60.1 | 55.9 | 68.3 | 26.71 | 0.0734 | 0.45 | 13.76 | 0
September | 3 | 11PM to 12AM | 63 | 59.2 | 57 | 71.1 | 26.17 | 0.0739 | 0.47 | 13.66 | 0
September | 4 | 12AM to 1AM | 63 | 59.2 | 57 | 71.1 | 26.17 | 0.0739 | 0.47 | 13.66 | 0
September | 4 | 1AM to 2AM | 62.1 | 58.3 | 55.9 | 68.3 | 25.52 | 0.0741 | 0.45 | 13.63 | 0
September | 4 | 2AM to 3AM | 60.1 | 57.5 | 55.9 | 68.3 | 25.04 | 0.0744 | 0.45 | 13.58 | 0
September | 4 | 3AM to 4AM | 60.1 | 57 | 55 | 66.1 | 24.69 | 0.0744 | 0.44 | 13.57 | 0
September | 4 | 4AM to 5AM | 59 | 54.4 | 51.1 | 57 | 23.02 | 0.0746 | 0.38 | 13.52 | 0
September | 4 | 5AM to 6AM | 57.9 | 55 | 53.1 | 61.4 | 23.44 | 0.0747 | 0.41 | 13.5 | 0
September | 4 | 6AM to 7AM | 63 | 58.6 | 55.9 | 68.3 | 25.74 | 0.074 | 0.45 | 13.65 | 0
September | 4 | 7AM to 8AM | 70 | 66 | 64 | 91.7 | 31.1 | 0.0728 | 0.6 | 13.91 | 0
September | 4 | 8AM to 9AM | 75.9 | 64.9 | 59 | 76.4 | 30.17 | 0.0721 | 0.5 | 14.02 | 0
September | 4 | 9AM to 10AM | 80.1 | 65.6 | 57.9 | 73.5 | 30.72 | 0.0716 | 0.48 | 14.12 | 0
September | 4 | 10AM to 11AM | 82 | 64.8 | 55 | 66.1 | 30.05 | 0.0714 | 0.44 | 14.15 | 0
September | 4 | 11AM to 12PM | 84 | 64.5 | 53.1 | 61.4 | 29.8 | 0.0711 | 0.41 | 14.18 | 0
September | 4 | 12PM to 1PM | 86 | 64.2 | 51.1 | 57 | 29.6 | 0.0709 | 0.38 | 14.22 | 0
September | 4 | 1PM to 2PM | 86 | 64.2 | 51.1 | 57 | 29.6 | 0.0709 | 0.38 | 14.22 | 0
September | 4 | 2PM to 3PM | 84.9 | 64.7 | 53.1 | 61.4 | 30.02 | 0.071 | 0.41 | 14.21 | 0
September | 4 | 3PM to 4PM | 86 | 64.2 | 51.1 | 57 | 29.6 | 0.0709 | 0.38 | 14.22 | 0
September | 4 | 4PM to 5PM | 84.9 | 63.4 | 50 | 54.7 | 28.98 | 0.071 | 0.36 | 14.18 | 0
September | 4 | 5PM to 6PM | 82.9 | 63.6 | 52 | 59 | 29.16 | 0.0713 | 0.39 | 14.15 | 0
September | 4 | 6PM to 7PM | 79 | 62.8 | 53.1 | 61.4 | 28.57 | 0.0718 | 0.41 | 14.05 | 0
September | 4 | 7PM to 8PM | 75 | 61.9 | 54 | 63.5 | 27.93 | 0.0723 | 0.42 | 13.95 | 0
September | 4 | 8PM to 9PM | 70 | 61.1 | 55.9 | 68.3 | 27.45 | 0.073 | 0.45 | 13.84 | 0
September | 4 | 9PM to 10PM | 70 | 61.1 | 55.9 | 68.3 | 27.45 | 0.073 | 0.45 | 13.84 | 0
September | 4 | 10PM to 11PM | 66.9 | 61.2 | 57.9 | 73.5 | 27.51 | 0.0734 | 0.48 | 13.77 | 0
September | 4 | 11PM to 12AM | 66.9 | 60.7 | 57 | 71.1 | 27.14 | 0.0734 | 0.47 | 13.77 | 0
September | 5 | 12AM to 1AM | 64.9 | 60.5 | 57.9 | 73.5 | 27.02 | 0.0736 | 0.48 | 13.72 | 0
September | 5 | 1AM to 2AM | 64 | 60.2 | 57.9 | 73.5 | 26.8 | 0.0738 | 0.48 | 13.7 | 0
September | 5 | 2AM to 3AM | 63 | 59.2 | 57 | 71.1 | 26.17 | 0.0739 | 0.47 | 13.66 | 0
September | 5 | 3AM to 4AM | 64.9 | 60.5 | 57.9 | 73.5 | 27.02 | 0.0736 | 0.48 | 13.72 | 0
September | 5 | 4AM to 5AM | 62.1 | 59.5 | 57.9 | 73.5 | 26.32 | 0.074 | 0.48 | 13.65 | 0
September | 5 | 5AM to 6AM | 63 | 59.8 | 57.9 | 73.5 | 26.54 | 0.0739 | 0.48 | 13.67 | 0
September | 5 | 6AM to 7AM | 66 | 60.9 | 57.9 | 73.5 | 27.29 | 0.0735 | 0.48 | 13.75 | 0
September | 5 | 7AM to 8AM | 73 | 65.1 | 61 | 82.1 | 30.36 | 0.0725 | 0.54 | 13.96 | 0
September | 5 | 8AM to 9AM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
September | 5 | 9AM to 10AM | 82.9 | 67.1 | 59 | 76.4 | 31.89 | 0.0712 | 0.5 | 14.2 | 0
September | 5 | 10AM to 11AM | 86 | 65.1 | 53.1 | 61.4 | 30.28 | 0.0709 | 0.41 | 14.23 | 0
September | 5 | 11AM to 12PM | 88 | 68.1 | 57.9 | 73.5 | 32.66 | 0.0705 | 0.48 | 14.32 | 0
September | 5 | 12PM to 1PM | 88 | 68.1 | 57.9 | 73.5 | 32.66 | 0.0705 | 0.48 | 14.32 | 0
September | 5 | 1PM to 2PM | 90 | 67.7 | 55.9 | 68.3 | 32.34 | 0.0703 | 0.45 | 14.36 | 0
September | 5 | 2PM to 3PM | 89.1 | 68 | 57 | 71.1 | 32.55 | 0.0704 | 0.47 | 14.35 | 0
September | 5 | 3PM to 4PM | 89.1 | 68.4 | 57.9 | 73.5 | 32.93 | 0.0704 | 0.48 | 14.35 | 0
September | 5 | 4PM to 5PM | 86 | 67.5 | 57.9 | 73.5 | 32.18 | 0.0708 | 0.48 | 14.27 | 0
September | 5 | 5PM to 6PM | 84.9 | 68.3 | 60.1 | 79.5 | 32.86 | 0.0709 | 0.52 | 14.26 | 0
September | 5 | 6PM to 7PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
September | 5 | 7PM to 8PM | 79 | 65.8 | 59 | 76.4 | 30.92 | 0.0717 | 0.5 | 14.1 | 0
September | 5 | 8PM to 9PM | 77 | 64.6 | 57.9 | 73.5 | 29.98 | 0.072 | 0.48 | 14.04 | 0
September | 5 | 9PM to 10PM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
September | 5 | 10PM to 11PM | 75 | 64.6 | 59 | 76.4 | 29.95 | 0.0722 | 0.5 | 14 | 0
September | 5 | 11PM to 12AM | 73.9 | 64.2 | 59 | 76.4 | 29.69 | 0.0724 | 0.5 | 13.97 | 0
September | 6 | 12AM to 1AM | 73 | 63.3 | 57.9 | 73.5 | 29.01 | 0.0725 | 0.48 | 13.93 | 0
September | 6 | 1AM to 2AM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
September | 6 | 2AM to 3AM | 72 | 62.4 | 57 | 71.1 | 28.37 | 0.0727 | 0.47 | 13.9 | 0
September | 6 | 3AM to 4AM | 71.1 | 62.6 | 57.9 | 73.5 | 28.52 | 0.0728 | 0.48 | 13.88 | 0
September | 6 | 4AM to 5AM | 69.1 | 61.9 | 57.9 | 73.5 | 28.04 | 0.0731 | 0.48 | 13.83 | 0
September | 6 | 5AM to 6AM | 66.9 | 62.5 | 60.1 | 79.5 | 28.45 | 0.0733 | 0.52 | 13.79 | 0
September | 6 | 6AM to 7AM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
September | 6 | 7AM to 8AM | 75.9 | 66 | 61 | 82.1 | 31.06 | 0.0721 | 0.54 | 14.04 | 0
September | 6 | 8AM to 9AM | 82 | 67.9 | 61 | 82.1 | 32.56 | 0.0713 | 0.54 | 14.2 | 0
September | 6 | 9AM to 10AM | 86 | 68.6 | 60.1 | 79.5 | 33.12 | 0.0708 | 0.52 | 14.29 | 0
September | 6 | 10AM to 11AM | 88 | 70.8 | 63 | 88.2 | 34.97 | 0.0705 | 0.58 | 14.37 | 0
September | 6 | 11AM to 12PM | 89.1 | 68.4 | 57.9 | 73.5 | 32.93 | 0.0704 | 0.48 | 14.35 | 0
September | 6 | 12PM to 1PM | 90 | 67.3 | 55 | 66.1 | 31.99 | 0.0703 | 0.44 | 14.35 | 0
September | 6 | 1PM to 2PM | 89.1 | 67.4 | 55.9 | 68.3 | 32.12 | 0.0704 | 0.45 | 14.34 | 0
September | 6 | 2PM to 3PM | 91 | 67.6 | 55 | 66.1 | 32.25 | 0.0702 | 0.44 | 14.38 | 0
September | 6 | 3PM to 4PM | 90 | 67.7 | 55.9 | 68.3 | 32.34 | 0.0703 | 0.45 | 14.36 | 0
September | 6 | 4PM to 5PM | 88 | 67.6 | 57 | 71.1 | 32.29 | 0.0706 | 0.47 | 14.32 | 0
September | 6 | 5PM to 6PM | 87.1 | 67.8 | 57.9 | 73.5 | 32.44 | 0.0707 | 0.48 | 14.3 | 0
September | 6 | 6PM to 7PM | 82.9 | 67.1 | 59 | 76.4 | 31.89 | 0.0712 | 0.5 | 14.2 | 0
September | 6 | 7PM to 8PM | 81 | 67.1 | 60.1 | 79.5 | 31.89 | 0.0714 | 0.52 | 14.16 | 0
September | 6 | 8PM to 9PM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
September | 6 | 9PM to 10PM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
September | 6 | 10PM to 11PM | 80.1 | 67.9 | 62.1 | 85.4 | 32.59 | 0.0715 | 0.56 | 14.16 | 0
September | 6 | 11PM to 12AM | 79 | 67.6 | 62.1 | 85.4 | 32.32 | 0.0716 | 0.56 | 14.13 | 0
September | 7 | 12AM to 1AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
September | 7 | 1AM to 2AM | 71.1 | 65.6 | 63 | 88.2 | 30.82 | 0.0727 | 0.58 | 13.93 | 0
September | 7 | 2AM to 3AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
September | 7 | 3AM to 4AM | 69.1 | 65.7 | 64 | 91.7 | 30.87 | 0.073 | 0.6 | 13.89 | 0
September | 7 | 4AM to 5AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
September | 7 | 5AM to 6AM | 69.1 | 65 | 63 | 88.2 | 30.33 | 0.073 | 0.58 | 13.88 | 0
September | 7 | 6AM to 7AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
September | 7 | 7AM to 8AM | 70 | 65.3 | 63 | 88.2 | 30.55 | 0.0728 | 0.58 | 13.9 | 0
September | 7 | 8AM to 9AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
September | 7 | 9AM to 10AM | 73 | 66.9 | 64 | 91.7 | 31.85 | 0.0724 | 0.6 | 13.99 | 0
September | 7 | 10AM to 11AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
September | 7 | 11AM to 12PM | 75.9 | 69.1 | 66 | 98.4 | 33.6 | 0.072 | 0.64 | 14.09 | 0
September | 7 | 12PM to 1PM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
September | 7 | 1PM to 2PM | 75.9 | 69.7 | 66.9 | 101.5 | 34.1 | 0.072 | 0.67 | 14.1 | 0
September | 7 | 2PM to 3PM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
September | 7 | 3PM to 4PM | 73.9 | 69.1 | 66.9 | 101.5 | 33.61 | 0.0722 | 0.67 | 14.05 | 0
September | 7 | 4PM to 5PM | 73 | 69.5 | 68 | 105.5 | 34.01 | 0.0723 | 0.69 | 14.03 | 0
September | 7 | 5PM to 6PM | 73 | 68.8 | 66.9 | 101.5 | 33.39 | 0.0723 | 0.67 | 14.02 | 0
September | 7 | 6PM to 7PM | 72 | 68.5 | 66.9 | 101.5 | 33.13 | 0.0725 | 0.67 | 13.99 | 0
September | 7 | 7PM to 8PM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
September | 7 | 8PM to 9PM | 71.1 | 68.9 | 68 | 105.5 | 33.52 | 0.0726 | 0.69 | 13.98 | 0
September | 7 | 9PM to 10PM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
September | 7 | 10PM to 11PM | 70 | 67.9 | 66.9 | 101.5 | 32.64 | 0.0728 | 0.67 | 13.94 | 0
September | 7 | 11PM to 12AM | 70 | 68.6 | 68 | 105.5 | 33.25 | 0.0727 | 0.69 | 13.95 | 0
September | 8 | 12AM to 1AM | 69.1 | 67 | 66 | 98.4 | 31.92 | 0.0729 | 0.64 | 13.91 | 0
September | 8 | 1AM to 2AM | 69.1 | 68.3 | 68 | 105.5 | 33.03 | 0.0729 | 0.69 | 13.93 | 0
September | 8 | 2AM to 3AM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
September | 8 | 3AM to 4AM | 68 | 67.3 | 66.9 | 101.5 | 32.15 | 0.073 | 0.67 | 13.89 | 0
September | 8 | 4AM to 5AM | 68 | 67.3 | 66.9 | 101.5 | 32.15 | 0.073 | 0.67 | 13.89 | 0
September | 8 | 5AM to 6AM | 66.9 | 66.3 | 66 | 98.4 | 31.39 | 0.0732 | 0.64 | 13.85 | 0
September | 8 | 6AM to 7AM | 68 | 67.3 | 66.9 | 101.5 | 32.15 | 0.073 | 0.67 | 13.89 | 0
September | 8 | 7AM to 8AM | 69.1 | 67.6 | 66.9 | 101.5 | 32.42 | 0.0729 | 0.67 | 13.92 | 0
September | 8 | 8AM to 9AM | 72 | 68.5 | 66.9 | 101.5 | 33.13 | 0.0725 | 0.67 | 13.99 | 0
September | 8 | 9AM to 10AM | 75.9 | 69.1 | 66 | 98.4 | 33.6 | 0.072 | 0.64 | 14.09 | 0
September | 8 | 10AM to 11AM | 79 | 70 | 66 | 98.4 | 34.36 | 0.0716 | 0.64 | 14.17 | 0
September | 8 | 11AM to 12PM | 82 | 70.9 | 66 | 98.4 | 35.11 | 0.0712 | 0.64 | 14.25 | 0
September | 8 | 12PM to 1PM | 81 | 71.1 | 66.9 | 101.5 | 35.34 | 0.0713 | 0.67 | 14.23 | 0
September | 8 | 1PM to 2PM | 82.9 | 69.3 | 63 | 88.2 | 33.74 | 0.0711 | 0.58 | 14.24 | 0
September | 8 | 2PM to 3PM | 84 | 68 | 60.1 | 79.5 | 32.64 | 0.071 | 0.52 | 14.24 | 0
September | 8 | 3PM to 4PM | 84 | 66.9 | 57.9 | 73.5 | 31.69 | 0.0711 | 0.48 | 14.22 | 0
September | 8 | 4PM to 5PM | 81 | 67.6 | 61 | 82.1 | 32.3 | 0.0714 | 0.54 | 14.17 | 0
September | 8 | 5PM to 6PM | 80.1 | 68.4 | 63 | 88.2 | 33.03 | 0.0715 | 0.58 | 14.16 | 0
September | 8 | 6PM to 7PM | 77 | 67 | 62.1 | 85.4 | 31.84 | 0.0719 | 0.56 | 14.08 | 0
September | 8 | 7PM to 8PM | 75 | 66.9 | 63 | 88.2 | 31.79 | 0.0722 | 0.58 | 14.03 | 0
September | 8 | 8PM to 9PM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
September | 8 | 9PM to 10PM | 72 | 65.4 | 62.1 | 85.4 | 30.6 | 0.0726 | 0.56 | 13.94 | 0
September | 8 | 10PM to 11PM | 70 | 65.3 | 63 | 88.2 | 30.55 | 0.0728 | 0.58 | 13.9 | 0
September | 8 | 11PM to 12AM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
September | 9 | 12AM to 1AM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
September | 9 | 1AM to 2AM | 66.9 | 63.7 | 62.1 | 85.4 | 29.36 | 0.0733 | 0.56 | 13.81 | 0
September | 9 | 2AM to 3AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
September | 9 | 3AM to 4AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
September | 9 | 4AM to 5AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
September | 9 | 5AM to 6AM | 63 | 61.7 | 61 | 82.1 | 27.89 | 0.0739 | 0.54 | 13.7 | 0
September | 9 | 6AM to 7AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
September | 9 | 7AM to 8AM | 68 | 64.6 | 63 | 88.2 | 30.07 | 0.0731 | 0.58 | 13.85 | 0
September | 9 | 8AM to 9AM | 72 | 65.9 | 63 | 88.2 | 31.04 | 0.0726 | 0.58 | 13.95 | 0
September | 9 | 9AM to 10AM | 75 | 67.6 | 64 | 91.7 | 32.33 | 0.0721 | 0.6 | 14.04 | 0
September | 9 | 10AM to 11AM | 77 | 67 | 62.1 | 85.4 | 31.84 | 0.0719 | 0.56 | 14.08 | 0
September | 9 | 11AM to 12PM | 77 | 64.6 | 57.9 | 73.5 | 29.98 | 0.072 | 0.48 | 14.04 | 0
September | 9 | 12PM to 1PM | 79 | 64.8 | 57 | 71.1 | 30.09 | 0.0717 | 0.47 | 14.08 | 0
September | 9 | 1PM to 2PM | 81 | 65.4 | 57 | 71.1 | 30.57 | 0.0715 | 0.47 | 14.13 | 0
September | 9 | 2PM to 3PM | 81 | 64.4 | 55 | 66.1 | 29.79 | 0.0715 | 0.44 | 14.12 | 0
September | 9 | 3PM to 4PM | 80.1 | 63.6 | 54 | 63.5 | 29.16 | 0.0716 | 0.42 | 14.09 | 0
September | 9 | 4PM to 5PM | 79 | 63.8 | 55 | 66.1 | 29.3 | 0.0718 | 0.44 | 14.07 | 0
September | 9 | 5PM to 6PM | 75.9 | 62.2 | 54 | 63.5 | 28.15 | 0.0722 | 0.42 | 13.98 | 0
September | 9 | 6PM to 7PM | 75 | 62.4 | 55 | 66.1 | 28.34 | 0.0723 | 0.44 | 13.96 | 0
September | 9 | 7PM to 8PM | 73.9 | 62 | 55 | 66.1 | 28.07 | 0.0724 | 0.44 | 13.93 | 0
September | 9 | 8PM to 9PM | 71.1 | 62.1 | 57 | 71.1 | 28.15 | 0.0728 | 0.47 | 13.87 | 0
September | 9 | 9PM to 10PM | 69.1 | 60.8 | 55.9 | 68.3 | 27.23 | 0.0731 | 0.45 | 13.81 | 0
September | 9 | 10PM to 11PM | 68 | 59.4 | 54 | 63.5 | 26.22 | 0.0733 | 0.42 | 13.77 | 0
September | 9 | 11PM to 12AM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
September | 10 | 12AM to 1AM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
September | 10 | 1AM to 2AM | 63 | 58.6 | 55.9 | 68.3 | 25.74 | 0.074 | 0.45 | 13.65 | 0
September | 10 | 2AM to 3AM | 64 | 58.5 | 55 | 66.1 | 25.66 | 0.0738 | 0.44 | 13.68 | 0
September | 10 | 3AM to 4AM | 63 | 57.5 | 54 | 63.5 | 24.99 | 0.074 | 0.42 | 13.64 | 0
September | 10 | 4AM to 5AM | 62.1 | 57.8 | 55 | 66.1 | 25.17 | 0.0741 | 0.44 | 13.62 | 0
September | 10 | 5AM to 6AM | 62.1 | 57.8 | 55 | 66.1 | 25.17 | 0.0741 | 0.44 | 13.62 | 0
September | 10 | 6AM to 7AM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
September | 10 | 7AM to 8AM | 70 | 61.7 | 57 | 71.1 | 27.89 | 0.073 | 0.47 | 13.85 | 0
September | 10 | 8AM to 9AM | 75.9 | 63.8 | 57 | 71.1 | 29.34 | 0.0721 | 0.47 | 14 | 0
September | 10 | 9AM to 10AM | 80.1 | 65.6 | 57.9 | 73.5 | 30.72 | 0.0716 | 0.48 | 14.12 | 0
September | 10 | 10AM to 11AM | 82.9 | 67.7 | 60.1 | 79.5 | 32.37 | 0.0712 | 0.52 | 14.21 | 0
September | 10 | 11AM to 12PM | 82 | 66.8 | 59 | 76.4 | 31.67 | 0.0713 | 0.5 | 14.18 | 0
September | 10 | 12PM to 1PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
September | 10 | 1PM to 2PM | 75 | 65.2 | 60.1 | 79.5 | 30.43 | 0.0722 | 0.52 | 14 | 0
September | 10 | 2PM to 3PM | 69.1 | 65.7 | 64 | 91.7 | 30.87 | 0.073 | 0.6 | 13.89 | 0
September | 10 | 3PM to 4PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
September | 10 | 4PM to 5PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
September | 10 | 5PM to 6PM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
September | 10 | 6PM to 7PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
September | 10 | 7PM to 8PM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
September | 10 | 8PM to 9PM | 66.9 | 65.6 | 64.9 | 94.6 | 30.81 | 0.0732 | 0.62 | 13.84 | 0
September | 10 | 9PM to 10PM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
September | 10 | 10PM to 11PM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
September | 10 | 11PM to 12AM | 64.9 | 64.3 | 64 | 91.7 | 29.86 | 0.0735 | 0.6 | 13.78 | 0
September | 11 | 12AM to 1AM | 64.9 | 64.3 | 64 | 91.7 | 29.86 | 0.0735 | 0.6 | 13.78 | 0
September | 11 | 1AM to 2AM | 64 | 63.3 | 63 | 88.2 | 29.09 | 0.0737 | 0.58 | 13.74 | 0
September | 11 | 2AM to 3AM | 62.1 | 61.4 | 61 | 82.1 | 27.66 | 0.074 | 0.54 | 13.67 | 0
September | 11 | 3AM to 4AM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
September | 11 | 4AM to 5AM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
September | 11 | 5AM to 6AM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
September | 11 | 6AM to 7AM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
September | 11 | 7AM to 8AM | 63 | 63 | 63 | 88.2 | 28.83 | 0.0738 | 0.58 | 13.72 | 0
September | 11 | 8AM to 9AM | 66.9 | 65 | 64 | 91.7 | 30.34 | 0.0733 | 0.6 | 13.83 | 0
September | 11 | 9AM to 10AM | 73.9 | 67.2 | 64 | 91.7 | 32.07 | 0.0723 | 0.6 | 14.01 | 0
September | 11 | 10AM to 11AM | 75.9 | 66.6 | 62.1 | 85.4 | 31.57 | 0.0721 | 0.56 | 14.05 | 0
September | 11 | 11AM to 12PM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
September | 11 | 12PM to 1PM | 81 | 68.7 | 63 | 88.2 | 33.25 | 0.0714 | 0.58 | 14.19 | 0
September | 11 | 1PM to 2PM | 82 | 65.8 | 57 | 71.1 | 30.84 | 0.0713 | 0.47 | 14.16 | 0
September | 11 | 2PM to 3PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
September | 11 | 3PM to 4PM | 80.1 | 66.2 | 59 | 76.4 | 31.19 | 0.0716 | 0.5 | 14.13 | 0
September | 11 | 4PM to 5PM | 79 | 65.8 | 59 | 76.4 | 30.92 | 0.0717 | 0.5 | 14.1 | 0
September | 11 | 5PM to 6PM | 77 | 65.2 | 59 | 76.4 | 30.44 | 0.072 | 0.5 | 14.05 | 0
September | 11 | 6PM to 7PM | 75.9 | 62.7 | 55 | 66.1 | 28.56 | 0.0722 | 0.44 | 13.99 | 0
September | 11 | 7PM to 8PM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
September | 11 | 8PM to 9PM | 73 | 64.5 | 60.1 | 79.5 | 29.95 | 0.0725 | 0.52 | 13.95 | 0
September | 11 | 9PM to 10PM | 71.1 | 64.4 | 61 | 82.1 | 29.87 | 0.0727 | 0.54 | 13.91 | 0
September | 11 | 10PM to 11PM | 71.1 | 64.4 | 61 | 82.1 | 29.87 | 0.0727 | 0.54 | 13.91 | 0
September | 11 | 11PM to 12AM | 72 | 64.7 | 61 | 82.1 | 30.09 | 0.0726 | 0.54 | 13.93 | 0
September | 12 | 12AM to 1AM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
September | 12 | 1AM to 2AM | 71.1 | 65.6 | 63 | 88.2 | 30.82 | 0.0727 | 0.58 | 13.93 | 0
September | 12 | 2AM to 3AM | 66.9 | 60.1 | 55.9 | 68.3 | 26.71 | 0.0734 | 0.45 | 13.76 | 0
September | 12 | 3AM to 4AM | 64 | 60.2 | 57.9 | 73.5 | 26.8 | 0.0738 | 0.48 | 13.7 | 0
September | 12 | 4AM to 5AM | 63 | 59.8 | 57.9 | 73.5 | 26.54 | 0.0739 | 0.48 | 13.67 | 0
September | 12 | 5AM to 6AM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
September | 12 | 6AM to 7AM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
September | 12 | 7AM to 8AM | 68 | 64.6 | 63 | 88.2 | 30.07 | 0.0731 | 0.58 | 13.85 | 0
September | 12 | 8AM to 9AM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
September | 12 | 9AM to 10AM | 73.9 | 62.5 | 55.9 | 68.3 | 28.42 | 0.0724 | 0.45 | 13.94 | 0
September | 12 | 10AM to 11AM | 77 | 65.8 | 60.1 | 79.5 | 30.92 | 0.0719 | 0.52 | 14.06 | 0
September | 12 | 11AM to 12PM | 79 | 66.4 | 60.1 | 79.5 | 31.4 | 0.0717 | 0.52 | 14.11 | 0
September | 12 | 12PM to 1PM | 80.1 | 67.3 | 61 | 82.1 | 32.08 | 0.0715 | 0.54 | 14.15 | 0
September | 12 | 1PM to 2PM | 81 | 68.2 | 62.1 | 85.4 | 32.81 | 0.0714 | 0.56 | 14.18 | 0
September | 12 | 2PM to 3PM | 79 | 64.8 | 57 | 71.1 | 30.09 | 0.0717 | 0.47 | 14.08 | 0
September | 12 | 3PM to 4PM | 80.1 | 65.6 | 57.9 | 73.5 | 30.72 | 0.0716 | 0.48 | 14.12 | 0
September | 12 | 4PM to 5PM | 78.1 | 64.5 | 57 | 71.1 | 29.87 | 0.0719 | 0.47 | 14.06 | 0
September | 12 | 5PM to 6PM | 75 | 62.9 | 55.9 | 68.3 | 28.69 | 0.0723 | 0.45 | 13.97 | 0
September | 12 | 6PM to 7PM | 73 | 62.2 | 55.9 | 68.3 | 28.2 | 0.0726 | 0.45 | 13.92 | 0
September | 12 | 7PM to 8PM | 71.1 | 59.4 | 52 | 59 | 26.26 | 0.0729 | 0.39 | 13.84 | 0
September | 12 | 8PM to 9PM | 68 | 59.4 | 54 | 63.5 | 26.22 | 0.0733 | 0.42 | 13.77 | 0
September | 12 | 9PM to 10PM | 66.9 | 57.9 | 52 | 59 | 25.25 | 0.0735 | 0.39 | 13.73 | 0
September | 12 | 10PM to 11PM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
September | 12 | 11PM to 12AM | 64.9 | 56.7 | 51.1 | 57 | 24.47 | 0.0737 | 0.38 | 13.67 | 0
September | 13 | 12AM to 1AM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
September | 13 | 1AM to 2AM | 63 | 55.9 | 51.1 | 57 | 23.98 | 0.074 | 0.38 | 13.62 | 0
September | 13 | 2AM to 3AM | 63 | 55.4 | 50 | 54.7 | 23.63 | 0.074 | 0.36 | 13.61 | 0
September | 13 | 3AM to 4AM | 63 | 56.4 | 52 | 59 | 24.29 | 0.074 | 0.39 | 13.63 | 0
September | 13 | 4AM to 5AM | 62.1 | 54 | 48 | 50.8 | 22.8 | 0.0742 | 0.34 | 13.58 | 0
September | 13 | 5AM to 6AM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
September | 13 | 6AM to 7AM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
September | 13 | 7AM to 8AM | 68 | 58.3 | 52 | 59 | 25.52 | 0.0733 | 0.39 | 13.76 | 0
September | 13 | 8AM to 9AM | 71.1 | 58.5 | 50 | 54.7 | 25.6 | 0.0729 | 0.36 | 13.82 | 0
September | 13 | 9AM to 10AM | 75 | 60.4 | 51.1 | 57 | 26.92 | 0.0724 | 0.38 | 13.93 | 0
September | 13 | 10AM to 11AM | 78.1 | 63.4 | 55 | 66.1 | 29.08 | 0.0719 | 0.44 | 14.04 | 0
September | 13 | 11AM to 12PM | 80.1 | 64.1 | 55 | 66.1 | 29.57 | 0.0716 | 0.44 | 14.09 | 0
September | 13 | 12PM to 1PM | 81 | 64.9 | 55.9 | 68.3 | 30.14 | 0.0715 | 0.45 | 14.12 | 0
September | 13 | 1PM to 2PM | 84.9 | 66.1 | 55.9 | 68.3 | 31.11 | 0.071 | 0.45 | 14.23 | 0
September | 13 | 2PM to 3PM | 86 | 66.5 | 55.9 | 68.3 | 31.37 | 0.0708 | 0.45 | 14.26 | 0
September | 13 | 3PM to 4PM | 87.1 | 67.3 | 57 | 71.1 | 32.07 | 0.0707 | 0.47 | 14.29 | 0
September | 13 | 4PM to 5PM | 84.9 | 66.1 | 55.9 | 68.3 | 31.11 | 0.071 | 0.45 | 14.23 | 0
September | 13 | 5PM to 6PM | 81 | 68.7 | 63 | 88.2 | 33.25 | 0.0714 | 0.58 | 14.19 | 0
September | 13 | 6PM to 7PM | 80.1 | 68.4 | 63 | 88.2 | 33.03 | 0.0715 | 0.58 | 14.16 | 0
September | 13 | 7PM to 8PM | 78.1 | 65 | 57.9 | 73.5 | 30.24 | 0.0718 | 0.48 | 14.07 | 0
September | 13 | 8PM to 9PM | 75.9 | 66 | 61 | 82.1 | 31.06 | 0.0721 | 0.54 | 14.04 | 0
September | 13 | 9PM to 10PM | 75 | 65.7 | 61 | 82.1 | 30.84 | 0.0722 | 0.54 | 14.01 | 0
September | 13 | 10PM to 11PM | 73 | 63.9 | 59 | 76.4 | 29.47 | 0.0725 | 0.5 | 13.94 | 0
September | 13 | 11PM to 12AM | 72 | 64.2 | 60.1 | 79.5 | 29.68 | 0.0726 | 0.52 | 13.92 | 0
September | 14 | 12AM to 1AM | 71.1 | 63.9 | 60.1 | 79.5 | 29.46 | 0.0728 | 0.52 | 13.9 | 0
September | 14 | 1AM to 2AM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
September | 14 | 2AM to 3AM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
September | 14 | 3AM to 4AM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
September | 14 | 4AM to 5AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
September | 14 | 5AM to 6AM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
September | 14 | 6AM to 7AM | 70 | 64.7 | 62.1 | 85.4 | 30.12 | 0.0729 | 0.56 | 13.89 | 0
September | 14 | 7AM to 8AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
September | 14 | 8AM to 9AM | 79 | 68.1 | 63 | 88.2 | 32.76 | 0.0716 | 0.58 | 14.14 | 0
September | 14 | 9AM to 10AM | 82 | 69 | 63 | 88.2 | 33.52 | 0.0712 | 0.58 | 14.22 | 0
September | 14 | 10AM to 11AM | 84.9 | 69.4 | 62.1 | 85.4 | 33.78 | 0.0709 | 0.56 | 14.28 | 0
September | 14 | 11AM to 12PM | 87.1 | 70 | 62.1 | 85.4 | 34.31 | 0.0706 | 0.56 | 14.34 | 0
September | 14 | 12PM to 1PM | 88 | 70.3 | 62.1 | 85.4 | 34.53 | 0.0705 | 0.56 | 14.36 | 0
September | 14 | 1PM to 2PM | 89.1 | 69.5 | 60.1 | 79.5 | 33.87 | 0.0704 | 0.52 | 14.37 | 0
September | 14 | 2PM to 3PM | 88 | 68.6 | 59 | 76.4 | 33.13 | 0.0705 | 0.5 | 14.33 | 0
September | 14 | 3PM to 4PM | 86 | 69.1 | 61 | 82.1 | 33.53 | 0.0707 | 0.54 | 14.3 | 0
September | 14 | 4PM to 5PM | 84.9 | 68.8 | 61 | 82.1 | 33.27 | 0.0709 | 0.54 | 14.27 | 0
September | 14 | 5PM to 6PM | 81 | 68.2 | 62.1 | 85.4 | 32.81 | 0.0714 | 0.56 | 14.18 | 0
September | 14 | 6PM to 7PM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
September | 14 | 7PM to 8PM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
September | 14 | 8PM to 9PM | 73.9 | 69.8 | 68 | 105.5 | 34.23 | 0.0722 | 0.69 | 14.06 | 0
September | 14 | 9PM to 10PM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
September | 14 | 10PM to 11PM | 75.9 | 69.1 | 66 | 98.4 | 33.6 | 0.072 | 0.64 | 14.09 | 0
September | 14 | 11PM to 12AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
September | 15 | 12AM to 1AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
September | 15 | 1AM to 2AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
September | 15 | 2AM to 3AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
September | 15 | 3AM to 4AM | 73.9 | 67.8 | 64.9 | 94.6 | 32.54 | 0.0723 | 0.62 | 14.02 | 0
September | 15 | 4AM to 5AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
September | 15 | 5AM to 6AM | 71.1 | 66.9 | 64.9 | 94.6 | 31.83 | 0.0727 | 0.62 | 13.95 | 0
September | 15 | 6AM to 7AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
September | 15 | 7AM to 8AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
September | 15 | 8AM to 9AM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
September | 15 | 9AM to 10AM | 75 | 68.1 | 64.9 | 94.6 | 32.8 | 0.0721 | 0.62 | 14.05 | 0
September | 15 | 10AM to 11AM | 75.9 | 67.8 | 64 | 91.7 | 32.56 | 0.072 | 0.6 | 14.07 | 0
September | 15 | 11AM to 12PM | 77 | 68.2 | 64 | 91.7 | 32.82 | 0.0719 | 0.6 | 14.1 | 0
September | 15 | 12PM to 1PM | 79 | 69.3 | 64.9 | 94.6 | 33.78 | 0.0716 | 0.62 | 14.16 | 0
September | 15 | 1PM to 2PM | 80.1 | 70.3 | 66 | 98.4 | 34.62 | 0.0714 | 0.64 | 14.2 | 0
September | 15 | 2PM to 3PM | 80.1 | 70.3 | 66 | 98.4 | 34.62 | 0.0714 | 0.64 | 14.2 | 0
September | 15 | 3PM to 4PM | 80.1 | 69.6 | 64.9 | 94.6 | 34.04 | 0.0714 | 0.62 | 14.19 | 0
September | 15 | 4PM to 5PM | 79 | 70 | 66 | 98.4 | 34.36 | 0.0716 | 0.64 | 14.17 | 0
September | 15 | 5PM to 6PM | 78.1 | 70.3 | 66.9 | 101.5 | 34.63 | 0.0717 | 0.67 | 14.15 | 0
September | 15 | 6PM to 7PM | 78.1 | 69 | 64.9 | 94.6 | 33.56 | 0.0717 | 0.62 | 14.13 | 0
September | 15 | 7PM to 8PM | 75.9 | 69.1 | 66 | 98.4 | 33.6 | 0.072 | 0.64 | 14.09 | 0
September | 15 | 8PM to 9PM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
September | 15 | 9PM to 10PM | 75 | 69.4 | 66.9 | 101.5 | 33.88 | 0.0721 | 0.67 | 14.07 | 0
September | 15 | 10PM to 11PM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
September | 15 | 11PM to 12AM | 73.9 | 68.5 | 66 | 98.4 | 33.12 | 0.0722 | 0.64 | 14.04 | 0
September | 16 | 12AM to 1AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
September | 16 | 1AM to 2AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
September | 16 | 2AM to 3AM | 73 | 68.2 | 66 | 98.4 | 32.89 | 0.0724 | 0.64 | 14.01 | 0
September | 16 | 3AM to 4AM | 71.1 | 67.6 | 66 | 98.4 | 32.41 | 0.0726 | 0.64 | 13.96 | 0
September | 16 | 4AM to 5AM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
September | 16 | 5AM to 6AM | 69.1 | 63.2 | 60.1 | 79.5 | 28.98 | 0.073 | 0.52 | 13.85 | 0
September | 16 | 6AM to 7AM | 69.1 | 67 | 66 | 98.4 | 31.92 | 0.0729 | 0.64 | 13.91 | 0
September | 16 | 7AM to 8AM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
September | 16 | 8AM to 9AM | 75 | 68.8 | 66 | 98.4 | 33.38 | 0.0721 | 0.64 | 14.06 | 0
September | 16 | 9AM to 10AM | 78.1 | 70.3 | 66.9 | 101.5 | 34.63 | 0.0717 | 0.67 | 14.15 | 0
September | 16 | 10AM to 11AM | 80.1 | 70.9 | 66.9 | 101.5 | 35.12 | 0.0714 | 0.67 | 14.21 | 0
September | 16 | 11AM to 12PM | 82.9 | 71.7 | 66.9 | 101.5 | 35.83 | 0.071 | 0.67 | 14.28 | 0
September | 16 | 12PM to 1PM | 84.9 | 73.6 | 69.1 | 109.6 | 37.58 | 0.0707 | 0.72 | 14.36 | 0
September | 16 | 1PM to 2PM | 86 | 73.2 | 68 | 105.5 | 37.21 | 0.0706 | 0.69 | 14.38 | 0
September | 16 | 2PM to 3PM | 84.9 | 69.9 | 63 | 88.2 | 34.22 | 0.0709 | 0.58 | 14.29 | 0
September | 16 | 3PM to 4PM | 84.9 | 71.7 | 66 | 98.4 | 35.82 | 0.0708 | 0.64 | 14.32 | 0
September | 16 | 4PM to 5PM | 84 | 70.8 | 64.9 | 94.6 | 35.02 | 0.0709 | 0.62 | 14.29 | 0
September | 16 | 5PM to 6PM | 70 | 61.1 | 55.9 | 68.3 | 27.45 | 0.073 | 0.45 | 13.84 | 0
September | 16 | 6PM to 7PM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
September | 16 | 7PM to 8PM | 71.1 | 68.2 | 66.9 | 101.5 | 32.9 | 0.0726 | 0.67 | 13.97 | 0
September | 16 | 8PM to 9PM | 71.1 | 68.9 | 68 | 105.5 | 33.52 | 0.0726 | 0.69 | 13.98 | 0
September | 16 | 9PM to 10PM | 72 | 69.2 | 68 | 105.5 | 33.74 | 0.0725 | 0.69 | 14.01 | 0
September | 16 | 10PM to 11PM | 72 | 67.9 | 66 | 98.4 | 32.63 | 0.0725 | 0.64 | 13.98 | 0
September | 16 | 11PM to 12AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
September | 17 | 12AM to 1AM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
September | 17 | 1AM to 2AM | 69.1 | 65.7 | 64 | 91.7 | 30.87 | 0.073 | 0.6 | 13.89 | 0
September | 17 | 2AM to 3AM | 68 | 65.3 | 64 | 91.7 | 30.61 | 0.0731 | 0.6 | 13.86 | 0
September | 17 | 3AM to 4AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
September | 17 | 4AM to 5AM | 68 | 65.3 | 64 | 91.7 | 30.61 | 0.0731 | 0.6 | 13.86 | 0
September | 17 | 5AM to 6AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
September | 17 | 6AM to 7AM | 66.9 | 64.3 | 63 | 88.2 | 29.8 | 0.0733 | 0.58 | 13.82 | 0
September | 17 | 7AM to 8AM | 70 | 66 | 64 | 91.7 | 31.1 | 0.0728 | 0.6 | 13.91 | 0
September | 17 | 8AM to 9AM | 73 | 66.3 | 63 | 88.2 | 31.3 | 0.0724 | 0.58 | 13.98 | 0
September | 17 | 9AM to 10AM | 75.9 | 67.2 | 63 | 88.2 | 32.01 | 0.072 | 0.58 | 14.06 | 0
September | 17 | 10AM to 11AM | 78.1 | 67.3 | 62.1 | 85.4 | 32.1 | 0.0718 | 0.56 | 14.1 | 0
September | 17 | 11AM to 12PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
September | 17 | 12PM to 1PM | 78.1 | 66.7 | 61 | 82.1 | 31.59 | 0.0718 | 0.54 | 14.09 | 0
September | 17 | 1PM to 2PM | 78.1 | 67.3 | 62.1 | 85.4 | 32.1 | 0.0718 | 0.56 | 14.1 | 0
September | 17 | 2PM to 3PM | 77 | 66.3 | 61 | 82.1 | 31.33 | 0.0719 | 0.54 | 14.07 | 0
September | 17 | 3PM to 4PM | 75 | 66.3 | 62.1 | 85.4 | 31.35 | 0.0722 | 0.56 | 14.02 | 0
September | 17 | 4PM to 5PM | 75.9 | 66 | 61 | 82.1 | 31.06 | 0.0721 | 0.54 | 14.04 | 0
September | 17 | 5PM to 6PM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
September | 17 | 6PM to 7PM | 73 | 65.7 | 62.1 | 85.4 | 30.87 | 0.0724 | 0.56 | 13.97 | 0
September | 17 | 7PM to 8PM | 71.1 | 65.1 | 62.1 | 85.4 | 30.38 | 0.0727 | 0.56 | 13.92 | 0
September | 17 | 8PM to 9PM | 69.1 | 64.4 | 62.1 | 85.4 | 29.89 | 0.073 | 0.56 | 13.87 | 0
September | 17 | 9PM to 10PM | 68 | 64.6 | 63 | 88.2 | 30.07 | 0.0731 | 0.58 | 13.85 | 0
September | 17 | 10PM to 11PM | 68 | 64.6 | 63 | 88.2 | 30.07 | 0.0731 | 0.58 | 13.85 | 0
September | 17 | 11PM to 12AM | 66.9 | 63.7 | 62.1 | 85.4 | 29.36 | 0.0733 | 0.56 | 13.81 | 0
September | 18 | 12AM to 1AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
September | 18 | 1AM to 2AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
September | 18 | 2AM to 3AM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
September | 18 | 3AM to 4AM | 64 | 62 | 61 | 82.1 | 28.15 | 0.0737 | 0.54 | 13.73 | 0
September | 18 | 4AM to 5AM | 63 | 61.7 | 61 | 82.1 | 27.89 | 0.0739 | 0.54 | 13.7 | 0
September | 18 | 5AM to 6AM | 62.1 | 58.9 | 57 | 71.1 | 25.95 | 0.0741 | 0.47 | 13.64 | 0
September | 18 | 6AM to 7AM | 63 | 60.4 | 59 | 76.4 | 27 | 0.0739 | 0.5 | 13.68 | 0
September | 18 | 7AM to 8AM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
September | 18 | 8AM to 9AM | 66.9 | 61.2 | 57.9 | 73.5 | 27.51 | 0.0734 | 0.48 | 13.77 | 0
September | 18 | 9AM to 10AM | 70 | 63.5 | 60.1 | 79.5 | 29.2 | 0.0729 | 0.52 | 13.87 | 0
September | 18 | 10AM to 11AM | 72 | 62.4 | 57 | 71.1 | 28.37 | 0.0727 | 0.47 | 13.9 | 0
September | 18 | 11AM to 12PM | 73.9 | 63.6 | 57.9 | 73.5 | 29.23 | 0.0724 | 0.48 | 13.96 | 0
September | 18 | 12PM to 1PM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
September | 18 | 1PM to 2PM | 72 | 62.4 | 57 | 71.1 | 28.37 | 0.0727 | 0.47 | 13.9 | 0
September | 18 | 2PM to 3PM | 71.1 | 61.5 | 55.9 | 68.3 | 27.72 | 0.0728 | 0.45 | 13.87 | 0
September | 18 | 3PM to 4PM | 69.1 | 60.8 | 55.9 | 68.3 | 27.23 | 0.0731 | 0.45 | 13.81 | 0
September | 18 | 4PM to 5PM | 66 | 60.3 | 57 | 71.1 | 26.92 | 0.0735 | 0.47 | 13.74 | 0
September | 18 | 5PM to 6PM | 66 | 60.3 | 57 | 71.1 | 26.92 | 0.0735 | 0.47 | 13.74 | 0
September | 18 | 6PM to 7PM | 64.9 | 61.1 | 59 | 76.4 | 27.48 | 0.0736 | 0.5 | 13.73 | 0
September | 18 | 7PM to 8PM | 64 | 61.5 | 60.1 | 79.5 | 27.74 | 0.0737 | 0.52 | 13.72 | 0
September | 18 | 8PM to 9PM | 62.1 | 60.8 | 60.1 | 79.5 | 27.26 | 0.074 | 0.52 | 13.67 | 0
September | 18 | 9PM to 10PM | 61 | 60.4 | 60.1 | 79.5 | 26.99 | 0.0742 | 0.52 | 13.64 | 0
September | 18 | 10PM to 11PM | 57.9 | 57.4 | 57 | 71.1 | 24.94 | 0.0747 | 0.47 | 13.53 | 0
September | 18 | 11PM to 12AM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
September | 19 | 12AM to 1AM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
September | 19 | 1AM to 2AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
September | 19 | 2AM to 3AM | 55 | 54.4 | 54 | 63.5 | 23.06 | 0.0751 | 0.42 | 13.43 | 0
September | 19 | 3AM to 4AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
September | 19 | 4AM to 5AM | 55 | 54.4 | 54 | 63.5 | 23.06 | 0.0751 | 0.42 | 13.43 | 0
September | 19 | 5AM to 6AM | 55 | 54.4 | 54 | 63.5 | 23.06 | 0.0751 | 0.42 | 13.43 | 0
September | 19 | 6AM to 7AM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
September | 19 | 7AM to 8AM | 61 | 56.7 | 54 | 63.5 | 24.51 | 0.0743 | 0.42 | 13.59 | 0
September | 19 | 8AM to 9AM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
September | 19 | 9AM to 10AM | 69.1 | 58.3 | 51.1 | 57 | 25.47 | 0.0732 | 0.38 | 13.78 | 0
September | 19 | 10AM to 11AM | 73 | 59.2 | 50 | 54.7 | 26.08 | 0.0726 | 0.36 | 13.88 | 0
September | 19 | 11AM to 12PM | 75 | 59 | 48 | 50.8 | 25.95 | 0.0724 | 0.34 | 13.91 | 0
September | 19 | 12PM to 1PM | 75 | 58.2 | 46 | 47.1 | 25.37 | 0.0724 | 0.31 | 13.9 | 0
September | 19 | 1PM to 2PM | 75.9 | 58.9 | 46.9 | 48.8 | 25.85 | 0.0723 | 0.32 | 13.93 | 0
September | 19 | 2PM to 3PM | 75.9 | 58.5 | 46 | 47.1 | 25.59 | 0.0723 | 0.31 | 13.93 | 0
September | 19 | 3PM to 4PM | 77 | 57.7 | 43 | 41.9 | 25.03 | 0.0722 | 0.28 | 13.94 | 0
September | 19 | 4PM to 5PM | 75.9 | 56.9 | 42.1 | 40.4 | 24.54 | 0.0723 | 0.27 | 13.91 | 0
September | 19 | 5PM to 6PM | 72 | 56.6 | 45 | 45.2 | 24.33 | 0.0728 | 0.3 | 13.82 | 0
September | 19 | 6PM to 7PM | 66.9 | 55.1 | 46 | 47.1 | 23.4 | 0.0735 | 0.31 | 13.69 | 0
September | 19 | 7PM to 8PM | 64.9 | 53.8 | 45 | 45.2 | 22.62 | 0.0738 | 0.3 | 13.63 | 0
September | 19 | 8PM to 9PM | 63 | 54.4 | 48 | 50.8 | 23.01 | 0.0741 | 0.34 | 13.6 | 0
September | 19 | 9PM to 10PM | 61 | 52.6 | 46 | 47.1 | 21.96 | 0.0744 | 0.31 | 13.54 | 0
September | 19 | 10PM to 11PM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
September | 19 | 11PM to 12AM | 60.1 | 52.3 | 46 | 47.1 | 21.74 | 0.0745 | 0.31 | 13.51 | 0
September | 20 | 12AM to 1AM | 57.9 | 51.3 | 46 | 47.1 | 21.22 | 0.0748 | 0.31 | 13.46 | 0
September | 20 | 1AM to 2AM | 57 | 51.4 | 46.9 | 48.8 | 21.25 | 0.0749 | 0.32 | 13.44 | 0
September | 20 | 2AM to 3AM | 54 | 48.7 | 44.1 | 43.6 | 19.72 | 0.0754 | 0.29 | 13.34 | 0
September | 20 | 3AM to 4AM | 55 | 49.6 | 45 | 45.2 | 20.22 | 0.0752 | 0.3 | 13.38 | 0
September | 20 | 4AM to 5AM | 53.1 | 48.7 | 45 | 45.2 | 19.74 | 0.0755 | 0.3 | 13.33 | 0
September | 20 | 5AM to 6AM | 54 | 49.1 | 45 | 45.2 | 19.96 | 0.0754 | 0.3 | 13.35 | 0
September | 20 | 6AM to 7AM | 55.9 | 50.9 | 46.9 | 48.8 | 20.99 | 0.0751 | 0.32 | 13.41 | 0
September | 20 | 7AM to 8AM | 61 | 53.6 | 48 | 50.8 | 22.53 | 0.0743 | 0.34 | 13.55 | 0
September | 20 | 8AM to 9AM | 64.9 | 55.6 | 48.9 | 52.6 | 23.77 | 0.0738 | 0.35 | 13.66 | 0
September | 20 | 9AM to 10AM | 68 | 56.8 | 48.9 | 52.6 | 24.52 | 0.0733 | 0.35 | 13.74 | 0
September | 20 | 10AM to 11AM | 71.1 | 58 | 48.9 | 52.6 | 25.26 | 0.0729 | 0.35 | 13.82 | 0
September | 20 | 11AM to 12PM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
September | 20 | 12PM to 1PM | 70 | 56.7 | 46.9 | 48.8 | 24.4 | 0.0731 | 0.32 | 13.78 | 0
September | 20 | 1PM to 2PM | 73.9 | 57.8 | 46 | 47.1 | 25.11 | 0.0726 | 0.31 | 13.87 | 0
September | 20 | 2PM to 3PM | 73 | 57.4 | 46 | 47.1 | 24.89 | 0.0727 | 0.31 | 13.85 | 0
September | 20 | 3PM to 4PM | 72 | 57.4 | 46.9 | 48.8 | 24.88 | 0.0728 | 0.32 | 13.83 | 0
September | 20 | 4PM to 5PM | 70 | 56.3 | 46 | 47.1 | 24.15 | 0.0731 | 0.31 | 13.77 | 0
September | 20 | 5PM to 6PM | 68 | 55.5 | 46 | 47.1 | 23.66 | 0.0734 | 0.31 | 13.72 | 0
September | 20 | 6PM to 7PM | 64.9 | 53.8 | 45 | 45.2 | 22.62 | 0.0738 | 0.3 | 13.63 | 0
September | 20 | 7PM to 8PM | 63 | 53 | 45 | 45.2 | 22.14 | 0.0741 | 0.3 | 13.58 | 0
September | 20 | 8PM to 9PM | 60.1 | 52.3 | 46 | 47.1 | 21.74 | 0.0745 | 0.31 | 13.51 | 0
September | 20 | 9PM to 10PM | 57 | 51 | 46 | 47.1 | 21 | 0.0749 | 0.31 | 13.43 | 0
September | 20 | 10PM to 11PM | 55 | 50.6 | 46.9 | 48.8 | 20.77 | 0.0752 | 0.32 | 13.39 | 0
September | 20 | 11PM to 12AM | 53.1 | 49.7 | 46.9 | 48.8 | 20.29 | 0.0755 | 0.32 | 13.34 | 0
September | 21 | 12AM to 1AM | 54 | 50.1 | 46.9 | 48.8 | 20.51 | 0.0754 | 0.32 | 13.36 | 0
September | 21 | 1AM to 2AM | 52 | 49.2 | 46.9 | 48.8 | 20.03 | 0.0757 | 0.32 | 13.31 | 0
September | 21 | 2AM to 3AM | 51.1 | 48.8 | 46.9 | 48.8 | 19.81 | 0.0758 | 0.32 | 13.29 | 1
September | 21 | 3AM to 4AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
September | 21 | 4AM to 5AM | 51.1 | 49.4 | 48 | 50.8 | 20.13 | 0.0758 | 0.34 | 13.29 | 1
September | 21 | 5AM to 6AM | 51.1 | 49.4 | 48 | 50.8 | 20.13 | 0.0758 | 0.34 | 13.29 | 1
September | 21 | 6AM to 7AM | 53.1 | 51.3 | 50 | 54.7 | 21.22 | 0.0755 | 0.36 | 13.35 | 0
September | 21 | 7AM to 8AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
September | 21 | 8AM to 9AM | 60.1 | 54.8 | 51.1 | 57 | 23.28 | 0.0744 | 0.38 | 13.54 | 0
September | 21 | 9AM to 10AM | 64 | 56.4 | 51.1 | 57 | 24.25 | 0.0739 | 0.38 | 13.65 | 0
September | 21 | 10AM to 11AM | 68 | 57.3 | 50 | 54.7 | 24.86 | 0.0733 | 0.36 | 13.74 | 0
September | 21 | 11AM to 12PM | 70 | 57.6 | 48.9 | 52.6 | 25 | 0.0731 | 0.35 | 13.79 | 0
September | 21 | 12PM to 1PM | 69.1 | 57.2 | 48.9 | 52.6 | 24.78 | 0.0732 | 0.35 | 13.77 | 0
September | 21 | 1PM to 2PM | 72 | 57.4 | 46.9 | 48.8 | 24.88 | 0.0728 | 0.32 | 13.83 | 0
September | 21 | 2PM to 3PM | 69.1 | 55.4 | 45 | 45.2 | 23.63 | 0.0732 | 0.3 | 13.74 | 0
September | 21 | 3PM to 4PM | 68 | 56.4 | 48 | 50.8 | 24.24 | 0.0734 | 0.34 | 13.73 | 0
September | 21 | 4PM to 5PM | 68 | 56.4 | 48 | 50.8 | 24.24 | 0.0734 | 0.34 | 13.73 | 0
September | 21 | 5PM to 6PM | 66.9 | 56 | 48 | 50.8 | 23.98 | 0.0735 | 0.34 | 13.7 | 0
September | 21 | 6PM to 7PM | 64.9 | 55.2 | 48 | 50.8 | 23.5 | 0.0738 | 0.34 | 13.65 | 0
September | 21 | 7PM to 8PM | 63 | 54.8 | 48.9 | 52.6 | 23.29 | 0.074 | 0.35 | 13.61 | 0
September | 21 | 8PM to 9PM | 63 | 55.4 | 50 | 54.7 | 23.63 | 0.074 | 0.36 | 13.61 | 0
September | 21 | 9PM to 10PM | 61 | 55.2 | 51.1 | 57 | 23.5 | 0.0743 | 0.38 | 13.57 | 0
September | 21 | 10PM to 11PM | 57.9 | 53.9 | 51.1 | 57 | 22.75 | 0.0747 | 0.38 | 13.49 | 0
September | 21 | 11PM to 12AM | 57.9 | 54.4 | 52 | 59 | 23.06 | 0.0747 | 0.39 | 13.49 | 0
September | 22 | 12AM to 1AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
September | 22 | 1AM to 2AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
September | 22 | 2AM to 3AM | 53.1 | 51.3 | 50 | 54.7 | 21.22 | 0.0755 | 0.36 | 13.35 | 0
September | 22 | 3AM to 4AM | 52 | 50.9 | 50 | 54.7 | 20.96 | 0.0756 | 0.36 | 13.33 | 0
September | 22 | 4AM to 5AM | 52 | 50.9 | 50 | 54.7 | 20.96 | 0.0756 | 0.36 | 13.33 | 0
September | 22 | 5AM to 6AM | 52 | 50.3 | 48.9 | 52.6 | 20.62 | 0.0756 | 0.35 | 13.32 | 0
September | 22 | 6AM to 7AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
September | 22 | 7AM to 8AM | 57 | 54.7 | 53.1 | 61.4 | 23.22 | 0.0748 | 0.41 | 13.48 | 0
September | 22 | 8AM to 9AM | 61 | 57.9 | 55.9 | 68.3 | 25.26 | 0.0742 | 0.45 | 13.6 | 0
September | 22 | 9AM to 10AM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
September | 22 | 10AM to 11AM | 69.1 | 60.8 | 55.9 | 68.3 | 27.23 | 0.0731 | 0.45 | 13.81 | 0
September | 22 | 11AM to 12PM | 71.1 | 61.5 | 55.9 | 68.3 | 27.72 | 0.0728 | 0.45 | 13.87 | 0
September | 22 | 12PM to 1PM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
September | 22 | 1PM to 2PM | 70 | 58.1 | 50 | 54.7 | 25.34 | 0.0731 | 0.36 | 13.8 | 0
September | 22 | 2PM to 3PM | 69.1 | 57.7 | 50 | 54.7 | 25.12 | 0.0732 | 0.36 | 13.77 | 0
September | 22 | 3PM to 4PM | 68 | 56.8 | 48.9 | 52.6 | 24.52 | 0.0733 | 0.35 | 13.74 | 0
September | 22 | 4PM to 5PM | 66.9 | 56 | 48 | 50.8 | 23.98 | 0.0735 | 0.34 | 13.7 | 0
September | 22 | 5PM to 6PM | 64.9 | 55.2 | 48 | 50.8 | 23.5 | 0.0738 | 0.34 | 13.65 | 0
September | 22 | 6PM to 7PM | 64 | 55.3 | 48.9 | 52.6 | 23.55 | 0.0739 | 0.35 | 13.63 | 0
September | 22 | 7PM to 8PM | 63 | 53.9 | 46.9 | 48.8 | 22.7 | 0.0741 | 0.32 | 13.59 | 0
September | 22 | 8PM to 9PM | 63 | 54.8 | 48.9 | 52.6 | 23.29 | 0.074 | 0.35 | 13.61 | 0
September | 22 | 9PM to 10PM | 61 | 54.6 | 50 | 54.7 | 23.15 | 0.0743 | 0.36 | 13.56 | 0
September | 22 | 10PM to 11PM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
September | 22 | 11PM to 12AM | 57.9 | 52.8 | 48.9 | 52.6 | 22.06 | 0.0748 | 0.35 | 13.47 | 0
September | 23 | 12AM to 1AM | 55.9 | 52 | 48.9 | 52.6 | 21.58 | 0.0751 | 0.35 | 13.42 | 0
September | 23 | 1AM to 2AM | 55.9 | 52 | 48.9 | 52.6 | 21.58 | 0.0751 | 0.35 | 13.42 | 0
September | 23 | 2AM to 3AM | 52 | 49.8 | 48 | 50.8 | 20.34 | 0.0756 | 0.34 | 13.31 | 0
September | 23 | 3AM to 4AM | 54 | 51.7 | 50 | 54.7 | 21.44 | 0.0753 | 0.36 | 13.38 | 0
September | 23 | 4AM to 5AM | 55 | 50.6 | 46.9 | 48.8 | 20.77 | 0.0752 | 0.32 | 13.39 | 0
September | 23 | 5AM to 6AM | 55 | 52.2 | 50 | 54.7 | 21.7 | 0.0752 | 0.36 | 13.41 | 0
September | 23 | 6AM to 7AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
September | 23 | 7AM to 8AM | 60.1 | 56.4 | 54 | 63.5 | 24.29 | 0.0744 | 0.42 | 13.56 | 0
September | 23 | 8AM to 9AM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
September | 23 | 9AM to 10AM | 69.1 | 58.3 | 51.1 | 57 | 25.47 | 0.0732 | 0.38 | 13.78 | 0
September | 23 | 10AM to 11AM | 66.9 | 54.6 | 45 | 45.2 | 23.1 | 0.0735 | 0.3 | 13.69 | 0
September | 23 | 11AM to 12PM | 71.1 | 58 | 48.9 | 52.6 | 25.26 | 0.0729 | 0.35 | 13.82 | 0
September | 23 | 12PM to 1PM | 72 | 57 | 46 | 47.1 | 24.63 | 0.0728 | 0.31 | 13.82 | 0
September | 23 | 1PM to 2PM | 73 | 59.7 | 51.1 | 57 | 26.44 | 0.0726 | 0.38 | 13.88 | 0
September | 23 | 2PM to 3PM | 73.9 | 57.8 | 46 | 47.1 | 25.11 | 0.0726 | 0.31 | 13.87 | 0
September | 23 | 3PM to 4PM | 75 | 58.6 | 46.9 | 48.8 | 25.63 | 0.0724 | 0.32 | 13.91 | 0
September | 23 | 4PM to 5PM | 73.9 | 58.6 | 48 | 50.8 | 25.69 | 0.0725 | 0.34 | 13.89 | 0
September | 23 | 5PM to 6PM | 71.1 | 58 | 48.9 | 52.6 | 25.26 | 0.0729 | 0.35 | 13.82 | 0
September | 23 | 6PM to 7PM | 66 | 56 | 48.9 | 52.6 | 24.03 | 0.0736 | 0.35 | 13.69 | 0
September | 23 | 7PM to 8PM | 63 | 55.4 | 50 | 54.7 | 23.63 | 0.074 | 0.36 | 13.61 | 0
September | 23 | 8PM to 9PM | 59 | 54.9 | 52 | 59 | 23.32 | 0.0746 | 0.39 | 13.52 | 0
September | 23 | 9PM to 10PM | 62.1 | 55 | 50 | 54.7 | 23.41 | 0.0742 | 0.36 | 13.59 | 0
September | 23 | 10PM to 11PM | 61 | 54.6 | 50 | 54.7 | 23.15 | 0.0743 | 0.36 | 13.56 | 0
September | 23 | 11PM to 12AM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
September | 24 | 12AM to 1AM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
September | 24 | 1AM to 2AM | 57.9 | 52.8 | 48.9 | 52.6 | 22.06 | 0.0748 | 0.35 | 13.47 | 0
September | 24 | 2AM to 3AM | 55.9 | 52 | 48.9 | 52.6 | 21.58 | 0.0751 | 0.35 | 13.42 | 0
September | 24 | 3AM to 4AM | 57 | 52.4 | 48.9 | 52.6 | 21.84 | 0.0749 | 0.35 | 13.45 | 0
September | 24 | 4AM to 5AM | 55 | 51.1 | 48 | 50.8 | 21.09 | 0.0752 | 0.34 | 13.39 | 0
September | 24 | 5AM to 6AM | 55.9 | 52 | 48.9 | 52.6 | 21.58 | 0.0751 | 0.35 | 13.42 | 0
September | 24 | 6AM to 7AM | 57.9 | 53.9 | 51.1 | 57 | 22.75 | 0.0747 | 0.38 | 13.49 | 0
September | 24 | 7AM to 8AM | 62.1 | 56.1 | 52 | 59 | 24.07 | 0.0741 | 0.39 | 13.6 | 0
September | 24 | 8AM to 9AM | 68 | 58.3 | 52 | 59 | 25.52 | 0.0733 | 0.39 | 13.76 | 0
September | 24 | 9AM to 10AM | 72 | 60.3 | 53.1 | 61.4 | 26.86 | 0.0727 | 0.41 | 13.87 | 0
September | 24 | 10AM to 11AM | 75.9 | 62.2 | 54 | 63.5 | 28.15 | 0.0722 | 0.42 | 13.98 | 0
September | 24 | 11AM to 12PM | 80.1 | 63.6 | 54 | 63.5 | 29.16 | 0.0716 | 0.42 | 14.09 | 0
September | 24 | 12PM to 1PM | 82.9 | 62.2 | 48.9 | 52.6 | 28.15 | 0.0713 | 0.35 | 14.13 | 0
September | 24 | 1PM to 2PM | 84 | 64 | 52 | 59 | 29.42 | 0.0711 | 0.39 | 14.17 | 0
September | 24 | 2PM to 3PM | 84.9 | 63.4 | 50 | 54.7 | 28.98 | 0.071 | 0.36 | 14.18 | 0
September | 24 | 3PM to 4PM | 84.9 | 63.8 | 51.1 | 57 | 29.33 | 0.071 | 0.38 | 14.19 | 0
September | 24 | 4PM to 5PM | 82 | 62.4 | 50 | 54.7 | 28.28 | 0.0714 | 0.36 | 14.11 | 0
September | 24 | 5PM to 6PM | 80.1 | 63.1 | 53.1 | 61.4 | 28.83 | 0.0716 | 0.41 | 14.08 | 0
September | 24 | 6PM to 7PM | 75 | 61.9 | 54 | 63.5 | 27.93 | 0.0723 | 0.42 | 13.95 | 0
September | 24 | 7PM to 8PM | 73 | 62.8 | 57 | 71.1 | 28.63 | 0.0725 | 0.47 | 13.93 | 0
September | 24 | 8PM to 9PM | 71.1 | 61.5 | 55.9 | 68.3 | 27.72 | 0.0728 | 0.45 | 13.87 | 0
September | 24 | 9PM to 10PM | 70 | 60.7 | 55 | 66.1 | 27.11 | 0.073 | 0.44 | 13.83 | 0
September | 24 | 10PM to 11PM | 69.1 | 60.3 | 55 | 66.1 | 26.89 | 0.0731 | 0.44 | 13.81 | 0
September | 24 | 11PM to 12AM | 66.9 | 59.6 | 55 | 66.1 | 26.36 | 0.0734 | 0.44 | 13.75 | 0
September | 25 | 12AM to 1AM | 64.9 | 58.8 | 55 | 66.1 | 25.88 | 0.0737 | 0.44 | 13.7 | 0
September | 25 | 1AM to 2AM | 63 | 57 | 53.1 | 61.4 | 24.66 | 0.074 | 0.41 | 13.63 | 0
September | 25 | 2AM to 3AM | 61 | 55.2 | 51.1 | 57 | 23.5 | 0.0743 | 0.38 | 13.57 | 0
September | 25 | 3AM to 4AM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
September | 25 | 4AM to 5AM | 57.9 | 52.8 | 48.9 | 52.6 | 22.06 | 0.0748 | 0.35 | 13.47 | 0
September | 25 | 5AM to 6AM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
September | 25 | 6AM to 7AM | 57.9 | 52.8 | 48.9 | 52.6 | 22.06 | 0.0748 | 0.35 | 13.47 | 0
September | 25 | 7AM to 8AM | 60.1 | 53.2 | 48 | 50.8 | 22.31 | 0.0745 | 0.34 | 13.53 | 0
September | 25 | 8AM to 9AM | 64 | 54.3 | 46.9 | 48.8 | 22.96 | 0.0739 | 0.32 | 13.62 | 0
September | 25 | 9AM to 10AM | 68 | 55.9 | 46.9 | 48.8 | 23.92 | 0.0734 | 0.32 | 13.73 | 0
September | 25 | 10AM to 11AM | 71.1 | 57.1 | 46.9 | 48.8 | 24.67 | 0.0729 | 0.32 | 13.8 | 0
September | 25 | 11AM to 12PM | 73.9 | 56.9 | 44.1 | 43.6 | 24.57 | 0.0726 | 0.29 | 13.86 | 0
September | 25 | 12PM to 1PM | 75.9 | 57.7 | 44.1 | 43.6 | 25.05 | 0.0723 | 0.29 | 13.92 | 0
September | 25 | 1PM to 2PM | 80.1 | 59.2 | 44.1 | 43.6 | 26.05 | 0.0718 | 0.29 | 14.02 | 0
September | 25 | 2PM to 3PM | 80.1 | 59.6 | 45 | 45.2 | 26.3 | 0.0717 | 0.3 | 14.03 | 0
September | 25 | 3PM to 4PM | 80.1 | 59.2 | 44.1 | 43.6 | 26.05 | 0.0718 | 0.29 | 14.02 | 0
September | 25 | 4PM to 5PM | 78.1 | 57.3 | 41 | 38.8 | 24.81 | 0.0721 | 0.26 | 13.96 | 0
September | 25 | 5PM to 6PM | 75 | 55.8 | 39.9 | 37.2 | 23.81 | 0.0725 | 0.25 | 13.87 | 0
September | 25 | 6PM to 7PM | 71.1 | 52.5 | 35.1 | 30.6 | 21.84 | 0.0731 | 0.2 | 13.75 | 0
September | 25 | 7PM to 8PM | 70 | 51.4 | 33.1 | 28.3 | 21.21 | 0.0732 | 0.19 | 13.71 | 0
September | 25 | 8PM to 9PM | 66 | 55.6 | 48 | 50.8 | 23.76 | 0.0736 | 0.34 | 13.68 | 0
September | 25 | 9PM to 10PM | 63 | 54.8 | 48.9 | 52.6 | 23.29 | 0.074 | 0.35 | 13.61 | 0
September | 25 | 10PM to 11PM | 62.1 | 55 | 50 | 54.7 | 23.41 | 0.0742 | 0.36 | 13.59 | 0
September | 25 | 11PM to 12AM | 61 | 55.2 | 51.1 | 57 | 23.5 | 0.0743 | 0.38 | 13.57 | 0
September | 26 | 12AM to 1AM | 61 | 54 | 48.9 | 52.6 | 22.81 | 0.0743 | 0.35 | 13.55 | 0
September | 26 | 1AM to 2AM | 62.1 | 54.5 | 48.9 | 52.6 | 23.07 | 0.0742 | 0.35 | 13.58 | 0
September | 26 | 2AM to 3AM | 62.1 | 54.5 | 48.9 | 52.6 | 23.07 | 0.0742 | 0.35 | 13.58 | 0
September | 26 | 3AM to 4AM | 63 | 53.9 | 46.9 | 48.8 | 22.7 | 0.0741 | 0.32 | 13.59 | 0
September | 26 | 4AM to 5AM | 63 | 54.4 | 48 | 50.8 | 23.01 | 0.0741 | 0.34 | 13.6 | 0
September | 26 | 5AM to 6AM | 62.1 | 55 | 50 | 54.7 | 23.41 | 0.0742 | 0.36 | 13.59 | 0
September | 26 | 6AM to 7AM | 63 | 55.9 | 51.1 | 57 | 23.98 | 0.074 | 0.38 | 13.62 | 0
September | 26 | 7AM to 8AM | 69.1 | 57.2 | 48.9 | 52.6 | 24.78 | 0.0732 | 0.35 | 13.77 | 0
September | 26 | 8AM to 9AM | 73 | 59.7 | 51.1 | 57 | 26.44 | 0.0726 | 0.38 | 13.88 | 0
September | 26 | 9AM to 10AM | 73.9 | 60 | 51.1 | 57 | 26.66 | 0.0725 | 0.38 | 13.91 | 0
September | 26 | 10AM to 11AM | 78.1 | 63.9 | 55.9 | 68.3 | 29.43 | 0.0719 | 0.45 | 14.05 | 0
September | 26 | 11AM to 12PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
September | 26 | 12PM to 1PM | 79 | 65.3 | 57.9 | 73.5 | 30.46 | 0.0717 | 0.48 | 14.09 | 0
September | 26 | 1PM to 2PM | 82.9 | 66.5 | 57.9 | 73.5 | 31.43 | 0.0712 | 0.48 | 14.19 | 0
September | 26 | 2PM to 3PM | 84 | 66.9 | 57.9 | 73.5 | 31.69 | 0.0711 | 0.48 | 14.22 | 0
September | 26 | 3PM to 4PM | 82.9 | 65.1 | 55 | 66.1 | 30.27 | 0.0712 | 0.44 | 14.17 | 0
September | 26 | 4PM to 5PM | 78.1 | 62.5 | 53.1 | 61.4 | 28.35 | 0.0719 | 0.41 | 14.03 | 0
September | 26 | 5PM to 6PM | 75.9 | 64.3 | 57.9 | 73.5 | 29.71 | 0.0721 | 0.48 | 14.01 | 0
September | 26 | 6PM to 7PM | 79 | 63.2 | 54 | 63.5 | 28.9 | 0.0718 | 0.42 | 14.06 | 0
September | 26 | 7PM to 8PM | 73.9 | 66 | 62.1 | 85.4 | 31.09 | 0.0723 | 0.56 | 14 | 0
September | 26 | 8PM to 9PM | 75 | 63.5 | 57 | 71.1 | 29.12 | 0.0723 | 0.47 | 13.98 | 0
September | 26 | 9PM to 10PM | 73.9 | 61 | 53.1 | 61.4 | 27.34 | 0.0725 | 0.41 | 13.92 | 0
September | 26 | 10PM to 11PM | 72 | 59.8 | 52 | 59 | 26.48 | 0.0728 | 0.39 | 13.86 | 0
September | 26 | 11PM to 12AM | 70 | 58.1 | 50 | 54.7 | 25.34 | 0.0731 | 0.36 | 13.8 | 0
September | 27 | 12AM to 1AM | 70 | 55.8 | 45 | 45.2 | 23.85 | 0.0731 | 0.3 | 13.77 | 0
September | 27 | 1AM to 2AM | 66.9 | 56.9 | 50 | 54.7 | 24.59 | 0.0735 | 0.36 | 13.72 | 0
September | 27 | 2AM to 3AM | 66 | 58.6 | 54 | 63.5 | 25.74 | 0.0735 | 0.42 | 13.72 | 0
September | 27 | 3AM to 4AM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
September | 27 | 4AM to 5AM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
September | 27 | 5AM to 6AM | 62.1 | 57.1 | 54 | 63.5 | 24.77 | 0.0741 | 0.42 | 13.62 | 0
September | 27 | 6AM to 7AM | 63 | 58.1 | 55 | 66.1 | 25.39 | 0.074 | 0.44 | 13.65 | 0
September | 27 | 7AM to 8AM | 70 | 56.7 | 46.9 | 48.8 | 24.4 | 0.0731 | 0.32 | 13.78 | 0
September | 27 | 8AM to 9AM | 75 | 60.4 | 51.1 | 57 | 26.92 | 0.0724 | 0.38 | 13.93 | 0
September | 27 | 9AM to 10AM | 77 | 64.1 | 57 | 71.1 | 29.6 | 0.072 | 0.47 | 14.03 | 0
September | 27 | 10AM to 11AM | 80.1 | 64.6 | 55.9 | 68.3 | 29.92 | 0.0716 | 0.45 | 14.1 | 0
September | 27 | 11AM to 12PM | 82 | 64.2 | 54 | 63.5 | 29.65 | 0.0714 | 0.42 | 14.14 | 0
September | 27 | 12PM to 1PM | 82.9 | 64.5 | 54 | 63.5 | 29.87 | 0.0713 | 0.42 | 14.16 | 0
September | 27 | 1PM to 2PM | 84 | 63.5 | 51.1 | 57 | 29.11 | 0.0712 | 0.38 | 14.17 | 0
September | 27 | 2PM to 3PM | 84 | 64 | 52 | 59 | 29.42 | 0.0711 | 0.39 | 14.17 | 0
September | 27 | 3PM to 4PM | 82.9 | 63.2 | 51.1 | 57 | 28.85 | 0.0713 | 0.38 | 14.14 | 0
September | 27 | 4PM to 5PM | 82 | 62.9 | 51.1 | 57 | 28.63 | 0.0714 | 0.38 | 14.12 | 0
September | 27 | 5PM to 6PM | 80.1 | 63.1 | 53.1 | 61.4 | 28.83 | 0.0716 | 0.41 | 14.08 | 0
September | 27 | 6PM to 7PM | 78.1 | 61.9 | 52 | 59 | 27.97 | 0.0719 | 0.39 | 14.02 | 0
September | 27 | 7PM to 8PM | 75.9 | 61.2 | 52 | 59 | 27.45 | 0.0722 | 0.39 | 13.96 | 0
September | 27 | 8PM to 9PM | 73 | 59.7 | 51.1 | 57 | 26.44 | 0.0726 | 0.38 | 13.88 | 0
September | 27 | 9PM to 10PM | 72 | 57 | 46 | 47.1 | 24.63 | 0.0728 | 0.31 | 13.82 | 0
September | 27 | 10PM to 11PM | 71.1 | 57.6 | 48 | 50.8 | 24.98 | 0.0729 | 0.34 | 13.81 | 0
September | 27 | 11PM to 12AM | 70 | 56.3 | 46 | 47.1 | 24.15 | 0.0731 | 0.31 | 13.77 | 0
September | 28 | 12AM to 1AM | 68 | 55.9 | 46.9 | 48.8 | 23.92 | 0.0734 | 0.32 | 13.73 | 0
September | 28 | 1AM to 2AM | 69.1 | 57.7 | 50 | 54.7 | 25.12 | 0.0732 | 0.36 | 13.77 | 0
September | 28 | 2AM to 3AM | 68 | 58.3 | 52 | 59 | 25.52 | 0.0733 | 0.39 | 13.76 | 0
September | 28 | 3AM to 4AM | 66 | 56 | 48.9 | 52.6 | 24.03 | 0.0736 | 0.35 | 13.69 | 0
September | 28 | 4AM to 5AM | 66 | 59.7 | 55.9 | 68.3 | 26.49 | 0.0735 | 0.45 | 13.73 | 0
September | 28 | 5AM to 6AM | 66 | 60.3 | 57 | 71.1 | 26.92 | 0.0735 | 0.47 | 13.74 | 0
September | 28 | 6AM to 7AM | 68 | 60.4 | 55.9 | 68.3 | 26.97 | 0.0732 | 0.45 | 13.79 | 0
September | 28 | 7AM to 8AM | 69.1 | 59.8 | 54 | 63.5 | 26.48 | 0.0731 | 0.42 | 13.8 | 0
September | 28 | 8AM to 9AM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
September | 28 | 9AM to 10AM | 78.1 | 65 | 57.9 | 73.5 | 30.24 | 0.0718 | 0.48 | 14.07 | 0
September | 28 | 10AM to 11AM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
September | 28 | 11AM to 12PM | 82 | 65.8 | 57 | 71.1 | 30.84 | 0.0713 | 0.47 | 14.16 | 0
September | 28 | 12PM to 1PM | 79 | 64.8 | 57 | 71.1 | 30.09 | 0.0717 | 0.47 | 14.08 | 0
September | 28 | 1PM to 2PM | 81 | 67.6 | 61 | 82.1 | 32.3 | 0.0714 | 0.54 | 14.17 | 0
September | 28 | 2PM to 3PM | 82 | 66.2 | 57.9 | 73.5 | 31.21 | 0.0713 | 0.48 | 14.17 | 0
September | 28 | 3PM to 4PM | 81 | 65.9 | 57.9 | 73.5 | 30.94 | 0.0715 | 0.48 | 14.14 | 0
September | 28 | 4PM to 5PM | 72 | 62.9 | 57.9 | 73.5 | 28.74 | 0.0727 | 0.48 | 13.91 | 0
September | 28 | 5PM to 6PM | 69.1 | 66.3 | 64.9 | 94.6 | 31.34 | 0.0729 | 0.62 | 13.9 | 0
September | 28 | 6PM to 7PM | 68 | 65.9 | 64.9 | 94.6 | 31.08 | 0.0731 | 0.62 | 13.87 | 0
September | 28 | 7PM to 8PM | 66.9 | 66.3 | 66 | 98.4 | 31.39 | 0.0732 | 0.64 | 13.85 | 0
September | 28 | 8PM to 9PM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
September | 28 | 9PM to 10PM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
September | 28 | 10PM to 11PM | 66 | 65.3 | 64.9 | 94.6 | 30.59 | 0.0734 | 0.62 | 13.82 | 0
September | 28 | 11PM to 12AM | 64 | 63.3 | 63 | 88.2 | 29.09 | 0.0737 | 0.58 | 13.74 | 0
September | 29 | 12AM to 1AM | 64 | 64 | 64 | 91.7 | 29.64 | 0.0737 | 0.6 | 13.75 | 0
September | 29 | 1AM to 2AM | 64 | 63.3 | 63 | 88.2 | 29.09 | 0.0737 | 0.58 | 13.74 | 0
September | 29 | 2AM to 3AM | 64 | 63.3 | 63 | 88.2 | 29.09 | 0.0737 | 0.58 | 13.74 | 0
September | 29 | 3AM to 4AM | 64 | 63.3 | 63 | 88.2 | 29.09 | 0.0737 | 0.58 | 13.74 | 0
September | 29 | 4AM to 5AM | 62.1 | 61.4 | 61 | 82.1 | 27.66 | 0.074 | 0.54 | 13.67 | 0
September | 29 | 5AM to 6AM | 62.1 | 60.8 | 60.1 | 79.5 | 27.26 | 0.074 | 0.52 | 13.67 | 0
September | 29 | 6AM to 7AM | 60.1 | 58.7 | 57.9 | 73.5 | 25.84 | 0.0743 | 0.48 | 13.6 | 0
September | 29 | 7AM to 8AM | 61 | 59.1 | 57.9 | 73.5 | 26.06 | 0.0742 | 0.48 | 13.62 | 0
September | 29 | 8AM to 9AM | 64 | 59 | 55.9 | 68.3 | 26 | 0.0738 | 0.45 | 13.68 | 0
September | 29 | 9AM to 10AM | 66 | 59.7 | 55.9 | 68.3 | 26.49 | 0.0735 | 0.45 | 13.73 | 0
September | 29 | 10AM to 11AM | 68 | 58.9 | 53.1 | 61.4 | 25.89 | 0.0733 | 0.41 | 13.76 | 0
September | 29 | 11AM to 12PM | 66.9 | 57.9 | 52 | 59 | 25.25 | 0.0735 | 0.39 | 13.73 | 0
September | 29 | 12PM to 1PM | 70 | 59.1 | 52 | 59 | 26 | 0.073 | 0.39 | 13.81 | 0
September | 29 | 1PM to 2PM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
September | 29 | 2PM to 3PM | 66.9 | 56.9 | 50 | 54.7 | 24.59 | 0.0735 | 0.36 | 13.72 | 0
September | 29 | 3PM to 4PM | 66.9 | 57.9 | 52 | 59 | 25.25 | 0.0735 | 0.39 | 13.73 | 0
September | 29 | 4PM to 5PM | 66 | 57.1 | 51.1 | 57 | 24.73 | 0.0736 | 0.38 | 13.7 | 0
September | 29 | 5PM to 6PM | 64.9 | 57.2 | 52 | 59 | 24.77 | 0.0737 | 0.39 | 13.68 | 0
September | 29 | 6PM to 7PM | 61 | 55.6 | 52 | 59 | 23.8 | 0.0743 | 0.39 | 13.57 | 0
September | 29 | 7PM to 8PM | 60.1 | 55.9 | 53.1 | 61.4 | 23.96 | 0.0744 | 0.41 | 13.56 | 0
September | 29 | 8PM to 9PM | 60.1 | 55.9 | 53.1 | 61.4 | 23.96 | 0.0744 | 0.41 | 13.56 | 0
September | 29 | 9PM to 10PM | 57.9 | 55 | 53.1 | 61.4 | 23.44 | 0.0747 | 0.41 | 13.5 | 0
September | 29 | 10PM to 11PM | 55.9 | 53.1 | 51.1 | 57 | 22.27 | 0.075 | 0.38 | 13.44 | 0
September | 29 | 11PM to 12AM | 57 | 54.7 | 53.1 | 61.4 | 23.22 | 0.0748 | 0.41 | 13.48 | 0
September | 30 | 12AM to 1AM | 55.9 | 50.9 | 46.9 | 48.8 | 20.99 | 0.0751 | 0.32 | 13.41 | 0
September | 30 | 1AM to 2AM | 55 | 49.6 | 45 | 45.2 | 20.22 | 0.0752 | 0.3 | 13.38 | 0
September | 30 | 2AM to 3AM | 54 | 50.6 | 48 | 50.8 | 20.83 | 0.0754 | 0.34 | 13.37 | 0
September | 30 | 3AM to 4AM | 51.1 | 48.8 | 46.9 | 48.8 | 19.81 | 0.0758 | 0.32 | 13.29 | 1
September | 30 | 4AM to 5AM | 50 | 45.4 | 41 | 38.8 | 18 | 0.076 | 0.26 | 13.23 | 1
September | 30 | 5AM to 6AM | 50 | 47.3 | 45 | 45.2 | 19 | 0.076 | 0.3 | 13.25 | 1
September | 30 | 6AM to 7AM | 51.1 | 48.4 | 46 | 47.1 | 19.55 | 0.0758 | 0.31 | 13.28 | 1
September | 30 | 7AM to 8AM | 55.9 | 50.5 | 46 | 47.1 | 20.73 | 0.0751 | 0.31 | 13.41 | 0
September | 30 | 8AM to 9AM | 59 | 52.8 | 48 | 50.8 | 22.05 | 0.0746 | 0.34 | 13.5 | 0
September | 30 | 9AM to 10AM | 63 | 54.8 | 48.9 | 52.6 | 23.29 | 0.074 | 0.35 | 13.61 | 0
September | 30 | 10AM to 11AM | 69.1 | 57.2 | 48.9 | 52.6 | 24.78 | 0.0732 | 0.35 | 13.77 | 0
September | 30 | 11AM to 12PM | 72 | 57.4 | 46.9 | 48.8 | 24.88 | 0.0728 | 0.32 | 13.83 | 0
September | 30 | 12PM to 1PM | 73 | 56.6 | 44.1 | 43.6 | 24.35 | 0.0727 | 0.29 | 13.84 | 0
September | 30 | 1PM to 2PM | 73.9 | 56.9 | 44.1 | 43.6 | 24.57 | 0.0726 | 0.29 | 13.86 | 0
September | 30 | 2PM to 3PM | 73.9 | 57.8 | 46 | 47.1 | 25.11 | 0.0726 | 0.31 | 13.87 | 0
September | 30 | 3PM to 4PM | 73.9 | 57.8 | 46 | 47.1 | 25.11 | 0.0726 | 0.31 | 13.87 | 0
September | 30 | 4PM to 5PM | 71.1 | 56.7 | 46 | 47.1 | 24.41 | 0.073 | 0.31 | 13.8 | 0
September | 30 | 5PM to 6PM | 69.1 | 56.3 | 46.9 | 48.8 | 24.18 | 0.0732 | 0.32 | 13.75 | 0
September | 30 | 6PM to 7PM | 64.9 | 54.7 | 46.9 | 48.8 | 23.18 | 0.0738 | 0.32 | 13.65 | 0
September | 30 | 7PM to 8PM | 63 | 53 | 45 | 45.2 | 22.14 | 0.0741 | 0.3 | 13.58 | 0
September | 30 | 8PM to 9PM | 60.1 | 51.3 | 44.1 | 43.6 | 21.2 | 0.0745 | 0.29 | 13.5 | 0
September | 30 | 9PM to 10PM | 58.6 | 51.1 | 45 | 45.2 | 21.09 | 0.0747 | 0.3 | 13.47 | 0
September | 30 | 10PM to 11PM | 57.2 | 50.9 | 45.7 | 46.5 | 20.94 | 0.0749 | 0.31 | 13.44 | 0
September | 30 | 11PM to 12AM | 55.8 | 50.7 | 46.6 | 48.1 | 20.84 | 0.0751 | 0.32 | 13.4 | 0
October | 1 | 12AM to 1AM | 54.3 | 50.5 | 47.5 | 49.8 | 20.75 | 0.0753 | 0.33 | 13.37 | 0
October | 1 | 1AM to 2AM | 52.9 | 50.4 | 48.4 | 51.5 | 20.67 | 0.0755 | 0.34 | 13.34 | 0
October | 1 | 2AM to 3AM | 51.4 | 50.1 | 49.1 | 52.9 | 20.54 | 0.0757 | 0.35 | 13.31 | 1
October | 1 | 3AM to 4AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 1 | 4AM to 5AM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
October | 1 | 5AM to 6AM | 48 | 48 | 48 | 50.8 | 19.38 | 0.0762 | 0.34 | 13.21 | 1
October | 1 | 6AM to 7AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 1 | 7AM to 8AM | 54 | 53.4 | 53.1 | 61.4 | 22.47 | 0.0753 | 0.41 | 13.4 | 0
October | 1 | 8AM to 9AM | 61 | 55.6 | 52 | 59 | 23.8 | 0.0743 | 0.39 | 13.57 | 0
October | 1 | 9AM to 10AM | 64.9 | 56.7 | 51.1 | 57 | 24.47 | 0.0737 | 0.38 | 13.67 | 0
October | 1 | 10AM to 11AM | 66.9 | 56.4 | 48.9 | 52.6 | 24.25 | 0.0735 | 0.35 | 13.71 | 0
October | 1 | 11AM to 12PM | 69.1 | 57.7 | 50 | 54.7 | 25.12 | 0.0732 | 0.36 | 13.77 | 0
October | 1 | 12PM to 1PM | 70 | 57.6 | 48.9 | 52.6 | 25 | 0.0731 | 0.35 | 13.79 | 0
October | 1 | 1PM to 2PM | 72 | 58.3 | 48.9 | 52.6 | 25.48 | 0.0728 | 0.35 | 13.84 | 0
October | 1 | 2PM to 3PM | 73 | 58.7 | 48.9 | 52.6 | 25.74 | 0.0726 | 0.35 | 13.87 | 0
October | 1 | 3PM to 4PM | 72 | 59.3 | 51.1 | 57 | 26.18 | 0.0728 | 0.38 | 13.85 | 0
October | 1 | 4PM to 5PM | 70 | 57.1 | 48 | 50.8 | 24.72 | 0.0731 | 0.34 | 13.78 | 0
October | 1 | 5PM to 6PM | 64 | 56.4 | 51.1 | 57 | 24.25 | 0.0739 | 0.38 | 13.65 | 0
October | 1 | 6PM to 7PM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
October | 1 | 7PM to 8PM | 57.9 | 54.4 | 52 | 59 | 23.06 | 0.0747 | 0.39 | 13.49 | 0
October | 1 | 8PM to 9PM | 55.9 | 53.1 | 51.1 | 57 | 22.27 | 0.075 | 0.38 | 13.44 | 0
October | 1 | 9PM to 10PM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
October | 1 | 10PM to 11PM | 59 | 53.8 | 50 | 54.7 | 22.67 | 0.0746 | 0.36 | 13.51 | 0
October | 1 | 11PM to 12AM | 55.9 | 53.1 | 51.1 | 57 | 22.27 | 0.075 | 0.38 | 13.44 | 0
October | 2 | 12AM to 1AM | 57 | 53.6 | 51.1 | 57 | 22.54 | 0.0749 | 0.38 | 13.46 | 0
October | 2 | 1AM to 2AM | 57 | 53.6 | 51.1 | 57 | 22.54 | 0.0749 | 0.38 | 13.46 | 0
October | 2 | 2AM to 3AM | 55.9 | 53.1 | 51.1 | 57 | 22.27 | 0.075 | 0.38 | 13.44 | 0
October | 2 | 3AM to 4AM | 53.1 | 51.9 | 51.1 | 57 | 21.57 | 0.0755 | 0.38 | 13.36 | 0
October | 2 | 4AM to 5AM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
October | 2 | 5AM to 6AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
October | 2 | 6AM to 7AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
October | 2 | 7AM to 8AM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
October | 2 | 8AM to 9AM | 64 | 57.4 | 53.1 | 61.4 | 24.93 | 0.0738 | 0.41 | 13.66 | 0
October | 2 | 9AM to 10AM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
October | 2 | 10AM to 11AM | 71.1 | 60 | 53.1 | 61.4 | 26.64 | 0.0729 | 0.41 | 13.84 | 0
October | 2 | 11AM to 12PM | 72 | 59.8 | 52 | 59 | 26.48 | 0.0728 | 0.39 | 13.86 | 0
October | 2 | 12PM to 1PM | 75 | 61.9 | 54 | 63.5 | 27.93 | 0.0723 | 0.42 | 13.95 | 0
October | 2 | 1PM to 2PM | 75.9 | 61.7 | 53.1 | 61.4 | 27.83 | 0.0722 | 0.41 | 13.97 | 0
October | 2 | 2PM to 3PM | 77 | 62.1 | 53.1 | 61.4 | 28.09 | 0.0721 | 0.41 | 14 | 0
October | 2 | 3PM to 4PM | 78.1 | 62.5 | 53.1 | 61.4 | 28.35 | 0.0719 | 0.41 | 14.03 | 0
October | 2 | 4PM to 5PM | 77 | 62.5 | 54 | 63.5 | 28.42 | 0.072 | 0.42 | 14.01 | 0
October | 2 | 5PM to 6PM | 73.9 | 61 | 53.1 | 61.4 | 27.34 | 0.0725 | 0.41 | 13.92 | 0
October | 2 | 6PM to 7PM | 72 | 60.8 | 54 | 63.5 | 27.19 | 0.0727 | 0.42 | 13.87 | 0
October | 2 | 7PM to 8PM | 71.1 | 61 | 55 | 66.1 | 27.37 | 0.0728 | 0.44 | 13.86 | 0
October | 2 | 8PM to 9PM | 70 | 61.1 | 55.9 | 68.3 | 27.45 | 0.073 | 0.45 | 13.84 | 0
October | 2 | 9PM to 10PM | 70 | 61.1 | 55.9 | 68.3 | 27.45 | 0.073 | 0.45 | 13.84 | 0
October | 2 | 10PM to 11PM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
October | 2 | 11PM to 12AM | 63 | 61.7 | 61 | 82.1 | 27.89 | 0.0739 | 0.54 | 13.7 | 0
October | 3 | 12AM to 1AM | 62.1 | 61.4 | 61 | 82.1 | 27.66 | 0.074 | 0.54 | 13.67 | 0
October | 3 | 1AM to 2AM | 61 | 60.4 | 60.1 | 79.5 | 26.99 | 0.0742 | 0.52 | 13.64 | 0
October | 3 | 2AM to 3AM | 60.1 | 60.1 | 60.1 | 79.5 | 26.77 | 0.0743 | 0.52 | 13.61 | 0
October | 3 | 3AM to 4AM | 60.1 | 60.1 | 60.1 | 79.5 | 26.77 | 0.0743 | 0.52 | 13.61 | 0
October | 3 | 4AM to 5AM | 60.1 | 60.1 | 60.1 | 79.5 | 26.77 | 0.0743 | 0.52 | 13.61 | 0
October | 3 | 5AM to 6AM | 60.1 | 59.4 | 59 | 76.4 | 26.29 | 0.0743 | 0.5 | 13.6 | 0
October | 3 | 6AM to 7AM | 60.1 | 58.7 | 57.9 | 73.5 | 25.84 | 0.0743 | 0.48 | 13.6 | 0
October | 3 | 7AM to 8AM | 60.1 | 58.2 | 57 | 71.1 | 25.47 | 0.0743 | 0.47 | 13.59 | 0
October | 3 | 8AM to 9AM | 60.1 | 57.5 | 55.9 | 68.3 | 25.04 | 0.0744 | 0.45 | 13.58 | 0
October | 3 | 9AM to 10AM | 61 | 57.3 | 55 | 66.1 | 24.91 | 0.0742 | 0.44 | 13.6 | 0
October | 3 | 10AM to 11AM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
October | 3 | 11AM to 12PM | 62.1 | 56.6 | 53.1 | 61.4 | 24.44 | 0.0741 | 0.41 | 13.61 | 0
October | 3 | 12PM to 1PM | 69.1 | 55.9 | 46 | 47.1 | 23.93 | 0.0732 | 0.31 | 13.75 | 0
October | 3 | 1PM to 2PM | 71.1 | 55 | 42.1 | 40.4 | 23.37 | 0.073 | 0.27 | 13.78 | 0
October | 3 | 2PM to 3PM | 71.1 | 54.6 | 41 | 38.8 | 23.11 | 0.073 | 0.26 | 13.77 | 0
October | 3 | 3PM to 4PM | 69.1 | 55 | 44.1 | 43.6 | 23.39 | 0.0732 | 0.29 | 13.74 | 0
October | 3 | 4PM to 5PM | 64.9 | 53.4 | 44.1 | 43.6 | 22.38 | 0.0738 | 0.29 | 13.63 | 0
October | 3 | 5PM to 6PM | 62.1 | 53.1 | 46 | 47.1 | 22.22 | 0.0742 | 0.31 | 13.57 | 0
October | 3 | 6PM to 7PM | 60.1 | 52.3 | 46 | 47.1 | 21.74 | 0.0745 | 0.31 | 13.51 | 0
October | 3 | 7PM to 8PM | 57 | 51.4 | 46.9 | 48.8 | 21.25 | 0.0749 | 0.32 | 13.44 | 0
October | 3 | 8PM to 9PM | 57 | 51.4 | 46.9 | 48.8 | 21.25 | 0.0749 | 0.32 | 13.44 | 0
October | 3 | 9PM to 10PM | 55.9 | 51.5 | 48 | 50.8 | 21.31 | 0.0751 | 0.34 | 13.42 | 0
October | 3 | 10PM to 11PM | 55.9 | 51.5 | 48 | 50.8 | 21.31 | 0.0751 | 0.34 | 13.42 | 0
October | 3 | 11PM to 12AM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
October | 4 | 12AM to 1AM | 52 | 49.8 | 48 | 50.8 | 20.34 | 0.0756 | 0.34 | 13.31 | 0
October | 4 | 1AM to 2AM | 52 | 49.8 | 48 | 50.8 | 20.34 | 0.0756 | 0.34 | 13.31 | 0
October | 4 | 2AM to 3AM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
October | 4 | 3AM to 4AM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
October | 4 | 4AM to 5AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
October | 4 | 5AM to 6AM | 46.9 | 46.5 | 46 | 47.1 | 18.55 | 0.0764 | 0.31 | 13.17 | 1
October | 4 | 6AM to 7AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
October | 4 | 7AM to 8AM | 55 | 50.6 | 46.9 | 48.8 | 20.77 | 0.0752 | 0.32 | 13.39 | 0
October | 4 | 8AM to 9AM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
October | 4 | 9AM to 10AM | 63 | 53 | 45 | 45.2 | 22.14 | 0.0741 | 0.3 | 13.58 | 0
October | 4 | 10AM to 11AM | 68 | 55.9 | 46.9 | 48.8 | 23.92 | 0.0734 | 0.32 | 13.73 | 0
October | 4 | 11AM to 12PM | 70 | 57.1 | 48 | 50.8 | 24.72 | 0.0731 | 0.34 | 13.78 | 0
October | 4 | 12PM to 1PM | 73.9 | 56.9 | 44.1 | 43.6 | 24.57 | 0.0726 | 0.29 | 13.86 | 0
October | 4 | 1PM to 2PM | 73.9 | 56.5 | 43 | 41.9 | 24.29 | 0.0726 | 0.28 | 13.86 | 0
October | 4 | 2PM to 3PM | 75 | 56.6 | 42.1 | 40.4 | 24.33 | 0.0725 | 0.27 | 13.88 | 0
October | 4 | 3PM to 4PM | 75.9 | 56.9 | 42.1 | 40.4 | 24.54 | 0.0723 | 0.27 | 13.91 | 0
October | 4 | 4PM to 5PM | 73 | 56.2 | 43 | 41.9 | 24.07 | 0.0727 | 0.28 | 13.83 | 0
October | 4 | 5PM to 6PM | 71.1 | 55.8 | 44.1 | 43.6 | 23.87 | 0.073 | 0.29 | 13.79 | 0
October | 4 | 6PM to 7PM | 69.1 | 55 | 44.1 | 43.6 | 23.39 | 0.0732 | 0.29 | 13.74 | 0
October | 4 | 7PM to 8PM | 68 | 54.6 | 44.1 | 43.6 | 23.13 | 0.0734 | 0.29 | 13.71 | 0
October | 4 | 8PM to 9PM | 66 | 54.2 | 45 | 45.2 | 22.89 | 0.0737 | 0.3 | 13.66 | 0
October | 4 | 9PM to 10PM | 66 | 53.4 | 43 | 41.9 | 22.37 | 0.0737 | 0.28 | 13.65 | 0
October | 4 | 10PM to 11PM | 66.9 | 53.7 | 43 | 41.9 | 22.59 | 0.0736 | 0.28 | 13.68 | 0
October | 4 | 11PM to 12AM | 66.9 | 53.7 | 43 | 41.9 | 22.59 | 0.0736 | 0.28 | 13.68 | 0
October | 5 | 12AM to 1AM | 64 | 53 | 44.1 | 43.6 | 22.17 | 0.074 | 0.29 | 13.61 | 0
October | 5 | 1AM to 2AM | 57.9 | 55 | 53.1 | 61.4 | 23.44 | 0.0747 | 0.41 | 13.5 | 0
October | 5 | 2AM to 3AM | 57.9 | 54.4 | 52 | 59 | 23.06 | 0.0747 | 0.39 | 13.49 | 0
October | 5 | 3AM to 4AM | 57.9 | 54.4 | 52 | 59 | 23.06 | 0.0747 | 0.39 | 13.49 | 0
October | 5 | 4AM to 5AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
October | 5 | 5AM to 6AM | 55 | 53.3 | 52 | 59 | 22.36 | 0.0751 | 0.39 | 13.42 | 0
October | 5 | 6AM to 7AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
October | 5 | 7AM to 8AM | 57 | 54.7 | 53.1 | 61.4 | 23.22 | 0.0748 | 0.41 | 13.48 | 0
October | 5 | 8AM to 9AM | 61 | 54.6 | 50 | 54.7 | 23.15 | 0.0743 | 0.36 | 13.56 | 0
October | 5 | 9AM to 10AM | 63 | 53.9 | 46.9 | 48.8 | 22.7 | 0.0741 | 0.32 | 13.59 | 0
October | 5 | 10AM to 11AM | 64 | 52.5 | 43 | 41.9 | 21.89 | 0.074 | 0.28 | 13.6 | 0
October | 5 | 11AM to 12PM | 64 | 52.2 | 42.1 | 40.4 | 21.66 | 0.074 | 0.27 | 13.6 | 0
October | 5 | 12PM to 1PM | 64 | 53 | 44.1 | 43.6 | 22.17 | 0.074 | 0.29 | 13.61 | 0
October | 5 | 1PM to 2PM | 62.1 | 51.3 | 42.1 | 40.4 | 21.18 | 0.0743 | 0.27 | 13.55 | 0
October | 5 | 2PM to 3PM | 59 | 49.5 | 41 | 38.8 | 20.18 | 0.0747 | 0.26 | 13.46 | 0
October | 5 | 3PM to 4PM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
October | 5 | 4PM to 5PM | 57 | 49.1 | 42.1 | 40.4 | 19.96 | 0.075 | 0.27 | 13.41 | 0
October | 5 | 5PM to 6PM | 55.9 | 48.7 | 42.1 | 40.4 | 19.7 | 0.0751 | 0.27 | 13.39 | 0
October | 5 | 6PM to 7PM | 54 | 47.8 | 42.1 | 40.4 | 19.22 | 0.0754 | 0.27 | 13.33 | 0
October | 5 | 7PM to 8PM | 53.1 | 47.3 | 42.1 | 40.4 | 19 | 0.0756 | 0.27 | 13.31 | 0
October | 5 | 8PM to 9PM | 52 | 46.9 | 42.1 | 40.4 | 18.74 | 0.0757 | 0.27 | 13.28 | 0
October | 5 | 9PM to 10PM | 51.1 | 46.9 | 43 | 41.9 | 18.74 | 0.0758 | 0.28 | 13.26 | 1
October | 5 | 10PM to 11PM | 50 | 46.9 | 44.1 | 43.6 | 18.76 | 0.076 | 0.29 | 13.24 | 1
October | 5 | 11PM to 12AM | 48 | 46 | 44.1 | 43.6 | 18.28 | 0.0763 | 0.29 | 13.19 | 1
October | 6 | 12AM to 1AM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
October | 6 | 1AM to 2AM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
October | 6 | 2AM to 3AM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
October | 6 | 3AM to 4AM | 45 | 44.5 | 44.1 | 43.6 | 17.53 | 0.0767 | 0.29 | 13.11 | 1
October | 6 | 4AM to 5AM | 44.1 | 43.5 | 43 | 41.9 | 17.04 | 0.0769 | 0.28 | 13.08 | 1
October | 6 | 5AM to 6AM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
October | 6 | 6AM to 7AM | 44.1 | 43.5 | 43 | 41.9 | 17.04 | 0.0769 | 0.28 | 13.08 | 1
October | 6 | 7AM to 8AM | 46.9 | 44.9 | 43 | 41.9 | 17.74 | 0.0765 | 0.28 | 13.16 | 1
October | 6 | 8AM to 9AM | 51.1 | 46.9 | 43 | 41.9 | 18.74 | 0.0758 | 0.28 | 13.26 | 1
October | 6 | 9AM to 10AM | 55.9 | 49.1 | 43 | 41.9 | 19.92 | 0.0751 | 0.28 | 13.39 | 0
October | 6 | 10AM to 11AM | 55.9 | 49.1 | 43 | 41.9 | 19.92 | 0.0751 | 0.28 | 13.39 | 0
October | 6 | 11AM to 12PM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
October | 6 | 12PM to 1PM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
October | 6 | 1PM to 2PM | 55.9 | 48.2 | 41 | 38.8 | 19.44 | 0.0751 | 0.26 | 13.38 | 0
October | 6 | 2PM to 3PM | 57 | 48.7 | 41 | 38.8 | 19.7 | 0.075 | 0.26 | 13.41 | 0
October | 6 | 3PM to 4PM | 55.9 | 47.7 | 39.9 | 37.2 | 19.19 | 0.0752 | 0.25 | 13.38 | 0
October | 6 | 4PM to 5PM | 55 | 47.3 | 39.9 | 37.2 | 18.97 | 0.0753 | 0.25 | 13.35 | 0
October | 6 | 5PM to 6PM | 53.1 | 46.4 | 39.9 | 37.2 | 18.49 | 0.0756 | 0.25 | 13.3 | 0
October | 6 | 6PM to 7PM | 50 | 45.4 | 41 | 38.8 | 18 | 0.076 | 0.26 | 13.23 | 1
October | 6 | 7PM to 8PM | 48.9 | 45.4 | 42.1 | 40.4 | 18 | 0.0762 | 0.27 | 13.2 | 1
October | 6 | 8PM to 9PM | 48.9 | 45.4 | 42.1 | 40.4 | 18 | 0.0762 | 0.27 | 13.2 | 1
October | 6 | 9PM to 10PM | 48 | 44.5 | 41 | 38.8 | 17.52 | 0.0763 | 0.26 | 13.18 | 1
October | 6 | 10PM to 11PM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
October | 6 | 11PM to 12AM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
October | 7 | 12AM to 1AM | 41 | 41 | 41 | 38.8 | 15.82 | 0.0774 | 0.26 | 12.99 | 1
October | 7 | 1AM to 2AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
October | 7 | 2AM to 3AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
October | 7 | 3AM to 4AM | 41 | 41 | 41 | 38.8 | 15.82 | 0.0774 | 0.26 | 12.99 | 1
October | 7 | 4AM to 5AM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
October | 7 | 5AM to 6AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
October | 7 | 6AM to 7AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
October | 7 | 7AM to 8AM | 46 | 44 | 42.1 | 40.4 | 17.3 | 0.0766 | 0.27 | 13.13 | 1
October | 7 | 8AM to 9AM | 48.9 | 45.4 | 42.1 | 40.4 | 18 | 0.0762 | 0.27 | 13.2 | 1
October | 7 | 9AM to 10AM | 48.9 | 45.4 | 42.1 | 40.4 | 18 | 0.0762 | 0.27 | 13.2 | 1
October | 7 | 10AM to 11AM | 55 | 47.8 | 41 | 38.8 | 19.22 | 0.0753 | 0.26 | 13.36 | 0
October | 7 | 11AM to 12PM | 55 | 45.7 | 36 | 31.8 | 18.14 | 0.0753 | 0.21 | 13.34 | 0
October | 7 | 12PM to 1PM | 55 | 45.7 | 36 | 31.8 | 18.14 | 0.0753 | 0.21 | 13.34 | 0
October | 7 | 1PM to 2PM | 55.9 | 46.6 | 37 | 33.2 | 18.57 | 0.0752 | 0.22 | 13.36 | 0
October | 7 | 2PM to 3PM | 55.9 | 46.6 | 37 | 33.2 | 18.57 | 0.0752 | 0.22 | 13.36 | 0
October | 7 | 3PM to 4PM | 55 | 46.5 | 37.9 | 34.4 | 18.54 | 0.0753 | 0.23 | 13.34 | 0
October | 7 | 4PM to 5PM | 54 | 45.6 | 37 | 33.2 | 18.09 | 0.0755 | 0.22 | 13.31 | 0
October | 7 | 5PM to 6PM | 51.1 | 44.6 | 37.9 | 34.4 | 17.58 | 0.0759 | 0.23 | 13.24 | 1
October | 7 | 6PM to 7PM | 48 | 43.6 | 39 | 35.9 | 17.07 | 0.0763 | 0.24 | 13.17 | 1
October | 7 | 7PM to 8PM | 46 | 42.6 | 39 | 35.9 | 16.59 | 0.0766 | 0.24 | 13.12 | 1
October | 7 | 8PM to 9PM | 45 | 42.1 | 39 | 35.9 | 16.33 | 0.0768 | 0.24 | 13.09 | 1
October | 7 | 9PM to 10PM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
October | 7 | 10PM to 11PM | 39.9 | 39.5 | 39 | 35.9 | 15.11 | 0.0776 | 0.24 | 12.96 | 1
October | 7 | 11PM to 12AM | 39 | 39 | 39 | 35.9 | 14.89 | 0.0777 | 0.24 | 12.93 | 1
October | 8 | 12AM to 1AM | 39 | 39 | 39 | 35.9 | 14.89 | 0.0777 | 0.24 | 12.93 | 1
October | 8 | 1AM to 2AM | 37.9 | 37.9 | 37.9 | 34.4 | 14.4 | 0.0779 | 0.23 | 12.9 | 1
October | 8 | 2AM to 3AM | 37.9 | 37.9 | 37.9 | 34.4 | 14.4 | 0.0779 | 0.23 | 12.9 | 1
October | 8 | 3AM to 4AM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
October | 8 | 4AM to 5AM | 37 | 37 | 37 | 33.2 | 14 | 0.078 | 0.22 | 12.87 | 1
October | 8 | 5AM to 6AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
October | 8 | 6AM to 7AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
October | 8 | 7AM to 8AM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
October | 8 | 8AM to 9AM | 51.1 | 45.9 | 41 | 38.8 | 18.26 | 0.0759 | 0.26 | 13.26 | 1
October | 8 | 9AM to 10AM | 54 | 46 | 37.9 | 34.4 | 18.28 | 0.0755 | 0.23 | 13.32 | 0
October | 8 | 10AM to 11AM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
October | 8 | 11AM to 12PM | 57.9 | 48.2 | 39 | 35.9 | 19.47 | 0.0749 | 0.24 | 13.42 | 0
October | 8 | 12PM to 1PM | 60.1 | 49.2 | 39 | 35.9 | 19.99 | 0.0746 | 0.24 | 13.48 | 0
October | 8 | 1PM to 2PM | 61 | 49.6 | 39 | 35.9 | 20.21 | 0.0744 | 0.24 | 13.5 | 0
October | 8 | 2PM to 3PM | 63 | 50.1 | 37.9 | 34.4 | 20.46 | 0.0742 | 0.23 | 13.55 | 0
October | 8 | 3PM to 4PM | 63 | 50.5 | 39 | 35.9 | 20.69 | 0.0742 | 0.24 | 13.55 | 0
October | 8 | 4PM to 5PM | 62.1 | 49.7 | 37.9 | 34.4 | 20.24 | 0.0743 | 0.23 | 13.53 | 0
October | 8 | 5PM to 6PM | 55 | 47.3 | 39.9 | 37.2 | 18.97 | 0.0753 | 0.25 | 13.35 | 0
October | 8 | 6PM to 7PM | 50 | 45.4 | 41 | 38.8 | 18 | 0.076 | 0.26 | 13.23 | 1
October | 8 | 7PM to 8PM | 50 | 45.4 | 41 | 38.8 | 18 | 0.076 | 0.26 | 13.23 | 1
October | 8 | 8PM to 9PM | 54 | 46.8 | 39.9 | 37.2 | 18.71 | 0.0754 | 0.25 | 13.33 | 0
October | 8 | 9PM to 10PM | 55 | 47.8 | 41 | 38.8 | 19.22 | 0.0753 | 0.26 | 13.36 | 0
October | 8 | 10PM to 11PM | 53.1 | 46.9 | 41 | 38.8 | 18.74 | 0.0756 | 0.26 | 13.31 | 0
October | 8 | 11PM to 12AM | 53.1 | 46.9 | 41 | 38.8 | 18.74 | 0.0756 | 0.26 | 13.31 | 0
October | 9 | 12AM to 1AM | 51.1 | 46.4 | 42.1 | 40.4 | 18.52 | 0.0758 | 0.27 | 13.26 | 1
October | 9 | 1AM to 2AM | 51.1 | 45.9 | 41 | 38.8 | 18.26 | 0.0759 | 0.26 | 13.26 | 1
October | 9 | 2AM to 3AM | 51.1 | 45.9 | 41 | 38.8 | 18.26 | 0.0759 | 0.26 | 13.26 | 1
October | 9 | 3AM to 4AM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
October | 9 | 4AM to 5AM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
October | 9 | 5AM to 6AM | 48.9 | 45.8 | 43 | 41.9 | 18.22 | 0.0762 | 0.28 | 13.21 | 1
October | 9 | 6AM to 7AM | 51.1 | 46.9 | 43 | 41.9 | 18.74 | 0.0758 | 0.28 | 13.26 | 1
October | 9 | 7AM to 8AM | 55.9 | 50.5 | 46 | 47.1 | 20.73 | 0.0751 | 0.31 | 13.41 | 0
October | 9 | 8AM to 9AM | 57.9 | 51.8 | 46.9 | 48.8 | 21.47 | 0.0748 | 0.32 | 13.46 | 0
October | 9 | 9AM to 10AM | 68 | 57.9 | 51.1 | 57 | 25.21 | 0.0733 | 0.38 | 13.75 | 0
October | 9 | 10AM to 11AM | 71.1 | 59 | 51.1 | 57 | 25.96 | 0.0729 | 0.38 | 13.83 | 0
October | 9 | 11AM to 12PM | 68 | 57.9 | 51.1 | 57 | 25.21 | 0.0733 | 0.38 | 13.75 | 0
October | 9 | 12PM to 1PM | 64.9 | 56.2 | 50 | 54.7 | 24.11 | 0.0738 | 0.36 | 13.66 | 0
October | 9 | 1PM to 2PM | 66.9 | 56.9 | 50 | 54.7 | 24.59 | 0.0735 | 0.36 | 13.72 | 0
October | 9 | 2PM to 3PM | 68 | 57.9 | 51.1 | 57 | 25.21 | 0.0733 | 0.38 | 13.75 | 0
October | 9 | 3PM to 4PM | 69.1 | 57.7 | 50 | 54.7 | 25.12 | 0.0732 | 0.36 | 13.77 | 0
October | 9 | 4PM to 5PM | 66.9 | 56.9 | 50 | 54.7 | 24.59 | 0.0735 | 0.36 | 13.72 | 0
October | 9 | 5PM to 6PM | 64.9 | 56.2 | 50 | 54.7 | 24.11 | 0.0738 | 0.36 | 13.66 | 0
October | 9 | 6PM to 7PM | 63 | 54.8 | 48.9 | 52.6 | 23.29 | 0.074 | 0.35 | 13.61 | 0
October | 9 | 7PM to 8PM | 61 | 54 | 48.9 | 52.6 | 22.81 | 0.0743 | 0.35 | 13.55 | 0
October | 9 | 8PM to 9PM | 60.1 | 53.7 | 48.9 | 52.6 | 22.59 | 0.0745 | 0.35 | 13.53 | 0
October | 9 | 9PM to 10PM | 57 | 53.6 | 51.1 | 57 | 22.54 | 0.0749 | 0.38 | 13.46 | 0
October | 9 | 10PM to 11PM | 55.9 | 53.6 | 52 | 59 | 22.58 | 0.075 | 0.39 | 13.44 | 0
October | 9 | 11PM to 12AM | 55.9 | 53.6 | 52 | 59 | 22.58 | 0.075 | 0.39 | 13.44 | 0
October | 10 | 12AM to 1AM | 55 | 53.3 | 52 | 59 | 22.36 | 0.0751 | 0.39 | 13.42 | 0
October | 10 | 1AM to 2AM | 55 | 53.3 | 52 | 59 | 22.36 | 0.0751 | 0.39 | 13.42 | 0
October | 10 | 2AM to 3AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
October | 10 | 3AM to 4AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
October | 10 | 4AM to 5AM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
October | 10 | 5AM to 6AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
October | 10 | 6AM to 7AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
October | 10 | 7AM to 8AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
October | 10 | 8AM to 9AM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
October | 10 | 9AM to 10AM | 55.9 | 53.1 | 51.1 | 57 | 22.27 | 0.075 | 0.38 | 13.44 | 0
October | 10 | 10AM to 11AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
October | 10 | 11AM to 12PM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
October | 10 | 12PM to 1PM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
October | 10 | 1PM to 2PM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
October | 10 | 2PM to 3PM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
October | 10 | 3PM to 4PM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
October | 10 | 4PM to 5PM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
October | 10 | 5PM to 6PM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
October | 10 | 6PM to 7PM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
October | 10 | 7PM to 8PM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
October | 10 | 8PM to 9PM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
October | 10 | 9PM to 10PM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
October | 10 | 10PM to 11PM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
October | 10 | 11PM to 12AM | 55 | 54.4 | 54 | 63.5 | 23.06 | 0.0751 | 0.42 | 13.43 | 0
October | 11 | 12AM to 1AM | 54 | 53.4 | 53.1 | 61.4 | 22.47 | 0.0753 | 0.41 | 13.4 | 0
October | 11 | 1AM to 2AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 11 | 2AM to 3AM | 48 | 48 | 48 | 50.8 | 19.38 | 0.0762 | 0.34 | 13.21 | 1
October | 11 | 3AM to 4AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 11 | 4AM to 5AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 11 | 5AM to 6AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 11 | 6AM to 7AM | 53.1 | 53.1 | 53.1 | 61.4 | 22.25 | 0.0754 | 0.41 | 13.38 | 0
October | 11 | 7AM to 8AM | 55 | 54.4 | 54 | 63.5 | 23.06 | 0.0751 | 0.42 | 13.43 | 0
October | 11 | 8AM to 9AM | 57 | 55.8 | 55 | 66.1 | 23.94 | 0.0748 | 0.44 | 13.49 | 0
October | 11 | 9AM to 10AM | 60.1 | 57 | 55 | 66.1 | 24.69 | 0.0744 | 0.44 | 13.57 | 0
October | 11 | 10AM to 11AM | 62.1 | 58.3 | 55.9 | 68.3 | 25.52 | 0.0741 | 0.45 | 13.63 | 0
October | 11 | 11AM to 12PM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
October | 11 | 12PM to 1PM | 66 | 60.9 | 57.9 | 73.5 | 27.29 | 0.0735 | 0.48 | 13.75 | 0
October | 11 | 1PM to 2PM | 68 | 61.6 | 57.9 | 73.5 | 27.77 | 0.0732 | 0.48 | 13.8 | 0
October | 11 | 2PM to 3PM | 70 | 61.7 | 57 | 71.1 | 27.89 | 0.073 | 0.47 | 13.85 | 0
October | 11 | 3PM to 4PM | 71.1 | 62.6 | 57.9 | 73.5 | 28.52 | 0.0728 | 0.48 | 13.88 | 0
October | 11 | 4PM to 5PM | 69.1 | 61.9 | 57.9 | 73.5 | 28.04 | 0.0731 | 0.48 | 13.83 | 0
October | 11 | 5PM to 6PM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
October | 11 | 6PM to 7PM | 62.1 | 59.5 | 57.9 | 73.5 | 26.32 | 0.074 | 0.48 | 13.65 | 0
October | 11 | 7PM to 8PM | 64.9 | 61.8 | 60.1 | 79.5 | 27.96 | 0.0736 | 0.52 | 13.74 | 0
October | 11 | 8PM to 9PM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
October | 11 | 9PM to 10PM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
October | 11 | 10PM to 11PM | 64 | 61.5 | 60.1 | 79.5 | 27.74 | 0.0737 | 0.52 | 13.72 | 0
October | 11 | 11PM to 12AM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
October | 12 | 12AM to 1AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
October | 12 | 1AM to 2AM | 66 | 63.4 | 62.1 | 85.4 | 29.14 | 0.0734 | 0.56 | 13.79 | 0
October | 12 | 2AM to 3AM | 63 | 61.7 | 61 | 82.1 | 27.89 | 0.0739 | 0.54 | 13.7 | 0
October | 12 | 3AM to 4AM | 62.1 | 61.4 | 61 | 82.1 | 27.66 | 0.074 | 0.54 | 13.67 | 0
October | 12 | 4AM to 5AM | 62.1 | 61.4 | 61 | 82.1 | 27.66 | 0.074 | 0.54 | 13.67 | 0
October | 12 | 5AM to 6AM | 63 | 61.7 | 61 | 82.1 | 27.89 | 0.0739 | 0.54 | 13.7 | 0
October | 12 | 6AM to 7AM | 63 | 61.7 | 61 | 82.1 | 27.89 | 0.0739 | 0.54 | 13.7 | 0
October | 12 | 7AM to 8AM | 64.9 | 63 | 62.1 | 85.4 | 28.88 | 0.0736 | 0.56 | 13.76 | 0
October | 12 | 8AM to 9AM | 68 | 65.3 | 64 | 91.7 | 30.61 | 0.0731 | 0.6 | 13.86 | 0
October | 12 | 9AM to 10AM | 70 | 66 | 64 | 91.7 | 31.1 | 0.0728 | 0.6 | 13.91 | 0
October | 12 | 10AM to 11AM | 73 | 67.5 | 64.9 | 94.6 | 32.32 | 0.0724 | 0.62 | 14 | 0
October | 12 | 11AM to 12PM | 70 | 66.6 | 64.9 | 94.6 | 31.56 | 0.0728 | 0.62 | 13.92 | 0
October | 12 | 12PM to 1PM | 68 | 64.6 | 63 | 88.2 | 30.07 | 0.0731 | 0.58 | 13.85 | 0
October | 12 | 1PM to 2PM | 68 | 64.6 | 63 | 88.2 | 30.07 | 0.0731 | 0.58 | 13.85 | 0
October | 12 | 2PM to 3PM | 64 | 62.7 | 62.1 | 85.4 | 28.66 | 0.0737 | 0.56 | 13.74 | 0
October | 12 | 3PM to 4PM | 63 | 58.6 | 55.9 | 68.3 | 25.74 | 0.074 | 0.45 | 13.65 | 0
October | 12 | 4PM to 5PM | 60.1 | 56.4 | 54 | 63.5 | 24.29 | 0.0744 | 0.42 | 13.56 | 0
October | 12 | 5PM to 6PM | 59 | 56.6 | 55 | 66.1 | 24.43 | 0.0745 | 0.44 | 13.54 | 0
October | 12 | 6PM to 7PM | 57.9 | 53.9 | 51.1 | 57 | 22.75 | 0.0747 | 0.38 | 13.49 | 0
October | 12 | 7PM to 8PM | 57 | 52.4 | 48.9 | 52.6 | 21.84 | 0.0749 | 0.35 | 13.45 | 0
October | 12 | 8PM to 9PM | 52 | 51.5 | 51.1 | 57 | 21.31 | 0.0756 | 0.38 | 13.33 | 0
October | 12 | 9PM to 10PM | 51.1 | 51.1 | 51.1 | 57 | 21.09 | 0.0757 | 0.38 | 13.31 | 1
October | 12 | 10PM to 11PM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
October | 12 | 11PM to 12AM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
October | 13 | 12AM to 1AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 13 | 1AM to 2AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 13 | 2AM to 3AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 13 | 3AM to 4AM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
October | 13 | 4AM to 5AM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
October | 13 | 5AM to 6AM | 48 | 48 | 48 | 50.8 | 19.38 | 0.0762 | 0.34 | 13.21 | 1
October | 13 | 6AM to 7AM | 48 | 48 | 48 | 50.8 | 19.38 | 0.0762 | 0.34 | 13.21 | 1
October | 13 | 7AM to 8AM | 50 | 49.4 | 48.9 | 52.6 | 20.14 | 0.0759 | 0.35 | 13.27 | 1
October | 13 | 8AM to 9AM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
October | 13 | 9AM to 10AM | 53.1 | 51.9 | 51.1 | 57 | 21.57 | 0.0755 | 0.38 | 13.36 | 0
October | 13 | 10AM to 11AM | 57 | 53.6 | 51.1 | 57 | 22.54 | 0.0749 | 0.38 | 13.46 | 0
October | 13 | 11AM to 12PM | 61 | 52.6 | 46 | 47.1 | 21.96 | 0.0744 | 0.31 | 13.54 | 0
October | 13 | 12PM to 1PM | 61 | 50.4 | 41 | 38.8 | 20.66 | 0.0744 | 0.26 | 13.51 | 0
October | 13 | 1PM to 2PM | 61 | 49.6 | 39 | 35.9 | 20.21 | 0.0744 | 0.24 | 13.5 | 0
October | 13 | 2PM to 3PM | 60.1 | 50 | 41 | 38.8 | 20.44 | 0.0745 | 0.26 | 13.49 | 0
October | 13 | 3PM to 4PM | 52 | 48.8 | 46 | 47.1 | 19.77 | 0.0757 | 0.31 | 13.3 | 0
October | 13 | 4PM to 5PM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
October | 13 | 5PM to 6PM | 48.9 | 48.4 | 48 | 50.8 | 19.6 | 0.0761 | 0.34 | 13.24 | 1
October | 13 | 6PM to 7PM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
October | 13 | 7PM to 8PM | 46.9 | 45.9 | 45 | 45.2 | 18.25 | 0.0764 | 0.3 | 13.17 | 1
October | 13 | 8PM to 9PM | 45 | 45 | 45 | 45.2 | 17.77 | 0.0767 | 0.3 | 13.12 | 1
October | 13 | 9PM to 10PM | 44.1 | 43.5 | 43 | 41.9 | 17.04 | 0.0769 | 0.28 | 13.08 | 1
October | 13 | 10PM to 11PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
October | 13 | 11PM to 12AM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
October | 14 | 12AM to 1AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
October | 14 | 1AM to 2AM | 39 | 39 | 39 | 35.9 | 14.89 | 0.0777 | 0.24 | 12.93 | 1
October | 14 | 2AM to 3AM | 37.9 | 37.9 | 37.9 | 34.4 | 14.4 | 0.0779 | 0.23 | 12.9 | 1
October | 14 | 3AM to 4AM | 37.9 | 37.9 | 37.9 | 34.4 | 14.4 | 0.0779 | 0.23 | 12.9 | 1
October | 14 | 4AM to 5AM | 37.9 | 37.9 | 37.9 | 34.4 | 14.4 | 0.0779 | 0.23 | 12.9 | 1
October | 14 | 5AM to 6AM | 39 | 39 | 39 | 35.9 | 14.89 | 0.0777 | 0.24 | 12.93 | 1
October | 14 | 6AM to 7AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
October | 14 | 7AM to 8AM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
October | 14 | 8AM to 9AM | 46 | 43.5 | 41 | 38.8 | 17.04 | 0.0766 | 0.26 | 13.12 | 1
October | 14 | 9AM to 10AM | 48.9 | 45.4 | 42.1 | 40.4 | 18 | 0.0762 | 0.27 | 13.2 | 1
October | 14 | 10AM to 11AM | 51.1 | 46.4 | 42.1 | 40.4 | 18.52 | 0.0758 | 0.27 | 13.26 | 1
October | 14 | 11AM to 12PM | 51.1 | 45.9 | 41 | 38.8 | 18.26 | 0.0759 | 0.26 | 13.26 | 1
October | 14 | 12PM to 1PM | 54 | 47.3 | 41 | 38.8 | 18.96 | 0.0754 | 0.26 | 13.33 | 0
October | 14 | 1PM to 2PM | 55.9 | 46.9 | 37.9 | 34.4 | 18.76 | 0.0752 | 0.23 | 13.37 | 0
October | 14 | 2PM to 3PM | 54 | 44.2 | 33.1 | 28.3 | 17.34 | 0.0755 | 0.19 | 13.3 | 0
October | 14 | 3PM to 4PM | 53.1 | 44 | 34 | 29.3 | 17.28 | 0.0756 | 0.2 | 13.28 | 0
October | 14 | 4PM to 5PM | 52 | 43.5 | 34 | 29.3 | 17.02 | 0.0758 | 0.2 | 13.25 | 0
October | 14 | 5PM to 6PM | 46 | 40.5 | 34 | 29.3 | 15.58 | 0.0767 | 0.2 | 13.1 | 1
October | 14 | 6PM to 7PM | 44.1 | 39.9 | 35.1 | 30.6 | 15.31 | 0.077 | 0.2 | 13.05 | 1
October | 14 | 7PM to 8PM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
October | 14 | 8PM to 9PM | 41 | 38.7 | 36 | 31.8 | 14.74 | 0.0774 | 0.21 | 12.97 | 1
October | 14 | 9PM to 10PM | 39.9 | 38.6 | 37 | 33.2 | 14.69 | 0.0776 | 0.22 | 12.95 | 1
October | 14 | 10PM to 11PM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
October | 14 | 11PM to 12AM | 39.9 | 38.6 | 37 | 33.2 | 14.69 | 0.0776 | 0.22 | 12.95 | 1
October | 15 | 12AM to 1AM | 39.9 | 37.7 | 35.1 | 30.6 | 14.3 | 0.0776 | 0.2 | 12.94 | 1
October | 15 | 1AM to 2AM | 37.9 | 36.7 | 35.1 | 30.6 | 13.83 | 0.0779 | 0.2 | 12.89 | 1
October | 15 | 2AM to 3AM | 37 | 36.6 | 36 | 31.8 | 13.78 | 0.0781 | 0.21 | 12.87 | 1
October | 15 | 3AM to 4AM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
October | 15 | 4AM to 5AM | 42.1 | 39.7 | 37 | 33.2 | 15.22 | 0.0773 | 0.22 | 13 | 1
October | 15 | 5AM to 6AM | 42.1 | 39.7 | 37 | 33.2 | 15.22 | 0.0773 | 0.22 | 13 | 1
October | 15 | 6AM to 7AM | 44.1 | 40.8 | 37 | 33.2 | 15.69 | 0.077 | 0.22 | 13.06 | 1
October | 15 | 7AM to 8AM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
October | 15 | 8AM to 9AM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
October | 15 | 9AM to 10AM | 48 | 43.1 | 37.9 | 34.4 | 16.84 | 0.0763 | 0.23 | 13.16 | 1
October | 15 | 10AM to 11AM | 51.1 | 45.5 | 39.9 | 37.2 | 18.01 | 0.0759 | 0.25 | 13.25 | 1
October | 15 | 11AM to 12PM | 55.9 | 48.2 | 41 | 38.8 | 19.44 | 0.0751 | 0.26 | 13.38 | 0
October | 15 | 12PM to 1PM | 63 | 50.8 | 39.9 | 37.2 | 20.89 | 0.0741 | 0.25 | 13.56 | 0
October | 15 | 1PM to 2PM | 66.9 | 51.8 | 37.9 | 34.4 | 21.42 | 0.0736 | 0.23 | 13.65 | 0
October | 15 | 2PM to 3PM | 66.9 | 52.2 | 39 | 35.9 | 21.65 | 0.0736 | 0.24 | 13.66 | 0
October | 15 | 3PM to 4PM | 66 | 51.8 | 39 | 35.9 | 21.43 | 0.0737 | 0.24 | 13.63 | 0
October | 15 | 4PM to 5PM | 62.1 | 49.7 | 37.9 | 34.4 | 20.24 | 0.0743 | 0.23 | 13.53 | 0
October | 15 | 5PM to 6PM | 57.9 | 47.5 | 37 | 33.2 | 19.05 | 0.0749 | 0.22 | 13.42 | 0
October | 15 | 6PM to 7PM | 55.9 | 47.3 | 39 | 35.9 | 18.99 | 0.0752 | 0.24 | 13.37 | 0
October | 15 | 7PM to 8PM | 54 | 45.6 | 37 | 33.2 | 18.09 | 0.0755 | 0.22 | 13.31 | 0
October | 15 | 8PM to 9PM | 53.1 | 44.8 | 36 | 31.8 | 17.66 | 0.0756 | 0.21 | 13.29 | 0
October | 15 | 9PM to 10PM | 50 | 43.3 | 36 | 31.8 | 16.92 | 0.0761 | 0.21 | 13.21 | 1
October | 15 | 10PM to 11PM | 46.9 | 41.4 | 35.1 | 30.6 | 16 | 0.0765 | 0.2 | 13.12 | 1
October | 15 | 11PM to 12AM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
October | 16 | 12AM to 1AM | 42.1 | 39.7 | 37 | 33.2 | 15.22 | 0.0773 | 0.22 | 13 | 1
October | 16 | 1AM to 2AM | 39.9 | 38.6 | 37 | 33.2 | 14.69 | 0.0776 | 0.22 | 12.95 | 1
October | 16 | 2AM to 3AM | 39.9 | 38.1 | 36 | 31.8 | 14.48 | 0.0776 | 0.21 | 12.94 | 1
October | 16 | 3AM to 4AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
October | 16 | 4AM to 5AM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
October | 16 | 5AM to 6AM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
October | 16 | 6AM to 7AM | 39 | 39 | 39 | 35.9 | 14.89 | 0.0777 | 0.24 | 12.93 | 1
October | 16 | 7AM to 8AM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
October | 16 | 8AM to 9AM | 46 | 43.5 | 41 | 38.8 | 17.04 | 0.0766 | 0.26 | 13.12 | 1
October | 16 | 9AM to 10AM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
October | 16 | 10AM to 11AM | 50 | 44.6 | 39 | 35.9 | 17.55 | 0.076 | 0.24 | 13.22 | 1
October | 16 | 11AM to 12PM | 52 | 45.9 | 39.9 | 37.2 | 18.23 | 0.0757 | 0.25 | 13.27 | 0
October | 16 | 12PM to 1PM | 53.1 | 46.4 | 39.9 | 37.2 | 18.49 | 0.0756 | 0.25 | 13.3 | 0
October | 16 | 1PM to 2PM | 54 | 46.4 | 39 | 35.9 | 18.51 | 0.0755 | 0.24 | 13.32 | 0
October | 16 | 2PM to 3PM | 55 | 46.9 | 39 | 35.9 | 18.77 | 0.0753 | 0.24 | 13.35 | 0
October | 16 | 3PM to 4PM | 54 | 46.4 | 39 | 35.9 | 18.51 | 0.0755 | 0.24 | 13.32 | 0
October | 16 | 4PM to 5PM | 50 | 44.6 | 39 | 35.9 | 17.55 | 0.076 | 0.24 | 13.22 | 1
October | 16 | 5PM to 6PM | 46.9 | 43.1 | 39 | 35.9 | 16.81 | 0.0765 | 0.24 | 13.14 | 1
October | 16 | 6PM to 7PM | 46 | 42.6 | 39 | 35.9 | 16.59 | 0.0766 | 0.24 | 13.12 | 1
October | 16 | 7PM to 8PM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
October | 16 | 8PM to 9PM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
October | 16 | 9PM to 10PM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
October | 16 | 10PM to 11PM | 42.1 | 40.6 | 39 | 35.9 | 15.63 | 0.0772 | 0.24 | 13.01 | 1
October | 16 | 11PM to 12AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
October | 17 | 12AM to 1AM | 37.9 | 37.9 | 37.9 | 34.4 | 14.4 | 0.0779 | 0.23 | 12.9 | 1
October | 17 | 1AM to 2AM | 37.9 | 37.9 | 37.9 | 34.4 | 14.4 | 0.0779 | 0.23 | 12.9 | 1
October | 17 | 2AM to 3AM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
October | 17 | 3AM to 4AM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
October | 17 | 4AM to 5AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
October | 17 | 5AM to 6AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
October | 17 | 6AM to 7AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
October | 17 | 7AM to 8AM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
October | 17 | 8AM to 9AM | 46.9 | 44.9 | 43 | 41.9 | 17.74 | 0.0765 | 0.28 | 13.16 | 1
October | 17 | 9AM to 10AM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
October | 17 | 10AM to 11AM | 53.1 | 47.3 | 42.1 | 40.4 | 19 | 0.0756 | 0.27 | 13.31 | 0
October | 17 | 11AM to 12PM | 55 | 47.8 | 41 | 38.8 | 19.22 | 0.0753 | 0.26 | 13.36 | 0
October | 17 | 12PM to 1PM | 55.9 | 48.2 | 41 | 38.8 | 19.44 | 0.0751 | 0.26 | 13.38 | 0
October | 17 | 1PM to 2PM | 57.9 | 49.1 | 41 | 38.8 | 19.92 | 0.0749 | 0.26 | 13.43 | 0
October | 17 | 2PM to 3PM | 57.9 | 49.1 | 41 | 38.8 | 19.92 | 0.0749 | 0.26 | 13.43 | 0
October | 17 | 3PM to 4PM | 57.9 | 49.1 | 41 | 38.8 | 19.92 | 0.0749 | 0.26 | 13.43 | 0
October | 17 | 4PM to 5PM | 55.9 | 48.2 | 41 | 38.8 | 19.44 | 0.0751 | 0.26 | 13.38 | 0
October | 17 | 5PM to 6PM | 52 | 46.4 | 41 | 38.8 | 18.48 | 0.0757 | 0.26 | 13.28 | 0
October | 17 | 6PM to 7PM | 53.1 | 46.9 | 41 | 38.8 | 18.74 | 0.0756 | 0.26 | 13.31 | 0
October | 17 | 7PM to 8PM | 52 | 45.9 | 39.9 | 37.2 | 18.23 | 0.0757 | 0.25 | 13.27 | 0
October | 17 | 8PM to 9PM | 51.1 | 45.5 | 39.9 | 37.2 | 18.01 | 0.0759 | 0.25 | 13.25 | 1
October | 17 | 9PM to 10PM | 51.1 | 45.5 | 39.9 | 37.2 | 18.01 | 0.0759 | 0.25 | 13.25 | 1
October | 17 | 10PM to 11PM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
October | 17 | 11PM to 12AM | 48.9 | 44.9 | 41 | 38.8 | 17.74 | 0.0762 | 0.26 | 13.2 | 1
October | 18 | 12AM to 1AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
October | 18 | 1AM to 2AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
October | 18 | 2AM to 3AM | 46 | 43 | 39.9 | 37.2 | 16.79 | 0.0766 | 0.25 | 13.12 | 1
October | 18 | 3AM to 4AM | 45 | 42.5 | 39.9 | 37.2 | 16.53 | 0.0768 | 0.25 | 13.09 | 1
October | 18 | 4AM to 5AM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
October | 18 | 5AM to 6AM | 42.1 | 40.6 | 39 | 35.9 | 15.63 | 0.0772 | 0.24 | 13.01 | 1
October | 18 | 6AM to 7AM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
October | 18 | 7AM to 8AM | 48.9 | 44.9 | 41 | 38.8 | 17.74 | 0.0762 | 0.26 | 13.2 | 1
October | 18 | 8AM to 9AM | 55 | 47.8 | 41 | 38.8 | 19.22 | 0.0753 | 0.26 | 13.36 | 0
October | 18 | 9AM to 10AM | 60.1 | 50 | 41 | 38.8 | 20.44 | 0.0745 | 0.26 | 13.49 | 0
October | 18 | 10AM to 11AM | 64 | 52.5 | 43 | 41.9 | 21.89 | 0.074 | 0.28 | 13.6 | 0
October | 18 | 11AM to 12PM | 64.9 | 53.4 | 44.1 | 43.6 | 22.38 | 0.0738 | 0.29 | 13.63 | 0
October | 18 | 12PM to 1PM | 70 | 55.8 | 45 | 45.2 | 23.85 | 0.0731 | 0.3 | 13.77 | 0
October | 18 | 1PM to 2PM | 73 | 57 | 45 | 45.2 | 24.59 | 0.0727 | 0.3 | 13.85 | 0
October | 18 | 2PM to 3PM | 75 | 57.7 | 45 | 45.2 | 25.07 | 0.0724 | 0.3 | 13.9 | 0
October | 18 | 3PM to 4PM | 70 | 56.7 | 46.9 | 48.8 | 24.4 | 0.0731 | 0.32 | 13.78 | 0
October | 18 | 4PM to 5PM | 66 | 55.1 | 46.9 | 48.8 | 23.44 | 0.0736 | 0.32 | 13.67 | 0
October | 18 | 5PM to 6PM | 63 | 54.4 | 48 | 50.8 | 23.01 | 0.0741 | 0.34 | 13.6 | 0
October | 18 | 6PM to 7PM | 60.1 | 53.2 | 48 | 50.8 | 22.31 | 0.0745 | 0.34 | 13.53 | 0
October | 18 | 7PM to 8PM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
October | 18 | 8PM to 9PM | 57.9 | 51.8 | 46.9 | 48.8 | 21.47 | 0.0748 | 0.32 | 13.46 | 0
October | 18 | 9PM to 10PM | 55 | 50.6 | 46.9 | 48.8 | 20.77 | 0.0752 | 0.32 | 13.39 | 0
October | 18 | 10PM to 11PM | 51.1 | 48.4 | 46 | 47.1 | 19.55 | 0.0758 | 0.31 | 13.28 | 1
October | 18 | 11PM to 12AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
October | 19 | 12AM to 1AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
October | 19 | 1AM to 2AM | 46.9 | 46.5 | 46 | 47.1 | 18.55 | 0.0764 | 0.31 | 13.17 | 1
October | 19 | 2AM to 3AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
October | 19 | 3AM to 4AM | 45 | 45 | 45 | 45.2 | 17.77 | 0.0767 | 0.3 | 13.12 | 1
October | 19 | 4AM to 5AM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
October | 19 | 5AM to 6AM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
October | 19 | 6AM to 7AM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
October | 19 | 7AM to 8AM | 45 | 44.5 | 44.1 | 43.6 | 17.53 | 0.0767 | 0.29 | 13.11 | 1
October | 19 | 8AM to 9AM | 51.1 | 47.8 | 45 | 45.2 | 19.26 | 0.0758 | 0.3 | 13.27 | 1
October | 19 | 9AM to 10AM | 57 | 50 | 44.1 | 43.6 | 20.46 | 0.075 | 0.29 | 13.42 | 0
October | 19 | 10AM to 11AM | 59 | 50 | 42.1 | 40.4 | 20.44 | 0.0747 | 0.27 | 13.47 | 0
October | 19 | 11AM to 12PM | 61 | 50.9 | 42.1 | 40.4 | 20.92 | 0.0744 | 0.27 | 13.52 | 0
October | 19 | 12PM to 1PM | 64 | 50.2 | 37 | 33.2 | 20.53 | 0.074 | 0.22 | 13.57 | 0
October | 19 | 1PM to 2PM | 64 | 49.1 | 34 | 29.3 | 19.94 | 0.074 | 0.2 | 13.56 | 0
October | 19 | 2PM to 3PM | 66.9 | 50.8 | 35.1 | 30.6 | 20.84 | 0.0736 | 0.2 | 13.64 | 0
October | 19 | 3PM to 4PM | 64.9 | 50.2 | 36 | 31.8 | 20.53 | 0.0739 | 0.21 | 13.59 | 0
October | 19 | 4PM to 5PM | 64 | 50.5 | 37.9 | 34.4 | 20.72 | 0.074 | 0.23 | 13.58 | 0
October | 19 | 5PM to 6PM | 59 | 49.1 | 39.9 | 37.2 | 19.93 | 0.0747 | 0.25 | 13.46 | 0
October | 19 | 6PM to 7PM | 57.9 | 48.6 | 39.9 | 37.2 | 19.67 | 0.0749 | 0.25 | 13.43 | 0
October | 19 | 7PM to 8PM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
October | 19 | 8PM to 9PM | 54 | 46.8 | 39.9 | 37.2 | 18.71 | 0.0754 | 0.25 | 13.33 | 0
October | 19 | 9PM to 10PM | 53.1 | 46 | 39 | 35.9 | 18.29 | 0.0756 | 0.24 | 13.3 | 0
October | 19 | 10PM to 11PM | 52 | 45.5 | 39 | 35.9 | 18.03 | 0.0757 | 0.24 | 13.27 | 0
October | 19 | 11PM to 12AM | 52 | 45.5 | 39 | 35.9 | 18.03 | 0.0757 | 0.24 | 13.27 | 0
October | 20 | 12AM to 1AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
October | 20 | 1AM to 2AM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
October | 20 | 2AM to 3AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
October | 20 | 3AM to 4AM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
October | 20 | 4AM to 5AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
October | 20 | 5AM to 6AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
October | 20 | 6AM to 7AM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
October | 20 | 7AM to 8AM | 54 | 47.3 | 41 | 38.8 | 18.96 | 0.0754 | 0.26 | 13.33 | 0
October | 20 | 8AM to 9AM | 57.9 | 49.5 | 42.1 | 40.4 | 20.18 | 0.0748 | 0.27 | 13.44 | 0
October | 20 | 9AM to 10AM | 64 | 53 | 44.1 | 43.6 | 22.17 | 0.074 | 0.29 | 13.61 | 0
October | 20 | 10AM to 11AM | 69.1 | 55.4 | 45 | 45.2 | 23.63 | 0.0732 | 0.3 | 13.74 | 0
October | 20 | 11AM to 12PM | 73 | 56.6 | 44.1 | 43.6 | 24.35 | 0.0727 | 0.29 | 13.84 | 0
October | 20 | 12PM to 1PM | 75 | 57.7 | 45 | 45.2 | 25.07 | 0.0724 | 0.3 | 13.9 | 0
October | 20 | 1PM to 2PM | 75.9 | 57.3 | 43 | 41.9 | 24.77 | 0.0723 | 0.28 | 13.91 | 0
October | 20 | 2PM to 3PM | 77 | 57.7 | 43 | 41.9 | 25.03 | 0.0722 | 0.28 | 13.94 | 0
October | 20 | 3PM to 4PM | 77 | 57.7 | 43 | 41.9 | 25.03 | 0.0722 | 0.28 | 13.94 | 0
October | 20 | 4PM to 5PM | 75 | 56.9 | 43 | 41.9 | 24.55 | 0.0724 | 0.28 | 13.89 | 0
October | 20 | 5PM to 6PM | 69.1 | 56.3 | 46.9 | 48.8 | 24.18 | 0.0732 | 0.32 | 13.75 | 0
October | 20 | 6PM to 7PM | 66.9 | 55.5 | 46.9 | 48.8 | 23.66 | 0.0735 | 0.32 | 13.7 | 0
October | 20 | 7PM to 8PM | 66 | 55.1 | 46.9 | 48.8 | 23.44 | 0.0736 | 0.32 | 13.67 | 0
October | 20 | 8PM to 9PM | 63 | 53.9 | 46.9 | 48.8 | 22.7 | 0.0741 | 0.32 | 13.59 | 0
October | 20 | 9PM to 10PM | 61 | 53.6 | 48 | 50.8 | 22.53 | 0.0743 | 0.34 | 13.55 | 0
October | 20 | 10PM to 11PM | 60.1 | 52.7 | 46.9 | 48.8 | 22 | 0.0745 | 0.32 | 13.52 | 0
October | 20 | 11PM to 12AM | 57.9 | 51.8 | 46.9 | 48.8 | 21.47 | 0.0748 | 0.32 | 13.46 | 0
October | 21 | 12AM to 1AM | 57.9 | 51.3 | 46 | 47.1 | 21.22 | 0.0748 | 0.31 | 13.46 | 0
October | 21 | 1AM to 2AM | 59 | 52.2 | 46.9 | 48.8 | 21.73 | 0.0746 | 0.32 | 13.49 | 0
October | 21 | 2AM to 3AM | 57.9 | 52.3 | 48 | 50.8 | 21.79 | 0.0748 | 0.34 | 13.47 | 0
October | 21 | 3AM to 4AM | 55.9 | 51.5 | 48 | 50.8 | 21.31 | 0.0751 | 0.34 | 13.42 | 0
October | 21 | 4AM to 5AM | 55 | 51.1 | 48 | 50.8 | 21.09 | 0.0752 | 0.34 | 13.39 | 0
October | 21 | 5AM to 6AM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
October | 21 | 6AM to 7AM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
October | 21 | 7AM to 8AM | 61 | 54.6 | 50 | 54.7 | 23.15 | 0.0743 | 0.36 | 13.56 | 0
October | 21 | 8AM to 9AM | 66 | 57.6 | 52 | 59 | 25.03 | 0.0736 | 0.39 | 13.71 | 0
October | 21 | 9AM to 10AM | 72 | 60.8 | 54 | 63.5 | 27.19 | 0.0727 | 0.42 | 13.87 | 0
October | 21 | 10AM to 11AM | 77 | 62.5 | 54 | 63.5 | 28.42 | 0.072 | 0.42 | 14.01 | 0
October | 21 | 11AM to 12PM | 80.1 | 63.6 | 54 | 63.5 | 29.16 | 0.0716 | 0.42 | 14.09 | 0
October | 21 | 12PM to 1PM | 80.1 | 63.6 | 54 | 63.5 | 29.16 | 0.0716 | 0.42 | 14.09 | 0
October | 21 | 1PM to 2PM | 84.9 | 64.3 | 52 | 59 | 29.64 | 0.071 | 0.39 | 14.2 | 0
October | 21 | 2PM to 3PM | 86 | 64.6 | 52 | 59 | 29.9 | 0.0709 | 0.39 | 14.23 | 0
October | 21 | 3PM to 4PM | 84 | 63.5 | 51.1 | 57 | 29.11 | 0.0712 | 0.38 | 14.17 | 0
October | 21 | 4PM to 5PM | 80.1 | 62.6 | 52 | 59 | 28.45 | 0.0717 | 0.39 | 14.07 | 0
October | 21 | 5PM to 6PM | 77 | 61.6 | 52 | 59 | 27.71 | 0.0721 | 0.39 | 13.99 | 0
October | 21 | 6PM to 7PM | 73 | 60.7 | 53.1 | 61.4 | 27.12 | 0.0726 | 0.41 | 13.9 | 0
October | 21 | 7PM to 8PM | 72 | 60.3 | 53.1 | 61.4 | 26.86 | 0.0727 | 0.41 | 13.87 | 0
October | 21 | 8PM to 9PM | 71.1 | 60 | 53.1 | 61.4 | 26.64 | 0.0729 | 0.41 | 13.84 | 0
October | 21 | 9PM to 10PM | 70 | 59.6 | 53.1 | 61.4 | 26.38 | 0.073 | 0.41 | 13.82 | 0
October | 21 | 10PM to 11PM | 68 | 58.9 | 53.1 | 61.4 | 25.89 | 0.0733 | 0.41 | 13.76 | 0
October | 21 | 11PM to 12AM | 66 | 58.6 | 54 | 63.5 | 25.74 | 0.0735 | 0.42 | 13.72 | 0
October | 22 | 12AM to 1AM | 66.9 | 59 | 54 | 63.5 | 25.96 | 0.0734 | 0.42 | 13.74 | 0
October | 22 | 1AM to 2AM | 66.9 | 59 | 54 | 63.5 | 25.96 | 0.0734 | 0.42 | 13.74 | 0
October | 22 | 2AM to 3AM | 66.9 | 59 | 54 | 63.5 | 25.96 | 0.0734 | 0.42 | 13.74 | 0
October | 22 | 3AM to 4AM | 66.9 | 59 | 54 | 63.5 | 25.96 | 0.0734 | 0.42 | 13.74 | 0
October | 22 | 4AM to 5AM | 66 | 58.6 | 54 | 63.5 | 25.74 | 0.0735 | 0.42 | 13.72 | 0
October | 22 | 5AM to 6AM | 66 | 58.6 | 54 | 63.5 | 25.74 | 0.0735 | 0.42 | 13.72 | 0
October | 22 | 6AM to 7AM | 64.9 | 58.2 | 54 | 63.5 | 25.47 | 0.0737 | 0.42 | 13.69 | 0
October | 22 | 7AM to 8AM | 66 | 59.2 | 55 | 66.1 | 26.14 | 0.0735 | 0.44 | 13.73 | 0
October | 22 | 8AM to 9AM | 72 | 61.4 | 55 | 66.1 | 27.59 | 0.0727 | 0.44 | 13.88 | 0
October | 22 | 9AM to 10AM | 75 | 62.4 | 55 | 66.1 | 28.34 | 0.0723 | 0.44 | 13.96 | 0
October | 22 | 10AM to 11AM | 77 | 63.1 | 55 | 66.1 | 28.82 | 0.072 | 0.44 | 14.01 | 0
October | 22 | 11AM to 12PM | 78.1 | 63.4 | 55 | 66.1 | 29.08 | 0.0719 | 0.44 | 14.04 | 0
October | 22 | 12PM to 1PM | 77 | 63.1 | 55 | 66.1 | 28.82 | 0.072 | 0.44 | 14.01 | 0
October | 22 | 1PM to 2PM | 79 | 63.2 | 54 | 63.5 | 28.9 | 0.0718 | 0.42 | 14.06 | 0
October | 22 | 2PM to 3PM | 78.1 | 62.9 | 54 | 63.5 | 28.68 | 0.0719 | 0.42 | 14.03 | 0
October | 22 | 3PM to 4PM | 77 | 62.5 | 54 | 63.5 | 28.42 | 0.072 | 0.42 | 14.01 | 0
October | 22 | 4PM to 5PM | 77 | 62.5 | 54 | 63.5 | 28.42 | 0.072 | 0.42 | 14.01 | 0
October | 22 | 5PM to 6PM | 73 | 61.2 | 54 | 63.5 | 27.45 | 0.0726 | 0.42 | 13.9 | 0
October | 22 | 6PM to 7PM | 71.1 | 59.4 | 52 | 59 | 26.26 | 0.0729 | 0.39 | 13.84 | 0
October | 22 | 7PM to 8PM | 70 | 59.1 | 52 | 59 | 26 | 0.073 | 0.39 | 13.81 | 0
October | 22 | 8PM to 9PM | 66.9 | 58.5 | 53.1 | 61.4 | 25.63 | 0.0734 | 0.41 | 13.74 | 0
October | 22 | 9PM to 10PM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
October | 22 | 10PM to 11PM | 62.1 | 57.1 | 54 | 63.5 | 24.77 | 0.0741 | 0.42 | 13.62 | 0
October | 22 | 11PM to 12AM | 60.1 | 57 | 55 | 66.1 | 24.69 | 0.0744 | 0.44 | 13.57 | 0
October | 23 | 12AM to 1AM | 57.9 | 56.2 | 55 | 66.1 | 24.16 | 0.0747 | 0.44 | 13.52 | 0
October | 23 | 1AM to 2AM | 55 | 53.3 | 52 | 59 | 22.36 | 0.0751 | 0.39 | 13.42 | 0
October | 23 | 2AM to 3AM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
October | 23 | 3AM to 4AM | 53.1 | 52.4 | 52 | 59 | 21.87 | 0.0754 | 0.39 | 13.37 | 0
October | 23 | 4AM to 5AM | 52 | 52 | 52 | 59 | 21.61 | 0.0756 | 0.39 | 13.34 | 0
October | 23 | 5AM to 6AM | 51.1 | 51.1 | 51.1 | 57 | 21.09 | 0.0757 | 0.38 | 13.31 | 1
October | 23 | 6AM to 7AM | 51.1 | 51.1 | 51.1 | 57 | 21.09 | 0.0757 | 0.38 | 13.31 | 1
October | 23 | 7AM to 8AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 23 | 8AM to 9AM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
October | 23 | 9AM to 10AM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
October | 23 | 10AM to 11AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 23 | 11AM to 12PM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 23 | 12PM to 1PM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 23 | 1PM to 2PM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
October | 23 | 2PM to 3PM | 52 | 50.9 | 50 | 54.7 | 20.96 | 0.0756 | 0.36 | 13.33 | 0
October | 23 | 3PM to 4PM | 53.1 | 50.7 | 48.9 | 52.6 | 20.88 | 0.0755 | 0.35 | 13.35 | 0
October | 23 | 4PM to 5PM | 52 | 49.8 | 48 | 50.8 | 20.34 | 0.0756 | 0.34 | 13.31 | 0
October | 23 | 5PM to 6PM | 50 | 49.4 | 48.9 | 52.6 | 20.14 | 0.0759 | 0.35 | 13.27 | 1
October | 23 | 6PM to 7PM | 50 | 48.3 | 46.9 | 48.8 | 19.55 | 0.076 | 0.32 | 13.26 | 1
October | 23 | 7PM to 8PM | 44.1 | 44.1 | 44.1 | 43.6 | 17.31 | 0.0769 | 0.29 | 13.09 | 1
October | 23 | 8PM to 9PM | 43 | 42.5 | 42.1 | 40.4 | 16.55 | 0.0771 | 0.27 | 13.05 | 1
October | 23 | 9PM to 10PM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
October | 23 | 10PM to 11PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
October | 23 | 11PM to 12AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
October | 24 | 12AM to 1AM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
October | 24 | 1AM to 2AM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
October | 24 | 2AM to 3AM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
October | 24 | 3AM to 4AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
October | 24 | 4AM to 5AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
October | 24 | 5AM to 6AM | 32 | 32 | 32 | 27.1 | 11.84 | 0.0789 | 0.18 | 12.73 | 1
October | 24 | 6AM to 7AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
October | 24 | 7AM to 8AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
October | 24 | 8AM to 9AM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
October | 24 | 9AM to 10AM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
October | 24 | 10AM to 11AM | 51.1 | 45.5 | 39.9 | 37.2 | 18.01 | 0.0759 | 0.25 | 13.25 | 1
October | 24 | 11AM to 12PM | 54 | 46.4 | 39 | 35.9 | 18.51 | 0.0755 | 0.24 | 13.32 | 0
October | 24 | 12PM to 1PM | 57 | 48.2 | 39.9 | 37.2 | 19.45 | 0.075 | 0.25 | 13.4 | 0
October | 24 | 1PM to 2PM | 60.1 | 49.6 | 39.9 | 37.2 | 20.19 | 0.0746 | 0.25 | 13.48 | 0
October | 24 | 2PM to 3PM | 61 | 50.4 | 41 | 38.8 | 20.66 | 0.0744 | 0.26 | 13.51 | 0
October | 24 | 3PM to 4PM | 61 | 49.6 | 39 | 35.9 | 20.21 | 0.0744 | 0.24 | 13.5 | 0
October | 24 | 4PM to 5PM | 59 | 49.1 | 39.9 | 37.2 | 19.93 | 0.0747 | 0.25 | 13.46 | 0
October | 24 | 5PM to 6PM | 53.1 | 46.9 | 41 | 38.8 | 18.74 | 0.0756 | 0.26 | 13.31 | 0
October | 24 | 6PM to 7PM | 52 | 46.9 | 42.1 | 40.4 | 18.74 | 0.0757 | 0.27 | 13.28 | 0
October | 24 | 7PM to 8PM | 53.1 | 46.9 | 41 | 38.8 | 18.74 | 0.0756 | 0.26 | 13.31 | 0
October | 24 | 8PM to 9PM | 52 | 46.4 | 41 | 38.8 | 18.48 | 0.0757 | 0.26 | 13.28 | 0
October | 24 | 9PM to 10PM | 52 | 46.9 | 42.1 | 40.4 | 18.74 | 0.0757 | 0.27 | 13.28 | 0
October | 24 | 10PM to 11PM | 52 | 46.9 | 42.1 | 40.4 | 18.74 | 0.0757 | 0.27 | 13.28 | 0
October | 24 | 11PM to 12AM | 52 | 45.9 | 39.9 | 37.2 | 18.23 | 0.0757 | 0.25 | 13.27 | 0
October | 25 | 12AM to 1AM | 51.1 | 45.1 | 39 | 35.9 | 17.81 | 0.0759 | 0.24 | 13.25 | 1
October | 25 | 1AM to 2AM | 52 | 45.9 | 39.9 | 37.2 | 18.23 | 0.0757 | 0.25 | 13.27 | 0
October | 25 | 2AM to 3AM | 52 | 46.9 | 42.1 | 40.4 | 18.74 | 0.0757 | 0.27 | 13.28 | 0
October | 25 | 3AM to 4AM | 53.1 | 47.8 | 43 | 41.9 | 19.22 | 0.0755 | 0.28 | 13.32 | 0
October | 25 | 4AM to 5AM | 55 | 50.1 | 46 | 47.1 | 20.52 | 0.0752 | 0.31 | 13.38 | 0
October | 25 | 5AM to 6AM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
October | 25 | 6AM to 7AM | 57 | 55.2 | 54 | 63.5 | 23.54 | 0.0748 | 0.42 | 13.48 | 0
October | 25 | 7AM to 8AM | 55 | 55 | 55 | 66.1 | 23.46 | 0.0751 | 0.44 | 13.44 | 0
October | 25 | 8AM to 9AM | 55.9 | 55.9 | 55.9 | 68.3 | 24.02 | 0.075 | 0.45 | 13.47 | 0
October | 25 | 9AM to 10AM | 57.9 | 56.7 | 55.9 | 68.3 | 24.51 | 0.0747 | 0.45 | 13.52 | 0
October | 25 | 10AM to 11AM | 60.1 | 58.2 | 57 | 71.1 | 25.47 | 0.0743 | 0.47 | 13.59 | 0
October | 25 | 11AM to 12PM | 64.9 | 61.1 | 59 | 76.4 | 27.48 | 0.0736 | 0.5 | 13.73 | 0
October | 25 | 12PM to 1PM | 69.1 | 63.2 | 60.1 | 79.5 | 28.98 | 0.073 | 0.52 | 13.85 | 0
October | 25 | 1PM to 2PM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
October | 25 | 2PM to 3PM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
October | 25 | 3PM to 4PM | 70 | 63.5 | 60.1 | 79.5 | 29.2 | 0.0729 | 0.52 | 13.87 | 0
October | 25 | 4PM to 5PM | 69.1 | 62.6 | 59 | 76.4 | 28.5 | 0.073 | 0.5 | 13.84 | 0
October | 25 | 5PM to 6PM | 68 | 62.2 | 59 | 76.4 | 28.23 | 0.0732 | 0.5 | 13.81 | 0
October | 25 | 6PM to 7PM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
October | 25 | 7PM to 8PM | 61 | 59.1 | 57.9 | 73.5 | 26.06 | 0.0742 | 0.48 | 13.62 | 0
October | 25 | 8PM to 9PM | 60.1 | 57 | 55 | 66.1 | 24.69 | 0.0744 | 0.44 | 13.57 | 0
October | 25 | 9PM to 10PM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
October | 25 | 10PM to 11PM | 52 | 50.3 | 48.9 | 52.6 | 20.62 | 0.0756 | 0.35 | 13.32 | 0
October | 25 | 11PM to 12AM | 51.1 | 48.8 | 46.9 | 48.8 | 19.81 | 0.0758 | 0.32 | 13.29 | 1
October | 26 | 12AM to 1AM | 48.9 | 45.8 | 43 | 41.9 | 18.22 | 0.0762 | 0.28 | 13.21 | 1
October | 26 | 1AM to 2AM | 48.9 | 45.4 | 42.1 | 40.4 | 18 | 0.0762 | 0.27 | 13.2 | 1
October | 26 | 2AM to 3AM | 48 | 45 | 42.1 | 40.4 | 17.78 | 0.0763 | 0.27 | 13.18 | 1
October | 26 | 3AM to 4AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
October | 26 | 4AM to 5AM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
October | 26 | 5AM to 6AM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
October | 26 | 6AM to 7AM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
October | 26 | 7AM to 8AM | 46 | 43 | 39.9 | 37.2 | 16.79 | 0.0766 | 0.25 | 13.12 | 1
October | 26 | 8AM to 9AM | 45 | 41.6 | 37.9 | 34.4 | 16.1 | 0.0768 | 0.23 | 13.08 | 1
October | 26 | 9AM to 10AM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
October | 26 | 10AM to 11AM | 50 | 44.1 | 37.9 | 34.4 | 17.32 | 0.076 | 0.23 | 13.21 | 1
October | 26 | 11AM to 12PM | 53.1 | 45.6 | 37.9 | 34.4 | 18.06 | 0.0756 | 0.23 | 13.29 | 0
October | 26 | 12PM to 1PM | 55 | 46.1 | 37 | 33.2 | 18.35 | 0.0753 | 0.22 | 13.34 | 0
October | 26 | 1PM to 2PM | 55.9 | 45.8 | 35.1 | 30.6 | 18.18 | 0.0752 | 0.2 | 13.36 | 0
October | 26 | 2PM to 3PM | 57 | 46.3 | 35.1 | 30.6 | 18.44 | 0.075 | 0.2 | 13.38 | 0
October | 26 | 3PM to 4PM | 57 | 46.3 | 35.1 | 30.6 | 18.44 | 0.075 | 0.2 | 13.38 | 0
October | 26 | 4PM to 5PM | 55 | 45.4 | 35.1 | 30.6 | 17.96 | 0.0753 | 0.2 | 13.33 | 0
October | 26 | 5PM to 6PM | 51.1 | 43.8 | 36 | 31.8 | 17.18 | 0.0759 | 0.21 | 13.23 | 1
October | 26 | 6PM to 7PM | 51.1 | 43.8 | 36 | 31.8 | 17.18 | 0.0759 | 0.21 | 13.23 | 1
October | 26 | 7PM to 8PM | 48 | 43.1 | 37.9 | 34.4 | 16.84 | 0.0763 | 0.23 | 13.16 | 1
October | 26 | 8PM to 9PM | 48 | 42.3 | 36 | 31.8 | 16.44 | 0.0764 | 0.21 | 13.15 | 1
October | 26 | 9PM to 10PM | 45 | 40.8 | 36 | 31.8 | 15.7 | 0.0768 | 0.21 | 13.08 | 1
October | 26 | 10PM to 11PM | 46 | 41.3 | 36 | 31.8 | 15.96 | 0.0767 | 0.21 | 13.1 | 1
October | 26 | 11PM to 12AM | 44.1 | 39.9 | 35.1 | 30.6 | 15.31 | 0.077 | 0.2 | 13.05 | 1
October | 27 | 12AM to 1AM | 41 | 38.3 | 35.1 | 30.6 | 14.57 | 0.0774 | 0.2 | 12.97 | 1
October | 27 | 1AM to 2AM | 41 | 38.3 | 35.1 | 30.6 | 14.57 | 0.0774 | 0.2 | 12.97 | 1
October | 27 | 2AM to 3AM | 39.9 | 37.7 | 35.1 | 30.6 | 14.3 | 0.0776 | 0.2 | 12.94 | 1
October | 27 | 3AM to 4AM | 39 | 37.2 | 35.1 | 30.6 | 14.09 | 0.0777 | 0.2 | 12.92 | 1
October | 27 | 4AM to 5AM | 42.1 | 38.9 | 35.1 | 30.6 | 14.83 | 0.0773 | 0.2 | 13 | 1
October | 27 | 5AM to 6AM | 43 | 39.4 | 35.1 | 30.6 | 15.04 | 0.0771 | 0.2 | 13.02 | 1
October | 27 | 6AM to 7AM | 43 | 39.4 | 35.1 | 30.6 | 15.04 | 0.0771 | 0.2 | 13.02 | 1
October | 27 | 7AM to 8AM | 48 | 42 | 35.1 | 30.6 | 16.26 | 0.0764 | 0.2 | 13.15 | 1
October | 27 | 8AM to 9AM | 52 | 43.9 | 35.1 | 30.6 | 17.22 | 0.0758 | 0.2 | 13.25 | 0
October | 27 | 9AM to 10AM | 55.9 | 46.6 | 37 | 33.2 | 18.57 | 0.0752 | 0.22 | 13.36 | 0
October | 27 | 10AM to 11AM | 59 | 48.7 | 39 | 35.9 | 19.73 | 0.0747 | 0.24 | 13.45 | 0
October | 27 | 11AM to 12PM | 63 | 50.5 | 39 | 35.9 | 20.69 | 0.0742 | 0.24 | 13.55 | 0
October | 27 | 12PM to 1PM | 66 | 51.1 | 37 | 33.2 | 21.01 | 0.0737 | 0.22 | 13.63 | 0
October | 27 | 1PM to 2PM | 68 | 51.9 | 37 | 33.2 | 21.49 | 0.0735 | 0.22 | 13.68 | 0
October | 27 | 2PM to 3PM | 68 | 51.9 | 37 | 33.2 | 21.49 | 0.0735 | 0.22 | 13.68 | 0
October | 27 | 3PM to 4PM | 68 | 51.9 | 37 | 33.2 | 21.49 | 0.0735 | 0.22 | 13.68 | 0
October | 27 | 4PM to 5PM | 64.9 | 50.2 | 36 | 31.8 | 20.53 | 0.0739 | 0.21 | 13.59 | 0
October | 27 | 5PM to 6PM | 62.1 | 49.3 | 37 | 33.2 | 20.05 | 0.0743 | 0.22 | 13.52 | 0
October | 27 | 6PM to 7PM | 61 | 48.9 | 37 | 33.2 | 19.79 | 0.0745 | 0.22 | 13.49 | 0
October | 27 | 7PM to 8PM | 59 | 48 | 37 | 33.2 | 19.31 | 0.0747 | 0.22 | 13.44 | 0
October | 27 | 8PM to 9PM | 57.9 | 47.5 | 37 | 33.2 | 19.05 | 0.0749 | 0.22 | 13.42 | 0
October | 27 | 9PM to 10PM | 52 | 45.9 | 39.9 | 37.2 | 18.23 | 0.0757 | 0.25 | 13.27 | 0
October | 27 | 10PM to 11PM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
October | 27 | 11PM to 12AM | 50 | 45.4 | 41 | 38.8 | 18 | 0.076 | 0.26 | 13.23 | 1
October | 28 | 12AM to 1AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
October | 28 | 1AM to 2AM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
October | 28 | 2AM to 3AM | 45 | 40.8 | 36 | 31.8 | 15.7 | 0.0768 | 0.21 | 13.08 | 1
October | 28 | 3AM to 4AM | 42.1 | 38.9 | 35.1 | 30.6 | 14.83 | 0.0773 | 0.2 | 13 | 1
October | 28 | 4AM to 5AM | 41 | 38.7 | 36 | 31.8 | 14.74 | 0.0774 | 0.21 | 12.97 | 1
October | 28 | 5AM to 6AM | 41 | 39.2 | 37 | 33.2 | 14.95 | 0.0774 | 0.22 | 12.98 | 1
October | 28 | 6AM to 7AM | 39.9 | 38.6 | 37 | 33.2 | 14.69 | 0.0776 | 0.22 | 12.95 | 1
October | 28 | 7AM to 8AM | 44.1 | 41.1 | 37.9 | 34.4 | 15.88 | 0.0769 | 0.23 | 13.06 | 1
October | 28 | 8AM to 9AM | 48 | 43.1 | 37.9 | 34.4 | 16.84 | 0.0763 | 0.23 | 13.16 | 1
October | 28 | 9AM to 10AM | 54 | 46.4 | 39 | 35.9 | 18.51 | 0.0755 | 0.24 | 13.32 | 0
October | 28 | 10AM to 11AM | 55.9 | 46.6 | 37 | 33.2 | 18.57 | 0.0752 | 0.22 | 13.36 | 0
October | 28 | 11AM to 12PM | 59 | 48 | 37 | 33.2 | 19.31 | 0.0747 | 0.22 | 13.44 | 0
October | 28 | 12PM to 1PM | 59 | 47.6 | 36 | 31.8 | 19.1 | 0.0747 | 0.21 | 13.44 | 0
October | 28 | 1PM to 2PM | 60.1 | 47.4 | 34 | 29.3 | 18.98 | 0.0746 | 0.2 | 13.46 | 0
October | 28 | 2PM to 3PM | 61 | 46.7 | 30.9 | 25.8 | 18.64 | 0.0745 | 0.17 | 13.47 | 0
October | 28 | 3PM to 4PM | 59 | 46.2 | 32 | 27.1 | 18.37 | 0.0748 | 0.18 | 13.42 | 0
October | 28 | 4PM to 5PM | 53.1 | 44 | 34 | 29.3 | 17.28 | 0.0756 | 0.2 | 13.28 | 0
October | 28 | 5PM to 6PM | 50 | 42.2 | 33.1 | 28.3 | 16.38 | 0.0761 | 0.19 | 13.2 | 1
October | 28 | 6PM to 7PM | 48 | 42 | 35.1 | 30.6 | 16.26 | 0.0764 | 0.2 | 13.15 | 1
October | 28 | 7PM to 8PM | 46 | 41 | 35.1 | 30.6 | 15.79 | 0.0767 | 0.2 | 13.1 | 1
October | 28 | 8PM to 9PM | 45 | 40.8 | 36 | 31.8 | 15.7 | 0.0768 | 0.21 | 13.08 | 1
October | 28 | 9PM to 10PM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
October | 28 | 10PM to 11PM | 41 | 38.7 | 36 | 31.8 | 14.74 | 0.0774 | 0.21 | 12.97 | 1
October | 28 | 11PM to 12AM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
October | 29 | 12AM to 1AM | 41 | 39.2 | 37 | 33.2 | 14.95 | 0.0774 | 0.22 | 12.98 | 1
October | 29 | 1AM to 2AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
October | 29 | 2AM to 3AM | 39.9 | 39.5 | 39 | 35.9 | 15.11 | 0.0776 | 0.24 | 12.96 | 1
October | 29 | 3AM to 4AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
October | 29 | 4AM to 5AM | 37 | 37 | 37 | 33.2 | 14 | 0.078 | 0.22 | 12.87 | 1
October | 29 | 5AM to 6AM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
October | 29 | 6AM to 7AM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
October | 29 | 7AM to 8AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
October | 29 | 8AM to 9AM | 50 | 46.4 | 43 | 41.9 | 18.48 | 0.076 | 0.28 | 13.24 | 1
October | 29 | 9AM to 10AM | 55 | 48.7 | 43 | 41.9 | 19.7 | 0.0753 | 0.28 | 13.37 | 0
October | 29 | 10AM to 11AM | 57.9 | 49.9 | 43 | 41.9 | 20.4 | 0.0748 | 0.28 | 13.44 | 0
October | 29 | 11AM to 12PM | 61 | 51.3 | 43 | 41.9 | 21.14 | 0.0744 | 0.28 | 13.52 | 0
October | 29 | 12PM to 1PM | 63 | 51.7 | 42.1 | 40.4 | 21.4 | 0.0741 | 0.27 | 13.57 | 0
October | 29 | 1PM to 2PM | 64.9 | 52.5 | 42.1 | 40.4 | 21.88 | 0.0738 | 0.27 | 13.62 | 0
October | 29 | 2PM to 3PM | 64.9 | 52.5 | 42.1 | 40.4 | 21.88 | 0.0738 | 0.27 | 13.62 | 0
October | 29 | 3PM to 4PM | 64 | 52.2 | 42.1 | 40.4 | 21.66 | 0.074 | 0.27 | 13.6 | 0
October | 29 | 4PM to 5PM | 57 | 49.1 | 42.1 | 40.4 | 19.96 | 0.075 | 0.27 | 13.41 | 0
October | 29 | 5PM to 6PM | 54 | 47.3 | 41 | 38.8 | 18.96 | 0.0754 | 0.26 | 13.33 | 0
October | 29 | 6PM to 7PM | 51.1 | 45.5 | 39.9 | 37.2 | 18.01 | 0.0759 | 0.25 | 13.25 | 1
October | 29 | 7PM to 8PM | 53.1 | 46.4 | 39.9 | 37.2 | 18.49 | 0.0756 | 0.25 | 13.3 | 0
October | 29 | 8PM to 9PM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
October | 29 | 9PM to 10PM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
October | 29 | 10PM to 11PM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
October | 29 | 11PM to 12AM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
October | 30 | 12AM to 1AM | 46 | 43 | 39.9 | 37.2 | 16.79 | 0.0766 | 0.25 | 13.12 | 1
October | 30 | 1AM to 2AM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
October | 30 | 2AM to 3AM | 44.1 | 42 | 39.9 | 37.2 | 16.31 | 0.0769 | 0.25 | 13.07 | 1
October | 30 | 3AM to 4AM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
October | 30 | 4AM to 5AM | 41 | 40.5 | 39.9 | 37.2 | 15.57 | 0.0774 | 0.25 | 12.99 | 1
October | 30 | 5AM to 6AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
October | 30 | 6AM to 7AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
October | 30 | 7AM to 8AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
October | 30 | 8AM to 9AM | 53.1 | 48.7 | 45 | 45.2 | 19.74 | 0.0755 | 0.3 | 13.33 | 0
October | 30 | 9AM to 10AM | 57.9 | 50.8 | 45 | 45.2 | 20.92 | 0.0748 | 0.3 | 13.45 | 0
October | 30 | 10AM to 11AM | 62.1 | 52.6 | 45 | 45.2 | 21.92 | 0.0742 | 0.3 | 13.56 | 0
October | 30 | 11AM to 12PM | 66 | 54.7 | 46 | 47.1 | 23.18 | 0.0737 | 0.31 | 13.67 | 0
October | 30 | 12PM to 1PM | 69.1 | 55.4 | 45 | 45.2 | 23.63 | 0.0732 | 0.3 | 13.74 | 0
October | 30 | 1PM to 2PM | 72 | 56.6 | 45 | 45.2 | 24.33 | 0.0728 | 0.3 | 13.82 | 0
October | 30 | 2PM to 3PM | 73 | 56.6 | 44.1 | 43.6 | 24.35 | 0.0727 | 0.29 | 13.84 | 0
October | 30 | 3PM to 4PM | 71.1 | 56.7 | 46 | 47.1 | 24.41 | 0.073 | 0.31 | 13.8 | 0
October | 30 | 4PM to 5PM | 64 | 54.3 | 46.9 | 48.8 | 22.96 | 0.0739 | 0.32 | 13.62 | 0
October | 30 | 5PM to 6PM | 59 | 52.2 | 46.9 | 48.8 | 21.73 | 0.0746 | 0.32 | 13.49 | 0
October | 30 | 6PM to 7PM | 59 | 52.2 | 46.9 | 48.8 | 21.73 | 0.0746 | 0.32 | 13.49 | 0
October | 30 | 7PM to 8PM | 57 | 51.9 | 48 | 50.8 | 21.57 | 0.0749 | 0.34 | 13.45 | 0
October | 30 | 8PM to 9PM | 55 | 51.6 | 48.9 | 52.6 | 21.36 | 0.0752 | 0.35 | 13.4 | 0
October | 30 | 9PM to 10PM | 54 | 52.8 | 52 | 59 | 22.09 | 0.0753 | 0.39 | 13.39 | 0
October | 30 | 10PM to 11PM | 55.9 | 54.8 | 54 | 63.5 | 23.28 | 0.075 | 0.42 | 13.46 | 0
October | 30 | 11PM to 12AM | 57 | 55.8 | 55 | 66.1 | 23.94 | 0.0748 | 0.44 | 13.49 | 0
October | 31 | 12AM to 1AM | 51.1 | 51.1 | 51.1 | 57 | 21.09 | 0.0757 | 0.38 | 13.31 | 1
October | 31 | 1AM to 2AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
October | 31 | 2AM to 3AM | 48.9 | 48.9 | 48.9 | 52.6 | 19.87 | 0.0761 | 0.35 | 13.24 | 1
October | 31 | 3AM to 4AM | 46.9 | 46.9 | 46.9 | 48.8 | 18.8 | 0.0764 | 0.32 | 13.18 | 1
October | 31 | 4AM to 5AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
October | 31 | 5AM to 6AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
October | 31 | 6AM to 7AM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
October | 31 | 7AM to 8AM | 53.1 | 53.1 | 53.1 | 61.4 | 22.25 | 0.0754 | 0.41 | 13.38 | 0
October | 31 | 8AM to 9AM | 57.9 | 55 | 53.1 | 61.4 | 23.44 | 0.0747 | 0.41 | 13.5 | 0
October | 31 | 9AM to 10AM | 63 | 55.4 | 50 | 54.7 | 23.63 | 0.074 | 0.36 | 13.61 | 0
October | 31 | 10AM to 11AM | 68 | 57.9 | 51.1 | 57 | 25.21 | 0.0733 | 0.38 | 13.75 | 0
October | 31 | 11AM to 12PM | 71.1 | 58 | 48.9 | 52.6 | 25.26 | 0.0729 | 0.35 | 13.82 | 0
October | 31 | 12PM to 1PM | 73 | 57.8 | 46.9 | 48.8 | 25.15 | 0.0727 | 0.32 | 13.86 | 0
October | 31 | 1PM to 2PM | 73.9 | 57.3 | 45 | 45.2 | 24.81 | 0.0726 | 0.3 | 13.87 | 0
October | 31 | 2PM to 3PM | 73.9 | 57.8 | 46 | 47.1 | 25.11 | 0.0726 | 0.31 | 13.87 | 0
October | 31 | 3PM to 4PM | 72 | 56.6 | 45 | 45.2 | 24.33 | 0.0728 | 0.3 | 13.82 | 0
October | 31 | 4PM to 5PM | 66 | 53.4 | 43 | 41.9 | 22.37 | 0.0737 | 0.28 | 13.65 | 0
October | 31 | 5PM to 6PM | 62.1 | 51.7 | 43 | 41.9 | 21.41 | 0.0742 | 0.28 | 13.55 | 0
October | 31 | 6PM to 7PM | 61 | 51.7 | 44.1 | 43.6 | 21.42 | 0.0744 | 0.29 | 13.53 | 0
October | 31 | 7PM to 8PM | 55 | 49.6 | 45 | 45.2 | 20.22 | 0.0752 | 0.3 | 13.38 | 0
October | 31 | 8PM to 9PM | 55 | 50.1 | 46 | 47.1 | 20.52 | 0.0752 | 0.31 | 13.38 | 0
October | 31 | 9PM to 10PM | 54.1 | 48.9 | 44.4 | 44.3 | 19.86 | 0.0754 | 0.29 | 13.35 | 0
October | 31 | 10PM to 11PM | 53.2 | 47.8 | 43 | 41.9 | 19.27 | 0.0755 | 0.28 | 13.32 | 0
October | 31 | 11PM to 12AM | 52.3 | 46.7 | 41.4 | 39.3 | 18.65 | 0.0757 | 0.26 | 13.29 | 0
November | 1 | 12AM to 1AM | 51.6 | 45.6 | 39.7 | 36.9 | 18.1 | 0.0758 | 0.25 | 13.26 | 1
November | 1 | 1AM to 2AM | 50.7 | 44.5 | 38.1 | 34.6 | 17.53 | 0.0759 | 0.23 | 13.23 | 1
November | 1 | 2AM to 3AM | 49.8 | 43.5 | 36.7 | 32.7 | 17.02 | 0.0761 | 0.22 | 13.2 | 1
November | 1 | 3AM to 4AM | 48.9 | 42.4 | 35.1 | 30.6 | 16.48 | 0.0762 | 0.2 | 13.17 | 1
November | 1 | 4AM to 5AM | 48.9 | 41.7 | 33.1 | 28.3 | 16.12 | 0.0763 | 0.19 | 13.17 | 1
November | 1 | 5AM to 6AM | 48.9 | 41.3 | 32 | 27.1 | 15.93 | 0.0763 | 0.18 | 13.16 | 1
November | 1 | 6AM to 7AM | 48 | 40.8 | 32 | 27.1 | 15.71 | 0.0764 | 0.18 | 13.14 | 1
November | 1 | 7AM to 8AM | 48 | 40.8 | 32 | 27.1 | 15.71 | 0.0764 | 0.18 | 13.14 | 1
November | 1 | 8AM to 9AM | 48.9 | 41.3 | 32 | 27.1 | 15.93 | 0.0763 | 0.18 | 13.16 | 1
November | 1 | 9AM to 10AM | 51.1 | 42.7 | 33.1 | 28.3 | 16.64 | 0.0759 | 0.19 | 13.22 | 1
November | 1 | 10AM to 11AM | 53.1 | 43.3 | 32 | 27.1 | 16.93 | 0.0756 | 0.18 | 13.27 | 0
November | 1 | 11AM to 12PM | 54 | 44.2 | 33.1 | 28.3 | 17.34 | 0.0755 | 0.19 | 13.3 | 0
November | 1 | 12PM to 1PM | 55.9 | 44.3 | 30.9 | 25.8 | 17.42 | 0.0752 | 0.17 | 13.34 | 0
November | 1 | 1PM to 2PM | 57 | 44.5 | 30 | 24.7 | 17.52 | 0.0751 | 0.16 | 13.37 | 0
November | 1 | 2PM to 3PM | 55.9 | 43.3 | 28 | 22.5 | 16.92 | 0.0752 | 0.15 | 13.33 | 0
November | 1 | 3PM to 4PM | 55 | 43.2 | 28.9 | 23.5 | 16.86 | 0.0754 | 0.16 | 13.31 | 0
November | 1 | 4PM to 5PM | 54 | 42.7 | 28.9 | 23.5 | 16.6 | 0.0755 | 0.16 | 13.28 | 0
November | 1 | 5PM to 6PM | 50 | 41.4 | 30.9 | 25.8 | 15.99 | 0.0761 | 0.17 | 13.19 | 1
November | 1 | 6PM to 7PM | 50 | 41.4 | 30.9 | 25.8 | 15.99 | 0.0761 | 0.17 | 13.19 | 1
November | 1 | 7PM to 8PM | 48 | 40 | 30 | 24.7 | 15.35 | 0.0764 | 0.16 | 13.13 | 1
November | 1 | 8PM to 9PM | 44.1 | 39.2 | 33.1 | 28.3 | 14.94 | 0.077 | 0.19 | 13.04 | 1
November | 1 | 9PM to 10PM | 42.1 | 38.9 | 35.1 | 30.6 | 14.83 | 0.0773 | 0.2 | 13 | 1
November | 1 | 10PM to 11PM | 43 | 38.2 | 32 | 27.1 | 14.5 | 0.0772 | 0.18 | 13.01 | 1
November | 1 | 11PM to 12AM | 42.1 | 38.1 | 33.1 | 28.3 | 14.47 | 0.0773 | 0.19 | 12.99 | 1
November | 2 | 12AM to 1AM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
November | 2 | 1AM to 2AM | 39.9 | 36.5 | 32 | 27.1 | 13.76 | 0.0776 | 0.18 | 12.93 | 1
November | 2 | 2AM to 3AM | 39 | 36 | 32 | 27.1 | 13.54 | 0.0778 | 0.18 | 12.91 | 1
November | 2 | 3AM to 4AM | 37.9 | 35.8 | 33.1 | 28.3 | 13.46 | 0.0779 | 0.19 | 12.88 | 1
November | 2 | 4AM to 5AM | 37.9 | 35.8 | 33.1 | 28.3 | 13.46 | 0.0779 | 0.19 | 12.88 | 1
November | 2 | 5AM to 6AM | 37.9 | 35.8 | 33.1 | 28.3 | 13.46 | 0.0779 | 0.19 | 12.88 | 1
November | 2 | 6AM to 7AM | 37.9 | 35.8 | 33.1 | 28.3 | 13.46 | 0.0779 | 0.19 | 12.88 | 1
November | 2 | 7AM to 8AM | 39 | 36 | 32 | 27.1 | 13.54 | 0.0778 | 0.18 | 12.91 | 1
November | 2 | 8AM to 9AM | 43 | 38.9 | 34 | 29.3 | 14.84 | 0.0771 | 0.2 | 13.02 | 1
November | 2 | 9AM to 10AM | 45 | 40 | 34 | 29.3 | 15.32 | 0.0768 | 0.2 | 13.07 | 1
November | 2 | 10AM to 11AM | 50 | 42.2 | 33.1 | 28.3 | 16.38 | 0.0761 | 0.19 | 13.2 | 1
November | 2 | 11AM to 12PM | 52 | 42.4 | 30.9 | 25.8 | 16.47 | 0.0758 | 0.17 | 13.24 | 0
November | 2 | 12PM to 1PM | 54 | 41.7 | 26.1 | 20.5 | 16.14 | 0.0756 | 0.14 | 13.27 | 0
November | 2 | 1PM to 2PM | 54 | 41.1 | 24.1 | 18.7 | 15.85 | 0.0756 | 0.12 | 13.27 | 0
November | 2 | 2PM to 3PM | 54 | 41.1 | 24.1 | 18.7 | 15.85 | 0.0756 | 0.12 | 13.27 | 0
November | 2 | 3PM to 4PM | 51.1 | 38.8 | 21 | 16.2 | 14.76 | 0.076 | 0.11 | 13.19 | 1
November | 2 | 4PM to 5PM | 51.1 | 39 | 21.9 | 16.9 | 14.87 | 0.076 | 0.11 | 13.19 | 1
November | 2 | 5PM to 6PM | 45 | 36.6 | 25 | 19.5 | 13.81 | 0.0769 | 0.13 | 13.04 | 1
November | 2 | 6PM to 7PM | 45 | 36.6 | 25 | 19.5 | 13.81 | 0.0769 | 0.13 | 13.04 | 1
November | 2 | 7PM to 8PM | 44.1 | 36.5 | 26.1 | 20.5 | 13.75 | 0.077 | 0.14 | 13.02 | 1
November | 2 | 8PM to 9PM | 39.9 | 35.7 | 30 | 24.7 | 13.39 | 0.0776 | 0.16 | 12.92 | 1
November | 2 | 9PM to 10PM | 39 | 35.5 | 30.9 | 25.8 | 13.34 | 0.0778 | 0.17 | 12.9 | 1
November | 2 | 10PM to 11PM | 37.9 | 34.6 | 30 | 24.7 | 12.91 | 0.078 | 0.16 | 12.87 | 1
November | 2 | 11PM to 12AM | 37.9 | 33.8 | 28 | 22.5 | 12.58 | 0.078 | 0.15 | 12.87 | 1
November | 3 | 12AM to 1AM | 41 | 34.4 | 25 | 19.5 | 12.85 | 0.0775 | 0.13 | 12.94 | 1
November | 3 | 1AM to 2AM | 42.1 | 34.7 | 24.1 | 18.7 | 12.99 | 0.0774 | 0.12 | 12.96 | 1
November | 3 | 2AM to 3AM | 42.1 | 35 | 25 | 19.5 | 13.11 | 0.0773 | 0.13 | 12.96 | 1
November | 3 | 3AM to 4AM | 43 | 36.2 | 27 | 21.4 | 13.62 | 0.0772 | 0.14 | 12.99 | 1
November | 3 | 4AM to 5AM | 42.1 | 34.7 | 24.1 | 18.7 | 12.99 | 0.0774 | 0.12 | 12.96 | 1
November | 3 | 5AM to 6AM | 39.9 | 35.7 | 30 | 24.7 | 13.39 | 0.0776 | 0.16 | 12.92 | 1
November | 3 | 6AM to 7AM | 39 | 35.5 | 30.9 | 25.8 | 13.34 | 0.0778 | 0.17 | 12.9 | 1
November | 3 | 7AM to 8AM | 41 | 37.5 | 33.1 | 28.3 | 14.2 | 0.0775 | 0.19 | 12.96 | 1
November | 3 | 8AM to 9AM | 44.1 | 40.8 | 37 | 33.2 | 15.69 | 0.077 | 0.22 | 13.06 | 1
November | 3 | 9AM to 10AM | 46.9 | 43.1 | 39 | 35.9 | 16.81 | 0.0765 | 0.24 | 13.14 | 1
November | 3 | 10AM to 11AM | 50 | 44.6 | 39 | 35.9 | 17.55 | 0.076 | 0.24 | 13.22 | 1
November | 3 | 11AM to 12PM | 52 | 44.7 | 37 | 33.2 | 17.61 | 0.0758 | 0.22 | 13.26 | 0
November | 3 | 12PM to 1PM | 54 | 46 | 37.9 | 34.4 | 18.28 | 0.0755 | 0.23 | 13.32 | 0
November | 3 | 1PM to 2PM | 55 | 46.5 | 37.9 | 34.4 | 18.54 | 0.0753 | 0.23 | 13.34 | 0
November | 3 | 2PM to 3PM | 55 | 42.5 | 27 | 21.4 | 16.53 | 0.0754 | 0.14 | 13.31 | 0
November | 3 | 3PM to 4PM | 54 | 42.4 | 28 | 22.5 | 16.45 | 0.0755 | 0.15 | 13.28 | 0
November | 3 | 4PM to 5PM | 51.1 | 40.9 | 28 | 22.5 | 15.75 | 0.076 | 0.15 | 13.21 | 1
November | 3 | 5PM to 6PM | 46 | 38.6 | 28.9 | 23.5 | 14.68 | 0.0767 | 0.16 | 13.08 | 1
November | 3 | 6PM to 7PM | 45 | 38.4 | 30 | 24.7 | 14.61 | 0.0769 | 0.16 | 13.05 | 1
November | 3 | 7PM to 8PM | 42.1 | 37.2 | 30.9 | 25.8 | 14.08 | 0.0773 | 0.17 | 12.98 | 1
November | 3 | 8PM to 9PM | 41 | 37.1 | 32 | 27.1 | 14.02 | 0.0775 | 0.18 | 12.96 | 1
November | 3 | 9PM to 10PM | 37.9 | 35.4 | 32 | 27.1 | 13.28 | 0.0779 | 0.18 | 12.88 | 1
November | 3 | 10PM to 11PM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
November | 3 | 11PM to 12AM | 36 | 34.3 | 32 | 27.1 | 12.8 | 0.0783 | 0.18 | 12.83 | 1
November | 4 | 12AM to 1AM | 36 | 34.3 | 32 | 27.1 | 12.8 | 0.0783 | 0.18 | 12.83 | 1
November | 4 | 1AM to 2AM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
November | 4 | 2AM to 3AM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
November | 4 | 3AM to 4AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
November | 4 | 4AM to 5AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
November | 4 | 5AM to 6AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
November | 4 | 6AM to 7AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
November | 4 | 7AM to 8AM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
November | 4 | 8AM to 9AM | 44.1 | 39.2 | 33.1 | 28.3 | 14.94 | 0.077 | 0.19 | 13.04 | 1
November | 4 | 9AM to 10AM | 48.9 | 41.3 | 32 | 27.1 | 15.93 | 0.0763 | 0.18 | 13.16 | 1
November | 4 | 10AM to 11AM | 53.1 | 43.7 | 33.1 | 28.3 | 17.12 | 0.0756 | 0.19 | 13.27 | 0
November | 4 | 11AM to 12PM | 55 | 44.3 | 32 | 27.1 | 17.41 | 0.0754 | 0.18 | 13.32 | 0
November | 4 | 12PM to 1PM | 57.9 | 45 | 30 | 24.7 | 17.74 | 0.0749 | 0.16 | 13.39 | 0
November | 4 | 1PM to 2PM | 60.1 | 45 | 27 | 21.4 | 17.75 | 0.0747 | 0.14 | 13.44 | 0
November | 4 | 2PM to 3PM | 60.1 | 44.7 | 26.1 | 20.5 | 17.61 | 0.0747 | 0.14 | 13.43 | 0
November | 4 | 3PM to 4PM | 60.1 | 45 | 27 | 21.4 | 17.75 | 0.0747 | 0.14 | 13.44 | 0
November | 4 | 4PM to 5PM | 55.9 | 44.3 | 30.9 | 25.8 | 17.42 | 0.0752 | 0.17 | 13.34 | 0
November | 4 | 5PM to 6PM | 53.1 | 43.7 | 33.1 | 28.3 | 17.12 | 0.0756 | 0.19 | 13.27 | 0
November | 4 | 6PM to 7PM | 53.1 | 43.7 | 33.1 | 28.3 | 17.12 | 0.0756 | 0.19 | 13.27 | 0
November | 4 | 7PM to 8PM | 55 | 44.7 | 33.1 | 28.3 | 17.6 | 0.0753 | 0.19 | 13.33 | 0
November | 4 | 8PM to 9PM | 54 | 44.2 | 33.1 | 28.3 | 17.34 | 0.0755 | 0.19 | 13.3 | 0
November | 4 | 9PM to 10PM | 53.1 | 43.7 | 33.1 | 28.3 | 17.12 | 0.0756 | 0.19 | 13.27 | 0
November | 4 | 10PM to 11PM | 53.1 | 44 | 34 | 29.3 | 17.28 | 0.0756 | 0.2 | 13.28 | 0
November | 4 | 11PM to 12AM | 53.1 | 44.4 | 35.1 | 30.6 | 17.48 | 0.0756 | 0.2 | 13.28 | 0
November | 5 | 12AM to 1AM | 51.1 | 44.3 | 37 | 33.2 | 17.39 | 0.0759 | 0.22 | 13.24 | 1
November | 5 | 1AM to 2AM | 46 | 41.8 | 37 | 33.2 | 16.17 | 0.0767 | 0.22 | 13.11 | 1
November | 5 | 2AM to 3AM | 45 | 41.2 | 37 | 33.2 | 15.91 | 0.0768 | 0.22 | 13.08 | 1
November | 5 | 3AM to 4AM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
November | 5 | 4AM to 5AM | 42.1 | 39.7 | 37 | 33.2 | 15.22 | 0.0773 | 0.22 | 13 | 1
November | 5 | 5AM to 6AM | 42.1 | 39.7 | 37 | 33.2 | 15.22 | 0.0773 | 0.22 | 13 | 1
November | 5 | 6AM to 7AM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
November | 5 | 7AM to 8AM | 45 | 40.8 | 36 | 31.8 | 15.7 | 0.0768 | 0.21 | 13.08 | 1
November | 5 | 8AM to 9AM | 53.1 | 44.4 | 35.1 | 30.6 | 17.48 | 0.0756 | 0.2 | 13.28 | 0
November | 5 | 9AM to 10AM | 55.9 | 45.8 | 35.1 | 30.6 | 18.18 | 0.0752 | 0.2 | 13.36 | 0
November | 5 | 10AM to 11AM | 60.1 | 47.4 | 34 | 29.3 | 18.98 | 0.0746 | 0.2 | 13.46 | 0
November | 5 | 11AM to 12PM | 64 | 49.1 | 34 | 29.3 | 19.94 | 0.074 | 0.2 | 13.56 | 0
November | 5 | 12PM to 1PM | 66 | 49.4 | 32 | 27.1 | 20.07 | 0.0738 | 0.18 | 13.61 | 0
November | 5 | 1PM to 2PM | 66 | 49.7 | 33.1 | 28.3 | 20.25 | 0.0738 | 0.19 | 13.61 | 0
November | 5 | 2PM to 3PM | 66 | 49.4 | 32 | 27.1 | 20.07 | 0.0738 | 0.18 | 13.61 | 0
November | 5 | 3PM to 4PM | 64.9 | 49.2 | 33.1 | 28.3 | 19.99 | 0.0739 | 0.19 | 13.58 | 0
November | 5 | 4PM to 5PM | 64.9 | 49.5 | 34 | 29.3 | 20.16 | 0.0739 | 0.2 | 13.59 | 0
November | 5 | 5PM to 6PM | 64.9 | 49.5 | 34 | 29.3 | 20.16 | 0.0739 | 0.2 | 13.59 | 0
November | 5 | 6PM to 7PM | 64 | 49.5 | 35.1 | 30.6 | 20.14 | 0.074 | 0.2 | 13.57 | 0
November | 5 | 7PM to 8PM | 63 | 49.3 | 36 | 31.8 | 20.05 | 0.0742 | 0.21 | 13.54 | 0
November | 5 | 8PM to 9PM | 62.1 | 49.3 | 37 | 33.2 | 20.05 | 0.0743 | 0.22 | 13.52 | 0
November | 5 | 9PM to 10PM | 61 | 49.2 | 37.9 | 34.4 | 19.98 | 0.0744 | 0.23 | 13.5 | 0
November | 5 | 10PM to 11PM | 62.1 | 50.4 | 39.9 | 37.2 | 20.67 | 0.0743 | 0.25 | 13.54 | 0
November | 5 | 11PM to 12AM | 59 | 51.3 | 45 | 45.2 | 21.18 | 0.0747 | 0.3 | 13.48 | 0
November | 6 | 12AM to 1AM | 57 | 51 | 46 | 47.1 | 21 | 0.0749 | 0.31 | 13.43 | 0
November | 6 | 1AM to 2AM | 55 | 50.6 | 46.9 | 48.8 | 20.77 | 0.0752 | 0.32 | 13.39 | 0
November | 6 | 2AM to 3AM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
November | 6 | 3AM to 4AM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
November | 6 | 4AM to 5AM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
November | 6 | 5AM to 6AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
November | 6 | 6AM to 7AM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
November | 6 | 7AM to 8AM | 44.1 | 41.6 | 39 | 35.9 | 16.11 | 0.0769 | 0.24 | 13.06 | 1
November | 6 | 8AM to 9AM | 44.1 | 41.6 | 39 | 35.9 | 16.11 | 0.0769 | 0.24 | 13.06 | 1
November | 6 | 9AM to 10AM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
November | 6 | 10AM to 11AM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
November | 6 | 11AM to 12PM | 43 | 39.7 | 36 | 31.8 | 15.22 | 0.0771 | 0.21 | 13.02 | 1
November | 6 | 12PM to 1PM | 42.1 | 38.9 | 35.1 | 30.6 | 14.83 | 0.0773 | 0.2 | 13 | 1
November | 6 | 1PM to 2PM | 42.1 | 38.9 | 35.1 | 30.6 | 14.83 | 0.0773 | 0.2 | 13 | 1
November | 6 | 2PM to 3PM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
November | 6 | 3PM to 4PM | 41 | 37.5 | 33.1 | 28.3 | 14.2 | 0.0775 | 0.19 | 12.96 | 1
November | 6 | 4PM to 5PM | 41 | 37.5 | 33.1 | 28.3 | 14.2 | 0.0775 | 0.19 | 12.96 | 1
November | 6 | 5PM to 6PM | 39.9 | 36.9 | 33.1 | 28.3 | 13.94 | 0.0776 | 0.19 | 12.93 | 1
November | 6 | 6PM to 7PM | 39.9 | 36.9 | 33.1 | 28.3 | 13.94 | 0.0776 | 0.19 | 12.93 | 1
November | 6 | 7PM to 8PM | 39 | 36 | 32 | 27.1 | 13.54 | 0.0778 | 0.18 | 12.91 | 1
November | 6 | 8PM to 9PM | 39 | 36 | 32 | 27.1 | 13.54 | 0.0778 | 0.18 | 12.91 | 1
November | 6 | 9PM to 10PM | 39 | 35.2 | 30 | 24.7 | 13.17 | 0.0778 | 0.16 | 12.9 | 1
November | 6 | 10PM to 11PM | 39 | 35.2 | 30 | 24.7 | 13.17 | 0.0778 | 0.16 | 12.9 | 1
November | 6 | 11PM to 12AM | 37.9 | 34.1 | 28.9 | 23.5 | 12.73 | 0.078 | 0.16 | 12.87 | 1
November | 7 | 12AM to 1AM | 35.1 | 32.1 | 28 | 22.5 | 11.88 | 0.0784 | 0.15 | 12.79 | 1
November | 7 | 1AM to 2AM | 34 | 31.3 | 28 | 22.5 | 11.62 | 0.0786 | 0.15 | 12.76 | 1
November | 7 | 2AM to 3AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
November | 7 | 3AM to 4AM | 32 | 30.6 | 28.9 | 23.5 | 11.29 | 0.0789 | 0.16 | 12.72 | 1
November | 7 | 4AM to 5AM | 30 | 30 | 30 | 24.7 | 11 | 0.0792 | 0.16 | 12.67 | 1
November | 7 | 5AM to 6AM | 30 | 30 | 30 | 24.7 | 11 | 0.0792 | 0.16 | 12.67 | 1
November | 7 | 6AM to 7AM | 30 | 30 | 30 | 24.7 | 11 | 0.0792 | 0.16 | 12.67 | 1
November | 7 | 7AM to 8AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
November | 7 | 8AM to 9AM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
November | 7 | 9AM to 10AM | 39.9 | 35.7 | 30 | 24.7 | 13.39 | 0.0776 | 0.16 | 12.92 | 1
November | 7 | 10AM to 11AM | 42.1 | 36.9 | 30 | 24.7 | 13.91 | 0.0773 | 0.16 | 12.98 | 1
November | 7 | 11AM to 12PM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
November | 7 | 12PM to 1PM | 45 | 38 | 28.9 | 23.5 | 14.42 | 0.0769 | 0.16 | 13.05 | 1
November | 7 | 1PM to 2PM | 46.9 | 38.7 | 28 | 22.5 | 14.75 | 0.0766 | 0.15 | 13.1 | 1
November | 7 | 2PM to 3PM | 46.9 | 38.7 | 28 | 22.5 | 14.75 | 0.0766 | 0.15 | 13.1 | 1
November | 7 | 3PM to 4PM | 46.9 | 39.1 | 28.9 | 23.5 | 14.9 | 0.0766 | 0.16 | 13.1 | 1
November | 7 | 4PM to 5PM | 46.9 | 39.1 | 28.9 | 23.5 | 14.9 | 0.0766 | 0.16 | 13.1 | 1
November | 7 | 5PM to 6PM | 46.9 | 39.1 | 28.9 | 23.5 | 14.9 | 0.0766 | 0.16 | 13.1 | 1
November | 7 | 6PM to 7PM | 46.9 | 39.5 | 30 | 24.7 | 15.09 | 0.0766 | 0.16 | 13.11 | 1
November | 7 | 7PM to 8PM | 44.1 | 40.8 | 37 | 33.2 | 15.69 | 0.077 | 0.22 | 13.06 | 1
November | 7 | 8PM to 9PM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
November | 7 | 9PM to 10PM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
November | 7 | 10PM to 11PM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
November | 7 | 11PM to 12AM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
November | 8 | 12AM to 1AM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
November | 8 | 1AM to 2AM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
November | 8 | 2AM to 3AM | 43 | 42.5 | 42.1 | 40.4 | 16.55 | 0.0771 | 0.27 | 13.05 | 1
November | 8 | 3AM to 4AM | 43 | 42 | 41 | 38.8 | 16.3 | 0.0771 | 0.26 | 13.04 | 1
November | 8 | 4AM to 5AM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
November | 8 | 5AM to 6AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
November | 8 | 6AM to 7AM | 44.1 | 43.1 | 42.1 | 40.4 | 16.82 | 0.0769 | 0.27 | 13.08 | 1
November | 8 | 7AM to 8AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
November | 8 | 8AM to 9AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
November | 8 | 9AM to 10AM | 45 | 44 | 43 | 41.9 | 17.26 | 0.0768 | 0.28 | 13.11 | 1
November | 8 | 10AM to 11AM | 46 | 44.5 | 43 | 41.9 | 17.52 | 0.0766 | 0.28 | 13.13 | 1
November | 8 | 11AM to 12PM | 46 | 44 | 42.1 | 40.4 | 17.3 | 0.0766 | 0.27 | 13.13 | 1
November | 8 | 12PM to 1PM | 46 | 44 | 42.1 | 40.4 | 17.3 | 0.0766 | 0.27 | 13.13 | 1
November | 8 | 1PM to 2PM | 46 | 44 | 42.1 | 40.4 | 17.3 | 0.0766 | 0.27 | 13.13 | 1
November | 8 | 2PM to 3PM | 46 | 44.5 | 43 | 41.9 | 17.52 | 0.0766 | 0.28 | 13.13 | 1
November | 8 | 3PM to 4PM | 46 | 44.5 | 43 | 41.9 | 17.52 | 0.0766 | 0.28 | 13.13 | 1
November | 8 | 4PM to 5PM | 46.9 | 44.9 | 43 | 41.9 | 17.74 | 0.0765 | 0.28 | 13.16 | 1
November | 8 | 5PM to 6PM | 46 | 44.5 | 43 | 41.9 | 17.52 | 0.0766 | 0.28 | 13.13 | 1
November | 8 | 6PM to 7PM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
November | 8 | 7PM to 8PM | 46 | 45 | 44.1 | 43.6 | 17.8 | 0.0766 | 0.29 | 13.14 | 1
November | 8 | 8PM to 9PM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
November | 8 | 9PM to 10PM | 46 | 45.5 | 45 | 45.2 | 18.03 | 0.0766 | 0.3 | 13.14 | 1
November | 8 | 10PM to 11PM | 45 | 45 | 45 | 45.2 | 17.77 | 0.0767 | 0.3 | 13.12 | 1
November | 8 | 11PM to 12AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 12AM to 1AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 1AM to 2AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 2AM to 3AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 3AM to 4AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 4AM to 5AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 5AM to 6AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 6AM to 7AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 7AM to 8AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 8AM to 9AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 9AM to 10AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 9 | 10AM to 11AM | 46.9 | 46.9 | 46.9 | 48.8 | 18.8 | 0.0764 | 0.32 | 13.18 | 1
November | 9 | 11AM to 12PM | 46.9 | 46.5 | 46 | 47.1 | 18.55 | 0.0764 | 0.31 | 13.17 | 1
November | 9 | 12PM to 1PM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
November | 9 | 1PM to 2PM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
November | 9 | 2PM to 3PM | 48.9 | 47.4 | 46 | 47.1 | 19.03 | 0.0761 | 0.31 | 13.22 | 1
November | 9 | 3PM to 4PM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
November | 9 | 4PM to 5PM | 45 | 44.5 | 44.1 | 43.6 | 17.53 | 0.0767 | 0.29 | 13.11 | 1
November | 9 | 5PM to 6PM | 44.1 | 43.5 | 43 | 41.9 | 17.04 | 0.0769 | 0.28 | 13.08 | 1
November | 9 | 6PM to 7PM | 43 | 42.5 | 42.1 | 40.4 | 16.55 | 0.0771 | 0.27 | 13.05 | 1
November | 9 | 7PM to 8PM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
November | 9 | 8PM to 9PM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 9 | 9PM to 10PM | 36 | 31.9 | 27 | 21.4 | 11.93 | 0.0783 | 0.14 | 12.81 | 1
November | 9 | 10PM to 11PM | 34 | 30.5 | 26.1 | 20.5 | 11.31 | 0.0786 | 0.14 | 12.76 | 1
November | 9 | 11PM to 12AM | 33.1 | 30.4 | 27 | 21.4 | 11.23 | 0.0787 | 0.14 | 12.74 | 1
November | 10 | 12AM to 1AM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
November | 10 | 1AM to 2AM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
November | 10 | 2AM to 3AM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
November | 10 | 3AM to 4AM | 32 | 30.6 | 28.9 | 23.5 | 11.29 | 0.0789 | 0.16 | 12.72 | 1
November | 10 | 4AM to 5AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
November | 10 | 5AM to 6AM | 33.1 | 30.8 | 28 | 22.5 | 11.4 | 0.0787 | 0.15 | 12.74 | 1
November | 10 | 6AM to 7AM | 33.1 | 30.8 | 28 | 22.5 | 11.4 | 0.0787 | 0.15 | 12.74 | 1
November | 10 | 7AM to 8AM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
November | 10 | 8AM to 9AM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
November | 10 | 9AM to 10AM | 32 | 29.4 | 26.1 | 20.5 | 10.84 | 0.0789 | 0.14 | 12.71 | 1
November | 10 | 10AM to 11AM | 32 | 29 | 25 | 19.5 | 10.68 | 0.0789 | 0.13 | 12.7 | 1
November | 10 | 11AM to 12PM | 32 | 29 | 25 | 19.5 | 10.68 | 0.0789 | 0.13 | 12.7 | 1
November | 10 | 12PM to 1PM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
November | 10 | 1PM to 2PM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
November | 10 | 2PM to 3PM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
November | 10 | 3PM to 4PM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
November | 10 | 4PM to 5PM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
November | 10 | 5PM to 6PM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
November | 10 | 6PM to 7PM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
November | 10 | 7PM to 8PM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
November | 10 | 8PM to 9PM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
November | 10 | 9PM to 10PM | 27 | 25.4 | 23 | 17.8 | 9.2 | 0.0798 | 0.12 | 12.57 | 1
November | 10 | 10PM to 11PM | 27 | 24.7 | 21 | 16.2 | 8.95 | 0.0798 | 0.11 | 12.56 | 1
November | 10 | 11PM to 12AM | 26.1 | 24.9 | 23 | 17.8 | 8.98 | 0.0799 | 0.12 | 12.55 | 1
November | 11 | 12AM to 1AM | 26.1 | 24.5 | 21.9 | 16.9 | 8.84 | 0.0799 | 0.11 | 12.54 | 1
November | 11 | 1AM to 2AM | 24.1 | 23.7 | 23 | 17.8 | 8.5 | 0.0802 | 0.12 | 12.49 | 1
November | 11 | 2AM to 3AM | 24.1 | 23.7 | 23 | 17.8 | 8.5 | 0.0802 | 0.12 | 12.49 | 1
November | 11 | 3AM to 4AM | 24.1 | 23.7 | 23 | 17.8 | 8.5 | 0.0802 | 0.12 | 12.49 | 1
November | 11 | 4AM to 5AM | 23 | 22.6 | 21.9 | 16.9 | 8.1 | 0.0804 | 0.11 | 12.46 | 1
November | 11 | 5AM to 6AM | 23 | 23 | 23 | 17.8 | 8.24 | 0.0804 | 0.12 | 12.47 | 1
November | 11 | 6AM to 7AM | 23 | 22.6 | 21.9 | 16.9 | 8.1 | 0.0804 | 0.11 | 12.46 | 1
November | 11 | 7AM to 8AM | 25 | 24.6 | 24.1 | 18.7 | 8.86 | 0.0801 | 0.12 | 12.52 | 1
November | 11 | 8AM to 9AM | 28.9 | 26.6 | 23 | 17.8 | 9.67 | 0.0794 | 0.12 | 12.62 | 1
November | 11 | 9AM to 10AM | 32 | 28 | 21.9 | 16.9 | 10.27 | 0.079 | 0.11 | 12.7 | 1
November | 11 | 10AM to 11AM | 34 | 29.1 | 21.9 | 16.9 | 10.75 | 0.0786 | 0.11 | 12.75 | 1
November | 11 | 11AM to 12PM | 36 | 30.5 | 23 | 17.8 | 11.37 | 0.0783 | 0.12 | 12.8 | 1
November | 11 | 12PM to 1PM | 37.9 | 31.6 | 23 | 17.8 | 11.84 | 0.078 | 0.12 | 12.85 | 1
November | 11 | 1PM to 2PM | 41 | 33.8 | 23 | 17.8 | 12.58 | 0.0775 | 0.12 | 12.93 | 1
November | 11 | 2PM to 3PM | 42.1 | 34.4 | 23 | 17.8 | 12.84 | 0.0774 | 0.12 | 12.96 | 1
November | 11 | 3PM to 4PM | 42.1 | 34.4 | 23 | 17.8 | 12.84 | 0.0774 | 0.12 | 12.96 | 1
November | 11 | 4PM to 5PM | 39.9 | 33.5 | 24.1 | 18.7 | 12.47 | 0.0777 | 0.12 | 12.91 | 1
November | 11 | 5PM to 6PM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
November | 11 | 6PM to 7PM | 34 | 30.5 | 26.1 | 20.5 | 11.31 | 0.0786 | 0.14 | 12.76 | 1
November | 11 | 7PM to 8PM | 34 | 30.5 | 26.1 | 20.5 | 11.31 | 0.0786 | 0.14 | 12.76 | 1
November | 11 | 8PM to 9PM | 33.1 | 30 | 26.1 | 20.5 | 11.1 | 0.0788 | 0.14 | 12.74 | 1
November | 11 | 9PM to 10PM | 30.9 | 28.8 | 26.1 | 20.5 | 10.58 | 0.0791 | 0.14 | 12.68 | 1
November | 11 | 10PM to 11PM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
November | 11 | 11PM to 12AM | 30 | 28.7 | 27 | 21.4 | 10.5 | 0.0792 | 0.14 | 12.66 | 1
November | 12 | 12AM to 1AM | 30 | 28.7 | 27 | 21.4 | 10.5 | 0.0792 | 0.14 | 12.66 | 1
November | 12 | 1AM to 2AM | 30 | 28.3 | 26.1 | 20.5 | 10.36 | 0.0792 | 0.14 | 12.66 | 1
November | 12 | 2AM to 3AM | 28.9 | 27.7 | 26.1 | 20.5 | 10.1 | 0.0794 | 0.14 | 12.63 | 1
November | 12 | 3AM to 4AM | 27 | 26.6 | 26.1 | 20.5 | 9.62 | 0.0797 | 0.14 | 12.58 | 1
November | 12 | 4AM to 5AM | 27 | 26.6 | 26.1 | 20.5 | 9.62 | 0.0797 | 0.14 | 12.58 | 1
November | 12 | 5AM to 6AM | 26.1 | 25.6 | 25 | 19.5 | 9.25 | 0.0799 | 0.13 | 12.55 | 1
November | 12 | 6AM to 7AM | 27 | 26.6 | 26.1 | 20.5 | 9.62 | 0.0797 | 0.14 | 12.58 | 1
November | 12 | 7AM to 8AM | 28 | 28 | 28 | 22.5 | 10.19 | 0.0796 | 0.15 | 12.61 | 1
November | 12 | 8AM to 9AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
November | 12 | 9AM to 10AM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
November | 12 | 10AM to 11AM | 39 | 35.2 | 30 | 24.7 | 13.17 | 0.0778 | 0.16 | 12.9 | 1
November | 12 | 11AM to 12PM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
November | 12 | 12PM to 1PM | 46.9 | 39.1 | 28.9 | 23.5 | 14.9 | 0.0766 | 0.16 | 13.1 | 1
November | 12 | 1PM to 2PM | 48 | 40.4 | 30.9 | 25.8 | 15.51 | 0.0764 | 0.17 | 13.14 | 1
November | 12 | 2PM to 3PM | 46 | 39.3 | 30.9 | 25.8 | 15.03 | 0.0767 | 0.17 | 13.09 | 1
November | 12 | 3PM to 4PM | 45 | 37.7 | 28 | 22.5 | 14.27 | 0.0769 | 0.15 | 13.05 | 1
November | 12 | 4PM to 5PM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
November | 12 | 5PM to 6PM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
November | 12 | 6PM to 7PM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
November | 12 | 7PM to 8PM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
November | 12 | 8PM to 9PM | 42.1 | 37.7 | 32 | 27.1 | 14.28 | 0.0773 | 0.18 | 12.99 | 1
November | 12 | 9PM to 10PM | 43 | 38.2 | 32 | 27.1 | 14.5 | 0.0772 | 0.18 | 13.01 | 1
November | 12 | 10PM to 11PM | 42.1 | 38.1 | 33.1 | 28.3 | 14.47 | 0.0773 | 0.19 | 12.99 | 1
November | 12 | 11PM to 12AM | 41 | 38.3 | 35.1 | 30.6 | 14.57 | 0.0774 | 0.2 | 12.97 | 1
November | 13 | 12AM to 1AM | 39.9 | 39.5 | 39 | 35.9 | 15.11 | 0.0776 | 0.24 | 12.96 | 1
November | 13 | 1AM to 2AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
November | 13 | 2AM to 3AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
November | 13 | 3AM to 4AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
November | 13 | 4AM to 5AM | 37 | 37 | 37 | 33.2 | 14 | 0.078 | 0.22 | 12.87 | 1
November | 13 | 5AM to 6AM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
November | 13 | 6AM to 7AM | 37 | 35.7 | 34 | 29.3 | 13.41 | 0.0781 | 0.2 | 12.86 | 1
November | 13 | 7AM to 8AM | 37 | 35.7 | 34 | 29.3 | 13.41 | 0.0781 | 0.2 | 12.86 | 1
November | 13 | 8AM to 9AM | 37 | 35.7 | 34 | 29.3 | 13.41 | 0.0781 | 0.2 | 12.86 | 1
November | 13 | 9AM to 10AM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
November | 13 | 10AM to 11AM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
November | 13 | 11AM to 12PM | 39.9 | 36 | 30.9 | 25.8 | 13.55 | 0.0776 | 0.17 | 12.93 | 1
November | 13 | 12PM to 1PM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
November | 13 | 1PM to 2PM | 45 | 38.8 | 30.9 | 25.8 | 14.77 | 0.0769 | 0.17 | 13.06 | 1
November | 13 | 2PM to 3PM | 46 | 38.3 | 28 | 22.5 | 14.53 | 0.0767 | 0.15 | 13.08 | 1
November | 13 | 3PM to 4PM | 45 | 37.7 | 28 | 22.5 | 14.27 | 0.0769 | 0.15 | 13.05 | 1
November | 13 | 4PM to 5PM | 43 | 36.2 | 27 | 21.4 | 13.62 | 0.0772 | 0.14 | 12.99 | 1
November | 13 | 5PM to 6PM | 39.9 | 35.2 | 28.9 | 23.5 | 13.21 | 0.0777 | 0.16 | 12.92 | 1
November | 13 | 6PM to 7PM | 39 | 34.7 | 28.9 | 23.5 | 12.99 | 0.0778 | 0.16 | 12.9 | 1
November | 13 | 7PM to 8PM | 37 | 33.6 | 28.9 | 23.5 | 12.51 | 0.0781 | 0.16 | 12.85 | 1
November | 13 | 8PM to 9PM | 36 | 33.4 | 30 | 24.7 | 12.43 | 0.0783 | 0.16 | 12.82 | 1
November | 13 | 9PM to 10PM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
November | 13 | 10PM to 11PM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
November | 13 | 11PM to 12AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
November | 14 | 12AM to 1AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
November | 14 | 1AM to 2AM | 28.9 | 28.9 | 28.9 | 23.5 | 10.55 | 0.0794 | 0.16 | 12.64 | 1
November | 14 | 2AM to 3AM | 28.9 | 28.9 | 28.9 | 23.5 | 10.55 | 0.0794 | 0.16 | 12.64 | 1
November | 14 | 3AM to 4AM | 28.9 | 28.9 | 28.9 | 23.5 | 10.55 | 0.0794 | 0.16 | 12.64 | 1
November | 14 | 4AM to 5AM | 28 | 28 | 28 | 22.5 | 10.19 | 0.0796 | 0.15 | 12.61 | 1
November | 14 | 5AM to 6AM | 28.9 | 28.9 | 28.9 | 23.5 | 10.55 | 0.0794 | 0.16 | 12.64 | 1
November | 14 | 6AM to 7AM | 28.9 | 28.5 | 28 | 22.5 | 10.41 | 0.0794 | 0.15 | 12.63 | 1
November | 14 | 7AM to 8AM | 33.1 | 32.1 | 30.9 | 25.8 | 11.9 | 0.0787 | 0.17 | 12.75 | 1
November | 14 | 8AM to 9AM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
November | 14 | 9AM to 10AM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
November | 14 | 10AM to 11AM | 45 | 38.8 | 30.9 | 25.8 | 14.77 | 0.0769 | 0.17 | 13.06 | 1
November | 14 | 11AM to 12PM | 48 | 40 | 30 | 24.7 | 15.35 | 0.0764 | 0.16 | 13.13 | 1
November | 14 | 12PM to 1PM | 50 | 41.1 | 30 | 24.7 | 15.83 | 0.0761 | 0.16 | 13.18 | 1
November | 14 | 1PM to 2PM | 52 | 42.4 | 30.9 | 25.8 | 16.47 | 0.0758 | 0.17 | 13.24 | 0
November | 14 | 2PM to 3PM | 53.1 | 42.6 | 30 | 24.7 | 16.57 | 0.0757 | 0.16 | 13.26 | 0
November | 14 | 3PM to 4PM | 54 | 43 | 30 | 24.7 | 16.78 | 0.0755 | 0.16 | 13.29 | 0
November | 14 | 4PM to 5PM | 52 | 41.7 | 28.9 | 23.5 | 16.12 | 0.0758 | 0.16 | 13.23 | 0
November | 14 | 5PM to 6PM | 48.9 | 39.4 | 27 | 21.4 | 15.06 | 0.0763 | 0.14 | 13.15 | 1
November | 14 | 6PM to 7PM | 46 | 38.6 | 28.9 | 23.5 | 14.68 | 0.0767 | 0.16 | 13.08 | 1
November | 14 | 7PM to 8PM | 42.1 | 37.7 | 32 | 27.1 | 14.28 | 0.0773 | 0.18 | 12.99 | 1
November | 14 | 8PM to 9PM | 41 | 37.1 | 32 | 27.1 | 14.02 | 0.0775 | 0.18 | 12.96 | 1
November | 14 | 9PM to 10PM | 42.1 | 36.9 | 30 | 24.7 | 13.91 | 0.0773 | 0.16 | 12.98 | 1
November | 14 | 10PM to 11PM | 43 | 36.6 | 28 | 22.5 | 13.79 | 0.0772 | 0.15 | 13 | 1
November | 14 | 11PM to 12AM | 42.1 | 36.1 | 28 | 22.5 | 13.58 | 0.0773 | 0.15 | 12.97 | 1
November | 15 | 12AM to 1AM | 42.1 | 36.9 | 30 | 24.7 | 13.91 | 0.0773 | 0.16 | 12.98 | 1
November | 15 | 1AM to 2AM | 42.1 | 35.4 | 26.1 | 20.5 | 13.27 | 0.0773 | 0.14 | 12.97 | 1
November | 15 | 2AM to 3AM | 39.9 | 34.5 | 27 | 21.4 | 12.88 | 0.0777 | 0.14 | 12.91 | 1
November | 15 | 3AM to 4AM | 39 | 34 | 27 | 21.4 | 12.67 | 0.0778 | 0.14 | 12.89 | 1
November | 15 | 4AM to 5AM | 39 | 34.4 | 28 | 22.5 | 12.84 | 0.0778 | 0.15 | 12.89 | 1
November | 15 | 5AM to 6AM | 39.9 | 34.9 | 28 | 22.5 | 13.06 | 0.0777 | 0.15 | 12.92 | 1
November | 15 | 6AM to 7AM | 41 | 36.3 | 30 | 24.7 | 13.65 | 0.0775 | 0.16 | 12.95 | 1
November | 15 | 7AM to 8AM | 43 | 37.7 | 30.9 | 25.8 | 14.29 | 0.0772 | 0.17 | 13.01 | 1
November | 15 | 8AM to 9AM | 42.1 | 40.1 | 37.9 | 34.4 | 15.4 | 0.0772 | 0.23 | 13.01 | 1
November | 15 | 9AM to 10AM | 51.1 | 43.1 | 34 | 29.3 | 16.8 | 0.0759 | 0.2 | 13.23 | 1
November | 15 | 10AM to 11AM | 55.9 | 45.8 | 35.1 | 30.6 | 18.18 | 0.0752 | 0.2 | 13.36 | 0
November | 15 | 11AM to 12PM | 57.9 | 47.1 | 36 | 31.8 | 18.83 | 0.0749 | 0.21 | 13.41 | 0
November | 15 | 12PM to 1PM | 62.1 | 48.9 | 36 | 31.8 | 19.84 | 0.0743 | 0.21 | 13.52 | 0
November | 15 | 1PM to 2PM | 64.9 | 49.5 | 34 | 29.3 | 20.16 | 0.0739 | 0.2 | 13.59 | 0
November | 15 | 2PM to 3PM | 66 | 50.4 | 35.1 | 30.6 | 20.62 | 0.0738 | 0.2 | 13.62 | 0
November | 15 | 3PM to 4PM | 64.9 | 49.9 | 35.1 | 30.6 | 20.36 | 0.0739 | 0.2 | 13.59 | 0
November | 15 | 4PM to 5PM | 61 | 48.5 | 36 | 31.8 | 19.57 | 0.0745 | 0.21 | 13.49 | 0
November | 15 | 5PM to 6PM | 57.9 | 47.5 | 37 | 33.2 | 19.05 | 0.0749 | 0.22 | 13.42 | 0
November | 15 | 6PM to 7PM | 54 | 46.4 | 39 | 35.9 | 18.51 | 0.0755 | 0.24 | 13.32 | 0
November | 15 | 7PM to 8PM | 51.1 | 44.6 | 37.9 | 34.4 | 17.58 | 0.0759 | 0.23 | 13.24 | 1
November | 15 | 8PM to 9PM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
November | 15 | 9PM to 10PM | 48 | 42.3 | 36 | 31.8 | 16.44 | 0.0764 | 0.21 | 13.15 | 1
November | 15 | 10PM to 11PM | 45 | 41.2 | 37 | 33.2 | 15.91 | 0.0768 | 0.22 | 13.08 | 1
November | 15 | 11PM to 12AM | 45 | 41.6 | 37.9 | 34.4 | 16.1 | 0.0768 | 0.23 | 13.08 | 1
November | 16 | 12AM to 1AM | 42.1 | 39.7 | 37 | 33.2 | 15.22 | 0.0773 | 0.22 | 13 | 1
November | 16 | 1AM to 2AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
November | 16 | 2AM to 3AM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
November | 16 | 3AM to 4AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
November | 16 | 4AM to 5AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
November | 16 | 5AM to 6AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
November | 16 | 6AM to 7AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
November | 16 | 7AM to 8AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
November | 16 | 8AM to 9AM | 39 | 37.2 | 35.1 | 30.6 | 14.09 | 0.0777 | 0.2 | 12.92 | 1
November | 16 | 9AM to 10AM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
November | 16 | 10AM to 11AM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
November | 16 | 11AM to 12PM | 52 | 45.9 | 39.9 | 37.2 | 18.23 | 0.0757 | 0.25 | 13.27 | 0
November | 16 | 12PM to 1PM | 55 | 47.3 | 39.9 | 37.2 | 18.97 | 0.0753 | 0.25 | 13.35 | 0
November | 16 | 1PM to 2PM | 57.9 | 48.6 | 39.9 | 37.2 | 19.67 | 0.0749 | 0.25 | 13.43 | 0
November | 16 | 2PM to 3PM | 59 | 48.7 | 39 | 35.9 | 19.73 | 0.0747 | 0.24 | 13.45 | 0
November | 16 | 3PM to 4PM | 59 | 48 | 37 | 33.2 | 19.31 | 0.0747 | 0.22 | 13.44 | 0
November | 16 | 4PM to 5PM | 54 | 46.8 | 39.9 | 37.2 | 18.71 | 0.0754 | 0.25 | 13.33 | 0
November | 16 | 5PM to 6PM | 53.1 | 46.9 | 41 | 38.8 | 18.74 | 0.0756 | 0.26 | 13.31 | 0
November | 16 | 6PM to 7PM | 53.1 | 46.9 | 41 | 38.8 | 18.74 | 0.0756 | 0.26 | 13.31 | 0
November | 16 | 7PM to 8PM | 51.1 | 45.9 | 41 | 38.8 | 18.26 | 0.0759 | 0.26 | 13.26 | 1
November | 16 | 8PM to 9PM | 50 | 45.4 | 41 | 38.8 | 18 | 0.076 | 0.26 | 13.23 | 1
November | 16 | 9PM to 10PM | 46 | 43.5 | 41 | 38.8 | 17.04 | 0.0766 | 0.26 | 13.12 | 1
November | 16 | 10PM to 11PM | 46.9 | 44 | 41 | 38.8 | 17.26 | 0.0765 | 0.26 | 13.15 | 1
November | 16 | 11PM to 12AM | 46.9 | 43.5 | 39.9 | 37.2 | 17.01 | 0.0765 | 0.25 | 13.14 | 1
November | 17 | 12AM to 1AM | 46 | 43.5 | 41 | 38.8 | 17.04 | 0.0766 | 0.26 | 13.12 | 1
November | 17 | 1AM to 2AM | 45 | 43 | 41 | 38.8 | 16.78 | 0.0768 | 0.26 | 13.1 | 1
November | 17 | 2AM to 3AM | 48 | 44.5 | 41 | 38.8 | 17.52 | 0.0763 | 0.26 | 13.18 | 1
November | 17 | 3AM to 4AM | 48.9 | 44.9 | 41 | 38.8 | 17.74 | 0.0762 | 0.26 | 13.2 | 1
November | 17 | 4AM to 5AM | 48.9 | 44.9 | 41 | 38.8 | 17.74 | 0.0762 | 0.26 | 13.2 | 1
November | 17 | 5AM to 6AM | 48 | 44.5 | 41 | 38.8 | 17.52 | 0.0763 | 0.26 | 13.18 | 1
November | 17 | 6AM to 7AM | 48.9 | 44 | 39 | 35.9 | 17.29 | 0.0762 | 0.24 | 13.19 | 1
November | 17 | 7AM to 8AM | 52 | 45.5 | 39 | 35.9 | 18.03 | 0.0757 | 0.24 | 13.27 | 0
November | 17 | 8AM to 9AM | 55.9 | 46.9 | 37.9 | 34.4 | 18.76 | 0.0752 | 0.23 | 13.37 | 0
November | 17 | 9AM to 10AM | 62.1 | 49.7 | 37.9 | 34.4 | 20.24 | 0.0743 | 0.23 | 13.53 | 0
November | 17 | 10AM to 11AM | 68 | 52.2 | 37.9 | 34.4 | 21.68 | 0.0735 | 0.23 | 13.68 | 0
November | 17 | 11AM to 12PM | 70 | 52.7 | 37 | 33.2 | 21.97 | 0.0732 | 0.22 | 13.73 | 0
November | 17 | 12PM to 1PM | 72 | 53.2 | 36 | 31.8 | 22.23 | 0.0729 | 0.21 | 13.78 | 0
November | 17 | 1PM to 2PM | 73.9 | 53.7 | 35.1 | 30.6 | 22.54 | 0.0727 | 0.2 | 13.82 | 0
November | 17 | 2PM to 3PM | 73 | 53.3 | 35.1 | 30.6 | 22.32 | 0.0728 | 0.2 | 13.8 | 0
November | 17 | 3PM to 4PM | 72 | 52.9 | 35.1 | 30.6 | 22.06 | 0.0729 | 0.2 | 13.77 | 0
November | 17 | 4PM to 5PM | 68 | 51.2 | 35.1 | 30.6 | 21.1 | 0.0735 | 0.2 | 13.67 | 0
November | 17 | 5PM to 6PM | 66 | 50.7 | 36 | 31.8 | 20.79 | 0.0737 | 0.21 | 13.62 | 0
November | 17 | 6PM to 7PM | 64 | 50.2 | 37 | 33.2 | 20.53 | 0.074 | 0.22 | 13.57 | 0
November | 17 | 7PM to 8PM | 62.1 | 47.6 | 32 | 27.1 | 19.11 | 0.0743 | 0.18 | 13.5 | 0
November | 17 | 8PM to 9PM | 60.1 | 49.6 | 39.9 | 37.2 | 20.19 | 0.0746 | 0.25 | 13.48 | 0
November | 17 | 9PM to 10PM | 57.9 | 49.1 | 41 | 38.8 | 19.92 | 0.0749 | 0.26 | 13.43 | 0
November | 17 | 10PM to 11PM | 57 | 48.7 | 41 | 38.8 | 19.7 | 0.075 | 0.26 | 13.41 | 0
November | 17 | 11PM to 12AM | 55 | 47.8 | 41 | 38.8 | 19.22 | 0.0753 | 0.26 | 13.36 | 0
November | 18 | 12AM to 1AM | 55.9 | 48.7 | 42.1 | 40.4 | 19.7 | 0.0751 | 0.27 | 13.39 | 0
November | 18 | 1AM to 2AM | 55 | 48.2 | 42.1 | 40.4 | 19.48 | 0.0753 | 0.27 | 13.36 | 0
November | 18 | 2AM to 3AM | 55 | 48.2 | 42.1 | 40.4 | 19.48 | 0.0753 | 0.27 | 13.36 | 0
November | 18 | 3AM to 4AM | 55 | 48.2 | 42.1 | 40.4 | 19.48 | 0.0753 | 0.27 | 13.36 | 0
November | 18 | 4AM to 5AM | 52 | 46.9 | 42.1 | 40.4 | 18.74 | 0.0757 | 0.27 | 13.28 | 0
November | 18 | 5AM to 6AM | 50 | 45.9 | 42.1 | 40.4 | 18.26 | 0.076 | 0.27 | 13.23 | 1
November | 18 | 6AM to 7AM | 48.9 | 45.4 | 42.1 | 40.4 | 18 | 0.0762 | 0.27 | 13.2 | 1
November | 18 | 7AM to 8AM | 51.1 | 46.4 | 42.1 | 40.4 | 18.52 | 0.0758 | 0.27 | 13.26 | 1
November | 18 | 8AM to 9AM | 57.9 | 50.8 | 45 | 45.2 | 20.92 | 0.0748 | 0.3 | 13.45 | 0
November | 18 | 9AM to 10AM | 62.1 | 53.1 | 46 | 47.1 | 22.22 | 0.0742 | 0.31 | 13.57 | 0
November | 18 | 10AM to 11AM | 64.9 | 55.6 | 48.9 | 52.6 | 23.77 | 0.0738 | 0.35 | 13.66 | 0
November | 18 | 11AM to 12PM | 69.1 | 58.3 | 51.1 | 57 | 25.47 | 0.0732 | 0.38 | 13.78 | 0
November | 18 | 12PM to 1PM | 71.1 | 59 | 51.1 | 57 | 25.96 | 0.0729 | 0.38 | 13.83 | 0
November | 18 | 1PM to 2PM | 72 | 59.3 | 51.1 | 57 | 26.18 | 0.0728 | 0.38 | 13.85 | 0
November | 18 | 2PM to 3PM | 73 | 59.7 | 51.1 | 57 | 26.44 | 0.0726 | 0.38 | 13.88 | 0
November | 18 | 3PM to 4PM | 72 | 58.8 | 50 | 54.7 | 25.82 | 0.0728 | 0.36 | 13.85 | 0
November | 18 | 4PM to 5PM | 70 | 58.1 | 50 | 54.7 | 25.34 | 0.0731 | 0.36 | 13.8 | 0
November | 18 | 5PM to 6PM | 66.9 | 56.4 | 48.9 | 52.6 | 24.25 | 0.0735 | 0.35 | 13.71 | 0
November | 18 | 6PM to 7PM | 64.9 | 55.6 | 48.9 | 52.6 | 23.77 | 0.0738 | 0.35 | 13.66 | 0
November | 18 | 7PM to 8PM | 64 | 55.3 | 48.9 | 52.6 | 23.55 | 0.0739 | 0.35 | 13.63 | 0
November | 18 | 8PM to 9PM | 63 | 54.8 | 48.9 | 52.6 | 23.29 | 0.074 | 0.35 | 13.61 | 0
November | 18 | 9PM to 10PM | 63 | 55.4 | 50 | 54.7 | 23.63 | 0.074 | 0.36 | 13.61 | 0
November | 18 | 10PM to 11PM | 62.1 | 55 | 50 | 54.7 | 23.41 | 0.0742 | 0.36 | 13.59 | 0
November | 18 | 11PM to 12AM | 61 | 55.2 | 51.1 | 57 | 23.5 | 0.0743 | 0.38 | 13.57 | 0
November | 19 | 12AM to 1AM | 60.1 | 54.2 | 50 | 54.7 | 22.93 | 0.0744 | 0.36 | 13.54 | 0
November | 19 | 1AM to 2AM | 60.1 | 54.8 | 51.1 | 57 | 23.28 | 0.0744 | 0.38 | 13.54 | 0
November | 19 | 2AM to 3AM | 59 | 54.4 | 51.1 | 57 | 23.02 | 0.0746 | 0.38 | 13.52 | 0
November | 19 | 3AM to 4AM | 59 | 54.9 | 52 | 59 | 23.32 | 0.0746 | 0.39 | 13.52 | 0
November | 19 | 4AM to 5AM | 57.9 | 54.4 | 52 | 59 | 23.06 | 0.0747 | 0.39 | 13.49 | 0
November | 19 | 5AM to 6AM | 59 | 54.9 | 52 | 59 | 23.32 | 0.0746 | 0.39 | 13.52 | 0
November | 19 | 6AM to 7AM | 61 | 56.7 | 54 | 63.5 | 24.51 | 0.0743 | 0.42 | 13.59 | 0
November | 19 | 7AM to 8AM | 64.9 | 57.7 | 53.1 | 61.4 | 25.15 | 0.0737 | 0.41 | 13.68 | 0
November | 19 | 8AM to 9AM | 64.9 | 59.3 | 55.9 | 68.3 | 26.22 | 0.0737 | 0.45 | 13.71 | 0
November | 19 | 9AM to 10AM | 66.9 | 61.2 | 57.9 | 73.5 | 27.51 | 0.0734 | 0.48 | 13.77 | 0
November | 19 | 10AM to 11AM | 70 | 62.9 | 59 | 76.4 | 28.72 | 0.0729 | 0.5 | 13.86 | 0
November | 19 | 11AM to 12PM | 72 | 63.5 | 59 | 76.4 | 29.2 | 0.0726 | 0.5 | 13.92 | 0
November | 19 | 12PM to 1PM | 75 | 63.5 | 57 | 71.1 | 29.12 | 0.0723 | 0.47 | 13.98 | 0
November | 19 | 1PM to 2PM | 75.9 | 63.2 | 55.9 | 68.3 | 28.91 | 0.0722 | 0.45 | 13.99 | 0
November | 19 | 2PM to 3PM | 75.9 | 63.2 | 55.9 | 68.3 | 28.91 | 0.0722 | 0.45 | 13.99 | 0
November | 19 | 3PM to 4PM | 75 | 62.4 | 55 | 66.1 | 28.34 | 0.0723 | 0.44 | 13.96 | 0
November | 19 | 4PM to 5PM | 71.1 | 61 | 55 | 66.1 | 27.37 | 0.0728 | 0.44 | 13.86 | 0
November | 19 | 5PM to 6PM | 68 | 59.9 | 55 | 66.1 | 26.62 | 0.0733 | 0.44 | 13.78 | 0
November | 19 | 6PM to 7PM | 64.9 | 58.2 | 54 | 63.5 | 25.47 | 0.0737 | 0.42 | 13.69 | 0
November | 19 | 7PM to 8PM | 64.9 | 58.2 | 54 | 63.5 | 25.47 | 0.0737 | 0.42 | 13.69 | 0
November | 19 | 8PM to 9PM | 61 | 56.7 | 54 | 63.5 | 24.51 | 0.0743 | 0.42 | 13.59 | 0
November | 19 | 9PM to 10PM | 55 | 52.7 | 51.1 | 57 | 22.05 | 0.0752 | 0.38 | 13.41 | 0
November | 19 | 10PM to 11PM | 53.1 | 51.9 | 51.1 | 57 | 21.57 | 0.0755 | 0.38 | 13.36 | 0
November | 19 | 11PM to 12AM | 51.1 | 50.5 | 50 | 54.7 | 20.74 | 0.0758 | 0.36 | 13.3 | 1
November | 20 | 12AM to 1AM | 50 | 50 | 50 | 54.7 | 20.47 | 0.0759 | 0.36 | 13.28 | 1
November | 20 | 1AM to 2AM | 48 | 48 | 48 | 50.8 | 19.38 | 0.0762 | 0.34 | 13.21 | 1
November | 20 | 2AM to 3AM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
November | 20 | 3AM to 4AM | 48 | 47.4 | 46.9 | 48.8 | 19.06 | 0.0763 | 0.32 | 13.21 | 1
November | 20 | 4AM to 5AM | 46 | 46 | 46 | 47.1 | 18.33 | 0.0766 | 0.31 | 13.15 | 1
November | 20 | 5AM to 6AM | 48 | 45.4 | 43 | 41.9 | 18 | 0.0763 | 0.28 | 13.19 | 1
November | 20 | 6AM to 7AM | 50 | 46.9 | 44.1 | 43.6 | 18.76 | 0.076 | 0.29 | 13.24 | 1
November | 20 | 7AM to 8AM | 53.1 | 47.8 | 43 | 41.9 | 19.22 | 0.0755 | 0.28 | 13.32 | 0
November | 20 | 8AM to 9AM | 55.9 | 49.6 | 44.1 | 43.6 | 20.2 | 0.0751 | 0.29 | 13.4 | 0
November | 20 | 9AM to 10AM | 59 | 50.9 | 44.1 | 43.6 | 20.94 | 0.0747 | 0.29 | 13.48 | 0
November | 20 | 10AM to 11AM | 63 | 52.6 | 44.1 | 43.6 | 21.9 | 0.0741 | 0.29 | 13.58 | 0
November | 20 | 11AM to 12PM | 64 | 57.9 | 54 | 63.5 | 25.25 | 0.0738 | 0.42 | 13.67 | 0
November | 20 | 12PM to 1PM | 64.9 | 60 | 57 | 71.1 | 26.65 | 0.0737 | 0.47 | 13.71 | 0
November | 20 | 1PM to 2PM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
November | 20 | 2PM to 3PM | 66.9 | 62.5 | 60.1 | 79.5 | 28.45 | 0.0733 | 0.52 | 13.79 | 0
November | 20 | 3PM to 4PM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
November | 20 | 4PM to 5PM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
November | 20 | 5PM to 6PM | 68 | 63.4 | 61 | 82.1 | 29.12 | 0.0732 | 0.54 | 13.83 | 0
November | 20 | 6PM to 7PM | 69.1 | 63.8 | 61 | 82.1 | 29.39 | 0.073 | 0.54 | 13.86 | 0
November | 20 | 7PM to 8PM | 68 | 62.8 | 60.1 | 79.5 | 28.71 | 0.0732 | 0.52 | 13.82 | 0
November | 20 | 8PM to 9PM | 66.9 | 61.8 | 59 | 76.4 | 27.97 | 0.0733 | 0.5 | 13.78 | 0
November | 20 | 9PM to 10PM | 66 | 61.5 | 59 | 76.4 | 27.75 | 0.0735 | 0.5 | 13.76 | 0
November | 20 | 10PM to 11PM | 66 | 60.9 | 57.9 | 73.5 | 27.29 | 0.0735 | 0.48 | 13.75 | 0
November | 20 | 11PM to 12AM | 66.9 | 60.7 | 57 | 71.1 | 27.14 | 0.0734 | 0.47 | 13.77 | 0
November | 21 | 12AM to 1AM | 63 | 60.4 | 59 | 76.4 | 27 | 0.0739 | 0.5 | 13.68 | 0
November | 21 | 1AM to 2AM | 62.1 | 60.1 | 59 | 76.4 | 26.78 | 0.074 | 0.5 | 13.66 | 0
November | 21 | 2AM to 3AM | 61 | 60.4 | 60.1 | 79.5 | 26.99 | 0.0742 | 0.52 | 13.64 | 0
November | 21 | 3AM to 4AM | 60.1 | 59.4 | 59 | 76.4 | 26.29 | 0.0743 | 0.5 | 13.6 | 0
November | 21 | 4AM to 5AM | 59 | 59 | 59 | 76.4 | 26.03 | 0.0745 | 0.5 | 13.58 | 0
November | 21 | 5AM to 6AM | 59 | 59 | 59 | 76.4 | 26.03 | 0.0745 | 0.5 | 13.58 | 0
November | 21 | 6AM to 7AM | 59 | 59 | 59 | 76.4 | 26.03 | 0.0745 | 0.5 | 13.58 | 0
November | 21 | 7AM to 8AM | 59 | 58.3 | 57.9 | 73.5 | 25.57 | 0.0745 | 0.48 | 13.57 | 0
November | 21 | 8AM to 9AM | 60.1 | 58.7 | 57.9 | 73.5 | 25.84 | 0.0743 | 0.48 | 13.6 | 0
November | 21 | 9AM to 10AM | 61 | 59.1 | 57.9 | 73.5 | 26.06 | 0.0742 | 0.48 | 13.62 | 0
November | 21 | 10AM to 11AM | 61 | 59.7 | 59 | 76.4 | 26.52 | 0.0742 | 0.5 | 13.63 | 0
November | 21 | 11AM to 12PM | 63 | 61.1 | 60.1 | 79.5 | 27.48 | 0.0739 | 0.52 | 13.69 | 0
November | 21 | 12PM to 1PM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
November | 21 | 1PM to 2PM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
November | 21 | 2PM to 3PM | 66 | 62.7 | 61 | 82.1 | 28.64 | 0.0734 | 0.54 | 13.78 | 0
November | 21 | 3PM to 4PM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
November | 21 | 4PM to 5PM | 64.9 | 62.4 | 61 | 82.1 | 28.37 | 0.0736 | 0.54 | 13.75 | 0
November | 21 | 5PM to 6PM | 63 | 61.7 | 61 | 82.1 | 27.89 | 0.0739 | 0.54 | 13.7 | 0
November | 21 | 6PM to 7PM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
November | 21 | 7PM to 8PM | 63 | 62.4 | 62.1 | 85.4 | 28.39 | 0.0738 | 0.56 | 13.71 | 0
November | 21 | 8PM to 9PM | 62.1 | 62.1 | 62.1 | 85.4 | 28.17 | 0.074 | 0.56 | 13.68 | 0
November | 21 | 9PM to 10PM | 63 | 62.4 | 62.1 | 85.4 | 28.39 | 0.0738 | 0.56 | 13.71 | 0
November | 21 | 10PM to 11PM | 57.9 | 57.9 | 57.9 | 73.5 | 25.31 | 0.0746 | 0.48 | 13.54 | 0
November | 21 | 11PM to 12AM | 57.9 | 56.2 | 55 | 66.1 | 24.16 | 0.0747 | 0.44 | 13.52 | 0
November | 22 | 12AM to 1AM | 55.9 | 55.4 | 55 | 66.1 | 23.68 | 0.075 | 0.44 | 13.46 | 0
November | 22 | 1AM to 2AM | 55 | 53.9 | 53.1 | 61.4 | 22.73 | 0.0751 | 0.41 | 13.43 | 0
November | 22 | 2AM to 3AM | 53.1 | 53.1 | 53.1 | 61.4 | 22.25 | 0.0754 | 0.41 | 13.38 | 0
November | 22 | 3AM to 4AM | 59 | 55.5 | 53.1 | 61.4 | 23.7 | 0.0746 | 0.41 | 13.53 | 0
November | 22 | 4AM to 5AM | 53.1 | 52.4 | 52 | 59 | 21.87 | 0.0754 | 0.39 | 13.37 | 0
November | 22 | 5AM to 6AM | 52 | 52 | 52 | 59 | 21.61 | 0.0756 | 0.39 | 13.34 | 0
November | 22 | 6AM to 7AM | 52 | 52 | 52 | 59 | 21.61 | 0.0756 | 0.39 | 13.34 | 0
November | 22 | 7AM to 8AM | 52 | 52 | 52 | 59 | 21.61 | 0.0756 | 0.39 | 13.34 | 0
November | 22 | 8AM to 9AM | 50 | 49.4 | 48.9 | 52.6 | 20.14 | 0.0759 | 0.35 | 13.27 | 1
November | 22 | 9AM to 10AM | 48.9 | 47.8 | 46.9 | 48.8 | 19.28 | 0.0761 | 0.32 | 13.23 | 1
November | 22 | 10AM to 11AM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
November | 22 | 11AM to 12PM | 48 | 45 | 42.1 | 40.4 | 17.78 | 0.0763 | 0.27 | 13.18 | 1
November | 22 | 12PM to 1PM | 50 | 44.9 | 39.9 | 37.2 | 17.75 | 0.076 | 0.25 | 13.22 | 1
November | 22 | 1PM to 2PM | 50 | 44.6 | 39 | 35.9 | 17.55 | 0.076 | 0.24 | 13.22 | 1
November | 22 | 2PM to 3PM | 50 | 43.3 | 36 | 31.8 | 16.92 | 0.0761 | 0.21 | 13.21 | 1
November | 22 | 3PM to 4PM | 48 | 42.8 | 37 | 33.2 | 16.65 | 0.0764 | 0.22 | 13.16 | 1
November | 22 | 4PM to 5PM | 45 | 40.4 | 35.1 | 30.6 | 15.52 | 0.0768 | 0.2 | 13.07 | 1
November | 22 | 5PM to 6PM | 44.1 | 39.9 | 35.1 | 30.6 | 15.31 | 0.077 | 0.2 | 13.05 | 1
November | 22 | 6PM to 7PM | 44.1 | 39.9 | 35.1 | 30.6 | 15.31 | 0.077 | 0.2 | 13.05 | 1
November | 22 | 7PM to 8PM | 43 | 39.4 | 35.1 | 30.6 | 15.04 | 0.0771 | 0.2 | 13.02 | 1
November | 22 | 8PM to 9PM | 42.1 | 38.5 | 34 | 29.3 | 14.63 | 0.0773 | 0.2 | 12.99 | 1
November | 22 | 9PM to 10PM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
November | 22 | 10PM to 11PM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
November | 22 | 11PM to 12AM | 39.9 | 36.9 | 33.1 | 28.3 | 13.94 | 0.0776 | 0.19 | 12.93 | 1
November | 23 | 12AM to 1AM | 41 | 37.5 | 33.1 | 28.3 | 14.2 | 0.0775 | 0.19 | 12.96 | 1
November | 23 | 1AM to 2AM | 41 | 37.5 | 33.1 | 28.3 | 14.2 | 0.0775 | 0.19 | 12.96 | 1
November | 23 | 2AM to 3AM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
November | 23 | 3AM to 4AM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
November | 23 | 4AM to 5AM | 39.9 | 36.9 | 33.1 | 28.3 | 13.94 | 0.0776 | 0.19 | 12.93 | 1
November | 23 | 5AM to 6AM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
November | 23 | 6AM to 7AM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
November | 23 | 7AM to 8AM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
November | 23 | 8AM to 9AM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
November | 23 | 9AM to 10AM | 39 | 35.2 | 30 | 24.7 | 13.17 | 0.0778 | 0.16 | 12.9 | 1
November | 23 | 10AM to 11AM | 39 | 35.2 | 30 | 24.7 | 13.17 | 0.0778 | 0.16 | 12.9 | 1
November | 23 | 11AM to 12PM | 39.9 | 35.7 | 30 | 24.7 | 13.39 | 0.0776 | 0.16 | 12.92 | 1
November | 23 | 12PM to 1PM | 41 | 36.6 | 30.9 | 25.8 | 13.81 | 0.0775 | 0.17 | 12.96 | 1
November | 23 | 1PM to 2PM | 42.1 | 36.9 | 30 | 24.7 | 13.91 | 0.0773 | 0.16 | 12.98 | 1
November | 23 | 2PM to 3PM | 41 | 35.8 | 28.9 | 23.5 | 13.47 | 0.0775 | 0.16 | 12.95 | 1
November | 23 | 3PM to 4PM | 42.1 | 36.4 | 28.9 | 23.5 | 13.73 | 0.0773 | 0.16 | 12.98 | 1
November | 23 | 4PM to 5PM | 41 | 35.5 | 28 | 22.5 | 13.32 | 0.0775 | 0.15 | 12.95 | 1
November | 23 | 5PM to 6PM | 39.9 | 34.9 | 28 | 22.5 | 13.06 | 0.0777 | 0.15 | 12.92 | 1
November | 23 | 6PM to 7PM | 39 | 34.4 | 28 | 22.5 | 12.84 | 0.0778 | 0.15 | 12.89 | 1
November | 23 | 7PM to 8PM | 39 | 34.4 | 28 | 22.5 | 12.84 | 0.0778 | 0.15 | 12.89 | 1
November | 23 | 8PM to 9PM | 37 | 33.6 | 28.9 | 23.5 | 12.51 | 0.0781 | 0.16 | 12.85 | 1
November | 23 | 9PM to 10PM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
November | 23 | 10PM to 11PM | 36 | 33.4 | 30 | 24.7 | 12.43 | 0.0783 | 0.16 | 12.82 | 1
November | 23 | 11PM to 12AM | 36 | 33.4 | 30 | 24.7 | 12.43 | 0.0783 | 0.16 | 12.82 | 1
November | 24 | 12AM to 1AM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
November | 24 | 1AM to 2AM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
November | 24 | 2AM to 3AM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
November | 24 | 3AM to 4AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
November | 24 | 4AM to 5AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
November | 24 | 5AM to 6AM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
November | 24 | 6AM to 7AM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
November | 24 | 7AM to 8AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
November | 24 | 8AM to 9AM | 39 | 36 | 32 | 27.1 | 13.54 | 0.0778 | 0.18 | 12.91 | 1
November | 24 | 9AM to 10AM | 46 | 39.8 | 32 | 27.1 | 15.24 | 0.0767 | 0.18 | 13.09 | 1
November | 24 | 10AM to 11AM | 48.9 | 40.8 | 30.9 | 25.8 | 15.73 | 0.0763 | 0.17 | 13.16 | 1
November | 24 | 11AM to 12PM | 48.9 | 41.7 | 33.1 | 28.3 | 16.12 | 0.0763 | 0.19 | 13.17 | 1
November | 24 | 12PM to 1PM | 55 | 45 | 34 | 29.3 | 17.76 | 0.0753 | 0.2 | 13.33 | 0
November | 24 | 1PM to 2PM | 55.9 | 44.7 | 32 | 27.1 | 17.63 | 0.0752 | 0.18 | 13.35 | 0
November | 24 | 2PM to 3PM | 55.9 | 45.1 | 33.1 | 28.3 | 17.82 | 0.0752 | 0.19 | 13.35 | 0
November | 24 | 3PM to 4PM | 55 | 43.9 | 30.9 | 25.8 | 17.21 | 0.0754 | 0.17 | 13.32 | 0
November | 24 | 4PM to 5PM | 53.1 | 42.9 | 30.9 | 25.8 | 16.73 | 0.0757 | 0.17 | 13.27 | 0
November | 24 | 5PM to 6PM | 48 | 41.2 | 33.1 | 28.3 | 15.9 | 0.0764 | 0.19 | 13.14 | 1
November | 24 | 6PM to 7PM | 48 | 42 | 35.1 | 30.6 | 16.26 | 0.0764 | 0.2 | 13.15 | 1
November | 24 | 7PM to 8PM | 48 | 42 | 35.1 | 30.6 | 16.26 | 0.0764 | 0.2 | 13.15 | 1
November | 24 | 8PM to 9PM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
November | 24 | 9PM to 10PM | 46 | 42.1 | 37.9 | 34.4 | 16.36 | 0.0766 | 0.23 | 13.11 | 1
November | 24 | 10PM to 11PM | 46 | 42.6 | 39 | 35.9 | 16.59 | 0.0766 | 0.24 | 13.12 | 1
November | 24 | 11PM to 12AM | 45 | 42.5 | 39.9 | 37.2 | 16.53 | 0.0768 | 0.25 | 13.09 | 1
November | 25 | 12AM to 1AM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
November | 25 | 1AM to 2AM | 41 | 40.5 | 39.9 | 37.2 | 15.57 | 0.0774 | 0.25 | 12.99 | 1
November | 25 | 2AM to 3AM | 42.1 | 41 | 39.9 | 37.2 | 15.83 | 0.0772 | 0.25 | 13.02 | 1
November | 25 | 3AM to 4AM | 41 | 40.5 | 39.9 | 37.2 | 15.57 | 0.0774 | 0.25 | 12.99 | 1
November | 25 | 4AM to 5AM | 41 | 40.5 | 39.9 | 37.2 | 15.57 | 0.0774 | 0.25 | 12.99 | 1
November | 25 | 5AM to 6AM | 39 | 39 | 39 | 35.9 | 14.89 | 0.0777 | 0.24 | 12.93 | 1
November | 25 | 6AM to 7AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
November | 25 | 7AM to 8AM | 39.9 | 39.9 | 39.9 | 37.2 | 15.31 | 0.0776 | 0.25 | 12.96 | 1
November | 25 | 8AM to 9AM | 41 | 40.5 | 39.9 | 37.2 | 15.57 | 0.0774 | 0.25 | 12.99 | 1
November | 25 | 9AM to 10AM | 41 | 41 | 41 | 38.8 | 15.82 | 0.0774 | 0.26 | 12.99 | 1
November | 25 | 10AM to 11AM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
November | 25 | 11AM to 12PM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
November | 25 | 12PM to 1PM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
November | 25 | 1PM to 2PM | 44.1 | 44.1 | 44.1 | 43.6 | 17.31 | 0.0769 | 0.29 | 13.09 | 1
November | 25 | 2PM to 3PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 25 | 3PM to 4PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 25 | 4PM to 5PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 25 | 5PM to 6PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 25 | 6PM to 7PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 25 | 7PM to 8PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 25 | 8PM to 9PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 25 | 9PM to 10PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 25 | 10PM to 11PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
November | 25 | 11PM to 12AM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
November | 26 | 12AM to 1AM | 41 | 41 | 41 | 38.8 | 15.82 | 0.0774 | 0.26 | 12.99 | 1
November | 26 | 1AM to 2AM | 41 | 41 | 41 | 38.8 | 15.82 | 0.0774 | 0.26 | 12.99 | 1
November | 26 | 2AM to 3AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 26 | 3AM to 4AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 26 | 4AM to 5AM | 41 | 39.6 | 37.9 | 34.4 | 15.14 | 0.0774 | 0.23 | 12.98 | 1
November | 26 | 5AM to 6AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 26 | 6AM to 7AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 26 | 7AM to 8AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 26 | 8AM to 9AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 26 | 9AM to 10AM | 41 | 39.6 | 37.9 | 34.4 | 15.14 | 0.0774 | 0.23 | 12.98 | 1
November | 26 | 10AM to 11AM | 43 | 40.6 | 37.9 | 34.4 | 15.62 | 0.0771 | 0.23 | 13.03 | 1
November | 26 | 11AM to 12PM | 45 | 41.6 | 37.9 | 34.4 | 16.1 | 0.0768 | 0.23 | 13.08 | 1
November | 26 | 12PM to 1PM | 45 | 41.6 | 37.9 | 34.4 | 16.1 | 0.0768 | 0.23 | 13.08 | 1
November | 26 | 1PM to 2PM | 46.9 | 42.6 | 37.9 | 34.4 | 16.58 | 0.0765 | 0.23 | 13.13 | 1
November | 26 | 2PM to 3PM | 48.9 | 43.6 | 37.9 | 34.4 | 17.06 | 0.0762 | 0.23 | 13.19 | 1
November | 26 | 3PM to 4PM | 50 | 44.1 | 37.9 | 34.4 | 17.32 | 0.076 | 0.23 | 13.21 | 1
November | 26 | 4PM to 5PM | 48 | 43.1 | 37.9 | 34.4 | 16.84 | 0.0763 | 0.23 | 13.16 | 1
November | 26 | 5PM to 6PM | 46 | 42.1 | 37.9 | 34.4 | 16.36 | 0.0766 | 0.23 | 13.11 | 1
November | 26 | 6PM to 7PM | 46 | 42.1 | 37.9 | 34.4 | 16.36 | 0.0766 | 0.23 | 13.11 | 1
November | 26 | 7PM to 8PM | 45 | 41.6 | 37.9 | 34.4 | 16.1 | 0.0768 | 0.23 | 13.08 | 1
November | 26 | 8PM to 9PM | 41 | 39.6 | 37.9 | 34.4 | 15.14 | 0.0774 | 0.23 | 12.98 | 1
November | 26 | 9PM to 10PM | 39 | 38.5 | 37.9 | 34.4 | 14.66 | 0.0777 | 0.23 | 12.93 | 1
November | 26 | 10PM to 11PM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 26 | 11PM to 12AM | 37.9 | 37 | 36 | 31.8 | 14 | 0.0779 | 0.21 | 12.89 | 1
November | 27 | 12AM to 1AM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
November | 27 | 1AM to 2AM | 36 | 35.1 | 34 | 29.3 | 13.15 | 0.0782 | 0.2 | 12.84 | 1
November | 27 | 2AM to 3AM | 37.9 | 37 | 36 | 31.8 | 14 | 0.0779 | 0.21 | 12.89 | 1
November | 27 | 3AM to 4AM | 39 | 38.1 | 37 | 33.2 | 14.47 | 0.0777 | 0.22 | 12.93 | 1
November | 27 | 4AM to 5AM | 39.9 | 39.5 | 39 | 35.9 | 15.11 | 0.0776 | 0.24 | 12.96 | 1
November | 27 | 5AM to 6AM | 39.9 | 39 | 37.9 | 34.4 | 14.88 | 0.0776 | 0.23 | 12.95 | 1
November | 27 | 6AM to 7AM | 39.9 | 39.5 | 39 | 35.9 | 15.11 | 0.0776 | 0.24 | 12.96 | 1
November | 27 | 7AM to 8AM | 39.9 | 39.5 | 39 | 35.9 | 15.11 | 0.0776 | 0.24 | 12.96 | 1
November | 27 | 8AM to 9AM | 41 | 41 | 41 | 38.8 | 15.82 | 0.0774 | 0.26 | 12.99 | 1
November | 27 | 9AM to 10AM | 42.1 | 41.5 | 41 | 38.8 | 16.08 | 0.0772 | 0.26 | 13.02 | 1
November | 27 | 10AM to 11AM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
November | 27 | 11AM to 12PM | 46.9 | 44.9 | 43 | 41.9 | 17.74 | 0.0765 | 0.28 | 13.16 | 1
November | 27 | 12PM to 1PM | 45 | 43.5 | 42.1 | 40.4 | 17.04 | 0.0768 | 0.27 | 13.1 | 1
November | 27 | 1PM to 2PM | 44.1 | 42.5 | 41 | 38.8 | 16.56 | 0.0769 | 0.26 | 13.07 | 1
November | 27 | 2PM to 3PM | 42.1 | 40.1 | 37.9 | 34.4 | 15.4 | 0.0772 | 0.23 | 13.01 | 1
November | 27 | 3PM to 4PM | 37.9 | 37.5 | 37 | 33.2 | 14.21 | 0.0779 | 0.22 | 12.9 | 1
November | 27 | 4PM to 5PM | 37 | 37 | 37 | 33.2 | 14 | 0.078 | 0.22 | 12.87 | 1
November | 27 | 5PM to 6PM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
November | 27 | 6PM to 7PM | 36 | 36 | 36 | 31.8 | 13.52 | 0.0782 | 0.21 | 12.84 | 1
November | 27 | 7PM to 8PM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
November | 27 | 8PM to 9PM | 37 | 37 | 37 | 33.2 | 14 | 0.078 | 0.22 | 12.87 | 1
November | 27 | 9PM to 10PM | 37.9 | 37.9 | 37.9 | 34.4 | 14.4 | 0.0779 | 0.23 | 12.9 | 1
November | 27 | 10PM to 11PM | 37 | 37 | 37 | 33.2 | 14 | 0.078 | 0.22 | 12.87 | 1
November | 27 | 11PM to 12AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
November | 28 | 12AM to 1AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
November | 28 | 1AM to 2AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
November | 28 | 2AM to 3AM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
November | 28 | 3AM to 4AM | 33.1 | 32.1 | 30.9 | 25.8 | 11.9 | 0.0787 | 0.17 | 12.75 | 1
November | 28 | 4AM to 5AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
November | 28 | 5AM to 6AM | 30.9 | 30.5 | 30 | 24.7 | 11.22 | 0.0791 | 0.16 | 12.69 | 1
November | 28 | 6AM to 7AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
November | 28 | 7AM to 8AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
November | 28 | 8AM to 9AM | 32 | 29 | 25 | 19.5 | 10.68 | 0.0789 | 0.13 | 12.7 | 1
November | 28 | 9AM to 10AM | 32 | 28.3 | 23 | 17.8 | 10.41 | 0.0789 | 0.12 | 12.7 | 1
November | 28 | 10AM to 11AM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
November | 28 | 11AM to 12PM | 32 | 29 | 25 | 19.5 | 10.68 | 0.0789 | 0.13 | 12.7 | 1
November | 28 | 12PM to 1PM | 32 | 27.7 | 21 | 16.2 | 10.16 | 0.079 | 0.11 | 12.69 | 1
November | 28 | 1PM to 2PM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
November | 28 | 2PM to 3PM | 30.9 | 26.7 | 19.9 | 15.3 | 9.78 | 0.0791 | 0.1 | 12.66 | 1
November | 28 | 3PM to 4PM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
November | 28 | 4PM to 5PM | 28.9 | 25.3 | 19 | 14.7 | 9.2 | 0.0795 | 0.1 | 12.61 | 1
November | 28 | 5PM to 6PM | 28 | 24.4 | 18 | 13.9 | 8.87 | 0.0796 | 0.09 | 12.59 | 1
November | 28 | 6PM to 7PM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
November | 28 | 7PM to 8PM | 27 | 23.7 | 18 | 13.9 | 8.61 | 0.0798 | 0.09 | 12.56 | 1
November | 28 | 8PM to 9PM | 27 | 23.7 | 18 | 13.9 | 8.61 | 0.0798 | 0.09 | 12.56 | 1
November | 28 | 9PM to 10PM | 27 | 23.7 | 18 | 13.9 | 8.61 | 0.0798 | 0.09 | 12.56 | 1
November | 28 | 10PM to 11PM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
November | 28 | 11PM to 12AM | 25 | 22.8 | 19 | 14.7 | 8.25 | 0.0801 | 0.1 | 12.51 | 1
November | 29 | 12AM to 1AM | 24.1 | 21.9 | 18 | 13.9 | 7.92 | 0.0803 | 0.09 | 12.48 | 1
November | 29 | 1AM to 2AM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
November | 29 | 2AM to 3AM | 23 | 22.3 | 21 | 16.2 | 8 | 0.0804 | 0.11 | 12.46 | 1
November | 29 | 3AM to 4AM | 23 | 22.3 | 21 | 16.2 | 8 | 0.0804 | 0.11 | 12.46 | 1
November | 29 | 4AM to 5AM | 23 | 22.3 | 21 | 16.2 | 8 | 0.0804 | 0.11 | 12.46 | 1
November | 29 | 5AM to 6AM | 24.1 | 22.6 | 19.9 | 15.3 | 8.13 | 0.0803 | 0.1 | 12.49 | 1
November | 29 | 6AM to 7AM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
November | 29 | 7AM to 8AM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
November | 29 | 8AM to 9AM | 24.1 | 22.6 | 19.9 | 15.3 | 8.13 | 0.0803 | 0.1 | 12.49 | 1
November | 29 | 9AM to 10AM | 25 | 23.5 | 21 | 16.2 | 8.47 | 0.0801 | 0.11 | 12.51 | 1
November | 29 | 10AM to 11AM | 26.1 | 24.2 | 21 | 16.2 | 8.73 | 0.0799 | 0.11 | 12.54 | 1
November | 29 | 11AM to 12PM | 28 | 25.4 | 21 | 16.2 | 9.21 | 0.0796 | 0.11 | 12.59 | 1
November | 29 | 12PM to 1PM | 28 | 25.4 | 21 | 16.2 | 9.21 | 0.0796 | 0.11 | 12.59 | 1
November | 29 | 1PM to 2PM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
November | 29 | 2PM to 3PM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
November | 29 | 3PM to 4PM | 28 | 25.4 | 21 | 16.2 | 9.21 | 0.0796 | 0.11 | 12.59 | 1
November | 29 | 4PM to 5PM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
November | 29 | 5PM to 6PM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
November | 29 | 6PM to 7PM | 28 | 25 | 19.9 | 15.3 | 9.08 | 0.0796 | 0.1 | 12.59 | 1
November | 29 | 7PM to 8PM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
November | 29 | 8PM to 9PM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
November | 29 | 9PM to 10PM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
November | 29 | 10PM to 11PM | 25 | 22.8 | 19 | 14.7 | 8.25 | 0.0801 | 0.1 | 12.51 | 1
November | 29 | 11PM to 12AM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
November | 30 | 12AM to 1AM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
November | 30 | 1AM to 2AM | 23 | 21.6 | 19 | 14.7 | 7.77 | 0.0804 | 0.1 | 12.46 | 1
November | 30 | 2AM to 3AM | 21.9 | 20.9 | 19 | 14.7 | 7.51 | 0.0806 | 0.1 | 12.43 | 1
November | 30 | 3AM to 4AM | 21 | 20.3 | 19 | 14.7 | 7.29 | 0.0808 | 0.1 | 12.41 | 1
November | 30 | 4AM to 5AM | 21 | 20.3 | 19 | 14.7 | 7.29 | 0.0808 | 0.1 | 12.41 | 1
November | 30 | 5AM to 6AM | 21 | 20 | 18 | 13.9 | 7.18 | 0.0808 | 0.09 | 12.4 | 1
November | 30 | 6AM to 7AM | 19.9 | 19.3 | 18 | 13.9 | 6.92 | 0.081 | 0.09 | 12.38 | 1
November | 30 | 7AM to 8AM | 19.9 | 19.3 | 18 | 13.9 | 6.92 | 0.081 | 0.09 | 12.38 | 1
November | 30 | 8AM to 9AM | 23 | 21.3 | 18 | 13.9 | 7.66 | 0.0804 | 0.09 | 12.46 | 1
November | 30 | 9AM to 10AM | 26.1 | 23.5 | 19 | 14.7 | 8.51 | 0.0799 | 0.1 | 12.54 | 1
November | 30 | 10AM to 11AM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
November | 30 | 11AM to 12PM | 32 | 27.3 | 19.9 | 15.3 | 10.04 | 0.079 | 0.1 | 12.69 | 1
November | 30 | 12PM to 1PM | 32 | 27.3 | 19.9 | 15.3 | 10.04 | 0.079 | 0.1 | 12.69 | 1
November | 30 | 1PM to 2PM | 33.1 | 27.9 | 19.9 | 15.3 | 10.3 | 0.0788 | 0.1 | 12.72 | 1
November | 30 | 2PM to 3PM | 34 | 28.8 | 21 | 16.2 | 10.64 | 0.0786 | 0.11 | 12.75 | 1
November | 30 | 3PM to 4PM | 34 | 28.8 | 21 | 16.2 | 10.64 | 0.0786 | 0.11 | 12.75 | 1
November | 30 | 4PM to 5PM | 34 | 28.8 | 21 | 16.2 | 10.64 | 0.0786 | 0.11 | 12.75 | 1
November | 30 | 5PM to 6PM | 33.1 | 28.3 | 21 | 16.2 | 10.42 | 0.0788 | 0.11 | 12.72 | 1
November | 30 | 6PM to 7PM | 33.1 | 28.3 | 21 | 16.2 | 10.42 | 0.0788 | 0.11 | 12.72 | 1
November | 30 | 7PM to 8PM | 33.1 | 28.3 | 21 | 16.2 | 10.42 | 0.0788 | 0.11 | 12.72 | 1
November | 30 | 8PM to 9PM | 33.1 | 28.3 | 21 | 16.2 | 10.42 | 0.0788 | 0.11 | 12.72 | 1
November | 30 | 9PM to 10PM | 35.2 | 30.4 | 23.9 | 18.5 | 11.31 | 0.0784 | 0.12 | 12.79 | 1
November | 30 | 10PM to 11PM | 37.4 | 32.9 | 26.6 | 21.1 | 12.22 | 0.0781 | 0.14 | 12.85 | 1
November | 30 | 11PM to 12AM | 39.6 | 35.2 | 29.3 | 23.9 | 13.18 | 0.0777 | 0.16 | 12.91 | 1
December | 1 | 12AM to 1AM | 41.5 | 37.4 | 32 | 27.1 | 14.15 | 0.0774 | 0.18 | 12.97 | 1
December | 1 | 1AM to 2AM | 43.7 | 39.5 | 34.5 | 30 | 15.12 | 0.077 | 0.2 | 13.04 | 1
December | 1 | 2AM to 3AM | 45.9 | 41.7 | 37.2 | 33.4 | 16.17 | 0.0767 | 0.22 | 13.1 | 1
December | 1 | 3AM to 4AM | 48 | 44 | 39.9 | 37.2 | 17.27 | 0.0763 | 0.25 | 13.17 | 1
December | 1 | 4AM to 5AM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
December | 1 | 5AM to 6AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
December | 1 | 6AM to 7AM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
December | 1 | 7AM to 8AM | 44.1 | 39.2 | 33.1 | 28.3 | 14.94 | 0.077 | 0.19 | 13.04 | 1
December | 1 | 8AM to 9AM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
December | 1 | 9AM to 10AM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
December | 1 | 10AM to 11AM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
December | 1 | 11AM to 12PM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
December | 1 | 12PM to 1PM | 42.1 | 36.9 | 30 | 24.7 | 13.91 | 0.0773 | 0.16 | 12.98 | 1
December | 1 | 1PM to 2PM | 42.1 | 37.7 | 32 | 27.1 | 14.28 | 0.0773 | 0.18 | 12.99 | 1
December | 1 | 2PM to 3PM | 41 | 36.6 | 30.9 | 25.8 | 13.81 | 0.0775 | 0.17 | 12.96 | 1
December | 1 | 3PM to 4PM | 39.9 | 36.5 | 32 | 27.1 | 13.76 | 0.0776 | 0.18 | 12.93 | 1
December | 1 | 4PM to 5PM | 39 | 36.8 | 34 | 29.3 | 13.89 | 0.0778 | 0.2 | 12.91 | 1
December | 1 | 5PM to 6PM | 39 | 36.8 | 34 | 29.3 | 13.89 | 0.0778 | 0.2 | 12.91 | 1
December | 1 | 6PM to 7PM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
December | 1 | 7PM to 8PM | 37.9 | 36.2 | 34 | 29.3 | 13.63 | 0.0779 | 0.2 | 12.89 | 1
December | 1 | 8PM to 9PM | 37.9 | 35.8 | 33.1 | 28.3 | 13.46 | 0.0779 | 0.19 | 12.88 | 1
December | 1 | 9PM to 10PM | 37.9 | 35.4 | 32 | 27.1 | 13.28 | 0.0779 | 0.18 | 12.88 | 1
December | 1 | 10PM to 11PM | 37.9 | 35.4 | 32 | 27.1 | 13.28 | 0.0779 | 0.18 | 12.88 | 1
December | 1 | 11PM to 12AM | 37.9 | 34.9 | 30.9 | 25.8 | 13.08 | 0.0779 | 0.17 | 12.88 | 1
December | 2 | 12AM to 1AM | 37 | 33.6 | 28.9 | 23.5 | 12.51 | 0.0781 | 0.16 | 12.85 | 1
December | 2 | 1AM to 2AM | 37 | 33.6 | 28.9 | 23.5 | 12.51 | 0.0781 | 0.16 | 12.85 | 1
December | 2 | 2AM to 3AM | 37 | 33.6 | 28.9 | 23.5 | 12.51 | 0.0781 | 0.16 | 12.85 | 1
December | 2 | 3AM to 4AM | 36 | 32.6 | 28 | 22.5 | 12.1 | 0.0783 | 0.15 | 12.82 | 1
December | 2 | 4AM to 5AM | 36 | 33 | 28.9 | 23.5 | 12.25 | 0.0783 | 0.16 | 12.82 | 1
December | 2 | 5AM to 6AM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
December | 2 | 6AM to 7AM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
December | 2 | 7AM to 8AM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
December | 2 | 8AM to 9AM | 35.1 | 32.1 | 28 | 22.5 | 11.88 | 0.0784 | 0.15 | 12.79 | 1
December | 2 | 9AM to 10AM | 37 | 33.3 | 28 | 22.5 | 12.36 | 0.0781 | 0.15 | 12.84 | 1
December | 2 | 10AM to 11AM | 39 | 34 | 27 | 21.4 | 12.67 | 0.0778 | 0.14 | 12.89 | 1
December | 2 | 11AM to 12PM | 42.1 | 35 | 25 | 19.5 | 13.11 | 0.0773 | 0.13 | 12.96 | 1
December | 2 | 12PM to 1PM | 44.1 | 35.8 | 24.1 | 18.7 | 13.46 | 0.077 | 0.12 | 13.01 | 1
December | 2 | 1PM to 2PM | 44.1 | 34.9 | 21 | 16.2 | 13.07 | 0.0771 | 0.11 | 13.01 | 1
December | 2 | 2PM to 3PM | 45 | 35.7 | 21.9 | 16.9 | 13.4 | 0.0769 | 0.11 | 13.03 | 1
December | 2 | 3PM to 4PM | 44.1 | 35.2 | 21.9 | 16.9 | 13.18 | 0.0771 | 0.11 | 13.01 | 1
December | 2 | 4PM to 5PM | 44.1 | 35.5 | 23 | 17.8 | 13.32 | 0.0771 | 0.12 | 13.01 | 1
December | 2 | 5PM to 6PM | 44.1 | 35.5 | 23 | 17.8 | 13.32 | 0.0771 | 0.12 | 13.01 | 1
December | 2 | 6PM to 7PM | 44.1 | 35.8 | 24.1 | 18.7 | 13.46 | 0.077 | 0.12 | 13.01 | 1
December | 2 | 7PM to 8PM | 44.1 | 36.8 | 27 | 21.4 | 13.88 | 0.077 | 0.14 | 13.02 | 1
December | 2 | 8PM to 9PM | 43 | 36.6 | 28 | 22.5 | 13.79 | 0.0772 | 0.15 | 13 | 1
December | 2 | 9PM to 10PM | 39.9 | 36 | 30.9 | 25.8 | 13.55 | 0.0776 | 0.17 | 12.93 | 1
December | 2 | 10PM to 11PM | 39.9 | 36.9 | 33.1 | 28.3 | 13.94 | 0.0776 | 0.19 | 12.93 | 1
December | 2 | 11PM to 12AM | 41 | 38.3 | 35.1 | 30.6 | 14.57 | 0.0774 | 0.2 | 12.97 | 1
December | 3 | 12AM to 1AM | 41 | 38.7 | 36 | 31.8 | 14.74 | 0.0774 | 0.21 | 12.97 | 1
December | 3 | 1AM to 2AM | 41 | 39.2 | 37 | 33.2 | 14.95 | 0.0774 | 0.22 | 12.98 | 1
December | 3 | 2AM to 3AM | 41 | 38.7 | 36 | 31.8 | 14.74 | 0.0774 | 0.21 | 12.97 | 1
December | 3 | 3AM to 4AM | 39.9 | 37.7 | 35.1 | 30.6 | 14.3 | 0.0776 | 0.2 | 12.94 | 1
December | 3 | 4AM to 5AM | 37.9 | 36.2 | 34 | 29.3 | 13.63 | 0.0779 | 0.2 | 12.89 | 1
December | 3 | 5AM to 6AM | 37 | 35.3 | 33.1 | 28.3 | 13.25 | 0.0781 | 0.19 | 12.86 | 1
December | 3 | 6AM to 7AM | 37.9 | 36.2 | 34 | 29.3 | 13.63 | 0.0779 | 0.2 | 12.89 | 1
December | 3 | 7AM to 8AM | 39 | 37.6 | 36 | 31.8 | 14.26 | 0.0777 | 0.21 | 12.92 | 1
December | 3 | 8AM to 9AM | 41 | 38.3 | 35.1 | 30.6 | 14.57 | 0.0774 | 0.2 | 12.97 | 1
December | 3 | 9AM to 10AM | 44.1 | 39.9 | 35.1 | 30.6 | 15.31 | 0.077 | 0.2 | 13.05 | 1
December | 3 | 10AM to 11AM | 46 | 41 | 35.1 | 30.6 | 15.79 | 0.0767 | 0.2 | 13.1 | 1
December | 3 | 11AM to 12PM | 50 | 42.5 | 34 | 29.3 | 16.54 | 0.0761 | 0.2 | 13.2 | 1
December | 3 | 12PM to 1PM | 51.1 | 43.5 | 35.1 | 30.6 | 17 | 0.0759 | 0.2 | 13.23 | 1
December | 3 | 1PM to 2PM | 52 | 43.2 | 33.1 | 28.3 | 16.86 | 0.0758 | 0.19 | 13.25 | 0
December | 3 | 2PM to 3PM | 53.1 | 42.9 | 30.9 | 25.8 | 16.73 | 0.0757 | 0.17 | 13.27 | 0
December | 3 | 3PM to 4PM | 52 | 42.8 | 32 | 27.1 | 16.67 | 0.0758 | 0.18 | 13.24 | 0
December | 3 | 4PM to 5PM | 45 | 42.5 | 39.9 | 37.2 | 16.53 | 0.0768 | 0.25 | 13.09 | 1
December | 3 | 5PM to 6PM | 45 | 42.1 | 39 | 35.9 | 16.33 | 0.0768 | 0.24 | 13.09 | 1
December | 3 | 6PM to 7PM | 45 | 40 | 34 | 29.3 | 15.32 | 0.0768 | 0.2 | 13.07 | 1
December | 3 | 7PM to 8PM | 44.1 | 37.9 | 30 | 24.7 | 14.39 | 0.077 | 0.16 | 13.03 | 1
December | 3 | 8PM to 9PM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
December | 3 | 9PM to 10PM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
December | 3 | 10PM to 11PM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
December | 3 | 11PM to 12AM | 43 | 37.4 | 30 | 24.7 | 14.13 | 0.0772 | 0.16 | 13 | 1
December | 4 | 12AM to 1AM | 43 | 37.7 | 30.9 | 25.8 | 14.29 | 0.0772 | 0.17 | 13.01 | 1
December | 4 | 1AM to 2AM | 42.1 | 37.7 | 32 | 27.1 | 14.28 | 0.0773 | 0.18 | 12.99 | 1
December | 4 | 2AM to 3AM | 39.9 | 35.7 | 30 | 24.7 | 13.39 | 0.0776 | 0.16 | 12.92 | 1
December | 4 | 3AM to 4AM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
December | 4 | 4AM to 5AM | 36 | 33.4 | 30 | 24.7 | 12.43 | 0.0783 | 0.16 | 12.82 | 1
December | 4 | 5AM to 6AM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
December | 4 | 6AM to 7AM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
December | 4 | 7AM to 8AM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
December | 4 | 8AM to 9AM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
December | 4 | 9AM to 10AM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
December | 4 | 10AM to 11AM | 37 | 33.3 | 28 | 22.5 | 12.36 | 0.0781 | 0.15 | 12.84 | 1
December | 4 | 11AM to 12PM | 39 | 34.4 | 28 | 22.5 | 12.84 | 0.0778 | 0.15 | 12.89 | 1
December | 4 | 12PM to 1PM | 39.9 | 34.2 | 26.1 | 20.5 | 12.75 | 0.0777 | 0.14 | 12.91 | 1
December | 4 | 1PM to 2PM | 41 | 35.5 | 28 | 22.5 | 13.32 | 0.0775 | 0.15 | 12.95 | 1
December | 4 | 2PM to 3PM | 41 | 35.1 | 27 | 21.4 | 13.15 | 0.0775 | 0.14 | 12.94 | 1
December | 4 | 3PM to 4PM | 41 | 35.1 | 27 | 21.4 | 13.15 | 0.0775 | 0.14 | 12.94 | 1
December | 4 | 4PM to 5PM | 37 | 33.3 | 28 | 22.5 | 12.36 | 0.0781 | 0.15 | 12.84 | 1
December | 4 | 5PM to 6PM | 34 | 31.3 | 28 | 22.5 | 11.62 | 0.0786 | 0.15 | 12.76 | 1
December | 4 | 6PM to 7PM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
December | 4 | 7PM to 8PM | 33.1 | 31.2 | 28.9 | 23.5 | 11.55 | 0.0787 | 0.16 | 12.74 | 1
December | 4 | 8PM to 9PM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
December | 4 | 9PM to 10PM | 32 | 30.6 | 28.9 | 23.5 | 11.29 | 0.0789 | 0.16 | 12.72 | 1
December | 4 | 10PM to 11PM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
December | 4 | 11PM to 12AM | 32 | 30.6 | 28.9 | 23.5 | 11.29 | 0.0789 | 0.16 | 12.72 | 1
December | 5 | 12AM to 1AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
December | 5 | 1AM to 2AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
December | 5 | 2AM to 3AM | 30 | 29.2 | 28 | 22.5 | 10.67 | 0.0792 | 0.15 | 12.66 | 1
December | 5 | 3AM to 4AM | 28.9 | 28.5 | 28 | 22.5 | 10.41 | 0.0794 | 0.15 | 12.63 | 1
December | 5 | 4AM to 5AM | 28.9 | 28.5 | 28 | 22.5 | 10.41 | 0.0794 | 0.15 | 12.63 | 1
December | 5 | 5AM to 6AM | 30 | 29.5 | 28.9 | 23.5 | 10.81 | 0.0792 | 0.16 | 12.66 | 1
December | 5 | 6AM to 7AM | 28 | 27.6 | 27 | 21.4 | 10.02 | 0.0796 | 0.14 | 12.61 | 1
December | 5 | 7AM to 8AM | 30 | 29.2 | 28 | 22.5 | 10.67 | 0.0792 | 0.15 | 12.66 | 1
December | 5 | 8AM to 9AM | 33.1 | 32.1 | 30.9 | 25.8 | 11.9 | 0.0787 | 0.17 | 12.75 | 1
December | 5 | 9AM to 10AM | 37.9 | 35.8 | 33.1 | 28.3 | 13.46 | 0.0779 | 0.19 | 12.88 | 1
December | 5 | 10AM to 11AM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
December | 5 | 11AM to 12PM | 42.1 | 38.5 | 34 | 29.3 | 14.63 | 0.0773 | 0.2 | 12.99 | 1
December | 5 | 12PM to 1PM | 43 | 38.9 | 34 | 29.3 | 14.84 | 0.0771 | 0.2 | 13.02 | 1
December | 5 | 1PM to 2PM | 44.1 | 39.5 | 34 | 29.3 | 15.11 | 0.077 | 0.2 | 13.04 | 1
December | 5 | 2PM to 3PM | 44.1 | 39.2 | 33.1 | 28.3 | 14.94 | 0.077 | 0.19 | 13.04 | 1
December | 5 | 3PM to 4PM | 43 | 38.6 | 33.1 | 28.3 | 14.68 | 0.0772 | 0.19 | 13.01 | 1
December | 5 | 4PM to 5PM | 41 | 37.9 | 34 | 29.3 | 14.37 | 0.0774 | 0.2 | 12.97 | 1
December | 5 | 5PM to 6PM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
December | 5 | 6PM to 7PM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
December | 5 | 7PM to 8PM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
December | 5 | 8PM to 9PM | 37.9 | 35.8 | 33.1 | 28.3 | 13.46 | 0.0779 | 0.19 | 12.88 | 1
December | 5 | 9PM to 10PM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
December | 5 | 10PM to 11PM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
December | 5 | 11PM to 12AM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
December | 6 | 12AM to 1AM | 37 | 35.7 | 34 | 29.3 | 13.41 | 0.0781 | 0.2 | 12.86 | 1
December | 6 | 1AM to 2AM | 39 | 36.8 | 34 | 29.3 | 13.89 | 0.0778 | 0.2 | 12.91 | 1
December | 6 | 2AM to 3AM | 39 | 36.8 | 34 | 29.3 | 13.89 | 0.0778 | 0.2 | 12.91 | 1
December | 6 | 3AM to 4AM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
December | 6 | 4AM to 5AM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
December | 6 | 5AM to 6AM | 37 | 35.7 | 34 | 29.3 | 13.41 | 0.0781 | 0.2 | 12.86 | 1
December | 6 | 6AM to 7AM | 37 | 35.3 | 33.1 | 28.3 | 13.25 | 0.0781 | 0.19 | 12.86 | 1
December | 6 | 7AM to 8AM | 37.9 | 35.4 | 32 | 27.1 | 13.28 | 0.0779 | 0.18 | 12.88 | 1
December | 6 | 8AM to 9AM | 41 | 37.1 | 32 | 27.1 | 14.02 | 0.0775 | 0.18 | 12.96 | 1
December | 6 | 9AM to 10AM | 45 | 39.2 | 32 | 27.1 | 14.98 | 0.0769 | 0.18 | 13.06 | 1
December | 6 | 10AM to 11AM | 48 | 40.4 | 30.9 | 25.8 | 15.51 | 0.0764 | 0.17 | 13.14 | 1
December | 6 | 11AM to 12PM | 52 | 42.8 | 32 | 27.1 | 16.67 | 0.0758 | 0.18 | 13.24 | 0
December | 6 | 12PM to 1PM | 54 | 44.2 | 33.1 | 28.3 | 17.34 | 0.0755 | 0.19 | 13.3 | 0
December | 6 | 1PM to 2PM | 55 | 45 | 34 | 29.3 | 17.76 | 0.0753 | 0.2 | 13.33 | 0
December | 6 | 2PM to 3PM | 57 | 45.9 | 34 | 29.3 | 18.24 | 0.075 | 0.2 | 13.38 | 0
December | 6 | 3PM to 4PM | 55 | 45 | 34 | 29.3 | 17.76 | 0.0753 | 0.2 | 13.33 | 0
December | 6 | 4PM to 5PM | 53.1 | 44.4 | 35.1 | 30.6 | 17.48 | 0.0756 | 0.2 | 13.28 | 0
December | 6 | 5PM to 6PM | 51.1 | 43.5 | 35.1 | 30.6 | 17 | 0.0759 | 0.2 | 13.23 | 1
December | 6 | 6PM to 7PM | 50 | 42.9 | 35.1 | 30.6 | 16.74 | 0.0761 | 0.2 | 13.2 | 1
December | 6 | 7PM to 8PM | 48.9 | 42.8 | 36 | 31.8 | 16.66 | 0.0762 | 0.21 | 13.18 | 1
December | 6 | 8PM to 9PM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
December | 6 | 9PM to 10PM | 48.9 | 44 | 39 | 35.9 | 17.29 | 0.0762 | 0.24 | 13.19 | 1
December | 6 | 10PM to 11PM | 48 | 43.6 | 39 | 35.9 | 17.07 | 0.0763 | 0.24 | 13.17 | 1
December | 6 | 11PM to 12AM | 48.9 | 44.4 | 39.9 | 37.2 | 17.49 | 0.0762 | 0.25 | 13.19 | 1
December | 7 | 12AM to 1AM | 48 | 44.5 | 41 | 38.8 | 17.52 | 0.0763 | 0.26 | 13.18 | 1
December | 7 | 1AM to 2AM | 48 | 45.4 | 43 | 41.9 | 18 | 0.0763 | 0.28 | 13.19 | 1
December | 7 | 2AM to 3AM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
December | 7 | 3AM to 4AM | 46.9 | 45.4 | 44.1 | 43.6 | 18.01 | 0.0764 | 0.29 | 13.16 | 1
December | 7 | 4AM to 5AM | 48 | 47 | 46 | 47.1 | 18.81 | 0.0763 | 0.31 | 13.2 | 1
December | 7 | 5AM to 6AM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
December | 7 | 6AM to 7AM | 50 | 48.9 | 48 | 50.8 | 19.86 | 0.0759 | 0.34 | 13.26 | 1
December | 7 | 7AM to 8AM | 50 | 49.4 | 48.9 | 52.6 | 20.14 | 0.0759 | 0.35 | 13.27 | 1
December | 7 | 8AM to 9AM | 54 | 52.3 | 51.1 | 57 | 21.79 | 0.0753 | 0.38 | 13.39 | 0
December | 7 | 9AM to 10AM | 57 | 54.1 | 52 | 59 | 22.84 | 0.0749 | 0.39 | 13.47 | 0
December | 7 | 10AM to 11AM | 61 | 55.2 | 51.1 | 57 | 23.5 | 0.0743 | 0.38 | 13.57 | 0
December | 7 | 11AM to 12PM | 63 | 55.4 | 50 | 54.7 | 23.63 | 0.074 | 0.36 | 13.61 | 0
December | 7 | 12PM to 1PM | 64.9 | 55.6 | 48.9 | 52.6 | 23.77 | 0.0738 | 0.35 | 13.66 | 0
December | 7 | 1PM to 2PM | 64 | 54.3 | 46.9 | 48.8 | 22.96 | 0.0739 | 0.32 | 13.62 | 0
December | 7 | 2PM to 3PM | 64.9 | 54.7 | 46.9 | 48.8 | 23.18 | 0.0738 | 0.32 | 13.65 | 0
December | 7 | 3PM to 4PM | 63 | 53.9 | 46.9 | 48.8 | 22.7 | 0.0741 | 0.32 | 13.59 | 0
December | 7 | 4PM to 5PM | 57.9 | 50.8 | 45 | 45.2 | 20.92 | 0.0748 | 0.3 | 13.45 | 0
December | 7 | 5PM to 6PM | 55 | 49.2 | 44.1 | 43.6 | 19.98 | 0.0752 | 0.29 | 13.37 | 0
December | 7 | 6PM to 7PM | 53.1 | 47.8 | 43 | 41.9 | 19.22 | 0.0755 | 0.28 | 13.32 | 0
December | 7 | 7PM to 8PM | 51.1 | 46.4 | 42.1 | 40.4 | 18.52 | 0.0758 | 0.27 | 13.26 | 1
December | 7 | 8PM to 9PM | 50 | 44.1 | 37.9 | 34.4 | 17.32 | 0.076 | 0.23 | 13.21 | 1
December | 7 | 9PM to 10PM | 46.9 | 42.2 | 37 | 33.2 | 16.39 | 0.0765 | 0.22 | 13.13 | 1
December | 7 | 10PM to 11PM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
December | 7 | 11PM to 12AM | 43 | 40.2 | 37 | 33.2 | 15.43 | 0.0771 | 0.22 | 13.03 | 1
December | 8 | 12AM to 1AM | 39.9 | 37.7 | 35.1 | 30.6 | 14.3 | 0.0776 | 0.2 | 12.94 | 1
December | 8 | 1AM to 2AM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
December | 8 | 2AM to 3AM | 35.1 | 33.3 | 30.9 | 25.8 | 12.38 | 0.0784 | 0.17 | 12.8 | 1
December | 8 | 3AM to 4AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
December | 8 | 4AM to 5AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
December | 8 | 5AM to 6AM | 30.9 | 30.5 | 30 | 24.7 | 11.22 | 0.0791 | 0.16 | 12.69 | 1
December | 8 | 6AM to 7AM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
December | 8 | 7AM to 8AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
December | 8 | 8AM to 9AM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
December | 8 | 9AM to 10AM | 36 | 33.4 | 30 | 24.7 | 12.43 | 0.0783 | 0.16 | 12.82 | 1
December | 8 | 10AM to 11AM | 39 | 35.5 | 30.9 | 25.8 | 13.34 | 0.0778 | 0.17 | 12.9 | 1
December | 8 | 11AM to 12PM | 42.1 | 36.9 | 30 | 24.7 | 13.91 | 0.0773 | 0.16 | 12.98 | 1
December | 8 | 12PM to 1PM | 44.1 | 37.5 | 28.9 | 23.5 | 14.2 | 0.077 | 0.16 | 13.03 | 1
December | 8 | 1PM to 2PM | 46.9 | 38.7 | 28 | 22.5 | 14.75 | 0.0766 | 0.15 | 13.1 | 1
December | 8 | 2PM to 3PM | 46.9 | 37.1 | 23 | 17.8 | 14.01 | 0.0766 | 0.12 | 13.08 | 1
December | 8 | 3PM to 4PM | 45 | 35.7 | 21.9 | 16.9 | 13.4 | 0.0769 | 0.11 | 13.03 | 1
December | 8 | 4PM to 5PM | 42.1 | 35 | 25 | 19.5 | 13.11 | 0.0773 | 0.13 | 12.96 | 1
December | 8 | 5PM to 6PM | 42.1 | 35.7 | 27 | 21.4 | 13.41 | 0.0773 | 0.14 | 12.97 | 1
December | 8 | 6PM to 7PM | 39 | 34 | 27 | 21.4 | 12.67 | 0.0778 | 0.14 | 12.89 | 1
December | 8 | 7PM to 8PM | 37.9 | 33.8 | 28 | 22.5 | 12.58 | 0.078 | 0.15 | 12.87 | 1
December | 8 | 8PM to 9PM | 35.1 | 32.1 | 28 | 22.5 | 11.88 | 0.0784 | 0.15 | 12.79 | 1
December | 8 | 9PM to 10PM | 37 | 34.4 | 30.9 | 25.8 | 12.86 | 0.0781 | 0.17 | 12.85 | 1
December | 8 | 10PM to 11PM | 39 | 36 | 32 | 27.1 | 13.54 | 0.0778 | 0.18 | 12.91 | 1
December | 8 | 11PM to 12AM | 39 | 35.5 | 30.9 | 25.8 | 13.34 | 0.0778 | 0.17 | 12.9 | 1
December | 9 | 12AM to 1AM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
December | 9 | 1AM to 2AM | 35.1 | 32.1 | 28 | 22.5 | 11.88 | 0.0784 | 0.15 | 12.79 | 1
December | 9 | 2AM to 3AM | 33.1 | 30.4 | 27 | 21.4 | 11.23 | 0.0787 | 0.14 | 12.74 | 1
December | 9 | 3AM to 4AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
December | 9 | 4AM to 5AM | 30 | 28.3 | 26.1 | 20.5 | 10.36 | 0.0792 | 0.14 | 12.66 | 1
December | 9 | 5AM to 6AM | 28 | 26.8 | 25 | 19.5 | 9.72 | 0.0796 | 0.13 | 12.6 | 1
December | 9 | 6AM to 7AM | 26.1 | 25.3 | 24.1 | 18.7 | 9.12 | 0.0799 | 0.12 | 12.55 | 1
December | 9 | 7AM to 8AM | 28 | 26.8 | 25 | 19.5 | 9.72 | 0.0796 | 0.13 | 12.6 | 1
December | 9 | 8AM to 9AM | 30.9 | 28.8 | 26.1 | 20.5 | 10.58 | 0.0791 | 0.14 | 12.68 | 1
December | 9 | 9AM to 10AM | 33.1 | 28.9 | 23 | 17.8 | 10.67 | 0.0788 | 0.12 | 12.73 | 1
December | 9 | 10AM to 11AM | 35.1 | 29.7 | 21.9 | 16.9 | 11.01 | 0.0785 | 0.11 | 12.78 | 1
December | 9 | 11AM to 12PM | 34 | 29.1 | 21.9 | 16.9 | 10.75 | 0.0786 | 0.11 | 12.75 | 1
December | 9 | 12PM to 1PM | 34 | 29.4 | 23 | 17.8 | 10.89 | 0.0786 | 0.12 | 12.75 | 1
December | 9 | 1PM to 2PM | 34 | 29.1 | 21.9 | 16.9 | 10.75 | 0.0786 | 0.11 | 12.75 | 1
December | 9 | 2PM to 3PM | 34 | 29.1 | 21.9 | 16.9 | 10.75 | 0.0786 | 0.11 | 12.75 | 1
December | 9 | 3PM to 4PM | 33.1 | 28.9 | 23 | 17.8 | 10.67 | 0.0788 | 0.12 | 12.73 | 1
December | 9 | 4PM to 5PM | 33.1 | 28.6 | 21.9 | 16.9 | 10.53 | 0.0788 | 0.11 | 12.72 | 1
December | 9 | 5PM to 6PM | 32 | 28 | 21.9 | 16.9 | 10.27 | 0.079 | 0.11 | 12.7 | 1
December | 9 | 6PM to 7PM | 32 | 28 | 21.9 | 16.9 | 10.27 | 0.079 | 0.11 | 12.7 | 1
December | 9 | 7PM to 8PM | 32 | 28 | 21.9 | 16.9 | 10.27 | 0.079 | 0.11 | 12.7 | 1
December | 9 | 8PM to 9PM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
December | 9 | 9PM to 10PM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
December | 9 | 10PM to 11PM | 30 | 26.5 | 21 | 16.2 | 9.69 | 0.0793 | 0.11 | 12.64 | 1
December | 9 | 11PM to 12AM | 30 | 26.5 | 21 | 16.2 | 9.69 | 0.0793 | 0.11 | 12.64 | 1
December | 10 | 12AM to 1AM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
December | 10 | 1AM to 2AM | 30 | 26.2 | 19.9 | 15.3 | 9.56 | 0.0793 | 0.1 | 12.64 | 1
December | 10 | 2AM to 3AM | 28 | 24.7 | 19 | 14.7 | 8.98 | 0.0796 | 0.1 | 12.59 | 1
December | 10 | 3AM to 4AM | 27 | 24.1 | 19 | 14.7 | 8.72 | 0.0798 | 0.1 | 12.56 | 1
December | 10 | 4AM to 5AM | 25 | 23.1 | 19.9 | 15.3 | 8.35 | 0.0801 | 0.1 | 12.51 | 1
December | 10 | 5AM to 6AM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
December | 10 | 6AM to 7AM | 23 | 21 | 17.1 | 13.3 | 7.56 | 0.0804 | 0.09 | 12.45 | 1
December | 10 | 7AM to 8AM | 23 | 21 | 17.1 | 13.3 | 7.56 | 0.0804 | 0.09 | 12.45 | 1
December | 10 | 8AM to 9AM | 25 | 22.2 | 17.1 | 13.3 | 8.04 | 0.0801 | 0.09 | 12.51 | 1
December | 10 | 9AM to 10AM | 28 | 23.8 | 16 | 12.7 | 8.67 | 0.0796 | 0.08 | 12.58 | 1
December | 10 | 10AM to 11AM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
December | 10 | 11AM to 12PM | 32 | 25.4 | 12.9 | 10.9 | 9.35 | 0.079 | 0.07 | 12.68 | 1
December | 10 | 12PM to 1PM | 34 | 26.6 | 12.9 | 10.9 | 9.83 | 0.0787 | 0.07 | 12.73 | 1
December | 10 | 1PM to 2PM | 35.1 | 27.5 | 14 | 11.5 | 10.18 | 0.0785 | 0.08 | 12.76 | 1
December | 10 | 2PM to 3PM | 36 | 28 | 14 | 11.5 | 10.4 | 0.0784 | 0.08 | 12.78 | 1
December | 10 | 3PM to 4PM | 35.1 | 28 | 16 | 12.7 | 10.36 | 0.0785 | 0.08 | 12.76 | 1
December | 10 | 4PM to 5PM | 33.1 | 26.8 | 16 | 12.7 | 9.89 | 0.0788 | 0.08 | 12.71 | 1
December | 10 | 5PM to 6PM | 32 | 26.2 | 16 | 12.7 | 9.63 | 0.079 | 0.08 | 12.68 | 1
December | 10 | 6PM to 7PM | 30 | 25 | 16 | 12.7 | 9.15 | 0.0793 | 0.08 | 12.63 | 1
December | 10 | 7PM to 8PM | 30 | 25 | 16 | 12.7 | 9.15 | 0.0793 | 0.08 | 12.63 | 1
December | 10 | 8PM to 9PM | 30.9 | 25.8 | 17.1 | 13.3 | 9.47 | 0.0791 | 0.09 | 12.66 | 1
December | 10 | 9PM to 10PM | 30.9 | 25.8 | 17.1 | 13.3 | 9.47 | 0.0791 | 0.09 | 12.66 | 1
December | 10 | 10PM to 11PM | 30.9 | 25.6 | 16 | 12.7 | 9.37 | 0.0792 | 0.08 | 12.66 | 1
December | 10 | 11PM to 12AM | 30.9 | 25.6 | 16 | 12.7 | 9.37 | 0.0792 | 0.08 | 12.66 | 1
December | 11 | 12AM to 1AM | 32 | 26.2 | 16 | 12.7 | 9.63 | 0.079 | 0.08 | 12.68 | 1
December | 11 | 1AM to 2AM | 32 | 26.5 | 17.1 | 13.3 | 9.73 | 0.079 | 0.09 | 12.69 | 1
December | 11 | 2AM to 3AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
December | 11 | 3AM to 4AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
December | 11 | 4AM to 5AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
December | 11 | 5AM to 6AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
December | 11 | 6AM to 7AM | 30.9 | 26.4 | 19 | 14.7 | 9.68 | 0.0791 | 0.1 | 12.66 | 1
December | 11 | 7AM to 8AM | 32 | 27.3 | 19.9 | 15.3 | 10.04 | 0.079 | 0.1 | 12.69 | 1
December | 11 | 8AM to 9AM | 32 | 27 | 19 | 14.7 | 9.94 | 0.079 | 0.1 | 12.69 | 1
December | 11 | 9AM to 10AM | 33.1 | 27.7 | 19 | 14.7 | 10.2 | 0.0788 | 0.1 | 12.72 | 1
December | 11 | 10AM to 11AM | 34 | 28.4 | 19.9 | 15.3 | 10.52 | 0.0786 | 0.1 | 12.74 | 1
December | 11 | 11AM to 12PM | 35.1 | 29.1 | 19.9 | 15.3 | 10.78 | 0.0785 | 0.1 | 12.77 | 1
December | 11 | 12PM to 1PM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
December | 11 | 1PM to 2PM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
December | 11 | 2PM to 3PM | 37 | 30.5 | 21 | 16.2 | 11.38 | 0.0782 | 0.11 | 12.82 | 1
December | 11 | 3PM to 4PM | 37 | 30.7 | 21.9 | 16.9 | 11.49 | 0.0782 | 0.11 | 12.83 | 1
December | 11 | 4PM to 5PM | 36 | 30.5 | 23 | 17.8 | 11.37 | 0.0783 | 0.12 | 12.8 | 1
December | 11 | 5PM to 6PM | 34 | 29.4 | 23 | 17.8 | 10.89 | 0.0786 | 0.12 | 12.75 | 1
December | 11 | 6PM to 7PM | 35.1 | 30 | 23 | 17.8 | 11.15 | 0.0785 | 0.12 | 12.78 | 1
December | 11 | 7PM to 8PM | 36 | 30.9 | 24.1 | 18.7 | 11.51 | 0.0783 | 0.12 | 12.8 | 1
December | 11 | 8PM to 9PM | 35.1 | 30 | 23 | 17.8 | 11.15 | 0.0785 | 0.12 | 12.78 | 1
December | 11 | 9PM to 10PM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
December | 11 | 10PM to 11PM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
December | 11 | 11PM to 12AM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
December | 12 | 12AM to 1AM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
December | 12 | 1AM to 2AM | 30 | 27.9 | 25 | 19.5 | 10.2 | 0.0793 | 0.13 | 12.65 | 1
December | 12 | 2AM to 3AM | 28 | 26.8 | 25 | 19.5 | 9.72 | 0.0796 | 0.13 | 12.6 | 1
December | 12 | 3AM to 4AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
December | 12 | 4AM to 5AM | 27 | 25.8 | 24.1 | 18.7 | 9.34 | 0.0798 | 0.12 | 12.57 | 1
December | 12 | 5AM to 6AM | 27 | 25.4 | 23 | 17.8 | 9.2 | 0.0798 | 0.12 | 12.57 | 1
December | 12 | 6AM to 7AM | 26.1 | 24.5 | 21.9 | 16.9 | 8.84 | 0.0799 | 0.11 | 12.54 | 1
December | 12 | 7AM to 8AM | 26.1 | 24.5 | 21.9 | 16.9 | 8.84 | 0.0799 | 0.11 | 12.54 | 1
December | 12 | 8AM to 9AM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
December | 12 | 9AM to 10AM | 33.1 | 30 | 26.1 | 20.5 | 11.1 | 0.0788 | 0.14 | 12.74 | 1
December | 12 | 10AM to 11AM | 37.9 | 31.9 | 24.1 | 18.7 | 11.99 | 0.078 | 0.12 | 12.86 | 1
December | 12 | 11AM to 12PM | 39.9 | 31.7 | 19.9 | 15.3 | 11.95 | 0.0777 | 0.1 | 12.9 | 1
December | 12 | 12PM to 1PM | 42.1 | 32.5 | 16 | 12.7 | 12.05 | 0.0774 | 0.08 | 12.94 | 1
December | 12 | 1PM to 2PM | 42.1 | 32.3 | 15.1 | 12.1 | 11.97 | 0.0774 | 0.08 | 12.94 | 1
December | 12 | 2PM to 3PM | 42.1 | 32.5 | 16 | 12.7 | 12.05 | 0.0774 | 0.08 | 12.94 | 1
December | 12 | 3PM to 4PM | 39.9 | 31.4 | 19 | 14.7 | 11.85 | 0.0777 | 0.1 | 12.89 | 1
December | 12 | 4PM to 5PM | 37 | 29.9 | 19 | 14.7 | 11.15 | 0.0782 | 0.1 | 12.82 | 1
December | 12 | 5PM to 6PM | 37 | 29.9 | 19 | 14.7 | 11.15 | 0.0782 | 0.1 | 12.82 | 1
December | 12 | 6PM to 7PM | 34 | 28.8 | 21 | 16.2 | 10.64 | 0.0786 | 0.11 | 12.75 | 1
December | 12 | 7PM to 8PM | 30 | 27.6 | 24.1 | 18.7 | 10.08 | 0.0793 | 0.12 | 12.65 | 1
December | 12 | 8PM to 9PM | 28.9 | 26.6 | 23 | 17.8 | 9.67 | 0.0794 | 0.12 | 12.62 | 1
December | 12 | 9PM to 10PM | 28.9 | 26.6 | 23 | 17.8 | 9.67 | 0.0794 | 0.12 | 12.62 | 1
December | 12 | 10PM to 11PM | 28 | 26.4 | 24.1 | 18.7 | 9.6 | 0.0796 | 0.12 | 12.6 | 1
December | 12 | 11PM to 12AM | 27 | 25.8 | 24.1 | 18.7 | 9.34 | 0.0798 | 0.12 | 12.57 | 1
December | 13 | 12AM to 1AM | 27 | 26.2 | 25 | 19.5 | 9.46 | 0.0798 | 0.13 | 12.57 | 1
December | 13 | 1AM to 2AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
December | 13 | 2AM to 3AM | 28.9 | 27 | 24.1 | 18.7 | 9.82 | 0.0794 | 0.12 | 12.62 | 1
December | 13 | 3AM to 4AM | 28.9 | 27.3 | 25 | 19.5 | 9.94 | 0.0794 | 0.13 | 12.63 | 1
December | 13 | 4AM to 5AM | 28.9 | 27.7 | 26.1 | 20.5 | 10.1 | 0.0794 | 0.14 | 12.63 | 1
December | 13 | 5AM to 6AM | 28.9 | 27.7 | 26.1 | 20.5 | 10.1 | 0.0794 | 0.14 | 12.63 | 1
December | 13 | 6AM to 7AM | 28 | 27.2 | 26.1 | 20.5 | 9.88 | 0.0796 | 0.14 | 12.6 | 1
December | 13 | 7AM to 8AM | 28 | 27.6 | 27 | 21.4 | 10.02 | 0.0796 | 0.14 | 12.61 | 1
December | 13 | 8AM to 9AM | 30 | 28.7 | 27 | 21.4 | 10.5 | 0.0792 | 0.14 | 12.66 | 1
December | 13 | 9AM to 10AM | 33.1 | 30 | 26.1 | 20.5 | 11.1 | 0.0788 | 0.14 | 12.74 | 1
December | 13 | 10AM to 11AM | 35.1 | 31.1 | 26.1 | 20.5 | 11.58 | 0.0784 | 0.14 | 12.79 | 1
December | 13 | 11AM to 12PM | 37.9 | 33 | 26.1 | 20.5 | 12.27 | 0.078 | 0.14 | 12.86 | 1
December | 13 | 12PM to 1PM | 39.9 | 33.8 | 25 | 19.5 | 12.59 | 0.0777 | 0.13 | 12.91 | 1
December | 13 | 1PM to 2PM | 39.9 | 33.2 | 23 | 17.8 | 12.32 | 0.0777 | 0.12 | 12.9 | 1
December | 13 | 2PM to 3PM | 39 | 33 | 24.1 | 18.7 | 12.25 | 0.0778 | 0.12 | 12.88 | 1
December | 13 | 3PM to 4PM | 39 | 33.3 | 25 | 19.5 | 12.37 | 0.0778 | 0.13 | 12.89 | 1
December | 13 | 4PM to 5PM | 37.9 | 33 | 26.1 | 20.5 | 12.27 | 0.078 | 0.14 | 12.86 | 1
December | 13 | 5PM to 6PM | 37 | 32.5 | 26.1 | 20.5 | 12.05 | 0.0781 | 0.14 | 12.84 | 1
December | 13 | 6PM to 7PM | 37 | 32.8 | 27 | 21.4 | 12.19 | 0.0781 | 0.14 | 12.84 | 1
December | 13 | 7PM to 8PM | 37 | 32.8 | 27 | 21.4 | 12.19 | 0.0781 | 0.14 | 12.84 | 1
December | 13 | 8PM to 9PM | 37 | 32.8 | 27 | 21.4 | 12.19 | 0.0781 | 0.14 | 12.84 | 1
December | 13 | 9PM to 10PM | 36 | 31.9 | 27 | 21.4 | 11.93 | 0.0783 | 0.14 | 12.81 | 1
December | 13 | 10PM to 11PM | 36 | 32.6 | 28 | 22.5 | 12.1 | 0.0783 | 0.15 | 12.82 | 1
December | 13 | 11PM to 12AM | 36 | 32.6 | 28 | 22.5 | 12.1 | 0.0783 | 0.15 | 12.82 | 1
December | 14 | 12AM to 1AM | 35.1 | 32.1 | 28 | 22.5 | 11.88 | 0.0784 | 0.15 | 12.79 | 1
December | 14 | 1AM to 2AM | 32 | 30.2 | 28 | 22.5 | 11.14 | 0.0789 | 0.15 | 12.71 | 1
December | 14 | 2AM to 3AM | 30 | 28.7 | 27 | 21.4 | 10.5 | 0.0792 | 0.14 | 12.66 | 1
December | 14 | 3AM to 4AM | 28.9 | 28.5 | 28 | 22.5 | 10.41 | 0.0794 | 0.15 | 12.63 | 1
December | 14 | 4AM to 5AM | 30 | 29.5 | 28.9 | 23.5 | 10.81 | 0.0792 | 0.16 | 12.66 | 1
December | 14 | 5AM to 6AM | 28.9 | 28.5 | 28 | 22.5 | 10.41 | 0.0794 | 0.15 | 12.63 | 1
December | 14 | 6AM to 7AM | 30 | 29.5 | 28.9 | 23.5 | 10.81 | 0.0792 | 0.16 | 12.66 | 1
December | 14 | 7AM to 8AM | 30 | 29.5 | 28.9 | 23.5 | 10.81 | 0.0792 | 0.16 | 12.66 | 1
December | 14 | 8AM to 9AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
December | 14 | 9AM to 10AM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
December | 14 | 10AM to 11AM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
December | 14 | 11AM to 12PM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
December | 14 | 12PM to 1PM | 37 | 34.4 | 30.9 | 25.8 | 12.86 | 0.0781 | 0.17 | 12.85 | 1
December | 14 | 1PM to 2PM | 39 | 36 | 32 | 27.1 | 13.54 | 0.0778 | 0.18 | 12.91 | 1
December | 14 | 2PM to 3PM | 39 | 35.5 | 30.9 | 25.8 | 13.34 | 0.0778 | 0.17 | 12.9 | 1
December | 14 | 3PM to 4PM | 39 | 35.5 | 30.9 | 25.8 | 13.34 | 0.0778 | 0.17 | 12.9 | 1
December | 14 | 4PM to 5PM | 39 | 35.5 | 30.9 | 25.8 | 13.34 | 0.0778 | 0.17 | 12.9 | 1
December | 14 | 5PM to 6PM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
December | 14 | 6PM to 7PM | 37 | 34 | 30 | 24.7 | 12.7 | 0.0781 | 0.16 | 12.85 | 1
December | 14 | 7PM to 8PM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
December | 14 | 8PM to 9PM | 36 | 33.8 | 30.9 | 25.8 | 12.6 | 0.0783 | 0.17 | 12.82 | 1
December | 14 | 9PM to 10PM | 35.1 | 32.9 | 30 | 24.7 | 12.22 | 0.0784 | 0.16 | 12.8 | 1
December | 14 | 10PM to 11PM | 34 | 30.5 | 26.1 | 20.5 | 11.31 | 0.0786 | 0.14 | 12.76 | 1
December | 14 | 11PM to 12AM | 33.1 | 28.3 | 21 | 16.2 | 10.42 | 0.0788 | 0.11 | 12.72 | 1
December | 15 | 12AM to 1AM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
December | 15 | 1AM to 2AM | 27 | 23.5 | 17.1 | 13.3 | 8.52 | 0.0798 | 0.09 | 12.56 | 1
December | 15 | 2AM to 3AM | 25 | 22.5 | 18 | 13.9 | 8.13 | 0.0801 | 0.09 | 12.51 | 1
December | 15 | 3AM to 4AM | 25 | 22.8 | 19 | 14.7 | 8.25 | 0.0801 | 0.1 | 12.51 | 1
December | 15 | 4AM to 5AM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
December | 15 | 5AM to 6AM | 23 | 20.7 | 16 | 12.7 | 7.46 | 0.0805 | 0.08 | 12.45 | 1
December | 15 | 6AM to 7AM | 21 | 19.4 | 16 | 12.7 | 6.98 | 0.0808 | 0.08 | 12.4 | 1
December | 15 | 7AM to 8AM | 21.9 | 20 | 16 | 12.7 | 7.2 | 0.0806 | 0.08 | 12.42 | 1
December | 15 | 8AM to 9AM | 23 | 20.4 | 15.1 | 12.1 | 7.37 | 0.0805 | 0.08 | 12.45 | 1
December | 15 | 9AM to 10AM | 26.1 | 22.1 | 14 | 11.5 | 8.02 | 0.08 | 0.08 | 12.53 | 1
December | 15 | 10AM to 11AM | 28.9 | 23.8 | 14 | 11.5 | 8.71 | 0.0795 | 0.08 | 12.6 | 1
December | 15 | 11AM to 12PM | 30 | 24.5 | 14 | 11.5 | 8.97 | 0.0793 | 0.08 | 12.63 | 1
December | 15 | 12PM to 1PM | 30 | 24.2 | 12.9 | 10.9 | 8.88 | 0.0793 | 0.07 | 12.63 | 1
December | 15 | 1PM to 2PM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
December | 15 | 2PM to 3PM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
December | 15 | 3PM to 4PM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
December | 15 | 4PM to 5PM | 30.9 | 25 | 14 | 11.5 | 9.19 | 0.0792 | 0.08 | 12.65 | 1
December | 15 | 5PM to 6PM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
December | 15 | 6PM to 7PM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
December | 15 | 7PM to 8PM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
December | 15 | 8PM to 9PM | 30 | 25 | 16 | 12.7 | 9.15 | 0.0793 | 0.08 | 12.63 | 1
December | 15 | 9PM to 10PM | 30 | 25.3 | 17.1 | 13.3 | 9.25 | 0.0793 | 0.09 | 12.64 | 1
December | 15 | 10PM to 11PM | 30 | 25.3 | 17.1 | 13.3 | 9.25 | 0.0793 | 0.09 | 12.64 | 1
December | 15 | 11PM to 12AM | 30 | 25.3 | 17.1 | 13.3 | 9.25 | 0.0793 | 0.09 | 12.64 | 1
December | 16 | 12AM to 1AM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
December | 16 | 1AM to 2AM | 30 | 25.6 | 18 | 13.9 | 9.35 | 0.0793 | 0.09 | 12.64 | 1
December | 16 | 2AM to 3AM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
December | 16 | 3AM to 4AM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
December | 16 | 4AM to 5AM | 30 | 26.2 | 19.9 | 15.3 | 9.56 | 0.0793 | 0.1 | 12.64 | 1
December | 16 | 5AM to 6AM | 30 | 26.2 | 19.9 | 15.3 | 9.56 | 0.0793 | 0.1 | 12.64 | 1
December | 16 | 6AM to 7AM | 30 | 26.5 | 21 | 16.2 | 9.69 | 0.0793 | 0.11 | 12.64 | 1
December | 16 | 7AM to 8AM | 30 | 26.5 | 21 | 16.2 | 9.69 | 0.0793 | 0.11 | 12.64 | 1
December | 16 | 8AM to 9AM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
December | 16 | 9AM to 10AM | 30.9 | 28.8 | 26.1 | 20.5 | 10.58 | 0.0791 | 0.14 | 12.68 | 1
December | 16 | 10AM to 11AM | 30.9 | 29.6 | 28 | 22.5 | 10.88 | 0.0791 | 0.15 | 12.69 | 1
December | 16 | 11AM to 12PM | 33.1 | 30.4 | 27 | 21.4 | 11.23 | 0.0787 | 0.14 | 12.74 | 1
December | 16 | 12PM to 1PM | 34 | 30.5 | 26.1 | 20.5 | 11.31 | 0.0786 | 0.14 | 12.76 | 1
December | 16 | 1PM to 2PM | 35.1 | 31.1 | 26.1 | 20.5 | 11.58 | 0.0784 | 0.14 | 12.79 | 1
December | 16 | 2PM to 3PM | 35.1 | 31.1 | 26.1 | 20.5 | 11.58 | 0.0784 | 0.14 | 12.79 | 1
December | 16 | 3PM to 4PM | 35.1 | 31.1 | 26.1 | 20.5 | 11.58 | 0.0784 | 0.14 | 12.79 | 1
December | 16 | 4PM to 5PM | 35.1 | 31.1 | 26.1 | 20.5 | 11.58 | 0.0784 | 0.14 | 12.79 | 1
December | 16 | 5PM to 6PM | 33.1 | 31.2 | 28.9 | 23.5 | 11.55 | 0.0787 | 0.16 | 12.74 | 1
December | 16 | 6PM to 7PM | 32 | 32 | 32 | 27.1 | 11.84 | 0.0789 | 0.18 | 12.73 | 1
December | 16 | 7PM to 8PM | 32 | 32 | 32 | 27.1 | 11.84 | 0.0789 | 0.18 | 12.73 | 1
December | 16 | 8PM to 9PM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 16 | 9PM to 10PM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 16 | 10PM to 11PM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 16 | 11PM to 12AM | 28.9 | 28.9 | 28.9 | 23.5 | 10.55 | 0.0794 | 0.16 | 12.64 | 1
December | 17 | 12AM to 1AM | 28 | 28 | 28 | 22.5 | 10.19 | 0.0796 | 0.15 | 12.61 | 1
December | 17 | 1AM to 2AM | 25 | 24.6 | 24.1 | 18.7 | 8.86 | 0.0801 | 0.12 | 12.52 | 1
December | 17 | 2AM to 3AM | 21.9 | 21.6 | 21 | 16.2 | 7.73 | 0.0806 | 0.11 | 12.43 | 1
December | 17 | 3AM to 4AM | 21 | 21 | 21 | 16.2 | 7.52 | 0.0808 | 0.11 | 12.41 | 1
December | 17 | 4AM to 5AM | 19.9 | 19.3 | 18 | 13.9 | 6.92 | 0.081 | 0.09 | 12.38 | 1
December | 17 | 5AM to 6AM | 18 | 17.3 | 16 | 12.7 | 6.24 | 0.0813 | 0.08 | 12.32 | 1
December | 17 | 6AM to 7AM | 16 | 15.4 | 14 | 11.5 | 5.59 | 0.0816 | 0.08 | 12.27 | 1
December | 17 | 7AM to 8AM | 15.1 | 14.2 | 12 | 10.4 | 5.21 | 0.0818 | 0.07 | 12.24 | 1
December | 17 | 8AM to 9AM | 14 | 13.2 | 10.9 | 9.9 | 4.86 | 0.082 | 0.07 | 12.21 | 1
December | 17 | 9AM to 10AM | 12 | 10.8 | 7 | 8.1 | 4.12 | 0.0824 | 0.05 | 12.16 | 1
December | 17 | 10AM to 11AM | 12 | 10.4 | 5 | 7.3 | 4 | 0.0824 | 0.05 | 12.15 | 1
December | 17 | 11AM to 12PM | 12 | 10.4 | 5 | 7.3 | 4 | 0.0824 | 0.05 | 12.15 | 1
December | 17 | 12PM to 1PM | 12.9 | 11.2 | 6.1 | 7.7 | 4.28 | 0.0822 | 0.05 | 12.18 | 1
December | 17 | 1PM to 2PM | 12.9 | 11.2 | 6.1 | 7.7 | 4.28 | 0.0822 | 0.05 | 12.18 | 1
December | 17 | 2PM to 3PM | 12 | 10.8 | 7 | 8.1 | 4.12 | 0.0824 | 0.05 | 12.16 | 1
December | 17 | 3PM to 4PM | 12 | 10.8 | 7 | 8.1 | 4.12 | 0.0824 | 0.05 | 12.16 | 1
December | 17 | 4PM to 5PM | 10 | 8.9 | 5 | 7.3 | 3.52 | 0.0827 | 0.05 | 12.1 | 1
December | 17 | 5PM to 6PM | 9 | 7.8 | 3.9 | 6.9 | 3.2 | 0.0829 | 0.05 | 12.07 | 1
December | 17 | 6PM to 7PM | 8.1 | 7 | 3 | 6.6 | 2.94 | 0.0831 | 0.04 | 12.05 | 1
December | 17 | 7PM to 8PM | 7 | 6.1 | 3 | 6.6 | 2.68 | 0.0833 | 0.04 | 12.02 | 1
December | 17 | 8PM to 9PM | 6.1 | 5.2 | 1.9 | 6.2 | 2.41 | 0.0834 | 0.04 | 12 | 1
December | 17 | 9PM to 10PM | 6.1 | 5.2 | 1.9 | 6.2 | 2.41 | 0.0834 | 0.04 | 12 | 1
December | 17 | 10PM to 11PM | 5 | 4.4 | 1.9 | 6.2 | 2.15 | 0.0836 | 0.04 | 11.97 | 1
December | 17 | 11PM to 12AM | 3.9 | 3.4 | 1 | 5.9 | 1.85 | 0.0838 | 0.04 | 11.94 | 1
December | 18 | 12AM to 1AM | 3 | 2.6 | 1 | 5.9 | 1.63 | 0.084 | 0.04 | 11.92 | 1
December | 18 | 1AM to 2AM | 3 | 2.5 | 0 | 5.6 | 1.58 | 0.084 | 0.04 | 11.92 | 1
December | 18 | 2AM to 3AM | 1.9 | 1.6 | 0 | 5.6 | 1.32 | 0.0842 | 0.04 | 11.89 | 1
December | 18 | 3AM to 4AM | 1 | 0.8 | 0 | 5.6 | 1.1 | 0.0843 | 0.04 | 11.87 | 1
December | 18 | 4AM to 5AM | 1 | 0.8 | 0 | 5.6 | 1.1 | 0.0843 | 0.04 | 11.87 | 1
December | 18 | 5AM to 6AM | 0 | -0.5 | -2.9 | 4.8 | 0.72 | 0.0845 | 0.03 | 11.84 | 1
December | 18 | 6AM to 7AM | -0.9 | -1.7 | -6 | 4.1 | 0.4 | 0.0847 | 0.03 | 11.81 | 1
December | 18 | 7AM to 8AM | -2 | -2.9 | -8 | 3.7 | 0.07 | 0.0849 | 0.02 | 11.78 | 1
December | 18 | 8AM to 9AM | -0.9 | -2 | -8 | 3.7 | 0.33 | 0.0847 | 0.02 | 11.81 | 1
December | 18 | 9AM to 10AM | 1.9 | 0.7 | -6 | 4.1 | 1.09 | 0.0842 | 0.03 | 11.89 | 1
December | 18 | 10AM to 11AM | 3 | 1.6 | -6 | 4.1 | 1.35 | 0.084 | 0.03 | 11.91 | 1
December | 18 | 11AM to 12PM | 6.1 | 4.4 | -2.9 | 4.8 | 2.19 | 0.0834 | 0.03 | 11.99 | 1
December | 18 | 12PM to 1PM | 8.1 | 6.1 | -2 | 5.1 | 2.71 | 0.0831 | 0.03 | 12.05 | 1
December | 18 | 1PM to 2PM | 10 | 7.8 | -0.9 | 5.4 | 3.23 | 0.0827 | 0.04 | 12.1 | 1
December | 18 | 2PM to 3PM | 10.9 | 8.6 | 0 | 5.6 | 3.48 | 0.0826 | 0.04 | 12.12 | 1
December | 18 | 3PM to 4PM | 10.9 | 8.6 | 0 | 5.6 | 3.48 | 0.0826 | 0.04 | 12.12 | 1
December | 18 | 4PM to 5PM | 9 | 7.3 | 1 | 5.9 | 3.06 | 0.0829 | 0.04 | 12.07 | 1
December | 18 | 5PM to 6PM | 9 | 7.3 | 1 | 5.9 | 3.06 | 0.0829 | 0.04 | 12.07 | 1
December | 18 | 6PM to 7PM | 7 | 5.6 | 0 | 5.6 | 2.53 | 0.0833 | 0.04 | 12.02 | 1
December | 18 | 7PM to 8PM | 6.1 | 4.9 | 0 | 5.6 | 2.31 | 0.0834 | 0.04 | 12 | 1
December | 18 | 8PM to 9PM | 5 | 3.9 | -0.9 | 5.4 | 2.02 | 0.0836 | 0.04 | 11.97 | 1
December | 18 | 9PM to 10PM | 3.9 | 2.9 | -2 | 5.1 | 1.71 | 0.0838 | 0.03 | 11.94 | 1
December | 18 | 10PM to 11PM | 3 | 2 | -2.9 | 4.8 | 1.46 | 0.084 | 0.03 | 11.92 | 1
December | 18 | 11PM to 12AM | 3 | 2 | -2.9 | 4.8 | 1.46 | 0.084 | 0.03 | 11.92 | 1
December | 19 | 12AM to 1AM | 1.9 | 1 | -4 | 4.6 | 1.16 | 0.0842 | 0.03 | 11.89 | 1
December | 19 | 1AM to 2AM | 1 | 0.2 | -4 | 4.6 | 0.94 | 0.0843 | 0.03 | 11.86 | 1
December | 19 | 2AM to 3AM | 1 | 0.2 | -4 | 4.6 | 0.94 | 0.0843 | 0.03 | 11.86 | 1
December | 19 | 3AM to 4AM | 0 | -0.7 | -4 | 4.6 | 0.68 | 0.0845 | 0.03 | 11.84 | 1
December | 19 | 4AM to 5AM | 0 | -0.7 | -4 | 4.6 | 0.68 | 0.0845 | 0.03 | 11.84 | 1
December | 19 | 5AM to 6AM | 0 | -0.7 | -4 | 4.6 | 0.68 | 0.0845 | 0.03 | 11.84 | 1
December | 19 | 6AM to 7AM | -0.9 | -1.6 | -5.1 | 4.3 | 0.43 | 0.0847 | 0.03 | 11.81 | 1
December | 19 | 7AM to 8AM | -0.9 | -1.6 | -5.1 | 4.3 | 0.43 | 0.0847 | 0.03 | 11.81 | 1
December | 19 | 8AM to 9AM | 1 | 0.2 | -4 | 4.6 | 0.94 | 0.0843 | 0.03 | 11.86 | 1
December | 19 | 9AM to 10AM | 3 | 2.1 | -2 | 5.1 | 1.49 | 0.084 | 0.03 | 11.92 | 1
December | 19 | 10AM to 11AM | 7 | 5.6 | 0 | 5.6 | 2.53 | 0.0833 | 0.04 | 12.02 | 1
December | 19 | 11AM to 12PM | 10 | 8.3 | 1.9 | 6.2 | 3.36 | 0.0827 | 0.04 | 12.1 | 1
December | 19 | 12PM to 1PM | 12.9 | 10.6 | 3 | 6.6 | 4.11 | 0.0822 | 0.04 | 12.18 | 1
December | 19 | 1PM to 2PM | 14 | 11.4 | 3 | 6.6 | 4.37 | 0.082 | 0.04 | 12.2 | 1
December | 19 | 2PM to 3PM | 15.1 | 12.2 | 3 | 6.6 | 4.63 | 0.0818 | 0.04 | 12.23 | 1
December | 19 | 3PM to 4PM | 15.1 | 12.2 | 3 | 6.6 | 4.63 | 0.0818 | 0.04 | 12.23 | 1
December | 19 | 4PM to 5PM | 10.9 | 9.2 | 3 | 6.6 | 3.63 | 0.0826 | 0.04 | 12.12 | 1
December | 19 | 5PM to 6PM | 7 | 5.6 | 0 | 5.6 | 2.53 | 0.0833 | 0.04 | 12.02 | 1
December | 19 | 6PM to 7PM | 10 | 8.1 | 1 | 5.9 | 3.32 | 0.0827 | 0.04 | 12.1 | 1
December | 19 | 7PM to 8PM | 8.1 | 6.6 | 1 | 5.9 | 2.84 | 0.0831 | 0.04 | 12.05 | 1
December | 19 | 8PM to 9PM | 7 | 5.8 | 1 | 5.9 | 2.58 | 0.0833 | 0.04 | 12.02 | 1
December | 19 | 9PM to 10PM | 7 | 5.8 | 1 | 5.9 | 2.58 | 0.0833 | 0.04 | 12.02 | 1
December | 19 | 10PM to 11PM | 8.1 | 7 | 3 | 6.6 | 2.94 | 0.0831 | 0.04 | 12.05 | 1
December | 19 | 11PM to 12AM | 3 | 2.3 | -0.9 | 5.4 | 1.54 | 0.084 | 0.04 | 11.92 | 1
December | 20 | 12AM to 1AM | 5 | 4.4 | 1.9 | 6.2 | 2.15 | 0.0836 | 0.04 | 11.97 | 1
December | 20 | 1AM to 2AM | 3 | 2.5 | 0 | 5.6 | 1.58 | 0.084 | 0.04 | 11.92 | 1
December | 20 | 2AM to 3AM | 3 | 2.5 | 0 | 5.6 | 1.58 | 0.084 | 0.04 | 11.92 | 1
December | 20 | 3AM to 4AM | 1.9 | 1.3 | -2 | 5.1 | 1.24 | 0.0842 | 0.03 | 11.89 | 1
December | 20 | 4AM to 5AM | 3.9 | 3.5 | 1.9 | 6.2 | 1.89 | 0.0838 | 0.04 | 11.94 | 1
December | 20 | 5AM to 6AM | 1.9 | 1.4 | -0.9 | 5.4 | 1.28 | 0.0842 | 0.04 | 11.89 | 1
December | 20 | 6AM to 7AM | 8.1 | 7.6 | 6.1 | 7.7 | 3.11 | 0.0831 | 0.05 | 12.05 | 1
December | 20 | 7AM to 8AM | 10 | 8.9 | 5 | 7.3 | 3.52 | 0.0827 | 0.05 | 12.1 | 1
December | 20 | 8AM to 9AM | 12 | 10.6 | 6.1 | 7.7 | 4.06 | 0.0824 | 0.05 | 12.16 | 1
December | 20 | 9AM to 10AM | 18 | 15.3 | 8.1 | 8.5 | 5.61 | 0.0813 | 0.06 | 12.31 | 1
December | 20 | 10AM to 11AM | 21.9 | 18.2 | 9 | 8.9 | 6.63 | 0.0807 | 0.06 | 12.41 | 1
December | 20 | 11AM to 12PM | 25 | 20.6 | 10.9 | 9.9 | 7.51 | 0.0801 | 0.07 | 12.5 | 1
December | 20 | 12PM to 1PM | 27 | 22.6 | 14 | 11.5 | 8.23 | 0.0798 | 0.08 | 12.55 | 1
December | 20 | 1PM to 2PM | 30 | 24.8 | 15.1 | 12.1 | 9.06 | 0.0793 | 0.08 | 12.63 | 1
December | 20 | 2PM to 3PM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
December | 20 | 3PM to 4PM | 30.9 | 25.6 | 16 | 12.7 | 9.37 | 0.0792 | 0.08 | 12.66 | 1
December | 20 | 4PM to 5PM | 30.9 | 25.3 | 15.1 | 12.1 | 9.28 | 0.0792 | 0.08 | 12.65 | 1
December | 20 | 5PM to 6PM | 30.9 | 25.8 | 17.1 | 13.3 | 9.47 | 0.0791 | 0.09 | 12.66 | 1
December | 20 | 6PM to 7PM | 30.9 | 25.6 | 16 | 12.7 | 9.37 | 0.0792 | 0.08 | 12.66 | 1
December | 20 | 7PM to 8PM | 30.9 | 25.6 | 16 | 12.7 | 9.37 | 0.0792 | 0.08 | 12.66 | 1
December | 20 | 8PM to 9PM | 30.9 | 25.6 | 16 | 12.7 | 9.37 | 0.0792 | 0.08 | 12.66 | 1
December | 20 | 9PM to 10PM | 30.9 | 26.1 | 18 | 13.9 | 9.56 | 0.0791 | 0.09 | 12.66 | 1
December | 20 | 10PM to 11PM | 30 | 25.9 | 19 | 14.7 | 9.46 | 0.0793 | 0.1 | 12.64 | 1
December | 20 | 11PM to 12AM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
December | 21 | 12AM to 1AM | 30.9 | 28.8 | 26.1 | 20.5 | 10.58 | 0.0791 | 0.14 | 12.68 | 1
December | 21 | 1AM to 2AM | 30.9 | 29.2 | 27 | 21.4 | 10.71 | 0.0791 | 0.14 | 12.68 | 1
December | 21 | 2AM to 3AM | 30.9 | 30.5 | 30 | 24.7 | 11.22 | 0.0791 | 0.16 | 12.69 | 1
December | 21 | 3AM to 4AM | 32 | 31.5 | 30.9 | 25.8 | 11.64 | 0.0789 | 0.17 | 12.72 | 1
December | 21 | 4AM to 5AM | 33.1 | 32.1 | 30.9 | 25.8 | 11.9 | 0.0787 | 0.17 | 12.75 | 1
December | 21 | 5AM to 6AM | 33.1 | 32.6 | 32 | 27.1 | 12.1 | 0.0787 | 0.18 | 12.75 | 1
December | 21 | 6AM to 7AM | 33.1 | 32.6 | 32 | 27.1 | 12.1 | 0.0787 | 0.18 | 12.75 | 1
December | 21 | 7AM to 8AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 21 | 8AM to 9AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 21 | 9AM to 10AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 21 | 10AM to 11AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 11AM to 12PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 12PM to 1PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 1PM to 2PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 2PM to 3PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 3PM to 4PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 4PM to 5PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 5PM to 6PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 6PM to 7PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 7PM to 8PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 8PM to 9PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 9PM to 10PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 10PM to 11PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 21 | 11PM to 12AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 22 | 12AM to 1AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 1AM to 2AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 2AM to 3AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 3AM to 4AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 4AM to 5AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 5AM to 6AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 22 | 6AM to 7AM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 7AM to 8AM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 22 | 8AM to 9AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
December | 22 | 9AM to 10AM | 35.1 | 35.1 | 35.1 | 30.6 | 13.13 | 0.0784 | 0.2 | 12.82 | 1
December | 22 | 10AM to 11AM | 36 | 35.6 | 35.1 | 30.6 | 13.35 | 0.0782 | 0.2 | 12.84 | 1
December | 22 | 11AM to 12PM | 34 | 34 | 34 | 29.3 | 12.67 | 0.0786 | 0.2 | 12.78 | 1
December | 22 | 12PM to 1PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 1PM to 2PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 2PM to 3PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 3PM to 4PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 4PM to 5PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 5PM to 6PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 6PM to 7PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 7PM to 8PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 8PM to 9PM | 33.1 | 33.1 | 33.1 | 28.3 | 12.29 | 0.0787 | 0.19 | 12.76 | 1
December | 22 | 9PM to 10PM | 32 | 32 | 32 | 27.1 | 11.84 | 0.0789 | 0.18 | 12.73 | 1
December | 22 | 10PM to 11PM | 32 | 32 | 32 | 27.1 | 11.84 | 0.0789 | 0.18 | 12.73 | 1
December | 22 | 11PM to 12AM | 32 | 32 | 32 | 27.1 | 11.84 | 0.0789 | 0.18 | 12.73 | 1
December | 23 | 12AM to 1AM | 32 | 31.5 | 30.9 | 25.8 | 11.64 | 0.0789 | 0.17 | 12.72 | 1
December | 23 | 1AM to 2AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
December | 23 | 2AM to 3AM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
December | 23 | 3AM to 4AM | 30 | 29.5 | 28.9 | 23.5 | 10.81 | 0.0792 | 0.16 | 12.66 | 1
December | 23 | 4AM to 5AM | 28.9 | 28.1 | 27 | 21.4 | 10.23 | 0.0794 | 0.14 | 12.63 | 1
December | 23 | 5AM to 6AM | 27 | 25.4 | 23 | 17.8 | 9.2 | 0.0798 | 0.12 | 12.57 | 1
December | 23 | 6AM to 7AM | 21 | 19.7 | 17.1 | 13.3 | 7.09 | 0.0808 | 0.09 | 12.4 | 1
December | 23 | 7AM to 8AM | 18 | 17.1 | 15.1 | 12.1 | 6.16 | 0.0813 | 0.08 | 12.32 | 1
December | 23 | 8AM to 9AM | 19.9 | 18.7 | 16 | 12.7 | 6.72 | 0.081 | 0.08 | 12.37 | 1
December | 23 | 9AM to 10AM | 23 | 20.7 | 16 | 12.7 | 7.46 | 0.0805 | 0.08 | 12.45 | 1
December | 23 | 10AM to 11AM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
December | 23 | 11AM to 12PM | 25 | 22.2 | 17.1 | 13.3 | 8.04 | 0.0801 | 0.09 | 12.51 | 1
December | 23 | 12PM to 1PM | 26.1 | 23.2 | 18 | 13.9 | 8.39 | 0.0799 | 0.09 | 12.53 | 1
December | 23 | 1PM to 2PM | 27 | 23.5 | 17.1 | 13.3 | 8.52 | 0.0798 | 0.09 | 12.56 | 1
December | 23 | 2PM to 3PM | 27 | 24.3 | 19.9 | 15.3 | 8.82 | 0.0798 | 0.1 | 12.56 | 1
December | 23 | 3PM to 4PM | 27 | 24.3 | 19.9 | 15.3 | 8.82 | 0.0798 | 0.1 | 12.56 | 1
December | 23 | 4PM to 5PM | 25 | 23.5 | 21 | 16.2 | 8.47 | 0.0801 | 0.11 | 12.51 | 1
December | 23 | 5PM to 6PM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
December | 23 | 6PM to 7PM | 25 | 23.8 | 21.9 | 16.9 | 8.58 | 0.0801 | 0.11 | 12.52 | 1
December | 23 | 7PM to 8PM | 25 | 23.5 | 21 | 16.2 | 8.47 | 0.0801 | 0.11 | 12.51 | 1
December | 23 | 8PM to 9PM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
December | 23 | 9PM to 10PM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
December | 23 | 10PM to 11PM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
December | 23 | 11PM to 12AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
December | 24 | 12AM to 1AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
December | 24 | 1AM to 2AM | 25 | 24.2 | 23 | 17.8 | 8.72 | 0.0801 | 0.12 | 12.52 | 1
December | 24 | 2AM to 3AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
December | 24 | 3AM to 4AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
December | 24 | 4AM to 5AM | 24.1 | 23.3 | 21.9 | 16.9 | 8.36 | 0.0802 | 0.11 | 12.49 | 1
December | 24 | 5AM to 6AM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
December | 24 | 6AM to 7AM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
December | 24 | 7AM to 8AM | 21 | 20.6 | 19.9 | 15.3 | 7.39 | 0.0808 | 0.1 | 12.41 | 1
December | 24 | 8AM to 9AM | 24.1 | 22.9 | 21 | 16.2 | 8.26 | 0.0802 | 0.11 | 12.49 | 1
December | 24 | 9AM to 10AM | 28 | 25.7 | 21.9 | 16.9 | 9.32 | 0.0796 | 0.11 | 12.59 | 1
December | 24 | 10AM to 11AM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
December | 24 | 11AM to 12PM | 32 | 28.7 | 24.1 | 18.7 | 10.55 | 0.0789 | 0.12 | 12.7 | 1
December | 24 | 12PM to 1PM | 35.1 | 30.4 | 24.1 | 18.7 | 11.29 | 0.0785 | 0.12 | 12.78 | 1
December | 24 | 1PM to 2PM | 36 | 30.9 | 24.1 | 18.7 | 11.51 | 0.0783 | 0.12 | 12.8 | 1
December | 24 | 2PM to 3PM | 36 | 31.9 | 27 | 21.4 | 11.93 | 0.0783 | 0.14 | 12.81 | 1
December | 24 | 3PM to 4PM | 37 | 31.1 | 23 | 17.8 | 11.63 | 0.0781 | 0.12 | 12.83 | 1
December | 24 | 4PM to 5PM | 37 | 31.5 | 24.1 | 18.7 | 11.77 | 0.0781 | 0.12 | 12.83 | 1
December | 24 | 5PM to 6PM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
December | 24 | 6PM to 7PM | 25 | 24.2 | 23 | 17.8 | 8.72 | 0.0801 | 0.12 | 12.52 | 1
December | 24 | 7PM to 8PM | 33.1 | 30 | 26.1 | 20.5 | 11.1 | 0.0788 | 0.14 | 12.74 | 1
December | 24 | 8PM to 9PM | 32 | 28.7 | 24.1 | 18.7 | 10.55 | 0.0789 | 0.12 | 12.7 | 1
December | 24 | 9PM to 10PM | 30.9 | 28.1 | 24.1 | 18.7 | 10.29 | 0.0791 | 0.12 | 12.67 | 1
December | 24 | 10PM to 11PM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
December | 24 | 11PM to 12AM | 28.9 | 26.2 | 21.9 | 16.9 | 9.54 | 0.0794 | 0.11 | 12.62 | 1
December | 25 | 12AM to 1AM | 30.9 | 27 | 21 | 16.2 | 9.9 | 0.0791 | 0.11 | 12.67 | 1
December | 25 | 1AM to 2AM | 28.9 | 25.9 | 21 | 16.2 | 9.43 | 0.0795 | 0.11 | 12.62 | 1
December | 25 | 2AM to 3AM | 28 | 25.4 | 21 | 16.2 | 9.21 | 0.0796 | 0.11 | 12.59 | 1
December | 25 | 3AM to 4AM | 26.1 | 24.5 | 21.9 | 16.9 | 8.84 | 0.0799 | 0.11 | 12.54 | 1
December | 25 | 4AM to 5AM | 30 | 27.2 | 23 | 17.8 | 9.93 | 0.0793 | 0.12 | 12.65 | 1
December | 25 | 5AM to 6AM | 32 | 28 | 21.9 | 16.9 | 10.27 | 0.079 | 0.11 | 12.7 | 1
December | 25 | 6AM to 7AM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
December | 25 | 7AM to 8AM | 28.9 | 26.2 | 21.9 | 16.9 | 9.54 | 0.0794 | 0.11 | 12.62 | 1
December | 25 | 8AM to 9AM | 30.9 | 27.3 | 21.9 | 16.9 | 10.01 | 0.0791 | 0.11 | 12.67 | 1
December | 25 | 9AM to 10AM | 36 | 29.9 | 21 | 16.2 | 11.12 | 0.0783 | 0.11 | 12.8 | 1
December | 25 | 10AM to 11AM | 39 | 31 | 19 | 14.7 | 11.63 | 0.0779 | 0.1 | 12.87 | 1
December | 25 | 11AM to 12PM | 41 | 32.6 | 19 | 14.7 | 12.11 | 0.0775 | 0.1 | 12.92 | 1
December | 25 | 12PM to 1PM | 43 | 34 | 19.9 | 15.3 | 12.68 | 0.0772 | 0.1 | 12.98 | 1
December | 25 | 1PM to 2PM | 42.1 | 35 | 25 | 19.5 | 13.11 | 0.0773 | 0.13 | 12.96 | 1
December | 25 | 2PM to 3PM | 39 | 34 | 27 | 21.4 | 12.67 | 0.0778 | 0.14 | 12.89 | 1
December | 25 | 3PM to 4PM | 39 | 34.7 | 28.9 | 23.5 | 12.99 | 0.0778 | 0.16 | 12.9 | 1
December | 25 | 4PM to 5PM | 37 | 33.6 | 28.9 | 23.5 | 12.51 | 0.0781 | 0.16 | 12.85 | 1
December | 25 | 5PM to 6PM | 37 | 32.8 | 27 | 21.4 | 12.19 | 0.0781 | 0.14 | 12.84 | 1
December | 25 | 6PM to 7PM | 37 | 32.5 | 26.1 | 20.5 | 12.05 | 0.0781 | 0.14 | 12.84 | 1
December | 25 | 7PM to 8PM | 37 | 31.5 | 24.1 | 18.7 | 11.77 | 0.0781 | 0.12 | 12.83 | 1
December | 25 | 8PM to 9PM | 37 | 31.5 | 24.1 | 18.7 | 11.77 | 0.0781 | 0.12 | 12.83 | 1
December | 25 | 9PM to 10PM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
December | 25 | 10PM to 11PM | 35.1 | 31.1 | 26.1 | 20.5 | 11.58 | 0.0784 | 0.14 | 12.79 | 1
December | 25 | 11PM to 12AM | 35.1 | 31.1 | 26.1 | 20.5 | 11.58 | 0.0784 | 0.14 | 12.79 | 1
December | 26 | 12AM to 1AM | 35.1 | 30.7 | 25 | 19.5 | 11.42 | 0.0784 | 0.13 | 12.78 | 1
December | 26 | 1AM to 2AM | 35.1 | 30.7 | 25 | 19.5 | 11.42 | 0.0784 | 0.13 | 12.78 | 1
December | 26 | 2AM to 3AM | 35.1 | 30.4 | 24.1 | 18.7 | 11.29 | 0.0785 | 0.12 | 12.78 | 1
December | 26 | 3AM to 4AM | 35.1 | 30.7 | 25 | 19.5 | 11.42 | 0.0784 | 0.13 | 12.78 | 1
December | 26 | 4AM to 5AM | 35.1 | 30 | 23 | 17.8 | 11.15 | 0.0785 | 0.12 | 12.78 | 1
December | 26 | 5AM to 6AM | 34 | 29.4 | 23 | 17.8 | 10.89 | 0.0786 | 0.12 | 12.75 | 1
December | 26 | 6AM to 7AM | 34 | 29.8 | 24.1 | 18.7 | 11.03 | 0.0786 | 0.12 | 12.75 | 1
December | 26 | 7AM to 8AM | 32 | 28.7 | 24.1 | 18.7 | 10.55 | 0.0789 | 0.12 | 12.7 | 1
December | 26 | 8AM to 9AM | 34 | 30.5 | 26.1 | 20.5 | 11.31 | 0.0786 | 0.14 | 12.76 | 1
December | 26 | 9AM to 10AM | 37 | 32.8 | 27 | 21.4 | 12.19 | 0.0781 | 0.14 | 12.84 | 1
December | 26 | 10AM to 11AM | 41 | 35.8 | 28.9 | 23.5 | 13.47 | 0.0775 | 0.16 | 12.95 | 1
December | 26 | 11AM to 12PM | 43 | 37.7 | 30.9 | 25.8 | 14.29 | 0.0772 | 0.17 | 13.01 | 1
December | 26 | 12PM to 1PM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
December | 26 | 1PM to 2PM | 43 | 38.2 | 32 | 27.1 | 14.5 | 0.0772 | 0.18 | 13.01 | 1
December | 26 | 2PM to 3PM | 44.1 | 38.7 | 32 | 27.1 | 14.76 | 0.077 | 0.18 | 13.04 | 1
December | 26 | 3PM to 4PM | 41 | 37.1 | 32 | 27.1 | 14.02 | 0.0775 | 0.18 | 12.96 | 1
December | 26 | 4PM to 5PM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
December | 26 | 5PM to 6PM | 37.9 | 35.4 | 32 | 27.1 | 13.28 | 0.0779 | 0.18 | 12.88 | 1
December | 26 | 6PM to 7PM | 37 | 34.9 | 32 | 27.1 | 13.06 | 0.0781 | 0.18 | 12.86 | 1
December | 26 | 7PM to 8PM | 35.1 | 33.8 | 32 | 27.1 | 12.58 | 0.0784 | 0.18 | 12.81 | 1
December | 26 | 8PM to 9PM | 34 | 32.7 | 30.9 | 25.8 | 12.12 | 0.0786 | 0.17 | 12.77 | 1
December | 26 | 9PM to 10PM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
December | 26 | 10PM to 11PM | 34 | 31.7 | 28.9 | 23.5 | 11.77 | 0.0786 | 0.16 | 12.77 | 1
December | 26 | 11PM to 12AM | 32 | 29.8 | 27 | 21.4 | 10.97 | 0.0789 | 0.14 | 12.71 | 1
December | 27 | 12AM to 1AM | 30.9 | 29.2 | 27 | 21.4 | 10.71 | 0.0791 | 0.14 | 12.68 | 1
December | 27 | 1AM to 2AM | 28 | 27.2 | 26.1 | 20.5 | 9.88 | 0.0796 | 0.14 | 12.6 | 1
December | 27 | 2AM to 3AM | 27 | 26.2 | 25 | 19.5 | 9.46 | 0.0798 | 0.13 | 12.57 | 1
December | 27 | 3AM to 4AM | 27 | 26.2 | 25 | 19.5 | 9.46 | 0.0798 | 0.13 | 12.57 | 1
December | 27 | 4AM to 5AM | 28 | 27.2 | 26.1 | 20.5 | 9.88 | 0.0796 | 0.14 | 12.6 | 1
December | 27 | 5AM to 6AM | 28.9 | 27.3 | 25 | 19.5 | 9.94 | 0.0794 | 0.13 | 12.63 | 1
December | 27 | 6AM to 7AM | 30 | 28.3 | 26.1 | 20.5 | 10.36 | 0.0792 | 0.14 | 12.66 | 1
December | 27 | 7AM to 8AM | 27 | 26.2 | 25 | 19.5 | 9.46 | 0.0798 | 0.13 | 12.57 | 1
December | 27 | 8AM to 9AM | 28.9 | 27.3 | 25 | 19.5 | 9.94 | 0.0794 | 0.13 | 12.63 | 1
December | 27 | 9AM to 10AM | 30.9 | 28.4 | 25 | 19.5 | 10.42 | 0.0791 | 0.13 | 12.68 | 1
December | 27 | 10AM to 11AM | 33.1 | 30 | 26.1 | 20.5 | 11.1 | 0.0788 | 0.14 | 12.74 | 1
December | 27 | 11AM to 12PM | 36 | 31.2 | 25 | 19.5 | 11.64 | 0.0783 | 0.13 | 12.81 | 1
December | 27 | 12PM to 1PM | 36 | 30.5 | 23 | 17.8 | 11.37 | 0.0783 | 0.12 | 12.8 | 1
December | 27 | 1PM to 2PM | 36 | 31.6 | 26.1 | 20.5 | 11.79 | 0.0783 | 0.14 | 12.81 | 1
December | 27 | 2PM to 3PM | 36 | 32.6 | 28 | 22.5 | 12.1 | 0.0783 | 0.15 | 12.82 | 1
December | 27 | 3PM to 4PM | 36 | 33 | 28.9 | 23.5 | 12.25 | 0.0783 | 0.16 | 12.82 | 1
December | 27 | 4PM to 5PM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
December | 27 | 5PM to 6PM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
December | 27 | 6PM to 7PM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
December | 27 | 7PM to 8PM | 34 | 32.3 | 30 | 24.7 | 11.96 | 0.0786 | 0.16 | 12.77 | 1
December | 27 | 8PM to 9PM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
December | 27 | 9PM to 10PM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
December | 27 | 10PM to 11PM | 33.1 | 31.7 | 30 | 24.7 | 11.74 | 0.0787 | 0.16 | 12.75 | 1
December | 27 | 11PM to 12AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 12AM to 1AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 1AM to 2AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 2AM to 3AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 3AM to 4AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 4AM to 5AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 5AM to 6AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 6AM to 7AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 7AM to 8AM | 32 | 32 | 32 | 27.1 | 11.84 | 0.0789 | 0.18 | 12.73 | 1
December | 28 | 8AM to 9AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 9AM to 10AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 10AM to 11AM | 30.9 | 30.9 | 30.9 | 25.8 | 11.38 | 0.0791 | 0.17 | 12.69 | 1
December | 28 | 11AM to 12PM | 32 | 32 | 32 | 27.1 | 11.84 | 0.0789 | 0.18 | 12.73 | 1
December | 28 | 12PM to 1PM | 32 | 31.1 | 30 | 24.7 | 11.48 | 0.0789 | 0.16 | 12.72 | 1
December | 28 | 1PM to 2PM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
December | 28 | 2PM to 3PM | 30.9 | 29.6 | 28 | 22.5 | 10.88 | 0.0791 | 0.15 | 12.69 | 1
December | 28 | 3PM to 4PM | 28.9 | 28.1 | 27 | 21.4 | 10.23 | 0.0794 | 0.14 | 12.63 | 1
December | 28 | 4PM to 5PM | 28 | 26.8 | 25 | 19.5 | 9.72 | 0.0796 | 0.13 | 12.6 | 1
December | 28 | 5PM to 6PM | 28 | 26.8 | 25 | 19.5 | 9.72 | 0.0796 | 0.13 | 12.6 | 1
December | 28 | 6PM to 7PM | 26.1 | 24.9 | 23 | 17.8 | 8.98 | 0.0799 | 0.12 | 12.55 | 1
December | 28 | 7PM to 8PM | 23 | 21.9 | 19.9 | 15.3 | 7.87 | 0.0804 | 0.1 | 12.46 | 1
December | 28 | 8PM to 9PM | 21.9 | 20.6 | 18 | 13.9 | 7.39 | 0.0806 | 0.09 | 12.43 | 1
December | 28 | 9PM to 10PM | 21 | 19.7 | 17.1 | 13.3 | 7.09 | 0.0808 | 0.09 | 12.4 | 1
December | 28 | 10PM to 11PM | 17.1 | 16.1 | 14 | 11.5 | 5.85 | 0.0815 | 0.08 | 12.3 | 1
December | 28 | 11PM to 12AM | 14 | 13.4 | 12 | 10.4 | 4.95 | 0.082 | 0.07 | 12.21 | 1
December | 29 | 12AM to 1AM | 12.9 | 12.4 | 10.9 | 9.9 | 4.61 | 0.0822 | 0.07 | 12.18 | 1
December | 29 | 1AM to 2AM | 12 | 11.5 | 10 | 9.4 | 4.32 | 0.0823 | 0.06 | 12.16 | 1
December | 29 | 2AM to 3AM | 12 | 11.5 | 10 | 9.4 | 4.32 | 0.0823 | 0.06 | 12.16 | 1
December | 29 | 3AM to 4AM | 10.9 | 10.7 | 10 | 9.4 | 4.06 | 0.0825 | 0.06 | 12.13 | 1
December | 29 | 4AM to 5AM | 9 | 9 | 9 | 8.9 | 3.51 | 0.0829 | 0.06 | 12.08 | 1
December | 29 | 5AM to 6AM | 10 | 10 | 10 | 9.4 | 3.85 | 0.0827 | 0.06 | 12.11 | 1
December | 29 | 6AM to 7AM | 7 | 7 | 7 | 8.1 | 2.9 | 0.0832 | 0.05 | 12.03 | 1
December | 29 | 7AM to 8AM | 10.9 | 10.9 | 10.9 | 9.9 | 4.13 | 0.0825 | 0.07 | 12.13 | 1
December | 29 | 8AM to 9AM | 12.9 | 12.7 | 12 | 10.4 | 4.69 | 0.0822 | 0.07 | 12.19 | 1
December | 29 | 9AM to 10AM | 16 | 15.1 | 12.9 | 10.9 | 5.5 | 0.0817 | 0.07 | 12.27 | 1
December | 29 | 10AM to 11AM | 21 | 19.1 | 15.1 | 12.1 | 6.9 | 0.0808 | 0.08 | 12.4 | 1
December | 29 | 11AM to 12PM | 24.1 | 21.3 | 16 | 12.7 | 7.72 | 0.0803 | 0.08 | 12.48 | 1
December | 29 | 12PM to 1PM | 25 | 22.2 | 17.1 | 13.3 | 8.04 | 0.0801 | 0.09 | 12.51 | 1
December | 29 | 1PM to 2PM | 27 | 23.5 | 17.1 | 13.3 | 8.52 | 0.0798 | 0.09 | 12.56 | 1
December | 29 | 2PM to 3PM | 28 | 24.4 | 18 | 13.9 | 8.87 | 0.0796 | 0.09 | 12.59 | 1
December | 29 | 3PM to 4PM | 27 | 23.7 | 18 | 13.9 | 8.61 | 0.0798 | 0.09 | 12.56 | 1
December | 29 | 4PM to 5PM | 25 | 22.8 | 19 | 14.7 | 8.25 | 0.0801 | 0.1 | 12.51 | 1
December | 29 | 5PM to 6PM | 19.9 | 19 | 17.1 | 13.3 | 6.83 | 0.081 | 0.09 | 12.38 | 1
December | 29 | 6PM to 7PM | 19 | 18.4 | 17.1 | 13.3 | 6.61 | 0.0811 | 0.09 | 12.35 | 1
December | 29 | 7PM to 8PM | 25 | 23.1 | 19.9 | 15.3 | 8.35 | 0.0801 | 0.1 | 12.51 | 1
December | 29 | 8PM to 9PM | 26.1 | 23.8 | 19.9 | 15.3 | 8.61 | 0.0799 | 0.1 | 12.54 | 1
December | 29 | 9PM to 10PM | 21 | 20 | 18 | 13.9 | 7.18 | 0.0808 | 0.09 | 12.4 | 1
December | 29 | 10PM to 11PM | 15.1 | 14.8 | 14 | 11.5 | 5.37 | 0.0818 | 0.08 | 12.24 | 1
December | 29 | 11PM to 12AM | 21.9 | 21.2 | 19.9 | 15.3 | 7.61 | 0.0806 | 0.1 | 12.43 | 1
December | 30 | 12AM to 1AM | 21.9 | 21.2 | 19.9 | 15.3 | 7.61 | 0.0806 | 0.1 | 12.43 | 1
December | 30 | 1AM to 2AM | 21 | 20.3 | 19 | 14.7 | 7.29 | 0.0808 | 0.1 | 12.41 | 1
December | 30 | 2AM to 3AM | 24.1 | 22.6 | 19.9 | 15.3 | 8.13 | 0.0803 | 0.1 | 12.49 | 1
December | 30 | 3AM to 4AM | 24.1 | 22.6 | 19.9 | 15.3 | 8.13 | 0.0803 | 0.1 | 12.49 | 1
December | 30 | 4AM to 5AM | 16 | 16 | 16 | 12.7 | 5.77 | 0.0816 | 0.08 | 12.27 | 1
December | 30 | 5AM to 6AM | 14 | 14 | 14 | 11.5 | 5.11 | 0.082 | 0.08 | 12.22 | 1
December | 30 | 6AM to 7AM | 12.9 | 12.9 | 12.9 | 10.9 | 4.76 | 0.0822 | 0.07 | 12.19 | 1
December | 30 | 7AM to 8AM | 16 | 16 | 16 | 12.7 | 5.77 | 0.0816 | 0.08 | 12.27 | 1
December | 30 | 8AM to 9AM | 21.9 | 21.9 | 21.9 | 16.9 | 7.84 | 0.0806 | 0.11 | 12.44 | 1
December | 30 | 9AM to 10AM | 30 | 26.8 | 21.9 | 16.9 | 9.8 | 0.0793 | 0.11 | 12.65 | 1
December | 30 | 10AM to 11AM | 32 | 28.7 | 24.1 | 18.7 | 10.55 | 0.0789 | 0.12 | 12.7 | 1
December | 30 | 11AM to 12PM | 34 | 29.8 | 24.1 | 18.7 | 11.03 | 0.0786 | 0.12 | 12.75 | 1
December | 30 | 12PM to 1PM | 37.9 | 31.2 | 21.9 | 16.9 | 11.71 | 0.078 | 0.11 | 12.85 | 1
December | 30 | 1PM to 2PM | 39 | 33 | 24.1 | 18.7 | 12.25 | 0.0778 | 0.12 | 12.88 | 1
December | 30 | 2PM to 3PM | 39.9 | 33.2 | 23 | 17.8 | 12.32 | 0.0777 | 0.12 | 12.9 | 1
December | 30 | 3PM to 4PM | 39.9 | 33.2 | 23 | 17.8 | 12.32 | 0.0777 | 0.12 | 12.9 | 1
December | 30 | 4PM to 5PM | 39 | 32.6 | 23 | 17.8 | 12.1 | 0.0778 | 0.12 | 12.88 | 1
December | 30 | 5PM to 6PM | 37 | 31.1 | 23 | 17.8 | 11.63 | 0.0781 | 0.12 | 12.83 | 1
December | 30 | 6PM to 7PM | 37 | 31.1 | 23 | 17.8 | 11.63 | 0.0781 | 0.12 | 12.83 | 1
December | 30 | 7PM to 8PM | 37 | 31.5 | 24.1 | 18.7 | 11.77 | 0.0781 | 0.12 | 12.83 | 1
December | 30 | 8PM to 9PM | 37.9 | 33 | 26.1 | 20.5 | 12.27 | 0.078 | 0.14 | 12.86 | 1
December | 30 | 9PM to 10PM | 37.9 | 33 | 26.1 | 20.5 | 12.27 | 0.078 | 0.14 | 12.86 | 1
December | 30 | 10PM to 11PM | 37.9 | 33 | 26.1 | 20.5 | 12.27 | 0.078 | 0.14 | 12.86 | 1
December | 30 | 11PM to 12AM | 37.9 | 33.4 | 27 | 21.4 | 12.41 | 0.078 | 0.14 | 12.86 | 1
December | 31 | 12AM to 1AM | 37.9 | 34.1 | 28.9 | 23.5 | 12.73 | 0.078 | 0.16 | 12.87 | 1
December | 31 | 1AM to 2AM | 37.9 | 34.6 | 30 | 24.7 | 12.91 | 0.078 | 0.16 | 12.87 | 1
December | 31 | 2AM to 3AM | 39 | 36 | 32 | 27.1 | 13.54 | 0.0778 | 0.18 | 12.91 | 1
December | 31 | 3AM to 4AM | 39 | 36.4 | 33.1 | 28.3 | 13.73 | 0.0778 | 0.19 | 12.91 | 1
December | 31 | 4AM to 5AM | 39.9 | 37.3 | 34 | 29.3 | 14.1 | 0.0776 | 0.2 | 12.94 | 1
December | 31 | 5AM to 6AM | 41 | 38.3 | 35.1 | 30.6 | 14.57 | 0.0774 | 0.2 | 12.97 | 1
December | 31 | 6AM to 7AM | 42.1 | 39.7 | 37 | 33.2 | 15.22 | 0.0773 | 0.22 | 13 | 1
December | 31 | 7AM to 8AM | 42.1 | 40.1 | 37.9 | 34.4 | 15.4 | 0.0772 | 0.23 | 13.01 | 1
December | 31 | 8AM to 9AM | 43 | 41.1 | 39 | 35.9 | 15.85 | 0.0771 | 0.24 | 13.04 | 1
December | 31 | 9AM to 10AM | 43 | 41.5 | 39.9 | 37.2 | 16.05 | 0.0771 | 0.25 | 13.04 | 1
December | 31 | 10AM to 11AM | 43 | 42 | 41 | 38.8 | 16.3 | 0.0771 | 0.26 | 13.04 | 1
December | 31 | 11AM to 12PM | 44.1 | 43.5 | 43 | 41.9 | 17.04 | 0.0769 | 0.28 | 13.08 | 1
December | 31 | 12PM to 1PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
December | 31 | 1PM to 2PM | 43 | 43 | 43 | 41.9 | 16.78 | 0.0771 | 0.28 | 13.05 | 1
December | 31 | 2PM to 3PM | 44.1 | 44.1 | 44.1 | 43.6 | 17.31 | 0.0769 | 0.29 | 13.09 | 1
December | 31 | 3PM to 4PM | 42.1 | 42.1 | 42.1 | 40.4 | 16.34 | 0.0772 | 0.27 | 13.03 | 1
December | 31 | 4PM to 5PM | 39.9 | 38.1 | 36 | 31.8 | 14.48 | 0.0776 | 0.21 | 12.94 | 1
December | 31 | 5PM to 6PM | 36 | 34.7 | 33.1 | 28.3 | 12.99 | 0.0782 | 0.19 | 12.83 | 1
December | 31 | 6PM to 7PM | 30.9 | 30 | 28.9 | 23.5 | 11.03 | 0.0791 | 0.16 | 12.69 | 1
December | 31 | 7PM to 8PM | 28.9 | 27.3 | 25 | 19.5 | 9.94 | 0.0794 | 0.13 | 12.63 | 1
December | 31 | 8PM to 9PM | 27 | 25 | 21.9 | 16.9 | 9.06 | 0.0798 | 0.11 | 12.57 | 1
December | 31 | 9PM to 10PM | 24.1 | 22.3 | 19 | 14.7 | 8.03 | 0.0803 | 0.1 | 12.49 | 1
December | 31 | 10PM to 11PM | 21 | 19.7 | 17.1 | 13.3 | 7.09 | 0.0808 | 0.09 | 12.4 | 1
December | 31 | 11PM to 12AM | 19.9 | 18.4 | 15.1 | 12.1 | 6.64 | 0.081 | 0.08 | 12.37 | 1