## Slide 1: The Hijend Hotel Chilled Water System

## Slide 2: The Hijend Hotel Chilled Water System

## Slide 3: The Hijend Hotel Chilled Water System

## Slide 4: The Hijend Hotel Chilled Water System

## Slide 5: Simplified System Diagram
Ch1
Pm
Ch2 (VFD & HG)
Pm
Pm
Pm
VF1
AHU8
AHU9
AHU10
AHU1
AHU7
South FC Riser 1A
South FC Riser 8A
North FC Riser 8D
North FC Riser 1D
AHU5
AHU6
AHU2
AHU3
AHU4
A
B
C
D
MATCH LINE
See Below
A
B
C
D
MATCH LINE
See Above
See Sheet 11
See Sheets 7 - 10
See Sheets 3 - 6
See Sheet 2
See Sheet 1

## Slide 6
VF-1 Elec. Rm.
SD
TDV
Chiller 2 VFD & HG
SD
TDV
Chiller 1 No VFD
SD
TDV
SD
TDV
As Installed
1,100 gpm @ 40 ft.w.c., 15 hp (Typical)
1,100 gpm @ 90 ft.w.c., 40 hp (Typical)
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 286 kW
Match Line – See Sheet 2
A
B
42.5 gpm from 42.0°F to 54°F, 9.8 ft.w.c. Δ p, 22.1 tons
1,100 gpm from 54.0°F to 42.0°F, 9.8 ft.w.c. Δp, 309 kW
Hijend Hotel CHW System Diagram
Sheet 1

## Slide 7
Match Line – See Sheet 1
A
B
Match Line – See Sheet 3
C
D
73.7 gpm from 42.0°F to 54°F, 9.3 ft.w.c. Δ p, 36.9 tons
157.2 gpm from 42.0°F to 54°F, 9.6 ft.w.c. Δ p, 78.6 tons
43.9 gpm from 42.0°F to 54°F, 7.8 ft.w.c. Δ p, 21.9 tons; bypass balanced for 5 gpm in full bypass.
AHU8 Cafe
AHU9 Rest/Lng
AHU10 Kitchen
141 gpm from 42.0°F to 54°F, 8.6 ft.w.c. Δ p, 42.2 tons
57.9 gpm from 42.0°F to 54°F, 3.1 ft.w.c. Δ p, 29 tons
AHU1 Admin/Lby
AHU7 Laundry
Hijend Hotel CHW System Diagram
Sheet 2

## Slide 8
Match Line – See Sheet 2
C
D
1st Floor (Typical through Floor 23)
Fan Coil Riser 1.5 A, North Face
62 gpm at 42°EWT, LWT varies, 19.1 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
West FCU
24th Floor
West FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 2.5 A, North Face
125.4 gpm at 42°EWT, LWT varies, 34.9 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 4
E
H
G
F
Hijend Hotel CHW System Diagram
Sheet 3

## Slide 9
Match Line – See Sheet 3
1st Floor (Typical through Floor 24)
Fan Coil Riser 3.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 4.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 5
I
L
K
J
E
H
G
F
Hijend Hotel CHW System Diagram
Sheet 4

## Slide 10
Match Line – See Sheet 4
1st Floor (Typical through Floor 24)
Fan Coil Riser 5.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; ; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 6.5 A, North Face
124.5 gpm at 42°EWT, LWT varies, 34.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 6
M
P
O
N
I
L
K
J
Hijend Hotel CHW System Diagram
Sheet 5

## Slide 11
Match Line – See Sheet 5
1st Floor (Typical through Floor 24)
Fan Coil Riser 7.5 A, North Face
125.4 gpm at 42°EWT, LWT varies, 34.9 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
1st Floor (Typical through Floor 23)
Fan Coil Riser 8.5 A, North Face
121.5 gpm at 42°EWT, LWT varies, 35.5 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
East FCU
Match Line – See Sheet 7
Q
T
S
R
M
P
O
N
Hijend Hotel CHW System Diagram
Sheet 6

## Slide 12
Match Line – See Sheet 6
1st Floor (Typical through Floor 23)
Fan Coil Riser 8.5 D, South Face
90.6 gpm at 42°EWT, LWT varies, 30.6 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 7.5 D, South Face
187.6 gpm at 42°EWT, LWT varies, 63.4 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 8
U
X
W
V
Q
T
S
R
Hijend Hotel CHW System Diagram
Sheet 7

## Slide 13
Match Line – See Sheet 7
1st Floor (Typical through Floor 24)
Fan Coil Riser 6.5 D, South Face
189.5 gpm at 42°EWT, LWT varies, 64.0 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
1st Floor (Typical through Floor 24)
Fan Coil Riser 5.5 D, South Face
94.7 gpm at 42°EWT, LWT varies, 32 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
25th Floor
East FCU
Match Line – See Sheet 9
Y
B
A
Z
U
X
W
V
Hijend Hotel CHW System Diagram
Sheet 8

## Slide 14
Match Line – See Sheet 8
1st Floor (Typical through Floor 24)
Fan Coil Riser 4.5 D, South Face
189.5 gpm at 42°EWT, LWT varies, 64.0 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
West FCU
East FCU
Match Line – See Sheet 10
Y
B
A
Z
U
X
W
V
1st Floor (Typical through Floor 24)
Fan Coil Riser 3.5 D, South Face
185.4 gpm at 42°EWT, LWT varies, 62.6 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
25th Floor
East FCU
Hijend Hotel CHW System Diagram
Sheet 9

## Slide 15
Fan Coil Riser 1.5 D, South Face
467.4 gpm at 42°EWT, LWT varies, 218.3 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
Match Line – See Sheet 9
1st Floor (Typical through Floor 23)
Fan Coil Riser 2.5 D, South Face
181.2 gpm at 42°EWT, LWT varies, 61.2 tons
See coil schedule and fan coil riser schedule for details; three way valve bypass balanced for design flow in full bypass.
East FCU
West FCU
24th Floor
West FCU
East FCU
Match Line – See Sheet 11
Y
Z
U
X
W
V
1st Floor
West FCU (Typical through 24th floor)
25th Floor
West FCU
186.3 gpm from 42.0°F to 54°F, 6.9 ft.w.c. Δ p, 91.2 tons (Typical of each MAU)
AHU5 Corr. MAU
AHU6 Corr.MAU
Roof Level
Hijend Hotel CHW System Diagram
Sheet 10

## Slide 16
Match Line – See Sheet 10
Y
Z
88.7 gpm from 42.0°F to 54°F, 9.2 ft.w.c. Δ p, 44.3 tons
120.1 gpm from 42.0°F to 54°F, 9.1 ft.w.c. Δ p, 60.1 tons; bypass balanced for 5 gpm in full bypass.
148.7 gpm from 42.0°F to 54°F, 11 ft.w.c. Δ p, 74.4 tons
AHU4 Mtg. Rooms
AHU3 Jr. Ball Room
AHU2 Ball Room
Hijend Hotel CHW System Diagram
Sheet 11

## Slide 17: Fan Coil Unit Riser Schedule

## Slide 18: Cooling Coil Schedule

## Slide 19: System Volume Projection