## Cooling Coils
Mark | Serves | Location | Air Flow, cfm | MBH |  | Tons |  | Face Area, sq.ft. | Face Velocity (calculated) | Entering Air Temperature |  | Leaving Air Temperature |  | Airside Pressure Drop, in.w.c. | Entering Water Temperature, °F | LeavingWater Temperature, °F | Water Flow, gpm | gpm per ton, calculated | Waterside Pressure Drop, ft.wc. | Notes
|  |  |  | Sensible | Total | Sensible | Total |  |  | tdb, °F | twb, °F | tdb, °F | twb, °F
CC-11A | Arcade | 11th Floor | 3400 | 111.2 | 133.1 | 9.2667 | 11.0917 | 8.25 | 412.1212 | 85 | 67 | 55 | 54.5 |  | 44 | 60 | 17 | 1.5 | 6 | Note 1 | 16
11.3333
CC-16 Through CC-38 | AHU16 - 38 | 16th through 38th Floor | 14000 | 457.9 | 514.2 | 38.1583 | 42.85 | 29 | 482.7586 | 82 | 64 | 52 | 51.5 | 0.87 | 44 | 60 | 64 | 1.5 | 16
Notes
1 | Pace 6 row, 8 fins per inch 36" tube length, 33" tube height, duct mounted coil
2
3
4
5
6 | Pace 6 row, 12 fins per inch

## Combined Data
This model was developed using the Greenheck Coil Selection Program. It models CC-16, which is typical of the vast majority of the coils in the facility.
Construction Details
Finned Length - |  |  | 70 |  | inches | Tube Material - |  | Copper
Finned Height - |  |  | 30 |  | inches | Tube Diameter - |  | 0.625 |  | inch
Face Area - |  |  | 14.5833 | 0 | sq.ft. | Tube Wall Thickness - |  | 0.02 |  | inches
Coils in the Coil Bank - |  |  | 2 |  |  | Tube interior - |  | Smooth
Coil Bank Face Area - |  |  | 29.1667 | 0 | sq.ft. | Connection Hand - |  | Right |  | (Facing with Air Flow Direction)
Rows - |  |  | 6 |  |  | Supply Connection Size - |  | 2
Fins per Inch - |  |  | 12 |  |  | Return Connection Size - |  | 2
Fin Material - |  |  | Aluminum |  |  | Number of Feeds - |  | 15
Fin Thickness - |  |  | 0.006 |  |  | Number of Passes - |  | 8
Fin Type - |  |  | Sine-wave |  |  | Circuiting - |  | 0.53333 |  | Serpentine
Casing Material - |  |  | Galvanized Steel |  |  | Dry Weight - |  | 315 |  | per coil
Coating - |  |  | None |  |  | Operating Weight - |  | 418 |  | per coil
Greenheck File Location - |  | ..\Coil Models
Columns with orange over them use one of KW Engineering's "Get Psyched" plug-ins to calculate a psychrometric parameter. See Note 18 below.
Design Condition - Seattle 0.4% Design Conditions, 62.5% Minimum Outdoor Air, SHR = .92, Space = 72°F, 50% RH | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lb | Coil SHR |  | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face |  |  | Water Flow Turbulent, Transition, or Laminar | Humid, Normal or Dry
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
14000 | 82 | 64 | 52 | 51.9 | 463174.6127 | 28525.3873 | 491700 | 480 | 0.84 | 0 | 61.3 | 44 | 60 | 16 | 40.8667 | 1.5 | 2.23 | 3.8 | 0 | Note 2 | 0.008597 | 60.1788 | 0.0081689 | 57.1825 | 459100 | 32600 | 453600 | 28525.3873 | 29.1144 | See Below |  | 0.625 | 1.407e-05 | 8254.8567 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
Design Condition - Seattle 2% Design Conditions | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lb | Coil SHR |  | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
14000 | 78.1 | 62.3 | 52 | 52 | 389828.2359 | 8871.7641 | 398700 | 480 | 0.72 | 0 | 48 | 44 | 60.6 | 16.6 | 33.2 | 1.4458 | 1.75 | 2.4 | 0 | Note 6 | 0.0083556 | 58.4894 | 0.0082225 | 57.5575 | 398700 | 0 | 394632 | 8871.7641 | 27.8991 | 0.97775 |  | 0.625 | 1.407e-05 | 6478.0265 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
Design Airflow and Leaving Air Temperature, Different Entering Conditions | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lbn (Red Exceeds Design) | Coil SHR | Point on Psych Chart | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face |  |  |  | Humid, Normal or Dry
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr (Model output) | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) |  |  | OA tdb | OA tdw | Tons for 50 identical loacs
14000 | 90 | 67.3 | 52 | 51.9 | 587468.3642 | 61031.6358 | 648500 | 480 | 0.86 | 0 | 84 | 44 | 59.4 | 15.4 | 53.9 | 1.5584 | 3.06 | 6.7 | 0 | Note 11 | 0.0090848 | 63.5933 | 0.0081689 | 57.1825 | 581400 | 67100 | 574560 | 61031.6358 | 31.602 | 0.90589 | 1 | 0.625 | 1.407e-05 | 11327.2921 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Normal | 90 | 67.3 | 2695
14000 | 87 | 65.4 | 52 | 52 | 521437.1175 | 12962.8825 | 534400 | 480 | 0.72 | 0 | 59 | 44 | 62.1 | 18.1 | 44.4958 | 1.326 | 2.15 | 3.5 | 0 | Note 10 | 0.008417 | 58.9192 | 0.0082225 | 57.5575 | 534400 | 0 | 529200 | 12962.8825 | 30.1356 | 0.97574 | 2 | 0.625 | 1.407e-05 | 7958.7183 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Normal | 87 | 65.4 | 2224.7917
14000 | 83.4 | 66.4 | 52 | 51.9 | 489665.4874 | 118634.5126 | 608300 | 480 | 0.9 | 0 | 93 | 44 | 57 | 13 | 50.375 | 1.8462 | 3.38 | 8.2 | 0 | Note 14 | 0.0099492 | 69.6441 | 0.0081689 | 57.1825 | 482100 | 126200 | 474768 | 118634.5126 | 30.9405 | 0.80497 | 3 | 0.625 | 1.407e-05 | 12511.8455 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Humid | 87 | 68.5 | 2518.75
14000 | 83 | 64.4 | 52 | 52 | 446528.7367 | 27871.2633 | 474400 | 480 | 0.72 | 0 | 54.5 | 44 | 61.4 | 17.4 | 39.5125 | 1.3793 | 1.98 | 3 | 0 | Note 9 | 0.0086407 | 60.4852 | 0.0082225 | 57.5575 | 474400 | 0 | 468720 | 27871.2633 | 29.4063 | 0.94125 | 4 | 0.625 | 1.407e-05 | 7329.4243 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Humid |  |  | 1975.625
14000 | 82 | 64 | 52 | 51.9 | 463174.6127 | 28525.3873 | 491700 | 480 | 0.84 | 0 | 61.3 | 44 | 60 | 16 | 40.8667 | 1.5 | 2.23 | 3.8 | 0 | Note 2 | 0.008597 | 60.1788 | 0.0081689 | 57.1825 | 459100 | 32600 | 453600 | 28525.3873 | 29.1144 | 0.94199 | 5 | 0.625 | 1.407e-05 | 8254.8567 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Normal | 86.1 | 65.6 | 2043.3333
14000 | 80.6 | 63.4 | 52 | 52 | 417264.9316 | 19335.0684 | 436600 | 480 | 0.72 | 0 | 51 | 44 | 61.1 | 17.1 | 36.3375 | 1.4035 | 1.86 | 2.7 | 0 | Note 7 | 0.0085126 | 59.5885 | 0.0082225 | 57.5575 | 436600 | 0 | 432432 | 19335.0684 | 28.6806 | 0.95571 | 6 | 0.625 | 1.407e-05 | 6885.2168 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Normal |  |  | 1816.875 | Bin Data Plot |  | MOA Mix at 0.4% Design Condition
14000 | 79.9 | 66.6 | 52 | 51.9 | 437799.7744 | 181900.2256 | 619700 | 480 | 0.91 | 0 | 104 | 44 | 55.9 | 11.9 | 51.5667 | 2.0168 | 3.78 | 10.1 | 0 | Note 8 | 0.010899 | 76.2896 | 0.0081689 | 57.1825 | 429100 | 190600 | 421848 | 181900.2256 | 31.126 | 0.70647 | 7 | 0.625 | 1.407e-05 | 13992.5373 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Humid | 82 | 68.8 | 2578.3333
14000 | 78.1 | 62.3 | 52 | 52 | 389828.2359 | 8871.7641 | 398700 | 480 | 0.72 | 0 | 48 | 44 | 60.6 | 16.6 | 33.2 | 1.4458 | 1.75 | 2.4 | 0 | Note 6 | 0.0083556 | 58.4894 | 0.0082225 | 57.5575 | 398700 | 0 | 394632 | 8871.7641 | 27.8991 | 0.97775 | 12 | 0.625 | 1.407e-05 | 6478.0265 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Normal | 79.4 | 62.8 | 1660
14000 | 76 | 61.7 | 52 | 52 | 352151.3337 | 14848.6663 | 367000 | 480 | 0.72 | 0 | 45.5 | 44 | 60.1 | 16.1 | 30.5229 | 1.4907 | 1.66 | 2.2 | 0 | Note 5 | 0.0084453 | 59.1173 | 0.0082225 | 57.5575 | 367000 | 0 | 362880 | 14848.6663 | 27.4855 | 0.95954 | 8 | 0.625 | 1.407e-05 | 6144.8709 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Normal | 92 | 67.3 | 1526.1458
14000 | 75.6 | 64.2 | 52 | 52 | 235072.1228 | 131927.8772 | 367000 | 480 | 0.72 | 0 | 45.5 | 44 | 60.1 | 16.1 | 30.5229 | 1.4907 | 1.66 | 2.2 | 0 | Note 13 | 0.010202 | 71.4155 | 0.0082225 | 57.5575 | 367000 | 0 | 356832 | 131927.8772 | 29.311 | 0.64052 | 9 | 0.625 | 1.407e-05 | 6144.8709 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Humid | 76 | 66 | 1526.1458
14000 | 72 | 67.8 | 52 | 52 | 330376.907 | 358923.093 | 689300 | 480 | 0.92 | 0 | 124 | 44 | 55 | 11 | 56.8333 | 2.1818 | 4.51 | 14 | 0 | Note 4 | 0.013609 | 95.2595 | 0.0082225 | 57.5575 | 309600 | 379700 | 302400 | 358923.093 | 32.1537 | 0.47929 | 10 | 0.625 | 1.407e-05 | 16694.7998 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Humid |  |  | 2841.6667
14000 | 72 | 51.5 | 52 | 42.1 | 305189.6939 | 1110.3061 | 306300 | 480 | 0.72 | 0 | 40.5 | 44 | 59.1 | 15.1 | 25.4812 | 1.5894 | 1.47 | 1.8 | 0 | Note 17 | 0.0034184 | 23.9287 | 0.0034017 | 23.8121 | 306300 | 0 | 302400 | 1110.3061 | 21.0162 | 0.99638 | 21 | 0.625 | 1.407e-05 | 5441.5423 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Dry |  |  | 1274.0625
14000 | 72 | 59.8 | 52 | 51.8 | 303741.1257 | 2558.8743 | 306300 | 480 | 0.72 | 0 | 40.5 | 44 | 59.1 | 15.1 | 25.4812 | 1.5894 | 1.47 | 1.8 | 0 | Note 3 | 0.0081539 | 57.077 | 0.0081155 | 56.8082 | 306300 | 0 | 302400 | 2558.8743 | 26.1919 | 0.99165 | 11 | 0.625 | 1.407e-05 | 5441.5423 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Normal |  |  | 1274.0625
14000 | 67 | 66 | 52 | 52 | 248989.1725 | 348710.8275 | 597700 | 480 | 0.92 | 0 | 107 | 44 | 55.1 | 11.1 | 49.4875 | 2.1622 | 3.89 | 10.6 | 0 | Note 4 | 0.013455 | 94.1868 | 0.0082225 | 57.5575 | 232700 | 365000 | 226800 | 348710.8275 | 30.7563 | 0.41658 | 13 | 0.625 | 1.407e-05 | 14399.7276 | 64.6154 | 0.000152 | 283400.8097 | Turbulent |  |  |  | 2474.375
14000 | 67 | 57.6 | 52 | 51.5 | 228931.0437 | 68.9563 | 229000 | 480 | 0.73 | 0 | 33.5 | 44 | 57.6 | 13.6 | 18.9833 | 1.7647 | 1.22 | 1.3 | 0 | Note 3 | 0.0079567 | 55.6971 | 0.0079557 | 55.6898 | 229000 | 0 | 226800 | 68.9563 | 24.7588 | 0.9997 | 14 | 0.625 | 1.407e-05 | 4516.1099 | 64.6154 | 0.000152 | 283400.8097 | Turbulent |  |  |  | 949.1667
14000 | 67 | 46.5 | 52 | 39 | 229000 | 0 | 229000 | 480 | 0.73 | 0 | 33.5 | 44 | 57.6 | 13.6 | 18.9833 | 1.7647 | 1.22 | 1.3 | 0 | Note 16 | 0.0020514 | 14.3597 | 0.0020693 | 14.4851 | 229000 | 0 | 226800 | 0 | 18.3176 | 1 | 20 | 0.625 | 1.407e-05 | 4516.1099 | 64.6154 | 0.000152 | 283400.8097 | Turbulent |  |  |  | 949.1667
14000 | 62 | 62 | 52 | 52 | 164751.6699 | 242748.3301 | 407500 | 480 | 0.92 | 0 | 73 | 44 | 55.1 | 11.1 | 33.7625 | 2.1622 | 2.66 | 5.2 | 0 | Note 4 | 0.011865 | 83.0563 | 0.0082225 | 57.5575 | 154700 | 252800 | 151200 | 242748.3301 | 27.7956 | 0.4043 | 15 | 0.625 | 1.407e-05 | 9846.6003 | 64.6154 | 0.000152 | 283400.8097 | Turbulent |  |  |  | 1688.125
14000 | 62 | 55.4 | 52 | 51.2 | 150810.2842 | 1289.7158 | 152100 | 480 | 0.73 | 0 | 26 | 44 | 55.7 | 11.7 | 12.675 | 2.0513 | 0.95 | 0.8 | 0 | Note 3 | 0.0078163 | 54.7138 | 0.0077969 | 54.5783 | 152100 | 0 | 151200 | 1289.7158 | 23.3882 | 0.99152 | 16 | 0.625 | 1.407e-05 | 3516.643 | 64.6154 | 0.000152 | 283400.8097 | Transition |  |  |  | 633.75
14000 | 57 | 57 | 52 | 52 | 81675.95 | 111424.05 | 193100 | 480 | 0.92 | 0 | 39 | 44 | 53.9 | 9.9 | 16.0875 | 2.4242 | 1.42 | 1.7 | 0 | Note 4 | 0.0098945 | 69.2617 | 0.0082225 | 57.5575 | 77300 | 115800 | 75600 | 111424.05 | 24.4285 | 0.42297 | 17 | 0.625 | 1.407e-05 | 5256.4558 | 64.6154 | 0.000152 | 283400.8097 | Turbulent |  |  |  | 804.375
14000 | 57 | 52.2 | 52 | 50 | 75351.5469 | 1048.4531 | 76400 | 480 | 0.73 | 0 | 17.3 | 44 | 52.8 | 8.8 | 6.3433 | 2.7273 | 0.63 | 0.4 | 0 | Note 3 | 0.0071871 | 50.3094 | 0.0071713 | 50.1993 | 76400 | 0 | 75600 | 1048.4531 | 21.4874 | 0.98628 | 18 | 0.625 | 1.407e-05 | 2332.0896 | 64.6154 | 0.000152 | 283400.8097 | Transition |  |  |  | 317.1667
14000 | 57 | 43.1 | 52 | 40.5 | 75811.1282 | 1288.8718 | 77100 | 480 | 0.73 | 0 | 17.4 | 44 | 52.8 | 8.8 | 6.38 | 2.7273 | 0.63 | 0.4 | 0 | Note 15 | 0.002724 | 19.0679 | 0.0027046 | 18.9325 | 77100 | 0 | 75600 | 1288.8718 | 16.6391 | 0.98328 | 19 | 0.625 | 1.407e-05 | 2332.0896 | 64.6154 | 0.000152 | 283400.8097 | Transition |  |  |  | 319 |  | Bin Data Plot
10000 | 90 | 67.3 | 52 | 52 | 419456.3903 | 41043.6097 | 460500 | 343 | 0.52 | 0 | 49 | 44 | 62.7 | 18.7 | 38.1792 | 1.2834 | 1.78 | 2.5 | 0 | Note 11 | 0.0090848 | 63.5933 | 0.0082225 | 57.5575 | 415100 | 45400 | 410400 | 41043.6097 | 31.602 | 0.91087 | 1 | 0.625 | 1.407e-05 | 6589.0784 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1908.9583
10000 | 87 | 65.4 | 52 | 52 | 372440.7982 | 9259.2018 | 381700 | 343 | 0.41 | 0 | 37.5 | 44 | 64.3 | 20.3 | 31.7187 | 1.1823 | 2.15 | 1.5 | 0 | Note 10 | 0.008417 | 58.9192 | 0.0082225 | 57.5575 | 381700 | 0 | 378000 | 9259.2018 | 30.1356 | 0.97574 | 2 | 0.625 | 1.407e-05 | 7958.7183 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1585.9375
10000 | 83.4 | 66.4 | 52 | 52 | 349311.4783 | 82188.5217 | 431500 | 343 | 0.55 | 0 | 54 | 44 | 59.9 | 15.9 | 35.775 | 1.5094 | 1.96 | 3 | 0 | Note 14 | 0.0099492 | 69.6441 | 0.0082225 | 57.5575 | 343900 | 87600 | 339120 | 82188.5217 | 30.9405 | 0.80953 | 3 | 0.625 | 1.407e-05 | 7255.3897 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1788.75
10000 | 83 | 64.4 | 52 | 51.9 | 340641.5389 | 22458.4611 | 363100 | 343 | 0.5 | 0 | 40 | 44 | 62.1 | 18.1 | 30.1667 | 1.326 | 1.46 | 1.7 | 0 | Note 9 | 0.0086407 | 60.4852 | 0.0081689 | 57.1825 | 339200 | 23900 | 334800 | 22458.4611 | 29.4063 | 0.93815 | 4 | 0.625 | 1.407e-05 | 5404.525 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1508.3333
10000 | 82 | 64 | 52 | 52 | 309375.1392 | 17824.8608 | 327200 | 343 | 0.41 | 0 | 34.5 | 44 | 62.9 | 18.9 | 27.1687 | 1.2698 | 1.26 | 1.3 | 0 | Note 2 | 0.008597 | 60.1788 | 0.0082225 | 57.5575 | 327200 | 0 | 324000 | 17824.8608 | 29.1144 | 0.94552 | 5 | 0.625 | 1.407e-05 | 4664.1791 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1358.4375 |  |  | MOA Mix at 0.4% Design Condition
10000 | 80.6 | 63.4 | 52 | 51.9 | 313938.821 | 16361.179 | 330300 | 343 | 0.49 | 0 | 37 | 44 | 61.8 | 17.8 | 27.4417 | 1.3483 | 1.35 | 1.5 | 0 | Note 7 | 0.0085126 | 59.5885 | 0.0081689 | 57.1825 | 312800 | 17500 | 308880 | 16361.179 | 28.6806 | 0.95047 | 6 | 0.625 | 1.407e-05 | 4997.3348 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1372.0833
10000 | 79.9 | 66.6 | 52 | 51.9 | 312671.2674 | 129928.7326 | 442600 | 343 | 0.57 | 0 | 61 | 44 | 58.5 | 14.5 | 36.8542 | 1.6552 | 2.22 | 3.7 | 0 | Note 8 | 0.010899 | 76.2896 | 0.0081689 | 57.1825 | 307100 | 135500 | 301320 | 129928.7326 | 31.126 | 0.70644 | 7 | 0.625 | 1.407e-05 | 8217.8394 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1842.7083
10000 | 78.1 | 62.3 | 52 | 52 | 278663.0257 | 6336.9743 | 285000 | 343 | 0.41 | 0 | 32.1 | 44 | 61.7 | 17.7 | 23.6738 | 1.3559 | 1.17 | 1.2 | 0 | Note 6 | 0.0083556 | 58.4894 | 0.0082225 | 57.5575 | 285000 | 0 | 281880 | 6336.9743 | 27.8991 | 0.97777 | 12 | 0.625 | 1.407e-05 | 4331.0235 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1183.6875
10000 | 76 | 61.7 | 52 | 52 | 251593.8098 | 10606.1902 | 262200 | 343 | 0.41 | 0 | 30.8 | 44 | 61 | 17 | 21.8167 | 1.4118 | 1.66 | 1.1 | 0 | Note 5 | 0.0084453 | 59.1173 | 0.0082225 | 57.5575 | 262200 | 0 | 259200 | 10606.1902 | 27.4855 | 0.95955 | 8 | 0.625 | 1.407e-05 | 6144.8709 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1090.8333
10000 | 75.6 | 64.2 | 52 | 51.9 | 263215.3862 | 96784.6138 | 360000 | 343 | 0.57 | 0 | 50.8 | 44 | 58.1 | 14.1 | 29.845 | 1.7021 | 1.85 | 2.7 | 0 | Note 13 | 0.010202 | 71.4155 | 0.0081689 | 57.1825 | 259600 | 100400 | 254880 | 96784.6138 | 29.311 | 0.73115 | 9 | 0.625 | 1.407e-05 | 6848.1995 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1492.25
10000 | 72 | 67.8 | 52 | 52 | 233426.3621 | 256373.6379 | 489800 | 343 | 0.59 | 0 | 72 | 44 | 57.6 | 13.6 | 40.8 | 1.7647 | 2.62 | 5.1 | 0 | Note 4 | 0.013609 | 95.2595 | 0.0082225 | 57.5575 | 221000 | 268800 | 216000 | 256373.6379 | 32.1537 | 0.47657 | 10 | 0.625 | 1.407e-05 | 9698.5312 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 2040
10000 | 72 | 51.5 | 52 | 42.1 | 218006.9242 | 793.0758 | 218800 | 343 | 0.41 | 0 | 28 | 44 | 59.6 | 15.6 | 18.2 | 1.5385 | 1.02 | 0.6 | 0 | Note 17 | 0.0034184 | 23.9287 | 0.0034017 | 23.8121 | 218800 | 0 | 216000 | 793.0758 | 21.0162 | 0.99638 | 21 | 0.625 | 1.407e-05 | 3775.764 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 910
10000 | 72 | 59.8 | 52 | 51.9 | 217800 | 0 | 217800 | 343 | 0.41 | 0 | 27.8 | 44 | 59.6 | 15.6 | 18.07 | 1.5385 | 1.01 | 0.9 | 0 | Note 3 | 0.0081539 | 57.077 | 0.0081689 | 57.1825 | 217800 | 0 | 216000 | 0 | 26.1919 | 1 | 11 | 0.625 | 1.407e-05 | 3738.7467 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 903.5
10000 | 71 | 63.8 | 52 | 52 | 214997.4287 | 131702.5713 | 346700 | 343 | 0.58 | 0 | 52.5 | 44 | 57.2 | 13.2 | 28.875 | 1.8182 | 1.91 | 2.9 | 0 | Note 6 | 0.010989 | 76.9255 | 0.0082225 | 57.5575 | 208800 | 137900 | 205200 | 131702.5713 | 29.0461 | 0.62013 | 12 | 0.625 | 1.407e-05 | 7070.3032 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1443.75
10000 | 67 | 66 | 52 | 52 | 177220.8375 | 249079.1625 | 426300 | 343 | 0.59 | 0 | 64 | 44 | 57.3 | 13.3 | 35.4667 | 1.8045 | 2.33 | 4.1 | 0 | Note 4 | 0.013455 | 94.1868 | 0.0082225 | 57.5575 | 165900 | 260400 | 162000 | 249079.1625 | 30.7563 | 0.41572 | 13 | 0.625 | 1.407e-05 | 8625.0296 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1773.3333
10000 | 67 | 57.6 | 52 | 51.5 | 163850.7455 | 49.2545 | 163900 | 343 | 0.42 | 0 | 24 | 44 | 57.6 | 13.6 | 13.6 | 1.7647 | 0.87 | 0.7 | 0 | Note 3 | 0.0079567 | 55.6971 | 0.0079557 | 55.6898 | 163900 | 0 | 162000 | 49.2545 | 24.7588 | 0.9997 | 14 | 0.625 | 1.407e-05 | 3220.5046 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 680
10000 | 67 | 46.5 | 52 | 38.9 | 162665.2194 | 1134.7806 | 163800 | 343 | 0.42 | 0 | 24 | 44 | 57.6 | 13.6 | 13.6 | 1.7647 | 0.87 | 0.7 | 0 | Note 16 | 0.0020514 | 14.3597 | 0.0020276 | 14.1929 | 163800 | 0 | 163900 | 1134.7806 | 18.3176 | 0.99307 | 20 | 0.625 | 1.407e-05 | 3220.5046 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 680
10000 | 62 | 62 | 52 | 52 | 117108.3357 | 173391.6643 | 290500 | 343 | 0.52 | 0 | 47.3 | 44 | 56.2 | 12.2 | 24.0442 | 1.9672 | 1.72 | 2.4 | 0 | Note 4 | 0.011865 | 83.0563 | 0.0082225 | 57.5575 | 110200 | 180300 | 108000 | 173391.6643 | 27.7956 | 0.40313 | 15 | 0.625 | 1.407e-05 | 6366.9747 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  |  |  | 1202.2083
10000 | 62 | 55.4 | 52 | 51.3 | 108900 | 0 | 108900 | 343 | 0.42 | 0 | 19.3 | 44 | 55.2 | 11.2 | 9.0067 | 2.1429 | 0.7 | 0.05 | 0 | Note 3 | 0.0078163 | 54.7138 | 0.0078497 | 54.9481 | 108900 | 0 | 108000 | 0 | 23.3882 | 1 | 16 | 0.625 | 1.407e-05 | 2591.2106 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 450.3333
10000 | 57 | 57 | 52 | 52 | 59311.3928 | 79588.6072 | 138900 | 343 | 0.59 | 0 | 28 | 44 | 53.9 | 9.9 | 11.55 | 2.4242 | 1.02 | 0.9 | 0 | Note 4 | 0.0098945 | 69.2617 | 0.0082225 | 57.5575 | 55600 | 83300 | 54000 | 79588.6072 | 24.4285 | 0.42701 | 17 | 0.625 | 1.407e-05 | 3775.764 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 577.5
10000 | 57 | 52.2 | 52 | 50 | 53951.1049 | 748.8951 | 54700 | 343 | 0.42 | 0 | 11 | 44 | 53.9 | 9.9 | 4.5375 | 2.4242 | 0.4 | 0.2 | 0 | Note 3 | 0.0071871 | 50.3094 | 0.0071713 | 50.1993 | 54700 | 0 | 54000 | 748.8951 | 21.4874 | 0.98631 | 18 | 0.625 | 1.407e-05 | 1480.6918 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 226.875
10000 | 57 | 43.1 | 52 | 40.6 | 54100 | 0 | 54100 | 343 | 0.42 | 0 | 10.8 | 44 | 54 | 10 | 4.5 | 2.4 | 0.39 | 0.2 | 0 | Note 15 | 0.002724 | 19.0679 | 0.0027476 | 19.2333 | 54100 | 0 | 54000 | 0 | 16.6391 | 1 | 19 | 0.625 | 1.407e-05 | 1443.6745 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 225
10000 | 90 | 67.3 | 60 | 56.8 | 327500 | 0 | 327500 | 343 | 0.41 | 0 | 22.7 | 44 | 72.8 | 28.8 | 27.24 | 0.83333 | 0.83 | 0.6 | 0 | Note 11 | 0.0090848 | 63.5933 | 0.0090865 | 63.6054 | 327500 | 0 | 324000 | 0 | 31.602 | 1 | 1 | 0.625 | 1.407e-05 | 3072.4354 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  | Bin Data Plot | 1362
10000 | 87 | 65.4 | 60 | 55.7 | 294500 | 0 | 294500 | 343 | 0.41 | 0 | 21.5 | 44 | 71.4 | 27.4 | 24.5458 | 0.87591 | 0.78 | 0.5 | 0 | Note 10 | 0.008417 | 58.9192 | 0.0084459 | 59.1215 | 294500 | 0 | 291600 | 0 | 30.1356 | 1 | 2 | 0.625 | 1.407e-05 | 2887.349 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 1227.2917
10000 | 83.4 | 66.4 | 60 | 58.2 | 254093.5799 | 1206.4201 | 255300 | 343 | 0.41 | 0 | 20 | 44 | 69.5 | 25.5 | 21.25 | 0.94118 | 0.73 | 0.5 | 0 | Note 14 | 0.0099492 | 69.6441 | 0.0099238 | 69.4667 | 255300 | 0 | 252720 | 1206.4201 | 30.9405 | 0.99527 | 3 | 0.625 | 1.407e-05 | 2702.2625 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 1062.5
10000 | 83 | 64.4 | 60 | 56 | 249772.1509 | 1027.8491 | 250800 | 343 | 0.41 | 0 | 19.8 | 44 | 69.3 | 25.3 | 20.8725 | 0.94862 | 0.72 | 0.5 | 0 | Note 9 | 0.0086407 | 60.4852 | 0.0086191 | 60.334 | 250800 | 0 | 248400 | 1027.8491 | 29.4063 | 0.9959 | 4 | 0.625 | 1.407e-05 | 2665.2452 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 1043.625
10000 | 82 | 64 | 60 | 56 | 240300 | 0 | 240300 | 343 | 0.414 | 0 | 19.4 | 44 | 68.7 | 24.7 | 19.9658 | 0.97166 | 0.71 | 0.5 | 0 | Note 2 | 0.008597 | 60.1788 | 0.0086191 | 60.334 | 240300 | 0 | 237600 | 0 | 29.1144 | 1 | 5 | 0.625 | 1.407e-05 | 2628.2279 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 998.2917
10000 | 80.6 | 63.4 | 60 | 55.8 | 224066.8749 | 433.1251 | 224500 | 343 | 0.41 | 0 | 18.7 | 44 | 68 | 24 | 18.7 | 1 | 0.68 | 0.4 | 0 | Note 7 | 0.0085126 | 59.5885 | 0.0085035 | 59.5248 | 224500 | 0 | 222480 | 433.1251 | 28.6806 | 0.99807 | 6 | 0.625 | 1.407e-05 | 2517.176 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 935 |  |  | MOA Mix at 0.4% Design Condition
10000 | 79.9 | 66.6 | 60 | 59.8 | 217100 | 0 | 217100 | 343 | 0.41 | 0 | 18.4 | 44 | 67.5 | 23.5 | 18.0167 | 1.0213 | 0.67 | 0.4 | 0 | Note 8 | 0.010899 | 76.2896 | 0.010912 | 76.3856 | 217100 | 0 | 214920 | 0 | 31.126 | 1 | 7 | 0.625 | 1.407e-05 | 2480.1587 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 900.8333
10000 | 78.1 | 62.3 | 60 | 55.5 | 196030.3756 | 1169.6244 | 197200 | 343 | 0.41 | 0 | 17.5 | 44 | 66.5 | 22.5 | 16.4062 | 1.0667 | 0.64 | 0.4 | 0 | Note 6 | 0.0083556 | 58.4894 | 0.0083311 | 58.3174 | 197200 | 0 | 195480 | 1169.6244 | 27.8991 | 0.99407 | 12 | 0.625 | 1.407e-05 | 2369.1068 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 820.3125
10000 | 76 | 61.7 | 60 | 55.7 | 174400 | 0 | 174400 | 343 | 0.41 | 0 | 16.4 | 44 | 65.2 | 21.2 | 14.4867 | 1.1321 | 0.6 | 0.3 | 0 | Note 5 | 0.0084453 | 59.1173 | 0.0084459 | 59.1215 | 174400 | 0 | 172800 | 0 | 27.4855 | 1 | 8 | 0.625 | 1.407e-05 | 2221.0377 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 724.3333
10000 | 75.6 | 64.2 | 60 | 58.6 | 168557.6676 | 1642.3324 | 170200 | 343 | 0.41 | 0 | 16.2 | 44 | 65 | 21 | 14.175 | 1.1429 | 0.59 | 0.03 | 0 | Note 13 | 0.010202 | 71.4155 | 0.010168 | 71.174 | 170200 | 0 | 168480 | 1642.3324 | 29.311 | 0.99035 | 9 | 0.625 | 1.407e-05 | 2184.0204 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 708.75
10000 | 72 | 67.8 | 60 | 60 | 138954.5527 | 122345.4473 | 261300 | 343 | 0.58 | 0 | 26.6 | 44 | 63.6 | 19.6 | 21.7233 | 1.2245 | 0.97 | 0.8 | 0 | Note 4 | 0.013609 | 95.2595 | 0.011038 | 77.2675 | 132400 | 128900 | 129600 | 122345.4473 | 32.1537 | 0.53178 | 10 | 0.625 | 1.407e-05 | 3590.6776 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 1086.1667
10000 | 72 | 51.5 | 60 | 46.1 | 130900 | 0 | 130900 | 343 | 0.41 | 0 | 13.2 | 44 | 63.8 | 19.8 | 10.89 | 1.2121 | 0.48 | 0.2 | 0 | Note 17 | 0.0034184 | 23.9287 | 0.0034326 | 24.0284 | 130900 | 0 | 129600 | 0 | 21.0162 | 1 | 21 | 0.625 | 1.407e-05 | 1776.8301 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 544.5
10000 | 72 | 59.8 | 60 | 55.2 | 131000 | 0 | 131000 | 343 | 0.41 | 0 | 13.2 | 44 | 63.8 | 19.8 | 10.89 | 1.2121 | 0.48 | 0.2 | 0 | Note 3 | 0.0081539 | 57.077 | 0.0081597 | 57.1177 | 131000 | 0 | 129600 | 0 | 26.1919 | 1 | 11 | 0.625 | 1.407e-05 | 1776.8301 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 544.5
10000 | 71 | 63.8 | 60 | 59.9 | 119123.8167 | 676.1833 | 119800 | 343 | 0.41 | 0 | 12 | 44 | 63.9 | 19.9 | 9.95 | 1.206 | 0.44 | 0.2 | 0 | Note 6 | 0.010989 | 76.9255 | 0.010975 | 76.8261 | 119800 | 0 | 118800 | 676.1833 | 29.0461 | 0.99436 | 12 | 0.625 | 1.407e-05 | 1628.761 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 497.5
10000 | 67 | 66 | 60 | 60 | 83349.0281 | 115050.9719 | 198400 | 343 | 0.59 | 0 | 22.2 | 44 | 61.8 | 17.8 | 16.465 | 1.3483 | 0.81 | 0.6 | 0 | Note 4 | 0.013455 | 94.1868 | 0.011038 | 77.2675 | 77500 | 120900 | 75600 | 115050.9719 | 30.7563 | 0.42011 | 13 | 0.625 | 1.407e-05 | 2998.4009 | 64.6154 | 0.000152 | 202513.4953 | Transition |  |  |  | 823.25
10000 | 67 | 57.6 | 60 | 54.8 | 75461.7942 | 1138.2058 | 76600 | 343 | 0.41 | 0 | 7.7 | 44 | 63.9 | 19.9 | 6.3846 | 1.206 | 0.28 | 0.1 | 0 | Note 3 | 0.0079567 | 55.6971 | 0.0079328 | 55.5297 | 76600 | 0 | 75600 | 1138.2058 | 24.7588 | 0.98514 | 14 | 0.625 | 1.407e-05 | 1036.4842 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 319.2292
10000 | 67 | 46.5 | 60 | 43.1 | 76300 | 0 | 76300 | 343 | 0.41 | 0 | 7.7 | 44 | 63.9 | 19.9 | 6.3846 | 1.206 | 0.28 | 0.1 | 0 | Note 16 | 0.0020514 | 14.3597 | 0.0020518 | 14.3626 | 76300 | 0 | 163900 | 0 | 18.3176 | 1 | 20 | 0.625 | 1.407e-05 | 1036.4842 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 319.2292
10000 | 62 | 62 | 60 | 60 | 22836.5263 | 39363.4737 | 62200 | 343 | 0.59 | 0 | 7.4 | 44 | 60.8 | 16.8 | 5.18 | 1.4286 | 0.27 | 0.1 | 0 | Note 4 | 0.011865 | 83.0563 | 0.011038 | 77.2675 | 21700 | 40500 | 21600 | 39363.4737 | 27.7956 | 0.36715 | 15 | 0.625 | 1.407e-05 | 999.467 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 259
10000 | 62 | 55.4 | 60 | 54.6 | 21600 | 0 | 21600 | 343 | 0.42 | 0 | 2.4 | 44 | 61.9 | 17.9 | 1.79 | 1.3408 | 0.09 | 0.0005 | 0 | Note 15 | 0.0078163 | 54.7138 | 0.0078201 | 54.7407 | 21600 | 0 | 21600 | 0 | 23.3882 | 1 | 19 | 0.625 | 1.407e-05 | 333.1557 | 64.6154 | 0.000152 | 202513.4953 | Laminar |  |  |  | 89.5
Notes
1 | Because the Greenheck model reports loads as Mbtu, for low latent loads, it may report 0 Btu/hr of latent load even though it shows a slightly lower leaving wetbulb than dry bulb temperature and a slightly higher pressrue drop relative to a dry coil. To overcome this, the modeled total load is used. The latent load is calculated based on the difference between entering and leaving w, with the leaving w being set by the modeled leaving conditions. The sensible load is calculated by subtracting the latent load from the total load.
2 | This analysis is based on the selection point on the CDs and the Seattle 0.4% cooling design condition; see psych chart to the right
3 | Dry bulb is the middle of temperature of a 5°F by 8 hour bin; Wet bulb is the mean coincident wet bulb for the bin. See psych chart to the right.
4 | This is the operating condition for the drybulb bin but at the highest observed wet bulb temperature based on the bin plot in Akton Psych chart to illustrate the impact of a heavier latent load.
5 | This is a mixed condition based on the design return condition and the 77°F bin conditions
6 | This analysis is based on the selection point on the CDs and the Seattle 2% cooling design condition; see psych chart to the right
7 | This is a mixed condition based on 50% outdoor air vs. the apparent design percentage. Its also very close to the mix condition for the 82°F bin.
8 | This is a humid MOA condition for the 82°F bin.
9 | This is a mixed condition based on the design return condition and the 87°F bin conditions
10 | This is a mixed condition based on the design return condition and the 92°F bin conditions
11 | This is a mixed condition based on the design return condition and the 97°F bin conditions
12 | This is a humid MOA condition for the 82°F bin.
13 | This is a humid MOA condition for the 77°F bin.
14 | This is a humid MOA condition for the 87°F bin.
15 | This is a dry condition for the 57°F bin.
16 | This is a dry condition for the 67°F bin.
17 | This is a dry condition for the 72°F bin.
18 | You can fix the error by obtaining a copy of Get Psyched from the KW Engineering website (Just Google for KW Engineering Get Psyched). It is a free Excel plug-in. Once you install and activate it, the formula should work. If you still show an error, click into one of the cells and you will probably see something that looks like this. ='C:\Program Files (x86)\Microsoft Office\Root\Office16\LIBRARY\PSYCH.XLA'!humidratio(B29,14.7,1,C29) The 'C:\Program Files (x86)\Microsoft Office\Root\Office16\LIBRARY\PSYCH.XLA'! is where the Get Psyched plug-in was located on my computer and it is confusing your computer. In my experience, if you edit it the formula so that it looks like this: =<GetPsychedFunction>(B29,14.7,1,C29) where <GetPsychedFunction> is one of the Get Psyched Functions like "humidratio" or "enthalpy", then the formula will start to work. You should only need to make the edit in one row. Once you hae done that, you can copy and paste the repaired formulas down to all of the other rows in the column.
MOA Mix at the 2% Design Condition
Blank Condition
Air Side | [10 empty] | Water Side
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr | Latent Btu/hr | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fpm | Pressure Drop, ft.w.c. | Fouling Factor
[6 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
[6 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
MOA Mix at a Humid 82°F Bin Condition
MOA Mix at the 0.4% Design Condition but with 50% MOA
MOA Mix at a Humid 76°F Bin Condition
MOA Mix at a Humid 87°F Bin Condition

## CC Model Design Flow and LAT
This model was developed using the Greenheck Coil Selection Program. It models CC-16, which is typical of the vast majority of the coils in the facility.
Construction Details
Finned Length - |  |  | 70 |  | inches | Tube Material - |  | Copper
Finned Height - |  |  | 30 |  | inches | Tube Diameter - |  | 0.625 |  | inch
Face Area - |  |  | 14.5833 | 0 | sq.ft. | Tube Wall Thickness - |  | 0.02 |  | inches
Coils in the Coil Bank - |  |  | 2 |  |  | Tube interior - |  | Smooth
Coil Bank Face Area - |  |  | 29.1667 | 0 | sq.ft. | Connection Hand - |  | Right |  | (Facing with Air Flow Direction)
Rows - |  |  | 6 |  |  | Supply Connection Size - |  | 2
Fins per Inch - |  |  | 12 |  |  | Return Connection Size - |  | 2
Fin Material - |  |  | Aluminum |  |  | Number of Feeds - |  | 15
Fin Thickness - |  |  | 0.006 |  |  | Number of Passes - |  | 8
Fin Type - |  |  | Sine-wave |  |  | Circuiting - |  | 0.53333 |  | Serpentine
Casing Material - |  |  | Galvanized Steel |  |  | Dry Weight - |  | 315 |  | per coil
Coating - |  |  | None |  |  | Operating Weight - |  | 418 |  | per coil
Greenheck File Location - |  | ..\Coil Models
Design Condition - Seattle 0.4% Design Conditions, 62.5% Minimum Outdoor Air, SHR = .92, Space = 72°F, 50% RH | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lb | Coil SHR |  | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | Water Flow Turbulent, Transition, or Laminar
14000 | 82 | 64 | 52 | 51.9 | #NAME? | #NAME? | 491700 | 480 | 0.84 | 0 | 61.3 | 44 | 60 | 16 | 40.8667 | 1.5 | 2.23 | 3.8 | 0 | Note 2 | #NAME? | #NAME? | #NAME? | #NAME? | 459100 | 32600 | 453600 | #NAME? | #NAME? | See Below |  | 0.625 | 1.407e-05 | 8254.8567 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
Design Condition - Seattle 2% Design Conditions | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lb | Coil SHR |  | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
14000 | 78.1 | 62.3 | 52 | 52 | #NAME? | #NAME? | 398700 | 480 | 0.72 | 0 | 48 | 44 | 60.6 | 16.6 | 33.2 | 1.4458 | 1.75 | 2.4 | 0 | Note 6 | #NAME? | #NAME? | #NAME? | #NAME? | 398700 | 0 | 394632 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 6478.0265 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
Design Airflow and Leaving Air Temperature, Different Entering Conditions | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lbn (Red Exceeds Design) | Coil SHR | Point on Psych Chart | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr (Model output) | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
14000 | 90 | 67.3 | 52 | 51.9 | #NAME? | #NAME? | 648500 | 480 | 0.86 | 0 | 84 | 44 | 59.4 | 15.4 | 53.9 | 1.5584 | 3.06 | 6.7 | 0 | Note 11 | #NAME? | #NAME? | #NAME? | #NAME? | 581400 | 67100 | 574560 | #NAME? | #NAME? | #NAME? | 1 | 0.625 | 1.407e-05 | 11327.2921 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 87 | 65.4 | 52 | 52 | #NAME? | #NAME? | 534400 | 480 | 0.72 | 0 | 59 | 44 | 62.1 | 18.1 | 44.4958 | 1.326 | 2.15 | 3.5 | 0 | Note 10 | #NAME? | #NAME? | #NAME? | #NAME? | 534400 | 0 | 529200 | #NAME? | #NAME? | #NAME? | 2 | 0.625 | 1.407e-05 | 7958.7183 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 83.4 | 66.4 | 52 | 51.9 | #NAME? | #NAME? | 608300 | 480 | 0.9 | 0 | 93 | 44 | 57 | 13 | 50.375 | 1.8462 | 3.38 | 8.2 | 0 | Note 14 | #NAME? | #NAME? | #NAME? | #NAME? | 482100 | 126200 | 474768 | #NAME? | #NAME? | #NAME? | 3 | 0.625 | 1.407e-05 | 12511.8455 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 83 | 64.4 | 52 | 52 | #NAME? | #NAME? | 474400 | 480 | 0.72 | 0 | 54.5 | 44 | 61.4 | 17.4 | 39.5125 | 1.3793 | 1.98 | 3 | 0 | Note 9 | #NAME? | #NAME? | #NAME? | #NAME? | 474400 | 0 | 468720 | #NAME? | #NAME? | #NAME? | 4 | 0.625 | 1.407e-05 | 7329.4243 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 82 | 64 | 52 | 51.9 | #NAME? | #NAME? | 491700 | 480 | 0.84 | 0 | 61.3 | 44 | 60 | 16 | 40.8667 | 1.5 | 2.23 | 3.8 | 0 | Note 2 | #NAME? | #NAME? | #NAME? | #NAME? | 459100 | 32600 | 453600 | #NAME? | #NAME? | #NAME? | 5 | 0.625 | 1.407e-05 | 8254.8567 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 80.6 | 63.4 | 52 | 52 | #NAME? | #NAME? | 436600 | 480 | 0.72 | 0 | 51 | 44 | 61.1 | 17.1 | 36.3375 | 1.4035 | 1.86 | 2.7 | 0 | Note 7 | #NAME? | #NAME? | #NAME? | #NAME? | 436600 | 0 | 432432 | #NAME? | #NAME? | #NAME? | 6 | 0.625 | 1.407e-05 | 6885.2168 | 64.6154 | 0.000152 | 283400.8097 | Turbulent | Bin Data Plot | MOA Mix at 0.4% Design Condition
14000 | 79.9 | 66.6 | 52 | 51.9 | #NAME? | #NAME? | 619700 | 480 | 0.91 | 0 | 104 | 44 | 55.9 | 11.9 | 51.5667 | 2.0168 | 3.78 | 10.1 | 0 | Note 8 | #NAME? | #NAME? | #NAME? | #NAME? | 429100 | 190600 | 421848 | #NAME? | #NAME? | #NAME? | 7 | 0.625 | 1.407e-05 | 13992.5373 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 78.1 | 62.3 | 52 | 52 | #NAME? | #NAME? | 398700 | 480 | 0.72 | 0 | 48 | 44 | 60.6 | 16.6 | 33.2 | 1.4458 | 1.75 | 2.4 | 0 | Note 6 | #NAME? | #NAME? | #NAME? | #NAME? | 398700 | 0 | 394632 | #NAME? | #NAME? | #NAME? | 12 | 0.625 | 1.407e-05 | 6478.0265 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 76 | 61.7 | 52 | 52 | #NAME? | #NAME? | 367000 | 480 | 0.72 | 0 | 45.5 | 44 | 60.1 | 16.1 | 30.5229 | 1.4907 | 1.66 | 2.2 | 0 | Note 5 | #NAME? | #NAME? | #NAME? | #NAME? | 367000 | 0 | 362880 | #NAME? | #NAME? | #NAME? | 8 | 0.625 | 1.407e-05 | 6144.8709 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 75.6 | 64.2 | 52 | 52 | #NAME? | #NAME? | 367000 | 480 | 0.72 | 0 | 45.5 | 44 | 60.1 | 16.1 | 30.5229 | 1.4907 | 1.66 | 2.2 | 0 | Note 13 | #NAME? | #NAME? | #NAME? | #NAME? | 367000 | 0 | 356832 | #NAME? | #NAME? | #NAME? | 9 | 0.625 | 1.407e-05 | 6144.8709 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 72 | 67.8 | 52 | 52 | #NAME? | #NAME? | 689300 | 480 | 0.92 | 0 | 124 | 44 | 55 | 11 | 56.8333 | 2.1818 | 4.51 | 14 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 309600 | 379700 | 302400 | #NAME? | #NAME? | #NAME? | 10 | 0.625 | 1.407e-05 | 16694.7998 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 72 | 51.5 | 52 | 42.1 | #NAME? | #NAME? | 306300 | 480 | 0.72 | 0 | 40.5 | 44 | 59.1 | 15.1 | 25.4812 | 1.5894 | 1.47 | 1.8 | 0 | Note 17 | #NAME? | #NAME? | #NAME? | #NAME? | 306300 | 0 | 302400 | #NAME? | #NAME? | #NAME? | 21 | 0.625 | 1.407e-05 | 5441.5423 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 72 | 59.8 | 52 | 51.8 | #NAME? | #NAME? | 306300 | 480 | 0.72 | 0 | 40.5 | 44 | 59.1 | 15.1 | 25.4812 | 1.5894 | 1.47 | 1.8 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 306300 | 0 | 302400 | #NAME? | #NAME? | #NAME? | 11 | 0.625 | 1.407e-05 | 5441.5423 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 67 | 66 | 52 | 52 | #NAME? | #NAME? | 597700 | 480 | 0.92 | 0 | 107 | 44 | 55.1 | 11.1 | 49.4875 | 2.1622 | 3.89 | 10.6 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 232700 | 365000 | 226800 | #NAME? | #NAME? | #NAME? | 13 | 0.625 | 1.407e-05 | 14399.7276 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 67 | 57.6 | 52 | 51.5 | #NAME? | #NAME? | 229000 | 480 | 0.73 | 0 | 33.5 | 44 | 57.6 | 13.6 | 18.9833 | 1.7647 | 1.22 | 1.3 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 229000 | 0 | 226800 | #NAME? | #NAME? | #NAME? | 14 | 0.625 | 1.407e-05 | 4516.1099 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 67 | 46.5 | 52 | 39 | #NAME? | #NAME? | 229000 | 480 | 0.73 | 0 | 33.5 | 44 | 57.6 | 13.6 | 18.9833 | 1.7647 | 1.22 | 1.3 | 0 | Note 16 | #NAME? | #NAME? | #NAME? | #NAME? | 229000 | 0 | 226800 | #NAME? | #NAME? | #NAME? | 20 | 0.625 | 1.407e-05 | 4516.1099 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 62 | 62 | 52 | 52 | #NAME? | #NAME? | 407500 | 480 | 0.92 | 0 | 73 | 44 | 55.1 | 11.1 | 33.7625 | 2.1622 | 2.66 | 5.2 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 154700 | 252800 | 151200 | #NAME? | #NAME? | #NAME? | 15 | 0.625 | 1.407e-05 | 9846.6003 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 62 | 55.4 | 52 | 51.2 | #NAME? | #NAME? | 152100 | 480 | 0.73 | 0 | 26 | 44 | 55.7 | 11.7 | 12.675 | 2.0513 | 0.95 | 0.8 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 152100 | 0 | 151200 | #NAME? | #NAME? | #NAME? | 16 | 0.625 | 1.407e-05 | 3516.643 | 64.6154 | 0.000152 | 283400.8097 | Transition
14000 | 57 | 57 | 52 | 52 | #NAME? | #NAME? | 193100 | 480 | 0.92 | 0 | 39 | 44 | 53.9 | 9.9 | 16.0875 | 2.4242 | 1.42 | 1.7 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 77300 | 115800 | 75600 | #NAME? | #NAME? | #NAME? | 17 | 0.625 | 1.407e-05 | 5256.4558 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
14000 | 57 | 52.2 | 52 | 50 | #NAME? | #NAME? | 76400 | 480 | 0.73 | 0 | 17.3 | 44 | 52.8 | 8.8 | 6.3433 | 2.7273 | 0.63 | 0.4 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 76400 | 0 | 75600 | #NAME? | #NAME? | #NAME? | 18 | 0.625 | 1.407e-05 | 2332.0896 | 64.6154 | 0.000152 | 283400.8097 | Transition
14000 | 57 | 43.1 | 52 | 40.5 | #NAME? | #NAME? | 77100 | 480 | 0.73 | 0 | 17.4 | 44 | 52.8 | 8.8 | 6.38 | 2.7273 | 0.63 | 0.4 | 0 | Note 15 | #NAME? | #NAME? | #NAME? | #NAME? | 77100 | 0 | 75600 | #NAME? | #NAME? | #NAME? | 19 | 0.625 | 1.407e-05 | 2332.0896 | 64.6154 | 0.000152 | 283400.8097 | Transition
Notes
1 | Because the Greenheck model reports loads as Mbtu, for low latent loads, it may report 0 Btu/hr of latent load even though it shows a slightly lower leaving wetbulb than dry bulb temperature and a slightly higher pressrue drop relative to a dry coil. To overcome this, the modeled total load is used. The latent load is calculated based on the difference between entering and leaving w, with the leaving w being set by the modeled leaving conditions. The sensible load is calculated by subtracting the latent load from the total load.
2 | This analysis is based on the selection point on the CDs and the Seattle 0.4% cooling design condition; see psych chart to the right
3 | Dry bulb is the middle of temperature of a 5°F by 8 hour bin; Wet bulb is the mean coincident wet bulb for the bin. See psych chart to the right.
4 | This is the operating condition for the drybulb bin but at the highest observed wet bulb temperature based on the bin plot in Akton Psych chart to illustrate the impact of a heavier latent load.
5 | This is a mixed condition based on the design return condition and the 77°F bin conditions
6 | This analysis is based on the selection point on the CDs and the Seattle 2% cooling design condition; see psych chart to the right
7 | This is a mixed condition based on 50% outdoor air vs. the apparent design percentage. Its also very close to the mix condition for the 82°F bin.
8 | This is a humid MOA condition for the 82°F bin.
9 | This is a mixed condition based on the design return condition and the 87°F bin conditions
10 | This is a mixed condition based on the design return condition and the 92°F bin conditions
11 | This is a mixed condition based on the design return condition and the 97°F bin conditions
12 | This is a humid MOA condition for the 82°F bin.
13 | This is a humid MOA condition for the 77°F bin.
14 | This is a humid MOA condition for the 87°F bin.
15 | This is a dry condition for the 57°F bin.
16 | This is a dry condition for the 67°F bin.
17 | This is a dry condition for the 72°F bin.
MOA Mix at the 2% Design Condition
Blank Condition
Air Side | [10 empty] | Water Side
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr | Latent Btu/hr | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fpm | Pressure Drop, ft.w.c. | Fouling Factor
[6 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
[6 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
MOA Mix at a Humid 82°F Bin Condition
MOA Mix at the 0.4% Design Condition but with 50% MOA
MOA Mix at a Humid 76°F Bin Condition
MOA Mix at a Humid 87°F Bin Condition

## CC Model Lower Flow Design LAT
This model was developed using the Greenheck Coil Selection Program. It models CC-16, which is typical of the vast majority of the coils in the facility.
Construction Details
Finned Length - |  |  | 70 |  | inches | Tube Material - |  | Copper
Finned Height - |  |  | 30 |  | inches | Tube Diameter - |  | 0.625 |  | inch
Face Area - |  |  | 14.5833 | 0 | sq.ft. | Tube Wall Thickness - |  | 0.02 |  | inches
Coils in the Coil Bank - |  |  | 2 |  |  | Tube interior - |  | Smooth
Coil Bank Face Area - |  |  | 29.1667 | 0 | sq.ft. | Connection Hand - |  | Right |  | (Facing with Air Flow Direction)
Rows - |  |  | 6 |  |  | Supply Connection Size - |  | 2
Fins per Inch - |  |  | 12 |  |  | Return Connection Size - |  | 2
Fin Material - |  |  | Aluminum |  |  | Number of Feeds - |  | 15
Fin Thickness - |  |  | 0.006 |  |  | Number of Passes - |  | 8
Fin Type - |  |  | Sine-wave |  |  | Circuiting - |  | 0.53333 |  | Serpentine
Casing Material - |  |  | Galvanized Steel |  |  | Dry Weight - |  | 315 |  | per coil
Coating - |  |  | None |  |  | Operating Weight - |  | 418 |  | per coil
Greenheck File Location - |  | ..\Coil Models
Design Condition - Seattle 0.4% Design Conditions, 62.5% Minimum Outdoor Air, SHR = .92, Space = 72°F, 50% RH | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lb | Coil SHR |  | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | Water Flow Turbulent, Transition, or Laminar
14000 | 82 | 64 | 52 | 51.9 | #NAME? | #NAME? | 491700 | 480 | 0.84 | 0 | 61.3 | 44 | 60 | 16 | 40.8667 | 1.5 | 2.23 | 3.8 | 0 | Note 2 | #NAME? | #NAME? | #NAME? | #NAME? | 459100 | 32600 | 453600 | #NAME? | #NAME? | See Below |  | 0.625 | 1.407e-05 | 8254.8567 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
Design Condition - Seattle 2% Design Conditions | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lb | Coil SHR |  | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
14000 | 78.1 | 62.3 | 52 | 52 | #NAME? | #NAME? | 398700 | 480 | 0.72 | 0 | 48 | 44 | 60.6 | 16.6 | 33.2 | 1.4458 | 1.75 | 2.4 | 0 | Note 6 | #NAME? | #NAME? | #NAME? | #NAME? | 398700 | 0 | 394632 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 6478.0265 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
Design Airflow and Leaving Air Temperature, Different Entering Conditions | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lbn (Red Exceeds Design) | Coil SHR | Point on Psych Chart | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr (Model output) | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
10000 | 90 | 67.3 | 52 | 52 | #NAME? | #NAME? | 460500 | 343 | 0.52 | 0 | 49 | 44 | 62.7 | 18.7 | 38.1792 | 1.2834 | 1.78 | 2.5 | 0 | Note 11 | #NAME? | #NAME? | #NAME? | #NAME? | 415100 | 45400 | 410400 | #NAME? | #NAME? | #NAME? | 1 | 0.625 | 1.407e-05 | 6589.0784 | 64.6154 | 0.000152 | 202513.4953 | Turbulent | Bin Data Plot
10000 | 87 | 65.4 | 52 | 52 | #NAME? | #NAME? | 381700 | 343 | 0.41 | 0 | 37.5 | 44 | 64.3 | 20.3 | 31.7187 | 1.1823 | 2.15 | 1.5 | 0 | Note 10 | #NAME? | #NAME? | #NAME? | #NAME? | 381700 | 0 | 378000 | #NAME? | #NAME? | #NAME? | 2 | 0.625 | 1.407e-05 | 7958.7183 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 83.4 | 66.4 | 52 | 52 | #NAME? | #NAME? | 431500 | 343 | 0.55 | 0 | 54 | 44 | 59.9 | 15.9 | 35.775 | 1.5094 | 1.96 | 3 | 0 | Note 14 | #NAME? | #NAME? | #NAME? | #NAME? | 343900 | 87600 | 339120 | #NAME? | #NAME? | #NAME? | 3 | 0.625 | 1.407e-05 | 7255.3897 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 83 | 64.4 | 52 | 51.9 | #NAME? | #NAME? | 363100 | 343 | 0.5 | 0 | 40 | 44 | 62.1 | 18.1 | 30.1667 | 1.326 | 1.46 | 1.7 | 0 | Note 9 | #NAME? | #NAME? | #NAME? | #NAME? | 339200 | 23900 | 334800 | #NAME? | #NAME? | #NAME? | 4 | 0.625 | 1.407e-05 | 5404.525 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 82 | 64 | 52 | 52 | #NAME? | #NAME? | 327200 | 343 | 0.41 | 0 | 34.5 | 44 | 62.9 | 18.9 | 27.1687 | 1.2698 | 1.26 | 1.3 | 0 | Note 2 | #NAME? | #NAME? | #NAME? | #NAME? | 327200 | 0 | 324000 | #NAME? | #NAME? | #NAME? | 5 | 0.625 | 1.407e-05 | 4664.1791 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 80.6 | 63.4 | 52 | 51.9 | #NAME? | #NAME? | 330300 | 343 | 0.49 | 0 | 37 | 44 | 61.8 | 17.8 | 27.4417 | 1.3483 | 1.35 | 1.5 | 0 | Note 7 | #NAME? | #NAME? | #NAME? | #NAME? | 312800 | 17500 | 308880 | #NAME? | #NAME? | #NAME? | 6 | 0.625 | 1.407e-05 | 4997.3348 | 64.6154 | 0.000152 | 202513.4953 | Turbulent |  | MOA Mix at 0.4% Design Condition
10000 | 79.9 | 66.6 | 52 | 51.9 | #NAME? | #NAME? | 442600 | 343 | 0.57 | 0 | 61 | 44 | 58.5 | 14.5 | 36.8542 | 1.6552 | 2.22 | 3.7 | 0 | Note 8 | #NAME? | #NAME? | #NAME? | #NAME? | 307100 | 135500 | 301320 | #NAME? | #NAME? | #NAME? | 7 | 0.625 | 1.407e-05 | 8217.8394 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 78.1 | 62.3 | 52 | 52 | #NAME? | #NAME? | 285000 | 343 | 0.41 | 0 | 32.1 | 44 | 61.7 | 17.7 | 23.6738 | 1.3559 | 1.17 | 1.2 | 0 | Note 6 | #NAME? | #NAME? | #NAME? | #NAME? | 285000 | 0 | 281880 | #NAME? | #NAME? | #NAME? | 12 | 0.625 | 1.407e-05 | 4331.0235 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 76 | 61.7 | 52 | 52 | #NAME? | #NAME? | 262200 | 343 | 0.41 | 0 | 30.8 | 44 | 61 | 17 | 21.8167 | 1.4118 | 1.66 | 1.1 | 0 | Note 5 | #NAME? | #NAME? | #NAME? | #NAME? | 262200 | 0 | 259200 | #NAME? | #NAME? | #NAME? | 8 | 0.625 | 1.407e-05 | 6144.8709 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 75.6 | 64.2 | 52 | 51.9 | #NAME? | #NAME? | 360000 | 343 | 0.57 | 0 | 50.8 | 44 | 58.1 | 14.1 | 29.845 | 1.7021 | 1.85 | 2.7 | 0 | Note 13 | #NAME? | #NAME? | #NAME? | #NAME? | 259600 | 100400 | 254880 | #NAME? | #NAME? | #NAME? | 9 | 0.625 | 1.407e-05 | 6848.1995 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 72 | 67.8 | 52 | 52 | #NAME? | #NAME? | 489800 | 343 | 0.59 | 0 | 72 | 44 | 57.6 | 13.6 | 40.8 | 1.7647 | 2.62 | 5.1 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 221000 | 268800 | 216000 | #NAME? | #NAME? | #NAME? | 10 | 0.625 | 1.407e-05 | 9698.5312 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 72 | 51.5 | 52 | 42.1 | #NAME? | #NAME? | 218800 | 343 | 0.41 | 0 | 28 | 44 | 59.6 | 15.6 | 18.2 | 1.5385 | 1.02 | 0.6 | 0 | Note 17 | #NAME? | #NAME? | #NAME? | #NAME? | 218800 | 0 | 216000 | #NAME? | #NAME? | #NAME? | 21 | 0.625 | 1.407e-05 | 3775.764 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 72 | 59.8 | 52 | 51.9 | #NAME? | #NAME? | 217800 | 343 | 0.41 | 0 | 27.8 | 44 | 59.6 | 15.6 | 18.07 | 1.5385 | 1.01 | 0.9 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 217800 | 0 | 216000 | #NAME? | #NAME? | #NAME? | 11 | 0.625 | 1.407e-05 | 3738.7467 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 71 | 63.8 | 52 | 52 | #NAME? | #NAME? | 346700 | 343 | 0.58 | 0 | 52.5 | 44 | 57.2 | 13.2 | 28.875 | 1.8182 | 1.91 | 2.9 | 0 | Note 6 | #NAME? | #NAME? | #NAME? | #NAME? | 208800 | 137900 | 205200 | #NAME? | #NAME? | #NAME? | 12 | 0.625 | 1.407e-05 | 7070.3032 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 67 | 66 | 52 | 52 | #NAME? | #NAME? | 426300 | 343 | 0.59 | 0 | 64 | 44 | 57.3 | 13.3 | 35.4667 | 1.8045 | 2.33 | 4.1 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 165900 | 260400 | 162000 | #NAME? | #NAME? | #NAME? | 13 | 0.625 | 1.407e-05 | 8625.0296 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 67 | 57.6 | 52 | 51.5 | #NAME? | #NAME? | 163900 | 343 | 0.42 | 0 | 24 | 44 | 57.6 | 13.6 | 13.6 | 1.7647 | 0.87 | 0.7 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 163900 | 0 | 162000 | #NAME? | #NAME? | #NAME? | 14 | 0.625 | 1.407e-05 | 3220.5046 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 67 | 46.5 | 52 | 38.9 | #NAME? | #NAME? | 163800 | 343 | 0.42 | 0 | 24 | 44 | 57.6 | 13.6 | 13.6 | 1.7647 | 0.87 | 0.7 | 0 | Note 16 | #NAME? | #NAME? | #NAME? | #NAME? | 163800 | 0 | 163900 | #NAME? | #NAME? | #NAME? | 20 | 0.625 | 1.407e-05 | 3220.5046 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 62 | 62 | 52 | 52 | #NAME? | #NAME? | 290500 | 343 | 0.52 | 0 | 47.3 | 44 | 56.2 | 12.2 | 24.0442 | 1.9672 | 1.72 | 2.4 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 110200 | 180300 | 108000 | #NAME? | #NAME? | #NAME? | 15 | 0.625 | 1.407e-05 | 6366.9747 | 64.6154 | 0.000152 | 202513.4953 | Turbulent
10000 | 62 | 55.4 | 52 | 51.3 | #NAME? | #NAME? | 108900 | 343 | 0.42 | 0 | 19.3 | 44 | 55.2 | 11.2 | 9.0067 | 2.1429 | 0.7 | 0.05 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 108900 | 0 | 108000 | #NAME? | #NAME? | #NAME? | 16 | 0.625 | 1.407e-05 | 2591.2106 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 57 | 57 | 52 | 52 | #NAME? | #NAME? | 138900 | 343 | 0.59 | 0 | 28 | 44 | 53.9 | 9.9 | 11.55 | 2.4242 | 1.02 | 0.9 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 55600 | 83300 | 54000 | #NAME? | #NAME? | #NAME? | 17 | 0.625 | 1.407e-05 | 3775.764 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 57 | 52.2 | 52 | 50 | #NAME? | #NAME? | 54700 | 343 | 0.42 | 0 | 11 | 44 | 53.9 | 9.9 | 4.5375 | 2.4242 | 0.4 | 0.2 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 54700 | 0 | 54000 | #NAME? | #NAME? | #NAME? | 18 | 0.625 | 1.407e-05 | 1480.6918 | 64.6154 | 0.000152 | 202513.4953 | Laminar
10000 | 57 | 43.1 | 52 | 40.6 | #NAME? | #NAME? | 54100 | 343 | 0.42 | 0 | 10.8 | 44 | 54 | 10 | 4.5 | 2.4 | 0.39 | 0.2 | 0 | Note 15 | #NAME? | #NAME? | #NAME? | #NAME? | 54100 | 0 | 54000 | #NAME? | #NAME? | #NAME? | 19 | 0.625 | 1.407e-05 | 1443.6745 | 64.6154 | 0.000152 | 202513.4953 | Laminar
Notes
1 | Because the Greenheck model reports loads as Mbtu, for low latent loads, it may report 0 Btu/hr of latent load even though it shows a slightly lower leaving wetbulb than dry bulb temperature and a slightly higher pressrue drop relative to a dry coil. To overcome this, if there is a wet bulb depression indicated by the model output, the sensible load is calculated based on 1.08 x cfm x ∆t and the latent load is calculated by subtracting the sensible load from the total load. As a cross check the latent load is calculated based on the wet bulb depression. There will be slight differences due to rounding errors and the specific units conversion constant used.
2 | This analysis is based on the selection point on the CDs and the Seattle 0.4% cooling design condition; see psych chart to the right
3 | Dry bulb is the middle of temperature of a 5°F by 8 hour bin; Wet bulb is the mean coincident wet bulb for the bin. See psych chart to the right.
4 | This is the operating condition for the drybulb bin but at the highest observed wet bulb temperature based on the bin plot in Akton Psych chart to illustrate the impact of a heavier latent load.
5 | This is a mixed condition based on the design return condition and the 77°F bin conditions
6 | This analysis is based on the selection point on the CDs and the Seattle 2% cooling design condition; see psych chart to the right
7 | This is a mixed condition based on 50% outdoor air vs. the apparent design percentage. Its also very close to the mix condition for the 82°F bin.
8 | This is a humid MOA condition for the 82°F bin.
9 | This is a mixed condition based on the design return condition and the 87°F bin conditions
10 | This is a mixed condition based on the design return condition and the 92°F bin conditions
11 | This is a mixed condition based on the design return condition and the 97°F bin conditions
12 | This is a humid MOA condition for the 82°F bin.
13 | This is a humid MOA condition for the 77°F bin.
14 | This is a humid MOA condition for the 87°F bin.
15 | This is a dry condition for the 57°F bin.
16 | This is a dry condition for the 67°F bin.
17 | This is a dry condition for the 72°F bin.
MOA Mix at the 2% Design Condition
Blank Condition
Air Side | [10 empty] | Water Side
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr | Latent Btu/hr | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fpm | Pressure Drop, ft.w.c. | Fouling Factor
[6 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
[6 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
MOA Mix at a Humid 82°F Bin Condition
MOA Mix at the 0.4% Design Condition but with 50% MOA
MOA Mix at a Humid 76°F Bin Condition
MOA Mix at a Humid 87°F Bin Condition

## CC Model Lower Flow Higher LAT
This model was developed using the Greenheck Coil Selection Program. It models CC-16, which is typical of the vast majority of the coils in the facility.
Construction Details
Finned Length - |  |  | 70 |  | inches | Tube Material - |  | Copper
Finned Height - |  |  | 30 |  | inches | Tube Diameter - |  | 0.625 |  | inch
Face Area - |  |  | 14.5833 | 0 | sq.ft. | Tube Wall Thickness - |  | 0.02 |  | inches
Coils in the Coil Bank - |  |  | 2 |  |  | Tube interior - |  | Smooth
Coil Bank Face Area - |  |  | 29.1667 | 0 | sq.ft. | Connection Hand - |  | Right |  | (Facing with Air Flow Direction)
Rows - |  |  | 6 |  |  | Supply Connection Size - |  | 2
Fins per Inch - |  |  | 12 |  |  | Return Connection Size - |  | 2
Fin Material - |  |  | Aluminum |  |  | Number of Feeds - |  | 15
Fin Thickness - |  |  | 0.006 |  |  | Number of Passes - |  | 8
Fin Type - |  |  | Sine-wave |  |  | Circuiting - |  | 0.53333 |  | Serpentine
Casing Material - |  |  | Galvanized Steel |  |  | Dry Weight - |  | 315 |  | per coil
Coating - |  |  | None |  |  | Operating Weight - |  | 418 |  | per coil
Greenheck File Location - |  | ..\Coil Models
Design Condition - Seattle 0.4% Design Conditions, 62.5% Minimum Outdoor Air, SHR = .92, Space = 72°F, 50% RH | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lb | Coil SHR |  | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | Water Flow Turbulent, Transition, or Laminar
14000 | 82 | 64 | 52 | 51.9 | #NAME? | #NAME? | 491700 | 480 | 0.84 | 0 | 61.3 | 44 | 60 | 16 | 40.8667 | 1.5 | 2.23 | 3.8 | 0 | Note 2 | #NAME? | #NAME? | #NAME? | #NAME? | 459100 | 32600 | 453600 | #NAME? | #NAME? | See Below |  | 0.625 | 1.407e-05 | 8254.8567 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
Design Condition - Seattle 2% Design Conditions | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lb | Coil SHR |  | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
14000 | 78.1 | 62.3 | 52 | 52 | #NAME? | #NAME? | 398700 | 480 | 0.72 | 0 | 48 | 44 | 60.6 | 16.6 | 33.2 | 1.4458 | 1.75 | 2.4 | 0 | Note 6 | #NAME? | #NAME? | #NAME? | #NAME? | 398700 | 0 | 394632 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 6478.0265 | 64.6154 | 0.000152 | 283400.8097 | Turbulent
Design Airflow and Leaving Air Temperature, Different Entering Conditions | [19 empty] | Support
Air Side | [10 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lbn (Red Exceeds Design) | Coil SHR | Point on Psych Chart | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr (Model output) | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
10000 | 90 | 67.3 | 60 | 56.8 | #NAME? | #NAME? | 327500 | 343 | 0.41 | 0 | 22.7 | 44 | 72.8 | 28.8 | 27.24 | 0.83333 | 0.83 | 0.6 | 0 | Note 11 | #NAME? | #NAME? | #NAME? | #NAME? | 327500 | 0 | 324000 | #NAME? | #NAME? | #NAME? | 1 | 0.625 | 1.407e-05 | 3072.4354 | 64.6154 | 0.000152 | 202513.4953 | Transition | Bin Data Plot
10000 | 87 | 65.4 | 60 | 55.7 | #NAME? | #NAME? | 294500 | 343 | 0.41 | 0 | 21.5 | 44 | 71.4 | 27.4 | 24.5458 | 0.87591 | 0.78 | 0.5 | 0 | Note 10 | #NAME? | #NAME? | #NAME? | #NAME? | 294500 | 0 | 291600 | #NAME? | #NAME? | #NAME? | 2 | 0.625 | 1.407e-05 | 2887.349 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 83.4 | 66.4 | 60 | 58.2 | #NAME? | #NAME? | 255300 | 343 | 0.41 | 0 | 20 | 44 | 69.5 | 25.5 | 21.25 | 0.94118 | 0.73 | 0.5 | 0 | Note 14 | #NAME? | #NAME? | #NAME? | #NAME? | 255300 | 0 | 252720 | #NAME? | #NAME? | #NAME? | 3 | 0.625 | 1.407e-05 | 2702.2625 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 83 | 64.4 | 60 | 56 | #NAME? | #NAME? | 250800 | 343 | 0.41 | 0 | 19.8 | 44 | 69.3 | 25.3 | 20.8725 | 0.94862 | 0.72 | 0.5 | 0 | Note 9 | #NAME? | #NAME? | #NAME? | #NAME? | 250800 | 0 | 248400 | #NAME? | #NAME? | #NAME? | 4 | 0.625 | 1.407e-05 | 2665.2452 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 82 | 64 | 60 | 56 | #NAME? | #NAME? | 240300 | 343 | 0.414 | 0 | 19.4 | 44 | 68.7 | 24.7 | 19.9658 | 0.97166 | 0.71 | 0.5 | 0 | Note 2 | #NAME? | #NAME? | #NAME? | #NAME? | 240300 | 0 | 237600 | #NAME? | #NAME? | #NAME? | 5 | 0.625 | 1.407e-05 | 2628.2279 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 80.6 | 63.4 | 60 | 55.8 | #NAME? | #NAME? | 224500 | 343 | 0.41 | 0 | 18.7 | 44 | 68 | 24 | 18.7 | 1 | 0.68 | 0.4 | 0 | Note 7 | #NAME? | #NAME? | #NAME? | #NAME? | 224500 | 0 | 222480 | #NAME? | #NAME? | #NAME? | 6 | 0.625 | 1.407e-05 | 2517.176 | 64.6154 | 0.000152 | 202513.4953 | Transition |  | MOA Mix at 0.4% Design Condition
10000 | 79.9 | 66.6 | 60 | 59.8 | #NAME? | #NAME? | 217100 | 343 | 0.41 | 0 | 18.4 | 44 | 67.5 | 23.5 | 18.0167 | 1.0213 | 0.67 | 0.4 | 0 | Note 8 | #NAME? | #NAME? | #NAME? | #NAME? | 217100 | 0 | 214920 | #NAME? | #NAME? | #NAME? | 7 | 0.625 | 1.407e-05 | 2480.1587 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 78.1 | 62.3 | 60 | 55.5 | #NAME? | #NAME? | 197200 | 343 | 0.41 | 0 | 17.5 | 44 | 66.5 | 22.5 | 16.4062 | 1.0667 | 0.64 | 0.4 | 0 | Note 6 | #NAME? | #NAME? | #NAME? | #NAME? | 197200 | 0 | 195480 | #NAME? | #NAME? | #NAME? | 12 | 0.625 | 1.407e-05 | 2369.1068 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 76 | 61.7 | 60 | 55.7 | #NAME? | #NAME? | 174400 | 343 | 0.41 | 0 | 16.4 | 44 | 65.2 | 21.2 | 14.4867 | 1.1321 | 0.6 | 0.3 | 0 | Note 5 | #NAME? | #NAME? | #NAME? | #NAME? | 174400 | 0 | 172800 | #NAME? | #NAME? | #NAME? | 8 | 0.625 | 1.407e-05 | 2221.0377 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 75.6 | 64.2 | 60 | 58.6 | #NAME? | #NAME? | 170200 | 343 | 0.41 | 0 | 16.2 | 44 | 65 | 21 | 14.175 | 1.1429 | 0.59 | 0.03 | 0 | Note 13 | #NAME? | #NAME? | #NAME? | #NAME? | 170200 | 0 | 168480 | #NAME? | #NAME? | #NAME? | 9 | 0.625 | 1.407e-05 | 2184.0204 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 72 | 67.8 | 60 | 60 | #NAME? | #NAME? | 261300 | 343 | 0.58 | 0 | 26.6 | 44 | 63.6 | 19.6 | 21.7233 | 1.2245 | 0.97 | 0.8 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 132400 | 128900 | 129600 | #NAME? | #NAME? | #NAME? | 10 | 0.625 | 1.407e-05 | 3590.6776 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 72 | 51.5 | 60 | 46.1 | #NAME? | #NAME? | 130900 | 343 | 0.41 | 0 | 13.2 | 44 | 63.8 | 19.8 | 10.89 | 1.2121 | 0.48 | 0.2 | 0 | Note 17 | #NAME? | #NAME? | #NAME? | #NAME? | 130900 | 0 | 129600 | #NAME? | #NAME? | #NAME? | 21 | 0.625 | 1.407e-05 | 1776.8301 | 64.6154 | 0.000152 | 202513.4953 | Laminar
10000 | 72 | 59.8 | 60 | 55.2 | #NAME? | #NAME? | 131000 | 343 | 0.41 | 0 | 13.2 | 44 | 63.8 | 19.8 | 10.89 | 1.2121 | 0.48 | 0.2 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 131000 | 0 | 129600 | #NAME? | #NAME? | #NAME? | 11 | 0.625 | 1.407e-05 | 1776.8301 | 64.6154 | 0.000152 | 202513.4953 | Laminar
10000 | 71 | 63.8 | 60 | 59.9 | #NAME? | #NAME? | 119800 | 343 | 0.41 | 0 | 12 | 44 | 63.9 | 19.9 | 9.95 | 1.206 | 0.44 | 0.2 | 0 | Note 6 | #NAME? | #NAME? | #NAME? | #NAME? | 119800 | 0 | 118800 | #NAME? | #NAME? | #NAME? | 12 | 0.625 | 1.407e-05 | 1628.761 | 64.6154 | 0.000152 | 202513.4953 | Laminar
10000 | 67 | 66 | 60 | 60 | #NAME? | #NAME? | 198400 | 343 | 0.59 | 0 | 22.2 | 44 | 61.8 | 17.8 | 16.465 | 1.3483 | 0.81 | 0.6 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 77500 | 120900 | 75600 | #NAME? | #NAME? | #NAME? | 13 | 0.625 | 1.407e-05 | 2998.4009 | 64.6154 | 0.000152 | 202513.4953 | Transition
10000 | 67 | 57.6 | 60 | 54.8 | #NAME? | #NAME? | 76600 | 343 | 0.41 | 0 | 7.7 | 44 | 63.9 | 19.9 | 6.3846 | 1.206 | 0.28 | 0.1 | 0 | Note 3 | #NAME? | #NAME? | #NAME? | #NAME? | 76600 | 0 | 75600 | #NAME? | #NAME? | #NAME? | 14 | 0.625 | 1.407e-05 | 1036.4842 | 64.6154 | 0.000152 | 202513.4953 | Laminar
10000 | 67 | 46.5 | 60 | 43.1 | #NAME? | #NAME? | 76300 | 343 | 0.41 | 0 | 7.7 | 44 | 63.9 | 19.9 | 6.3846 | 1.206 | 0.28 | 0.1 | 0 | Note 16 | #NAME? | #NAME? | #NAME? | #NAME? | 76300 | 0 | 163900 | #NAME? | #NAME? | #NAME? | 20 | 0.625 | 1.407e-05 | 1036.4842 | 64.6154 | 0.000152 | 202513.4953 | Laminar
10000 | 62 | 62 | 60 | 60 | #NAME? | #NAME? | 62200 | 343 | 0.59 | 0 | 7.4 | 44 | 60.8 | 16.8 | 5.18 | 1.4286 | 0.27 | 0.1 | 0 | Note 4 | #NAME? | #NAME? | #NAME? | #NAME? | 21700 | 40500 | 21600 | #NAME? | #NAME? | #NAME? | 15 | 0.625 | 1.407e-05 | 999.467 | 64.6154 | 0.000152 | 202513.4953 | Laminar
10000 | 62 | 55.4 | 60 | 54.6 | #NAME? | #NAME? | 21600 | 343 | 0.42 | 0 | 2.4 | 44 | 61.9 | 17.9 | 1.79 | 1.3408 | 0.09 | 0.0005 | 0 | Note 15 | #NAME? | #NAME? | #NAME? | #NAME? | 21600 | 0 | 21600 | #NAME? | #NAME? | #NAME? | 19 | 0.625 | 1.407e-05 | 333.1557 | 64.6154 | 0.000152 | 202513.4953 | Laminar
Notes
1 | Because the Greenheck model reports loads as Mbtu, for low latent loads, it may report 0 Btu/hr of latent load even though it shows a slightly lower leaving wetbulb than dry bulb temperature and a slightly higher pressrue drop relative to a dry coil. To overcome this, if there is a wet bulb depression indicated by the model output, the sensible load is calculated based on 1.08 x cfm x ∆t and the latent load is calculated by subtracting the sensible load from the total load. As a cross check the latent load is calculated based on the wet bulb depression. There will be slight differences due to rounding errors and the specific units conversion constant used.
2 | This analysis is based on the selection point on the CDs and the Seattle 0.4% cooling design condition; see psych chart to the right
3 | Dry bulb is the middle of temperature of a 5°F by 8 hour bin; Wet bulb is the mean coincident wet bulb for the bin. See psych chart to the right.
4 | This is the operating condition for the drybulb bin but at the highest observed wet bulb temperature based on the bin plot in Akton Psych chart to illustrate the impact of a heavier latent load.
5 | This is a mixed condition based on the design return condition and the 77°F bin conditions
6 | This analysis is based on the selection point on the CDs and the Seattle 2% cooling design condition; see psych chart to the right
7 | This is a mixed condition based on 50% outdoor air vs. the apparent design percentage. Its also very close to the mix condition for the 82°F bin.
8 | This is a humid MOA condition for the 82°F bin.
9 | This is a mixed condition based on the design return condition and the 87°F bin conditions
10 | This is a mixed condition based on the design return condition and the 92°F bin conditions
11 | This is a mixed condition based on the design return condition and the 97°F bin conditions
12 | This is a humid MOA condition for the 82°F bin.
13 | This is a humid MOA condition for the 77°F bin.
14 | This is a humid MOA condition for the 87°F bin.
15 | This is a dry condition for the 57°F bin.
16 | This is a dry condition for the 67°F bin.
17 | This is a dry condition for the 72°F bin.
MOA Mix at the 2% Design Condition
Blank Condition
Air Side | [10 empty] | Water Side
Flow, cfm | Entering tdb, °F | Entering twb, °F | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr | Latent Btu/hr | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fpm | Pressure Drop, ft.w.c. | Fouling Factor
[6 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
[6 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
MOA Mix at a Humid 82°F Bin Condition
MOA Mix at the 0.4% Design Condition but with 50% MOA
MOA Mix at a Humid 76°F Bin Condition
MOA Mix at a Humid 87°F Bin Condition

## CC Model 2015-05-21
This model was developed using the Greenheck Coil Selection Program. It models CC-16, which is typical of the vast majority of the coils in the facility.
Construction Details
| Finned Length - |  |  |  |  | 70 |  | inches | Tube Material - |  | Copper
| Finned Height - |  |  |  |  | 30 |  | inches | Tube Diameter - |  | 0.625 |  | inch
| Face Area - |  |  |  |  | 14.5833 | 0 | sq.ft. | Tube Wall Thickness - |  | 0.02 |  | inches
| Coils in the Coil Bank - |  |  |  |  | 2 |  |  | Tube interior - |  | Smooth
| Coil Bank Face Area - |  |  |  |  | 29.1667 | 0 | sq.ft. | Connection Hand - |  | Right |  | (Facing with Air Flow Direction)
| Rows - |  |  |  |  | 6 |  |  | Supply Connection Size - |  | 2
| Fins per Inch - |  |  |  |  | 12 |  |  | Return Connection Size - |  | 2
| Fin Material - |  |  |  |  | Aluminum |  |  | Number of Feeds - |  | 15
| Fin Thickness - |  |  |  |  | 0.006 |  |  | Number of Passes - |  | 8
| Fin Type - |  |  |  |  | Sine-wave |  |  | Circuiting - |  | 0.53333 |  | Serpentine
| Casing Material - |  |  |  |  | Galvanized Steel |  |  | Dry Weight - |  | 315 |  | per coil
| Coating - |  |  |  |  | None |  |  | Operating Weight - |  | 418 |  | per coil
| Greenheck File Location - |  | ..\Coil Models | [5 empty] | Approximate number of similar coils - | 52
Design Airflow and Leaving Air Temperature, Different Entering Conditions | [22 empty] | Support
Time | Air Side | [12 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lbn (Red Exceeds Design) | Coil SHR | Point on Psych Chart | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face |  |  |  | Total Load for 52 Similar Coils | Load on 2015-09-24
| Flow, cfm from Generic Day flow profile | Outdoor tdb, °F, Note 18 | Outdoor twb, °F, Note 18 | Entering tdb, °F, Note 18 | Emtering twb, °F, Note 18 | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr (Model output) | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
0.29167 | 7438.2954 | 62.1 | 56.1456 | 62.1 | 56.1456 | 58 | 54.5 | #NAME? | #NAME? | 33300 | 255 | 0.25 | 0 | 3.8 | 44 | 61.5 | 17.5 | 2.7708 | 1.3714 | 0.14 | 1e-05 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 33300 | 0 | 32936.7719 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 518.2421 | 64.6154 | 0.000152 | 150556.6802 | Laminar | 144.0833 | 83
0.33333 | 9395.809 | 64 | 57.4716 | 64 | 57.4716 | 58 | 55.1 | #NAME? | #NAME? | 61800 | 322 | 0.37 | 0 | 7 | 44 | 61.6 | 17.6 | 5.1333 | 1.3636 | 0.25 | 0.1 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 61800 | 0 | 60884.8423 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 925.4324 | 64.6154 | 0.000152 | 190114.7099 | Laminar | 266.9333 | 96
0.375 | 9986.5443 | 66 | 58.2351 | 66 | 58.2351 | 58 | 55.1 | #NAME? | #NAME? | 87400 | 342 | 0.41 | 0 | 10 | 44 | 61.4 | 17.4 | 7.25 | 1.3793 | 0.36 | 0.1 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 87400 | 0 | 86283.7432 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 1332.6226 | 64.6154 | 0.000152 | 201923.0769 | Laminar | 377 | 201
0.41667 | 10577.2797 | 68 | 58.9872 | 68 | 58.9872 | 58 | 55.1 | #NAME? | #NAME? | 115300 | 363 | 0.46 | 0 | 13.6 | 44 | 60.9 | 16.9 | 9.5767 | 1.4201 | 0.49 | 0.2 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 115300 | 0 | 114234.6209 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 1813.8474 | 64.6154 | 0.000152 | 214321.8623 | Laminar | 497.9867 | 455
0.45833 | 11332.3042 | 72 | 59.4715 | 73.1 | 60.1 | 58 | 54.3 | #NAME? | #NAME? | 186600 | 389 | 0.51 | 0 | 19.2 | 44 | 63.4 | 19.4 | 15.52 | 1.2371 | 0.7 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 186600 | 0 | 171344.4388 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2591.2106 | 64.6154 | 0.000152 | 229672.7395 | Transition | 807.04 | 649
0.5 | 11059.4316 | 73 | 59.8398 | 73.8 | 60.3 | 58 | 54.2 | #NAME? | #NAME? | 190900 | 379 | 0.49 | 0 | 19.3 | 44 | 63.7 | 19.7 | 15.8421 | 1.2183 | 0.7 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 190900 | 0 | 179162.7922 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2591.2106 | 64.6154 | 0.000152 | 223768.556 | Transition | 823.7883 | 675 | Bin Data Plot | MOA Mix at 0.4% Design Condition
0.54167 | 11328.8354 | 75.9 | 60.8926 | 75.6 | 61 | 58 | 54.3 | #NAME? | #NAME? | 217600 | 388 | 0.51 | 0 | 20.9 | 44 | 64.8 | 20.8 | 18.1133 | 1.1538 | 0.76 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 217600 | 0 | 219009.0467 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2813.3144 | 64.6154 | 0.000152 | 229082.3212 | Transition | 941.8933 | 711
0.58333 | 11598.2393 | 75.9 | 62.2983 | 75.6 | 61.9 | 58 | 55.3 | #NAME? | #NAME? | 223200 | 398 | 0.53 | 0 | 21.4 | 44 | 64.8 | 20.8 | 18.5467 | 1.1538 | 0.78 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 223200 | 0 | 224217.1614 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2887.349 | 64.6154 | 0.000152 | 234986.5047 | Transition | 964.4267 | 774
0.625 | 11294.1483 | 79 | 64.3196 | 77.5 | 63.1 | 58 | 55.9 | #NAME? | #NAME? | 240000 | 387 | 0.5 | 0 | 22 | 44 | 65.8 | 21.8 | 19.9833 | 1.1009 | 0.8 | 0.6 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 240000 | 0 | 256151.2823 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2961.3836 | 64.6154 | 0.000152 | 228491.9028 | Transition | 1039.1333 | 710
0.66667 | 11125.3373 | 80.1 | 64.6868 | 78.2 | 63.4 | 58 | 56 | #NAME? | #NAME? | 245600 | 381 | 0.49 | 0 | 22.2 | 44 | 66.1 | 22.1 | 20.4425 | 1.086 | 0.81 | 0.6 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 245600 | 0 | 265539.55 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2998.4009 | 64.6154 | 0.000152 | 224949.3927 | Transition | 1063.01 | 552
0.70833 | 10541.4363 | 80.1 | 63.7434 | 78.2 | 62.8 | 58 | 55.3 | #NAME? | #NAME? | 232400 | 361 | 0.45 | 0 | 21.1 | 44 | 66 | 22 | 19.3417 | 1.0909 | 0.77 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 232400 | 0 | 251603.0012 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2850.3317 | 64.6154 | 0.000152 | 213141.0256 | Transition | 1005.7667 | 184
0.75 | 9703.1626 | 79 | 63.369 | 77.5 | 62.6 | 58 | 55.3 | #NAME? | #NAME? | 206100 | 333 | 0.39 | 0 | 19.2 | 44 | 65.4 | 21.4 | 17.12 | 1.1215 | 0.7 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 206100 | 0 | 220067.7274 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2591.2106 | 64.6154 | 0.000152 | 196609.3117 | Transition | 890.24 | 87
Notes
| 1 | Because the Greenheck model reports loads as Mbtu, for low latent loads, it may report 0 Btu/hr of latent load even though it shows a slightly lower leaving wetbulb than dry bulb temperature and a slightly higher pressrue drop relative to a dry coil. To overcome this, the modeled total load is used. The latent load is calculated based on the difference between entering and leaving w, with the leaving w being set by the modeled leaving conditions. The sensible load is calculated by subtracting the latent load from the total load.
| 2 | This analysis is based on the selection point on the CDs and the Seattle 0.4% cooling design condition; see psych chart to the right
| 3 | Dry bulb is the middle of temperature of a 5°F by 8 hour bin; Wet bulb is the mean coincident wet bulb for the bin. See psych chart to the right.
| 4 | This is the operating condition for the drybulb bin but at the highest observed wet bulb temperature based on the bin plot in Akton Psych chart to illustrate the impact of a heavier latent load.
| 5 | This is a mixed condition based on the design return condition and the 77°F bin conditions
| 6 | This analysis is based on the selection point on the CDs and the Seattle 2% cooling design condition; see psych chart to the right
| 7 | This is a mixed condition based on 50% outdoor air vs. the apparent design percentage. Its also very close to the mix condition for the 82°F bin.
| 8 | This is a humid MOA condition for the 82°F bin.
| 9 | This is a mixed condition based on the design return condition and the 87°F bin conditions
| 10 | This is a mixed condition based on the design return condition and the 92°F bin conditions
| 11 | This is a mixed condition based on the design return condition and the 97°F bin conditions
| 12 | This is a humid MOA condition for the 82°F bin.
| 13 | This is a humid MOA condition for the 77°F bin.
| 14 | This is a humid MOA condition for the 87°F bin.
| 15 | This is a dry condition for the 57°F bin.
| 16 | This is a dry condition for the 67°F bin.
| 17 | This is a dry condition for the 72°F bin.
| 18 | This is from the hourly weather for Boeing Field on May 21, 2015, the day Ron was looking at AHUs. It got up into the 80's with scattered clouds to mostly cloudy later in the day. The assumptin is that the systems are on 100% outdoor air until 72°F outside, then the MOA associated with the original design with the mixed condition calculated based on the outdoor condition and the projected indoor condition from that condition and a SHR of .91.
MOA Mix at the 2% Design Condition
Blank Condition
| Air Side | [12 empty] | Water Side
| Flow, cfm | Entering tdb, °F | Entering twb, °F |  |  | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr | Latent Btu/hr | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fpm | Pressure Drop, ft.w.c. | Fouling Factor
[9 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
[9 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
MOA Mix at a Humid 82°F Bin Condition
MOA Mix at the 0.4% Design Condition but with 50% MOA
MOA Mix at a Humid 76°F Bin Condition
MOA Mix at a Humid 87°F Bin Condition

## CC Model 2015-09-24
This model was developed using the Greenheck Coil Selection Program. It models CC-16, which is typical of the vast majority of the coils in the facility.
Construction Details
| Finned Length - |  |  |  |  | 70 |  | inches | Tube Material - |  | Copper
| Finned Height - |  |  |  |  | 30 |  | inches | Tube Diameter - |  | 0.625 |  | inch
| Face Area - |  |  |  |  | 14.5833 | 0 | sq.ft. | Tube Wall Thickness - |  | 0.02 |  | inches
| Coils in the Coil Bank - |  |  |  |  | 2 |  |  | Tube interior - |  | Smooth
| Coil Bank Face Area - |  |  |  |  | 29.1667 | 0 | sq.ft. | Connection Hand - |  | Right |  | (Facing with Air Flow Direction)
| Rows - |  |  |  |  | 6 |  |  | Supply Connection Size - |  | 2
| Fins per Inch - |  |  |  |  | 12 |  |  | Return Connection Size - |  | 2
| Fin Material - |  |  |  |  | Aluminum |  |  | Number of Feeds - |  | 15
| Fin Thickness - |  |  |  |  | 0.006 |  |  | Number of Passes - |  | 8
| Fin Type - |  |  |  |  | Sine-wave |  |  | Circuiting - |  | 0.53333 |  | Serpentine
| Casing Material - |  |  |  |  | Galvanized Steel |  |  | Dry Weight - |  | 315 |  | per coil
| Coating - |  |  |  |  | None |  |  | Operating Weight - |  | 418 |  | per coil
| Greenheck File Location - |  | ..\Coil Models | [5 empty] | Approximate number of similar coils - | 52
Design Airflow and Leaving Air Temperature, Different Entering Conditions | [22 empty] | Support
Time | Air Side | [12 empty] | Water Side | [8 empty] | Comments | Entering Humidity Ratio |  | Leaving Humidity Ratio |  | Greenheck Sensible Load, Btu/hr | Greenheck Latent Load, Btu/hr | Calculated Sensible Load, Btu/hr. Note 1 | Calculated Latent Load, Btu/hr. Note 1 | Entering Enthalpy, Btu/lbn (Red Exceeds Design) | Coil SHR | Point on Psych Chart | Tube Reynolds Number |  |  | AHU Reynolds Number at Coil Face |  |  |  | Total Load for 52 Similar Coils | Load on 2015-09-24 | Difference Relative to Trend Data
| Flow, cfm from Generic Day flow profile | Outdoor tdb, °F, Note 18 | Outdoor twb, °F, Note 18 | Entering tdb, °F, Note 18 | Emtering twb, °F, Note 18 | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr (Note 1) | Latent Btu/hr (Note 1) | Total Btu/hr (Model output) | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fps | Pressure Drop, ft.w.c. | Fouling Factor |  | lbWater per lbDryAir | GrainsWater per lbDryAir | lbWater per lbDryAir | GrainsWater per lbDryAir | [7 empty] | Tube Diameter, inches | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right) | AHU Casing Hydraulic Diameter, inches (See Equation, Below, Right) | kinematic viscosity - ft2 per sec | Reynolds Number (See Equation Below, Right)
0.29167 | 7438.2954 | 55 | 51 | 55 | 51 | 58 |  | #NAME? | #NAME? |  | 255 | 0.25 | 0 | 0.001 | 44 | 44.001 | 0.001 | 4.1667e-08 | 24000 | 0 | 0 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? |  | 0 | -24100.077 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 0 | 64.6154 | 0.000152 | 150556.6802 | Laminar | 2.1667e-06 | 83
0.33333 | 9395.809 | 59 | 53 | 59 | 53 | 58 | 52.6 | #NAME? | #NAME? | 9800 | 322 | 0.37 | 0 | 1.3 | 44 | 59 | 15 | 0.8125 | 1.6 | 0.05 | 0 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 9800 | 0 | 10147.4737 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 185.0865 | 64.6154 | 0.000152 | 190114.7099 | Laminar | 42.25 | 96 | 227.2%
0.375 | 9986.5443 | 63 | 58 | 63 | 58 | 58 | 56.1 | #NAME? | #NAME? | 54400 | 342 | 0.41 | 0 | 6.3 | 44 | 61.2 | 17.2 | 4.515 | 1.3953 | 0.23 | 0.1 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 54400 | 0 | 53927.3395 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 851.3978 | 64.6154 | 0.000152 | 201923.0769 | Laminar | 234.78 | 201 | 85.61%
0.41667 | 10577.2797 | 68 | 57 | 68 | 57 | 58 | 53 | #NAME? | #NAME? | 115300 | 363 | 0.46 | 0 | 13.6 | 44 | 60.9 | 16.9 | 9.5767 | 1.4201 | 0.49 | 0.2 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 115300 | 0 | 114234.6209 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 1813.8474 | 64.6154 | 0.000152 | 214321.8623 | Laminar | 497.9867 | 455 | 91.37%
0.45833 | 11332.3042 | 71 | 58 | 72 | 59.2 | 58 | 53.7 | #NAME? | #NAME? | 173700 | 389 | 0.51 | 0 | 18.5 | 44 | 62.7 | 18.7 | 14.4146 | 1.2834 | 0.67 | 0.4 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 173700 | 0 | 159105.5504 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2480.1587 | 64.6154 | 0.000152 | 229672.7395 | Transition | 749.5583 | 649 | 86.58%
0.5 | 11059.4316 | 72 | 58 | 73 | 59.2 | 58 | 53.3 | #NAME? | #NAME? | 180700 | 379 | 0.49 | 0 | 18.7 | 44 | 63.3 | 19.3 | 15.0379 | 1.2435 | 0.68 | 0.4 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 180700 | 0 | 167218.606 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2517.176 | 64.6154 | 0.000152 | 223768.556 | Transition | 781.9717 | 675 | 86.32% | Bin Data Plot | MOA Mix at 0.4% Design Condition
0.54167 | 11328.8354 | 73 | 59 | 73.8 | 59.8 | 58 | 53.6 | #NAME? | #NAME? | 195300 | 388 | 0.51 | 0 | 19.7 | 44 | 63.8 | 19.8 | 16.2525 | 1.2121 | 0.72 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 195300 | 0 | 183527.1341 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2665.2452 | 64.6154 | 0.000152 | 229082.3212 | Transition | 845.13 | 711 | 84.13%
0.58333 | 11598.2393 | 75 | 61 | 75 | 61.1 | 58 | 54.6 | #NAME? | #NAME? | 215700 | 398 | 0.53 | 0 | 21 | 44 | 64.5 | 20.5 | 17.9375 | 1.1707 | 0.76 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 215700 | 0 | 212943.6728 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2813.3144 | 64.6154 | 0.000152 | 234986.5047 | Transition | 932.75 | 774 | 82.98%
0.625 | 11294.1483 | 74 | 61 | 74.4 | 61.1 | 58 | 54.9 | #NAME? | #NAME? | 210700 | 387 | 0.5 | 0 | 20 | 44 | 64.1 | 20.1 | 16.75 | 1.194 | 0.73 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 201700 | 9000 | 195162.8818 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2702.2625 | 64.6154 | 0.000152 | 228491.9028 | Transition | 871 | 710 | 81.52%
0.66667 | 11125.3373 | 73 | 60 | 73.8 | 60.4 | 58 | 54.3 | #NAME? | #NAME? | 192000 | 381 | 0.49 | 0 | 19.4 | 44 | 63.7 | 19.7 | 15.9242 | 1.2183 | 0.71 | 0.5 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 192000 | 0 | 180230.4638 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2628.2279 | 64.6154 | 0.000152 | 224949.3927 | Transition | 828.0567 | 552 | 66.66%
0.70833 | 10541.4363 | 72 | 60 | 73.1 | 60.4 | 58 | 54.6 | #NAME? | #NAME? | 173200 | 361 | 0.45 | 0 | 18 | 44 | 63.2 | 19.2 | 14.4 | 1.25 | 0.65 | 0.4 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 173200 | 0 | 159386.5166 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2406.1241 | 64.6154 | 0.000152 | 213141.0256 | Transition | 748.8 | 184 | 24.57%
0.75 | 9703.1626 | 71 | 60 | 72.5 | 60.4 | 58 | 54.9 | #NAME? | #NAME? | 153400 | 333 | 0.39 | 0 | 16.5 | 44 | 62.5 | 18.5 | 12.7188 | 1.2973 | 0.6 | 0.3 | 0 |  | #NAME? | #NAME? | #NAME? | #NAME? | 153400 | 0 | 136232.4027 | #NAME? | #NAME? | #NAME? |  | 0.625 | 1.407e-05 | 2221.0377 | 64.6154 | 0.000152 | 196609.3117 | Transition | 661.375 | 87 | 13.15%
Notes
| 1 | Because the Greenheck model reports loads as Mbtu, for low latent loads, it may report 0 Btu/hr of latent load even though it shows a slightly lower leaving wetbulb than dry bulb temperature and a slightly higher pressrue drop relative to a dry coil. To overcome this, the modeled total load is used. The latent load is calculated based on the difference between entering and leaving w, with the leaving w being set by the modeled leaving conditions. The sensible load is calculated by subtracting the latent load from the total load.
| 2 | This analysis is based on the selection point on the CDs and the Seattle 0.4% cooling design condition; see psych chart to the right
| 3 | Dry bulb is the middle of temperature of a 5°F by 8 hour bin; Wet bulb is the mean coincident wet bulb for the bin. See psych chart to the right.
| 4 | This is the operating condition for the drybulb bin but at the highest observed wet bulb temperature based on the bin plot in Akton Psych chart to illustrate the impact of a heavier latent load.
| 5 | This is a mixed condition based on the design return condition and the 77°F bin conditions
| 6 | This analysis is based on the selection point on the CDs and the Seattle 2% cooling design condition; see psych chart to the right
| 7 | This is a mixed condition based on 50% outdoor air vs. the apparent design percentage. Its also very close to the mix condition for the 82°F bin.
| 8 | This is a humid MOA condition for the 82°F bin.
| 9 | This is a mixed condition based on the design return condition and the 87°F bin conditions
| 10 | This is a mixed condition based on the design return condition and the 92°F bin conditions
| 11 | This is a mixed condition based on the design return condition and the 97°F bin conditions
| 12 | This is a humid MOA condition for the 82°F bin.
| 13 | This is a humid MOA condition for the 77°F bin.
| 14 | This is a humid MOA condition for the 87°F bin.
| 15 | This is a dry condition for the 57°F bin.
| 16 | This is a dry condition for the 67°F bin.
| 17 | This is a dry condition for the 72°F bin.
| 18 | This is from the hourly weather for Boeing Field on May 21, 2015, the day Ron was looking at AHUs. It got up into the 80's with scattered clouds to mostly cloudy later in the day. The assumptin is that the systems are on 100% outdoor air until 72°F outside, then the MOA associated with the original design with the mixed condition calculated based on the outdoor condition and the projected indoor condition from that condition and a SHR of .91.
MOA Mix at the 2% Design Condition
Blank Condition
| Air Side | [12 empty] | Water Side
| Flow, cfm | Entering tdb, °F | Entering twb, °F |  |  | Leaving tdb, °F | Leaving twb, °F | Sensible Btu/hr | Latent Btu/hr | Total Btu/hr | Face Velocity, fpm | Pressure Drop, in.w.c. | Fouling Factor | Flow, gpm | Entering Temperature, °F | Leaving Temperature, °F | Fluid ∆t | Tons | gpm/ton | Tube Velocity, fpm | Pressure Drop, ft.w.c. | Fouling Factor
[9 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
[9 empty] | 0 | [7 empty] | 0 | 0 | #DIV/0!
MOA Mix at a Humid 82°F Bin Condition
MOA Mix at the 0.4% Design Condition but with 50% MOA
MOA Mix at a Humid 76°F Bin Condition
MOA Mix at a Humid 87°F Bin Condition

## Flow Profile Generator
Based on the flow provile from the "day in a life of a VAV system" which is based on the logged data from Kaiser Building | [11 empty] | ..\..\..\FDE Tools\VAV System Day\VAV System Day v7.xlsx
Modified where highlighted to reflect scheduled operation
|  | Peak flow for the Kaiser Building system - | 200000
|  | Peak flow for the modeled system - | 14000
Static at design flow -
|  | Motor hp - |  | per motor
Number of motors -
Total hp -
Minimum static pressure -
|  | Assumed belt efficiency - | 98% | Industry best practice for well adjusted belts
|  | Assumed VFD efficiency - | 94.3% | Full load 50 hp, current technology Safetronics VFD efficiency (conservative for 10 hp and variable profile)
Orange cells were manually set to 0 cfm to reflect the building being shut down for those hours
Monday through Friday Energy
Time | Time, even hours | Flow |  | Modeled System
|  | cfm | % of peak | Flow, cfm | Static, in.w.c. | Fan efficiency | BhpFan = (Flowcfm x Staticin.w.c.)/(6,356 x EfficiencyFan) | Motor % loaded | Motor Efficiency | Energy Into VFD (Includes belt and VFD losses) |  | Motor Losses |  | Time interval, hours | Fan Energy kWh | Motor Losses, Btu
[10 empty] | hp | kW | kW | Btu/hr
2009-03-01 23:53 | 2009-03-02 | 18945.8115 | 9.473% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 00:53 | 2009-03-02 01:00 | 18945.8115 | 9.473% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 01:53 | 2009-03-02 02:00 | 32572.9208 | 16.29% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 02:53 | 2009-03-02 03:00 | 37908.1406 | 18.95% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 03:53 | 2009-03-02 04:00 | 44812.5427 | 22.41% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 04:53 | 2009-03-02 05:00 | 51716.9448 | 25.86% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 05:53 | 2009-03-02 06:00 | 78989.1536 | 39.49% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 06:53 | 2009-03-02 07:00 | 106261.3625 | 53.13% | 7438.2954 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 07:53 | 2009-03-02 08:00 | 134225.8427 | 67.11% | 9395.809 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 08:53 | 2009-03-02 09:00 | 142664.9193 | 71.33% | 9986.5443 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 09:53 | 2009-03-02 10:00 | 151103.9958 | 75.55% | 10577.2797 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 10:53 | 2009-03-02 11:00 | 161890.0594 | 80.95% | 11332.3042 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 11:53 | 2009-03-02 12:00 | 157991.8802 | 79% | 11059.4316 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 12:53 | 2009-03-02 13:00 | 161840.5063 | 80.92% | 11328.8354 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 13:53 | 2009-03-02 14:00 | 165689.1323 | 82.84% | 11598.2393 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 14:53 | 2009-03-02 15:00 | 161344.975 | 80.67% | 11294.1483 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 15:53 | 2009-03-02 16:00 | 158933.3896 | 79.47% | 11125.3373 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 16:53 | 2009-03-02 17:00 | 150591.9469 | 75.3% | 10541.4363 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 17:53 | 2009-03-02 18:00 | 138616.6083 | 69.31% | 9703.1626 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 18:53 | 2009-03-02 19:00 | 113773.975 | 56.89% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 19:53 | 2009-03-02 20:00 | 101666.4948 | 50.83% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 20:53 | 2009-03-02 21:00 | 83810.8521 | 41.91% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 21:53 | 2009-03-02 22:00 | 35711.2854 | 17.86% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 22:53 | 2009-03-02 23:00 | 28493.0469 | 14.25% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 23:53 | 2009-03-03 | 21274.8083 | 10.64% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-03 00:53 | 2009-03-03 01:00 | 18945.8115 | 9.473% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
[14 empty] | TOTALS | 0 | 0
Saturday (assume no operation on Sunday)
Time | Time, even hours | Flow |  | AC2 System
|  | cfm | % of peak | Flow, cfm | Static, in.w.c. | Fan efficiency | BhpFan = (Flowcfm x Staticin.w.c.)/(6,356 x EfficiencyFan) | Motor % loaded | Motor Efficiency | Energy Into VFD (Includes belt and VFD losses) |  | Motor Losses |  | Time interval, hours | Fan Energy kWh | Motor Losses, Btu
[10 empty] | hp | kW | kW | Btu/hr
2009-03-01 23:53 | 2009-03-02 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 00:53 | 2009-03-02 01:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 01:53 | 2009-03-02 02:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 02:53 | 2009-03-02 03:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 03:53 | 2009-03-02 04:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 04:53 | 2009-03-02 05:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 05:53 | 2009-03-02 06:00 | 78989.1536 | 39.49% | 5529.2408 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 06:53 | 2009-03-02 07:00 | 106261.3625 | 53.13% | 7438.2954 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 07:53 | 2009-03-02 08:00 | 134225.8427 | 67.11% | 9395.809 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 08:53 | 2009-03-02 09:00 | 142664.9193 | 71.33% | 9986.5443 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 09:53 | 2009-03-02 10:00 | 151103.9958 | 75.55% | 10577.2797 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 10:53 | 2009-03-02 11:00 | 161890.0594 | 80.95% | 11332.3042 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 11:53 | 2009-03-02 12:00 | 157991.8802 | 79% | 11059.4316 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 12:53 | 2009-03-02 13:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 13:53 | 2009-03-02 14:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 14:53 | 2009-03-02 15:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 15:53 | 2009-03-02 16:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 16:53 | 2009-03-02 17:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 17:53 | 2009-03-02 18:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 18:53 | 2009-03-02 19:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 19:53 | 2009-03-02 20:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 20:53 | 2009-03-02 21:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 21:53 | 2009-03-02 22:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 22:53 | 2009-03-02 23:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-02 23:53 | 2009-03-03 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
2009-03-03 00:53 | 2009-03-03 01:00 | 0 | 0% | 0 | 0 | 70.68% | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 1 | 0 | 0
[14 empty] | TOTALS | 0 | 0
AHU2 Design Flow | cfm
2009-03-02 | 14000
2009-03-03 | 14000
Formulas:
Time, even hours = [Time]+(7*(1/(24*60)))

## 2015-05-21 Boeing Field Weather
TimePDT | TemperatureF | Calculated Wet Bulb | Dew PointF | Humidity | Sea Level PressureIn | VisibilityMPH | Wind Direction | Wind SpeedMPH | Gust SpeedMPH | PrecipitationIn | Events | Conditions | WindDirDegrees | DateUTC
12:53 AM | 63 | #NAME? | 51.1 | 65 | 29.87 | 10 | Calm | Calm | - | N/A |  | Clear | 0 | 2015-05-21 07:53
1:53 AM | 62.1 | #NAME? | 51.1 | 67 | 29.87 | 10 | Calm | Calm | - | N/A |  | Clear | 0 | 2015-05-21 08:53
2:53 AM | 60.1 | #NAME? | 51.1 | 72 | 29.87 | 10 | Calm | Calm | - | N/A |  | Clear | 0 | 2015-05-21 09:53
3:53 AM | 57.9 | #NAME? | 50 | 75 | 29.88 | 10 | Calm | Calm | - | N/A |  | Clear | 0 | 2015-05-21 10:53
4:53 AM | 59 | #NAME? | 51.1 | 75 | 29.88 | 10 | Calm | Calm | - | N/A |  | Clear | 0 | 2015-05-21 11:53
5:53 AM | 59 | #NAME? | 50 | 72 | 29.87 | 10 | Calm | Calm | - | N/A |  | Scattered Clouds | 0 | 2015-05-21 12:53
6:53 AM | 60.1 | #NAME? | 51.1 | 72 | 29.88 | 10 | Calm | Calm | - | N/A |  | Scattered Clouds | 0 | 2015-05-21 13:53
7:53 AM | 62.1 | #NAME? | 52 | 70 | 29.88 | 10 | Calm | Calm | - | N/A |  | Mostly Cloudy | 0 | 2015-05-21 14:53
8:53 AM | 64 | #NAME? | 53.1 | 67 | 29.88 | 10 | NW | 3.5 | - | N/A |  | Scattered Clouds | 310 | 2015-05-21 15:53
9:53 AM | 66 | #NAME? | 53.1 | 63 | 29.87 | 10 | Variable | 3.5 | - | N/A |  | Scattered Clouds | 0 | 2015-05-21 16:53
10:53 AM | 68 | #NAME? | 53.1 | 59 | 29.87 | 10 | Variable | 4.6 | - | N/A |  | Scattered Clouds | 0 | 2015-05-21 17:53
11:53 AM | 72 | #NAME? | 51.1 | 48 | 29.87 | 10 | WNW | 4.6 | - | N/A |  | Mostly Cloudy | 300 | 2015-05-21 18:53
12:53 PM | 73 | #NAME? | 51.1 | 46 | 29.86 | 10 | Variable | 5.8 | - | N/A |  | Mostly Cloudy | 0 | 2015-05-21 19:53
1:53 PM | 75.9 | #NAME? | 51.1 | 42 | 29.84 | 10 | NNW | 6.9 | - | N/A |  | Mostly Cloudy | 330 | 2015-05-21 20:53
2:53 PM | 75.9 | #NAME? | 54 | 46 | 29.82 | 10 | Calm | Calm | - | N/A |  | Mostly Cloudy | 0 | 2015-05-21 21:53
3:53 PM | 79 | #NAME? | 55.9 | 45 | 29.82 | 10 | Calm | Calm | - | N/A |  | Mostly Cloudy | 0 | 2015-05-21 22:53
4:53 PM | 80.1 | #NAME? | 55.9 | 43 | 29.82 | 10 | SSW | 5.8 | - | N/A |  | Mostly Cloudy | 210 | 2015-05-21 23:53
5:53 PM | 80.1 | #NAME? | 54 | 40 | 29.81 | 10 | Variable | 3.5 | - | N/A |  | Mostly Cloudy | 0 | 2015-05-22 00:53
6:53 PM | 79 | #NAME? | 54 | 42 | 29.81 | 10 | Variable | 5.8 | - | N/A |  | Mostly Cloudy | 0 | 2015-05-22 01:53
7:53 PM | 77 | #NAME? | 53.1 | 43 | 29.81 | 10 | NW | 4.6 | - | N/A |  | Mostly Cloudy | 310 | 2015-05-22 02:53
8:53 PM | 75 | #NAME? | 52 | 44 | 29.82 | 10 | Calm | Calm | - | N/A |  | Scattered Clouds | 0 | 2015-05-22 03:53
9:53 PM | 72 | #NAME? | 51.1 | 48 | 29.84 | 10 | Variable | 3.5 | - | N/A |  | Clear | 0 | 2015-05-22 04:53
10:53 PM | 68 | #NAME? | 51.1 | 55 | 29.86 | 10 | NNW | 4.6 | - | N/A |  | Clear | 330 | 2015-05-22 05:53
11:53 PM | 64 | #NAME? | 53.1 | 67 | 29.88 | 10 | WSW | 6.9 | - | N/A |  | Clear | 240 | 2015-05-22 06:53

## OA Conditions for Min no HG Ld
Assumptions
1 | We need about 30% load to keep from using hot gas bypass, based on the performance curve from the Smardt water cooled chiller cataloge and an assumption that part of the reason the kW/to starts to go back up around that point is that hot gas is being used.
2 | The load on the central plant is approximately equal to 50 coils similar to the one that I have modeled
3 | Nominal number of similar AHUs with integrated economizer cycles = 50
Design Air Flow and LAT Condition Analysis - Enthalpy Basis - All AHUs Running
| Small chiller full load tonnage - | 300 | tons
| 30% load point - | 90 | tons
| Design condition AHU flow rate - | 14000 | cfm
| Design leaving air temperature - | 52 | °F
| Enthalpy change to load a chiller with AHUs on 100% OA in an integrated economizer cycle - | 0.34286 | Btu/lb
| OA Enthalpy on a typical day when the OAT is the same as the design LAT - | 19.6 | Btu/lb
| OA enthalpy that will generate a 90 ton load on a typical day - | 19.9429 | Btu/lb
| Typical OAT where the load on 100% OA will be 90 tons - | 53.6 | °F (from psych chart)
Typcial Operating Air Flow and LAT Condition Analysis - Enthalpy Basis - All AHUs Running
| Small chiller full load tonnage - | 300 | tons
| 30% load point - | 90 | tons
| Typical AHU operating condition flow rate - | 10000 | cfm
| Typical leaving air temperature - | 60 | °F
| Enthalpy change to load a chiller with AHUs on 10)% OA in an integrated economizer cycle - | 0.48 | Btu/lb
| OA Enthalpy on a typical day when the OAT is the same as the design LAT - | 22.7 | Btu/lb
| OA enthalpy that will generate a 90 ton load on a typical day - | 23.18 | Btu/lb
| Typical OAT where the load on 100% OA will be 90 tons - | 61.3 | °F (from psych chart)
Design Air Flow and LAT Condition Analysis - Sensible Basis - All AHUs Running
| Small chiller full load tonnage - | 300 | tons
| 30% load point - | 90 | tons
| Design condition AHU flow rate - | 14000 | cfm
| Design leaving air temperature - | 52 | °F
| Cooling coil ∆t with no latent load to load a chiller with AHUs on 100% OA in an integrated economizer cycle - | 1.4286 | °F
| OAT that will generate a 90 ton load on a typical day - | 53.4286 | °F
Typcial Operating Air Flow and LAT Condition Analysis - Sensible Basis - All AHUs Running
| Small chiller full load tonnage - | 300 | tons
| 30% load point - | 90 | tons
| Typical AHU operating condition flow rate - | 10000 | cfm
| Typical leaving air temperature - | 60 | °F
| Cooling coil ∆t with no latent load to load a chiller with AHUs on 100% OA in an integrated economizer cycle - | 2 | °F
| OAT that will generate a 90 ton load on a typical day - | 62 | °F
Design Air Flow and LAT Condition Analysis - Sensible Basis - 5 AHUs Running
| Small chiller full load tonnage - | 300 | tons
| 30% load point - | 90 | tons
| Design condition AHU flow rate - | 14000 | cfm
| Design leaving air temperature - | 52 | °F
| Cooling coil ∆t with no latent load to load a chiller with AHUs on 100% OA in an integrated economizer cycle - | 14.2857 | °F
| OAT that will generate a 90 ton load on a typical day - | 66.2857 | °F
Typcial Operating Air Flow and LAT Condition Analysis - Sensible Basis - 5 AHUs Running
| Small chiller full load tonnage - | 300 | tons
| 30% load point - | 90 | tons
| Typical AHU operating condition flow rate - | 10000 | cfm
| Typical leaving air temperature - | 60 | °F
| Cooling coil ∆t with no latent load to load a chiller with AHUs on 100% OA in an integrated economizer cycle - | 20 | °F
| OAT that will generate a 90 ton load on a typical day - | 80 | °F