## Blank Damper Schedule
Control Damper Schedule
Damper | Unit or | Nominal Size |  | Blade Characteristics |  | Damper Performance Data | [9 empty] | Actuator Data | [7 empty] | Comments
Number | System Served | Height | Width | Blade | Blade | Design | Leakage |  | Sizing |  |  |  |  | Type | Manufacturer/ | Action | Failure | Type | Power | Range | Quantity | Location | Manufacturer/
|  | inches | inches | Orientation (Note 1) | Design (Note 2) | Flow Rate cfm | Rate cfm per sq.ft. of damper | Pressure difference in.w.c. | Target ΔP in.w.c. (Note 3) | Target Velocity fpm | Target alpha (Note 5) | Basis (Note 5) |  | (Note 6) | Model (Note 4) |  | Position (Note 7) |  |  | (Note 8) |  | (Facing with the air flow) | Model (Note 4)
[12 empty] | System | ΔP in.w.c.
Notes
1, Vertical or horizontal. Vertical blades to have thrust bearings.
2. Flat plate, airfoil, or curtain, parallel or opposed blade where applicable
3. Wide open, including velocity conversion losses associated with any blank-off plates
4. Basis of scheduled selection for the scheduled valve. Equivalent makes and models as allowed by the specification will also be acceptable.
5. Based on the damper performance curves published in ASHRAE and the indicated system static pressure.
6. Modulating control, two position control, smoke, fire, cobination smoke/fire, backdraft, etc.
7. This is the position the damper will go to upon loss of control power.
8. This is the range of input signal that will cause the damper to go from its fully closed position to its fully open position.

## Sample calcs
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | DATE?
Project Name: | NAME?
Project Number: | NUMBER?
Engineer: | ENGINEER?
Assumptions
1 | See the graph tabs for damper characteristic curves.
2 | Unit capacity - | 10000 | cfm
3 | System static pressure rating - | 3.5 | in.w.c.
4 | Economizer damper design - | Parallel | (to allow directional control to promote mixing)
5 | Economizer target alpha maximum - | 10 |  | Flow at 50% damper stroke - | 76%
6 | Economizer target alpha minimum - | 5 |  | Flow at 50% damper stroke - | 60%
7 | Minimum outdoor air quantity - | 3000 | cfm
8 | Flow for sizing economizer and relief dampers - | 7000 | cfm
9 | Damper make and model used for sizing - | Ruskin | CD 35
10 | Maximum building pressure for relief damper sizing - | 0.1 | in.w.c.
11 | Relief damper design - | Opposed | (to allow better alpha at lower pressrue drop)
12 | Economizer target alpha maximum - | 20 |  | Flow at 50% damper stroke - | 62%
13 | Economizer target alpha minimum - | 10 |  | Flow at 50% damper stroke - | 48%
First pass, Economizer damper sizing (return and outdoor air)
| Pressure drop at maximum target alpha - | 0.35 | in.w.c., including blank-off plates and associated velocity conversions
| Pressure drop at minimum target alpha - | 0.7 | in.w.c., including blank-off plates and associated velocity conversions
| Damper height - | 12 | inches
| Damper width - | 42 | inches
| Velocity - | 2000 | fpm
| Damper loss at design velocity - | 0.13 | in.w.c. (From ASHRAE fitting data base)
| Entry loss - | 0.1 | in.w.c. (From ASHRAE fitting data base)
| Exit loss - | 0.25 | in.w.c. (From ASHRAE fitting data base)
| Total loss - | 0.48 | in.w.c.
Minimum outdoor air damper sizing
Size for the same pressure drop as the economizer dampers at the design flow rate
| Target velocity - | 2000 | fpm
| Target damper loss at design velocity - | 0.13 | in.w.c. (From damper curves)
| Design flow rate - | 3000 | cfm
| Damper height - | 6 | inches (one blade)
| Damper width - | 36 | inches
| Actual velocity based on size and flow - | 2000 | fpm
Relief damper sizing
| Pressure drop at maximum target alpha - | 0.005 | in.w.c., including blank-off plates and associated velocity conversions
| Pressure drop at minimum target alpha - | 0.01 | in.w.c., including blank-off plates and associated velocity conversions
| Damper height - | 48 | inches
| Damper width - | 48 | inches
| Velocity - | 437.5 | fpm
| Damper loss at design velocity - | 0.01 | in.w.c. (From ASHRAE fitting data base)
| Entry loss - | 0.01 | in.w.c. (From ASHRAE fitting data base)
| Exit loss - | 0.01 | in.w.c. (From ASHRAE fitting data base)
| Total loss - | 0.03 | in.w.c.
Conclusion:
The selection at this velocity is with-in the target loss range. Use this size
Conclusion:
Entry and exit losses are rounded up by the ASHRAE data base and are actually less than shown here. Thus the over-all damper loss will be slightly less. A slightly higher loss than the minimum alpha pressure drop will improve linearity and provides some margin since the building will leak and the net relief flow through the damper will probably be less than the design value.

## Sample ASHRAE Fitting Info
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | DATE?
Project Name: | NAME?
Project Number: | NUMBER?
Engineer: | ENGINEER?
Economizer Dampers
Relief dampers

## Parallel Blade Graph Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | DATE?
Project Name: | NAME?
Project Number: | NUMBER?
Engineer: | ENGINEER?
Assumptions
1 | Developed from data in the 2001 ASHRAE Handbook of Fundamentals, Figure 14
| Percent flow at different alpha | [8 empty] | Percent stroke
Percent stroke | 1 | 2 | 3 | 5 | 10 | 20 | 50 | 100 | 200
0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
10% | 5% | 6.5% | 7% | 9.75% | 12% | 15.5% | 22% | 28.5% | 37.5% | 10%
20% | 11.5% | 14% | 16% | 20.5% | 28.5% | 34.5% | 51.5% | 65% | 76.5% | 20%
30% | 20% | 24.5% | 28% | 34% | 44.5% | 55.5% | 73.75% | 83.5% | 90% | 30%
40% | 30.5% | 35% | 40% | 47.5% | 58.75% | 71.5% | 84.75% | 92% | 95% | 40%
50% | 41% | 48% | 53% | 61% | 72% | 81.75% | 91.25% | 95.5% | 97.5% | 50%
60% | 52% | 59.5% | 65% | 72% | 82% | 88.25% | 95% | 97.5% | 99.25% | 60%
70% | 64% | 70% | 75% | 81.5% | 88.25% | 93.25% | 97.5% | 99% | 100% | 70%
80% | 74.5% | 81% | 84% | 88.75% | 93.25% | 97.5% | 99.5% | 100% | 100% | 80%
90% | 87.5% | 90.5% | 92% | 95% | 97.5% | 100% | 100% | 100% | 100% | 90%
100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## Opposed Blade Graph Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | DATE?
Project Name: | NAME?
Project Number: | NUMBER?
Engineer: | ENGINEER?
Assumptions
1 | Developed from data in the 2001 ASHRAE Handbook of Fundamentals, Figure 15
| Percent flow at different alpha | [7 empty] | Percent stroke
Percent stroke | 1 | 3 | 5 | 10 | 20 | 50 | 100 | 200
0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
10% | 2.5% | 3.5% | 4% | 6.5% | 8.5% | 12% | 17.5% | 22.5% | 10%
20% | 5.5% | 8.5% | 10.05% | 14.5% | 18.5% | 27.5% | 36% | 47.5% | 20%
30% | 10% | 14.7% | 18% | 23% | 31.5% | 44% | 58% | 69.75% | 30%
40% | 15.5% | 22% | 27% | 35% | 45% | 62% | 74.5% | 85.75% | 40%
50% | 22.5% | 32% | 38% | 48% | 61% | 76% | 85.5% | 92.5% | 50%
60% | 32.75% | 44.5% | 51.5% | 62.5% | 75% | 86.75% | 92% | 96.5% | 60%
70% | 46.75% | 57.5% | 66% | 76% | 85% | 92.5% | 95.25% | 98% | 70%
80% | 61.5% | 72.5% | 79% | 87% | 92% | 97% | 98% | 99% | 80%
90% | 78.5% | 88% | 91% | 94.5% | 97.5% | 99% | 100% | 100% | 90%
100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%