## Data
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: | 2014-08-16 08:29
Project Name: | Construct Your Own Psych Chart
Project Number:
Engineer: | David
Assumptions
1 |  | Grains per pound = | 7000
2 |  | Barometric pressure = | 14.696 | psia
3 |  | Volume of sample = | 1 | ft.3
4 | Dalton's Law
5 | Assessing humidity ratio at saturation
6 | Assessing relative humidity or Φ
7 | Assessing Enthalpy and Internal Energy
8
7 | Assessing wet bulb temperature.
Saturation Curve
Notes | Dry Bulb Temperature Axis Values, tdb, °F | Saturated Humidity Ratio, ws
|  | Total pressure, psia (Given; sea level atmospheric pressure) | Vapor pressure, ps, psia (from steam table) | Air pressure. Psia | Gas Constants |  | ws (From the equation for ws)
[5 empty] | Air, ft./°F | Water, ft./°F | lbwater/lbdryair | grains/lb
Not plotted but used for refernce subsequently | 32.1 | 14.696 | 0.089007 | 14.607 | 53.3 | 85.8 | 0.0037853 | 26.4973
| 35 | 14.696 | 0.09998 | 14.596 | 53.3 | 85.8 | 0.0042552 | 29.7863
| 40 | 14.696 | 0.12173 | 14.5743 | 53.3 | 85.8 | 0.0051886 | 36.3202
| 45 | 14.696 | 0.14757 | 14.5484 | 53.3 | 85.8 | 0.0063012 | 44.1083
| 50 | 14.696 | 0.17814 | 14.5179 | 53.3 | 85.8 | 0.0076225 | 53.3577
| 55 | 14.696 | 0.21414 | 14.4819 | 53.3 | 85.8 | 0.0091857 | 64.3001
| 60 | 14.696 | 0.2564 | 14.4396 | 53.3 | 85.8 | 0.011031 | 77.2148
| 65 | 14.696 | 0.3058 | 14.3902 | 53.3 | 85.8 | 0.013201 | 92.4078
| 70 | 14.696 | 0.36336 | 14.3326 | 53.3 | 85.8 | 0.015749 | 110.2425
| 75 | 14.696 | 0.43017 | 14.2658 | 53.3 | 85.8 | 0.018732 | 131.1237
| 80 | 14.696 | 0.50747 | 14.1885 | 53.3 | 85.8 | 0.022218 | 155.5288
| 85 | 14.696 | 0.5966 | 14.0994 | 53.3 | 85.8 | 0.026286 | 184.0012
| 90 | 14.696 | 0.69904 | 13.997 | 53.3 | 85.8 | 0.031025 | 217.1732
| 95 | 14.696 | 0.81642 | 13.8796 | 53.3 | 85.8 | 0.036541 | 255.7851
| 100 | 14.696 | 0.95051 | 13.7455 | 53.3 | 85.8 | 0.042957 | 300.7007
Dew Point Temperature Axis Values Corresponding to w Axis Values,tdp
| ws axis values |  | Gas Constants |  | Pressure, psia | Dew Point, tdp, °F, from steam table based on ps for ws
| lbwater/lbdryair | grains/lb | Air, ft./°F | Water, ft./°F
[6 empty] | ps, psia | tdp, °F
| 0.005 | 35 | 53.3 | 85.8 | 14.696 | 0.11734 | 39.05
| 0.01 | 70 | 53.3 | 85.8 | 14.696 | 0.23282 | 57.3
| 0.015 | 105 | 53.3 | 85.8 | 14.696 | 0.34649 | 68.61
| 0.02 | 140 | 53.3 | 85.8 | 14.696 | 0.45838 | 76.9
| 0.025 | 175 | 53.3 | 85.8 | 14.696 | 0.56854 | 83.5
| 0.03 | 210 | 53.3 | 85.8 | 14.696 | 0.67701 | 88.98
| 0.035 | 245 | 53.3 | 85.8 | 14.696 | 0.78383 | 93.67
| 0.04 | 280 | 53.3 | 85.8 | 14.696 | 0.88903 | 97.78
| 0.045 | 315 | 53.3 | 85.8 | 14.696 | 0.99266 | 101.44
| 0.05 | 350 | 53.3 | 85.8 | 14.696 | 1.0947 | 104.73
Constant Dew Point Lines at Values Corresponding to Major Dry Bulb Gradutrations at Saturation Line,tdp
| Gas Constants |  | Dry Bulb Temperature, tdb, °F | Pressure, psia | Dew Point, tdp, °F, from steam table based on ps for ws
| Air, ft./°F | Water, ft./°F |  |  | Constant ws at ts, lbwater/lbdryair | ps, psia | tdp, °F | Lable
| 53.3 | 85.8 | 35 | 14.696 | 0.0042552 | 0.09998 | 35 | Dew Point = 35 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.0042552
| 53.3 | 85.8 | 40 | 14.696 | 0.0051886 | 0.12173 | 39.99 | Dew Point = 40 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.0051886
| 53.3 | 85.8 | 45 | 14.696 | 0.0063012 | 0.14757 | 45 | Dew Point = 45 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.0063012
| 53.3 | 85.8 | 50 | 14.696 | 0.0076225 | 0.17814 | 50 | Dew Point = 50 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.0076225
| 53.3 | 85.8 | 55 | 14.696 | 0.0091857 | 0.21414 | 55 | Dew Point = 55 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.0091857
| 53.3 | 85.8 | 60 | 14.696 | 0.011031 | 0.2564 | 60 | Dew Point = 60 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.011031
| 53.3 | 85.8 | 65 | 14.696 | 0.013201 | 0.3058 | 65 | Dew Point = 65 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.013201
| 53.3 | 85.8 | 70 | 14.696 | 0.015749 | 0.36336 | 70 | Dew Point = 70 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.015749
| 53.3 | 85.8 | 75 | 14.696 | 0.018732 | 0.43017 | 75 | Dew Point = 75 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.018732
| 53.3 | 85.8 | 80 | 14.696 | 0.022218 | 0.50747 | 80 | Dew Point = 80 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.022218
| 53.3 | 85.8 | 85 | 14.696 | 0.026286 | 0.5966 | 85 | Dew Point = 85 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.026286
| 53.3 | 85.8 | 90 | 14.696 | 0.031025 | 0.69904 | 90 | Dew Point = 90 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.031025
| 53.3 | 85.8 | 95 | 14.696 | 0.036541 | 0.81642 | 95 | Dew Point = 95 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.036541
| 53.3 | 85.8 | 100 | 14.696 | 0.042957 | 0.95051 | 99.99 | Dew Point = 100 °F
| 53.3 | 85.8 | 105 | 14.696 | 0.042957
Constant Relative Humidity Lines; % RH or Φ
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 90% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 90% | 14.5743 | 0.10956 | 0.0046658
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 90% | 14.5179 | 0.16033 | 0.0068519
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 90% | 14.4396 | 0.23076 | 0.00991
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 90% | 14.3326 | 0.32702 | 0.014138
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 90% | 14.1885 | 0.45672 | 0.019925
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 90% | 13.997 | 0.62914 | 0.027784
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 90% | 13.7455 | 0.85546 | 0.038396
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 80% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 80% | 14.5743 | 0.097384 | 0.004144
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 80% | 14.5179 | 0.14251 | 0.0060831
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 80% | 14.4396 | 0.20512 | 0.0087933
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 80% | 14.3326 | 0.29069 | 0.012536
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 80% | 14.1885 | 0.40598 | 0.017648
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 80% | 13.997 | 0.55923 | 0.024574
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 80% | 13.7455 | 0.76041 | 0.033897
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 70% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 70% | 14.5743 | 0.085211 | 0.0036229
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 70% | 14.5179 | 0.1247 | 0.0053162
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 70% | 14.4396 | 0.17948 | 0.0076806
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 70% | 14.3326 | 0.25435 | 0.010941
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 70% | 14.1885 | 0.35523 | 0.015388
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 70% | 13.997 | 0.48933 | 0.021397
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 70% | 13.7455 | 0.66536 | 0.029459
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 60% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 60% | 14.5743 | 0.073038 | 0.0031028
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 60% | 14.5179 | 0.10688 | 0.0045512
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 60% | 14.4396 | 0.15384 | 0.0065717
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 60% | 14.3326 | 0.21802 | 0.0093545
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 60% | 14.1885 | 0.30448 | 0.013143
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 60% | 13.997 | 0.41942 | 0.01825
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 60% | 13.7455 | 0.57031 | 0.025081
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 50% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 50% | 14.5743 | 0.060865 | 0.0025835
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 50% | 14.5179 | 0.08907 | 0.003788
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 50% | 14.4396 | 0.1282 | 0.0054668
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 50% | 14.3326 | 0.18168 | 0.0077759
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 50% | 14.1885 | 0.25373 | 0.010914
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 50% | 13.997 | 0.34952 | 0.015134
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 50% | 13.7455 | 0.47525 | 0.020761
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 40% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 40% | 14.5743 | 0.048692 | 0.0020651
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 40% | 14.5179 | 0.071256 | 0.0030267
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 40% | 14.4396 | 0.10256 | 0.0043658
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 40% | 14.3326 | 0.14534 | 0.0062052
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 40% | 14.1885 | 0.20299 | 0.0087006
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 40% | 13.997 | 0.27962 | 0.012049
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 40% | 13.7455 | 0.3802 | 0.016498
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 30% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 30% | 14.5743 | 0.036519 | 0.0015475
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 30% | 14.5179 | 0.053442 | 0.0022673
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 30% | 14.4396 | 0.07692 | 0.0032686
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 30% | 14.3326 | 0.10901 | 0.0046423
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 30% | 14.1885 | 0.15224 | 0.0065027
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 30% | 13.997 | 0.20971 | 0.008993
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 30% | 13.7455 | 0.28515 | 0.012292
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 20% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 20% | 14.5743 | 0.024346 | 0.0010308
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 20% | 14.5179 | 0.035628 | 0.0015097
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 20% | 14.4396 | 0.05128 | 0.0021752
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 20% | 14.3326 | 0.072672 | 0.0030872
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 20% | 14.1885 | 0.10149 | 0.0043201
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 20% | 13.997 | 0.13981 | 0.0059666
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 20% | 13.7455 | 0.1901 | 0.0081411
| Dry Bulb Temperature Axis Values, tdb, °F | Total pressure, psia (Given) | Saturation pressure, ps, psia (from steam table) | Gas Constants |  | 10% RH
|  |  |  | Air, ft./°F | Water, ft./°F | % RH | Air pressure. psia | pH, psia | wH, lbwatervapor/lbdryair
| 40 | 14.696 | 0.12173 | 53.3 | 85.8 | 10% | 14.5743 | 0.012173 | 0.00051499
| 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 10% | 14.5179 | 0.017814 | 0.00075393
| 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 10% | 14.4396 | 0.02564 | 0.0010857
| 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 10% | 14.3326 | 0.036336 | 0.0015398
| 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 10% | 14.1885 | 0.050747 | 0.0021526
| 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 10% | 13.997 | 0.069904 | 0.002969
| 100 | 14.696 | 0.95051 | 53.3 | 85.8 | 10% | 13.7455 | 0.095051 | 0.004044
Constant enthalpy lines
This analysis assumes the constant enthalpy lines are approximately straight and defined by a point on the saturation curve and a point associated with the same enthalpy at the w associated with 32.1 °F
This first table comes up with the enthalpy associated with different temperature points on the saturation curve, which will become one point on the consant enthalpy line.
| Saturation Temperature, °F | ws (From saturation curve development and assumption 8) |  | Total lb in moist air sample | Vapor pressure, ps, psia (From steam table) | ha, Btu/lb (From table) | hs, Btu/lb (From steam table) | H, Btu (From assumption 8) | h, Btu/lb for the water vapor/air mixture
|  | lbwater/lbdryair | grains/lb
| 40 | 0.0051886 | 36.3202 | 1 | 0.12173 | 9.6139 | 1079.4 | 15.2145 | 15.2145
| 45 | 0.0063012 | 44.1083 | 1.0063 | 0.14757 | 10.816 | 1081.6 | 17.6314 | 17.521
| 50 | 0.0076225 | 53.3577 | 1.0076 | 0.17814 | 12.018 | 1083.8 | 20.2793 | 20.1259
| 55 | 0.0091857 | 64.3001 | 1.0092 | 0.21414 | 13.22 | 1086 | 23.1957 | 22.9846
| 60 | 0.011031 | 77.2148 | 1.011 | 0.2564 | 14.422 | 1088.2 | 26.4256 | 26.1373
| 65 | 0.013201 | 92.4078 | 1.0132 | 0.3058 | 15.624 | 1090.3 | 30.0172 | 29.6261
| 70 | 0.015749 | 110.2425 | 1.0157 | 0.36336 | 16.827 | 1092.5 | 34.0327 | 33.505
| 75 | 0.018732 | 131.1237 | 1.0187 | 0.43017 | 18.029 | 1094.7 | 38.5349 | 37.8263
| 80 | 0.022218 | 155.5288 | 1.0222 | 0.50747 | 19.232 | 1096.8 | 43.6011 | 42.6535
| 85 | 0.026286 | 184.0012 | 1.0263 | 0.5966 | 20.435 | 1099 | 49.3232 | 48.0599
| 90 | 0.031025 | 217.1732 | 1.031 | 0.69904 | 21.637 | 1101.1 | 55.7983 | 54.1193
| 95 | 0.036541 | 255.7851 | 1.0365 | 0.81642 | 22.84 | 1103.3 | 63.1554 | 60.929
This table comes up with the drybulb temperature associated with each of the enthalpy values calculated above at the w associated with a saturation temperature that will give an enthalpy line that goes across the chart most of the way
| Point 1 on the line |  |  |  | ts for the 2nd point, °F, selected to be plottable on the chart as far down as possible | ps psia, associated with ws for the 2nd point, °F (from steam table) | p, psia (Given) | Gas Constants |  | ws lbwater/lbdryair (from assumption 5) | hs at 32.1°F, Btu/lb (From steam table) | Assumed hH where the w line and constant h line cross the tdb line (From assumption 8) | mH x hH, Btu | HTotal from the previous table (the constant h line value) | HTotal - mHhH = maha, Btu, where Htotal is the constant h from the previous table | ha, Btu/lb (ma is 1 lb by the definition of w) | tdb (from air table), °F | Δh from previous | Akton cross check
| Saturation Temperature, °F | ws (From saturation curve development and assumption 8) |  | h, Btu/lb for the water vapor/air mixture |  |  |  | Air, ft./°F | Water, ft./°F | [9 empty] | t | h | Δh from previous
|  | lbwater/lbdryair | grains/lb
| 40 | 0.0051886 | 36.3202 | 15.2145 | 32.1 | 0.089007 | 14.696 | 53.3 | 85.8 | 0.0037853 | 1076 | 1076 | 4.073 | 15.2145 | 11.1415 | 11.1415 | 46.35 |  | 46.34 | 15.18
| 45 | 0.0063012 | 44.1083 | 17.521 | 32.1 | 0.089007 | 14.696 | 53.3 | 85.8 | 0.0037853 | 1076 | 1076 | 4.073 | 17.6314 | 13.5583 | 13.5583 | 56.4 | 2.4169 | 56.369 | 17.599 | 2.419
| 50 | 0.0076225 | 53.3577 | 20.1259 | 32.1 | 0.089007 | 14.696 | 53.3 | 85.8 | 0.0037853 | 1076 | 1076 | 4.073 | 20.2793 | 16.2063 | 16.2063 | 67.42 | 2.6479 | 67.331 | 20.248 | 2.649
| 55 | 0.0091857 | 64.3001 | 22.9846 | 32.1 | 0.089007 | 14.696 | 53.3 | 85.8 | 0.0037853 | 1076 | 1076 | 4.073 | 23.1957 | 19.1227 | 19.1227 | 79.54 | 2.9164 | 79.39 | 23.162 | 2.914
| 60 | 0.011031 | 77.2148 | 26.1373 | 32.1 | 0.089007 | 14.696 | 53.3 | 85.8 | 0.0037853 | 1076 | 1076 | 4.073 | 26.4256 | 22.3526 | 22.3526 | 92.97 | 3.2299 | 92.909 | 26.411 | 3.249
| 65 | 0.013201 | 92.4078 | 29.6261 | 37 | 0.10823 | 14.696 | 53.3 | 85.8 | 0.0046089 | 1076 | 1076 | 4.9592 | 30.0172 | 25.058 | 25.058 | 104.21 | 3.5916 | 87.332 | 30.006 | 3.595
| 70 | 0.015749 | 110.2425 | 33.505 | 52 | 0.19184 | 14.696 | 53.3 | 85.8 | 0.0082165 | 1076 | 1076 | 8.8409 | 34.0327 | 25.1918 | 25.1918 | 104.77 | 4.0155 | 104.004 | 34.068 | 4.062
| 75 | 0.018732 | 131.1237 | 37.8263 | 63.25 | 0.28764 | 14.696 | 53.3 | 85.8 | 0.012402 | 1076 | 1076 | 13.344 | 38.5349 | 25.1908 | 25.1908 | 104.76 | 4.5022 | 103.485 | 38.601 | 4.533
| 80 | 0.022218 | 155.5288 | 42.6535 | 72.3 | 0.39287 | 14.696 | 53.3 | 85.8 | 0.017063 | 1076 | 1076 | 18.3599 | 43.6011 | 25.2413 | 25.2413 | 104.97 | 5.0663 | 102.884 | 43.677 | 5.076
| 85 | 0.026286 | 184.0012 | 48.0599 | 80.25 | 0.51163 | 14.696 | 53.3 | 85.8 | 0.022407 | 1076 | 1076 | 24.1101 | 49.3232 | 25.2131 | 25.2131 | 104.86 | 5.722 | 102.24 | 49.463 | 5.786
| 90 | 0.031025 | 217.1732 | 54.1193 | 87.4 | 0.64401 | 14.696 | 53.3 | 85.8 | 0.02847 | 1076 | 1076 | 30.6342 | 55.7983 | 25.1641 | 25.1641 | 104.65 | 6.4752 | 101.083 | 55.94 | 6.477
| 95 | 0.036541 | 255.7851 | 60.929 | 94 | 0.79167 | 14.696 | 53.3 | 85.8 | 0.03537 | 1076 | 1076 | 38.058 | 63.1554 | 25.0974 | 25.0974 | 104.38 | 7.357
Point pairs for the consant enthalpy lines
Enthalpy = h = 15.21
| tdb, °F | w lbwater/lbdryair
Saturation Line | 40 | 0.0051886
ws for tdb @ 2nd point | 46.35 | 0.0037853
h = 17.63
| tdb, °F | w lbwater/lbdryair
| 45 | 0.0063012
| 56.4 | 0.0037853
h = 20.28
| tdb, °F | w lbwater/lbdryair
| 50 | 0.0076225
| 67.42 | 0.0037853
h = 23.2
| tdb, °F | w lbwater/lbdryair
| 55 | 0.0091857
| 79.54 | 0.0037853
h = 26.43
| tdb, °F | w lbwater/lbdryair
| 60 | 0.011031
| 92.97 | 0.0037853
h = 30.02
| tdb, °F | w lbwater/lbdryair
| 65 | 0.013201
| 104.21 | 0.0046089
h = 34.03
| tdb, °F | w lbwater/lbdryair
| 70 | 0.015749
| 104.77 | 0.0082165
h = 38.53
| tdb, °F | w lbwater/lbdryair
| 75 | 0.018732
| 104.76 | 0.012402
h = 43.6
| tdb, °F | w lbwater/lbdryair
| 80 | 0.022218
| 104.97 | 0.017063
h = 49.32
| tdb, °F | w lbwater/lbdryair
| 85 | 0.026286
| 104.86 | 0.022407
h = 55.8
| tdb, °F | w lbwater/lbdryair
| 90 | 0.031025
| 104.65 | 0.02847
h = 63.16
| tdb, °F | w lbwater/lbdryair
| 95 | 0.036541
| 104.38 | 0.03537
Constant Thermodynamic Wet Bulb Lines, twb Based on the adiabatic saturation calculation for the 2nd poitn and the first point being on the saturation curve at the indicated drybulb
| Point 1 on the line |  |  |  | Point pair for 2nd point |  | atmospheric pressure, P, psia | Saturation pressure, ps for twb, psia (From steam table) | Gas Constants |  | Latent heat of vaporization, hfg, for twb, Btu/lb (From steam table) | Vapor enthalpy, hg, for the entering water vapor, Btu/lb | Liquid enthalpy, hf, for the make up water, Btu/lb | ws for twb, lbWater/lbAir (From assumption 5) | ws for the 2nd tdb, lbWater/lbAir (From assumption 7)
| Saturation Temperature, °F | ws (From saturation curve development and assumption 8) |  | h, Btu/lb for the water vapor/air mixture | tdb, °F | twb, °F |  |  | Air, ft./°F | Water, ft./°F
|  | lbwater/lbdryair | grains/lb
| 45 | 0.0063012 | 44.1083 | 20.1259 | 56 | 45 | 14.696 | 0.14757 | 53.3 | 85.8 | 1068.539 | 1086.4 | 13.061 | 0.0063012 | 0.0038031
| 50 | 0.0076225 | 53.3577 | 22.9846 | 67 | 50 | 14.696 | 0.17814 | 53.3 | 85.8 | 1065.722 | 1091.2 | 18.078 | 0.0076225 | 0.0037521
| 55 | 0.0091857 | 64.3001 | 26.1373 | 79 | 55 | 14.696 | 0.21414 | 53.3 | 85.8 | 1062.911 | 1096.4 | 23.089 | 0.0091857 | 0.0037078
| 60 | 0.011031 | 77.2148 | 29.6261 | 93 | 60 | 14.696 | 0.2564 | 53.3 | 85.8 | 1060.104 | 1102.4 | 28.096 | 0.011031 | 0.003482
| 65 | 0.013201 | 92.4078 | 33.505 | 104 | 65 | 14.696 | 0.3058 | 53.3 | 85.8 | 1057.2 | 1107.2 | 33.1 | 0.013201 | 0.0042428
| 70 | 0.015749 | 110.2425 | 37.8263 | 104 | 70 | 14.696 | 0.36336 | 53.3 | 85.8 | 1054.399 | 1107.2 | 38.101 | 0.015749 | 0.007868
| 75 | 0.018732 | 131.1237 | 42.6535 | 104 | 75 | 14.696 | 0.43017 | 53.3 | 85.8 | 1051.6 | 1107.2 | 43.1 | 0.018732 | 0.011944
| 80 | 0.022218 | 155.5288 | 48.0599 | 104 | 80 | 14.696 | 0.50747 | 53.3 | 85.8 | 1048.703 | 1107.2 | 48.097 | 0.022218 | 0.016539
| 85 | 0.026286 | 184.0012 | 54.1193 | 104 | 85 | 14.696 | 0.5966 | 53.3 | 85.8 | 1045.907 | 1107.2 | 53.093 | 0.026286 | 0.021737
| 90 | 0.031025 | 217.1732 | 0 | 104 | 90 | 14.696 | 0.69904 | 53.3 | 85.8 | 1043.012 | 1107.2 | 58.088 | 0.031025 | 0.027628
| 95 | 0.036541 | 255.7851 | 0 | 104 | 95 | 14.696 | 0.81642 | 53.3 | 85.8 | 1040.217 | 1107.2 | 63.083 | 0.036541 | 0.034327
Point pairs for the consant twb lines
Wet bulb temperature = twb = 45 °F
| tdb, °F | w lbwater/lbdryair
Saturation Line | 45 | 0.0063012
ws for tdb @ 2nd point | 56 | 0.0038031
Point pairs for the consant twb lines
twb = 50 °F
| tdb, °F | w lbwater/lbdryair
| 50 | 0.0076225
| 67 | 0.0037521
Point pairs for the consant twb lines
twb = 55 °F
| tdb, °F | w lbwater/lbdryair
| 55 | 0.0091857
| 79 | 0.0037078
Point pairs for the consant twb lines
twb = 60 °F
| tdb, °F | w lbwater/lbdryair
| 60 | 0.011031
| 93 | 0.003482
Point pairs for the consant twb lines
twb = 65 °F
| tdb, °F | w lbwater/lbdryair
| 65 | 0.013201
| 104 | 0.0042428
Point pairs for the consant twb lines
twb = 70 °F
| tdb, °F | w lbwater/lbdryair
| 70 | 0.015749
| 104 | 0.007868
Point pairs for the consant twb lines
twb = 75 °F
| tdb, °F | w lbwater/lbdryair
| 75 | 0.018732
| 104 | 0.011944
Point pairs for the consant twb lines
twb = 80 °F
| tdb, °F | w lbwater/lbdryair
| 80 | 0.022218
| 104 | 0.016539
Point pairs for the consant twb lines
twb = 85 °F
| tdb, °F | w lbwater/lbdryair
| 85 | 0.026286
| 104 | 0.021737
Point pairs for the consant twb lines
twb = 90 °F
| tdb, °F | w lbwater/lbdryair
| 90 | 0.031025
| 104 | 0.027628
Point pairs for the consant twb lines
twb = 95 °F
| tdb, °F | w lbwater/lbdryair
| 95 | 0.036541
| 104 | 0.034327

## Water at Saturation 35-220F .01
Reference state for enthalpy and entropy is 0°F at atmospheric pressure
Look up pressure | [7 empty] | Look up temperature
4:00 | V/L | water: | sat. | T=32.0 | to | 220 | ｰF | 4:00 | water: | V/L | sat. | T=32.0 | to | 220 | ｰF
| Vapor | Liquid | Liquid | Vapor | Liquid | Vapor |  |  | Liquid | Vapor | Liquid | Vapor | Liquid | Vapor | Latent Heat
| Pressure | Temperature | Density | Density | Enthalpy | Enthalpy |  |  | Temperature | Pressure | Density | Density | Enthalpy | Enthalpy | hfg
| (psia) | (F) | (lbm/ft^3) | (lbm/ft^3) | (Btu/lbm) | (Btu/lbm) |  |  | (F) | (psia) | (lbm/ft^3) | (lbm/ft^3) | (Btu/lbm) | (Btu/lbm) | Btu/lb
1 | 0.08872 | 32.02 | 62.415 | 0.00030308 | 0.0022804 | 1075.9 |  | 1 | 32.02 | 0.08872 | 62.415 | 0.00030308 | 0.0022804 | 1075.9 | 1075.8977
2 | 0.088756 | 32.03 | 62.415 | 0.0003032 | 0.012366 | 1075.9 |  | 2 | 32.03 | 0.088756 | 62.415 | 0.0003032 | 0.012366 | 1075.9 | 1075.8876
3 | 0.088792 | 32.04 | 62.415 | 0.00030332 | 0.022452 | 1075.9 |  | 3 | 32.04 | 0.088792 | 62.415 | 0.00030332 | 0.022452 | 1075.9 | 1075.8775
4 | 0.088828 | 32.05 | 62.415 | 0.00030343 | 0.032538 | 1075.9 |  | 4 | 32.05 | 0.088828 | 62.415 | 0.00030343 | 0.032538 | 1075.9 | 1075.8675
5 | 0.088864 | 32.06 | 62.415 | 0.00030355 | 0.042624 | 1075.9 |  | 5 | 32.06 | 0.088864 | 62.415 | 0.00030355 | 0.042624 | 1075.9 | 1075.8574
6 | 0.088899 | 32.07 | 62.415 | 0.00030367 | 0.052709 | 1075.9 |  | 6 | 32.07 | 0.088899 | 62.415 | 0.00030367 | 0.052709 | 1075.9 | 1075.8473
7 | 0.088935 | 32.08 | 62.415 | 0.00030378 | 0.062795 | 1075.9 |  | 7 | 32.08 | 0.088935 | 62.415 | 0.00030378 | 0.062795 | 1075.9 | 1075.8372
8 | 0.088971 | 32.09 | 62.415 | 0.0003039 | 0.072881 | 1076 |  | 8 | 32.09 | 0.088971 | 62.415 | 0.0003039 | 0.072881 | 1076 | 1075.9271
9 | 0.089007 | 32.1 | 62.415 | 0.00030402 | 0.082966 | 1076 |  | 9 | 32.1 | 0.089007 | 62.415 | 0.00030402 | 0.082966 | 1076 | 1075.917
10 | 0.089043 | 32.11 | 62.415 | 0.00030413 | 0.093052 | 1076 |  | 10 | 32.11 | 0.089043 | 62.415 | 0.00030413 | 0.093052 | 1076 | 1075.9069
11 | 0.089079 | 32.12 | 62.415 | 0.00030425 | 0.10314 | 1076 |  | 11 | 32.12 | 0.089079 | 62.415 | 0.00030425 | 0.10314 | 1076 | 1075.8969
12 | 0.089115 | 32.13 | 62.415 | 0.00030437 | 0.11322 | 1076 |  | 12 | 32.13 | 0.089115 | 62.415 | 0.00030437 | 0.11322 | 1076 | 1075.8868
13 | 0.089151 | 32.14 | 62.415 | 0.00030448 | 0.12331 | 1076 |  | 13 | 32.14 | 0.089151 | 62.415 | 0.00030448 | 0.12331 | 1076 | 1075.8767
14 | 0.089187 | 32.15 | 62.415 | 0.0003046 | 0.13339 | 1076 |  | 14 | 32.15 | 0.089187 | 62.415 | 0.0003046 | 0.13339 | 1076 | 1075.8666
15 | 0.089223 | 32.16 | 62.415 | 0.00030472 | 0.14348 | 1076 |  | 15 | 32.16 | 0.089223 | 62.415 | 0.00030472 | 0.14348 | 1076 | 1075.8565
16 | 0.089259 | 32.17 | 62.415 | 0.00030483 | 0.15356 | 1076 |  | 16 | 32.17 | 0.089259 | 62.415 | 0.00030483 | 0.15356 | 1076 | 1075.8464
17 | 0.089295 | 32.18 | 62.415 | 0.00030495 | 0.16365 | 1076 |  | 17 | 32.18 | 0.089295 | 62.415 | 0.00030495 | 0.16365 | 1076 | 1075.8364
18 | 0.089331 | 32.19 | 62.415 | 0.00030507 | 0.17373 | 1076 |  | 18 | 32.19 | 0.089331 | 62.415 | 0.00030507 | 0.17373 | 1076 | 1075.8263
19 | 0.089367 | 32.2 | 62.415 | 0.00030518 | 0.18382 | 1076 |  | 19 | 32.2 | 0.089367 | 62.415 | 0.00030518 | 0.18382 | 1076 | 1075.8162
20 | 0.089403 | 32.21 | 62.415 | 0.0003053 | 0.1939 | 1076 |  | 20 | 32.21 | 0.089403 | 62.415 | 0.0003053 | 0.1939 | 1076 | 1075.8061
21 | 0.089439 | 32.22 | 62.415 | 0.00030542 | 0.20399 | 1076 |  | 21 | 32.22 | 0.089439 | 62.415 | 0.00030542 | 0.20399 | 1076 | 1075.796
22 | 0.089475 | 32.23 | 62.415 | 0.00030553 | 0.21407 | 1076 |  | 22 | 32.23 | 0.089475 | 62.415 | 0.00030553 | 0.21407 | 1076 | 1075.7859
23 | 0.089511 | 32.24 | 62.416 | 0.00030565 | 0.22416 | 1076 |  | 23 | 32.24 | 0.089511 | 62.416 | 0.00030565 | 0.22416 | 1076 | 1075.7758
24 | 0.089547 | 32.25 | 62.416 | 0.00030577 | 0.23424 | 1076 |  | 24 | 32.25 | 0.089547 | 62.416 | 0.00030577 | 0.23424 | 1076 | 1075.7658
25 | 0.089583 | 32.26 | 62.416 | 0.00030589 | 0.24433 | 1076 |  | 25 | 32.26 | 0.089583 | 62.416 | 0.00030589 | 0.24433 | 1076 | 1075.7557
26 | 0.08962 | 32.27 | 62.416 | 0.000306 | 0.25441 | 1076 |  | 26 | 32.27 | 0.08962 | 62.416 | 0.000306 | 0.25441 | 1076 | 1075.7456
27 | 0.089656 | 32.28 | 62.416 | 0.00030612 | 0.2645 | 1076 |  | 27 | 32.28 | 0.089656 | 62.416 | 0.00030612 | 0.2645 | 1076 | 1075.7355
28 | 0.089692 | 32.29 | 62.416 | 0.00030624 | 0.27458 | 1076 |  | 28 | 32.29 | 0.089692 | 62.416 | 0.00030624 | 0.27458 | 1076 | 1075.7254
29 | 0.089728 | 32.3 | 62.416 | 0.00030635 | 0.28467 | 1076 |  | 29 | 32.3 | 0.089728 | 62.416 | 0.00030635 | 0.28467 | 1076 | 1075.7153
30 | 0.089764 | 32.31 | 62.416 | 0.00030647 | 0.29475 | 1076 |  | 30 | 32.31 | 0.089764 | 62.416 | 0.00030647 | 0.29475 | 1076 | 1075.7052
31 | 0.0898 | 32.32 | 62.416 | 0.00030659 | 0.30484 | 1076.1 |  | 31 | 32.32 | 0.0898 | 62.416 | 0.00030659 | 0.30484 | 1076.1 | 1075.7952
32 | 0.089837 | 32.33 | 62.416 | 0.00030671 | 0.31492 | 1076.1 |  | 32 | 32.33 | 0.089837 | 62.416 | 0.00030671 | 0.31492 | 1076.1 | 1075.7851
33 | 0.089873 | 32.34 | 62.416 | 0.00030682 | 0.32501 | 1076.1 |  | 33 | 32.34 | 0.089873 | 62.416 | 0.00030682 | 0.32501 | 1076.1 | 1075.775
34 | 0.089909 | 32.35 | 62.416 | 0.00030694 | 0.33509 | 1076.1 |  | 34 | 32.35 | 0.089909 | 62.416 | 0.00030694 | 0.33509 | 1076.1 | 1075.7649
35 | 0.089945 | 32.36 | 62.416 | 0.00030706 | 0.34518 | 1076.1 |  | 35 | 32.36 | 0.089945 | 62.416 | 0.00030706 | 0.34518 | 1076.1 | 1075.7548
36 | 0.089982 | 32.37 | 62.416 | 0.00030718 | 0.35526 | 1076.1 |  | 36 | 32.37 | 0.089982 | 62.416 | 0.00030718 | 0.35526 | 1076.1 | 1075.7447
37 | 0.090018 | 32.38 | 62.416 | 0.00030729 | 0.36534 | 1076.1 |  | 37 | 32.38 | 0.090018 | 62.416 | 0.00030729 | 0.36534 | 1076.1 | 1075.7347
38 | 0.090054 | 32.39 | 62.416 | 0.00030741 | 0.37543 | 1076.1 |  | 38 | 32.39 | 0.090054 | 62.416 | 0.00030741 | 0.37543 | 1076.1 | 1075.7246
39 | 0.09009 | 32.4 | 62.416 | 0.00030753 | 0.38551 | 1076.1 |  | 39 | 32.4 | 0.09009 | 62.416 | 0.00030753 | 0.38551 | 1076.1 | 1075.7145
40 | 0.090127 | 32.41 | 62.416 | 0.00030765 | 0.3956 | 1076.1 |  | 40 | 32.41 | 0.090127 | 62.416 | 0.00030765 | 0.3956 | 1076.1 | 1075.7044
41 | 0.090163 | 32.42 | 62.416 | 0.00030777 | 0.40568 | 1076.1 |  | 41 | 32.42 | 0.090163 | 62.416 | 0.00030777 | 0.40568 | 1076.1 | 1075.6943
42 | 0.090199 | 32.43 | 62.416 | 0.00030788 | 0.41576 | 1076.1 |  | 42 | 32.43 | 0.090199 | 62.416 | 0.00030788 | 0.41576 | 1076.1 | 1075.6842
43 | 0.090236 | 32.44 | 62.416 | 0.000308 | 0.42585 | 1076.1 |  | 43 | 32.44 | 0.090236 | 62.416 | 0.000308 | 0.42585 | 1076.1 | 1075.6741
44 | 0.090272 | 32.45 | 62.416 | 0.00030812 | 0.43593 | 1076.1 |  | 44 | 32.45 | 0.090272 | 62.416 | 0.00030812 | 0.43593 | 1076.1 | 1075.6641
45 | 0.090309 | 32.46 | 62.416 | 0.00030824 | 0.44602 | 1076.1 |  | 45 | 32.46 | 0.090309 | 62.416 | 0.00030824 | 0.44602 | 1076.1 | 1075.654
46 | 0.090345 | 32.47 | 62.416 | 0.00030835 | 0.4561 | 1076.1 |  | 46 | 32.47 | 0.090345 | 62.416 | 0.00030835 | 0.4561 | 1076.1 | 1075.6439
47 | 0.090381 | 32.48 | 62.416 | 0.00030847 | 0.46618 | 1076.1 |  | 47 | 32.48 | 0.090381 | 62.416 | 0.00030847 | 0.46618 | 1076.1 | 1075.6338
48 | 0.090418 | 32.49 | 62.416 | 0.00030859 | 0.47627 | 1076.1 |  | 48 | 32.49 | 0.090418 | 62.416 | 0.00030859 | 0.47627 | 1076.1 | 1075.6237
49 | 0.090454 | 32.5 | 62.416 | 0.00030871 | 0.48635 | 1076.1 |  | 49 | 32.5 | 0.090454 | 62.416 | 0.00030871 | 0.48635 | 1076.1 | 1075.6137
50 | 0.090491 | 32.51 | 62.416 | 0.00030883 | 0.49644 | 1076.1 |  | 50 | 32.51 | 0.090491 | 62.416 | 0.00030883 | 0.49644 | 1076.1 | 1075.6036
51 | 0.090527 | 32.52 | 62.416 | 0.00030895 | 0.50652 | 1076.1 |  | 51 | 32.52 | 0.090527 | 62.416 | 0.00030895 | 0.50652 | 1076.1 | 1075.5935
52 | 0.090564 | 32.53 | 62.416 | 0.00030906 | 0.5166 | 1076.1 |  | 52 | 32.53 | 0.090564 | 62.416 | 0.00030906 | 0.5166 | 1076.1 | 1075.5834
53 | 0.0906 | 32.54 | 62.416 | 0.00030918 | 0.52669 | 1076.1 |  | 53 | 32.54 | 0.0906 | 62.416 | 0.00030918 | 0.52669 | 1076.1 | 1075.5733
54 | 0.090637 | 32.55 | 62.416 | 0.0003093 | 0.53677 | 1076.2 |  | 54 | 32.55 | 0.090637 | 62.416 | 0.0003093 | 0.53677 | 1076.2 | 1075.6632
55 | 0.090673 | 32.56 | 62.416 | 0.00030942 | 0.54685 | 1076.2 |  | 55 | 32.56 | 0.090673 | 62.416 | 0.00030942 | 0.54685 | 1076.2 | 1075.6532
56 | 0.09071 | 32.57 | 62.416 | 0.00030954 | 0.55694 | 1076.2 |  | 56 | 32.57 | 0.09071 | 62.416 | 0.00030954 | 0.55694 | 1076.2 | 1075.6431
57 | 0.090746 | 32.58 | 62.416 | 0.00030966 | 0.56702 | 1076.2 |  | 57 | 32.58 | 0.090746 | 62.416 | 0.00030966 | 0.56702 | 1076.2 | 1075.633
58 | 0.090783 | 32.59 | 62.416 | 0.00030977 | 0.5771 | 1076.2 |  | 58 | 32.59 | 0.090783 | 62.416 | 0.00030977 | 0.5771 | 1076.2 | 1075.6229
59 | 0.090819 | 32.6 | 62.416 | 0.00030989 | 0.58719 | 1076.2 |  | 59 | 32.6 | 0.090819 | 62.416 | 0.00030989 | 0.58719 | 1076.2 | 1075.6128
60 | 0.090856 | 32.61 | 62.416 | 0.00031001 | 0.59727 | 1076.2 |  | 60 | 32.61 | 0.090856 | 62.416 | 0.00031001 | 0.59727 | 1076.2 | 1075.6027
61 | 0.090892 | 32.62 | 62.416 | 0.00031013 | 0.60735 | 1076.2 |  | 61 | 32.62 | 0.090892 | 62.416 | 0.00031013 | 0.60735 | 1076.2 | 1075.5927
62 | 0.090929 | 32.63 | 62.416 | 0.00031025 | 0.61744 | 1076.2 |  | 62 | 32.63 | 0.090929 | 62.416 | 0.00031025 | 0.61744 | 1076.2 | 1075.5826
63 | 0.090966 | 32.64 | 62.416 | 0.00031037 | 0.62752 | 1076.2 |  | 63 | 32.64 | 0.090966 | 62.416 | 0.00031037 | 0.62752 | 1076.2 | 1075.5725
64 | 0.091002 | 32.65 | 62.416 | 0.00031049 | 0.6376 | 1076.2 |  | 64 | 32.65 | 0.091002 | 62.416 | 0.00031049 | 0.6376 | 1076.2 | 1075.5624
65 | 0.091039 | 32.66 | 62.416 | 0.0003106 | 0.64769 | 1076.2 |  | 65 | 32.66 | 0.091039 | 62.416 | 0.0003106 | 0.64769 | 1076.2 | 1075.5523
66 | 0.091075 | 32.67 | 62.416 | 0.00031072 | 0.65777 | 1076.2 |  | 66 | 32.67 | 0.091075 | 62.416 | 0.00031072 | 0.65777 | 1076.2 | 1075.5422
67 | 0.091112 | 32.68 | 62.416 | 0.00031084 | 0.66785 | 1076.2 |  | 67 | 32.68 | 0.091112 | 62.416 | 0.00031084 | 0.66785 | 1076.2 | 1075.5322
68 | 0.091149 | 32.69 | 62.417 | 0.00031096 | 0.67794 | 1076.2 |  | 68 | 32.69 | 0.091149 | 62.417 | 0.00031096 | 0.67794 | 1076.2 | 1075.5221
69 | 0.091186 | 32.7 | 62.417 | 0.00031108 | 0.68802 | 1076.2 |  | 69 | 32.7 | 0.091186 | 62.417 | 0.00031108 | 0.68802 | 1076.2 | 1075.512
70 | 0.091222 | 32.71 | 62.417 | 0.0003112 | 0.6981 | 1076.2 |  | 70 | 32.71 | 0.091222 | 62.417 | 0.0003112 | 0.6981 | 1076.2 | 1075.5019
71 | 0.091259 | 32.72 | 62.417 | 0.00031132 | 0.70818 | 1076.2 |  | 71 | 32.72 | 0.091259 | 62.417 | 0.00031132 | 0.70818 | 1076.2 | 1075.4918
72 | 0.091296 | 32.73 | 62.417 | 0.00031144 | 0.71827 | 1076.2 |  | 72 | 32.73 | 0.091296 | 62.417 | 0.00031144 | 0.71827 | 1076.2 | 1075.4817
73 | 0.091332 | 32.74 | 62.417 | 0.00031156 | 0.72835 | 1076.2 |  | 73 | 32.74 | 0.091332 | 62.417 | 0.00031156 | 0.72835 | 1076.2 | 1075.4716
74 | 0.091369 | 32.75 | 62.417 | 0.00031167 | 0.73843 | 1076.2 |  | 74 | 32.75 | 0.091369 | 62.417 | 0.00031167 | 0.73843 | 1076.2 | 1075.4616
75 | 0.091406 | 32.76 | 62.417 | 0.00031179 | 0.74851 | 1076.2 |  | 75 | 32.76 | 0.091406 | 62.417 | 0.00031179 | 0.74851 | 1076.2 | 1075.4515
76 | 0.091443 | 32.77 | 62.417 | 0.00031191 | 0.7586 | 1076.2 |  | 76 | 32.77 | 0.091443 | 62.417 | 0.00031191 | 0.7586 | 1076.2 | 1075.4414
77 | 0.09148 | 32.78 | 62.417 | 0.00031203 | 0.76868 | 1076.3 |  | 77 | 32.78 | 0.09148 | 62.417 | 0.00031203 | 0.76868 | 1076.3 | 1075.5313
78 | 0.091516 | 32.79 | 62.417 | 0.00031215 | 0.77876 | 1076.3 |  | 78 | 32.79 | 0.091516 | 62.417 | 0.00031215 | 0.77876 | 1076.3 | 1075.5212
79 | 0.091553 | 32.8 | 62.417 | 0.00031227 | 0.78884 | 1076.3 |  | 79 | 32.8 | 0.091553 | 62.417 | 0.00031227 | 0.78884 | 1076.3 | 1075.5112
80 | 0.09159 | 32.81 | 62.417 | 0.00031239 | 0.79893 | 1076.3 |  | 80 | 32.81 | 0.09159 | 62.417 | 0.00031239 | 0.79893 | 1076.3 | 1075.5011
81 | 0.091627 | 32.82 | 62.417 | 0.00031251 | 0.80901 | 1076.3 |  | 81 | 32.82 | 0.091627 | 62.417 | 0.00031251 | 0.80901 | 1076.3 | 1075.491
82 | 0.091664 | 32.83 | 62.417 | 0.00031263 | 0.81909 | 1076.3 |  | 82 | 32.83 | 0.091664 | 62.417 | 0.00031263 | 0.81909 | 1076.3 | 1075.4809
83 | 0.091701 | 32.84 | 62.417 | 0.00031275 | 0.82917 | 1076.3 |  | 83 | 32.84 | 0.091701 | 62.417 | 0.00031275 | 0.82917 | 1076.3 | 1075.4708
84 | 0.091737 | 32.85 | 62.417 | 0.00031287 | 0.83926 | 1076.3 |  | 84 | 32.85 | 0.091737 | 62.417 | 0.00031287 | 0.83926 | 1076.3 | 1075.4607
85 | 0.091774 | 32.86 | 62.417 | 0.00031299 | 0.84934 | 1076.3 |  | 85 | 32.86 | 0.091774 | 62.417 | 0.00031299 | 0.84934 | 1076.3 | 1075.4507
86 | 0.091811 | 32.87 | 62.417 | 0.00031311 | 0.85942 | 1076.3 |  | 86 | 32.87 | 0.091811 | 62.417 | 0.00031311 | 0.85942 | 1076.3 | 1075.4406
87 | 0.091848 | 32.88 | 62.417 | 0.00031323 | 0.8695 | 1076.3 |  | 87 | 32.88 | 0.091848 | 62.417 | 0.00031323 | 0.8695 | 1076.3 | 1075.4305
88 | 0.091885 | 32.89 | 62.417 | 0.00031335 | 0.87958 | 1076.3 |  | 88 | 32.89 | 0.091885 | 62.417 | 0.00031335 | 0.87958 | 1076.3 | 1075.4204
89 | 0.091922 | 32.9 | 62.417 | 0.00031347 | 0.88967 | 1076.3 |  | 89 | 32.9 | 0.091922 | 62.417 | 0.00031347 | 0.88967 | 1076.3 | 1075.4103
90 | 0.091959 | 32.91 | 62.417 | 0.00031359 | 0.89975 | 1076.3 |  | 90 | 32.91 | 0.091959 | 62.417 | 0.00031359 | 0.89975 | 1076.3 | 1075.4002
91 | 0.091996 | 32.92 | 62.417 | 0.00031371 | 0.90983 | 1076.3 |  | 91 | 32.92 | 0.091996 | 62.417 | 0.00031371 | 0.90983 | 1076.3 | 1075.3902
92 | 0.092033 | 32.93 | 62.417 | 0.00031383 | 0.91991 | 1076.3 |  | 92 | 32.93 | 0.092033 | 62.417 | 0.00031383 | 0.91991 | 1076.3 | 1075.3801
93 | 0.09207 | 32.94 | 62.417 | 0.00031394 | 0.92999 | 1076.3 |  | 93 | 32.94 | 0.09207 | 62.417 | 0.00031394 | 0.92999 | 1076.3 | 1075.37
94 | 0.092107 | 32.95 | 62.417 | 0.00031406 | 0.94008 | 1076.3 |  | 94 | 32.95 | 0.092107 | 62.417 | 0.00031406 | 0.94008 | 1076.3 | 1075.3599
95 | 0.092144 | 32.96 | 62.417 | 0.00031418 | 0.95016 | 1076.3 |  | 95 | 32.96 | 0.092144 | 62.417 | 0.00031418 | 0.95016 | 1076.3 | 1075.3498
96 | 0.092181 | 32.97 | 62.417 | 0.0003143 | 0.96024 | 1076.3 |  | 96 | 32.97 | 0.092181 | 62.417 | 0.0003143 | 0.96024 | 1076.3 | 1075.3398
97 | 0.092218 | 32.98 | 62.417 | 0.00031442 | 0.97032 | 1076.3 |  | 97 | 32.98 | 0.092218 | 62.417 | 0.00031442 | 0.97032 | 1076.3 | 1075.3297
98 | 0.092255 | 32.99 | 62.417 | 0.00031454 | 0.9804 | 1076.3 |  | 98 | 32.99 | 0.092255 | 62.417 | 0.00031454 | 0.9804 | 1076.3 | 1075.3196
99 | 0.092292 | 33 | 62.417 | 0.00031466 | 0.99048 | 1076.4 |  | 99 | 33 | 0.092292 | 62.417 | 0.00031466 | 0.99048 | 1076.4 | 1075.4095
100 | 0.092329 | 33.01 | 62.417 | 0.00031479 | 1.0006 | 1076.4 |  | 100 | 33.01 | 0.092329 | 62.417 | 0.00031479 | 1.0006 | 1076.4 | 1075.3994
101 | 0.092366 | 33.02 | 62.417 | 0.00031491 | 1.0106 | 1076.4 |  | 101 | 33.02 | 0.092366 | 62.417 | 0.00031491 | 1.0106 | 1076.4 | 1075.3894
102 | 0.092404 | 33.03 | 62.417 | 0.00031503 | 1.0207 | 1076.4 |  | 102 | 33.03 | 0.092404 | 62.417 | 0.00031503 | 1.0207 | 1076.4 | 1075.3793
103 | 0.092441 | 33.04 | 62.417 | 0.00031515 | 1.0308 | 1076.4 |  | 103 | 33.04 | 0.092441 | 62.417 | 0.00031515 | 1.0308 | 1076.4 | 1075.3692
104 | 0.092478 | 33.05 | 62.417 | 0.00031527 | 1.0409 | 1076.4 |  | 104 | 33.05 | 0.092478 | 62.417 | 0.00031527 | 1.0409 | 1076.4 | 1075.3591
105 | 0.092515 | 33.06 | 62.417 | 0.00031539 | 1.051 | 1076.4 |  | 105 | 33.06 | 0.092515 | 62.417 | 0.00031539 | 1.051 | 1076.4 | 1075.349
106 | 0.092552 | 33.07 | 62.417 | 0.00031551 | 1.0611 | 1076.4 |  | 106 | 33.07 | 0.092552 | 62.417 | 0.00031551 | 1.0611 | 1076.4 | 1075.3389
107 | 0.092589 | 33.08 | 62.417 | 0.00031563 | 1.0711 | 1076.4 |  | 107 | 33.08 | 0.092589 | 62.417 | 0.00031563 | 1.0711 | 1076.4 | 1075.3289
108 | 0.092627 | 33.09 | 62.417 | 0.00031575 | 1.0812 | 1076.4 |  | 108 | 33.09 | 0.092627 | 62.417 | 0.00031575 | 1.0812 | 1076.4 | 1075.3188
109 | 0.092664 | 33.1 | 62.417 | 0.00031587 | 1.0913 | 1076.4 |  | 109 | 33.1 | 0.092664 | 62.417 | 0.00031587 | 1.0913 | 1076.4 | 1075.3087
110 | 0.092701 | 33.11 | 62.417 | 0.00031599 | 1.1014 | 1076.4 |  | 110 | 33.11 | 0.092701 | 62.417 | 0.00031599 | 1.1014 | 1076.4 | 1075.2986
111 | 0.092738 | 33.12 | 62.417 | 0.00031611 | 1.1115 | 1076.4 |  | 111 | 33.12 | 0.092738 | 62.417 | 0.00031611 | 1.1115 | 1076.4 | 1075.2885
112 | 0.092776 | 33.13 | 62.417 | 0.00031623 | 1.1215 | 1076.4 |  | 112 | 33.13 | 0.092776 | 62.417 | 0.00031623 | 1.1215 | 1076.4 | 1075.2785
113 | 0.092813 | 33.14 | 62.417 | 0.00031635 | 1.1316 | 1076.4 |  | 113 | 33.14 | 0.092813 | 62.417 | 0.00031635 | 1.1316 | 1076.4 | 1075.2684
114 | 0.09285 | 33.15 | 62.417 | 0.00031647 | 1.1417 | 1076.4 |  | 114 | 33.15 | 0.09285 | 62.417 | 0.00031647 | 1.1417 | 1076.4 | 1075.2583
115 | 0.092887 | 33.16 | 62.417 | 0.00031659 | 1.1518 | 1076.4 |  | 115 | 33.16 | 0.092887 | 62.417 | 0.00031659 | 1.1518 | 1076.4 | 1075.2482
116 | 0.092925 | 33.17 | 62.417 | 0.00031671 | 1.1619 | 1076.4 |  | 116 | 33.17 | 0.092925 | 62.417 | 0.00031671 | 1.1619 | 1076.4 | 1075.2381
117 | 0.092962 | 33.18 | 62.418 | 0.00031683 | 1.1719 | 1076.4 |  | 117 | 33.18 | 0.092962 | 62.418 | 0.00031683 | 1.1719 | 1076.4 | 1075.2281
118 | 0.092999 | 33.19 | 62.418 | 0.00031695 | 1.182 | 1076.4 |  | 118 | 33.19 | 0.092999 | 62.418 | 0.00031695 | 1.182 | 1076.4 | 1075.218
119 | 0.093037 | 33.2 | 62.418 | 0.00031708 | 1.1921 | 1076.4 |  | 119 | 33.2 | 0.093037 | 62.418 | 0.00031708 | 1.1921 | 1076.4 | 1075.2079
120 | 0.093074 | 33.21 | 62.418 | 0.0003172 | 1.2022 | 1076.4 |  | 120 | 33.21 | 0.093074 | 62.418 | 0.0003172 | 1.2022 | 1076.4 | 1075.1978
121 | 0.093112 | 33.22 | 62.418 | 0.00031732 | 1.2123 | 1076.4 |  | 121 | 33.22 | 0.093112 | 62.418 | 0.00031732 | 1.2123 | 1076.4 | 1075.1877
122 | 0.093149 | 33.23 | 62.418 | 0.00031744 | 1.2223 | 1076.5 |  | 122 | 33.23 | 0.093149 | 62.418 | 0.00031744 | 1.2223 | 1076.5 | 1075.2777
123 | 0.093186 | 33.24 | 62.418 | 0.00031756 | 1.2324 | 1076.5 |  | 123 | 33.24 | 0.093186 | 62.418 | 0.00031756 | 1.2324 | 1076.5 | 1075.2676
124 | 0.093224 | 33.25 | 62.418 | 0.00031768 | 1.2425 | 1076.5 |  | 124 | 33.25 | 0.093224 | 62.418 | 0.00031768 | 1.2425 | 1076.5 | 1075.2575
125 | 0.093261 | 33.26 | 62.418 | 0.0003178 | 1.2526 | 1076.5 |  | 125 | 33.26 | 0.093261 | 62.418 | 0.0003178 | 1.2526 | 1076.5 | 1075.2474
126 | 0.093299 | 33.27 | 62.418 | 0.00031792 | 1.2627 | 1076.5 |  | 126 | 33.27 | 0.093299 | 62.418 | 0.00031792 | 1.2627 | 1076.5 | 1075.2373
127 | 0.093336 | 33.28 | 62.418 | 0.00031804 | 1.2727 | 1076.5 |  | 127 | 33.28 | 0.093336 | 62.418 | 0.00031804 | 1.2727 | 1076.5 | 1075.2273
128 | 0.093374 | 33.29 | 62.418 | 0.00031817 | 1.2828 | 1076.5 |  | 128 | 33.29 | 0.093374 | 62.418 | 0.00031817 | 1.2828 | 1076.5 | 1075.2172
129 | 0.093411 | 33.3 | 62.418 | 0.00031829 | 1.2929 | 1076.5 |  | 129 | 33.3 | 0.093411 | 62.418 | 0.00031829 | 1.2929 | 1076.5 | 1075.2071
130 | 0.093448 | 33.31 | 62.418 | 0.00031841 | 1.303 | 1076.5 |  | 130 | 33.31 | 0.093448 | 62.418 | 0.00031841 | 1.303 | 1076.5 | 1075.197
131 | 0.093486 | 33.32 | 62.418 | 0.00031853 | 1.3131 | 1076.5 |  | 131 | 33.32 | 0.093486 | 62.418 | 0.00031853 | 1.3131 | 1076.5 | 1075.1869
132 | 0.093524 | 33.33 | 62.418 | 0.00031865 | 1.3231 | 1076.5 |  | 132 | 33.33 | 0.093524 | 62.418 | 0.00031865 | 1.3231 | 1076.5 | 1075.1769
133 | 0.093561 | 33.34 | 62.418 | 0.00031877 | 1.3332 | 1076.5 |  | 133 | 33.34 | 0.093561 | 62.418 | 0.00031877 | 1.3332 | 1076.5 | 1075.1668
134 | 0.093599 | 33.35 | 62.418 | 0.00031889 | 1.3433 | 1076.5 |  | 134 | 33.35 | 0.093599 | 62.418 | 0.00031889 | 1.3433 | 1076.5 | 1075.1567
135 | 0.093636 | 33.36 | 62.418 | 0.00031902 | 1.3534 | 1076.5 |  | 135 | 33.36 | 0.093636 | 62.418 | 0.00031902 | 1.3534 | 1076.5 | 1075.1466
136 | 0.093674 | 33.37 | 62.418 | 0.00031914 | 1.3635 | 1076.5 |  | 136 | 33.37 | 0.093674 | 62.418 | 0.00031914 | 1.3635 | 1076.5 | 1075.1365
137 | 0.093711 | 33.38 | 62.418 | 0.00031926 | 1.3735 | 1076.5 |  | 137 | 33.38 | 0.093711 | 62.418 | 0.00031926 | 1.3735 | 1076.5 | 1075.1265
138 | 0.093749 | 33.39 | 62.418 | 0.00031938 | 1.3836 | 1076.5 |  | 138 | 33.39 | 0.093749 | 62.418 | 0.00031938 | 1.3836 | 1076.5 | 1075.1164
139 | 0.093787 | 33.4 | 62.418 | 0.0003195 | 1.3937 | 1076.5 |  | 139 | 33.4 | 0.093787 | 62.418 | 0.0003195 | 1.3937 | 1076.5 | 1075.1063
140 | 0.093824 | 33.41 | 62.418 | 0.00031962 | 1.4038 | 1076.5 |  | 140 | 33.41 | 0.093824 | 62.418 | 0.00031962 | 1.4038 | 1076.5 | 1075.0962
141 | 0.093862 | 33.42 | 62.418 | 0.00031975 | 1.4139 | 1076.5 |  | 141 | 33.42 | 0.093862 | 62.418 | 0.00031975 | 1.4139 | 1076.5 | 1075.0861
142 | 0.0939 | 33.43 | 62.418 | 0.00031987 | 1.4239 | 1076.5 |  | 142 | 33.43 | 0.0939 | 62.418 | 0.00031987 | 1.4239 | 1076.5 | 1075.0761
143 | 0.093937 | 33.44 | 62.418 | 0.00031999 | 1.434 | 1076.5 |  | 143 | 33.44 | 0.093937 | 62.418 | 0.00031999 | 1.434 | 1076.5 | 1075.066
144 | 0.093975 | 33.45 | 62.418 | 0.00032011 | 1.4441 | 1076.5 |  | 144 | 33.45 | 0.093975 | 62.418 | 0.00032011 | 1.4441 | 1076.5 | 1075.0559
145 | 0.094013 | 33.46 | 62.418 | 0.00032023 | 1.4542 | 1076.6 |  | 145 | 33.46 | 0.094013 | 62.418 | 0.00032023 | 1.4542 | 1076.6 | 1075.1458
146 | 0.09405 | 33.47 | 62.418 | 0.00032036 | 1.4643 | 1076.6 |  | 146 | 33.47 | 0.09405 | 62.418 | 0.00032036 | 1.4643 | 1076.6 | 1075.1357
147 | 0.094088 | 33.48 | 62.418 | 0.00032048 | 1.4743 | 1076.6 |  | 147 | 33.48 | 0.094088 | 62.418 | 0.00032048 | 1.4743 | 1076.6 | 1075.1257
148 | 0.094126 | 33.49 | 62.418 | 0.0003206 | 1.4844 | 1076.6 |  | 148 | 33.49 | 0.094126 | 62.418 | 0.0003206 | 1.4844 | 1076.6 | 1075.1156
149 | 0.094163 | 33.5 | 62.418 | 0.00032072 | 1.4945 | 1076.6 |  | 149 | 33.5 | 0.094163 | 62.418 | 0.00032072 | 1.4945 | 1076.6 | 1075.1055
150 | 0.094201 | 33.51 | 62.418 | 0.00032084 | 1.5046 | 1076.6 |  | 150 | 33.51 | 0.094201 | 62.418 | 0.00032084 | 1.5046 | 1076.6 | 1075.0954
151 | 0.094239 | 33.52 | 62.418 | 0.00032097 | 1.5147 | 1076.6 |  | 151 | 33.52 | 0.094239 | 62.418 | 0.00032097 | 1.5147 | 1076.6 | 1075.0853
152 | 0.094277 | 33.53 | 62.418 | 0.00032109 | 1.5247 | 1076.6 |  | 152 | 33.53 | 0.094277 | 62.418 | 0.00032109 | 1.5247 | 1076.6 | 1075.0753
153 | 0.094315 | 33.54 | 62.418 | 0.00032121 | 1.5348 | 1076.6 |  | 153 | 33.54 | 0.094315 | 62.418 | 0.00032121 | 1.5348 | 1076.6 | 1075.0652
154 | 0.094352 | 33.55 | 62.418 | 0.00032133 | 1.5449 | 1076.6 |  | 154 | 33.55 | 0.094352 | 62.418 | 0.00032133 | 1.5449 | 1076.6 | 1075.0551
155 | 0.09439 | 33.56 | 62.418 | 0.00032146 | 1.555 | 1076.6 |  | 155 | 33.56 | 0.09439 | 62.418 | 0.00032146 | 1.555 | 1076.6 | 1075.045
156 | 0.094428 | 33.57 | 62.418 | 0.00032158 | 1.5651 | 1076.6 |  | 156 | 33.57 | 0.094428 | 62.418 | 0.00032158 | 1.5651 | 1076.6 | 1075.0349
157 | 0.094466 | 33.58 | 62.418 | 0.0003217 | 1.5751 | 1076.6 |  | 157 | 33.58 | 0.094466 | 62.418 | 0.0003217 | 1.5751 | 1076.6 | 1075.0249
158 | 0.094504 | 33.59 | 62.418 | 0.00032182 | 1.5852 | 1076.6 |  | 158 | 33.59 | 0.094504 | 62.418 | 0.00032182 | 1.5852 | 1076.6 | 1075.0148
159 | 0.094542 | 33.6 | 62.418 | 0.00032195 | 1.5953 | 1076.6 |  | 159 | 33.6 | 0.094542 | 62.418 | 0.00032195 | 1.5953 | 1076.6 | 1075.0047
160 | 0.09458 | 33.61 | 62.418 | 0.00032207 | 1.6054 | 1076.6 |  | 160 | 33.61 | 0.09458 | 62.418 | 0.00032207 | 1.6054 | 1076.6 | 1074.9946
161 | 0.094618 | 33.62 | 62.418 | 0.00032219 | 1.6155 | 1076.6 |  | 161 | 33.62 | 0.094618 | 62.418 | 0.00032219 | 1.6155 | 1076.6 | 1074.9845
162 | 0.094655 | 33.63 | 62.418 | 0.00032231 | 1.6255 | 1076.6 |  | 162 | 33.63 | 0.094655 | 62.418 | 0.00032231 | 1.6255 | 1076.6 | 1074.9745
163 | 0.094693 | 33.64 | 62.418 | 0.00032244 | 1.6356 | 1076.6 |  | 163 | 33.64 | 0.094693 | 62.418 | 0.00032244 | 1.6356 | 1076.6 | 1074.9644
164 | 0.094731 | 33.65 | 62.418 | 0.00032256 | 1.6457 | 1076.6 |  | 164 | 33.65 | 0.094731 | 62.418 | 0.00032256 | 1.6457 | 1076.6 | 1074.9543
165 | 0.094769 | 33.66 | 62.418 | 0.00032268 | 1.6558 | 1076.6 |  | 165 | 33.66 | 0.094769 | 62.418 | 0.00032268 | 1.6558 | 1076.6 | 1074.9442
166 | 0.094807 | 33.67 | 62.418 | 0.0003228 | 1.6658 | 1076.6 |  | 166 | 33.67 | 0.094807 | 62.418 | 0.0003228 | 1.6658 | 1076.6 | 1074.9342
167 | 0.094845 | 33.68 | 62.418 | 0.00032293 | 1.6759 | 1076.6 |  | 167 | 33.68 | 0.094845 | 62.418 | 0.00032293 | 1.6759 | 1076.6 | 1074.9241
168 | 0.094883 | 33.69 | 62.418 | 0.00032305 | 1.686 | 1076.7 |  | 168 | 33.69 | 0.094883 | 62.418 | 0.00032305 | 1.686 | 1076.7 | 1075.014
169 | 0.094921 | 33.7 | 62.418 | 0.00032317 | 1.6961 | 1076.7 |  | 169 | 33.7 | 0.094921 | 62.418 | 0.00032317 | 1.6961 | 1076.7 | 1075.0039
170 | 0.094959 | 33.71 | 62.418 | 0.0003233 | 1.7062 | 1076.7 |  | 170 | 33.71 | 0.094959 | 62.418 | 0.0003233 | 1.7062 | 1076.7 | 1074.9938
171 | 0.094997 | 33.72 | 62.419 | 0.00032342 | 1.7162 | 1076.7 |  | 171 | 33.72 | 0.094997 | 62.419 | 0.00032342 | 1.7162 | 1076.7 | 1074.9838
172 | 0.095035 | 33.73 | 62.419 | 0.00032354 | 1.7263 | 1076.7 |  | 172 | 33.73 | 0.095035 | 62.419 | 0.00032354 | 1.7263 | 1076.7 | 1074.9737
173 | 0.095073 | 33.74 | 62.419 | 0.00032366 | 1.7364 | 1076.7 |  | 173 | 33.74 | 0.095073 | 62.419 | 0.00032366 | 1.7364 | 1076.7 | 1074.9636
174 | 0.095112 | 33.75 | 62.419 | 0.00032379 | 1.7465 | 1076.7 |  | 174 | 33.75 | 0.095112 | 62.419 | 0.00032379 | 1.7465 | 1076.7 | 1074.9535
175 | 0.09515 | 33.76 | 62.419 | 0.00032391 | 1.7566 | 1076.7 |  | 175 | 33.76 | 0.09515 | 62.419 | 0.00032391 | 1.7566 | 1076.7 | 1074.9434
176 | 0.095188 | 33.77 | 62.419 | 0.00032403 | 1.7666 | 1076.7 |  | 176 | 33.77 | 0.095188 | 62.419 | 0.00032403 | 1.7666 | 1076.7 | 1074.9334
177 | 0.095226 | 33.78 | 62.419 | 0.00032416 | 1.7767 | 1076.7 |  | 177 | 33.78 | 0.095226 | 62.419 | 0.00032416 | 1.7767 | 1076.7 | 1074.9233
178 | 0.095264 | 33.79 | 62.419 | 0.00032428 | 1.7868 | 1076.7 |  | 178 | 33.79 | 0.095264 | 62.419 | 0.00032428 | 1.7868 | 1076.7 | 1074.9132
179 | 0.095302 | 33.8 | 62.419 | 0.0003244 | 1.7969 | 1076.7 |  | 179 | 33.8 | 0.095302 | 62.419 | 0.0003244 | 1.7969 | 1076.7 | 1074.9031
180 | 0.09534 | 33.81 | 62.419 | 0.00032453 | 1.8069 | 1076.7 |  | 180 | 33.81 | 0.09534 | 62.419 | 0.00032453 | 1.8069 | 1076.7 | 1074.8931
181 | 0.095379 | 33.82 | 62.419 | 0.00032465 | 1.817 | 1076.7 |  | 181 | 33.82 | 0.095379 | 62.419 | 0.00032465 | 1.817 | 1076.7 | 1074.883
182 | 0.095417 | 33.83 | 62.419 | 0.00032477 | 1.8271 | 1076.7 |  | 182 | 33.83 | 0.095417 | 62.419 | 0.00032477 | 1.8271 | 1076.7 | 1074.8729
183 | 0.095455 | 33.84 | 62.419 | 0.0003249 | 1.8372 | 1076.7 |  | 183 | 33.84 | 0.095455 | 62.419 | 0.0003249 | 1.8372 | 1076.7 | 1074.8628
184 | 0.095493 | 33.85 | 62.419 | 0.00032502 | 1.8473 | 1076.7 |  | 184 | 33.85 | 0.095493 | 62.419 | 0.00032502 | 1.8473 | 1076.7 | 1074.8527
185 | 0.095531 | 33.86 | 62.419 | 0.00032515 | 1.8573 | 1076.7 |  | 185 | 33.86 | 0.095531 | 62.419 | 0.00032515 | 1.8573 | 1076.7 | 1074.8427
186 | 0.09557 | 33.87 | 62.419 | 0.00032527 | 1.8674 | 1076.7 |  | 186 | 33.87 | 0.09557 | 62.419 | 0.00032527 | 1.8674 | 1076.7 | 1074.8326
187 | 0.095608 | 33.88 | 62.419 | 0.00032539 | 1.8775 | 1076.7 |  | 187 | 33.88 | 0.095608 | 62.419 | 0.00032539 | 1.8775 | 1076.7 | 1074.8225
188 | 0.095646 | 33.89 | 62.419 | 0.00032552 | 1.8876 | 1076.7 |  | 188 | 33.89 | 0.095646 | 62.419 | 0.00032552 | 1.8876 | 1076.7 | 1074.8124
189 | 0.095684 | 33.9 | 62.419 | 0.00032564 | 1.8976 | 1076.7 |  | 189 | 33.9 | 0.095684 | 62.419 | 0.00032564 | 1.8976 | 1076.7 | 1074.8024
190 | 0.095723 | 33.91 | 62.419 | 0.00032576 | 1.9077 | 1076.7 |  | 190 | 33.91 | 0.095723 | 62.419 | 0.00032576 | 1.9077 | 1076.7 | 1074.7923
191 | 0.095761 | 33.92 | 62.419 | 0.00032589 | 1.9178 | 1076.8 |  | 191 | 33.92 | 0.095761 | 62.419 | 0.00032589 | 1.9178 | 1076.8 | 1074.8822
192 | 0.095799 | 33.93 | 62.419 | 0.00032601 | 1.9279 | 1076.8 |  | 192 | 33.93 | 0.095799 | 62.419 | 0.00032601 | 1.9279 | 1076.8 | 1074.8721
193 | 0.095838 | 33.94 | 62.419 | 0.00032614 | 1.938 | 1076.8 |  | 193 | 33.94 | 0.095838 | 62.419 | 0.00032614 | 1.938 | 1076.8 | 1074.862
194 | 0.095876 | 33.95 | 62.419 | 0.00032626 | 1.948 | 1076.8 |  | 194 | 33.95 | 0.095876 | 62.419 | 0.00032626 | 1.948 | 1076.8 | 1074.852
195 | 0.095915 | 33.96 | 62.419 | 0.00032638 | 1.9581 | 1076.8 |  | 195 | 33.96 | 0.095915 | 62.419 | 0.00032638 | 1.9581 | 1076.8 | 1074.8419
196 | 0.095953 | 33.97 | 62.419 | 0.00032651 | 1.9682 | 1076.8 |  | 196 | 33.97 | 0.095953 | 62.419 | 0.00032651 | 1.9682 | 1076.8 | 1074.8318
197 | 0.095991 | 33.98 | 62.419 | 0.00032663 | 1.9783 | 1076.8 |  | 197 | 33.98 | 0.095991 | 62.419 | 0.00032663 | 1.9783 | 1076.8 | 1074.8217
198 | 0.09603 | 33.99 | 62.419 | 0.00032676 | 1.9883 | 1076.8 |  | 198 | 33.99 | 0.09603 | 62.419 | 0.00032676 | 1.9883 | 1076.8 | 1074.8117
199 | 0.096068 | 34 | 62.419 | 0.00032688 | 1.9984 | 1076.8 |  | 199 | 34 | 0.096068 | 62.419 | 0.00032688 | 1.9984 | 1076.8 | 1074.8016
200 | 0.096107 | 34.01 | 62.419 | 0.000327 | 2.0085 | 1076.8 |  | 200 | 34.01 | 0.096107 | 62.419 | 0.000327 | 2.0085 | 1076.8 | 1074.7915
201 | 0.096145 | 34.02 | 62.419 | 0.00032713 | 2.0186 | 1076.8 |  | 201 | 34.02 | 0.096145 | 62.419 | 0.00032713 | 2.0186 | 1076.8 | 1074.7814
202 | 0.096184 | 34.03 | 62.419 | 0.00032725 | 2.0286 | 1076.8 |  | 202 | 34.03 | 0.096184 | 62.419 | 0.00032725 | 2.0286 | 1076.8 | 1074.7714
203 | 0.096222 | 34.04 | 62.419 | 0.00032738 | 2.0387 | 1076.8 |  | 203 | 34.04 | 0.096222 | 62.419 | 0.00032738 | 2.0387 | 1076.8 | 1074.7613
204 | 0.09626 | 34.05 | 62.419 | 0.0003275 | 2.0488 | 1076.8 |  | 204 | 34.05 | 0.09626 | 62.419 | 0.0003275 | 2.0488 | 1076.8 | 1074.7512
205 | 0.096299 | 34.06 | 62.419 | 0.00032763 | 2.0589 | 1076.8 |  | 205 | 34.06 | 0.096299 | 62.419 | 0.00032763 | 2.0589 | 1076.8 | 1074.7411
206 | 0.096338 | 34.07 | 62.419 | 0.00032775 | 2.069 | 1076.8 |  | 206 | 34.07 | 0.096338 | 62.419 | 0.00032775 | 2.069 | 1076.8 | 1074.731
207 | 0.096376 | 34.08 | 62.419 | 0.00032787 | 2.079 | 1076.8 |  | 207 | 34.08 | 0.096376 | 62.419 | 0.00032787 | 2.079 | 1076.8 | 1074.721
208 | 0.096415 | 34.09 | 62.419 | 0.000328 | 2.0891 | 1076.8 |  | 208 | 34.09 | 0.096415 | 62.419 | 0.000328 | 2.0891 | 1076.8 | 1074.7109
209 | 0.096453 | 34.1 | 62.419 | 0.00032812 | 2.0992 | 1076.8 |  | 209 | 34.1 | 0.096453 | 62.419 | 0.00032812 | 2.0992 | 1076.8 | 1074.7008
210 | 0.096492 | 34.11 | 62.419 | 0.00032825 | 2.1093 | 1076.8 |  | 210 | 34.11 | 0.096492 | 62.419 | 0.00032825 | 2.1093 | 1076.8 | 1074.6907
211 | 0.09653 | 34.12 | 62.419 | 0.00032837 | 2.1193 | 1076.8 |  | 211 | 34.12 | 0.09653 | 62.419 | 0.00032837 | 2.1193 | 1076.8 | 1074.6807
212 | 0.096569 | 34.13 | 62.419 | 0.0003285 | 2.1294 | 1076.8 |  | 212 | 34.13 | 0.096569 | 62.419 | 0.0003285 | 2.1294 | 1076.8 | 1074.6706
213 | 0.096608 | 34.14 | 62.419 | 0.00032862 | 2.1395 | 1076.8 |  | 213 | 34.14 | 0.096608 | 62.419 | 0.00032862 | 2.1395 | 1076.8 | 1074.6605
214 | 0.096646 | 34.15 | 62.419 | 0.00032875 | 2.1496 | 1076.9 |  | 214 | 34.15 | 0.096646 | 62.419 | 0.00032875 | 2.1496 | 1076.9 | 1074.7504
215 | 0.096685 | 34.16 | 62.419 | 0.00032887 | 2.1596 | 1076.9 |  | 215 | 34.16 | 0.096685 | 62.419 | 0.00032887 | 2.1596 | 1076.9 | 1074.7404
216 | 0.096723 | 34.17 | 62.419 | 0.000329 | 2.1697 | 1076.9 |  | 216 | 34.17 | 0.096723 | 62.419 | 0.000329 | 2.1697 | 1076.9 | 1074.7303
217 | 0.096762 | 34.18 | 62.419 | 0.00032912 | 2.1798 | 1076.9 |  | 217 | 34.18 | 0.096762 | 62.419 | 0.00032912 | 2.1798 | 1076.9 | 1074.7202
218 | 0.096801 | 34.19 | 62.419 | 0.00032925 | 2.1899 | 1076.9 |  | 218 | 34.19 | 0.096801 | 62.419 | 0.00032925 | 2.1899 | 1076.9 | 1074.7101
219 | 0.09684 | 34.2 | 62.419 | 0.00032937 | 2.2 | 1076.9 |  | 219 | 34.2 | 0.09684 | 62.419 | 0.00032937 | 2.2 | 1076.9 | 1074.7
220 | 0.096878 | 34.21 | 62.419 | 0.0003295 | 2.21 | 1076.9 |  | 220 | 34.21 | 0.096878 | 62.419 | 0.0003295 | 2.21 | 1076.9 | 1074.69
221 | 0.096917 | 34.22 | 62.419 | 0.00032962 | 2.2201 | 1076.9 |  | 221 | 34.22 | 0.096917 | 62.419 | 0.00032962 | 2.2201 | 1076.9 | 1074.6799
222 | 0.096956 | 34.23 | 62.419 | 0.00032975 | 2.2302 | 1076.9 |  | 222 | 34.23 | 0.096956 | 62.419 | 0.00032975 | 2.2302 | 1076.9 | 1074.6698
223 | 0.096994 | 34.24 | 62.419 | 0.00032987 | 2.2403 | 1076.9 |  | 223 | 34.24 | 0.096994 | 62.419 | 0.00032987 | 2.2403 | 1076.9 | 1074.6597
224 | 0.097033 | 34.25 | 62.419 | 0.00033 | 2.2503 | 1076.9 |  | 224 | 34.25 | 0.097033 | 62.419 | 0.00033 | 2.2503 | 1076.9 | 1074.6497
225 | 0.097072 | 34.26 | 62.419 | 0.00033012 | 2.2604 | 1076.9 |  | 225 | 34.26 | 0.097072 | 62.419 | 0.00033012 | 2.2604 | 1076.9 | 1074.6396
226 | 0.097111 | 34.27 | 62.419 | 0.00033025 | 2.2705 | 1076.9 |  | 226 | 34.27 | 0.097111 | 62.419 | 0.00033025 | 2.2705 | 1076.9 | 1074.6295
227 | 0.09715 | 34.28 | 62.419 | 0.00033037 | 2.2806 | 1076.9 |  | 227 | 34.28 | 0.09715 | 62.419 | 0.00033037 | 2.2806 | 1076.9 | 1074.6194
228 | 0.097188 | 34.29 | 62.419 | 0.0003305 | 2.2906 | 1076.9 |  | 228 | 34.29 | 0.097188 | 62.419 | 0.0003305 | 2.2906 | 1076.9 | 1074.6094
229 | 0.097227 | 34.3 | 62.419 | 0.00033062 | 2.3007 | 1076.9 |  | 229 | 34.3 | 0.097227 | 62.419 | 0.00033062 | 2.3007 | 1076.9 | 1074.5993
230 | 0.097266 | 34.31 | 62.42 | 0.00033075 | 2.3108 | 1076.9 |  | 230 | 34.31 | 0.097266 | 62.42 | 0.00033075 | 2.3108 | 1076.9 | 1074.5892
231 | 0.097305 | 34.32 | 62.42 | 0.00033088 | 2.3209 | 1076.9 |  | 231 | 34.32 | 0.097305 | 62.42 | 0.00033088 | 2.3209 | 1076.9 | 1074.5791
232 | 0.097344 | 34.33 | 62.42 | 0.000331 | 2.3309 | 1076.9 |  | 232 | 34.33 | 0.097344 | 62.42 | 0.000331 | 2.3309 | 1076.9 | 1074.5691
233 | 0.097383 | 34.34 | 62.42 | 0.00033113 | 2.341 | 1076.9 |  | 233 | 34.34 | 0.097383 | 62.42 | 0.00033113 | 2.341 | 1076.9 | 1074.559
234 | 0.097422 | 34.35 | 62.42 | 0.00033125 | 2.3511 | 1076.9 |  | 234 | 34.35 | 0.097422 | 62.42 | 0.00033125 | 2.3511 | 1076.9 | 1074.5489
235 | 0.097461 | 34.36 | 62.42 | 0.00033138 | 2.3612 | 1076.9 |  | 235 | 34.36 | 0.097461 | 62.42 | 0.00033138 | 2.3612 | 1076.9 | 1074.5388
236 | 0.0975 | 34.37 | 62.42 | 0.0003315 | 2.3712 | 1077 |  | 236 | 34.37 | 0.0975 | 62.42 | 0.0003315 | 2.3712 | 1077 | 1074.6288
237 | 0.097538 | 34.38 | 62.42 | 0.00033163 | 2.3813 | 1077 |  | 237 | 34.38 | 0.097538 | 62.42 | 0.00033163 | 2.3813 | 1077 | 1074.6187
238 | 0.097577 | 34.39 | 62.42 | 0.00033176 | 2.3914 | 1077 |  | 238 | 34.39 | 0.097577 | 62.42 | 0.00033176 | 2.3914 | 1077 | 1074.6086
239 | 0.097616 | 34.4 | 62.42 | 0.00033188 | 2.4015 | 1077 |  | 239 | 34.4 | 0.097616 | 62.42 | 0.00033188 | 2.4015 | 1077 | 1074.5985
240 | 0.097655 | 34.41 | 62.42 | 0.00033201 | 2.4115 | 1077 |  | 240 | 34.41 | 0.097655 | 62.42 | 0.00033201 | 2.4115 | 1077 | 1074.5885
241 | 0.097694 | 34.42 | 62.42 | 0.00033213 | 2.4216 | 1077 |  | 241 | 34.42 | 0.097694 | 62.42 | 0.00033213 | 2.4216 | 1077 | 1074.5784
242 | 0.097733 | 34.43 | 62.42 | 0.00033226 | 2.4317 | 1077 |  | 242 | 34.43 | 0.097733 | 62.42 | 0.00033226 | 2.4317 | 1077 | 1074.5683
243 | 0.097772 | 34.44 | 62.42 | 0.00033238 | 2.4418 | 1077 |  | 243 | 34.44 | 0.097772 | 62.42 | 0.00033238 | 2.4418 | 1077 | 1074.5582
244 | 0.097811 | 34.45 | 62.42 | 0.00033251 | 2.4518 | 1077 |  | 244 | 34.45 | 0.097811 | 62.42 | 0.00033251 | 2.4518 | 1077 | 1074.5482
245 | 0.09785 | 34.46 | 62.42 | 0.00033264 | 2.4619 | 1077 |  | 245 | 34.46 | 0.09785 | 62.42 | 0.00033264 | 2.4619 | 1077 | 1074.5381
246 | 0.09789 | 34.47 | 62.42 | 0.00033276 | 2.472 | 1077 |  | 246 | 34.47 | 0.09789 | 62.42 | 0.00033276 | 2.472 | 1077 | 1074.528
247 | 0.097929 | 34.48 | 62.42 | 0.00033289 | 2.4821 | 1077 |  | 247 | 34.48 | 0.097929 | 62.42 | 0.00033289 | 2.4821 | 1077 | 1074.5179
248 | 0.097968 | 34.49 | 62.42 | 0.00033302 | 2.4921 | 1077 |  | 248 | 34.49 | 0.097968 | 62.42 | 0.00033302 | 2.4921 | 1077 | 1074.5079
249 | 0.098007 | 34.5 | 62.42 | 0.00033314 | 2.5022 | 1077 |  | 249 | 34.5 | 0.098007 | 62.42 | 0.00033314 | 2.5022 | 1077 | 1074.4978
250 | 0.098046 | 34.51 | 62.42 | 0.00033327 | 2.5123 | 1077 |  | 250 | 34.51 | 0.098046 | 62.42 | 0.00033327 | 2.5123 | 1077 | 1074.4877
251 | 0.098085 | 34.52 | 62.42 | 0.00033339 | 2.5224 | 1077 |  | 251 | 34.52 | 0.098085 | 62.42 | 0.00033339 | 2.5224 | 1077 | 1074.4776
252 | 0.098124 | 34.53 | 62.42 | 0.00033352 | 2.5324 | 1077 |  | 252 | 34.53 | 0.098124 | 62.42 | 0.00033352 | 2.5324 | 1077 | 1074.4676
253 | 0.098163 | 34.54 | 62.42 | 0.00033365 | 2.5425 | 1077 |  | 253 | 34.54 | 0.098163 | 62.42 | 0.00033365 | 2.5425 | 1077 | 1074.4575
254 | 0.098203 | 34.55 | 62.42 | 0.00033377 | 2.5526 | 1077 |  | 254 | 34.55 | 0.098203 | 62.42 | 0.00033377 | 2.5526 | 1077 | 1074.4474
255 | 0.098242 | 34.56 | 62.42 | 0.0003339 | 2.5627 | 1077 |  | 255 | 34.56 | 0.098242 | 62.42 | 0.0003339 | 2.5627 | 1077 | 1074.4373
256 | 0.098281 | 34.57 | 62.42 | 0.00033403 | 2.5727 | 1077 |  | 256 | 34.57 | 0.098281 | 62.42 | 0.00033403 | 2.5727 | 1077 | 1074.4273
257 | 0.09832 | 34.58 | 62.42 | 0.00033415 | 2.5828 | 1077 |  | 257 | 34.58 | 0.09832 | 62.42 | 0.00033415 | 2.5828 | 1077 | 1074.4172
258 | 0.09836 | 34.59 | 62.42 | 0.00033428 | 2.5929 | 1077 |  | 258 | 34.59 | 0.09836 | 62.42 | 0.00033428 | 2.5929 | 1077 | 1074.4071
259 | 0.098399 | 34.6 | 62.42 | 0.00033441 | 2.603 | 1077.1 |  | 259 | 34.6 | 0.098399 | 62.42 | 0.00033441 | 2.603 | 1077.1 | 1074.497
260 | 0.098438 | 34.61 | 62.42 | 0.00033453 | 2.613 | 1077.1 |  | 260 | 34.61 | 0.098438 | 62.42 | 0.00033453 | 2.613 | 1077.1 | 1074.487
261 | 0.098477 | 34.62 | 62.42 | 0.00033466 | 2.6231 | 1077.1 |  | 261 | 34.62 | 0.098477 | 62.42 | 0.00033466 | 2.6231 | 1077.1 | 1074.4769
262 | 0.098517 | 34.63 | 62.42 | 0.00033479 | 2.6332 | 1077.1 |  | 262 | 34.63 | 0.098517 | 62.42 | 0.00033479 | 2.6332 | 1077.1 | 1074.4668
263 | 0.098556 | 34.64 | 62.42 | 0.00033491 | 2.6433 | 1077.1 |  | 263 | 34.64 | 0.098556 | 62.42 | 0.00033491 | 2.6433 | 1077.1 | 1074.4567
264 | 0.098595 | 34.65 | 62.42 | 0.00033504 | 2.6533 | 1077.1 |  | 264 | 34.65 | 0.098595 | 62.42 | 0.00033504 | 2.6533 | 1077.1 | 1074.4467
265 | 0.098635 | 34.66 | 62.42 | 0.00033517 | 2.6634 | 1077.1 |  | 265 | 34.66 | 0.098635 | 62.42 | 0.00033517 | 2.6634 | 1077.1 | 1074.4366
266 | 0.098674 | 34.67 | 62.42 | 0.00033529 | 2.6735 | 1077.1 |  | 266 | 34.67 | 0.098674 | 62.42 | 0.00033529 | 2.6735 | 1077.1 | 1074.4265
267 | 0.098713 | 34.68 | 62.42 | 0.00033542 | 2.6836 | 1077.1 |  | 267 | 34.68 | 0.098713 | 62.42 | 0.00033542 | 2.6836 | 1077.1 | 1074.4164
268 | 0.098753 | 34.69 | 62.42 | 0.00033555 | 2.6936 | 1077.1 |  | 268 | 34.69 | 0.098753 | 62.42 | 0.00033555 | 2.6936 | 1077.1 | 1074.4064
269 | 0.098792 | 34.7 | 62.42 | 0.00033568 | 2.7037 | 1077.1 |  | 269 | 34.7 | 0.098792 | 62.42 | 0.00033568 | 2.7037 | 1077.1 | 1074.3963
270 | 0.098831 | 34.71 | 62.42 | 0.0003358 | 2.7138 | 1077.1 |  | 270 | 34.71 | 0.098831 | 62.42 | 0.0003358 | 2.7138 | 1077.1 | 1074.3862
271 | 0.098871 | 34.72 | 62.42 | 0.00033593 | 2.7239 | 1077.1 |  | 271 | 34.72 | 0.098871 | 62.42 | 0.00033593 | 2.7239 | 1077.1 | 1074.3761
272 | 0.09891 | 34.73 | 62.42 | 0.00033606 | 2.7339 | 1077.1 |  | 272 | 34.73 | 0.09891 | 62.42 | 0.00033606 | 2.7339 | 1077.1 | 1074.3661
273 | 0.09895 | 34.74 | 62.42 | 0.00033618 | 2.744 | 1077.1 |  | 273 | 34.74 | 0.09895 | 62.42 | 0.00033618 | 2.744 | 1077.1 | 1074.356
274 | 0.098989 | 34.75 | 62.42 | 0.00033631 | 2.7541 | 1077.1 |  | 274 | 34.75 | 0.098989 | 62.42 | 0.00033631 | 2.7541 | 1077.1 | 1074.3459
275 | 0.099029 | 34.76 | 62.42 | 0.00033644 | 2.7642 | 1077.1 |  | 275 | 34.76 | 0.099029 | 62.42 | 0.00033644 | 2.7642 | 1077.1 | 1074.3358
276 | 0.099068 | 34.77 | 62.42 | 0.00033657 | 2.7742 | 1077.1 |  | 276 | 34.77 | 0.099068 | 62.42 | 0.00033657 | 2.7742 | 1077.1 | 1074.3258
277 | 0.099108 | 34.78 | 62.42 | 0.00033669 | 2.7843 | 1077.1 |  | 277 | 34.78 | 0.099108 | 62.42 | 0.00033669 | 2.7843 | 1077.1 | 1074.3157
278 | 0.099147 | 34.79 | 62.42 | 0.00033682 | 2.7944 | 1077.1 |  | 278 | 34.79 | 0.099147 | 62.42 | 0.00033682 | 2.7944 | 1077.1 | 1074.3056
279 | 0.099187 | 34.8 | 62.42 | 0.00033695 | 2.8045 | 1077.1 |  | 279 | 34.8 | 0.099187 | 62.42 | 0.00033695 | 2.8045 | 1077.1 | 1074.2955
280 | 0.099226 | 34.81 | 62.42 | 0.00033708 | 2.8145 | 1077.1 |  | 280 | 34.81 | 0.099226 | 62.42 | 0.00033708 | 2.8145 | 1077.1 | 1074.2855
281 | 0.099266 | 34.82 | 62.42 | 0.0003372 | 2.8246 | 1077.1 |  | 281 | 34.82 | 0.099266 | 62.42 | 0.0003372 | 2.8246 | 1077.1 | 1074.2754
282 | 0.099305 | 34.83 | 62.42 | 0.00033733 | 2.8347 | 1077.2 |  | 282 | 34.83 | 0.099305 | 62.42 | 0.00033733 | 2.8347 | 1077.2 | 1074.3653
283 | 0.099345 | 34.84 | 62.42 | 0.00033746 | 2.8448 | 1077.2 |  | 283 | 34.84 | 0.099345 | 62.42 | 0.00033746 | 2.8448 | 1077.2 | 1074.3552
284 | 0.099385 | 34.85 | 62.42 | 0.00033759 | 2.8548 | 1077.2 |  | 284 | 34.85 | 0.099385 | 62.42 | 0.00033759 | 2.8548 | 1077.2 | 1074.3452
285 | 0.099424 | 34.86 | 62.42 | 0.00033772 | 2.8649 | 1077.2 |  | 285 | 34.86 | 0.099424 | 62.42 | 0.00033772 | 2.8649 | 1077.2 | 1074.3351
286 | 0.099464 | 34.87 | 62.42 | 0.00033784 | 2.875 | 1077.2 |  | 286 | 34.87 | 0.099464 | 62.42 | 0.00033784 | 2.875 | 1077.2 | 1074.325
287 | 0.099503 | 34.88 | 62.42 | 0.00033797 | 2.885 | 1077.2 |  | 287 | 34.88 | 0.099503 | 62.42 | 0.00033797 | 2.885 | 1077.2 | 1074.315
288 | 0.099543 | 34.89 | 62.42 | 0.0003381 | 2.8951 | 1077.2 |  | 288 | 34.89 | 0.099543 | 62.42 | 0.0003381 | 2.8951 | 1077.2 | 1074.3049
289 | 0.099583 | 34.9 | 62.42 | 0.00033823 | 2.9052 | 1077.2 |  | 289 | 34.9 | 0.099583 | 62.42 | 0.00033823 | 2.9052 | 1077.2 | 1074.2948
290 | 0.099622 | 34.91 | 62.42 | 0.00033835 | 2.9153 | 1077.2 |  | 290 | 34.91 | 0.099622 | 62.42 | 0.00033835 | 2.9153 | 1077.2 | 1074.2847
291 | 0.099662 | 34.92 | 62.42 | 0.00033848 | 2.9253 | 1077.2 |  | 291 | 34.92 | 0.099662 | 62.42 | 0.00033848 | 2.9253 | 1077.2 | 1074.2747
292 | 0.099702 | 34.93 | 62.42 | 0.00033861 | 2.9354 | 1077.2 |  | 292 | 34.93 | 0.099702 | 62.42 | 0.00033861 | 2.9354 | 1077.2 | 1074.2646
293 | 0.099742 | 34.94 | 62.42 | 0.00033874 | 2.9455 | 1077.2 |  | 293 | 34.94 | 0.099742 | 62.42 | 0.00033874 | 2.9455 | 1077.2 | 1074.2545
294 | 0.099781 | 34.95 | 62.42 | 0.00033887 | 2.9556 | 1077.2 |  | 294 | 34.95 | 0.099781 | 62.42 | 0.00033887 | 2.9556 | 1077.2 | 1074.2444
295 | 0.099821 | 34.96 | 62.42 | 0.000339 | 2.9656 | 1077.2 |  | 295 | 34.96 | 0.099821 | 62.42 | 0.000339 | 2.9656 | 1077.2 | 1074.2344
296 | 0.099861 | 34.97 | 62.42 | 0.00033912 | 2.9757 | 1077.2 |  | 296 | 34.97 | 0.099861 | 62.42 | 0.00033912 | 2.9757 | 1077.2 | 1074.2243
297 | 0.099901 | 34.98 | 62.42 | 0.00033925 | 2.9858 | 1077.2 |  | 297 | 34.98 | 0.099901 | 62.42 | 0.00033925 | 2.9858 | 1077.2 | 1074.2142
298 | 0.09994 | 34.99 | 62.42 | 0.00033938 | 2.9959 | 1077.2 |  | 298 | 34.99 | 0.09994 | 62.42 | 0.00033938 | 2.9959 | 1077.2 | 1074.2041
299 | 0.09998 | 35 | 62.421 | 0.00033951 | 3.0059 | 1077.2 |  | 299 | 35 | 0.09998 | 62.421 | 0.00033951 | 3.0059 | 1077.2 | 1074.1941
300 | 0.10002 | 35.01 | 62.421 | 0.00033964 | 3.016 | 1077.2 |  | 300 | 35.01 | 0.10002 | 62.421 | 0.00033964 | 3.016 | 1077.2 | 1074.184
301 | 0.10006 | 35.02 | 62.421 | 0.00033977 | 3.0261 | 1077.2 |  | 301 | 35.02 | 0.10006 | 62.421 | 0.00033977 | 3.0261 | 1077.2 | 1074.1739
302 | 0.1001 | 35.03 | 62.421 | 0.00033989 | 3.0361 | 1077.2 |  | 302 | 35.03 | 0.1001 | 62.421 | 0.00033989 | 3.0361 | 1077.2 | 1074.1639
303 | 0.10014 | 35.04 | 62.421 | 0.00034002 | 3.0462 | 1077.2 |  | 303 | 35.04 | 0.10014 | 62.421 | 0.00034002 | 3.0462 | 1077.2 | 1074.1538
304 | 0.10018 | 35.05 | 62.421 | 0.00034015 | 3.0563 | 1077.2 |  | 304 | 35.05 | 0.10018 | 62.421 | 0.00034015 | 3.0563 | 1077.2 | 1074.1437
305 | 0.10022 | 35.06 | 62.421 | 0.00034028 | 3.0664 | 1077.3 |  | 305 | 35.06 | 0.10022 | 62.421 | 0.00034028 | 3.0664 | 1077.3 | 1074.2336
306 | 0.10026 | 35.07 | 62.421 | 0.00034041 | 3.0764 | 1077.3 |  | 306 | 35.07 | 0.10026 | 62.421 | 0.00034041 | 3.0764 | 1077.3 | 1074.2236
307 | 0.1003 | 35.08 | 62.421 | 0.00034054 | 3.0865 | 1077.3 |  | 307 | 35.08 | 0.1003 | 62.421 | 0.00034054 | 3.0865 | 1077.3 | 1074.2135
308 | 0.10034 | 35.09 | 62.421 | 0.00034067 | 3.0966 | 1077.3 |  | 308 | 35.09 | 0.10034 | 62.421 | 0.00034067 | 3.0966 | 1077.3 | 1074.2034
309 | 0.10038 | 35.1 | 62.421 | 0.00034079 | 3.1067 | 1077.3 |  | 309 | 35.1 | 0.10038 | 62.421 | 0.00034079 | 3.1067 | 1077.3 | 1074.1933
310 | 0.10042 | 35.11 | 62.421 | 0.00034092 | 3.1167 | 1077.3 |  | 310 | 35.11 | 0.10042 | 62.421 | 0.00034092 | 3.1167 | 1077.3 | 1074.1833
311 | 0.10046 | 35.12 | 62.421 | 0.00034105 | 3.1268 | 1077.3 |  | 311 | 35.12 | 0.10046 | 62.421 | 0.00034105 | 3.1268 | 1077.3 | 1074.1732
312 | 0.1005 | 35.13 | 62.421 | 0.00034118 | 3.1369 | 1077.3 |  | 312 | 35.13 | 0.1005 | 62.421 | 0.00034118 | 3.1369 | 1077.3 | 1074.1631
313 | 0.10054 | 35.14 | 62.421 | 0.00034131 | 3.1469 | 1077.3 |  | 313 | 35.14 | 0.10054 | 62.421 | 0.00034131 | 3.1469 | 1077.3 | 1074.1531
314 | 0.10058 | 35.15 | 62.421 | 0.00034144 | 3.157 | 1077.3 |  | 314 | 35.15 | 0.10058 | 62.421 | 0.00034144 | 3.157 | 1077.3 | 1074.143
315 | 0.10062 | 35.16 | 62.421 | 0.00034157 | 3.1671 | 1077.3 |  | 315 | 35.16 | 0.10062 | 62.421 | 0.00034157 | 3.1671 | 1077.3 | 1074.1329
316 | 0.10066 | 35.17 | 62.421 | 0.0003417 | 3.1772 | 1077.3 |  | 316 | 35.17 | 0.10066 | 62.421 | 0.0003417 | 3.1772 | 1077.3 | 1074.1228
317 | 0.1007 | 35.18 | 62.421 | 0.00034183 | 3.1872 | 1077.3 |  | 317 | 35.18 | 0.1007 | 62.421 | 0.00034183 | 3.1872 | 1077.3 | 1074.1128
318 | 0.10074 | 35.19 | 62.421 | 0.00034196 | 3.1973 | 1077.3 |  | 318 | 35.19 | 0.10074 | 62.421 | 0.00034196 | 3.1973 | 1077.3 | 1074.1027
319 | 0.10078 | 35.2 | 62.421 | 0.00034209 | 3.2074 | 1077.3 |  | 319 | 35.2 | 0.10078 | 62.421 | 0.00034209 | 3.2074 | 1077.3 | 1074.0926
320 | 0.10082 | 35.21 | 62.421 | 0.00034221 | 3.2174 | 1077.3 |  | 320 | 35.21 | 0.10082 | 62.421 | 0.00034221 | 3.2174 | 1077.3 | 1074.0826
321 | 0.10086 | 35.22 | 62.421 | 0.00034234 | 3.2275 | 1077.3 |  | 321 | 35.22 | 0.10086 | 62.421 | 0.00034234 | 3.2275 | 1077.3 | 1074.0725
322 | 0.1009 | 35.23 | 62.421 | 0.00034247 | 3.2376 | 1077.3 |  | 322 | 35.23 | 0.1009 | 62.421 | 0.00034247 | 3.2376 | 1077.3 | 1074.0624
323 | 0.10094 | 35.24 | 62.421 | 0.0003426 | 3.2477 | 1077.3 |  | 323 | 35.24 | 0.10094 | 62.421 | 0.0003426 | 3.2477 | 1077.3 | 1074.0523
324 | 0.10098 | 35.25 | 62.421 | 0.00034273 | 3.2577 | 1077.3 |  | 324 | 35.25 | 0.10098 | 62.421 | 0.00034273 | 3.2577 | 1077.3 | 1074.0423
325 | 0.10102 | 35.26 | 62.421 | 0.00034286 | 3.2678 | 1077.3 |  | 325 | 35.26 | 0.10102 | 62.421 | 0.00034286 | 3.2678 | 1077.3 | 1074.0322
326 | 0.10106 | 35.27 | 62.421 | 0.00034299 | 3.2779 | 1077.3 |  | 326 | 35.27 | 0.10106 | 62.421 | 0.00034299 | 3.2779 | 1077.3 | 1074.0221
327 | 0.1011 | 35.28 | 62.421 | 0.00034312 | 3.288 | 1077.3 |  | 327 | 35.28 | 0.1011 | 62.421 | 0.00034312 | 3.288 | 1077.3 | 1074.012
328 | 0.10114 | 35.29 | 62.421 | 0.00034325 | 3.298 | 1077.4 |  | 328 | 35.29 | 0.10114 | 62.421 | 0.00034325 | 3.298 | 1077.4 | 1074.102
329 | 0.10118 | 35.3 | 62.421 | 0.00034338 | 3.3081 | 1077.4 |  | 329 | 35.3 | 0.10118 | 62.421 | 0.00034338 | 3.3081 | 1077.4 | 1074.0919
330 | 0.10122 | 35.31 | 62.421 | 0.00034351 | 3.3182 | 1077.4 |  | 330 | 35.31 | 0.10122 | 62.421 | 0.00034351 | 3.3182 | 1077.4 | 1074.0818
331 | 0.10126 | 35.32 | 62.421 | 0.00034364 | 3.3282 | 1077.4 |  | 331 | 35.32 | 0.10126 | 62.421 | 0.00034364 | 3.3282 | 1077.4 | 1074.0718
332 | 0.1013 | 35.33 | 62.421 | 0.00034377 | 3.3383 | 1077.4 |  | 332 | 35.33 | 0.1013 | 62.421 | 0.00034377 | 3.3383 | 1077.4 | 1074.0617
333 | 0.10134 | 35.34 | 62.421 | 0.0003439 | 3.3484 | 1077.4 |  | 333 | 35.34 | 0.10134 | 62.421 | 0.0003439 | 3.3484 | 1077.4 | 1074.0516
334 | 0.10138 | 35.35 | 62.421 | 0.00034403 | 3.3585 | 1077.4 |  | 334 | 35.35 | 0.10138 | 62.421 | 0.00034403 | 3.3585 | 1077.4 | 1074.0415
335 | 0.10142 | 35.36 | 62.421 | 0.00034416 | 3.3685 | 1077.4 |  | 335 | 35.36 | 0.10142 | 62.421 | 0.00034416 | 3.3685 | 1077.4 | 1074.0315
336 | 0.10146 | 35.37 | 62.421 | 0.00034429 | 3.3786 | 1077.4 |  | 336 | 35.37 | 0.10146 | 62.421 | 0.00034429 | 3.3786 | 1077.4 | 1074.0214
337 | 0.1015 | 35.38 | 62.421 | 0.00034442 | 3.3887 | 1077.4 |  | 337 | 35.38 | 0.1015 | 62.421 | 0.00034442 | 3.3887 | 1077.4 | 1074.0113
338 | 0.10154 | 35.39 | 62.421 | 0.00034455 | 3.3987 | 1077.4 |  | 338 | 35.39 | 0.10154 | 62.421 | 0.00034455 | 3.3987 | 1077.4 | 1074.0013
339 | 0.10158 | 35.4 | 62.421 | 0.00034468 | 3.4088 | 1077.4 |  | 339 | 35.4 | 0.10158 | 62.421 | 0.00034468 | 3.4088 | 1077.4 | 1073.9912
340 | 0.10162 | 35.41 | 62.421 | 0.00034481 | 3.4189 | 1077.4 |  | 340 | 35.41 | 0.10162 | 62.421 | 0.00034481 | 3.4189 | 1077.4 | 1073.9811
341 | 0.10166 | 35.42 | 62.421 | 0.00034494 | 3.429 | 1077.4 |  | 341 | 35.42 | 0.10166 | 62.421 | 0.00034494 | 3.429 | 1077.4 | 1073.971
342 | 0.10171 | 35.43 | 62.421 | 0.00034507 | 3.439 | 1077.4 |  | 342 | 35.43 | 0.10171 | 62.421 | 0.00034507 | 3.439 | 1077.4 | 1073.961
343 | 0.10175 | 35.44 | 62.421 | 0.0003452 | 3.4491 | 1077.4 |  | 343 | 35.44 | 0.10175 | 62.421 | 0.0003452 | 3.4491 | 1077.4 | 1073.9509
344 | 0.10179 | 35.45 | 62.421 | 0.00034533 | 3.4592 | 1077.4 |  | 344 | 35.45 | 0.10179 | 62.421 | 0.00034533 | 3.4592 | 1077.4 | 1073.9408
345 | 0.10183 | 35.46 | 62.421 | 0.00034546 | 3.4692 | 1077.4 |  | 345 | 35.46 | 0.10183 | 62.421 | 0.00034546 | 3.4692 | 1077.4 | 1073.9308
346 | 0.10187 | 35.47 | 62.421 | 0.00034559 | 3.4793 | 1077.4 |  | 346 | 35.47 | 0.10187 | 62.421 | 0.00034559 | 3.4793 | 1077.4 | 1073.9207
347 | 0.10191 | 35.48 | 62.421 | 0.00034572 | 3.4894 | 1077.4 |  | 347 | 35.48 | 0.10191 | 62.421 | 0.00034572 | 3.4894 | 1077.4 | 1073.9106
348 | 0.10195 | 35.49 | 62.421 | 0.00034585 | 3.4995 | 1077.4 |  | 348 | 35.49 | 0.10195 | 62.421 | 0.00034585 | 3.4995 | 1077.4 | 1073.9005
349 | 0.10199 | 35.5 | 62.421 | 0.00034598 | 3.5095 | 1077.4 |  | 349 | 35.5 | 0.10199 | 62.421 | 0.00034598 | 3.5095 | 1077.4 | 1073.8905
350 | 0.10203 | 35.51 | 62.421 | 0.00034611 | 3.5196 | 1077.5 |  | 350 | 35.51 | 0.10203 | 62.421 | 0.00034611 | 3.5196 | 1077.5 | 1073.9804
351 | 0.10207 | 35.52 | 62.421 | 0.00034624 | 3.5297 | 1077.5 |  | 351 | 35.52 | 0.10207 | 62.421 | 0.00034624 | 3.5297 | 1077.5 | 1073.9703
352 | 0.10211 | 35.53 | 62.421 | 0.00034637 | 3.5397 | 1077.5 |  | 352 | 35.53 | 0.10211 | 62.421 | 0.00034637 | 3.5397 | 1077.5 | 1073.9603
353 | 0.10215 | 35.54 | 62.421 | 0.0003465 | 3.5498 | 1077.5 |  | 353 | 35.54 | 0.10215 | 62.421 | 0.0003465 | 3.5498 | 1077.5 | 1073.9502
354 | 0.10219 | 35.55 | 62.421 | 0.00034663 | 3.5599 | 1077.5 |  | 354 | 35.55 | 0.10219 | 62.421 | 0.00034663 | 3.5599 | 1077.5 | 1073.9401
355 | 0.10223 | 35.56 | 62.421 | 0.00034677 | 3.57 | 1077.5 |  | 355 | 35.56 | 0.10223 | 62.421 | 0.00034677 | 3.57 | 1077.5 | 1073.93
356 | 0.10227 | 35.57 | 62.421 | 0.0003469 | 3.58 | 1077.5 |  | 356 | 35.57 | 0.10227 | 62.421 | 0.0003469 | 3.58 | 1077.5 | 1073.92
357 | 0.10231 | 35.58 | 62.421 | 0.00034703 | 3.5901 | 1077.5 |  | 357 | 35.58 | 0.10231 | 62.421 | 0.00034703 | 3.5901 | 1077.5 | 1073.9099
358 | 0.10235 | 35.59 | 62.421 | 0.00034716 | 3.6002 | 1077.5 |  | 358 | 35.59 | 0.10235 | 62.421 | 0.00034716 | 3.6002 | 1077.5 | 1073.8998
359 | 0.10239 | 35.6 | 62.421 | 0.00034729 | 3.6102 | 1077.5 |  | 359 | 35.6 | 0.10239 | 62.421 | 0.00034729 | 3.6102 | 1077.5 | 1073.8898
360 | 0.10244 | 35.61 | 62.421 | 0.00034742 | 3.6203 | 1077.5 |  | 360 | 35.61 | 0.10244 | 62.421 | 0.00034742 | 3.6203 | 1077.5 | 1073.8797
361 | 0.10248 | 35.62 | 62.421 | 0.00034755 | 3.6304 | 1077.5 |  | 361 | 35.62 | 0.10248 | 62.421 | 0.00034755 | 3.6304 | 1077.5 | 1073.8696
362 | 0.10252 | 35.63 | 62.421 | 0.00034768 | 3.6404 | 1077.5 |  | 362 | 35.63 | 0.10252 | 62.421 | 0.00034768 | 3.6404 | 1077.5 | 1073.8596
363 | 0.10256 | 35.64 | 62.421 | 0.00034781 | 3.6505 | 1077.5 |  | 363 | 35.64 | 0.10256 | 62.421 | 0.00034781 | 3.6505 | 1077.5 | 1073.8495
364 | 0.1026 | 35.65 | 62.421 | 0.00034794 | 3.6606 | 1077.5 |  | 364 | 35.65 | 0.1026 | 62.421 | 0.00034794 | 3.6606 | 1077.5 | 1073.8394
365 | 0.10264 | 35.66 | 62.421 | 0.00034808 | 3.6707 | 1077.5 |  | 365 | 35.66 | 0.10264 | 62.421 | 0.00034808 | 3.6707 | 1077.5 | 1073.8293
366 | 0.10268 | 35.67 | 62.421 | 0.00034821 | 3.6807 | 1077.5 |  | 366 | 35.67 | 0.10268 | 62.421 | 0.00034821 | 3.6807 | 1077.5 | 1073.8193
367 | 0.10272 | 35.68 | 62.421 | 0.00034834 | 3.6908 | 1077.5 |  | 367 | 35.68 | 0.10272 | 62.421 | 0.00034834 | 3.6908 | 1077.5 | 1073.8092
368 | 0.10276 | 35.69 | 62.421 | 0.00034847 | 3.7009 | 1077.5 |  | 368 | 35.69 | 0.10276 | 62.421 | 0.00034847 | 3.7009 | 1077.5 | 1073.7991
369 | 0.1028 | 35.7 | 62.421 | 0.0003486 | 3.7109 | 1077.5 |  | 369 | 35.7 | 0.1028 | 62.421 | 0.0003486 | 3.7109 | 1077.5 | 1073.7891
370 | 0.10284 | 35.71 | 62.421 | 0.00034873 | 3.721 | 1077.5 |  | 370 | 35.71 | 0.10284 | 62.421 | 0.00034873 | 3.721 | 1077.5 | 1073.779
371 | 0.10288 | 35.72 | 62.421 | 0.00034886 | 3.7311 | 1077.5 |  | 371 | 35.72 | 0.10288 | 62.421 | 0.00034886 | 3.7311 | 1077.5 | 1073.7689
372 | 0.10292 | 35.73 | 62.421 | 0.000349 | 3.7411 | 1077.5 |  | 372 | 35.73 | 0.10292 | 62.421 | 0.000349 | 3.7411 | 1077.5 | 1073.7589
373 | 0.10297 | 35.74 | 62.421 | 0.00034913 | 3.7512 | 1077.6 |  | 373 | 35.74 | 0.10297 | 62.421 | 0.00034913 | 3.7512 | 1077.6 | 1073.8488
374 | 0.10301 | 35.75 | 62.421 | 0.00034926 | 3.7613 | 1077.6 |  | 374 | 35.75 | 0.10301 | 62.421 | 0.00034926 | 3.7613 | 1077.6 | 1073.8387
375 | 0.10305 | 35.76 | 62.421 | 0.00034939 | 3.7714 | 1077.6 |  | 375 | 35.76 | 0.10305 | 62.421 | 0.00034939 | 3.7714 | 1077.6 | 1073.8286
376 | 0.10309 | 35.77 | 62.421 | 0.00034952 | 3.7814 | 1077.6 |  | 376 | 35.77 | 0.10309 | 62.421 | 0.00034952 | 3.7814 | 1077.6 | 1073.8186
377 | 0.10313 | 35.78 | 62.421 | 0.00034965 | 3.7915 | 1077.6 |  | 377 | 35.78 | 0.10313 | 62.421 | 0.00034965 | 3.7915 | 1077.6 | 1073.8085
378 | 0.10317 | 35.79 | 62.421 | 0.00034979 | 3.8016 | 1077.6 |  | 378 | 35.79 | 0.10317 | 62.421 | 0.00034979 | 3.8016 | 1077.6 | 1073.7984
379 | 0.10321 | 35.8 | 62.421 | 0.00034992 | 3.8116 | 1077.6 |  | 379 | 35.8 | 0.10321 | 62.421 | 0.00034992 | 3.8116 | 1077.6 | 1073.7884
380 | 0.10325 | 35.81 | 62.421 | 0.00035005 | 3.8217 | 1077.6 |  | 380 | 35.81 | 0.10325 | 62.421 | 0.00035005 | 3.8217 | 1077.6 | 1073.7783
381 | 0.10329 | 35.82 | 62.421 | 0.00035018 | 3.8318 | 1077.6 |  | 381 | 35.82 | 0.10329 | 62.421 | 0.00035018 | 3.8318 | 1077.6 | 1073.7682
382 | 0.10333 | 35.83 | 62.422 | 0.00035031 | 3.8418 | 1077.6 |  | 382 | 35.83 | 0.10333 | 62.422 | 0.00035031 | 3.8418 | 1077.6 | 1073.7582
383 | 0.10337 | 35.84 | 62.422 | 0.00035045 | 3.8519 | 1077.6 |  | 383 | 35.84 | 0.10337 | 62.422 | 0.00035045 | 3.8519 | 1077.6 | 1073.7481
384 | 0.10342 | 35.85 | 62.422 | 0.00035058 | 3.862 | 1077.6 |  | 384 | 35.85 | 0.10342 | 62.422 | 0.00035058 | 3.862 | 1077.6 | 1073.738
385 | 0.10346 | 35.86 | 62.422 | 0.00035071 | 3.8721 | 1077.6 |  | 385 | 35.86 | 0.10346 | 62.422 | 0.00035071 | 3.8721 | 1077.6 | 1073.7279
386 | 0.1035 | 35.87 | 62.422 | 0.00035084 | 3.8821 | 1077.6 |  | 386 | 35.87 | 0.1035 | 62.422 | 0.00035084 | 3.8821 | 1077.6 | 1073.7179
387 | 0.10354 | 35.88 | 62.422 | 0.00035097 | 3.8922 | 1077.6 |  | 387 | 35.88 | 0.10354 | 62.422 | 0.00035097 | 3.8922 | 1077.6 | 1073.7078
388 | 0.10358 | 35.89 | 62.422 | 0.00035111 | 3.9023 | 1077.6 |  | 388 | 35.89 | 0.10358 | 62.422 | 0.00035111 | 3.9023 | 1077.6 | 1073.6977
389 | 0.10362 | 35.9 | 62.422 | 0.00035124 | 3.9123 | 1077.6 |  | 389 | 35.9 | 0.10362 | 62.422 | 0.00035124 | 3.9123 | 1077.6 | 1073.6877
390 | 0.10366 | 35.91 | 62.422 | 0.00035137 | 3.9224 | 1077.6 |  | 390 | 35.91 | 0.10366 | 62.422 | 0.00035137 | 3.9224 | 1077.6 | 1073.6776
391 | 0.1037 | 35.92 | 62.422 | 0.0003515 | 3.9325 | 1077.6 |  | 391 | 35.92 | 0.1037 | 62.422 | 0.0003515 | 3.9325 | 1077.6 | 1073.6675
392 | 0.10374 | 35.93 | 62.422 | 0.00035163 | 3.9425 | 1077.6 |  | 392 | 35.93 | 0.10374 | 62.422 | 0.00035163 | 3.9425 | 1077.6 | 1073.6575
393 | 0.10379 | 35.94 | 62.422 | 0.00035177 | 3.9526 | 1077.6 |  | 393 | 35.94 | 0.10379 | 62.422 | 0.00035177 | 3.9526 | 1077.6 | 1073.6474
394 | 0.10383 | 35.95 | 62.422 | 0.0003519 | 3.9627 | 1077.6 |  | 394 | 35.95 | 0.10383 | 62.422 | 0.0003519 | 3.9627 | 1077.6 | 1073.6373
395 | 0.10387 | 35.96 | 62.422 | 0.00035203 | 3.9728 | 1077.6 |  | 395 | 35.96 | 0.10387 | 62.422 | 0.00035203 | 3.9728 | 1077.6 | 1073.6272
396 | 0.10391 | 35.97 | 62.422 | 0.00035216 | 3.9828 | 1077.7 |  | 396 | 35.97 | 0.10391 | 62.422 | 0.00035216 | 3.9828 | 1077.7 | 1073.7172
397 | 0.10395 | 35.98 | 62.422 | 0.0003523 | 3.9929 | 1077.7 |  | 397 | 35.98 | 0.10395 | 62.422 | 0.0003523 | 3.9929 | 1077.7 | 1073.7071
398 | 0.10399 | 35.99 | 62.422 | 0.00035243 | 4.003 | 1077.7 |  | 398 | 35.99 | 0.10399 | 62.422 | 0.00035243 | 4.003 | 1077.7 | 1073.697
399 | 0.10403 | 36 | 62.422 | 0.00035256 | 4.013 | 1077.7 |  | 399 | 36 | 0.10403 | 62.422 | 0.00035256 | 4.013 | 1077.7 | 1073.687
400 | 0.10407 | 36.01 | 62.422 | 0.0003527 | 4.0231 | 1077.7 |  | 400 | 36.01 | 0.10407 | 62.422 | 0.0003527 | 4.0231 | 1077.7 | 1073.6769
401 | 0.10412 | 36.02 | 62.422 | 0.00035283 | 4.0332 | 1077.7 |  | 401 | 36.02 | 0.10412 | 62.422 | 0.00035283 | 4.0332 | 1077.7 | 1073.6668
402 | 0.10416 | 36.03 | 62.422 | 0.00035296 | 4.0432 | 1077.7 |  | 402 | 36.03 | 0.10416 | 62.422 | 0.00035296 | 4.0432 | 1077.7 | 1073.6568
403 | 0.1042 | 36.04 | 62.422 | 0.00035309 | 4.0533 | 1077.7 |  | 403 | 36.04 | 0.1042 | 62.422 | 0.00035309 | 4.0533 | 1077.7 | 1073.6467
404 | 0.10424 | 36.05 | 62.422 | 0.00035323 | 4.0634 | 1077.7 |  | 404 | 36.05 | 0.10424 | 62.422 | 0.00035323 | 4.0634 | 1077.7 | 1073.6366
405 | 0.10428 | 36.06 | 62.422 | 0.00035336 | 4.0734 | 1077.7 |  | 405 | 36.06 | 0.10428 | 62.422 | 0.00035336 | 4.0734 | 1077.7 | 1073.6266
406 | 0.10432 | 36.07 | 62.422 | 0.00035349 | 4.0835 | 1077.7 |  | 406 | 36.07 | 0.10432 | 62.422 | 0.00035349 | 4.0835 | 1077.7 | 1073.6165
407 | 0.10436 | 36.08 | 62.422 | 0.00035363 | 4.0936 | 1077.7 |  | 407 | 36.08 | 0.10436 | 62.422 | 0.00035363 | 4.0936 | 1077.7 | 1073.6064
408 | 0.1044 | 36.09 | 62.422 | 0.00035376 | 4.1036 | 1077.7 |  | 408 | 36.09 | 0.1044 | 62.422 | 0.00035376 | 4.1036 | 1077.7 | 1073.5964
409 | 0.10445 | 36.1 | 62.422 | 0.00035389 | 4.1137 | 1077.7 |  | 409 | 36.1 | 0.10445 | 62.422 | 0.00035389 | 4.1137 | 1077.7 | 1073.5863
410 | 0.10449 | 36.11 | 62.422 | 0.00035403 | 4.1238 | 1077.7 |  | 410 | 36.11 | 0.10449 | 62.422 | 0.00035403 | 4.1238 | 1077.7 | 1073.5762
411 | 0.10453 | 36.12 | 62.422 | 0.00035416 | 4.1339 | 1077.7 |  | 411 | 36.12 | 0.10453 | 62.422 | 0.00035416 | 4.1339 | 1077.7 | 1073.5661
412 | 0.10457 | 36.13 | 62.422 | 0.00035429 | 4.1439 | 1077.7 |  | 412 | 36.13 | 0.10457 | 62.422 | 0.00035429 | 4.1439 | 1077.7 | 1073.5561
413 | 0.10461 | 36.14 | 62.422 | 0.00035442 | 4.154 | 1077.7 |  | 413 | 36.14 | 0.10461 | 62.422 | 0.00035442 | 4.154 | 1077.7 | 1073.546
414 | 0.10465 | 36.15 | 62.422 | 0.00035456 | 4.1641 | 1077.7 |  | 414 | 36.15 | 0.10465 | 62.422 | 0.00035456 | 4.1641 | 1077.7 | 1073.5359
415 | 0.10469 | 36.16 | 62.422 | 0.00035469 | 4.1741 | 1077.7 |  | 415 | 36.16 | 0.10469 | 62.422 | 0.00035469 | 4.1741 | 1077.7 | 1073.5259
416 | 0.10474 | 36.17 | 62.422 | 0.00035483 | 4.1842 | 1077.7 |  | 416 | 36.17 | 0.10474 | 62.422 | 0.00035483 | 4.1842 | 1077.7 | 1073.5158
417 | 0.10478 | 36.18 | 62.422 | 0.00035496 | 4.1943 | 1077.7 |  | 417 | 36.18 | 0.10478 | 62.422 | 0.00035496 | 4.1943 | 1077.7 | 1073.5057
418 | 0.10482 | 36.19 | 62.422 | 0.00035509 | 4.2043 | 1077.7 |  | 418 | 36.19 | 0.10482 | 62.422 | 0.00035509 | 4.2043 | 1077.7 | 1073.4957
419 | 0.10486 | 36.2 | 62.422 | 0.00035523 | 4.2144 | 1077.8 |  | 419 | 36.2 | 0.10486 | 62.422 | 0.00035523 | 4.2144 | 1077.8 | 1073.5856
420 | 0.1049 | 36.21 | 62.422 | 0.00035536 | 4.2245 | 1077.8 |  | 420 | 36.21 | 0.1049 | 62.422 | 0.00035536 | 4.2245 | 1077.8 | 1073.5755
421 | 0.10494 | 36.22 | 62.422 | 0.00035549 | 4.2345 | 1077.8 |  | 421 | 36.22 | 0.10494 | 62.422 | 0.00035549 | 4.2345 | 1077.8 | 1073.5655
422 | 0.10499 | 36.23 | 62.422 | 0.00035563 | 4.2446 | 1077.8 |  | 422 | 36.23 | 0.10499 | 62.422 | 0.00035563 | 4.2446 | 1077.8 | 1073.5554
423 | 0.10503 | 36.24 | 62.422 | 0.00035576 | 4.2547 | 1077.8 |  | 423 | 36.24 | 0.10503 | 62.422 | 0.00035576 | 4.2547 | 1077.8 | 1073.5453
424 | 0.10507 | 36.25 | 62.422 | 0.00035589 | 4.2647 | 1077.8 |  | 424 | 36.25 | 0.10507 | 62.422 | 0.00035589 | 4.2647 | 1077.8 | 1073.5353
425 | 0.10511 | 36.26 | 62.422 | 0.00035603 | 4.2748 | 1077.8 |  | 425 | 36.26 | 0.10511 | 62.422 | 0.00035603 | 4.2748 | 1077.8 | 1073.5252
426 | 0.10515 | 36.27 | 62.422 | 0.00035616 | 4.2849 | 1077.8 |  | 426 | 36.27 | 0.10515 | 62.422 | 0.00035616 | 4.2849 | 1077.8 | 1073.5151
427 | 0.10519 | 36.28 | 62.422 | 0.0003563 | 4.2949 | 1077.8 |  | 427 | 36.28 | 0.10519 | 62.422 | 0.0003563 | 4.2949 | 1077.8 | 1073.5051
428 | 0.10523 | 36.29 | 62.422 | 0.00035643 | 4.305 | 1077.8 |  | 428 | 36.29 | 0.10523 | 62.422 | 0.00035643 | 4.305 | 1077.8 | 1073.495
429 | 0.10528 | 36.3 | 62.422 | 0.00035656 | 4.3151 | 1077.8 |  | 429 | 36.3 | 0.10528 | 62.422 | 0.00035656 | 4.3151 | 1077.8 | 1073.4849
430 | 0.10532 | 36.31 | 62.422 | 0.0003567 | 4.3251 | 1077.8 |  | 430 | 36.31 | 0.10532 | 62.422 | 0.0003567 | 4.3251 | 1077.8 | 1073.4749
431 | 0.10536 | 36.32 | 62.422 | 0.00035683 | 4.3352 | 1077.8 |  | 431 | 36.32 | 0.10536 | 62.422 | 0.00035683 | 4.3352 | 1077.8 | 1073.4648
432 | 0.1054 | 36.33 | 62.422 | 0.00035697 | 4.3453 | 1077.8 |  | 432 | 36.33 | 0.1054 | 62.422 | 0.00035697 | 4.3453 | 1077.8 | 1073.4547
433 | 0.10544 | 36.34 | 62.422 | 0.0003571 | 4.3554 | 1077.8 |  | 433 | 36.34 | 0.10544 | 62.422 | 0.0003571 | 4.3554 | 1077.8 | 1073.4446
434 | 0.10549 | 36.35 | 62.422 | 0.00035723 | 4.3654 | 1077.8 |  | 434 | 36.35 | 0.10549 | 62.422 | 0.00035723 | 4.3654 | 1077.8 | 1073.4346
435 | 0.10553 | 36.36 | 62.422 | 0.00035737 | 4.3755 | 1077.8 |  | 435 | 36.36 | 0.10553 | 62.422 | 0.00035737 | 4.3755 | 1077.8 | 1073.4245
436 | 0.10557 | 36.37 | 62.422 | 0.0003575 | 4.3856 | 1077.8 |  | 436 | 36.37 | 0.10557 | 62.422 | 0.0003575 | 4.3856 | 1077.8 | 1073.4144
437 | 0.10561 | 36.38 | 62.422 | 0.00035764 | 4.3956 | 1077.8 |  | 437 | 36.38 | 0.10561 | 62.422 | 0.00035764 | 4.3956 | 1077.8 | 1073.4044
438 | 0.10565 | 36.39 | 62.422 | 0.00035777 | 4.4057 | 1077.8 |  | 438 | 36.39 | 0.10565 | 62.422 | 0.00035777 | 4.4057 | 1077.8 | 1073.3943
439 | 0.10569 | 36.4 | 62.422 | 0.00035791 | 4.4158 | 1077.8 |  | 439 | 36.4 | 0.10569 | 62.422 | 0.00035791 | 4.4158 | 1077.8 | 1073.3842
440 | 0.10574 | 36.41 | 62.422 | 0.00035804 | 4.4258 | 1077.8 |  | 440 | 36.41 | 0.10574 | 62.422 | 0.00035804 | 4.4258 | 1077.8 | 1073.3742
441 | 0.10578 | 36.42 | 62.422 | 0.00035818 | 4.4359 | 1077.8 |  | 441 | 36.42 | 0.10578 | 62.422 | 0.00035818 | 4.4359 | 1077.8 | 1073.3641
442 | 0.10582 | 36.43 | 62.422 | 0.00035831 | 4.446 | 1077.9 |  | 442 | 36.43 | 0.10582 | 62.422 | 0.00035831 | 4.446 | 1077.9 | 1073.454
443 | 0.10586 | 36.44 | 62.422 | 0.00035844 | 4.456 | 1077.9 |  | 443 | 36.44 | 0.10586 | 62.422 | 0.00035844 | 4.456 | 1077.9 | 1073.444
444 | 0.1059 | 36.45 | 62.422 | 0.00035858 | 4.4661 | 1077.9 |  | 444 | 36.45 | 0.1059 | 62.422 | 0.00035858 | 4.4661 | 1077.9 | 1073.4339
445 | 0.10595 | 36.46 | 62.422 | 0.00035871 | 4.4762 | 1077.9 |  | 445 | 36.46 | 0.10595 | 62.422 | 0.00035871 | 4.4762 | 1077.9 | 1073.4238
446 | 0.10599 | 36.47 | 62.422 | 0.00035885 | 4.4862 | 1077.9 |  | 446 | 36.47 | 0.10599 | 62.422 | 0.00035885 | 4.4862 | 1077.9 | 1073.4138
447 | 0.10603 | 36.48 | 62.422 | 0.00035898 | 4.4963 | 1077.9 |  | 447 | 36.48 | 0.10603 | 62.422 | 0.00035898 | 4.4963 | 1077.9 | 1073.4037
448 | 0.10607 | 36.49 | 62.422 | 0.00035912 | 4.5064 | 1077.9 |  | 448 | 36.49 | 0.10607 | 62.422 | 0.00035912 | 4.5064 | 1077.9 | 1073.3936
449 | 0.10611 | 36.5 | 62.422 | 0.00035925 | 4.5164 | 1077.9 |  | 449 | 36.5 | 0.10611 | 62.422 | 0.00035925 | 4.5164 | 1077.9 | 1073.3836
450 | 0.10615 | 36.51 | 62.422 | 0.00035939 | 4.5265 | 1077.9 |  | 450 | 36.51 | 0.10615 | 62.422 | 0.00035939 | 4.5265 | 1077.9 | 1073.3735
451 | 0.1062 | 36.52 | 62.422 | 0.00035952 | 4.5366 | 1077.9 |  | 451 | 36.52 | 0.1062 | 62.422 | 0.00035952 | 4.5366 | 1077.9 | 1073.3634
452 | 0.10624 | 36.53 | 62.422 | 0.00035966 | 4.5466 | 1077.9 |  | 452 | 36.53 | 0.10624 | 62.422 | 0.00035966 | 4.5466 | 1077.9 | 1073.3534
453 | 0.10628 | 36.54 | 62.422 | 0.00035979 | 4.5567 | 1077.9 |  | 453 | 36.54 | 0.10628 | 62.422 | 0.00035979 | 4.5567 | 1077.9 | 1073.3433
454 | 0.10632 | 36.55 | 62.422 | 0.00035993 | 4.5668 | 1077.9 |  | 454 | 36.55 | 0.10632 | 62.422 | 0.00035993 | 4.5668 | 1077.9 | 1073.3332
455 | 0.10637 | 36.56 | 62.422 | 0.00036006 | 4.5768 | 1077.9 |  | 455 | 36.56 | 0.10637 | 62.422 | 0.00036006 | 4.5768 | 1077.9 | 1073.3232
456 | 0.10641 | 36.57 | 62.422 | 0.0003602 | 4.5869 | 1077.9 |  | 456 | 36.57 | 0.10641 | 62.422 | 0.0003602 | 4.5869 | 1077.9 | 1073.3131
457 | 0.10645 | 36.58 | 62.422 | 0.00036033 | 4.597 | 1077.9 |  | 457 | 36.58 | 0.10645 | 62.422 | 0.00036033 | 4.597 | 1077.9 | 1073.303
458 | 0.10649 | 36.59 | 62.422 | 0.00036047 | 4.607 | 1077.9 |  | 458 | 36.59 | 0.10649 | 62.422 | 0.00036047 | 4.607 | 1077.9 | 1073.293
459 | 0.10653 | 36.6 | 62.422 | 0.0003606 | 4.6171 | 1077.9 |  | 459 | 36.6 | 0.10653 | 62.422 | 0.0003606 | 4.6171 | 1077.9 | 1073.2829
460 | 0.10658 | 36.61 | 62.422 | 0.00036074 | 4.6272 | 1077.9 |  | 460 | 36.61 | 0.10658 | 62.422 | 0.00036074 | 4.6272 | 1077.9 | 1073.2728
461 | 0.10662 | 36.62 | 62.422 | 0.00036088 | 4.6372 | 1077.9 |  | 461 | 36.62 | 0.10662 | 62.422 | 0.00036088 | 4.6372 | 1077.9 | 1073.2628
462 | 0.10666 | 36.63 | 62.422 | 0.00036101 | 4.6473 | 1077.9 |  | 462 | 36.63 | 0.10666 | 62.422 | 0.00036101 | 4.6473 | 1077.9 | 1073.2527
463 | 0.1067 | 36.64 | 62.422 | 0.00036115 | 4.6574 | 1077.9 |  | 463 | 36.64 | 0.1067 | 62.422 | 0.00036115 | 4.6574 | 1077.9 | 1073.2426
464 | 0.10674 | 36.65 | 62.422 | 0.00036128 | 4.6674 | 1077.9 |  | 464 | 36.65 | 0.10674 | 62.422 | 0.00036128 | 4.6674 | 1077.9 | 1073.2326
465 | 0.10679 | 36.66 | 62.422 | 0.00036142 | 4.6775 | 1078 |  | 465 | 36.66 | 0.10679 | 62.422 | 0.00036142 | 4.6775 | 1078 | 1073.3225
466 | 0.10683 | 36.67 | 62.422 | 0.00036155 | 4.6876 | 1078 |  | 466 | 36.67 | 0.10683 | 62.422 | 0.00036155 | 4.6876 | 1078 | 1073.3124
467 | 0.10687 | 36.68 | 62.422 | 0.00036169 | 4.6976 | 1078 |  | 467 | 36.68 | 0.10687 | 62.422 | 0.00036169 | 4.6976 | 1078 | 1073.3024
468 | 0.10691 | 36.69 | 62.422 | 0.00036182 | 4.7077 | 1078 |  | 468 | 36.69 | 0.10691 | 62.422 | 0.00036182 | 4.7077 | 1078 | 1073.2923
469 | 0.10696 | 36.7 | 62.422 | 0.00036196 | 4.7178 | 1078 |  | 469 | 36.7 | 0.10696 | 62.422 | 0.00036196 | 4.7178 | 1078 | 1073.2822
470 | 0.107 | 36.71 | 62.422 | 0.0003621 | 4.7278 | 1078 |  | 470 | 36.71 | 0.107 | 62.422 | 0.0003621 | 4.7278 | 1078 | 1073.2722
471 | 0.10704 | 36.72 | 62.422 | 0.00036223 | 4.7379 | 1078 |  | 471 | 36.72 | 0.10704 | 62.422 | 0.00036223 | 4.7379 | 1078 | 1073.2621
472 | 0.10708 | 36.73 | 62.422 | 0.00036237 | 4.748 | 1078 |  | 472 | 36.73 | 0.10708 | 62.422 | 0.00036237 | 4.748 | 1078 | 1073.252
473 | 0.10712 | 36.74 | 62.422 | 0.0003625 | 4.758 | 1078 |  | 473 | 36.74 | 0.10712 | 62.422 | 0.0003625 | 4.758 | 1078 | 1073.242
474 | 0.10717 | 36.75 | 62.422 | 0.00036264 | 4.7681 | 1078 |  | 474 | 36.75 | 0.10717 | 62.422 | 0.00036264 | 4.7681 | 1078 | 1073.2319
475 | 0.10721 | 36.76 | 62.422 | 0.00036278 | 4.7782 | 1078 |  | 475 | 36.76 | 0.10721 | 62.422 | 0.00036278 | 4.7782 | 1078 | 1073.2218
476 | 0.10725 | 36.77 | 62.422 | 0.00036291 | 4.7882 | 1078 |  | 476 | 36.77 | 0.10725 | 62.422 | 0.00036291 | 4.7882 | 1078 | 1073.2118
477 | 0.10729 | 36.78 | 62.422 | 0.00036305 | 4.7983 | 1078 |  | 477 | 36.78 | 0.10729 | 62.422 | 0.00036305 | 4.7983 | 1078 | 1073.2017
478 | 0.10734 | 36.79 | 62.422 | 0.00036318 | 4.8084 | 1078 |  | 478 | 36.79 | 0.10734 | 62.422 | 0.00036318 | 4.8084 | 1078 | 1073.1916
479 | 0.10738 | 36.8 | 62.422 | 0.00036332 | 4.8184 | 1078 |  | 479 | 36.8 | 0.10738 | 62.422 | 0.00036332 | 4.8184 | 1078 | 1073.1816
480 | 0.10742 | 36.81 | 62.422 | 0.00036346 | 4.8285 | 1078 |  | 480 | 36.81 | 0.10742 | 62.422 | 0.00036346 | 4.8285 | 1078 | 1073.1715
481 | 0.10746 | 36.82 | 62.422 | 0.00036359 | 4.8386 | 1078 |  | 481 | 36.82 | 0.10746 | 62.422 | 0.00036359 | 4.8386 | 1078 | 1073.1614
482 | 0.10751 | 36.83 | 62.422 | 0.00036373 | 4.8486 | 1078 |  | 482 | 36.83 | 0.10751 | 62.422 | 0.00036373 | 4.8486 | 1078 | 1073.1514
483 | 0.10755 | 36.84 | 62.422 | 0.00036387 | 4.8587 | 1078 |  | 483 | 36.84 | 0.10755 | 62.422 | 0.00036387 | 4.8587 | 1078 | 1073.1413
484 | 0.10759 | 36.85 | 62.422 | 0.000364 | 4.8688 | 1078 |  | 484 | 36.85 | 0.10759 | 62.422 | 0.000364 | 4.8688 | 1078 | 1073.1312
485 | 0.10763 | 36.86 | 62.422 | 0.00036414 | 4.8788 | 1078 |  | 485 | 36.86 | 0.10763 | 62.422 | 0.00036414 | 4.8788 | 1078 | 1073.1212
486 | 0.10768 | 36.87 | 62.422 | 0.00036428 | 4.8889 | 1078 |  | 486 | 36.87 | 0.10768 | 62.422 | 0.00036428 | 4.8889 | 1078 | 1073.1111
487 | 0.10772 | 36.88 | 62.422 | 0.00036441 | 4.899 | 1078.1 |  | 487 | 36.88 | 0.10772 | 62.422 | 0.00036441 | 4.899 | 1078.1 | 1073.201
488 | 0.10776 | 36.89 | 62.422 | 0.00036455 | 4.909 | 1078.1 |  | 488 | 36.89 | 0.10776 | 62.422 | 0.00036455 | 4.909 | 1078.1 | 1073.191
489 | 0.1078 | 36.9 | 62.422 | 0.00036469 | 4.9191 | 1078.1 |  | 489 | 36.9 | 0.1078 | 62.422 | 0.00036469 | 4.9191 | 1078.1 | 1073.1809
490 | 0.10785 | 36.91 | 62.422 | 0.00036482 | 4.9292 | 1078.1 |  | 490 | 36.91 | 0.10785 | 62.422 | 0.00036482 | 4.9292 | 1078.1 | 1073.1708
491 | 0.10789 | 36.92 | 62.422 | 0.00036496 | 4.9392 | 1078.1 |  | 491 | 36.92 | 0.10789 | 62.422 | 0.00036496 | 4.9392 | 1078.1 | 1073.1608
492 | 0.10793 | 36.93 | 62.422 | 0.0003651 | 4.9493 | 1078.1 |  | 492 | 36.93 | 0.10793 | 62.422 | 0.0003651 | 4.9493 | 1078.1 | 1073.1507
493 | 0.10797 | 36.94 | 62.422 | 0.00036523 | 4.9593 | 1078.1 |  | 493 | 36.94 | 0.10797 | 62.422 | 0.00036523 | 4.9593 | 1078.1 | 1073.1407
494 | 0.10802 | 36.95 | 62.422 | 0.00036537 | 4.9694 | 1078.1 |  | 494 | 36.95 | 0.10802 | 62.422 | 0.00036537 | 4.9694 | 1078.1 | 1073.1306
495 | 0.10806 | 36.96 | 62.423 | 0.00036551 | 4.9795 | 1078.1 |  | 495 | 36.96 | 0.10806 | 62.423 | 0.00036551 | 4.9795 | 1078.1 | 1073.1205
496 | 0.1081 | 36.97 | 62.423 | 0.00036564 | 4.9895 | 1078.1 |  | 496 | 36.97 | 0.1081 | 62.423 | 0.00036564 | 4.9895 | 1078.1 | 1073.1105
497 | 0.10814 | 36.98 | 62.423 | 0.00036578 | 4.9996 | 1078.1 |  | 497 | 36.98 | 0.10814 | 62.423 | 0.00036578 | 4.9996 | 1078.1 | 1073.1004
498 | 0.10819 | 36.99 | 62.423 | 0.00036592 | 5.0097 | 1078.1 |  | 498 | 36.99 | 0.10819 | 62.423 | 0.00036592 | 5.0097 | 1078.1 | 1073.0903
499 | 0.10823 | 37 | 62.423 | 0.00036605 | 5.0197 | 1078.1 |  | 499 | 37 | 0.10823 | 62.423 | 0.00036605 | 5.0197 | 1078.1 | 1073.0803
500 | 0.10827 | 37.01 | 62.423 | 0.00036619 | 5.0298 | 1078.1 |  | 500 | 37.01 | 0.10827 | 62.423 | 0.00036619 | 5.0298 | 1078.1 | 1073.0702
501 | 0.10832 | 37.02 | 62.423 | 0.00036633 | 5.0399 | 1078.1 |  | 501 | 37.02 | 0.10832 | 62.423 | 0.00036633 | 5.0399 | 1078.1 | 1073.0601
502 | 0.10836 | 37.03 | 62.423 | 0.00036647 | 5.0499 | 1078.1 |  | 502 | 37.03 | 0.10836 | 62.423 | 0.00036647 | 5.0499 | 1078.1 | 1073.0501
503 | 0.1084 | 37.04 | 62.423 | 0.0003666 | 5.06 | 1078.1 |  | 503 | 37.04 | 0.1084 | 62.423 | 0.0003666 | 5.06 | 1078.1 | 1073.04
504 | 0.10844 | 37.05 | 62.423 | 0.00036674 | 5.0701 | 1078.1 |  | 504 | 37.05 | 0.10844 | 62.423 | 0.00036674 | 5.0701 | 1078.1 | 1073.0299
505 | 0.10849 | 37.06 | 62.423 | 0.00036688 | 5.0801 | 1078.1 |  | 505 | 37.06 | 0.10849 | 62.423 | 0.00036688 | 5.0801 | 1078.1 | 1073.0199
506 | 0.10853 | 37.07 | 62.423 | 0.00036702 | 5.0902 | 1078.1 |  | 506 | 37.07 | 0.10853 | 62.423 | 0.00036702 | 5.0902 | 1078.1 | 1073.0098
507 | 0.10857 | 37.08 | 62.423 | 0.00036715 | 5.1003 | 1078.1 |  | 507 | 37.08 | 0.10857 | 62.423 | 0.00036715 | 5.1003 | 1078.1 | 1072.9997
508 | 0.10861 | 37.09 | 62.423 | 0.00036729 | 5.1103 | 1078.1 |  | 508 | 37.09 | 0.10861 | 62.423 | 0.00036729 | 5.1103 | 1078.1 | 1072.9897
509 | 0.10866 | 37.1 | 62.423 | 0.00036743 | 5.1204 | 1078.1 |  | 509 | 37.1 | 0.10866 | 62.423 | 0.00036743 | 5.1204 | 1078.1 | 1072.9796
510 | 0.1087 | 37.11 | 62.423 | 0.00036757 | 5.1305 | 1078.2 |  | 510 | 37.11 | 0.1087 | 62.423 | 0.00036757 | 5.1305 | 1078.2 | 1073.0695
511 | 0.10874 | 37.12 | 62.423 | 0.0003677 | 5.1405 | 1078.2 |  | 511 | 37.12 | 0.10874 | 62.423 | 0.0003677 | 5.1405 | 1078.2 | 1073.0595
512 | 0.10879 | 37.13 | 62.423 | 0.00036784 | 5.1506 | 1078.2 |  | 512 | 37.13 | 0.10879 | 62.423 | 0.00036784 | 5.1506 | 1078.2 | 1073.0494
513 | 0.10883 | 37.14 | 62.423 | 0.00036798 | 5.1606 | 1078.2 |  | 513 | 37.14 | 0.10883 | 62.423 | 0.00036798 | 5.1606 | 1078.2 | 1073.0394
514 | 0.10887 | 37.15 | 62.423 | 0.00036812 | 5.1707 | 1078.2 |  | 514 | 37.15 | 0.10887 | 62.423 | 0.00036812 | 5.1707 | 1078.2 | 1073.0293
515 | 0.10892 | 37.16 | 62.423 | 0.00036825 | 5.1808 | 1078.2 |  | 515 | 37.16 | 0.10892 | 62.423 | 0.00036825 | 5.1808 | 1078.2 | 1073.0192
516 | 0.10896 | 37.17 | 62.423 | 0.00036839 | 5.1908 | 1078.2 |  | 516 | 37.17 | 0.10896 | 62.423 | 0.00036839 | 5.1908 | 1078.2 | 1073.0092
517 | 0.109 | 37.18 | 62.423 | 0.00036853 | 5.2009 | 1078.2 |  | 517 | 37.18 | 0.109 | 62.423 | 0.00036853 | 5.2009 | 1078.2 | 1072.9991
518 | 0.10904 | 37.19 | 62.423 | 0.00036867 | 5.211 | 1078.2 |  | 518 | 37.19 | 0.10904 | 62.423 | 0.00036867 | 5.211 | 1078.2 | 1072.989
519 | 0.10909 | 37.2 | 62.423 | 0.00036881 | 5.221 | 1078.2 |  | 519 | 37.2 | 0.10909 | 62.423 | 0.00036881 | 5.221 | 1078.2 | 1072.979
520 | 0.10913 | 37.21 | 62.423 | 0.00036894 | 5.2311 | 1078.2 |  | 520 | 37.21 | 0.10913 | 62.423 | 0.00036894 | 5.2311 | 1078.2 | 1072.9689
521 | 0.10917 | 37.22 | 62.423 | 0.00036908 | 5.2412 | 1078.2 |  | 521 | 37.22 | 0.10917 | 62.423 | 0.00036908 | 5.2412 | 1078.2 | 1072.9588
522 | 0.10922 | 37.23 | 62.423 | 0.00036922 | 5.2512 | 1078.2 |  | 522 | 37.23 | 0.10922 | 62.423 | 0.00036922 | 5.2512 | 1078.2 | 1072.9488
523 | 0.10926 | 37.24 | 62.423 | 0.00036936 | 5.2613 | 1078.2 |  | 523 | 37.24 | 0.10926 | 62.423 | 0.00036936 | 5.2613 | 1078.2 | 1072.9387
524 | 0.1093 | 37.25 | 62.423 | 0.0003695 | 5.2714 | 1078.2 |  | 524 | 37.25 | 0.1093 | 62.423 | 0.0003695 | 5.2714 | 1078.2 | 1072.9286
525 | 0.10935 | 37.26 | 62.423 | 0.00036964 | 5.2814 | 1078.2 |  | 525 | 37.26 | 0.10935 | 62.423 | 0.00036964 | 5.2814 | 1078.2 | 1072.9186
526 | 0.10939 | 37.27 | 62.423 | 0.00036977 | 5.2915 | 1078.2 |  | 526 | 37.27 | 0.10939 | 62.423 | 0.00036977 | 5.2915 | 1078.2 | 1072.9085
527 | 0.10943 | 37.28 | 62.423 | 0.00036991 | 5.3016 | 1078.2 |  | 527 | 37.28 | 0.10943 | 62.423 | 0.00036991 | 5.3016 | 1078.2 | 1072.8984
528 | 0.10947 | 37.29 | 62.423 | 0.00037005 | 5.3116 | 1078.2 |  | 528 | 37.29 | 0.10947 | 62.423 | 0.00037005 | 5.3116 | 1078.2 | 1072.8884
529 | 0.10952 | 37.3 | 62.423 | 0.00037019 | 5.3217 | 1078.2 |  | 529 | 37.3 | 0.10952 | 62.423 | 0.00037019 | 5.3217 | 1078.2 | 1072.8783
530 | 0.10956 | 37.31 | 62.423 | 0.00037033 | 5.3317 | 1078.2 |  | 530 | 37.31 | 0.10956 | 62.423 | 0.00037033 | 5.3317 | 1078.2 | 1072.8683
531 | 0.1096 | 37.32 | 62.423 | 0.00037047 | 5.3418 | 1078.2 |  | 531 | 37.32 | 0.1096 | 62.423 | 0.00037047 | 5.3418 | 1078.2 | 1072.8582
532 | 0.10965 | 37.33 | 62.423 | 0.0003706 | 5.3519 | 1078.2 |  | 532 | 37.33 | 0.10965 | 62.423 | 0.0003706 | 5.3519 | 1078.2 | 1072.8481
533 | 0.10969 | 37.34 | 62.423 | 0.00037074 | 5.3619 | 1078.3 |  | 533 | 37.34 | 0.10969 | 62.423 | 0.00037074 | 5.3619 | 1078.3 | 1072.9381
534 | 0.10973 | 37.35 | 62.423 | 0.00037088 | 5.372 | 1078.3 |  | 534 | 37.35 | 0.10973 | 62.423 | 0.00037088 | 5.372 | 1078.3 | 1072.928
535 | 0.10978 | 37.36 | 62.423 | 0.00037102 | 5.3821 | 1078.3 |  | 535 | 37.36 | 0.10978 | 62.423 | 0.00037102 | 5.3821 | 1078.3 | 1072.9179
536 | 0.10982 | 37.37 | 62.423 | 0.00037116 | 5.3921 | 1078.3 |  | 536 | 37.37 | 0.10982 | 62.423 | 0.00037116 | 5.3921 | 1078.3 | 1072.9079
537 | 0.10986 | 37.38 | 62.423 | 0.0003713 | 5.4022 | 1078.3 |  | 537 | 37.38 | 0.10986 | 62.423 | 0.0003713 | 5.4022 | 1078.3 | 1072.8978
538 | 0.10991 | 37.39 | 62.423 | 0.00037144 | 5.4123 | 1078.3 |  | 538 | 37.39 | 0.10991 | 62.423 | 0.00037144 | 5.4123 | 1078.3 | 1072.8877
539 | 0.10995 | 37.4 | 62.423 | 0.00037158 | 5.4223 | 1078.3 |  | 539 | 37.4 | 0.10995 | 62.423 | 0.00037158 | 5.4223 | 1078.3 | 1072.8777
540 | 0.10999 | 37.41 | 62.423 | 0.00037172 | 5.4324 | 1078.3 |  | 540 | 37.41 | 0.10999 | 62.423 | 0.00037172 | 5.4324 | 1078.3 | 1072.8676
541 | 0.11004 | 37.42 | 62.423 | 0.00037185 | 5.4424 | 1078.3 |  | 541 | 37.42 | 0.11004 | 62.423 | 0.00037185 | 5.4424 | 1078.3 | 1072.8576
542 | 0.11008 | 37.43 | 62.423 | 0.00037199 | 5.4525 | 1078.3 |  | 542 | 37.43 | 0.11008 | 62.423 | 0.00037199 | 5.4525 | 1078.3 | 1072.8475
543 | 0.11012 | 37.44 | 62.423 | 0.00037213 | 5.4626 | 1078.3 |  | 543 | 37.44 | 0.11012 | 62.423 | 0.00037213 | 5.4626 | 1078.3 | 1072.8374
544 | 0.11017 | 37.45 | 62.423 | 0.00037227 | 5.4726 | 1078.3 |  | 544 | 37.45 | 0.11017 | 62.423 | 0.00037227 | 5.4726 | 1078.3 | 1072.8274
545 | 0.11021 | 37.46 | 62.423 | 0.00037241 | 5.4827 | 1078.3 |  | 545 | 37.46 | 0.11021 | 62.423 | 0.00037241 | 5.4827 | 1078.3 | 1072.8173
546 | 0.11025 | 37.47 | 62.423 | 0.00037255 | 5.4928 | 1078.3 |  | 546 | 37.47 | 0.11025 | 62.423 | 0.00037255 | 5.4928 | 1078.3 | 1072.8072
547 | 0.1103 | 37.48 | 62.423 | 0.00037269 | 5.5028 | 1078.3 |  | 547 | 37.48 | 0.1103 | 62.423 | 0.00037269 | 5.5028 | 1078.3 | 1072.7972
548 | 0.11034 | 37.49 | 62.423 | 0.00037283 | 5.5129 | 1078.3 |  | 548 | 37.49 | 0.11034 | 62.423 | 0.00037283 | 5.5129 | 1078.3 | 1072.7871
549 | 0.11038 | 37.5 | 62.423 | 0.00037297 | 5.523 | 1078.3 |  | 549 | 37.5 | 0.11038 | 62.423 | 0.00037297 | 5.523 | 1078.3 | 1072.777
550 | 0.11043 | 37.51 | 62.423 | 0.00037311 | 5.533 | 1078.3 |  | 550 | 37.51 | 0.11043 | 62.423 | 0.00037311 | 5.533 | 1078.3 | 1072.767
551 | 0.11047 | 37.52 | 62.423 | 0.00037325 | 5.5431 | 1078.3 |  | 551 | 37.52 | 0.11047 | 62.423 | 0.00037325 | 5.5431 | 1078.3 | 1072.7569
552 | 0.11051 | 37.53 | 62.423 | 0.00037339 | 5.5531 | 1078.3 |  | 552 | 37.53 | 0.11051 | 62.423 | 0.00037339 | 5.5531 | 1078.3 | 1072.7469
553 | 0.11056 | 37.54 | 62.423 | 0.00037353 | 5.5632 | 1078.3 |  | 553 | 37.54 | 0.11056 | 62.423 | 0.00037353 | 5.5632 | 1078.3 | 1072.7368
554 | 0.1106 | 37.55 | 62.423 | 0.00037367 | 5.5733 | 1078.3 |  | 554 | 37.55 | 0.1106 | 62.423 | 0.00037367 | 5.5733 | 1078.3 | 1072.7267
555 | 0.11065 | 37.56 | 62.423 | 0.00037381 | 5.5833 | 1078.3 |  | 555 | 37.56 | 0.11065 | 62.423 | 0.00037381 | 5.5833 | 1078.3 | 1072.7167
556 | 0.11069 | 37.57 | 62.423 | 0.00037395 | 5.5934 | 1078.4 |  | 556 | 37.57 | 0.11069 | 62.423 | 0.00037395 | 5.5934 | 1078.4 | 1072.8066
557 | 0.11073 | 37.58 | 62.423 | 0.00037408 | 5.6035 | 1078.4 |  | 557 | 37.58 | 0.11073 | 62.423 | 0.00037408 | 5.6035 | 1078.4 | 1072.7965
558 | 0.11078 | 37.59 | 62.423 | 0.00037422 | 5.6135 | 1078.4 |  | 558 | 37.59 | 0.11078 | 62.423 | 0.00037422 | 5.6135 | 1078.4 | 1072.7865
559 | 0.11082 | 37.6 | 62.423 | 0.00037436 | 5.6236 | 1078.4 |  | 559 | 37.6 | 0.11082 | 62.423 | 0.00037436 | 5.6236 | 1078.4 | 1072.7764
560 | 0.11086 | 37.61 | 62.423 | 0.0003745 | 5.6336 | 1078.4 |  | 560 | 37.61 | 0.11086 | 62.423 | 0.0003745 | 5.6336 | 1078.4 | 1072.7664
561 | 0.11091 | 37.62 | 62.423 | 0.00037464 | 5.6437 | 1078.4 |  | 561 | 37.62 | 0.11091 | 62.423 | 0.00037464 | 5.6437 | 1078.4 | 1072.7563
562 | 0.11095 | 37.63 | 62.423 | 0.00037478 | 5.6538 | 1078.4 |  | 562 | 37.63 | 0.11095 | 62.423 | 0.00037478 | 5.6538 | 1078.4 | 1072.7462
563 | 0.11099 | 37.64 | 62.423 | 0.00037492 | 5.6638 | 1078.4 |  | 563 | 37.64 | 0.11099 | 62.423 | 0.00037492 | 5.6638 | 1078.4 | 1072.7362
564 | 0.11104 | 37.65 | 62.423 | 0.00037506 | 5.6739 | 1078.4 |  | 564 | 37.65 | 0.11104 | 62.423 | 0.00037506 | 5.6739 | 1078.4 | 1072.7261
565 | 0.11108 | 37.66 | 62.423 | 0.0003752 | 5.684 | 1078.4 |  | 565 | 37.66 | 0.11108 | 62.423 | 0.0003752 | 5.684 | 1078.4 | 1072.716
566 | 0.11113 | 37.67 | 62.423 | 0.00037534 | 5.694 | 1078.4 |  | 566 | 37.67 | 0.11113 | 62.423 | 0.00037534 | 5.694 | 1078.4 | 1072.706
567 | 0.11117 | 37.68 | 62.423 | 0.00037548 | 5.7041 | 1078.4 |  | 567 | 37.68 | 0.11117 | 62.423 | 0.00037548 | 5.7041 | 1078.4 | 1072.6959
568 | 0.11121 | 37.69 | 62.423 | 0.00037563 | 5.7142 | 1078.4 |  | 568 | 37.69 | 0.11121 | 62.423 | 0.00037563 | 5.7142 | 1078.4 | 1072.6858
569 | 0.11126 | 37.7 | 62.423 | 0.00037577 | 5.7242 | 1078.4 |  | 569 | 37.7 | 0.11126 | 62.423 | 0.00037577 | 5.7242 | 1078.4 | 1072.6758
570 | 0.1113 | 37.71 | 62.423 | 0.00037591 | 5.7343 | 1078.4 |  | 570 | 37.71 | 0.1113 | 62.423 | 0.00037591 | 5.7343 | 1078.4 | 1072.6657
571 | 0.11134 | 37.72 | 62.423 | 0.00037605 | 5.7443 | 1078.4 |  | 571 | 37.72 | 0.11134 | 62.423 | 0.00037605 | 5.7443 | 1078.4 | 1072.6557
572 | 0.11139 | 37.73 | 62.423 | 0.00037619 | 5.7544 | 1078.4 |  | 572 | 37.73 | 0.11139 | 62.423 | 0.00037619 | 5.7544 | 1078.4 | 1072.6456
573 | 0.11143 | 37.74 | 62.423 | 0.00037633 | 5.7645 | 1078.4 |  | 573 | 37.74 | 0.11143 | 62.423 | 0.00037633 | 5.7645 | 1078.4 | 1072.6355
574 | 0.11148 | 37.75 | 62.423 | 0.00037647 | 5.7745 | 1078.4 |  | 574 | 37.75 | 0.11148 | 62.423 | 0.00037647 | 5.7745 | 1078.4 | 1072.6255
575 | 0.11152 | 37.76 | 62.423 | 0.00037661 | 5.7846 | 1078.4 |  | 575 | 37.76 | 0.11152 | 62.423 | 0.00037661 | 5.7846 | 1078.4 | 1072.6154
576 | 0.11156 | 37.77 | 62.423 | 0.00037675 | 5.7947 | 1078.4 |  | 576 | 37.77 | 0.11156 | 62.423 | 0.00037675 | 5.7947 | 1078.4 | 1072.6053
577 | 0.11161 | 37.78 | 62.423 | 0.00037689 | 5.8047 | 1078.4 |  | 577 | 37.78 | 0.11161 | 62.423 | 0.00037689 | 5.8047 | 1078.4 | 1072.5953
578 | 0.11165 | 37.79 | 62.423 | 0.00037703 | 5.8148 | 1078.4 |  | 578 | 37.79 | 0.11165 | 62.423 | 0.00037703 | 5.8148 | 1078.4 | 1072.5852
579 | 0.11169 | 37.8 | 62.423 | 0.00037717 | 5.8248 | 1078.5 |  | 579 | 37.8 | 0.11169 | 62.423 | 0.00037717 | 5.8248 | 1078.5 | 1072.6752
580 | 0.11174 | 37.81 | 62.423 | 0.00037731 | 5.8349 | 1078.5 |  | 580 | 37.81 | 0.11174 | 62.423 | 0.00037731 | 5.8349 | 1078.5 | 1072.6651
581 | 0.11178 | 37.82 | 62.423 | 0.00037745 | 5.845 | 1078.5 |  | 581 | 37.82 | 0.11178 | 62.423 | 0.00037745 | 5.845 | 1078.5 | 1072.655
582 | 0.11183 | 37.83 | 62.423 | 0.00037759 | 5.855 | 1078.5 |  | 582 | 37.83 | 0.11183 | 62.423 | 0.00037759 | 5.855 | 1078.5 | 1072.645
583 | 0.11187 | 37.84 | 62.423 | 0.00037773 | 5.8651 | 1078.5 |  | 583 | 37.84 | 0.11187 | 62.423 | 0.00037773 | 5.8651 | 1078.5 | 1072.6349
584 | 0.11191 | 37.85 | 62.423 | 0.00037788 | 5.8752 | 1078.5 |  | 584 | 37.85 | 0.11191 | 62.423 | 0.00037788 | 5.8752 | 1078.5 | 1072.6248
585 | 0.11196 | 37.86 | 62.423 | 0.00037802 | 5.8852 | 1078.5 |  | 585 | 37.86 | 0.11196 | 62.423 | 0.00037802 | 5.8852 | 1078.5 | 1072.6148
586 | 0.112 | 37.87 | 62.423 | 0.00037816 | 5.8953 | 1078.5 |  | 586 | 37.87 | 0.112 | 62.423 | 0.00037816 | 5.8953 | 1078.5 | 1072.6047
587 | 0.11205 | 37.88 | 62.423 | 0.0003783 | 5.9053 | 1078.5 |  | 587 | 37.88 | 0.11205 | 62.423 | 0.0003783 | 5.9053 | 1078.5 | 1072.5947
588 | 0.11209 | 37.89 | 62.423 | 0.00037844 | 5.9154 | 1078.5 |  | 588 | 37.89 | 0.11209 | 62.423 | 0.00037844 | 5.9154 | 1078.5 | 1072.5846
589 | 0.11213 | 37.9 | 62.423 | 0.00037858 | 5.9255 | 1078.5 |  | 589 | 37.9 | 0.11213 | 62.423 | 0.00037858 | 5.9255 | 1078.5 | 1072.5745
590 | 0.11218 | 37.91 | 62.423 | 0.00037872 | 5.9355 | 1078.5 |  | 590 | 37.91 | 0.11218 | 62.423 | 0.00037872 | 5.9355 | 1078.5 | 1072.5645
591 | 0.11222 | 37.92 | 62.423 | 0.00037886 | 5.9456 | 1078.5 |  | 591 | 37.92 | 0.11222 | 62.423 | 0.00037886 | 5.9456 | 1078.5 | 1072.5544
592 | 0.11227 | 37.93 | 62.423 | 0.00037901 | 5.9556 | 1078.5 |  | 592 | 37.93 | 0.11227 | 62.423 | 0.00037901 | 5.9556 | 1078.5 | 1072.5444
593 | 0.11231 | 37.94 | 62.423 | 0.00037915 | 5.9657 | 1078.5 |  | 593 | 37.94 | 0.11231 | 62.423 | 0.00037915 | 5.9657 | 1078.5 | 1072.5343
594 | 0.11236 | 37.95 | 62.423 | 0.00037929 | 5.9758 | 1078.5 |  | 594 | 37.95 | 0.11236 | 62.423 | 0.00037929 | 5.9758 | 1078.5 | 1072.5242
595 | 0.1124 | 37.96 | 62.423 | 0.00037943 | 5.9858 | 1078.5 |  | 595 | 37.96 | 0.1124 | 62.423 | 0.00037943 | 5.9858 | 1078.5 | 1072.5142
596 | 0.11244 | 37.97 | 62.423 | 0.00037957 | 5.9959 | 1078.5 |  | 596 | 37.97 | 0.11244 | 62.423 | 0.00037957 | 5.9959 | 1078.5 | 1072.5041
597 | 0.11249 | 37.98 | 62.423 | 0.00037971 | 6.006 | 1078.5 |  | 597 | 37.98 | 0.11249 | 62.423 | 0.00037971 | 6.006 | 1078.5 | 1072.494
598 | 0.11253 | 37.99 | 62.423 | 0.00037985 | 6.016 | 1078.5 |  | 598 | 37.99 | 0.11253 | 62.423 | 0.00037985 | 6.016 | 1078.5 | 1072.484
599 | 0.11258 | 38 | 62.423 | 0.00038 | 6.0261 | 1078.5 |  | 599 | 38 | 0.11258 | 62.423 | 0.00038 | 6.0261 | 1078.5 | 1072.4739
600 | 0.11262 | 38.01 | 62.423 | 0.00038014 | 6.0361 | 1078.5 |  | 600 | 38.01 | 0.11262 | 62.423 | 0.00038014 | 6.0361 | 1078.5 | 1072.4639
601 | 0.11266 | 38.02 | 62.423 | 0.00038028 | 6.0462 | 1078.5 |  | 601 | 38.02 | 0.11266 | 62.423 | 0.00038028 | 6.0462 | 1078.5 | 1072.4538
602 | 0.11271 | 38.03 | 62.423 | 0.00038042 | 6.0563 | 1078.6 |  | 602 | 38.03 | 0.11271 | 62.423 | 0.00038042 | 6.0563 | 1078.6 | 1072.5437
603 | 0.11275 | 38.04 | 62.423 | 0.00038056 | 6.0663 | 1078.6 |  | 603 | 38.04 | 0.11275 | 62.423 | 0.00038056 | 6.0663 | 1078.6 | 1072.5337
604 | 0.1128 | 38.05 | 62.423 | 0.00038071 | 6.0764 | 1078.6 |  | 604 | 38.05 | 0.1128 | 62.423 | 0.00038071 | 6.0764 | 1078.6 | 1072.5236
605 | 0.11284 | 38.06 | 62.423 | 0.00038085 | 6.0864 | 1078.6 |  | 605 | 38.06 | 0.11284 | 62.423 | 0.00038085 | 6.0864 | 1078.6 | 1072.5136
606 | 0.11289 | 38.07 | 62.423 | 0.00038099 | 6.0965 | 1078.6 |  | 606 | 38.07 | 0.11289 | 62.423 | 0.00038099 | 6.0965 | 1078.6 | 1072.5035
607 | 0.11293 | 38.08 | 62.423 | 0.00038113 | 6.1066 | 1078.6 |  | 607 | 38.08 | 0.11293 | 62.423 | 0.00038113 | 6.1066 | 1078.6 | 1072.4934
608 | 0.11297 | 38.09 | 62.423 | 0.00038127 | 6.1166 | 1078.6 |  | 608 | 38.09 | 0.11297 | 62.423 | 0.00038127 | 6.1166 | 1078.6 | 1072.4834
609 | 0.11302 | 38.1 | 62.423 | 0.00038142 | 6.1267 | 1078.6 |  | 609 | 38.1 | 0.11302 | 62.423 | 0.00038142 | 6.1267 | 1078.6 | 1072.4733
610 | 0.11306 | 38.11 | 62.423 | 0.00038156 | 6.1368 | 1078.6 |  | 610 | 38.11 | 0.11306 | 62.423 | 0.00038156 | 6.1368 | 1078.6 | 1072.4632
611 | 0.11311 | 38.12 | 62.423 | 0.0003817 | 6.1468 | 1078.6 |  | 611 | 38.12 | 0.11311 | 62.423 | 0.0003817 | 6.1468 | 1078.6 | 1072.4532
612 | 0.11315 | 38.13 | 62.423 | 0.00038184 | 6.1569 | 1078.6 |  | 612 | 38.13 | 0.11315 | 62.423 | 0.00038184 | 6.1569 | 1078.6 | 1072.4431
613 | 0.1132 | 38.14 | 62.423 | 0.00038198 | 6.1669 | 1078.6 |  | 613 | 38.14 | 0.1132 | 62.423 | 0.00038198 | 6.1669 | 1078.6 | 1072.4331
614 | 0.11324 | 38.15 | 62.423 | 0.00038213 | 6.177 | 1078.6 |  | 614 | 38.15 | 0.11324 | 62.423 | 0.00038213 | 6.177 | 1078.6 | 1072.423
615 | 0.11329 | 38.16 | 62.423 | 0.00038227 | 6.1871 | 1078.6 |  | 615 | 38.16 | 0.11329 | 62.423 | 0.00038227 | 6.1871 | 1078.6 | 1072.4129
616 | 0.11333 | 38.17 | 62.423 | 0.00038241 | 6.1971 | 1078.6 |  | 616 | 38.17 | 0.11333 | 62.423 | 0.00038241 | 6.1971 | 1078.6 | 1072.4029
617 | 0.11337 | 38.18 | 62.423 | 0.00038255 | 6.2072 | 1078.6 |  | 617 | 38.18 | 0.11337 | 62.423 | 0.00038255 | 6.2072 | 1078.6 | 1072.3928
618 | 0.11342 | 38.19 | 62.423 | 0.0003827 | 6.2172 | 1078.6 |  | 618 | 38.19 | 0.11342 | 62.423 | 0.0003827 | 6.2172 | 1078.6 | 1072.3828
619 | 0.11346 | 38.2 | 62.423 | 0.00038284 | 6.2273 | 1078.6 |  | 619 | 38.2 | 0.11346 | 62.423 | 0.00038284 | 6.2273 | 1078.6 | 1072.3727
620 | 0.11351 | 38.21 | 62.423 | 0.00038298 | 6.2374 | 1078.6 |  | 620 | 38.21 | 0.11351 | 62.423 | 0.00038298 | 6.2374 | 1078.6 | 1072.3626
621 | 0.11355 | 38.22 | 62.423 | 0.00038312 | 6.2474 | 1078.6 |  | 621 | 38.22 | 0.11355 | 62.423 | 0.00038312 | 6.2474 | 1078.6 | 1072.3526
622 | 0.1136 | 38.23 | 62.423 | 0.00038327 | 6.2575 | 1078.6 |  | 622 | 38.23 | 0.1136 | 62.423 | 0.00038327 | 6.2575 | 1078.6 | 1072.3425
623 | 0.11364 | 38.24 | 62.423 | 0.00038341 | 6.2675 | 1078.6 |  | 623 | 38.24 | 0.11364 | 62.423 | 0.00038341 | 6.2675 | 1078.6 | 1072.3325
624 | 0.11369 | 38.25 | 62.423 | 0.00038355 | 6.2776 | 1078.7 |  | 624 | 38.25 | 0.11369 | 62.423 | 0.00038355 | 6.2776 | 1078.7 | 1072.4224
625 | 0.11373 | 38.26 | 62.423 | 0.0003837 | 6.2877 | 1078.7 |  | 625 | 38.26 | 0.11373 | 62.423 | 0.0003837 | 6.2877 | 1078.7 | 1072.4123
626 | 0.11378 | 38.27 | 62.423 | 0.00038384 | 6.2977 | 1078.7 |  | 626 | 38.27 | 0.11378 | 62.423 | 0.00038384 | 6.2977 | 1078.7 | 1072.4023
627 | 0.11382 | 38.28 | 62.423 | 0.00038398 | 6.3078 | 1078.7 |  | 627 | 38.28 | 0.11382 | 62.423 | 0.00038398 | 6.3078 | 1078.7 | 1072.3922
628 | 0.11387 | 38.29 | 62.423 | 0.00038412 | 6.3178 | 1078.7 |  | 628 | 38.29 | 0.11387 | 62.423 | 0.00038412 | 6.3178 | 1078.7 | 1072.3822
629 | 0.11391 | 38.3 | 62.423 | 0.00038427 | 6.3279 | 1078.7 |  | 629 | 38.3 | 0.11391 | 62.423 | 0.00038427 | 6.3279 | 1078.7 | 1072.3721
630 | 0.11395 | 38.31 | 62.423 | 0.00038441 | 6.338 | 1078.7 |  | 630 | 38.31 | 0.11395 | 62.423 | 0.00038441 | 6.338 | 1078.7 | 1072.362
631 | 0.114 | 38.32 | 62.423 | 0.00038455 | 6.348 | 1078.7 |  | 631 | 38.32 | 0.114 | 62.423 | 0.00038455 | 6.348 | 1078.7 | 1072.352
632 | 0.11404 | 38.33 | 62.423 | 0.0003847 | 6.3581 | 1078.7 |  | 632 | 38.33 | 0.11404 | 62.423 | 0.0003847 | 6.3581 | 1078.7 | 1072.3419
633 | 0.11409 | 38.34 | 62.423 | 0.00038484 | 6.3682 | 1078.7 |  | 633 | 38.34 | 0.11409 | 62.423 | 0.00038484 | 6.3682 | 1078.7 | 1072.3318
634 | 0.11413 | 38.35 | 62.423 | 0.00038498 | 6.3782 | 1078.7 |  | 634 | 38.35 | 0.11413 | 62.423 | 0.00038498 | 6.3782 | 1078.7 | 1072.3218
635 | 0.11418 | 38.36 | 62.423 | 0.00038513 | 6.3883 | 1078.7 |  | 635 | 38.36 | 0.11418 | 62.423 | 0.00038513 | 6.3883 | 1078.7 | 1072.3117
636 | 0.11422 | 38.37 | 62.423 | 0.00038527 | 6.3983 | 1078.7 |  | 636 | 38.37 | 0.11422 | 62.423 | 0.00038527 | 6.3983 | 1078.7 | 1072.3017
637 | 0.11427 | 38.38 | 62.423 | 0.00038541 | 6.4084 | 1078.7 |  | 637 | 38.38 | 0.11427 | 62.423 | 0.00038541 | 6.4084 | 1078.7 | 1072.2916
638 | 0.11431 | 38.39 | 62.423 | 0.00038556 | 6.4185 | 1078.7 |  | 638 | 38.39 | 0.11431 | 62.423 | 0.00038556 | 6.4185 | 1078.7 | 1072.2815
639 | 0.11436 | 38.4 | 62.423 | 0.0003857 | 6.4285 | 1078.7 |  | 639 | 38.4 | 0.11436 | 62.423 | 0.0003857 | 6.4285 | 1078.7 | 1072.2715
640 | 0.1144 | 38.41 | 62.423 | 0.00038584 | 6.4386 | 1078.7 |  | 640 | 38.41 | 0.1144 | 62.423 | 0.00038584 | 6.4386 | 1078.7 | 1072.2614
641 | 0.11445 | 38.42 | 62.423 | 0.00038599 | 6.4486 | 1078.7 |  | 641 | 38.42 | 0.11445 | 62.423 | 0.00038599 | 6.4486 | 1078.7 | 1072.2514
642 | 0.11449 | 38.43 | 62.423 | 0.00038613 | 6.4587 | 1078.7 |  | 642 | 38.43 | 0.11449 | 62.423 | 0.00038613 | 6.4587 | 1078.7 | 1072.2413
643 | 0.11454 | 38.44 | 62.423 | 0.00038628 | 6.4688 | 1078.7 |  | 643 | 38.44 | 0.11454 | 62.423 | 0.00038628 | 6.4688 | 1078.7 | 1072.2312
644 | 0.11458 | 38.45 | 62.423 | 0.00038642 | 6.4788 | 1078.7 |  | 644 | 38.45 | 0.11458 | 62.423 | 0.00038642 | 6.4788 | 1078.7 | 1072.2212
645 | 0.11463 | 38.46 | 62.423 | 0.00038656 | 6.4889 | 1078.7 |  | 645 | 38.46 | 0.11463 | 62.423 | 0.00038656 | 6.4889 | 1078.7 | 1072.2111
646 | 0.11467 | 38.47 | 62.423 | 0.00038671 | 6.4989 | 1078.7 |  | 646 | 38.47 | 0.11467 | 62.423 | 0.00038671 | 6.4989 | 1078.7 | 1072.2011
647 | 0.11472 | 38.48 | 62.423 | 0.00038685 | 6.509 | 1078.8 |  | 647 | 38.48 | 0.11472 | 62.423 | 0.00038685 | 6.509 | 1078.8 | 1072.291
648 | 0.11476 | 38.49 | 62.423 | 0.000387 | 6.5191 | 1078.8 |  | 648 | 38.49 | 0.11476 | 62.423 | 0.000387 | 6.5191 | 1078.8 | 1072.2809
649 | 0.11481 | 38.5 | 62.423 | 0.00038714 | 6.5291 | 1078.8 |  | 649 | 38.5 | 0.11481 | 62.423 | 0.00038714 | 6.5291 | 1078.8 | 1072.2709
650 | 0.11485 | 38.51 | 62.423 | 0.00038728 | 6.5392 | 1078.8 |  | 650 | 38.51 | 0.11485 | 62.423 | 0.00038728 | 6.5392 | 1078.8 | 1072.2608
651 | 0.1149 | 38.52 | 62.423 | 0.00038743 | 6.5492 | 1078.8 |  | 651 | 38.52 | 0.1149 | 62.423 | 0.00038743 | 6.5492 | 1078.8 | 1072.2508
652 | 0.11494 | 38.53 | 62.423 | 0.00038757 | 6.5593 | 1078.8 |  | 652 | 38.53 | 0.11494 | 62.423 | 0.00038757 | 6.5593 | 1078.8 | 1072.2407
653 | 0.11499 | 38.54 | 62.423 | 0.00038772 | 6.5694 | 1078.8 |  | 653 | 38.54 | 0.11499 | 62.423 | 0.00038772 | 6.5694 | 1078.8 | 1072.2306
654 | 0.11503 | 38.55 | 62.423 | 0.00038786 | 6.5794 | 1078.8 |  | 654 | 38.55 | 0.11503 | 62.423 | 0.00038786 | 6.5794 | 1078.8 | 1072.2206
655 | 0.11508 | 38.56 | 62.423 | 0.000388 | 6.5895 | 1078.8 |  | 655 | 38.56 | 0.11508 | 62.423 | 0.000388 | 6.5895 | 1078.8 | 1072.2105
656 | 0.11512 | 38.57 | 62.423 | 0.00038815 | 6.5995 | 1078.8 |  | 656 | 38.57 | 0.11512 | 62.423 | 0.00038815 | 6.5995 | 1078.8 | 1072.2005
657 | 0.11517 | 38.58 | 62.423 | 0.00038829 | 6.6096 | 1078.8 |  | 657 | 38.58 | 0.11517 | 62.423 | 0.00038829 | 6.6096 | 1078.8 | 1072.1904
658 | 0.11521 | 38.59 | 62.423 | 0.00038844 | 6.6196 | 1078.8 |  | 658 | 38.59 | 0.11521 | 62.423 | 0.00038844 | 6.6196 | 1078.8 | 1072.1804
659 | 0.11526 | 38.6 | 62.423 | 0.00038858 | 6.6297 | 1078.8 |  | 659 | 38.6 | 0.11526 | 62.423 | 0.00038858 | 6.6297 | 1078.8 | 1072.1703
660 | 0.1153 | 38.61 | 62.423 | 0.00038873 | 6.6398 | 1078.8 |  | 660 | 38.61 | 0.1153 | 62.423 | 0.00038873 | 6.6398 | 1078.8 | 1072.1602
661 | 0.11535 | 38.62 | 62.423 | 0.00038887 | 6.6498 | 1078.8 |  | 661 | 38.62 | 0.11535 | 62.423 | 0.00038887 | 6.6498 | 1078.8 | 1072.1502
662 | 0.11539 | 38.63 | 62.423 | 0.00038902 | 6.6599 | 1078.8 |  | 662 | 38.63 | 0.11539 | 62.423 | 0.00038902 | 6.6599 | 1078.8 | 1072.1401
663 | 0.11544 | 38.64 | 62.423 | 0.00038916 | 6.6699 | 1078.8 |  | 663 | 38.64 | 0.11544 | 62.423 | 0.00038916 | 6.6699 | 1078.8 | 1072.1301
664 | 0.11548 | 38.65 | 62.423 | 0.00038931 | 6.68 | 1078.8 |  | 664 | 38.65 | 0.11548 | 62.423 | 0.00038931 | 6.68 | 1078.8 | 1072.12
665 | 0.11553 | 38.66 | 62.423 | 0.00038945 | 6.6901 | 1078.8 |  | 665 | 38.66 | 0.11553 | 62.423 | 0.00038945 | 6.6901 | 1078.8 | 1072.1099
666 | 0.11557 | 38.67 | 62.423 | 0.00038959 | 6.7001 | 1078.8 |  | 666 | 38.67 | 0.11557 | 62.423 | 0.00038959 | 6.7001 | 1078.8 | 1072.0999
667 | 0.11562 | 38.68 | 62.423 | 0.00038974 | 6.7102 | 1078.8 |  | 667 | 38.68 | 0.11562 | 62.423 | 0.00038974 | 6.7102 | 1078.8 | 1072.0898
668 | 0.11566 | 38.69 | 62.423 | 0.00038988 | 6.7202 | 1078.8 |  | 668 | 38.69 | 0.11566 | 62.423 | 0.00038988 | 6.7202 | 1078.8 | 1072.0798
669 | 0.11571 | 38.7 | 62.423 | 0.00039003 | 6.7303 | 1078.8 |  | 669 | 38.7 | 0.11571 | 62.423 | 0.00039003 | 6.7303 | 1078.8 | 1072.0697
670 | 0.11576 | 38.71 | 62.423 | 0.00039017 | 6.7404 | 1078.9 |  | 670 | 38.71 | 0.11576 | 62.423 | 0.00039017 | 6.7404 | 1078.9 | 1072.1596
671 | 0.1158 | 38.72 | 62.423 | 0.00039032 | 6.7504 | 1078.9 |  | 671 | 38.72 | 0.1158 | 62.423 | 0.00039032 | 6.7504 | 1078.9 | 1072.1496
672 | 0.11585 | 38.73 | 62.423 | 0.00039046 | 6.7605 | 1078.9 |  | 672 | 38.73 | 0.11585 | 62.423 | 0.00039046 | 6.7605 | 1078.9 | 1072.1395
673 | 0.11589 | 38.74 | 62.423 | 0.00039061 | 6.7705 | 1078.9 |  | 673 | 38.74 | 0.11589 | 62.423 | 0.00039061 | 6.7705 | 1078.9 | 1072.1295
674 | 0.11594 | 38.75 | 62.423 | 0.00039075 | 6.7806 | 1078.9 |  | 674 | 38.75 | 0.11594 | 62.423 | 0.00039075 | 6.7806 | 1078.9 | 1072.1194
675 | 0.11598 | 38.76 | 62.423 | 0.0003909 | 6.7907 | 1078.9 |  | 675 | 38.76 | 0.11598 | 62.423 | 0.0003909 | 6.7907 | 1078.9 | 1072.1093
676 | 0.11603 | 38.77 | 62.423 | 0.00039105 | 6.8007 | 1078.9 |  | 676 | 38.77 | 0.11603 | 62.423 | 0.00039105 | 6.8007 | 1078.9 | 1072.0993
677 | 0.11607 | 38.78 | 62.423 | 0.00039119 | 6.8108 | 1078.9 |  | 677 | 38.78 | 0.11607 | 62.423 | 0.00039119 | 6.8108 | 1078.9 | 1072.0892
678 | 0.11612 | 38.79 | 62.423 | 0.00039134 | 6.8208 | 1078.9 |  | 678 | 38.79 | 0.11612 | 62.423 | 0.00039134 | 6.8208 | 1078.9 | 1072.0792
679 | 0.11616 | 38.8 | 62.423 | 0.00039148 | 6.8309 | 1078.9 |  | 679 | 38.8 | 0.11616 | 62.423 | 0.00039148 | 6.8309 | 1078.9 | 1072.0691
680 | 0.11621 | 38.81 | 62.423 | 0.00039163 | 6.8409 | 1078.9 |  | 680 | 38.81 | 0.11621 | 62.423 | 0.00039163 | 6.8409 | 1078.9 | 1072.0591
681 | 0.11625 | 38.82 | 62.423 | 0.00039177 | 6.851 | 1078.9 |  | 681 | 38.82 | 0.11625 | 62.423 | 0.00039177 | 6.851 | 1078.9 | 1072.049
682 | 0.1163 | 38.83 | 62.423 | 0.00039192 | 6.8611 | 1078.9 |  | 682 | 38.83 | 0.1163 | 62.423 | 0.00039192 | 6.8611 | 1078.9 | 1072.0389
683 | 0.11635 | 38.84 | 62.423 | 0.00039206 | 6.8711 | 1078.9 |  | 683 | 38.84 | 0.11635 | 62.423 | 0.00039206 | 6.8711 | 1078.9 | 1072.0289
684 | 0.11639 | 38.85 | 62.423 | 0.00039221 | 6.8812 | 1078.9 |  | 684 | 38.85 | 0.11639 | 62.423 | 0.00039221 | 6.8812 | 1078.9 | 1072.0188
685 | 0.11644 | 38.86 | 62.423 | 0.00039236 | 6.8912 | 1078.9 |  | 685 | 38.86 | 0.11644 | 62.423 | 0.00039236 | 6.8912 | 1078.9 | 1072.0088
686 | 0.11648 | 38.87 | 62.423 | 0.0003925 | 6.9013 | 1078.9 |  | 686 | 38.87 | 0.11648 | 62.423 | 0.0003925 | 6.9013 | 1078.9 | 1071.9987
687 | 0.11653 | 38.88 | 62.423 | 0.00039265 | 6.9114 | 1078.9 |  | 687 | 38.88 | 0.11653 | 62.423 | 0.00039265 | 6.9114 | 1078.9 | 1071.9886
688 | 0.11657 | 38.89 | 62.423 | 0.00039279 | 6.9214 | 1078.9 |  | 688 | 38.89 | 0.11657 | 62.423 | 0.00039279 | 6.9214 | 1078.9 | 1071.9786
689 | 0.11662 | 38.9 | 62.423 | 0.00039294 | 6.9315 | 1078.9 |  | 689 | 38.9 | 0.11662 | 62.423 | 0.00039294 | 6.9315 | 1078.9 | 1071.9685
690 | 0.11666 | 38.91 | 62.423 | 0.00039308 | 6.9415 | 1078.9 |  | 690 | 38.91 | 0.11666 | 62.423 | 0.00039308 | 6.9415 | 1078.9 | 1071.9585
691 | 0.11671 | 38.92 | 62.423 | 0.00039323 | 6.9516 | 1078.9 |  | 691 | 38.92 | 0.11671 | 62.423 | 0.00039323 | 6.9516 | 1078.9 | 1071.9484
692 | 0.11676 | 38.93 | 62.423 | 0.00039338 | 6.9617 | 1078.9 |  | 692 | 38.93 | 0.11676 | 62.423 | 0.00039338 | 6.9617 | 1078.9 | 1071.9383
693 | 0.1168 | 38.94 | 62.423 | 0.00039352 | 6.9717 | 1079 |  | 693 | 38.94 | 0.1168 | 62.423 | 0.00039352 | 6.9717 | 1079 | 1072.0283
694 | 0.11685 | 38.95 | 62.423 | 0.00039367 | 6.9818 | 1079 |  | 694 | 38.95 | 0.11685 | 62.423 | 0.00039367 | 6.9818 | 1079 | 1072.0182
695 | 0.11689 | 38.96 | 62.423 | 0.00039381 | 6.9918 | 1079 |  | 695 | 38.96 | 0.11689 | 62.423 | 0.00039381 | 6.9918 | 1079 | 1072.0082
696 | 0.11694 | 38.97 | 62.423 | 0.00039396 | 7.0019 | 1079 |  | 696 | 38.97 | 0.11694 | 62.423 | 0.00039396 | 7.0019 | 1079 | 1071.9981
697 | 0.11698 | 38.98 | 62.423 | 0.00039411 | 7.0119 | 1079 |  | 697 | 38.98 | 0.11698 | 62.423 | 0.00039411 | 7.0119 | 1079 | 1071.9881
698 | 0.11703 | 38.99 | 62.423 | 0.00039425 | 7.022 | 1079 |  | 698 | 38.99 | 0.11703 | 62.423 | 0.00039425 | 7.022 | 1079 | 1071.978
699 | 0.11708 | 39 | 62.423 | 0.0003944 | 7.0321 | 1079 |  | 699 | 39 | 0.11708 | 62.423 | 0.0003944 | 7.0321 | 1079 | 1071.9679
700 | 0.11712 | 39.01 | 62.423 | 0.00039455 | 7.0421 | 1079 |  | 700 | 39.01 | 0.11712 | 62.423 | 0.00039455 | 7.0421 | 1079 | 1071.9579
701 | 0.11717 | 39.02 | 62.423 | 0.00039469 | 7.0522 | 1079 |  | 701 | 39.02 | 0.11717 | 62.423 | 0.00039469 | 7.0522 | 1079 | 1071.9478
702 | 0.11721 | 39.03 | 62.423 | 0.00039484 | 7.0622 | 1079 |  | 702 | 39.03 | 0.11721 | 62.423 | 0.00039484 | 7.0622 | 1079 | 1071.9378
703 | 0.11726 | 39.04 | 62.423 | 0.00039499 | 7.0723 | 1079 |  | 703 | 39.04 | 0.11726 | 62.423 | 0.00039499 | 7.0723 | 1079 | 1071.9277
704 | 0.11731 | 39.05 | 62.423 | 0.00039513 | 7.0823 | 1079 |  | 704 | 39.05 | 0.11731 | 62.423 | 0.00039513 | 7.0823 | 1079 | 1071.9177
705 | 0.11735 | 39.06 | 62.423 | 0.00039528 | 7.0924 | 1079 |  | 705 | 39.06 | 0.11735 | 62.423 | 0.00039528 | 7.0924 | 1079 | 1071.9076
706 | 0.1174 | 39.07 | 62.423 | 0.00039543 | 7.1025 | 1079 |  | 706 | 39.07 | 0.1174 | 62.423 | 0.00039543 | 7.1025 | 1079 | 1071.8975
707 | 0.11744 | 39.08 | 62.423 | 0.00039557 | 7.1125 | 1079 |  | 707 | 39.08 | 0.11744 | 62.423 | 0.00039557 | 7.1125 | 1079 | 1071.8875
708 | 0.11749 | 39.09 | 62.423 | 0.00039572 | 7.1226 | 1079 |  | 708 | 39.09 | 0.11749 | 62.423 | 0.00039572 | 7.1226 | 1079 | 1071.8774
709 | 0.11753 | 39.1 | 62.423 | 0.00039587 | 7.1326 | 1079 |  | 709 | 39.1 | 0.11753 | 62.423 | 0.00039587 | 7.1326 | 1079 | 1071.8674
710 | 0.11758 | 39.11 | 62.423 | 0.00039601 | 7.1427 | 1079 |  | 710 | 39.11 | 0.11758 | 62.423 | 0.00039601 | 7.1427 | 1079 | 1071.8573
711 | 0.11763 | 39.12 | 62.423 | 0.00039616 | 7.1528 | 1079 |  | 711 | 39.12 | 0.11763 | 62.423 | 0.00039616 | 7.1528 | 1079 | 1071.8472
712 | 0.11767 | 39.13 | 62.423 | 0.00039631 | 7.1628 | 1079 |  | 712 | 39.13 | 0.11767 | 62.423 | 0.00039631 | 7.1628 | 1079 | 1071.8372
713 | 0.11772 | 39.14 | 62.423 | 0.00039645 | 7.1729 | 1079 |  | 713 | 39.14 | 0.11772 | 62.423 | 0.00039645 | 7.1729 | 1079 | 1071.8271
714 | 0.11776 | 39.15 | 62.423 | 0.0003966 | 7.1829 | 1079 |  | 714 | 39.15 | 0.11776 | 62.423 | 0.0003966 | 7.1829 | 1079 | 1071.8171
715 | 0.11781 | 39.16 | 62.423 | 0.00039675 | 7.193 | 1079 |  | 715 | 39.16 | 0.11781 | 62.423 | 0.00039675 | 7.193 | 1079 | 1071.807
716 | 0.11786 | 39.17 | 62.423 | 0.0003969 | 7.203 | 1079.1 |  | 716 | 39.17 | 0.11786 | 62.423 | 0.0003969 | 7.203 | 1079.1 | 1071.897
717 | 0.1179 | 39.18 | 62.423 | 0.00039704 | 7.2131 | 1079.1 |  | 717 | 39.18 | 0.1179 | 62.423 | 0.00039704 | 7.2131 | 1079.1 | 1071.8869
718 | 0.11795 | 39.19 | 62.423 | 0.00039719 | 7.2232 | 1079.1 |  | 718 | 39.19 | 0.11795 | 62.423 | 0.00039719 | 7.2232 | 1079.1 | 1071.8768
719 | 0.118 | 39.2 | 62.423 | 0.00039734 | 7.2332 | 1079.1 |  | 719 | 39.2 | 0.118 | 62.423 | 0.00039734 | 7.2332 | 1079.1 | 1071.8668
720 | 0.11804 | 39.21 | 62.423 | 0.00039748 | 7.2433 | 1079.1 |  | 720 | 39.21 | 0.11804 | 62.423 | 0.00039748 | 7.2433 | 1079.1 | 1071.8567
721 | 0.11809 | 39.22 | 62.423 | 0.00039763 | 7.2533 | 1079.1 |  | 721 | 39.22 | 0.11809 | 62.423 | 0.00039763 | 7.2533 | 1079.1 | 1071.8467
722 | 0.11813 | 39.23 | 62.423 | 0.00039778 | 7.2634 | 1079.1 |  | 722 | 39.23 | 0.11813 | 62.423 | 0.00039778 | 7.2634 | 1079.1 | 1071.8366
723 | 0.11818 | 39.24 | 62.423 | 0.00039793 | 7.2734 | 1079.1 |  | 723 | 39.24 | 0.11818 | 62.423 | 0.00039793 | 7.2734 | 1079.1 | 1071.8266
724 | 0.11823 | 39.25 | 62.423 | 0.00039807 | 7.2835 | 1079.1 |  | 724 | 39.25 | 0.11823 | 62.423 | 0.00039807 | 7.2835 | 1079.1 | 1071.8165
725 | 0.11827 | 39.26 | 62.423 | 0.00039822 | 7.2936 | 1079.1 |  | 725 | 39.26 | 0.11827 | 62.423 | 0.00039822 | 7.2936 | 1079.1 | 1071.8064
726 | 0.11832 | 39.27 | 62.423 | 0.00039837 | 7.3036 | 1079.1 |  | 726 | 39.27 | 0.11832 | 62.423 | 0.00039837 | 7.3036 | 1079.1 | 1071.7964
727 | 0.11836 | 39.28 | 62.423 | 0.00039852 | 7.3137 | 1079.1 |  | 727 | 39.28 | 0.11836 | 62.423 | 0.00039852 | 7.3137 | 1079.1 | 1071.7863
728 | 0.11841 | 39.29 | 62.423 | 0.00039867 | 7.3237 | 1079.1 |  | 728 | 39.29 | 0.11841 | 62.423 | 0.00039867 | 7.3237 | 1079.1 | 1071.7763
729 | 0.11846 | 39.3 | 62.423 | 0.00039881 | 7.3338 | 1079.1 |  | 729 | 39.3 | 0.11846 | 62.423 | 0.00039881 | 7.3338 | 1079.1 | 1071.7662
730 | 0.1185 | 39.31 | 62.423 | 0.00039896 | 7.3438 | 1079.1 |  | 730 | 39.31 | 0.1185 | 62.423 | 0.00039896 | 7.3438 | 1079.1 | 1071.7562
731 | 0.11855 | 39.32 | 62.423 | 0.00039911 | 7.3539 | 1079.1 |  | 731 | 39.32 | 0.11855 | 62.423 | 0.00039911 | 7.3539 | 1079.1 | 1071.7461
732 | 0.1186 | 39.33 | 62.423 | 0.00039926 | 7.364 | 1079.1 |  | 732 | 39.33 | 0.1186 | 62.423 | 0.00039926 | 7.364 | 1079.1 | 1071.736
733 | 0.11864 | 39.34 | 62.423 | 0.0003994 | 7.374 | 1079.1 |  | 733 | 39.34 | 0.11864 | 62.423 | 0.0003994 | 7.374 | 1079.1 | 1071.726
734 | 0.11869 | 39.35 | 62.423 | 0.00039955 | 7.3841 | 1079.1 |  | 734 | 39.35 | 0.11869 | 62.423 | 0.00039955 | 7.3841 | 1079.1 | 1071.7159
735 | 0.11873 | 39.36 | 62.423 | 0.0003997 | 7.3941 | 1079.1 |  | 735 | 39.36 | 0.11873 | 62.423 | 0.0003997 | 7.3941 | 1079.1 | 1071.7059
736 | 0.11878 | 39.37 | 62.423 | 0.00039985 | 7.4042 | 1079.1 |  | 736 | 39.37 | 0.11878 | 62.423 | 0.00039985 | 7.4042 | 1079.1 | 1071.6958
737 | 0.11883 | 39.38 | 62.423 | 0.0004 | 7.4142 | 1079.1 |  | 737 | 39.38 | 0.11883 | 62.423 | 0.0004 | 7.4142 | 1079.1 | 1071.6858
738 | 0.11887 | 39.39 | 62.423 | 0.00040015 | 7.4243 | 1079.1 |  | 738 | 39.39 | 0.11887 | 62.423 | 0.00040015 | 7.4243 | 1079.1 | 1071.6757
739 | 0.11892 | 39.4 | 62.423 | 0.00040029 | 7.4344 | 1079.2 |  | 739 | 39.4 | 0.11892 | 62.423 | 0.00040029 | 7.4344 | 1079.2 | 1071.7656
740 | 0.11897 | 39.41 | 62.423 | 0.00040044 | 7.4444 | 1079.2 |  | 740 | 39.41 | 0.11897 | 62.423 | 0.00040044 | 7.4444 | 1079.2 | 1071.7556
741 | 0.11901 | 39.42 | 62.423 | 0.00040059 | 7.4545 | 1079.2 |  | 741 | 39.42 | 0.11901 | 62.423 | 0.00040059 | 7.4545 | 1079.2 | 1071.7455
742 | 0.11906 | 39.43 | 62.423 | 0.00040074 | 7.4645 | 1079.2 |  | 742 | 39.43 | 0.11906 | 62.423 | 0.00040074 | 7.4645 | 1079.2 | 1071.7355
743 | 0.11911 | 39.44 | 62.423 | 0.00040089 | 7.4746 | 1079.2 |  | 743 | 39.44 | 0.11911 | 62.423 | 0.00040089 | 7.4746 | 1079.2 | 1071.7254
744 | 0.11915 | 39.45 | 62.423 | 0.00040104 | 7.4846 | 1079.2 |  | 744 | 39.45 | 0.11915 | 62.423 | 0.00040104 | 7.4846 | 1079.2 | 1071.7154
745 | 0.1192 | 39.46 | 62.423 | 0.00040118 | 7.4947 | 1079.2 |  | 745 | 39.46 | 0.1192 | 62.423 | 0.00040118 | 7.4947 | 1079.2 | 1071.7053
746 | 0.11925 | 39.47 | 62.423 | 0.00040133 | 7.5047 | 1079.2 |  | 746 | 39.47 | 0.11925 | 62.423 | 0.00040133 | 7.5047 | 1079.2 | 1071.6953
747 | 0.11929 | 39.48 | 62.423 | 0.00040148 | 7.5148 | 1079.2 |  | 747 | 39.48 | 0.11929 | 62.423 | 0.00040148 | 7.5148 | 1079.2 | 1071.6852
748 | 0.11934 | 39.49 | 62.423 | 0.00040163 | 7.5249 | 1079.2 |  | 748 | 39.49 | 0.11934 | 62.423 | 0.00040163 | 7.5249 | 1079.2 | 1071.6751
749 | 0.11939 | 39.5 | 62.423 | 0.00040178 | 7.5349 | 1079.2 |  | 749 | 39.5 | 0.11939 | 62.423 | 0.00040178 | 7.5349 | 1079.2 | 1071.6651
750 | 0.11943 | 39.51 | 62.423 | 0.00040193 | 7.545 | 1079.2 |  | 750 | 39.51 | 0.11943 | 62.423 | 0.00040193 | 7.545 | 1079.2 | 1071.655
751 | 0.11948 | 39.52 | 62.423 | 0.00040208 | 7.555 | 1079.2 |  | 751 | 39.52 | 0.11948 | 62.423 | 0.00040208 | 7.555 | 1079.2 | 1071.645
752 | 0.11953 | 39.53 | 62.423 | 0.00040223 | 7.5651 | 1079.2 |  | 752 | 39.53 | 0.11953 | 62.423 | 0.00040223 | 7.5651 | 1079.2 | 1071.6349
753 | 0.11957 | 39.54 | 62.423 | 0.00040237 | 7.5751 | 1079.2 |  | 753 | 39.54 | 0.11957 | 62.423 | 0.00040237 | 7.5751 | 1079.2 | 1071.6249
754 | 0.11962 | 39.55 | 62.423 | 0.00040252 | 7.5852 | 1079.2 |  | 754 | 39.55 | 0.11962 | 62.423 | 0.00040252 | 7.5852 | 1079.2 | 1071.6148
755 | 0.11967 | 39.56 | 62.423 | 0.00040267 | 7.5953 | 1079.2 |  | 755 | 39.56 | 0.11967 | 62.423 | 0.00040267 | 7.5953 | 1079.2 | 1071.6047
756 | 0.11971 | 39.57 | 62.423 | 0.00040282 | 7.6053 | 1079.2 |  | 756 | 39.57 | 0.11971 | 62.423 | 0.00040282 | 7.6053 | 1079.2 | 1071.5947
757 | 0.11976 | 39.58 | 62.423 | 0.00040297 | 7.6154 | 1079.2 |  | 757 | 39.58 | 0.11976 | 62.423 | 0.00040297 | 7.6154 | 1079.2 | 1071.5846
758 | 0.11981 | 39.59 | 62.423 | 0.00040312 | 7.6254 | 1079.2 |  | 758 | 39.59 | 0.11981 | 62.423 | 0.00040312 | 7.6254 | 1079.2 | 1071.5746
759 | 0.11985 | 39.6 | 62.423 | 0.00040327 | 7.6355 | 1079.2 |  | 759 | 39.6 | 0.11985 | 62.423 | 0.00040327 | 7.6355 | 1079.2 | 1071.5645
760 | 0.1199 | 39.61 | 62.423 | 0.00040342 | 7.6455 | 1079.2 |  | 760 | 39.61 | 0.1199 | 62.423 | 0.00040342 | 7.6455 | 1079.2 | 1071.5545
761 | 0.11995 | 39.62 | 62.423 | 0.00040357 | 7.6556 | 1079.3 |  | 761 | 39.62 | 0.11995 | 62.423 | 0.00040357 | 7.6556 | 1079.3 | 1071.6444
762 | 0.11999 | 39.63 | 62.423 | 0.00040372 | 7.6656 | 1079.3 |  | 762 | 39.63 | 0.11999 | 62.423 | 0.00040372 | 7.6656 | 1079.3 | 1071.6344
763 | 0.12004 | 39.64 | 62.423 | 0.00040387 | 7.6757 | 1079.3 |  | 763 | 39.64 | 0.12004 | 62.423 | 0.00040387 | 7.6757 | 1079.3 | 1071.6243
764 | 0.12009 | 39.65 | 62.423 | 0.00040402 | 7.6858 | 1079.3 |  | 764 | 39.65 | 0.12009 | 62.423 | 0.00040402 | 7.6858 | 1079.3 | 1071.6142
765 | 0.12013 | 39.66 | 62.423 | 0.00040417 | 7.6958 | 1079.3 |  | 765 | 39.66 | 0.12013 | 62.423 | 0.00040417 | 7.6958 | 1079.3 | 1071.6042
766 | 0.12018 | 39.67 | 62.423 | 0.00040432 | 7.7059 | 1079.3 |  | 766 | 39.67 | 0.12018 | 62.423 | 0.00040432 | 7.7059 | 1079.3 | 1071.5941
767 | 0.12023 | 39.68 | 62.423 | 0.00040447 | 7.7159 | 1079.3 |  | 767 | 39.68 | 0.12023 | 62.423 | 0.00040447 | 7.7159 | 1079.3 | 1071.5841
768 | 0.12027 | 39.69 | 62.423 | 0.00040462 | 7.726 | 1079.3 |  | 768 | 39.69 | 0.12027 | 62.423 | 0.00040462 | 7.726 | 1079.3 | 1071.574
769 | 0.12032 | 39.7 | 62.423 | 0.00040476 | 7.736 | 1079.3 |  | 769 | 39.7 | 0.12032 | 62.423 | 0.00040476 | 7.736 | 1079.3 | 1071.564
770 | 0.12037 | 39.71 | 62.423 | 0.00040491 | 7.7461 | 1079.3 |  | 770 | 39.71 | 0.12037 | 62.423 | 0.00040491 | 7.7461 | 1079.3 | 1071.5539
771 | 0.12041 | 39.72 | 62.423 | 0.00040506 | 7.7561 | 1079.3 |  | 771 | 39.72 | 0.12041 | 62.423 | 0.00040506 | 7.7561 | 1079.3 | 1071.5439
772 | 0.12046 | 39.73 | 62.423 | 0.00040521 | 7.7662 | 1079.3 |  | 772 | 39.73 | 0.12046 | 62.423 | 0.00040521 | 7.7662 | 1079.3 | 1071.5338
773 | 0.12051 | 39.74 | 62.423 | 0.00040536 | 7.7763 | 1079.3 |  | 773 | 39.74 | 0.12051 | 62.423 | 0.00040536 | 7.7763 | 1079.3 | 1071.5237
774 | 0.12056 | 39.75 | 62.423 | 0.00040551 | 7.7863 | 1079.3 |  | 774 | 39.75 | 0.12056 | 62.423 | 0.00040551 | 7.7863 | 1079.3 | 1071.5137
775 | 0.1206 | 39.76 | 62.423 | 0.00040566 | 7.7964 | 1079.3 |  | 775 | 39.76 | 0.1206 | 62.423 | 0.00040566 | 7.7964 | 1079.3 | 1071.5036
776 | 0.12065 | 39.77 | 62.423 | 0.00040581 | 7.8064 | 1079.3 |  | 776 | 39.77 | 0.12065 | 62.423 | 0.00040581 | 7.8064 | 1079.3 | 1071.4936
777 | 0.1207 | 39.78 | 62.423 | 0.00040596 | 7.8165 | 1079.3 |  | 777 | 39.78 | 0.1207 | 62.423 | 0.00040596 | 7.8165 | 1079.3 | 1071.4835
778 | 0.12074 | 39.79 | 62.423 | 0.00040611 | 7.8265 | 1079.3 |  | 778 | 39.79 | 0.12074 | 62.423 | 0.00040611 | 7.8265 | 1079.3 | 1071.4735
779 | 0.12079 | 39.8 | 62.423 | 0.00040626 | 7.8366 | 1079.3 |  | 779 | 39.8 | 0.12079 | 62.423 | 0.00040626 | 7.8366 | 1079.3 | 1071.4634
780 | 0.12084 | 39.81 | 62.423 | 0.00040642 | 7.8466 | 1079.3 |  | 780 | 39.81 | 0.12084 | 62.423 | 0.00040642 | 7.8466 | 1079.3 | 1071.4534
781 | 0.12088 | 39.82 | 62.423 | 0.00040657 | 7.8567 | 1079.3 |  | 781 | 39.82 | 0.12088 | 62.423 | 0.00040657 | 7.8567 | 1079.3 | 1071.4433
782 | 0.12093 | 39.83 | 62.423 | 0.00040672 | 7.8668 | 1079.3 |  | 782 | 39.83 | 0.12093 | 62.423 | 0.00040672 | 7.8668 | 1079.3 | 1071.4332
783 | 0.12098 | 39.84 | 62.423 | 0.00040687 | 7.8768 | 1079.3 |  | 783 | 39.84 | 0.12098 | 62.423 | 0.00040687 | 7.8768 | 1079.3 | 1071.4232
784 | 0.12103 | 39.85 | 62.423 | 0.00040702 | 7.8869 | 1079.4 |  | 784 | 39.85 | 0.12103 | 62.423 | 0.00040702 | 7.8869 | 1079.4 | 1071.5131
785 | 0.12107 | 39.86 | 62.423 | 0.00040717 | 7.8969 | 1079.4 |  | 785 | 39.86 | 0.12107 | 62.423 | 0.00040717 | 7.8969 | 1079.4 | 1071.5031
786 | 0.12112 | 39.87 | 62.423 | 0.00040732 | 7.907 | 1079.4 |  | 786 | 39.87 | 0.12112 | 62.423 | 0.00040732 | 7.907 | 1079.4 | 1071.493
787 | 0.12117 | 39.88 | 62.423 | 0.00040747 | 7.917 | 1079.4 |  | 787 | 39.88 | 0.12117 | 62.423 | 0.00040747 | 7.917 | 1079.4 | 1071.483
788 | 0.12121 | 39.89 | 62.423 | 0.00040762 | 7.9271 | 1079.4 |  | 788 | 39.89 | 0.12121 | 62.423 | 0.00040762 | 7.9271 | 1079.4 | 1071.4729
789 | 0.12126 | 39.9 | 62.423 | 0.00040777 | 7.9371 | 1079.4 |  | 789 | 39.9 | 0.12126 | 62.423 | 0.00040777 | 7.9371 | 1079.4 | 1071.4629
790 | 0.12131 | 39.91 | 62.423 | 0.00040792 | 7.9472 | 1079.4 |  | 790 | 39.91 | 0.12131 | 62.423 | 0.00040792 | 7.9472 | 1079.4 | 1071.4528
791 | 0.12136 | 39.92 | 62.423 | 0.00040807 | 7.9573 | 1079.4 |  | 791 | 39.92 | 0.12136 | 62.423 | 0.00040807 | 7.9573 | 1079.4 | 1071.4427
792 | 0.1214 | 39.93 | 62.423 | 0.00040822 | 7.9673 | 1079.4 |  | 792 | 39.93 | 0.1214 | 62.423 | 0.00040822 | 7.9673 | 1079.4 | 1071.4327
793 | 0.12145 | 39.94 | 62.423 | 0.00040837 | 7.9774 | 1079.4 |  | 793 | 39.94 | 0.12145 | 62.423 | 0.00040837 | 7.9774 | 1079.4 | 1071.4226
794 | 0.1215 | 39.95 | 62.423 | 0.00040852 | 7.9874 | 1079.4 |  | 794 | 39.95 | 0.1215 | 62.423 | 0.00040852 | 7.9874 | 1079.4 | 1071.4126
795 | 0.12155 | 39.96 | 62.423 | 0.00040867 | 7.9975 | 1079.4 |  | 795 | 39.96 | 0.12155 | 62.423 | 0.00040867 | 7.9975 | 1079.4 | 1071.4025
796 | 0.12159 | 39.97 | 62.423 | 0.00040883 | 8.0075 | 1079.4 |  | 796 | 39.97 | 0.12159 | 62.423 | 0.00040883 | 8.0075 | 1079.4 | 1071.3925
797 | 0.12164 | 39.98 | 62.423 | 0.00040898 | 8.0176 | 1079.4 |  | 797 | 39.98 | 0.12164 | 62.423 | 0.00040898 | 8.0176 | 1079.4 | 1071.3824
798 | 0.12169 | 39.99 | 62.423 | 0.00040913 | 8.0276 | 1079.4 |  | 798 | 39.99 | 0.12169 | 62.423 | 0.00040913 | 8.0276 | 1079.4 | 1071.3724
799 | 0.12173 | 40 | 62.423 | 0.00040928 | 8.0377 | 1079.4 |  | 799 | 40 | 0.12173 | 62.423 | 0.00040928 | 8.0377 | 1079.4 | 1071.3623
800 | 0.12178 | 40.01 | 62.423 | 0.00040943 | 8.0477 | 1079.4 |  | 800 | 40.01 | 0.12178 | 62.423 | 0.00040943 | 8.0477 | 1079.4 | 1071.3523
801 | 0.12183 | 40.02 | 62.423 | 0.00040958 | 8.0578 | 1079.4 |  | 801 | 40.02 | 0.12183 | 62.423 | 0.00040958 | 8.0578 | 1079.4 | 1071.3422
802 | 0.12188 | 40.03 | 62.423 | 0.00040973 | 8.0679 | 1079.4 |  | 802 | 40.03 | 0.12188 | 62.423 | 0.00040973 | 8.0679 | 1079.4 | 1071.3321
803 | 0.12192 | 40.04 | 62.423 | 0.00040988 | 8.0779 | 1079.4 |  | 803 | 40.04 | 0.12192 | 62.423 | 0.00040988 | 8.0779 | 1079.4 | 1071.3221
804 | 0.12197 | 40.05 | 62.423 | 0.00041004 | 8.088 | 1079.4 |  | 804 | 40.05 | 0.12197 | 62.423 | 0.00041004 | 8.088 | 1079.4 | 1071.312
805 | 0.12202 | 40.06 | 62.423 | 0.00041019 | 8.098 | 1079.4 |  | 805 | 40.06 | 0.12202 | 62.423 | 0.00041019 | 8.098 | 1079.4 | 1071.302
806 | 0.12207 | 40.07 | 62.423 | 0.00041034 | 8.1081 | 1079.4 |  | 806 | 40.07 | 0.12207 | 62.423 | 0.00041034 | 8.1081 | 1079.4 | 1071.2919
807 | 0.12211 | 40.08 | 62.423 | 0.00041049 | 8.1181 | 1079.5 |  | 807 | 40.08 | 0.12211 | 62.423 | 0.00041049 | 8.1181 | 1079.5 | 1071.3819
808 | 0.12216 | 40.09 | 62.423 | 0.00041064 | 8.1282 | 1079.5 |  | 808 | 40.09 | 0.12216 | 62.423 | 0.00041064 | 8.1282 | 1079.5 | 1071.3718
809 | 0.12221 | 40.1 | 62.423 | 0.00041079 | 8.1382 | 1079.5 |  | 809 | 40.1 | 0.12221 | 62.423 | 0.00041079 | 8.1382 | 1079.5 | 1071.3618
810 | 0.12226 | 40.11 | 62.423 | 0.00041095 | 8.1483 | 1079.5 |  | 810 | 40.11 | 0.12226 | 62.423 | 0.00041095 | 8.1483 | 1079.5 | 1071.3517
811 | 0.1223 | 40.12 | 62.423 | 0.0004111 | 8.1583 | 1079.5 |  | 811 | 40.12 | 0.1223 | 62.423 | 0.0004111 | 8.1583 | 1079.5 | 1071.3417
812 | 0.12235 | 40.13 | 62.423 | 0.00041125 | 8.1684 | 1079.5 |  | 812 | 40.13 | 0.12235 | 62.423 | 0.00041125 | 8.1684 | 1079.5 | 1071.3316
813 | 0.1224 | 40.14 | 62.423 | 0.0004114 | 8.1785 | 1079.5 |  | 813 | 40.14 | 0.1224 | 62.423 | 0.0004114 | 8.1785 | 1079.5 | 1071.3215
814 | 0.12245 | 40.15 | 62.423 | 0.00041155 | 8.1885 | 1079.5 |  | 814 | 40.15 | 0.12245 | 62.423 | 0.00041155 | 8.1885 | 1079.5 | 1071.3115
815 | 0.1225 | 40.16 | 62.423 | 0.00041171 | 8.1986 | 1079.5 |  | 815 | 40.16 | 0.1225 | 62.423 | 0.00041171 | 8.1986 | 1079.5 | 1071.3014
816 | 0.12254 | 40.17 | 62.423 | 0.00041186 | 8.2086 | 1079.5 |  | 816 | 40.17 | 0.12254 | 62.423 | 0.00041186 | 8.2086 | 1079.5 | 1071.2914
817 | 0.12259 | 40.18 | 62.423 | 0.00041201 | 8.2187 | 1079.5 |  | 817 | 40.18 | 0.12259 | 62.423 | 0.00041201 | 8.2187 | 1079.5 | 1071.2813
818 | 0.12264 | 40.19 | 62.423 | 0.00041216 | 8.2287 | 1079.5 |  | 818 | 40.19 | 0.12264 | 62.423 | 0.00041216 | 8.2287 | 1079.5 | 1071.2713
819 | 0.12269 | 40.2 | 62.423 | 0.00041231 | 8.2388 | 1079.5 |  | 819 | 40.2 | 0.12269 | 62.423 | 0.00041231 | 8.2388 | 1079.5 | 1071.2612
820 | 0.12273 | 40.21 | 62.423 | 0.00041247 | 8.2488 | 1079.5 |  | 820 | 40.21 | 0.12273 | 62.423 | 0.00041247 | 8.2488 | 1079.5 | 1071.2512
821 | 0.12278 | 40.22 | 62.423 | 0.00041262 | 8.2589 | 1079.5 |  | 821 | 40.22 | 0.12278 | 62.423 | 0.00041262 | 8.2589 | 1079.5 | 1071.2411
822 | 0.12283 | 40.23 | 62.423 | 0.00041277 | 8.2689 | 1079.5 |  | 822 | 40.23 | 0.12283 | 62.423 | 0.00041277 | 8.2689 | 1079.5 | 1071.2311
823 | 0.12288 | 40.24 | 62.423 | 0.00041292 | 8.279 | 1079.5 |  | 823 | 40.24 | 0.12288 | 62.423 | 0.00041292 | 8.279 | 1079.5 | 1071.221
824 | 0.12292 | 40.25 | 62.423 | 0.00041307 | 8.2891 | 1079.5 |  | 824 | 40.25 | 0.12292 | 62.423 | 0.00041307 | 8.2891 | 1079.5 | 1071.2109
825 | 0.12297 | 40.26 | 62.423 | 0.00041323 | 8.2991 | 1079.5 |  | 825 | 40.26 | 0.12297 | 62.423 | 0.00041323 | 8.2991 | 1079.5 | 1071.2009
826 | 0.12302 | 40.27 | 62.423 | 0.00041338 | 8.3092 | 1079.5 |  | 826 | 40.27 | 0.12302 | 62.423 | 0.00041338 | 8.3092 | 1079.5 | 1071.1908
827 | 0.12307 | 40.28 | 62.423 | 0.00041353 | 8.3192 | 1079.5 |  | 827 | 40.28 | 0.12307 | 62.423 | 0.00041353 | 8.3192 | 1079.5 | 1071.1808
828 | 0.12312 | 40.29 | 62.423 | 0.00041369 | 8.3293 | 1079.5 |  | 828 | 40.29 | 0.12312 | 62.423 | 0.00041369 | 8.3293 | 1079.5 | 1071.1707
829 | 0.12316 | 40.3 | 62.423 | 0.00041384 | 8.3393 | 1079.5 |  | 829 | 40.3 | 0.12316 | 62.423 | 0.00041384 | 8.3393 | 1079.5 | 1071.1607
830 | 0.12321 | 40.31 | 62.423 | 0.00041399 | 8.3494 | 1079.6 |  | 830 | 40.31 | 0.12321 | 62.423 | 0.00041399 | 8.3494 | 1079.6 | 1071.2506
831 | 0.12326 | 40.32 | 62.423 | 0.00041414 | 8.3594 | 1079.6 |  | 831 | 40.32 | 0.12326 | 62.423 | 0.00041414 | 8.3594 | 1079.6 | 1071.2406
832 | 0.12331 | 40.33 | 62.423 | 0.0004143 | 8.3695 | 1079.6 |  | 832 | 40.33 | 0.12331 | 62.423 | 0.0004143 | 8.3695 | 1079.6 | 1071.2305
833 | 0.12336 | 40.34 | 62.423 | 0.00041445 | 8.3795 | 1079.6 |  | 833 | 40.34 | 0.12336 | 62.423 | 0.00041445 | 8.3795 | 1079.6 | 1071.2205
834 | 0.1234 | 40.35 | 62.423 | 0.0004146 | 8.3896 | 1079.6 |  | 834 | 40.35 | 0.1234 | 62.423 | 0.0004146 | 8.3896 | 1079.6 | 1071.2104
835 | 0.12345 | 40.36 | 62.423 | 0.00041475 | 8.3996 | 1079.6 |  | 835 | 40.36 | 0.12345 | 62.423 | 0.00041475 | 8.3996 | 1079.6 | 1071.2004
836 | 0.1235 | 40.37 | 62.423 | 0.00041491 | 8.4097 | 1079.6 |  | 836 | 40.37 | 0.1235 | 62.423 | 0.00041491 | 8.4097 | 1079.6 | 1071.1903
837 | 0.12355 | 40.38 | 62.423 | 0.00041506 | 8.4197 | 1079.6 |  | 837 | 40.38 | 0.12355 | 62.423 | 0.00041506 | 8.4197 | 1079.6 | 1071.1803
838 | 0.1236 | 40.39 | 62.423 | 0.00041521 | 8.4298 | 1079.6 |  | 838 | 40.39 | 0.1236 | 62.423 | 0.00041521 | 8.4298 | 1079.6 | 1071.1702
839 | 0.12364 | 40.4 | 62.423 | 0.00041537 | 8.4399 | 1079.6 |  | 839 | 40.4 | 0.12364 | 62.423 | 0.00041537 | 8.4399 | 1079.6 | 1071.1601
840 | 0.12369 | 40.41 | 62.423 | 0.00041552 | 8.4499 | 1079.6 |  | 840 | 40.41 | 0.12369 | 62.423 | 0.00041552 | 8.4499 | 1079.6 | 1071.1501
841 | 0.12374 | 40.42 | 62.423 | 0.00041567 | 8.46 | 1079.6 |  | 841 | 40.42 | 0.12374 | 62.423 | 0.00041567 | 8.46 | 1079.6 | 1071.14
842 | 0.12379 | 40.43 | 62.423 | 0.00041583 | 8.47 | 1079.6 |  | 842 | 40.43 | 0.12379 | 62.423 | 0.00041583 | 8.47 | 1079.6 | 1071.13
843 | 0.12384 | 40.44 | 62.423 | 0.00041598 | 8.4801 | 1079.6 |  | 843 | 40.44 | 0.12384 | 62.423 | 0.00041598 | 8.4801 | 1079.6 | 1071.1199
844 | 0.12388 | 40.45 | 62.423 | 0.00041613 | 8.4901 | 1079.6 |  | 844 | 40.45 | 0.12388 | 62.423 | 0.00041613 | 8.4901 | 1079.6 | 1071.1099
845 | 0.12393 | 40.46 | 62.423 | 0.00041629 | 8.5002 | 1079.6 |  | 845 | 40.46 | 0.12393 | 62.423 | 0.00041629 | 8.5002 | 1079.6 | 1071.0998
846 | 0.12398 | 40.47 | 62.423 | 0.00041644 | 8.5102 | 1079.6 |  | 846 | 40.47 | 0.12398 | 62.423 | 0.00041644 | 8.5102 | 1079.6 | 1071.0898
847 | 0.12403 | 40.48 | 62.423 | 0.00041659 | 8.5203 | 1079.6 |  | 847 | 40.48 | 0.12403 | 62.423 | 0.00041659 | 8.5203 | 1079.6 | 1071.0797
848 | 0.12408 | 40.49 | 62.423 | 0.00041675 | 8.5303 | 1079.6 |  | 848 | 40.49 | 0.12408 | 62.423 | 0.00041675 | 8.5303 | 1079.6 | 1071.0697
849 | 0.12412 | 40.5 | 62.423 | 0.0004169 | 8.5404 | 1079.6 |  | 849 | 40.5 | 0.12412 | 62.423 | 0.0004169 | 8.5404 | 1079.6 | 1071.0596
850 | 0.12417 | 40.51 | 62.423 | 0.00041706 | 8.5504 | 1079.6 |  | 850 | 40.51 | 0.12417 | 62.423 | 0.00041706 | 8.5504 | 1079.6 | 1071.0496
851 | 0.12422 | 40.52 | 62.423 | 0.00041721 | 8.5605 | 1079.6 |  | 851 | 40.52 | 0.12422 | 62.423 | 0.00041721 | 8.5605 | 1079.6 | 1071.0395
852 | 0.12427 | 40.53 | 62.423 | 0.00041736 | 8.5705 | 1079.6 |  | 852 | 40.53 | 0.12427 | 62.423 | 0.00041736 | 8.5705 | 1079.6 | 1071.0295
853 | 0.12432 | 40.54 | 62.423 | 0.00041752 | 8.5806 | 1079.7 |  | 853 | 40.54 | 0.12432 | 62.423 | 0.00041752 | 8.5806 | 1079.7 | 1071.1194
854 | 0.12437 | 40.55 | 62.423 | 0.00041767 | 8.5907 | 1079.7 |  | 854 | 40.55 | 0.12437 | 62.423 | 0.00041767 | 8.5907 | 1079.7 | 1071.1093
855 | 0.12441 | 40.56 | 62.423 | 0.00041782 | 8.6007 | 1079.7 |  | 855 | 40.56 | 0.12441 | 62.423 | 0.00041782 | 8.6007 | 1079.7 | 1071.0993
856 | 0.12446 | 40.57 | 62.423 | 0.00041798 | 8.6108 | 1079.7 |  | 856 | 40.57 | 0.12446 | 62.423 | 0.00041798 | 8.6108 | 1079.7 | 1071.0892
857 | 0.12451 | 40.58 | 62.423 | 0.00041813 | 8.6208 | 1079.7 |  | 857 | 40.58 | 0.12451 | 62.423 | 0.00041813 | 8.6208 | 1079.7 | 1071.0792
858 | 0.12456 | 40.59 | 62.423 | 0.00041829 | 8.6309 | 1079.7 |  | 858 | 40.59 | 0.12456 | 62.423 | 0.00041829 | 8.6309 | 1079.7 | 1071.0691
859 | 0.12461 | 40.6 | 62.423 | 0.00041844 | 8.6409 | 1079.7 |  | 859 | 40.6 | 0.12461 | 62.423 | 0.00041844 | 8.6409 | 1079.7 | 1071.0591
860 | 0.12466 | 40.61 | 62.423 | 0.00041859 | 8.651 | 1079.7 |  | 860 | 40.61 | 0.12466 | 62.423 | 0.00041859 | 8.651 | 1079.7 | 1071.049
861 | 0.1247 | 40.62 | 62.423 | 0.00041875 | 8.661 | 1079.7 |  | 861 | 40.62 | 0.1247 | 62.423 | 0.00041875 | 8.661 | 1079.7 | 1071.039
862 | 0.12475 | 40.63 | 62.423 | 0.0004189 | 8.6711 | 1079.7 |  | 862 | 40.63 | 0.12475 | 62.423 | 0.0004189 | 8.6711 | 1079.7 | 1071.0289
863 | 0.1248 | 40.64 | 62.423 | 0.00041906 | 8.6811 | 1079.7 |  | 863 | 40.64 | 0.1248 | 62.423 | 0.00041906 | 8.6811 | 1079.7 | 1071.0189
864 | 0.12485 | 40.65 | 62.423 | 0.00041921 | 8.6912 | 1079.7 |  | 864 | 40.65 | 0.12485 | 62.423 | 0.00041921 | 8.6912 | 1079.7 | 1071.0088
865 | 0.1249 | 40.66 | 62.423 | 0.00041937 | 8.7012 | 1079.7 |  | 865 | 40.66 | 0.1249 | 62.423 | 0.00041937 | 8.7012 | 1079.7 | 1070.9988
866 | 0.12495 | 40.67 | 62.423 | 0.00041952 | 8.7113 | 1079.7 |  | 866 | 40.67 | 0.12495 | 62.423 | 0.00041952 | 8.7113 | 1079.7 | 1070.9887
867 | 0.125 | 40.68 | 62.423 | 0.00041968 | 8.7213 | 1079.7 |  | 867 | 40.68 | 0.125 | 62.423 | 0.00041968 | 8.7213 | 1079.7 | 1070.9787
868 | 0.12504 | 40.69 | 62.423 | 0.00041983 | 8.7314 | 1079.7 |  | 868 | 40.69 | 0.12504 | 62.423 | 0.00041983 | 8.7314 | 1079.7 | 1070.9686
869 | 0.12509 | 40.7 | 62.423 | 0.00041998 | 8.7414 | 1079.7 |  | 869 | 40.7 | 0.12509 | 62.423 | 0.00041998 | 8.7414 | 1079.7 | 1070.9586
870 | 0.12514 | 40.71 | 62.423 | 0.00042014 | 8.7515 | 1079.7 |  | 870 | 40.71 | 0.12514 | 62.423 | 0.00042014 | 8.7515 | 1079.7 | 1070.9485
871 | 0.12519 | 40.72 | 62.423 | 0.00042029 | 8.7615 | 1079.7 |  | 871 | 40.72 | 0.12519 | 62.423 | 0.00042029 | 8.7615 | 1079.7 | 1070.9385
872 | 0.12524 | 40.73 | 62.423 | 0.00042045 | 8.7716 | 1079.7 |  | 872 | 40.73 | 0.12524 | 62.423 | 0.00042045 | 8.7716 | 1079.7 | 1070.9284
873 | 0.12529 | 40.74 | 62.423 | 0.0004206 | 8.7817 | 1079.7 |  | 873 | 40.74 | 0.12529 | 62.423 | 0.0004206 | 8.7817 | 1079.7 | 1070.9183
874 | 0.12534 | 40.75 | 62.423 | 0.00042076 | 8.7917 | 1079.7 |  | 874 | 40.75 | 0.12534 | 62.423 | 0.00042076 | 8.7917 | 1079.7 | 1070.9083
875 | 0.12538 | 40.76 | 62.423 | 0.00042091 | 8.8018 | 1079.7 |  | 875 | 40.76 | 0.12538 | 62.423 | 0.00042091 | 8.8018 | 1079.7 | 1070.8982
876 | 0.12543 | 40.77 | 62.423 | 0.00042107 | 8.8118 | 1079.8 |  | 876 | 40.77 | 0.12543 | 62.423 | 0.00042107 | 8.8118 | 1079.8 | 1070.9882
877 | 0.12548 | 40.78 | 62.423 | 0.00042122 | 8.8219 | 1079.8 |  | 877 | 40.78 | 0.12548 | 62.423 | 0.00042122 | 8.8219 | 1079.8 | 1070.9781
878 | 0.12553 | 40.79 | 62.423 | 0.00042138 | 8.8319 | 1079.8 |  | 878 | 40.79 | 0.12553 | 62.423 | 0.00042138 | 8.8319 | 1079.8 | 1070.9681
879 | 0.12558 | 40.8 | 62.423 | 0.00042153 | 8.842 | 1079.8 |  | 879 | 40.8 | 0.12558 | 62.423 | 0.00042153 | 8.842 | 1079.8 | 1070.958
880 | 0.12563 | 40.81 | 62.423 | 0.00042169 | 8.852 | 1079.8 |  | 880 | 40.81 | 0.12563 | 62.423 | 0.00042169 | 8.852 | 1079.8 | 1070.948
881 | 0.12568 | 40.82 | 62.423 | 0.00042184 | 8.8621 | 1079.8 |  | 881 | 40.82 | 0.12568 | 62.423 | 0.00042184 | 8.8621 | 1079.8 | 1070.9379
882 | 0.12572 | 40.83 | 62.423 | 0.000422 | 8.8721 | 1079.8 |  | 882 | 40.83 | 0.12572 | 62.423 | 0.000422 | 8.8721 | 1079.8 | 1070.9279
883 | 0.12577 | 40.84 | 62.423 | 0.00042216 | 8.8822 | 1079.8 |  | 883 | 40.84 | 0.12577 | 62.423 | 0.00042216 | 8.8822 | 1079.8 | 1070.9178
884 | 0.12582 | 40.85 | 62.423 | 0.00042231 | 8.8922 | 1079.8 |  | 884 | 40.85 | 0.12582 | 62.423 | 0.00042231 | 8.8922 | 1079.8 | 1070.9078
885 | 0.12587 | 40.86 | 62.423 | 0.00042247 | 8.9023 | 1079.8 |  | 885 | 40.86 | 0.12587 | 62.423 | 0.00042247 | 8.9023 | 1079.8 | 1070.8977
886 | 0.12592 | 40.87 | 62.423 | 0.00042262 | 8.9123 | 1079.8 |  | 886 | 40.87 | 0.12592 | 62.423 | 0.00042262 | 8.9123 | 1079.8 | 1070.8877
887 | 0.12597 | 40.88 | 62.423 | 0.00042278 | 8.9224 | 1079.8 |  | 887 | 40.88 | 0.12597 | 62.423 | 0.00042278 | 8.9224 | 1079.8 | 1070.8776
888 | 0.12602 | 40.89 | 62.423 | 0.00042293 | 8.9324 | 1079.8 |  | 888 | 40.89 | 0.12602 | 62.423 | 0.00042293 | 8.9324 | 1079.8 | 1070.8676
889 | 0.12607 | 40.9 | 62.423 | 0.00042309 | 8.9425 | 1079.8 |  | 889 | 40.9 | 0.12607 | 62.423 | 0.00042309 | 8.9425 | 1079.8 | 1070.8575
890 | 0.12612 | 40.91 | 62.423 | 0.00042324 | 8.9525 | 1079.8 |  | 890 | 40.91 | 0.12612 | 62.423 | 0.00042324 | 8.9525 | 1079.8 | 1070.8475
891 | 0.12616 | 40.92 | 62.423 | 0.0004234 | 8.9626 | 1079.8 |  | 891 | 40.92 | 0.12616 | 62.423 | 0.0004234 | 8.9626 | 1079.8 | 1070.8374
892 | 0.12621 | 40.93 | 62.423 | 0.00042356 | 8.9726 | 1079.8 |  | 892 | 40.93 | 0.12621 | 62.423 | 0.00042356 | 8.9726 | 1079.8 | 1070.8274
893 | 0.12626 | 40.94 | 62.423 | 0.00042371 | 8.9827 | 1079.8 |  | 893 | 40.94 | 0.12626 | 62.423 | 0.00042371 | 8.9827 | 1079.8 | 1070.8173
894 | 0.12631 | 40.95 | 62.423 | 0.00042387 | 8.9927 | 1079.8 |  | 894 | 40.95 | 0.12631 | 62.423 | 0.00042387 | 8.9927 | 1079.8 | 1070.8073
895 | 0.12636 | 40.96 | 62.423 | 0.00042402 | 9.0028 | 1079.8 |  | 895 | 40.96 | 0.12636 | 62.423 | 0.00042402 | 9.0028 | 1079.8 | 1070.7972
896 | 0.12641 | 40.97 | 62.423 | 0.00042418 | 9.0128 | 1079.8 |  | 896 | 40.97 | 0.12641 | 62.423 | 0.00042418 | 9.0128 | 1079.8 | 1070.7872
897 | 0.12646 | 40.98 | 62.423 | 0.00042434 | 9.0229 | 1079.8 |  | 897 | 40.98 | 0.12646 | 62.423 | 0.00042434 | 9.0229 | 1079.8 | 1070.7771
898 | 0.12651 | 40.99 | 62.423 | 0.00042449 | 9.0329 | 1079.9 |  | 898 | 40.99 | 0.12651 | 62.423 | 0.00042449 | 9.0329 | 1079.9 | 1070.8671
899 | 0.12656 | 41 | 62.423 | 0.00042465 | 9.043 | 1079.9 |  | 899 | 41 | 0.12656 | 62.423 | 0.00042465 | 9.043 | 1079.9 | 1070.857
900 | 0.12661 | 41.01 | 62.423 | 0.0004248 | 9.0531 | 1079.9 |  | 900 | 41.01 | 0.12661 | 62.423 | 0.0004248 | 9.0531 | 1079.9 | 1070.8469
901 | 0.12665 | 41.02 | 62.423 | 0.00042496 | 9.0631 | 1079.9 |  | 901 | 41.02 | 0.12665 | 62.423 | 0.00042496 | 9.0631 | 1079.9 | 1070.8369
902 | 0.1267 | 41.03 | 62.423 | 0.00042512 | 9.0732 | 1079.9 |  | 902 | 41.03 | 0.1267 | 62.423 | 0.00042512 | 9.0732 | 1079.9 | 1070.8268
903 | 0.12675 | 41.04 | 62.423 | 0.00042527 | 9.0832 | 1079.9 |  | 903 | 41.04 | 0.12675 | 62.423 | 0.00042527 | 9.0832 | 1079.9 | 1070.8168
904 | 0.1268 | 41.05 | 62.423 | 0.00042543 | 9.0933 | 1079.9 |  | 904 | 41.05 | 0.1268 | 62.423 | 0.00042543 | 9.0933 | 1079.9 | 1070.8067
905 | 0.12685 | 41.06 | 62.423 | 0.00042559 | 9.1033 | 1079.9 |  | 905 | 41.06 | 0.12685 | 62.423 | 0.00042559 | 9.1033 | 1079.9 | 1070.7967
906 | 0.1269 | 41.07 | 62.423 | 0.00042574 | 9.1134 | 1079.9 |  | 906 | 41.07 | 0.1269 | 62.423 | 0.00042574 | 9.1134 | 1079.9 | 1070.7866
907 | 0.12695 | 41.08 | 62.423 | 0.0004259 | 9.1234 | 1079.9 |  | 907 | 41.08 | 0.12695 | 62.423 | 0.0004259 | 9.1234 | 1079.9 | 1070.7766
908 | 0.127 | 41.09 | 62.423 | 0.00042605 | 9.1335 | 1079.9 |  | 908 | 41.09 | 0.127 | 62.423 | 0.00042605 | 9.1335 | 1079.9 | 1070.7665
909 | 0.12705 | 41.1 | 62.423 | 0.00042621 | 9.1435 | 1079.9 |  | 909 | 41.1 | 0.12705 | 62.423 | 0.00042621 | 9.1435 | 1079.9 | 1070.7565
910 | 0.1271 | 41.11 | 62.423 | 0.00042637 | 9.1536 | 1079.9 |  | 910 | 41.11 | 0.1271 | 62.423 | 0.00042637 | 9.1536 | 1079.9 | 1070.7464
911 | 0.12715 | 41.12 | 62.423 | 0.00042652 | 9.1636 | 1079.9 |  | 911 | 41.12 | 0.12715 | 62.423 | 0.00042652 | 9.1636 | 1079.9 | 1070.7364
912 | 0.1272 | 41.13 | 62.423 | 0.00042668 | 9.1737 | 1079.9 |  | 912 | 41.13 | 0.1272 | 62.423 | 0.00042668 | 9.1737 | 1079.9 | 1070.7263
913 | 0.12724 | 41.14 | 62.423 | 0.00042684 | 9.1837 | 1079.9 |  | 913 | 41.14 | 0.12724 | 62.423 | 0.00042684 | 9.1837 | 1079.9 | 1070.7163
914 | 0.12729 | 41.15 | 62.423 | 0.000427 | 9.1938 | 1079.9 |  | 914 | 41.15 | 0.12729 | 62.423 | 0.000427 | 9.1938 | 1079.9 | 1070.7062
915 | 0.12734 | 41.16 | 62.423 | 0.00042715 | 9.2038 | 1079.9 |  | 915 | 41.16 | 0.12734 | 62.423 | 0.00042715 | 9.2038 | 1079.9 | 1070.6962
916 | 0.12739 | 41.17 | 62.423 | 0.00042731 | 9.2139 | 1079.9 |  | 916 | 41.17 | 0.12739 | 62.423 | 0.00042731 | 9.2139 | 1079.9 | 1070.6861
917 | 0.12744 | 41.18 | 62.423 | 0.00042747 | 9.2239 | 1079.9 |  | 917 | 41.18 | 0.12744 | 62.423 | 0.00042747 | 9.2239 | 1079.9 | 1070.6761
918 | 0.12749 | 41.19 | 62.423 | 0.00042762 | 9.234 | 1079.9 |  | 918 | 41.19 | 0.12749 | 62.423 | 0.00042762 | 9.234 | 1079.9 | 1070.666
919 | 0.12754 | 41.2 | 62.423 | 0.00042778 | 9.244 | 1079.9 |  | 919 | 41.2 | 0.12754 | 62.423 | 0.00042778 | 9.244 | 1079.9 | 1070.656
920 | 0.12759 | 41.21 | 62.423 | 0.00042794 | 9.2541 | 1079.9 |  | 920 | 41.21 | 0.12759 | 62.423 | 0.00042794 | 9.2541 | 1079.9 | 1070.6459
921 | 0.12764 | 41.22 | 62.423 | 0.0004281 | 9.2641 | 1080 |  | 921 | 41.22 | 0.12764 | 62.423 | 0.0004281 | 9.2641 | 1080 | 1070.7359
922 | 0.12769 | 41.23 | 62.423 | 0.00042825 | 9.2742 | 1080 |  | 922 | 41.23 | 0.12769 | 62.423 | 0.00042825 | 9.2742 | 1080 | 1070.7258
923 | 0.12774 | 41.24 | 62.423 | 0.00042841 | 9.2842 | 1080 |  | 923 | 41.24 | 0.12774 | 62.423 | 0.00042841 | 9.2842 | 1080 | 1070.7158
924 | 0.12779 | 41.25 | 62.423 | 0.00042857 | 9.2943 | 1080 |  | 924 | 41.25 | 0.12779 | 62.423 | 0.00042857 | 9.2943 | 1080 | 1070.7057
925 | 0.12784 | 41.26 | 62.423 | 0.00042872 | 9.3043 | 1080 |  | 925 | 41.26 | 0.12784 | 62.423 | 0.00042872 | 9.3043 | 1080 | 1070.6957
926 | 0.12789 | 41.27 | 62.423 | 0.00042888 | 9.3144 | 1080 |  | 926 | 41.27 | 0.12789 | 62.423 | 0.00042888 | 9.3144 | 1080 | 1070.6856
927 | 0.12794 | 41.28 | 62.423 | 0.00042904 | 9.3244 | 1080 |  | 927 | 41.28 | 0.12794 | 62.423 | 0.00042904 | 9.3244 | 1080 | 1070.6756
928 | 0.12799 | 41.29 | 62.423 | 0.0004292 | 9.3345 | 1080 |  | 928 | 41.29 | 0.12799 | 62.423 | 0.0004292 | 9.3345 | 1080 | 1070.6655
929 | 0.12804 | 41.3 | 62.423 | 0.00042935 | 9.3445 | 1080 |  | 929 | 41.3 | 0.12804 | 62.423 | 0.00042935 | 9.3445 | 1080 | 1070.6555
930 | 0.12808 | 41.31 | 62.423 | 0.00042951 | 9.3546 | 1080 |  | 930 | 41.31 | 0.12808 | 62.423 | 0.00042951 | 9.3546 | 1080 | 1070.6454
931 | 0.12813 | 41.32 | 62.423 | 0.00042967 | 9.3646 | 1080 |  | 931 | 41.32 | 0.12813 | 62.423 | 0.00042967 | 9.3646 | 1080 | 1070.6354
932 | 0.12818 | 41.33 | 62.423 | 0.00042983 | 9.3747 | 1080 |  | 932 | 41.33 | 0.12818 | 62.423 | 0.00042983 | 9.3747 | 1080 | 1070.6253
933 | 0.12823 | 41.34 | 62.423 | 0.00042999 | 9.3847 | 1080 |  | 933 | 41.34 | 0.12823 | 62.423 | 0.00042999 | 9.3847 | 1080 | 1070.6153
934 | 0.12828 | 41.35 | 62.423 | 0.00043014 | 9.3948 | 1080 |  | 934 | 41.35 | 0.12828 | 62.423 | 0.00043014 | 9.3948 | 1080 | 1070.6052
935 | 0.12833 | 41.36 | 62.423 | 0.0004303 | 9.4048 | 1080 |  | 935 | 41.36 | 0.12833 | 62.423 | 0.0004303 | 9.4048 | 1080 | 1070.5952
936 | 0.12838 | 41.37 | 62.423 | 0.00043046 | 9.4149 | 1080 |  | 936 | 41.37 | 0.12838 | 62.423 | 0.00043046 | 9.4149 | 1080 | 1070.5851
937 | 0.12843 | 41.38 | 62.423 | 0.00043062 | 9.4249 | 1080 |  | 937 | 41.38 | 0.12843 | 62.423 | 0.00043062 | 9.4249 | 1080 | 1070.5751
938 | 0.12848 | 41.39 | 62.423 | 0.00043078 | 9.435 | 1080 |  | 938 | 41.39 | 0.12848 | 62.423 | 0.00043078 | 9.435 | 1080 | 1070.565
939 | 0.12853 | 41.4 | 62.423 | 0.00043093 | 9.445 | 1080 |  | 939 | 41.4 | 0.12853 | 62.423 | 0.00043093 | 9.445 | 1080 | 1070.555
940 | 0.12858 | 41.41 | 62.423 | 0.00043109 | 9.4551 | 1080 |  | 940 | 41.41 | 0.12858 | 62.423 | 0.00043109 | 9.4551 | 1080 | 1070.5449
941 | 0.12863 | 41.42 | 62.423 | 0.00043125 | 9.4651 | 1080 |  | 941 | 41.42 | 0.12863 | 62.423 | 0.00043125 | 9.4651 | 1080 | 1070.5349
942 | 0.12868 | 41.43 | 62.423 | 0.00043141 | 9.4752 | 1080 |  | 942 | 41.43 | 0.12868 | 62.423 | 0.00043141 | 9.4752 | 1080 | 1070.5248
943 | 0.12873 | 41.44 | 62.423 | 0.00043157 | 9.4852 | 1080 |  | 943 | 41.44 | 0.12873 | 62.423 | 0.00043157 | 9.4852 | 1080 | 1070.5148
944 | 0.12878 | 41.45 | 62.423 | 0.00043173 | 9.4953 | 1080.1 |  | 944 | 41.45 | 0.12878 | 62.423 | 0.00043173 | 9.4953 | 1080.1 | 1070.6047
945 | 0.12883 | 41.46 | 62.423 | 0.00043188 | 9.5053 | 1080.1 |  | 945 | 41.46 | 0.12883 | 62.423 | 0.00043188 | 9.5053 | 1080.1 | 1070.5947
946 | 0.12888 | 41.47 | 62.423 | 0.00043204 | 9.5154 | 1080.1 |  | 946 | 41.47 | 0.12888 | 62.423 | 0.00043204 | 9.5154 | 1080.1 | 1070.5846
947 | 0.12893 | 41.48 | 62.422 | 0.0004322 | 9.5254 | 1080.1 |  | 947 | 41.48 | 0.12893 | 62.422 | 0.0004322 | 9.5254 | 1080.1 | 1070.5746
948 | 0.12898 | 41.49 | 62.422 | 0.00043236 | 9.5355 | 1080.1 |  | 948 | 41.49 | 0.12898 | 62.422 | 0.00043236 | 9.5355 | 1080.1 | 1070.5645
949 | 0.12903 | 41.5 | 62.422 | 0.00043252 | 9.5455 | 1080.1 |  | 949 | 41.5 | 0.12903 | 62.422 | 0.00043252 | 9.5455 | 1080.1 | 1070.5545
950 | 0.12908 | 41.51 | 62.422 | 0.00043268 | 9.5556 | 1080.1 |  | 950 | 41.51 | 0.12908 | 62.422 | 0.00043268 | 9.5556 | 1080.1 | 1070.5444
951 | 0.12913 | 41.52 | 62.422 | 0.00043284 | 9.5656 | 1080.1 |  | 951 | 41.52 | 0.12913 | 62.422 | 0.00043284 | 9.5656 | 1080.1 | 1070.5344
952 | 0.12918 | 41.53 | 62.422 | 0.00043299 | 9.5757 | 1080.1 |  | 952 | 41.53 | 0.12918 | 62.422 | 0.00043299 | 9.5757 | 1080.1 | 1070.5243
953 | 0.12923 | 41.54 | 62.422 | 0.00043315 | 9.5857 | 1080.1 |  | 953 | 41.54 | 0.12923 | 62.422 | 0.00043315 | 9.5857 | 1080.1 | 1070.5143
954 | 0.12928 | 41.55 | 62.422 | 0.00043331 | 9.5958 | 1080.1 |  | 954 | 41.55 | 0.12928 | 62.422 | 0.00043331 | 9.5958 | 1080.1 | 1070.5042
955 | 0.12933 | 41.56 | 62.422 | 0.00043347 | 9.6058 | 1080.1 |  | 955 | 41.56 | 0.12933 | 62.422 | 0.00043347 | 9.6058 | 1080.1 | 1070.4942
956 | 0.12938 | 41.57 | 62.422 | 0.00043363 | 9.6159 | 1080.1 |  | 956 | 41.57 | 0.12938 | 62.422 | 0.00043363 | 9.6159 | 1080.1 | 1070.4841
957 | 0.12943 | 41.58 | 62.422 | 0.00043379 | 9.6259 | 1080.1 |  | 957 | 41.58 | 0.12943 | 62.422 | 0.00043379 | 9.6259 | 1080.1 | 1070.4741
958 | 0.12948 | 41.59 | 62.422 | 0.00043395 | 9.636 | 1080.1 |  | 958 | 41.59 | 0.12948 | 62.422 | 0.00043395 | 9.636 | 1080.1 | 1070.464
959 | 0.12953 | 41.6 | 62.422 | 0.00043411 | 9.646 | 1080.1 |  | 959 | 41.6 | 0.12953 | 62.422 | 0.00043411 | 9.646 | 1080.1 | 1070.454
960 | 0.12958 | 41.61 | 62.422 | 0.00043427 | 9.6561 | 1080.1 |  | 960 | 41.61 | 0.12958 | 62.422 | 0.00043427 | 9.6561 | 1080.1 | 1070.4439
961 | 0.12963 | 41.62 | 62.422 | 0.00043443 | 9.6661 | 1080.1 |  | 961 | 41.62 | 0.12963 | 62.422 | 0.00043443 | 9.6661 | 1080.1 | 1070.4339
962 | 0.12968 | 41.63 | 62.422 | 0.00043459 | 9.6762 | 1080.1 |  | 962 | 41.63 | 0.12968 | 62.422 | 0.00043459 | 9.6762 | 1080.1 | 1070.4238
963 | 0.12973 | 41.64 | 62.422 | 0.00043475 | 9.6862 | 1080.1 |  | 963 | 41.64 | 0.12973 | 62.422 | 0.00043475 | 9.6862 | 1080.1 | 1070.4138
964 | 0.12978 | 41.65 | 62.422 | 0.0004349 | 9.6963 | 1080.1 |  | 964 | 41.65 | 0.12978 | 62.422 | 0.0004349 | 9.6963 | 1080.1 | 1070.4037
965 | 0.12983 | 41.66 | 62.422 | 0.00043506 | 9.7063 | 1080.1 |  | 965 | 41.66 | 0.12983 | 62.422 | 0.00043506 | 9.7063 | 1080.1 | 1070.3937
966 | 0.12988 | 41.67 | 62.422 | 0.00043522 | 9.7164 | 1080.1 |  | 966 | 41.67 | 0.12988 | 62.422 | 0.00043522 | 9.7164 | 1080.1 | 1070.3836
967 | 0.12993 | 41.68 | 62.422 | 0.00043538 | 9.7264 | 1080.2 |  | 967 | 41.68 | 0.12993 | 62.422 | 0.00043538 | 9.7264 | 1080.2 | 1070.4736
968 | 0.12998 | 41.69 | 62.422 | 0.00043554 | 9.7365 | 1080.2 |  | 968 | 41.69 | 0.12998 | 62.422 | 0.00043554 | 9.7365 | 1080.2 | 1070.4635
969 | 0.13003 | 41.7 | 62.422 | 0.0004357 | 9.7465 | 1080.2 |  | 969 | 41.7 | 0.13003 | 62.422 | 0.0004357 | 9.7465 | 1080.2 | 1070.4535
970 | 0.13008 | 41.71 | 62.422 | 0.00043586 | 9.7566 | 1080.2 |  | 970 | 41.71 | 0.13008 | 62.422 | 0.00043586 | 9.7566 | 1080.2 | 1070.4434
971 | 0.13013 | 41.72 | 62.422 | 0.00043602 | 9.7666 | 1080.2 |  | 971 | 41.72 | 0.13013 | 62.422 | 0.00043602 | 9.7666 | 1080.2 | 1070.4334
972 | 0.13018 | 41.73 | 62.422 | 0.00043618 | 9.7767 | 1080.2 |  | 972 | 41.73 | 0.13018 | 62.422 | 0.00043618 | 9.7767 | 1080.2 | 1070.4233
973 | 0.13023 | 41.74 | 62.422 | 0.00043634 | 9.7867 | 1080.2 |  | 973 | 41.74 | 0.13023 | 62.422 | 0.00043634 | 9.7867 | 1080.2 | 1070.4133
974 | 0.13028 | 41.75 | 62.422 | 0.0004365 | 9.7968 | 1080.2 |  | 974 | 41.75 | 0.13028 | 62.422 | 0.0004365 | 9.7968 | 1080.2 | 1070.4032
975 | 0.13033 | 41.76 | 62.422 | 0.00043666 | 9.8068 | 1080.2 |  | 975 | 41.76 | 0.13033 | 62.422 | 0.00043666 | 9.8068 | 1080.2 | 1070.3932
976 | 0.13038 | 41.77 | 62.422 | 0.00043682 | 9.8169 | 1080.2 |  | 976 | 41.77 | 0.13038 | 62.422 | 0.00043682 | 9.8169 | 1080.2 | 1070.3831
977 | 0.13043 | 41.78 | 62.422 | 0.00043698 | 9.8269 | 1080.2 |  | 977 | 41.78 | 0.13043 | 62.422 | 0.00043698 | 9.8269 | 1080.2 | 1070.3731
978 | 0.13048 | 41.79 | 62.422 | 0.00043714 | 9.837 | 1080.2 |  | 978 | 41.79 | 0.13048 | 62.422 | 0.00043714 | 9.837 | 1080.2 | 1070.363
979 | 0.13053 | 41.8 | 62.422 | 0.0004373 | 9.847 | 1080.2 |  | 979 | 41.8 | 0.13053 | 62.422 | 0.0004373 | 9.847 | 1080.2 | 1070.353
980 | 0.13058 | 41.81 | 62.422 | 0.00043746 | 9.8571 | 1080.2 |  | 980 | 41.81 | 0.13058 | 62.422 | 0.00043746 | 9.8571 | 1080.2 | 1070.3429
981 | 0.13064 | 41.82 | 62.422 | 0.00043762 | 9.8671 | 1080.2 |  | 981 | 41.82 | 0.13064 | 62.422 | 0.00043762 | 9.8671 | 1080.2 | 1070.3329
982 | 0.13069 | 41.83 | 62.422 | 0.00043778 | 9.8772 | 1080.2 |  | 982 | 41.83 | 0.13069 | 62.422 | 0.00043778 | 9.8772 | 1080.2 | 1070.3228
983 | 0.13074 | 41.84 | 62.422 | 0.00043794 | 9.8872 | 1080.2 |  | 983 | 41.84 | 0.13074 | 62.422 | 0.00043794 | 9.8872 | 1080.2 | 1070.3128
984 | 0.13079 | 41.85 | 62.422 | 0.0004381 | 9.8973 | 1080.2 |  | 984 | 41.85 | 0.13079 | 62.422 | 0.0004381 | 9.8973 | 1080.2 | 1070.3027
985 | 0.13084 | 41.86 | 62.422 | 0.00043826 | 9.9073 | 1080.2 |  | 985 | 41.86 | 0.13084 | 62.422 | 0.00043826 | 9.9073 | 1080.2 | 1070.2927
986 | 0.13089 | 41.87 | 62.422 | 0.00043843 | 9.9174 | 1080.2 |  | 986 | 41.87 | 0.13089 | 62.422 | 0.00043843 | 9.9174 | 1080.2 | 1070.2826
987 | 0.13094 | 41.88 | 62.422 | 0.00043859 | 9.9274 | 1080.2 |  | 987 | 41.88 | 0.13094 | 62.422 | 0.00043859 | 9.9274 | 1080.2 | 1070.2726
988 | 0.13099 | 41.89 | 62.422 | 0.00043875 | 9.9375 | 1080.2 |  | 988 | 41.89 | 0.13099 | 62.422 | 0.00043875 | 9.9375 | 1080.2 | 1070.2625
989 | 0.13104 | 41.9 | 62.422 | 0.00043891 | 9.9475 | 1080.2 |  | 989 | 41.9 | 0.13104 | 62.422 | 0.00043891 | 9.9475 | 1080.2 | 1070.2525
990 | 0.13109 | 41.91 | 62.422 | 0.00043907 | 9.9576 | 1080.3 |  | 990 | 41.91 | 0.13109 | 62.422 | 0.00043907 | 9.9576 | 1080.3 | 1070.3424
991 | 0.13114 | 41.92 | 62.422 | 0.00043923 | 9.9676 | 1080.3 |  | 991 | 41.92 | 0.13114 | 62.422 | 0.00043923 | 9.9676 | 1080.3 | 1070.3324
992 | 0.13119 | 41.93 | 62.422 | 0.00043939 | 9.9777 | 1080.3 |  | 992 | 41.93 | 0.13119 | 62.422 | 0.00043939 | 9.9777 | 1080.3 | 1070.3223
993 | 0.13124 | 41.94 | 62.422 | 0.00043955 | 9.9877 | 1080.3 |  | 993 | 41.94 | 0.13124 | 62.422 | 0.00043955 | 9.9877 | 1080.3 | 1070.3123
994 | 0.13129 | 41.95 | 62.422 | 0.00043971 | 9.9977 | 1080.3 |  | 994 | 41.95 | 0.13129 | 62.422 | 0.00043971 | 9.9977 | 1080.3 | 1070.3023
995 | 0.13134 | 41.96 | 62.422 | 0.00043987 | 10.008 | 1080.3 |  | 995 | 41.96 | 0.13134 | 62.422 | 0.00043987 | 10.008 | 1080.3 | 1070.292
996 | 0.13139 | 41.97 | 62.422 | 0.00044003 | 10.018 | 1080.3 |  | 996 | 41.97 | 0.13139 | 62.422 | 0.00044003 | 10.018 | 1080.3 | 1070.282
997 | 0.13144 | 41.98 | 62.422 | 0.00044019 | 10.028 | 1080.3 |  | 997 | 41.98 | 0.13144 | 62.422 | 0.00044019 | 10.028 | 1080.3 | 1070.272
998 | 0.1315 | 41.99 | 62.422 | 0.00044036 | 10.038 | 1080.3 |  | 998 | 41.99 | 0.1315 | 62.422 | 0.00044036 | 10.038 | 1080.3 | 1070.262
999 | 0.13155 | 42 | 62.422 | 0.00044052 | 10.048 | 1080.3 |  | 999 | 42 | 0.13155 | 62.422 | 0.00044052 | 10.048 | 1080.3 | 1070.252
1000 | 0.1316 | 42.01 | 62.422 | 0.00044068 | 10.058 | 1080.3 |  | 1000 | 42.01 | 0.1316 | 62.422 | 0.00044068 | 10.058 | 1080.3 | 1070.242
1001 | 0.13165 | 42.02 | 62.422 | 0.00044084 | 10.068 | 1080.3 |  | 1001 | 42.02 | 0.13165 | 62.422 | 0.00044084 | 10.068 | 1080.3 | 1070.232
1002 | 0.1317 | 42.03 | 62.422 | 0.000441 | 10.078 | 1080.3 |  | 1002 | 42.03 | 0.1317 | 62.422 | 0.000441 | 10.078 | 1080.3 | 1070.222
1003 | 0.13175 | 42.04 | 62.422 | 0.00044116 | 10.088 | 1080.3 |  | 1003 | 42.04 | 0.13175 | 62.422 | 0.00044116 | 10.088 | 1080.3 | 1070.212
1004 | 0.1318 | 42.05 | 62.422 | 0.00044132 | 10.098 | 1080.3 |  | 1004 | 42.05 | 0.1318 | 62.422 | 0.00044132 | 10.098 | 1080.3 | 1070.202
1005 | 0.13185 | 42.06 | 62.422 | 0.00044149 | 10.108 | 1080.3 |  | 1005 | 42.06 | 0.13185 | 62.422 | 0.00044149 | 10.108 | 1080.3 | 1070.192
1006 | 0.1319 | 42.07 | 62.422 | 0.00044165 | 10.118 | 1080.3 |  | 1006 | 42.07 | 0.1319 | 62.422 | 0.00044165 | 10.118 | 1080.3 | 1070.182
1007 | 0.13195 | 42.08 | 62.422 | 0.00044181 | 10.128 | 1080.3 |  | 1007 | 42.08 | 0.13195 | 62.422 | 0.00044181 | 10.128 | 1080.3 | 1070.172
1008 | 0.132 | 42.09 | 62.422 | 0.00044197 | 10.138 | 1080.3 |  | 1008 | 42.09 | 0.132 | 62.422 | 0.00044197 | 10.138 | 1080.3 | 1070.162
1009 | 0.13205 | 42.1 | 62.422 | 0.00044213 | 10.148 | 1080.3 |  | 1009 | 42.1 | 0.13205 | 62.422 | 0.00044213 | 10.148 | 1080.3 | 1070.152
1010 | 0.13211 | 42.11 | 62.422 | 0.00044229 | 10.159 | 1080.3 |  | 1010 | 42.11 | 0.13211 | 62.422 | 0.00044229 | 10.159 | 1080.3 | 1070.141
1011 | 0.13216 | 42.12 | 62.422 | 0.00044246 | 10.169 | 1080.3 |  | 1011 | 42.12 | 0.13216 | 62.422 | 0.00044246 | 10.169 | 1080.3 | 1070.131
1012 | 0.13221 | 42.13 | 62.422 | 0.00044262 | 10.179 | 1080.3 |  | 1012 | 42.13 | 0.13221 | 62.422 | 0.00044262 | 10.179 | 1080.3 | 1070.121
1013 | 0.13226 | 42.14 | 62.422 | 0.00044278 | 10.189 | 1080.4 |  | 1013 | 42.14 | 0.13226 | 62.422 | 0.00044278 | 10.189 | 1080.4 | 1070.211
1014 | 0.13231 | 42.15 | 62.422 | 0.00044294 | 10.199 | 1080.4 |  | 1014 | 42.15 | 0.13231 | 62.422 | 0.00044294 | 10.199 | 1080.4 | 1070.201
1015 | 0.13236 | 42.16 | 62.422 | 0.0004431 | 10.209 | 1080.4 |  | 1015 | 42.16 | 0.13236 | 62.422 | 0.0004431 | 10.209 | 1080.4 | 1070.191
1016 | 0.13241 | 42.17 | 62.422 | 0.00044327 | 10.219 | 1080.4 |  | 1016 | 42.17 | 0.13241 | 62.422 | 0.00044327 | 10.219 | 1080.4 | 1070.181
1017 | 0.13246 | 42.18 | 62.422 | 0.00044343 | 10.229 | 1080.4 |  | 1017 | 42.18 | 0.13246 | 62.422 | 0.00044343 | 10.229 | 1080.4 | 1070.171
1018 | 0.13251 | 42.19 | 62.422 | 0.00044359 | 10.239 | 1080.4 |  | 1018 | 42.19 | 0.13251 | 62.422 | 0.00044359 | 10.239 | 1080.4 | 1070.161
1019 | 0.13256 | 42.2 | 62.422 | 0.00044375 | 10.249 | 1080.4 |  | 1019 | 42.2 | 0.13256 | 62.422 | 0.00044375 | 10.249 | 1080.4 | 1070.151
1020 | 0.13262 | 42.21 | 62.422 | 0.00044391 | 10.259 | 1080.4 |  | 1020 | 42.21 | 0.13262 | 62.422 | 0.00044391 | 10.259 | 1080.4 | 1070.141
1021 | 0.13267 | 42.22 | 62.422 | 0.00044408 | 10.269 | 1080.4 |  | 1021 | 42.22 | 0.13267 | 62.422 | 0.00044408 | 10.269 | 1080.4 | 1070.131
1022 | 0.13272 | 42.23 | 62.422 | 0.00044424 | 10.279 | 1080.4 |  | 1022 | 42.23 | 0.13272 | 62.422 | 0.00044424 | 10.279 | 1080.4 | 1070.121
1023 | 0.13277 | 42.24 | 62.422 | 0.0004444 | 10.289 | 1080.4 |  | 1023 | 42.24 | 0.13277 | 62.422 | 0.0004444 | 10.289 | 1080.4 | 1070.111
1024 | 0.13282 | 42.25 | 62.422 | 0.00044456 | 10.299 | 1080.4 |  | 1024 | 42.25 | 0.13282 | 62.422 | 0.00044456 | 10.299 | 1080.4 | 1070.101
1025 | 0.13287 | 42.26 | 62.422 | 0.00044473 | 10.309 | 1080.4 |  | 1025 | 42.26 | 0.13287 | 62.422 | 0.00044473 | 10.309 | 1080.4 | 1070.091
1026 | 0.13292 | 42.27 | 62.422 | 0.00044489 | 10.319 | 1080.4 |  | 1026 | 42.27 | 0.13292 | 62.422 | 0.00044489 | 10.319 | 1080.4 | 1070.081
1027 | 0.13297 | 42.28 | 62.422 | 0.00044505 | 10.329 | 1080.4 |  | 1027 | 42.28 | 0.13297 | 62.422 | 0.00044505 | 10.329 | 1080.4 | 1070.071
1028 | 0.13302 | 42.29 | 62.422 | 0.00044522 | 10.339 | 1080.4 |  | 1028 | 42.29 | 0.13302 | 62.422 | 0.00044522 | 10.339 | 1080.4 | 1070.061
1029 | 0.13308 | 42.3 | 62.422 | 0.00044538 | 10.349 | 1080.4 |  | 1029 | 42.3 | 0.13308 | 62.422 | 0.00044538 | 10.349 | 1080.4 | 1070.051
1030 | 0.13313 | 42.31 | 62.422 | 0.00044554 | 10.359 | 1080.4 |  | 1030 | 42.31 | 0.13313 | 62.422 | 0.00044554 | 10.359 | 1080.4 | 1070.041
1031 | 0.13318 | 42.32 | 62.422 | 0.0004457 | 10.37 | 1080.4 |  | 1031 | 42.32 | 0.13318 | 62.422 | 0.0004457 | 10.37 | 1080.4 | 1070.03
1032 | 0.13323 | 42.33 | 62.422 | 0.00044587 | 10.38 | 1080.4 |  | 1032 | 42.33 | 0.13323 | 62.422 | 0.00044587 | 10.38 | 1080.4 | 1070.02
1033 | 0.13328 | 42.34 | 62.422 | 0.00044603 | 10.39 | 1080.4 |  | 1033 | 42.34 | 0.13328 | 62.422 | 0.00044603 | 10.39 | 1080.4 | 1070.01
1034 | 0.13333 | 42.35 | 62.422 | 0.00044619 | 10.4 | 1080.4 |  | 1034 | 42.35 | 0.13333 | 62.422 | 0.00044619 | 10.4 | 1080.4 | 1070
1035 | 0.13338 | 42.36 | 62.422 | 0.00044636 | 10.41 | 1080.4 |  | 1035 | 42.36 | 0.13338 | 62.422 | 0.00044636 | 10.41 | 1080.4 | 1069.99
1036 | 0.13344 | 42.37 | 62.422 | 0.00044652 | 10.42 | 1080.5 |  | 1036 | 42.37 | 0.13344 | 62.422 | 0.00044652 | 10.42 | 1080.5 | 1070.08
1037 | 0.13349 | 42.38 | 62.422 | 0.00044668 | 10.43 | 1080.5 |  | 1037 | 42.38 | 0.13349 | 62.422 | 0.00044668 | 10.43 | 1080.5 | 1070.07
1038 | 0.13354 | 42.39 | 62.422 | 0.00044685 | 10.44 | 1080.5 |  | 1038 | 42.39 | 0.13354 | 62.422 | 0.00044685 | 10.44 | 1080.5 | 1070.06
1039 | 0.13359 | 42.4 | 62.422 | 0.00044701 | 10.45 | 1080.5 |  | 1039 | 42.4 | 0.13359 | 62.422 | 0.00044701 | 10.45 | 1080.5 | 1070.05
1040 | 0.13364 | 42.41 | 62.422 | 0.00044717 | 10.46 | 1080.5 |  | 1040 | 42.41 | 0.13364 | 62.422 | 0.00044717 | 10.46 | 1080.5 | 1070.04
1041 | 0.13369 | 42.42 | 62.422 | 0.00044734 | 10.47 | 1080.5 |  | 1041 | 42.42 | 0.13369 | 62.422 | 0.00044734 | 10.47 | 1080.5 | 1070.03
1042 | 0.13374 | 42.43 | 62.422 | 0.0004475 | 10.48 | 1080.5 |  | 1042 | 42.43 | 0.13374 | 62.422 | 0.0004475 | 10.48 | 1080.5 | 1070.02
1043 | 0.1338 | 42.44 | 62.422 | 0.00044766 | 10.49 | 1080.5 |  | 1043 | 42.44 | 0.1338 | 62.422 | 0.00044766 | 10.49 | 1080.5 | 1070.01
1044 | 0.13385 | 42.45 | 62.422 | 0.00044783 | 10.5 | 1080.5 |  | 1044 | 42.45 | 0.13385 | 62.422 | 0.00044783 | 10.5 | 1080.5 | 1070
1045 | 0.1339 | 42.46 | 62.422 | 0.00044799 | 10.51 | 1080.5 |  | 1045 | 42.46 | 0.1339 | 62.422 | 0.00044799 | 10.51 | 1080.5 | 1069.99
1046 | 0.13395 | 42.47 | 62.422 | 0.00044815 | 10.52 | 1080.5 |  | 1046 | 42.47 | 0.13395 | 62.422 | 0.00044815 | 10.52 | 1080.5 | 1069.98
1047 | 0.134 | 42.48 | 62.422 | 0.00044832 | 10.53 | 1080.5 |  | 1047 | 42.48 | 0.134 | 62.422 | 0.00044832 | 10.53 | 1080.5 | 1069.97
1048 | 0.13405 | 42.49 | 62.422 | 0.00044848 | 10.54 | 1080.5 |  | 1048 | 42.49 | 0.13405 | 62.422 | 0.00044848 | 10.54 | 1080.5 | 1069.96
1049 | 0.13411 | 42.5 | 62.422 | 0.00044864 | 10.55 | 1080.5 |  | 1049 | 42.5 | 0.13411 | 62.422 | 0.00044864 | 10.55 | 1080.5 | 1069.95
1050 | 0.13416 | 42.51 | 62.422 | 0.00044881 | 10.56 | 1080.5 |  | 1050 | 42.51 | 0.13416 | 62.422 | 0.00044881 | 10.56 | 1080.5 | 1069.94
1051 | 0.13421 | 42.52 | 62.422 | 0.00044897 | 10.57 | 1080.5 |  | 1051 | 42.52 | 0.13421 | 62.422 | 0.00044897 | 10.57 | 1080.5 | 1069.93
1052 | 0.13426 | 42.53 | 62.422 | 0.00044914 | 10.581 | 1080.5 |  | 1052 | 42.53 | 0.13426 | 62.422 | 0.00044914 | 10.581 | 1080.5 | 1069.919
1053 | 0.13431 | 42.54 | 62.422 | 0.0004493 | 10.591 | 1080.5 |  | 1053 | 42.54 | 0.13431 | 62.422 | 0.0004493 | 10.591 | 1080.5 | 1069.909
1054 | 0.13436 | 42.55 | 62.422 | 0.00044946 | 10.601 | 1080.5 |  | 1054 | 42.55 | 0.13436 | 62.422 | 0.00044946 | 10.601 | 1080.5 | 1069.899
1055 | 0.13442 | 42.56 | 62.422 | 0.00044963 | 10.611 | 1080.5 |  | 1055 | 42.56 | 0.13442 | 62.422 | 0.00044963 | 10.611 | 1080.5 | 1069.889
1056 | 0.13447 | 42.57 | 62.422 | 0.00044979 | 10.621 | 1080.5 |  | 1056 | 42.57 | 0.13447 | 62.422 | 0.00044979 | 10.621 | 1080.5 | 1069.879
1057 | 0.13452 | 42.58 | 62.422 | 0.00044996 | 10.631 | 1080.5 |  | 1057 | 42.58 | 0.13452 | 62.422 | 0.00044996 | 10.631 | 1080.5 | 1069.869
1058 | 0.13457 | 42.59 | 62.422 | 0.00045012 | 10.641 | 1080.6 |  | 1058 | 42.59 | 0.13457 | 62.422 | 0.00045012 | 10.641 | 1080.6 | 1069.959
1059 | 0.13462 | 42.6 | 62.422 | 0.00045029 | 10.651 | 1080.6 |  | 1059 | 42.6 | 0.13462 | 62.422 | 0.00045029 | 10.651 | 1080.6 | 1069.949
1060 | 0.13467 | 42.61 | 62.422 | 0.00045045 | 10.661 | 1080.6 |  | 1060 | 42.61 | 0.13467 | 62.422 | 0.00045045 | 10.661 | 1080.6 | 1069.939
1061 | 0.13473 | 42.62 | 62.422 | 0.00045061 | 10.671 | 1080.6 |  | 1061 | 42.62 | 0.13473 | 62.422 | 0.00045061 | 10.671 | 1080.6 | 1069.929
1062 | 0.13478 | 42.63 | 62.422 | 0.00045078 | 10.681 | 1080.6 |  | 1062 | 42.63 | 0.13478 | 62.422 | 0.00045078 | 10.681 | 1080.6 | 1069.919
1063 | 0.13483 | 42.64 | 62.422 | 0.00045094 | 10.691 | 1080.6 |  | 1063 | 42.64 | 0.13483 | 62.422 | 0.00045094 | 10.691 | 1080.6 | 1069.909
1064 | 0.13488 | 42.65 | 62.421 | 0.00045111 | 10.701 | 1080.6 |  | 1064 | 42.65 | 0.13488 | 62.421 | 0.00045111 | 10.701 | 1080.6 | 1069.899
1065 | 0.13493 | 42.66 | 62.421 | 0.00045127 | 10.711 | 1080.6 |  | 1065 | 42.66 | 0.13493 | 62.421 | 0.00045127 | 10.711 | 1080.6 | 1069.889
1066 | 0.13499 | 42.67 | 62.421 | 0.00045144 | 10.721 | 1080.6 |  | 1066 | 42.67 | 0.13499 | 62.421 | 0.00045144 | 10.721 | 1080.6 | 1069.879
1067 | 0.13504 | 42.68 | 62.421 | 0.0004516 | 10.731 | 1080.6 |  | 1067 | 42.68 | 0.13504 | 62.421 | 0.0004516 | 10.731 | 1080.6 | 1069.869
1068 | 0.13509 | 42.69 | 62.421 | 0.00045177 | 10.741 | 1080.6 |  | 1068 | 42.69 | 0.13509 | 62.421 | 0.00045177 | 10.741 | 1080.6 | 1069.859
1069 | 0.13514 | 42.7 | 62.421 | 0.00045193 | 10.751 | 1080.6 |  | 1069 | 42.7 | 0.13514 | 62.421 | 0.00045193 | 10.751 | 1080.6 | 1069.849
1070 | 0.13519 | 42.71 | 62.421 | 0.0004521 | 10.761 | 1080.6 |  | 1070 | 42.71 | 0.13519 | 62.421 | 0.0004521 | 10.761 | 1080.6 | 1069.839
1071 | 0.13525 | 42.72 | 62.421 | 0.00045226 | 10.771 | 1080.6 |  | 1071 | 42.72 | 0.13525 | 62.421 | 0.00045226 | 10.771 | 1080.6 | 1069.829
1072 | 0.1353 | 42.73 | 62.421 | 0.00045243 | 10.781 | 1080.6 |  | 1072 | 42.73 | 0.1353 | 62.421 | 0.00045243 | 10.781 | 1080.6 | 1069.819
1073 | 0.13535 | 42.74 | 62.421 | 0.00045259 | 10.791 | 1080.6 |  | 1073 | 42.74 | 0.13535 | 62.421 | 0.00045259 | 10.791 | 1080.6 | 1069.809
1074 | 0.1354 | 42.75 | 62.421 | 0.00045276 | 10.802 | 1080.6 |  | 1074 | 42.75 | 0.1354 | 62.421 | 0.00045276 | 10.802 | 1080.6 | 1069.798
1075 | 0.13545 | 42.76 | 62.421 | 0.00045292 | 10.812 | 1080.6 |  | 1075 | 42.76 | 0.13545 | 62.421 | 0.00045292 | 10.812 | 1080.6 | 1069.788
1076 | 0.13551 | 42.77 | 62.421 | 0.00045309 | 10.822 | 1080.6 |  | 1076 | 42.77 | 0.13551 | 62.421 | 0.00045309 | 10.822 | 1080.6 | 1069.778
1077 | 0.13556 | 42.78 | 62.421 | 0.00045325 | 10.832 | 1080.6 |  | 1077 | 42.78 | 0.13556 | 62.421 | 0.00045325 | 10.832 | 1080.6 | 1069.768
1078 | 0.13561 | 42.79 | 62.421 | 0.00045342 | 10.842 | 1080.6 |  | 1078 | 42.79 | 0.13561 | 62.421 | 0.00045342 | 10.842 | 1080.6 | 1069.758
1079 | 0.13566 | 42.8 | 62.421 | 0.00045358 | 10.852 | 1080.6 |  | 1079 | 42.8 | 0.13566 | 62.421 | 0.00045358 | 10.852 | 1080.6 | 1069.748
1080 | 0.13571 | 42.81 | 62.421 | 0.00045375 | 10.862 | 1080.6 |  | 1080 | 42.81 | 0.13571 | 62.421 | 0.00045375 | 10.862 | 1080.6 | 1069.738
1081 | 0.13577 | 42.82 | 62.421 | 0.00045391 | 10.872 | 1080.7 |  | 1081 | 42.82 | 0.13577 | 62.421 | 0.00045391 | 10.872 | 1080.7 | 1069.828
1082 | 0.13582 | 42.83 | 62.421 | 0.00045408 | 10.882 | 1080.7 |  | 1082 | 42.83 | 0.13582 | 62.421 | 0.00045408 | 10.882 | 1080.7 | 1069.818
1083 | 0.13587 | 42.84 | 62.421 | 0.00045425 | 10.892 | 1080.7 |  | 1083 | 42.84 | 0.13587 | 62.421 | 0.00045425 | 10.892 | 1080.7 | 1069.808
1084 | 0.13592 | 42.85 | 62.421 | 0.00045441 | 10.902 | 1080.7 |  | 1084 | 42.85 | 0.13592 | 62.421 | 0.00045441 | 10.902 | 1080.7 | 1069.798
1085 | 0.13597 | 42.86 | 62.421 | 0.00045458 | 10.912 | 1080.7 |  | 1085 | 42.86 | 0.13597 | 62.421 | 0.00045458 | 10.912 | 1080.7 | 1069.788
1086 | 0.13603 | 42.87 | 62.421 | 0.00045474 | 10.922 | 1080.7 |  | 1086 | 42.87 | 0.13603 | 62.421 | 0.00045474 | 10.922 | 1080.7 | 1069.778
1087 | 0.13608 | 42.88 | 62.421 | 0.00045491 | 10.932 | 1080.7 |  | 1087 | 42.88 | 0.13608 | 62.421 | 0.00045491 | 10.932 | 1080.7 | 1069.768
1088 | 0.13613 | 42.89 | 62.421 | 0.00045507 | 10.942 | 1080.7 |  | 1088 | 42.89 | 0.13613 | 62.421 | 0.00045507 | 10.942 | 1080.7 | 1069.758
1089 | 0.13618 | 42.9 | 62.421 | 0.00045524 | 10.952 | 1080.7 |  | 1089 | 42.9 | 0.13618 | 62.421 | 0.00045524 | 10.952 | 1080.7 | 1069.748
1090 | 0.13624 | 42.91 | 62.421 | 0.00045541 | 10.962 | 1080.7 |  | 1090 | 42.91 | 0.13624 | 62.421 | 0.00045541 | 10.962 | 1080.7 | 1069.738
1091 | 0.13629 | 42.92 | 62.421 | 0.00045557 | 10.972 | 1080.7 |  | 1091 | 42.92 | 0.13629 | 62.421 | 0.00045557 | 10.972 | 1080.7 | 1069.728
1092 | 0.13634 | 42.93 | 62.421 | 0.00045574 | 10.982 | 1080.7 |  | 1092 | 42.93 | 0.13634 | 62.421 | 0.00045574 | 10.982 | 1080.7 | 1069.718
1093 | 0.13639 | 42.94 | 62.421 | 0.0004559 | 10.992 | 1080.7 |  | 1093 | 42.94 | 0.13639 | 62.421 | 0.0004559 | 10.992 | 1080.7 | 1069.708
1094 | 0.13645 | 42.95 | 62.421 | 0.00045607 | 11.002 | 1080.7 |  | 1094 | 42.95 | 0.13645 | 62.421 | 0.00045607 | 11.002 | 1080.7 | 1069.698
1095 | 0.1365 | 42.96 | 62.421 | 0.00045624 | 11.012 | 1080.7 |  | 1095 | 42.96 | 0.1365 | 62.421 | 0.00045624 | 11.012 | 1080.7 | 1069.688
1096 | 0.13655 | 42.97 | 62.421 | 0.0004564 | 11.023 | 1080.7 |  | 1096 | 42.97 | 0.13655 | 62.421 | 0.0004564 | 11.023 | 1080.7 | 1069.677
1097 | 0.1366 | 42.98 | 62.421 | 0.00045657 | 11.033 | 1080.7 |  | 1097 | 42.98 | 0.1366 | 62.421 | 0.00045657 | 11.033 | 1080.7 | 1069.667
1098 | 0.13666 | 42.99 | 62.421 | 0.00045674 | 11.043 | 1080.7 |  | 1098 | 42.99 | 0.13666 | 62.421 | 0.00045674 | 11.043 | 1080.7 | 1069.657
1099 | 0.13671 | 43 | 62.421 | 0.0004569 | 11.053 | 1080.7 |  | 1099 | 43 | 0.13671 | 62.421 | 0.0004569 | 11.053 | 1080.7 | 1069.647
1100 | 0.13676 | 43.01 | 62.421 | 0.00045707 | 11.063 | 1080.7 |  | 1100 | 43.01 | 0.13676 | 62.421 | 0.00045707 | 11.063 | 1080.7 | 1069.637
1101 | 0.13681 | 43.02 | 62.421 | 0.00045724 | 11.073 | 1080.7 |  | 1101 | 43.02 | 0.13681 | 62.421 | 0.00045724 | 11.073 | 1080.7 | 1069.627
1102 | 0.13687 | 43.03 | 62.421 | 0.0004574 | 11.083 | 1080.7 |  | 1102 | 43.03 | 0.13687 | 62.421 | 0.0004574 | 11.083 | 1080.7 | 1069.617
1103 | 0.13692 | 43.04 | 62.421 | 0.00045757 | 11.093 | 1080.7 |  | 1103 | 43.04 | 0.13692 | 62.421 | 0.00045757 | 11.093 | 1080.7 | 1069.607
1104 | 0.13697 | 43.05 | 62.421 | 0.00045774 | 11.103 | 1080.8 |  | 1104 | 43.05 | 0.13697 | 62.421 | 0.00045774 | 11.103 | 1080.8 | 1069.697
1105 | 0.13702 | 43.06 | 62.421 | 0.0004579 | 11.113 | 1080.8 |  | 1105 | 43.06 | 0.13702 | 62.421 | 0.0004579 | 11.113 | 1080.8 | 1069.687
1106 | 0.13708 | 43.07 | 62.421 | 0.00045807 | 11.123 | 1080.8 |  | 1106 | 43.07 | 0.13708 | 62.421 | 0.00045807 | 11.123 | 1080.8 | 1069.677
1107 | 0.13713 | 43.08 | 62.421 | 0.00045824 | 11.133 | 1080.8 |  | 1107 | 43.08 | 0.13713 | 62.421 | 0.00045824 | 11.133 | 1080.8 | 1069.667
1108 | 0.13718 | 43.09 | 62.421 | 0.0004584 | 11.143 | 1080.8 |  | 1108 | 43.09 | 0.13718 | 62.421 | 0.0004584 | 11.143 | 1080.8 | 1069.657
1109 | 0.13723 | 43.1 | 62.421 | 0.00045857 | 11.153 | 1080.8 |  | 1109 | 43.1 | 0.13723 | 62.421 | 0.00045857 | 11.153 | 1080.8 | 1069.647
1110 | 0.13729 | 43.11 | 62.421 | 0.00045874 | 11.163 | 1080.8 |  | 1110 | 43.11 | 0.13729 | 62.421 | 0.00045874 | 11.163 | 1080.8 | 1069.637
1111 | 0.13734 | 43.12 | 62.421 | 0.0004589 | 11.173 | 1080.8 |  | 1111 | 43.12 | 0.13734 | 62.421 | 0.0004589 | 11.173 | 1080.8 | 1069.627
1112 | 0.13739 | 43.13 | 62.421 | 0.00045907 | 11.183 | 1080.8 |  | 1112 | 43.13 | 0.13739 | 62.421 | 0.00045907 | 11.183 | 1080.8 | 1069.617
1113 | 0.13745 | 43.14 | 62.421 | 0.00045924 | 11.193 | 1080.8 |  | 1113 | 43.14 | 0.13745 | 62.421 | 0.00045924 | 11.193 | 1080.8 | 1069.607
1114 | 0.1375 | 43.15 | 62.421 | 0.00045941 | 11.203 | 1080.8 |  | 1114 | 43.15 | 0.1375 | 62.421 | 0.00045941 | 11.203 | 1080.8 | 1069.597
1115 | 0.13755 | 43.16 | 62.421 | 0.00045957 | 11.213 | 1080.8 |  | 1115 | 43.16 | 0.13755 | 62.421 | 0.00045957 | 11.213 | 1080.8 | 1069.587
1116 | 0.1376 | 43.17 | 62.421 | 0.00045974 | 11.223 | 1080.8 |  | 1116 | 43.17 | 0.1376 | 62.421 | 0.00045974 | 11.223 | 1080.8 | 1069.577
1117 | 0.13766 | 43.18 | 62.421 | 0.00045991 | 11.233 | 1080.8 |  | 1117 | 43.18 | 0.13766 | 62.421 | 0.00045991 | 11.233 | 1080.8 | 1069.567
1118 | 0.13771 | 43.19 | 62.421 | 0.00046008 | 11.244 | 1080.8 |  | 1118 | 43.19 | 0.13771 | 62.421 | 0.00046008 | 11.244 | 1080.8 | 1069.556
1119 | 0.13776 | 43.2 | 62.421 | 0.00046024 | 11.254 | 1080.8 |  | 1119 | 43.2 | 0.13776 | 62.421 | 0.00046024 | 11.254 | 1080.8 | 1069.546
1120 | 0.13781 | 43.21 | 62.421 | 0.00046041 | 11.264 | 1080.8 |  | 1120 | 43.21 | 0.13781 | 62.421 | 0.00046041 | 11.264 | 1080.8 | 1069.536
1121 | 0.13787 | 43.22 | 62.421 | 0.00046058 | 11.274 | 1080.8 |  | 1121 | 43.22 | 0.13787 | 62.421 | 0.00046058 | 11.274 | 1080.8 | 1069.526
1122 | 0.13792 | 43.23 | 62.421 | 0.00046075 | 11.284 | 1080.8 |  | 1122 | 43.23 | 0.13792 | 62.421 | 0.00046075 | 11.284 | 1080.8 | 1069.516
1123 | 0.13797 | 43.24 | 62.421 | 0.00046091 | 11.294 | 1080.8 |  | 1123 | 43.24 | 0.13797 | 62.421 | 0.00046091 | 11.294 | 1080.8 | 1069.506
1124 | 0.13803 | 43.25 | 62.421 | 0.00046108 | 11.304 | 1080.8 |  | 1124 | 43.25 | 0.13803 | 62.421 | 0.00046108 | 11.304 | 1080.8 | 1069.496
1125 | 0.13808 | 43.26 | 62.421 | 0.00046125 | 11.314 | 1080.8 |  | 1125 | 43.26 | 0.13808 | 62.421 | 0.00046125 | 11.314 | 1080.8 | 1069.486
1126 | 0.13813 | 43.27 | 62.421 | 0.00046142 | 11.324 | 1080.8 |  | 1126 | 43.27 | 0.13813 | 62.421 | 0.00046142 | 11.324 | 1080.8 | 1069.476
1127 | 0.13819 | 43.28 | 62.421 | 0.00046159 | 11.334 | 1080.9 |  | 1127 | 43.28 | 0.13819 | 62.421 | 0.00046159 | 11.334 | 1080.9 | 1069.566
1128 | 0.13824 | 43.29 | 62.421 | 0.00046175 | 11.344 | 1080.9 |  | 1128 | 43.29 | 0.13824 | 62.421 | 0.00046175 | 11.344 | 1080.9 | 1069.556
1129 | 0.13829 | 43.3 | 62.421 | 0.00046192 | 11.354 | 1080.9 |  | 1129 | 43.3 | 0.13829 | 62.421 | 0.00046192 | 11.354 | 1080.9 | 1069.546
1130 | 0.13834 | 43.31 | 62.421 | 0.00046209 | 11.364 | 1080.9 |  | 1130 | 43.31 | 0.13834 | 62.421 | 0.00046209 | 11.364 | 1080.9 | 1069.536
1131 | 0.1384 | 43.32 | 62.421 | 0.00046226 | 11.374 | 1080.9 |  | 1131 | 43.32 | 0.1384 | 62.421 | 0.00046226 | 11.374 | 1080.9 | 1069.526
1132 | 0.13845 | 43.33 | 62.421 | 0.00046243 | 11.384 | 1080.9 |  | 1132 | 43.33 | 0.13845 | 62.421 | 0.00046243 | 11.384 | 1080.9 | 1069.516
1133 | 0.1385 | 43.34 | 62.421 | 0.00046259 | 11.394 | 1080.9 |  | 1133 | 43.34 | 0.1385 | 62.421 | 0.00046259 | 11.394 | 1080.9 | 1069.506
1134 | 0.13856 | 43.35 | 62.421 | 0.00046276 | 11.404 | 1080.9 |  | 1134 | 43.35 | 0.13856 | 62.421 | 0.00046276 | 11.404 | 1080.9 | 1069.496
1135 | 0.13861 | 43.36 | 62.421 | 0.00046293 | 11.414 | 1080.9 |  | 1135 | 43.36 | 0.13861 | 62.421 | 0.00046293 | 11.414 | 1080.9 | 1069.486
1136 | 0.13866 | 43.37 | 62.421 | 0.0004631 | 11.424 | 1080.9 |  | 1136 | 43.37 | 0.13866 | 62.421 | 0.0004631 | 11.424 | 1080.9 | 1069.476
1137 | 0.13872 | 43.38 | 62.421 | 0.00046327 | 11.434 | 1080.9 |  | 1137 | 43.38 | 0.13872 | 62.421 | 0.00046327 | 11.434 | 1080.9 | 1069.466
1138 | 0.13877 | 43.39 | 62.421 | 0.00046344 | 11.444 | 1080.9 |  | 1138 | 43.39 | 0.13877 | 62.421 | 0.00046344 | 11.444 | 1080.9 | 1069.456
1139 | 0.13882 | 43.4 | 62.421 | 0.0004636 | 11.454 | 1080.9 |  | 1139 | 43.4 | 0.13882 | 62.421 | 0.0004636 | 11.454 | 1080.9 | 1069.446
1140 | 0.13888 | 43.41 | 62.421 | 0.00046377 | 11.465 | 1080.9 |  | 1140 | 43.41 | 0.13888 | 62.421 | 0.00046377 | 11.465 | 1080.9 | 1069.435
1141 | 0.13893 | 43.42 | 62.421 | 0.00046394 | 11.475 | 1080.9 |  | 1141 | 43.42 | 0.13893 | 62.421 | 0.00046394 | 11.475 | 1080.9 | 1069.425
1142 | 0.13898 | 43.43 | 62.421 | 0.00046411 | 11.485 | 1080.9 |  | 1142 | 43.43 | 0.13898 | 62.421 | 0.00046411 | 11.485 | 1080.9 | 1069.415
1143 | 0.13904 | 43.44 | 62.421 | 0.00046428 | 11.495 | 1080.9 |  | 1143 | 43.44 | 0.13904 | 62.421 | 0.00046428 | 11.495 | 1080.9 | 1069.405
1144 | 0.13909 | 43.45 | 62.421 | 0.00046445 | 11.505 | 1080.9 |  | 1144 | 43.45 | 0.13909 | 62.421 | 0.00046445 | 11.505 | 1080.9 | 1069.395
1145 | 0.13914 | 43.46 | 62.421 | 0.00046462 | 11.515 | 1080.9 |  | 1145 | 43.46 | 0.13914 | 62.421 | 0.00046462 | 11.515 | 1080.9 | 1069.385
1146 | 0.1392 | 43.47 | 62.421 | 0.00046479 | 11.525 | 1080.9 |  | 1146 | 43.47 | 0.1392 | 62.421 | 0.00046479 | 11.525 | 1080.9 | 1069.375
1147 | 0.13925 | 43.48 | 62.421 | 0.00046496 | 11.535 | 1080.9 |  | 1147 | 43.48 | 0.13925 | 62.421 | 0.00046496 | 11.535 | 1080.9 | 1069.365
1148 | 0.1393 | 43.49 | 62.421 | 0.00046512 | 11.545 | 1080.9 |  | 1148 | 43.49 | 0.1393 | 62.421 | 0.00046512 | 11.545 | 1080.9 | 1069.355
1149 | 0.13936 | 43.5 | 62.421 | 0.00046529 | 11.555 | 1080.9 |  | 1149 | 43.5 | 0.13936 | 62.421 | 0.00046529 | 11.555 | 1080.9 | 1069.345
1150 | 0.13941 | 43.51 | 62.421 | 0.00046546 | 11.565 | 1081 |  | 1150 | 43.51 | 0.13941 | 62.421 | 0.00046546 | 11.565 | 1081 | 1069.435
1151 | 0.13946 | 43.52 | 62.42 | 0.00046563 | 11.575 | 1081 |  | 1151 | 43.52 | 0.13946 | 62.42 | 0.00046563 | 11.575 | 1081 | 1069.425
1152 | 0.13952 | 43.53 | 62.42 | 0.0004658 | 11.585 | 1081 |  | 1152 | 43.53 | 0.13952 | 62.42 | 0.0004658 | 11.585 | 1081 | 1069.415
1153 | 0.13957 | 43.54 | 62.42 | 0.00046597 | 11.595 | 1081 |  | 1153 | 43.54 | 0.13957 | 62.42 | 0.00046597 | 11.595 | 1081 | 1069.405
1154 | 0.13962 | 43.55 | 62.42 | 0.00046614 | 11.605 | 1081 |  | 1154 | 43.55 | 0.13962 | 62.42 | 0.00046614 | 11.605 | 1081 | 1069.395
1155 | 0.13968 | 43.56 | 62.42 | 0.00046631 | 11.615 | 1081 |  | 1155 | 43.56 | 0.13968 | 62.42 | 0.00046631 | 11.615 | 1081 | 1069.385
1156 | 0.13973 | 43.57 | 62.42 | 0.00046648 | 11.625 | 1081 |  | 1156 | 43.57 | 0.13973 | 62.42 | 0.00046648 | 11.625 | 1081 | 1069.375
1157 | 0.13978 | 43.58 | 62.42 | 0.00046665 | 11.635 | 1081 |  | 1157 | 43.58 | 0.13978 | 62.42 | 0.00046665 | 11.635 | 1081 | 1069.365
1158 | 0.13984 | 43.59 | 62.42 | 0.00046682 | 11.645 | 1081 |  | 1158 | 43.59 | 0.13984 | 62.42 | 0.00046682 | 11.645 | 1081 | 1069.355
1159 | 0.13989 | 43.6 | 62.42 | 0.00046699 | 11.655 | 1081 |  | 1159 | 43.6 | 0.13989 | 62.42 | 0.00046699 | 11.655 | 1081 | 1069.345
1160 | 0.13994 | 43.61 | 62.42 | 0.00046716 | 11.665 | 1081 |  | 1160 | 43.61 | 0.13994 | 62.42 | 0.00046716 | 11.665 | 1081 | 1069.335
1161 | 0.14 | 43.62 | 62.42 | 0.00046733 | 11.675 | 1081 |  | 1161 | 43.62 | 0.14 | 62.42 | 0.00046733 | 11.675 | 1081 | 1069.325
1162 | 0.14005 | 43.63 | 62.42 | 0.0004675 | 11.685 | 1081 |  | 1162 | 43.63 | 0.14005 | 62.42 | 0.0004675 | 11.685 | 1081 | 1069.315
1163 | 0.14011 | 43.64 | 62.42 | 0.00046767 | 11.696 | 1081 |  | 1163 | 43.64 | 0.14011 | 62.42 | 0.00046767 | 11.696 | 1081 | 1069.304
1164 | 0.14016 | 43.65 | 62.42 | 0.00046784 | 11.706 | 1081 |  | 1164 | 43.65 | 0.14016 | 62.42 | 0.00046784 | 11.706 | 1081 | 1069.294
1165 | 0.14021 | 43.66 | 62.42 | 0.00046801 | 11.716 | 1081 |  | 1165 | 43.66 | 0.14021 | 62.42 | 0.00046801 | 11.716 | 1081 | 1069.284
1166 | 0.14027 | 43.67 | 62.42 | 0.00046818 | 11.726 | 1081 |  | 1166 | 43.67 | 0.14027 | 62.42 | 0.00046818 | 11.726 | 1081 | 1069.274
1167 | 0.14032 | 43.68 | 62.42 | 0.00046835 | 11.736 | 1081 |  | 1167 | 43.68 | 0.14032 | 62.42 | 0.00046835 | 11.736 | 1081 | 1069.264
1168 | 0.14037 | 43.69 | 62.42 | 0.00046852 | 11.746 | 1081 |  | 1168 | 43.69 | 0.14037 | 62.42 | 0.00046852 | 11.746 | 1081 | 1069.254
1169 | 0.14043 | 43.7 | 62.42 | 0.00046869 | 11.756 | 1081 |  | 1169 | 43.7 | 0.14043 | 62.42 | 0.00046869 | 11.756 | 1081 | 1069.244
1170 | 0.14048 | 43.71 | 62.42 | 0.00046886 | 11.766 | 1081 |  | 1170 | 43.71 | 0.14048 | 62.42 | 0.00046886 | 11.766 | 1081 | 1069.234
1171 | 0.14054 | 43.72 | 62.42 | 0.00046903 | 11.776 | 1081 |  | 1171 | 43.72 | 0.14054 | 62.42 | 0.00046903 | 11.776 | 1081 | 1069.224
1172 | 0.14059 | 43.73 | 62.42 | 0.0004692 | 11.786 | 1081 |  | 1172 | 43.73 | 0.14059 | 62.42 | 0.0004692 | 11.786 | 1081 | 1069.214
1173 | 0.14064 | 43.74 | 62.42 | 0.00046937 | 11.796 | 1081.1 |  | 1173 | 43.74 | 0.14064 | 62.42 | 0.00046937 | 11.796 | 1081.1 | 1069.304
1174 | 0.1407 | 43.75 | 62.42 | 0.00046954 | 11.806 | 1081.1 |  | 1174 | 43.75 | 0.1407 | 62.42 | 0.00046954 | 11.806 | 1081.1 | 1069.294
1175 | 0.14075 | 43.76 | 62.42 | 0.00046971 | 11.816 | 1081.1 |  | 1175 | 43.76 | 0.14075 | 62.42 | 0.00046971 | 11.816 | 1081.1 | 1069.284
1176 | 0.1408 | 43.77 | 62.42 | 0.00046988 | 11.826 | 1081.1 |  | 1176 | 43.77 | 0.1408 | 62.42 | 0.00046988 | 11.826 | 1081.1 | 1069.274
1177 | 0.14086 | 43.78 | 62.42 | 0.00047005 | 11.836 | 1081.1 |  | 1177 | 43.78 | 0.14086 | 62.42 | 0.00047005 | 11.836 | 1081.1 | 1069.264
1178 | 0.14091 | 43.79 | 62.42 | 0.00047022 | 11.846 | 1081.1 |  | 1178 | 43.79 | 0.14091 | 62.42 | 0.00047022 | 11.846 | 1081.1 | 1069.254
1179 | 0.14097 | 43.8 | 62.42 | 0.00047039 | 11.856 | 1081.1 |  | 1179 | 43.8 | 0.14097 | 62.42 | 0.00047039 | 11.856 | 1081.1 | 1069.244
1180 | 0.14102 | 43.81 | 62.42 | 0.00047056 | 11.866 | 1081.1 |  | 1180 | 43.81 | 0.14102 | 62.42 | 0.00047056 | 11.866 | 1081.1 | 1069.234
1181 | 0.14107 | 43.82 | 62.42 | 0.00047073 | 11.876 | 1081.1 |  | 1181 | 43.82 | 0.14107 | 62.42 | 0.00047073 | 11.876 | 1081.1 | 1069.224
1182 | 0.14113 | 43.83 | 62.42 | 0.0004709 | 11.886 | 1081.1 |  | 1182 | 43.83 | 0.14113 | 62.42 | 0.0004709 | 11.886 | 1081.1 | 1069.214
1183 | 0.14118 | 43.84 | 62.42 | 0.00047108 | 11.896 | 1081.1 |  | 1183 | 43.84 | 0.14118 | 62.42 | 0.00047108 | 11.896 | 1081.1 | 1069.204
1184 | 0.14124 | 43.85 | 62.42 | 0.00047125 | 11.906 | 1081.1 |  | 1184 | 43.85 | 0.14124 | 62.42 | 0.00047125 | 11.906 | 1081.1 | 1069.194
1185 | 0.14129 | 43.86 | 62.42 | 0.00047142 | 11.916 | 1081.1 |  | 1185 | 43.86 | 0.14129 | 62.42 | 0.00047142 | 11.916 | 1081.1 | 1069.184
1186 | 0.14134 | 43.87 | 62.42 | 0.00047159 | 11.927 | 1081.1 |  | 1186 | 43.87 | 0.14134 | 62.42 | 0.00047159 | 11.927 | 1081.1 | 1069.173
1187 | 0.1414 | 43.88 | 62.42 | 0.00047176 | 11.937 | 1081.1 |  | 1187 | 43.88 | 0.1414 | 62.42 | 0.00047176 | 11.937 | 1081.1 | 1069.163
1188 | 0.14145 | 43.89 | 62.42 | 0.00047193 | 11.947 | 1081.1 |  | 1188 | 43.89 | 0.14145 | 62.42 | 0.00047193 | 11.947 | 1081.1 | 1069.153
1189 | 0.14151 | 43.9 | 62.42 | 0.0004721 | 11.957 | 1081.1 |  | 1189 | 43.9 | 0.14151 | 62.42 | 0.0004721 | 11.957 | 1081.1 | 1069.143
1190 | 0.14156 | 43.91 | 62.42 | 0.00047227 | 11.967 | 1081.1 |  | 1190 | 43.91 | 0.14156 | 62.42 | 0.00047227 | 11.967 | 1081.1 | 1069.133
1191 | 0.14162 | 43.92 | 62.42 | 0.00047245 | 11.977 | 1081.1 |  | 1191 | 43.92 | 0.14162 | 62.42 | 0.00047245 | 11.977 | 1081.1 | 1069.123
1192 | 0.14167 | 43.93 | 62.42 | 0.00047262 | 11.987 | 1081.1 |  | 1192 | 43.93 | 0.14167 | 62.42 | 0.00047262 | 11.987 | 1081.1 | 1069.113
1193 | 0.14172 | 43.94 | 62.42 | 0.00047279 | 11.997 | 1081.1 |  | 1193 | 43.94 | 0.14172 | 62.42 | 0.00047279 | 11.997 | 1081.1 | 1069.103
1194 | 0.14178 | 43.95 | 62.42 | 0.00047296 | 12.007 | 1081.1 |  | 1194 | 43.95 | 0.14178 | 62.42 | 0.00047296 | 12.007 | 1081.1 | 1069.093
1195 | 0.14183 | 43.96 | 62.42 | 0.00047313 | 12.017 | 1081.1 |  | 1195 | 43.96 | 0.14183 | 62.42 | 0.00047313 | 12.017 | 1081.1 | 1069.083
1196 | 0.14189 | 43.97 | 62.42 | 0.0004733 | 12.027 | 1081.2 |  | 1196 | 43.97 | 0.14189 | 62.42 | 0.0004733 | 12.027 | 1081.2 | 1069.173
1197 | 0.14194 | 43.98 | 62.42 | 0.00047347 | 12.037 | 1081.2 |  | 1197 | 43.98 | 0.14194 | 62.42 | 0.00047347 | 12.037 | 1081.2 | 1069.163
1198 | 0.14199 | 43.99 | 62.42 | 0.00047365 | 12.047 | 1081.2 |  | 1198 | 43.99 | 0.14199 | 62.42 | 0.00047365 | 12.047 | 1081.2 | 1069.153
1199 | 0.14205 | 44 | 62.42 | 0.00047382 | 12.057 | 1081.2 |  | 1199 | 44 | 0.14205 | 62.42 | 0.00047382 | 12.057 | 1081.2 | 1069.143
1200 | 0.1421 | 44.01 | 62.42 | 0.00047399 | 12.067 | 1081.2 |  | 1200 | 44.01 | 0.1421 | 62.42 | 0.00047399 | 12.067 | 1081.2 | 1069.133
1201 | 0.14216 | 44.02 | 62.42 | 0.00047416 | 12.077 | 1081.2 |  | 1201 | 44.02 | 0.14216 | 62.42 | 0.00047416 | 12.077 | 1081.2 | 1069.123
1202 | 0.14221 | 44.03 | 62.42 | 0.00047433 | 12.087 | 1081.2 |  | 1202 | 44.03 | 0.14221 | 62.42 | 0.00047433 | 12.087 | 1081.2 | 1069.113
1203 | 0.14227 | 44.04 | 62.42 | 0.00047451 | 12.097 | 1081.2 |  | 1203 | 44.04 | 0.14227 | 62.42 | 0.00047451 | 12.097 | 1081.2 | 1069.103
1204 | 0.14232 | 44.05 | 62.42 | 0.00047468 | 12.107 | 1081.2 |  | 1204 | 44.05 | 0.14232 | 62.42 | 0.00047468 | 12.107 | 1081.2 | 1069.093
1205 | 0.14238 | 44.06 | 62.42 | 0.00047485 | 12.117 | 1081.2 |  | 1205 | 44.06 | 0.14238 | 62.42 | 0.00047485 | 12.117 | 1081.2 | 1069.083
1206 | 0.14243 | 44.07 | 62.42 | 0.00047502 | 12.127 | 1081.2 |  | 1206 | 44.07 | 0.14243 | 62.42 | 0.00047502 | 12.127 | 1081.2 | 1069.073
1207 | 0.14248 | 44.08 | 62.42 | 0.0004752 | 12.137 | 1081.2 |  | 1207 | 44.08 | 0.14248 | 62.42 | 0.0004752 | 12.137 | 1081.2 | 1069.063
1208 | 0.14254 | 44.09 | 62.42 | 0.00047537 | 12.147 | 1081.2 |  | 1208 | 44.09 | 0.14254 | 62.42 | 0.00047537 | 12.147 | 1081.2 | 1069.053
1209 | 0.14259 | 44.1 | 62.42 | 0.00047554 | 12.157 | 1081.2 |  | 1209 | 44.1 | 0.14259 | 62.42 | 0.00047554 | 12.157 | 1081.2 | 1069.043
1210 | 0.14265 | 44.11 | 62.42 | 0.00047571 | 12.168 | 1081.2 |  | 1210 | 44.11 | 0.14265 | 62.42 | 0.00047571 | 12.168 | 1081.2 | 1069.032
1211 | 0.1427 | 44.12 | 62.42 | 0.00047588 | 12.178 | 1081.2 |  | 1211 | 44.12 | 0.1427 | 62.42 | 0.00047588 | 12.178 | 1081.2 | 1069.022
1212 | 0.14276 | 44.13 | 62.42 | 0.00047606 | 12.188 | 1081.2 |  | 1212 | 44.13 | 0.14276 | 62.42 | 0.00047606 | 12.188 | 1081.2 | 1069.012
1213 | 0.14281 | 44.14 | 62.42 | 0.00047623 | 12.198 | 1081.2 |  | 1213 | 44.14 | 0.14281 | 62.42 | 0.00047623 | 12.198 | 1081.2 | 1069.002
1214 | 0.14287 | 44.15 | 62.42 | 0.0004764 | 12.208 | 1081.2 |  | 1214 | 44.15 | 0.14287 | 62.42 | 0.0004764 | 12.208 | 1081.2 | 1068.992
1215 | 0.14292 | 44.16 | 62.42 | 0.00047658 | 12.218 | 1081.2 |  | 1215 | 44.16 | 0.14292 | 62.42 | 0.00047658 | 12.218 | 1081.2 | 1068.982
1216 | 0.14297 | 44.17 | 62.42 | 0.00047675 | 12.228 | 1081.2 |  | 1216 | 44.17 | 0.14297 | 62.42 | 0.00047675 | 12.228 | 1081.2 | 1068.972
1217 | 0.14303 | 44.18 | 62.42 | 0.00047692 | 12.238 | 1081.2 |  | 1217 | 44.18 | 0.14303 | 62.42 | 0.00047692 | 12.238 | 1081.2 | 1068.962
1218 | 0.14308 | 44.19 | 62.42 | 0.00047709 | 12.248 | 1081.3 |  | 1218 | 44.19 | 0.14308 | 62.42 | 0.00047709 | 12.248 | 1081.3 | 1069.052
1219 | 0.14314 | 44.2 | 62.42 | 0.00047727 | 12.258 | 1081.3 |  | 1219 | 44.2 | 0.14314 | 62.42 | 0.00047727 | 12.258 | 1081.3 | 1069.042
1220 | 0.14319 | 44.21 | 62.42 | 0.00047744 | 12.268 | 1081.3 |  | 1220 | 44.21 | 0.14319 | 62.42 | 0.00047744 | 12.268 | 1081.3 | 1069.032
1221 | 0.14325 | 44.22 | 62.42 | 0.00047761 | 12.278 | 1081.3 |  | 1221 | 44.22 | 0.14325 | 62.42 | 0.00047761 | 12.278 | 1081.3 | 1069.022
1222 | 0.1433 | 44.23 | 62.42 | 0.00047779 | 12.288 | 1081.3 |  | 1222 | 44.23 | 0.1433 | 62.42 | 0.00047779 | 12.288 | 1081.3 | 1069.012
1223 | 0.14336 | 44.24 | 62.419 | 0.00047796 | 12.298 | 1081.3 |  | 1223 | 44.24 | 0.14336 | 62.419 | 0.00047796 | 12.298 | 1081.3 | 1069.002
1224 | 0.14341 | 44.25 | 62.419 | 0.00047813 | 12.308 | 1081.3 |  | 1224 | 44.25 | 0.14341 | 62.419 | 0.00047813 | 12.308 | 1081.3 | 1068.992
1225 | 0.14347 | 44.26 | 62.419 | 0.00047831 | 12.318 | 1081.3 |  | 1225 | 44.26 | 0.14347 | 62.419 | 0.00047831 | 12.318 | 1081.3 | 1068.982
1226 | 0.14352 | 44.27 | 62.419 | 0.00047848 | 12.328 | 1081.3 |  | 1226 | 44.27 | 0.14352 | 62.419 | 0.00047848 | 12.328 | 1081.3 | 1068.972
1227 | 0.14358 | 44.28 | 62.419 | 0.00047865 | 12.338 | 1081.3 |  | 1227 | 44.28 | 0.14358 | 62.419 | 0.00047865 | 12.338 | 1081.3 | 1068.962
1228 | 0.14363 | 44.29 | 62.419 | 0.00047883 | 12.348 | 1081.3 |  | 1228 | 44.29 | 0.14363 | 62.419 | 0.00047883 | 12.348 | 1081.3 | 1068.952
1229 | 0.14369 | 44.3 | 62.419 | 0.000479 | 12.358 | 1081.3 |  | 1229 | 44.3 | 0.14369 | 62.419 | 0.000479 | 12.358 | 1081.3 | 1068.942
1230 | 0.14374 | 44.31 | 62.419 | 0.00047917 | 12.368 | 1081.3 |  | 1230 | 44.31 | 0.14374 | 62.419 | 0.00047917 | 12.368 | 1081.3 | 1068.932
1231 | 0.1438 | 44.32 | 62.419 | 0.00047935 | 12.378 | 1081.3 |  | 1231 | 44.32 | 0.1438 | 62.419 | 0.00047935 | 12.378 | 1081.3 | 1068.922
1232 | 0.14385 | 44.33 | 62.419 | 0.00047952 | 12.388 | 1081.3 |  | 1232 | 44.33 | 0.14385 | 62.419 | 0.00047952 | 12.388 | 1081.3 | 1068.912
1233 | 0.14391 | 44.34 | 62.419 | 0.00047969 | 12.399 | 1081.3 |  | 1233 | 44.34 | 0.14391 | 62.419 | 0.00047969 | 12.399 | 1081.3 | 1068.901
1234 | 0.14396 | 44.35 | 62.419 | 0.00047987 | 12.409 | 1081.3 |  | 1234 | 44.35 | 0.14396 | 62.419 | 0.00047987 | 12.409 | 1081.3 | 1068.891
1235 | 0.14402 | 44.36 | 62.419 | 0.00048004 | 12.419 | 1081.3 |  | 1235 | 44.36 | 0.14402 | 62.419 | 0.00048004 | 12.419 | 1081.3 | 1068.881
1236 | 0.14407 | 44.37 | 62.419 | 0.00048021 | 12.429 | 1081.3 |  | 1236 | 44.37 | 0.14407 | 62.419 | 0.00048021 | 12.429 | 1081.3 | 1068.871
1237 | 0.14413 | 44.38 | 62.419 | 0.00048039 | 12.439 | 1081.3 |  | 1237 | 44.38 | 0.14413 | 62.419 | 0.00048039 | 12.439 | 1081.3 | 1068.861
1238 | 0.14418 | 44.39 | 62.419 | 0.00048056 | 12.449 | 1081.3 |  | 1238 | 44.39 | 0.14418 | 62.419 | 0.00048056 | 12.449 | 1081.3 | 1068.851
1239 | 0.14424 | 44.4 | 62.419 | 0.00048074 | 12.459 | 1081.3 |  | 1239 | 44.4 | 0.14424 | 62.419 | 0.00048074 | 12.459 | 1081.3 | 1068.841
1240 | 0.14429 | 44.41 | 62.419 | 0.00048091 | 12.469 | 1081.3 |  | 1240 | 44.41 | 0.14429 | 62.419 | 0.00048091 | 12.469 | 1081.3 | 1068.831
1241 | 0.14435 | 44.42 | 62.419 | 0.00048108 | 12.479 | 1081.4 |  | 1241 | 44.42 | 0.14435 | 62.419 | 0.00048108 | 12.479 | 1081.4 | 1068.921
1242 | 0.1444 | 44.43 | 62.419 | 0.00048126 | 12.489 | 1081.4 |  | 1242 | 44.43 | 0.1444 | 62.419 | 0.00048126 | 12.489 | 1081.4 | 1068.911
1243 | 0.14446 | 44.44 | 62.419 | 0.00048143 | 12.499 | 1081.4 |  | 1243 | 44.44 | 0.14446 | 62.419 | 0.00048143 | 12.499 | 1081.4 | 1068.901
1244 | 0.14451 | 44.45 | 62.419 | 0.00048161 | 12.509 | 1081.4 |  | 1244 | 44.45 | 0.14451 | 62.419 | 0.00048161 | 12.509 | 1081.4 | 1068.891
1245 | 0.14457 | 44.46 | 62.419 | 0.00048178 | 12.519 | 1081.4 |  | 1245 | 44.46 | 0.14457 | 62.419 | 0.00048178 | 12.519 | 1081.4 | 1068.881
1246 | 0.14462 | 44.47 | 62.419 | 0.00048196 | 12.529 | 1081.4 |  | 1246 | 44.47 | 0.14462 | 62.419 | 0.00048196 | 12.529 | 1081.4 | 1068.871
1247 | 0.14468 | 44.48 | 62.419 | 0.00048213 | 12.539 | 1081.4 |  | 1247 | 44.48 | 0.14468 | 62.419 | 0.00048213 | 12.539 | 1081.4 | 1068.861
1248 | 0.14473 | 44.49 | 62.419 | 0.0004823 | 12.549 | 1081.4 |  | 1248 | 44.49 | 0.14473 | 62.419 | 0.0004823 | 12.549 | 1081.4 | 1068.851
1249 | 0.14479 | 44.5 | 62.419 | 0.00048248 | 12.559 | 1081.4 |  | 1249 | 44.5 | 0.14479 | 62.419 | 0.00048248 | 12.559 | 1081.4 | 1068.841
1250 | 0.14484 | 44.51 | 62.419 | 0.00048265 | 12.569 | 1081.4 |  | 1250 | 44.51 | 0.14484 | 62.419 | 0.00048265 | 12.569 | 1081.4 | 1068.831
1251 | 0.1449 | 44.52 | 62.419 | 0.00048283 | 12.579 | 1081.4 |  | 1251 | 44.52 | 0.1449 | 62.419 | 0.00048283 | 12.579 | 1081.4 | 1068.821
1252 | 0.14495 | 44.53 | 62.419 | 0.000483 | 12.589 | 1081.4 |  | 1252 | 44.53 | 0.14495 | 62.419 | 0.000483 | 12.589 | 1081.4 | 1068.811
1253 | 0.14501 | 44.54 | 62.419 | 0.00048318 | 12.599 | 1081.4 |  | 1253 | 44.54 | 0.14501 | 62.419 | 0.00048318 | 12.599 | 1081.4 | 1068.801
1254 | 0.14506 | 44.55 | 62.419 | 0.00048335 | 12.609 | 1081.4 |  | 1254 | 44.55 | 0.14506 | 62.419 | 0.00048335 | 12.609 | 1081.4 | 1068.791
1255 | 0.14512 | 44.56 | 62.419 | 0.00048353 | 12.619 | 1081.4 |  | 1255 | 44.56 | 0.14512 | 62.419 | 0.00048353 | 12.619 | 1081.4 | 1068.781
1256 | 0.14517 | 44.57 | 62.419 | 0.0004837 | 12.629 | 1081.4 |  | 1256 | 44.57 | 0.14517 | 62.419 | 0.0004837 | 12.629 | 1081.4 | 1068.771
1257 | 0.14523 | 44.58 | 62.419 | 0.00048388 | 12.639 | 1081.4 |  | 1257 | 44.58 | 0.14523 | 62.419 | 0.00048388 | 12.639 | 1081.4 | 1068.761
1258 | 0.14529 | 44.59 | 62.419 | 0.00048405 | 12.65 | 1081.4 |  | 1258 | 44.59 | 0.14529 | 62.419 | 0.00048405 | 12.65 | 1081.4 | 1068.75
1259 | 0.14534 | 44.6 | 62.419 | 0.00048423 | 12.66 | 1081.4 |  | 1259 | 44.6 | 0.14534 | 62.419 | 0.00048423 | 12.66 | 1081.4 | 1068.74
1260 | 0.1454 | 44.61 | 62.419 | 0.0004844 | 12.67 | 1081.4 |  | 1260 | 44.61 | 0.1454 | 62.419 | 0.0004844 | 12.67 | 1081.4 | 1068.73
1261 | 0.14545 | 44.62 | 62.419 | 0.00048458 | 12.68 | 1081.4 |  | 1261 | 44.62 | 0.14545 | 62.419 | 0.00048458 | 12.68 | 1081.4 | 1068.72
1262 | 0.14551 | 44.63 | 62.419 | 0.00048475 | 12.69 | 1081.4 |  | 1262 | 44.63 | 0.14551 | 62.419 | 0.00048475 | 12.69 | 1081.4 | 1068.71
1263 | 0.14556 | 44.64 | 62.419 | 0.00048493 | 12.7 | 1081.4 |  | 1263 | 44.64 | 0.14556 | 62.419 | 0.00048493 | 12.7 | 1081.4 | 1068.7
1264 | 0.14562 | 44.65 | 62.419 | 0.0004851 | 12.71 | 1081.5 |  | 1264 | 44.65 | 0.14562 | 62.419 | 0.0004851 | 12.71 | 1081.5 | 1068.79
1265 | 0.14567 | 44.66 | 62.419 | 0.00048528 | 12.72 | 1081.5 |  | 1265 | 44.66 | 0.14567 | 62.419 | 0.00048528 | 12.72 | 1081.5 | 1068.78
1266 | 0.14573 | 44.67 | 62.419 | 0.00048546 | 12.73 | 1081.5 |  | 1266 | 44.67 | 0.14573 | 62.419 | 0.00048546 | 12.73 | 1081.5 | 1068.77
1267 | 0.14579 | 44.68 | 62.419 | 0.00048563 | 12.74 | 1081.5 |  | 1267 | 44.68 | 0.14579 | 62.419 | 0.00048563 | 12.74 | 1081.5 | 1068.76
1268 | 0.14584 | 44.69 | 62.419 | 0.00048581 | 12.75 | 1081.5 |  | 1268 | 44.69 | 0.14584 | 62.419 | 0.00048581 | 12.75 | 1081.5 | 1068.75
1269 | 0.1459 | 44.7 | 62.419 | 0.00048598 | 12.76 | 1081.5 |  | 1269 | 44.7 | 0.1459 | 62.419 | 0.00048598 | 12.76 | 1081.5 | 1068.74
1270 | 0.14595 | 44.71 | 62.419 | 0.00048616 | 12.77 | 1081.5 |  | 1270 | 44.71 | 0.14595 | 62.419 | 0.00048616 | 12.77 | 1081.5 | 1068.73
1271 | 0.14601 | 44.72 | 62.419 | 0.00048633 | 12.78 | 1081.5 |  | 1271 | 44.72 | 0.14601 | 62.419 | 0.00048633 | 12.78 | 1081.5 | 1068.72
1272 | 0.14606 | 44.73 | 62.419 | 0.00048651 | 12.79 | 1081.5 |  | 1272 | 44.73 | 0.14606 | 62.419 | 0.00048651 | 12.79 | 1081.5 | 1068.71
1273 | 0.14612 | 44.74 | 62.419 | 0.00048669 | 12.8 | 1081.5 |  | 1273 | 44.74 | 0.14612 | 62.419 | 0.00048669 | 12.8 | 1081.5 | 1068.7
1274 | 0.14617 | 44.75 | 62.419 | 0.00048686 | 12.81 | 1081.5 |  | 1274 | 44.75 | 0.14617 | 62.419 | 0.00048686 | 12.81 | 1081.5 | 1068.69
1275 | 0.14623 | 44.76 | 62.419 | 0.00048704 | 12.82 | 1081.5 |  | 1275 | 44.76 | 0.14623 | 62.419 | 0.00048704 | 12.82 | 1081.5 | 1068.68
1276 | 0.14629 | 44.77 | 62.419 | 0.00048721 | 12.83 | 1081.5 |  | 1276 | 44.77 | 0.14629 | 62.419 | 0.00048721 | 12.83 | 1081.5 | 1068.67
1277 | 0.14634 | 44.78 | 62.419 | 0.00048739 | 12.84 | 1081.5 |  | 1277 | 44.78 | 0.14634 | 62.419 | 0.00048739 | 12.84 | 1081.5 | 1068.66
1278 | 0.1464 | 44.79 | 62.419 | 0.00048757 | 12.85 | 1081.5 |  | 1278 | 44.79 | 0.1464 | 62.419 | 0.00048757 | 12.85 | 1081.5 | 1068.65
1279 | 0.14645 | 44.8 | 62.419 | 0.00048774 | 12.86 | 1081.5 |  | 1279 | 44.8 | 0.14645 | 62.419 | 0.00048774 | 12.86 | 1081.5 | 1068.64
1280 | 0.14651 | 44.81 | 62.419 | 0.00048792 | 12.87 | 1081.5 |  | 1280 | 44.81 | 0.14651 | 62.419 | 0.00048792 | 12.87 | 1081.5 | 1068.63
1281 | 0.14656 | 44.82 | 62.419 | 0.00048809 | 12.88 | 1081.5 |  | 1281 | 44.82 | 0.14656 | 62.419 | 0.00048809 | 12.88 | 1081.5 | 1068.62
1282 | 0.14662 | 44.83 | 62.419 | 0.00048827 | 12.891 | 1081.5 |  | 1282 | 44.83 | 0.14662 | 62.419 | 0.00048827 | 12.891 | 1081.5 | 1068.609
1283 | 0.14668 | 44.84 | 62.419 | 0.00048845 | 12.901 | 1081.5 |  | 1283 | 44.84 | 0.14668 | 62.419 | 0.00048845 | 12.901 | 1081.5 | 1068.599
1284 | 0.14673 | 44.85 | 62.419 | 0.00048862 | 12.911 | 1081.5 |  | 1284 | 44.85 | 0.14673 | 62.419 | 0.00048862 | 12.911 | 1081.5 | 1068.589
1285 | 0.14679 | 44.86 | 62.419 | 0.0004888 | 12.921 | 1081.5 |  | 1285 | 44.86 | 0.14679 | 62.419 | 0.0004888 | 12.921 | 1081.5 | 1068.579
1286 | 0.14684 | 44.87 | 62.419 | 0.00048898 | 12.931 | 1081.5 |  | 1286 | 44.87 | 0.14684 | 62.419 | 0.00048898 | 12.931 | 1081.5 | 1068.569
1287 | 0.1469 | 44.88 | 62.418 | 0.00048915 | 12.941 | 1081.6 |  | 1287 | 44.88 | 0.1469 | 62.418 | 0.00048915 | 12.941 | 1081.6 | 1068.659
1288 | 0.14696 | 44.89 | 62.418 | 0.00048933 | 12.951 | 1081.6 |  | 1288 | 44.89 | 0.14696 | 62.418 | 0.00048933 | 12.951 | 1081.6 | 1068.649
1289 | 0.14701 | 44.9 | 62.418 | 0.00048951 | 12.961 | 1081.6 |  | 1289 | 44.9 | 0.14701 | 62.418 | 0.00048951 | 12.961 | 1081.6 | 1068.639
1290 | 0.14707 | 44.91 | 62.418 | 0.00048968 | 12.971 | 1081.6 |  | 1290 | 44.91 | 0.14707 | 62.418 | 0.00048968 | 12.971 | 1081.6 | 1068.629
1291 | 0.14712 | 44.92 | 62.418 | 0.00048986 | 12.981 | 1081.6 |  | 1291 | 44.92 | 0.14712 | 62.418 | 0.00048986 | 12.981 | 1081.6 | 1068.619
1292 | 0.14718 | 44.93 | 62.418 | 0.00049004 | 12.991 | 1081.6 |  | 1292 | 44.93 | 0.14718 | 62.418 | 0.00049004 | 12.991 | 1081.6 | 1068.609
1293 | 0.14724 | 44.94 | 62.418 | 0.00049021 | 13.001 | 1081.6 |  | 1293 | 44.94 | 0.14724 | 62.418 | 0.00049021 | 13.001 | 1081.6 | 1068.599
1294 | 0.14729 | 44.95 | 62.418 | 0.00049039 | 13.011 | 1081.6 |  | 1294 | 44.95 | 0.14729 | 62.418 | 0.00049039 | 13.011 | 1081.6 | 1068.589
1295 | 0.14735 | 44.96 | 62.418 | 0.00049057 | 13.021 | 1081.6 |  | 1295 | 44.96 | 0.14735 | 62.418 | 0.00049057 | 13.021 | 1081.6 | 1068.579
1296 | 0.1474 | 44.97 | 62.418 | 0.00049075 | 13.031 | 1081.6 |  | 1296 | 44.97 | 0.1474 | 62.418 | 0.00049075 | 13.031 | 1081.6 | 1068.569
1297 | 0.14746 | 44.98 | 62.418 | 0.00049092 | 13.041 | 1081.6 |  | 1297 | 44.98 | 0.14746 | 62.418 | 0.00049092 | 13.041 | 1081.6 | 1068.559
1298 | 0.14752 | 44.99 | 62.418 | 0.0004911 | 13.051 | 1081.6 |  | 1298 | 44.99 | 0.14752 | 62.418 | 0.0004911 | 13.051 | 1081.6 | 1068.549
1299 | 0.14757 | 45 | 62.418 | 0.00049128 | 13.061 | 1081.6 |  | 1299 | 45 | 0.14757 | 62.418 | 0.00049128 | 13.061 | 1081.6 | 1068.539
1300 | 0.14763 | 45.01 | 62.418 | 0.00049146 | 13.071 | 1081.6 |  | 1300 | 45.01 | 0.14763 | 62.418 | 0.00049146 | 13.071 | 1081.6 | 1068.529
1301 | 0.14769 | 45.02 | 62.418 | 0.00049163 | 13.081 | 1081.6 |  | 1301 | 45.02 | 0.14769 | 62.418 | 0.00049163 | 13.081 | 1081.6 | 1068.519
1302 | 0.14774 | 45.03 | 62.418 | 0.00049181 | 13.091 | 1081.6 |  | 1302 | 45.03 | 0.14774 | 62.418 | 0.00049181 | 13.091 | 1081.6 | 1068.509
1303 | 0.1478 | 45.04 | 62.418 | 0.00049199 | 13.101 | 1081.6 |  | 1303 | 45.04 | 0.1478 | 62.418 | 0.00049199 | 13.101 | 1081.6 | 1068.499
1304 | 0.14785 | 45.05 | 62.418 | 0.00049217 | 13.111 | 1081.6 |  | 1304 | 45.05 | 0.14785 | 62.418 | 0.00049217 | 13.111 | 1081.6 | 1068.489
1305 | 0.14791 | 45.06 | 62.418 | 0.00049234 | 13.121 | 1081.6 |  | 1305 | 45.06 | 0.14791 | 62.418 | 0.00049234 | 13.121 | 1081.6 | 1068.479
1306 | 0.14797 | 45.07 | 62.418 | 0.00049252 | 13.131 | 1081.6 |  | 1306 | 45.07 | 0.14797 | 62.418 | 0.00049252 | 13.131 | 1081.6 | 1068.469
1307 | 0.14802 | 45.08 | 62.418 | 0.0004927 | 13.142 | 1081.6 |  | 1307 | 45.08 | 0.14802 | 62.418 | 0.0004927 | 13.142 | 1081.6 | 1068.458
1308 | 0.14808 | 45.09 | 62.418 | 0.00049288 | 13.152 | 1081.6 |  | 1308 | 45.09 | 0.14808 | 62.418 | 0.00049288 | 13.152 | 1081.6 | 1068.448
1309 | 0.14814 | 45.1 | 62.418 | 0.00049305 | 13.162 | 1081.6 |  | 1309 | 45.1 | 0.14814 | 62.418 | 0.00049305 | 13.162 | 1081.6 | 1068.438
1310 | 0.14819 | 45.11 | 62.418 | 0.00049323 | 13.172 | 1081.7 |  | 1310 | 45.11 | 0.14819 | 62.418 | 0.00049323 | 13.172 | 1081.7 | 1068.528
1311 | 0.14825 | 45.12 | 62.418 | 0.00049341 | 13.182 | 1081.7 |  | 1311 | 45.12 | 0.14825 | 62.418 | 0.00049341 | 13.182 | 1081.7 | 1068.518
1312 | 0.1483 | 45.13 | 62.418 | 0.00049359 | 13.192 | 1081.7 |  | 1312 | 45.13 | 0.1483 | 62.418 | 0.00049359 | 13.192 | 1081.7 | 1068.508
1313 | 0.14836 | 45.14 | 62.418 | 0.00049377 | 13.202 | 1081.7 |  | 1313 | 45.14 | 0.14836 | 62.418 | 0.00049377 | 13.202 | 1081.7 | 1068.498
1314 | 0.14842 | 45.15 | 62.418 | 0.00049394 | 13.212 | 1081.7 |  | 1314 | 45.15 | 0.14842 | 62.418 | 0.00049394 | 13.212 | 1081.7 | 1068.488
1315 | 0.14847 | 45.16 | 62.418 | 0.00049412 | 13.222 | 1081.7 |  | 1315 | 45.16 | 0.14847 | 62.418 | 0.00049412 | 13.222 | 1081.7 | 1068.478
1316 | 0.14853 | 45.17 | 62.418 | 0.0004943 | 13.232 | 1081.7 |  | 1316 | 45.17 | 0.14853 | 62.418 | 0.0004943 | 13.232 | 1081.7 | 1068.468
1317 | 0.14859 | 45.18 | 62.418 | 0.00049448 | 13.242 | 1081.7 |  | 1317 | 45.18 | 0.14859 | 62.418 | 0.00049448 | 13.242 | 1081.7 | 1068.458
1318 | 0.14864 | 45.19 | 62.418 | 0.00049466 | 13.252 | 1081.7 |  | 1318 | 45.19 | 0.14864 | 62.418 | 0.00049466 | 13.252 | 1081.7 | 1068.448
1319 | 0.1487 | 45.2 | 62.418 | 0.00049484 | 13.262 | 1081.7 |  | 1319 | 45.2 | 0.1487 | 62.418 | 0.00049484 | 13.262 | 1081.7 | 1068.438
1320 | 0.14876 | 45.21 | 62.418 | 0.00049502 | 13.272 | 1081.7 |  | 1320 | 45.21 | 0.14876 | 62.418 | 0.00049502 | 13.272 | 1081.7 | 1068.428
1321 | 0.14881 | 45.22 | 62.418 | 0.00049519 | 13.282 | 1081.7 |  | 1321 | 45.22 | 0.14881 | 62.418 | 0.00049519 | 13.282 | 1081.7 | 1068.418
1322 | 0.14887 | 45.23 | 62.418 | 0.00049537 | 13.292 | 1081.7 |  | 1322 | 45.23 | 0.14887 | 62.418 | 0.00049537 | 13.292 | 1081.7 | 1068.408
1323 | 0.14893 | 45.24 | 62.418 | 0.00049555 | 13.302 | 1081.7 |  | 1323 | 45.24 | 0.14893 | 62.418 | 0.00049555 | 13.302 | 1081.7 | 1068.398
1324 | 0.14898 | 45.25 | 62.418 | 0.00049573 | 13.312 | 1081.7 |  | 1324 | 45.25 | 0.14898 | 62.418 | 0.00049573 | 13.312 | 1081.7 | 1068.388
1325 | 0.14904 | 45.26 | 62.418 | 0.00049591 | 13.322 | 1081.7 |  | 1325 | 45.26 | 0.14904 | 62.418 | 0.00049591 | 13.322 | 1081.7 | 1068.378
1326 | 0.1491 | 45.27 | 62.418 | 0.00049609 | 13.332 | 1081.7 |  | 1326 | 45.27 | 0.1491 | 62.418 | 0.00049609 | 13.332 | 1081.7 | 1068.368
1327 | 0.14915 | 45.28 | 62.418 | 0.00049627 | 13.342 | 1081.7 |  | 1327 | 45.28 | 0.14915 | 62.418 | 0.00049627 | 13.342 | 1081.7 | 1068.358
1328 | 0.14921 | 45.29 | 62.418 | 0.00049645 | 13.352 | 1081.7 |  | 1328 | 45.29 | 0.14921 | 62.418 | 0.00049645 | 13.352 | 1081.7 | 1068.348
1329 | 0.14927 | 45.3 | 62.418 | 0.00049662 | 13.362 | 1081.7 |  | 1329 | 45.3 | 0.14927 | 62.418 | 0.00049662 | 13.362 | 1081.7 | 1068.338
1330 | 0.14932 | 45.31 | 62.418 | 0.0004968 | 13.372 | 1081.7 |  | 1330 | 45.31 | 0.14932 | 62.418 | 0.0004968 | 13.372 | 1081.7 | 1068.328
1331 | 0.14938 | 45.32 | 62.418 | 0.00049698 | 13.382 | 1081.7 |  | 1331 | 45.32 | 0.14938 | 62.418 | 0.00049698 | 13.382 | 1081.7 | 1068.318
1332 | 0.14944 | 45.33 | 62.418 | 0.00049716 | 13.392 | 1081.7 |  | 1332 | 45.33 | 0.14944 | 62.418 | 0.00049716 | 13.392 | 1081.7 | 1068.308
1333 | 0.14949 | 45.34 | 62.418 | 0.00049734 | 13.403 | 1081.8 |  | 1333 | 45.34 | 0.14949 | 62.418 | 0.00049734 | 13.403 | 1081.8 | 1068.397
1334 | 0.14955 | 45.35 | 62.418 | 0.00049752 | 13.413 | 1081.8 |  | 1334 | 45.35 | 0.14955 | 62.418 | 0.00049752 | 13.413 | 1081.8 | 1068.387
1335 | 0.14961 | 45.36 | 62.418 | 0.0004977 | 13.423 | 1081.8 |  | 1335 | 45.36 | 0.14961 | 62.418 | 0.0004977 | 13.423 | 1081.8 | 1068.377
1336 | 0.14966 | 45.37 | 62.418 | 0.00049788 | 13.433 | 1081.8 |  | 1336 | 45.37 | 0.14966 | 62.418 | 0.00049788 | 13.433 | 1081.8 | 1068.367
1337 | 0.14972 | 45.38 | 62.418 | 0.00049806 | 13.443 | 1081.8 |  | 1337 | 45.38 | 0.14972 | 62.418 | 0.00049806 | 13.443 | 1081.8 | 1068.357
1338 | 0.14978 | 45.39 | 62.418 | 0.00049824 | 13.453 | 1081.8 |  | 1338 | 45.39 | 0.14978 | 62.418 | 0.00049824 | 13.453 | 1081.8 | 1068.347
1339 | 0.14984 | 45.4 | 62.418 | 0.00049842 | 13.463 | 1081.8 |  | 1339 | 45.4 | 0.14984 | 62.418 | 0.00049842 | 13.463 | 1081.8 | 1068.337
1340 | 0.14989 | 45.41 | 62.418 | 0.0004986 | 13.473 | 1081.8 |  | 1340 | 45.41 | 0.14989 | 62.418 | 0.0004986 | 13.473 | 1081.8 | 1068.327
1341 | 0.14995 | 45.42 | 62.418 | 0.00049878 | 13.483 | 1081.8 |  | 1341 | 45.42 | 0.14995 | 62.418 | 0.00049878 | 13.483 | 1081.8 | 1068.317
1342 | 0.15001 | 45.43 | 62.418 | 0.00049896 | 13.493 | 1081.8 |  | 1342 | 45.43 | 0.15001 | 62.418 | 0.00049896 | 13.493 | 1081.8 | 1068.307
1343 | 0.15006 | 45.44 | 62.418 | 0.00049914 | 13.503 | 1081.8 |  | 1343 | 45.44 | 0.15006 | 62.418 | 0.00049914 | 13.503 | 1081.8 | 1068.297
1344 | 0.15012 | 45.45 | 62.417 | 0.00049932 | 13.513 | 1081.8 |  | 1344 | 45.45 | 0.15012 | 62.417 | 0.00049932 | 13.513 | 1081.8 | 1068.287
1345 | 0.15018 | 45.46 | 62.417 | 0.0004995 | 13.523 | 1081.8 |  | 1345 | 45.46 | 0.15018 | 62.417 | 0.0004995 | 13.523 | 1081.8 | 1068.277
1346 | 0.15023 | 45.47 | 62.417 | 0.00049968 | 13.533 | 1081.8 |  | 1346 | 45.47 | 0.15023 | 62.417 | 0.00049968 | 13.533 | 1081.8 | 1068.267
1347 | 0.15029 | 45.48 | 62.417 | 0.00049986 | 13.543 | 1081.8 |  | 1347 | 45.48 | 0.15029 | 62.417 | 0.00049986 | 13.543 | 1081.8 | 1068.257
1348 | 0.15035 | 45.49 | 62.417 | 0.00050004 | 13.553 | 1081.8 |  | 1348 | 45.49 | 0.15035 | 62.417 | 0.00050004 | 13.553 | 1081.8 | 1068.247
1349 | 0.15041 | 45.5 | 62.417 | 0.00050022 | 13.563 | 1081.8 |  | 1349 | 45.5 | 0.15041 | 62.417 | 0.00050022 | 13.563 | 1081.8 | 1068.237
1350 | 0.15046 | 45.51 | 62.417 | 0.0005004 | 13.573 | 1081.8 |  | 1350 | 45.51 | 0.15046 | 62.417 | 0.0005004 | 13.573 | 1081.8 | 1068.227
1351 | 0.15052 | 45.52 | 62.417 | 0.00050058 | 13.583 | 1081.8 |  | 1351 | 45.52 | 0.15052 | 62.417 | 0.00050058 | 13.583 | 1081.8 | 1068.217
1352 | 0.15058 | 45.53 | 62.417 | 0.00050076 | 13.593 | 1081.8 |  | 1352 | 45.53 | 0.15058 | 62.417 | 0.00050076 | 13.593 | 1081.8 | 1068.207
1353 | 0.15063 | 45.54 | 62.417 | 0.00050094 | 13.603 | 1081.8 |  | 1353 | 45.54 | 0.15063 | 62.417 | 0.00050094 | 13.603 | 1081.8 | 1068.197
1354 | 0.15069 | 45.55 | 62.417 | 0.00050112 | 13.613 | 1081.8 |  | 1354 | 45.55 | 0.15069 | 62.417 | 0.00050112 | 13.613 | 1081.8 | 1068.187
1355 | 0.15075 | 45.56 | 62.417 | 0.0005013 | 13.623 | 1081.8 |  | 1355 | 45.56 | 0.15075 | 62.417 | 0.0005013 | 13.623 | 1081.8 | 1068.177
1356 | 0.15081 | 45.57 | 62.417 | 0.00050148 | 13.633 | 1081.9 |  | 1356 | 45.57 | 0.15081 | 62.417 | 0.00050148 | 13.633 | 1081.9 | 1068.267
1357 | 0.15086 | 45.58 | 62.417 | 0.00050166 | 13.643 | 1081.9 |  | 1357 | 45.58 | 0.15086 | 62.417 | 0.00050166 | 13.643 | 1081.9 | 1068.257
1358 | 0.15092 | 45.59 | 62.417 | 0.00050184 | 13.653 | 1081.9 |  | 1358 | 45.59 | 0.15092 | 62.417 | 0.00050184 | 13.653 | 1081.9 | 1068.247
1359 | 0.15098 | 45.6 | 62.417 | 0.00050202 | 13.664 | 1081.9 |  | 1359 | 45.6 | 0.15098 | 62.417 | 0.00050202 | 13.664 | 1081.9 | 1068.236
1360 | 0.15103 | 45.61 | 62.417 | 0.0005022 | 13.674 | 1081.9 |  | 1360 | 45.61 | 0.15103 | 62.417 | 0.0005022 | 13.674 | 1081.9 | 1068.226
1361 | 0.15109 | 45.62 | 62.417 | 0.00050238 | 13.684 | 1081.9 |  | 1361 | 45.62 | 0.15109 | 62.417 | 0.00050238 | 13.684 | 1081.9 | 1068.216
1362 | 0.15115 | 45.63 | 62.417 | 0.00050256 | 13.694 | 1081.9 |  | 1362 | 45.63 | 0.15115 | 62.417 | 0.00050256 | 13.694 | 1081.9 | 1068.206
1363 | 0.15121 | 45.64 | 62.417 | 0.00050274 | 13.704 | 1081.9 |  | 1363 | 45.64 | 0.15121 | 62.417 | 0.00050274 | 13.704 | 1081.9 | 1068.196
1364 | 0.15126 | 45.65 | 62.417 | 0.00050293 | 13.714 | 1081.9 |  | 1364 | 45.65 | 0.15126 | 62.417 | 0.00050293 | 13.714 | 1081.9 | 1068.186
1365 | 0.15132 | 45.66 | 62.417 | 0.00050311 | 13.724 | 1081.9 |  | 1365 | 45.66 | 0.15132 | 62.417 | 0.00050311 | 13.724 | 1081.9 | 1068.176
1366 | 0.15138 | 45.67 | 62.417 | 0.00050329 | 13.734 | 1081.9 |  | 1366 | 45.67 | 0.15138 | 62.417 | 0.00050329 | 13.734 | 1081.9 | 1068.166
1367 | 0.15144 | 45.68 | 62.417 | 0.00050347 | 13.744 | 1081.9 |  | 1367 | 45.68 | 0.15144 | 62.417 | 0.00050347 | 13.744 | 1081.9 | 1068.156
1368 | 0.15149 | 45.69 | 62.417 | 0.00050365 | 13.754 | 1081.9 |  | 1368 | 45.69 | 0.15149 | 62.417 | 0.00050365 | 13.754 | 1081.9 | 1068.146
1369 | 0.15155 | 45.7 | 62.417 | 0.00050383 | 13.764 | 1081.9 |  | 1369 | 45.7 | 0.15155 | 62.417 | 0.00050383 | 13.764 | 1081.9 | 1068.136
1370 | 0.15161 | 45.71 | 62.417 | 0.00050401 | 13.774 | 1081.9 |  | 1370 | 45.71 | 0.15161 | 62.417 | 0.00050401 | 13.774 | 1081.9 | 1068.126
1371 | 0.15167 | 45.72 | 62.417 | 0.00050419 | 13.784 | 1081.9 |  | 1371 | 45.72 | 0.15167 | 62.417 | 0.00050419 | 13.784 | 1081.9 | 1068.116
1372 | 0.15172 | 45.73 | 62.417 | 0.00050438 | 13.794 | 1081.9 |  | 1372 | 45.73 | 0.15172 | 62.417 | 0.00050438 | 13.794 | 1081.9 | 1068.106
1373 | 0.15178 | 45.74 | 62.417 | 0.00050456 | 13.804 | 1081.9 |  | 1373 | 45.74 | 0.15178 | 62.417 | 0.00050456 | 13.804 | 1081.9 | 1068.096
1374 | 0.15184 | 45.75 | 62.417 | 0.00050474 | 13.814 | 1081.9 |  | 1374 | 45.75 | 0.15184 | 62.417 | 0.00050474 | 13.814 | 1081.9 | 1068.086
1375 | 0.1519 | 45.76 | 62.417 | 0.00050492 | 13.824 | 1081.9 |  | 1375 | 45.76 | 0.1519 | 62.417 | 0.00050492 | 13.824 | 1081.9 | 1068.076
1376 | 0.15195 | 45.77 | 62.417 | 0.0005051 | 13.834 | 1081.9 |  | 1376 | 45.77 | 0.15195 | 62.417 | 0.0005051 | 13.834 | 1081.9 | 1068.066
1377 | 0.15201 | 45.78 | 62.417 | 0.00050528 | 13.844 | 1081.9 |  | 1377 | 45.78 | 0.15201 | 62.417 | 0.00050528 | 13.844 | 1081.9 | 1068.056
1378 | 0.15207 | 45.79 | 62.417 | 0.00050547 | 13.854 | 1081.9 |  | 1378 | 45.79 | 0.15207 | 62.417 | 0.00050547 | 13.854 | 1081.9 | 1068.046
1379 | 0.15213 | 45.8 | 62.417 | 0.00050565 | 13.864 | 1082 |  | 1379 | 45.8 | 0.15213 | 62.417 | 0.00050565 | 13.864 | 1082 | 1068.136
1380 | 0.15219 | 45.81 | 62.417 | 0.00050583 | 13.874 | 1082 |  | 1380 | 45.81 | 0.15219 | 62.417 | 0.00050583 | 13.874 | 1082 | 1068.126
1381 | 0.15224 | 45.82 | 62.417 | 0.00050601 | 13.884 | 1082 |  | 1381 | 45.82 | 0.15224 | 62.417 | 0.00050601 | 13.884 | 1082 | 1068.116
1382 | 0.1523 | 45.83 | 62.417 | 0.00050619 | 13.894 | 1082 |  | 1382 | 45.83 | 0.1523 | 62.417 | 0.00050619 | 13.894 | 1082 | 1068.106
1383 | 0.15236 | 45.84 | 62.417 | 0.00050638 | 13.904 | 1082 |  | 1383 | 45.84 | 0.15236 | 62.417 | 0.00050638 | 13.904 | 1082 | 1068.096
1384 | 0.15242 | 45.85 | 62.417 | 0.00050656 | 13.914 | 1082 |  | 1384 | 45.85 | 0.15242 | 62.417 | 0.00050656 | 13.914 | 1082 | 1068.086
1385 | 0.15247 | 45.86 | 62.417 | 0.00050674 | 13.925 | 1082 |  | 1385 | 45.86 | 0.15247 | 62.417 | 0.00050674 | 13.925 | 1082 | 1068.075
1386 | 0.15253 | 45.87 | 62.417 | 0.00050692 | 13.935 | 1082 |  | 1386 | 45.87 | 0.15253 | 62.417 | 0.00050692 | 13.935 | 1082 | 1068.065
1387 | 0.15259 | 45.88 | 62.417 | 0.0005071 | 13.945 | 1082 |  | 1387 | 45.88 | 0.15259 | 62.417 | 0.0005071 | 13.945 | 1082 | 1068.055
1388 | 0.15265 | 45.89 | 62.417 | 0.00050729 | 13.955 | 1082 |  | 1388 | 45.89 | 0.15265 | 62.417 | 0.00050729 | 13.955 | 1082 | 1068.045
1389 | 0.15271 | 45.9 | 62.417 | 0.00050747 | 13.965 | 1082 |  | 1389 | 45.9 | 0.15271 | 62.417 | 0.00050747 | 13.965 | 1082 | 1068.035
1390 | 0.15276 | 45.91 | 62.417 | 0.00050765 | 13.975 | 1082 |  | 1390 | 45.91 | 0.15276 | 62.417 | 0.00050765 | 13.975 | 1082 | 1068.025
1391 | 0.15282 | 45.92 | 62.417 | 0.00050783 | 13.985 | 1082 |  | 1391 | 45.92 | 0.15282 | 62.417 | 0.00050783 | 13.985 | 1082 | 1068.015
1392 | 0.15288 | 45.93 | 62.417 | 0.00050802 | 13.995 | 1082 |  | 1392 | 45.93 | 0.15288 | 62.417 | 0.00050802 | 13.995 | 1082 | 1068.005
1393 | 0.15294 | 45.94 | 62.417 | 0.0005082 | 14.005 | 1082 |  | 1393 | 45.94 | 0.15294 | 62.417 | 0.0005082 | 14.005 | 1082 | 1067.995
1394 | 0.153 | 45.95 | 62.417 | 0.00050838 | 14.015 | 1082 |  | 1394 | 45.95 | 0.153 | 62.417 | 0.00050838 | 14.015 | 1082 | 1067.985
1395 | 0.15305 | 45.96 | 62.417 | 0.00050857 | 14.025 | 1082 |  | 1395 | 45.96 | 0.15305 | 62.417 | 0.00050857 | 14.025 | 1082 | 1067.975
1396 | 0.15311 | 45.97 | 62.417 | 0.00050875 | 14.035 | 1082 |  | 1396 | 45.97 | 0.15311 | 62.417 | 0.00050875 | 14.035 | 1082 | 1067.965
1397 | 0.15317 | 45.98 | 62.416 | 0.00050893 | 14.045 | 1082 |  | 1397 | 45.98 | 0.15317 | 62.416 | 0.00050893 | 14.045 | 1082 | 1067.955
1398 | 0.15323 | 45.99 | 62.416 | 0.00050911 | 14.055 | 1082 |  | 1398 | 45.99 | 0.15323 | 62.416 | 0.00050911 | 14.055 | 1082 | 1067.945
1399 | 0.15329 | 46 | 62.416 | 0.0005093 | 14.065 | 1082 |  | 1399 | 46 | 0.15329 | 62.416 | 0.0005093 | 14.065 | 1082 | 1067.935
1400 | 0.15334 | 46.01 | 62.416 | 0.00050948 | 14.075 | 1082 |  | 1400 | 46.01 | 0.15334 | 62.416 | 0.00050948 | 14.075 | 1082 | 1067.925
1401 | 0.1534 | 46.02 | 62.416 | 0.00050966 | 14.085 | 1082.1 |  | 1401 | 46.02 | 0.1534 | 62.416 | 0.00050966 | 14.085 | 1082.1 | 1068.015
1402 | 0.15346 | 46.03 | 62.416 | 0.00050985 | 14.095 | 1082.1 |  | 1402 | 46.03 | 0.15346 | 62.416 | 0.00050985 | 14.095 | 1082.1 | 1068.005
1403 | 0.15352 | 46.04 | 62.416 | 0.00051003 | 14.105 | 1082.1 |  | 1403 | 46.04 | 0.15352 | 62.416 | 0.00051003 | 14.105 | 1082.1 | 1067.995
1404 | 0.15358 | 46.05 | 62.416 | 0.00051021 | 14.115 | 1082.1 |  | 1404 | 46.05 | 0.15358 | 62.416 | 0.00051021 | 14.115 | 1082.1 | 1067.985
1405 | 0.15363 | 46.06 | 62.416 | 0.0005104 | 14.125 | 1082.1 |  | 1405 | 46.06 | 0.15363 | 62.416 | 0.0005104 | 14.125 | 1082.1 | 1067.975
1406 | 0.15369 | 46.07 | 62.416 | 0.00051058 | 14.135 | 1082.1 |  | 1406 | 46.07 | 0.15369 | 62.416 | 0.00051058 | 14.135 | 1082.1 | 1067.965
1407 | 0.15375 | 46.08 | 62.416 | 0.00051076 | 14.145 | 1082.1 |  | 1407 | 46.08 | 0.15375 | 62.416 | 0.00051076 | 14.145 | 1082.1 | 1067.955
1408 | 0.15381 | 46.09 | 62.416 | 0.00051095 | 14.155 | 1082.1 |  | 1408 | 46.09 | 0.15381 | 62.416 | 0.00051095 | 14.155 | 1082.1 | 1067.945
1409 | 0.15387 | 46.1 | 62.416 | 0.00051113 | 14.165 | 1082.1 |  | 1409 | 46.1 | 0.15387 | 62.416 | 0.00051113 | 14.165 | 1082.1 | 1067.935
1410 | 0.15393 | 46.11 | 62.416 | 0.00051131 | 14.175 | 1082.1 |  | 1410 | 46.11 | 0.15393 | 62.416 | 0.00051131 | 14.175 | 1082.1 | 1067.925
1411 | 0.15398 | 46.12 | 62.416 | 0.0005115 | 14.185 | 1082.1 |  | 1411 | 46.12 | 0.15398 | 62.416 | 0.0005115 | 14.185 | 1082.1 | 1067.915
1412 | 0.15404 | 46.13 | 62.416 | 0.00051168 | 14.196 | 1082.1 |  | 1412 | 46.13 | 0.15404 | 62.416 | 0.00051168 | 14.196 | 1082.1 | 1067.904
1413 | 0.1541 | 46.14 | 62.416 | 0.00051186 | 14.206 | 1082.1 |  | 1413 | 46.14 | 0.1541 | 62.416 | 0.00051186 | 14.206 | 1082.1 | 1067.894
1414 | 0.15416 | 46.15 | 62.416 | 0.00051205 | 14.216 | 1082.1 |  | 1414 | 46.15 | 0.15416 | 62.416 | 0.00051205 | 14.216 | 1082.1 | 1067.884
1415 | 0.15422 | 46.16 | 62.416 | 0.00051223 | 14.226 | 1082.1 |  | 1415 | 46.16 | 0.15422 | 62.416 | 0.00051223 | 14.226 | 1082.1 | 1067.874
1416 | 0.15428 | 46.17 | 62.416 | 0.00051242 | 14.236 | 1082.1 |  | 1416 | 46.17 | 0.15428 | 62.416 | 0.00051242 | 14.236 | 1082.1 | 1067.864
1417 | 0.15433 | 46.18 | 62.416 | 0.0005126 | 14.246 | 1082.1 |  | 1417 | 46.18 | 0.15433 | 62.416 | 0.0005126 | 14.246 | 1082.1 | 1067.854
1418 | 0.15439 | 46.19 | 62.416 | 0.00051278 | 14.256 | 1082.1 |  | 1418 | 46.19 | 0.15439 | 62.416 | 0.00051278 | 14.256 | 1082.1 | 1067.844
1419 | 0.15445 | 46.2 | 62.416 | 0.00051297 | 14.266 | 1082.1 |  | 1419 | 46.2 | 0.15445 | 62.416 | 0.00051297 | 14.266 | 1082.1 | 1067.834
1420 | 0.15451 | 46.21 | 62.416 | 0.00051315 | 14.276 | 1082.1 |  | 1420 | 46.21 | 0.15451 | 62.416 | 0.00051315 | 14.276 | 1082.1 | 1067.824
1421 | 0.15457 | 46.22 | 62.416 | 0.00051334 | 14.286 | 1082.1 |  | 1421 | 46.22 | 0.15457 | 62.416 | 0.00051334 | 14.286 | 1082.1 | 1067.814
1422 | 0.15463 | 46.23 | 62.416 | 0.00051352 | 14.296 | 1082.1 |  | 1422 | 46.23 | 0.15463 | 62.416 | 0.00051352 | 14.296 | 1082.1 | 1067.804
1423 | 0.15469 | 46.24 | 62.416 | 0.00051371 | 14.306 | 1082.1 |  | 1423 | 46.24 | 0.15469 | 62.416 | 0.00051371 | 14.306 | 1082.1 | 1067.794
1424 | 0.15474 | 46.25 | 62.416 | 0.00051389 | 14.316 | 1082.2 |  | 1424 | 46.25 | 0.15474 | 62.416 | 0.00051389 | 14.316 | 1082.2 | 1067.884
1425 | 0.1548 | 46.26 | 62.416 | 0.00051407 | 14.326 | 1082.2 |  | 1425 | 46.26 | 0.1548 | 62.416 | 0.00051407 | 14.326 | 1082.2 | 1067.874
1426 | 0.15486 | 46.27 | 62.416 | 0.00051426 | 14.336 | 1082.2 |  | 1426 | 46.27 | 0.15486 | 62.416 | 0.00051426 | 14.336 | 1082.2 | 1067.864
1427 | 0.15492 | 46.28 | 62.416 | 0.00051444 | 14.346 | 1082.2 |  | 1427 | 46.28 | 0.15492 | 62.416 | 0.00051444 | 14.346 | 1082.2 | 1067.854
1428 | 0.15498 | 46.29 | 62.416 | 0.00051463 | 14.356 | 1082.2 |  | 1428 | 46.29 | 0.15498 | 62.416 | 0.00051463 | 14.356 | 1082.2 | 1067.844
1429 | 0.15504 | 46.3 | 62.416 | 0.00051481 | 14.366 | 1082.2 |  | 1429 | 46.3 | 0.15504 | 62.416 | 0.00051481 | 14.366 | 1082.2 | 1067.834
1430 | 0.1551 | 46.31 | 62.416 | 0.000515 | 14.376 | 1082.2 |  | 1430 | 46.31 | 0.1551 | 62.416 | 0.000515 | 14.376 | 1082.2 | 1067.824
1431 | 0.15515 | 46.32 | 62.416 | 0.00051518 | 14.386 | 1082.2 |  | 1431 | 46.32 | 0.15515 | 62.416 | 0.00051518 | 14.386 | 1082.2 | 1067.814
1432 | 0.15521 | 46.33 | 62.416 | 0.00051537 | 14.396 | 1082.2 |  | 1432 | 46.33 | 0.15521 | 62.416 | 0.00051537 | 14.396 | 1082.2 | 1067.804
1433 | 0.15527 | 46.34 | 62.416 | 0.00051555 | 14.406 | 1082.2 |  | 1433 | 46.34 | 0.15527 | 62.416 | 0.00051555 | 14.406 | 1082.2 | 1067.794
1434 | 0.15533 | 46.35 | 62.416 | 0.00051574 | 14.416 | 1082.2 |  | 1434 | 46.35 | 0.15533 | 62.416 | 0.00051574 | 14.416 | 1082.2 | 1067.784
1435 | 0.15539 | 46.36 | 62.416 | 0.00051592 | 14.426 | 1082.2 |  | 1435 | 46.36 | 0.15539 | 62.416 | 0.00051592 | 14.426 | 1082.2 | 1067.774
1436 | 0.15545 | 46.37 | 62.416 | 0.00051611 | 14.436 | 1082.2 |  | 1436 | 46.37 | 0.15545 | 62.416 | 0.00051611 | 14.436 | 1082.2 | 1067.764
1437 | 0.15551 | 46.38 | 62.416 | 0.00051629 | 14.446 | 1082.2 |  | 1437 | 46.38 | 0.15551 | 62.416 | 0.00051629 | 14.446 | 1082.2 | 1067.754
1438 | 0.15557 | 46.39 | 62.416 | 0.00051648 | 14.456 | 1082.2 |  | 1438 | 46.39 | 0.15557 | 62.416 | 0.00051648 | 14.456 | 1082.2 | 1067.744
1439 | 0.15562 | 46.4 | 62.416 | 0.00051666 | 14.467 | 1082.2 |  | 1439 | 46.4 | 0.15562 | 62.416 | 0.00051666 | 14.467 | 1082.2 | 1067.733
1440 | 0.15568 | 46.41 | 62.416 | 0.00051685 | 14.477 | 1082.2 |  | 1440 | 46.41 | 0.15568 | 62.416 | 0.00051685 | 14.477 | 1082.2 | 1067.723
1441 | 0.15574 | 46.42 | 62.416 | 0.00051703 | 14.487 | 1082.2 |  | 1441 | 46.42 | 0.15574 | 62.416 | 0.00051703 | 14.487 | 1082.2 | 1067.713
1442 | 0.1558 | 46.43 | 62.416 | 0.00051722 | 14.497 | 1082.2 |  | 1442 | 46.43 | 0.1558 | 62.416 | 0.00051722 | 14.497 | 1082.2 | 1067.703
1443 | 0.15586 | 46.44 | 62.416 | 0.00051741 | 14.507 | 1082.2 |  | 1443 | 46.44 | 0.15586 | 62.416 | 0.00051741 | 14.507 | 1082.2 | 1067.693
1444 | 0.15592 | 46.45 | 62.416 | 0.00051759 | 14.517 | 1082.2 |  | 1444 | 46.45 | 0.15592 | 62.416 | 0.00051759 | 14.517 | 1082.2 | 1067.683
1445 | 0.15598 | 46.46 | 62.416 | 0.00051778 | 14.527 | 1082.2 |  | 1445 | 46.46 | 0.15598 | 62.416 | 0.00051778 | 14.527 | 1082.2 | 1067.673
1446 | 0.15604 | 46.47 | 62.415 | 0.00051796 | 14.537 | 1082.2 |  | 1446 | 46.47 | 0.15604 | 62.415 | 0.00051796 | 14.537 | 1082.2 | 1067.663
1447 | 0.1561 | 46.48 | 62.415 | 0.00051815 | 14.547 | 1082.3 |  | 1447 | 46.48 | 0.1561 | 62.415 | 0.00051815 | 14.547 | 1082.3 | 1067.753
1448 | 0.15616 | 46.49 | 62.415 | 0.00051833 | 14.557 | 1082.3 |  | 1448 | 46.49 | 0.15616 | 62.415 | 0.00051833 | 14.557 | 1082.3 | 1067.743
1449 | 0.15621 | 46.5 | 62.415 | 0.00051852 | 14.567 | 1082.3 |  | 1449 | 46.5 | 0.15621 | 62.415 | 0.00051852 | 14.567 | 1082.3 | 1067.733
1450 | 0.15627 | 46.51 | 62.415 | 0.00051871 | 14.577 | 1082.3 |  | 1450 | 46.51 | 0.15627 | 62.415 | 0.00051871 | 14.577 | 1082.3 | 1067.723
1451 | 0.15633 | 46.52 | 62.415 | 0.00051889 | 14.587 | 1082.3 |  | 1451 | 46.52 | 0.15633 | 62.415 | 0.00051889 | 14.587 | 1082.3 | 1067.713
1452 | 0.15639 | 46.53 | 62.415 | 0.00051908 | 14.597 | 1082.3 |  | 1452 | 46.53 | 0.15639 | 62.415 | 0.00051908 | 14.597 | 1082.3 | 1067.703
1453 | 0.15645 | 46.54 | 62.415 | 0.00051926 | 14.607 | 1082.3 |  | 1453 | 46.54 | 0.15645 | 62.415 | 0.00051926 | 14.607 | 1082.3 | 1067.693
1454 | 0.15651 | 46.55 | 62.415 | 0.00051945 | 14.617 | 1082.3 |  | 1454 | 46.55 | 0.15651 | 62.415 | 0.00051945 | 14.617 | 1082.3 | 1067.683
1455 | 0.15657 | 46.56 | 62.415 | 0.00051964 | 14.627 | 1082.3 |  | 1455 | 46.56 | 0.15657 | 62.415 | 0.00051964 | 14.627 | 1082.3 | 1067.673
1456 | 0.15663 | 46.57 | 62.415 | 0.00051982 | 14.637 | 1082.3 |  | 1456 | 46.57 | 0.15663 | 62.415 | 0.00051982 | 14.637 | 1082.3 | 1067.663
1457 | 0.15669 | 46.58 | 62.415 | 0.00052001 | 14.647 | 1082.3 |  | 1457 | 46.58 | 0.15669 | 62.415 | 0.00052001 | 14.647 | 1082.3 | 1067.653
1458 | 0.15675 | 46.59 | 62.415 | 0.0005202 | 14.657 | 1082.3 |  | 1458 | 46.59 | 0.15675 | 62.415 | 0.0005202 | 14.657 | 1082.3 | 1067.643
1459 | 0.15681 | 46.6 | 62.415 | 0.00052038 | 14.667 | 1082.3 |  | 1459 | 46.6 | 0.15681 | 62.415 | 0.00052038 | 14.667 | 1082.3 | 1067.633
1460 | 0.15687 | 46.61 | 62.415 | 0.00052057 | 14.677 | 1082.3 |  | 1460 | 46.61 | 0.15687 | 62.415 | 0.00052057 | 14.677 | 1082.3 | 1067.623
1461 | 0.15692 | 46.62 | 62.415 | 0.00052076 | 14.687 | 1082.3 |  | 1461 | 46.62 | 0.15692 | 62.415 | 0.00052076 | 14.687 | 1082.3 | 1067.613
1462 | 0.15698 | 46.63 | 62.415 | 0.00052094 | 14.697 | 1082.3 |  | 1462 | 46.63 | 0.15698 | 62.415 | 0.00052094 | 14.697 | 1082.3 | 1067.603
1463 | 0.15704 | 46.64 | 62.415 | 0.00052113 | 14.707 | 1082.3 |  | 1463 | 46.64 | 0.15704 | 62.415 | 0.00052113 | 14.707 | 1082.3 | 1067.593
1464 | 0.1571 | 46.65 | 62.415 | 0.00052132 | 14.717 | 1082.3 |  | 1464 | 46.65 | 0.1571 | 62.415 | 0.00052132 | 14.717 | 1082.3 | 1067.583
1465 | 0.15716 | 46.66 | 62.415 | 0.0005215 | 14.727 | 1082.3 |  | 1465 | 46.66 | 0.15716 | 62.415 | 0.0005215 | 14.727 | 1082.3 | 1067.573
1466 | 0.15722 | 46.67 | 62.415 | 0.00052169 | 14.737 | 1082.3 |  | 1466 | 46.67 | 0.15722 | 62.415 | 0.00052169 | 14.737 | 1082.3 | 1067.563
1467 | 0.15728 | 46.68 | 62.415 | 0.00052188 | 14.748 | 1082.3 |  | 1467 | 46.68 | 0.15728 | 62.415 | 0.00052188 | 14.748 | 1082.3 | 1067.552
1468 | 0.15734 | 46.69 | 62.415 | 0.00052206 | 14.758 | 1082.3 |  | 1468 | 46.69 | 0.15734 | 62.415 | 0.00052206 | 14.758 | 1082.3 | 1067.542
1469 | 0.1574 | 46.7 | 62.415 | 0.00052225 | 14.768 | 1082.3 |  | 1469 | 46.7 | 0.1574 | 62.415 | 0.00052225 | 14.768 | 1082.3 | 1067.532
1470 | 0.15746 | 46.71 | 62.415 | 0.00052244 | 14.778 | 1082.4 |  | 1470 | 46.71 | 0.15746 | 62.415 | 0.00052244 | 14.778 | 1082.4 | 1067.622
1471 | 0.15752 | 46.72 | 62.415 | 0.00052262 | 14.788 | 1082.4 |  | 1471 | 46.72 | 0.15752 | 62.415 | 0.00052262 | 14.788 | 1082.4 | 1067.612
1472 | 0.15758 | 46.73 | 62.415 | 0.00052281 | 14.798 | 1082.4 |  | 1472 | 46.73 | 0.15758 | 62.415 | 0.00052281 | 14.798 | 1082.4 | 1067.602
1473 | 0.15764 | 46.74 | 62.415 | 0.000523 | 14.808 | 1082.4 |  | 1473 | 46.74 | 0.15764 | 62.415 | 0.000523 | 14.808 | 1082.4 | 1067.592
1474 | 0.1577 | 46.75 | 62.415 | 0.00052319 | 14.818 | 1082.4 |  | 1474 | 46.75 | 0.1577 | 62.415 | 0.00052319 | 14.818 | 1082.4 | 1067.582
1475 | 0.15776 | 46.76 | 62.415 | 0.00052337 | 14.828 | 1082.4 |  | 1475 | 46.76 | 0.15776 | 62.415 | 0.00052337 | 14.828 | 1082.4 | 1067.572
1476 | 0.15782 | 46.77 | 62.415 | 0.00052356 | 14.838 | 1082.4 |  | 1476 | 46.77 | 0.15782 | 62.415 | 0.00052356 | 14.838 | 1082.4 | 1067.562
1477 | 0.15788 | 46.78 | 62.415 | 0.00052375 | 14.848 | 1082.4 |  | 1477 | 46.78 | 0.15788 | 62.415 | 0.00052375 | 14.848 | 1082.4 | 1067.552
1478 | 0.15794 | 46.79 | 62.415 | 0.00052394 | 14.858 | 1082.4 |  | 1478 | 46.79 | 0.15794 | 62.415 | 0.00052394 | 14.858 | 1082.4 | 1067.542
1479 | 0.158 | 46.8 | 62.415 | 0.00052412 | 14.868 | 1082.4 |  | 1479 | 46.8 | 0.158 | 62.415 | 0.00052412 | 14.868 | 1082.4 | 1067.532
1480 | 0.15806 | 46.81 | 62.415 | 0.00052431 | 14.878 | 1082.4 |  | 1480 | 46.81 | 0.15806 | 62.415 | 0.00052431 | 14.878 | 1082.4 | 1067.522
1481 | 0.15811 | 46.82 | 62.415 | 0.0005245 | 14.888 | 1082.4 |  | 1481 | 46.82 | 0.15811 | 62.415 | 0.0005245 | 14.888 | 1082.4 | 1067.512
1482 | 0.15817 | 46.83 | 62.415 | 0.00052469 | 14.898 | 1082.4 |  | 1482 | 46.83 | 0.15817 | 62.415 | 0.00052469 | 14.898 | 1082.4 | 1067.502
1483 | 0.15823 | 46.84 | 62.415 | 0.00052488 | 14.908 | 1082.4 |  | 1483 | 46.84 | 0.15823 | 62.415 | 0.00052488 | 14.908 | 1082.4 | 1067.492
1484 | 0.15829 | 46.85 | 62.415 | 0.00052506 | 14.918 | 1082.4 |  | 1484 | 46.85 | 0.15829 | 62.415 | 0.00052506 | 14.918 | 1082.4 | 1067.482
1485 | 0.15835 | 46.86 | 62.415 | 0.00052525 | 14.928 | 1082.4 |  | 1485 | 46.86 | 0.15835 | 62.415 | 0.00052525 | 14.928 | 1082.4 | 1067.472
1486 | 0.15841 | 46.87 | 62.415 | 0.00052544 | 14.938 | 1082.4 |  | 1486 | 46.87 | 0.15841 | 62.415 | 0.00052544 | 14.938 | 1082.4 | 1067.462
1487 | 0.15847 | 46.88 | 62.415 | 0.00052563 | 14.948 | 1082.4 |  | 1487 | 46.88 | 0.15847 | 62.415 | 0.00052563 | 14.948 | 1082.4 | 1067.452
1488 | 0.15853 | 46.89 | 62.415 | 0.00052582 | 14.958 | 1082.4 |  | 1488 | 46.89 | 0.15853 | 62.415 | 0.00052582 | 14.958 | 1082.4 | 1067.442
1489 | 0.15859 | 46.9 | 62.415 | 0.000526 | 14.968 | 1082.4 |  | 1489 | 46.9 | 0.15859 | 62.415 | 0.000526 | 14.968 | 1082.4 | 1067.432
1490 | 0.15865 | 46.91 | 62.415 | 0.00052619 | 14.978 | 1082.4 |  | 1490 | 46.91 | 0.15865 | 62.415 | 0.00052619 | 14.978 | 1082.4 | 1067.422
1491 | 0.15871 | 46.92 | 62.415 | 0.00052638 | 14.988 | 1082.4 |  | 1491 | 46.92 | 0.15871 | 62.415 | 0.00052638 | 14.988 | 1082.4 | 1067.412
1492 | 0.15877 | 46.93 | 62.414 | 0.00052657 | 14.998 | 1082.4 |  | 1492 | 46.93 | 0.15877 | 62.414 | 0.00052657 | 14.998 | 1082.4 | 1067.402
1493 | 0.15883 | 46.94 | 62.414 | 0.00052676 | 15.008 | 1082.5 |  | 1493 | 46.94 | 0.15883 | 62.414 | 0.00052676 | 15.008 | 1082.5 | 1067.492
1494 | 0.15889 | 46.95 | 62.414 | 0.00052695 | 15.018 | 1082.5 |  | 1494 | 46.95 | 0.15889 | 62.414 | 0.00052695 | 15.018 | 1082.5 | 1067.482
1495 | 0.15895 | 46.96 | 62.414 | 0.00052713 | 15.028 | 1082.5 |  | 1495 | 46.96 | 0.15895 | 62.414 | 0.00052713 | 15.028 | 1082.5 | 1067.472
1496 | 0.15901 | 46.97 | 62.414 | 0.00052732 | 15.039 | 1082.5 |  | 1496 | 46.97 | 0.15901 | 62.414 | 0.00052732 | 15.039 | 1082.5 | 1067.461
1497 | 0.15907 | 46.98 | 62.414 | 0.00052751 | 15.049 | 1082.5 |  | 1497 | 46.98 | 0.15907 | 62.414 | 0.00052751 | 15.049 | 1082.5 | 1067.451
1498 | 0.15913 | 46.99 | 62.414 | 0.0005277 | 15.059 | 1082.5 |  | 1498 | 46.99 | 0.15913 | 62.414 | 0.0005277 | 15.059 | 1082.5 | 1067.441
1499 | 0.15919 | 47 | 62.414 | 0.00052789 | 15.069 | 1082.5 |  | 1499 | 47 | 0.15919 | 62.414 | 0.00052789 | 15.069 | 1082.5 | 1067.431
1500 | 0.15925 | 47.01 | 62.414 | 0.00052808 | 15.079 | 1082.5 |  | 1500 | 47.01 | 0.15925 | 62.414 | 0.00052808 | 15.079 | 1082.5 | 1067.421
1501 | 0.15931 | 47.02 | 62.414 | 0.00052827 | 15.089 | 1082.5 |  | 1501 | 47.02 | 0.15931 | 62.414 | 0.00052827 | 15.089 | 1082.5 | 1067.411
1502 | 0.15937 | 47.03 | 62.414 | 0.00052846 | 15.099 | 1082.5 |  | 1502 | 47.03 | 0.15937 | 62.414 | 0.00052846 | 15.099 | 1082.5 | 1067.401
1503 | 0.15943 | 47.04 | 62.414 | 0.00052864 | 15.109 | 1082.5 |  | 1503 | 47.04 | 0.15943 | 62.414 | 0.00052864 | 15.109 | 1082.5 | 1067.391
1504 | 0.15949 | 47.05 | 62.414 | 0.00052883 | 15.119 | 1082.5 |  | 1504 | 47.05 | 0.15949 | 62.414 | 0.00052883 | 15.119 | 1082.5 | 1067.381
1505 | 0.15955 | 47.06 | 62.414 | 0.00052902 | 15.129 | 1082.5 |  | 1505 | 47.06 | 0.15955 | 62.414 | 0.00052902 | 15.129 | 1082.5 | 1067.371
1506 | 0.15961 | 47.07 | 62.414 | 0.00052921 | 15.139 | 1082.5 |  | 1506 | 47.07 | 0.15961 | 62.414 | 0.00052921 | 15.139 | 1082.5 | 1067.361
1507 | 0.15967 | 47.08 | 62.414 | 0.0005294 | 15.149 | 1082.5 |  | 1507 | 47.08 | 0.15967 | 62.414 | 0.0005294 | 15.149 | 1082.5 | 1067.351
1508 | 0.15973 | 47.09 | 62.414 | 0.00052959 | 15.159 | 1082.5 |  | 1508 | 47.09 | 0.15973 | 62.414 | 0.00052959 | 15.159 | 1082.5 | 1067.341
1509 | 0.15979 | 47.1 | 62.414 | 0.00052978 | 15.169 | 1082.5 |  | 1509 | 47.1 | 0.15979 | 62.414 | 0.00052978 | 15.169 | 1082.5 | 1067.331
1510 | 0.15985 | 47.11 | 62.414 | 0.00052997 | 15.179 | 1082.5 |  | 1510 | 47.11 | 0.15985 | 62.414 | 0.00052997 | 15.179 | 1082.5 | 1067.321
1511 | 0.15991 | 47.12 | 62.414 | 0.00053016 | 15.189 | 1082.5 |  | 1511 | 47.12 | 0.15991 | 62.414 | 0.00053016 | 15.189 | 1082.5 | 1067.311
1512 | 0.15997 | 47.13 | 62.414 | 0.00053035 | 15.199 | 1082.5 |  | 1512 | 47.13 | 0.15997 | 62.414 | 0.00053035 | 15.199 | 1082.5 | 1067.301
1513 | 0.16004 | 47.14 | 62.414 | 0.00053054 | 15.209 | 1082.5 |  | 1513 | 47.14 | 0.16004 | 62.414 | 0.00053054 | 15.209 | 1082.5 | 1067.291
1514 | 0.1601 | 47.15 | 62.414 | 0.00053073 | 15.219 | 1082.5 |  | 1514 | 47.15 | 0.1601 | 62.414 | 0.00053073 | 15.219 | 1082.5 | 1067.281
1515 | 0.16016 | 47.16 | 62.414 | 0.00053092 | 15.229 | 1082.5 |  | 1515 | 47.16 | 0.16016 | 62.414 | 0.00053092 | 15.229 | 1082.5 | 1067.271
1516 | 0.16022 | 47.17 | 62.414 | 0.00053111 | 15.239 | 1082.6 |  | 1516 | 47.17 | 0.16022 | 62.414 | 0.00053111 | 15.239 | 1082.6 | 1067.361
1517 | 0.16028 | 47.18 | 62.414 | 0.0005313 | 15.249 | 1082.6 |  | 1517 | 47.18 | 0.16028 | 62.414 | 0.0005313 | 15.249 | 1082.6 | 1067.351
1518 | 0.16034 | 47.19 | 62.414 | 0.00053149 | 15.259 | 1082.6 |  | 1518 | 47.19 | 0.16034 | 62.414 | 0.00053149 | 15.259 | 1082.6 | 1067.341
1519 | 0.1604 | 47.2 | 62.414 | 0.00053168 | 15.269 | 1082.6 |  | 1519 | 47.2 | 0.1604 | 62.414 | 0.00053168 | 15.269 | 1082.6 | 1067.331
1520 | 0.16046 | 47.21 | 62.414 | 0.00053187 | 15.279 | 1082.6 |  | 1520 | 47.21 | 0.16046 | 62.414 | 0.00053187 | 15.279 | 1082.6 | 1067.321
1521 | 0.16052 | 47.22 | 62.414 | 0.00053206 | 15.289 | 1082.6 |  | 1521 | 47.22 | 0.16052 | 62.414 | 0.00053206 | 15.289 | 1082.6 | 1067.311
1522 | 0.16058 | 47.23 | 62.414 | 0.00053225 | 15.299 | 1082.6 |  | 1522 | 47.23 | 0.16058 | 62.414 | 0.00053225 | 15.299 | 1082.6 | 1067.301
1523 | 0.16064 | 47.24 | 62.414 | 0.00053244 | 15.309 | 1082.6 |  | 1523 | 47.24 | 0.16064 | 62.414 | 0.00053244 | 15.309 | 1082.6 | 1067.291
1524 | 0.1607 | 47.25 | 62.414 | 0.00053263 | 15.319 | 1082.6 |  | 1524 | 47.25 | 0.1607 | 62.414 | 0.00053263 | 15.319 | 1082.6 | 1067.281
1525 | 0.16076 | 47.26 | 62.414 | 0.00053282 | 15.33 | 1082.6 |  | 1525 | 47.26 | 0.16076 | 62.414 | 0.00053282 | 15.33 | 1082.6 | 1067.27
1526 | 0.16082 | 47.27 | 62.414 | 0.00053301 | 15.34 | 1082.6 |  | 1526 | 47.27 | 0.16082 | 62.414 | 0.00053301 | 15.34 | 1082.6 | 1067.26
1527 | 0.16088 | 47.28 | 62.414 | 0.0005332 | 15.35 | 1082.6 |  | 1527 | 47.28 | 0.16088 | 62.414 | 0.0005332 | 15.35 | 1082.6 | 1067.25
1528 | 0.16094 | 47.29 | 62.414 | 0.00053339 | 15.36 | 1082.6 |  | 1528 | 47.29 | 0.16094 | 62.414 | 0.00053339 | 15.36 | 1082.6 | 1067.24
1529 | 0.161 | 47.3 | 62.414 | 0.00053358 | 15.37 | 1082.6 |  | 1529 | 47.3 | 0.161 | 62.414 | 0.00053358 | 15.37 | 1082.6 | 1067.23
1530 | 0.16106 | 47.31 | 62.414 | 0.00053377 | 15.38 | 1082.6 |  | 1530 | 47.31 | 0.16106 | 62.414 | 0.00053377 | 15.38 | 1082.6 | 1067.22
1531 | 0.16112 | 47.32 | 62.414 | 0.00053396 | 15.39 | 1082.6 |  | 1531 | 47.32 | 0.16112 | 62.414 | 0.00053396 | 15.39 | 1082.6 | 1067.21
1532 | 0.16119 | 47.33 | 62.414 | 0.00053415 | 15.4 | 1082.6 |  | 1532 | 47.33 | 0.16119 | 62.414 | 0.00053415 | 15.4 | 1082.6 | 1067.2
1533 | 0.16125 | 47.34 | 62.414 | 0.00053434 | 15.41 | 1082.6 |  | 1533 | 47.34 | 0.16125 | 62.414 | 0.00053434 | 15.41 | 1082.6 | 1067.19
1534 | 0.16131 | 47.35 | 62.414 | 0.00053453 | 15.42 | 1082.6 |  | 1534 | 47.35 | 0.16131 | 62.414 | 0.00053453 | 15.42 | 1082.6 | 1067.18
1535 | 0.16137 | 47.36 | 62.414 | 0.00053473 | 15.43 | 1082.6 |  | 1535 | 47.36 | 0.16137 | 62.414 | 0.00053473 | 15.43 | 1082.6 | 1067.17
1536 | 0.16143 | 47.37 | 62.413 | 0.00053492 | 15.44 | 1082.6 |  | 1536 | 47.37 | 0.16143 | 62.413 | 0.00053492 | 15.44 | 1082.6 | 1067.16
1537 | 0.16149 | 47.38 | 62.413 | 0.00053511 | 15.45 | 1082.6 |  | 1537 | 47.38 | 0.16149 | 62.413 | 0.00053511 | 15.45 | 1082.6 | 1067.15
1538 | 0.16155 | 47.39 | 62.413 | 0.0005353 | 15.46 | 1082.6 |  | 1538 | 47.39 | 0.16155 | 62.413 | 0.0005353 | 15.46 | 1082.6 | 1067.14
1539 | 0.16161 | 47.4 | 62.413 | 0.00053549 | 15.47 | 1082.7 |  | 1539 | 47.4 | 0.16161 | 62.413 | 0.00053549 | 15.47 | 1082.7 | 1067.23
1540 | 0.16167 | 47.41 | 62.413 | 0.00053568 | 15.48 | 1082.7 |  | 1540 | 47.41 | 0.16167 | 62.413 | 0.00053568 | 15.48 | 1082.7 | 1067.22
1541 | 0.16173 | 47.42 | 62.413 | 0.00053587 | 15.49 | 1082.7 |  | 1541 | 47.42 | 0.16173 | 62.413 | 0.00053587 | 15.49 | 1082.7 | 1067.21
1542 | 0.16179 | 47.43 | 62.413 | 0.00053606 | 15.5 | 1082.7 |  | 1542 | 47.43 | 0.16179 | 62.413 | 0.00053606 | 15.5 | 1082.7 | 1067.2
1543 | 0.16185 | 47.44 | 62.413 | 0.00053626 | 15.51 | 1082.7 |  | 1543 | 47.44 | 0.16185 | 62.413 | 0.00053626 | 15.51 | 1082.7 | 1067.19
1544 | 0.16192 | 47.45 | 62.413 | 0.00053645 | 15.52 | 1082.7 |  | 1544 | 47.45 | 0.16192 | 62.413 | 0.00053645 | 15.52 | 1082.7 | 1067.18
1545 | 0.16198 | 47.46 | 62.413 | 0.00053664 | 15.53 | 1082.7 |  | 1545 | 47.46 | 0.16198 | 62.413 | 0.00053664 | 15.53 | 1082.7 | 1067.17
1546 | 0.16204 | 47.47 | 62.413 | 0.00053683 | 15.54 | 1082.7 |  | 1546 | 47.47 | 0.16204 | 62.413 | 0.00053683 | 15.54 | 1082.7 | 1067.16
1547 | 0.1621 | 47.48 | 62.413 | 0.00053702 | 15.55 | 1082.7 |  | 1547 | 47.48 | 0.1621 | 62.413 | 0.00053702 | 15.55 | 1082.7 | 1067.15
1548 | 0.16216 | 47.49 | 62.413 | 0.00053721 | 15.56 | 1082.7 |  | 1548 | 47.49 | 0.16216 | 62.413 | 0.00053721 | 15.56 | 1082.7 | 1067.14
1549 | 0.16222 | 47.5 | 62.413 | 0.00053741 | 15.57 | 1082.7 |  | 1549 | 47.5 | 0.16222 | 62.413 | 0.00053741 | 15.57 | 1082.7 | 1067.13
1550 | 0.16228 | 47.51 | 62.413 | 0.0005376 | 15.58 | 1082.7 |  | 1550 | 47.51 | 0.16228 | 62.413 | 0.0005376 | 15.58 | 1082.7 | 1067.12
1551 | 0.16234 | 47.52 | 62.413 | 0.00053779 | 15.59 | 1082.7 |  | 1551 | 47.52 | 0.16234 | 62.413 | 0.00053779 | 15.59 | 1082.7 | 1067.11
1552 | 0.1624 | 47.53 | 62.413 | 0.00053798 | 15.6 | 1082.7 |  | 1552 | 47.53 | 0.1624 | 62.413 | 0.00053798 | 15.6 | 1082.7 | 1067.1
1553 | 0.16246 | 47.54 | 62.413 | 0.00053817 | 15.61 | 1082.7 |  | 1553 | 47.54 | 0.16246 | 62.413 | 0.00053817 | 15.61 | 1082.7 | 1067.09
1554 | 0.16253 | 47.55 | 62.413 | 0.00053836 | 15.621 | 1082.7 |  | 1554 | 47.55 | 0.16253 | 62.413 | 0.00053836 | 15.621 | 1082.7 | 1067.079
1555 | 0.16259 | 47.56 | 62.413 | 0.00053856 | 15.631 | 1082.7 |  | 1555 | 47.56 | 0.16259 | 62.413 | 0.00053856 | 15.631 | 1082.7 | 1067.069
1556 | 0.16265 | 47.57 | 62.413 | 0.00053875 | 15.641 | 1082.7 |  | 1556 | 47.57 | 0.16265 | 62.413 | 0.00053875 | 15.641 | 1082.7 | 1067.059
1557 | 0.16271 | 47.58 | 62.413 | 0.00053894 | 15.651 | 1082.7 |  | 1557 | 47.58 | 0.16271 | 62.413 | 0.00053894 | 15.651 | 1082.7 | 1067.049
1558 | 0.16277 | 47.59 | 62.413 | 0.00053913 | 15.661 | 1082.7 |  | 1558 | 47.59 | 0.16277 | 62.413 | 0.00053913 | 15.661 | 1082.7 | 1067.039
1559 | 0.16283 | 47.6 | 62.413 | 0.00053933 | 15.671 | 1082.7 |  | 1559 | 47.6 | 0.16283 | 62.413 | 0.00053933 | 15.671 | 1082.7 | 1067.029
1560 | 0.16289 | 47.61 | 62.413 | 0.00053952 | 15.681 | 1082.7 |  | 1560 | 47.61 | 0.16289 | 62.413 | 0.00053952 | 15.681 | 1082.7 | 1067.019
1561 | 0.16295 | 47.62 | 62.413 | 0.00053971 | 15.691 | 1082.7 |  | 1561 | 47.62 | 0.16295 | 62.413 | 0.00053971 | 15.691 | 1082.7 | 1067.009
1562 | 0.16302 | 47.63 | 62.413 | 0.0005399 | 15.701 | 1082.8 |  | 1562 | 47.63 | 0.16302 | 62.413 | 0.0005399 | 15.701 | 1082.8 | 1067.099
1563 | 0.16308 | 47.64 | 62.413 | 0.0005401 | 15.711 | 1082.8 |  | 1563 | 47.64 | 0.16308 | 62.413 | 0.0005401 | 15.711 | 1082.8 | 1067.089
1564 | 0.16314 | 47.65 | 62.413 | 0.00054029 | 15.721 | 1082.8 |  | 1564 | 47.65 | 0.16314 | 62.413 | 0.00054029 | 15.721 | 1082.8 | 1067.079
1565 | 0.1632 | 47.66 | 62.413 | 0.00054048 | 15.731 | 1082.8 |  | 1565 | 47.66 | 0.1632 | 62.413 | 0.00054048 | 15.731 | 1082.8 | 1067.069
1566 | 0.16326 | 47.67 | 62.413 | 0.00054067 | 15.741 | 1082.8 |  | 1566 | 47.67 | 0.16326 | 62.413 | 0.00054067 | 15.741 | 1082.8 | 1067.059
1567 | 0.16332 | 47.68 | 62.413 | 0.00054087 | 15.751 | 1082.8 |  | 1567 | 47.68 | 0.16332 | 62.413 | 0.00054087 | 15.751 | 1082.8 | 1067.049
1568 | 0.16338 | 47.69 | 62.413 | 0.00054106 | 15.761 | 1082.8 |  | 1568 | 47.69 | 0.16338 | 62.413 | 0.00054106 | 15.761 | 1082.8 | 1067.039
1569 | 0.16345 | 47.7 | 62.413 | 0.00054125 | 15.771 | 1082.8 |  | 1569 | 47.7 | 0.16345 | 62.413 | 0.00054125 | 15.771 | 1082.8 | 1067.029
1570 | 0.16351 | 47.71 | 62.413 | 0.00054145 | 15.781 | 1082.8 |  | 1570 | 47.71 | 0.16351 | 62.413 | 0.00054145 | 15.781 | 1082.8 | 1067.019
1571 | 0.16357 | 47.72 | 62.413 | 0.00054164 | 15.791 | 1082.8 |  | 1571 | 47.72 | 0.16357 | 62.413 | 0.00054164 | 15.791 | 1082.8 | 1067.009
1572 | 0.16363 | 47.73 | 62.413 | 0.00054183 | 15.801 | 1082.8 |  | 1572 | 47.73 | 0.16363 | 62.413 | 0.00054183 | 15.801 | 1082.8 | 1066.999
1573 | 0.16369 | 47.74 | 62.413 | 0.00054203 | 15.811 | 1082.8 |  | 1573 | 47.74 | 0.16369 | 62.413 | 0.00054203 | 15.811 | 1082.8 | 1066.989
1574 | 0.16375 | 47.75 | 62.413 | 0.00054222 | 15.821 | 1082.8 |  | 1574 | 47.75 | 0.16375 | 62.413 | 0.00054222 | 15.821 | 1082.8 | 1066.979
1575 | 0.16382 | 47.76 | 62.413 | 0.00054241 | 15.831 | 1082.8 |  | 1575 | 47.76 | 0.16382 | 62.413 | 0.00054241 | 15.831 | 1082.8 | 1066.969
1576 | 0.16388 | 47.77 | 62.413 | 0.00054261 | 15.841 | 1082.8 |  | 1576 | 47.77 | 0.16388 | 62.413 | 0.00054261 | 15.841 | 1082.8 | 1066.959
1577 | 0.16394 | 47.78 | 62.413 | 0.0005428 | 15.851 | 1082.8 |  | 1577 | 47.78 | 0.16394 | 62.413 | 0.0005428 | 15.851 | 1082.8 | 1066.949
1578 | 0.164 | 47.79 | 62.412 | 0.00054299 | 15.861 | 1082.8 |  | 1578 | 47.79 | 0.164 | 62.412 | 0.00054299 | 15.861 | 1082.8 | 1066.939
1579 | 0.16406 | 47.8 | 62.412 | 0.00054319 | 15.871 | 1082.8 |  | 1579 | 47.8 | 0.16406 | 62.412 | 0.00054319 | 15.871 | 1082.8 | 1066.929
1580 | 0.16412 | 47.81 | 62.412 | 0.00054338 | 15.881 | 1082.8 |  | 1580 | 47.81 | 0.16412 | 62.412 | 0.00054338 | 15.881 | 1082.8 | 1066.919
1581 | 0.16418 | 47.82 | 62.412 | 0.00054357 | 15.891 | 1082.8 |  | 1581 | 47.82 | 0.16418 | 62.412 | 0.00054357 | 15.891 | 1082.8 | 1066.909
1582 | 0.16425 | 47.83 | 62.412 | 0.00054377 | 15.901 | 1082.8 |  | 1582 | 47.83 | 0.16425 | 62.412 | 0.00054377 | 15.901 | 1082.8 | 1066.899
1583 | 0.16431 | 47.84 | 62.412 | 0.00054396 | 15.911 | 1082.8 |  | 1583 | 47.84 | 0.16431 | 62.412 | 0.00054396 | 15.911 | 1082.8 | 1066.889
1584 | 0.16437 | 47.85 | 62.412 | 0.00054416 | 15.921 | 1082.9 |  | 1584 | 47.85 | 0.16437 | 62.412 | 0.00054416 | 15.921 | 1082.9 | 1066.979
1585 | 0.16443 | 47.86 | 62.412 | 0.00054435 | 15.932 | 1082.9 |  | 1585 | 47.86 | 0.16443 | 62.412 | 0.00054435 | 15.932 | 1082.9 | 1066.968
1586 | 0.16449 | 47.87 | 62.412 | 0.00054454 | 15.942 | 1082.9 |  | 1586 | 47.87 | 0.16449 | 62.412 | 0.00054454 | 15.942 | 1082.9 | 1066.958
1587 | 0.16456 | 47.88 | 62.412 | 0.00054474 | 15.952 | 1082.9 |  | 1587 | 47.88 | 0.16456 | 62.412 | 0.00054474 | 15.952 | 1082.9 | 1066.948
1588 | 0.16462 | 47.89 | 62.412 | 0.00054493 | 15.962 | 1082.9 |  | 1588 | 47.89 | 0.16462 | 62.412 | 0.00054493 | 15.962 | 1082.9 | 1066.938
1589 | 0.16468 | 47.9 | 62.412 | 0.00054513 | 15.972 | 1082.9 |  | 1589 | 47.9 | 0.16468 | 62.412 | 0.00054513 | 15.972 | 1082.9 | 1066.928
1590 | 0.16474 | 47.91 | 62.412 | 0.00054532 | 15.982 | 1082.9 |  | 1590 | 47.91 | 0.16474 | 62.412 | 0.00054532 | 15.982 | 1082.9 | 1066.918
1591 | 0.1648 | 47.92 | 62.412 | 0.00054551 | 15.992 | 1082.9 |  | 1591 | 47.92 | 0.1648 | 62.412 | 0.00054551 | 15.992 | 1082.9 | 1066.908
1592 | 0.16487 | 47.93 | 62.412 | 0.00054571 | 16.002 | 1082.9 |  | 1592 | 47.93 | 0.16487 | 62.412 | 0.00054571 | 16.002 | 1082.9 | 1066.898
1593 | 0.16493 | 47.94 | 62.412 | 0.0005459 | 16.012 | 1082.9 |  | 1593 | 47.94 | 0.16493 | 62.412 | 0.0005459 | 16.012 | 1082.9 | 1066.888
1594 | 0.16499 | 47.95 | 62.412 | 0.0005461 | 16.022 | 1082.9 |  | 1594 | 47.95 | 0.16499 | 62.412 | 0.0005461 | 16.022 | 1082.9 | 1066.878
1595 | 0.16505 | 47.96 | 62.412 | 0.00054629 | 16.032 | 1082.9 |  | 1595 | 47.96 | 0.16505 | 62.412 | 0.00054629 | 16.032 | 1082.9 | 1066.868
1596 | 0.16511 | 47.97 | 62.412 | 0.00054649 | 16.042 | 1082.9 |  | 1596 | 47.97 | 0.16511 | 62.412 | 0.00054649 | 16.042 | 1082.9 | 1066.858
1597 | 0.16518 | 47.98 | 62.412 | 0.00054668 | 16.052 | 1082.9 |  | 1597 | 47.98 | 0.16518 | 62.412 | 0.00054668 | 16.052 | 1082.9 | 1066.848
1598 | 0.16524 | 47.99 | 62.412 | 0.00054688 | 16.062 | 1082.9 |  | 1598 | 47.99 | 0.16524 | 62.412 | 0.00054688 | 16.062 | 1082.9 | 1066.838
1599 | 0.1653 | 48 | 62.412 | 0.00054707 | 16.072 | 1082.9 |  | 1599 | 48 | 0.1653 | 62.412 | 0.00054707 | 16.072 | 1082.9 | 1066.828
1600 | 0.16536 | 48.01 | 62.412 | 0.00054727 | 16.082 | 1082.9 |  | 1600 | 48.01 | 0.16536 | 62.412 | 0.00054727 | 16.082 | 1082.9 | 1066.818
1601 | 0.16542 | 48.02 | 62.412 | 0.00054746 | 16.092 | 1082.9 |  | 1601 | 48.02 | 0.16542 | 62.412 | 0.00054746 | 16.092 | 1082.9 | 1066.808
1602 | 0.16549 | 48.03 | 62.412 | 0.00054766 | 16.102 | 1082.9 |  | 1602 | 48.03 | 0.16549 | 62.412 | 0.00054766 | 16.102 | 1082.9 | 1066.798
1603 | 0.16555 | 48.04 | 62.412 | 0.00054785 | 16.112 | 1082.9 |  | 1603 | 48.04 | 0.16555 | 62.412 | 0.00054785 | 16.112 | 1082.9 | 1066.788
1604 | 0.16561 | 48.05 | 62.412 | 0.00054805 | 16.122 | 1082.9 |  | 1604 | 48.05 | 0.16561 | 62.412 | 0.00054805 | 16.122 | 1082.9 | 1066.778
1605 | 0.16567 | 48.06 | 62.412 | 0.00054824 | 16.132 | 1082.9 |  | 1605 | 48.06 | 0.16567 | 62.412 | 0.00054824 | 16.132 | 1082.9 | 1066.768
1606 | 0.16573 | 48.07 | 62.412 | 0.00054844 | 16.142 | 1082.9 |  | 1606 | 48.07 | 0.16573 | 62.412 | 0.00054844 | 16.142 | 1082.9 | 1066.758
1607 | 0.1658 | 48.08 | 62.412 | 0.00054863 | 16.152 | 1083 |  | 1607 | 48.08 | 0.1658 | 62.412 | 0.00054863 | 16.152 | 1083 | 1066.848
1608 | 0.16586 | 48.09 | 62.412 | 0.00054883 | 16.162 | 1083 |  | 1608 | 48.09 | 0.16586 | 62.412 | 0.00054883 | 16.162 | 1083 | 1066.838
1609 | 0.16592 | 48.1 | 62.412 | 0.00054902 | 16.172 | 1083 |  | 1609 | 48.1 | 0.16592 | 62.412 | 0.00054902 | 16.172 | 1083 | 1066.828
1610 | 0.16598 | 48.11 | 62.412 | 0.00054922 | 16.182 | 1083 |  | 1610 | 48.11 | 0.16598 | 62.412 | 0.00054922 | 16.182 | 1083 | 1066.818
1611 | 0.16605 | 48.12 | 62.412 | 0.00054941 | 16.192 | 1083 |  | 1611 | 48.12 | 0.16605 | 62.412 | 0.00054941 | 16.192 | 1083 | 1066.808
1612 | 0.16611 | 48.13 | 62.412 | 0.00054961 | 16.202 | 1083 |  | 1612 | 48.13 | 0.16611 | 62.412 | 0.00054961 | 16.202 | 1083 | 1066.798
1613 | 0.16617 | 48.14 | 62.412 | 0.0005498 | 16.212 | 1083 |  | 1613 | 48.14 | 0.16617 | 62.412 | 0.0005498 | 16.212 | 1083 | 1066.788
1614 | 0.16623 | 48.15 | 62.412 | 0.00055 | 16.222 | 1083 |  | 1614 | 48.15 | 0.16623 | 62.412 | 0.00055 | 16.222 | 1083 | 1066.778
1615 | 0.1663 | 48.16 | 62.412 | 0.0005502 | 16.232 | 1083 |  | 1615 | 48.16 | 0.1663 | 62.412 | 0.0005502 | 16.232 | 1083 | 1066.768
1616 | 0.16636 | 48.17 | 62.412 | 0.00055039 | 16.243 | 1083 |  | 1616 | 48.17 | 0.16636 | 62.412 | 0.00055039 | 16.243 | 1083 | 1066.757
1617 | 0.16642 | 48.18 | 62.411 | 0.00055059 | 16.253 | 1083 |  | 1617 | 48.18 | 0.16642 | 62.411 | 0.00055059 | 16.253 | 1083 | 1066.747
1618 | 0.16648 | 48.19 | 62.411 | 0.00055078 | 16.263 | 1083 |  | 1618 | 48.19 | 0.16648 | 62.411 | 0.00055078 | 16.263 | 1083 | 1066.737
1619 | 0.16655 | 48.2 | 62.411 | 0.00055098 | 16.273 | 1083 |  | 1619 | 48.2 | 0.16655 | 62.411 | 0.00055098 | 16.273 | 1083 | 1066.727
1620 | 0.16661 | 48.21 | 62.411 | 0.00055117 | 16.283 | 1083 |  | 1620 | 48.21 | 0.16661 | 62.411 | 0.00055117 | 16.283 | 1083 | 1066.717
1621 | 0.16667 | 48.22 | 62.411 | 0.00055137 | 16.293 | 1083 |  | 1621 | 48.22 | 0.16667 | 62.411 | 0.00055137 | 16.293 | 1083 | 1066.707
1622 | 0.16673 | 48.23 | 62.411 | 0.00055157 | 16.303 | 1083 |  | 1622 | 48.23 | 0.16673 | 62.411 | 0.00055157 | 16.303 | 1083 | 1066.697
1623 | 0.1668 | 48.24 | 62.411 | 0.00055176 | 16.313 | 1083 |  | 1623 | 48.24 | 0.1668 | 62.411 | 0.00055176 | 16.313 | 1083 | 1066.687
1624 | 0.16686 | 48.25 | 62.411 | 0.00055196 | 16.323 | 1083 |  | 1624 | 48.25 | 0.16686 | 62.411 | 0.00055196 | 16.323 | 1083 | 1066.677
1625 | 0.16692 | 48.26 | 62.411 | 0.00055216 | 16.333 | 1083 |  | 1625 | 48.26 | 0.16692 | 62.411 | 0.00055216 | 16.333 | 1083 | 1066.667
1626 | 0.16698 | 48.27 | 62.411 | 0.00055235 | 16.343 | 1083 |  | 1626 | 48.27 | 0.16698 | 62.411 | 0.00055235 | 16.343 | 1083 | 1066.657
1627 | 0.16705 | 48.28 | 62.411 | 0.00055255 | 16.353 | 1083 |  | 1627 | 48.28 | 0.16705 | 62.411 | 0.00055255 | 16.353 | 1083 | 1066.647
1628 | 0.16711 | 48.29 | 62.411 | 0.00055275 | 16.363 | 1083 |  | 1628 | 48.29 | 0.16711 | 62.411 | 0.00055275 | 16.363 | 1083 | 1066.637
1629 | 0.16717 | 48.3 | 62.411 | 0.00055294 | 16.373 | 1083 |  | 1629 | 48.3 | 0.16717 | 62.411 | 0.00055294 | 16.373 | 1083 | 1066.627
1630 | 0.16723 | 48.31 | 62.411 | 0.00055314 | 16.383 | 1083.1 |  | 1630 | 48.31 | 0.16723 | 62.411 | 0.00055314 | 16.383 | 1083.1 | 1066.717
1631 | 0.1673 | 48.32 | 62.411 | 0.00055334 | 16.393 | 1083.1 |  | 1631 | 48.32 | 0.1673 | 62.411 | 0.00055334 | 16.393 | 1083.1 | 1066.707
1632 | 0.16736 | 48.33 | 62.411 | 0.00055353 | 16.403 | 1083.1 |  | 1632 | 48.33 | 0.16736 | 62.411 | 0.00055353 | 16.403 | 1083.1 | 1066.697
1633 | 0.16742 | 48.34 | 62.411 | 0.00055373 | 16.413 | 1083.1 |  | 1633 | 48.34 | 0.16742 | 62.411 | 0.00055373 | 16.413 | 1083.1 | 1066.687
1634 | 0.16748 | 48.35 | 62.411 | 0.00055393 | 16.423 | 1083.1 |  | 1634 | 48.35 | 0.16748 | 62.411 | 0.00055393 | 16.423 | 1083.1 | 1066.677
1635 | 0.16755 | 48.36 | 62.411 | 0.00055412 | 16.433 | 1083.1 |  | 1635 | 48.36 | 0.16755 | 62.411 | 0.00055412 | 16.433 | 1083.1 | 1066.667
1636 | 0.16761 | 48.37 | 62.411 | 0.00055432 | 16.443 | 1083.1 |  | 1636 | 48.37 | 0.16761 | 62.411 | 0.00055432 | 16.443 | 1083.1 | 1066.657
1637 | 0.16767 | 48.38 | 62.411 | 0.00055452 | 16.453 | 1083.1 |  | 1637 | 48.38 | 0.16767 | 62.411 | 0.00055452 | 16.453 | 1083.1 | 1066.647
1638 | 0.16774 | 48.39 | 62.411 | 0.00055471 | 16.463 | 1083.1 |  | 1638 | 48.39 | 0.16774 | 62.411 | 0.00055471 | 16.463 | 1083.1 | 1066.637
1639 | 0.1678 | 48.4 | 62.411 | 0.00055491 | 16.473 | 1083.1 |  | 1639 | 48.4 | 0.1678 | 62.411 | 0.00055491 | 16.473 | 1083.1 | 1066.627
1640 | 0.16786 | 48.41 | 62.411 | 0.00055511 | 16.483 | 1083.1 |  | 1640 | 48.41 | 0.16786 | 62.411 | 0.00055511 | 16.483 | 1083.1 | 1066.617
1641 | 0.16792 | 48.42 | 62.411 | 0.00055531 | 16.493 | 1083.1 |  | 1641 | 48.42 | 0.16792 | 62.411 | 0.00055531 | 16.493 | 1083.1 | 1066.607
1642 | 0.16799 | 48.43 | 62.411 | 0.0005555 | 16.503 | 1083.1 |  | 1642 | 48.43 | 0.16799 | 62.411 | 0.0005555 | 16.503 | 1083.1 | 1066.597
1643 | 0.16805 | 48.44 | 62.411 | 0.0005557 | 16.513 | 1083.1 |  | 1643 | 48.44 | 0.16805 | 62.411 | 0.0005557 | 16.513 | 1083.1 | 1066.587
1644 | 0.16811 | 48.45 | 62.411 | 0.0005559 | 16.523 | 1083.1 |  | 1644 | 48.45 | 0.16811 | 62.411 | 0.0005559 | 16.523 | 1083.1 | 1066.577
1645 | 0.16818 | 48.46 | 62.411 | 0.0005561 | 16.533 | 1083.1 |  | 1645 | 48.46 | 0.16818 | 62.411 | 0.0005561 | 16.533 | 1083.1 | 1066.567
1646 | 0.16824 | 48.47 | 62.411 | 0.00055629 | 16.543 | 1083.1 |  | 1646 | 48.47 | 0.16824 | 62.411 | 0.00055629 | 16.543 | 1083.1 | 1066.557
1647 | 0.1683 | 48.48 | 62.411 | 0.00055649 | 16.554 | 1083.1 |  | 1647 | 48.48 | 0.1683 | 62.411 | 0.00055649 | 16.554 | 1083.1 | 1066.546
1648 | 0.16837 | 48.49 | 62.411 | 0.00055669 | 16.564 | 1083.1 |  | 1648 | 48.49 | 0.16837 | 62.411 | 0.00055669 | 16.564 | 1083.1 | 1066.536
1649 | 0.16843 | 48.5 | 62.411 | 0.00055689 | 16.574 | 1083.1 |  | 1649 | 48.5 | 0.16843 | 62.411 | 0.00055689 | 16.574 | 1083.1 | 1066.526
1650 | 0.16849 | 48.51 | 62.411 | 0.00055708 | 16.584 | 1083.1 |  | 1650 | 48.51 | 0.16849 | 62.411 | 0.00055708 | 16.584 | 1083.1 | 1066.516
1651 | 0.16856 | 48.52 | 62.411 | 0.00055728 | 16.594 | 1083.1 |  | 1651 | 48.52 | 0.16856 | 62.411 | 0.00055728 | 16.594 | 1083.1 | 1066.506
1652 | 0.16862 | 48.53 | 62.411 | 0.00055748 | 16.604 | 1083.1 |  | 1652 | 48.53 | 0.16862 | 62.411 | 0.00055748 | 16.604 | 1083.1 | 1066.496
1653 | 0.16868 | 48.54 | 62.411 | 0.00055768 | 16.614 | 1083.2 |  | 1653 | 48.54 | 0.16868 | 62.411 | 0.00055768 | 16.614 | 1083.2 | 1066.586
1654 | 0.16875 | 48.55 | 62.411 | 0.00055788 | 16.624 | 1083.2 |  | 1654 | 48.55 | 0.16875 | 62.411 | 0.00055788 | 16.624 | 1083.2 | 1066.576
1655 | 0.16881 | 48.56 | 62.411 | 0.00055808 | 16.634 | 1083.2 |  | 1655 | 48.56 | 0.16881 | 62.411 | 0.00055808 | 16.634 | 1083.2 | 1066.566
1656 | 0.16887 | 48.57 | 62.41 | 0.00055827 | 16.644 | 1083.2 |  | 1656 | 48.57 | 0.16887 | 62.41 | 0.00055827 | 16.644 | 1083.2 | 1066.556
1657 | 0.16893 | 48.58 | 62.41 | 0.00055847 | 16.654 | 1083.2 |  | 1657 | 48.58 | 0.16893 | 62.41 | 0.00055847 | 16.654 | 1083.2 | 1066.546
1658 | 0.169 | 48.59 | 62.41 | 0.00055867 | 16.664 | 1083.2 |  | 1658 | 48.59 | 0.169 | 62.41 | 0.00055867 | 16.664 | 1083.2 | 1066.536
1659 | 0.16906 | 48.6 | 62.41 | 0.00055887 | 16.674 | 1083.2 |  | 1659 | 48.6 | 0.16906 | 62.41 | 0.00055887 | 16.674 | 1083.2 | 1066.526
1660 | 0.16912 | 48.61 | 62.41 | 0.00055907 | 16.684 | 1083.2 |  | 1660 | 48.61 | 0.16912 | 62.41 | 0.00055907 | 16.684 | 1083.2 | 1066.516
1661 | 0.16919 | 48.62 | 62.41 | 0.00055927 | 16.694 | 1083.2 |  | 1661 | 48.62 | 0.16919 | 62.41 | 0.00055927 | 16.694 | 1083.2 | 1066.506
1662 | 0.16925 | 48.63 | 62.41 | 0.00055946 | 16.704 | 1083.2 |  | 1662 | 48.63 | 0.16925 | 62.41 | 0.00055946 | 16.704 | 1083.2 | 1066.496
1663 | 0.16932 | 48.64 | 62.41 | 0.00055966 | 16.714 | 1083.2 |  | 1663 | 48.64 | 0.16932 | 62.41 | 0.00055966 | 16.714 | 1083.2 | 1066.486
1664 | 0.16938 | 48.65 | 62.41 | 0.00055986 | 16.724 | 1083.2 |  | 1664 | 48.65 | 0.16938 | 62.41 | 0.00055986 | 16.724 | 1083.2 | 1066.476
1665 | 0.16944 | 48.66 | 62.41 | 0.00056006 | 16.734 | 1083.2 |  | 1665 | 48.66 | 0.16944 | 62.41 | 0.00056006 | 16.734 | 1083.2 | 1066.466
1666 | 0.16951 | 48.67 | 62.41 | 0.00056026 | 16.744 | 1083.2 |  | 1666 | 48.67 | 0.16951 | 62.41 | 0.00056026 | 16.744 | 1083.2 | 1066.456
1667 | 0.16957 | 48.68 | 62.41 | 0.00056046 | 16.754 | 1083.2 |  | 1667 | 48.68 | 0.16957 | 62.41 | 0.00056046 | 16.754 | 1083.2 | 1066.446
1668 | 0.16963 | 48.69 | 62.41 | 0.00056066 | 16.764 | 1083.2 |  | 1668 | 48.69 | 0.16963 | 62.41 | 0.00056066 | 16.764 | 1083.2 | 1066.436
1669 | 0.1697 | 48.7 | 62.41 | 0.00056086 | 16.774 | 1083.2 |  | 1669 | 48.7 | 0.1697 | 62.41 | 0.00056086 | 16.774 | 1083.2 | 1066.426
1670 | 0.16976 | 48.71 | 62.41 | 0.00056106 | 16.784 | 1083.2 |  | 1670 | 48.71 | 0.16976 | 62.41 | 0.00056106 | 16.784 | 1083.2 | 1066.416
1671 | 0.16982 | 48.72 | 62.41 | 0.00056125 | 16.794 | 1083.2 |  | 1671 | 48.72 | 0.16982 | 62.41 | 0.00056125 | 16.794 | 1083.2 | 1066.406
1672 | 0.16989 | 48.73 | 62.41 | 0.00056145 | 16.804 | 1083.2 |  | 1672 | 48.73 | 0.16989 | 62.41 | 0.00056145 | 16.804 | 1083.2 | 1066.396
1673 | 0.16995 | 48.74 | 62.41 | 0.00056165 | 16.814 | 1083.2 |  | 1673 | 48.74 | 0.16995 | 62.41 | 0.00056165 | 16.814 | 1083.2 | 1066.386
1674 | 0.17001 | 48.75 | 62.41 | 0.00056185 | 16.824 | 1083.2 |  | 1674 | 48.75 | 0.17001 | 62.41 | 0.00056185 | 16.824 | 1083.2 | 1066.376
1675 | 0.17008 | 48.76 | 62.41 | 0.00056205 | 16.834 | 1083.2 |  | 1675 | 48.76 | 0.17008 | 62.41 | 0.00056205 | 16.834 | 1083.2 | 1066.366
1676 | 0.17014 | 48.77 | 62.41 | 0.00056225 | 16.844 | 1083.3 |  | 1676 | 48.77 | 0.17014 | 62.41 | 0.00056225 | 16.844 | 1083.3 | 1066.456
1677 | 0.1702 | 48.78 | 62.41 | 0.00056245 | 16.854 | 1083.3 |  | 1677 | 48.78 | 0.1702 | 62.41 | 0.00056245 | 16.854 | 1083.3 | 1066.446
1678 | 0.17027 | 48.79 | 62.41 | 0.00056265 | 16.864 | 1083.3 |  | 1678 | 48.79 | 0.17027 | 62.41 | 0.00056265 | 16.864 | 1083.3 | 1066.436
1679 | 0.17033 | 48.8 | 62.41 | 0.00056285 | 16.874 | 1083.3 |  | 1679 | 48.8 | 0.17033 | 62.41 | 0.00056285 | 16.874 | 1083.3 | 1066.426
1680 | 0.1704 | 48.81 | 62.41 | 0.00056305 | 16.885 | 1083.3 |  | 1680 | 48.81 | 0.1704 | 62.41 | 0.00056305 | 16.885 | 1083.3 | 1066.415
1681 | 0.17046 | 48.82 | 62.41 | 0.00056325 | 16.895 | 1083.3 |  | 1681 | 48.82 | 0.17046 | 62.41 | 0.00056325 | 16.895 | 1083.3 | 1066.405
1682 | 0.17052 | 48.83 | 62.41 | 0.00056345 | 16.905 | 1083.3 |  | 1682 | 48.83 | 0.17052 | 62.41 | 0.00056345 | 16.905 | 1083.3 | 1066.395
1683 | 0.17059 | 48.84 | 62.41 | 0.00056365 | 16.915 | 1083.3 |  | 1683 | 48.84 | 0.17059 | 62.41 | 0.00056365 | 16.915 | 1083.3 | 1066.385
1684 | 0.17065 | 48.85 | 62.41 | 0.00056385 | 16.925 | 1083.3 |  | 1684 | 48.85 | 0.17065 | 62.41 | 0.00056385 | 16.925 | 1083.3 | 1066.375
1685 | 0.17072 | 48.86 | 62.41 | 0.00056405 | 16.935 | 1083.3 |  | 1685 | 48.86 | 0.17072 | 62.41 | 0.00056405 | 16.935 | 1083.3 | 1066.365
1686 | 0.17078 | 48.87 | 62.41 | 0.00056425 | 16.945 | 1083.3 |  | 1686 | 48.87 | 0.17078 | 62.41 | 0.00056425 | 16.945 | 1083.3 | 1066.355
1687 | 0.17084 | 48.88 | 62.41 | 0.00056445 | 16.955 | 1083.3 |  | 1687 | 48.88 | 0.17084 | 62.41 | 0.00056445 | 16.955 | 1083.3 | 1066.345
1688 | 0.17091 | 48.89 | 62.41 | 0.00056465 | 16.965 | 1083.3 |  | 1688 | 48.89 | 0.17091 | 62.41 | 0.00056465 | 16.965 | 1083.3 | 1066.335
1689 | 0.17097 | 48.9 | 62.41 | 0.00056485 | 16.975 | 1083.3 |  | 1689 | 48.9 | 0.17097 | 62.41 | 0.00056485 | 16.975 | 1083.3 | 1066.325
1690 | 0.17103 | 48.91 | 62.41 | 0.00056505 | 16.985 | 1083.3 |  | 1690 | 48.91 | 0.17103 | 62.41 | 0.00056505 | 16.985 | 1083.3 | 1066.315
1691 | 0.1711 | 48.92 | 62.41 | 0.00056525 | 16.995 | 1083.3 |  | 1691 | 48.92 | 0.1711 | 62.41 | 0.00056525 | 16.995 | 1083.3 | 1066.305
1692 | 0.17116 | 48.93 | 62.41 | 0.00056545 | 17.005 | 1083.3 |  | 1692 | 48.93 | 0.17116 | 62.41 | 0.00056545 | 17.005 | 1083.3 | 1066.295
1693 | 0.17123 | 48.94 | 62.409 | 0.00056565 | 17.015 | 1083.3 |  | 1693 | 48.94 | 0.17123 | 62.409 | 0.00056565 | 17.015 | 1083.3 | 1066.285
1694 | 0.17129 | 48.95 | 62.409 | 0.00056585 | 17.025 | 1083.3 |  | 1694 | 48.95 | 0.17129 | 62.409 | 0.00056585 | 17.025 | 1083.3 | 1066.275
1695 | 0.17135 | 48.96 | 62.409 | 0.00056605 | 17.035 | 1083.3 |  | 1695 | 48.96 | 0.17135 | 62.409 | 0.00056605 | 17.035 | 1083.3 | 1066.265
1696 | 0.17142 | 48.97 | 62.409 | 0.00056625 | 17.045 | 1083.3 |  | 1696 | 48.97 | 0.17142 | 62.409 | 0.00056625 | 17.045 | 1083.3 | 1066.255
1697 | 0.17148 | 48.98 | 62.409 | 0.00056645 | 17.055 | 1083.3 |  | 1697 | 48.98 | 0.17148 | 62.409 | 0.00056645 | 17.055 | 1083.3 | 1066.245
1698 | 0.17155 | 48.99 | 62.409 | 0.00056666 | 17.065 | 1083.3 |  | 1698 | 48.99 | 0.17155 | 62.409 | 0.00056666 | 17.065 | 1083.3 | 1066.235
1699 | 0.17161 | 49 | 62.409 | 0.00056686 | 17.075 | 1083.4 |  | 1699 | 49 | 0.17161 | 62.409 | 0.00056686 | 17.075 | 1083.4 | 1066.325
1700 | 0.17168 | 49.01 | 62.409 | 0.00056706 | 17.085 | 1083.4 |  | 1700 | 49.01 | 0.17168 | 62.409 | 0.00056706 | 17.085 | 1083.4 | 1066.315
1701 | 0.17174 | 49.02 | 62.409 | 0.00056726 | 17.095 | 1083.4 |  | 1701 | 49.02 | 0.17174 | 62.409 | 0.00056726 | 17.095 | 1083.4 | 1066.305
1702 | 0.1718 | 49.03 | 62.409 | 0.00056746 | 17.105 | 1083.4 |  | 1702 | 49.03 | 0.1718 | 62.409 | 0.00056746 | 17.105 | 1083.4 | 1066.295
1703 | 0.17187 | 49.04 | 62.409 | 0.00056766 | 17.115 | 1083.4 |  | 1703 | 49.04 | 0.17187 | 62.409 | 0.00056766 | 17.115 | 1083.4 | 1066.285
1704 | 0.17193 | 49.05 | 62.409 | 0.00056786 | 17.125 | 1083.4 |  | 1704 | 49.05 | 0.17193 | 62.409 | 0.00056786 | 17.125 | 1083.4 | 1066.275
1705 | 0.172 | 49.06 | 62.409 | 0.00056806 | 17.135 | 1083.4 |  | 1705 | 49.06 | 0.172 | 62.409 | 0.00056806 | 17.135 | 1083.4 | 1066.265
1706 | 0.17206 | 49.07 | 62.409 | 0.00056826 | 17.145 | 1083.4 |  | 1706 | 49.07 | 0.17206 | 62.409 | 0.00056826 | 17.145 | 1083.4 | 1066.255
1707 | 0.17213 | 49.08 | 62.409 | 0.00056847 | 17.155 | 1083.4 |  | 1707 | 49.08 | 0.17213 | 62.409 | 0.00056847 | 17.155 | 1083.4 | 1066.245
1708 | 0.17219 | 49.09 | 62.409 | 0.00056867 | 17.165 | 1083.4 |  | 1708 | 49.09 | 0.17219 | 62.409 | 0.00056867 | 17.165 | 1083.4 | 1066.235
1709 | 0.17225 | 49.1 | 62.409 | 0.00056887 | 17.175 | 1083.4 |  | 1709 | 49.1 | 0.17225 | 62.409 | 0.00056887 | 17.175 | 1083.4 | 1066.225
1710 | 0.17232 | 49.11 | 62.409 | 0.00056907 | 17.185 | 1083.4 |  | 1710 | 49.11 | 0.17232 | 62.409 | 0.00056907 | 17.185 | 1083.4 | 1066.215
1711 | 0.17238 | 49.12 | 62.409 | 0.00056927 | 17.195 | 1083.4 |  | 1711 | 49.12 | 0.17238 | 62.409 | 0.00056927 | 17.195 | 1083.4 | 1066.205
1712 | 0.17245 | 49.13 | 62.409 | 0.00056947 | 17.205 | 1083.4 |  | 1712 | 49.13 | 0.17245 | 62.409 | 0.00056947 | 17.205 | 1083.4 | 1066.195
1713 | 0.17251 | 49.14 | 62.409 | 0.00056968 | 17.216 | 1083.4 |  | 1713 | 49.14 | 0.17251 | 62.409 | 0.00056968 | 17.216 | 1083.4 | 1066.184
1714 | 0.17258 | 49.15 | 62.409 | 0.00056988 | 17.226 | 1083.4 |  | 1714 | 49.15 | 0.17258 | 62.409 | 0.00056988 | 17.226 | 1083.4 | 1066.174
1715 | 0.17264 | 49.16 | 62.409 | 0.00057008 | 17.236 | 1083.4 |  | 1715 | 49.16 | 0.17264 | 62.409 | 0.00057008 | 17.236 | 1083.4 | 1066.164
1716 | 0.17271 | 49.17 | 62.409 | 0.00057028 | 17.246 | 1083.4 |  | 1716 | 49.17 | 0.17271 | 62.409 | 0.00057028 | 17.246 | 1083.4 | 1066.154
1717 | 0.17277 | 49.18 | 62.409 | 0.00057048 | 17.256 | 1083.4 |  | 1717 | 49.18 | 0.17277 | 62.409 | 0.00057048 | 17.256 | 1083.4 | 1066.144
1718 | 0.17283 | 49.19 | 62.409 | 0.00057069 | 17.266 | 1083.4 |  | 1718 | 49.19 | 0.17283 | 62.409 | 0.00057069 | 17.266 | 1083.4 | 1066.134
1719 | 0.1729 | 49.2 | 62.409 | 0.00057089 | 17.276 | 1083.4 |  | 1719 | 49.2 | 0.1729 | 62.409 | 0.00057089 | 17.276 | 1083.4 | 1066.124
1720 | 0.17296 | 49.21 | 62.409 | 0.00057109 | 17.286 | 1083.4 |  | 1720 | 49.21 | 0.17296 | 62.409 | 0.00057109 | 17.286 | 1083.4 | 1066.114
1721 | 0.17303 | 49.22 | 62.409 | 0.00057129 | 17.296 | 1083.4 |  | 1721 | 49.22 | 0.17303 | 62.409 | 0.00057129 | 17.296 | 1083.4 | 1066.104
1722 | 0.17309 | 49.23 | 62.409 | 0.00057149 | 17.306 | 1083.5 |  | 1722 | 49.23 | 0.17309 | 62.409 | 0.00057149 | 17.306 | 1083.5 | 1066.194
1723 | 0.17316 | 49.24 | 62.409 | 0.0005717 | 17.316 | 1083.5 |  | 1723 | 49.24 | 0.17316 | 62.409 | 0.0005717 | 17.316 | 1083.5 | 1066.184
1724 | 0.17322 | 49.25 | 62.409 | 0.0005719 | 17.326 | 1083.5 |  | 1724 | 49.25 | 0.17322 | 62.409 | 0.0005719 | 17.326 | 1083.5 | 1066.174
1725 | 0.17329 | 49.26 | 62.409 | 0.0005721 | 17.336 | 1083.5 |  | 1725 | 49.26 | 0.17329 | 62.409 | 0.0005721 | 17.336 | 1083.5 | 1066.164
1726 | 0.17335 | 49.27 | 62.409 | 0.0005723 | 17.346 | 1083.5 |  | 1726 | 49.27 | 0.17335 | 62.409 | 0.0005723 | 17.346 | 1083.5 | 1066.154
1727 | 0.17342 | 49.28 | 62.409 | 0.00057251 | 17.356 | 1083.5 |  | 1727 | 49.28 | 0.17342 | 62.409 | 0.00057251 | 17.356 | 1083.5 | 1066.144
1728 | 0.17348 | 49.29 | 62.408 | 0.00057271 | 17.366 | 1083.5 |  | 1728 | 49.29 | 0.17348 | 62.408 | 0.00057271 | 17.366 | 1083.5 | 1066.134
1729 | 0.17355 | 49.3 | 62.408 | 0.00057291 | 17.376 | 1083.5 |  | 1729 | 49.3 | 0.17355 | 62.408 | 0.00057291 | 17.376 | 1083.5 | 1066.124
1730 | 0.17361 | 49.31 | 62.408 | 0.00057312 | 17.386 | 1083.5 |  | 1730 | 49.31 | 0.17361 | 62.408 | 0.00057312 | 17.386 | 1083.5 | 1066.114
1731 | 0.17368 | 49.32 | 62.408 | 0.00057332 | 17.396 | 1083.5 |  | 1731 | 49.32 | 0.17368 | 62.408 | 0.00057332 | 17.396 | 1083.5 | 1066.104
1732 | 0.17374 | 49.33 | 62.408 | 0.00057352 | 17.406 | 1083.5 |  | 1732 | 49.33 | 0.17374 | 62.408 | 0.00057352 | 17.406 | 1083.5 | 1066.094
1733 | 0.17381 | 49.34 | 62.408 | 0.00057372 | 17.416 | 1083.5 |  | 1733 | 49.34 | 0.17381 | 62.408 | 0.00057372 | 17.416 | 1083.5 | 1066.084
1734 | 0.17387 | 49.35 | 62.408 | 0.00057393 | 17.426 | 1083.5 |  | 1734 | 49.35 | 0.17387 | 62.408 | 0.00057393 | 17.426 | 1083.5 | 1066.074
1735 | 0.17394 | 49.36 | 62.408 | 0.00057413 | 17.436 | 1083.5 |  | 1735 | 49.36 | 0.17394 | 62.408 | 0.00057413 | 17.436 | 1083.5 | 1066.064
1736 | 0.174 | 49.37 | 62.408 | 0.00057433 | 17.446 | 1083.5 |  | 1736 | 49.37 | 0.174 | 62.408 | 0.00057433 | 17.446 | 1083.5 | 1066.054
1737 | 0.17407 | 49.38 | 62.408 | 0.00057454 | 17.456 | 1083.5 |  | 1737 | 49.38 | 0.17407 | 62.408 | 0.00057454 | 17.456 | 1083.5 | 1066.044
1738 | 0.17413 | 49.39 | 62.408 | 0.00057474 | 17.466 | 1083.5 |  | 1738 | 49.39 | 0.17413 | 62.408 | 0.00057474 | 17.466 | 1083.5 | 1066.034
1739 | 0.1742 | 49.4 | 62.408 | 0.00057494 | 17.476 | 1083.5 |  | 1739 | 49.4 | 0.1742 | 62.408 | 0.00057494 | 17.476 | 1083.5 | 1066.024
1740 | 0.17426 | 49.41 | 62.408 | 0.00057515 | 17.486 | 1083.5 |  | 1740 | 49.41 | 0.17426 | 62.408 | 0.00057515 | 17.486 | 1083.5 | 1066.014
1741 | 0.17433 | 49.42 | 62.408 | 0.00057535 | 17.496 | 1083.5 |  | 1741 | 49.42 | 0.17433 | 62.408 | 0.00057535 | 17.496 | 1083.5 | 1066.004
1742 | 0.17439 | 49.43 | 62.408 | 0.00057555 | 17.506 | 1083.5 |  | 1742 | 49.43 | 0.17439 | 62.408 | 0.00057555 | 17.506 | 1083.5 | 1065.994
1743 | 0.17446 | 49.44 | 62.408 | 0.00057576 | 17.516 | 1083.5 |  | 1743 | 49.44 | 0.17446 | 62.408 | 0.00057576 | 17.516 | 1083.5 | 1065.984
1744 | 0.17452 | 49.45 | 62.408 | 0.00057596 | 17.526 | 1083.5 |  | 1744 | 49.45 | 0.17452 | 62.408 | 0.00057596 | 17.526 | 1083.5 | 1065.974
1745 | 0.17459 | 49.46 | 62.408 | 0.00057617 | 17.536 | 1083.6 |  | 1745 | 49.46 | 0.17459 | 62.408 | 0.00057617 | 17.536 | 1083.6 | 1066.064
1746 | 0.17465 | 49.47 | 62.408 | 0.00057637 | 17.546 | 1083.6 |  | 1746 | 49.47 | 0.17465 | 62.408 | 0.00057637 | 17.546 | 1083.6 | 1066.054
1747 | 0.17472 | 49.48 | 62.408 | 0.00057657 | 17.557 | 1083.6 |  | 1747 | 49.48 | 0.17472 | 62.408 | 0.00057657 | 17.557 | 1083.6 | 1066.043
1748 | 0.17478 | 49.49 | 62.408 | 0.00057678 | 17.567 | 1083.6 |  | 1748 | 49.49 | 0.17478 | 62.408 | 0.00057678 | 17.567 | 1083.6 | 1066.033
1749 | 0.17485 | 49.5 | 62.408 | 0.00057698 | 17.577 | 1083.6 |  | 1749 | 49.5 | 0.17485 | 62.408 | 0.00057698 | 17.577 | 1083.6 | 1066.023
1750 | 0.17491 | 49.51 | 62.408 | 0.00057719 | 17.587 | 1083.6 |  | 1750 | 49.51 | 0.17491 | 62.408 | 0.00057719 | 17.587 | 1083.6 | 1066.013
1751 | 0.17498 | 49.52 | 62.408 | 0.00057739 | 17.597 | 1083.6 |  | 1751 | 49.52 | 0.17498 | 62.408 | 0.00057739 | 17.597 | 1083.6 | 1066.003
1752 | 0.17504 | 49.53 | 62.408 | 0.00057759 | 17.607 | 1083.6 |  | 1752 | 49.53 | 0.17504 | 62.408 | 0.00057759 | 17.607 | 1083.6 | 1065.993
1753 | 0.17511 | 49.54 | 62.408 | 0.0005778 | 17.617 | 1083.6 |  | 1753 | 49.54 | 0.17511 | 62.408 | 0.0005778 | 17.617 | 1083.6 | 1065.983
1754 | 0.17517 | 49.55 | 62.408 | 0.000578 | 17.627 | 1083.6 |  | 1754 | 49.55 | 0.17517 | 62.408 | 0.000578 | 17.627 | 1083.6 | 1065.973
1755 | 0.17524 | 49.56 | 62.408 | 0.00057821 | 17.637 | 1083.6 |  | 1755 | 49.56 | 0.17524 | 62.408 | 0.00057821 | 17.637 | 1083.6 | 1065.963
1756 | 0.1753 | 49.57 | 62.408 | 0.00057841 | 17.647 | 1083.6 |  | 1756 | 49.57 | 0.1753 | 62.408 | 0.00057841 | 17.647 | 1083.6 | 1065.953
1757 | 0.17537 | 49.58 | 62.408 | 0.00057862 | 17.657 | 1083.6 |  | 1757 | 49.58 | 0.17537 | 62.408 | 0.00057862 | 17.657 | 1083.6 | 1065.943
1758 | 0.17543 | 49.59 | 62.408 | 0.00057882 | 17.667 | 1083.6 |  | 1758 | 49.59 | 0.17543 | 62.408 | 0.00057882 | 17.667 | 1083.6 | 1065.933
1759 | 0.1755 | 49.6 | 62.408 | 0.00057902 | 17.677 | 1083.6 |  | 1759 | 49.6 | 0.1755 | 62.408 | 0.00057902 | 17.677 | 1083.6 | 1065.923
1760 | 0.17557 | 49.61 | 62.408 | 0.00057923 | 17.687 | 1083.6 |  | 1760 | 49.61 | 0.17557 | 62.408 | 0.00057923 | 17.687 | 1083.6 | 1065.913
1761 | 0.17563 | 49.62 | 62.408 | 0.00057943 | 17.697 | 1083.6 |  | 1761 | 49.62 | 0.17563 | 62.408 | 0.00057943 | 17.697 | 1083.6 | 1065.903
1762 | 0.1757 | 49.63 | 62.408 | 0.00057964 | 17.707 | 1083.6 |  | 1762 | 49.63 | 0.1757 | 62.408 | 0.00057964 | 17.707 | 1083.6 | 1065.893
1763 | 0.17576 | 49.64 | 62.407 | 0.00057984 | 17.717 | 1083.6 |  | 1763 | 49.64 | 0.17576 | 62.407 | 0.00057984 | 17.717 | 1083.6 | 1065.883
1764 | 0.17583 | 49.65 | 62.407 | 0.00058005 | 17.727 | 1083.6 |  | 1764 | 49.65 | 0.17583 | 62.407 | 0.00058005 | 17.727 | 1083.6 | 1065.873
1765 | 0.17589 | 49.66 | 62.407 | 0.00058025 | 17.737 | 1083.6 |  | 1765 | 49.66 | 0.17589 | 62.407 | 0.00058025 | 17.737 | 1083.6 | 1065.863
1766 | 0.17596 | 49.67 | 62.407 | 0.00058046 | 17.747 | 1083.6 |  | 1766 | 49.67 | 0.17596 | 62.407 | 0.00058046 | 17.747 | 1083.6 | 1065.853
1767 | 0.17602 | 49.68 | 62.407 | 0.00058066 | 17.757 | 1083.6 |  | 1767 | 49.68 | 0.17602 | 62.407 | 0.00058066 | 17.757 | 1083.6 | 1065.843
1768 | 0.17609 | 49.69 | 62.407 | 0.00058087 | 17.767 | 1083.7 |  | 1768 | 49.69 | 0.17609 | 62.407 | 0.00058087 | 17.767 | 1083.7 | 1065.933
1769 | 0.17616 | 49.7 | 62.407 | 0.00058107 | 17.777 | 1083.7 |  | 1769 | 49.7 | 0.17616 | 62.407 | 0.00058107 | 17.777 | 1083.7 | 1065.923
1770 | 0.17622 | 49.71 | 62.407 | 0.00058128 | 17.787 | 1083.7 |  | 1770 | 49.71 | 0.17622 | 62.407 | 0.00058128 | 17.787 | 1083.7 | 1065.913
1771 | 0.17629 | 49.72 | 62.407 | 0.00058149 | 17.797 | 1083.7 |  | 1771 | 49.72 | 0.17629 | 62.407 | 0.00058149 | 17.797 | 1083.7 | 1065.903
1772 | 0.17635 | 49.73 | 62.407 | 0.00058169 | 17.807 | 1083.7 |  | 1772 | 49.73 | 0.17635 | 62.407 | 0.00058169 | 17.807 | 1083.7 | 1065.893
1773 | 0.17642 | 49.74 | 62.407 | 0.0005819 | 17.817 | 1083.7 |  | 1773 | 49.74 | 0.17642 | 62.407 | 0.0005819 | 17.817 | 1083.7 | 1065.883
1774 | 0.17648 | 49.75 | 62.407 | 0.0005821 | 17.827 | 1083.7 |  | 1774 | 49.75 | 0.17648 | 62.407 | 0.0005821 | 17.827 | 1083.7 | 1065.873
1775 | 0.17655 | 49.76 | 62.407 | 0.00058231 | 17.837 | 1083.7 |  | 1775 | 49.76 | 0.17655 | 62.407 | 0.00058231 | 17.837 | 1083.7 | 1065.863
1776 | 0.17662 | 49.77 | 62.407 | 0.00058251 | 17.847 | 1083.7 |  | 1776 | 49.77 | 0.17662 | 62.407 | 0.00058251 | 17.847 | 1083.7 | 1065.853
1777 | 0.17668 | 49.78 | 62.407 | 0.00058272 | 17.857 | 1083.7 |  | 1777 | 49.78 | 0.17668 | 62.407 | 0.00058272 | 17.857 | 1083.7 | 1065.843
1778 | 0.17675 | 49.79 | 62.407 | 0.00058293 | 17.867 | 1083.7 |  | 1778 | 49.79 | 0.17675 | 62.407 | 0.00058293 | 17.867 | 1083.7 | 1065.833
1779 | 0.17681 | 49.8 | 62.407 | 0.00058313 | 17.877 | 1083.7 |  | 1779 | 49.8 | 0.17681 | 62.407 | 0.00058313 | 17.877 | 1083.7 | 1065.823
1780 | 0.17688 | 49.81 | 62.407 | 0.00058334 | 17.887 | 1083.7 |  | 1780 | 49.81 | 0.17688 | 62.407 | 0.00058334 | 17.887 | 1083.7 | 1065.813
1781 | 0.17695 | 49.82 | 62.407 | 0.00058354 | 17.897 | 1083.7 |  | 1781 | 49.82 | 0.17695 | 62.407 | 0.00058354 | 17.897 | 1083.7 | 1065.803
1782 | 0.17701 | 49.83 | 62.407 | 0.00058375 | 17.908 | 1083.7 |  | 1782 | 49.83 | 0.17701 | 62.407 | 0.00058375 | 17.908 | 1083.7 | 1065.792
1783 | 0.17708 | 49.84 | 62.407 | 0.00058396 | 17.918 | 1083.7 |  | 1783 | 49.84 | 0.17708 | 62.407 | 0.00058396 | 17.918 | 1083.7 | 1065.782
1784 | 0.17714 | 49.85 | 62.407 | 0.00058416 | 17.928 | 1083.7 |  | 1784 | 49.85 | 0.17714 | 62.407 | 0.00058416 | 17.928 | 1083.7 | 1065.772
1785 | 0.17721 | 49.86 | 62.407 | 0.00058437 | 17.938 | 1083.7 |  | 1785 | 49.86 | 0.17721 | 62.407 | 0.00058437 | 17.938 | 1083.7 | 1065.762
1786 | 0.17727 | 49.87 | 62.407 | 0.00058457 | 17.948 | 1083.7 |  | 1786 | 49.87 | 0.17727 | 62.407 | 0.00058457 | 17.948 | 1083.7 | 1065.752
1787 | 0.17734 | 49.88 | 62.407 | 0.00058478 | 17.958 | 1083.7 |  | 1787 | 49.88 | 0.17734 | 62.407 | 0.00058478 | 17.958 | 1083.7 | 1065.742
1788 | 0.17741 | 49.89 | 62.407 | 0.00058499 | 17.968 | 1083.7 |  | 1788 | 49.89 | 0.17741 | 62.407 | 0.00058499 | 17.968 | 1083.7 | 1065.732
1789 | 0.17747 | 49.9 | 62.407 | 0.00058519 | 17.978 | 1083.7 |  | 1789 | 49.9 | 0.17747 | 62.407 | 0.00058519 | 17.978 | 1083.7 | 1065.722
1790 | 0.17754 | 49.91 | 62.407 | 0.0005854 | 17.988 | 1083.8 |  | 1790 | 49.91 | 0.17754 | 62.407 | 0.0005854 | 17.988 | 1083.8 | 1065.812
1791 | 0.17761 | 49.92 | 62.407 | 0.00058561 | 17.998 | 1083.8 |  | 1791 | 49.92 | 0.17761 | 62.407 | 0.00058561 | 17.998 | 1083.8 | 1065.802
1792 | 0.17767 | 49.93 | 62.407 | 0.00058581 | 18.008 | 1083.8 |  | 1792 | 49.93 | 0.17767 | 62.407 | 0.00058581 | 18.008 | 1083.8 | 1065.792
1793 | 0.17774 | 49.94 | 62.407 | 0.00058602 | 18.018 | 1083.8 |  | 1793 | 49.94 | 0.17774 | 62.407 | 0.00058602 | 18.018 | 1083.8 | 1065.782
1794 | 0.1778 | 49.95 | 62.407 | 0.00058623 | 18.028 | 1083.8 |  | 1794 | 49.95 | 0.1778 | 62.407 | 0.00058623 | 18.028 | 1083.8 | 1065.772
1795 | 0.17787 | 49.96 | 62.407 | 0.00058643 | 18.038 | 1083.8 |  | 1795 | 49.96 | 0.17787 | 62.407 | 0.00058643 | 18.038 | 1083.8 | 1065.762
1796 | 0.17794 | 49.97 | 62.406 | 0.00058664 | 18.048 | 1083.8 |  | 1796 | 49.97 | 0.17794 | 62.406 | 0.00058664 | 18.048 | 1083.8 | 1065.752
1797 | 0.178 | 49.98 | 62.406 | 0.00058685 | 18.058 | 1083.8 |  | 1797 | 49.98 | 0.178 | 62.406 | 0.00058685 | 18.058 | 1083.8 | 1065.742
1798 | 0.17807 | 49.99 | 62.406 | 0.00058706 | 18.068 | 1083.8 |  | 1798 | 49.99 | 0.17807 | 62.406 | 0.00058706 | 18.068 | 1083.8 | 1065.732
1799 | 0.17814 | 50 | 62.406 | 0.00058726 | 18.078 | 1083.8 |  | 1799 | 50 | 0.17814 | 62.406 | 0.00058726 | 18.078 | 1083.8 | 1065.722
1800 | 0.1782 | 50.01 | 62.406 | 0.00058747 | 18.088 | 1083.8 |  | 1800 | 50.01 | 0.1782 | 62.406 | 0.00058747 | 18.088 | 1083.8 | 1065.712
1801 | 0.17827 | 50.02 | 62.406 | 0.00058768 | 18.098 | 1083.8 |  | 1801 | 50.02 | 0.17827 | 62.406 | 0.00058768 | 18.098 | 1083.8 | 1065.702
1802 | 0.17833 | 50.03 | 62.406 | 0.00058789 | 18.108 | 1083.8 |  | 1802 | 50.03 | 0.17833 | 62.406 | 0.00058789 | 18.108 | 1083.8 | 1065.692
1803 | 0.1784 | 50.04 | 62.406 | 0.00058809 | 18.118 | 1083.8 |  | 1803 | 50.04 | 0.1784 | 62.406 | 0.00058809 | 18.118 | 1083.8 | 1065.682
1804 | 0.17847 | 50.05 | 62.406 | 0.0005883 | 18.128 | 1083.8 |  | 1804 | 50.05 | 0.17847 | 62.406 | 0.0005883 | 18.128 | 1083.8 | 1065.672
1805 | 0.17853 | 50.06 | 62.406 | 0.00058851 | 18.138 | 1083.8 |  | 1805 | 50.06 | 0.17853 | 62.406 | 0.00058851 | 18.138 | 1083.8 | 1065.662
1806 | 0.1786 | 50.07 | 62.406 | 0.00058872 | 18.148 | 1083.8 |  | 1806 | 50.07 | 0.1786 | 62.406 | 0.00058872 | 18.148 | 1083.8 | 1065.652
1807 | 0.17867 | 50.08 | 62.406 | 0.00058892 | 18.158 | 1083.8 |  | 1807 | 50.08 | 0.17867 | 62.406 | 0.00058892 | 18.158 | 1083.8 | 1065.642
1808 | 0.17873 | 50.09 | 62.406 | 0.00058913 | 18.168 | 1083.8 |  | 1808 | 50.09 | 0.17873 | 62.406 | 0.00058913 | 18.168 | 1083.8 | 1065.632
1809 | 0.1788 | 50.1 | 62.406 | 0.00058934 | 18.178 | 1083.8 |  | 1809 | 50.1 | 0.1788 | 62.406 | 0.00058934 | 18.178 | 1083.8 | 1065.622
1810 | 0.17887 | 50.11 | 62.406 | 0.00058955 | 18.188 | 1083.8 |  | 1810 | 50.11 | 0.17887 | 62.406 | 0.00058955 | 18.188 | 1083.8 | 1065.612
1811 | 0.17893 | 50.12 | 62.406 | 0.00058975 | 18.198 | 1083.8 |  | 1811 | 50.12 | 0.17893 | 62.406 | 0.00058975 | 18.198 | 1083.8 | 1065.602
1812 | 0.179 | 50.13 | 62.406 | 0.00058996 | 18.208 | 1083.8 |  | 1812 | 50.13 | 0.179 | 62.406 | 0.00058996 | 18.208 | 1083.8 | 1065.592
1813 | 0.17907 | 50.14 | 62.406 | 0.00059017 | 18.218 | 1083.9 |  | 1813 | 50.14 | 0.17907 | 62.406 | 0.00059017 | 18.218 | 1083.9 | 1065.682
1814 | 0.17913 | 50.15 | 62.406 | 0.00059038 | 18.228 | 1083.9 |  | 1814 | 50.15 | 0.17913 | 62.406 | 0.00059038 | 18.228 | 1083.9 | 1065.672
1815 | 0.1792 | 50.16 | 62.406 | 0.00059059 | 18.238 | 1083.9 |  | 1815 | 50.16 | 0.1792 | 62.406 | 0.00059059 | 18.238 | 1083.9 | 1065.662
1816 | 0.17927 | 50.17 | 62.406 | 0.0005908 | 18.248 | 1083.9 |  | 1816 | 50.17 | 0.17927 | 62.406 | 0.0005908 | 18.248 | 1083.9 | 1065.652
1817 | 0.17933 | 50.18 | 62.406 | 0.000591 | 18.258 | 1083.9 |  | 1817 | 50.18 | 0.17933 | 62.406 | 0.000591 | 18.258 | 1083.9 | 1065.642
1818 | 0.1794 | 50.19 | 62.406 | 0.00059121 | 18.269 | 1083.9 |  | 1818 | 50.19 | 0.1794 | 62.406 | 0.00059121 | 18.269 | 1083.9 | 1065.631
1819 | 0.17947 | 50.2 | 62.406 | 0.00059142 | 18.279 | 1083.9 |  | 1819 | 50.2 | 0.17947 | 62.406 | 0.00059142 | 18.279 | 1083.9 | 1065.621
1820 | 0.17953 | 50.21 | 62.406 | 0.00059163 | 18.289 | 1083.9 |  | 1820 | 50.21 | 0.17953 | 62.406 | 0.00059163 | 18.289 | 1083.9 | 1065.611
1821 | 0.1796 | 50.22 | 62.406 | 0.00059184 | 18.299 | 1083.9 |  | 1821 | 50.22 | 0.1796 | 62.406 | 0.00059184 | 18.299 | 1083.9 | 1065.601
1822 | 0.17967 | 50.23 | 62.406 | 0.00059205 | 18.309 | 1083.9 |  | 1822 | 50.23 | 0.17967 | 62.406 | 0.00059205 | 18.309 | 1083.9 | 1065.591
1823 | 0.17973 | 50.24 | 62.406 | 0.00059225 | 18.319 | 1083.9 |  | 1823 | 50.24 | 0.17973 | 62.406 | 0.00059225 | 18.319 | 1083.9 | 1065.581
1824 | 0.1798 | 50.25 | 62.406 | 0.00059246 | 18.329 | 1083.9 |  | 1824 | 50.25 | 0.1798 | 62.406 | 0.00059246 | 18.329 | 1083.9 | 1065.571
1825 | 0.17987 | 50.26 | 62.406 | 0.00059267 | 18.339 | 1083.9 |  | 1825 | 50.26 | 0.17987 | 62.406 | 0.00059267 | 18.339 | 1083.9 | 1065.561
1826 | 0.17993 | 50.27 | 62.406 | 0.00059288 | 18.349 | 1083.9 |  | 1826 | 50.27 | 0.17993 | 62.406 | 0.00059288 | 18.349 | 1083.9 | 1065.551
1827 | 0.18 | 50.28 | 62.406 | 0.00059309 | 18.359 | 1083.9 |  | 1827 | 50.28 | 0.18 | 62.406 | 0.00059309 | 18.359 | 1083.9 | 1065.541
1828 | 0.18007 | 50.29 | 62.406 | 0.0005933 | 18.369 | 1083.9 |  | 1828 | 50.29 | 0.18007 | 62.406 | 0.0005933 | 18.369 | 1083.9 | 1065.531
1829 | 0.18013 | 50.3 | 62.405 | 0.00059351 | 18.379 | 1083.9 |  | 1829 | 50.3 | 0.18013 | 62.405 | 0.00059351 | 18.379 | 1083.9 | 1065.521
1830 | 0.1802 | 50.31 | 62.405 | 0.00059372 | 18.389 | 1083.9 |  | 1830 | 50.31 | 0.1802 | 62.405 | 0.00059372 | 18.389 | 1083.9 | 1065.511
1831 | 0.18027 | 50.32 | 62.405 | 0.00059393 | 18.399 | 1083.9 |  | 1831 | 50.32 | 0.18027 | 62.405 | 0.00059393 | 18.399 | 1083.9 | 1065.501
1832 | 0.18034 | 50.33 | 62.405 | 0.00059414 | 18.409 | 1083.9 |  | 1832 | 50.33 | 0.18034 | 62.405 | 0.00059414 | 18.409 | 1083.9 | 1065.491
1833 | 0.1804 | 50.34 | 62.405 | 0.00059435 | 18.419 | 1083.9 |  | 1833 | 50.34 | 0.1804 | 62.405 | 0.00059435 | 18.419 | 1083.9 | 1065.481
1834 | 0.18047 | 50.35 | 62.405 | 0.00059455 | 18.429 | 1083.9 |  | 1834 | 50.35 | 0.18047 | 62.405 | 0.00059455 | 18.429 | 1083.9 | 1065.471
1835 | 0.18054 | 50.36 | 62.405 | 0.00059476 | 18.439 | 1083.9 |  | 1835 | 50.36 | 0.18054 | 62.405 | 0.00059476 | 18.439 | 1083.9 | 1065.461
1836 | 0.1806 | 50.37 | 62.405 | 0.00059497 | 18.449 | 1084 |  | 1836 | 50.37 | 0.1806 | 62.405 | 0.00059497 | 18.449 | 1084 | 1065.551
1837 | 0.18067 | 50.38 | 62.405 | 0.00059518 | 18.459 | 1084 |  | 1837 | 50.38 | 0.18067 | 62.405 | 0.00059518 | 18.459 | 1084 | 1065.541
1838 | 0.18074 | 50.39 | 62.405 | 0.00059539 | 18.469 | 1084 |  | 1838 | 50.39 | 0.18074 | 62.405 | 0.00059539 | 18.469 | 1084 | 1065.531
1839 | 0.18081 | 50.4 | 62.405 | 0.0005956 | 18.479 | 1084 |  | 1839 | 50.4 | 0.18081 | 62.405 | 0.0005956 | 18.479 | 1084 | 1065.521
1840 | 0.18087 | 50.41 | 62.405 | 0.00059581 | 18.489 | 1084 |  | 1840 | 50.41 | 0.18087 | 62.405 | 0.00059581 | 18.489 | 1084 | 1065.511
1841 | 0.18094 | 50.42 | 62.405 | 0.00059602 | 18.499 | 1084 |  | 1841 | 50.42 | 0.18094 | 62.405 | 0.00059602 | 18.499 | 1084 | 1065.501
1842 | 0.18101 | 50.43 | 62.405 | 0.00059623 | 18.509 | 1084 |  | 1842 | 50.43 | 0.18101 | 62.405 | 0.00059623 | 18.509 | 1084 | 1065.491
1843 | 0.18107 | 50.44 | 62.405 | 0.00059644 | 18.519 | 1084 |  | 1843 | 50.44 | 0.18107 | 62.405 | 0.00059644 | 18.519 | 1084 | 1065.481
1844 | 0.18114 | 50.45 | 62.405 | 0.00059665 | 18.529 | 1084 |  | 1844 | 50.45 | 0.18114 | 62.405 | 0.00059665 | 18.529 | 1084 | 1065.471
1845 | 0.18121 | 50.46 | 62.405 | 0.00059686 | 18.539 | 1084 |  | 1845 | 50.46 | 0.18121 | 62.405 | 0.00059686 | 18.539 | 1084 | 1065.461
1846 | 0.18128 | 50.47 | 62.405 | 0.00059707 | 18.549 | 1084 |  | 1846 | 50.47 | 0.18128 | 62.405 | 0.00059707 | 18.549 | 1084 | 1065.451
1847 | 0.18134 | 50.48 | 62.405 | 0.00059728 | 18.559 | 1084 |  | 1847 | 50.48 | 0.18134 | 62.405 | 0.00059728 | 18.559 | 1084 | 1065.441
1848 | 0.18141 | 50.49 | 62.405 | 0.00059749 | 18.569 | 1084 |  | 1848 | 50.49 | 0.18141 | 62.405 | 0.00059749 | 18.569 | 1084 | 1065.431
1849 | 0.18148 | 50.5 | 62.405 | 0.0005977 | 18.579 | 1084 |  | 1849 | 50.5 | 0.18148 | 62.405 | 0.0005977 | 18.579 | 1084 | 1065.421
1850 | 0.18155 | 50.51 | 62.405 | 0.00059791 | 18.589 | 1084 |  | 1850 | 50.51 | 0.18155 | 62.405 | 0.00059791 | 18.589 | 1084 | 1065.411
1851 | 0.18161 | 50.52 | 62.405 | 0.00059813 | 18.599 | 1084 |  | 1851 | 50.52 | 0.18161 | 62.405 | 0.00059813 | 18.599 | 1084 | 1065.401
1852 | 0.18168 | 50.53 | 62.405 | 0.00059834 | 18.609 | 1084 |  | 1852 | 50.53 | 0.18168 | 62.405 | 0.00059834 | 18.609 | 1084 | 1065.391
1853 | 0.18175 | 50.54 | 62.405 | 0.00059855 | 18.619 | 1084 |  | 1853 | 50.54 | 0.18175 | 62.405 | 0.00059855 | 18.619 | 1084 | 1065.381
1854 | 0.18182 | 50.55 | 62.405 | 0.00059876 | 18.629 | 1084 |  | 1854 | 50.55 | 0.18182 | 62.405 | 0.00059876 | 18.629 | 1084 | 1065.371
1855 | 0.18188 | 50.56 | 62.405 | 0.00059897 | 18.639 | 1084 |  | 1855 | 50.56 | 0.18188 | 62.405 | 0.00059897 | 18.639 | 1084 | 1065.361
1856 | 0.18195 | 50.57 | 62.405 | 0.00059918 | 18.65 | 1084 |  | 1856 | 50.57 | 0.18195 | 62.405 | 0.00059918 | 18.65 | 1084 | 1065.35
1857 | 0.18202 | 50.58 | 62.405 | 0.00059939 | 18.66 | 1084 |  | 1857 | 50.58 | 0.18202 | 62.405 | 0.00059939 | 18.66 | 1084 | 1065.34
1858 | 0.18209 | 50.59 | 62.405 | 0.0005996 | 18.67 | 1084 |  | 1858 | 50.59 | 0.18209 | 62.405 | 0.0005996 | 18.67 | 1084 | 1065.33
1859 | 0.18215 | 50.6 | 62.405 | 0.00059981 | 18.68 | 1084.1 |  | 1859 | 50.6 | 0.18215 | 62.405 | 0.00059981 | 18.68 | 1084.1 | 1065.42
1860 | 0.18222 | 50.61 | 62.404 | 0.00060002 | 18.69 | 1084.1 |  | 1860 | 50.61 | 0.18222 | 62.404 | 0.00060002 | 18.69 | 1084.1 | 1065.41
1861 | 0.18229 | 50.62 | 62.404 | 0.00060023 | 18.7 | 1084.1 |  | 1861 | 50.62 | 0.18229 | 62.404 | 0.00060023 | 18.7 | 1084.1 | 1065.4
1862 | 0.18236 | 50.63 | 62.404 | 0.00060045 | 18.71 | 1084.1 |  | 1862 | 50.63 | 0.18236 | 62.404 | 0.00060045 | 18.71 | 1084.1 | 1065.39
1863 | 0.18242 | 50.64 | 62.404 | 0.00060066 | 18.72 | 1084.1 |  | 1863 | 50.64 | 0.18242 | 62.404 | 0.00060066 | 18.72 | 1084.1 | 1065.38
1864 | 0.18249 | 50.65 | 62.404 | 0.00060087 | 18.73 | 1084.1 |  | 1864 | 50.65 | 0.18249 | 62.404 | 0.00060087 | 18.73 | 1084.1 | 1065.37
1865 | 0.18256 | 50.66 | 62.404 | 0.00060108 | 18.74 | 1084.1 |  | 1865 | 50.66 | 0.18256 | 62.404 | 0.00060108 | 18.74 | 1084.1 | 1065.36
1866 | 0.18263 | 50.67 | 62.404 | 0.00060129 | 18.75 | 1084.1 |  | 1866 | 50.67 | 0.18263 | 62.404 | 0.00060129 | 18.75 | 1084.1 | 1065.35
1867 | 0.1827 | 50.68 | 62.404 | 0.0006015 | 18.76 | 1084.1 |  | 1867 | 50.68 | 0.1827 | 62.404 | 0.0006015 | 18.76 | 1084.1 | 1065.34
1868 | 0.18276 | 50.69 | 62.404 | 0.00060171 | 18.77 | 1084.1 |  | 1868 | 50.69 | 0.18276 | 62.404 | 0.00060171 | 18.77 | 1084.1 | 1065.33
1869 | 0.18283 | 50.7 | 62.404 | 0.00060193 | 18.78 | 1084.1 |  | 1869 | 50.7 | 0.18283 | 62.404 | 0.00060193 | 18.78 | 1084.1 | 1065.32
1870 | 0.1829 | 50.71 | 62.404 | 0.00060214 | 18.79 | 1084.1 |  | 1870 | 50.71 | 0.1829 | 62.404 | 0.00060214 | 18.79 | 1084.1 | 1065.31
1871 | 0.18297 | 50.72 | 62.404 | 0.00060235 | 18.8 | 1084.1 |  | 1871 | 50.72 | 0.18297 | 62.404 | 0.00060235 | 18.8 | 1084.1 | 1065.3
1872 | 0.18303 | 50.73 | 62.404 | 0.00060256 | 18.81 | 1084.1 |  | 1872 | 50.73 | 0.18303 | 62.404 | 0.00060256 | 18.81 | 1084.1 | 1065.29
1873 | 0.1831 | 50.74 | 62.404 | 0.00060277 | 18.82 | 1084.1 |  | 1873 | 50.74 | 0.1831 | 62.404 | 0.00060277 | 18.82 | 1084.1 | 1065.28
1874 | 0.18317 | 50.75 | 62.404 | 0.00060299 | 18.83 | 1084.1 |  | 1874 | 50.75 | 0.18317 | 62.404 | 0.00060299 | 18.83 | 1084.1 | 1065.27
1875 | 0.18324 | 50.76 | 62.404 | 0.0006032 | 18.84 | 1084.1 |  | 1875 | 50.76 | 0.18324 | 62.404 | 0.0006032 | 18.84 | 1084.1 | 1065.26
1876 | 0.18331 | 50.77 | 62.404 | 0.00060341 | 18.85 | 1084.1 |  | 1876 | 50.77 | 0.18331 | 62.404 | 0.00060341 | 18.85 | 1084.1 | 1065.25
1877 | 0.18337 | 50.78 | 62.404 | 0.00060362 | 18.86 | 1084.1 |  | 1877 | 50.78 | 0.18337 | 62.404 | 0.00060362 | 18.86 | 1084.1 | 1065.24
1878 | 0.18344 | 50.79 | 62.404 | 0.00060383 | 18.87 | 1084.1 |  | 1878 | 50.79 | 0.18344 | 62.404 | 0.00060383 | 18.87 | 1084.1 | 1065.23
1879 | 0.18351 | 50.8 | 62.404 | 0.00060405 | 18.88 | 1084.1 |  | 1879 | 50.8 | 0.18351 | 62.404 | 0.00060405 | 18.88 | 1084.1 | 1065.22
1880 | 0.18358 | 50.81 | 62.404 | 0.00060426 | 18.89 | 1084.1 |  | 1880 | 50.81 | 0.18358 | 62.404 | 0.00060426 | 18.89 | 1084.1 | 1065.21
1881 | 0.18365 | 50.82 | 62.404 | 0.00060447 | 18.9 | 1084.1 |  | 1881 | 50.82 | 0.18365 | 62.404 | 0.00060447 | 18.9 | 1084.1 | 1065.2
1882 | 0.18371 | 50.83 | 62.404 | 0.00060468 | 18.91 | 1084.2 |  | 1882 | 50.83 | 0.18371 | 62.404 | 0.00060468 | 18.91 | 1084.2 | 1065.29
1883 | 0.18378 | 50.84 | 62.404 | 0.0006049 | 18.92 | 1084.2 |  | 1883 | 50.84 | 0.18378 | 62.404 | 0.0006049 | 18.92 | 1084.2 | 1065.28
1884 | 0.18385 | 50.85 | 62.404 | 0.00060511 | 18.93 | 1084.2 |  | 1884 | 50.85 | 0.18385 | 62.404 | 0.00060511 | 18.93 | 1084.2 | 1065.27
1885 | 0.18392 | 50.86 | 62.404 | 0.00060532 | 18.94 | 1084.2 |  | 1885 | 50.86 | 0.18392 | 62.404 | 0.00060532 | 18.94 | 1084.2 | 1065.26
1886 | 0.18399 | 50.87 | 62.404 | 0.00060553 | 18.95 | 1084.2 |  | 1886 | 50.87 | 0.18399 | 62.404 | 0.00060553 | 18.95 | 1084.2 | 1065.25
1887 | 0.18406 | 50.88 | 62.404 | 0.00060575 | 18.96 | 1084.2 |  | 1887 | 50.88 | 0.18406 | 62.404 | 0.00060575 | 18.96 | 1084.2 | 1065.24
1888 | 0.18412 | 50.89 | 62.404 | 0.00060596 | 18.97 | 1084.2 |  | 1888 | 50.89 | 0.18412 | 62.404 | 0.00060596 | 18.97 | 1084.2 | 1065.23
1889 | 0.18419 | 50.9 | 62.404 | 0.00060617 | 18.98 | 1084.2 |  | 1889 | 50.9 | 0.18419 | 62.404 | 0.00060617 | 18.98 | 1084.2 | 1065.22
1890 | 0.18426 | 50.91 | 62.404 | 0.00060639 | 18.99 | 1084.2 |  | 1890 | 50.91 | 0.18426 | 62.404 | 0.00060639 | 18.99 | 1084.2 | 1065.21
1891 | 0.18433 | 50.92 | 62.403 | 0.0006066 | 19 | 1084.2 |  | 1891 | 50.92 | 0.18433 | 62.403 | 0.0006066 | 19 | 1084.2 | 1065.2
1892 | 0.1844 | 50.93 | 62.403 | 0.00060681 | 19.01 | 1084.2 |  | 1892 | 50.93 | 0.1844 | 62.403 | 0.00060681 | 19.01 | 1084.2 | 1065.19
1893 | 0.18447 | 50.94 | 62.403 | 0.00060703 | 19.02 | 1084.2 |  | 1893 | 50.94 | 0.18447 | 62.403 | 0.00060703 | 19.02 | 1084.2 | 1065.18
1894 | 0.18453 | 50.95 | 62.403 | 0.00060724 | 19.031 | 1084.2 |  | 1894 | 50.95 | 0.18453 | 62.403 | 0.00060724 | 19.031 | 1084.2 | 1065.169
1895 | 0.1846 | 50.96 | 62.403 | 0.00060745 | 19.041 | 1084.2 |  | 1895 | 50.96 | 0.1846 | 62.403 | 0.00060745 | 19.041 | 1084.2 | 1065.159
1896 | 0.18467 | 50.97 | 62.403 | 0.00060767 | 19.051 | 1084.2 |  | 1896 | 50.97 | 0.18467 | 62.403 | 0.00060767 | 19.051 | 1084.2 | 1065.149
1897 | 0.18474 | 50.98 | 62.403 | 0.00060788 | 19.061 | 1084.2 |  | 1897 | 50.98 | 0.18474 | 62.403 | 0.00060788 | 19.061 | 1084.2 | 1065.139
1898 | 0.18481 | 50.99 | 62.403 | 0.00060809 | 19.071 | 1084.2 |  | 1898 | 50.99 | 0.18481 | 62.403 | 0.00060809 | 19.071 | 1084.2 | 1065.129
1899 | 0.18488 | 51 | 62.403 | 0.00060831 | 19.081 | 1084.2 |  | 1899 | 51 | 0.18488 | 62.403 | 0.00060831 | 19.081 | 1084.2 | 1065.119
1900 | 0.18494 | 51.01 | 62.403 | 0.00060852 | 19.091 | 1084.2 |  | 1900 | 51.01 | 0.18494 | 62.403 | 0.00060852 | 19.091 | 1084.2 | 1065.109
1901 | 0.18501 | 51.02 | 62.403 | 0.00060873 | 19.101 | 1084.2 |  | 1901 | 51.02 | 0.18501 | 62.403 | 0.00060873 | 19.101 | 1084.2 | 1065.099
1902 | 0.18508 | 51.03 | 62.403 | 0.00060895 | 19.111 | 1084.2 |  | 1902 | 51.03 | 0.18508 | 62.403 | 0.00060895 | 19.111 | 1084.2 | 1065.089
1903 | 0.18515 | 51.04 | 62.403 | 0.00060916 | 19.121 | 1084.2 |  | 1903 | 51.04 | 0.18515 | 62.403 | 0.00060916 | 19.121 | 1084.2 | 1065.079
1904 | 0.18522 | 51.05 | 62.403 | 0.00060938 | 19.131 | 1084.2 |  | 1904 | 51.05 | 0.18522 | 62.403 | 0.00060938 | 19.131 | 1084.2 | 1065.069
1905 | 0.18529 | 51.06 | 62.403 | 0.00060959 | 19.141 | 1084.3 |  | 1905 | 51.06 | 0.18529 | 62.403 | 0.00060959 | 19.141 | 1084.3 | 1065.159
1906 | 0.18536 | 51.07 | 62.403 | 0.0006098 | 19.151 | 1084.3 |  | 1906 | 51.07 | 0.18536 | 62.403 | 0.0006098 | 19.151 | 1084.3 | 1065.149
1907 | 0.18543 | 51.08 | 62.403 | 0.00061002 | 19.161 | 1084.3 |  | 1907 | 51.08 | 0.18543 | 62.403 | 0.00061002 | 19.161 | 1084.3 | 1065.139
1908 | 0.18549 | 51.09 | 62.403 | 0.00061023 | 19.171 | 1084.3 |  | 1908 | 51.09 | 0.18549 | 62.403 | 0.00061023 | 19.171 | 1084.3 | 1065.129
1909 | 0.18556 | 51.1 | 62.403 | 0.00061045 | 19.181 | 1084.3 |  | 1909 | 51.1 | 0.18556 | 62.403 | 0.00061045 | 19.181 | 1084.3 | 1065.119
1910 | 0.18563 | 51.11 | 62.403 | 0.00061066 | 19.191 | 1084.3 |  | 1910 | 51.11 | 0.18563 | 62.403 | 0.00061066 | 19.191 | 1084.3 | 1065.109
1911 | 0.1857 | 51.12 | 62.403 | 0.00061088 | 19.201 | 1084.3 |  | 1911 | 51.12 | 0.1857 | 62.403 | 0.00061088 | 19.201 | 1084.3 | 1065.099
1912 | 0.18577 | 51.13 | 62.403 | 0.00061109 | 19.211 | 1084.3 |  | 1912 | 51.13 | 0.18577 | 62.403 | 0.00061109 | 19.211 | 1084.3 | 1065.089
1913 | 0.18584 | 51.14 | 62.403 | 0.0006113 | 19.221 | 1084.3 |  | 1913 | 51.14 | 0.18584 | 62.403 | 0.0006113 | 19.221 | 1084.3 | 1065.079
1914 | 0.18591 | 51.15 | 62.403 | 0.00061152 | 19.231 | 1084.3 |  | 1914 | 51.15 | 0.18591 | 62.403 | 0.00061152 | 19.231 | 1084.3 | 1065.069
1915 | 0.18598 | 51.16 | 62.403 | 0.00061173 | 19.241 | 1084.3 |  | 1915 | 51.16 | 0.18598 | 62.403 | 0.00061173 | 19.241 | 1084.3 | 1065.059
1916 | 0.18604 | 51.17 | 62.403 | 0.00061195 | 19.251 | 1084.3 |  | 1916 | 51.17 | 0.18604 | 62.403 | 0.00061195 | 19.251 | 1084.3 | 1065.049
1917 | 0.18611 | 51.18 | 62.403 | 0.00061216 | 19.261 | 1084.3 |  | 1917 | 51.18 | 0.18611 | 62.403 | 0.00061216 | 19.261 | 1084.3 | 1065.039
1918 | 0.18618 | 51.19 | 62.403 | 0.00061238 | 19.271 | 1084.3 |  | 1918 | 51.19 | 0.18618 | 62.403 | 0.00061238 | 19.271 | 1084.3 | 1065.029
1919 | 0.18625 | 51.2 | 62.403 | 0.00061259 | 19.281 | 1084.3 |  | 1919 | 51.2 | 0.18625 | 62.403 | 0.00061259 | 19.281 | 1084.3 | 1065.019
1920 | 0.18632 | 51.21 | 62.403 | 0.00061281 | 19.291 | 1084.3 |  | 1920 | 51.21 | 0.18632 | 62.403 | 0.00061281 | 19.291 | 1084.3 | 1065.009
1921 | 0.18639 | 51.22 | 62.403 | 0.00061302 | 19.301 | 1084.3 |  | 1921 | 51.22 | 0.18639 | 62.403 | 0.00061302 | 19.301 | 1084.3 | 1064.999
1922 | 0.18646 | 51.23 | 62.402 | 0.00061324 | 19.311 | 1084.3 |  | 1922 | 51.23 | 0.18646 | 62.402 | 0.00061324 | 19.311 | 1084.3 | 1064.989
1923 | 0.18653 | 51.24 | 62.402 | 0.00061345 | 19.321 | 1084.3 |  | 1923 | 51.24 | 0.18653 | 62.402 | 0.00061345 | 19.321 | 1084.3 | 1064.979
1924 | 0.1866 | 51.25 | 62.402 | 0.00061367 | 19.331 | 1084.3 |  | 1924 | 51.25 | 0.1866 | 62.402 | 0.00061367 | 19.331 | 1084.3 | 1064.969
1925 | 0.18667 | 51.26 | 62.402 | 0.00061388 | 19.341 | 1084.3 |  | 1925 | 51.26 | 0.18667 | 62.402 | 0.00061388 | 19.341 | 1084.3 | 1064.959
1926 | 0.18673 | 51.27 | 62.402 | 0.0006141 | 19.351 | 1084.3 |  | 1926 | 51.27 | 0.18673 | 62.402 | 0.0006141 | 19.351 | 1084.3 | 1064.949
1927 | 0.1868 | 51.28 | 62.402 | 0.00061431 | 19.361 | 1084.3 |  | 1927 | 51.28 | 0.1868 | 62.402 | 0.00061431 | 19.361 | 1084.3 | 1064.939
1928 | 0.18687 | 51.29 | 62.402 | 0.00061453 | 19.371 | 1084.4 |  | 1928 | 51.29 | 0.18687 | 62.402 | 0.00061453 | 19.371 | 1084.4 | 1065.029
1929 | 0.18694 | 51.3 | 62.402 | 0.00061475 | 19.381 | 1084.4 |  | 1929 | 51.3 | 0.18694 | 62.402 | 0.00061475 | 19.381 | 1084.4 | 1065.019
1930 | 0.18701 | 51.31 | 62.402 | 0.00061496 | 19.391 | 1084.4 |  | 1930 | 51.31 | 0.18701 | 62.402 | 0.00061496 | 19.391 | 1084.4 | 1065.009
1931 | 0.18708 | 51.32 | 62.402 | 0.00061518 | 19.401 | 1084.4 |  | 1931 | 51.32 | 0.18708 | 62.402 | 0.00061518 | 19.401 | 1084.4 | 1064.999
1932 | 0.18715 | 51.33 | 62.402 | 0.00061539 | 19.411 | 1084.4 |  | 1932 | 51.33 | 0.18715 | 62.402 | 0.00061539 | 19.411 | 1084.4 | 1064.989
1933 | 0.18722 | 51.34 | 62.402 | 0.00061561 | 19.422 | 1084.4 |  | 1933 | 51.34 | 0.18722 | 62.402 | 0.00061561 | 19.422 | 1084.4 | 1064.978
1934 | 0.18729 | 51.35 | 62.402 | 0.00061583 | 19.432 | 1084.4 |  | 1934 | 51.35 | 0.18729 | 62.402 | 0.00061583 | 19.432 | 1084.4 | 1064.968
1935 | 0.18736 | 51.36 | 62.402 | 0.00061604 | 19.442 | 1084.4 |  | 1935 | 51.36 | 0.18736 | 62.402 | 0.00061604 | 19.442 | 1084.4 | 1064.958
1936 | 0.18743 | 51.37 | 62.402 | 0.00061626 | 19.452 | 1084.4 |  | 1936 | 51.37 | 0.18743 | 62.402 | 0.00061626 | 19.452 | 1084.4 | 1064.948
1937 | 0.1875 | 51.38 | 62.402 | 0.00061647 | 19.462 | 1084.4 |  | 1937 | 51.38 | 0.1875 | 62.402 | 0.00061647 | 19.462 | 1084.4 | 1064.938
1938 | 0.18757 | 51.39 | 62.402 | 0.00061669 | 19.472 | 1084.4 |  | 1938 | 51.39 | 0.18757 | 62.402 | 0.00061669 | 19.472 | 1084.4 | 1064.928
1939 | 0.18764 | 51.4 | 62.402 | 0.00061691 | 19.482 | 1084.4 |  | 1939 | 51.4 | 0.18764 | 62.402 | 0.00061691 | 19.482 | 1084.4 | 1064.918
1940 | 0.1877 | 51.41 | 62.402 | 0.00061712 | 19.492 | 1084.4 |  | 1940 | 51.41 | 0.1877 | 62.402 | 0.00061712 | 19.492 | 1084.4 | 1064.908
1941 | 0.18777 | 51.42 | 62.402 | 0.00061734 | 19.502 | 1084.4 |  | 1941 | 51.42 | 0.18777 | 62.402 | 0.00061734 | 19.502 | 1084.4 | 1064.898
1942 | 0.18784 | 51.43 | 62.402 | 0.00061756 | 19.512 | 1084.4 |  | 1942 | 51.43 | 0.18784 | 62.402 | 0.00061756 | 19.512 | 1084.4 | 1064.888
1943 | 0.18791 | 51.44 | 62.402 | 0.00061777 | 19.522 | 1084.4 |  | 1943 | 51.44 | 0.18791 | 62.402 | 0.00061777 | 19.522 | 1084.4 | 1064.878
1944 | 0.18798 | 51.45 | 62.402 | 0.00061799 | 19.532 | 1084.4 |  | 1944 | 51.45 | 0.18798 | 62.402 | 0.00061799 | 19.532 | 1084.4 | 1064.868
1945 | 0.18805 | 51.46 | 62.402 | 0.0006182 | 19.542 | 1084.4 |  | 1945 | 51.46 | 0.18805 | 62.402 | 0.0006182 | 19.542 | 1084.4 | 1064.858
1946 | 0.18812 | 51.47 | 62.402 | 0.00061842 | 19.552 | 1084.4 |  | 1946 | 51.47 | 0.18812 | 62.402 | 0.00061842 | 19.552 | 1084.4 | 1064.848
1947 | 0.18819 | 51.48 | 62.402 | 0.00061864 | 19.562 | 1084.4 |  | 1947 | 51.48 | 0.18819 | 62.402 | 0.00061864 | 19.562 | 1084.4 | 1064.838
1948 | 0.18826 | 51.49 | 62.402 | 0.00061886 | 19.572 | 1084.4 |  | 1948 | 51.49 | 0.18826 | 62.402 | 0.00061886 | 19.572 | 1084.4 | 1064.828
1949 | 0.18833 | 51.5 | 62.402 | 0.00061907 | 19.582 | 1084.4 |  | 1949 | 51.5 | 0.18833 | 62.402 | 0.00061907 | 19.582 | 1084.4 | 1064.818
1950 | 0.1884 | 51.51 | 62.402 | 0.00061929 | 19.592 | 1084.4 |  | 1950 | 51.51 | 0.1884 | 62.402 | 0.00061929 | 19.592 | 1084.4 | 1064.808
1951 | 0.18847 | 51.52 | 62.401 | 0.00061951 | 19.602 | 1084.5 |  | 1951 | 51.52 | 0.18847 | 62.401 | 0.00061951 | 19.602 | 1084.5 | 1064.898
1952 | 0.18854 | 51.53 | 62.401 | 0.00061972 | 19.612 | 1084.5 |  | 1952 | 51.53 | 0.18854 | 62.401 | 0.00061972 | 19.612 | 1084.5 | 1064.888
1953 | 0.18861 | 51.54 | 62.401 | 0.00061994 | 19.622 | 1084.5 |  | 1953 | 51.54 | 0.18861 | 62.401 | 0.00061994 | 19.622 | 1084.5 | 1064.878
1954 | 0.18868 | 51.55 | 62.401 | 0.00062016 | 19.632 | 1084.5 |  | 1954 | 51.55 | 0.18868 | 62.401 | 0.00062016 | 19.632 | 1084.5 | 1064.868
1955 | 0.18875 | 51.56 | 62.401 | 0.00062038 | 19.642 | 1084.5 |  | 1955 | 51.56 | 0.18875 | 62.401 | 0.00062038 | 19.642 | 1084.5 | 1064.858
1956 | 0.18882 | 51.57 | 62.401 | 0.00062059 | 19.652 | 1084.5 |  | 1956 | 51.57 | 0.18882 | 62.401 | 0.00062059 | 19.652 | 1084.5 | 1064.848
1957 | 0.18889 | 51.58 | 62.401 | 0.00062081 | 19.662 | 1084.5 |  | 1957 | 51.58 | 0.18889 | 62.401 | 0.00062081 | 19.662 | 1084.5 | 1064.838
1958 | 0.18896 | 51.59 | 62.401 | 0.00062103 | 19.672 | 1084.5 |  | 1958 | 51.59 | 0.18896 | 62.401 | 0.00062103 | 19.672 | 1084.5 | 1064.828
1959 | 0.18903 | 51.6 | 62.401 | 0.00062125 | 19.682 | 1084.5 |  | 1959 | 51.6 | 0.18903 | 62.401 | 0.00062125 | 19.682 | 1084.5 | 1064.818
1960 | 0.1891 | 51.61 | 62.401 | 0.00062146 | 19.692 | 1084.5 |  | 1960 | 51.61 | 0.1891 | 62.401 | 0.00062146 | 19.692 | 1084.5 | 1064.808
1961 | 0.18917 | 51.62 | 62.401 | 0.00062168 | 19.702 | 1084.5 |  | 1961 | 51.62 | 0.18917 | 62.401 | 0.00062168 | 19.702 | 1084.5 | 1064.798
1962 | 0.18924 | 51.63 | 62.401 | 0.0006219 | 19.712 | 1084.5 |  | 1962 | 51.63 | 0.18924 | 62.401 | 0.0006219 | 19.712 | 1084.5 | 1064.788
1963 | 0.18931 | 51.64 | 62.401 | 0.00062212 | 19.722 | 1084.5 |  | 1963 | 51.64 | 0.18931 | 62.401 | 0.00062212 | 19.722 | 1084.5 | 1064.778
1964 | 0.18938 | 51.65 | 62.401 | 0.00062233 | 19.732 | 1084.5 |  | 1964 | 51.65 | 0.18938 | 62.401 | 0.00062233 | 19.732 | 1084.5 | 1064.768
1965 | 0.18945 | 51.66 | 62.401 | 0.00062255 | 19.742 | 1084.5 |  | 1965 | 51.66 | 0.18945 | 62.401 | 0.00062255 | 19.742 | 1084.5 | 1064.758
1966 | 0.18952 | 51.67 | 62.401 | 0.00062277 | 19.752 | 1084.5 |  | 1966 | 51.67 | 0.18952 | 62.401 | 0.00062277 | 19.752 | 1084.5 | 1064.748
1967 | 0.18959 | 51.68 | 62.401 | 0.00062299 | 19.762 | 1084.5 |  | 1967 | 51.68 | 0.18959 | 62.401 | 0.00062299 | 19.762 | 1084.5 | 1064.738
1968 | 0.18966 | 51.69 | 62.401 | 0.00062321 | 19.772 | 1084.5 |  | 1968 | 51.69 | 0.18966 | 62.401 | 0.00062321 | 19.772 | 1084.5 | 1064.728
1969 | 0.18973 | 51.7 | 62.401 | 0.00062342 | 19.782 | 1084.5 |  | 1969 | 51.7 | 0.18973 | 62.401 | 0.00062342 | 19.782 | 1084.5 | 1064.718
1970 | 0.1898 | 51.71 | 62.401 | 0.00062364 | 19.792 | 1084.5 |  | 1970 | 51.71 | 0.1898 | 62.401 | 0.00062364 | 19.792 | 1084.5 | 1064.708
1971 | 0.18987 | 51.72 | 62.401 | 0.00062386 | 19.802 | 1084.5 |  | 1971 | 51.72 | 0.18987 | 62.401 | 0.00062386 | 19.802 | 1084.5 | 1064.698
1972 | 0.18994 | 51.73 | 62.401 | 0.00062408 | 19.812 | 1084.5 |  | 1972 | 51.73 | 0.18994 | 62.401 | 0.00062408 | 19.812 | 1084.5 | 1064.688
1973 | 0.19001 | 51.74 | 62.401 | 0.0006243 | 19.822 | 1084.5 |  | 1973 | 51.74 | 0.19001 | 62.401 | 0.0006243 | 19.822 | 1084.5 | 1064.678
1974 | 0.19008 | 51.75 | 62.401 | 0.00062452 | 19.833 | 1084.6 |  | 1974 | 51.75 | 0.19008 | 62.401 | 0.00062452 | 19.833 | 1084.6 | 1064.767
1975 | 0.19015 | 51.76 | 62.401 | 0.00062474 | 19.843 | 1084.6 |  | 1975 | 51.76 | 0.19015 | 62.401 | 0.00062474 | 19.843 | 1084.6 | 1064.757
1976 | 0.19022 | 51.77 | 62.401 | 0.00062495 | 19.853 | 1084.6 |  | 1976 | 51.77 | 0.19022 | 62.401 | 0.00062495 | 19.853 | 1084.6 | 1064.747
1977 | 0.19029 | 51.78 | 62.401 | 0.00062517 | 19.863 | 1084.6 |  | 1977 | 51.78 | 0.19029 | 62.401 | 0.00062517 | 19.863 | 1084.6 | 1064.737
1978 | 0.19036 | 51.79 | 62.401 | 0.00062539 | 19.873 | 1084.6 |  | 1978 | 51.79 | 0.19036 | 62.401 | 0.00062539 | 19.873 | 1084.6 | 1064.727
1979 | 0.19043 | 51.8 | 62.401 | 0.00062561 | 19.883 | 1084.6 |  | 1979 | 51.8 | 0.19043 | 62.401 | 0.00062561 | 19.883 | 1084.6 | 1064.717
1980 | 0.1905 | 51.81 | 62.4 | 0.00062583 | 19.893 | 1084.6 |  | 1980 | 51.81 | 0.1905 | 62.4 | 0.00062583 | 19.893 | 1084.6 | 1064.707
1981 | 0.19057 | 51.82 | 62.4 | 0.00062605 | 19.903 | 1084.6 |  | 1981 | 51.82 | 0.19057 | 62.4 | 0.00062605 | 19.903 | 1084.6 | 1064.697
1982 | 0.19064 | 51.83 | 62.4 | 0.00062627 | 19.913 | 1084.6 |  | 1982 | 51.83 | 0.19064 | 62.4 | 0.00062627 | 19.913 | 1084.6 | 1064.687
1983 | 0.19071 | 51.84 | 62.4 | 0.00062649 | 19.923 | 1084.6 |  | 1983 | 51.84 | 0.19071 | 62.4 | 0.00062649 | 19.923 | 1084.6 | 1064.677
1984 | 0.19078 | 51.85 | 62.4 | 0.00062671 | 19.933 | 1084.6 |  | 1984 | 51.85 | 0.19078 | 62.4 | 0.00062671 | 19.933 | 1084.6 | 1064.667
1985 | 0.19085 | 51.86 | 62.4 | 0.00062693 | 19.943 | 1084.6 |  | 1985 | 51.86 | 0.19085 | 62.4 | 0.00062693 | 19.943 | 1084.6 | 1064.657
1986 | 0.19092 | 51.87 | 62.4 | 0.00062715 | 19.953 | 1084.6 |  | 1986 | 51.87 | 0.19092 | 62.4 | 0.00062715 | 19.953 | 1084.6 | 1064.647
1987 | 0.19099 | 51.88 | 62.4 | 0.00062736 | 19.963 | 1084.6 |  | 1987 | 51.88 | 0.19099 | 62.4 | 0.00062736 | 19.963 | 1084.6 | 1064.637
1988 | 0.19106 | 51.89 | 62.4 | 0.00062758 | 19.973 | 1084.6 |  | 1988 | 51.89 | 0.19106 | 62.4 | 0.00062758 | 19.973 | 1084.6 | 1064.627
1989 | 0.19113 | 51.9 | 62.4 | 0.0006278 | 19.983 | 1084.6 |  | 1989 | 51.9 | 0.19113 | 62.4 | 0.0006278 | 19.983 | 1084.6 | 1064.617
1990 | 0.19121 | 51.91 | 62.4 | 0.00062802 | 19.993 | 1084.6 |  | 1990 | 51.91 | 0.19121 | 62.4 | 0.00062802 | 19.993 | 1084.6 | 1064.607
1991 | 0.19128 | 51.92 | 62.4 | 0.00062824 | 20.003 | 1084.6 |  | 1991 | 51.92 | 0.19128 | 62.4 | 0.00062824 | 20.003 | 1084.6 | 1064.597
1992 | 0.19135 | 51.93 | 62.4 | 0.00062846 | 20.013 | 1084.6 |  | 1992 | 51.93 | 0.19135 | 62.4 | 0.00062846 | 20.013 | 1084.6 | 1064.587
1993 | 0.19142 | 51.94 | 62.4 | 0.00062868 | 20.023 | 1084.6 |  | 1993 | 51.94 | 0.19142 | 62.4 | 0.00062868 | 20.023 | 1084.6 | 1064.577
1994 | 0.19149 | 51.95 | 62.4 | 0.0006289 | 20.033 | 1084.6 |  | 1994 | 51.95 | 0.19149 | 62.4 | 0.0006289 | 20.033 | 1084.6 | 1064.567
1995 | 0.19156 | 51.96 | 62.4 | 0.00062912 | 20.043 | 1084.6 |  | 1995 | 51.96 | 0.19156 | 62.4 | 0.00062912 | 20.043 | 1084.6 | 1064.557
1996 | 0.19163 | 51.97 | 62.4 | 0.00062934 | 20.053 | 1084.6 |  | 1996 | 51.97 | 0.19163 | 62.4 | 0.00062934 | 20.053 | 1084.6 | 1064.547
1997 | 0.1917 | 51.98 | 62.4 | 0.00062956 | 20.063 | 1084.7 |  | 1997 | 51.98 | 0.1917 | 62.4 | 0.00062956 | 20.063 | 1084.7 | 1064.637
1998 | 0.19177 | 51.99 | 62.4 | 0.00062978 | 20.073 | 1084.7 |  | 1998 | 51.99 | 0.19177 | 62.4 | 0.00062978 | 20.073 | 1084.7 | 1064.627
1999 | 0.19184 | 52 | 62.4 | 0.00063 | 20.083 | 1084.7 |  | 1999 | 52 | 0.19184 | 62.4 | 0.00063 | 20.083 | 1084.7 | 1064.617
2000 | 0.19191 | 52.01 | 62.4 | 0.00063022 | 20.093 | 1084.7 |  | 2000 | 52.01 | 0.19191 | 62.4 | 0.00063022 | 20.093 | 1084.7 | 1064.607
2001 | 0.19198 | 52.02 | 62.4 | 0.00063044 | 20.103 | 1084.7 |  | 2001 | 52.02 | 0.19198 | 62.4 | 0.00063044 | 20.103 | 1084.7 | 1064.597
2002 | 0.19205 | 52.03 | 62.4 | 0.00063066 | 20.113 | 1084.7 |  | 2002 | 52.03 | 0.19205 | 62.4 | 0.00063066 | 20.113 | 1084.7 | 1064.587
2003 | 0.19212 | 52.04 | 62.4 | 0.00063088 | 20.123 | 1084.7 |  | 2003 | 52.04 | 0.19212 | 62.4 | 0.00063088 | 20.123 | 1084.7 | 1064.577
2004 | 0.1922 | 52.05 | 62.4 | 0.00063111 | 20.133 | 1084.7 |  | 2004 | 52.05 | 0.1922 | 62.4 | 0.00063111 | 20.133 | 1084.7 | 1064.567
2005 | 0.19227 | 52.06 | 62.4 | 0.00063133 | 20.143 | 1084.7 |  | 2005 | 52.06 | 0.19227 | 62.4 | 0.00063133 | 20.143 | 1084.7 | 1064.557
2006 | 0.19234 | 52.07 | 62.4 | 0.00063155 | 20.153 | 1084.7 |  | 2006 | 52.07 | 0.19234 | 62.4 | 0.00063155 | 20.153 | 1084.7 | 1064.547
2007 | 0.19241 | 52.08 | 62.4 | 0.00063177 | 20.163 | 1084.7 |  | 2007 | 52.08 | 0.19241 | 62.4 | 0.00063177 | 20.163 | 1084.7 | 1064.537
2008 | 0.19248 | 52.09 | 62.399 | 0.00063199 | 20.173 | 1084.7 |  | 2008 | 52.09 | 0.19248 | 62.399 | 0.00063199 | 20.173 | 1084.7 | 1064.527
2009 | 0.19255 | 52.1 | 62.399 | 0.00063221 | 20.183 | 1084.7 |  | 2009 | 52.1 | 0.19255 | 62.399 | 0.00063221 | 20.183 | 1084.7 | 1064.517
2010 | 0.19262 | 52.11 | 62.399 | 0.00063243 | 20.193 | 1084.7 |  | 2010 | 52.11 | 0.19262 | 62.399 | 0.00063243 | 20.193 | 1084.7 | 1064.507
2011 | 0.19269 | 52.12 | 62.399 | 0.00063265 | 20.203 | 1084.7 |  | 2011 | 52.12 | 0.19269 | 62.399 | 0.00063265 | 20.203 | 1084.7 | 1064.497
2012 | 0.19276 | 52.13 | 62.399 | 0.00063287 | 20.213 | 1084.7 |  | 2012 | 52.13 | 0.19276 | 62.399 | 0.00063287 | 20.213 | 1084.7 | 1064.487
2013 | 0.19283 | 52.14 | 62.399 | 0.00063309 | 20.223 | 1084.7 |  | 2013 | 52.14 | 0.19283 | 62.399 | 0.00063309 | 20.223 | 1084.7 | 1064.477
2014 | 0.19291 | 52.15 | 62.399 | 0.00063332 | 20.233 | 1084.7 |  | 2014 | 52.15 | 0.19291 | 62.399 | 0.00063332 | 20.233 | 1084.7 | 1064.467
2015 | 0.19298 | 52.16 | 62.399 | 0.00063354 | 20.243 | 1084.7 |  | 2015 | 52.16 | 0.19298 | 62.399 | 0.00063354 | 20.243 | 1084.7 | 1064.457
2016 | 0.19305 | 52.17 | 62.399 | 0.00063376 | 20.254 | 1084.7 |  | 2016 | 52.17 | 0.19305 | 62.399 | 0.00063376 | 20.254 | 1084.7 | 1064.446
2017 | 0.19312 | 52.18 | 62.399 | 0.00063398 | 20.264 | 1084.7 |  | 2017 | 52.18 | 0.19312 | 62.399 | 0.00063398 | 20.264 | 1084.7 | 1064.436
2018 | 0.19319 | 52.19 | 62.399 | 0.0006342 | 20.274 | 1084.7 |  | 2018 | 52.19 | 0.19319 | 62.399 | 0.0006342 | 20.274 | 1084.7 | 1064.426
2019 | 0.19326 | 52.2 | 62.399 | 0.00063442 | 20.284 | 1084.7 |  | 2019 | 52.2 | 0.19326 | 62.399 | 0.00063442 | 20.284 | 1084.7 | 1064.416
2020 | 0.19333 | 52.21 | 62.399 | 0.00063464 | 20.294 | 1084.8 |  | 2020 | 52.21 | 0.19333 | 62.399 | 0.00063464 | 20.294 | 1084.8 | 1064.506
2021 | 0.1934 | 52.22 | 62.399 | 0.00063487 | 20.304 | 1084.8 |  | 2021 | 52.22 | 0.1934 | 62.399 | 0.00063487 | 20.304 | 1084.8 | 1064.496
2022 | 0.19348 | 52.23 | 62.399 | 0.00063509 | 20.314 | 1084.8 |  | 2022 | 52.23 | 0.19348 | 62.399 | 0.00063509 | 20.314 | 1084.8 | 1064.486
2023 | 0.19355 | 52.24 | 62.399 | 0.00063531 | 20.324 | 1084.8 |  | 2023 | 52.24 | 0.19355 | 62.399 | 0.00063531 | 20.324 | 1084.8 | 1064.476
2024 | 0.19362 | 52.25 | 62.399 | 0.00063553 | 20.334 | 1084.8 |  | 2024 | 52.25 | 0.19362 | 62.399 | 0.00063553 | 20.334 | 1084.8 | 1064.466
2025 | 0.19369 | 52.26 | 62.399 | 0.00063575 | 20.344 | 1084.8 |  | 2025 | 52.26 | 0.19369 | 62.399 | 0.00063575 | 20.344 | 1084.8 | 1064.456
2026 | 0.19376 | 52.27 | 62.399 | 0.00063598 | 20.354 | 1084.8 |  | 2026 | 52.27 | 0.19376 | 62.399 | 0.00063598 | 20.354 | 1084.8 | 1064.446
2027 | 0.19383 | 52.28 | 62.399 | 0.0006362 | 20.364 | 1084.8 |  | 2027 | 52.28 | 0.19383 | 62.399 | 0.0006362 | 20.364 | 1084.8 | 1064.436
2028 | 0.1939 | 52.29 | 62.399 | 0.00063642 | 20.374 | 1084.8 |  | 2028 | 52.29 | 0.1939 | 62.399 | 0.00063642 | 20.374 | 1084.8 | 1064.426
2029 | 0.19398 | 52.3 | 62.399 | 0.00063664 | 20.384 | 1084.8 |  | 2029 | 52.3 | 0.19398 | 62.399 | 0.00063664 | 20.384 | 1084.8 | 1064.416
2030 | 0.19405 | 52.31 | 62.399 | 0.00063686 | 20.394 | 1084.8 |  | 2030 | 52.31 | 0.19405 | 62.399 | 0.00063686 | 20.394 | 1084.8 | 1064.406
2031 | 0.19412 | 52.32 | 62.399 | 0.00063709 | 20.404 | 1084.8 |  | 2031 | 52.32 | 0.19412 | 62.399 | 0.00063709 | 20.404 | 1084.8 | 1064.396
2032 | 0.19419 | 52.33 | 62.399 | 0.00063731 | 20.414 | 1084.8 |  | 2032 | 52.33 | 0.19419 | 62.399 | 0.00063731 | 20.414 | 1084.8 | 1064.386
2033 | 0.19426 | 52.34 | 62.399 | 0.00063753 | 20.424 | 1084.8 |  | 2033 | 52.34 | 0.19426 | 62.399 | 0.00063753 | 20.424 | 1084.8 | 1064.376
2034 | 0.19433 | 52.35 | 62.399 | 0.00063775 | 20.434 | 1084.8 |  | 2034 | 52.35 | 0.19433 | 62.399 | 0.00063775 | 20.434 | 1084.8 | 1064.366
2035 | 0.1944 | 52.36 | 62.399 | 0.00063798 | 20.444 | 1084.8 |  | 2035 | 52.36 | 0.1944 | 62.399 | 0.00063798 | 20.444 | 1084.8 | 1064.356
2036 | 0.19448 | 52.37 | 62.398 | 0.0006382 | 20.454 | 1084.8 |  | 2036 | 52.37 | 0.19448 | 62.398 | 0.0006382 | 20.454 | 1084.8 | 1064.346
2037 | 0.19455 | 52.38 | 62.398 | 0.00063842 | 20.464 | 1084.8 |  | 2037 | 52.38 | 0.19455 | 62.398 | 0.00063842 | 20.464 | 1084.8 | 1064.336
2038 | 0.19462 | 52.39 | 62.398 | 0.00063865 | 20.474 | 1084.8 |  | 2038 | 52.39 | 0.19462 | 62.398 | 0.00063865 | 20.474 | 1084.8 | 1064.326
2039 | 0.19469 | 52.4 | 62.398 | 0.00063887 | 20.484 | 1084.8 |  | 2039 | 52.4 | 0.19469 | 62.398 | 0.00063887 | 20.484 | 1084.8 | 1064.316
2040 | 0.19476 | 52.41 | 62.398 | 0.00063909 | 20.494 | 1084.8 |  | 2040 | 52.41 | 0.19476 | 62.398 | 0.00063909 | 20.494 | 1084.8 | 1064.306
2041 | 0.19483 | 52.42 | 62.398 | 0.00063931 | 20.504 | 1084.8 |  | 2041 | 52.42 | 0.19483 | 62.398 | 0.00063931 | 20.504 | 1084.8 | 1064.296
2042 | 0.19491 | 52.43 | 62.398 | 0.00063954 | 20.514 | 1084.9 |  | 2042 | 52.43 | 0.19491 | 62.398 | 0.00063954 | 20.514 | 1084.9 | 1064.386
2043 | 0.19498 | 52.44 | 62.398 | 0.00063976 | 20.524 | 1084.9 |  | 2043 | 52.44 | 0.19498 | 62.398 | 0.00063976 | 20.524 | 1084.9 | 1064.376
2044 | 0.19505 | 52.45 | 62.398 | 0.00063998 | 20.534 | 1084.9 |  | 2044 | 52.45 | 0.19505 | 62.398 | 0.00063998 | 20.534 | 1084.9 | 1064.366
2045 | 0.19512 | 52.46 | 62.398 | 0.00064021 | 20.544 | 1084.9 |  | 2045 | 52.46 | 0.19512 | 62.398 | 0.00064021 | 20.544 | 1084.9 | 1064.356
2046 | 0.19519 | 52.47 | 62.398 | 0.00064043 | 20.554 | 1084.9 |  | 2046 | 52.47 | 0.19519 | 62.398 | 0.00064043 | 20.554 | 1084.9 | 1064.346
2047 | 0.19527 | 52.48 | 62.398 | 0.00064065 | 20.564 | 1084.9 |  | 2047 | 52.48 | 0.19527 | 62.398 | 0.00064065 | 20.564 | 1084.9 | 1064.336
2048 | 0.19534 | 52.49 | 62.398 | 0.00064088 | 20.574 | 1084.9 |  | 2048 | 52.49 | 0.19534 | 62.398 | 0.00064088 | 20.574 | 1084.9 | 1064.326
2049 | 0.19541 | 52.5 | 62.398 | 0.0006411 | 20.584 | 1084.9 |  | 2049 | 52.5 | 0.19541 | 62.398 | 0.0006411 | 20.584 | 1084.9 | 1064.316
2050 | 0.19548 | 52.51 | 62.398 | 0.00064133 | 20.594 | 1084.9 |  | 2050 | 52.51 | 0.19548 | 62.398 | 0.00064133 | 20.594 | 1084.9 | 1064.306
2051 | 0.19555 | 52.52 | 62.398 | 0.00064155 | 20.604 | 1084.9 |  | 2051 | 52.52 | 0.19555 | 62.398 | 0.00064155 | 20.604 | 1084.9 | 1064.296
2052 | 0.19563 | 52.53 | 62.398 | 0.00064177 | 20.614 | 1084.9 |  | 2052 | 52.53 | 0.19563 | 62.398 | 0.00064177 | 20.614 | 1084.9 | 1064.286
2053 | 0.1957 | 52.54 | 62.398 | 0.000642 | 20.624 | 1084.9 |  | 2053 | 52.54 | 0.1957 | 62.398 | 0.000642 | 20.624 | 1084.9 | 1064.276
2054 | 0.19577 | 52.55 | 62.398 | 0.00064222 | 20.634 | 1084.9 |  | 2054 | 52.55 | 0.19577 | 62.398 | 0.00064222 | 20.634 | 1084.9 | 1064.266
2055 | 0.19584 | 52.56 | 62.398 | 0.00064245 | 20.644 | 1084.9 |  | 2055 | 52.56 | 0.19584 | 62.398 | 0.00064245 | 20.644 | 1084.9 | 1064.256
2056 | 0.19591 | 52.57 | 62.398 | 0.00064267 | 20.654 | 1084.9 |  | 2056 | 52.57 | 0.19591 | 62.398 | 0.00064267 | 20.654 | 1084.9 | 1064.246
2057 | 0.19599 | 52.58 | 62.398 | 0.00064289 | 20.664 | 1084.9 |  | 2057 | 52.58 | 0.19599 | 62.398 | 0.00064289 | 20.664 | 1084.9 | 1064.236
2058 | 0.19606 | 52.59 | 62.398 | 0.00064312 | 20.674 | 1084.9 |  | 2058 | 52.59 | 0.19606 | 62.398 | 0.00064312 | 20.674 | 1084.9 | 1064.226
2059 | 0.19613 | 52.6 | 62.398 | 0.00064334 | 20.684 | 1084.9 |  | 2059 | 52.6 | 0.19613 | 62.398 | 0.00064334 | 20.684 | 1084.9 | 1064.216
2060 | 0.1962 | 52.61 | 62.398 | 0.00064357 | 20.695 | 1084.9 |  | 2060 | 52.61 | 0.1962 | 62.398 | 0.00064357 | 20.695 | 1084.9 | 1064.205
2061 | 0.19627 | 52.62 | 62.398 | 0.00064379 | 20.705 | 1084.9 |  | 2061 | 52.62 | 0.19627 | 62.398 | 0.00064379 | 20.705 | 1084.9 | 1064.195
2062 | 0.19635 | 52.63 | 62.398 | 0.00064402 | 20.715 | 1084.9 |  | 2062 | 52.63 | 0.19635 | 62.398 | 0.00064402 | 20.715 | 1084.9 | 1064.185
2063 | 0.19642 | 52.64 | 62.397 | 0.00064424 | 20.725 | 1084.9 |  | 2063 | 52.64 | 0.19642 | 62.397 | 0.00064424 | 20.725 | 1084.9 | 1064.175
2064 | 0.19649 | 52.65 | 62.397 | 0.00064446 | 20.735 | 1084.9 |  | 2064 | 52.65 | 0.19649 | 62.397 | 0.00064446 | 20.735 | 1084.9 | 1064.165
2065 | 0.19656 | 52.66 | 62.397 | 0.00064469 | 20.745 | 1085 |  | 2065 | 52.66 | 0.19656 | 62.397 | 0.00064469 | 20.745 | 1085 | 1064.255
2066 | 0.19664 | 52.67 | 62.397 | 0.00064491 | 20.755 | 1085 |  | 2066 | 52.67 | 0.19664 | 62.397 | 0.00064491 | 20.755 | 1085 | 1064.245
2067 | 0.19671 | 52.68 | 62.397 | 0.00064514 | 20.765 | 1085 |  | 2067 | 52.68 | 0.19671 | 62.397 | 0.00064514 | 20.765 | 1085 | 1064.235
2068 | 0.19678 | 52.69 | 62.397 | 0.00064536 | 20.775 | 1085 |  | 2068 | 52.69 | 0.19678 | 62.397 | 0.00064536 | 20.775 | 1085 | 1064.225
2069 | 0.19685 | 52.7 | 62.397 | 0.00064559 | 20.785 | 1085 |  | 2069 | 52.7 | 0.19685 | 62.397 | 0.00064559 | 20.785 | 1085 | 1064.215
2070 | 0.19693 | 52.71 | 62.397 | 0.00064581 | 20.795 | 1085 |  | 2070 | 52.71 | 0.19693 | 62.397 | 0.00064581 | 20.795 | 1085 | 1064.205
2071 | 0.197 | 52.72 | 62.397 | 0.00064604 | 20.805 | 1085 |  | 2071 | 52.72 | 0.197 | 62.397 | 0.00064604 | 20.805 | 1085 | 1064.195
2072 | 0.19707 | 52.73 | 62.397 | 0.00064626 | 20.815 | 1085 |  | 2072 | 52.73 | 0.19707 | 62.397 | 0.00064626 | 20.815 | 1085 | 1064.185
2073 | 0.19714 | 52.74 | 62.397 | 0.00064649 | 20.825 | 1085 |  | 2073 | 52.74 | 0.19714 | 62.397 | 0.00064649 | 20.825 | 1085 | 1064.175
2074 | 0.19722 | 52.75 | 62.397 | 0.00064671 | 20.835 | 1085 |  | 2074 | 52.75 | 0.19722 | 62.397 | 0.00064671 | 20.835 | 1085 | 1064.165
2075 | 0.19729 | 52.76 | 62.397 | 0.00064694 | 20.845 | 1085 |  | 2075 | 52.76 | 0.19729 | 62.397 | 0.00064694 | 20.845 | 1085 | 1064.155
2076 | 0.19736 | 52.77 | 62.397 | 0.00064717 | 20.855 | 1085 |  | 2076 | 52.77 | 0.19736 | 62.397 | 0.00064717 | 20.855 | 1085 | 1064.145
2077 | 0.19743 | 52.78 | 62.397 | 0.00064739 | 20.865 | 1085 |  | 2077 | 52.78 | 0.19743 | 62.397 | 0.00064739 | 20.865 | 1085 | 1064.135
2078 | 0.19751 | 52.79 | 62.397 | 0.00064762 | 20.875 | 1085 |  | 2078 | 52.79 | 0.19751 | 62.397 | 0.00064762 | 20.875 | 1085 | 1064.125
2079 | 0.19758 | 52.8 | 62.397 | 0.00064784 | 20.885 | 1085 |  | 2079 | 52.8 | 0.19758 | 62.397 | 0.00064784 | 20.885 | 1085 | 1064.115
2080 | 0.19765 | 52.81 | 62.397 | 0.00064807 | 20.895 | 1085 |  | 2080 | 52.81 | 0.19765 | 62.397 | 0.00064807 | 20.895 | 1085 | 1064.105
2081 | 0.19772 | 52.82 | 62.397 | 0.00064829 | 20.905 | 1085 |  | 2081 | 52.82 | 0.19772 | 62.397 | 0.00064829 | 20.905 | 1085 | 1064.095
2082 | 0.1978 | 52.83 | 62.397 | 0.00064852 | 20.915 | 1085 |  | 2082 | 52.83 | 0.1978 | 62.397 | 0.00064852 | 20.915 | 1085 | 1064.085
2083 | 0.19787 | 52.84 | 62.397 | 0.00064875 | 20.925 | 1085 |  | 2083 | 52.84 | 0.19787 | 62.397 | 0.00064875 | 20.925 | 1085 | 1064.075
2084 | 0.19794 | 52.85 | 62.397 | 0.00064897 | 20.935 | 1085 |  | 2084 | 52.85 | 0.19794 | 62.397 | 0.00064897 | 20.935 | 1085 | 1064.065
2085 | 0.19801 | 52.86 | 62.397 | 0.0006492 | 20.945 | 1085 |  | 2085 | 52.86 | 0.19801 | 62.397 | 0.0006492 | 20.945 | 1085 | 1064.055
2086 | 0.19809 | 52.87 | 62.397 | 0.00064942 | 20.955 | 1085 |  | 2086 | 52.87 | 0.19809 | 62.397 | 0.00064942 | 20.955 | 1085 | 1064.045
2087 | 0.19816 | 52.88 | 62.397 | 0.00064965 | 20.965 | 1085 |  | 2087 | 52.88 | 0.19816 | 62.397 | 0.00064965 | 20.965 | 1085 | 1064.035
2088 | 0.19823 | 52.89 | 62.397 | 0.00064988 | 20.975 | 1085.1 |  | 2088 | 52.89 | 0.19823 | 62.397 | 0.00064988 | 20.975 | 1085.1 | 1064.125
2089 | 0.19831 | 52.9 | 62.397 | 0.0006501 | 20.985 | 1085.1 |  | 2089 | 52.9 | 0.19831 | 62.397 | 0.0006501 | 20.985 | 1085.1 | 1064.115
2090 | 0.19838 | 52.91 | 62.396 | 0.00065033 | 20.995 | 1085.1 |  | 2090 | 52.91 | 0.19838 | 62.396 | 0.00065033 | 20.995 | 1085.1 | 1064.105
2091 | 0.19845 | 52.92 | 62.396 | 0.00065056 | 21.005 | 1085.1 |  | 2091 | 52.92 | 0.19845 | 62.396 | 0.00065056 | 21.005 | 1085.1 | 1064.095
2092 | 0.19852 | 52.93 | 62.396 | 0.00065078 | 21.015 | 1085.1 |  | 2092 | 52.93 | 0.19852 | 62.396 | 0.00065078 | 21.015 | 1085.1 | 1064.085
2093 | 0.1986 | 52.94 | 62.396 | 0.00065101 | 21.025 | 1085.1 |  | 2093 | 52.94 | 0.1986 | 62.396 | 0.00065101 | 21.025 | 1085.1 | 1064.075
2094 | 0.19867 | 52.95 | 62.396 | 0.00065124 | 21.035 | 1085.1 |  | 2094 | 52.95 | 0.19867 | 62.396 | 0.00065124 | 21.035 | 1085.1 | 1064.065
2095 | 0.19874 | 52.96 | 62.396 | 0.00065146 | 21.045 | 1085.1 |  | 2095 | 52.96 | 0.19874 | 62.396 | 0.00065146 | 21.045 | 1085.1 | 1064.055
2096 | 0.19882 | 52.97 | 62.396 | 0.00065169 | 21.055 | 1085.1 |  | 2096 | 52.97 | 0.19882 | 62.396 | 0.00065169 | 21.055 | 1085.1 | 1064.045
2097 | 0.19889 | 52.98 | 62.396 | 0.00065192 | 21.065 | 1085.1 |  | 2097 | 52.98 | 0.19889 | 62.396 | 0.00065192 | 21.065 | 1085.1 | 1064.035
2098 | 0.19896 | 52.99 | 62.396 | 0.00065214 | 21.075 | 1085.1 |  | 2098 | 52.99 | 0.19896 | 62.396 | 0.00065214 | 21.075 | 1085.1 | 1064.025
2099 | 0.19904 | 53 | 62.396 | 0.00065237 | 21.085 | 1085.1 |  | 2099 | 53 | 0.19904 | 62.396 | 0.00065237 | 21.085 | 1085.1 | 1064.015
2100 | 0.19911 | 53.01 | 62.396 | 0.0006526 | 21.095 | 1085.1 |  | 2100 | 53.01 | 0.19911 | 62.396 | 0.0006526 | 21.095 | 1085.1 | 1064.005
2101 | 0.19918 | 53.02 | 62.396 | 0.00065282 | 21.105 | 1085.1 |  | 2101 | 53.02 | 0.19918 | 62.396 | 0.00065282 | 21.105 | 1085.1 | 1063.995
2102 | 0.19926 | 53.03 | 62.396 | 0.00065305 | 21.115 | 1085.1 |  | 2102 | 53.03 | 0.19926 | 62.396 | 0.00065305 | 21.115 | 1085.1 | 1063.985
2103 | 0.19933 | 53.04 | 62.396 | 0.00065328 | 21.125 | 1085.1 |  | 2103 | 53.04 | 0.19933 | 62.396 | 0.00065328 | 21.125 | 1085.1 | 1063.975
2104 | 0.1994 | 53.05 | 62.396 | 0.00065351 | 21.135 | 1085.1 |  | 2104 | 53.05 | 0.1994 | 62.396 | 0.00065351 | 21.135 | 1085.1 | 1063.965
2105 | 0.19948 | 53.06 | 62.396 | 0.00065373 | 21.146 | 1085.1 |  | 2105 | 53.06 | 0.19948 | 62.396 | 0.00065373 | 21.146 | 1085.1 | 1063.954
2106 | 0.19955 | 53.07 | 62.396 | 0.00065396 | 21.156 | 1085.1 |  | 2106 | 53.07 | 0.19955 | 62.396 | 0.00065396 | 21.156 | 1085.1 | 1063.944
2107 | 0.19962 | 53.08 | 62.396 | 0.00065419 | 21.166 | 1085.1 |  | 2107 | 53.08 | 0.19962 | 62.396 | 0.00065419 | 21.166 | 1085.1 | 1063.934
2108 | 0.1997 | 53.09 | 62.396 | 0.00065442 | 21.176 | 1085.1 |  | 2108 | 53.09 | 0.1997 | 62.396 | 0.00065442 | 21.176 | 1085.1 | 1063.924
2109 | 0.19977 | 53.1 | 62.396 | 0.00065464 | 21.186 | 1085.1 |  | 2109 | 53.1 | 0.19977 | 62.396 | 0.00065464 | 21.186 | 1085.1 | 1063.914
2110 | 0.19984 | 53.11 | 62.396 | 0.00065487 | 21.196 | 1085.1 |  | 2110 | 53.11 | 0.19984 | 62.396 | 0.00065487 | 21.196 | 1085.1 | 1063.904
2111 | 0.19992 | 53.12 | 62.396 | 0.0006551 | 21.206 | 1085.2 |  | 2111 | 53.12 | 0.19992 | 62.396 | 0.0006551 | 21.206 | 1085.2 | 1063.994
2112 | 0.19999 | 53.13 | 62.396 | 0.00065533 | 21.216 | 1085.2 |  | 2112 | 53.13 | 0.19999 | 62.396 | 0.00065533 | 21.216 | 1085.2 | 1063.984
2113 | 0.20006 | 53.14 | 62.396 | 0.00065556 | 21.226 | 1085.2 |  | 2113 | 53.14 | 0.20006 | 62.396 | 0.00065556 | 21.226 | 1085.2 | 1063.974
2114 | 0.20014 | 53.15 | 62.396 | 0.00065578 | 21.236 | 1085.2 |  | 2114 | 53.15 | 0.20014 | 62.396 | 0.00065578 | 21.236 | 1085.2 | 1063.964
2115 | 0.20021 | 53.16 | 62.396 | 0.00065601 | 21.246 | 1085.2 |  | 2115 | 53.16 | 0.20021 | 62.396 | 0.00065601 | 21.246 | 1085.2 | 1063.954
2116 | 0.20028 | 53.17 | 62.395 | 0.00065624 | 21.256 | 1085.2 |  | 2116 | 53.17 | 0.20028 | 62.395 | 0.00065624 | 21.256 | 1085.2 | 1063.944
2117 | 0.20036 | 53.18 | 62.395 | 0.00065647 | 21.266 | 1085.2 |  | 2117 | 53.18 | 0.20036 | 62.395 | 0.00065647 | 21.266 | 1085.2 | 1063.934
2118 | 0.20043 | 53.19 | 62.395 | 0.0006567 | 21.276 | 1085.2 |  | 2118 | 53.19 | 0.20043 | 62.395 | 0.0006567 | 21.276 | 1085.2 | 1063.924
2119 | 0.2005 | 53.2 | 62.395 | 0.00065693 | 21.286 | 1085.2 |  | 2119 | 53.2 | 0.2005 | 62.395 | 0.00065693 | 21.286 | 1085.2 | 1063.914
2120 | 0.20058 | 53.21 | 62.395 | 0.00065715 | 21.296 | 1085.2 |  | 2120 | 53.21 | 0.20058 | 62.395 | 0.00065715 | 21.296 | 1085.2 | 1063.904
2121 | 0.20065 | 53.22 | 62.395 | 0.00065738 | 21.306 | 1085.2 |  | 2121 | 53.22 | 0.20065 | 62.395 | 0.00065738 | 21.306 | 1085.2 | 1063.894
2122 | 0.20072 | 53.23 | 62.395 | 0.00065761 | 21.316 | 1085.2 |  | 2122 | 53.23 | 0.20072 | 62.395 | 0.00065761 | 21.316 | 1085.2 | 1063.884
2123 | 0.2008 | 53.24 | 62.395 | 0.00065784 | 21.326 | 1085.2 |  | 2123 | 53.24 | 0.2008 | 62.395 | 0.00065784 | 21.326 | 1085.2 | 1063.874
2124 | 0.20087 | 53.25 | 62.395 | 0.00065807 | 21.336 | 1085.2 |  | 2124 | 53.25 | 0.20087 | 62.395 | 0.00065807 | 21.336 | 1085.2 | 1063.864
2125 | 0.20095 | 53.26 | 62.395 | 0.0006583 | 21.346 | 1085.2 |  | 2125 | 53.26 | 0.20095 | 62.395 | 0.0006583 | 21.346 | 1085.2 | 1063.854
2126 | 0.20102 | 53.27 | 62.395 | 0.00065853 | 21.356 | 1085.2 |  | 2126 | 53.27 | 0.20102 | 62.395 | 0.00065853 | 21.356 | 1085.2 | 1063.844
2127 | 0.20109 | 53.28 | 62.395 | 0.00065876 | 21.366 | 1085.2 |  | 2127 | 53.28 | 0.20109 | 62.395 | 0.00065876 | 21.366 | 1085.2 | 1063.834
2128 | 0.20117 | 53.29 | 62.395 | 0.00065898 | 21.376 | 1085.2 |  | 2128 | 53.29 | 0.20117 | 62.395 | 0.00065898 | 21.376 | 1085.2 | 1063.824
2129 | 0.20124 | 53.3 | 62.395 | 0.00065921 | 21.386 | 1085.2 |  | 2129 | 53.3 | 0.20124 | 62.395 | 0.00065921 | 21.386 | 1085.2 | 1063.814
2130 | 0.20131 | 53.31 | 62.395 | 0.00065944 | 21.396 | 1085.2 |  | 2130 | 53.31 | 0.20131 | 62.395 | 0.00065944 | 21.396 | 1085.2 | 1063.804
2131 | 0.20139 | 53.32 | 62.395 | 0.00065967 | 21.406 | 1085.2 |  | 2131 | 53.32 | 0.20139 | 62.395 | 0.00065967 | 21.406 | 1085.2 | 1063.794
2132 | 0.20146 | 53.33 | 62.395 | 0.0006599 | 21.416 | 1085.2 |  | 2132 | 53.33 | 0.20146 | 62.395 | 0.0006599 | 21.416 | 1085.2 | 1063.784
2133 | 0.20154 | 53.34 | 62.395 | 0.00066013 | 21.426 | 1085.2 |  | 2133 | 53.34 | 0.20154 | 62.395 | 0.00066013 | 21.426 | 1085.2 | 1063.774
2134 | 0.20161 | 53.35 | 62.395 | 0.00066036 | 21.436 | 1085.3 |  | 2134 | 53.35 | 0.20161 | 62.395 | 0.00066036 | 21.436 | 1085.3 | 1063.864
2135 | 0.20168 | 53.36 | 62.395 | 0.00066059 | 21.446 | 1085.3 |  | 2135 | 53.36 | 0.20168 | 62.395 | 0.00066059 | 21.446 | 1085.3 | 1063.854
2136 | 0.20176 | 53.37 | 62.395 | 0.00066082 | 21.456 | 1085.3 |  | 2136 | 53.37 | 0.20176 | 62.395 | 0.00066082 | 21.456 | 1085.3 | 1063.844
2137 | 0.20183 | 53.38 | 62.395 | 0.00066105 | 21.466 | 1085.3 |  | 2137 | 53.38 | 0.20183 | 62.395 | 0.00066105 | 21.466 | 1085.3 | 1063.834
2138 | 0.20191 | 53.39 | 62.395 | 0.00066128 | 21.476 | 1085.3 |  | 2138 | 53.39 | 0.20191 | 62.395 | 0.00066128 | 21.476 | 1085.3 | 1063.824
2139 | 0.20198 | 53.4 | 62.395 | 0.00066151 | 21.486 | 1085.3 |  | 2139 | 53.4 | 0.20198 | 62.395 | 0.00066151 | 21.486 | 1085.3 | 1063.814
2140 | 0.20205 | 53.41 | 62.395 | 0.00066174 | 21.496 | 1085.3 |  | 2140 | 53.41 | 0.20205 | 62.395 | 0.00066174 | 21.496 | 1085.3 | 1063.804
2141 | 0.20213 | 53.42 | 62.395 | 0.00066197 | 21.506 | 1085.3 |  | 2141 | 53.42 | 0.20213 | 62.395 | 0.00066197 | 21.506 | 1085.3 | 1063.794
2142 | 0.2022 | 53.43 | 62.394 | 0.0006622 | 21.516 | 1085.3 |  | 2142 | 53.43 | 0.2022 | 62.394 | 0.0006622 | 21.516 | 1085.3 | 1063.784
2143 | 0.20228 | 53.44 | 62.394 | 0.00066243 | 21.526 | 1085.3 |  | 2143 | 53.44 | 0.20228 | 62.394 | 0.00066243 | 21.526 | 1085.3 | 1063.774
2144 | 0.20235 | 53.45 | 62.394 | 0.00066266 | 21.536 | 1085.3 |  | 2144 | 53.45 | 0.20235 | 62.394 | 0.00066266 | 21.536 | 1085.3 | 1063.764
2145 | 0.20242 | 53.46 | 62.394 | 0.00066289 | 21.546 | 1085.3 |  | 2145 | 53.46 | 0.20242 | 62.394 | 0.00066289 | 21.546 | 1085.3 | 1063.754
2146 | 0.2025 | 53.47 | 62.394 | 0.00066312 | 21.556 | 1085.3 |  | 2146 | 53.47 | 0.2025 | 62.394 | 0.00066312 | 21.556 | 1085.3 | 1063.744
2147 | 0.20257 | 53.48 | 62.394 | 0.00066335 | 21.566 | 1085.3 |  | 2147 | 53.48 | 0.20257 | 62.394 | 0.00066335 | 21.566 | 1085.3 | 1063.734
2148 | 0.20265 | 53.49 | 62.394 | 0.00066358 | 21.576 | 1085.3 |  | 2148 | 53.49 | 0.20265 | 62.394 | 0.00066358 | 21.576 | 1085.3 | 1063.724
2149 | 0.20272 | 53.5 | 62.394 | 0.00066381 | 21.586 | 1085.3 |  | 2149 | 53.5 | 0.20272 | 62.394 | 0.00066381 | 21.586 | 1085.3 | 1063.714
2150 | 0.2028 | 53.51 | 62.394 | 0.00066404 | 21.596 | 1085.3 |  | 2150 | 53.51 | 0.2028 | 62.394 | 0.00066404 | 21.596 | 1085.3 | 1063.704
2151 | 0.20287 | 53.52 | 62.394 | 0.00066427 | 21.606 | 1085.3 |  | 2151 | 53.52 | 0.20287 | 62.394 | 0.00066427 | 21.606 | 1085.3 | 1063.694
2152 | 0.20294 | 53.53 | 62.394 | 0.0006645 | 21.617 | 1085.3 |  | 2152 | 53.53 | 0.20294 | 62.394 | 0.0006645 | 21.617 | 1085.3 | 1063.683
2153 | 0.20302 | 53.54 | 62.394 | 0.00066473 | 21.627 | 1085.3 |  | 2153 | 53.54 | 0.20302 | 62.394 | 0.00066473 | 21.627 | 1085.3 | 1063.673
2154 | 0.20309 | 53.55 | 62.394 | 0.00066496 | 21.637 | 1085.3 |  | 2154 | 53.55 | 0.20309 | 62.394 | 0.00066496 | 21.637 | 1085.3 | 1063.663
2155 | 0.20317 | 53.56 | 62.394 | 0.0006652 | 21.647 | 1085.3 |  | 2155 | 53.56 | 0.20317 | 62.394 | 0.0006652 | 21.647 | 1085.3 | 1063.653
2156 | 0.20324 | 53.57 | 62.394 | 0.00066543 | 21.657 | 1085.3 |  | 2156 | 53.57 | 0.20324 | 62.394 | 0.00066543 | 21.657 | 1085.3 | 1063.643
2157 | 0.20332 | 53.58 | 62.394 | 0.00066566 | 21.667 | 1085.4 |  | 2157 | 53.58 | 0.20332 | 62.394 | 0.00066566 | 21.667 | 1085.4 | 1063.733
2158 | 0.20339 | 53.59 | 62.394 | 0.00066589 | 21.677 | 1085.4 |  | 2158 | 53.59 | 0.20339 | 62.394 | 0.00066589 | 21.677 | 1085.4 | 1063.723
2159 | 0.20347 | 53.6 | 62.394 | 0.00066612 | 21.687 | 1085.4 |  | 2159 | 53.6 | 0.20347 | 62.394 | 0.00066612 | 21.687 | 1085.4 | 1063.713
2160 | 0.20354 | 53.61 | 62.394 | 0.00066635 | 21.697 | 1085.4 |  | 2160 | 53.61 | 0.20354 | 62.394 | 0.00066635 | 21.697 | 1085.4 | 1063.703
2161 | 0.20362 | 53.62 | 62.394 | 0.00066658 | 21.707 | 1085.4 |  | 2161 | 53.62 | 0.20362 | 62.394 | 0.00066658 | 21.707 | 1085.4 | 1063.693
2162 | 0.20369 | 53.63 | 62.394 | 0.00066681 | 21.717 | 1085.4 |  | 2162 | 53.63 | 0.20369 | 62.394 | 0.00066681 | 21.717 | 1085.4 | 1063.683
2163 | 0.20376 | 53.64 | 62.394 | 0.00066704 | 21.727 | 1085.4 |  | 2163 | 53.64 | 0.20376 | 62.394 | 0.00066704 | 21.727 | 1085.4 | 1063.673
2164 | 0.20384 | 53.65 | 62.394 | 0.00066728 | 21.737 | 1085.4 |  | 2164 | 53.65 | 0.20384 | 62.394 | 0.00066728 | 21.737 | 1085.4 | 1063.663
2165 | 0.20391 | 53.66 | 62.394 | 0.00066751 | 21.747 | 1085.4 |  | 2165 | 53.66 | 0.20391 | 62.394 | 0.00066751 | 21.747 | 1085.4 | 1063.653
2166 | 0.20399 | 53.67 | 62.394 | 0.00066774 | 21.757 | 1085.4 |  | 2166 | 53.67 | 0.20399 | 62.394 | 0.00066774 | 21.757 | 1085.4 | 1063.643
2167 | 0.20406 | 53.68 | 62.393 | 0.00066797 | 21.767 | 1085.4 |  | 2167 | 53.68 | 0.20406 | 62.393 | 0.00066797 | 21.767 | 1085.4 | 1063.633
2168 | 0.20414 | 53.69 | 62.393 | 0.0006682 | 21.777 | 1085.4 |  | 2168 | 53.69 | 0.20414 | 62.393 | 0.0006682 | 21.777 | 1085.4 | 1063.623
2169 | 0.20421 | 53.7 | 62.393 | 0.00066844 | 21.787 | 1085.4 |  | 2169 | 53.7 | 0.20421 | 62.393 | 0.00066844 | 21.787 | 1085.4 | 1063.613
2170 | 0.20429 | 53.71 | 62.393 | 0.00066867 | 21.797 | 1085.4 |  | 2170 | 53.71 | 0.20429 | 62.393 | 0.00066867 | 21.797 | 1085.4 | 1063.603
2171 | 0.20436 | 53.72 | 62.393 | 0.0006689 | 21.807 | 1085.4 |  | 2171 | 53.72 | 0.20436 | 62.393 | 0.0006689 | 21.807 | 1085.4 | 1063.593
2172 | 0.20444 | 53.73 | 62.393 | 0.00066913 | 21.817 | 1085.4 |  | 2172 | 53.73 | 0.20444 | 62.393 | 0.00066913 | 21.817 | 1085.4 | 1063.583
2173 | 0.20451 | 53.74 | 62.393 | 0.00066936 | 21.827 | 1085.4 |  | 2173 | 53.74 | 0.20451 | 62.393 | 0.00066936 | 21.827 | 1085.4 | 1063.573
2174 | 0.20459 | 53.75 | 62.393 | 0.0006696 | 21.837 | 1085.4 |  | 2174 | 53.75 | 0.20459 | 62.393 | 0.0006696 | 21.837 | 1085.4 | 1063.563
2175 | 0.20466 | 53.76 | 62.393 | 0.00066983 | 21.847 | 1085.4 |  | 2175 | 53.76 | 0.20466 | 62.393 | 0.00066983 | 21.847 | 1085.4 | 1063.553
2176 | 0.20474 | 53.77 | 62.393 | 0.00067006 | 21.857 | 1085.4 |  | 2176 | 53.77 | 0.20474 | 62.393 | 0.00067006 | 21.857 | 1085.4 | 1063.543
2177 | 0.20481 | 53.78 | 62.393 | 0.00067029 | 21.867 | 1085.4 |  | 2177 | 53.78 | 0.20481 | 62.393 | 0.00067029 | 21.867 | 1085.4 | 1063.533
2178 | 0.20489 | 53.79 | 62.393 | 0.00067053 | 21.877 | 1085.4 |  | 2178 | 53.79 | 0.20489 | 62.393 | 0.00067053 | 21.877 | 1085.4 | 1063.523
2179 | 0.20496 | 53.8 | 62.393 | 0.00067076 | 21.887 | 1085.4 |  | 2179 | 53.8 | 0.20496 | 62.393 | 0.00067076 | 21.887 | 1085.4 | 1063.513
2180 | 0.20504 | 53.81 | 62.393 | 0.00067099 | 21.897 | 1085.5 |  | 2180 | 53.81 | 0.20504 | 62.393 | 0.00067099 | 21.897 | 1085.5 | 1063.603
2181 | 0.20511 | 53.82 | 62.393 | 0.00067122 | 21.907 | 1085.5 |  | 2181 | 53.82 | 0.20511 | 62.393 | 0.00067122 | 21.907 | 1085.5 | 1063.593
2182 | 0.20519 | 53.83 | 62.393 | 0.00067146 | 21.917 | 1085.5 |  | 2182 | 53.83 | 0.20519 | 62.393 | 0.00067146 | 21.917 | 1085.5 | 1063.583
2183 | 0.20526 | 53.84 | 62.393 | 0.00067169 | 21.927 | 1085.5 |  | 2183 | 53.84 | 0.20526 | 62.393 | 0.00067169 | 21.927 | 1085.5 | 1063.573
2184 | 0.20534 | 53.85 | 62.393 | 0.00067192 | 21.937 | 1085.5 |  | 2184 | 53.85 | 0.20534 | 62.393 | 0.00067192 | 21.937 | 1085.5 | 1063.563
2185 | 0.20541 | 53.86 | 62.393 | 0.00067216 | 21.947 | 1085.5 |  | 2185 | 53.86 | 0.20541 | 62.393 | 0.00067216 | 21.947 | 1085.5 | 1063.553
2186 | 0.20549 | 53.87 | 62.393 | 0.00067239 | 21.957 | 1085.5 |  | 2186 | 53.87 | 0.20549 | 62.393 | 0.00067239 | 21.957 | 1085.5 | 1063.543
2187 | 0.20556 | 53.88 | 62.393 | 0.00067262 | 21.967 | 1085.5 |  | 2187 | 53.88 | 0.20556 | 62.393 | 0.00067262 | 21.967 | 1085.5 | 1063.533
2188 | 0.20564 | 53.89 | 62.393 | 0.00067285 | 21.977 | 1085.5 |  | 2188 | 53.89 | 0.20564 | 62.393 | 0.00067285 | 21.977 | 1085.5 | 1063.523
2189 | 0.20571 | 53.9 | 62.393 | 0.00067309 | 21.987 | 1085.5 |  | 2189 | 53.9 | 0.20571 | 62.393 | 0.00067309 | 21.987 | 1085.5 | 1063.513
2190 | 0.20579 | 53.91 | 62.393 | 0.00067332 | 21.997 | 1085.5 |  | 2190 | 53.91 | 0.20579 | 62.393 | 0.00067332 | 21.997 | 1085.5 | 1063.503
2191 | 0.20586 | 53.92 | 62.393 | 0.00067355 | 22.007 | 1085.5 |  | 2191 | 53.92 | 0.20586 | 62.393 | 0.00067355 | 22.007 | 1085.5 | 1063.493
2192 | 0.20594 | 53.93 | 62.393 | 0.00067379 | 22.017 | 1085.5 |  | 2192 | 53.93 | 0.20594 | 62.393 | 0.00067379 | 22.017 | 1085.5 | 1063.483
2193 | 0.20601 | 53.94 | 62.392 | 0.00067402 | 22.027 | 1085.5 |  | 2193 | 53.94 | 0.20601 | 62.392 | 0.00067402 | 22.027 | 1085.5 | 1063.473
2194 | 0.20609 | 53.95 | 62.392 | 0.00067426 | 22.037 | 1085.5 |  | 2194 | 53.95 | 0.20609 | 62.392 | 0.00067426 | 22.037 | 1085.5 | 1063.463
2195 | 0.20617 | 53.96 | 62.392 | 0.00067449 | 22.047 | 1085.5 |  | 2195 | 53.96 | 0.20617 | 62.392 | 0.00067449 | 22.047 | 1085.5 | 1063.453
2196 | 0.20624 | 53.97 | 62.392 | 0.00067472 | 22.057 | 1085.5 |  | 2196 | 53.97 | 0.20624 | 62.392 | 0.00067472 | 22.057 | 1085.5 | 1063.443
2197 | 0.20632 | 53.98 | 62.392 | 0.00067496 | 22.067 | 1085.5 |  | 2197 | 53.98 | 0.20632 | 62.392 | 0.00067496 | 22.067 | 1085.5 | 1063.433
2198 | 0.20639 | 53.99 | 62.392 | 0.00067519 | 22.077 | 1085.5 |  | 2198 | 53.99 | 0.20639 | 62.392 | 0.00067519 | 22.077 | 1085.5 | 1063.423
2199 | 0.20647 | 54 | 62.392 | 0.00067542 | 22.087 | 1085.5 |  | 2199 | 54 | 0.20647 | 62.392 | 0.00067542 | 22.087 | 1085.5 | 1063.413
2200 | 0.20654 | 54.01 | 62.392 | 0.00067566 | 22.097 | 1085.5 |  | 2200 | 54.01 | 0.20654 | 62.392 | 0.00067566 | 22.097 | 1085.5 | 1063.403
2201 | 0.20662 | 54.02 | 62.392 | 0.00067589 | 22.107 | 1085.5 |  | 2201 | 54.02 | 0.20662 | 62.392 | 0.00067589 | 22.107 | 1085.5 | 1063.393
2202 | 0.20669 | 54.03 | 62.392 | 0.00067613 | 22.118 | 1085.5 |  | 2202 | 54.03 | 0.20669 | 62.392 | 0.00067613 | 22.118 | 1085.5 | 1063.382
2203 | 0.20677 | 54.04 | 62.392 | 0.00067636 | 22.128 | 1085.6 |  | 2203 | 54.04 | 0.20677 | 62.392 | 0.00067636 | 22.128 | 1085.6 | 1063.472
2204 | 0.20685 | 54.05 | 62.392 | 0.0006766 | 22.138 | 1085.6 |  | 2204 | 54.05 | 0.20685 | 62.392 | 0.0006766 | 22.138 | 1085.6 | 1063.462
2205 | 0.20692 | 54.06 | 62.392 | 0.00067683 | 22.148 | 1085.6 |  | 2205 | 54.06 | 0.20692 | 62.392 | 0.00067683 | 22.148 | 1085.6 | 1063.452
2206 | 0.207 | 54.07 | 62.392 | 0.00067706 | 22.158 | 1085.6 |  | 2206 | 54.07 | 0.207 | 62.392 | 0.00067706 | 22.158 | 1085.6 | 1063.442
2207 | 0.20707 | 54.08 | 62.392 | 0.0006773 | 22.168 | 1085.6 |  | 2207 | 54.08 | 0.20707 | 62.392 | 0.0006773 | 22.168 | 1085.6 | 1063.432
2208 | 0.20715 | 54.09 | 62.392 | 0.00067753 | 22.178 | 1085.6 |  | 2208 | 54.09 | 0.20715 | 62.392 | 0.00067753 | 22.178 | 1085.6 | 1063.422
2209 | 0.20722 | 54.1 | 62.392 | 0.00067777 | 22.188 | 1085.6 |  | 2209 | 54.1 | 0.20722 | 62.392 | 0.00067777 | 22.188 | 1085.6 | 1063.412
2210 | 0.2073 | 54.11 | 62.392 | 0.000678 | 22.198 | 1085.6 |  | 2210 | 54.11 | 0.2073 | 62.392 | 0.000678 | 22.198 | 1085.6 | 1063.402
2211 | 0.20738 | 54.12 | 62.392 | 0.00067824 | 22.208 | 1085.6 |  | 2211 | 54.12 | 0.20738 | 62.392 | 0.00067824 | 22.208 | 1085.6 | 1063.392
2212 | 0.20745 | 54.13 | 62.392 | 0.00067847 | 22.218 | 1085.6 |  | 2212 | 54.13 | 0.20745 | 62.392 | 0.00067847 | 22.218 | 1085.6 | 1063.382
2213 | 0.20753 | 54.14 | 62.392 | 0.00067871 | 22.228 | 1085.6 |  | 2213 | 54.14 | 0.20753 | 62.392 | 0.00067871 | 22.228 | 1085.6 | 1063.372
2214 | 0.2076 | 54.15 | 62.392 | 0.00067894 | 22.238 | 1085.6 |  | 2214 | 54.15 | 0.2076 | 62.392 | 0.00067894 | 22.238 | 1085.6 | 1063.362
2215 | 0.20768 | 54.16 | 62.392 | 0.00067918 | 22.248 | 1085.6 |  | 2215 | 54.16 | 0.20768 | 62.392 | 0.00067918 | 22.248 | 1085.6 | 1063.352
2216 | 0.20775 | 54.17 | 62.392 | 0.00067941 | 22.258 | 1085.6 |  | 2216 | 54.17 | 0.20775 | 62.392 | 0.00067941 | 22.258 | 1085.6 | 1063.342
2217 | 0.20783 | 54.18 | 62.391 | 0.00067965 | 22.268 | 1085.6 |  | 2217 | 54.18 | 0.20783 | 62.391 | 0.00067965 | 22.268 | 1085.6 | 1063.332
2218 | 0.20791 | 54.19 | 62.391 | 0.00067988 | 22.278 | 1085.6 |  | 2218 | 54.19 | 0.20791 | 62.391 | 0.00067988 | 22.278 | 1085.6 | 1063.322
2219 | 0.20798 | 54.2 | 62.391 | 0.00068012 | 22.288 | 1085.6 |  | 2219 | 54.2 | 0.20798 | 62.391 | 0.00068012 | 22.288 | 1085.6 | 1063.312
2220 | 0.20806 | 54.21 | 62.391 | 0.00068036 | 22.298 | 1085.6 |  | 2220 | 54.21 | 0.20806 | 62.391 | 0.00068036 | 22.298 | 1085.6 | 1063.302
2221 | 0.20813 | 54.22 | 62.391 | 0.00068059 | 22.308 | 1085.6 |  | 2221 | 54.22 | 0.20813 | 62.391 | 0.00068059 | 22.308 | 1085.6 | 1063.292
2222 | 0.20821 | 54.23 | 62.391 | 0.00068083 | 22.318 | 1085.6 |  | 2222 | 54.23 | 0.20821 | 62.391 | 0.00068083 | 22.318 | 1085.6 | 1063.282
2223 | 0.20829 | 54.24 | 62.391 | 0.00068106 | 22.328 | 1085.6 |  | 2223 | 54.24 | 0.20829 | 62.391 | 0.00068106 | 22.328 | 1085.6 | 1063.272
2224 | 0.20836 | 54.25 | 62.391 | 0.0006813 | 22.338 | 1085.6 |  | 2224 | 54.25 | 0.20836 | 62.391 | 0.0006813 | 22.338 | 1085.6 | 1063.262
2225 | 0.20844 | 54.26 | 62.391 | 0.00068153 | 22.348 | 1085.6 |  | 2225 | 54.26 | 0.20844 | 62.391 | 0.00068153 | 22.348 | 1085.6 | 1063.252
2226 | 0.20851 | 54.27 | 62.391 | 0.00068177 | 22.358 | 1085.7 |  | 2226 | 54.27 | 0.20851 | 62.391 | 0.00068177 | 22.358 | 1085.7 | 1063.342
2227 | 0.20859 | 54.28 | 62.391 | 0.00068201 | 22.368 | 1085.7 |  | 2227 | 54.28 | 0.20859 | 62.391 | 0.00068201 | 22.368 | 1085.7 | 1063.332
2228 | 0.20867 | 54.29 | 62.391 | 0.00068224 | 22.378 | 1085.7 |  | 2228 | 54.29 | 0.20867 | 62.391 | 0.00068224 | 22.378 | 1085.7 | 1063.322
2229 | 0.20874 | 54.3 | 62.391 | 0.00068248 | 22.388 | 1085.7 |  | 2229 | 54.3 | 0.20874 | 62.391 | 0.00068248 | 22.388 | 1085.7 | 1063.312
2230 | 0.20882 | 54.31 | 62.391 | 0.00068271 | 22.398 | 1085.7 |  | 2230 | 54.31 | 0.20882 | 62.391 | 0.00068271 | 22.398 | 1085.7 | 1063.302
2231 | 0.2089 | 54.32 | 62.391 | 0.00068295 | 22.408 | 1085.7 |  | 2231 | 54.32 | 0.2089 | 62.391 | 0.00068295 | 22.408 | 1085.7 | 1063.292
2232 | 0.20897 | 54.33 | 62.391 | 0.00068319 | 22.418 | 1085.7 |  | 2232 | 54.33 | 0.20897 | 62.391 | 0.00068319 | 22.418 | 1085.7 | 1063.282
2233 | 0.20905 | 54.34 | 62.391 | 0.00068342 | 22.428 | 1085.7 |  | 2233 | 54.34 | 0.20905 | 62.391 | 0.00068342 | 22.428 | 1085.7 | 1063.272
2234 | 0.20913 | 54.35 | 62.391 | 0.00068366 | 22.438 | 1085.7 |  | 2234 | 54.35 | 0.20913 | 62.391 | 0.00068366 | 22.438 | 1085.7 | 1063.262
2235 | 0.2092 | 54.36 | 62.391 | 0.0006839 | 22.448 | 1085.7 |  | 2235 | 54.36 | 0.2092 | 62.391 | 0.0006839 | 22.448 | 1085.7 | 1063.252
2236 | 0.20928 | 54.37 | 62.391 | 0.00068413 | 22.458 | 1085.7 |  | 2236 | 54.37 | 0.20928 | 62.391 | 0.00068413 | 22.458 | 1085.7 | 1063.242
2237 | 0.20935 | 54.38 | 62.391 | 0.00068437 | 22.468 | 1085.7 |  | 2237 | 54.38 | 0.20935 | 62.391 | 0.00068437 | 22.468 | 1085.7 | 1063.232
2238 | 0.20943 | 54.39 | 62.391 | 0.00068461 | 22.478 | 1085.7 |  | 2238 | 54.39 | 0.20943 | 62.391 | 0.00068461 | 22.478 | 1085.7 | 1063.222
2239 | 0.20951 | 54.4 | 62.391 | 0.00068484 | 22.488 | 1085.7 |  | 2239 | 54.4 | 0.20951 | 62.391 | 0.00068484 | 22.488 | 1085.7 | 1063.212
2240 | 0.20958 | 54.41 | 62.391 | 0.00068508 | 22.498 | 1085.7 |  | 2240 | 54.41 | 0.20958 | 62.391 | 0.00068508 | 22.498 | 1085.7 | 1063.202
2241 | 0.20966 | 54.42 | 62.39 | 0.00068532 | 22.508 | 1085.7 |  | 2241 | 54.42 | 0.20966 | 62.39 | 0.00068532 | 22.508 | 1085.7 | 1063.192
2242 | 0.20974 | 54.43 | 62.39 | 0.00068555 | 22.518 | 1085.7 |  | 2242 | 54.43 | 0.20974 | 62.39 | 0.00068555 | 22.518 | 1085.7 | 1063.182
2243 | 0.20981 | 54.44 | 62.39 | 0.00068579 | 22.528 | 1085.7 |  | 2243 | 54.44 | 0.20981 | 62.39 | 0.00068579 | 22.528 | 1085.7 | 1063.172
2244 | 0.20989 | 54.45 | 62.39 | 0.00068603 | 22.538 | 1085.7 |  | 2244 | 54.45 | 0.20989 | 62.39 | 0.00068603 | 22.538 | 1085.7 | 1063.162
2245 | 0.20997 | 54.46 | 62.39 | 0.00068627 | 22.548 | 1085.7 |  | 2245 | 54.46 | 0.20997 | 62.39 | 0.00068627 | 22.548 | 1085.7 | 1063.152
2246 | 0.21004 | 54.47 | 62.39 | 0.0006865 | 22.558 | 1085.7 |  | 2246 | 54.47 | 0.21004 | 62.39 | 0.0006865 | 22.558 | 1085.7 | 1063.142
2247 | 0.21012 | 54.48 | 62.39 | 0.00068674 | 22.568 | 1085.7 |  | 2247 | 54.48 | 0.21012 | 62.39 | 0.00068674 | 22.568 | 1085.7 | 1063.132
2248 | 0.2102 | 54.49 | 62.39 | 0.00068698 | 22.578 | 1085.7 |  | 2248 | 54.49 | 0.2102 | 62.39 | 0.00068698 | 22.578 | 1085.7 | 1063.122
2249 | 0.21027 | 54.5 | 62.39 | 0.00068722 | 22.588 | 1085.8 |  | 2249 | 54.5 | 0.21027 | 62.39 | 0.00068722 | 22.588 | 1085.8 | 1063.212
2250 | 0.21035 | 54.51 | 62.39 | 0.00068745 | 22.598 | 1085.8 |  | 2250 | 54.51 | 0.21035 | 62.39 | 0.00068745 | 22.598 | 1085.8 | 1063.202
2251 | 0.21043 | 54.52 | 62.39 | 0.00068769 | 22.608 | 1085.8 |  | 2251 | 54.52 | 0.21043 | 62.39 | 0.00068769 | 22.608 | 1085.8 | 1063.192
2252 | 0.2105 | 54.53 | 62.39 | 0.00068793 | 22.618 | 1085.8 |  | 2252 | 54.53 | 0.2105 | 62.39 | 0.00068793 | 22.618 | 1085.8 | 1063.182
2253 | 0.21058 | 54.54 | 62.39 | 0.00068817 | 22.629 | 1085.8 |  | 2253 | 54.54 | 0.21058 | 62.39 | 0.00068817 | 22.629 | 1085.8 | 1063.171
2254 | 0.21066 | 54.55 | 62.39 | 0.0006884 | 22.639 | 1085.8 |  | 2254 | 54.55 | 0.21066 | 62.39 | 0.0006884 | 22.639 | 1085.8 | 1063.161
2255 | 0.21073 | 54.56 | 62.39 | 0.00068864 | 22.649 | 1085.8 |  | 2255 | 54.56 | 0.21073 | 62.39 | 0.00068864 | 22.649 | 1085.8 | 1063.151
2256 | 0.21081 | 54.57 | 62.39 | 0.00068888 | 22.659 | 1085.8 |  | 2256 | 54.57 | 0.21081 | 62.39 | 0.00068888 | 22.659 | 1085.8 | 1063.141
2257 | 0.21089 | 54.58 | 62.39 | 0.00068912 | 22.669 | 1085.8 |  | 2257 | 54.58 | 0.21089 | 62.39 | 0.00068912 | 22.669 | 1085.8 | 1063.131
2258 | 0.21097 | 54.59 | 62.39 | 0.00068936 | 22.679 | 1085.8 |  | 2258 | 54.59 | 0.21097 | 62.39 | 0.00068936 | 22.679 | 1085.8 | 1063.121
2259 | 0.21104 | 54.6 | 62.39 | 0.00068959 | 22.689 | 1085.8 |  | 2259 | 54.6 | 0.21104 | 62.39 | 0.00068959 | 22.689 | 1085.8 | 1063.111
2260 | 0.21112 | 54.61 | 62.39 | 0.00068983 | 22.699 | 1085.8 |  | 2260 | 54.61 | 0.21112 | 62.39 | 0.00068983 | 22.699 | 1085.8 | 1063.101
2261 | 0.2112 | 54.62 | 62.39 | 0.00069007 | 22.709 | 1085.8 |  | 2261 | 54.62 | 0.2112 | 62.39 | 0.00069007 | 22.709 | 1085.8 | 1063.091
2262 | 0.21127 | 54.63 | 62.39 | 0.00069031 | 22.719 | 1085.8 |  | 2262 | 54.63 | 0.21127 | 62.39 | 0.00069031 | 22.719 | 1085.8 | 1063.081
2263 | 0.21135 | 54.64 | 62.39 | 0.00069055 | 22.729 | 1085.8 |  | 2263 | 54.64 | 0.21135 | 62.39 | 0.00069055 | 22.729 | 1085.8 | 1063.071
2264 | 0.21143 | 54.65 | 62.39 | 0.00069079 | 22.739 | 1085.8 |  | 2264 | 54.65 | 0.21143 | 62.39 | 0.00069079 | 22.739 | 1085.8 | 1063.061
2265 | 0.2115 | 54.66 | 62.389 | 0.00069103 | 22.749 | 1085.8 |  | 2265 | 54.66 | 0.2115 | 62.389 | 0.00069103 | 22.749 | 1085.8 | 1063.051
2266 | 0.21158 | 54.67 | 62.389 | 0.00069126 | 22.759 | 1085.8 |  | 2266 | 54.67 | 0.21158 | 62.389 | 0.00069126 | 22.759 | 1085.8 | 1063.041
2267 | 0.21166 | 54.68 | 62.389 | 0.0006915 | 22.769 | 1085.8 |  | 2267 | 54.68 | 0.21166 | 62.389 | 0.0006915 | 22.769 | 1085.8 | 1063.031
2268 | 0.21174 | 54.69 | 62.389 | 0.00069174 | 22.779 | 1085.8 |  | 2268 | 54.69 | 0.21174 | 62.389 | 0.00069174 | 22.779 | 1085.8 | 1063.021
2269 | 0.21181 | 54.7 | 62.389 | 0.00069198 | 22.789 | 1085.8 |  | 2269 | 54.7 | 0.21181 | 62.389 | 0.00069198 | 22.789 | 1085.8 | 1063.011
2270 | 0.21189 | 54.71 | 62.389 | 0.00069222 | 22.799 | 1085.8 |  | 2270 | 54.71 | 0.21189 | 62.389 | 0.00069222 | 22.799 | 1085.8 | 1063.001
2271 | 0.21197 | 54.72 | 62.389 | 0.00069246 | 22.809 | 1085.8 |  | 2271 | 54.72 | 0.21197 | 62.389 | 0.00069246 | 22.809 | 1085.8 | 1062.991
2272 | 0.21204 | 54.73 | 62.389 | 0.0006927 | 22.819 | 1085.9 |  | 2272 | 54.73 | 0.21204 | 62.389 | 0.0006927 | 22.819 | 1085.9 | 1063.081
2273 | 0.21212 | 54.74 | 62.389 | 0.00069294 | 22.829 | 1085.9 |  | 2273 | 54.74 | 0.21212 | 62.389 | 0.00069294 | 22.829 | 1085.9 | 1063.071
2274 | 0.2122 | 54.75 | 62.389 | 0.00069318 | 22.839 | 1085.9 |  | 2274 | 54.75 | 0.2122 | 62.389 | 0.00069318 | 22.839 | 1085.9 | 1063.061
2275 | 0.21228 | 54.76 | 62.389 | 0.00069342 | 22.849 | 1085.9 |  | 2275 | 54.76 | 0.21228 | 62.389 | 0.00069342 | 22.849 | 1085.9 | 1063.051
2276 | 0.21235 | 54.77 | 62.389 | 0.00069366 | 22.859 | 1085.9 |  | 2276 | 54.77 | 0.21235 | 62.389 | 0.00069366 | 22.859 | 1085.9 | 1063.041
2277 | 0.21243 | 54.78 | 62.389 | 0.0006939 | 22.869 | 1085.9 |  | 2277 | 54.78 | 0.21243 | 62.389 | 0.0006939 | 22.869 | 1085.9 | 1063.031
2278 | 0.21251 | 54.79 | 62.389 | 0.00069414 | 22.879 | 1085.9 |  | 2278 | 54.79 | 0.21251 | 62.389 | 0.00069414 | 22.879 | 1085.9 | 1063.021
2279 | 0.21259 | 54.8 | 62.389 | 0.00069438 | 22.889 | 1085.9 |  | 2279 | 54.8 | 0.21259 | 62.389 | 0.00069438 | 22.889 | 1085.9 | 1063.011
2280 | 0.21266 | 54.81 | 62.389 | 0.00069462 | 22.899 | 1085.9 |  | 2280 | 54.81 | 0.21266 | 62.389 | 0.00069462 | 22.899 | 1085.9 | 1063.001
2281 | 0.21274 | 54.82 | 62.389 | 0.00069486 | 22.909 | 1085.9 |  | 2281 | 54.82 | 0.21274 | 62.389 | 0.00069486 | 22.909 | 1085.9 | 1062.991
2282 | 0.21282 | 54.83 | 62.389 | 0.00069509 | 22.919 | 1085.9 |  | 2282 | 54.83 | 0.21282 | 62.389 | 0.00069509 | 22.919 | 1085.9 | 1062.981
2283 | 0.2129 | 54.84 | 62.389 | 0.00069533 | 22.929 | 1085.9 |  | 2283 | 54.84 | 0.2129 | 62.389 | 0.00069533 | 22.929 | 1085.9 | 1062.971
2284 | 0.21297 | 54.85 | 62.389 | 0.00069557 | 22.939 | 1085.9 |  | 2284 | 54.85 | 0.21297 | 62.389 | 0.00069557 | 22.939 | 1085.9 | 1062.961
2285 | 0.21305 | 54.86 | 62.389 | 0.00069582 | 22.949 | 1085.9 |  | 2285 | 54.86 | 0.21305 | 62.389 | 0.00069582 | 22.949 | 1085.9 | 1062.951
2286 | 0.21313 | 54.87 | 62.389 | 0.00069606 | 22.959 | 1085.9 |  | 2286 | 54.87 | 0.21313 | 62.389 | 0.00069606 | 22.959 | 1085.9 | 1062.941
2287 | 0.21321 | 54.88 | 62.389 | 0.0006963 | 22.969 | 1085.9 |  | 2287 | 54.88 | 0.21321 | 62.389 | 0.0006963 | 22.969 | 1085.9 | 1062.931
2288 | 0.21329 | 54.89 | 62.389 | 0.00069654 | 22.979 | 1085.9 |  | 2288 | 54.89 | 0.21329 | 62.389 | 0.00069654 | 22.979 | 1085.9 | 1062.921
2289 | 0.21336 | 54.9 | 62.388 | 0.00069678 | 22.989 | 1085.9 |  | 2289 | 54.9 | 0.21336 | 62.388 | 0.00069678 | 22.989 | 1085.9 | 1062.911
2290 | 0.21344 | 54.91 | 62.388 | 0.00069702 | 22.999 | 1085.9 |  | 2290 | 54.91 | 0.21344 | 62.388 | 0.00069702 | 22.999 | 1085.9 | 1062.901
2291 | 0.21352 | 54.92 | 62.388 | 0.00069726 | 23.009 | 1085.9 |  | 2291 | 54.92 | 0.21352 | 62.388 | 0.00069726 | 23.009 | 1085.9 | 1062.891
2292 | 0.2136 | 54.93 | 62.388 | 0.0006975 | 23.019 | 1085.9 |  | 2292 | 54.93 | 0.2136 | 62.388 | 0.0006975 | 23.019 | 1085.9 | 1062.881
2293 | 0.21367 | 54.94 | 62.388 | 0.00069774 | 23.029 | 1085.9 |  | 2293 | 54.94 | 0.21367 | 62.388 | 0.00069774 | 23.029 | 1085.9 | 1062.871
2294 | 0.21375 | 54.95 | 62.388 | 0.00069798 | 23.039 | 1085.9 |  | 2294 | 54.95 | 0.21375 | 62.388 | 0.00069798 | 23.039 | 1085.9 | 1062.861
2295 | 0.21383 | 54.96 | 62.388 | 0.00069822 | 23.049 | 1086 |  | 2295 | 54.96 | 0.21383 | 62.388 | 0.00069822 | 23.049 | 1086 | 1062.951
2296 | 0.21391 | 54.97 | 62.388 | 0.00069846 | 23.059 | 1086 |  | 2296 | 54.97 | 0.21391 | 62.388 | 0.00069846 | 23.059 | 1086 | 1062.941
2297 | 0.21399 | 54.98 | 62.388 | 0.0006987 | 23.069 | 1086 |  | 2297 | 54.98 | 0.21399 | 62.388 | 0.0006987 | 23.069 | 1086 | 1062.931
2298 | 0.21406 | 54.99 | 62.388 | 0.00069894 | 23.079 | 1086 |  | 2298 | 54.99 | 0.21406 | 62.388 | 0.00069894 | 23.079 | 1086 | 1062.921
2299 | 0.21414 | 55 | 62.388 | 0.00069918 | 23.089 | 1086 |  | 2299 | 55 | 0.21414 | 62.388 | 0.00069918 | 23.089 | 1086 | 1062.911
2300 | 0.21422 | 55.01 | 62.388 | 0.00069943 | 23.099 | 1086 |  | 2300 | 55.01 | 0.21422 | 62.388 | 0.00069943 | 23.099 | 1086 | 1062.901
2301 | 0.2143 | 55.02 | 62.388 | 0.00069967 | 23.109 | 1086 |  | 2301 | 55.02 | 0.2143 | 62.388 | 0.00069967 | 23.109 | 1086 | 1062.891
2302 | 0.21438 | 55.03 | 62.388 | 0.00069991 | 23.119 | 1086 |  | 2302 | 55.03 | 0.21438 | 62.388 | 0.00069991 | 23.119 | 1086 | 1062.881
2303 | 0.21445 | 55.04 | 62.388 | 0.00070015 | 23.129 | 1086 |  | 2303 | 55.04 | 0.21445 | 62.388 | 0.00070015 | 23.129 | 1086 | 1062.871
2304 | 0.21453 | 55.05 | 62.388 | 0.00070039 | 23.139 | 1086 |  | 2304 | 55.05 | 0.21453 | 62.388 | 0.00070039 | 23.139 | 1086 | 1062.861
2305 | 0.21461 | 55.06 | 62.388 | 0.00070063 | 23.149 | 1086 |  | 2305 | 55.06 | 0.21461 | 62.388 | 0.00070063 | 23.149 | 1086 | 1062.851
2306 | 0.21469 | 55.07 | 62.388 | 0.00070087 | 23.159 | 1086 |  | 2306 | 55.07 | 0.21469 | 62.388 | 0.00070087 | 23.159 | 1086 | 1062.841
2307 | 0.21477 | 55.08 | 62.388 | 0.00070112 | 23.169 | 1086 |  | 2307 | 55.08 | 0.21477 | 62.388 | 0.00070112 | 23.169 | 1086 | 1062.831
2308 | 0.21484 | 55.09 | 62.388 | 0.00070136 | 23.18 | 1086 |  | 2308 | 55.09 | 0.21484 | 62.388 | 0.00070136 | 23.18 | 1086 | 1062.82
2309 | 0.21492 | 55.1 | 62.388 | 0.0007016 | 23.19 | 1086 |  | 2309 | 55.1 | 0.21492 | 62.388 | 0.0007016 | 23.19 | 1086 | 1062.81
2310 | 0.215 | 55.11 | 62.388 | 0.00070184 | 23.2 | 1086 |  | 2310 | 55.11 | 0.215 | 62.388 | 0.00070184 | 23.2 | 1086 | 1062.8
2311 | 0.21508 | 55.12 | 62.388 | 0.00070208 | 23.21 | 1086 |  | 2311 | 55.12 | 0.21508 | 62.388 | 0.00070208 | 23.21 | 1086 | 1062.79
2312 | 0.21516 | 55.13 | 62.387 | 0.00070233 | 23.22 | 1086 |  | 2312 | 55.13 | 0.21516 | 62.387 | 0.00070233 | 23.22 | 1086 | 1062.78
2313 | 0.21524 | 55.14 | 62.387 | 0.00070257 | 23.23 | 1086 |  | 2313 | 55.14 | 0.21524 | 62.387 | 0.00070257 | 23.23 | 1086 | 1062.77
2314 | 0.21531 | 55.15 | 62.387 | 0.00070281 | 23.24 | 1086 |  | 2314 | 55.15 | 0.21531 | 62.387 | 0.00070281 | 23.24 | 1086 | 1062.76
2315 | 0.21539 | 55.16 | 62.387 | 0.00070305 | 23.25 | 1086 |  | 2315 | 55.16 | 0.21539 | 62.387 | 0.00070305 | 23.25 | 1086 | 1062.75
2316 | 0.21547 | 55.17 | 62.387 | 0.0007033 | 23.26 | 1086 |  | 2316 | 55.17 | 0.21547 | 62.387 | 0.0007033 | 23.26 | 1086 | 1062.74
2317 | 0.21555 | 55.18 | 62.387 | 0.00070354 | 23.27 | 1086.1 |  | 2317 | 55.18 | 0.21555 | 62.387 | 0.00070354 | 23.27 | 1086.1 | 1062.83
2318 | 0.21563 | 55.19 | 62.387 | 0.00070378 | 23.28 | 1086.1 |  | 2318 | 55.19 | 0.21563 | 62.387 | 0.00070378 | 23.28 | 1086.1 | 1062.82
2319 | 0.21571 | 55.2 | 62.387 | 0.00070402 | 23.29 | 1086.1 |  | 2319 | 55.2 | 0.21571 | 62.387 | 0.00070402 | 23.29 | 1086.1 | 1062.81
2320 | 0.21578 | 55.21 | 62.387 | 0.00070427 | 23.3 | 1086.1 |  | 2320 | 55.21 | 0.21578 | 62.387 | 0.00070427 | 23.3 | 1086.1 | 1062.8
2321 | 0.21586 | 55.22 | 62.387 | 0.00070451 | 23.31 | 1086.1 |  | 2321 | 55.22 | 0.21586 | 62.387 | 0.00070451 | 23.31 | 1086.1 | 1062.79
2322 | 0.21594 | 55.23 | 62.387 | 0.00070475 | 23.32 | 1086.1 |  | 2322 | 55.23 | 0.21594 | 62.387 | 0.00070475 | 23.32 | 1086.1 | 1062.78
2323 | 0.21602 | 55.24 | 62.387 | 0.00070499 | 23.33 | 1086.1 |  | 2323 | 55.24 | 0.21602 | 62.387 | 0.00070499 | 23.33 | 1086.1 | 1062.77
2324 | 0.2161 | 55.25 | 62.387 | 0.00070524 | 23.34 | 1086.1 |  | 2324 | 55.25 | 0.2161 | 62.387 | 0.00070524 | 23.34 | 1086.1 | 1062.76
2325 | 0.21618 | 55.26 | 62.387 | 0.00070548 | 23.35 | 1086.1 |  | 2325 | 55.26 | 0.21618 | 62.387 | 0.00070548 | 23.35 | 1086.1 | 1062.75
2326 | 0.21626 | 55.27 | 62.387 | 0.00070572 | 23.36 | 1086.1 |  | 2326 | 55.27 | 0.21626 | 62.387 | 0.00070572 | 23.36 | 1086.1 | 1062.74
2327 | 0.21633 | 55.28 | 62.387 | 0.00070597 | 23.37 | 1086.1 |  | 2327 | 55.28 | 0.21633 | 62.387 | 0.00070597 | 23.37 | 1086.1 | 1062.73
2328 | 0.21641 | 55.29 | 62.387 | 0.00070621 | 23.38 | 1086.1 |  | 2328 | 55.29 | 0.21641 | 62.387 | 0.00070621 | 23.38 | 1086.1 | 1062.72
2329 | 0.21649 | 55.3 | 62.387 | 0.00070645 | 23.39 | 1086.1 |  | 2329 | 55.3 | 0.21649 | 62.387 | 0.00070645 | 23.39 | 1086.1 | 1062.71
2330 | 0.21657 | 55.31 | 62.387 | 0.0007067 | 23.4 | 1086.1 |  | 2330 | 55.31 | 0.21657 | 62.387 | 0.0007067 | 23.4 | 1086.1 | 1062.7
2331 | 0.21665 | 55.32 | 62.387 | 0.00070694 | 23.41 | 1086.1 |  | 2331 | 55.32 | 0.21665 | 62.387 | 0.00070694 | 23.41 | 1086.1 | 1062.69
2332 | 0.21673 | 55.33 | 62.387 | 0.00070718 | 23.42 | 1086.1 |  | 2332 | 55.33 | 0.21673 | 62.387 | 0.00070718 | 23.42 | 1086.1 | 1062.68
2333 | 0.21681 | 55.34 | 62.387 | 0.00070743 | 23.43 | 1086.1 |  | 2333 | 55.34 | 0.21681 | 62.387 | 0.00070743 | 23.43 | 1086.1 | 1062.67
2334 | 0.21689 | 55.35 | 62.387 | 0.00070767 | 23.44 | 1086.1 |  | 2334 | 55.35 | 0.21689 | 62.387 | 0.00070767 | 23.44 | 1086.1 | 1062.66
2335 | 0.21696 | 55.36 | 62.386 | 0.00070791 | 23.45 | 1086.1 |  | 2335 | 55.36 | 0.21696 | 62.386 | 0.00070791 | 23.45 | 1086.1 | 1062.65
2336 | 0.21704 | 55.37 | 62.386 | 0.00070816 | 23.46 | 1086.1 |  | 2336 | 55.37 | 0.21704 | 62.386 | 0.00070816 | 23.46 | 1086.1 | 1062.64
2337 | 0.21712 | 55.38 | 62.386 | 0.0007084 | 23.47 | 1086.1 |  | 2337 | 55.38 | 0.21712 | 62.386 | 0.0007084 | 23.47 | 1086.1 | 1062.63
2338 | 0.2172 | 55.39 | 62.386 | 0.00070865 | 23.48 | 1086.1 |  | 2338 | 55.39 | 0.2172 | 62.386 | 0.00070865 | 23.48 | 1086.1 | 1062.62
2339 | 0.21728 | 55.4 | 62.386 | 0.00070889 | 23.49 | 1086.1 |  | 2339 | 55.4 | 0.21728 | 62.386 | 0.00070889 | 23.49 | 1086.1 | 1062.61
2340 | 0.21736 | 55.41 | 62.386 | 0.00070913 | 23.5 | 1086.2 |  | 2340 | 55.41 | 0.21736 | 62.386 | 0.00070913 | 23.5 | 1086.2 | 1062.7
2341 | 0.21744 | 55.42 | 62.386 | 0.00070938 | 23.51 | 1086.2 |  | 2341 | 55.42 | 0.21744 | 62.386 | 0.00070938 | 23.51 | 1086.2 | 1062.69
2342 | 0.21752 | 55.43 | 62.386 | 0.00070962 | 23.52 | 1086.2 |  | 2342 | 55.43 | 0.21752 | 62.386 | 0.00070962 | 23.52 | 1086.2 | 1062.68
2343 | 0.2176 | 55.44 | 62.386 | 0.00070987 | 23.53 | 1086.2 |  | 2343 | 55.44 | 0.2176 | 62.386 | 0.00070987 | 23.53 | 1086.2 | 1062.67
2344 | 0.21768 | 55.45 | 62.386 | 0.00071011 | 23.54 | 1086.2 |  | 2344 | 55.45 | 0.21768 | 62.386 | 0.00071011 | 23.54 | 1086.2 | 1062.66
2345 | 0.21775 | 55.46 | 62.386 | 0.00071036 | 23.55 | 1086.2 |  | 2345 | 55.46 | 0.21775 | 62.386 | 0.00071036 | 23.55 | 1086.2 | 1062.65
2346 | 0.21783 | 55.47 | 62.386 | 0.0007106 | 23.56 | 1086.2 |  | 2346 | 55.47 | 0.21783 | 62.386 | 0.0007106 | 23.56 | 1086.2 | 1062.64
2347 | 0.21791 | 55.48 | 62.386 | 0.00071084 | 23.57 | 1086.2 |  | 2347 | 55.48 | 0.21791 | 62.386 | 0.00071084 | 23.57 | 1086.2 | 1062.63
2348 | 0.21799 | 55.49 | 62.386 | 0.00071109 | 23.58 | 1086.2 |  | 2348 | 55.49 | 0.21799 | 62.386 | 0.00071109 | 23.58 | 1086.2 | 1062.62
2349 | 0.21807 | 55.5 | 62.386 | 0.00071133 | 23.59 | 1086.2 |  | 2349 | 55.5 | 0.21807 | 62.386 | 0.00071133 | 23.59 | 1086.2 | 1062.61
2350 | 0.21815 | 55.51 | 62.386 | 0.00071158 | 23.6 | 1086.2 |  | 2350 | 55.51 | 0.21815 | 62.386 | 0.00071158 | 23.6 | 1086.2 | 1062.6
2351 | 0.21823 | 55.52 | 62.386 | 0.00071182 | 23.61 | 1086.2 |  | 2351 | 55.52 | 0.21823 | 62.386 | 0.00071182 | 23.61 | 1086.2 | 1062.59
2352 | 0.21831 | 55.53 | 62.386 | 0.00071207 | 23.62 | 1086.2 |  | 2352 | 55.53 | 0.21831 | 62.386 | 0.00071207 | 23.62 | 1086.2 | 1062.58
2353 | 0.21839 | 55.54 | 62.386 | 0.00071231 | 23.63 | 1086.2 |  | 2353 | 55.54 | 0.21839 | 62.386 | 0.00071231 | 23.63 | 1086.2 | 1062.57
2354 | 0.21847 | 55.55 | 62.386 | 0.00071256 | 23.64 | 1086.2 |  | 2354 | 55.55 | 0.21847 | 62.386 | 0.00071256 | 23.64 | 1086.2 | 1062.56
2355 | 0.21855 | 55.56 | 62.386 | 0.0007128 | 23.65 | 1086.2 |  | 2355 | 55.56 | 0.21855 | 62.386 | 0.0007128 | 23.65 | 1086.2 | 1062.55
2356 | 0.21863 | 55.57 | 62.386 | 0.00071305 | 23.66 | 1086.2 |  | 2356 | 55.57 | 0.21863 | 62.386 | 0.00071305 | 23.66 | 1086.2 | 1062.54
2357 | 0.21871 | 55.58 | 62.386 | 0.0007133 | 23.67 | 1086.2 |  | 2357 | 55.58 | 0.21871 | 62.386 | 0.0007133 | 23.67 | 1086.2 | 1062.53
2358 | 0.21879 | 55.59 | 62.385 | 0.00071354 | 23.68 | 1086.2 |  | 2358 | 55.59 | 0.21879 | 62.385 | 0.00071354 | 23.68 | 1086.2 | 1062.52
2359 | 0.21887 | 55.6 | 62.385 | 0.00071379 | 23.69 | 1086.2 |  | 2359 | 55.6 | 0.21887 | 62.385 | 0.00071379 | 23.69 | 1086.2 | 1062.51
2360 | 0.21894 | 55.61 | 62.385 | 0.00071403 | 23.7 | 1086.2 |  | 2360 | 55.61 | 0.21894 | 62.385 | 0.00071403 | 23.7 | 1086.2 | 1062.5
2361 | 0.21902 | 55.62 | 62.385 | 0.00071428 | 23.71 | 1086.2 |  | 2361 | 55.62 | 0.21902 | 62.385 | 0.00071428 | 23.71 | 1086.2 | 1062.49
2362 | 0.2191 | 55.63 | 62.385 | 0.00071452 | 23.72 | 1086.2 |  | 2362 | 55.63 | 0.2191 | 62.385 | 0.00071452 | 23.72 | 1086.2 | 1062.48
2363 | 0.21918 | 55.64 | 62.385 | 0.00071477 | 23.73 | 1086.3 |  | 2363 | 55.64 | 0.21918 | 62.385 | 0.00071477 | 23.73 | 1086.3 | 1062.57
2364 | 0.21926 | 55.65 | 62.385 | 0.00071501 | 23.74 | 1086.3 |  | 2364 | 55.65 | 0.21926 | 62.385 | 0.00071501 | 23.74 | 1086.3 | 1062.56
2365 | 0.21934 | 55.66 | 62.385 | 0.00071526 | 23.751 | 1086.3 |  | 2365 | 55.66 | 0.21934 | 62.385 | 0.00071526 | 23.751 | 1086.3 | 1062.549
2366 | 0.21942 | 55.67 | 62.385 | 0.00071551 | 23.761 | 1086.3 |  | 2366 | 55.67 | 0.21942 | 62.385 | 0.00071551 | 23.761 | 1086.3 | 1062.539
2367 | 0.2195 | 55.68 | 62.385 | 0.00071575 | 23.771 | 1086.3 |  | 2367 | 55.68 | 0.2195 | 62.385 | 0.00071575 | 23.771 | 1086.3 | 1062.529
2368 | 0.21958 | 55.69 | 62.385 | 0.000716 | 23.781 | 1086.3 |  | 2368 | 55.69 | 0.21958 | 62.385 | 0.000716 | 23.781 | 1086.3 | 1062.519
2369 | 0.21966 | 55.7 | 62.385 | 0.00071625 | 23.791 | 1086.3 |  | 2369 | 55.7 | 0.21966 | 62.385 | 0.00071625 | 23.791 | 1086.3 | 1062.509
2370 | 0.21974 | 55.71 | 62.385 | 0.00071649 | 23.801 | 1086.3 |  | 2370 | 55.71 | 0.21974 | 62.385 | 0.00071649 | 23.801 | 1086.3 | 1062.499
2371 | 0.21982 | 55.72 | 62.385 | 0.00071674 | 23.811 | 1086.3 |  | 2371 | 55.72 | 0.21982 | 62.385 | 0.00071674 | 23.811 | 1086.3 | 1062.489
2372 | 0.2199 | 55.73 | 62.385 | 0.00071698 | 23.821 | 1086.3 |  | 2372 | 55.73 | 0.2199 | 62.385 | 0.00071698 | 23.821 | 1086.3 | 1062.479
2373 | 0.21998 | 55.74 | 62.385 | 0.00071723 | 23.831 | 1086.3 |  | 2373 | 55.74 | 0.21998 | 62.385 | 0.00071723 | 23.831 | 1086.3 | 1062.469
2374 | 0.22006 | 55.75 | 62.385 | 0.00071748 | 23.841 | 1086.3 |  | 2374 | 55.75 | 0.22006 | 62.385 | 0.00071748 | 23.841 | 1086.3 | 1062.459
2375 | 0.22014 | 55.76 | 62.385 | 0.00071772 | 23.851 | 1086.3 |  | 2375 | 55.76 | 0.22014 | 62.385 | 0.00071772 | 23.851 | 1086.3 | 1062.449
2376 | 0.22022 | 55.77 | 62.385 | 0.00071797 | 23.861 | 1086.3 |  | 2376 | 55.77 | 0.22022 | 62.385 | 0.00071797 | 23.861 | 1086.3 | 1062.439
2377 | 0.2203 | 55.78 | 62.385 | 0.00071822 | 23.871 | 1086.3 |  | 2377 | 55.78 | 0.2203 | 62.385 | 0.00071822 | 23.871 | 1086.3 | 1062.429
2378 | 0.22038 | 55.79 | 62.385 | 0.00071847 | 23.881 | 1086.3 |  | 2378 | 55.79 | 0.22038 | 62.385 | 0.00071847 | 23.881 | 1086.3 | 1062.419
2379 | 0.22046 | 55.8 | 62.385 | 0.00071871 | 23.891 | 1086.3 |  | 2379 | 55.8 | 0.22046 | 62.385 | 0.00071871 | 23.891 | 1086.3 | 1062.409
2380 | 0.22054 | 55.81 | 62.385 | 0.00071896 | 23.901 | 1086.3 |  | 2380 | 55.81 | 0.22054 | 62.385 | 0.00071896 | 23.901 | 1086.3 | 1062.399
2381 | 0.22062 | 55.82 | 62.384 | 0.00071921 | 23.911 | 1086.3 |  | 2381 | 55.82 | 0.22062 | 62.384 | 0.00071921 | 23.911 | 1086.3 | 1062.389
2382 | 0.2207 | 55.83 | 62.384 | 0.00071945 | 23.921 | 1086.3 |  | 2382 | 55.83 | 0.2207 | 62.384 | 0.00071945 | 23.921 | 1086.3 | 1062.379
2383 | 0.22078 | 55.84 | 62.384 | 0.0007197 | 23.931 | 1086.3 |  | 2383 | 55.84 | 0.22078 | 62.384 | 0.0007197 | 23.931 | 1086.3 | 1062.369
2384 | 0.22086 | 55.85 | 62.384 | 0.00071995 | 23.941 | 1086.3 |  | 2384 | 55.85 | 0.22086 | 62.384 | 0.00071995 | 23.941 | 1086.3 | 1062.359
2385 | 0.22094 | 55.86 | 62.384 | 0.0007202 | 23.951 | 1086.3 |  | 2385 | 55.86 | 0.22094 | 62.384 | 0.0007202 | 23.951 | 1086.3 | 1062.349
2386 | 0.22102 | 55.87 | 62.384 | 0.00072044 | 23.961 | 1086.4 |  | 2386 | 55.87 | 0.22102 | 62.384 | 0.00072044 | 23.961 | 1086.4 | 1062.439
2387 | 0.2211 | 55.88 | 62.384 | 0.00072069 | 23.971 | 1086.4 |  | 2387 | 55.88 | 0.2211 | 62.384 | 0.00072069 | 23.971 | 1086.4 | 1062.429
2388 | 0.22118 | 55.89 | 62.384 | 0.00072094 | 23.981 | 1086.4 |  | 2388 | 55.89 | 0.22118 | 62.384 | 0.00072094 | 23.981 | 1086.4 | 1062.419
2389 | 0.22126 | 55.9 | 62.384 | 0.00072119 | 23.991 | 1086.4 |  | 2389 | 55.9 | 0.22126 | 62.384 | 0.00072119 | 23.991 | 1086.4 | 1062.409
2390 | 0.22134 | 55.91 | 62.384 | 0.00072143 | 24.001 | 1086.4 |  | 2390 | 55.91 | 0.22134 | 62.384 | 0.00072143 | 24.001 | 1086.4 | 1062.399
2391 | 0.22142 | 55.92 | 62.384 | 0.00072168 | 24.011 | 1086.4 |  | 2391 | 55.92 | 0.22142 | 62.384 | 0.00072168 | 24.011 | 1086.4 | 1062.389
2392 | 0.2215 | 55.93 | 62.384 | 0.00072193 | 24.021 | 1086.4 |  | 2392 | 55.93 | 0.2215 | 62.384 | 0.00072193 | 24.021 | 1086.4 | 1062.379
2393 | 0.22158 | 55.94 | 62.384 | 0.00072218 | 24.031 | 1086.4 |  | 2393 | 55.94 | 0.22158 | 62.384 | 0.00072218 | 24.031 | 1086.4 | 1062.369
2394 | 0.22166 | 55.95 | 62.384 | 0.00072243 | 24.041 | 1086.4 |  | 2394 | 55.95 | 0.22166 | 62.384 | 0.00072243 | 24.041 | 1086.4 | 1062.359
2395 | 0.22174 | 55.96 | 62.384 | 0.00072267 | 24.051 | 1086.4 |  | 2395 | 55.96 | 0.22174 | 62.384 | 0.00072267 | 24.051 | 1086.4 | 1062.349
2396 | 0.22182 | 55.97 | 62.384 | 0.00072292 | 24.061 | 1086.4 |  | 2396 | 55.97 | 0.22182 | 62.384 | 0.00072292 | 24.061 | 1086.4 | 1062.339
2397 | 0.2219 | 55.98 | 62.384 | 0.00072317 | 24.071 | 1086.4 |  | 2397 | 55.98 | 0.2219 | 62.384 | 0.00072317 | 24.071 | 1086.4 | 1062.329
2398 | 0.22198 | 55.99 | 62.384 | 0.00072342 | 24.081 | 1086.4 |  | 2398 | 55.99 | 0.22198 | 62.384 | 0.00072342 | 24.081 | 1086.4 | 1062.319
2399 | 0.22207 | 56 | 62.384 | 0.00072367 | 24.091 | 1086.4 |  | 2399 | 56 | 0.22207 | 62.384 | 0.00072367 | 24.091 | 1086.4 | 1062.309
2400 | 0.22215 | 56.01 | 62.384 | 0.00072392 | 24.101 | 1086.4 |  | 2400 | 56.01 | 0.22215 | 62.384 | 0.00072392 | 24.101 | 1086.4 | 1062.299
2401 | 0.22223 | 56.02 | 62.384 | 0.00072416 | 24.111 | 1086.4 |  | 2401 | 56.02 | 0.22223 | 62.384 | 0.00072416 | 24.111 | 1086.4 | 1062.289
2402 | 0.22231 | 56.03 | 62.384 | 0.00072441 | 24.121 | 1086.4 |  | 2402 | 56.03 | 0.22231 | 62.384 | 0.00072441 | 24.121 | 1086.4 | 1062.279
2403 | 0.22239 | 56.04 | 62.383 | 0.00072466 | 24.131 | 1086.4 |  | 2403 | 56.04 | 0.22239 | 62.383 | 0.00072466 | 24.131 | 1086.4 | 1062.269
2404 | 0.22247 | 56.05 | 62.383 | 0.00072491 | 24.141 | 1086.4 |  | 2404 | 56.05 | 0.22247 | 62.383 | 0.00072491 | 24.141 | 1086.4 | 1062.259
2405 | 0.22255 | 56.06 | 62.383 | 0.00072516 | 24.151 | 1086.4 |  | 2405 | 56.06 | 0.22255 | 62.383 | 0.00072516 | 24.151 | 1086.4 | 1062.249
2406 | 0.22263 | 56.07 | 62.383 | 0.00072541 | 24.161 | 1086.4 |  | 2406 | 56.07 | 0.22263 | 62.383 | 0.00072541 | 24.161 | 1086.4 | 1062.239
2407 | 0.22271 | 56.08 | 62.383 | 0.00072566 | 24.171 | 1086.4 |  | 2407 | 56.08 | 0.22271 | 62.383 | 0.00072566 | 24.171 | 1086.4 | 1062.229
2408 | 0.22279 | 56.09 | 62.383 | 0.00072591 | 24.181 | 1086.4 |  | 2408 | 56.09 | 0.22279 | 62.383 | 0.00072591 | 24.181 | 1086.4 | 1062.219
2409 | 0.22287 | 56.1 | 62.383 | 0.00072616 | 24.191 | 1086.5 |  | 2409 | 56.1 | 0.22287 | 62.383 | 0.00072616 | 24.191 | 1086.5 | 1062.309
2410 | 0.22295 | 56.11 | 62.383 | 0.00072641 | 24.201 | 1086.5 |  | 2410 | 56.11 | 0.22295 | 62.383 | 0.00072641 | 24.201 | 1086.5 | 1062.299
2411 | 0.22303 | 56.12 | 62.383 | 0.00072665 | 24.211 | 1086.5 |  | 2411 | 56.12 | 0.22303 | 62.383 | 0.00072665 | 24.211 | 1086.5 | 1062.289
2412 | 0.22311 | 56.13 | 62.383 | 0.0007269 | 24.221 | 1086.5 |  | 2412 | 56.13 | 0.22311 | 62.383 | 0.0007269 | 24.221 | 1086.5 | 1062.279
2413 | 0.22319 | 56.14 | 62.383 | 0.00072715 | 24.231 | 1086.5 |  | 2413 | 56.14 | 0.22319 | 62.383 | 0.00072715 | 24.231 | 1086.5 | 1062.269
2414 | 0.22328 | 56.15 | 62.383 | 0.0007274 | 24.241 | 1086.5 |  | 2414 | 56.15 | 0.22328 | 62.383 | 0.0007274 | 24.241 | 1086.5 | 1062.259
2415 | 0.22336 | 56.16 | 62.383 | 0.00072765 | 24.251 | 1086.5 |  | 2415 | 56.16 | 0.22336 | 62.383 | 0.00072765 | 24.251 | 1086.5 | 1062.249
2416 | 0.22344 | 56.17 | 62.383 | 0.0007279 | 24.261 | 1086.5 |  | 2416 | 56.17 | 0.22344 | 62.383 | 0.0007279 | 24.261 | 1086.5 | 1062.239
2417 | 0.22352 | 56.18 | 62.383 | 0.00072815 | 24.271 | 1086.5 |  | 2417 | 56.18 | 0.22352 | 62.383 | 0.00072815 | 24.271 | 1086.5 | 1062.229
2418 | 0.2236 | 56.19 | 62.383 | 0.0007284 | 24.281 | 1086.5 |  | 2418 | 56.19 | 0.2236 | 62.383 | 0.0007284 | 24.281 | 1086.5 | 1062.219
2419 | 0.22368 | 56.2 | 62.383 | 0.00072865 | 24.291 | 1086.5 |  | 2419 | 56.2 | 0.22368 | 62.383 | 0.00072865 | 24.291 | 1086.5 | 1062.209
2420 | 0.22376 | 56.21 | 62.383 | 0.0007289 | 24.301 | 1086.5 |  | 2420 | 56.21 | 0.22376 | 62.383 | 0.0007289 | 24.301 | 1086.5 | 1062.199
2421 | 0.22384 | 56.22 | 62.383 | 0.00072915 | 24.311 | 1086.5 |  | 2421 | 56.22 | 0.22384 | 62.383 | 0.00072915 | 24.311 | 1086.5 | 1062.189
2422 | 0.22392 | 56.23 | 62.383 | 0.0007294 | 24.321 | 1086.5 |  | 2422 | 56.23 | 0.22392 | 62.383 | 0.0007294 | 24.321 | 1086.5 | 1062.179
2423 | 0.224 | 56.24 | 62.383 | 0.00072965 | 24.331 | 1086.5 |  | 2423 | 56.24 | 0.224 | 62.383 | 0.00072965 | 24.331 | 1086.5 | 1062.169
2424 | 0.22409 | 56.25 | 62.383 | 0.0007299 | 24.341 | 1086.5 |  | 2424 | 56.25 | 0.22409 | 62.383 | 0.0007299 | 24.341 | 1086.5 | 1062.159
2425 | 0.22417 | 56.26 | 62.382 | 0.00073015 | 24.351 | 1086.5 |  | 2425 | 56.26 | 0.22417 | 62.382 | 0.00073015 | 24.351 | 1086.5 | 1062.149
2426 | 0.22425 | 56.27 | 62.382 | 0.0007304 | 24.362 | 1086.5 |  | 2426 | 56.27 | 0.22425 | 62.382 | 0.0007304 | 24.362 | 1086.5 | 1062.138
2427 | 0.22433 | 56.28 | 62.382 | 0.00073065 | 24.372 | 1086.5 |  | 2427 | 56.28 | 0.22433 | 62.382 | 0.00073065 | 24.372 | 1086.5 | 1062.128
2428 | 0.22441 | 56.29 | 62.382 | 0.00073091 | 24.382 | 1086.5 |  | 2428 | 56.29 | 0.22441 | 62.382 | 0.00073091 | 24.382 | 1086.5 | 1062.118
2429 | 0.22449 | 56.3 | 62.382 | 0.00073116 | 24.392 | 1086.5 |  | 2429 | 56.3 | 0.22449 | 62.382 | 0.00073116 | 24.392 | 1086.5 | 1062.108
2430 | 0.22457 | 56.31 | 62.382 | 0.00073141 | 24.402 | 1086.5 |  | 2430 | 56.31 | 0.22457 | 62.382 | 0.00073141 | 24.402 | 1086.5 | 1062.098
2431 | 0.22465 | 56.32 | 62.382 | 0.00073166 | 24.412 | 1086.5 |  | 2431 | 56.32 | 0.22465 | 62.382 | 0.00073166 | 24.412 | 1086.5 | 1062.088
2432 | 0.22474 | 56.33 | 62.382 | 0.00073191 | 24.422 | 1086.6 |  | 2432 | 56.33 | 0.22474 | 62.382 | 0.00073191 | 24.422 | 1086.6 | 1062.178
2433 | 0.22482 | 56.34 | 62.382 | 0.00073216 | 24.432 | 1086.6 |  | 2433 | 56.34 | 0.22482 | 62.382 | 0.00073216 | 24.432 | 1086.6 | 1062.168
2434 | 0.2249 | 56.35 | 62.382 | 0.00073241 | 24.442 | 1086.6 |  | 2434 | 56.35 | 0.2249 | 62.382 | 0.00073241 | 24.442 | 1086.6 | 1062.158
2435 | 0.22498 | 56.36 | 62.382 | 0.00073266 | 24.452 | 1086.6 |  | 2435 | 56.36 | 0.22498 | 62.382 | 0.00073266 | 24.452 | 1086.6 | 1062.148
2436 | 0.22506 | 56.37 | 62.382 | 0.00073291 | 24.462 | 1086.6 |  | 2436 | 56.37 | 0.22506 | 62.382 | 0.00073291 | 24.462 | 1086.6 | 1062.138
2437 | 0.22514 | 56.38 | 62.382 | 0.00073316 | 24.472 | 1086.6 |  | 2437 | 56.38 | 0.22514 | 62.382 | 0.00073316 | 24.472 | 1086.6 | 1062.128
2438 | 0.22522 | 56.39 | 62.382 | 0.00073342 | 24.482 | 1086.6 |  | 2438 | 56.39 | 0.22522 | 62.382 | 0.00073342 | 24.482 | 1086.6 | 1062.118
2439 | 0.22531 | 56.4 | 62.382 | 0.00073367 | 24.492 | 1086.6 |  | 2439 | 56.4 | 0.22531 | 62.382 | 0.00073367 | 24.492 | 1086.6 | 1062.108
2440 | 0.22539 | 56.41 | 62.382 | 0.00073392 | 24.502 | 1086.6 |  | 2440 | 56.41 | 0.22539 | 62.382 | 0.00073392 | 24.502 | 1086.6 | 1062.098
2441 | 0.22547 | 56.42 | 62.382 | 0.00073417 | 24.512 | 1086.6 |  | 2441 | 56.42 | 0.22547 | 62.382 | 0.00073417 | 24.512 | 1086.6 | 1062.088
2442 | 0.22555 | 56.43 | 62.382 | 0.00073442 | 24.522 | 1086.6 |  | 2442 | 56.43 | 0.22555 | 62.382 | 0.00073442 | 24.522 | 1086.6 | 1062.078
2443 | 0.22563 | 56.44 | 62.382 | 0.00073467 | 24.532 | 1086.6 |  | 2443 | 56.44 | 0.22563 | 62.382 | 0.00073467 | 24.532 | 1086.6 | 1062.068
2444 | 0.22571 | 56.45 | 62.382 | 0.00073493 | 24.542 | 1086.6 |  | 2444 | 56.45 | 0.22571 | 62.382 | 0.00073493 | 24.542 | 1086.6 | 1062.058
2445 | 0.2258 | 56.46 | 62.382 | 0.00073518 | 24.552 | 1086.6 |  | 2445 | 56.46 | 0.2258 | 62.382 | 0.00073518 | 24.552 | 1086.6 | 1062.048
2446 | 0.22588 | 56.47 | 62.382 | 0.00073543 | 24.562 | 1086.6 |  | 2446 | 56.47 | 0.22588 | 62.382 | 0.00073543 | 24.562 | 1086.6 | 1062.038
2447 | 0.22596 | 56.48 | 62.381 | 0.00073568 | 24.572 | 1086.6 |  | 2447 | 56.48 | 0.22596 | 62.381 | 0.00073568 | 24.572 | 1086.6 | 1062.028
2448 | 0.22604 | 56.49 | 62.381 | 0.00073593 | 24.582 | 1086.6 |  | 2448 | 56.49 | 0.22604 | 62.381 | 0.00073593 | 24.582 | 1086.6 | 1062.018
2449 | 0.22612 | 56.5 | 62.381 | 0.00073619 | 24.592 | 1086.6 |  | 2449 | 56.5 | 0.22612 | 62.381 | 0.00073619 | 24.592 | 1086.6 | 1062.008
2450 | 0.2262 | 56.51 | 62.381 | 0.00073644 | 24.602 | 1086.6 |  | 2450 | 56.51 | 0.2262 | 62.381 | 0.00073644 | 24.602 | 1086.6 | 1061.998
2451 | 0.22629 | 56.52 | 62.381 | 0.00073669 | 24.612 | 1086.6 |  | 2451 | 56.52 | 0.22629 | 62.381 | 0.00073669 | 24.612 | 1086.6 | 1061.988
2452 | 0.22637 | 56.53 | 62.381 | 0.00073694 | 24.622 | 1086.6 |  | 2452 | 56.53 | 0.22637 | 62.381 | 0.00073694 | 24.622 | 1086.6 | 1061.978
2453 | 0.22645 | 56.54 | 62.381 | 0.0007372 | 24.632 | 1086.6 |  | 2453 | 56.54 | 0.22645 | 62.381 | 0.0007372 | 24.632 | 1086.6 | 1061.968
2454 | 0.22653 | 56.55 | 62.381 | 0.00073745 | 24.642 | 1086.6 |  | 2454 | 56.55 | 0.22653 | 62.381 | 0.00073745 | 24.642 | 1086.6 | 1061.958
2455 | 0.22661 | 56.56 | 62.381 | 0.0007377 | 24.652 | 1086.7 |  | 2455 | 56.56 | 0.22661 | 62.381 | 0.0007377 | 24.652 | 1086.7 | 1062.048
2456 | 0.2267 | 56.57 | 62.381 | 0.00073795 | 24.662 | 1086.7 |  | 2456 | 56.57 | 0.2267 | 62.381 | 0.00073795 | 24.662 | 1086.7 | 1062.038
2457 | 0.22678 | 56.58 | 62.381 | 0.00073821 | 24.672 | 1086.7 |  | 2457 | 56.58 | 0.22678 | 62.381 | 0.00073821 | 24.672 | 1086.7 | 1062.028
2458 | 0.22686 | 56.59 | 62.381 | 0.00073846 | 24.682 | 1086.7 |  | 2458 | 56.59 | 0.22686 | 62.381 | 0.00073846 | 24.682 | 1086.7 | 1062.018
2459 | 0.22694 | 56.6 | 62.381 | 0.00073871 | 24.692 | 1086.7 |  | 2459 | 56.6 | 0.22694 | 62.381 | 0.00073871 | 24.692 | 1086.7 | 1062.008
2460 | 0.22702 | 56.61 | 62.381 | 0.00073896 | 24.702 | 1086.7 |  | 2460 | 56.61 | 0.22702 | 62.381 | 0.00073896 | 24.702 | 1086.7 | 1061.998
2461 | 0.22711 | 56.62 | 62.381 | 0.00073922 | 24.712 | 1086.7 |  | 2461 | 56.62 | 0.22711 | 62.381 | 0.00073922 | 24.712 | 1086.7 | 1061.988
2462 | 0.22719 | 56.63 | 62.381 | 0.00073947 | 24.722 | 1086.7 |  | 2462 | 56.63 | 0.22719 | 62.381 | 0.00073947 | 24.722 | 1086.7 | 1061.978
2463 | 0.22727 | 56.64 | 62.381 | 0.00073972 | 24.732 | 1086.7 |  | 2463 | 56.64 | 0.22727 | 62.381 | 0.00073972 | 24.732 | 1086.7 | 1061.968
2464 | 0.22735 | 56.65 | 62.381 | 0.00073998 | 24.742 | 1086.7 |  | 2464 | 56.65 | 0.22735 | 62.381 | 0.00073998 | 24.742 | 1086.7 | 1061.958
2465 | 0.22743 | 56.66 | 62.381 | 0.00074023 | 24.752 | 1086.7 |  | 2465 | 56.66 | 0.22743 | 62.381 | 0.00074023 | 24.752 | 1086.7 | 1061.948
2466 | 0.22752 | 56.67 | 62.381 | 0.00074048 | 24.762 | 1086.7 |  | 2466 | 56.67 | 0.22752 | 62.381 | 0.00074048 | 24.762 | 1086.7 | 1061.938
2467 | 0.2276 | 56.68 | 62.381 | 0.00074074 | 24.772 | 1086.7 |  | 2467 | 56.68 | 0.2276 | 62.381 | 0.00074074 | 24.772 | 1086.7 | 1061.928
2468 | 0.22768 | 56.69 | 62.38 | 0.00074099 | 24.782 | 1086.7 |  | 2468 | 56.69 | 0.22768 | 62.38 | 0.00074099 | 24.782 | 1086.7 | 1061.918
2469 | 0.22776 | 56.7 | 62.38 | 0.00074125 | 24.792 | 1086.7 |  | 2469 | 56.7 | 0.22776 | 62.38 | 0.00074125 | 24.792 | 1086.7 | 1061.908
2470 | 0.22785 | 56.71 | 62.38 | 0.0007415 | 24.802 | 1086.7 |  | 2470 | 56.71 | 0.22785 | 62.38 | 0.0007415 | 24.802 | 1086.7 | 1061.898
2471 | 0.22793 | 56.72 | 62.38 | 0.00074175 | 24.812 | 1086.7 |  | 2471 | 56.72 | 0.22793 | 62.38 | 0.00074175 | 24.812 | 1086.7 | 1061.888
2472 | 0.22801 | 56.73 | 62.38 | 0.00074201 | 24.822 | 1086.7 |  | 2472 | 56.73 | 0.22801 | 62.38 | 0.00074201 | 24.822 | 1086.7 | 1061.878
2473 | 0.22809 | 56.74 | 62.38 | 0.00074226 | 24.832 | 1086.7 |  | 2473 | 56.74 | 0.22809 | 62.38 | 0.00074226 | 24.832 | 1086.7 | 1061.868
2474 | 0.22818 | 56.75 | 62.38 | 0.00074251 | 24.842 | 1086.7 |  | 2474 | 56.75 | 0.22818 | 62.38 | 0.00074251 | 24.842 | 1086.7 | 1061.858
2475 | 0.22826 | 56.76 | 62.38 | 0.00074277 | 24.852 | 1086.7 |  | 2475 | 56.76 | 0.22826 | 62.38 | 0.00074277 | 24.852 | 1086.7 | 1061.848
2476 | 0.22834 | 56.77 | 62.38 | 0.00074302 | 24.862 | 1086.7 |  | 2476 | 56.77 | 0.22834 | 62.38 | 0.00074302 | 24.862 | 1086.7 | 1061.838
2477 | 0.22842 | 56.78 | 62.38 | 0.00074328 | 24.872 | 1086.7 |  | 2477 | 56.78 | 0.22842 | 62.38 | 0.00074328 | 24.872 | 1086.7 | 1061.828
2478 | 0.22851 | 56.79 | 62.38 | 0.00074353 | 24.882 | 1086.8 |  | 2478 | 56.79 | 0.22851 | 62.38 | 0.00074353 | 24.882 | 1086.8 | 1061.918
2479 | 0.22859 | 56.8 | 62.38 | 0.00074379 | 24.892 | 1086.8 |  | 2479 | 56.8 | 0.22859 | 62.38 | 0.00074379 | 24.892 | 1086.8 | 1061.908
2480 | 0.22867 | 56.81 | 62.38 | 0.00074404 | 24.902 | 1086.8 |  | 2480 | 56.81 | 0.22867 | 62.38 | 0.00074404 | 24.902 | 1086.8 | 1061.898
2481 | 0.22875 | 56.82 | 62.38 | 0.0007443 | 24.912 | 1086.8 |  | 2481 | 56.82 | 0.22875 | 62.38 | 0.0007443 | 24.912 | 1086.8 | 1061.888
2482 | 0.22884 | 56.83 | 62.38 | 0.00074455 | 24.922 | 1086.8 |  | 2482 | 56.83 | 0.22884 | 62.38 | 0.00074455 | 24.922 | 1086.8 | 1061.878
2483 | 0.22892 | 56.84 | 62.38 | 0.0007448 | 24.932 | 1086.8 |  | 2483 | 56.84 | 0.22892 | 62.38 | 0.0007448 | 24.932 | 1086.8 | 1061.868
2484 | 0.229 | 56.85 | 62.38 | 0.00074506 | 24.942 | 1086.8 |  | 2484 | 56.85 | 0.229 | 62.38 | 0.00074506 | 24.942 | 1086.8 | 1061.858
2485 | 0.22908 | 56.86 | 62.38 | 0.00074531 | 24.952 | 1086.8 |  | 2485 | 56.86 | 0.22908 | 62.38 | 0.00074531 | 24.952 | 1086.8 | 1061.848
2486 | 0.22917 | 56.87 | 62.38 | 0.00074557 | 24.962 | 1086.8 |  | 2486 | 56.87 | 0.22917 | 62.38 | 0.00074557 | 24.962 | 1086.8 | 1061.838
2487 | 0.22925 | 56.88 | 62.38 | 0.00074582 | 24.972 | 1086.8 |  | 2487 | 56.88 | 0.22925 | 62.38 | 0.00074582 | 24.972 | 1086.8 | 1061.828
2488 | 0.22933 | 56.89 | 62.38 | 0.00074608 | 24.982 | 1086.8 |  | 2488 | 56.89 | 0.22933 | 62.38 | 0.00074608 | 24.982 | 1086.8 | 1061.818
2489 | 0.22942 | 56.9 | 62.379 | 0.00074634 | 24.992 | 1086.8 |  | 2489 | 56.9 | 0.22942 | 62.379 | 0.00074634 | 24.992 | 1086.8 | 1061.808
2490 | 0.2295 | 56.91 | 62.379 | 0.00074659 | 25.002 | 1086.8 |  | 2490 | 56.91 | 0.2295 | 62.379 | 0.00074659 | 25.002 | 1086.8 | 1061.798
2491 | 0.22958 | 56.92 | 62.379 | 0.00074685 | 25.013 | 1086.8 |  | 2491 | 56.92 | 0.22958 | 62.379 | 0.00074685 | 25.013 | 1086.8 | 1061.787
2492 | 0.22966 | 56.93 | 62.379 | 0.0007471 | 25.023 | 1086.8 |  | 2492 | 56.93 | 0.22966 | 62.379 | 0.0007471 | 25.023 | 1086.8 | 1061.777
2493 | 0.22975 | 56.94 | 62.379 | 0.00074736 | 25.033 | 1086.8 |  | 2493 | 56.94 | 0.22975 | 62.379 | 0.00074736 | 25.033 | 1086.8 | 1061.767
2494 | 0.22983 | 56.95 | 62.379 | 0.00074761 | 25.043 | 1086.8 |  | 2494 | 56.95 | 0.22983 | 62.379 | 0.00074761 | 25.043 | 1086.8 | 1061.757
2495 | 0.22991 | 56.96 | 62.379 | 0.00074787 | 25.053 | 1086.8 |  | 2495 | 56.96 | 0.22991 | 62.379 | 0.00074787 | 25.053 | 1086.8 | 1061.747
2496 | 0.23 | 56.97 | 62.379 | 0.00074812 | 25.063 | 1086.8 |  | 2496 | 56.97 | 0.23 | 62.379 | 0.00074812 | 25.063 | 1086.8 | 1061.737
2497 | 0.23008 | 56.98 | 62.379 | 0.00074838 | 25.073 | 1086.8 |  | 2497 | 56.98 | 0.23008 | 62.379 | 0.00074838 | 25.073 | 1086.8 | 1061.727
2498 | 0.23016 | 56.99 | 62.379 | 0.00074864 | 25.083 | 1086.8 |  | 2498 | 56.99 | 0.23016 | 62.379 | 0.00074864 | 25.083 | 1086.8 | 1061.717
2499 | 0.23025 | 57 | 62.379 | 0.00074889 | 25.093 | 1086.8 |  | 2499 | 57 | 0.23025 | 62.379 | 0.00074889 | 25.093 | 1086.8 | 1061.707
2500 | 0.23033 | 57.01 | 62.379 | 0.00074915 | 25.103 | 1086.8 |  | 2500 | 57.01 | 0.23033 | 62.379 | 0.00074915 | 25.103 | 1086.8 | 1061.697
2501 | 0.23041 | 57.02 | 62.379 | 0.0007494 | 25.113 | 1086.9 |  | 2501 | 57.02 | 0.23041 | 62.379 | 0.0007494 | 25.113 | 1086.9 | 1061.787
2502 | 0.23049 | 57.03 | 62.379 | 0.00074966 | 25.123 | 1086.9 |  | 2502 | 57.03 | 0.23049 | 62.379 | 0.00074966 | 25.123 | 1086.9 | 1061.777
2503 | 0.23058 | 57.04 | 62.379 | 0.00074992 | 25.133 | 1086.9 |  | 2503 | 57.04 | 0.23058 | 62.379 | 0.00074992 | 25.133 | 1086.9 | 1061.767
2504 | 0.23066 | 57.05 | 62.379 | 0.00075017 | 25.143 | 1086.9 |  | 2504 | 57.05 | 0.23066 | 62.379 | 0.00075017 | 25.143 | 1086.9 | 1061.757
2505 | 0.23074 | 57.06 | 62.379 | 0.00075043 | 25.153 | 1086.9 |  | 2505 | 57.06 | 0.23074 | 62.379 | 0.00075043 | 25.153 | 1086.9 | 1061.747
2506 | 0.23083 | 57.07 | 62.379 | 0.00075069 | 25.163 | 1086.9 |  | 2506 | 57.07 | 0.23083 | 62.379 | 0.00075069 | 25.163 | 1086.9 | 1061.737
2507 | 0.23091 | 57.08 | 62.379 | 0.00075094 | 25.173 | 1086.9 |  | 2507 | 57.08 | 0.23091 | 62.379 | 0.00075094 | 25.173 | 1086.9 | 1061.727
2508 | 0.23099 | 57.09 | 62.379 | 0.0007512 | 25.183 | 1086.9 |  | 2508 | 57.09 | 0.23099 | 62.379 | 0.0007512 | 25.183 | 1086.9 | 1061.717
2509 | 0.23108 | 57.1 | 62.379 | 0.00075146 | 25.193 | 1086.9 |  | 2509 | 57.1 | 0.23108 | 62.379 | 0.00075146 | 25.193 | 1086.9 | 1061.707
2510 | 0.23116 | 57.11 | 62.378 | 0.00075171 | 25.203 | 1086.9 |  | 2510 | 57.11 | 0.23116 | 62.378 | 0.00075171 | 25.203 | 1086.9 | 1061.697
2511 | 0.23124 | 57.12 | 62.378 | 0.00075197 | 25.213 | 1086.9 |  | 2511 | 57.12 | 0.23124 | 62.378 | 0.00075197 | 25.213 | 1086.9 | 1061.687
2512 | 0.23133 | 57.13 | 62.378 | 0.00075223 | 25.223 | 1086.9 |  | 2512 | 57.13 | 0.23133 | 62.378 | 0.00075223 | 25.223 | 1086.9 | 1061.677
2513 | 0.23141 | 57.14 | 62.378 | 0.00075248 | 25.233 | 1086.9 |  | 2513 | 57.14 | 0.23141 | 62.378 | 0.00075248 | 25.233 | 1086.9 | 1061.667
2514 | 0.2315 | 57.15 | 62.378 | 0.00075274 | 25.243 | 1086.9 |  | 2514 | 57.15 | 0.2315 | 62.378 | 0.00075274 | 25.243 | 1086.9 | 1061.657
2515 | 0.23158 | 57.16 | 62.378 | 0.000753 | 25.253 | 1086.9 |  | 2515 | 57.16 | 0.23158 | 62.378 | 0.000753 | 25.253 | 1086.9 | 1061.647
2516 | 0.23166 | 57.17 | 62.378 | 0.00075325 | 25.263 | 1086.9 |  | 2516 | 57.17 | 0.23166 | 62.378 | 0.00075325 | 25.263 | 1086.9 | 1061.637
2517 | 0.23175 | 57.18 | 62.378 | 0.00075351 | 25.273 | 1086.9 |  | 2517 | 57.18 | 0.23175 | 62.378 | 0.00075351 | 25.273 | 1086.9 | 1061.627
2518 | 0.23183 | 57.19 | 62.378 | 0.00075377 | 25.283 | 1086.9 |  | 2518 | 57.19 | 0.23183 | 62.378 | 0.00075377 | 25.283 | 1086.9 | 1061.617
2519 | 0.23191 | 57.2 | 62.378 | 0.00075403 | 25.293 | 1086.9 |  | 2519 | 57.2 | 0.23191 | 62.378 | 0.00075403 | 25.293 | 1086.9 | 1061.607
2520 | 0.232 | 57.21 | 62.378 | 0.00075428 | 25.303 | 1086.9 |  | 2520 | 57.21 | 0.232 | 62.378 | 0.00075428 | 25.303 | 1086.9 | 1061.597
2521 | 0.23208 | 57.22 | 62.378 | 0.00075454 | 25.313 | 1086.9 |  | 2521 | 57.22 | 0.23208 | 62.378 | 0.00075454 | 25.313 | 1086.9 | 1061.587
2522 | 0.23216 | 57.23 | 62.378 | 0.0007548 | 25.323 | 1086.9 |  | 2522 | 57.23 | 0.23216 | 62.378 | 0.0007548 | 25.323 | 1086.9 | 1061.577
2523 | 0.23225 | 57.24 | 62.378 | 0.00075506 | 25.333 | 1086.9 |  | 2523 | 57.24 | 0.23225 | 62.378 | 0.00075506 | 25.333 | 1086.9 | 1061.567
2524 | 0.23233 | 57.25 | 62.378 | 0.00075532 | 25.343 | 1087 |  | 2524 | 57.25 | 0.23233 | 62.378 | 0.00075532 | 25.343 | 1087 | 1061.657
2525 | 0.23242 | 57.26 | 62.378 | 0.00075557 | 25.353 | 1087 |  | 2525 | 57.26 | 0.23242 | 62.378 | 0.00075557 | 25.353 | 1087 | 1061.647
2526 | 0.2325 | 57.27 | 62.378 | 0.00075583 | 25.363 | 1087 |  | 2526 | 57.27 | 0.2325 | 62.378 | 0.00075583 | 25.363 | 1087 | 1061.637
2527 | 0.23258 | 57.28 | 62.378 | 0.00075609 | 25.373 | 1087 |  | 2527 | 57.28 | 0.23258 | 62.378 | 0.00075609 | 25.373 | 1087 | 1061.627
2528 | 0.23267 | 57.29 | 62.378 | 0.00075635 | 25.383 | 1087 |  | 2528 | 57.29 | 0.23267 | 62.378 | 0.00075635 | 25.383 | 1087 | 1061.617
2529 | 0.23275 | 57.3 | 62.378 | 0.00075661 | 25.393 | 1087 |  | 2529 | 57.3 | 0.23275 | 62.378 | 0.00075661 | 25.393 | 1087 | 1061.607
2530 | 0.23283 | 57.31 | 62.378 | 0.00075686 | 25.403 | 1087 |  | 2530 | 57.31 | 0.23283 | 62.378 | 0.00075686 | 25.403 | 1087 | 1061.597
2531 | 0.23292 | 57.32 | 62.377 | 0.00075712 | 25.413 | 1087 |  | 2531 | 57.32 | 0.23292 | 62.377 | 0.00075712 | 25.413 | 1087 | 1061.587
2532 | 0.233 | 57.33 | 62.377 | 0.00075738 | 25.423 | 1087 |  | 2532 | 57.33 | 0.233 | 62.377 | 0.00075738 | 25.423 | 1087 | 1061.577
2533 | 0.23309 | 57.34 | 62.377 | 0.00075764 | 25.433 | 1087 |  | 2533 | 57.34 | 0.23309 | 62.377 | 0.00075764 | 25.433 | 1087 | 1061.567
2534 | 0.23317 | 57.35 | 62.377 | 0.0007579 | 25.443 | 1087 |  | 2534 | 57.35 | 0.23317 | 62.377 | 0.0007579 | 25.443 | 1087 | 1061.557
2535 | 0.23325 | 57.36 | 62.377 | 0.00075816 | 25.453 | 1087 |  | 2535 | 57.36 | 0.23325 | 62.377 | 0.00075816 | 25.453 | 1087 | 1061.547
2536 | 0.23334 | 57.37 | 62.377 | 0.00075842 | 25.463 | 1087 |  | 2536 | 57.37 | 0.23334 | 62.377 | 0.00075842 | 25.463 | 1087 | 1061.537
2537 | 0.23342 | 57.38 | 62.377 | 0.00075867 | 25.473 | 1087 |  | 2537 | 57.38 | 0.23342 | 62.377 | 0.00075867 | 25.473 | 1087 | 1061.527
2538 | 0.23351 | 57.39 | 62.377 | 0.00075893 | 25.483 | 1087 |  | 2538 | 57.39 | 0.23351 | 62.377 | 0.00075893 | 25.483 | 1087 | 1061.517
2539 | 0.23359 | 57.4 | 62.377 | 0.00075919 | 25.493 | 1087 |  | 2539 | 57.4 | 0.23359 | 62.377 | 0.00075919 | 25.493 | 1087 | 1061.507
2540 | 0.23368 | 57.41 | 62.377 | 0.00075945 | 25.503 | 1087 |  | 2540 | 57.41 | 0.23368 | 62.377 | 0.00075945 | 25.503 | 1087 | 1061.497
2541 | 0.23376 | 57.42 | 62.377 | 0.00075971 | 25.513 | 1087 |  | 2541 | 57.42 | 0.23376 | 62.377 | 0.00075971 | 25.513 | 1087 | 1061.487
2542 | 0.23384 | 57.43 | 62.377 | 0.00075997 | 25.523 | 1087 |  | 2542 | 57.43 | 0.23384 | 62.377 | 0.00075997 | 25.523 | 1087 | 1061.477
2543 | 0.23393 | 57.44 | 62.377 | 0.00076023 | 25.533 | 1087 |  | 2543 | 57.44 | 0.23393 | 62.377 | 0.00076023 | 25.533 | 1087 | 1061.467
2544 | 0.23401 | 57.45 | 62.377 | 0.00076049 | 25.543 | 1087 |  | 2544 | 57.45 | 0.23401 | 62.377 | 0.00076049 | 25.543 | 1087 | 1061.457
2545 | 0.2341 | 57.46 | 62.377 | 0.00076075 | 25.553 | 1087 |  | 2545 | 57.46 | 0.2341 | 62.377 | 0.00076075 | 25.553 | 1087 | 1061.447
2546 | 0.23418 | 57.47 | 62.377 | 0.00076101 | 25.563 | 1087 |  | 2546 | 57.47 | 0.23418 | 62.377 | 0.00076101 | 25.563 | 1087 | 1061.437
2547 | 0.23427 | 57.48 | 62.377 | 0.00076127 | 25.573 | 1087.1 |  | 2547 | 57.48 | 0.23427 | 62.377 | 0.00076127 | 25.573 | 1087.1 | 1061.527
2548 | 0.23435 | 57.49 | 62.377 | 0.00076153 | 25.583 | 1087.1 |  | 2548 | 57.49 | 0.23435 | 62.377 | 0.00076153 | 25.583 | 1087.1 | 1061.517
2549 | 0.23443 | 57.5 | 62.377 | 0.00076179 | 25.593 | 1087.1 |  | 2549 | 57.5 | 0.23443 | 62.377 | 0.00076179 | 25.593 | 1087.1 | 1061.507
2550 | 0.23452 | 57.51 | 62.377 | 0.00076205 | 25.603 | 1087.1 |  | 2550 | 57.51 | 0.23452 | 62.377 | 0.00076205 | 25.603 | 1087.1 | 1061.497
2551 | 0.2346 | 57.52 | 62.377 | 0.00076231 | 25.613 | 1087.1 |  | 2551 | 57.52 | 0.2346 | 62.377 | 0.00076231 | 25.613 | 1087.1 | 1061.487
2552 | 0.23469 | 57.53 | 62.376 | 0.00076257 | 25.623 | 1087.1 |  | 2552 | 57.53 | 0.23469 | 62.376 | 0.00076257 | 25.623 | 1087.1 | 1061.477
2553 | 0.23477 | 57.54 | 62.376 | 0.00076283 | 25.633 | 1087.1 |  | 2553 | 57.54 | 0.23477 | 62.376 | 0.00076283 | 25.633 | 1087.1 | 1061.467
2554 | 0.23486 | 57.55 | 62.376 | 0.00076309 | 25.643 | 1087.1 |  | 2554 | 57.55 | 0.23486 | 62.376 | 0.00076309 | 25.643 | 1087.1 | 1061.457
2555 | 0.23494 | 57.56 | 62.376 | 0.00076335 | 25.653 | 1087.1 |  | 2555 | 57.56 | 0.23494 | 62.376 | 0.00076335 | 25.653 | 1087.1 | 1061.447
2556 | 0.23503 | 57.57 | 62.376 | 0.00076361 | 25.663 | 1087.1 |  | 2556 | 57.57 | 0.23503 | 62.376 | 0.00076361 | 25.663 | 1087.1 | 1061.437
2557 | 0.23511 | 57.58 | 62.376 | 0.00076387 | 25.673 | 1087.1 |  | 2557 | 57.58 | 0.23511 | 62.376 | 0.00076387 | 25.673 | 1087.1 | 1061.427
2558 | 0.2352 | 57.59 | 62.376 | 0.00076413 | 25.683 | 1087.1 |  | 2558 | 57.59 | 0.2352 | 62.376 | 0.00076413 | 25.683 | 1087.1 | 1061.417
2559 | 0.23528 | 57.6 | 62.376 | 0.00076439 | 25.693 | 1087.1 |  | 2559 | 57.6 | 0.23528 | 62.376 | 0.00076439 | 25.693 | 1087.1 | 1061.407
2560 | 0.23536 | 57.61 | 62.376 | 0.00076465 | 25.703 | 1087.1 |  | 2560 | 57.61 | 0.23536 | 62.376 | 0.00076465 | 25.703 | 1087.1 | 1061.397
2561 | 0.23545 | 57.62 | 62.376 | 0.00076491 | 25.714 | 1087.1 |  | 2561 | 57.62 | 0.23545 | 62.376 | 0.00076491 | 25.714 | 1087.1 | 1061.386
2562 | 0.23553 | 57.63 | 62.376 | 0.00076517 | 25.724 | 1087.1 |  | 2562 | 57.63 | 0.23553 | 62.376 | 0.00076517 | 25.724 | 1087.1 | 1061.376
2563 | 0.23562 | 57.64 | 62.376 | 0.00076543 | 25.734 | 1087.1 |  | 2563 | 57.64 | 0.23562 | 62.376 | 0.00076543 | 25.734 | 1087.1 | 1061.366
2564 | 0.2357 | 57.65 | 62.376 | 0.00076569 | 25.744 | 1087.1 |  | 2564 | 57.65 | 0.2357 | 62.376 | 0.00076569 | 25.744 | 1087.1 | 1061.356
2565 | 0.23579 | 57.66 | 62.376 | 0.00076595 | 25.754 | 1087.1 |  | 2565 | 57.66 | 0.23579 | 62.376 | 0.00076595 | 25.754 | 1087.1 | 1061.346
2566 | 0.23587 | 57.67 | 62.376 | 0.00076622 | 25.764 | 1087.1 |  | 2566 | 57.67 | 0.23587 | 62.376 | 0.00076622 | 25.764 | 1087.1 | 1061.336
2567 | 0.23596 | 57.68 | 62.376 | 0.00076648 | 25.774 | 1087.1 |  | 2567 | 57.68 | 0.23596 | 62.376 | 0.00076648 | 25.774 | 1087.1 | 1061.326
2568 | 0.23604 | 57.69 | 62.376 | 0.00076674 | 25.784 | 1087.1 |  | 2568 | 57.69 | 0.23604 | 62.376 | 0.00076674 | 25.784 | 1087.1 | 1061.316
2569 | 0.23613 | 57.7 | 62.376 | 0.000767 | 25.794 | 1087.1 |  | 2569 | 57.7 | 0.23613 | 62.376 | 0.000767 | 25.794 | 1087.1 | 1061.306
2570 | 0.23621 | 57.71 | 62.376 | 0.00076726 | 25.804 | 1087.2 |  | 2570 | 57.71 | 0.23621 | 62.376 | 0.00076726 | 25.804 | 1087.2 | 1061.396
2571 | 0.2363 | 57.72 | 62.376 | 0.00076752 | 25.814 | 1087.2 |  | 2571 | 57.72 | 0.2363 | 62.376 | 0.00076752 | 25.814 | 1087.2 | 1061.386
2572 | 0.23638 | 57.73 | 62.375 | 0.00076778 | 25.824 | 1087.2 |  | 2572 | 57.73 | 0.23638 | 62.375 | 0.00076778 | 25.824 | 1087.2 | 1061.376
2573 | 0.23647 | 57.74 | 62.375 | 0.00076805 | 25.834 | 1087.2 |  | 2573 | 57.74 | 0.23647 | 62.375 | 0.00076805 | 25.834 | 1087.2 | 1061.366
2574 | 0.23655 | 57.75 | 62.375 | 0.00076831 | 25.844 | 1087.2 |  | 2574 | 57.75 | 0.23655 | 62.375 | 0.00076831 | 25.844 | 1087.2 | 1061.356
2575 | 0.23664 | 57.76 | 62.375 | 0.00076857 | 25.854 | 1087.2 |  | 2575 | 57.76 | 0.23664 | 62.375 | 0.00076857 | 25.854 | 1087.2 | 1061.346
2576 | 0.23672 | 57.77 | 62.375 | 0.00076883 | 25.864 | 1087.2 |  | 2576 | 57.77 | 0.23672 | 62.375 | 0.00076883 | 25.864 | 1087.2 | 1061.336
2577 | 0.23681 | 57.78 | 62.375 | 0.00076909 | 25.874 | 1087.2 |  | 2577 | 57.78 | 0.23681 | 62.375 | 0.00076909 | 25.874 | 1087.2 | 1061.326
2578 | 0.23689 | 57.79 | 62.375 | 0.00076935 | 25.884 | 1087.2 |  | 2578 | 57.79 | 0.23689 | 62.375 | 0.00076935 | 25.884 | 1087.2 | 1061.316
2579 | 0.23698 | 57.8 | 62.375 | 0.00076962 | 25.894 | 1087.2 |  | 2579 | 57.8 | 0.23698 | 62.375 | 0.00076962 | 25.894 | 1087.2 | 1061.306
2580 | 0.23706 | 57.81 | 62.375 | 0.00076988 | 25.904 | 1087.2 |  | 2580 | 57.81 | 0.23706 | 62.375 | 0.00076988 | 25.904 | 1087.2 | 1061.296
2581 | 0.23715 | 57.82 | 62.375 | 0.00077014 | 25.914 | 1087.2 |  | 2581 | 57.82 | 0.23715 | 62.375 | 0.00077014 | 25.914 | 1087.2 | 1061.286
2582 | 0.23724 | 57.83 | 62.375 | 0.0007704 | 25.924 | 1087.2 |  | 2582 | 57.83 | 0.23724 | 62.375 | 0.0007704 | 25.924 | 1087.2 | 1061.276
2583 | 0.23732 | 57.84 | 62.375 | 0.00077067 | 25.934 | 1087.2 |  | 2583 | 57.84 | 0.23732 | 62.375 | 0.00077067 | 25.934 | 1087.2 | 1061.266
2584 | 0.23741 | 57.85 | 62.375 | 0.00077093 | 25.944 | 1087.2 |  | 2584 | 57.85 | 0.23741 | 62.375 | 0.00077093 | 25.944 | 1087.2 | 1061.256
2585 | 0.23749 | 57.86 | 62.375 | 0.00077119 | 25.954 | 1087.2 |  | 2585 | 57.86 | 0.23749 | 62.375 | 0.00077119 | 25.954 | 1087.2 | 1061.246
2586 | 0.23758 | 57.87 | 62.375 | 0.00077145 | 25.964 | 1087.2 |  | 2586 | 57.87 | 0.23758 | 62.375 | 0.00077145 | 25.964 | 1087.2 | 1061.236
2587 | 0.23766 | 57.88 | 62.375 | 0.00077172 | 25.974 | 1087.2 |  | 2587 | 57.88 | 0.23766 | 62.375 | 0.00077172 | 25.974 | 1087.2 | 1061.226
2588 | 0.23775 | 57.89 | 62.375 | 0.00077198 | 25.984 | 1087.2 |  | 2588 | 57.89 | 0.23775 | 62.375 | 0.00077198 | 25.984 | 1087.2 | 1061.216
2589 | 0.23783 | 57.9 | 62.375 | 0.00077224 | 25.994 | 1087.2 |  | 2589 | 57.9 | 0.23783 | 62.375 | 0.00077224 | 25.994 | 1087.2 | 1061.206
2590 | 0.23792 | 57.91 | 62.375 | 0.00077251 | 26.004 | 1087.2 |  | 2590 | 57.91 | 0.23792 | 62.375 | 0.00077251 | 26.004 | 1087.2 | 1061.196
2591 | 0.238 | 57.92 | 62.375 | 0.00077277 | 26.014 | 1087.2 |  | 2591 | 57.92 | 0.238 | 62.375 | 0.00077277 | 26.014 | 1087.2 | 1061.186
2592 | 0.23809 | 57.93 | 62.374 | 0.00077303 | 26.024 | 1087.2 |  | 2592 | 57.93 | 0.23809 | 62.374 | 0.00077303 | 26.024 | 1087.2 | 1061.176
2593 | 0.23818 | 57.94 | 62.374 | 0.00077329 | 26.034 | 1087.3 |  | 2593 | 57.94 | 0.23818 | 62.374 | 0.00077329 | 26.034 | 1087.3 | 1061.266
2594 | 0.23826 | 57.95 | 62.374 | 0.00077356 | 26.044 | 1087.3 |  | 2594 | 57.95 | 0.23826 | 62.374 | 0.00077356 | 26.044 | 1087.3 | 1061.256
2595 | 0.23835 | 57.96 | 62.374 | 0.00077382 | 26.054 | 1087.3 |  | 2595 | 57.96 | 0.23835 | 62.374 | 0.00077382 | 26.054 | 1087.3 | 1061.246
2596 | 0.23843 | 57.97 | 62.374 | 0.00077408 | 26.064 | 1087.3 |  | 2596 | 57.97 | 0.23843 | 62.374 | 0.00077408 | 26.064 | 1087.3 | 1061.236
2597 | 0.23852 | 57.98 | 62.374 | 0.00077435 | 26.074 | 1087.3 |  | 2597 | 57.98 | 0.23852 | 62.374 | 0.00077435 | 26.074 | 1087.3 | 1061.226
2598 | 0.2386 | 57.99 | 62.374 | 0.00077461 | 26.084 | 1087.3 |  | 2598 | 57.99 | 0.2386 | 62.374 | 0.00077461 | 26.084 | 1087.3 | 1061.216
2599 | 0.23869 | 58 | 62.374 | 0.00077488 | 26.094 | 1087.3 |  | 2599 | 58 | 0.23869 | 62.374 | 0.00077488 | 26.094 | 1087.3 | 1061.206
2600 | 0.23878 | 58.01 | 62.374 | 0.00077514 | 26.104 | 1087.3 |  | 2600 | 58.01 | 0.23878 | 62.374 | 0.00077514 | 26.104 | 1087.3 | 1061.196
2601 | 0.23886 | 58.02 | 62.374 | 0.0007754 | 26.114 | 1087.3 |  | 2601 | 58.02 | 0.23886 | 62.374 | 0.0007754 | 26.114 | 1087.3 | 1061.186
2602 | 0.23895 | 58.03 | 62.374 | 0.00077567 | 26.124 | 1087.3 |  | 2602 | 58.03 | 0.23895 | 62.374 | 0.00077567 | 26.124 | 1087.3 | 1061.176
2603 | 0.23903 | 58.04 | 62.374 | 0.00077593 | 26.134 | 1087.3 |  | 2603 | 58.04 | 0.23903 | 62.374 | 0.00077593 | 26.134 | 1087.3 | 1061.166
2604 | 0.23912 | 58.05 | 62.374 | 0.00077619 | 26.144 | 1087.3 |  | 2604 | 58.05 | 0.23912 | 62.374 | 0.00077619 | 26.144 | 1087.3 | 1061.156
2605 | 0.2392 | 58.06 | 62.374 | 0.00077646 | 26.154 | 1087.3 |  | 2605 | 58.06 | 0.2392 | 62.374 | 0.00077646 | 26.154 | 1087.3 | 1061.146
2606 | 0.23929 | 58.07 | 62.374 | 0.00077672 | 26.164 | 1087.3 |  | 2606 | 58.07 | 0.23929 | 62.374 | 0.00077672 | 26.164 | 1087.3 | 1061.136
2607 | 0.23938 | 58.08 | 62.374 | 0.00077699 | 26.174 | 1087.3 |  | 2607 | 58.08 | 0.23938 | 62.374 | 0.00077699 | 26.174 | 1087.3 | 1061.126
2608 | 0.23946 | 58.09 | 62.374 | 0.00077725 | 26.184 | 1087.3 |  | 2608 | 58.09 | 0.23946 | 62.374 | 0.00077725 | 26.184 | 1087.3 | 1061.116
2609 | 0.23955 | 58.1 | 62.374 | 0.00077752 | 26.194 | 1087.3 |  | 2609 | 58.1 | 0.23955 | 62.374 | 0.00077752 | 26.194 | 1087.3 | 1061.106
2610 | 0.23963 | 58.11 | 62.374 | 0.00077778 | 26.204 | 1087.3 |  | 2610 | 58.11 | 0.23963 | 62.374 | 0.00077778 | 26.204 | 1087.3 | 1061.096
2611 | 0.23972 | 58.12 | 62.374 | 0.00077805 | 26.214 | 1087.3 |  | 2611 | 58.12 | 0.23972 | 62.374 | 0.00077805 | 26.214 | 1087.3 | 1061.086
2612 | 0.23981 | 58.13 | 62.373 | 0.00077831 | 26.224 | 1087.3 |  | 2612 | 58.13 | 0.23981 | 62.373 | 0.00077831 | 26.224 | 1087.3 | 1061.076
2613 | 0.23989 | 58.14 | 62.373 | 0.00077857 | 26.234 | 1087.3 |  | 2613 | 58.14 | 0.23989 | 62.373 | 0.00077857 | 26.234 | 1087.3 | 1061.066
2614 | 0.23998 | 58.15 | 62.373 | 0.00077884 | 26.244 | 1087.3 |  | 2614 | 58.15 | 0.23998 | 62.373 | 0.00077884 | 26.244 | 1087.3 | 1061.056
2615 | 0.24007 | 58.16 | 62.373 | 0.0007791 | 26.254 | 1087.3 |  | 2615 | 58.16 | 0.24007 | 62.373 | 0.0007791 | 26.254 | 1087.3 | 1061.046
2616 | 0.24015 | 58.17 | 62.373 | 0.00077937 | 26.264 | 1087.4 |  | 2616 | 58.17 | 0.24015 | 62.373 | 0.00077937 | 26.264 | 1087.4 | 1061.136
2617 | 0.24024 | 58.18 | 62.373 | 0.00077963 | 26.274 | 1087.4 |  | 2617 | 58.18 | 0.24024 | 62.373 | 0.00077963 | 26.274 | 1087.4 | 1061.126
2618 | 0.24032 | 58.19 | 62.373 | 0.0007799 | 26.284 | 1087.4 |  | 2618 | 58.19 | 0.24032 | 62.373 | 0.0007799 | 26.284 | 1087.4 | 1061.116
2619 | 0.24041 | 58.2 | 62.373 | 0.00078017 | 26.294 | 1087.4 |  | 2619 | 58.2 | 0.24041 | 62.373 | 0.00078017 | 26.294 | 1087.4 | 1061.106
2620 | 0.2405 | 58.21 | 62.373 | 0.00078043 | 26.304 | 1087.4 |  | 2620 | 58.21 | 0.2405 | 62.373 | 0.00078043 | 26.304 | 1087.4 | 1061.096
2621 | 0.24058 | 58.22 | 62.373 | 0.0007807 | 26.314 | 1087.4 |  | 2621 | 58.22 | 0.24058 | 62.373 | 0.0007807 | 26.314 | 1087.4 | 1061.086
2622 | 0.24067 | 58.23 | 62.373 | 0.00078096 | 26.324 | 1087.4 |  | 2622 | 58.23 | 0.24067 | 62.373 | 0.00078096 | 26.324 | 1087.4 | 1061.076
2623 | 0.24076 | 58.24 | 62.373 | 0.00078123 | 26.334 | 1087.4 |  | 2623 | 58.24 | 0.24076 | 62.373 | 0.00078123 | 26.334 | 1087.4 | 1061.066
2624 | 0.24084 | 58.25 | 62.373 | 0.00078149 | 26.344 | 1087.4 |  | 2624 | 58.25 | 0.24084 | 62.373 | 0.00078149 | 26.344 | 1087.4 | 1061.056
2625 | 0.24093 | 58.26 | 62.373 | 0.00078176 | 26.354 | 1087.4 |  | 2625 | 58.26 | 0.24093 | 62.373 | 0.00078176 | 26.354 | 1087.4 | 1061.046
2626 | 0.24102 | 58.27 | 62.373 | 0.00078202 | 26.364 | 1087.4 |  | 2626 | 58.27 | 0.24102 | 62.373 | 0.00078202 | 26.364 | 1087.4 | 1061.036
2627 | 0.2411 | 58.28 | 62.373 | 0.00078229 | 26.374 | 1087.4 |  | 2627 | 58.28 | 0.2411 | 62.373 | 0.00078229 | 26.374 | 1087.4 | 1061.026
2628 | 0.24119 | 58.29 | 62.373 | 0.00078256 | 26.384 | 1087.4 |  | 2628 | 58.29 | 0.24119 | 62.373 | 0.00078256 | 26.384 | 1087.4 | 1061.016
2629 | 0.24128 | 58.3 | 62.373 | 0.00078282 | 26.394 | 1087.4 |  | 2629 | 58.3 | 0.24128 | 62.373 | 0.00078282 | 26.394 | 1087.4 | 1061.006
2630 | 0.24136 | 58.31 | 62.373 | 0.00078309 | 26.404 | 1087.4 |  | 2630 | 58.31 | 0.24136 | 62.373 | 0.00078309 | 26.404 | 1087.4 | 1060.996
2631 | 0.24145 | 58.32 | 62.373 | 0.00078335 | 26.414 | 1087.4 |  | 2631 | 58.32 | 0.24145 | 62.373 | 0.00078335 | 26.414 | 1087.4 | 1060.986
2632 | 0.24154 | 58.33 | 62.372 | 0.00078362 | 26.424 | 1087.4 |  | 2632 | 58.33 | 0.24154 | 62.372 | 0.00078362 | 26.424 | 1087.4 | 1060.976
2633 | 0.24162 | 58.34 | 62.372 | 0.00078389 | 26.434 | 1087.4 |  | 2633 | 58.34 | 0.24162 | 62.372 | 0.00078389 | 26.434 | 1087.4 | 1060.966
2634 | 0.24171 | 58.35 | 62.372 | 0.00078415 | 26.444 | 1087.4 |  | 2634 | 58.35 | 0.24171 | 62.372 | 0.00078415 | 26.444 | 1087.4 | 1060.956
2635 | 0.2418 | 58.36 | 62.372 | 0.00078442 | 26.454 | 1087.4 |  | 2635 | 58.36 | 0.2418 | 62.372 | 0.00078442 | 26.454 | 1087.4 | 1060.946
2636 | 0.24188 | 58.37 | 62.372 | 0.00078469 | 26.465 | 1087.4 |  | 2636 | 58.37 | 0.24188 | 62.372 | 0.00078469 | 26.465 | 1087.4 | 1060.935
2637 | 0.24197 | 58.38 | 62.372 | 0.00078495 | 26.475 | 1087.4 |  | 2637 | 58.38 | 0.24197 | 62.372 | 0.00078495 | 26.475 | 1087.4 | 1060.925
2638 | 0.24206 | 58.39 | 62.372 | 0.00078522 | 26.485 | 1087.4 |  | 2638 | 58.39 | 0.24206 | 62.372 | 0.00078522 | 26.485 | 1087.4 | 1060.915
2639 | 0.24214 | 58.4 | 62.372 | 0.00078549 | 26.495 | 1087.5 |  | 2639 | 58.4 | 0.24214 | 62.372 | 0.00078549 | 26.495 | 1087.5 | 1061.005
2640 | 0.24223 | 58.41 | 62.372 | 0.00078575 | 26.505 | 1087.5 |  | 2640 | 58.41 | 0.24223 | 62.372 | 0.00078575 | 26.505 | 1087.5 | 1060.995
2641 | 0.24232 | 58.42 | 62.372 | 0.00078602 | 26.515 | 1087.5 |  | 2641 | 58.42 | 0.24232 | 62.372 | 0.00078602 | 26.515 | 1087.5 | 1060.985
2642 | 0.2424 | 58.43 | 62.372 | 0.00078629 | 26.525 | 1087.5 |  | 2642 | 58.43 | 0.2424 | 62.372 | 0.00078629 | 26.525 | 1087.5 | 1060.975
2643 | 0.24249 | 58.44 | 62.372 | 0.00078655 | 26.535 | 1087.5 |  | 2643 | 58.44 | 0.24249 | 62.372 | 0.00078655 | 26.535 | 1087.5 | 1060.965
2644 | 0.24258 | 58.45 | 62.372 | 0.00078682 | 26.545 | 1087.5 |  | 2644 | 58.45 | 0.24258 | 62.372 | 0.00078682 | 26.545 | 1087.5 | 1060.955
2645 | 0.24266 | 58.46 | 62.372 | 0.00078709 | 26.555 | 1087.5 |  | 2645 | 58.46 | 0.24266 | 62.372 | 0.00078709 | 26.555 | 1087.5 | 1060.945
2646 | 0.24275 | 58.47 | 62.372 | 0.00078736 | 26.565 | 1087.5 |  | 2646 | 58.47 | 0.24275 | 62.372 | 0.00078736 | 26.565 | 1087.5 | 1060.935
2647 | 0.24284 | 58.48 | 62.372 | 0.00078762 | 26.575 | 1087.5 |  | 2647 | 58.48 | 0.24284 | 62.372 | 0.00078762 | 26.575 | 1087.5 | 1060.925
2648 | 0.24293 | 58.49 | 62.372 | 0.00078789 | 26.585 | 1087.5 |  | 2648 | 58.49 | 0.24293 | 62.372 | 0.00078789 | 26.585 | 1087.5 | 1060.915
2649 | 0.24301 | 58.5 | 62.372 | 0.00078816 | 26.595 | 1087.5 |  | 2649 | 58.5 | 0.24301 | 62.372 | 0.00078816 | 26.595 | 1087.5 | 1060.905
2650 | 0.2431 | 58.51 | 62.372 | 0.00078843 | 26.605 | 1087.5 |  | 2650 | 58.51 | 0.2431 | 62.372 | 0.00078843 | 26.605 | 1087.5 | 1060.895
2651 | 0.24319 | 58.52 | 62.372 | 0.00078869 | 26.615 | 1087.5 |  | 2651 | 58.52 | 0.24319 | 62.372 | 0.00078869 | 26.615 | 1087.5 | 1060.885
2652 | 0.24327 | 58.53 | 62.371 | 0.00078896 | 26.625 | 1087.5 |  | 2652 | 58.53 | 0.24327 | 62.371 | 0.00078896 | 26.625 | 1087.5 | 1060.875
2653 | 0.24336 | 58.54 | 62.371 | 0.00078923 | 26.635 | 1087.5 |  | 2653 | 58.54 | 0.24336 | 62.371 | 0.00078923 | 26.635 | 1087.5 | 1060.865
2654 | 0.24345 | 58.55 | 62.371 | 0.0007895 | 26.645 | 1087.5 |  | 2654 | 58.55 | 0.24345 | 62.371 | 0.0007895 | 26.645 | 1087.5 | 1060.855
2655 | 0.24354 | 58.56 | 62.371 | 0.00078977 | 26.655 | 1087.5 |  | 2655 | 58.56 | 0.24354 | 62.371 | 0.00078977 | 26.655 | 1087.5 | 1060.845
2656 | 0.24362 | 58.57 | 62.371 | 0.00079003 | 26.665 | 1087.5 |  | 2656 | 58.57 | 0.24362 | 62.371 | 0.00079003 | 26.665 | 1087.5 | 1060.835
2657 | 0.24371 | 58.58 | 62.371 | 0.0007903 | 26.675 | 1087.5 |  | 2657 | 58.58 | 0.24371 | 62.371 | 0.0007903 | 26.675 | 1087.5 | 1060.825
2658 | 0.2438 | 58.59 | 62.371 | 0.00079057 | 26.685 | 1087.5 |  | 2658 | 58.59 | 0.2438 | 62.371 | 0.00079057 | 26.685 | 1087.5 | 1060.815
2659 | 0.24389 | 58.6 | 62.371 | 0.00079084 | 26.695 | 1087.5 |  | 2659 | 58.6 | 0.24389 | 62.371 | 0.00079084 | 26.695 | 1087.5 | 1060.805
2660 | 0.24397 | 58.61 | 62.371 | 0.00079111 | 26.705 | 1087.5 |  | 2660 | 58.61 | 0.24397 | 62.371 | 0.00079111 | 26.705 | 1087.5 | 1060.795
2661 | 0.24406 | 58.62 | 62.371 | 0.00079138 | 26.715 | 1087.5 |  | 2661 | 58.62 | 0.24406 | 62.371 | 0.00079138 | 26.715 | 1087.5 | 1060.785
2662 | 0.24415 | 58.63 | 62.371 | 0.00079164 | 26.725 | 1087.6 |  | 2662 | 58.63 | 0.24415 | 62.371 | 0.00079164 | 26.725 | 1087.6 | 1060.875
2663 | 0.24424 | 58.64 | 62.371 | 0.00079191 | 26.735 | 1087.6 |  | 2663 | 58.64 | 0.24424 | 62.371 | 0.00079191 | 26.735 | 1087.6 | 1060.865
2664 | 0.24432 | 58.65 | 62.371 | 0.00079218 | 26.745 | 1087.6 |  | 2664 | 58.65 | 0.24432 | 62.371 | 0.00079218 | 26.745 | 1087.6 | 1060.855
2665 | 0.24441 | 58.66 | 62.371 | 0.00079245 | 26.755 | 1087.6 |  | 2665 | 58.66 | 0.24441 | 62.371 | 0.00079245 | 26.755 | 1087.6 | 1060.845
2666 | 0.2445 | 58.67 | 62.371 | 0.00079272 | 26.765 | 1087.6 |  | 2666 | 58.67 | 0.2445 | 62.371 | 0.00079272 | 26.765 | 1087.6 | 1060.835
2667 | 0.24459 | 58.68 | 62.371 | 0.00079299 | 26.775 | 1087.6 |  | 2667 | 58.68 | 0.24459 | 62.371 | 0.00079299 | 26.775 | 1087.6 | 1060.825
2668 | 0.24467 | 58.69 | 62.371 | 0.00079326 | 26.785 | 1087.6 |  | 2668 | 58.69 | 0.24467 | 62.371 | 0.00079326 | 26.785 | 1087.6 | 1060.815
2669 | 0.24476 | 58.7 | 62.371 | 0.00079353 | 26.795 | 1087.6 |  | 2669 | 58.7 | 0.24476 | 62.371 | 0.00079353 | 26.795 | 1087.6 | 1060.805
2670 | 0.24485 | 58.71 | 62.371 | 0.0007938 | 26.805 | 1087.6 |  | 2670 | 58.71 | 0.24485 | 62.371 | 0.0007938 | 26.805 | 1087.6 | 1060.795
2671 | 0.24494 | 58.72 | 62.37 | 0.00079407 | 26.815 | 1087.6 |  | 2671 | 58.72 | 0.24494 | 62.37 | 0.00079407 | 26.815 | 1087.6 | 1060.785
2672 | 0.24502 | 58.73 | 62.37 | 0.00079433 | 26.825 | 1087.6 |  | 2672 | 58.73 | 0.24502 | 62.37 | 0.00079433 | 26.825 | 1087.6 | 1060.775
2673 | 0.24511 | 58.74 | 62.37 | 0.0007946 | 26.835 | 1087.6 |  | 2673 | 58.74 | 0.24511 | 62.37 | 0.0007946 | 26.835 | 1087.6 | 1060.765
2674 | 0.2452 | 58.75 | 62.37 | 0.00079487 | 26.845 | 1087.6 |  | 2674 | 58.75 | 0.2452 | 62.37 | 0.00079487 | 26.845 | 1087.6 | 1060.755
2675 | 0.24529 | 58.76 | 62.37 | 0.00079514 | 26.855 | 1087.6 |  | 2675 | 58.76 | 0.24529 | 62.37 | 0.00079514 | 26.855 | 1087.6 | 1060.745
2676 | 0.24538 | 58.77 | 62.37 | 0.00079541 | 26.865 | 1087.6 |  | 2676 | 58.77 | 0.24538 | 62.37 | 0.00079541 | 26.865 | 1087.6 | 1060.735
2677 | 0.24546 | 58.78 | 62.37 | 0.00079568 | 26.875 | 1087.6 |  | 2677 | 58.78 | 0.24546 | 62.37 | 0.00079568 | 26.875 | 1087.6 | 1060.725
2678 | 0.24555 | 58.79 | 62.37 | 0.00079595 | 26.885 | 1087.6 |  | 2678 | 58.79 | 0.24555 | 62.37 | 0.00079595 | 26.885 | 1087.6 | 1060.715
2679 | 0.24564 | 58.8 | 62.37 | 0.00079622 | 26.895 | 1087.6 |  | 2679 | 58.8 | 0.24564 | 62.37 | 0.00079622 | 26.895 | 1087.6 | 1060.705
2680 | 0.24573 | 58.81 | 62.37 | 0.00079649 | 26.905 | 1087.6 |  | 2680 | 58.81 | 0.24573 | 62.37 | 0.00079649 | 26.905 | 1087.6 | 1060.695
2681 | 0.24582 | 58.82 | 62.37 | 0.00079676 | 26.915 | 1087.6 |  | 2681 | 58.82 | 0.24582 | 62.37 | 0.00079676 | 26.915 | 1087.6 | 1060.685
2682 | 0.2459 | 58.83 | 62.37 | 0.00079703 | 26.925 | 1087.6 |  | 2682 | 58.83 | 0.2459 | 62.37 | 0.00079703 | 26.925 | 1087.6 | 1060.675
2683 | 0.24599 | 58.84 | 62.37 | 0.0007973 | 26.935 | 1087.6 |  | 2683 | 58.84 | 0.24599 | 62.37 | 0.0007973 | 26.935 | 1087.6 | 1060.665
2684 | 0.24608 | 58.85 | 62.37 | 0.00079757 | 26.945 | 1087.6 |  | 2684 | 58.85 | 0.24608 | 62.37 | 0.00079757 | 26.945 | 1087.6 | 1060.655
2685 | 0.24617 | 58.86 | 62.37 | 0.00079784 | 26.955 | 1087.7 |  | 2685 | 58.86 | 0.24617 | 62.37 | 0.00079784 | 26.955 | 1087.7 | 1060.745
2686 | 0.24626 | 58.87 | 62.37 | 0.00079811 | 26.965 | 1087.7 |  | 2686 | 58.87 | 0.24626 | 62.37 | 0.00079811 | 26.965 | 1087.7 | 1060.735
2687 | 0.24634 | 58.88 | 62.37 | 0.00079839 | 26.975 | 1087.7 |  | 2687 | 58.88 | 0.24634 | 62.37 | 0.00079839 | 26.975 | 1087.7 | 1060.725
2688 | 0.24643 | 58.89 | 62.37 | 0.00079866 | 26.985 | 1087.7 |  | 2688 | 58.89 | 0.24643 | 62.37 | 0.00079866 | 26.985 | 1087.7 | 1060.715
2689 | 0.24652 | 58.9 | 62.37 | 0.00079893 | 26.995 | 1087.7 |  | 2689 | 58.9 | 0.24652 | 62.37 | 0.00079893 | 26.995 | 1087.7 | 1060.705
2690 | 0.24661 | 58.91 | 62.37 | 0.0007992 | 27.005 | 1087.7 |  | 2690 | 58.91 | 0.24661 | 62.37 | 0.0007992 | 27.005 | 1087.7 | 1060.695
2691 | 0.2467 | 58.92 | 62.369 | 0.00079947 | 27.015 | 1087.7 |  | 2691 | 58.92 | 0.2467 | 62.369 | 0.00079947 | 27.015 | 1087.7 | 1060.685
2692 | 0.24679 | 58.93 | 62.369 | 0.00079974 | 27.025 | 1087.7 |  | 2692 | 58.93 | 0.24679 | 62.369 | 0.00079974 | 27.025 | 1087.7 | 1060.675
2693 | 0.24687 | 58.94 | 62.369 | 0.00080001 | 27.035 | 1087.7 |  | 2693 | 58.94 | 0.24687 | 62.369 | 0.00080001 | 27.035 | 1087.7 | 1060.665
2694 | 0.24696 | 58.95 | 62.369 | 0.00080028 | 27.045 | 1087.7 |  | 2694 | 58.95 | 0.24696 | 62.369 | 0.00080028 | 27.045 | 1087.7 | 1060.655
2695 | 0.24705 | 58.96 | 62.369 | 0.00080055 | 27.055 | 1087.7 |  | 2695 | 58.96 | 0.24705 | 62.369 | 0.00080055 | 27.055 | 1087.7 | 1060.645
2696 | 0.24714 | 58.97 | 62.369 | 0.00080082 | 27.065 | 1087.7 |  | 2696 | 58.97 | 0.24714 | 62.369 | 0.00080082 | 27.065 | 1087.7 | 1060.635
2697 | 0.24723 | 58.98 | 62.369 | 0.0008011 | 27.075 | 1087.7 |  | 2697 | 58.98 | 0.24723 | 62.369 | 0.0008011 | 27.075 | 1087.7 | 1060.625
2698 | 0.24732 | 58.99 | 62.369 | 0.00080137 | 27.085 | 1087.7 |  | 2698 | 58.99 | 0.24732 | 62.369 | 0.00080137 | 27.085 | 1087.7 | 1060.615
2699 | 0.2474 | 59 | 62.369 | 0.00080164 | 27.095 | 1087.7 |  | 2699 | 59 | 0.2474 | 62.369 | 0.00080164 | 27.095 | 1087.7 | 1060.605
2700 | 0.24749 | 59.01 | 62.369 | 0.00080191 | 27.105 | 1087.7 |  | 2700 | 59.01 | 0.24749 | 62.369 | 0.00080191 | 27.105 | 1087.7 | 1060.595
2701 | 0.24758 | 59.02 | 62.369 | 0.00080218 | 27.115 | 1087.7 |  | 2701 | 59.02 | 0.24758 | 62.369 | 0.00080218 | 27.115 | 1087.7 | 1060.585
2702 | 0.24767 | 59.03 | 62.369 | 0.00080245 | 27.125 | 1087.7 |  | 2702 | 59.03 | 0.24767 | 62.369 | 0.00080245 | 27.125 | 1087.7 | 1060.575
2703 | 0.24776 | 59.04 | 62.369 | 0.00080273 | 27.135 | 1087.7 |  | 2703 | 59.04 | 0.24776 | 62.369 | 0.00080273 | 27.135 | 1087.7 | 1060.565
2704 | 0.24785 | 59.05 | 62.369 | 0.000803 | 27.145 | 1087.7 |  | 2704 | 59.05 | 0.24785 | 62.369 | 0.000803 | 27.145 | 1087.7 | 1060.555
2705 | 0.24794 | 59.06 | 62.369 | 0.00080327 | 27.155 | 1087.7 |  | 2705 | 59.06 | 0.24794 | 62.369 | 0.00080327 | 27.155 | 1087.7 | 1060.545
2706 | 0.24802 | 59.07 | 62.369 | 0.00080354 | 27.165 | 1087.7 |  | 2706 | 59.07 | 0.24802 | 62.369 | 0.00080354 | 27.165 | 1087.7 | 1060.535
2707 | 0.24811 | 59.08 | 62.369 | 0.00080381 | 27.175 | 1087.7 |  | 2707 | 59.08 | 0.24811 | 62.369 | 0.00080381 | 27.175 | 1087.7 | 1060.525
2708 | 0.2482 | 59.09 | 62.369 | 0.00080409 | 27.185 | 1087.8 |  | 2708 | 59.09 | 0.2482 | 62.369 | 0.00080409 | 27.185 | 1087.8 | 1060.615
2709 | 0.24829 | 59.1 | 62.369 | 0.00080436 | 27.195 | 1087.8 |  | 2709 | 59.1 | 0.24829 | 62.369 | 0.00080436 | 27.195 | 1087.8 | 1060.605
2710 | 0.24838 | 59.11 | 62.368 | 0.00080463 | 27.205 | 1087.8 |  | 2710 | 59.11 | 0.24838 | 62.368 | 0.00080463 | 27.205 | 1087.8 | 1060.595
2711 | 0.24847 | 59.12 | 62.368 | 0.0008049 | 27.215 | 1087.8 |  | 2711 | 59.12 | 0.24847 | 62.368 | 0.0008049 | 27.215 | 1087.8 | 1060.585
2712 | 0.24856 | 59.13 | 62.368 | 0.00080518 | 27.225 | 1087.8 |  | 2712 | 59.13 | 0.24856 | 62.368 | 0.00080518 | 27.225 | 1087.8 | 1060.575
2713 | 0.24865 | 59.14 | 62.368 | 0.00080545 | 27.235 | 1087.8 |  | 2713 | 59.14 | 0.24865 | 62.368 | 0.00080545 | 27.235 | 1087.8 | 1060.565
2714 | 0.24874 | 59.15 | 62.368 | 0.00080572 | 27.245 | 1087.8 |  | 2714 | 59.15 | 0.24874 | 62.368 | 0.00080572 | 27.245 | 1087.8 | 1060.555
2715 | 0.24882 | 59.16 | 62.368 | 0.00080599 | 27.255 | 1087.8 |  | 2715 | 59.16 | 0.24882 | 62.368 | 0.00080599 | 27.255 | 1087.8 | 1060.545
2716 | 0.24891 | 59.17 | 62.368 | 0.00080627 | 27.265 | 1087.8 |  | 2716 | 59.17 | 0.24891 | 62.368 | 0.00080627 | 27.265 | 1087.8 | 1060.535
2717 | 0.249 | 59.18 | 62.368 | 0.00080654 | 27.275 | 1087.8 |  | 2717 | 59.18 | 0.249 | 62.368 | 0.00080654 | 27.275 | 1087.8 | 1060.525
2718 | 0.24909 | 59.19 | 62.368 | 0.00080681 | 27.285 | 1087.8 |  | 2718 | 59.19 | 0.24909 | 62.368 | 0.00080681 | 27.285 | 1087.8 | 1060.515
2719 | 0.24918 | 59.2 | 62.368 | 0.00080709 | 27.296 | 1087.8 |  | 2719 | 59.2 | 0.24918 | 62.368 | 0.00080709 | 27.296 | 1087.8 | 1060.504
2720 | 0.24927 | 59.21 | 62.368 | 0.00080736 | 27.306 | 1087.8 |  | 2720 | 59.21 | 0.24927 | 62.368 | 0.00080736 | 27.306 | 1087.8 | 1060.494
2721 | 0.24936 | 59.22 | 62.368 | 0.00080763 | 27.316 | 1087.8 |  | 2721 | 59.22 | 0.24936 | 62.368 | 0.00080763 | 27.316 | 1087.8 | 1060.484
2722 | 0.24945 | 59.23 | 62.368 | 0.00080791 | 27.326 | 1087.8 |  | 2722 | 59.23 | 0.24945 | 62.368 | 0.00080791 | 27.326 | 1087.8 | 1060.474
2723 | 0.24954 | 59.24 | 62.368 | 0.00080818 | 27.336 | 1087.8 |  | 2723 | 59.24 | 0.24954 | 62.368 | 0.00080818 | 27.336 | 1087.8 | 1060.464
2724 | 0.24963 | 59.25 | 62.368 | 0.00080845 | 27.346 | 1087.8 |  | 2724 | 59.25 | 0.24963 | 62.368 | 0.00080845 | 27.346 | 1087.8 | 1060.454
2725 | 0.24972 | 59.26 | 62.368 | 0.00080873 | 27.356 | 1087.8 |  | 2725 | 59.26 | 0.24972 | 62.368 | 0.00080873 | 27.356 | 1087.8 | 1060.444
2726 | 0.2498 | 59.27 | 62.368 | 0.000809 | 27.366 | 1087.8 |  | 2726 | 59.27 | 0.2498 | 62.368 | 0.000809 | 27.366 | 1087.8 | 1060.434
2727 | 0.24989 | 59.28 | 62.368 | 0.00080927 | 27.376 | 1087.8 |  | 2727 | 59.28 | 0.24989 | 62.368 | 0.00080927 | 27.376 | 1087.8 | 1060.424
2728 | 0.24998 | 59.29 | 62.368 | 0.00080955 | 27.386 | 1087.8 |  | 2728 | 59.29 | 0.24998 | 62.368 | 0.00080955 | 27.386 | 1087.8 | 1060.414
2729 | 0.25007 | 59.3 | 62.367 | 0.00080982 | 27.396 | 1087.8 |  | 2729 | 59.3 | 0.25007 | 62.367 | 0.00080982 | 27.396 | 1087.8 | 1060.404
2730 | 0.25016 | 59.31 | 62.367 | 0.0008101 | 27.406 | 1087.9 |  | 2730 | 59.31 | 0.25016 | 62.367 | 0.0008101 | 27.406 | 1087.9 | 1060.494
2731 | 0.25025 | 59.32 | 62.367 | 0.00081037 | 27.416 | 1087.9 |  | 2731 | 59.32 | 0.25025 | 62.367 | 0.00081037 | 27.416 | 1087.9 | 1060.484
2732 | 0.25034 | 59.33 | 62.367 | 0.00081064 | 27.426 | 1087.9 |  | 2732 | 59.33 | 0.25034 | 62.367 | 0.00081064 | 27.426 | 1087.9 | 1060.474
2733 | 0.25043 | 59.34 | 62.367 | 0.00081092 | 27.436 | 1087.9 |  | 2733 | 59.34 | 0.25043 | 62.367 | 0.00081092 | 27.436 | 1087.9 | 1060.464
2734 | 0.25052 | 59.35 | 62.367 | 0.00081119 | 27.446 | 1087.9 |  | 2734 | 59.35 | 0.25052 | 62.367 | 0.00081119 | 27.446 | 1087.9 | 1060.454
2735 | 0.25061 | 59.36 | 62.367 | 0.00081147 | 27.456 | 1087.9 |  | 2735 | 59.36 | 0.25061 | 62.367 | 0.00081147 | 27.456 | 1087.9 | 1060.444
2736 | 0.2507 | 59.37 | 62.367 | 0.00081174 | 27.466 | 1087.9 |  | 2736 | 59.37 | 0.2507 | 62.367 | 0.00081174 | 27.466 | 1087.9 | 1060.434
2737 | 0.25079 | 59.38 | 62.367 | 0.00081202 | 27.476 | 1087.9 |  | 2737 | 59.38 | 0.25079 | 62.367 | 0.00081202 | 27.476 | 1087.9 | 1060.424
2738 | 0.25088 | 59.39 | 62.367 | 0.00081229 | 27.486 | 1087.9 |  | 2738 | 59.39 | 0.25088 | 62.367 | 0.00081229 | 27.486 | 1087.9 | 1060.414
2739 | 0.25097 | 59.4 | 62.367 | 0.00081257 | 27.496 | 1087.9 |  | 2739 | 59.4 | 0.25097 | 62.367 | 0.00081257 | 27.496 | 1087.9 | 1060.404
2740 | 0.25106 | 59.41 | 62.367 | 0.00081284 | 27.506 | 1087.9 |  | 2740 | 59.41 | 0.25106 | 62.367 | 0.00081284 | 27.506 | 1087.9 | 1060.394
2741 | 0.25115 | 59.42 | 62.367 | 0.00081312 | 27.516 | 1087.9 |  | 2741 | 59.42 | 0.25115 | 62.367 | 0.00081312 | 27.516 | 1087.9 | 1060.384
2742 | 0.25124 | 59.43 | 62.367 | 0.00081339 | 27.526 | 1087.9 |  | 2742 | 59.43 | 0.25124 | 62.367 | 0.00081339 | 27.526 | 1087.9 | 1060.374
2743 | 0.25133 | 59.44 | 62.367 | 0.00081367 | 27.536 | 1087.9 |  | 2743 | 59.44 | 0.25133 | 62.367 | 0.00081367 | 27.536 | 1087.9 | 1060.364
2744 | 0.25142 | 59.45 | 62.367 | 0.00081394 | 27.546 | 1087.9 |  | 2744 | 59.45 | 0.25142 | 62.367 | 0.00081394 | 27.546 | 1087.9 | 1060.354
2745 | 0.25151 | 59.46 | 62.367 | 0.00081422 | 27.556 | 1087.9 |  | 2745 | 59.46 | 0.25151 | 62.367 | 0.00081422 | 27.556 | 1087.9 | 1060.344
2746 | 0.2516 | 59.47 | 62.367 | 0.00081449 | 27.566 | 1087.9 |  | 2746 | 59.47 | 0.2516 | 62.367 | 0.00081449 | 27.566 | 1087.9 | 1060.334
2747 | 0.25169 | 59.48 | 62.367 | 0.00081477 | 27.576 | 1087.9 |  | 2747 | 59.48 | 0.25169 | 62.367 | 0.00081477 | 27.576 | 1087.9 | 1060.324
2748 | 0.25178 | 59.49 | 62.366 | 0.00081504 | 27.586 | 1087.9 |  | 2748 | 59.49 | 0.25178 | 62.366 | 0.00081504 | 27.586 | 1087.9 | 1060.314
2749 | 0.25187 | 59.5 | 62.366 | 0.00081532 | 27.596 | 1087.9 |  | 2749 | 59.5 | 0.25187 | 62.366 | 0.00081532 | 27.596 | 1087.9 | 1060.304
2750 | 0.25196 | 59.51 | 62.366 | 0.00081559 | 27.606 | 1087.9 |  | 2750 | 59.51 | 0.25196 | 62.366 | 0.00081559 | 27.606 | 1087.9 | 1060.294
2751 | 0.25205 | 59.52 | 62.366 | 0.00081587 | 27.616 | 1087.9 |  | 2751 | 59.52 | 0.25205 | 62.366 | 0.00081587 | 27.616 | 1087.9 | 1060.284
2752 | 0.25214 | 59.53 | 62.366 | 0.00081615 | 27.626 | 1087.9 |  | 2752 | 59.53 | 0.25214 | 62.366 | 0.00081615 | 27.626 | 1087.9 | 1060.274
2753 | 0.25223 | 59.54 | 62.366 | 0.00081642 | 27.636 | 1088 |  | 2753 | 59.54 | 0.25223 | 62.366 | 0.00081642 | 27.636 | 1088 | 1060.364
2754 | 0.25232 | 59.55 | 62.366 | 0.0008167 | 27.646 | 1088 |  | 2754 | 59.55 | 0.25232 | 62.366 | 0.0008167 | 27.646 | 1088 | 1060.354
2755 | 0.25241 | 59.56 | 62.366 | 0.00081697 | 27.656 | 1088 |  | 2755 | 59.56 | 0.25241 | 62.366 | 0.00081697 | 27.656 | 1088 | 1060.344
2756 | 0.2525 | 59.57 | 62.366 | 0.00081725 | 27.666 | 1088 |  | 2756 | 59.57 | 0.2525 | 62.366 | 0.00081725 | 27.666 | 1088 | 1060.334
2757 | 0.25259 | 59.58 | 62.366 | 0.00081753 | 27.676 | 1088 |  | 2757 | 59.58 | 0.25259 | 62.366 | 0.00081753 | 27.676 | 1088 | 1060.324
2758 | 0.25268 | 59.59 | 62.366 | 0.0008178 | 27.686 | 1088 |  | 2758 | 59.59 | 0.25268 | 62.366 | 0.0008178 | 27.686 | 1088 | 1060.314
2759 | 0.25277 | 59.6 | 62.366 | 0.00081808 | 27.696 | 1088 |  | 2759 | 59.6 | 0.25277 | 62.366 | 0.00081808 | 27.696 | 1088 | 1060.304
2760 | 0.25286 | 59.61 | 62.366 | 0.00081835 | 27.706 | 1088 |  | 2760 | 59.61 | 0.25286 | 62.366 | 0.00081835 | 27.706 | 1088 | 1060.294
2761 | 0.25295 | 59.62 | 62.366 | 0.00081863 | 27.716 | 1088 |  | 2761 | 59.62 | 0.25295 | 62.366 | 0.00081863 | 27.716 | 1088 | 1060.284
2762 | 0.25304 | 59.63 | 62.366 | 0.00081891 | 27.726 | 1088 |  | 2762 | 59.63 | 0.25304 | 62.366 | 0.00081891 | 27.726 | 1088 | 1060.274
2763 | 0.25313 | 59.64 | 62.366 | 0.00081918 | 27.736 | 1088 |  | 2763 | 59.64 | 0.25313 | 62.366 | 0.00081918 | 27.736 | 1088 | 1060.264
2764 | 0.25322 | 59.65 | 62.366 | 0.00081946 | 27.746 | 1088 |  | 2764 | 59.65 | 0.25322 | 62.366 | 0.00081946 | 27.746 | 1088 | 1060.254
2765 | 0.25331 | 59.66 | 62.366 | 0.00081974 | 27.756 | 1088 |  | 2765 | 59.66 | 0.25331 | 62.366 | 0.00081974 | 27.756 | 1088 | 1060.244
2766 | 0.2534 | 59.67 | 62.365 | 0.00082001 | 27.766 | 1088 |  | 2766 | 59.67 | 0.2534 | 62.365 | 0.00082001 | 27.766 | 1088 | 1060.234
2767 | 0.25349 | 59.68 | 62.365 | 0.00082029 | 27.776 | 1088 |  | 2767 | 59.68 | 0.25349 | 62.365 | 0.00082029 | 27.776 | 1088 | 1060.224
2768 | 0.25358 | 59.69 | 62.365 | 0.00082057 | 27.786 | 1088 |  | 2768 | 59.69 | 0.25358 | 62.365 | 0.00082057 | 27.786 | 1088 | 1060.214
2769 | 0.25367 | 59.7 | 62.365 | 0.00082085 | 27.796 | 1088 |  | 2769 | 59.7 | 0.25367 | 62.365 | 0.00082085 | 27.796 | 1088 | 1060.204
2770 | 0.25376 | 59.71 | 62.365 | 0.00082112 | 27.806 | 1088 |  | 2770 | 59.71 | 0.25376 | 62.365 | 0.00082112 | 27.806 | 1088 | 1060.194
2771 | 0.25385 | 59.72 | 62.365 | 0.0008214 | 27.816 | 1088 |  | 2771 | 59.72 | 0.25385 | 62.365 | 0.0008214 | 27.816 | 1088 | 1060.184
2772 | 0.25394 | 59.73 | 62.365 | 0.00082168 | 27.826 | 1088 |  | 2772 | 59.73 | 0.25394 | 62.365 | 0.00082168 | 27.826 | 1088 | 1060.174
2773 | 0.25403 | 59.74 | 62.365 | 0.00082196 | 27.836 | 1088 |  | 2773 | 59.74 | 0.25403 | 62.365 | 0.00082196 | 27.836 | 1088 | 1060.164
2774 | 0.25412 | 59.75 | 62.365 | 0.00082223 | 27.846 | 1088 |  | 2774 | 59.75 | 0.25412 | 62.365 | 0.00082223 | 27.846 | 1088 | 1060.154
2775 | 0.25421 | 59.76 | 62.365 | 0.00082251 | 27.856 | 1088 |  | 2775 | 59.76 | 0.25421 | 62.365 | 0.00082251 | 27.856 | 1088 | 1060.144
2776 | 0.2543 | 59.77 | 62.365 | 0.00082279 | 27.866 | 1088.1 |  | 2776 | 59.77 | 0.2543 | 62.365 | 0.00082279 | 27.866 | 1088.1 | 1060.234
2777 | 0.25439 | 59.78 | 62.365 | 0.00082307 | 27.876 | 1088.1 |  | 2777 | 59.78 | 0.25439 | 62.365 | 0.00082307 | 27.876 | 1088.1 | 1060.224
2778 | 0.25449 | 59.79 | 62.365 | 0.00082334 | 27.886 | 1088.1 |  | 2778 | 59.79 | 0.25449 | 62.365 | 0.00082334 | 27.886 | 1088.1 | 1060.214
2779 | 0.25458 | 59.8 | 62.365 | 0.00082362 | 27.896 | 1088.1 |  | 2779 | 59.8 | 0.25458 | 62.365 | 0.00082362 | 27.896 | 1088.1 | 1060.204
2780 | 0.25467 | 59.81 | 62.365 | 0.0008239 | 27.906 | 1088.1 |  | 2780 | 59.81 | 0.25467 | 62.365 | 0.0008239 | 27.906 | 1088.1 | 1060.194
2781 | 0.25476 | 59.82 | 62.365 | 0.00082418 | 27.916 | 1088.1 |  | 2781 | 59.82 | 0.25476 | 62.365 | 0.00082418 | 27.916 | 1088.1 | 1060.184
2782 | 0.25485 | 59.83 | 62.365 | 0.00082446 | 27.926 | 1088.1 |  | 2782 | 59.83 | 0.25485 | 62.365 | 0.00082446 | 27.926 | 1088.1 | 1060.174
2783 | 0.25494 | 59.84 | 62.365 | 0.00082474 | 27.936 | 1088.1 |  | 2783 | 59.84 | 0.25494 | 62.365 | 0.00082474 | 27.936 | 1088.1 | 1060.164
2784 | 0.25503 | 59.85 | 62.365 | 0.00082501 | 27.946 | 1088.1 |  | 2784 | 59.85 | 0.25503 | 62.365 | 0.00082501 | 27.946 | 1088.1 | 1060.154
2785 | 0.25512 | 59.86 | 62.364 | 0.00082529 | 27.956 | 1088.1 |  | 2785 | 59.86 | 0.25512 | 62.364 | 0.00082529 | 27.956 | 1088.1 | 1060.144
2786 | 0.25521 | 59.87 | 62.364 | 0.00082557 | 27.966 | 1088.1 |  | 2786 | 59.87 | 0.25521 | 62.364 | 0.00082557 | 27.966 | 1088.1 | 1060.134
2787 | 0.2553 | 59.88 | 62.364 | 0.00082585 | 27.976 | 1088.1 |  | 2787 | 59.88 | 0.2553 | 62.364 | 0.00082585 | 27.976 | 1088.1 | 1060.124
2788 | 0.25539 | 59.89 | 62.364 | 0.00082613 | 27.986 | 1088.1 |  | 2788 | 59.89 | 0.25539 | 62.364 | 0.00082613 | 27.986 | 1088.1 | 1060.114
2789 | 0.25549 | 59.9 | 62.364 | 0.00082641 | 27.996 | 1088.1 |  | 2789 | 59.9 | 0.25549 | 62.364 | 0.00082641 | 27.996 | 1088.1 | 1060.104
2790 | 0.25558 | 59.91 | 62.364 | 0.00082669 | 28.006 | 1088.1 |  | 2790 | 59.91 | 0.25558 | 62.364 | 0.00082669 | 28.006 | 1088.1 | 1060.094
2791 | 0.25567 | 59.92 | 62.364 | 0.00082696 | 28.016 | 1088.1 |  | 2791 | 59.92 | 0.25567 | 62.364 | 0.00082696 | 28.016 | 1088.1 | 1060.084
2792 | 0.25576 | 59.93 | 62.364 | 0.00082724 | 28.026 | 1088.1 |  | 2792 | 59.93 | 0.25576 | 62.364 | 0.00082724 | 28.026 | 1088.1 | 1060.074
2793 | 0.25585 | 59.94 | 62.364 | 0.00082752 | 28.036 | 1088.1 |  | 2793 | 59.94 | 0.25585 | 62.364 | 0.00082752 | 28.036 | 1088.1 | 1060.064
2794 | 0.25594 | 59.95 | 62.364 | 0.0008278 | 28.046 | 1088.1 |  | 2794 | 59.95 | 0.25594 | 62.364 | 0.0008278 | 28.046 | 1088.1 | 1060.054
2795 | 0.25603 | 59.96 | 62.364 | 0.00082808 | 28.056 | 1088.1 |  | 2795 | 59.96 | 0.25603 | 62.364 | 0.00082808 | 28.056 | 1088.1 | 1060.044
2796 | 0.25612 | 59.97 | 62.364 | 0.00082836 | 28.066 | 1088.1 |  | 2796 | 59.97 | 0.25612 | 62.364 | 0.00082836 | 28.066 | 1088.1 | 1060.034
2797 | 0.25621 | 59.98 | 62.364 | 0.00082864 | 28.076 | 1088.1 |  | 2797 | 59.98 | 0.25621 | 62.364 | 0.00082864 | 28.076 | 1088.1 | 1060.024
2798 | 0.25631 | 59.99 | 62.364 | 0.00082892 | 28.086 | 1088.1 |  | 2798 | 59.99 | 0.25631 | 62.364 | 0.00082892 | 28.086 | 1088.1 | 1060.014
2799 | 0.2564 | 60 | 62.364 | 0.0008292 | 28.096 | 1088.2 |  | 2799 | 60 | 0.2564 | 62.364 | 0.0008292 | 28.096 | 1088.2 | 1060.104
2800 | 0.25649 | 60.01 | 62.364 | 0.00082948 | 28.106 | 1088.2 |  | 2800 | 60.01 | 0.25649 | 62.364 | 0.00082948 | 28.106 | 1088.2 | 1060.094
2801 | 0.25658 | 60.02 | 62.364 | 0.00082976 | 28.116 | 1088.2 |  | 2801 | 60.02 | 0.25658 | 62.364 | 0.00082976 | 28.116 | 1088.2 | 1060.084
2802 | 0.25667 | 60.03 | 62.364 | 0.00083004 | 28.126 | 1088.2 |  | 2802 | 60.03 | 0.25667 | 62.364 | 0.00083004 | 28.126 | 1088.2 | 1060.074
2803 | 0.25676 | 60.04 | 62.363 | 0.00083032 | 28.136 | 1088.2 |  | 2803 | 60.04 | 0.25676 | 62.363 | 0.00083032 | 28.136 | 1088.2 | 1060.064
2804 | 0.25685 | 60.05 | 62.363 | 0.0008306 | 28.146 | 1088.2 |  | 2804 | 60.05 | 0.25685 | 62.363 | 0.0008306 | 28.146 | 1088.2 | 1060.054
2805 | 0.25695 | 60.06 | 62.363 | 0.00083088 | 28.156 | 1088.2 |  | 2805 | 60.06 | 0.25695 | 62.363 | 0.00083088 | 28.156 | 1088.2 | 1060.044
2806 | 0.25704 | 60.07 | 62.363 | 0.00083116 | 28.166 | 1088.2 |  | 2806 | 60.07 | 0.25704 | 62.363 | 0.00083116 | 28.166 | 1088.2 | 1060.034
2807 | 0.25713 | 60.08 | 62.363 | 0.00083144 | 28.176 | 1088.2 |  | 2807 | 60.08 | 0.25713 | 62.363 | 0.00083144 | 28.176 | 1088.2 | 1060.024
2808 | 0.25722 | 60.09 | 62.363 | 0.00083172 | 28.186 | 1088.2 |  | 2808 | 60.09 | 0.25722 | 62.363 | 0.00083172 | 28.186 | 1088.2 | 1060.014
2809 | 0.25731 | 60.1 | 62.363 | 0.000832 | 28.196 | 1088.2 |  | 2809 | 60.1 | 0.25731 | 62.363 | 0.000832 | 28.196 | 1088.2 | 1060.004
2810 | 0.2574 | 60.11 | 62.363 | 0.00083228 | 28.206 | 1088.2 |  | 2810 | 60.11 | 0.2574 | 62.363 | 0.00083228 | 28.206 | 1088.2 | 1059.994
2811 | 0.2575 | 60.12 | 62.363 | 0.00083256 | 28.216 | 1088.2 |  | 2811 | 60.12 | 0.2575 | 62.363 | 0.00083256 | 28.216 | 1088.2 | 1059.984
2812 | 0.25759 | 60.13 | 62.363 | 0.00083284 | 28.227 | 1088.2 |  | 2812 | 60.13 | 0.25759 | 62.363 | 0.00083284 | 28.227 | 1088.2 | 1059.973
2813 | 0.25768 | 60.14 | 62.363 | 0.00083312 | 28.237 | 1088.2 |  | 2813 | 60.14 | 0.25768 | 62.363 | 0.00083312 | 28.237 | 1088.2 | 1059.963
2814 | 0.25777 | 60.15 | 62.363 | 0.0008334 | 28.247 | 1088.2 |  | 2814 | 60.15 | 0.25777 | 62.363 | 0.0008334 | 28.247 | 1088.2 | 1059.953
2815 | 0.25786 | 60.16 | 62.363 | 0.00083368 | 28.257 | 1088.2 |  | 2815 | 60.16 | 0.25786 | 62.363 | 0.00083368 | 28.257 | 1088.2 | 1059.943
2816 | 0.25795 | 60.17 | 62.363 | 0.00083397 | 28.267 | 1088.2 |  | 2816 | 60.17 | 0.25795 | 62.363 | 0.00083397 | 28.267 | 1088.2 | 1059.933
2817 | 0.25805 | 60.18 | 62.363 | 0.00083425 | 28.277 | 1088.2 |  | 2817 | 60.18 | 0.25805 | 62.363 | 0.00083425 | 28.277 | 1088.2 | 1059.923
2818 | 0.25814 | 60.19 | 62.363 | 0.00083453 | 28.287 | 1088.2 |  | 2818 | 60.19 | 0.25814 | 62.363 | 0.00083453 | 28.287 | 1088.2 | 1059.913
2819 | 0.25823 | 60.2 | 62.363 | 0.00083481 | 28.297 | 1088.2 |  | 2819 | 60.2 | 0.25823 | 62.363 | 0.00083481 | 28.297 | 1088.2 | 1059.903
2820 | 0.25832 | 60.21 | 62.363 | 0.00083509 | 28.307 | 1088.2 |  | 2820 | 60.21 | 0.25832 | 62.363 | 0.00083509 | 28.307 | 1088.2 | 1059.893
2821 | 0.25841 | 60.22 | 62.363 | 0.00083537 | 28.317 | 1088.2 |  | 2821 | 60.22 | 0.25841 | 62.363 | 0.00083537 | 28.317 | 1088.2 | 1059.883
2822 | 0.25851 | 60.23 | 62.362 | 0.00083565 | 28.327 | 1088.3 |  | 2822 | 60.23 | 0.25851 | 62.362 | 0.00083565 | 28.327 | 1088.3 | 1059.973
2823 | 0.2586 | 60.24 | 62.362 | 0.00083594 | 28.337 | 1088.3 |  | 2823 | 60.24 | 0.2586 | 62.362 | 0.00083594 | 28.337 | 1088.3 | 1059.963
2824 | 0.25869 | 60.25 | 62.362 | 0.00083622 | 28.347 | 1088.3 |  | 2824 | 60.25 | 0.25869 | 62.362 | 0.00083622 | 28.347 | 1088.3 | 1059.953
2825 | 0.25878 | 60.26 | 62.362 | 0.0008365 | 28.357 | 1088.3 |  | 2825 | 60.26 | 0.25878 | 62.362 | 0.0008365 | 28.357 | 1088.3 | 1059.943
2826 | 0.25887 | 60.27 | 62.362 | 0.00083678 | 28.367 | 1088.3 |  | 2826 | 60.27 | 0.25887 | 62.362 | 0.00083678 | 28.367 | 1088.3 | 1059.933
2827 | 0.25897 | 60.28 | 62.362 | 0.00083706 | 28.377 | 1088.3 |  | 2827 | 60.28 | 0.25897 | 62.362 | 0.00083706 | 28.377 | 1088.3 | 1059.923
2828 | 0.25906 | 60.29 | 62.362 | 0.00083734 | 28.387 | 1088.3 |  | 2828 | 60.29 | 0.25906 | 62.362 | 0.00083734 | 28.387 | 1088.3 | 1059.913
2829 | 0.25915 | 60.3 | 62.362 | 0.00083763 | 28.397 | 1088.3 |  | 2829 | 60.3 | 0.25915 | 62.362 | 0.00083763 | 28.397 | 1088.3 | 1059.903
2830 | 0.25924 | 60.31 | 62.362 | 0.00083791 | 28.407 | 1088.3 |  | 2830 | 60.31 | 0.25924 | 62.362 | 0.00083791 | 28.407 | 1088.3 | 1059.893
2831 | 0.25934 | 60.32 | 62.362 | 0.00083819 | 28.417 | 1088.3 |  | 2831 | 60.32 | 0.25934 | 62.362 | 0.00083819 | 28.417 | 1088.3 | 1059.883
2832 | 0.25943 | 60.33 | 62.362 | 0.00083847 | 28.427 | 1088.3 |  | 2832 | 60.33 | 0.25943 | 62.362 | 0.00083847 | 28.427 | 1088.3 | 1059.873
2833 | 0.25952 | 60.34 | 62.362 | 0.00083876 | 28.437 | 1088.3 |  | 2833 | 60.34 | 0.25952 | 62.362 | 0.00083876 | 28.437 | 1088.3 | 1059.863
2834 | 0.25961 | 60.35 | 62.362 | 0.00083904 | 28.447 | 1088.3 |  | 2834 | 60.35 | 0.25961 | 62.362 | 0.00083904 | 28.447 | 1088.3 | 1059.853
2835 | 0.2597 | 60.36 | 62.362 | 0.00083932 | 28.457 | 1088.3 |  | 2835 | 60.36 | 0.2597 | 62.362 | 0.00083932 | 28.457 | 1088.3 | 1059.843
2836 | 0.2598 | 60.37 | 62.362 | 0.0008396 | 28.467 | 1088.3 |  | 2836 | 60.37 | 0.2598 | 62.362 | 0.0008396 | 28.467 | 1088.3 | 1059.833
2837 | 0.25989 | 60.38 | 62.362 | 0.00083989 | 28.477 | 1088.3 |  | 2837 | 60.38 | 0.25989 | 62.362 | 0.00083989 | 28.477 | 1088.3 | 1059.823
2838 | 0.25998 | 60.39 | 62.362 | 0.00084017 | 28.487 | 1088.3 |  | 2838 | 60.39 | 0.25998 | 62.362 | 0.00084017 | 28.487 | 1088.3 | 1059.813
2839 | 0.26007 | 60.4 | 62.362 | 0.00084045 | 28.497 | 1088.3 |  | 2839 | 60.4 | 0.26007 | 62.362 | 0.00084045 | 28.497 | 1088.3 | 1059.803
2840 | 0.26017 | 60.41 | 62.361 | 0.00084074 | 28.507 | 1088.3 |  | 2840 | 60.41 | 0.26017 | 62.361 | 0.00084074 | 28.507 | 1088.3 | 1059.793
2841 | 0.26026 | 60.42 | 62.361 | 0.00084102 | 28.517 | 1088.3 |  | 2841 | 60.42 | 0.26026 | 62.361 | 0.00084102 | 28.517 | 1088.3 | 1059.783
2842 | 0.26035 | 60.43 | 62.361 | 0.0008413 | 28.527 | 1088.3 |  | 2842 | 60.43 | 0.26035 | 62.361 | 0.0008413 | 28.527 | 1088.3 | 1059.773
2843 | 0.26044 | 60.44 | 62.361 | 0.00084158 | 28.537 | 1088.3 |  | 2843 | 60.44 | 0.26044 | 62.361 | 0.00084158 | 28.537 | 1088.3 | 1059.763
2844 | 0.26054 | 60.45 | 62.361 | 0.00084187 | 28.547 | 1088.3 |  | 2844 | 60.45 | 0.26054 | 62.361 | 0.00084187 | 28.547 | 1088.3 | 1059.753
2845 | 0.26063 | 60.46 | 62.361 | 0.00084215 | 28.557 | 1088.4 |  | 2845 | 60.46 | 0.26063 | 62.361 | 0.00084215 | 28.557 | 1088.4 | 1059.843
2846 | 0.26072 | 60.47 | 62.361 | 0.00084243 | 28.567 | 1088.4 |  | 2846 | 60.47 | 0.26072 | 62.361 | 0.00084243 | 28.567 | 1088.4 | 1059.833
2847 | 0.26081 | 60.48 | 62.361 | 0.00084272 | 28.577 | 1088.4 |  | 2847 | 60.48 | 0.26081 | 62.361 | 0.00084272 | 28.577 | 1088.4 | 1059.823
2848 | 0.26091 | 60.49 | 62.361 | 0.000843 | 28.587 | 1088.4 |  | 2848 | 60.49 | 0.26091 | 62.361 | 0.000843 | 28.587 | 1088.4 | 1059.813
2849 | 0.261 | 60.5 | 62.361 | 0.00084329 | 28.597 | 1088.4 |  | 2849 | 60.5 | 0.261 | 62.361 | 0.00084329 | 28.597 | 1088.4 | 1059.803
2850 | 0.26109 | 60.51 | 62.361 | 0.00084357 | 28.607 | 1088.4 |  | 2850 | 60.51 | 0.26109 | 62.361 | 0.00084357 | 28.607 | 1088.4 | 1059.793
2851 | 0.26119 | 60.52 | 62.361 | 0.00084385 | 28.617 | 1088.4 |  | 2851 | 60.52 | 0.26119 | 62.361 | 0.00084385 | 28.617 | 1088.4 | 1059.783
2852 | 0.26128 | 60.53 | 62.361 | 0.00084414 | 28.627 | 1088.4 |  | 2852 | 60.53 | 0.26128 | 62.361 | 0.00084414 | 28.627 | 1088.4 | 1059.773
2853 | 0.26137 | 60.54 | 62.361 | 0.00084442 | 28.637 | 1088.4 |  | 2853 | 60.54 | 0.26137 | 62.361 | 0.00084442 | 28.637 | 1088.4 | 1059.763
2854 | 0.26146 | 60.55 | 62.361 | 0.00084471 | 28.647 | 1088.4 |  | 2854 | 60.55 | 0.26146 | 62.361 | 0.00084471 | 28.647 | 1088.4 | 1059.753
2855 | 0.26156 | 60.56 | 62.361 | 0.00084499 | 28.657 | 1088.4 |  | 2855 | 60.56 | 0.26156 | 62.361 | 0.00084499 | 28.657 | 1088.4 | 1059.743
2856 | 0.26165 | 60.57 | 62.361 | 0.00084527 | 28.667 | 1088.4 |  | 2856 | 60.57 | 0.26165 | 62.361 | 0.00084527 | 28.667 | 1088.4 | 1059.733
2857 | 0.26174 | 60.58 | 62.361 | 0.00084556 | 28.677 | 1088.4 |  | 2857 | 60.58 | 0.26174 | 62.361 | 0.00084556 | 28.677 | 1088.4 | 1059.723
2858 | 0.26184 | 60.59 | 62.36 | 0.00084584 | 28.687 | 1088.4 |  | 2858 | 60.59 | 0.26184 | 62.36 | 0.00084584 | 28.687 | 1088.4 | 1059.713
2859 | 0.26193 | 60.6 | 62.36 | 0.00084613 | 28.697 | 1088.4 |  | 2859 | 60.6 | 0.26193 | 62.36 | 0.00084613 | 28.697 | 1088.4 | 1059.703
2860 | 0.26202 | 60.61 | 62.36 | 0.00084641 | 28.707 | 1088.4 |  | 2860 | 60.61 | 0.26202 | 62.36 | 0.00084641 | 28.707 | 1088.4 | 1059.693
2861 | 0.26212 | 60.62 | 62.36 | 0.0008467 | 28.717 | 1088.4 |  | 2861 | 60.62 | 0.26212 | 62.36 | 0.0008467 | 28.717 | 1088.4 | 1059.683
2862 | 0.26221 | 60.63 | 62.36 | 0.00084698 | 28.727 | 1088.4 |  | 2862 | 60.63 | 0.26221 | 62.36 | 0.00084698 | 28.727 | 1088.4 | 1059.673
2863 | 0.2623 | 60.64 | 62.36 | 0.00084727 | 28.737 | 1088.4 |  | 2863 | 60.64 | 0.2623 | 62.36 | 0.00084727 | 28.737 | 1088.4 | 1059.663
2864 | 0.2624 | 60.65 | 62.36 | 0.00084755 | 28.747 | 1088.4 |  | 2864 | 60.65 | 0.2624 | 62.36 | 0.00084755 | 28.747 | 1088.4 | 1059.653
2865 | 0.26249 | 60.66 | 62.36 | 0.00084784 | 28.757 | 1088.4 |  | 2865 | 60.66 | 0.26249 | 62.36 | 0.00084784 | 28.757 | 1088.4 | 1059.643
2866 | 0.26258 | 60.67 | 62.36 | 0.00084812 | 28.767 | 1088.4 |  | 2866 | 60.67 | 0.26258 | 62.36 | 0.00084812 | 28.767 | 1088.4 | 1059.633
2867 | 0.26268 | 60.68 | 62.36 | 0.00084841 | 28.777 | 1088.4 |  | 2867 | 60.68 | 0.26268 | 62.36 | 0.00084841 | 28.777 | 1088.4 | 1059.623
2868 | 0.26277 | 60.69 | 62.36 | 0.00084869 | 28.787 | 1088.5 |  | 2868 | 60.69 | 0.26277 | 62.36 | 0.00084869 | 28.787 | 1088.5 | 1059.713
2869 | 0.26286 | 60.7 | 62.36 | 0.00084898 | 28.797 | 1088.5 |  | 2869 | 60.7 | 0.26286 | 62.36 | 0.00084898 | 28.797 | 1088.5 | 1059.703
2870 | 0.26296 | 60.71 | 62.36 | 0.00084926 | 28.807 | 1088.5 |  | 2870 | 60.71 | 0.26296 | 62.36 | 0.00084926 | 28.807 | 1088.5 | 1059.693
2871 | 0.26305 | 60.72 | 62.36 | 0.00084955 | 28.817 | 1088.5 |  | 2871 | 60.72 | 0.26305 | 62.36 | 0.00084955 | 28.817 | 1088.5 | 1059.683
2872 | 0.26314 | 60.73 | 62.36 | 0.00084983 | 28.827 | 1088.5 |  | 2872 | 60.73 | 0.26314 | 62.36 | 0.00084983 | 28.827 | 1088.5 | 1059.673
2873 | 0.26324 | 60.74 | 62.36 | 0.00085012 | 28.837 | 1088.5 |  | 2873 | 60.74 | 0.26324 | 62.36 | 0.00085012 | 28.837 | 1088.5 | 1059.663
2874 | 0.26333 | 60.75 | 62.36 | 0.00085041 | 28.847 | 1088.5 |  | 2874 | 60.75 | 0.26333 | 62.36 | 0.00085041 | 28.847 | 1088.5 | 1059.653
2875 | 0.26342 | 60.76 | 62.36 | 0.00085069 | 28.857 | 1088.5 |  | 2875 | 60.76 | 0.26342 | 62.36 | 0.00085069 | 28.857 | 1088.5 | 1059.643
2876 | 0.26352 | 60.77 | 62.359 | 0.00085098 | 28.867 | 1088.5 |  | 2876 | 60.77 | 0.26352 | 62.359 | 0.00085098 | 28.867 | 1088.5 | 1059.633
2877 | 0.26361 | 60.78 | 62.359 | 0.00085126 | 28.877 | 1088.5 |  | 2877 | 60.78 | 0.26361 | 62.359 | 0.00085126 | 28.877 | 1088.5 | 1059.623
2878 | 0.2637 | 60.79 | 62.359 | 0.00085155 | 28.887 | 1088.5 |  | 2878 | 60.79 | 0.2637 | 62.359 | 0.00085155 | 28.887 | 1088.5 | 1059.613
2879 | 0.2638 | 60.8 | 62.359 | 0.00085184 | 28.897 | 1088.5 |  | 2879 | 60.8 | 0.2638 | 62.359 | 0.00085184 | 28.897 | 1088.5 | 1059.603
2880 | 0.26389 | 60.81 | 62.359 | 0.00085212 | 28.907 | 1088.5 |  | 2880 | 60.81 | 0.26389 | 62.359 | 0.00085212 | 28.907 | 1088.5 | 1059.593
2881 | 0.26398 | 60.82 | 62.359 | 0.00085241 | 28.917 | 1088.5 |  | 2881 | 60.82 | 0.26398 | 62.359 | 0.00085241 | 28.917 | 1088.5 | 1059.583
2882 | 0.26408 | 60.83 | 62.359 | 0.0008527 | 28.927 | 1088.5 |  | 2882 | 60.83 | 0.26408 | 62.359 | 0.0008527 | 28.927 | 1088.5 | 1059.573
2883 | 0.26417 | 60.84 | 62.359 | 0.00085298 | 28.937 | 1088.5 |  | 2883 | 60.84 | 0.26417 | 62.359 | 0.00085298 | 28.937 | 1088.5 | 1059.563
2884 | 0.26427 | 60.85 | 62.359 | 0.00085327 | 28.947 | 1088.5 |  | 2884 | 60.85 | 0.26427 | 62.359 | 0.00085327 | 28.947 | 1088.5 | 1059.553
2885 | 0.26436 | 60.86 | 62.359 | 0.00085356 | 28.957 | 1088.5 |  | 2885 | 60.86 | 0.26436 | 62.359 | 0.00085356 | 28.957 | 1088.5 | 1059.543
2886 | 0.26445 | 60.87 | 62.359 | 0.00085384 | 28.967 | 1088.5 |  | 2886 | 60.87 | 0.26445 | 62.359 | 0.00085384 | 28.967 | 1088.5 | 1059.533
2887 | 0.26455 | 60.88 | 62.359 | 0.00085413 | 28.977 | 1088.5 |  | 2887 | 60.88 | 0.26455 | 62.359 | 0.00085413 | 28.977 | 1088.5 | 1059.523
2888 | 0.26464 | 60.89 | 62.359 | 0.00085442 | 28.987 | 1088.5 |  | 2888 | 60.89 | 0.26464 | 62.359 | 0.00085442 | 28.987 | 1088.5 | 1059.513
2889 | 0.26474 | 60.9 | 62.359 | 0.0008547 | 28.997 | 1088.5 |  | 2889 | 60.9 | 0.26474 | 62.359 | 0.0008547 | 28.997 | 1088.5 | 1059.503
2890 | 0.26483 | 60.91 | 62.359 | 0.00085499 | 29.007 | 1088.5 |  | 2890 | 60.91 | 0.26483 | 62.359 | 0.00085499 | 29.007 | 1088.5 | 1059.493
2891 | 0.26492 | 60.92 | 62.359 | 0.00085528 | 29.017 | 1088.6 |  | 2891 | 60.92 | 0.26492 | 62.359 | 0.00085528 | 29.017 | 1088.6 | 1059.583
2892 | 0.26502 | 60.93 | 62.359 | 0.00085557 | 29.027 | 1088.6 |  | 2892 | 60.93 | 0.26502 | 62.359 | 0.00085557 | 29.027 | 1088.6 | 1059.573
2893 | 0.26511 | 60.94 | 62.358 | 0.00085585 | 29.037 | 1088.6 |  | 2893 | 60.94 | 0.26511 | 62.358 | 0.00085585 | 29.037 | 1088.6 | 1059.563
2894 | 0.26521 | 60.95 | 62.358 | 0.00085614 | 29.047 | 1088.6 |  | 2894 | 60.95 | 0.26521 | 62.358 | 0.00085614 | 29.047 | 1088.6 | 1059.553
2895 | 0.2653 | 60.96 | 62.358 | 0.00085643 | 29.057 | 1088.6 |  | 2895 | 60.96 | 0.2653 | 62.358 | 0.00085643 | 29.057 | 1088.6 | 1059.543
2896 | 0.26539 | 60.97 | 62.358 | 0.00085672 | 29.067 | 1088.6 |  | 2896 | 60.97 | 0.26539 | 62.358 | 0.00085672 | 29.067 | 1088.6 | 1059.533
2897 | 0.26549 | 60.98 | 62.358 | 0.000857 | 29.077 | 1088.6 |  | 2897 | 60.98 | 0.26549 | 62.358 | 0.000857 | 29.077 | 1088.6 | 1059.523
2898 | 0.26558 | 60.99 | 62.358 | 0.00085729 | 29.087 | 1088.6 |  | 2898 | 60.99 | 0.26558 | 62.358 | 0.00085729 | 29.087 | 1088.6 | 1059.513
2899 | 0.26568 | 61 | 62.358 | 0.00085758 | 29.097 | 1088.6 |  | 2899 | 61 | 0.26568 | 62.358 | 0.00085758 | 29.097 | 1088.6 | 1059.503
2900 | 0.26577 | 61.01 | 62.358 | 0.00085787 | 29.107 | 1088.6 |  | 2900 | 61.01 | 0.26577 | 62.358 | 0.00085787 | 29.107 | 1088.6 | 1059.493
2901 | 0.26586 | 61.02 | 62.358 | 0.00085816 | 29.117 | 1088.6 |  | 2901 | 61.02 | 0.26586 | 62.358 | 0.00085816 | 29.117 | 1088.6 | 1059.483
2902 | 0.26596 | 61.03 | 62.358 | 0.00085844 | 29.127 | 1088.6 |  | 2902 | 61.03 | 0.26596 | 62.358 | 0.00085844 | 29.127 | 1088.6 | 1059.473
2903 | 0.26605 | 61.04 | 62.358 | 0.00085873 | 29.137 | 1088.6 |  | 2903 | 61.04 | 0.26605 | 62.358 | 0.00085873 | 29.137 | 1088.6 | 1059.463
2904 | 0.26615 | 61.05 | 62.358 | 0.00085902 | 29.147 | 1088.6 |  | 2904 | 61.05 | 0.26615 | 62.358 | 0.00085902 | 29.147 | 1088.6 | 1059.453
2905 | 0.26624 | 61.06 | 62.358 | 0.00085931 | 29.157 | 1088.6 |  | 2905 | 61.06 | 0.26624 | 62.358 | 0.00085931 | 29.157 | 1088.6 | 1059.443
2906 | 0.26634 | 61.07 | 62.358 | 0.0008596 | 29.167 | 1088.6 |  | 2906 | 61.07 | 0.26634 | 62.358 | 0.0008596 | 29.167 | 1088.6 | 1059.433
2907 | 0.26643 | 61.08 | 62.358 | 0.00085989 | 29.177 | 1088.6 |  | 2907 | 61.08 | 0.26643 | 62.358 | 0.00085989 | 29.177 | 1088.6 | 1059.423
2908 | 0.26653 | 61.09 | 62.358 | 0.00086017 | 29.187 | 1088.6 |  | 2908 | 61.09 | 0.26653 | 62.358 | 0.00086017 | 29.187 | 1088.6 | 1059.413
2909 | 0.26662 | 61.1 | 62.358 | 0.00086046 | 29.197 | 1088.6 |  | 2909 | 61.1 | 0.26662 | 62.358 | 0.00086046 | 29.197 | 1088.6 | 1059.403
2910 | 0.26671 | 61.11 | 62.358 | 0.00086075 | 29.207 | 1088.6 |  | 2910 | 61.11 | 0.26671 | 62.358 | 0.00086075 | 29.207 | 1088.6 | 1059.393
2911 | 0.26681 | 61.12 | 62.357 | 0.00086104 | 29.217 | 1088.6 |  | 2911 | 61.12 | 0.26681 | 62.357 | 0.00086104 | 29.217 | 1088.6 | 1059.383
2912 | 0.2669 | 61.13 | 62.357 | 0.00086133 | 29.227 | 1088.6 |  | 2912 | 61.13 | 0.2669 | 62.357 | 0.00086133 | 29.227 | 1088.6 | 1059.373
2913 | 0.267 | 61.14 | 62.357 | 0.00086162 | 29.237 | 1088.6 |  | 2913 | 61.14 | 0.267 | 62.357 | 0.00086162 | 29.237 | 1088.6 | 1059.363
2914 | 0.26709 | 61.15 | 62.357 | 0.00086191 | 29.247 | 1088.7 |  | 2914 | 61.15 | 0.26709 | 62.357 | 0.00086191 | 29.247 | 1088.7 | 1059.453
2915 | 0.26719 | 61.16 | 62.357 | 0.0008622 | 29.257 | 1088.7 |  | 2915 | 61.16 | 0.26719 | 62.357 | 0.0008622 | 29.257 | 1088.7 | 1059.443
2916 | 0.26728 | 61.17 | 62.357 | 0.00086249 | 29.267 | 1088.7 |  | 2916 | 61.17 | 0.26728 | 62.357 | 0.00086249 | 29.267 | 1088.7 | 1059.433
2917 | 0.26738 | 61.18 | 62.357 | 0.00086278 | 29.277 | 1088.7 |  | 2917 | 61.18 | 0.26738 | 62.357 | 0.00086278 | 29.277 | 1088.7 | 1059.423
2918 | 0.26747 | 61.19 | 62.357 | 0.00086307 | 29.288 | 1088.7 |  | 2918 | 61.19 | 0.26747 | 62.357 | 0.00086307 | 29.288 | 1088.7 | 1059.412
2919 | 0.26757 | 61.2 | 62.357 | 0.00086335 | 29.298 | 1088.7 |  | 2919 | 61.2 | 0.26757 | 62.357 | 0.00086335 | 29.298 | 1088.7 | 1059.402
2920 | 0.26766 | 61.21 | 62.357 | 0.00086364 | 29.308 | 1088.7 |  | 2920 | 61.21 | 0.26766 | 62.357 | 0.00086364 | 29.308 | 1088.7 | 1059.392
2921 | 0.26776 | 61.22 | 62.357 | 0.00086393 | 29.318 | 1088.7 |  | 2921 | 61.22 | 0.26776 | 62.357 | 0.00086393 | 29.318 | 1088.7 | 1059.382
2922 | 0.26785 | 61.23 | 62.357 | 0.00086422 | 29.328 | 1088.7 |  | 2922 | 61.23 | 0.26785 | 62.357 | 0.00086422 | 29.328 | 1088.7 | 1059.372
2923 | 0.26795 | 61.24 | 62.357 | 0.00086451 | 29.338 | 1088.7 |  | 2923 | 61.24 | 0.26795 | 62.357 | 0.00086451 | 29.338 | 1088.7 | 1059.362
2924 | 0.26804 | 61.25 | 62.357 | 0.0008648 | 29.348 | 1088.7 |  | 2924 | 61.25 | 0.26804 | 62.357 | 0.0008648 | 29.348 | 1088.7 | 1059.352
2925 | 0.26814 | 61.26 | 62.357 | 0.00086509 | 29.358 | 1088.7 |  | 2925 | 61.26 | 0.26814 | 62.357 | 0.00086509 | 29.358 | 1088.7 | 1059.342
2926 | 0.26823 | 61.27 | 62.357 | 0.00086538 | 29.368 | 1088.7 |  | 2926 | 61.27 | 0.26823 | 62.357 | 0.00086538 | 29.368 | 1088.7 | 1059.332
2927 | 0.26833 | 61.28 | 62.357 | 0.00086567 | 29.378 | 1088.7 |  | 2927 | 61.28 | 0.26833 | 62.357 | 0.00086567 | 29.378 | 1088.7 | 1059.322
2928 | 0.26842 | 61.29 | 62.356 | 0.00086596 | 29.388 | 1088.7 |  | 2928 | 61.29 | 0.26842 | 62.356 | 0.00086596 | 29.388 | 1088.7 | 1059.312
2929 | 0.26852 | 61.3 | 62.356 | 0.00086626 | 29.398 | 1088.7 |  | 2929 | 61.3 | 0.26852 | 62.356 | 0.00086626 | 29.398 | 1088.7 | 1059.302
2930 | 0.26861 | 61.31 | 62.356 | 0.00086655 | 29.408 | 1088.7 |  | 2930 | 61.31 | 0.26861 | 62.356 | 0.00086655 | 29.408 | 1088.7 | 1059.292
2931 | 0.26871 | 61.32 | 62.356 | 0.00086684 | 29.418 | 1088.7 |  | 2931 | 61.32 | 0.26871 | 62.356 | 0.00086684 | 29.418 | 1088.7 | 1059.282
2932 | 0.2688 | 61.33 | 62.356 | 0.00086713 | 29.428 | 1088.7 |  | 2932 | 61.33 | 0.2688 | 62.356 | 0.00086713 | 29.428 | 1088.7 | 1059.272
2933 | 0.2689 | 61.34 | 62.356 | 0.00086742 | 29.438 | 1088.7 |  | 2933 | 61.34 | 0.2689 | 62.356 | 0.00086742 | 29.438 | 1088.7 | 1059.262
2934 | 0.26899 | 61.35 | 62.356 | 0.00086771 | 29.448 | 1088.7 |  | 2934 | 61.35 | 0.26899 | 62.356 | 0.00086771 | 29.448 | 1088.7 | 1059.252
2935 | 0.26909 | 61.36 | 62.356 | 0.000868 | 29.458 | 1088.7 |  | 2935 | 61.36 | 0.26909 | 62.356 | 0.000868 | 29.458 | 1088.7 | 1059.242
2936 | 0.26918 | 61.37 | 62.356 | 0.00086829 | 29.468 | 1088.7 |  | 2936 | 61.37 | 0.26918 | 62.356 | 0.00086829 | 29.468 | 1088.7 | 1059.232
2937 | 0.26928 | 61.38 | 62.356 | 0.00086858 | 29.478 | 1088.8 |  | 2937 | 61.38 | 0.26928 | 62.356 | 0.00086858 | 29.478 | 1088.8 | 1059.322
2938 | 0.26937 | 61.39 | 62.356 | 0.00086887 | 29.488 | 1088.8 |  | 2938 | 61.39 | 0.26937 | 62.356 | 0.00086887 | 29.488 | 1088.8 | 1059.312
2939 | 0.26947 | 61.4 | 62.356 | 0.00086916 | 29.498 | 1088.8 |  | 2939 | 61.4 | 0.26947 | 62.356 | 0.00086916 | 29.498 | 1088.8 | 1059.302
2940 | 0.26956 | 61.41 | 62.356 | 0.00086946 | 29.508 | 1088.8 |  | 2940 | 61.41 | 0.26956 | 62.356 | 0.00086946 | 29.508 | 1088.8 | 1059.292
2941 | 0.26966 | 61.42 | 62.356 | 0.00086975 | 29.518 | 1088.8 |  | 2941 | 61.42 | 0.26966 | 62.356 | 0.00086975 | 29.518 | 1088.8 | 1059.282
2942 | 0.26976 | 61.43 | 62.356 | 0.00087004 | 29.528 | 1088.8 |  | 2942 | 61.43 | 0.26976 | 62.356 | 0.00087004 | 29.528 | 1088.8 | 1059.272
2943 | 0.26985 | 61.44 | 62.356 | 0.00087033 | 29.538 | 1088.8 |  | 2943 | 61.44 | 0.26985 | 62.356 | 0.00087033 | 29.538 | 1088.8 | 1059.262
2944 | 0.26995 | 61.45 | 62.356 | 0.00087062 | 29.548 | 1088.8 |  | 2944 | 61.45 | 0.26995 | 62.356 | 0.00087062 | 29.548 | 1088.8 | 1059.252
2945 | 0.27004 | 61.46 | 62.356 | 0.00087091 | 29.558 | 1088.8 |  | 2945 | 61.46 | 0.27004 | 62.356 | 0.00087091 | 29.558 | 1088.8 | 1059.242
2946 | 0.27014 | 61.47 | 62.355 | 0.00087121 | 29.568 | 1088.8 |  | 2946 | 61.47 | 0.27014 | 62.355 | 0.00087121 | 29.568 | 1088.8 | 1059.232
2947 | 0.27023 | 61.48 | 62.355 | 0.0008715 | 29.578 | 1088.8 |  | 2947 | 61.48 | 0.27023 | 62.355 | 0.0008715 | 29.578 | 1088.8 | 1059.222
2948 | 0.27033 | 61.49 | 62.355 | 0.00087179 | 29.588 | 1088.8 |  | 2948 | 61.49 | 0.27033 | 62.355 | 0.00087179 | 29.588 | 1088.8 | 1059.212
2949 | 0.27042 | 61.5 | 62.355 | 0.00087208 | 29.598 | 1088.8 |  | 2949 | 61.5 | 0.27042 | 62.355 | 0.00087208 | 29.598 | 1088.8 | 1059.202
2950 | 0.27052 | 61.51 | 62.355 | 0.00087237 | 29.608 | 1088.8 |  | 2950 | 61.51 | 0.27052 | 62.355 | 0.00087237 | 29.608 | 1088.8 | 1059.192
2951 | 0.27062 | 61.52 | 62.355 | 0.00087267 | 29.618 | 1088.8 |  | 2951 | 61.52 | 0.27062 | 62.355 | 0.00087267 | 29.618 | 1088.8 | 1059.182
2952 | 0.27071 | 61.53 | 62.355 | 0.00087296 | 29.628 | 1088.8 |  | 2952 | 61.53 | 0.27071 | 62.355 | 0.00087296 | 29.628 | 1088.8 | 1059.172
2953 | 0.27081 | 61.54 | 62.355 | 0.00087325 | 29.638 | 1088.8 |  | 2953 | 61.54 | 0.27081 | 62.355 | 0.00087325 | 29.638 | 1088.8 | 1059.162
2954 | 0.2709 | 61.55 | 62.355 | 0.00087354 | 29.648 | 1088.8 |  | 2954 | 61.55 | 0.2709 | 62.355 | 0.00087354 | 29.648 | 1088.8 | 1059.152
2955 | 0.271 | 61.56 | 62.355 | 0.00087384 | 29.658 | 1088.8 |  | 2955 | 61.56 | 0.271 | 62.355 | 0.00087384 | 29.658 | 1088.8 | 1059.142
2956 | 0.2711 | 61.57 | 62.355 | 0.00087413 | 29.668 | 1088.8 |  | 2956 | 61.57 | 0.2711 | 62.355 | 0.00087413 | 29.668 | 1088.8 | 1059.132
2957 | 0.27119 | 61.58 | 62.355 | 0.00087442 | 29.678 | 1088.8 |  | 2957 | 61.58 | 0.27119 | 62.355 | 0.00087442 | 29.678 | 1088.8 | 1059.122
2958 | 0.27129 | 61.59 | 62.355 | 0.00087471 | 29.688 | 1088.8 |  | 2958 | 61.59 | 0.27129 | 62.355 | 0.00087471 | 29.688 | 1088.8 | 1059.112
2959 | 0.27138 | 61.6 | 62.355 | 0.00087501 | 29.698 | 1088.8 |  | 2959 | 61.6 | 0.27138 | 62.355 | 0.00087501 | 29.698 | 1088.8 | 1059.102
2960 | 0.27148 | 61.61 | 62.355 | 0.0008753 | 29.708 | 1088.9 |  | 2960 | 61.61 | 0.27148 | 62.355 | 0.0008753 | 29.708 | 1088.9 | 1059.192
2961 | 0.27158 | 61.62 | 62.355 | 0.00087559 | 29.718 | 1088.9 |  | 2961 | 61.62 | 0.27158 | 62.355 | 0.00087559 | 29.718 | 1088.9 | 1059.182
2962 | 0.27167 | 61.63 | 62.355 | 0.00087589 | 29.728 | 1088.9 |  | 2962 | 61.63 | 0.27167 | 62.355 | 0.00087589 | 29.728 | 1088.9 | 1059.172
2963 | 0.27177 | 61.64 | 62.354 | 0.00087618 | 29.738 | 1088.9 |  | 2963 | 61.64 | 0.27177 | 62.354 | 0.00087618 | 29.738 | 1088.9 | 1059.162
2964 | 0.27186 | 61.65 | 62.354 | 0.00087647 | 29.748 | 1088.9 |  | 2964 | 61.65 | 0.27186 | 62.354 | 0.00087647 | 29.748 | 1088.9 | 1059.152
2965 | 0.27196 | 61.66 | 62.354 | 0.00087677 | 29.758 | 1088.9 |  | 2965 | 61.66 | 0.27196 | 62.354 | 0.00087677 | 29.758 | 1088.9 | 1059.142
2966 | 0.27206 | 61.67 | 62.354 | 0.00087706 | 29.768 | 1088.9 |  | 2966 | 61.67 | 0.27206 | 62.354 | 0.00087706 | 29.768 | 1088.9 | 1059.132
2967 | 0.27215 | 61.68 | 62.354 | 0.00087735 | 29.778 | 1088.9 |  | 2967 | 61.68 | 0.27215 | 62.354 | 0.00087735 | 29.778 | 1088.9 | 1059.122
2968 | 0.27225 | 61.69 | 62.354 | 0.00087765 | 29.788 | 1088.9 |  | 2968 | 61.69 | 0.27225 | 62.354 | 0.00087765 | 29.788 | 1088.9 | 1059.112
2969 | 0.27235 | 61.7 | 62.354 | 0.00087794 | 29.798 | 1088.9 |  | 2969 | 61.7 | 0.27235 | 62.354 | 0.00087794 | 29.798 | 1088.9 | 1059.102
2970 | 0.27244 | 61.71 | 62.354 | 0.00087824 | 29.808 | 1088.9 |  | 2970 | 61.71 | 0.27244 | 62.354 | 0.00087824 | 29.808 | 1088.9 | 1059.092
2971 | 0.27254 | 61.72 | 62.354 | 0.00087853 | 29.818 | 1088.9 |  | 2971 | 61.72 | 0.27254 | 62.354 | 0.00087853 | 29.818 | 1088.9 | 1059.082
2972 | 0.27263 | 61.73 | 62.354 | 0.00087882 | 29.828 | 1088.9 |  | 2972 | 61.73 | 0.27263 | 62.354 | 0.00087882 | 29.828 | 1088.9 | 1059.072
2973 | 0.27273 | 61.74 | 62.354 | 0.00087912 | 29.838 | 1088.9 |  | 2973 | 61.74 | 0.27273 | 62.354 | 0.00087912 | 29.838 | 1088.9 | 1059.062
2974 | 0.27283 | 61.75 | 62.354 | 0.00087941 | 29.848 | 1088.9 |  | 2974 | 61.75 | 0.27283 | 62.354 | 0.00087941 | 29.848 | 1088.9 | 1059.052
2975 | 0.27292 | 61.76 | 62.354 | 0.00087971 | 29.858 | 1088.9 |  | 2975 | 61.76 | 0.27292 | 62.354 | 0.00087971 | 29.858 | 1088.9 | 1059.042
2976 | 0.27302 | 61.77 | 62.354 | 0.00088 | 29.868 | 1088.9 |  | 2976 | 61.77 | 0.27302 | 62.354 | 0.00088 | 29.868 | 1088.9 | 1059.032
2977 | 0.27312 | 61.78 | 62.354 | 0.0008803 | 29.878 | 1088.9 |  | 2977 | 61.78 | 0.27312 | 62.354 | 0.0008803 | 29.878 | 1088.9 | 1059.022
2978 | 0.27321 | 61.79 | 62.354 | 0.00088059 | 29.888 | 1088.9 |  | 2978 | 61.79 | 0.27321 | 62.354 | 0.00088059 | 29.888 | 1088.9 | 1059.012
2979 | 0.27331 | 61.8 | 62.354 | 0.00088089 | 29.898 | 1088.9 |  | 2979 | 61.8 | 0.27331 | 62.354 | 0.00088089 | 29.898 | 1088.9 | 1059.002
2980 | 0.27341 | 61.81 | 62.353 | 0.00088118 | 29.908 | 1088.9 |  | 2980 | 61.81 | 0.27341 | 62.353 | 0.00088118 | 29.908 | 1088.9 | 1058.992
2981 | 0.2735 | 61.82 | 62.353 | 0.00088147 | 29.918 | 1088.9 |  | 2981 | 61.82 | 0.2735 | 62.353 | 0.00088147 | 29.918 | 1088.9 | 1058.982
2982 | 0.2736 | 61.83 | 62.353 | 0.00088177 | 29.928 | 1088.9 |  | 2982 | 61.83 | 0.2736 | 62.353 | 0.00088177 | 29.928 | 1088.9 | 1058.972
2983 | 0.2737 | 61.84 | 62.353 | 0.00088206 | 29.938 | 1089 |  | 2983 | 61.84 | 0.2737 | 62.353 | 0.00088206 | 29.938 | 1089 | 1059.062
2984 | 0.27379 | 61.85 | 62.353 | 0.00088236 | 29.948 | 1089 |  | 2984 | 61.85 | 0.27379 | 62.353 | 0.00088236 | 29.948 | 1089 | 1059.052
2985 | 0.27389 | 61.86 | 62.353 | 0.00088265 | 29.958 | 1089 |  | 2985 | 61.86 | 0.27389 | 62.353 | 0.00088265 | 29.958 | 1089 | 1059.042
2986 | 0.27399 | 61.87 | 62.353 | 0.00088295 | 29.968 | 1089 |  | 2986 | 61.87 | 0.27399 | 62.353 | 0.00088295 | 29.968 | 1089 | 1059.032
2987 | 0.27408 | 61.88 | 62.353 | 0.00088325 | 29.978 | 1089 |  | 2987 | 61.88 | 0.27408 | 62.353 | 0.00088325 | 29.978 | 1089 | 1059.022
2988 | 0.27418 | 61.89 | 62.353 | 0.00088354 | 29.988 | 1089 |  | 2988 | 61.89 | 0.27418 | 62.353 | 0.00088354 | 29.988 | 1089 | 1059.012
2989 | 0.27428 | 61.9 | 62.353 | 0.00088384 | 29.998 | 1089 |  | 2989 | 61.9 | 0.27428 | 62.353 | 0.00088384 | 29.998 | 1089 | 1059.002
2990 | 0.27437 | 61.91 | 62.353 | 0.00088413 | 30.008 | 1089 |  | 2990 | 61.91 | 0.27437 | 62.353 | 0.00088413 | 30.008 | 1089 | 1058.992
2991 | 0.27447 | 61.92 | 62.353 | 0.00088443 | 30.018 | 1089 |  | 2991 | 61.92 | 0.27447 | 62.353 | 0.00088443 | 30.018 | 1089 | 1058.982
2992 | 0.27457 | 61.93 | 62.353 | 0.00088472 | 30.028 | 1089 |  | 2992 | 61.93 | 0.27457 | 62.353 | 0.00088472 | 30.028 | 1089 | 1058.972
2993 | 0.27467 | 61.94 | 62.353 | 0.00088502 | 30.038 | 1089 |  | 2993 | 61.94 | 0.27467 | 62.353 | 0.00088502 | 30.038 | 1089 | 1058.962
2994 | 0.27476 | 61.95 | 62.353 | 0.00088532 | 30.048 | 1089 |  | 2994 | 61.95 | 0.27476 | 62.353 | 0.00088532 | 30.048 | 1089 | 1058.952
2995 | 0.27486 | 61.96 | 62.353 | 0.00088561 | 30.058 | 1089 |  | 2995 | 61.96 | 0.27486 | 62.353 | 0.00088561 | 30.058 | 1089 | 1058.942
2996 | 0.27496 | 61.97 | 62.353 | 0.00088591 | 30.068 | 1089 |  | 2996 | 61.97 | 0.27496 | 62.353 | 0.00088591 | 30.068 | 1089 | 1058.932
2997 | 0.27505 | 61.98 | 62.352 | 0.0008862 | 30.078 | 1089 |  | 2997 | 61.98 | 0.27505 | 62.352 | 0.0008862 | 30.078 | 1089 | 1058.922
2998 | 0.27515 | 61.99 | 62.352 | 0.0008865 | 30.088 | 1089 |  | 2998 | 61.99 | 0.27515 | 62.352 | 0.0008865 | 30.088 | 1089 | 1058.912
2999 | 0.27525 | 62 | 62.352 | 0.0008868 | 30.098 | 1089 |  | 2999 | 62 | 0.27525 | 62.352 | 0.0008868 | 30.098 | 1089 | 1058.902
3000 | 0.27535 | 62.01 | 62.352 | 0.00088709 | 30.108 | 1089 |  | 3000 | 62.01 | 0.27535 | 62.352 | 0.00088709 | 30.108 | 1089 | 1058.892
3001 | 0.27544 | 62.02 | 62.352 | 0.00088739 | 30.118 | 1089 |  | 3001 | 62.02 | 0.27544 | 62.352 | 0.00088739 | 30.118 | 1089 | 1058.882
3002 | 0.27554 | 62.03 | 62.352 | 0.00088769 | 30.128 | 1089 |  | 3002 | 62.03 | 0.27554 | 62.352 | 0.00088769 | 30.128 | 1089 | 1058.872
3003 | 0.27564 | 62.04 | 62.352 | 0.00088798 | 30.138 | 1089 |  | 3003 | 62.04 | 0.27564 | 62.352 | 0.00088798 | 30.138 | 1089 | 1058.862
3004 | 0.27573 | 62.05 | 62.352 | 0.00088828 | 30.148 | 1089 |  | 3004 | 62.05 | 0.27573 | 62.352 | 0.00088828 | 30.148 | 1089 | 1058.852
3005 | 0.27583 | 62.06 | 62.352 | 0.00088858 | 30.158 | 1089 |  | 3005 | 62.06 | 0.27583 | 62.352 | 0.00088858 | 30.158 | 1089 | 1058.842
3006 | 0.27593 | 62.07 | 62.352 | 0.00088887 | 30.168 | 1089.1 |  | 3006 | 62.07 | 0.27593 | 62.352 | 0.00088887 | 30.168 | 1089.1 | 1058.932
3007 | 0.27603 | 62.08 | 62.352 | 0.00088917 | 30.178 | 1089.1 |  | 3007 | 62.08 | 0.27603 | 62.352 | 0.00088917 | 30.178 | 1089.1 | 1058.922
3008 | 0.27612 | 62.09 | 62.352 | 0.00088947 | 30.188 | 1089.1 |  | 3008 | 62.09 | 0.27612 | 62.352 | 0.00088947 | 30.188 | 1089.1 | 1058.912
3009 | 0.27622 | 62.1 | 62.352 | 0.00088977 | 30.198 | 1089.1 |  | 3009 | 62.1 | 0.27622 | 62.352 | 0.00088977 | 30.198 | 1089.1 | 1058.902
3010 | 0.27632 | 62.11 | 62.352 | 0.00089006 | 30.208 | 1089.1 |  | 3010 | 62.11 | 0.27632 | 62.352 | 0.00089006 | 30.208 | 1089.1 | 1058.892
3011 | 0.27642 | 62.12 | 62.352 | 0.00089036 | 30.218 | 1089.1 |  | 3011 | 62.12 | 0.27642 | 62.352 | 0.00089036 | 30.218 | 1089.1 | 1058.882
3012 | 0.27651 | 62.13 | 62.352 | 0.00089066 | 30.228 | 1089.1 |  | 3012 | 62.13 | 0.27651 | 62.352 | 0.00089066 | 30.228 | 1089.1 | 1058.872
3013 | 0.27661 | 62.14 | 62.352 | 0.00089096 | 30.238 | 1089.1 |  | 3013 | 62.14 | 0.27661 | 62.352 | 0.00089096 | 30.238 | 1089.1 | 1058.862
3014 | 0.27671 | 62.15 | 62.351 | 0.00089125 | 30.248 | 1089.1 |  | 3014 | 62.15 | 0.27671 | 62.351 | 0.00089125 | 30.248 | 1089.1 | 1058.852
3015 | 0.27681 | 62.16 | 62.351 | 0.00089155 | 30.258 | 1089.1 |  | 3015 | 62.16 | 0.27681 | 62.351 | 0.00089155 | 30.258 | 1089.1 | 1058.842
3016 | 0.2769 | 62.17 | 62.351 | 0.00089185 | 30.268 | 1089.1 |  | 3016 | 62.17 | 0.2769 | 62.351 | 0.00089185 | 30.268 | 1089.1 | 1058.832
3017 | 0.277 | 62.18 | 62.351 | 0.00089215 | 30.278 | 1089.1 |  | 3017 | 62.18 | 0.277 | 62.351 | 0.00089215 | 30.278 | 1089.1 | 1058.822
3018 | 0.2771 | 62.19 | 62.351 | 0.00089244 | 30.288 | 1089.1 |  | 3018 | 62.19 | 0.2771 | 62.351 | 0.00089244 | 30.288 | 1089.1 | 1058.812
3019 | 0.2772 | 62.2 | 62.351 | 0.00089274 | 30.298 | 1089.1 |  | 3019 | 62.2 | 0.2772 | 62.351 | 0.00089274 | 30.298 | 1089.1 | 1058.802
3020 | 0.2773 | 62.21 | 62.351 | 0.00089304 | 30.308 | 1089.1 |  | 3020 | 62.21 | 0.2773 | 62.351 | 0.00089304 | 30.308 | 1089.1 | 1058.792
3021 | 0.27739 | 62.22 | 62.351 | 0.00089334 | 30.318 | 1089.1 |  | 3021 | 62.22 | 0.27739 | 62.351 | 0.00089334 | 30.318 | 1089.1 | 1058.782
3022 | 0.27749 | 62.23 | 62.351 | 0.00089364 | 30.328 | 1089.1 |  | 3022 | 62.23 | 0.27749 | 62.351 | 0.00089364 | 30.328 | 1089.1 | 1058.772
3023 | 0.27759 | 62.24 | 62.351 | 0.00089394 | 30.338 | 1089.1 |  | 3023 | 62.24 | 0.27759 | 62.351 | 0.00089394 | 30.338 | 1089.1 | 1058.762
3024 | 0.27769 | 62.25 | 62.351 | 0.00089423 | 30.348 | 1089.1 |  | 3024 | 62.25 | 0.27769 | 62.351 | 0.00089423 | 30.348 | 1089.1 | 1058.752
3025 | 0.27779 | 62.26 | 62.351 | 0.00089453 | 30.358 | 1089.1 |  | 3025 | 62.26 | 0.27779 | 62.351 | 0.00089453 | 30.358 | 1089.1 | 1058.742
3026 | 0.27788 | 62.27 | 62.351 | 0.00089483 | 30.368 | 1089.1 |  | 3026 | 62.27 | 0.27788 | 62.351 | 0.00089483 | 30.368 | 1089.1 | 1058.732
3027 | 0.27798 | 62.28 | 62.351 | 0.00089513 | 30.378 | 1089.1 |  | 3027 | 62.28 | 0.27798 | 62.351 | 0.00089513 | 30.378 | 1089.1 | 1058.722
3028 | 0.27808 | 62.29 | 62.351 | 0.00089543 | 30.388 | 1089.1 |  | 3028 | 62.29 | 0.27808 | 62.351 | 0.00089543 | 30.388 | 1089.1 | 1058.712
3029 | 0.27818 | 62.3 | 62.351 | 0.00089573 | 30.398 | 1089.2 |  | 3029 | 62.3 | 0.27818 | 62.351 | 0.00089573 | 30.398 | 1089.2 | 1058.802
3030 | 0.27828 | 62.31 | 62.351 | 0.00089603 | 30.408 | 1089.2 |  | 3030 | 62.31 | 0.27828 | 62.351 | 0.00089603 | 30.408 | 1089.2 | 1058.792
3031 | 0.27837 | 62.32 | 62.35 | 0.00089633 | 30.418 | 1089.2 |  | 3031 | 62.32 | 0.27837 | 62.35 | 0.00089633 | 30.418 | 1089.2 | 1058.782
3032 | 0.27847 | 62.33 | 62.35 | 0.00089663 | 30.428 | 1089.2 |  | 3032 | 62.33 | 0.27847 | 62.35 | 0.00089663 | 30.428 | 1089.2 | 1058.772
3033 | 0.27857 | 62.34 | 62.35 | 0.00089693 | 30.438 | 1089.2 |  | 3033 | 62.34 | 0.27857 | 62.35 | 0.00089693 | 30.438 | 1089.2 | 1058.762
3034 | 0.27867 | 62.35 | 62.35 | 0.00089722 | 30.448 | 1089.2 |  | 3034 | 62.35 | 0.27867 | 62.35 | 0.00089722 | 30.448 | 1089.2 | 1058.752
3035 | 0.27877 | 62.36 | 62.35 | 0.00089752 | 30.458 | 1089.2 |  | 3035 | 62.36 | 0.27877 | 62.35 | 0.00089752 | 30.458 | 1089.2 | 1058.742
3036 | 0.27887 | 62.37 | 62.35 | 0.00089782 | 30.468 | 1089.2 |  | 3036 | 62.37 | 0.27887 | 62.35 | 0.00089782 | 30.468 | 1089.2 | 1058.732
3037 | 0.27896 | 62.38 | 62.35 | 0.00089812 | 30.478 | 1089.2 |  | 3037 | 62.38 | 0.27896 | 62.35 | 0.00089812 | 30.478 | 1089.2 | 1058.722
3038 | 0.27906 | 62.39 | 62.35 | 0.00089842 | 30.488 | 1089.2 |  | 3038 | 62.39 | 0.27906 | 62.35 | 0.00089842 | 30.488 | 1089.2 | 1058.712
3039 | 0.27916 | 62.4 | 62.35 | 0.00089872 | 30.498 | 1089.2 |  | 3039 | 62.4 | 0.27916 | 62.35 | 0.00089872 | 30.498 | 1089.2 | 1058.702
3040 | 0.27926 | 62.41 | 62.35 | 0.00089902 | 30.508 | 1089.2 |  | 3040 | 62.41 | 0.27926 | 62.35 | 0.00089902 | 30.508 | 1089.2 | 1058.692
3041 | 0.27936 | 62.42 | 62.35 | 0.00089932 | 30.518 | 1089.2 |  | 3041 | 62.42 | 0.27936 | 62.35 | 0.00089932 | 30.518 | 1089.2 | 1058.682
3042 | 0.27946 | 62.43 | 62.35 | 0.00089962 | 30.528 | 1089.2 |  | 3042 | 62.43 | 0.27946 | 62.35 | 0.00089962 | 30.528 | 1089.2 | 1058.672
3043 | 0.27955 | 62.44 | 62.35 | 0.00089992 | 30.538 | 1089.2 |  | 3043 | 62.44 | 0.27955 | 62.35 | 0.00089992 | 30.538 | 1089.2 | 1058.662
3044 | 0.27965 | 62.45 | 62.35 | 0.00090022 | 30.549 | 1089.2 |  | 3044 | 62.45 | 0.27965 | 62.35 | 0.00090022 | 30.549 | 1089.2 | 1058.651
3045 | 0.27975 | 62.46 | 62.35 | 0.00090052 | 30.559 | 1089.2 |  | 3045 | 62.46 | 0.27975 | 62.35 | 0.00090052 | 30.559 | 1089.2 | 1058.641
3046 | 0.27985 | 62.47 | 62.35 | 0.00090082 | 30.569 | 1089.2 |  | 3046 | 62.47 | 0.27985 | 62.35 | 0.00090082 | 30.569 | 1089.2 | 1058.631
3047 | 0.27995 | 62.48 | 62.35 | 0.00090112 | 30.579 | 1089.2 |  | 3047 | 62.48 | 0.27995 | 62.35 | 0.00090112 | 30.579 | 1089.2 | 1058.621
3048 | 0.28005 | 62.49 | 62.349 | 0.00090143 | 30.589 | 1089.2 |  | 3048 | 62.49 | 0.28005 | 62.349 | 0.00090143 | 30.589 | 1089.2 | 1058.611
3049 | 0.28015 | 62.5 | 62.349 | 0.00090173 | 30.599 | 1089.2 |  | 3049 | 62.5 | 0.28015 | 62.349 | 0.00090173 | 30.599 | 1089.2 | 1058.601
3050 | 0.28025 | 62.51 | 62.349 | 0.00090203 | 30.609 | 1089.2 |  | 3050 | 62.51 | 0.28025 | 62.349 | 0.00090203 | 30.609 | 1089.2 | 1058.591
3051 | 0.28034 | 62.52 | 62.349 | 0.00090233 | 30.619 | 1089.2 |  | 3051 | 62.52 | 0.28034 | 62.349 | 0.00090233 | 30.619 | 1089.2 | 1058.581
3052 | 0.28044 | 62.53 | 62.349 | 0.00090263 | 30.629 | 1089.3 |  | 3052 | 62.53 | 0.28044 | 62.349 | 0.00090263 | 30.629 | 1089.3 | 1058.671
3053 | 0.28054 | 62.54 | 62.349 | 0.00090293 | 30.639 | 1089.3 |  | 3053 | 62.54 | 0.28054 | 62.349 | 0.00090293 | 30.639 | 1089.3 | 1058.661
3054 | 0.28064 | 62.55 | 62.349 | 0.00090323 | 30.649 | 1089.3 |  | 3054 | 62.55 | 0.28064 | 62.349 | 0.00090323 | 30.649 | 1089.3 | 1058.651
3055 | 0.28074 | 62.56 | 62.349 | 0.00090353 | 30.659 | 1089.3 |  | 3055 | 62.56 | 0.28074 | 62.349 | 0.00090353 | 30.659 | 1089.3 | 1058.641
3056 | 0.28084 | 62.57 | 62.349 | 0.00090383 | 30.669 | 1089.3 |  | 3056 | 62.57 | 0.28084 | 62.349 | 0.00090383 | 30.669 | 1089.3 | 1058.631
3057 | 0.28094 | 62.58 | 62.349 | 0.00090413 | 30.679 | 1089.3 |  | 3057 | 62.58 | 0.28094 | 62.349 | 0.00090413 | 30.679 | 1089.3 | 1058.621
3058 | 0.28104 | 62.59 | 62.349 | 0.00090444 | 30.689 | 1089.3 |  | 3058 | 62.59 | 0.28104 | 62.349 | 0.00090444 | 30.689 | 1089.3 | 1058.611
3059 | 0.28114 | 62.6 | 62.349 | 0.00090474 | 30.699 | 1089.3 |  | 3059 | 62.6 | 0.28114 | 62.349 | 0.00090474 | 30.699 | 1089.3 | 1058.601
3060 | 0.28123 | 62.61 | 62.349 | 0.00090504 | 30.709 | 1089.3 |  | 3060 | 62.61 | 0.28123 | 62.349 | 0.00090504 | 30.709 | 1089.3 | 1058.591
3061 | 0.28133 | 62.62 | 62.349 | 0.00090534 | 30.719 | 1089.3 |  | 3061 | 62.62 | 0.28133 | 62.349 | 0.00090534 | 30.719 | 1089.3 | 1058.581
3062 | 0.28143 | 62.63 | 62.349 | 0.00090564 | 30.729 | 1089.3 |  | 3062 | 62.63 | 0.28143 | 62.349 | 0.00090564 | 30.729 | 1089.3 | 1058.571
3063 | 0.28153 | 62.64 | 62.349 | 0.00090595 | 30.739 | 1089.3 |  | 3063 | 62.64 | 0.28153 | 62.349 | 0.00090595 | 30.739 | 1089.3 | 1058.561
3064 | 0.28163 | 62.65 | 62.348 | 0.00090625 | 30.749 | 1089.3 |  | 3064 | 62.65 | 0.28163 | 62.348 | 0.00090625 | 30.749 | 1089.3 | 1058.551
3065 | 0.28173 | 62.66 | 62.348 | 0.00090655 | 30.759 | 1089.3 |  | 3065 | 62.66 | 0.28173 | 62.348 | 0.00090655 | 30.759 | 1089.3 | 1058.541
3066 | 0.28183 | 62.67 | 62.348 | 0.00090685 | 30.769 | 1089.3 |  | 3066 | 62.67 | 0.28183 | 62.348 | 0.00090685 | 30.769 | 1089.3 | 1058.531
3067 | 0.28193 | 62.68 | 62.348 | 0.00090715 | 30.779 | 1089.3 |  | 3067 | 62.68 | 0.28193 | 62.348 | 0.00090715 | 30.779 | 1089.3 | 1058.521
3068 | 0.28203 | 62.69 | 62.348 | 0.00090746 | 30.789 | 1089.3 |  | 3068 | 62.69 | 0.28203 | 62.348 | 0.00090746 | 30.789 | 1089.3 | 1058.511
3069 | 0.28213 | 62.7 | 62.348 | 0.00090776 | 30.799 | 1089.3 |  | 3069 | 62.7 | 0.28213 | 62.348 | 0.00090776 | 30.799 | 1089.3 | 1058.501
3070 | 0.28223 | 62.71 | 62.348 | 0.00090806 | 30.809 | 1089.3 |  | 3070 | 62.71 | 0.28223 | 62.348 | 0.00090806 | 30.809 | 1089.3 | 1058.491
3071 | 0.28233 | 62.72 | 62.348 | 0.00090836 | 30.819 | 1089.3 |  | 3071 | 62.72 | 0.28233 | 62.348 | 0.00090836 | 30.819 | 1089.3 | 1058.481
3072 | 0.28243 | 62.73 | 62.348 | 0.00090867 | 30.829 | 1089.3 |  | 3072 | 62.73 | 0.28243 | 62.348 | 0.00090867 | 30.829 | 1089.3 | 1058.471
3073 | 0.28252 | 62.74 | 62.348 | 0.00090897 | 30.839 | 1089.3 |  | 3073 | 62.74 | 0.28252 | 62.348 | 0.00090897 | 30.839 | 1089.3 | 1058.461
3074 | 0.28262 | 62.75 | 62.348 | 0.00090927 | 30.849 | 1089.3 |  | 3074 | 62.75 | 0.28262 | 62.348 | 0.00090927 | 30.849 | 1089.3 | 1058.451
3075 | 0.28272 | 62.76 | 62.348 | 0.00090958 | 30.859 | 1089.4 |  | 3075 | 62.76 | 0.28272 | 62.348 | 0.00090958 | 30.859 | 1089.4 | 1058.541
3076 | 0.28282 | 62.77 | 62.348 | 0.00090988 | 30.869 | 1089.4 |  | 3076 | 62.77 | 0.28282 | 62.348 | 0.00090988 | 30.869 | 1089.4 | 1058.531
3077 | 0.28292 | 62.78 | 62.348 | 0.00091018 | 30.879 | 1089.4 |  | 3077 | 62.78 | 0.28292 | 62.348 | 0.00091018 | 30.879 | 1089.4 | 1058.521
3078 | 0.28302 | 62.79 | 62.348 | 0.00091048 | 30.889 | 1089.4 |  | 3078 | 62.79 | 0.28302 | 62.348 | 0.00091048 | 30.889 | 1089.4 | 1058.511
3079 | 0.28312 | 62.8 | 62.348 | 0.00091079 | 30.899 | 1089.4 |  | 3079 | 62.8 | 0.28312 | 62.348 | 0.00091079 | 30.899 | 1089.4 | 1058.501
3080 | 0.28322 | 62.81 | 62.348 | 0.00091109 | 30.909 | 1089.4 |  | 3080 | 62.81 | 0.28322 | 62.348 | 0.00091109 | 30.909 | 1089.4 | 1058.491
3081 | 0.28332 | 62.82 | 62.347 | 0.00091139 | 30.919 | 1089.4 |  | 3081 | 62.82 | 0.28332 | 62.347 | 0.00091139 | 30.919 | 1089.4 | 1058.481
3082 | 0.28342 | 62.83 | 62.347 | 0.0009117 | 30.929 | 1089.4 |  | 3082 | 62.83 | 0.28342 | 62.347 | 0.0009117 | 30.929 | 1089.4 | 1058.471
3083 | 0.28352 | 62.84 | 62.347 | 0.000912 | 30.939 | 1089.4 |  | 3083 | 62.84 | 0.28352 | 62.347 | 0.000912 | 30.939 | 1089.4 | 1058.461
3084 | 0.28362 | 62.85 | 62.347 | 0.00091231 | 30.949 | 1089.4 |  | 3084 | 62.85 | 0.28362 | 62.347 | 0.00091231 | 30.949 | 1089.4 | 1058.451
3085 | 0.28372 | 62.86 | 62.347 | 0.00091261 | 30.959 | 1089.4 |  | 3085 | 62.86 | 0.28372 | 62.347 | 0.00091261 | 30.959 | 1089.4 | 1058.441
3086 | 0.28382 | 62.87 | 62.347 | 0.00091291 | 30.969 | 1089.4 |  | 3086 | 62.87 | 0.28382 | 62.347 | 0.00091291 | 30.969 | 1089.4 | 1058.431
3087 | 0.28392 | 62.88 | 62.347 | 0.00091322 | 30.979 | 1089.4 |  | 3087 | 62.88 | 0.28392 | 62.347 | 0.00091322 | 30.979 | 1089.4 | 1058.421
3088 | 0.28402 | 62.89 | 62.347 | 0.00091352 | 30.989 | 1089.4 |  | 3088 | 62.89 | 0.28402 | 62.347 | 0.00091352 | 30.989 | 1089.4 | 1058.411
3089 | 0.28412 | 62.9 | 62.347 | 0.00091383 | 30.999 | 1089.4 |  | 3089 | 62.9 | 0.28412 | 62.347 | 0.00091383 | 30.999 | 1089.4 | 1058.401
3090 | 0.28422 | 62.91 | 62.347 | 0.00091413 | 31.009 | 1089.4 |  | 3090 | 62.91 | 0.28422 | 62.347 | 0.00091413 | 31.009 | 1089.4 | 1058.391
3091 | 0.28432 | 62.92 | 62.347 | 0.00091443 | 31.019 | 1089.4 |  | 3091 | 62.92 | 0.28432 | 62.347 | 0.00091443 | 31.019 | 1089.4 | 1058.381
3092 | 0.28442 | 62.93 | 62.347 | 0.00091474 | 31.029 | 1089.4 |  | 3092 | 62.93 | 0.28442 | 62.347 | 0.00091474 | 31.029 | 1089.4 | 1058.371
3093 | 0.28452 | 62.94 | 62.347 | 0.00091504 | 31.039 | 1089.4 |  | 3093 | 62.94 | 0.28452 | 62.347 | 0.00091504 | 31.039 | 1089.4 | 1058.361
3094 | 0.28462 | 62.95 | 62.347 | 0.00091535 | 31.049 | 1089.4 |  | 3094 | 62.95 | 0.28462 | 62.347 | 0.00091535 | 31.049 | 1089.4 | 1058.351
3095 | 0.28472 | 62.96 | 62.347 | 0.00091565 | 31.059 | 1089.4 |  | 3095 | 62.96 | 0.28472 | 62.347 | 0.00091565 | 31.059 | 1089.4 | 1058.341
3096 | 0.28482 | 62.97 | 62.347 | 0.00091596 | 31.069 | 1089.4 |  | 3096 | 62.97 | 0.28482 | 62.347 | 0.00091596 | 31.069 | 1089.4 | 1058.331
3097 | 0.28492 | 62.98 | 62.346 | 0.00091626 | 31.079 | 1089.4 |  | 3097 | 62.98 | 0.28492 | 62.346 | 0.00091626 | 31.079 | 1089.4 | 1058.321
3098 | 0.28502 | 62.99 | 62.346 | 0.00091657 | 31.089 | 1089.5 |  | 3098 | 62.99 | 0.28502 | 62.346 | 0.00091657 | 31.089 | 1089.5 | 1058.411
3099 | 0.28512 | 63 | 62.346 | 0.00091687 | 31.099 | 1089.5 |  | 3099 | 63 | 0.28512 | 62.346 | 0.00091687 | 31.099 | 1089.5 | 1058.401
3100 | 0.28522 | 63.01 | 62.346 | 0.00091718 | 31.109 | 1089.5 |  | 3100 | 63.01 | 0.28522 | 62.346 | 0.00091718 | 31.109 | 1089.5 | 1058.391
3101 | 0.28532 | 63.02 | 62.346 | 0.00091748 | 31.119 | 1089.5 |  | 3101 | 63.02 | 0.28532 | 62.346 | 0.00091748 | 31.119 | 1089.5 | 1058.381
3102 | 0.28542 | 63.03 | 62.346 | 0.00091779 | 31.129 | 1089.5 |  | 3102 | 63.03 | 0.28542 | 62.346 | 0.00091779 | 31.129 | 1089.5 | 1058.371
3103 | 0.28552 | 63.04 | 62.346 | 0.00091809 | 31.139 | 1089.5 |  | 3103 | 63.04 | 0.28552 | 62.346 | 0.00091809 | 31.139 | 1089.5 | 1058.361
3104 | 0.28562 | 63.05 | 62.346 | 0.0009184 | 31.149 | 1089.5 |  | 3104 | 63.05 | 0.28562 | 62.346 | 0.0009184 | 31.149 | 1089.5 | 1058.351
3105 | 0.28572 | 63.06 | 62.346 | 0.00091871 | 31.159 | 1089.5 |  | 3105 | 63.06 | 0.28572 | 62.346 | 0.00091871 | 31.159 | 1089.5 | 1058.341
3106 | 0.28582 | 63.07 | 62.346 | 0.00091901 | 31.169 | 1089.5 |  | 3106 | 63.07 | 0.28582 | 62.346 | 0.00091901 | 31.169 | 1089.5 | 1058.331
3107 | 0.28592 | 63.08 | 62.346 | 0.00091932 | 31.179 | 1089.5 |  | 3107 | 63.08 | 0.28592 | 62.346 | 0.00091932 | 31.179 | 1089.5 | 1058.321
3108 | 0.28602 | 63.09 | 62.346 | 0.00091962 | 31.189 | 1089.5 |  | 3108 | 63.09 | 0.28602 | 62.346 | 0.00091962 | 31.189 | 1089.5 | 1058.311
3109 | 0.28613 | 63.1 | 62.346 | 0.00091993 | 31.199 | 1089.5 |  | 3109 | 63.1 | 0.28613 | 62.346 | 0.00091993 | 31.199 | 1089.5 | 1058.301
3110 | 0.28623 | 63.11 | 62.346 | 0.00092023 | 31.209 | 1089.5 |  | 3110 | 63.11 | 0.28623 | 62.346 | 0.00092023 | 31.209 | 1089.5 | 1058.291
3111 | 0.28633 | 63.12 | 62.346 | 0.00092054 | 31.219 | 1089.5 |  | 3111 | 63.12 | 0.28633 | 62.346 | 0.00092054 | 31.219 | 1089.5 | 1058.281
3112 | 0.28643 | 63.13 | 62.346 | 0.00092085 | 31.229 | 1089.5 |  | 3112 | 63.13 | 0.28643 | 62.346 | 0.00092085 | 31.229 | 1089.5 | 1058.271
3113 | 0.28653 | 63.14 | 62.346 | 0.00092115 | 31.239 | 1089.5 |  | 3113 | 63.14 | 0.28653 | 62.346 | 0.00092115 | 31.239 | 1089.5 | 1058.261
3114 | 0.28663 | 63.15 | 62.345 | 0.00092146 | 31.249 | 1089.5 |  | 3114 | 63.15 | 0.28663 | 62.345 | 0.00092146 | 31.249 | 1089.5 | 1058.251
3115 | 0.28673 | 63.16 | 62.345 | 0.00092177 | 31.259 | 1089.5 |  | 3115 | 63.16 | 0.28673 | 62.345 | 0.00092177 | 31.259 | 1089.5 | 1058.241
3116 | 0.28683 | 63.17 | 62.345 | 0.00092207 | 31.269 | 1089.5 |  | 3116 | 63.17 | 0.28683 | 62.345 | 0.00092207 | 31.269 | 1089.5 | 1058.231
3117 | 0.28693 | 63.18 | 62.345 | 0.00092238 | 31.279 | 1089.5 |  | 3117 | 63.18 | 0.28693 | 62.345 | 0.00092238 | 31.279 | 1089.5 | 1058.221
3118 | 0.28703 | 63.19 | 62.345 | 0.00092269 | 31.289 | 1089.5 |  | 3118 | 63.19 | 0.28703 | 62.345 | 0.00092269 | 31.289 | 1089.5 | 1058.211
3119 | 0.28713 | 63.2 | 62.345 | 0.00092299 | 31.299 | 1089.5 |  | 3119 | 63.2 | 0.28713 | 62.345 | 0.00092299 | 31.299 | 1089.5 | 1058.201
3120 | 0.28723 | 63.21 | 62.345 | 0.0009233 | 31.309 | 1089.5 |  | 3120 | 63.21 | 0.28723 | 62.345 | 0.0009233 | 31.309 | 1089.5 | 1058.191
3121 | 0.28733 | 63.22 | 62.345 | 0.00092361 | 31.319 | 1089.6 |  | 3121 | 63.22 | 0.28733 | 62.345 | 0.00092361 | 31.319 | 1089.6 | 1058.281
3122 | 0.28744 | 63.23 | 62.345 | 0.00092391 | 31.329 | 1089.6 |  | 3122 | 63.23 | 0.28744 | 62.345 | 0.00092391 | 31.329 | 1089.6 | 1058.271
3123 | 0.28754 | 63.24 | 62.345 | 0.00092422 | 31.339 | 1089.6 |  | 3123 | 63.24 | 0.28754 | 62.345 | 0.00092422 | 31.339 | 1089.6 | 1058.261
3124 | 0.28764 | 63.25 | 62.345 | 0.00092453 | 31.349 | 1089.6 |  | 3124 | 63.25 | 0.28764 | 62.345 | 0.00092453 | 31.349 | 1089.6 | 1058.251
3125 | 0.28774 | 63.26 | 62.345 | 0.00092484 | 31.359 | 1089.6 |  | 3125 | 63.26 | 0.28774 | 62.345 | 0.00092484 | 31.359 | 1089.6 | 1058.241
3126 | 0.28784 | 63.27 | 62.345 | 0.00092514 | 31.369 | 1089.6 |  | 3126 | 63.27 | 0.28784 | 62.345 | 0.00092514 | 31.369 | 1089.6 | 1058.231
3127 | 0.28794 | 63.28 | 62.345 | 0.00092545 | 31.379 | 1089.6 |  | 3127 | 63.28 | 0.28794 | 62.345 | 0.00092545 | 31.379 | 1089.6 | 1058.221
3128 | 0.28804 | 63.29 | 62.345 | 0.00092576 | 31.389 | 1089.6 |  | 3128 | 63.29 | 0.28804 | 62.345 | 0.00092576 | 31.389 | 1089.6 | 1058.211
3129 | 0.28814 | 63.3 | 62.345 | 0.00092607 | 31.399 | 1089.6 |  | 3129 | 63.3 | 0.28814 | 62.345 | 0.00092607 | 31.399 | 1089.6 | 1058.201
3130 | 0.28824 | 63.31 | 62.344 | 0.00092637 | 31.409 | 1089.6 |  | 3130 | 63.31 | 0.28824 | 62.344 | 0.00092637 | 31.409 | 1089.6 | 1058.191
3131 | 0.28835 | 63.32 | 62.344 | 0.00092668 | 31.419 | 1089.6 |  | 3131 | 63.32 | 0.28835 | 62.344 | 0.00092668 | 31.419 | 1089.6 | 1058.181
3132 | 0.28845 | 63.33 | 62.344 | 0.00092699 | 31.429 | 1089.6 |  | 3132 | 63.33 | 0.28845 | 62.344 | 0.00092699 | 31.429 | 1089.6 | 1058.171
3133 | 0.28855 | 63.34 | 62.344 | 0.0009273 | 31.439 | 1089.6 |  | 3133 | 63.34 | 0.28855 | 62.344 | 0.0009273 | 31.439 | 1089.6 | 1058.161
3134 | 0.28865 | 63.35 | 62.344 | 0.00092761 | 31.449 | 1089.6 |  | 3134 | 63.35 | 0.28865 | 62.344 | 0.00092761 | 31.449 | 1089.6 | 1058.151
3135 | 0.28875 | 63.36 | 62.344 | 0.00092791 | 31.459 | 1089.6 |  | 3135 | 63.36 | 0.28875 | 62.344 | 0.00092791 | 31.459 | 1089.6 | 1058.141
3136 | 0.28885 | 63.37 | 62.344 | 0.00092822 | 31.469 | 1089.6 |  | 3136 | 63.37 | 0.28885 | 62.344 | 0.00092822 | 31.469 | 1089.6 | 1058.131
3137 | 0.28895 | 63.38 | 62.344 | 0.00092853 | 31.479 | 1089.6 |  | 3137 | 63.38 | 0.28895 | 62.344 | 0.00092853 | 31.479 | 1089.6 | 1058.121
3138 | 0.28905 | 63.39 | 62.344 | 0.00092884 | 31.489 | 1089.6 |  | 3138 | 63.39 | 0.28905 | 62.344 | 0.00092884 | 31.489 | 1089.6 | 1058.111
3139 | 0.28916 | 63.4 | 62.344 | 0.00092915 | 31.499 | 1089.6 |  | 3139 | 63.4 | 0.28916 | 62.344 | 0.00092915 | 31.499 | 1089.6 | 1058.101
3140 | 0.28926 | 63.41 | 62.344 | 0.00092946 | 31.509 | 1089.6 |  | 3140 | 63.41 | 0.28926 | 62.344 | 0.00092946 | 31.509 | 1089.6 | 1058.091
3141 | 0.28936 | 63.42 | 62.344 | 0.00092977 | 31.519 | 1089.6 |  | 3141 | 63.42 | 0.28936 | 62.344 | 0.00092977 | 31.519 | 1089.6 | 1058.081
3142 | 0.28946 | 63.43 | 62.344 | 0.00093007 | 31.529 | 1089.6 |  | 3142 | 63.43 | 0.28946 | 62.344 | 0.00093007 | 31.529 | 1089.6 | 1058.071
3143 | 0.28956 | 63.44 | 62.344 | 0.00093038 | 31.539 | 1089.6 |  | 3143 | 63.44 | 0.28956 | 62.344 | 0.00093038 | 31.539 | 1089.6 | 1058.061
3144 | 0.28966 | 63.45 | 62.344 | 0.00093069 | 31.549 | 1089.7 |  | 3144 | 63.45 | 0.28966 | 62.344 | 0.00093069 | 31.549 | 1089.7 | 1058.151
3145 | 0.28977 | 63.46 | 62.344 | 0.000931 | 31.559 | 1089.7 |  | 3145 | 63.46 | 0.28977 | 62.344 | 0.000931 | 31.559 | 1089.7 | 1058.141
3146 | 0.28987 | 63.47 | 62.343 | 0.00093131 | 31.569 | 1089.7 |  | 3146 | 63.47 | 0.28987 | 62.343 | 0.00093131 | 31.569 | 1089.7 | 1058.131
3147 | 0.28997 | 63.48 | 62.343 | 0.00093162 | 31.579 | 1089.7 |  | 3147 | 63.48 | 0.28997 | 62.343 | 0.00093162 | 31.579 | 1089.7 | 1058.121
3148 | 0.29007 | 63.49 | 62.343 | 0.00093193 | 31.589 | 1089.7 |  | 3148 | 63.49 | 0.29007 | 62.343 | 0.00093193 | 31.589 | 1089.7 | 1058.111
3149 | 0.29017 | 63.5 | 62.343 | 0.00093224 | 31.599 | 1089.7 |  | 3149 | 63.5 | 0.29017 | 62.343 | 0.00093224 | 31.599 | 1089.7 | 1058.101
3150 | 0.29027 | 63.51 | 62.343 | 0.00093255 | 31.609 | 1089.7 |  | 3150 | 63.51 | 0.29027 | 62.343 | 0.00093255 | 31.609 | 1089.7 | 1058.091
3151 | 0.29038 | 63.52 | 62.343 | 0.00093286 | 31.619 | 1089.7 |  | 3151 | 63.52 | 0.29038 | 62.343 | 0.00093286 | 31.619 | 1089.7 | 1058.081
3152 | 0.29048 | 63.53 | 62.343 | 0.00093317 | 31.629 | 1089.7 |  | 3152 | 63.53 | 0.29048 | 62.343 | 0.00093317 | 31.629 | 1089.7 | 1058.071
3153 | 0.29058 | 63.54 | 62.343 | 0.00093348 | 31.639 | 1089.7 |  | 3153 | 63.54 | 0.29058 | 62.343 | 0.00093348 | 31.639 | 1089.7 | 1058.061
3154 | 0.29068 | 63.55 | 62.343 | 0.00093379 | 31.649 | 1089.7 |  | 3154 | 63.55 | 0.29068 | 62.343 | 0.00093379 | 31.649 | 1089.7 | 1058.051
3155 | 0.29078 | 63.56 | 62.343 | 0.0009341 | 31.659 | 1089.7 |  | 3155 | 63.56 | 0.29078 | 62.343 | 0.0009341 | 31.659 | 1089.7 | 1058.041
3156 | 0.29089 | 63.57 | 62.343 | 0.00093441 | 31.669 | 1089.7 |  | 3156 | 63.57 | 0.29089 | 62.343 | 0.00093441 | 31.669 | 1089.7 | 1058.031
3157 | 0.29099 | 63.58 | 62.343 | 0.00093472 | 31.679 | 1089.7 |  | 3157 | 63.58 | 0.29099 | 62.343 | 0.00093472 | 31.679 | 1089.7 | 1058.021
3158 | 0.29109 | 63.59 | 62.343 | 0.00093503 | 31.689 | 1089.7 |  | 3158 | 63.59 | 0.29109 | 62.343 | 0.00093503 | 31.689 | 1089.7 | 1058.011
3159 | 0.29119 | 63.6 | 62.343 | 0.00093534 | 31.699 | 1089.7 |  | 3159 | 63.6 | 0.29119 | 62.343 | 0.00093534 | 31.699 | 1089.7 | 1058.001
3160 | 0.29129 | 63.61 | 62.343 | 0.00093565 | 31.709 | 1089.7 |  | 3160 | 63.61 | 0.29129 | 62.343 | 0.00093565 | 31.709 | 1089.7 | 1057.991
3161 | 0.2914 | 63.62 | 62.343 | 0.00093596 | 31.719 | 1089.7 |  | 3161 | 63.62 | 0.2914 | 62.343 | 0.00093596 | 31.719 | 1089.7 | 1057.981
3162 | 0.2915 | 63.63 | 62.342 | 0.00093627 | 31.729 | 1089.7 |  | 3162 | 63.63 | 0.2915 | 62.342 | 0.00093627 | 31.729 | 1089.7 | 1057.971
3163 | 0.2916 | 63.64 | 62.342 | 0.00093658 | 31.739 | 1089.7 |  | 3163 | 63.64 | 0.2916 | 62.342 | 0.00093658 | 31.739 | 1089.7 | 1057.961
3164 | 0.2917 | 63.65 | 62.342 | 0.00093689 | 31.749 | 1089.7 |  | 3164 | 63.65 | 0.2917 | 62.342 | 0.00093689 | 31.749 | 1089.7 | 1057.951
3165 | 0.29181 | 63.66 | 62.342 | 0.0009372 | 31.759 | 1089.7 |  | 3165 | 63.66 | 0.29181 | 62.342 | 0.0009372 | 31.759 | 1089.7 | 1057.941
3166 | 0.29191 | 63.67 | 62.342 | 0.00093751 | 31.769 | 1089.7 |  | 3166 | 63.67 | 0.29191 | 62.342 | 0.00093751 | 31.769 | 1089.7 | 1057.931
3167 | 0.29201 | 63.68 | 62.342 | 0.00093783 | 31.779 | 1089.8 |  | 3167 | 63.68 | 0.29201 | 62.342 | 0.00093783 | 31.779 | 1089.8 | 1058.021
3168 | 0.29211 | 63.69 | 62.342 | 0.00093814 | 31.789 | 1089.8 |  | 3168 | 63.69 | 0.29211 | 62.342 | 0.00093814 | 31.789 | 1089.8 | 1058.011
3169 | 0.29222 | 63.7 | 62.342 | 0.00093845 | 31.799 | 1089.8 |  | 3169 | 63.7 | 0.29222 | 62.342 | 0.00093845 | 31.799 | 1089.8 | 1058.001
3170 | 0.29232 | 63.71 | 62.342 | 0.00093876 | 31.809 | 1089.8 |  | 3170 | 63.71 | 0.29232 | 62.342 | 0.00093876 | 31.809 | 1089.8 | 1057.991
3171 | 0.29242 | 63.72 | 62.342 | 0.00093907 | 31.819 | 1089.8 |  | 3171 | 63.72 | 0.29242 | 62.342 | 0.00093907 | 31.819 | 1089.8 | 1057.981
3172 | 0.29252 | 63.73 | 62.342 | 0.00093938 | 31.829 | 1089.8 |  | 3172 | 63.73 | 0.29252 | 62.342 | 0.00093938 | 31.829 | 1089.8 | 1057.971
3173 | 0.29263 | 63.74 | 62.342 | 0.00093969 | 31.839 | 1089.8 |  | 3173 | 63.74 | 0.29263 | 62.342 | 0.00093969 | 31.839 | 1089.8 | 1057.961
3174 | 0.29273 | 63.75 | 62.342 | 0.00094001 | 31.849 | 1089.8 |  | 3174 | 63.75 | 0.29273 | 62.342 | 0.00094001 | 31.849 | 1089.8 | 1057.951
3175 | 0.29283 | 63.76 | 62.342 | 0.00094032 | 31.859 | 1089.8 |  | 3175 | 63.76 | 0.29283 | 62.342 | 0.00094032 | 31.859 | 1089.8 | 1057.941
3176 | 0.29293 | 63.77 | 62.342 | 0.00094063 | 31.869 | 1089.8 |  | 3176 | 63.77 | 0.29293 | 62.342 | 0.00094063 | 31.869 | 1089.8 | 1057.931
3177 | 0.29304 | 63.78 | 62.342 | 0.00094094 | 31.879 | 1089.8 |  | 3177 | 63.78 | 0.29304 | 62.342 | 0.00094094 | 31.879 | 1089.8 | 1057.921
3178 | 0.29314 | 63.79 | 62.341 | 0.00094125 | 31.889 | 1089.8 |  | 3178 | 63.79 | 0.29314 | 62.341 | 0.00094125 | 31.889 | 1089.8 | 1057.911
3179 | 0.29324 | 63.8 | 62.341 | 0.00094157 | 31.899 | 1089.8 |  | 3179 | 63.8 | 0.29324 | 62.341 | 0.00094157 | 31.899 | 1089.8 | 1057.901
3180 | 0.29334 | 63.81 | 62.341 | 0.00094188 | 31.909 | 1089.8 |  | 3180 | 63.81 | 0.29334 | 62.341 | 0.00094188 | 31.909 | 1089.8 | 1057.891
3181 | 0.29345 | 63.82 | 62.341 | 0.00094219 | 31.919 | 1089.8 |  | 3181 | 63.82 | 0.29345 | 62.341 | 0.00094219 | 31.919 | 1089.8 | 1057.881
3182 | 0.29355 | 63.83 | 62.341 | 0.0009425 | 31.929 | 1089.8 |  | 3182 | 63.83 | 0.29355 | 62.341 | 0.0009425 | 31.929 | 1089.8 | 1057.871
3183 | 0.29365 | 63.84 | 62.341 | 0.00094282 | 31.939 | 1089.8 |  | 3183 | 63.84 | 0.29365 | 62.341 | 0.00094282 | 31.939 | 1089.8 | 1057.861
3184 | 0.29376 | 63.85 | 62.341 | 0.00094313 | 31.949 | 1089.8 |  | 3184 | 63.85 | 0.29376 | 62.341 | 0.00094313 | 31.949 | 1089.8 | 1057.851
3185 | 0.29386 | 63.86 | 62.341 | 0.00094344 | 31.959 | 1089.8 |  | 3185 | 63.86 | 0.29386 | 62.341 | 0.00094344 | 31.959 | 1089.8 | 1057.841
3186 | 0.29396 | 63.87 | 62.341 | 0.00094375 | 31.969 | 1089.8 |  | 3186 | 63.87 | 0.29396 | 62.341 | 0.00094375 | 31.969 | 1089.8 | 1057.831
3187 | 0.29406 | 63.88 | 62.341 | 0.00094407 | 31.979 | 1089.8 |  | 3187 | 63.88 | 0.29406 | 62.341 | 0.00094407 | 31.979 | 1089.8 | 1057.821
3188 | 0.29417 | 63.89 | 62.341 | 0.00094438 | 31.989 | 1089.8 |  | 3188 | 63.89 | 0.29417 | 62.341 | 0.00094438 | 31.989 | 1089.8 | 1057.811
3189 | 0.29427 | 63.9 | 62.341 | 0.00094469 | 31.999 | 1089.8 |  | 3189 | 63.9 | 0.29427 | 62.341 | 0.00094469 | 31.999 | 1089.8 | 1057.801
3190 | 0.29437 | 63.91 | 62.341 | 0.00094501 | 32.009 | 1089.9 |  | 3190 | 63.91 | 0.29437 | 62.341 | 0.00094501 | 32.009 | 1089.9 | 1057.891
3191 | 0.29448 | 63.92 | 62.341 | 0.00094532 | 32.019 | 1089.9 |  | 3191 | 63.92 | 0.29448 | 62.341 | 0.00094532 | 32.019 | 1089.9 | 1057.881
3192 | 0.29458 | 63.93 | 62.341 | 0.00094563 | 32.029 | 1089.9 |  | 3192 | 63.93 | 0.29458 | 62.341 | 0.00094563 | 32.029 | 1089.9 | 1057.871
3193 | 0.29468 | 63.94 | 62.341 | 0.00094595 | 32.039 | 1089.9 |  | 3193 | 63.94 | 0.29468 | 62.341 | 0.00094595 | 32.039 | 1089.9 | 1057.861
3194 | 0.29479 | 63.95 | 62.34 | 0.00094626 | 32.049 | 1089.9 |  | 3194 | 63.95 | 0.29479 | 62.34 | 0.00094626 | 32.049 | 1089.9 | 1057.851
3195 | 0.29489 | 63.96 | 62.34 | 0.00094657 | 32.059 | 1089.9 |  | 3195 | 63.96 | 0.29489 | 62.34 | 0.00094657 | 32.059 | 1089.9 | 1057.841
3196 | 0.29499 | 63.97 | 62.34 | 0.00094689 | 32.069 | 1089.9 |  | 3196 | 63.97 | 0.29499 | 62.34 | 0.00094689 | 32.069 | 1089.9 | 1057.831
3197 | 0.2951 | 63.98 | 62.34 | 0.0009472 | 32.079 | 1089.9 |  | 3197 | 63.98 | 0.2951 | 62.34 | 0.0009472 | 32.079 | 1089.9 | 1057.821
3198 | 0.2952 | 63.99 | 62.34 | 0.00094751 | 32.089 | 1089.9 |  | 3198 | 63.99 | 0.2952 | 62.34 | 0.00094751 | 32.089 | 1089.9 | 1057.811
3199 | 0.2953 | 64 | 62.34 | 0.00094783 | 32.099 | 1089.9 |  | 3199 | 64 | 0.2953 | 62.34 | 0.00094783 | 32.099 | 1089.9 | 1057.801
3200 | 0.29541 | 64.01 | 62.34 | 0.00094814 | 32.109 | 1089.9 |  | 3200 | 64.01 | 0.29541 | 62.34 | 0.00094814 | 32.109 | 1089.9 | 1057.791
3201 | 0.29551 | 64.02 | 62.34 | 0.00094846 | 32.119 | 1089.9 |  | 3201 | 64.02 | 0.29551 | 62.34 | 0.00094846 | 32.119 | 1089.9 | 1057.781
3202 | 0.29561 | 64.03 | 62.34 | 0.00094877 | 32.129 | 1089.9 |  | 3202 | 64.03 | 0.29561 | 62.34 | 0.00094877 | 32.129 | 1089.9 | 1057.771
3203 | 0.29572 | 64.04 | 62.34 | 0.00094909 | 32.139 | 1089.9 |  | 3203 | 64.04 | 0.29572 | 62.34 | 0.00094909 | 32.139 | 1089.9 | 1057.761
3204 | 0.29582 | 64.05 | 62.34 | 0.0009494 | 32.149 | 1089.9 |  | 3204 | 64.05 | 0.29582 | 62.34 | 0.0009494 | 32.149 | 1089.9 | 1057.751
3205 | 0.29592 | 64.06 | 62.34 | 0.00094971 | 32.159 | 1089.9 |  | 3205 | 64.06 | 0.29592 | 62.34 | 0.00094971 | 32.159 | 1089.9 | 1057.741
3206 | 0.29603 | 64.07 | 62.34 | 0.00095003 | 32.169 | 1089.9 |  | 3206 | 64.07 | 0.29603 | 62.34 | 0.00095003 | 32.169 | 1089.9 | 1057.731
3207 | 0.29613 | 64.08 | 62.34 | 0.00095034 | 32.18 | 1089.9 |  | 3207 | 64.08 | 0.29613 | 62.34 | 0.00095034 | 32.18 | 1089.9 | 1057.72
3208 | 0.29624 | 64.09 | 62.34 | 0.00095066 | 32.19 | 1089.9 |  | 3208 | 64.09 | 0.29624 | 62.34 | 0.00095066 | 32.19 | 1089.9 | 1057.71
3209 | 0.29634 | 64.1 | 62.34 | 0.00095097 | 32.2 | 1089.9 |  | 3209 | 64.1 | 0.29634 | 62.34 | 0.00095097 | 32.2 | 1089.9 | 1057.7
3210 | 0.29644 | 64.11 | 62.339 | 0.00095129 | 32.21 | 1089.9 |  | 3210 | 64.11 | 0.29644 | 62.339 | 0.00095129 | 32.21 | 1089.9 | 1057.69
3211 | 0.29655 | 64.12 | 62.339 | 0.0009516 | 32.22 | 1089.9 |  | 3211 | 64.12 | 0.29655 | 62.339 | 0.0009516 | 32.22 | 1089.9 | 1057.68
3212 | 0.29665 | 64.13 | 62.339 | 0.00095192 | 32.23 | 1089.9 |  | 3212 | 64.13 | 0.29665 | 62.339 | 0.00095192 | 32.23 | 1089.9 | 1057.67
3213 | 0.29675 | 64.14 | 62.339 | 0.00095223 | 32.24 | 1090 |  | 3213 | 64.14 | 0.29675 | 62.339 | 0.00095223 | 32.24 | 1090 | 1057.76
3214 | 0.29686 | 64.15 | 62.339 | 0.00095255 | 32.25 | 1090 |  | 3214 | 64.15 | 0.29686 | 62.339 | 0.00095255 | 32.25 | 1090 | 1057.75
3215 | 0.29696 | 64.16 | 62.339 | 0.00095286 | 32.26 | 1090 |  | 3215 | 64.16 | 0.29696 | 62.339 | 0.00095286 | 32.26 | 1090 | 1057.74
3216 | 0.29707 | 64.17 | 62.339 | 0.00095318 | 32.27 | 1090 |  | 3216 | 64.17 | 0.29707 | 62.339 | 0.00095318 | 32.27 | 1090 | 1057.73
3217 | 0.29717 | 64.18 | 62.339 | 0.0009535 | 32.28 | 1090 |  | 3217 | 64.18 | 0.29717 | 62.339 | 0.0009535 | 32.28 | 1090 | 1057.72
3218 | 0.29727 | 64.19 | 62.339 | 0.00095381 | 32.29 | 1090 |  | 3218 | 64.19 | 0.29727 | 62.339 | 0.00095381 | 32.29 | 1090 | 1057.71
3219 | 0.29738 | 64.2 | 62.339 | 0.00095413 | 32.3 | 1090 |  | 3219 | 64.2 | 0.29738 | 62.339 | 0.00095413 | 32.3 | 1090 | 1057.7
3220 | 0.29748 | 64.21 | 62.339 | 0.00095444 | 32.31 | 1090 |  | 3220 | 64.21 | 0.29748 | 62.339 | 0.00095444 | 32.31 | 1090 | 1057.69
3221 | 0.29759 | 64.22 | 62.339 | 0.00095476 | 32.32 | 1090 |  | 3221 | 64.22 | 0.29759 | 62.339 | 0.00095476 | 32.32 | 1090 | 1057.68
3222 | 0.29769 | 64.23 | 62.339 | 0.00095508 | 32.33 | 1090 |  | 3222 | 64.23 | 0.29769 | 62.339 | 0.00095508 | 32.33 | 1090 | 1057.67
3223 | 0.29779 | 64.24 | 62.339 | 0.00095539 | 32.34 | 1090 |  | 3223 | 64.24 | 0.29779 | 62.339 | 0.00095539 | 32.34 | 1090 | 1057.66
3224 | 0.2979 | 64.25 | 62.339 | 0.00095571 | 32.35 | 1090 |  | 3224 | 64.25 | 0.2979 | 62.339 | 0.00095571 | 32.35 | 1090 | 1057.65
3225 | 0.298 | 64.26 | 62.339 | 0.00095602 | 32.36 | 1090 |  | 3225 | 64.26 | 0.298 | 62.339 | 0.00095602 | 32.36 | 1090 | 1057.64
3226 | 0.29811 | 64.27 | 62.338 | 0.00095634 | 32.37 | 1090 |  | 3226 | 64.27 | 0.29811 | 62.338 | 0.00095634 | 32.37 | 1090 | 1057.63
3227 | 0.29821 | 64.28 | 62.338 | 0.00095666 | 32.38 | 1090 |  | 3227 | 64.28 | 0.29821 | 62.338 | 0.00095666 | 32.38 | 1090 | 1057.62
3228 | 0.29832 | 64.29 | 62.338 | 0.00095697 | 32.39 | 1090 |  | 3228 | 64.29 | 0.29832 | 62.338 | 0.00095697 | 32.39 | 1090 | 1057.61
3229 | 0.29842 | 64.3 | 62.338 | 0.00095729 | 32.4 | 1090 |  | 3229 | 64.3 | 0.29842 | 62.338 | 0.00095729 | 32.4 | 1090 | 1057.6
3230 | 0.29852 | 64.31 | 62.338 | 0.00095761 | 32.41 | 1090 |  | 3230 | 64.31 | 0.29852 | 62.338 | 0.00095761 | 32.41 | 1090 | 1057.59
3231 | 0.29863 | 64.32 | 62.338 | 0.00095792 | 32.42 | 1090 |  | 3231 | 64.32 | 0.29863 | 62.338 | 0.00095792 | 32.42 | 1090 | 1057.58
3232 | 0.29873 | 64.33 | 62.338 | 0.00095824 | 32.43 | 1090 |  | 3232 | 64.33 | 0.29873 | 62.338 | 0.00095824 | 32.43 | 1090 | 1057.57
3233 | 0.29884 | 64.34 | 62.338 | 0.00095856 | 32.44 | 1090 |  | 3233 | 64.34 | 0.29884 | 62.338 | 0.00095856 | 32.44 | 1090 | 1057.56
3234 | 0.29894 | 64.35 | 62.338 | 0.00095887 | 32.45 | 1090 |  | 3234 | 64.35 | 0.29894 | 62.338 | 0.00095887 | 32.45 | 1090 | 1057.55
3235 | 0.29905 | 64.36 | 62.338 | 0.00095919 | 32.46 | 1090 |  | 3235 | 64.36 | 0.29905 | 62.338 | 0.00095919 | 32.46 | 1090 | 1057.54
3236 | 0.29915 | 64.37 | 62.338 | 0.00095951 | 32.47 | 1090.1 |  | 3236 | 64.37 | 0.29915 | 62.338 | 0.00095951 | 32.47 | 1090.1 | 1057.63
3237 | 0.29926 | 64.38 | 62.338 | 0.00095983 | 32.48 | 1090.1 |  | 3237 | 64.38 | 0.29926 | 62.338 | 0.00095983 | 32.48 | 1090.1 | 1057.62
3238 | 0.29936 | 64.39 | 62.338 | 0.00096014 | 32.49 | 1090.1 |  | 3238 | 64.39 | 0.29936 | 62.338 | 0.00096014 | 32.49 | 1090.1 | 1057.61
3239 | 0.29946 | 64.4 | 62.338 | 0.00096046 | 32.5 | 1090.1 |  | 3239 | 64.4 | 0.29946 | 62.338 | 0.00096046 | 32.5 | 1090.1 | 1057.6
3240 | 0.29957 | 64.41 | 62.338 | 0.00096078 | 32.51 | 1090.1 |  | 3240 | 64.41 | 0.29957 | 62.338 | 0.00096078 | 32.51 | 1090.1 | 1057.59
3241 | 0.29967 | 64.42 | 62.337 | 0.0009611 | 32.52 | 1090.1 |  | 3241 | 64.42 | 0.29967 | 62.337 | 0.0009611 | 32.52 | 1090.1 | 1057.58
3242 | 0.29978 | 64.43 | 62.337 | 0.00096142 | 32.53 | 1090.1 |  | 3242 | 64.43 | 0.29978 | 62.337 | 0.00096142 | 32.53 | 1090.1 | 1057.57
3243 | 0.29988 | 64.44 | 62.337 | 0.00096173 | 32.54 | 1090.1 |  | 3243 | 64.44 | 0.29988 | 62.337 | 0.00096173 | 32.54 | 1090.1 | 1057.56
3244 | 0.29999 | 64.45 | 62.337 | 0.00096205 | 32.55 | 1090.1 |  | 3244 | 64.45 | 0.29999 | 62.337 | 0.00096205 | 32.55 | 1090.1 | 1057.55
3245 | 0.30009 | 64.46 | 62.337 | 0.00096237 | 32.56 | 1090.1 |  | 3245 | 64.46 | 0.30009 | 62.337 | 0.00096237 | 32.56 | 1090.1 | 1057.54
3246 | 0.3002 | 64.47 | 62.337 | 0.00096269 | 32.57 | 1090.1 |  | 3246 | 64.47 | 0.3002 | 62.337 | 0.00096269 | 32.57 | 1090.1 | 1057.53
3247 | 0.3003 | 64.48 | 62.337 | 0.00096301 | 32.58 | 1090.1 |  | 3247 | 64.48 | 0.3003 | 62.337 | 0.00096301 | 32.58 | 1090.1 | 1057.52
3248 | 0.30041 | 64.49 | 62.337 | 0.00096332 | 32.59 | 1090.1 |  | 3248 | 64.49 | 0.30041 | 62.337 | 0.00096332 | 32.59 | 1090.1 | 1057.51
3249 | 0.30051 | 64.5 | 62.337 | 0.00096364 | 32.6 | 1090.1 |  | 3249 | 64.5 | 0.30051 | 62.337 | 0.00096364 | 32.6 | 1090.1 | 1057.5
3250 | 0.30062 | 64.51 | 62.337 | 0.00096396 | 32.61 | 1090.1 |  | 3250 | 64.51 | 0.30062 | 62.337 | 0.00096396 | 32.61 | 1090.1 | 1057.49
3251 | 0.30072 | 64.52 | 62.337 | 0.00096428 | 32.62 | 1090.1 |  | 3251 | 64.52 | 0.30072 | 62.337 | 0.00096428 | 32.62 | 1090.1 | 1057.48
3252 | 0.30083 | 64.53 | 62.337 | 0.0009646 | 32.63 | 1090.1 |  | 3252 | 64.53 | 0.30083 | 62.337 | 0.0009646 | 32.63 | 1090.1 | 1057.47
3253 | 0.30093 | 64.54 | 62.337 | 0.00096492 | 32.64 | 1090.1 |  | 3253 | 64.54 | 0.30093 | 62.337 | 0.00096492 | 32.64 | 1090.1 | 1057.46
3254 | 0.30104 | 64.55 | 62.337 | 0.00096524 | 32.65 | 1090.1 |  | 3254 | 64.55 | 0.30104 | 62.337 | 0.00096524 | 32.65 | 1090.1 | 1057.45
3255 | 0.30114 | 64.56 | 62.337 | 0.00096556 | 32.66 | 1090.1 |  | 3255 | 64.56 | 0.30114 | 62.337 | 0.00096556 | 32.66 | 1090.1 | 1057.44
3256 | 0.30125 | 64.57 | 62.337 | 0.00096588 | 32.67 | 1090.1 |  | 3256 | 64.57 | 0.30125 | 62.337 | 0.00096588 | 32.67 | 1090.1 | 1057.43
3257 | 0.30135 | 64.58 | 62.336 | 0.00096619 | 32.68 | 1090.1 |  | 3257 | 64.58 | 0.30135 | 62.336 | 0.00096619 | 32.68 | 1090.1 | 1057.42
3258 | 0.30146 | 64.59 | 62.336 | 0.00096651 | 32.69 | 1090.1 |  | 3258 | 64.59 | 0.30146 | 62.336 | 0.00096651 | 32.69 | 1090.1 | 1057.41
3259 | 0.30156 | 64.6 | 62.336 | 0.00096683 | 32.7 | 1090.2 |  | 3259 | 64.6 | 0.30156 | 62.336 | 0.00096683 | 32.7 | 1090.2 | 1057.5
3260 | 0.30167 | 64.61 | 62.336 | 0.00096715 | 32.71 | 1090.2 |  | 3260 | 64.61 | 0.30167 | 62.336 | 0.00096715 | 32.71 | 1090.2 | 1057.49
3261 | 0.30178 | 64.62 | 62.336 | 0.00096747 | 32.72 | 1090.2 |  | 3261 | 64.62 | 0.30178 | 62.336 | 0.00096747 | 32.72 | 1090.2 | 1057.48
3262 | 0.30188 | 64.63 | 62.336 | 0.00096779 | 32.73 | 1090.2 |  | 3262 | 64.63 | 0.30188 | 62.336 | 0.00096779 | 32.73 | 1090.2 | 1057.47
3263 | 0.30199 | 64.64 | 62.336 | 0.00096811 | 32.74 | 1090.2 |  | 3263 | 64.64 | 0.30199 | 62.336 | 0.00096811 | 32.74 | 1090.2 | 1057.46
3264 | 0.30209 | 64.65 | 62.336 | 0.00096843 | 32.75 | 1090.2 |  | 3264 | 64.65 | 0.30209 | 62.336 | 0.00096843 | 32.75 | 1090.2 | 1057.45
3265 | 0.3022 | 64.66 | 62.336 | 0.00096875 | 32.76 | 1090.2 |  | 3265 | 64.66 | 0.3022 | 62.336 | 0.00096875 | 32.76 | 1090.2 | 1057.44
3266 | 0.3023 | 64.67 | 62.336 | 0.00096907 | 32.77 | 1090.2 |  | 3266 | 64.67 | 0.3023 | 62.336 | 0.00096907 | 32.77 | 1090.2 | 1057.43
3267 | 0.30241 | 64.68 | 62.336 | 0.00096939 | 32.78 | 1090.2 |  | 3267 | 64.68 | 0.30241 | 62.336 | 0.00096939 | 32.78 | 1090.2 | 1057.42
3268 | 0.30251 | 64.69 | 62.336 | 0.00096971 | 32.79 | 1090.2 |  | 3268 | 64.69 | 0.30251 | 62.336 | 0.00096971 | 32.79 | 1090.2 | 1057.41
3269 | 0.30262 | 64.7 | 62.336 | 0.00097003 | 32.8 | 1090.2 |  | 3269 | 64.7 | 0.30262 | 62.336 | 0.00097003 | 32.8 | 1090.2 | 1057.4
3270 | 0.30272 | 64.71 | 62.336 | 0.00097035 | 32.81 | 1090.2 |  | 3270 | 64.71 | 0.30272 | 62.336 | 0.00097035 | 32.81 | 1090.2 | 1057.39
3271 | 0.30283 | 64.72 | 62.336 | 0.00097067 | 32.82 | 1090.2 |  | 3271 | 64.72 | 0.30283 | 62.336 | 0.00097067 | 32.82 | 1090.2 | 1057.38
3272 | 0.30294 | 64.73 | 62.335 | 0.00097099 | 32.83 | 1090.2 |  | 3272 | 64.73 | 0.30294 | 62.335 | 0.00097099 | 32.83 | 1090.2 | 1057.37
3273 | 0.30304 | 64.74 | 62.335 | 0.00097131 | 32.84 | 1090.2 |  | 3273 | 64.74 | 0.30304 | 62.335 | 0.00097131 | 32.84 | 1090.2 | 1057.36
3274 | 0.30315 | 64.75 | 62.335 | 0.00097164 | 32.85 | 1090.2 |  | 3274 | 64.75 | 0.30315 | 62.335 | 0.00097164 | 32.85 | 1090.2 | 1057.35
3275 | 0.30325 | 64.76 | 62.335 | 0.00097196 | 32.86 | 1090.2 |  | 3275 | 64.76 | 0.30325 | 62.335 | 0.00097196 | 32.86 | 1090.2 | 1057.34
3276 | 0.30336 | 64.77 | 62.335 | 0.00097228 | 32.87 | 1090.2 |  | 3276 | 64.77 | 0.30336 | 62.335 | 0.00097228 | 32.87 | 1090.2 | 1057.33
3277 | 0.30347 | 64.78 | 62.335 | 0.0009726 | 32.88 | 1090.2 |  | 3277 | 64.78 | 0.30347 | 62.335 | 0.0009726 | 32.88 | 1090.2 | 1057.32
3278 | 0.30357 | 64.79 | 62.335 | 0.00097292 | 32.89 | 1090.2 |  | 3278 | 64.79 | 0.30357 | 62.335 | 0.00097292 | 32.89 | 1090.2 | 1057.31
3279 | 0.30368 | 64.8 | 62.335 | 0.00097324 | 32.9 | 1090.2 |  | 3279 | 64.8 | 0.30368 | 62.335 | 0.00097324 | 32.9 | 1090.2 | 1057.3
3280 | 0.30378 | 64.81 | 62.335 | 0.00097356 | 32.91 | 1090.2 |  | 3280 | 64.81 | 0.30378 | 62.335 | 0.00097356 | 32.91 | 1090.2 | 1057.29
3281 | 0.30389 | 64.82 | 62.335 | 0.00097388 | 32.92 | 1090.2 |  | 3281 | 64.82 | 0.30389 | 62.335 | 0.00097388 | 32.92 | 1090.2 | 1057.28
3282 | 0.304 | 64.83 | 62.335 | 0.00097421 | 32.93 | 1090.3 |  | 3282 | 64.83 | 0.304 | 62.335 | 0.00097421 | 32.93 | 1090.3 | 1057.37
3283 | 0.3041 | 64.84 | 62.335 | 0.00097453 | 32.94 | 1090.3 |  | 3283 | 64.84 | 0.3041 | 62.335 | 0.00097453 | 32.94 | 1090.3 | 1057.36
3284 | 0.30421 | 64.85 | 62.335 | 0.00097485 | 32.95 | 1090.3 |  | 3284 | 64.85 | 0.30421 | 62.335 | 0.00097485 | 32.95 | 1090.3 | 1057.35
3285 | 0.30431 | 64.86 | 62.335 | 0.00097517 | 32.96 | 1090.3 |  | 3285 | 64.86 | 0.30431 | 62.335 | 0.00097517 | 32.96 | 1090.3 | 1057.34
3286 | 0.30442 | 64.87 | 62.335 | 0.00097549 | 32.97 | 1090.3 |  | 3286 | 64.87 | 0.30442 | 62.335 | 0.00097549 | 32.97 | 1090.3 | 1057.33
3287 | 0.30453 | 64.88 | 62.335 | 0.00097581 | 32.98 | 1090.3 |  | 3287 | 64.88 | 0.30453 | 62.335 | 0.00097581 | 32.98 | 1090.3 | 1057.32
3288 | 0.30463 | 64.89 | 62.334 | 0.00097614 | 32.99 | 1090.3 |  | 3288 | 64.89 | 0.30463 | 62.334 | 0.00097614 | 32.99 | 1090.3 | 1057.31
3289 | 0.30474 | 64.9 | 62.334 | 0.00097646 | 33 | 1090.3 |  | 3289 | 64.9 | 0.30474 | 62.334 | 0.00097646 | 33 | 1090.3 | 1057.3
3290 | 0.30484 | 64.91 | 62.334 | 0.00097678 | 33.01 | 1090.3 |  | 3290 | 64.91 | 0.30484 | 62.334 | 0.00097678 | 33.01 | 1090.3 | 1057.29
3291 | 0.30495 | 64.92 | 62.334 | 0.0009771 | 33.02 | 1090.3 |  | 3291 | 64.92 | 0.30495 | 62.334 | 0.0009771 | 33.02 | 1090.3 | 1057.28
3292 | 0.30506 | 64.93 | 62.334 | 0.00097743 | 33.03 | 1090.3 |  | 3292 | 64.93 | 0.30506 | 62.334 | 0.00097743 | 33.03 | 1090.3 | 1057.27
3293 | 0.30516 | 64.94 | 62.334 | 0.00097775 | 33.04 | 1090.3 |  | 3293 | 64.94 | 0.30516 | 62.334 | 0.00097775 | 33.04 | 1090.3 | 1057.26
3294 | 0.30527 | 64.95 | 62.334 | 0.00097807 | 33.05 | 1090.3 |  | 3294 | 64.95 | 0.30527 | 62.334 | 0.00097807 | 33.05 | 1090.3 | 1057.25
3295 | 0.30538 | 64.96 | 62.334 | 0.00097839 | 33.06 | 1090.3 |  | 3295 | 64.96 | 0.30538 | 62.334 | 0.00097839 | 33.06 | 1090.3 | 1057.24
3296 | 0.30548 | 64.97 | 62.334 | 0.00097872 | 33.07 | 1090.3 |  | 3296 | 64.97 | 0.30548 | 62.334 | 0.00097872 | 33.07 | 1090.3 | 1057.23
3297 | 0.30559 | 64.98 | 62.334 | 0.00097904 | 33.08 | 1090.3 |  | 3297 | 64.98 | 0.30559 | 62.334 | 0.00097904 | 33.08 | 1090.3 | 1057.22
3298 | 0.3057 | 64.99 | 62.334 | 0.00097936 | 33.09 | 1090.3 |  | 3298 | 64.99 | 0.3057 | 62.334 | 0.00097936 | 33.09 | 1090.3 | 1057.21
3299 | 0.3058 | 65 | 62.334 | 0.00097969 | 33.1 | 1090.3 |  | 3299 | 65 | 0.3058 | 62.334 | 0.00097969 | 33.1 | 1090.3 | 1057.2
3300 | 0.30591 | 65.01 | 62.334 | 0.00098001 | 33.11 | 1090.3 |  | 3300 | 65.01 | 0.30591 | 62.334 | 0.00098001 | 33.11 | 1090.3 | 1057.19
3301 | 0.30602 | 65.02 | 62.334 | 0.00098033 | 33.12 | 1090.3 |  | 3301 | 65.02 | 0.30602 | 62.334 | 0.00098033 | 33.12 | 1090.3 | 1057.18
3302 | 0.30612 | 65.03 | 62.334 | 0.00098066 | 33.13 | 1090.3 |  | 3302 | 65.03 | 0.30612 | 62.334 | 0.00098066 | 33.13 | 1090.3 | 1057.17
3303 | 0.30623 | 65.04 | 62.333 | 0.00098098 | 33.14 | 1090.3 |  | 3303 | 65.04 | 0.30623 | 62.333 | 0.00098098 | 33.14 | 1090.3 | 1057.16
3304 | 0.30634 | 65.05 | 62.333 | 0.0009813 | 33.15 | 1090.3 |  | 3304 | 65.05 | 0.30634 | 62.333 | 0.0009813 | 33.15 | 1090.3 | 1057.15
3305 | 0.30644 | 65.06 | 62.333 | 0.00098163 | 33.16 | 1090.4 |  | 3305 | 65.06 | 0.30644 | 62.333 | 0.00098163 | 33.16 | 1090.4 | 1057.24
3306 | 0.30655 | 65.07 | 62.333 | 0.00098195 | 33.17 | 1090.4 |  | 3306 | 65.07 | 0.30655 | 62.333 | 0.00098195 | 33.17 | 1090.4 | 1057.23
3307 | 0.30666 | 65.08 | 62.333 | 0.00098227 | 33.18 | 1090.4 |  | 3307 | 65.08 | 0.30666 | 62.333 | 0.00098227 | 33.18 | 1090.4 | 1057.22
3308 | 0.30676 | 65.09 | 62.333 | 0.0009826 | 33.19 | 1090.4 |  | 3308 | 65.09 | 0.30676 | 62.333 | 0.0009826 | 33.19 | 1090.4 | 1057.21
3309 | 0.30687 | 65.1 | 62.333 | 0.00098292 | 33.2 | 1090.4 |  | 3309 | 65.1 | 0.30687 | 62.333 | 0.00098292 | 33.2 | 1090.4 | 1057.2
3310 | 0.30698 | 65.11 | 62.333 | 0.00098325 | 33.21 | 1090.4 |  | 3310 | 65.11 | 0.30698 | 62.333 | 0.00098325 | 33.21 | 1090.4 | 1057.19
3311 | 0.30708 | 65.12 | 62.333 | 0.00098357 | 33.22 | 1090.4 |  | 3311 | 65.12 | 0.30708 | 62.333 | 0.00098357 | 33.22 | 1090.4 | 1057.18
3312 | 0.30719 | 65.13 | 62.333 | 0.00098389 | 33.23 | 1090.4 |  | 3312 | 65.13 | 0.30719 | 62.333 | 0.00098389 | 33.23 | 1090.4 | 1057.17
3313 | 0.3073 | 65.14 | 62.333 | 0.00098422 | 33.24 | 1090.4 |  | 3313 | 65.14 | 0.3073 | 62.333 | 0.00098422 | 33.24 | 1090.4 | 1057.16
3314 | 0.30741 | 65.15 | 62.333 | 0.00098454 | 33.25 | 1090.4 |  | 3314 | 65.15 | 0.30741 | 62.333 | 0.00098454 | 33.25 | 1090.4 | 1057.15
3315 | 0.30751 | 65.16 | 62.333 | 0.00098487 | 33.26 | 1090.4 |  | 3315 | 65.16 | 0.30751 | 62.333 | 0.00098487 | 33.26 | 1090.4 | 1057.14
3316 | 0.30762 | 65.17 | 62.333 | 0.00098519 | 33.27 | 1090.4 |  | 3316 | 65.17 | 0.30762 | 62.333 | 0.00098519 | 33.27 | 1090.4 | 1057.13
3317 | 0.30773 | 65.18 | 62.333 | 0.00098552 | 33.28 | 1090.4 |  | 3317 | 65.18 | 0.30773 | 62.333 | 0.00098552 | 33.28 | 1090.4 | 1057.12
3318 | 0.30783 | 65.19 | 62.332 | 0.00098584 | 33.29 | 1090.4 |  | 3318 | 65.19 | 0.30783 | 62.332 | 0.00098584 | 33.29 | 1090.4 | 1057.11
3319 | 0.30794 | 65.2 | 62.332 | 0.00098617 | 33.3 | 1090.4 |  | 3319 | 65.2 | 0.30794 | 62.332 | 0.00098617 | 33.3 | 1090.4 | 1057.1
3320 | 0.30805 | 65.21 | 62.332 | 0.00098649 | 33.31 | 1090.4 |  | 3320 | 65.21 | 0.30805 | 62.332 | 0.00098649 | 33.31 | 1090.4 | 1057.09
3321 | 0.30816 | 65.22 | 62.332 | 0.00098682 | 33.32 | 1090.4 |  | 3321 | 65.22 | 0.30816 | 62.332 | 0.00098682 | 33.32 | 1090.4 | 1057.08
3322 | 0.30826 | 65.23 | 62.332 | 0.00098714 | 33.33 | 1090.4 |  | 3322 | 65.23 | 0.30826 | 62.332 | 0.00098714 | 33.33 | 1090.4 | 1057.07
3323 | 0.30837 | 65.24 | 62.332 | 0.00098747 | 33.34 | 1090.4 |  | 3323 | 65.24 | 0.30837 | 62.332 | 0.00098747 | 33.34 | 1090.4 | 1057.06
3324 | 0.30848 | 65.25 | 62.332 | 0.00098779 | 33.35 | 1090.4 |  | 3324 | 65.25 | 0.30848 | 62.332 | 0.00098779 | 33.35 | 1090.4 | 1057.05
3325 | 0.30859 | 65.26 | 62.332 | 0.00098812 | 33.36 | 1090.4 |  | 3325 | 65.26 | 0.30859 | 62.332 | 0.00098812 | 33.36 | 1090.4 | 1057.04
3326 | 0.30869 | 65.27 | 62.332 | 0.00098844 | 33.37 | 1090.4 |  | 3326 | 65.27 | 0.30869 | 62.332 | 0.00098844 | 33.37 | 1090.4 | 1057.03
3327 | 0.3088 | 65.28 | 62.332 | 0.00098877 | 33.38 | 1090.4 |  | 3327 | 65.28 | 0.3088 | 62.332 | 0.00098877 | 33.38 | 1090.4 | 1057.02
3328 | 0.30891 | 65.29 | 62.332 | 0.0009891 | 33.39 | 1090.5 |  | 3328 | 65.29 | 0.30891 | 62.332 | 0.0009891 | 33.39 | 1090.5 | 1057.11
3329 | 0.30902 | 65.3 | 62.332 | 0.00098942 | 33.4 | 1090.5 |  | 3329 | 65.3 | 0.30902 | 62.332 | 0.00098942 | 33.4 | 1090.5 | 1057.1
3330 | 0.30912 | 65.31 | 62.332 | 0.00098975 | 33.41 | 1090.5 |  | 3330 | 65.31 | 0.30912 | 62.332 | 0.00098975 | 33.41 | 1090.5 | 1057.09
3331 | 0.30923 | 65.32 | 62.332 | 0.00099007 | 33.42 | 1090.5 |  | 3331 | 65.32 | 0.30923 | 62.332 | 0.00099007 | 33.42 | 1090.5 | 1057.08
3332 | 0.30934 | 65.33 | 62.332 | 0.0009904 | 33.43 | 1090.5 |  | 3332 | 65.33 | 0.30934 | 62.332 | 0.0009904 | 33.43 | 1090.5 | 1057.07
3333 | 0.30945 | 65.34 | 62.332 | 0.00099073 | 33.44 | 1090.5 |  | 3333 | 65.34 | 0.30945 | 62.332 | 0.00099073 | 33.44 | 1090.5 | 1057.06
3334 | 0.30955 | 65.35 | 62.331 | 0.00099105 | 33.45 | 1090.5 |  | 3334 | 65.35 | 0.30955 | 62.331 | 0.00099105 | 33.45 | 1090.5 | 1057.05
3335 | 0.30966 | 65.36 | 62.331 | 0.00099138 | 33.46 | 1090.5 |  | 3335 | 65.36 | 0.30966 | 62.331 | 0.00099138 | 33.46 | 1090.5 | 1057.04
3336 | 0.30977 | 65.37 | 62.331 | 0.0009917 | 33.47 | 1090.5 |  | 3336 | 65.37 | 0.30977 | 62.331 | 0.0009917 | 33.47 | 1090.5 | 1057.03
3337 | 0.30988 | 65.38 | 62.331 | 0.00099203 | 33.48 | 1090.5 |  | 3337 | 65.38 | 0.30988 | 62.331 | 0.00099203 | 33.48 | 1090.5 | 1057.02
3338 | 0.30999 | 65.39 | 62.331 | 0.00099236 | 33.49 | 1090.5 |  | 3338 | 65.39 | 0.30999 | 62.331 | 0.00099236 | 33.49 | 1090.5 | 1057.01
3339 | 0.31009 | 65.4 | 62.331 | 0.00099268 | 33.5 | 1090.5 |  | 3339 | 65.4 | 0.31009 | 62.331 | 0.00099268 | 33.5 | 1090.5 | 1057
3340 | 0.3102 | 65.41 | 62.331 | 0.00099301 | 33.51 | 1090.5 |  | 3340 | 65.41 | 0.3102 | 62.331 | 0.00099301 | 33.51 | 1090.5 | 1056.99
3341 | 0.31031 | 65.42 | 62.331 | 0.00099334 | 33.52 | 1090.5 |  | 3341 | 65.42 | 0.31031 | 62.331 | 0.00099334 | 33.52 | 1090.5 | 1056.98
3342 | 0.31042 | 65.43 | 62.331 | 0.00099367 | 33.53 | 1090.5 |  | 3342 | 65.43 | 0.31042 | 62.331 | 0.00099367 | 33.53 | 1090.5 | 1056.97
3343 | 0.31053 | 65.44 | 62.331 | 0.00099399 | 33.54 | 1090.5 |  | 3343 | 65.44 | 0.31053 | 62.331 | 0.00099399 | 33.54 | 1090.5 | 1056.96
3344 | 0.31063 | 65.45 | 62.331 | 0.00099432 | 33.55 | 1090.5 |  | 3344 | 65.45 | 0.31063 | 62.331 | 0.00099432 | 33.55 | 1090.5 | 1056.95
3345 | 0.31074 | 65.46 | 62.331 | 0.00099465 | 33.56 | 1090.5 |  | 3345 | 65.46 | 0.31074 | 62.331 | 0.00099465 | 33.56 | 1090.5 | 1056.94
3346 | 0.31085 | 65.47 | 62.331 | 0.00099498 | 33.57 | 1090.5 |  | 3346 | 65.47 | 0.31085 | 62.331 | 0.00099498 | 33.57 | 1090.5 | 1056.93
3347 | 0.31096 | 65.48 | 62.331 | 0.0009953 | 33.58 | 1090.5 |  | 3347 | 65.48 | 0.31096 | 62.331 | 0.0009953 | 33.58 | 1090.5 | 1056.92
3348 | 0.31107 | 65.49 | 62.331 | 0.00099563 | 33.59 | 1090.5 |  | 3348 | 65.49 | 0.31107 | 62.331 | 0.00099563 | 33.59 | 1090.5 | 1056.91
3349 | 0.31117 | 65.5 | 62.33 | 0.00099596 | 33.6 | 1090.5 |  | 3349 | 65.5 | 0.31117 | 62.33 | 0.00099596 | 33.6 | 1090.5 | 1056.9
3350 | 0.31128 | 65.51 | 62.33 | 0.00099629 | 33.61 | 1090.5 |  | 3350 | 65.51 | 0.31128 | 62.33 | 0.00099629 | 33.61 | 1090.5 | 1056.89
3351 | 0.31139 | 65.52 | 62.33 | 0.00099661 | 33.62 | 1090.6 |  | 3351 | 65.52 | 0.31139 | 62.33 | 0.00099661 | 33.62 | 1090.6 | 1056.98
3352 | 0.3115 | 65.53 | 62.33 | 0.00099694 | 33.63 | 1090.6 |  | 3352 | 65.53 | 0.3115 | 62.33 | 0.00099694 | 33.63 | 1090.6 | 1056.97
3353 | 0.31161 | 65.54 | 62.33 | 0.00099727 | 33.64 | 1090.6 |  | 3353 | 65.54 | 0.31161 | 62.33 | 0.00099727 | 33.64 | 1090.6 | 1056.96
3354 | 0.31172 | 65.55 | 62.33 | 0.0009976 | 33.65 | 1090.6 |  | 3354 | 65.55 | 0.31172 | 62.33 | 0.0009976 | 33.65 | 1090.6 | 1056.95
3355 | 0.31182 | 65.56 | 62.33 | 0.00099793 | 33.66 | 1090.6 |  | 3355 | 65.56 | 0.31182 | 62.33 | 0.00099793 | 33.66 | 1090.6 | 1056.94
3356 | 0.31193 | 65.57 | 62.33 | 0.00099825 | 33.67 | 1090.6 |  | 3356 | 65.57 | 0.31193 | 62.33 | 0.00099825 | 33.67 | 1090.6 | 1056.93
3357 | 0.31204 | 65.58 | 62.33 | 0.00099858 | 33.68 | 1090.6 |  | 3357 | 65.58 | 0.31204 | 62.33 | 0.00099858 | 33.68 | 1090.6 | 1056.92
3358 | 0.31215 | 65.59 | 62.33 | 0.00099891 | 33.69 | 1090.6 |  | 3358 | 65.59 | 0.31215 | 62.33 | 0.00099891 | 33.69 | 1090.6 | 1056.91
3359 | 0.31226 | 65.6 | 62.33 | 0.00099924 | 33.7 | 1090.6 |  | 3359 | 65.6 | 0.31226 | 62.33 | 0.00099924 | 33.7 | 1090.6 | 1056.9
3360 | 0.31237 | 65.61 | 62.33 | 0.00099957 | 33.71 | 1090.6 |  | 3360 | 65.61 | 0.31237 | 62.33 | 0.00099957 | 33.71 | 1090.6 | 1056.89
3361 | 0.31248 | 65.62 | 62.33 | 0.0009999 | 33.72 | 1090.6 |  | 3361 | 65.62 | 0.31248 | 62.33 | 0.0009999 | 33.72 | 1090.6 | 1056.88
3362 | 0.31258 | 65.63 | 62.33 | 0.0010002 | 33.73 | 1090.6 |  | 3362 | 65.63 | 0.31258 | 62.33 | 0.0010002 | 33.73 | 1090.6 | 1056.87
3363 | 0.31269 | 65.64 | 62.33 | 0.0010006 | 33.74 | 1090.6 |  | 3363 | 65.64 | 0.31269 | 62.33 | 0.0010006 | 33.74 | 1090.6 | 1056.86
3364 | 0.3128 | 65.65 | 62.329 | 0.0010009 | 33.75 | 1090.6 |  | 3364 | 65.65 | 0.3128 | 62.329 | 0.0010009 | 33.75 | 1090.6 | 1056.85
3365 | 0.31291 | 65.66 | 62.329 | 0.0010012 | 33.76 | 1090.6 |  | 3365 | 65.66 | 0.31291 | 62.329 | 0.0010012 | 33.76 | 1090.6 | 1056.84
3366 | 0.31302 | 65.67 | 62.329 | 0.0010015 | 33.77 | 1090.6 |  | 3366 | 65.67 | 0.31302 | 62.329 | 0.0010015 | 33.77 | 1090.6 | 1056.83
3367 | 0.31313 | 65.68 | 62.329 | 0.0010019 | 33.78 | 1090.6 |  | 3367 | 65.68 | 0.31313 | 62.329 | 0.0010019 | 33.78 | 1090.6 | 1056.82
3368 | 0.31324 | 65.69 | 62.329 | 0.0010022 | 33.79 | 1090.6 |  | 3368 | 65.69 | 0.31324 | 62.329 | 0.0010022 | 33.79 | 1090.6 | 1056.81
3369 | 0.31335 | 65.7 | 62.329 | 0.0010025 | 33.8 | 1090.6 |  | 3369 | 65.7 | 0.31335 | 62.329 | 0.0010025 | 33.8 | 1090.6 | 1056.8
3370 | 0.31345 | 65.71 | 62.329 | 0.0010029 | 33.81 | 1090.6 |  | 3370 | 65.71 | 0.31345 | 62.329 | 0.0010029 | 33.81 | 1090.6 | 1056.79
3371 | 0.31356 | 65.72 | 62.329 | 0.0010032 | 33.82 | 1090.6 |  | 3371 | 65.72 | 0.31356 | 62.329 | 0.0010032 | 33.82 | 1090.6 | 1056.78
3372 | 0.31367 | 65.73 | 62.329 | 0.0010035 | 33.83 | 1090.6 |  | 3372 | 65.73 | 0.31367 | 62.329 | 0.0010035 | 33.83 | 1090.6 | 1056.77
3373 | 0.31378 | 65.74 | 62.329 | 0.0010039 | 33.84 | 1090.6 |  | 3373 | 65.74 | 0.31378 | 62.329 | 0.0010039 | 33.84 | 1090.6 | 1056.76
3374 | 0.31389 | 65.75 | 62.329 | 0.0010042 | 33.85 | 1090.7 |  | 3374 | 65.75 | 0.31389 | 62.329 | 0.0010042 | 33.85 | 1090.7 | 1056.85
3375 | 0.314 | 65.76 | 62.329 | 0.0010045 | 33.86 | 1090.7 |  | 3375 | 65.76 | 0.314 | 62.329 | 0.0010045 | 33.86 | 1090.7 | 1056.84
3376 | 0.31411 | 65.77 | 62.329 | 0.0010048 | 33.87 | 1090.7 |  | 3376 | 65.77 | 0.31411 | 62.329 | 0.0010048 | 33.87 | 1090.7 | 1056.83
3377 | 0.31422 | 65.78 | 62.329 | 0.0010052 | 33.88 | 1090.7 |  | 3377 | 65.78 | 0.31422 | 62.329 | 0.0010052 | 33.88 | 1090.7 | 1056.82
3378 | 0.31433 | 65.79 | 62.329 | 0.0010055 | 33.89 | 1090.7 |  | 3378 | 65.79 | 0.31433 | 62.329 | 0.0010055 | 33.89 | 1090.7 | 1056.81
3379 | 0.31444 | 65.8 | 62.328 | 0.0010058 | 33.9 | 1090.7 |  | 3379 | 65.8 | 0.31444 | 62.328 | 0.0010058 | 33.9 | 1090.7 | 1056.8
3380 | 0.31455 | 65.81 | 62.328 | 0.0010062 | 33.91 | 1090.7 |  | 3380 | 65.81 | 0.31455 | 62.328 | 0.0010062 | 33.91 | 1090.7 | 1056.79
3381 | 0.31465 | 65.82 | 62.328 | 0.0010065 | 33.92 | 1090.7 |  | 3381 | 65.82 | 0.31465 | 62.328 | 0.0010065 | 33.92 | 1090.7 | 1056.78
3382 | 0.31476 | 65.83 | 62.328 | 0.0010068 | 33.93 | 1090.7 |  | 3382 | 65.83 | 0.31476 | 62.328 | 0.0010068 | 33.93 | 1090.7 | 1056.77
3383 | 0.31487 | 65.84 | 62.328 | 0.0010072 | 33.94 | 1090.7 |  | 3383 | 65.84 | 0.31487 | 62.328 | 0.0010072 | 33.94 | 1090.7 | 1056.76
3384 | 0.31498 | 65.85 | 62.328 | 0.0010075 | 33.95 | 1090.7 |  | 3384 | 65.85 | 0.31498 | 62.328 | 0.0010075 | 33.95 | 1090.7 | 1056.75
3385 | 0.31509 | 65.86 | 62.328 | 0.0010078 | 33.96 | 1090.7 |  | 3385 | 65.86 | 0.31509 | 62.328 | 0.0010078 | 33.96 | 1090.7 | 1056.74
3386 | 0.3152 | 65.87 | 62.328 | 0.0010082 | 33.97 | 1090.7 |  | 3386 | 65.87 | 0.3152 | 62.328 | 0.0010082 | 33.97 | 1090.7 | 1056.73
3387 | 0.31531 | 65.88 | 62.328 | 0.0010085 | 33.98 | 1090.7 |  | 3387 | 65.88 | 0.31531 | 62.328 | 0.0010085 | 33.98 | 1090.7 | 1056.72
3388 | 0.31542 | 65.89 | 62.328 | 0.0010088 | 33.99 | 1090.7 |  | 3388 | 65.89 | 0.31542 | 62.328 | 0.0010088 | 33.99 | 1090.7 | 1056.71
3389 | 0.31553 | 65.9 | 62.328 | 0.0010091 | 34 | 1090.7 |  | 3389 | 65.9 | 0.31553 | 62.328 | 0.0010091 | 34 | 1090.7 | 1056.7
3390 | 0.31564 | 65.91 | 62.328 | 0.0010095 | 34.01 | 1090.7 |  | 3390 | 65.91 | 0.31564 | 62.328 | 0.0010095 | 34.01 | 1090.7 | 1056.69
3391 | 0.31575 | 65.92 | 62.328 | 0.0010098 | 34.02 | 1090.7 |  | 3391 | 65.92 | 0.31575 | 62.328 | 0.0010098 | 34.02 | 1090.7 | 1056.68
3392 | 0.31586 | 65.93 | 62.328 | 0.0010101 | 34.03 | 1090.7 |  | 3392 | 65.93 | 0.31586 | 62.328 | 0.0010101 | 34.03 | 1090.7 | 1056.67
3393 | 0.31597 | 65.94 | 62.328 | 0.0010105 | 34.04 | 1090.7 |  | 3393 | 65.94 | 0.31597 | 62.328 | 0.0010105 | 34.04 | 1090.7 | 1056.66
3394 | 0.31608 | 65.95 | 62.327 | 0.0010108 | 34.05 | 1090.7 |  | 3394 | 65.95 | 0.31608 | 62.327 | 0.0010108 | 34.05 | 1090.7 | 1056.65
3395 | 0.31619 | 65.96 | 62.327 | 0.0010111 | 34.06 | 1090.7 |  | 3395 | 65.96 | 0.31619 | 62.327 | 0.0010111 | 34.06 | 1090.7 | 1056.64
3396 | 0.3163 | 65.97 | 62.327 | 0.0010115 | 34.07 | 1090.7 |  | 3396 | 65.97 | 0.3163 | 62.327 | 0.0010115 | 34.07 | 1090.7 | 1056.63
3397 | 0.31641 | 65.98 | 62.327 | 0.0010118 | 34.08 | 1090.8 |  | 3397 | 65.98 | 0.31641 | 62.327 | 0.0010118 | 34.08 | 1090.8 | 1056.72
3398 | 0.31652 | 65.99 | 62.327 | 0.0010121 | 34.09 | 1090.8 |  | 3398 | 65.99 | 0.31652 | 62.327 | 0.0010121 | 34.09 | 1090.8 | 1056.71
3399 | 0.31663 | 66 | 62.327 | 0.0010125 | 34.1 | 1090.8 |  | 3399 | 66 | 0.31663 | 62.327 | 0.0010125 | 34.1 | 1090.8 | 1056.7
3400 | 0.31674 | 66.01 | 62.327 | 0.0010128 | 34.11 | 1090.8 |  | 3400 | 66.01 | 0.31674 | 62.327 | 0.0010128 | 34.11 | 1090.8 | 1056.69
3401 | 0.31685 | 66.02 | 62.327 | 0.0010131 | 34.12 | 1090.8 |  | 3401 | 66.02 | 0.31685 | 62.327 | 0.0010131 | 34.12 | 1090.8 | 1056.68
3402 | 0.31696 | 66.03 | 62.327 | 0.0010135 | 34.13 | 1090.8 |  | 3402 | 66.03 | 0.31696 | 62.327 | 0.0010135 | 34.13 | 1090.8 | 1056.67
3403 | 0.31707 | 66.04 | 62.327 | 0.0010138 | 34.14 | 1090.8 |  | 3403 | 66.04 | 0.31707 | 62.327 | 0.0010138 | 34.14 | 1090.8 | 1056.66
3404 | 0.31718 | 66.05 | 62.327 | 0.0010141 | 34.15 | 1090.8 |  | 3404 | 66.05 | 0.31718 | 62.327 | 0.0010141 | 34.15 | 1090.8 | 1056.65
3405 | 0.31729 | 66.06 | 62.327 | 0.0010145 | 34.16 | 1090.8 |  | 3405 | 66.06 | 0.31729 | 62.327 | 0.0010145 | 34.16 | 1090.8 | 1056.64
3406 | 0.3174 | 66.07 | 62.327 | 0.0010148 | 34.17 | 1090.8 |  | 3406 | 66.07 | 0.3174 | 62.327 | 0.0010148 | 34.17 | 1090.8 | 1056.63
3407 | 0.31751 | 66.08 | 62.327 | 0.0010151 | 34.18 | 1090.8 |  | 3407 | 66.08 | 0.31751 | 62.327 | 0.0010151 | 34.18 | 1090.8 | 1056.62
3408 | 0.31762 | 66.09 | 62.326 | 0.0010155 | 34.19 | 1090.8 |  | 3408 | 66.09 | 0.31762 | 62.326 | 0.0010155 | 34.19 | 1090.8 | 1056.61
3409 | 0.31773 | 66.1 | 62.326 | 0.0010158 | 34.2 | 1090.8 |  | 3409 | 66.1 | 0.31773 | 62.326 | 0.0010158 | 34.2 | 1090.8 | 1056.6
3410 | 0.31784 | 66.11 | 62.326 | 0.0010161 | 34.21 | 1090.8 |  | 3410 | 66.11 | 0.31784 | 62.326 | 0.0010161 | 34.21 | 1090.8 | 1056.59
3411 | 0.31795 | 66.12 | 62.326 | 0.0010165 | 34.22 | 1090.8 |  | 3411 | 66.12 | 0.31795 | 62.326 | 0.0010165 | 34.22 | 1090.8 | 1056.58
3412 | 0.31806 | 66.13 | 62.326 | 0.0010168 | 34.23 | 1090.8 |  | 3412 | 66.13 | 0.31806 | 62.326 | 0.0010168 | 34.23 | 1090.8 | 1056.57
3413 | 0.31817 | 66.14 | 62.326 | 0.0010171 | 34.24 | 1090.8 |  | 3413 | 66.14 | 0.31817 | 62.326 | 0.0010171 | 34.24 | 1090.8 | 1056.56
3414 | 0.31828 | 66.15 | 62.326 | 0.0010175 | 34.25 | 1090.8 |  | 3414 | 66.15 | 0.31828 | 62.326 | 0.0010175 | 34.25 | 1090.8 | 1056.55
3415 | 0.31839 | 66.16 | 62.326 | 0.0010178 | 34.26 | 1090.8 |  | 3415 | 66.16 | 0.31839 | 62.326 | 0.0010178 | 34.26 | 1090.8 | 1056.54
3416 | 0.3185 | 66.17 | 62.326 | 0.0010181 | 34.27 | 1090.8 |  | 3416 | 66.17 | 0.3185 | 62.326 | 0.0010181 | 34.27 | 1090.8 | 1056.53
3417 | 0.31861 | 66.18 | 62.326 | 0.0010185 | 34.28 | 1090.8 |  | 3417 | 66.18 | 0.31861 | 62.326 | 0.0010185 | 34.28 | 1090.8 | 1056.52
3418 | 0.31872 | 66.19 | 62.326 | 0.0010188 | 34.29 | 1090.8 |  | 3418 | 66.19 | 0.31872 | 62.326 | 0.0010188 | 34.29 | 1090.8 | 1056.51
3419 | 0.31883 | 66.2 | 62.326 | 0.0010191 | 34.3 | 1090.8 |  | 3419 | 66.2 | 0.31883 | 62.326 | 0.0010191 | 34.3 | 1090.8 | 1056.5
3420 | 0.31894 | 66.21 | 62.326 | 0.0010195 | 34.31 | 1090.9 |  | 3420 | 66.21 | 0.31894 | 62.326 | 0.0010195 | 34.31 | 1090.9 | 1056.59
3421 | 0.31905 | 66.22 | 62.326 | 0.0010198 | 34.32 | 1090.9 |  | 3421 | 66.22 | 0.31905 | 62.326 | 0.0010198 | 34.32 | 1090.9 | 1056.58
3422 | 0.31916 | 66.23 | 62.326 | 0.0010201 | 34.33 | 1090.9 |  | 3422 | 66.23 | 0.31916 | 62.326 | 0.0010201 | 34.33 | 1090.9 | 1056.57
3423 | 0.31928 | 66.24 | 62.325 | 0.0010205 | 34.34 | 1090.9 |  | 3423 | 66.24 | 0.31928 | 62.325 | 0.0010205 | 34.34 | 1090.9 | 1056.56
3424 | 0.31939 | 66.25 | 62.325 | 0.0010208 | 34.35 | 1090.9 |  | 3424 | 66.25 | 0.31939 | 62.325 | 0.0010208 | 34.35 | 1090.9 | 1056.55
3425 | 0.3195 | 66.26 | 62.325 | 0.0010211 | 34.36 | 1090.9 |  | 3425 | 66.26 | 0.3195 | 62.325 | 0.0010211 | 34.36 | 1090.9 | 1056.54
3426 | 0.31961 | 66.27 | 62.325 | 0.0010215 | 34.37 | 1090.9 |  | 3426 | 66.27 | 0.31961 | 62.325 | 0.0010215 | 34.37 | 1090.9 | 1056.53
3427 | 0.31972 | 66.28 | 62.325 | 0.0010218 | 34.38 | 1090.9 |  | 3427 | 66.28 | 0.31972 | 62.325 | 0.0010218 | 34.38 | 1090.9 | 1056.52
3428 | 0.31983 | 66.29 | 62.325 | 0.0010221 | 34.39 | 1090.9 |  | 3428 | 66.29 | 0.31983 | 62.325 | 0.0010221 | 34.39 | 1090.9 | 1056.51
3429 | 0.31994 | 66.3 | 62.325 | 0.0010225 | 34.4 | 1090.9 |  | 3429 | 66.3 | 0.31994 | 62.325 | 0.0010225 | 34.4 | 1090.9 | 1056.5
3430 | 0.32005 | 66.31 | 62.325 | 0.0010228 | 34.41 | 1090.9 |  | 3430 | 66.31 | 0.32005 | 62.325 | 0.0010228 | 34.41 | 1090.9 | 1056.49
3431 | 0.32016 | 66.32 | 62.325 | 0.0010232 | 34.42 | 1090.9 |  | 3431 | 66.32 | 0.32016 | 62.325 | 0.0010232 | 34.42 | 1090.9 | 1056.48
3432 | 0.32027 | 66.33 | 62.325 | 0.0010235 | 34.43 | 1090.9 |  | 3432 | 66.33 | 0.32027 | 62.325 | 0.0010235 | 34.43 | 1090.9 | 1056.47
3433 | 0.32038 | 66.34 | 62.325 | 0.0010238 | 34.44 | 1090.9 |  | 3433 | 66.34 | 0.32038 | 62.325 | 0.0010238 | 34.44 | 1090.9 | 1056.46
3434 | 0.3205 | 66.35 | 62.325 | 0.0010242 | 34.45 | 1090.9 |  | 3434 | 66.35 | 0.3205 | 62.325 | 0.0010242 | 34.45 | 1090.9 | 1056.45
3435 | 0.32061 | 66.36 | 62.325 | 0.0010245 | 34.46 | 1090.9 |  | 3435 | 66.36 | 0.32061 | 62.325 | 0.0010245 | 34.46 | 1090.9 | 1056.44
3436 | 0.32072 | 66.37 | 62.325 | 0.0010248 | 34.47 | 1090.9 |  | 3436 | 66.37 | 0.32072 | 62.325 | 0.0010248 | 34.47 | 1090.9 | 1056.43
3437 | 0.32083 | 66.38 | 62.325 | 0.0010252 | 34.48 | 1090.9 |  | 3437 | 66.38 | 0.32083 | 62.325 | 0.0010252 | 34.48 | 1090.9 | 1056.42
3438 | 0.32094 | 66.39 | 62.324 | 0.0010255 | 34.49 | 1090.9 |  | 3438 | 66.39 | 0.32094 | 62.324 | 0.0010255 | 34.49 | 1090.9 | 1056.41
3439 | 0.32105 | 66.4 | 62.324 | 0.0010258 | 34.5 | 1090.9 |  | 3439 | 66.4 | 0.32105 | 62.324 | 0.0010258 | 34.5 | 1090.9 | 1056.4
3440 | 0.32116 | 66.41 | 62.324 | 0.0010262 | 34.51 | 1090.9 |  | 3440 | 66.41 | 0.32116 | 62.324 | 0.0010262 | 34.51 | 1090.9 | 1056.39
3441 | 0.32127 | 66.42 | 62.324 | 0.0010265 | 34.52 | 1090.9 |  | 3441 | 66.42 | 0.32127 | 62.324 | 0.0010265 | 34.52 | 1090.9 | 1056.38
3442 | 0.32139 | 66.43 | 62.324 | 0.0010268 | 34.53 | 1090.9 |  | 3442 | 66.43 | 0.32139 | 62.324 | 0.0010268 | 34.53 | 1090.9 | 1056.37
3443 | 0.3215 | 66.44 | 62.324 | 0.0010272 | 34.54 | 1091 |  | 3443 | 66.44 | 0.3215 | 62.324 | 0.0010272 | 34.54 | 1091 | 1056.46
3444 | 0.32161 | 66.45 | 62.324 | 0.0010275 | 34.55 | 1091 |  | 3444 | 66.45 | 0.32161 | 62.324 | 0.0010275 | 34.55 | 1091 | 1056.45
3445 | 0.32172 | 66.46 | 62.324 | 0.0010279 | 34.56 | 1091 |  | 3445 | 66.46 | 0.32172 | 62.324 | 0.0010279 | 34.56 | 1091 | 1056.44
3446 | 0.32183 | 66.47 | 62.324 | 0.0010282 | 34.57 | 1091 |  | 3446 | 66.47 | 0.32183 | 62.324 | 0.0010282 | 34.57 | 1091 | 1056.43
3447 | 0.32194 | 66.48 | 62.324 | 0.0010285 | 34.58 | 1091 |  | 3447 | 66.48 | 0.32194 | 62.324 | 0.0010285 | 34.58 | 1091 | 1056.42
3448 | 0.32205 | 66.49 | 62.324 | 0.0010289 | 34.59 | 1091 |  | 3448 | 66.49 | 0.32205 | 62.324 | 0.0010289 | 34.59 | 1091 | 1056.41
3449 | 0.32217 | 66.5 | 62.324 | 0.0010292 | 34.6 | 1091 |  | 3449 | 66.5 | 0.32217 | 62.324 | 0.0010292 | 34.6 | 1091 | 1056.4
3450 | 0.32228 | 66.51 | 62.324 | 0.0010295 | 34.61 | 1091 |  | 3450 | 66.51 | 0.32228 | 62.324 | 0.0010295 | 34.61 | 1091 | 1056.39
3451 | 0.32239 | 66.52 | 62.324 | 0.0010299 | 34.62 | 1091 |  | 3451 | 66.52 | 0.32239 | 62.324 | 0.0010299 | 34.62 | 1091 | 1056.38
3452 | 0.3225 | 66.53 | 62.323 | 0.0010302 | 34.63 | 1091 |  | 3452 | 66.53 | 0.3225 | 62.323 | 0.0010302 | 34.63 | 1091 | 1056.37
3453 | 0.32261 | 66.54 | 62.323 | 0.0010306 | 34.64 | 1091 |  | 3453 | 66.54 | 0.32261 | 62.323 | 0.0010306 | 34.64 | 1091 | 1056.36
3454 | 0.32272 | 66.55 | 62.323 | 0.0010309 | 34.65 | 1091 |  | 3454 | 66.55 | 0.32272 | 62.323 | 0.0010309 | 34.65 | 1091 | 1056.35
3455 | 0.32284 | 66.56 | 62.323 | 0.0010312 | 34.66 | 1091 |  | 3455 | 66.56 | 0.32284 | 62.323 | 0.0010312 | 34.66 | 1091 | 1056.34
3456 | 0.32295 | 66.57 | 62.323 | 0.0010316 | 34.67 | 1091 |  | 3456 | 66.57 | 0.32295 | 62.323 | 0.0010316 | 34.67 | 1091 | 1056.33
3457 | 0.32306 | 66.58 | 62.323 | 0.0010319 | 34.68 | 1091 |  | 3457 | 66.58 | 0.32306 | 62.323 | 0.0010319 | 34.68 | 1091 | 1056.32
3458 | 0.32317 | 66.59 | 62.323 | 0.0010322 | 34.69 | 1091 |  | 3458 | 66.59 | 0.32317 | 62.323 | 0.0010322 | 34.69 | 1091 | 1056.31
3459 | 0.32328 | 66.6 | 62.323 | 0.0010326 | 34.7 | 1091 |  | 3459 | 66.6 | 0.32328 | 62.323 | 0.0010326 | 34.7 | 1091 | 1056.3
3460 | 0.32339 | 66.61 | 62.323 | 0.0010329 | 34.71 | 1091 |  | 3460 | 66.61 | 0.32339 | 62.323 | 0.0010329 | 34.71 | 1091 | 1056.29
3461 | 0.32351 | 66.62 | 62.323 | 0.0010333 | 34.72 | 1091 |  | 3461 | 66.62 | 0.32351 | 62.323 | 0.0010333 | 34.72 | 1091 | 1056.28
3462 | 0.32362 | 66.63 | 62.323 | 0.0010336 | 34.73 | 1091 |  | 3462 | 66.63 | 0.32362 | 62.323 | 0.0010336 | 34.73 | 1091 | 1056.27
3463 | 0.32373 | 66.64 | 62.323 | 0.0010339 | 34.74 | 1091 |  | 3463 | 66.64 | 0.32373 | 62.323 | 0.0010339 | 34.74 | 1091 | 1056.26
3464 | 0.32384 | 66.65 | 62.323 | 0.0010343 | 34.75 | 1091 |  | 3464 | 66.65 | 0.32384 | 62.323 | 0.0010343 | 34.75 | 1091 | 1056.25
3465 | 0.32396 | 66.66 | 62.323 | 0.0010346 | 34.76 | 1091 |  | 3465 | 66.66 | 0.32396 | 62.323 | 0.0010346 | 34.76 | 1091 | 1056.24
3466 | 0.32407 | 66.67 | 62.323 | 0.001035 | 34.77 | 1091.1 |  | 3466 | 66.67 | 0.32407 | 62.323 | 0.001035 | 34.77 | 1091.1 | 1056.33
3467 | 0.32418 | 66.68 | 62.322 | 0.0010353 | 34.78 | 1091.1 |  | 3467 | 66.68 | 0.32418 | 62.322 | 0.0010353 | 34.78 | 1091.1 | 1056.32
3468 | 0.32429 | 66.69 | 62.322 | 0.0010356 | 34.79 | 1091.1 |  | 3468 | 66.69 | 0.32429 | 62.322 | 0.0010356 | 34.79 | 1091.1 | 1056.31
3469 | 0.3244 | 66.7 | 62.322 | 0.001036 | 34.8 | 1091.1 |  | 3469 | 66.7 | 0.3244 | 62.322 | 0.001036 | 34.8 | 1091.1 | 1056.3
3470 | 0.32452 | 66.71 | 62.322 | 0.0010363 | 34.81 | 1091.1 |  | 3470 | 66.71 | 0.32452 | 62.322 | 0.0010363 | 34.81 | 1091.1 | 1056.29
3471 | 0.32463 | 66.72 | 62.322 | 0.0010366 | 34.821 | 1091.1 |  | 3471 | 66.72 | 0.32463 | 62.322 | 0.0010366 | 34.821 | 1091.1 | 1056.279
3472 | 0.32474 | 66.73 | 62.322 | 0.001037 | 34.831 | 1091.1 |  | 3472 | 66.73 | 0.32474 | 62.322 | 0.001037 | 34.831 | 1091.1 | 1056.269
3473 | 0.32485 | 66.74 | 62.322 | 0.0010373 | 34.841 | 1091.1 |  | 3473 | 66.74 | 0.32485 | 62.322 | 0.0010373 | 34.841 | 1091.1 | 1056.259
3474 | 0.32497 | 66.75 | 62.322 | 0.0010377 | 34.851 | 1091.1 |  | 3474 | 66.75 | 0.32497 | 62.322 | 0.0010377 | 34.851 | 1091.1 | 1056.249
3475 | 0.32508 | 66.76 | 62.322 | 0.001038 | 34.861 | 1091.1 |  | 3475 | 66.76 | 0.32508 | 62.322 | 0.001038 | 34.861 | 1091.1 | 1056.239
3476 | 0.32519 | 66.77 | 62.322 | 0.0010383 | 34.871 | 1091.1 |  | 3476 | 66.77 | 0.32519 | 62.322 | 0.0010383 | 34.871 | 1091.1 | 1056.229
3477 | 0.3253 | 66.78 | 62.322 | 0.0010387 | 34.881 | 1091.1 |  | 3477 | 66.78 | 0.3253 | 62.322 | 0.0010387 | 34.881 | 1091.1 | 1056.219
3478 | 0.32542 | 66.79 | 62.322 | 0.001039 | 34.891 | 1091.1 |  | 3478 | 66.79 | 0.32542 | 62.322 | 0.001039 | 34.891 | 1091.1 | 1056.209
3479 | 0.32553 | 66.8 | 62.322 | 0.0010394 | 34.901 | 1091.1 |  | 3479 | 66.8 | 0.32553 | 62.322 | 0.0010394 | 34.901 | 1091.1 | 1056.199
3480 | 0.32564 | 66.81 | 62.322 | 0.0010397 | 34.911 | 1091.1 |  | 3480 | 66.81 | 0.32564 | 62.322 | 0.0010397 | 34.911 | 1091.1 | 1056.189
3481 | 0.32575 | 66.82 | 62.322 | 0.00104 | 34.921 | 1091.1 |  | 3481 | 66.82 | 0.32575 | 62.322 | 0.00104 | 34.921 | 1091.1 | 1056.179
3482 | 0.32587 | 66.83 | 62.321 | 0.0010404 | 34.931 | 1091.1 |  | 3482 | 66.83 | 0.32587 | 62.321 | 0.0010404 | 34.931 | 1091.1 | 1056.169
3483 | 0.32598 | 66.84 | 62.321 | 0.0010407 | 34.941 | 1091.1 |  | 3483 | 66.84 | 0.32598 | 62.321 | 0.0010407 | 34.941 | 1091.1 | 1056.159
3484 | 0.32609 | 66.85 | 62.321 | 0.0010411 | 34.951 | 1091.1 |  | 3484 | 66.85 | 0.32609 | 62.321 | 0.0010411 | 34.951 | 1091.1 | 1056.149
3485 | 0.3262 | 66.86 | 62.321 | 0.0010414 | 34.961 | 1091.1 |  | 3485 | 66.86 | 0.3262 | 62.321 | 0.0010414 | 34.961 | 1091.1 | 1056.139
3486 | 0.32632 | 66.87 | 62.321 | 0.0010417 | 34.971 | 1091.1 |  | 3486 | 66.87 | 0.32632 | 62.321 | 0.0010417 | 34.971 | 1091.1 | 1056.129
3487 | 0.32643 | 66.88 | 62.321 | 0.0010421 | 34.981 | 1091.1 |  | 3487 | 66.88 | 0.32643 | 62.321 | 0.0010421 | 34.981 | 1091.1 | 1056.119
3488 | 0.32654 | 66.89 | 62.321 | 0.0010424 | 34.991 | 1091.1 |  | 3488 | 66.89 | 0.32654 | 62.321 | 0.0010424 | 34.991 | 1091.1 | 1056.109
3489 | 0.32666 | 66.9 | 62.321 | 0.0010428 | 35.001 | 1091.2 |  | 3489 | 66.9 | 0.32666 | 62.321 | 0.0010428 | 35.001 | 1091.2 | 1056.199
3490 | 0.32677 | 66.91 | 62.321 | 0.0010431 | 35.011 | 1091.2 |  | 3490 | 66.91 | 0.32677 | 62.321 | 0.0010431 | 35.011 | 1091.2 | 1056.189
3491 | 0.32688 | 66.92 | 62.321 | 0.0010435 | 35.021 | 1091.2 |  | 3491 | 66.92 | 0.32688 | 62.321 | 0.0010435 | 35.021 | 1091.2 | 1056.179
3492 | 0.327 | 66.93 | 62.321 | 0.0010438 | 35.031 | 1091.2 |  | 3492 | 66.93 | 0.327 | 62.321 | 0.0010438 | 35.031 | 1091.2 | 1056.169
3493 | 0.32711 | 66.94 | 62.321 | 0.0010441 | 35.041 | 1091.2 |  | 3493 | 66.94 | 0.32711 | 62.321 | 0.0010441 | 35.041 | 1091.2 | 1056.159
3494 | 0.32722 | 66.95 | 62.321 | 0.0010445 | 35.051 | 1091.2 |  | 3494 | 66.95 | 0.32722 | 62.321 | 0.0010445 | 35.051 | 1091.2 | 1056.149
3495 | 0.32733 | 66.96 | 62.321 | 0.0010448 | 35.061 | 1091.2 |  | 3495 | 66.96 | 0.32733 | 62.321 | 0.0010448 | 35.061 | 1091.2 | 1056.139
3496 | 0.32745 | 66.97 | 62.32 | 0.0010452 | 35.071 | 1091.2 |  | 3496 | 66.97 | 0.32745 | 62.32 | 0.0010452 | 35.071 | 1091.2 | 1056.129
3497 | 0.32756 | 66.98 | 62.32 | 0.0010455 | 35.081 | 1091.2 |  | 3497 | 66.98 | 0.32756 | 62.32 | 0.0010455 | 35.081 | 1091.2 | 1056.119
3498 | 0.32767 | 66.99 | 62.32 | 0.0010458 | 35.091 | 1091.2 |  | 3498 | 66.99 | 0.32767 | 62.32 | 0.0010458 | 35.091 | 1091.2 | 1056.109
3499 | 0.32779 | 67 | 62.32 | 0.0010462 | 35.101 | 1091.2 |  | 3499 | 67 | 0.32779 | 62.32 | 0.0010462 | 35.101 | 1091.2 | 1056.099
3500 | 0.3279 | 67.01 | 62.32 | 0.0010465 | 35.111 | 1091.2 |  | 3500 | 67.01 | 0.3279 | 62.32 | 0.0010465 | 35.111 | 1091.2 | 1056.089
3501 | 0.32801 | 67.02 | 62.32 | 0.0010469 | 35.121 | 1091.2 |  | 3501 | 67.02 | 0.32801 | 62.32 | 0.0010469 | 35.121 | 1091.2 | 1056.079
3502 | 0.32813 | 67.03 | 62.32 | 0.0010472 | 35.131 | 1091.2 |  | 3502 | 67.03 | 0.32813 | 62.32 | 0.0010472 | 35.131 | 1091.2 | 1056.069
3503 | 0.32824 | 67.04 | 62.32 | 0.0010476 | 35.141 | 1091.2 |  | 3503 | 67.04 | 0.32824 | 62.32 | 0.0010476 | 35.141 | 1091.2 | 1056.059
3504 | 0.32835 | 67.05 | 62.32 | 0.0010479 | 35.151 | 1091.2 |  | 3504 | 67.05 | 0.32835 | 62.32 | 0.0010479 | 35.151 | 1091.2 | 1056.049
3505 | 0.32847 | 67.06 | 62.32 | 0.0010482 | 35.161 | 1091.2 |  | 3505 | 67.06 | 0.32847 | 62.32 | 0.0010482 | 35.161 | 1091.2 | 1056.039
3506 | 0.32858 | 67.07 | 62.32 | 0.0010486 | 35.171 | 1091.2 |  | 3506 | 67.07 | 0.32858 | 62.32 | 0.0010486 | 35.171 | 1091.2 | 1056.029
3507 | 0.32869 | 67.08 | 62.32 | 0.0010489 | 35.181 | 1091.2 |  | 3507 | 67.08 | 0.32869 | 62.32 | 0.0010489 | 35.181 | 1091.2 | 1056.019
3508 | 0.32881 | 67.09 | 62.32 | 0.0010493 | 35.191 | 1091.2 |  | 3508 | 67.09 | 0.32881 | 62.32 | 0.0010493 | 35.191 | 1091.2 | 1056.009
3509 | 0.32892 | 67.1 | 62.32 | 0.0010496 | 35.201 | 1091.2 |  | 3509 | 67.1 | 0.32892 | 62.32 | 0.0010496 | 35.201 | 1091.2 | 1055.999
3510 | 0.32904 | 67.11 | 62.319 | 0.00105 | 35.211 | 1091.2 |  | 3510 | 67.11 | 0.32904 | 62.319 | 0.00105 | 35.211 | 1091.2 | 1055.989
3511 | 0.32915 | 67.12 | 62.319 | 0.0010503 | 35.221 | 1091.2 |  | 3511 | 67.12 | 0.32915 | 62.319 | 0.0010503 | 35.221 | 1091.2 | 1055.979
3512 | 0.32926 | 67.13 | 62.319 | 0.0010506 | 35.231 | 1091.3 |  | 3512 | 67.13 | 0.32926 | 62.319 | 0.0010506 | 35.231 | 1091.3 | 1056.069
3513 | 0.32938 | 67.14 | 62.319 | 0.001051 | 35.241 | 1091.3 |  | 3513 | 67.14 | 0.32938 | 62.319 | 0.001051 | 35.241 | 1091.3 | 1056.059
3514 | 0.32949 | 67.15 | 62.319 | 0.0010513 | 35.251 | 1091.3 |  | 3514 | 67.15 | 0.32949 | 62.319 | 0.0010513 | 35.251 | 1091.3 | 1056.049
3515 | 0.3296 | 67.16 | 62.319 | 0.0010517 | 35.261 | 1091.3 |  | 3515 | 67.16 | 0.3296 | 62.319 | 0.0010517 | 35.261 | 1091.3 | 1056.039
3516 | 0.32972 | 67.17 | 62.319 | 0.001052 | 35.271 | 1091.3 |  | 3516 | 67.17 | 0.32972 | 62.319 | 0.001052 | 35.271 | 1091.3 | 1056.029
3517 | 0.32983 | 67.18 | 62.319 | 0.0010524 | 35.281 | 1091.3 |  | 3517 | 67.18 | 0.32983 | 62.319 | 0.0010524 | 35.281 | 1091.3 | 1056.019
3518 | 0.32995 | 67.19 | 62.319 | 0.0010527 | 35.291 | 1091.3 |  | 3518 | 67.19 | 0.32995 | 62.319 | 0.0010527 | 35.291 | 1091.3 | 1056.009
3519 | 0.33006 | 67.2 | 62.319 | 0.001053 | 35.301 | 1091.3 |  | 3519 | 67.2 | 0.33006 | 62.319 | 0.001053 | 35.301 | 1091.3 | 1055.999
3520 | 0.33017 | 67.21 | 62.319 | 0.0010534 | 35.311 | 1091.3 |  | 3520 | 67.21 | 0.33017 | 62.319 | 0.0010534 | 35.311 | 1091.3 | 1055.989
3521 | 0.33029 | 67.22 | 62.319 | 0.0010537 | 35.321 | 1091.3 |  | 3521 | 67.22 | 0.33029 | 62.319 | 0.0010537 | 35.321 | 1091.3 | 1055.979
3522 | 0.3304 | 67.23 | 62.319 | 0.0010541 | 35.331 | 1091.3 |  | 3522 | 67.23 | 0.3304 | 62.319 | 0.0010541 | 35.331 | 1091.3 | 1055.969
3523 | 0.33052 | 67.24 | 62.319 | 0.0010544 | 35.341 | 1091.3 |  | 3523 | 67.24 | 0.33052 | 62.319 | 0.0010544 | 35.341 | 1091.3 | 1055.959
3524 | 0.33063 | 67.25 | 62.319 | 0.0010548 | 35.351 | 1091.3 |  | 3524 | 67.25 | 0.33063 | 62.319 | 0.0010548 | 35.351 | 1091.3 | 1055.949
3525 | 0.33074 | 67.26 | 62.318 | 0.0010551 | 35.361 | 1091.3 |  | 3525 | 67.26 | 0.33074 | 62.318 | 0.0010551 | 35.361 | 1091.3 | 1055.939
3526 | 0.33086 | 67.27 | 62.318 | 0.0010555 | 35.371 | 1091.3 |  | 3526 | 67.27 | 0.33086 | 62.318 | 0.0010555 | 35.371 | 1091.3 | 1055.929
3527 | 0.33097 | 67.28 | 62.318 | 0.0010558 | 35.381 | 1091.3 |  | 3527 | 67.28 | 0.33097 | 62.318 | 0.0010558 | 35.381 | 1091.3 | 1055.919
3528 | 0.33109 | 67.29 | 62.318 | 0.0010561 | 35.391 | 1091.3 |  | 3528 | 67.29 | 0.33109 | 62.318 | 0.0010561 | 35.391 | 1091.3 | 1055.909
3529 | 0.3312 | 67.3 | 62.318 | 0.0010565 | 35.401 | 1091.3 |  | 3529 | 67.3 | 0.3312 | 62.318 | 0.0010565 | 35.401 | 1091.3 | 1055.899
3530 | 0.33132 | 67.31 | 62.318 | 0.0010568 | 35.411 | 1091.3 |  | 3530 | 67.31 | 0.33132 | 62.318 | 0.0010568 | 35.411 | 1091.3 | 1055.889
3531 | 0.33143 | 67.32 | 62.318 | 0.0010572 | 35.421 | 1091.3 |  | 3531 | 67.32 | 0.33143 | 62.318 | 0.0010572 | 35.421 | 1091.3 | 1055.879
3532 | 0.33154 | 67.33 | 62.318 | 0.0010575 | 35.431 | 1091.3 |  | 3532 | 67.33 | 0.33154 | 62.318 | 0.0010575 | 35.431 | 1091.3 | 1055.869
3533 | 0.33166 | 67.34 | 62.318 | 0.0010579 | 35.441 | 1091.3 |  | 3533 | 67.34 | 0.33166 | 62.318 | 0.0010579 | 35.441 | 1091.3 | 1055.859
3534 | 0.33177 | 67.35 | 62.318 | 0.0010582 | 35.451 | 1091.3 |  | 3534 | 67.35 | 0.33177 | 62.318 | 0.0010582 | 35.451 | 1091.3 | 1055.849
3535 | 0.33189 | 67.36 | 62.318 | 0.0010586 | 35.461 | 1091.4 |  | 3535 | 67.36 | 0.33189 | 62.318 | 0.0010586 | 35.461 | 1091.4 | 1055.939
3536 | 0.332 | 67.37 | 62.318 | 0.0010589 | 35.471 | 1091.4 |  | 3536 | 67.37 | 0.332 | 62.318 | 0.0010589 | 35.471 | 1091.4 | 1055.929
3537 | 0.33212 | 67.38 | 62.318 | 0.0010593 | 35.481 | 1091.4 |  | 3537 | 67.38 | 0.33212 | 62.318 | 0.0010593 | 35.481 | 1091.4 | 1055.919
3538 | 0.33223 | 67.39 | 62.318 | 0.0010596 | 35.491 | 1091.4 |  | 3538 | 67.39 | 0.33223 | 62.318 | 0.0010596 | 35.491 | 1091.4 | 1055.909
3539 | 0.33235 | 67.4 | 62.317 | 0.0010599 | 35.501 | 1091.4 |  | 3539 | 67.4 | 0.33235 | 62.317 | 0.0010599 | 35.501 | 1091.4 | 1055.899
3540 | 0.33246 | 67.41 | 62.317 | 0.0010603 | 35.511 | 1091.4 |  | 3540 | 67.41 | 0.33246 | 62.317 | 0.0010603 | 35.511 | 1091.4 | 1055.889
3541 | 0.33258 | 67.42 | 62.317 | 0.0010606 | 35.521 | 1091.4 |  | 3541 | 67.42 | 0.33258 | 62.317 | 0.0010606 | 35.521 | 1091.4 | 1055.879
3542 | 0.33269 | 67.43 | 62.317 | 0.001061 | 35.531 | 1091.4 |  | 3542 | 67.43 | 0.33269 | 62.317 | 0.001061 | 35.531 | 1091.4 | 1055.869
3543 | 0.33281 | 67.44 | 62.317 | 0.0010613 | 35.541 | 1091.4 |  | 3543 | 67.44 | 0.33281 | 62.317 | 0.0010613 | 35.541 | 1091.4 | 1055.859
3544 | 0.33292 | 67.45 | 62.317 | 0.0010617 | 35.551 | 1091.4 |  | 3544 | 67.45 | 0.33292 | 62.317 | 0.0010617 | 35.551 | 1091.4 | 1055.849
3545 | 0.33304 | 67.46 | 62.317 | 0.001062 | 35.561 | 1091.4 |  | 3545 | 67.46 | 0.33304 | 62.317 | 0.001062 | 35.561 | 1091.4 | 1055.839
3546 | 0.33315 | 67.47 | 62.317 | 0.0010624 | 35.571 | 1091.4 |  | 3546 | 67.47 | 0.33315 | 62.317 | 0.0010624 | 35.571 | 1091.4 | 1055.829
3547 | 0.33326 | 67.48 | 62.317 | 0.0010627 | 35.581 | 1091.4 |  | 3547 | 67.48 | 0.33326 | 62.317 | 0.0010627 | 35.581 | 1091.4 | 1055.819
3548 | 0.33338 | 67.49 | 62.317 | 0.0010631 | 35.591 | 1091.4 |  | 3548 | 67.49 | 0.33338 | 62.317 | 0.0010631 | 35.591 | 1091.4 | 1055.809
3549 | 0.33349 | 67.5 | 62.317 | 0.0010634 | 35.601 | 1091.4 |  | 3549 | 67.5 | 0.33349 | 62.317 | 0.0010634 | 35.601 | 1091.4 | 1055.799
3550 | 0.33361 | 67.51 | 62.317 | 0.0010638 | 35.611 | 1091.4 |  | 3550 | 67.51 | 0.33361 | 62.317 | 0.0010638 | 35.611 | 1091.4 | 1055.789
3551 | 0.33373 | 67.52 | 62.317 | 0.0010641 | 35.621 | 1091.4 |  | 3551 | 67.52 | 0.33373 | 62.317 | 0.0010641 | 35.621 | 1091.4 | 1055.779
3552 | 0.33384 | 67.53 | 62.317 | 0.0010645 | 35.631 | 1091.4 |  | 3552 | 67.53 | 0.33384 | 62.317 | 0.0010645 | 35.631 | 1091.4 | 1055.769
3553 | 0.33396 | 67.54 | 62.316 | 0.0010648 | 35.641 | 1091.4 |  | 3553 | 67.54 | 0.33396 | 62.316 | 0.0010648 | 35.641 | 1091.4 | 1055.759
3554 | 0.33407 | 67.55 | 62.316 | 0.0010651 | 35.651 | 1091.4 |  | 3554 | 67.55 | 0.33407 | 62.316 | 0.0010651 | 35.651 | 1091.4 | 1055.749
3555 | 0.33419 | 67.56 | 62.316 | 0.0010655 | 35.661 | 1091.4 |  | 3555 | 67.56 | 0.33419 | 62.316 | 0.0010655 | 35.661 | 1091.4 | 1055.739
3556 | 0.3343 | 67.57 | 62.316 | 0.0010658 | 35.671 | 1091.4 |  | 3556 | 67.57 | 0.3343 | 62.316 | 0.0010658 | 35.671 | 1091.4 | 1055.729
3557 | 0.33442 | 67.58 | 62.316 | 0.0010662 | 35.681 | 1091.4 |  | 3557 | 67.58 | 0.33442 | 62.316 | 0.0010662 | 35.681 | 1091.4 | 1055.719
3558 | 0.33453 | 67.59 | 62.316 | 0.0010665 | 35.691 | 1091.5 |  | 3558 | 67.59 | 0.33453 | 62.316 | 0.0010665 | 35.691 | 1091.5 | 1055.809
3559 | 0.33465 | 67.6 | 62.316 | 0.0010669 | 35.701 | 1091.5 |  | 3559 | 67.6 | 0.33465 | 62.316 | 0.0010669 | 35.701 | 1091.5 | 1055.799
3560 | 0.33476 | 67.61 | 62.316 | 0.0010672 | 35.711 | 1091.5 |  | 3560 | 67.61 | 0.33476 | 62.316 | 0.0010672 | 35.711 | 1091.5 | 1055.789
3561 | 0.33488 | 67.62 | 62.316 | 0.0010676 | 35.721 | 1091.5 |  | 3561 | 67.62 | 0.33488 | 62.316 | 0.0010676 | 35.721 | 1091.5 | 1055.779
3562 | 0.33499 | 67.63 | 62.316 | 0.0010679 | 35.731 | 1091.5 |  | 3562 | 67.63 | 0.33499 | 62.316 | 0.0010679 | 35.731 | 1091.5 | 1055.769
3563 | 0.33511 | 67.64 | 62.316 | 0.0010683 | 35.741 | 1091.5 |  | 3563 | 67.64 | 0.33511 | 62.316 | 0.0010683 | 35.741 | 1091.5 | 1055.759
3564 | 0.33522 | 67.65 | 62.316 | 0.0010686 | 35.751 | 1091.5 |  | 3564 | 67.65 | 0.33522 | 62.316 | 0.0010686 | 35.751 | 1091.5 | 1055.749
3565 | 0.33534 | 67.66 | 62.316 | 0.001069 | 35.761 | 1091.5 |  | 3565 | 67.66 | 0.33534 | 62.316 | 0.001069 | 35.761 | 1091.5 | 1055.739
3566 | 0.33546 | 67.67 | 62.316 | 0.0010693 | 35.771 | 1091.5 |  | 3566 | 67.67 | 0.33546 | 62.316 | 0.0010693 | 35.771 | 1091.5 | 1055.729
3567 | 0.33557 | 67.68 | 62.315 | 0.0010697 | 35.781 | 1091.5 |  | 3567 | 67.68 | 0.33557 | 62.315 | 0.0010697 | 35.781 | 1091.5 | 1055.719
3568 | 0.33569 | 67.69 | 62.315 | 0.00107 | 35.791 | 1091.5 |  | 3568 | 67.69 | 0.33569 | 62.315 | 0.00107 | 35.791 | 1091.5 | 1055.709
3569 | 0.3358 | 67.7 | 62.315 | 0.0010704 | 35.801 | 1091.5 |  | 3569 | 67.7 | 0.3358 | 62.315 | 0.0010704 | 35.801 | 1091.5 | 1055.699
3570 | 0.33592 | 67.71 | 62.315 | 0.0010707 | 35.811 | 1091.5 |  | 3570 | 67.71 | 0.33592 | 62.315 | 0.0010707 | 35.811 | 1091.5 | 1055.689
3571 | 0.33603 | 67.72 | 62.315 | 0.0010711 | 35.821 | 1091.5 |  | 3571 | 67.72 | 0.33603 | 62.315 | 0.0010711 | 35.821 | 1091.5 | 1055.679
3572 | 0.33615 | 67.73 | 62.315 | 0.0010714 | 35.831 | 1091.5 |  | 3572 | 67.73 | 0.33615 | 62.315 | 0.0010714 | 35.831 | 1091.5 | 1055.669
3573 | 0.33627 | 67.74 | 62.315 | 0.0010718 | 35.841 | 1091.5 |  | 3573 | 67.74 | 0.33627 | 62.315 | 0.0010718 | 35.841 | 1091.5 | 1055.659
3574 | 0.33638 | 67.75 | 62.315 | 0.0010721 | 35.851 | 1091.5 |  | 3574 | 67.75 | 0.33638 | 62.315 | 0.0010721 | 35.851 | 1091.5 | 1055.649
3575 | 0.3365 | 67.76 | 62.315 | 0.0010725 | 35.861 | 1091.5 |  | 3575 | 67.76 | 0.3365 | 62.315 | 0.0010725 | 35.861 | 1091.5 | 1055.639
3576 | 0.33661 | 67.77 | 62.315 | 0.0010728 | 35.871 | 1091.5 |  | 3576 | 67.77 | 0.33661 | 62.315 | 0.0010728 | 35.871 | 1091.5 | 1055.629
3577 | 0.33673 | 67.78 | 62.315 | 0.0010732 | 35.881 | 1091.5 |  | 3577 | 67.78 | 0.33673 | 62.315 | 0.0010732 | 35.881 | 1091.5 | 1055.619
3578 | 0.33685 | 67.79 | 62.315 | 0.0010735 | 35.891 | 1091.5 |  | 3578 | 67.79 | 0.33685 | 62.315 | 0.0010735 | 35.891 | 1091.5 | 1055.609
3579 | 0.33696 | 67.8 | 62.315 | 0.0010739 | 35.901 | 1091.5 |  | 3579 | 67.8 | 0.33696 | 62.315 | 0.0010739 | 35.901 | 1091.5 | 1055.599
3580 | 0.33708 | 67.81 | 62.315 | 0.0010742 | 35.911 | 1091.5 |  | 3580 | 67.81 | 0.33708 | 62.315 | 0.0010742 | 35.911 | 1091.5 | 1055.589
3581 | 0.33719 | 67.82 | 62.314 | 0.0010746 | 35.921 | 1091.6 |  | 3581 | 67.82 | 0.33719 | 62.314 | 0.0010746 | 35.921 | 1091.6 | 1055.679
3582 | 0.33731 | 67.83 | 62.314 | 0.0010749 | 35.931 | 1091.6 |  | 3582 | 67.83 | 0.33731 | 62.314 | 0.0010749 | 35.931 | 1091.6 | 1055.669
3583 | 0.33743 | 67.84 | 62.314 | 0.0010753 | 35.941 | 1091.6 |  | 3583 | 67.84 | 0.33743 | 62.314 | 0.0010753 | 35.941 | 1091.6 | 1055.659
3584 | 0.33754 | 67.85 | 62.314 | 0.0010756 | 35.951 | 1091.6 |  | 3584 | 67.85 | 0.33754 | 62.314 | 0.0010756 | 35.951 | 1091.6 | 1055.649
3585 | 0.33766 | 67.86 | 62.314 | 0.001076 | 35.961 | 1091.6 |  | 3585 | 67.86 | 0.33766 | 62.314 | 0.001076 | 35.961 | 1091.6 | 1055.639
3586 | 0.33777 | 67.87 | 62.314 | 0.0010763 | 35.971 | 1091.6 |  | 3586 | 67.87 | 0.33777 | 62.314 | 0.0010763 | 35.971 | 1091.6 | 1055.629
3587 | 0.33789 | 67.88 | 62.314 | 0.0010767 | 35.981 | 1091.6 |  | 3587 | 67.88 | 0.33789 | 62.314 | 0.0010767 | 35.981 | 1091.6 | 1055.619
3588 | 0.33801 | 67.89 | 62.314 | 0.001077 | 35.991 | 1091.6 |  | 3588 | 67.89 | 0.33801 | 62.314 | 0.001077 | 35.991 | 1091.6 | 1055.609
3589 | 0.33812 | 67.9 | 62.314 | 0.0010774 | 36.001 | 1091.6 |  | 3589 | 67.9 | 0.33812 | 62.314 | 0.0010774 | 36.001 | 1091.6 | 1055.599
3590 | 0.33824 | 67.91 | 62.314 | 0.0010777 | 36.011 | 1091.6 |  | 3590 | 67.91 | 0.33824 | 62.314 | 0.0010777 | 36.011 | 1091.6 | 1055.589
3591 | 0.33836 | 67.92 | 62.314 | 0.0010781 | 36.021 | 1091.6 |  | 3591 | 67.92 | 0.33836 | 62.314 | 0.0010781 | 36.021 | 1091.6 | 1055.579
3592 | 0.33847 | 67.93 | 62.314 | 0.0010784 | 36.031 | 1091.6 |  | 3592 | 67.93 | 0.33847 | 62.314 | 0.0010784 | 36.031 | 1091.6 | 1055.569
3593 | 0.33859 | 67.94 | 62.314 | 0.0010788 | 36.041 | 1091.6 |  | 3593 | 67.94 | 0.33859 | 62.314 | 0.0010788 | 36.041 | 1091.6 | 1055.559
3594 | 0.33871 | 67.95 | 62.314 | 0.0010791 | 36.051 | 1091.6 |  | 3594 | 67.95 | 0.33871 | 62.314 | 0.0010791 | 36.051 | 1091.6 | 1055.549
3595 | 0.33882 | 67.96 | 62.313 | 0.0010795 | 36.061 | 1091.6 |  | 3595 | 67.96 | 0.33882 | 62.313 | 0.0010795 | 36.061 | 1091.6 | 1055.539
3596 | 0.33894 | 67.97 | 62.313 | 0.0010798 | 36.071 | 1091.6 |  | 3596 | 67.97 | 0.33894 | 62.313 | 0.0010798 | 36.071 | 1091.6 | 1055.529
3597 | 0.33906 | 67.98 | 62.313 | 0.0010802 | 36.081 | 1091.6 |  | 3597 | 67.98 | 0.33906 | 62.313 | 0.0010802 | 36.081 | 1091.6 | 1055.519
3598 | 0.33917 | 67.99 | 62.313 | 0.0010805 | 36.091 | 1091.6 |  | 3598 | 67.99 | 0.33917 | 62.313 | 0.0010805 | 36.091 | 1091.6 | 1055.509
3599 | 0.33929 | 68 | 62.313 | 0.0010809 | 36.101 | 1091.6 |  | 3599 | 68 | 0.33929 | 62.313 | 0.0010809 | 36.101 | 1091.6 | 1055.499
3600 | 0.33941 | 68.01 | 62.313 | 0.0010812 | 36.111 | 1091.6 |  | 3600 | 68.01 | 0.33941 | 62.313 | 0.0010812 | 36.111 | 1091.6 | 1055.489
3601 | 0.33952 | 68.02 | 62.313 | 0.0010816 | 36.121 | 1091.6 |  | 3601 | 68.02 | 0.33952 | 62.313 | 0.0010816 | 36.121 | 1091.6 | 1055.479
3602 | 0.33964 | 68.03 | 62.313 | 0.0010819 | 36.131 | 1091.6 |  | 3602 | 68.03 | 0.33964 | 62.313 | 0.0010819 | 36.131 | 1091.6 | 1055.469
3603 | 0.33976 | 68.04 | 62.313 | 0.0010823 | 36.141 | 1091.6 |  | 3603 | 68.04 | 0.33976 | 62.313 | 0.0010823 | 36.141 | 1091.6 | 1055.459
3604 | 0.33987 | 68.05 | 62.313 | 0.0010826 | 36.151 | 1091.7 |  | 3604 | 68.05 | 0.33987 | 62.313 | 0.0010826 | 36.151 | 1091.7 | 1055.549
3605 | 0.33999 | 68.06 | 62.313 | 0.001083 | 36.161 | 1091.7 |  | 3605 | 68.06 | 0.33999 | 62.313 | 0.001083 | 36.161 | 1091.7 | 1055.539
3606 | 0.34011 | 68.07 | 62.313 | 0.0010833 | 36.171 | 1091.7 |  | 3606 | 68.07 | 0.34011 | 62.313 | 0.0010833 | 36.171 | 1091.7 | 1055.529
3607 | 0.34022 | 68.08 | 62.313 | 0.0010837 | 36.181 | 1091.7 |  | 3607 | 68.08 | 0.34022 | 62.313 | 0.0010837 | 36.181 | 1091.7 | 1055.519
3608 | 0.34034 | 68.09 | 62.313 | 0.001084 | 36.191 | 1091.7 |  | 3608 | 68.09 | 0.34034 | 62.313 | 0.001084 | 36.191 | 1091.7 | 1055.509
3609 | 0.34046 | 68.1 | 62.312 | 0.0010844 | 36.201 | 1091.7 |  | 3609 | 68.1 | 0.34046 | 62.312 | 0.0010844 | 36.201 | 1091.7 | 1055.499
3610 | 0.34058 | 68.11 | 62.312 | 0.0010848 | 36.211 | 1091.7 |  | 3610 | 68.11 | 0.34058 | 62.312 | 0.0010848 | 36.211 | 1091.7 | 1055.489
3611 | 0.34069 | 68.12 | 62.312 | 0.0010851 | 36.221 | 1091.7 |  | 3611 | 68.12 | 0.34069 | 62.312 | 0.0010851 | 36.221 | 1091.7 | 1055.479
3612 | 0.34081 | 68.13 | 62.312 | 0.0010855 | 36.231 | 1091.7 |  | 3612 | 68.13 | 0.34081 | 62.312 | 0.0010855 | 36.231 | 1091.7 | 1055.469
3613 | 0.34093 | 68.14 | 62.312 | 0.0010858 | 36.241 | 1091.7 |  | 3613 | 68.14 | 0.34093 | 62.312 | 0.0010858 | 36.241 | 1091.7 | 1055.459
3614 | 0.34104 | 68.15 | 62.312 | 0.0010862 | 36.251 | 1091.7 |  | 3614 | 68.15 | 0.34104 | 62.312 | 0.0010862 | 36.251 | 1091.7 | 1055.449
3615 | 0.34116 | 68.16 | 62.312 | 0.0010865 | 36.261 | 1091.7 |  | 3615 | 68.16 | 0.34116 | 62.312 | 0.0010865 | 36.261 | 1091.7 | 1055.439
3616 | 0.34128 | 68.17 | 62.312 | 0.0010869 | 36.271 | 1091.7 |  | 3616 | 68.17 | 0.34128 | 62.312 | 0.0010869 | 36.271 | 1091.7 | 1055.429
3617 | 0.3414 | 68.18 | 62.312 | 0.0010872 | 36.281 | 1091.7 |  | 3617 | 68.18 | 0.3414 | 62.312 | 0.0010872 | 36.281 | 1091.7 | 1055.419
3618 | 0.34151 | 68.19 | 62.312 | 0.0010876 | 36.291 | 1091.7 |  | 3618 | 68.19 | 0.34151 | 62.312 | 0.0010876 | 36.291 | 1091.7 | 1055.409
3619 | 0.34163 | 68.2 | 62.312 | 0.0010879 | 36.301 | 1091.7 |  | 3619 | 68.2 | 0.34163 | 62.312 | 0.0010879 | 36.301 | 1091.7 | 1055.399
3620 | 0.34175 | 68.21 | 62.312 | 0.0010883 | 36.311 | 1091.7 |  | 3620 | 68.21 | 0.34175 | 62.312 | 0.0010883 | 36.311 | 1091.7 | 1055.389
3621 | 0.34187 | 68.22 | 62.312 | 0.0010886 | 36.321 | 1091.7 |  | 3621 | 68.22 | 0.34187 | 62.312 | 0.0010886 | 36.321 | 1091.7 | 1055.379
3622 | 0.34198 | 68.23 | 62.312 | 0.001089 | 36.331 | 1091.7 |  | 3622 | 68.23 | 0.34198 | 62.312 | 0.001089 | 36.331 | 1091.7 | 1055.369
3623 | 0.3421 | 68.24 | 62.311 | 0.0010894 | 36.341 | 1091.7 |  | 3623 | 68.24 | 0.3421 | 62.311 | 0.0010894 | 36.341 | 1091.7 | 1055.359
3624 | 0.34222 | 68.25 | 62.311 | 0.0010897 | 36.351 | 1091.7 |  | 3624 | 68.25 | 0.34222 | 62.311 | 0.0010897 | 36.351 | 1091.7 | 1055.349
3625 | 0.34234 | 68.26 | 62.311 | 0.0010901 | 36.361 | 1091.7 |  | 3625 | 68.26 | 0.34234 | 62.311 | 0.0010901 | 36.361 | 1091.7 | 1055.339
3626 | 0.34245 | 68.27 | 62.311 | 0.0010904 | 36.371 | 1091.7 |  | 3626 | 68.27 | 0.34245 | 62.311 | 0.0010904 | 36.371 | 1091.7 | 1055.329
3627 | 0.34257 | 68.28 | 62.311 | 0.0010908 | 36.381 | 1091.8 |  | 3627 | 68.28 | 0.34257 | 62.311 | 0.0010908 | 36.381 | 1091.8 | 1055.419
3628 | 0.34269 | 68.29 | 62.311 | 0.0010911 | 36.391 | 1091.8 |  | 3628 | 68.29 | 0.34269 | 62.311 | 0.0010911 | 36.391 | 1091.8 | 1055.409
3629 | 0.34281 | 68.3 | 62.311 | 0.0010915 | 36.401 | 1091.8 |  | 3629 | 68.3 | 0.34281 | 62.311 | 0.0010915 | 36.401 | 1091.8 | 1055.399
3630 | 0.34293 | 68.31 | 62.311 | 0.0010918 | 36.411 | 1091.8 |  | 3630 | 68.31 | 0.34293 | 62.311 | 0.0010918 | 36.411 | 1091.8 | 1055.389
3631 | 0.34304 | 68.32 | 62.311 | 0.0010922 | 36.421 | 1091.8 |  | 3631 | 68.32 | 0.34304 | 62.311 | 0.0010922 | 36.421 | 1091.8 | 1055.379
3632 | 0.34316 | 68.33 | 62.311 | 0.0010925 | 36.431 | 1091.8 |  | 3632 | 68.33 | 0.34316 | 62.311 | 0.0010925 | 36.431 | 1091.8 | 1055.369
3633 | 0.34328 | 68.34 | 62.311 | 0.0010929 | 36.441 | 1091.8 |  | 3633 | 68.34 | 0.34328 | 62.311 | 0.0010929 | 36.441 | 1091.8 | 1055.359
3634 | 0.3434 | 68.35 | 62.311 | 0.0010933 | 36.451 | 1091.8 |  | 3634 | 68.35 | 0.3434 | 62.311 | 0.0010933 | 36.451 | 1091.8 | 1055.349
3635 | 0.34352 | 68.36 | 62.311 | 0.0010936 | 36.461 | 1091.8 |  | 3635 | 68.36 | 0.34352 | 62.311 | 0.0010936 | 36.461 | 1091.8 | 1055.339
3636 | 0.34363 | 68.37 | 62.311 | 0.001094 | 36.471 | 1091.8 |  | 3636 | 68.37 | 0.34363 | 62.311 | 0.001094 | 36.471 | 1091.8 | 1055.329
3637 | 0.34375 | 68.38 | 62.31 | 0.0010943 | 36.481 | 1091.8 |  | 3637 | 68.38 | 0.34375 | 62.31 | 0.0010943 | 36.481 | 1091.8 | 1055.319
3638 | 0.34387 | 68.39 | 62.31 | 0.0010947 | 36.491 | 1091.8 |  | 3638 | 68.39 | 0.34387 | 62.31 | 0.0010947 | 36.491 | 1091.8 | 1055.309
3639 | 0.34399 | 68.4 | 62.31 | 0.001095 | 36.501 | 1091.8 |  | 3639 | 68.4 | 0.34399 | 62.31 | 0.001095 | 36.501 | 1091.8 | 1055.299
3640 | 0.34411 | 68.41 | 62.31 | 0.0010954 | 36.511 | 1091.8 |  | 3640 | 68.41 | 0.34411 | 62.31 | 0.0010954 | 36.511 | 1091.8 | 1055.289
3641 | 0.34422 | 68.42 | 62.31 | 0.0010957 | 36.521 | 1091.8 |  | 3641 | 68.42 | 0.34422 | 62.31 | 0.0010957 | 36.521 | 1091.8 | 1055.279
3642 | 0.34434 | 68.43 | 62.31 | 0.0010961 | 36.531 | 1091.8 |  | 3642 | 68.43 | 0.34434 | 62.31 | 0.0010961 | 36.531 | 1091.8 | 1055.269
3643 | 0.34446 | 68.44 | 62.31 | 0.0010965 | 36.541 | 1091.8 |  | 3643 | 68.44 | 0.34446 | 62.31 | 0.0010965 | 36.541 | 1091.8 | 1055.259
3644 | 0.34458 | 68.45 | 62.31 | 0.0010968 | 36.551 | 1091.8 |  | 3644 | 68.45 | 0.34458 | 62.31 | 0.0010968 | 36.551 | 1091.8 | 1055.249
3645 | 0.3447 | 68.46 | 62.31 | 0.0010972 | 36.561 | 1091.8 |  | 3645 | 68.46 | 0.3447 | 62.31 | 0.0010972 | 36.561 | 1091.8 | 1055.239
3646 | 0.34482 | 68.47 | 62.31 | 0.0010975 | 36.571 | 1091.8 |  | 3646 | 68.47 | 0.34482 | 62.31 | 0.0010975 | 36.571 | 1091.8 | 1055.229
3647 | 0.34493 | 68.48 | 62.31 | 0.0010979 | 36.581 | 1091.8 |  | 3647 | 68.48 | 0.34493 | 62.31 | 0.0010979 | 36.581 | 1091.8 | 1055.219
3648 | 0.34505 | 68.49 | 62.31 | 0.0010982 | 36.591 | 1091.8 |  | 3648 | 68.49 | 0.34505 | 62.31 | 0.0010982 | 36.591 | 1091.8 | 1055.209
3649 | 0.34517 | 68.5 | 62.31 | 0.0010986 | 36.601 | 1091.8 |  | 3649 | 68.5 | 0.34517 | 62.31 | 0.0010986 | 36.601 | 1091.8 | 1055.199
3650 | 0.34529 | 68.51 | 62.31 | 0.001099 | 36.611 | 1091.9 |  | 3650 | 68.51 | 0.34529 | 62.31 | 0.001099 | 36.611 | 1091.9 | 1055.289
3651 | 0.34541 | 68.52 | 62.309 | 0.0010993 | 36.621 | 1091.9 |  | 3651 | 68.52 | 0.34541 | 62.309 | 0.0010993 | 36.621 | 1091.9 | 1055.279
3652 | 0.34553 | 68.53 | 62.309 | 0.0010997 | 36.631 | 1091.9 |  | 3652 | 68.53 | 0.34553 | 62.309 | 0.0010997 | 36.631 | 1091.9 | 1055.269
3653 | 0.34565 | 68.54 | 62.309 | 0.0011 | 36.641 | 1091.9 |  | 3653 | 68.54 | 0.34565 | 62.309 | 0.0011 | 36.641 | 1091.9 | 1055.259
3654 | 0.34576 | 68.55 | 62.309 | 0.0011004 | 36.651 | 1091.9 |  | 3654 | 68.55 | 0.34576 | 62.309 | 0.0011004 | 36.651 | 1091.9 | 1055.249
3655 | 0.34588 | 68.56 | 62.309 | 0.0011007 | 36.661 | 1091.9 |  | 3655 | 68.56 | 0.34588 | 62.309 | 0.0011007 | 36.661 | 1091.9 | 1055.239
3656 | 0.346 | 68.57 | 62.309 | 0.0011011 | 36.671 | 1091.9 |  | 3656 | 68.57 | 0.346 | 62.309 | 0.0011011 | 36.671 | 1091.9 | 1055.229
3657 | 0.34612 | 68.58 | 62.309 | 0.0011015 | 36.681 | 1091.9 |  | 3657 | 68.58 | 0.34612 | 62.309 | 0.0011015 | 36.681 | 1091.9 | 1055.219
3658 | 0.34624 | 68.59 | 62.309 | 0.0011018 | 36.691 | 1091.9 |  | 3658 | 68.59 | 0.34624 | 62.309 | 0.0011018 | 36.691 | 1091.9 | 1055.209
3659 | 0.34636 | 68.6 | 62.309 | 0.0011022 | 36.701 | 1091.9 |  | 3659 | 68.6 | 0.34636 | 62.309 | 0.0011022 | 36.701 | 1091.9 | 1055.199
3660 | 0.34648 | 68.61 | 62.309 | 0.0011025 | 36.711 | 1091.9 |  | 3660 | 68.61 | 0.34648 | 62.309 | 0.0011025 | 36.711 | 1091.9 | 1055.189
3661 | 0.3466 | 68.62 | 62.309 | 0.0011029 | 36.721 | 1091.9 |  | 3661 | 68.62 | 0.3466 | 62.309 | 0.0011029 | 36.721 | 1091.9 | 1055.179
3662 | 0.34672 | 68.63 | 62.309 | 0.0011032 | 36.731 | 1091.9 |  | 3662 | 68.63 | 0.34672 | 62.309 | 0.0011032 | 36.731 | 1091.9 | 1055.169
3663 | 0.34683 | 68.64 | 62.309 | 0.0011036 | 36.741 | 1091.9 |  | 3663 | 68.64 | 0.34683 | 62.309 | 0.0011036 | 36.741 | 1091.9 | 1055.159
3664 | 0.34695 | 68.65 | 62.309 | 0.001104 | 36.751 | 1091.9 |  | 3664 | 68.65 | 0.34695 | 62.309 | 0.001104 | 36.751 | 1091.9 | 1055.149
3665 | 0.34707 | 68.66 | 62.308 | 0.0011043 | 36.761 | 1091.9 |  | 3665 | 68.66 | 0.34707 | 62.308 | 0.0011043 | 36.761 | 1091.9 | 1055.139
3666 | 0.34719 | 68.67 | 62.308 | 0.0011047 | 36.771 | 1091.9 |  | 3666 | 68.67 | 0.34719 | 62.308 | 0.0011047 | 36.771 | 1091.9 | 1055.129
3667 | 0.34731 | 68.68 | 62.308 | 0.001105 | 36.781 | 1091.9 |  | 3667 | 68.68 | 0.34731 | 62.308 | 0.001105 | 36.781 | 1091.9 | 1055.119
3668 | 0.34743 | 68.69 | 62.308 | 0.0011054 | 36.791 | 1091.9 |  | 3668 | 68.69 | 0.34743 | 62.308 | 0.0011054 | 36.791 | 1091.9 | 1055.109
3669 | 0.34755 | 68.7 | 62.308 | 0.0011057 | 36.801 | 1091.9 |  | 3669 | 68.7 | 0.34755 | 62.308 | 0.0011057 | 36.801 | 1091.9 | 1055.099
3670 | 0.34767 | 68.71 | 62.308 | 0.0011061 | 36.811 | 1091.9 |  | 3670 | 68.71 | 0.34767 | 62.308 | 0.0011061 | 36.811 | 1091.9 | 1055.089
3671 | 0.34779 | 68.72 | 62.308 | 0.0011065 | 36.821 | 1091.9 |  | 3671 | 68.72 | 0.34779 | 62.308 | 0.0011065 | 36.821 | 1091.9 | 1055.079
3672 | 0.34791 | 68.73 | 62.308 | 0.0011068 | 36.831 | 1091.9 |  | 3672 | 68.73 | 0.34791 | 62.308 | 0.0011068 | 36.831 | 1091.9 | 1055.069
3673 | 0.34803 | 68.74 | 62.308 | 0.0011072 | 36.841 | 1092 |  | 3673 | 68.74 | 0.34803 | 62.308 | 0.0011072 | 36.841 | 1092 | 1055.159
3674 | 0.34815 | 68.75 | 62.308 | 0.0011075 | 36.851 | 1092 |  | 3674 | 68.75 | 0.34815 | 62.308 | 0.0011075 | 36.851 | 1092 | 1055.149
3675 | 0.34827 | 68.76 | 62.308 | 0.0011079 | 36.861 | 1092 |  | 3675 | 68.76 | 0.34827 | 62.308 | 0.0011079 | 36.861 | 1092 | 1055.139
3676 | 0.34839 | 68.77 | 62.308 | 0.0011083 | 36.871 | 1092 |  | 3676 | 68.77 | 0.34839 | 62.308 | 0.0011083 | 36.871 | 1092 | 1055.129
3677 | 0.3485 | 68.78 | 62.308 | 0.0011086 | 36.881 | 1092 |  | 3677 | 68.78 | 0.3485 | 62.308 | 0.0011086 | 36.881 | 1092 | 1055.119
3678 | 0.34862 | 68.79 | 62.307 | 0.001109 | 36.891 | 1092 |  | 3678 | 68.79 | 0.34862 | 62.307 | 0.001109 | 36.891 | 1092 | 1055.109
3679 | 0.34874 | 68.8 | 62.307 | 0.0011093 | 36.901 | 1092 |  | 3679 | 68.8 | 0.34874 | 62.307 | 0.0011093 | 36.901 | 1092 | 1055.099
3680 | 0.34886 | 68.81 | 62.307 | 0.0011097 | 36.911 | 1092 |  | 3680 | 68.81 | 0.34886 | 62.307 | 0.0011097 | 36.911 | 1092 | 1055.089
3681 | 0.34898 | 68.82 | 62.307 | 0.0011101 | 36.921 | 1092 |  | 3681 | 68.82 | 0.34898 | 62.307 | 0.0011101 | 36.921 | 1092 | 1055.079
3682 | 0.3491 | 68.83 | 62.307 | 0.0011104 | 36.931 | 1092 |  | 3682 | 68.83 | 0.3491 | 62.307 | 0.0011104 | 36.931 | 1092 | 1055.069
3683 | 0.34922 | 68.84 | 62.307 | 0.0011108 | 36.941 | 1092 |  | 3683 | 68.84 | 0.34922 | 62.307 | 0.0011108 | 36.941 | 1092 | 1055.059
3684 | 0.34934 | 68.85 | 62.307 | 0.0011111 | 36.951 | 1092 |  | 3684 | 68.85 | 0.34934 | 62.307 | 0.0011111 | 36.951 | 1092 | 1055.049
3685 | 0.34946 | 68.86 | 62.307 | 0.0011115 | 36.961 | 1092 |  | 3685 | 68.86 | 0.34946 | 62.307 | 0.0011115 | 36.961 | 1092 | 1055.039
3686 | 0.34958 | 68.87 | 62.307 | 0.0011119 | 36.971 | 1092 |  | 3686 | 68.87 | 0.34958 | 62.307 | 0.0011119 | 36.971 | 1092 | 1055.029
3687 | 0.3497 | 68.88 | 62.307 | 0.0011122 | 36.981 | 1092 |  | 3687 | 68.88 | 0.3497 | 62.307 | 0.0011122 | 36.981 | 1092 | 1055.019
3688 | 0.34982 | 68.89 | 62.307 | 0.0011126 | 36.991 | 1092 |  | 3688 | 68.89 | 0.34982 | 62.307 | 0.0011126 | 36.991 | 1092 | 1055.009
3689 | 0.34994 | 68.9 | 62.307 | 0.0011129 | 37.001 | 1092 |  | 3689 | 68.9 | 0.34994 | 62.307 | 0.0011129 | 37.001 | 1092 | 1054.999
3690 | 0.35006 | 68.91 | 62.307 | 0.0011133 | 37.011 | 1092 |  | 3690 | 68.91 | 0.35006 | 62.307 | 0.0011133 | 37.011 | 1092 | 1054.989
3691 | 0.35018 | 68.92 | 62.307 | 0.0011137 | 37.021 | 1092 |  | 3691 | 68.92 | 0.35018 | 62.307 | 0.0011137 | 37.021 | 1092 | 1054.979
3692 | 0.3503 | 68.93 | 62.306 | 0.001114 | 37.031 | 1092 |  | 3692 | 68.93 | 0.3503 | 62.306 | 0.001114 | 37.031 | 1092 | 1054.969
3693 | 0.35042 | 68.94 | 62.306 | 0.0011144 | 37.041 | 1092 |  | 3693 | 68.94 | 0.35042 | 62.306 | 0.0011144 | 37.041 | 1092 | 1054.959
3694 | 0.35054 | 68.95 | 62.306 | 0.0011148 | 37.051 | 1092 |  | 3694 | 68.95 | 0.35054 | 62.306 | 0.0011148 | 37.051 | 1092 | 1054.949
3695 | 0.35066 | 68.96 | 62.306 | 0.0011151 | 37.061 | 1092 |  | 3695 | 68.96 | 0.35066 | 62.306 | 0.0011151 | 37.061 | 1092 | 1054.939
3696 | 0.35078 | 68.97 | 62.306 | 0.0011155 | 37.071 | 1092.1 |  | 3696 | 68.97 | 0.35078 | 62.306 | 0.0011155 | 37.071 | 1092.1 | 1055.029
3697 | 0.3509 | 68.98 | 62.306 | 0.0011158 | 37.081 | 1092.1 |  | 3697 | 68.98 | 0.3509 | 62.306 | 0.0011158 | 37.081 | 1092.1 | 1055.019
3698 | 0.35102 | 68.99 | 62.306 | 0.0011162 | 37.091 | 1092.1 |  | 3698 | 68.99 | 0.35102 | 62.306 | 0.0011162 | 37.091 | 1092.1 | 1055.009
3699 | 0.35114 | 69 | 62.306 | 0.0011166 | 37.101 | 1092.1 |  | 3699 | 69 | 0.35114 | 62.306 | 0.0011166 | 37.101 | 1092.1 | 1054.999
3700 | 0.35126 | 69.01 | 62.306 | 0.0011169 | 37.111 | 1092.1 |  | 3700 | 69.01 | 0.35126 | 62.306 | 0.0011169 | 37.111 | 1092.1 | 1054.989
3701 | 0.35138 | 69.02 | 62.306 | 0.0011173 | 37.121 | 1092.1 |  | 3701 | 69.02 | 0.35138 | 62.306 | 0.0011173 | 37.121 | 1092.1 | 1054.979
3702 | 0.3515 | 69.03 | 62.306 | 0.0011176 | 37.131 | 1092.1 |  | 3702 | 69.03 | 0.3515 | 62.306 | 0.0011176 | 37.131 | 1092.1 | 1054.969
3703 | 0.35162 | 69.04 | 62.306 | 0.001118 | 37.141 | 1092.1 |  | 3703 | 69.04 | 0.35162 | 62.306 | 0.001118 | 37.141 | 1092.1 | 1054.959
3704 | 0.35175 | 69.05 | 62.306 | 0.0011184 | 37.151 | 1092.1 |  | 3704 | 69.05 | 0.35175 | 62.306 | 0.0011184 | 37.151 | 1092.1 | 1054.949
3705 | 0.35187 | 69.06 | 62.306 | 0.0011187 | 37.161 | 1092.1 |  | 3705 | 69.06 | 0.35187 | 62.306 | 0.0011187 | 37.161 | 1092.1 | 1054.939
3706 | 0.35199 | 69.07 | 62.305 | 0.0011191 | 37.171 | 1092.1 |  | 3706 | 69.07 | 0.35199 | 62.305 | 0.0011191 | 37.171 | 1092.1 | 1054.929
3707 | 0.35211 | 69.08 | 62.305 | 0.0011195 | 37.181 | 1092.1 |  | 3707 | 69.08 | 0.35211 | 62.305 | 0.0011195 | 37.181 | 1092.1 | 1054.919
3708 | 0.35223 | 69.09 | 62.305 | 0.0011198 | 37.191 | 1092.1 |  | 3708 | 69.09 | 0.35223 | 62.305 | 0.0011198 | 37.191 | 1092.1 | 1054.909
3709 | 0.35235 | 69.1 | 62.305 | 0.0011202 | 37.201 | 1092.1 |  | 3709 | 69.1 | 0.35235 | 62.305 | 0.0011202 | 37.201 | 1092.1 | 1054.899
3710 | 0.35247 | 69.11 | 62.305 | 0.0011205 | 37.211 | 1092.1 |  | 3710 | 69.11 | 0.35247 | 62.305 | 0.0011205 | 37.211 | 1092.1 | 1054.889
3711 | 0.35259 | 69.12 | 62.305 | 0.0011209 | 37.221 | 1092.1 |  | 3711 | 69.12 | 0.35259 | 62.305 | 0.0011209 | 37.221 | 1092.1 | 1054.879
3712 | 0.35271 | 69.13 | 62.305 | 0.0011213 | 37.231 | 1092.1 |  | 3712 | 69.13 | 0.35271 | 62.305 | 0.0011213 | 37.231 | 1092.1 | 1054.869
3713 | 0.35283 | 69.14 | 62.305 | 0.0011216 | 37.241 | 1092.1 |  | 3713 | 69.14 | 0.35283 | 62.305 | 0.0011216 | 37.241 | 1092.1 | 1054.859
3714 | 0.35295 | 69.15 | 62.305 | 0.001122 | 37.251 | 1092.1 |  | 3714 | 69.15 | 0.35295 | 62.305 | 0.001122 | 37.251 | 1092.1 | 1054.849
3715 | 0.35307 | 69.16 | 62.305 | 0.0011224 | 37.261 | 1092.1 |  | 3715 | 69.16 | 0.35307 | 62.305 | 0.0011224 | 37.261 | 1092.1 | 1054.839
3716 | 0.35319 | 69.17 | 62.305 | 0.0011227 | 37.271 | 1092.1 |  | 3716 | 69.17 | 0.35319 | 62.305 | 0.0011227 | 37.271 | 1092.1 | 1054.829
3717 | 0.35332 | 69.18 | 62.305 | 0.0011231 | 37.281 | 1092.1 |  | 3717 | 69.18 | 0.35332 | 62.305 | 0.0011231 | 37.281 | 1092.1 | 1054.819
3718 | 0.35344 | 69.19 | 62.305 | 0.0011235 | 37.291 | 1092.1 |  | 3718 | 69.19 | 0.35344 | 62.305 | 0.0011235 | 37.291 | 1092.1 | 1054.809
3719 | 0.35356 | 69.2 | 62.304 | 0.0011238 | 37.301 | 1092.2 |  | 3719 | 69.2 | 0.35356 | 62.304 | 0.0011238 | 37.301 | 1092.2 | 1054.899
3720 | 0.35368 | 69.21 | 62.304 | 0.0011242 | 37.311 | 1092.2 |  | 3720 | 69.21 | 0.35368 | 62.304 | 0.0011242 | 37.311 | 1092.2 | 1054.889
3721 | 0.3538 | 69.22 | 62.304 | 0.0011245 | 37.321 | 1092.2 |  | 3721 | 69.22 | 0.3538 | 62.304 | 0.0011245 | 37.321 | 1092.2 | 1054.879
3722 | 0.35392 | 69.23 | 62.304 | 0.0011249 | 37.331 | 1092.2 |  | 3722 | 69.23 | 0.35392 | 62.304 | 0.0011249 | 37.331 | 1092.2 | 1054.869
3723 | 0.35404 | 69.24 | 62.304 | 0.0011253 | 37.341 | 1092.2 |  | 3723 | 69.24 | 0.35404 | 62.304 | 0.0011253 | 37.341 | 1092.2 | 1054.859
3724 | 0.35416 | 69.25 | 62.304 | 0.0011256 | 37.351 | 1092.2 |  | 3724 | 69.25 | 0.35416 | 62.304 | 0.0011256 | 37.351 | 1092.2 | 1054.849
3725 | 0.35428 | 69.26 | 62.304 | 0.001126 | 37.361 | 1092.2 |  | 3725 | 69.26 | 0.35428 | 62.304 | 0.001126 | 37.361 | 1092.2 | 1054.839
3726 | 0.35441 | 69.27 | 62.304 | 0.0011264 | 37.371 | 1092.2 |  | 3726 | 69.27 | 0.35441 | 62.304 | 0.0011264 | 37.371 | 1092.2 | 1054.829
3727 | 0.35453 | 69.28 | 62.304 | 0.0011267 | 37.381 | 1092.2 |  | 3727 | 69.28 | 0.35453 | 62.304 | 0.0011267 | 37.381 | 1092.2 | 1054.819
3728 | 0.35465 | 69.29 | 62.304 | 0.0011271 | 37.391 | 1092.2 |  | 3728 | 69.29 | 0.35465 | 62.304 | 0.0011271 | 37.391 | 1092.2 | 1054.809
3729 | 0.35477 | 69.3 | 62.304 | 0.0011275 | 37.401 | 1092.2 |  | 3729 | 69.3 | 0.35477 | 62.304 | 0.0011275 | 37.401 | 1092.2 | 1054.799
3730 | 0.35489 | 69.31 | 62.304 | 0.0011278 | 37.411 | 1092.2 |  | 3730 | 69.31 | 0.35489 | 62.304 | 0.0011278 | 37.411 | 1092.2 | 1054.789
3731 | 0.35501 | 69.32 | 62.304 | 0.0011282 | 37.421 | 1092.2 |  | 3731 | 69.32 | 0.35501 | 62.304 | 0.0011282 | 37.421 | 1092.2 | 1054.779
3732 | 0.35513 | 69.33 | 62.304 | 0.0011286 | 37.431 | 1092.2 |  | 3732 | 69.33 | 0.35513 | 62.304 | 0.0011286 | 37.431 | 1092.2 | 1054.769
3733 | 0.35526 | 69.34 | 62.303 | 0.0011289 | 37.441 | 1092.2 |  | 3733 | 69.34 | 0.35526 | 62.303 | 0.0011289 | 37.441 | 1092.2 | 1054.759
3734 | 0.35538 | 69.35 | 62.303 | 0.0011293 | 37.451 | 1092.2 |  | 3734 | 69.35 | 0.35538 | 62.303 | 0.0011293 | 37.451 | 1092.2 | 1054.749
3735 | 0.3555 | 69.36 | 62.303 | 0.0011297 | 37.461 | 1092.2 |  | 3735 | 69.36 | 0.3555 | 62.303 | 0.0011297 | 37.461 | 1092.2 | 1054.739
3736 | 0.35562 | 69.37 | 62.303 | 0.00113 | 37.471 | 1092.2 |  | 3736 | 69.37 | 0.35562 | 62.303 | 0.00113 | 37.471 | 1092.2 | 1054.729
3737 | 0.35574 | 69.38 | 62.303 | 0.0011304 | 37.481 | 1092.2 |  | 3737 | 69.38 | 0.35574 | 62.303 | 0.0011304 | 37.481 | 1092.2 | 1054.719
3738 | 0.35586 | 69.39 | 62.303 | 0.0011307 | 37.491 | 1092.2 |  | 3738 | 69.39 | 0.35586 | 62.303 | 0.0011307 | 37.491 | 1092.2 | 1054.709
3739 | 0.35599 | 69.4 | 62.303 | 0.0011311 | 37.501 | 1092.2 |  | 3739 | 69.4 | 0.35599 | 62.303 | 0.0011311 | 37.501 | 1092.2 | 1054.699
3740 | 0.35611 | 69.41 | 62.303 | 0.0011315 | 37.511 | 1092.2 |  | 3740 | 69.41 | 0.35611 | 62.303 | 0.0011315 | 37.511 | 1092.2 | 1054.689
3741 | 0.35623 | 69.42 | 62.303 | 0.0011318 | 37.521 | 1092.2 |  | 3741 | 69.42 | 0.35623 | 62.303 | 0.0011318 | 37.521 | 1092.2 | 1054.679
3742 | 0.35635 | 69.43 | 62.303 | 0.0011322 | 37.531 | 1092.3 |  | 3742 | 69.43 | 0.35635 | 62.303 | 0.0011322 | 37.531 | 1092.3 | 1054.769
3743 | 0.35647 | 69.44 | 62.303 | 0.0011326 | 37.541 | 1092.3 |  | 3743 | 69.44 | 0.35647 | 62.303 | 0.0011326 | 37.541 | 1092.3 | 1054.759
3744 | 0.35659 | 69.45 | 62.303 | 0.0011329 | 37.551 | 1092.3 |  | 3744 | 69.45 | 0.35659 | 62.303 | 0.0011329 | 37.551 | 1092.3 | 1054.749
3745 | 0.35672 | 69.46 | 62.303 | 0.0011333 | 37.561 | 1092.3 |  | 3745 | 69.46 | 0.35672 | 62.303 | 0.0011333 | 37.561 | 1092.3 | 1054.739
3746 | 0.35684 | 69.47 | 62.302 | 0.0011337 | 37.571 | 1092.3 |  | 3746 | 69.47 | 0.35684 | 62.302 | 0.0011337 | 37.571 | 1092.3 | 1054.729
3747 | 0.35696 | 69.48 | 62.302 | 0.001134 | 37.581 | 1092.3 |  | 3747 | 69.48 | 0.35696 | 62.302 | 0.001134 | 37.581 | 1092.3 | 1054.719
3748 | 0.35708 | 69.49 | 62.302 | 0.0011344 | 37.591 | 1092.3 |  | 3748 | 69.49 | 0.35708 | 62.302 | 0.0011344 | 37.591 | 1092.3 | 1054.709
3749 | 0.3572 | 69.5 | 62.302 | 0.0011348 | 37.601 | 1092.3 |  | 3749 | 69.5 | 0.3572 | 62.302 | 0.0011348 | 37.601 | 1092.3 | 1054.699
3750 | 0.35733 | 69.51 | 62.302 | 0.0011351 | 37.611 | 1092.3 |  | 3750 | 69.51 | 0.35733 | 62.302 | 0.0011351 | 37.611 | 1092.3 | 1054.689
3751 | 0.35745 | 69.52 | 62.302 | 0.0011355 | 37.621 | 1092.3 |  | 3751 | 69.52 | 0.35745 | 62.302 | 0.0011355 | 37.621 | 1092.3 | 1054.679
3752 | 0.35757 | 69.53 | 62.302 | 0.0011359 | 37.631 | 1092.3 |  | 3752 | 69.53 | 0.35757 | 62.302 | 0.0011359 | 37.631 | 1092.3 | 1054.669
3753 | 0.35769 | 69.54 | 62.302 | 0.0011362 | 37.641 | 1092.3 |  | 3753 | 69.54 | 0.35769 | 62.302 | 0.0011362 | 37.641 | 1092.3 | 1054.659
3754 | 0.35782 | 69.55 | 62.302 | 0.0011366 | 37.651 | 1092.3 |  | 3754 | 69.55 | 0.35782 | 62.302 | 0.0011366 | 37.651 | 1092.3 | 1054.649
3755 | 0.35794 | 69.56 | 62.302 | 0.001137 | 37.661 | 1092.3 |  | 3755 | 69.56 | 0.35794 | 62.302 | 0.001137 | 37.661 | 1092.3 | 1054.639
3756 | 0.35806 | 69.57 | 62.302 | 0.0011373 | 37.671 | 1092.3 |  | 3756 | 69.57 | 0.35806 | 62.302 | 0.0011373 | 37.671 | 1092.3 | 1054.629
3757 | 0.35818 | 69.58 | 62.302 | 0.0011377 | 37.681 | 1092.3 |  | 3757 | 69.58 | 0.35818 | 62.302 | 0.0011377 | 37.681 | 1092.3 | 1054.619
3758 | 0.35831 | 69.59 | 62.302 | 0.0011381 | 37.691 | 1092.3 |  | 3758 | 69.59 | 0.35831 | 62.302 | 0.0011381 | 37.691 | 1092.3 | 1054.609
3759 | 0.35843 | 69.6 | 62.302 | 0.0011385 | 37.701 | 1092.3 |  | 3759 | 69.6 | 0.35843 | 62.302 | 0.0011385 | 37.701 | 1092.3 | 1054.599
3760 | 0.35855 | 69.61 | 62.301 | 0.0011388 | 37.711 | 1092.3 |  | 3760 | 69.61 | 0.35855 | 62.301 | 0.0011388 | 37.711 | 1092.3 | 1054.589
3761 | 0.35867 | 69.62 | 62.301 | 0.0011392 | 37.721 | 1092.3 |  | 3761 | 69.62 | 0.35867 | 62.301 | 0.0011392 | 37.721 | 1092.3 | 1054.579
3762 | 0.3588 | 69.63 | 62.301 | 0.0011396 | 37.731 | 1092.3 |  | 3762 | 69.63 | 0.3588 | 62.301 | 0.0011396 | 37.731 | 1092.3 | 1054.569
3763 | 0.35892 | 69.64 | 62.301 | 0.0011399 | 37.741 | 1092.3 |  | 3763 | 69.64 | 0.35892 | 62.301 | 0.0011399 | 37.741 | 1092.3 | 1054.559
3764 | 0.35904 | 69.65 | 62.301 | 0.0011403 | 37.751 | 1092.3 |  | 3764 | 69.65 | 0.35904 | 62.301 | 0.0011403 | 37.751 | 1092.3 | 1054.549
3765 | 0.35916 | 69.66 | 62.301 | 0.0011407 | 37.761 | 1092.4 |  | 3765 | 69.66 | 0.35916 | 62.301 | 0.0011407 | 37.761 | 1092.4 | 1054.639
3766 | 0.35929 | 69.67 | 62.301 | 0.001141 | 37.771 | 1092.4 |  | 3766 | 69.67 | 0.35929 | 62.301 | 0.001141 | 37.771 | 1092.4 | 1054.629
3767 | 0.35941 | 69.68 | 62.301 | 0.0011414 | 37.781 | 1092.4 |  | 3767 | 69.68 | 0.35941 | 62.301 | 0.0011414 | 37.781 | 1092.4 | 1054.619
3768 | 0.35953 | 69.69 | 62.301 | 0.0011418 | 37.791 | 1092.4 |  | 3768 | 69.69 | 0.35953 | 62.301 | 0.0011418 | 37.791 | 1092.4 | 1054.609
3769 | 0.35966 | 69.7 | 62.301 | 0.0011421 | 37.801 | 1092.4 |  | 3769 | 69.7 | 0.35966 | 62.301 | 0.0011421 | 37.801 | 1092.4 | 1054.599
3770 | 0.35978 | 69.71 | 62.301 | 0.0011425 | 37.811 | 1092.4 |  | 3770 | 69.71 | 0.35978 | 62.301 | 0.0011425 | 37.811 | 1092.4 | 1054.589
3771 | 0.3599 | 69.72 | 62.301 | 0.0011429 | 37.821 | 1092.4 |  | 3771 | 69.72 | 0.3599 | 62.301 | 0.0011429 | 37.821 | 1092.4 | 1054.579
3772 | 0.36002 | 69.73 | 62.301 | 0.0011432 | 37.831 | 1092.4 |  | 3772 | 69.73 | 0.36002 | 62.301 | 0.0011432 | 37.831 | 1092.4 | 1054.569
3773 | 0.36015 | 69.74 | 62.3 | 0.0011436 | 37.841 | 1092.4 |  | 3773 | 69.74 | 0.36015 | 62.3 | 0.0011436 | 37.841 | 1092.4 | 1054.559
3774 | 0.36027 | 69.75 | 62.3 | 0.001144 | 37.851 | 1092.4 |  | 3774 | 69.75 | 0.36027 | 62.3 | 0.001144 | 37.851 | 1092.4 | 1054.549
3775 | 0.36039 | 69.76 | 62.3 | 0.0011444 | 37.861 | 1092.4 |  | 3775 | 69.76 | 0.36039 | 62.3 | 0.0011444 | 37.861 | 1092.4 | 1054.539
3776 | 0.36052 | 69.77 | 62.3 | 0.0011447 | 37.871 | 1092.4 |  | 3776 | 69.77 | 0.36052 | 62.3 | 0.0011447 | 37.871 | 1092.4 | 1054.529
3777 | 0.36064 | 69.78 | 62.3 | 0.0011451 | 37.881 | 1092.4 |  | 3777 | 69.78 | 0.36064 | 62.3 | 0.0011451 | 37.881 | 1092.4 | 1054.519
3778 | 0.36076 | 69.79 | 62.3 | 0.0011455 | 37.891 | 1092.4 |  | 3778 | 69.79 | 0.36076 | 62.3 | 0.0011455 | 37.891 | 1092.4 | 1054.509
3779 | 0.36089 | 69.8 | 62.3 | 0.0011458 | 37.901 | 1092.4 |  | 3779 | 69.8 | 0.36089 | 62.3 | 0.0011458 | 37.901 | 1092.4 | 1054.499
3780 | 0.36101 | 69.81 | 62.3 | 0.0011462 | 37.911 | 1092.4 |  | 3780 | 69.81 | 0.36101 | 62.3 | 0.0011462 | 37.911 | 1092.4 | 1054.489
3781 | 0.36113 | 69.82 | 62.3 | 0.0011466 | 37.921 | 1092.4 |  | 3781 | 69.82 | 0.36113 | 62.3 | 0.0011466 | 37.921 | 1092.4 | 1054.479
3782 | 0.36126 | 69.83 | 62.3 | 0.0011469 | 37.931 | 1092.4 |  | 3782 | 69.83 | 0.36126 | 62.3 | 0.0011469 | 37.931 | 1092.4 | 1054.469
3783 | 0.36138 | 69.84 | 62.3 | 0.0011473 | 37.941 | 1092.4 |  | 3783 | 69.84 | 0.36138 | 62.3 | 0.0011473 | 37.941 | 1092.4 | 1054.459
3784 | 0.3615 | 69.85 | 62.3 | 0.0011477 | 37.951 | 1092.4 |  | 3784 | 69.85 | 0.3615 | 62.3 | 0.0011477 | 37.951 | 1092.4 | 1054.449
3785 | 0.36163 | 69.86 | 62.3 | 0.0011481 | 37.961 | 1092.4 |  | 3785 | 69.86 | 0.36163 | 62.3 | 0.0011481 | 37.961 | 1092.4 | 1054.439
3786 | 0.36175 | 69.87 | 62.299 | 0.0011484 | 37.971 | 1092.4 |  | 3786 | 69.87 | 0.36175 | 62.299 | 0.0011484 | 37.971 | 1092.4 | 1054.429
3787 | 0.36187 | 69.88 | 62.299 | 0.0011488 | 37.981 | 1092.4 |  | 3787 | 69.88 | 0.36187 | 62.299 | 0.0011488 | 37.981 | 1092.4 | 1054.419
3788 | 0.362 | 69.89 | 62.299 | 0.0011492 | 37.991 | 1092.5 |  | 3788 | 69.89 | 0.362 | 62.299 | 0.0011492 | 37.991 | 1092.5 | 1054.509
3789 | 0.36212 | 69.9 | 62.299 | 0.0011495 | 38.001 | 1092.5 |  | 3789 | 69.9 | 0.36212 | 62.299 | 0.0011495 | 38.001 | 1092.5 | 1054.499
3790 | 0.36224 | 69.91 | 62.299 | 0.0011499 | 38.011 | 1092.5 |  | 3790 | 69.91 | 0.36224 | 62.299 | 0.0011499 | 38.011 | 1092.5 | 1054.489
3791 | 0.36237 | 69.92 | 62.299 | 0.0011503 | 38.021 | 1092.5 |  | 3791 | 69.92 | 0.36237 | 62.299 | 0.0011503 | 38.021 | 1092.5 | 1054.479
3792 | 0.36249 | 69.93 | 62.299 | 0.0011506 | 38.031 | 1092.5 |  | 3792 | 69.93 | 0.36249 | 62.299 | 0.0011506 | 38.031 | 1092.5 | 1054.469
3793 | 0.36261 | 69.94 | 62.299 | 0.001151 | 38.041 | 1092.5 |  | 3793 | 69.94 | 0.36261 | 62.299 | 0.001151 | 38.041 | 1092.5 | 1054.459
3794 | 0.36274 | 69.95 | 62.299 | 0.0011514 | 38.051 | 1092.5 |  | 3794 | 69.95 | 0.36274 | 62.299 | 0.0011514 | 38.051 | 1092.5 | 1054.449
3795 | 0.36286 | 69.96 | 62.299 | 0.0011518 | 38.061 | 1092.5 |  | 3795 | 69.96 | 0.36286 | 62.299 | 0.0011518 | 38.061 | 1092.5 | 1054.439
3796 | 0.36299 | 69.97 | 62.299 | 0.0011521 | 38.071 | 1092.5 |  | 3796 | 69.97 | 0.36299 | 62.299 | 0.0011521 | 38.071 | 1092.5 | 1054.429
3797 | 0.36311 | 69.98 | 62.299 | 0.0011525 | 38.081 | 1092.5 |  | 3797 | 69.98 | 0.36311 | 62.299 | 0.0011525 | 38.081 | 1092.5 | 1054.419
3798 | 0.36323 | 69.99 | 62.299 | 0.0011529 | 38.091 | 1092.5 |  | 3798 | 69.99 | 0.36323 | 62.299 | 0.0011529 | 38.091 | 1092.5 | 1054.409
3799 | 0.36336 | 70 | 62.298 | 0.0011533 | 38.101 | 1092.5 |  | 3799 | 70 | 0.36336 | 62.298 | 0.0011533 | 38.101 | 1092.5 | 1054.399
3800 | 0.36348 | 70.01 | 62.298 | 0.0011536 | 38.111 | 1092.5 |  | 3800 | 70.01 | 0.36348 | 62.298 | 0.0011536 | 38.111 | 1092.5 | 1054.389
3801 | 0.36361 | 70.02 | 62.298 | 0.001154 | 38.121 | 1092.5 |  | 3801 | 70.02 | 0.36361 | 62.298 | 0.001154 | 38.121 | 1092.5 | 1054.379
3802 | 0.36373 | 70.03 | 62.298 | 0.0011544 | 38.131 | 1092.5 |  | 3802 | 70.03 | 0.36373 | 62.298 | 0.0011544 | 38.131 | 1092.5 | 1054.369
3803 | 0.36385 | 70.04 | 62.298 | 0.0011547 | 38.141 | 1092.5 |  | 3803 | 70.04 | 0.36385 | 62.298 | 0.0011547 | 38.141 | 1092.5 | 1054.359
3804 | 0.36398 | 70.05 | 62.298 | 0.0011551 | 38.151 | 1092.5 |  | 3804 | 70.05 | 0.36398 | 62.298 | 0.0011551 | 38.151 | 1092.5 | 1054.349
3805 | 0.3641 | 70.06 | 62.298 | 0.0011555 | 38.161 | 1092.5 |  | 3805 | 70.06 | 0.3641 | 62.298 | 0.0011555 | 38.161 | 1092.5 | 1054.339
3806 | 0.36423 | 70.07 | 62.298 | 0.0011559 | 38.171 | 1092.5 |  | 3806 | 70.07 | 0.36423 | 62.298 | 0.0011559 | 38.171 | 1092.5 | 1054.329
3807 | 0.36435 | 70.08 | 62.298 | 0.0011562 | 38.181 | 1092.5 |  | 3807 | 70.08 | 0.36435 | 62.298 | 0.0011562 | 38.181 | 1092.5 | 1054.319
3808 | 0.36448 | 70.09 | 62.298 | 0.0011566 | 38.191 | 1092.5 |  | 3808 | 70.09 | 0.36448 | 62.298 | 0.0011566 | 38.191 | 1092.5 | 1054.309
3809 | 0.3646 | 70.1 | 62.298 | 0.001157 | 38.201 | 1092.5 |  | 3809 | 70.1 | 0.3646 | 62.298 | 0.001157 | 38.201 | 1092.5 | 1054.299
3810 | 0.36472 | 70.11 | 62.298 | 0.0011574 | 38.211 | 1092.5 |  | 3810 | 70.11 | 0.36472 | 62.298 | 0.0011574 | 38.211 | 1092.5 | 1054.289
3811 | 0.36485 | 70.12 | 62.298 | 0.0011577 | 38.221 | 1092.6 |  | 3811 | 70.12 | 0.36485 | 62.298 | 0.0011577 | 38.221 | 1092.6 | 1054.379
3812 | 0.36497 | 70.13 | 62.298 | 0.0011581 | 38.231 | 1092.6 |  | 3812 | 70.13 | 0.36497 | 62.298 | 0.0011581 | 38.231 | 1092.6 | 1054.369
3813 | 0.3651 | 70.14 | 62.297 | 0.0011585 | 38.241 | 1092.6 |  | 3813 | 70.14 | 0.3651 | 62.297 | 0.0011585 | 38.241 | 1092.6 | 1054.359
3814 | 0.36522 | 70.15 | 62.297 | 0.0011588 | 38.251 | 1092.6 |  | 3814 | 70.15 | 0.36522 | 62.297 | 0.0011588 | 38.251 | 1092.6 | 1054.349
3815 | 0.36535 | 70.16 | 62.297 | 0.0011592 | 38.261 | 1092.6 |  | 3815 | 70.16 | 0.36535 | 62.297 | 0.0011592 | 38.261 | 1092.6 | 1054.339
3816 | 0.36547 | 70.17 | 62.297 | 0.0011596 | 38.271 | 1092.6 |  | 3816 | 70.17 | 0.36547 | 62.297 | 0.0011596 | 38.271 | 1092.6 | 1054.329
3817 | 0.3656 | 70.18 | 62.297 | 0.00116 | 38.281 | 1092.6 |  | 3817 | 70.18 | 0.3656 | 62.297 | 0.00116 | 38.281 | 1092.6 | 1054.319
3818 | 0.36572 | 70.19 | 62.297 | 0.0011603 | 38.291 | 1092.6 |  | 3818 | 70.19 | 0.36572 | 62.297 | 0.0011603 | 38.291 | 1092.6 | 1054.309
3819 | 0.36584 | 70.2 | 62.297 | 0.0011607 | 38.301 | 1092.6 |  | 3819 | 70.2 | 0.36584 | 62.297 | 0.0011607 | 38.301 | 1092.6 | 1054.299
3820 | 0.36597 | 70.21 | 62.297 | 0.0011611 | 38.311 | 1092.6 |  | 3820 | 70.21 | 0.36597 | 62.297 | 0.0011611 | 38.311 | 1092.6 | 1054.289
3821 | 0.36609 | 70.22 | 62.297 | 0.0011615 | 38.321 | 1092.6 |  | 3821 | 70.22 | 0.36609 | 62.297 | 0.0011615 | 38.321 | 1092.6 | 1054.279
3822 | 0.36622 | 70.23 | 62.297 | 0.0011618 | 38.331 | 1092.6 |  | 3822 | 70.23 | 0.36622 | 62.297 | 0.0011618 | 38.331 | 1092.6 | 1054.269
3823 | 0.36634 | 70.24 | 62.297 | 0.0011622 | 38.341 | 1092.6 |  | 3823 | 70.24 | 0.36634 | 62.297 | 0.0011622 | 38.341 | 1092.6 | 1054.259
3824 | 0.36647 | 70.25 | 62.297 | 0.0011626 | 38.351 | 1092.6 |  | 3824 | 70.25 | 0.36647 | 62.297 | 0.0011626 | 38.351 | 1092.6 | 1054.249
3825 | 0.36659 | 70.26 | 62.297 | 0.001163 | 38.361 | 1092.6 |  | 3825 | 70.26 | 0.36659 | 62.297 | 0.001163 | 38.361 | 1092.6 | 1054.239
3826 | 0.36672 | 70.27 | 62.296 | 0.0011633 | 38.371 | 1092.6 |  | 3826 | 70.27 | 0.36672 | 62.296 | 0.0011633 | 38.371 | 1092.6 | 1054.229
3827 | 0.36684 | 70.28 | 62.296 | 0.0011637 | 38.381 | 1092.6 |  | 3827 | 70.28 | 0.36684 | 62.296 | 0.0011637 | 38.381 | 1092.6 | 1054.219
3828 | 0.36697 | 70.29 | 62.296 | 0.0011641 | 38.391 | 1092.6 |  | 3828 | 70.29 | 0.36697 | 62.296 | 0.0011641 | 38.391 | 1092.6 | 1054.209
3829 | 0.36709 | 70.3 | 62.296 | 0.0011645 | 38.401 | 1092.6 |  | 3829 | 70.3 | 0.36709 | 62.296 | 0.0011645 | 38.401 | 1092.6 | 1054.199
3830 | 0.36722 | 70.31 | 62.296 | 0.0011648 | 38.411 | 1092.6 |  | 3830 | 70.31 | 0.36722 | 62.296 | 0.0011648 | 38.411 | 1092.6 | 1054.189
3831 | 0.36734 | 70.32 | 62.296 | 0.0011652 | 38.421 | 1092.6 |  | 3831 | 70.32 | 0.36734 | 62.296 | 0.0011652 | 38.421 | 1092.6 | 1054.179
3832 | 0.36747 | 70.33 | 62.296 | 0.0011656 | 38.431 | 1092.6 |  | 3832 | 70.33 | 0.36747 | 62.296 | 0.0011656 | 38.431 | 1092.6 | 1054.169
3833 | 0.36759 | 70.34 | 62.296 | 0.001166 | 38.441 | 1092.6 |  | 3833 | 70.34 | 0.36759 | 62.296 | 0.001166 | 38.441 | 1092.6 | 1054.159
3834 | 0.36772 | 70.35 | 62.296 | 0.0011663 | 38.451 | 1092.7 |  | 3834 | 70.35 | 0.36772 | 62.296 | 0.0011663 | 38.451 | 1092.7 | 1054.249
3835 | 0.36785 | 70.36 | 62.296 | 0.0011667 | 38.461 | 1092.7 |  | 3835 | 70.36 | 0.36785 | 62.296 | 0.0011667 | 38.461 | 1092.7 | 1054.239
3836 | 0.36797 | 70.37 | 62.296 | 0.0011671 | 38.471 | 1092.7 |  | 3836 | 70.37 | 0.36797 | 62.296 | 0.0011671 | 38.471 | 1092.7 | 1054.229
3837 | 0.3681 | 70.38 | 62.296 | 0.0011675 | 38.481 | 1092.7 |  | 3837 | 70.38 | 0.3681 | 62.296 | 0.0011675 | 38.481 | 1092.7 | 1054.219
3838 | 0.36822 | 70.39 | 62.296 | 0.0011678 | 38.491 | 1092.7 |  | 3838 | 70.39 | 0.36822 | 62.296 | 0.0011678 | 38.491 | 1092.7 | 1054.209
3839 | 0.36835 | 70.4 | 62.295 | 0.0011682 | 38.501 | 1092.7 |  | 3839 | 70.4 | 0.36835 | 62.295 | 0.0011682 | 38.501 | 1092.7 | 1054.199
3840 | 0.36847 | 70.41 | 62.295 | 0.0011686 | 38.511 | 1092.7 |  | 3840 | 70.41 | 0.36847 | 62.295 | 0.0011686 | 38.511 | 1092.7 | 1054.189
3841 | 0.3686 | 70.42 | 62.295 | 0.001169 | 38.521 | 1092.7 |  | 3841 | 70.42 | 0.3686 | 62.295 | 0.001169 | 38.521 | 1092.7 | 1054.179
3842 | 0.36872 | 70.43 | 62.295 | 0.0011693 | 38.531 | 1092.7 |  | 3842 | 70.43 | 0.36872 | 62.295 | 0.0011693 | 38.531 | 1092.7 | 1054.169
3843 | 0.36885 | 70.44 | 62.295 | 0.0011697 | 38.541 | 1092.7 |  | 3843 | 70.44 | 0.36885 | 62.295 | 0.0011697 | 38.541 | 1092.7 | 1054.159
3844 | 0.36897 | 70.45 | 62.295 | 0.0011701 | 38.551 | 1092.7 |  | 3844 | 70.45 | 0.36897 | 62.295 | 0.0011701 | 38.551 | 1092.7 | 1054.149
3845 | 0.3691 | 70.46 | 62.295 | 0.0011705 | 38.561 | 1092.7 |  | 3845 | 70.46 | 0.3691 | 62.295 | 0.0011705 | 38.561 | 1092.7 | 1054.139
3846 | 0.36923 | 70.47 | 62.295 | 0.0011709 | 38.571 | 1092.7 |  | 3846 | 70.47 | 0.36923 | 62.295 | 0.0011709 | 38.571 | 1092.7 | 1054.129
3847 | 0.36935 | 70.48 | 62.295 | 0.0011712 | 38.581 | 1092.7 |  | 3847 | 70.48 | 0.36935 | 62.295 | 0.0011712 | 38.581 | 1092.7 | 1054.119
3848 | 0.36948 | 70.49 | 62.295 | 0.0011716 | 38.591 | 1092.7 |  | 3848 | 70.49 | 0.36948 | 62.295 | 0.0011716 | 38.591 | 1092.7 | 1054.109
3849 | 0.3696 | 70.5 | 62.295 | 0.001172 | 38.601 | 1092.7 |  | 3849 | 70.5 | 0.3696 | 62.295 | 0.001172 | 38.601 | 1092.7 | 1054.099
3850 | 0.36973 | 70.51 | 62.295 | 0.0011724 | 38.611 | 1092.7 |  | 3850 | 70.51 | 0.36973 | 62.295 | 0.0011724 | 38.611 | 1092.7 | 1054.089
3851 | 0.36986 | 70.52 | 62.295 | 0.0011727 | 38.621 | 1092.7 |  | 3851 | 70.52 | 0.36986 | 62.295 | 0.0011727 | 38.621 | 1092.7 | 1054.079
3852 | 0.36998 | 70.53 | 62.294 | 0.0011731 | 38.631 | 1092.7 |  | 3852 | 70.53 | 0.36998 | 62.294 | 0.0011731 | 38.631 | 1092.7 | 1054.069
3853 | 0.37011 | 70.54 | 62.294 | 0.0011735 | 38.641 | 1092.7 |  | 3853 | 70.54 | 0.37011 | 62.294 | 0.0011735 | 38.641 | 1092.7 | 1054.059
3854 | 0.37023 | 70.55 | 62.294 | 0.0011739 | 38.651 | 1092.7 |  | 3854 | 70.55 | 0.37023 | 62.294 | 0.0011739 | 38.651 | 1092.7 | 1054.049
3855 | 0.37036 | 70.56 | 62.294 | 0.0011743 | 38.661 | 1092.7 |  | 3855 | 70.56 | 0.37036 | 62.294 | 0.0011743 | 38.661 | 1092.7 | 1054.039
3856 | 0.37049 | 70.57 | 62.294 | 0.0011746 | 38.671 | 1092.7 |  | 3856 | 70.57 | 0.37049 | 62.294 | 0.0011746 | 38.671 | 1092.7 | 1054.029
3857 | 0.37061 | 70.58 | 62.294 | 0.001175 | 38.681 | 1092.8 |  | 3857 | 70.58 | 0.37061 | 62.294 | 0.001175 | 38.681 | 1092.8 | 1054.119
3858 | 0.37074 | 70.59 | 62.294 | 0.0011754 | 38.691 | 1092.8 |  | 3858 | 70.59 | 0.37074 | 62.294 | 0.0011754 | 38.691 | 1092.8 | 1054.109
3859 | 0.37086 | 70.6 | 62.294 | 0.0011758 | 38.701 | 1092.8 |  | 3859 | 70.6 | 0.37086 | 62.294 | 0.0011758 | 38.701 | 1092.8 | 1054.099
3860 | 0.37099 | 70.61 | 62.294 | 0.0011761 | 38.711 | 1092.8 |  | 3860 | 70.61 | 0.37099 | 62.294 | 0.0011761 | 38.711 | 1092.8 | 1054.089
3861 | 0.37112 | 70.62 | 62.294 | 0.0011765 | 38.721 | 1092.8 |  | 3861 | 70.62 | 0.37112 | 62.294 | 0.0011765 | 38.721 | 1092.8 | 1054.079
3862 | 0.37124 | 70.63 | 62.294 | 0.0011769 | 38.731 | 1092.8 |  | 3862 | 70.63 | 0.37124 | 62.294 | 0.0011769 | 38.731 | 1092.8 | 1054.069
3863 | 0.37137 | 70.64 | 62.294 | 0.0011773 | 38.741 | 1092.8 |  | 3863 | 70.64 | 0.37137 | 62.294 | 0.0011773 | 38.741 | 1092.8 | 1054.059
3864 | 0.3715 | 70.65 | 62.294 | 0.0011777 | 38.751 | 1092.8 |  | 3864 | 70.65 | 0.3715 | 62.294 | 0.0011777 | 38.751 | 1092.8 | 1054.049
3865 | 0.37162 | 70.66 | 62.293 | 0.001178 | 38.761 | 1092.8 |  | 3865 | 70.66 | 0.37162 | 62.293 | 0.001178 | 38.761 | 1092.8 | 1054.039
3866 | 0.37175 | 70.67 | 62.293 | 0.0011784 | 38.771 | 1092.8 |  | 3866 | 70.67 | 0.37175 | 62.293 | 0.0011784 | 38.771 | 1092.8 | 1054.029
3867 | 0.37187 | 70.68 | 62.293 | 0.0011788 | 38.781 | 1092.8 |  | 3867 | 70.68 | 0.37187 | 62.293 | 0.0011788 | 38.781 | 1092.8 | 1054.019
3868 | 0.372 | 70.69 | 62.293 | 0.0011792 | 38.791 | 1092.8 |  | 3868 | 70.69 | 0.372 | 62.293 | 0.0011792 | 38.791 | 1092.8 | 1054.009
3869 | 0.37213 | 70.7 | 62.293 | 0.0011796 | 38.801 | 1092.8 |  | 3869 | 70.7 | 0.37213 | 62.293 | 0.0011796 | 38.801 | 1092.8 | 1053.999
3870 | 0.37225 | 70.71 | 62.293 | 0.0011799 | 38.811 | 1092.8 |  | 3870 | 70.71 | 0.37225 | 62.293 | 0.0011799 | 38.811 | 1092.8 | 1053.989
3871 | 0.37238 | 70.72 | 62.293 | 0.0011803 | 38.821 | 1092.8 |  | 3871 | 70.72 | 0.37238 | 62.293 | 0.0011803 | 38.821 | 1092.8 | 1053.979
3872 | 0.37251 | 70.73 | 62.293 | 0.0011807 | 38.831 | 1092.8 |  | 3872 | 70.73 | 0.37251 | 62.293 | 0.0011807 | 38.831 | 1092.8 | 1053.969
3873 | 0.37263 | 70.74 | 62.293 | 0.0011811 | 38.841 | 1092.8 |  | 3873 | 70.74 | 0.37263 | 62.293 | 0.0011811 | 38.841 | 1092.8 | 1053.959
3874 | 0.37276 | 70.75 | 62.293 | 0.0011815 | 38.851 | 1092.8 |  | 3874 | 70.75 | 0.37276 | 62.293 | 0.0011815 | 38.851 | 1092.8 | 1053.949
3875 | 0.37289 | 70.76 | 62.293 | 0.0011818 | 38.861 | 1092.8 |  | 3875 | 70.76 | 0.37289 | 62.293 | 0.0011818 | 38.861 | 1092.8 | 1053.939
3876 | 0.37301 | 70.77 | 62.293 | 0.0011822 | 38.871 | 1092.8 |  | 3876 | 70.77 | 0.37301 | 62.293 | 0.0011822 | 38.871 | 1092.8 | 1053.929
3877 | 0.37314 | 70.78 | 62.293 | 0.0011826 | 38.881 | 1092.8 |  | 3877 | 70.78 | 0.37314 | 62.293 | 0.0011826 | 38.881 | 1092.8 | 1053.919
3878 | 0.37327 | 70.79 | 62.292 | 0.001183 | 38.891 | 1092.8 |  | 3878 | 70.79 | 0.37327 | 62.292 | 0.001183 | 38.891 | 1092.8 | 1053.909
3879 | 0.3734 | 70.8 | 62.292 | 0.0011834 | 38.901 | 1092.8 |  | 3879 | 70.8 | 0.3734 | 62.292 | 0.0011834 | 38.901 | 1092.8 | 1053.899
3880 | 0.37352 | 70.81 | 62.292 | 0.0011837 | 38.911 | 1092.8 |  | 3880 | 70.81 | 0.37352 | 62.292 | 0.0011837 | 38.911 | 1092.8 | 1053.889
3881 | 0.37365 | 70.82 | 62.292 | 0.0011841 | 38.921 | 1092.9 |  | 3881 | 70.82 | 0.37365 | 62.292 | 0.0011841 | 38.921 | 1092.9 | 1053.979
3882 | 0.37378 | 70.83 | 62.292 | 0.0011845 | 38.931 | 1092.9 |  | 3882 | 70.83 | 0.37378 | 62.292 | 0.0011845 | 38.931 | 1092.9 | 1053.969
3883 | 0.3739 | 70.84 | 62.292 | 0.0011849 | 38.941 | 1092.9 |  | 3883 | 70.84 | 0.3739 | 62.292 | 0.0011849 | 38.941 | 1092.9 | 1053.959
3884 | 0.37403 | 70.85 | 62.292 | 0.0011853 | 38.951 | 1092.9 |  | 3884 | 70.85 | 0.37403 | 62.292 | 0.0011853 | 38.951 | 1092.9 | 1053.949
3885 | 0.37416 | 70.86 | 62.292 | 0.0011856 | 38.961 | 1092.9 |  | 3885 | 70.86 | 0.37416 | 62.292 | 0.0011856 | 38.961 | 1092.9 | 1053.939
3886 | 0.37429 | 70.87 | 62.292 | 0.001186 | 38.971 | 1092.9 |  | 3886 | 70.87 | 0.37429 | 62.292 | 0.001186 | 38.971 | 1092.9 | 1053.929
3887 | 0.37441 | 70.88 | 62.292 | 0.0011864 | 38.981 | 1092.9 |  | 3887 | 70.88 | 0.37441 | 62.292 | 0.0011864 | 38.981 | 1092.9 | 1053.919
3888 | 0.37454 | 70.89 | 62.292 | 0.0011868 | 38.991 | 1092.9 |  | 3888 | 70.89 | 0.37454 | 62.292 | 0.0011868 | 38.991 | 1092.9 | 1053.909
3889 | 0.37467 | 70.9 | 62.292 | 0.0011872 | 39.001 | 1092.9 |  | 3889 | 70.9 | 0.37467 | 62.292 | 0.0011872 | 39.001 | 1092.9 | 1053.899
3890 | 0.37479 | 70.91 | 62.292 | 0.0011875 | 39.011 | 1092.9 |  | 3890 | 70.91 | 0.37479 | 62.292 | 0.0011875 | 39.011 | 1092.9 | 1053.889
3891 | 0.37492 | 70.92 | 62.291 | 0.0011879 | 39.021 | 1092.9 |  | 3891 | 70.92 | 0.37492 | 62.291 | 0.0011879 | 39.021 | 1092.9 | 1053.879
3892 | 0.37505 | 70.93 | 62.291 | 0.0011883 | 39.031 | 1092.9 |  | 3892 | 70.93 | 0.37505 | 62.291 | 0.0011883 | 39.031 | 1092.9 | 1053.869
3893 | 0.37518 | 70.94 | 62.291 | 0.0011887 | 39.041 | 1092.9 |  | 3893 | 70.94 | 0.37518 | 62.291 | 0.0011887 | 39.041 | 1092.9 | 1053.859
3894 | 0.3753 | 70.95 | 62.291 | 0.0011891 | 39.051 | 1092.9 |  | 3894 | 70.95 | 0.3753 | 62.291 | 0.0011891 | 39.051 | 1092.9 | 1053.849
3895 | 0.37543 | 70.96 | 62.291 | 0.0011895 | 39.061 | 1092.9 |  | 3895 | 70.96 | 0.37543 | 62.291 | 0.0011895 | 39.061 | 1092.9 | 1053.839
3896 | 0.37556 | 70.97 | 62.291 | 0.0011898 | 39.071 | 1092.9 |  | 3896 | 70.97 | 0.37556 | 62.291 | 0.0011898 | 39.071 | 1092.9 | 1053.829
3897 | 0.37569 | 70.98 | 62.291 | 0.0011902 | 39.081 | 1092.9 |  | 3897 | 70.98 | 0.37569 | 62.291 | 0.0011902 | 39.081 | 1092.9 | 1053.819
3898 | 0.37581 | 70.99 | 62.291 | 0.0011906 | 39.091 | 1092.9 |  | 3898 | 70.99 | 0.37581 | 62.291 | 0.0011906 | 39.091 | 1092.9 | 1053.809
3899 | 0.37594 | 71 | 62.291 | 0.001191 | 39.101 | 1092.9 |  | 3899 | 71 | 0.37594 | 62.291 | 0.001191 | 39.101 | 1092.9 | 1053.799
3900 | 0.37607 | 71.01 | 62.291 | 0.0011914 | 39.111 | 1092.9 |  | 3900 | 71.01 | 0.37607 | 62.291 | 0.0011914 | 39.111 | 1092.9 | 1053.789
3901 | 0.3762 | 71.02 | 62.291 | 0.0011917 | 39.121 | 1092.9 |  | 3901 | 71.02 | 0.3762 | 62.291 | 0.0011917 | 39.121 | 1092.9 | 1053.779
3902 | 0.37633 | 71.03 | 62.291 | 0.0011921 | 39.131 | 1092.9 |  | 3902 | 71.03 | 0.37633 | 62.291 | 0.0011921 | 39.131 | 1092.9 | 1053.769
3903 | 0.37645 | 71.04 | 62.291 | 0.0011925 | 39.141 | 1092.9 |  | 3903 | 71.04 | 0.37645 | 62.291 | 0.0011925 | 39.141 | 1092.9 | 1053.759
3904 | 0.37658 | 71.05 | 62.29 | 0.0011929 | 39.151 | 1093 |  | 3904 | 71.05 | 0.37658 | 62.29 | 0.0011929 | 39.151 | 1093 | 1053.849
3905 | 0.37671 | 71.06 | 62.29 | 0.0011933 | 39.161 | 1093 |  | 3905 | 71.06 | 0.37671 | 62.29 | 0.0011933 | 39.161 | 1093 | 1053.839
3906 | 0.37684 | 71.07 | 62.29 | 0.0011937 | 39.171 | 1093 |  | 3906 | 71.07 | 0.37684 | 62.29 | 0.0011937 | 39.171 | 1093 | 1053.829
3907 | 0.37697 | 71.08 | 62.29 | 0.001194 | 39.181 | 1093 |  | 3907 | 71.08 | 0.37697 | 62.29 | 0.001194 | 39.181 | 1093 | 1053.819
3908 | 0.37709 | 71.09 | 62.29 | 0.0011944 | 39.191 | 1093 |  | 3908 | 71.09 | 0.37709 | 62.29 | 0.0011944 | 39.191 | 1093 | 1053.809
3909 | 0.37722 | 71.1 | 62.29 | 0.0011948 | 39.201 | 1093 |  | 3909 | 71.1 | 0.37722 | 62.29 | 0.0011948 | 39.201 | 1093 | 1053.799
3910 | 0.37735 | 71.11 | 62.29 | 0.0011952 | 39.211 | 1093 |  | 3910 | 71.11 | 0.37735 | 62.29 | 0.0011952 | 39.211 | 1093 | 1053.789
3911 | 0.37748 | 71.12 | 62.29 | 0.0011956 | 39.221 | 1093 |  | 3911 | 71.12 | 0.37748 | 62.29 | 0.0011956 | 39.221 | 1093 | 1053.779
3912 | 0.37761 | 71.13 | 62.29 | 0.001196 | 39.231 | 1093 |  | 3912 | 71.13 | 0.37761 | 62.29 | 0.001196 | 39.231 | 1093 | 1053.769
3913 | 0.37773 | 71.14 | 62.29 | 0.0011963 | 39.241 | 1093 |  | 3913 | 71.14 | 0.37773 | 62.29 | 0.0011963 | 39.241 | 1093 | 1053.759
3914 | 0.37786 | 71.15 | 62.29 | 0.0011967 | 39.251 | 1093 |  | 3914 | 71.15 | 0.37786 | 62.29 | 0.0011967 | 39.251 | 1093 | 1053.749
3915 | 0.37799 | 71.16 | 62.29 | 0.0011971 | 39.261 | 1093 |  | 3915 | 71.16 | 0.37799 | 62.29 | 0.0011971 | 39.261 | 1093 | 1053.739
3916 | 0.37812 | 71.17 | 62.29 | 0.0011975 | 39.271 | 1093 |  | 3916 | 71.17 | 0.37812 | 62.29 | 0.0011975 | 39.271 | 1093 | 1053.729
3917 | 0.37825 | 71.18 | 62.289 | 0.0011979 | 39.281 | 1093 |  | 3917 | 71.18 | 0.37825 | 62.289 | 0.0011979 | 39.281 | 1093 | 1053.719
3918 | 0.37838 | 71.19 | 62.289 | 0.0011983 | 39.291 | 1093 |  | 3918 | 71.19 | 0.37838 | 62.289 | 0.0011983 | 39.291 | 1093 | 1053.709
3919 | 0.3785 | 71.2 | 62.289 | 0.0011987 | 39.301 | 1093 |  | 3919 | 71.2 | 0.3785 | 62.289 | 0.0011987 | 39.301 | 1093 | 1053.699
3920 | 0.37863 | 71.21 | 62.289 | 0.001199 | 39.311 | 1093 |  | 3920 | 71.21 | 0.37863 | 62.289 | 0.001199 | 39.311 | 1093 | 1053.689
3921 | 0.37876 | 71.22 | 62.289 | 0.0011994 | 39.321 | 1093 |  | 3921 | 71.22 | 0.37876 | 62.289 | 0.0011994 | 39.321 | 1093 | 1053.679
3922 | 0.37889 | 71.23 | 62.289 | 0.0011998 | 39.331 | 1093 |  | 3922 | 71.23 | 0.37889 | 62.289 | 0.0011998 | 39.331 | 1093 | 1053.669
3923 | 0.37902 | 71.24 | 62.289 | 0.0012002 | 39.341 | 1093 |  | 3923 | 71.24 | 0.37902 | 62.289 | 0.0012002 | 39.341 | 1093 | 1053.659
3924 | 0.37915 | 71.25 | 62.289 | 0.0012006 | 39.351 | 1093 |  | 3924 | 71.25 | 0.37915 | 62.289 | 0.0012006 | 39.351 | 1093 | 1053.649
3925 | 0.37928 | 71.26 | 62.289 | 0.001201 | 39.361 | 1093 |  | 3925 | 71.26 | 0.37928 | 62.289 | 0.001201 | 39.361 | 1093 | 1053.639
3926 | 0.3794 | 71.27 | 62.289 | 0.0012013 | 39.371 | 1093 |  | 3926 | 71.27 | 0.3794 | 62.289 | 0.0012013 | 39.371 | 1093 | 1053.629
3927 | 0.37953 | 71.28 | 62.289 | 0.0012017 | 39.381 | 1093.1 |  | 3927 | 71.28 | 0.37953 | 62.289 | 0.0012017 | 39.381 | 1093.1 | 1053.719
3928 | 0.37966 | 71.29 | 62.289 | 0.0012021 | 39.391 | 1093.1 |  | 3928 | 71.29 | 0.37966 | 62.289 | 0.0012021 | 39.391 | 1093.1 | 1053.709
3929 | 0.37979 | 71.3 | 62.289 | 0.0012025 | 39.401 | 1093.1 |  | 3929 | 71.3 | 0.37979 | 62.289 | 0.0012025 | 39.401 | 1093.1 | 1053.699
3930 | 0.37992 | 71.31 | 62.288 | 0.0012029 | 39.411 | 1093.1 |  | 3930 | 71.31 | 0.37992 | 62.288 | 0.0012029 | 39.411 | 1093.1 | 1053.689
3931 | 0.38005 | 71.32 | 62.288 | 0.0012033 | 39.421 | 1093.1 |  | 3931 | 71.32 | 0.38005 | 62.288 | 0.0012033 | 39.421 | 1093.1 | 1053.679
3932 | 0.38018 | 71.33 | 62.288 | 0.0012037 | 39.431 | 1093.1 |  | 3932 | 71.33 | 0.38018 | 62.288 | 0.0012037 | 39.431 | 1093.1 | 1053.669
3933 | 0.38031 | 71.34 | 62.288 | 0.0012041 | 39.441 | 1093.1 |  | 3933 | 71.34 | 0.38031 | 62.288 | 0.0012041 | 39.441 | 1093.1 | 1053.659
3934 | 0.38044 | 71.35 | 62.288 | 0.0012044 | 39.451 | 1093.1 |  | 3934 | 71.35 | 0.38044 | 62.288 | 0.0012044 | 39.451 | 1093.1 | 1053.649
3935 | 0.38057 | 71.36 | 62.288 | 0.0012048 | 39.461 | 1093.1 |  | 3935 | 71.36 | 0.38057 | 62.288 | 0.0012048 | 39.461 | 1093.1 | 1053.639
3936 | 0.38069 | 71.37 | 62.288 | 0.0012052 | 39.471 | 1093.1 |  | 3936 | 71.37 | 0.38069 | 62.288 | 0.0012052 | 39.471 | 1093.1 | 1053.629
3937 | 0.38082 | 71.38 | 62.288 | 0.0012056 | 39.481 | 1093.1 |  | 3937 | 71.38 | 0.38082 | 62.288 | 0.0012056 | 39.481 | 1093.1 | 1053.619
3938 | 0.38095 | 71.39 | 62.288 | 0.001206 | 39.491 | 1093.1 |  | 3938 | 71.39 | 0.38095 | 62.288 | 0.001206 | 39.491 | 1093.1 | 1053.609
3939 | 0.38108 | 71.4 | 62.288 | 0.0012064 | 39.501 | 1093.1 |  | 3939 | 71.4 | 0.38108 | 62.288 | 0.0012064 | 39.501 | 1093.1 | 1053.599
3940 | 0.38121 | 71.41 | 62.288 | 0.0012068 | 39.511 | 1093.1 |  | 3940 | 71.41 | 0.38121 | 62.288 | 0.0012068 | 39.511 | 1093.1 | 1053.589
3941 | 0.38134 | 71.42 | 62.288 | 0.0012071 | 39.521 | 1093.1 |  | 3941 | 71.42 | 0.38134 | 62.288 | 0.0012071 | 39.521 | 1093.1 | 1053.579
3942 | 0.38147 | 71.43 | 62.287 | 0.0012075 | 39.531 | 1093.1 |  | 3942 | 71.43 | 0.38147 | 62.287 | 0.0012075 | 39.531 | 1093.1 | 1053.569
3943 | 0.3816 | 71.44 | 62.287 | 0.0012079 | 39.541 | 1093.1 |  | 3943 | 71.44 | 0.3816 | 62.287 | 0.0012079 | 39.541 | 1093.1 | 1053.559
3944 | 0.38173 | 71.45 | 62.287 | 0.0012083 | 39.551 | 1093.1 |  | 3944 | 71.45 | 0.38173 | 62.287 | 0.0012083 | 39.551 | 1093.1 | 1053.549
3945 | 0.38186 | 71.46 | 62.287 | 0.0012087 | 39.561 | 1093.1 |  | 3945 | 71.46 | 0.38186 | 62.287 | 0.0012087 | 39.561 | 1093.1 | 1053.539
3946 | 0.38199 | 71.47 | 62.287 | 0.0012091 | 39.571 | 1093.1 |  | 3946 | 71.47 | 0.38199 | 62.287 | 0.0012091 | 39.571 | 1093.1 | 1053.529
3947 | 0.38212 | 71.48 | 62.287 | 0.0012095 | 39.581 | 1093.1 |  | 3947 | 71.48 | 0.38212 | 62.287 | 0.0012095 | 39.581 | 1093.1 | 1053.519
3948 | 0.38225 | 71.49 | 62.287 | 0.0012099 | 39.591 | 1093.1 |  | 3948 | 71.49 | 0.38225 | 62.287 | 0.0012099 | 39.591 | 1093.1 | 1053.509
3949 | 0.38238 | 71.5 | 62.287 | 0.0012102 | 39.601 | 1093.1 |  | 3949 | 71.5 | 0.38238 | 62.287 | 0.0012102 | 39.601 | 1093.1 | 1053.499
3950 | 0.38251 | 71.51 | 62.287 | 0.0012106 | 39.611 | 1093.2 |  | 3950 | 71.51 | 0.38251 | 62.287 | 0.0012106 | 39.611 | 1093.2 | 1053.589
3951 | 0.38264 | 71.52 | 62.287 | 0.001211 | 39.621 | 1093.2 |  | 3951 | 71.52 | 0.38264 | 62.287 | 0.001211 | 39.621 | 1093.2 | 1053.579
3952 | 0.38277 | 71.53 | 62.287 | 0.0012114 | 39.631 | 1093.2 |  | 3952 | 71.53 | 0.38277 | 62.287 | 0.0012114 | 39.631 | 1093.2 | 1053.569
3953 | 0.3829 | 71.54 | 62.287 | 0.0012118 | 39.641 | 1093.2 |  | 3953 | 71.54 | 0.3829 | 62.287 | 0.0012118 | 39.641 | 1093.2 | 1053.559
3954 | 0.38303 | 71.55 | 62.287 | 0.0012122 | 39.651 | 1093.2 |  | 3954 | 71.55 | 0.38303 | 62.287 | 0.0012122 | 39.651 | 1093.2 | 1053.549
3955 | 0.38315 | 71.56 | 62.286 | 0.0012126 | 39.661 | 1093.2 |  | 3955 | 71.56 | 0.38315 | 62.286 | 0.0012126 | 39.661 | 1093.2 | 1053.539
3956 | 0.38328 | 71.57 | 62.286 | 0.001213 | 39.671 | 1093.2 |  | 3956 | 71.57 | 0.38328 | 62.286 | 0.001213 | 39.671 | 1093.2 | 1053.529
3957 | 0.38341 | 71.58 | 62.286 | 0.0012133 | 39.681 | 1093.2 |  | 3957 | 71.58 | 0.38341 | 62.286 | 0.0012133 | 39.681 | 1093.2 | 1053.519
3958 | 0.38354 | 71.59 | 62.286 | 0.0012137 | 39.691 | 1093.2 |  | 3958 | 71.59 | 0.38354 | 62.286 | 0.0012137 | 39.691 | 1093.2 | 1053.509
3959 | 0.38367 | 71.6 | 62.286 | 0.0012141 | 39.701 | 1093.2 |  | 3959 | 71.6 | 0.38367 | 62.286 | 0.0012141 | 39.701 | 1093.2 | 1053.499
3960 | 0.3838 | 71.61 | 62.286 | 0.0012145 | 39.711 | 1093.2 |  | 3960 | 71.61 | 0.3838 | 62.286 | 0.0012145 | 39.711 | 1093.2 | 1053.489
3961 | 0.38393 | 71.62 | 62.286 | 0.0012149 | 39.721 | 1093.2 |  | 3961 | 71.62 | 0.38393 | 62.286 | 0.0012149 | 39.721 | 1093.2 | 1053.479
3962 | 0.38406 | 71.63 | 62.286 | 0.0012153 | 39.731 | 1093.2 |  | 3962 | 71.63 | 0.38406 | 62.286 | 0.0012153 | 39.731 | 1093.2 | 1053.469
3963 | 0.3842 | 71.64 | 62.286 | 0.0012157 | 39.741 | 1093.2 |  | 3963 | 71.64 | 0.3842 | 62.286 | 0.0012157 | 39.741 | 1093.2 | 1053.459
3964 | 0.38433 | 71.65 | 62.286 | 0.0012161 | 39.751 | 1093.2 |  | 3964 | 71.65 | 0.38433 | 62.286 | 0.0012161 | 39.751 | 1093.2 | 1053.449
3965 | 0.38446 | 71.66 | 62.286 | 0.0012165 | 39.761 | 1093.2 |  | 3965 | 71.66 | 0.38446 | 62.286 | 0.0012165 | 39.761 | 1093.2 | 1053.439
3966 | 0.38459 | 71.67 | 62.286 | 0.0012169 | 39.771 | 1093.2 |  | 3966 | 71.67 | 0.38459 | 62.286 | 0.0012169 | 39.771 | 1093.2 | 1053.429
3967 | 0.38472 | 71.68 | 62.286 | 0.0012172 | 39.781 | 1093.2 |  | 3967 | 71.68 | 0.38472 | 62.286 | 0.0012172 | 39.781 | 1093.2 | 1053.419
3968 | 0.38485 | 71.69 | 62.285 | 0.0012176 | 39.791 | 1093.2 |  | 3968 | 71.69 | 0.38485 | 62.285 | 0.0012176 | 39.791 | 1093.2 | 1053.409
3969 | 0.38498 | 71.7 | 62.285 | 0.001218 | 39.801 | 1093.2 |  | 3969 | 71.7 | 0.38498 | 62.285 | 0.001218 | 39.801 | 1093.2 | 1053.399
3970 | 0.38511 | 71.71 | 62.285 | 0.0012184 | 39.811 | 1093.2 |  | 3970 | 71.71 | 0.38511 | 62.285 | 0.0012184 | 39.811 | 1093.2 | 1053.389
3971 | 0.38524 | 71.72 | 62.285 | 0.0012188 | 39.821 | 1093.2 |  | 3971 | 71.72 | 0.38524 | 62.285 | 0.0012188 | 39.821 | 1093.2 | 1053.379
3972 | 0.38537 | 71.73 | 62.285 | 0.0012192 | 39.831 | 1093.2 |  | 3972 | 71.73 | 0.38537 | 62.285 | 0.0012192 | 39.831 | 1093.2 | 1053.369
3973 | 0.3855 | 71.74 | 62.285 | 0.0012196 | 39.841 | 1093.3 |  | 3973 | 71.74 | 0.3855 | 62.285 | 0.0012196 | 39.841 | 1093.3 | 1053.459
3974 | 0.38563 | 71.75 | 62.285 | 0.00122 | 39.851 | 1093.3 |  | 3974 | 71.75 | 0.38563 | 62.285 | 0.00122 | 39.851 | 1093.3 | 1053.449
3975 | 0.38576 | 71.76 | 62.285 | 0.0012204 | 39.861 | 1093.3 |  | 3975 | 71.76 | 0.38576 | 62.285 | 0.0012204 | 39.861 | 1093.3 | 1053.439
3976 | 0.38589 | 71.77 | 62.285 | 0.0012208 | 39.871 | 1093.3 |  | 3976 | 71.77 | 0.38589 | 62.285 | 0.0012208 | 39.871 | 1093.3 | 1053.429
3977 | 0.38602 | 71.78 | 62.285 | 0.0012211 | 39.881 | 1093.3 |  | 3977 | 71.78 | 0.38602 | 62.285 | 0.0012211 | 39.881 | 1093.3 | 1053.419
3978 | 0.38615 | 71.79 | 62.285 | 0.0012215 | 39.891 | 1093.3 |  | 3978 | 71.79 | 0.38615 | 62.285 | 0.0012215 | 39.891 | 1093.3 | 1053.409
3979 | 0.38628 | 71.8 | 62.285 | 0.0012219 | 39.901 | 1093.3 |  | 3979 | 71.8 | 0.38628 | 62.285 | 0.0012219 | 39.901 | 1093.3 | 1053.399
3980 | 0.38641 | 71.81 | 62.285 | 0.0012223 | 39.911 | 1093.3 |  | 3980 | 71.81 | 0.38641 | 62.285 | 0.0012223 | 39.911 | 1093.3 | 1053.389
3981 | 0.38654 | 71.82 | 62.284 | 0.0012227 | 39.921 | 1093.3 |  | 3981 | 71.82 | 0.38654 | 62.284 | 0.0012227 | 39.921 | 1093.3 | 1053.379
3982 | 0.38668 | 71.83 | 62.284 | 0.0012231 | 39.931 | 1093.3 |  | 3982 | 71.83 | 0.38668 | 62.284 | 0.0012231 | 39.931 | 1093.3 | 1053.369
3983 | 0.38681 | 71.84 | 62.284 | 0.0012235 | 39.941 | 1093.3 |  | 3983 | 71.84 | 0.38681 | 62.284 | 0.0012235 | 39.941 | 1093.3 | 1053.359
3984 | 0.38694 | 71.85 | 62.284 | 0.0012239 | 39.951 | 1093.3 |  | 3984 | 71.85 | 0.38694 | 62.284 | 0.0012239 | 39.951 | 1093.3 | 1053.349
3985 | 0.38707 | 71.86 | 62.284 | 0.0012243 | 39.961 | 1093.3 |  | 3985 | 71.86 | 0.38707 | 62.284 | 0.0012243 | 39.961 | 1093.3 | 1053.339
3986 | 0.3872 | 71.87 | 62.284 | 0.0012247 | 39.971 | 1093.3 |  | 3986 | 71.87 | 0.3872 | 62.284 | 0.0012247 | 39.971 | 1093.3 | 1053.329
3987 | 0.38733 | 71.88 | 62.284 | 0.0012251 | 39.981 | 1093.3 |  | 3987 | 71.88 | 0.38733 | 62.284 | 0.0012251 | 39.981 | 1093.3 | 1053.319
3988 | 0.38746 | 71.89 | 62.284 | 0.0012255 | 39.991 | 1093.3 |  | 3988 | 71.89 | 0.38746 | 62.284 | 0.0012255 | 39.991 | 1093.3 | 1053.309
3989 | 0.38759 | 71.9 | 62.284 | 0.0012258 | 40.001 | 1093.3 |  | 3989 | 71.9 | 0.38759 | 62.284 | 0.0012258 | 40.001 | 1093.3 | 1053.299
3990 | 0.38772 | 71.91 | 62.284 | 0.0012262 | 40.011 | 1093.3 |  | 3990 | 71.91 | 0.38772 | 62.284 | 0.0012262 | 40.011 | 1093.3 | 1053.289
3991 | 0.38786 | 71.92 | 62.284 | 0.0012266 | 40.021 | 1093.3 |  | 3991 | 71.92 | 0.38786 | 62.284 | 0.0012266 | 40.021 | 1093.3 | 1053.279
3992 | 0.38799 | 71.93 | 62.284 | 0.001227 | 40.031 | 1093.3 |  | 3992 | 71.93 | 0.38799 | 62.284 | 0.001227 | 40.031 | 1093.3 | 1053.269
3993 | 0.38812 | 71.94 | 62.283 | 0.0012274 | 40.041 | 1093.3 |  | 3993 | 71.94 | 0.38812 | 62.283 | 0.0012274 | 40.041 | 1093.3 | 1053.259
3994 | 0.38825 | 71.95 | 62.283 | 0.0012278 | 40.051 | 1093.3 |  | 3994 | 71.95 | 0.38825 | 62.283 | 0.0012278 | 40.051 | 1093.3 | 1053.249
3995 | 0.38838 | 71.96 | 62.283 | 0.0012282 | 40.061 | 1093.3 |  | 3995 | 71.96 | 0.38838 | 62.283 | 0.0012282 | 40.061 | 1093.3 | 1053.239
3996 | 0.38851 | 71.97 | 62.283 | 0.0012286 | 40.071 | 1093.4 |  | 3996 | 71.97 | 0.38851 | 62.283 | 0.0012286 | 40.071 | 1093.4 | 1053.329
3997 | 0.38864 | 71.98 | 62.283 | 0.001229 | 40.081 | 1093.4 |  | 3997 | 71.98 | 0.38864 | 62.283 | 0.001229 | 40.081 | 1093.4 | 1053.319
3998 | 0.38877 | 71.99 | 62.283 | 0.0012294 | 40.091 | 1093.4 |  | 3998 | 71.99 | 0.38877 | 62.283 | 0.0012294 | 40.091 | 1093.4 | 1053.309
3999 | 0.38891 | 72 | 62.283 | 0.0012298 | 40.101 | 1093.4 |  | 3999 | 72 | 0.38891 | 62.283 | 0.0012298 | 40.101 | 1093.4 | 1053.299
4000 | 0.38904 | 72.01 | 62.283 | 0.0012302 | 40.111 | 1093.4 |  | 4000 | 72.01 | 0.38904 | 62.283 | 0.0012302 | 40.111 | 1093.4 | 1053.289
4001 | 0.38917 | 72.02 | 62.283 | 0.0012306 | 40.121 | 1093.4 |  | 4001 | 72.02 | 0.38917 | 62.283 | 0.0012306 | 40.121 | 1093.4 | 1053.279
4002 | 0.3893 | 72.03 | 62.283 | 0.001231 | 40.131 | 1093.4 |  | 4002 | 72.03 | 0.3893 | 62.283 | 0.001231 | 40.131 | 1093.4 | 1053.269
4003 | 0.38943 | 72.04 | 62.283 | 0.0012313 | 40.141 | 1093.4 |  | 4003 | 72.04 | 0.38943 | 62.283 | 0.0012313 | 40.141 | 1093.4 | 1053.259
4004 | 0.38956 | 72.05 | 62.283 | 0.0012317 | 40.151 | 1093.4 |  | 4004 | 72.05 | 0.38956 | 62.283 | 0.0012317 | 40.151 | 1093.4 | 1053.249
4005 | 0.3897 | 72.06 | 62.283 | 0.0012321 | 40.161 | 1093.4 |  | 4005 | 72.06 | 0.3897 | 62.283 | 0.0012321 | 40.161 | 1093.4 | 1053.239
4006 | 0.38983 | 72.07 | 62.282 | 0.0012325 | 40.171 | 1093.4 |  | 4006 | 72.07 | 0.38983 | 62.282 | 0.0012325 | 40.171 | 1093.4 | 1053.229
4007 | 0.38996 | 72.08 | 62.282 | 0.0012329 | 40.181 | 1093.4 |  | 4007 | 72.08 | 0.38996 | 62.282 | 0.0012329 | 40.181 | 1093.4 | 1053.219
4008 | 0.39009 | 72.09 | 62.282 | 0.0012333 | 40.19 | 1093.4 |  | 4008 | 72.09 | 0.39009 | 62.282 | 0.0012333 | 40.19 | 1093.4 | 1053.21
4009 | 0.39022 | 72.1 | 62.282 | 0.0012337 | 40.2 | 1093.4 |  | 4009 | 72.1 | 0.39022 | 62.282 | 0.0012337 | 40.2 | 1093.4 | 1053.2
4010 | 0.39036 | 72.11 | 62.282 | 0.0012341 | 40.21 | 1093.4 |  | 4010 | 72.11 | 0.39036 | 62.282 | 0.0012341 | 40.21 | 1093.4 | 1053.19
4011 | 0.39049 | 72.12 | 62.282 | 0.0012345 | 40.22 | 1093.4 |  | 4011 | 72.12 | 0.39049 | 62.282 | 0.0012345 | 40.22 | 1093.4 | 1053.18
4012 | 0.39062 | 72.13 | 62.282 | 0.0012349 | 40.23 | 1093.4 |  | 4012 | 72.13 | 0.39062 | 62.282 | 0.0012349 | 40.23 | 1093.4 | 1053.17
4013 | 0.39075 | 72.14 | 62.282 | 0.0012353 | 40.24 | 1093.4 |  | 4013 | 72.14 | 0.39075 | 62.282 | 0.0012353 | 40.24 | 1093.4 | 1053.16
4014 | 0.39088 | 72.15 | 62.282 | 0.0012357 | 40.25 | 1093.4 |  | 4014 | 72.15 | 0.39088 | 62.282 | 0.0012357 | 40.25 | 1093.4 | 1053.15
4015 | 0.39102 | 72.16 | 62.282 | 0.0012361 | 40.26 | 1093.4 |  | 4015 | 72.16 | 0.39102 | 62.282 | 0.0012361 | 40.26 | 1093.4 | 1053.14
4016 | 0.39115 | 72.17 | 62.282 | 0.0012365 | 40.27 | 1093.4 |  | 4016 | 72.17 | 0.39115 | 62.282 | 0.0012365 | 40.27 | 1093.4 | 1053.13
4017 | 0.39128 | 72.18 | 62.282 | 0.0012369 | 40.28 | 1093.4 |  | 4017 | 72.18 | 0.39128 | 62.282 | 0.0012369 | 40.28 | 1093.4 | 1053.12
4018 | 0.39141 | 72.19 | 62.281 | 0.0012373 | 40.29 | 1093.4 |  | 4018 | 72.19 | 0.39141 | 62.281 | 0.0012373 | 40.29 | 1093.4 | 1053.11
4019 | 0.39155 | 72.2 | 62.281 | 0.0012377 | 40.3 | 1093.5 |  | 4019 | 72.2 | 0.39155 | 62.281 | 0.0012377 | 40.3 | 1093.5 | 1053.2
4020 | 0.39168 | 72.21 | 62.281 | 0.0012381 | 40.31 | 1093.5 |  | 4020 | 72.21 | 0.39168 | 62.281 | 0.0012381 | 40.31 | 1093.5 | 1053.19
4021 | 0.39181 | 72.22 | 62.281 | 0.0012385 | 40.32 | 1093.5 |  | 4021 | 72.22 | 0.39181 | 62.281 | 0.0012385 | 40.32 | 1093.5 | 1053.18
4022 | 0.39194 | 72.23 | 62.281 | 0.0012388 | 40.33 | 1093.5 |  | 4022 | 72.23 | 0.39194 | 62.281 | 0.0012388 | 40.33 | 1093.5 | 1053.17
4023 | 0.39208 | 72.24 | 62.281 | 0.0012392 | 40.34 | 1093.5 |  | 4023 | 72.24 | 0.39208 | 62.281 | 0.0012392 | 40.34 | 1093.5 | 1053.16
4024 | 0.39221 | 72.25 | 62.281 | 0.0012396 | 40.35 | 1093.5 |  | 4024 | 72.25 | 0.39221 | 62.281 | 0.0012396 | 40.35 | 1093.5 | 1053.15
4025 | 0.39234 | 72.26 | 62.281 | 0.00124 | 40.36 | 1093.5 |  | 4025 | 72.26 | 0.39234 | 62.281 | 0.00124 | 40.36 | 1093.5 | 1053.14
4026 | 0.39247 | 72.27 | 62.281 | 0.0012404 | 40.37 | 1093.5 |  | 4026 | 72.27 | 0.39247 | 62.281 | 0.0012404 | 40.37 | 1093.5 | 1053.13
4027 | 0.39261 | 72.28 | 62.281 | 0.0012408 | 40.38 | 1093.5 |  | 4027 | 72.28 | 0.39261 | 62.281 | 0.0012408 | 40.38 | 1093.5 | 1053.12
4028 | 0.39274 | 72.29 | 62.281 | 0.0012412 | 40.39 | 1093.5 |  | 4028 | 72.29 | 0.39274 | 62.281 | 0.0012412 | 40.39 | 1093.5 | 1053.11
4029 | 0.39287 | 72.3 | 62.281 | 0.0012416 | 40.4 | 1093.5 |  | 4029 | 72.3 | 0.39287 | 62.281 | 0.0012416 | 40.4 | 1093.5 | 1053.1
4030 | 0.393 | 72.31 | 62.281 | 0.001242 | 40.41 | 1093.5 |  | 4030 | 72.31 | 0.393 | 62.281 | 0.001242 | 40.41 | 1093.5 | 1053.09
4031 | 0.39314 | 72.32 | 62.28 | 0.0012424 | 40.42 | 1093.5 |  | 4031 | 72.32 | 0.39314 | 62.28 | 0.0012424 | 40.42 | 1093.5 | 1053.08
4032 | 0.39327 | 72.33 | 62.28 | 0.0012428 | 40.43 | 1093.5 |  | 4032 | 72.33 | 0.39327 | 62.28 | 0.0012428 | 40.43 | 1093.5 | 1053.07
4033 | 0.3934 | 72.34 | 62.28 | 0.0012432 | 40.44 | 1093.5 |  | 4033 | 72.34 | 0.3934 | 62.28 | 0.0012432 | 40.44 | 1093.5 | 1053.06
4034 | 0.39354 | 72.35 | 62.28 | 0.0012436 | 40.45 | 1093.5 |  | 4034 | 72.35 | 0.39354 | 62.28 | 0.0012436 | 40.45 | 1093.5 | 1053.05
4035 | 0.39367 | 72.36 | 62.28 | 0.001244 | 40.46 | 1093.5 |  | 4035 | 72.36 | 0.39367 | 62.28 | 0.001244 | 40.46 | 1093.5 | 1053.04
4036 | 0.3938 | 72.37 | 62.28 | 0.0012444 | 40.47 | 1093.5 |  | 4036 | 72.37 | 0.3938 | 62.28 | 0.0012444 | 40.47 | 1093.5 | 1053.03
4037 | 0.39393 | 72.38 | 62.28 | 0.0012448 | 40.48 | 1093.5 |  | 4037 | 72.38 | 0.39393 | 62.28 | 0.0012448 | 40.48 | 1093.5 | 1053.02
4038 | 0.39407 | 72.39 | 62.28 | 0.0012452 | 40.49 | 1093.5 |  | 4038 | 72.39 | 0.39407 | 62.28 | 0.0012452 | 40.49 | 1093.5 | 1053.01
4039 | 0.3942 | 72.4 | 62.28 | 0.0012456 | 40.5 | 1093.5 |  | 4039 | 72.4 | 0.3942 | 62.28 | 0.0012456 | 40.5 | 1093.5 | 1053
4040 | 0.39433 | 72.41 | 62.28 | 0.001246 | 40.51 | 1093.5 |  | 4040 | 72.41 | 0.39433 | 62.28 | 0.001246 | 40.51 | 1093.5 | 1052.99
4041 | 0.39447 | 72.42 | 62.28 | 0.0012464 | 40.52 | 1093.5 |  | 4041 | 72.42 | 0.39447 | 62.28 | 0.0012464 | 40.52 | 1093.5 | 1052.98
4042 | 0.3946 | 72.43 | 62.28 | 0.0012468 | 40.53 | 1093.6 |  | 4042 | 72.43 | 0.3946 | 62.28 | 0.0012468 | 40.53 | 1093.6 | 1053.07
4043 | 0.39473 | 72.44 | 62.279 | 0.0012472 | 40.54 | 1093.6 |  | 4043 | 72.44 | 0.39473 | 62.279 | 0.0012472 | 40.54 | 1093.6 | 1053.06
4044 | 0.39487 | 72.45 | 62.279 | 0.0012476 | 40.55 | 1093.6 |  | 4044 | 72.45 | 0.39487 | 62.279 | 0.0012476 | 40.55 | 1093.6 | 1053.05
4045 | 0.395 | 72.46 | 62.279 | 0.001248 | 40.56 | 1093.6 |  | 4045 | 72.46 | 0.395 | 62.279 | 0.001248 | 40.56 | 1093.6 | 1053.04
4046 | 0.39513 | 72.47 | 62.279 | 0.0012484 | 40.57 | 1093.6 |  | 4046 | 72.47 | 0.39513 | 62.279 | 0.0012484 | 40.57 | 1093.6 | 1053.03
4047 | 0.39527 | 72.48 | 62.279 | 0.0012488 | 40.58 | 1093.6 |  | 4047 | 72.48 | 0.39527 | 62.279 | 0.0012488 | 40.58 | 1093.6 | 1053.02
4048 | 0.3954 | 72.49 | 62.279 | 0.0012492 | 40.59 | 1093.6 |  | 4048 | 72.49 | 0.3954 | 62.279 | 0.0012492 | 40.59 | 1093.6 | 1053.01
4049 | 0.39553 | 72.5 | 62.279 | 0.0012496 | 40.6 | 1093.6 |  | 4049 | 72.5 | 0.39553 | 62.279 | 0.0012496 | 40.6 | 1093.6 | 1053
4050 | 0.39567 | 72.51 | 62.279 | 0.00125 | 40.61 | 1093.6 |  | 4050 | 72.51 | 0.39567 | 62.279 | 0.00125 | 40.61 | 1093.6 | 1052.99
4051 | 0.3958 | 72.52 | 62.279 | 0.0012504 | 40.62 | 1093.6 |  | 4051 | 72.52 | 0.3958 | 62.279 | 0.0012504 | 40.62 | 1093.6 | 1052.98
4052 | 0.39593 | 72.53 | 62.279 | 0.0012508 | 40.63 | 1093.6 |  | 4052 | 72.53 | 0.39593 | 62.279 | 0.0012508 | 40.63 | 1093.6 | 1052.97
4053 | 0.39607 | 72.54 | 62.279 | 0.0012512 | 40.64 | 1093.6 |  | 4053 | 72.54 | 0.39607 | 62.279 | 0.0012512 | 40.64 | 1093.6 | 1052.96
4054 | 0.3962 | 72.55 | 62.279 | 0.0012516 | 40.65 | 1093.6 |  | 4054 | 72.55 | 0.3962 | 62.279 | 0.0012516 | 40.65 | 1093.6 | 1052.95
4055 | 0.39634 | 72.56 | 62.279 | 0.001252 | 40.66 | 1093.6 |  | 4055 | 72.56 | 0.39634 | 62.279 | 0.001252 | 40.66 | 1093.6 | 1052.94
4056 | 0.39647 | 72.57 | 62.278 | 0.0012524 | 40.67 | 1093.6 |  | 4056 | 72.57 | 0.39647 | 62.278 | 0.0012524 | 40.67 | 1093.6 | 1052.93
4057 | 0.3966 | 72.58 | 62.278 | 0.0012528 | 40.68 | 1093.6 |  | 4057 | 72.58 | 0.3966 | 62.278 | 0.0012528 | 40.68 | 1093.6 | 1052.92
4058 | 0.39674 | 72.59 | 62.278 | 0.0012532 | 40.69 | 1093.6 |  | 4058 | 72.59 | 0.39674 | 62.278 | 0.0012532 | 40.69 | 1093.6 | 1052.91
4059 | 0.39687 | 72.6 | 62.278 | 0.0012536 | 40.7 | 1093.6 |  | 4059 | 72.6 | 0.39687 | 62.278 | 0.0012536 | 40.7 | 1093.6 | 1052.9
4060 | 0.397 | 72.61 | 62.278 | 0.001254 | 40.71 | 1093.6 |  | 4060 | 72.61 | 0.397 | 62.278 | 0.001254 | 40.71 | 1093.6 | 1052.89
4061 | 0.39714 | 72.62 | 62.278 | 0.0012544 | 40.72 | 1093.6 |  | 4061 | 72.62 | 0.39714 | 62.278 | 0.0012544 | 40.72 | 1093.6 | 1052.88
4062 | 0.39727 | 72.63 | 62.278 | 0.0012548 | 40.73 | 1093.6 |  | 4062 | 72.63 | 0.39727 | 62.278 | 0.0012548 | 40.73 | 1093.6 | 1052.87
4063 | 0.39741 | 72.64 | 62.278 | 0.0012552 | 40.74 | 1093.6 |  | 4063 | 72.64 | 0.39741 | 62.278 | 0.0012552 | 40.74 | 1093.6 | 1052.86
4064 | 0.39754 | 72.65 | 62.278 | 0.0012556 | 40.75 | 1093.6 |  | 4064 | 72.65 | 0.39754 | 62.278 | 0.0012556 | 40.75 | 1093.6 | 1052.85
4065 | 0.39768 | 72.66 | 62.278 | 0.001256 | 40.76 | 1093.7 |  | 4065 | 72.66 | 0.39768 | 62.278 | 0.001256 | 40.76 | 1093.7 | 1052.94
4066 | 0.39781 | 72.67 | 62.278 | 0.0012564 | 40.77 | 1093.7 |  | 4066 | 72.67 | 0.39781 | 62.278 | 0.0012564 | 40.77 | 1093.7 | 1052.93
4067 | 0.39794 | 72.68 | 62.278 | 0.0012568 | 40.78 | 1093.7 |  | 4067 | 72.68 | 0.39794 | 62.278 | 0.0012568 | 40.78 | 1093.7 | 1052.92
4068 | 0.39808 | 72.69 | 62.277 | 0.0012572 | 40.79 | 1093.7 |  | 4068 | 72.69 | 0.39808 | 62.277 | 0.0012572 | 40.79 | 1093.7 | 1052.91
4069 | 0.39821 | 72.7 | 62.277 | 0.0012576 | 40.8 | 1093.7 |  | 4069 | 72.7 | 0.39821 | 62.277 | 0.0012576 | 40.8 | 1093.7 | 1052.9
4070 | 0.39835 | 72.71 | 62.277 | 0.001258 | 40.81 | 1093.7 |  | 4070 | 72.71 | 0.39835 | 62.277 | 0.001258 | 40.81 | 1093.7 | 1052.89
4071 | 0.39848 | 72.72 | 62.277 | 0.0012584 | 40.82 | 1093.7 |  | 4071 | 72.72 | 0.39848 | 62.277 | 0.0012584 | 40.82 | 1093.7 | 1052.88
4072 | 0.39862 | 72.73 | 62.277 | 0.0012588 | 40.83 | 1093.7 |  | 4072 | 72.73 | 0.39862 | 62.277 | 0.0012588 | 40.83 | 1093.7 | 1052.87
4073 | 0.39875 | 72.74 | 62.277 | 0.0012592 | 40.84 | 1093.7 |  | 4073 | 72.74 | 0.39875 | 62.277 | 0.0012592 | 40.84 | 1093.7 | 1052.86
4074 | 0.39888 | 72.75 | 62.277 | 0.0012596 | 40.85 | 1093.7 |  | 4074 | 72.75 | 0.39888 | 62.277 | 0.0012596 | 40.85 | 1093.7 | 1052.85
4075 | 0.39902 | 72.76 | 62.277 | 0.00126 | 40.86 | 1093.7 |  | 4075 | 72.76 | 0.39902 | 62.277 | 0.00126 | 40.86 | 1093.7 | 1052.84
4076 | 0.39915 | 72.77 | 62.277 | 0.0012604 | 40.87 | 1093.7 |  | 4076 | 72.77 | 0.39915 | 62.277 | 0.0012604 | 40.87 | 1093.7 | 1052.83
4077 | 0.39929 | 72.78 | 62.277 | 0.0012608 | 40.88 | 1093.7 |  | 4077 | 72.78 | 0.39929 | 62.277 | 0.0012608 | 40.88 | 1093.7 | 1052.82
4078 | 0.39942 | 72.79 | 62.277 | 0.0012612 | 40.89 | 1093.7 |  | 4078 | 72.79 | 0.39942 | 62.277 | 0.0012612 | 40.89 | 1093.7 | 1052.81
4079 | 0.39956 | 72.8 | 62.277 | 0.0012616 | 40.9 | 1093.7 |  | 4079 | 72.8 | 0.39956 | 62.277 | 0.0012616 | 40.9 | 1093.7 | 1052.8
4080 | 0.39969 | 72.81 | 62.276 | 0.001262 | 40.91 | 1093.7 |  | 4080 | 72.81 | 0.39969 | 62.276 | 0.001262 | 40.91 | 1093.7 | 1052.79
4081 | 0.39983 | 72.82 | 62.276 | 0.0012624 | 40.92 | 1093.7 |  | 4081 | 72.82 | 0.39983 | 62.276 | 0.0012624 | 40.92 | 1093.7 | 1052.78
4082 | 0.39996 | 72.83 | 62.276 | 0.0012628 | 40.93 | 1093.7 |  | 4082 | 72.83 | 0.39996 | 62.276 | 0.0012628 | 40.93 | 1093.7 | 1052.77
4083 | 0.4001 | 72.84 | 62.276 | 0.0012632 | 40.94 | 1093.7 |  | 4083 | 72.84 | 0.4001 | 62.276 | 0.0012632 | 40.94 | 1093.7 | 1052.76
4084 | 0.40023 | 72.85 | 62.276 | 0.0012636 | 40.95 | 1093.7 |  | 4084 | 72.85 | 0.40023 | 62.276 | 0.0012636 | 40.95 | 1093.7 | 1052.75
4085 | 0.40037 | 72.86 | 62.276 | 0.001264 | 40.96 | 1093.7 |  | 4085 | 72.86 | 0.40037 | 62.276 | 0.001264 | 40.96 | 1093.7 | 1052.74
4086 | 0.4005 | 72.87 | 62.276 | 0.0012644 | 40.97 | 1093.7 |  | 4086 | 72.87 | 0.4005 | 62.276 | 0.0012644 | 40.97 | 1093.7 | 1052.73
4087 | 0.40064 | 72.88 | 62.276 | 0.0012648 | 40.98 | 1093.7 |  | 4087 | 72.88 | 0.40064 | 62.276 | 0.0012648 | 40.98 | 1093.7 | 1052.72
4088 | 0.40077 | 72.89 | 62.276 | 0.0012652 | 40.99 | 1093.8 |  | 4088 | 72.89 | 0.40077 | 62.276 | 0.0012652 | 40.99 | 1093.8 | 1052.81
4089 | 0.40091 | 72.9 | 62.276 | 0.0012656 | 41 | 1093.8 |  | 4089 | 72.9 | 0.40091 | 62.276 | 0.0012656 | 41 | 1093.8 | 1052.8
4090 | 0.40104 | 72.91 | 62.276 | 0.001266 | 41.01 | 1093.8 |  | 4090 | 72.91 | 0.40104 | 62.276 | 0.001266 | 41.01 | 1093.8 | 1052.79
4091 | 0.40118 | 72.92 | 62.276 | 0.0012664 | 41.02 | 1093.8 |  | 4091 | 72.92 | 0.40118 | 62.276 | 0.0012664 | 41.02 | 1093.8 | 1052.78
4092 | 0.40131 | 72.93 | 62.276 | 0.0012668 | 41.03 | 1093.8 |  | 4092 | 72.93 | 0.40131 | 62.276 | 0.0012668 | 41.03 | 1093.8 | 1052.77
4093 | 0.40145 | 72.94 | 62.275 | 0.0012672 | 41.04 | 1093.8 |  | 4093 | 72.94 | 0.40145 | 62.275 | 0.0012672 | 41.04 | 1093.8 | 1052.76
4094 | 0.40158 | 72.95 | 62.275 | 0.0012676 | 41.05 | 1093.8 |  | 4094 | 72.95 | 0.40158 | 62.275 | 0.0012676 | 41.05 | 1093.8 | 1052.75
4095 | 0.40172 | 72.96 | 62.275 | 0.001268 | 41.06 | 1093.8 |  | 4095 | 72.96 | 0.40172 | 62.275 | 0.001268 | 41.06 | 1093.8 | 1052.74
4096 | 0.40185 | 72.97 | 62.275 | 0.0012684 | 41.07 | 1093.8 |  | 4096 | 72.97 | 0.40185 | 62.275 | 0.0012684 | 41.07 | 1093.8 | 1052.73
4097 | 0.40199 | 72.98 | 62.275 | 0.0012688 | 41.08 | 1093.8 |  | 4097 | 72.98 | 0.40199 | 62.275 | 0.0012688 | 41.08 | 1093.8 | 1052.72
4098 | 0.40212 | 72.99 | 62.275 | 0.0012692 | 41.09 | 1093.8 |  | 4098 | 72.99 | 0.40212 | 62.275 | 0.0012692 | 41.09 | 1093.8 | 1052.71
4099 | 0.40226 | 73 | 62.275 | 0.0012696 | 41.1 | 1093.8 |  | 4099 | 73 | 0.40226 | 62.275 | 0.0012696 | 41.1 | 1093.8 | 1052.7
4100 | 0.40239 | 73.01 | 62.275 | 0.0012701 | 41.11 | 1093.8 |  | 4100 | 73.01 | 0.40239 | 62.275 | 0.0012701 | 41.11 | 1093.8 | 1052.69
4101 | 0.40253 | 73.02 | 62.275 | 0.0012705 | 41.12 | 1093.8 |  | 4101 | 73.02 | 0.40253 | 62.275 | 0.0012705 | 41.12 | 1093.8 | 1052.68
4102 | 0.40267 | 73.03 | 62.275 | 0.0012709 | 41.13 | 1093.8 |  | 4102 | 73.03 | 0.40267 | 62.275 | 0.0012709 | 41.13 | 1093.8 | 1052.67
4103 | 0.4028 | 73.04 | 62.275 | 0.0012713 | 41.14 | 1093.8 |  | 4103 | 73.04 | 0.4028 | 62.275 | 0.0012713 | 41.14 | 1093.8 | 1052.66
4104 | 0.40294 | 73.05 | 62.275 | 0.0012717 | 41.15 | 1093.8 |  | 4104 | 73.05 | 0.40294 | 62.275 | 0.0012717 | 41.15 | 1093.8 | 1052.65
4105 | 0.40307 | 73.06 | 62.274 | 0.0012721 | 41.16 | 1093.8 |  | 4105 | 73.06 | 0.40307 | 62.274 | 0.0012721 | 41.16 | 1093.8 | 1052.64
4106 | 0.40321 | 73.07 | 62.274 | 0.0012725 | 41.17 | 1093.8 |  | 4106 | 73.07 | 0.40321 | 62.274 | 0.0012725 | 41.17 | 1093.8 | 1052.63
4107 | 0.40334 | 73.08 | 62.274 | 0.0012729 | 41.18 | 1093.8 |  | 4107 | 73.08 | 0.40334 | 62.274 | 0.0012729 | 41.18 | 1093.8 | 1052.62
4108 | 0.40348 | 73.09 | 62.274 | 0.0012733 | 41.19 | 1093.8 |  | 4108 | 73.09 | 0.40348 | 62.274 | 0.0012733 | 41.19 | 1093.8 | 1052.61
4109 | 0.40362 | 73.1 | 62.274 | 0.0012737 | 41.2 | 1093.8 |  | 4109 | 73.1 | 0.40362 | 62.274 | 0.0012737 | 41.2 | 1093.8 | 1052.6
4110 | 0.40375 | 73.11 | 62.274 | 0.0012741 | 41.21 | 1093.8 |  | 4110 | 73.11 | 0.40375 | 62.274 | 0.0012741 | 41.21 | 1093.8 | 1052.59
4111 | 0.40389 | 73.12 | 62.274 | 0.0012745 | 41.22 | 1093.9 |  | 4111 | 73.12 | 0.40389 | 62.274 | 0.0012745 | 41.22 | 1093.9 | 1052.68
4112 | 0.40402 | 73.13 | 62.274 | 0.0012749 | 41.23 | 1093.9 |  | 4112 | 73.13 | 0.40402 | 62.274 | 0.0012749 | 41.23 | 1093.9 | 1052.67
4113 | 0.40416 | 73.14 | 62.274 | 0.0012753 | 41.24 | 1093.9 |  | 4113 | 73.14 | 0.40416 | 62.274 | 0.0012753 | 41.24 | 1093.9 | 1052.66
4114 | 0.4043 | 73.15 | 62.274 | 0.0012757 | 41.25 | 1093.9 |  | 4114 | 73.15 | 0.4043 | 62.274 | 0.0012757 | 41.25 | 1093.9 | 1052.65
4115 | 0.40443 | 73.16 | 62.274 | 0.0012761 | 41.26 | 1093.9 |  | 4115 | 73.16 | 0.40443 | 62.274 | 0.0012761 | 41.26 | 1093.9 | 1052.64
4116 | 0.40457 | 73.17 | 62.274 | 0.0012765 | 41.27 | 1093.9 |  | 4116 | 73.17 | 0.40457 | 62.274 | 0.0012765 | 41.27 | 1093.9 | 1052.63
4117 | 0.4047 | 73.18 | 62.273 | 0.0012769 | 41.28 | 1093.9 |  | 4117 | 73.18 | 0.4047 | 62.273 | 0.0012769 | 41.28 | 1093.9 | 1052.62
4118 | 0.40484 | 73.19 | 62.273 | 0.0012774 | 41.29 | 1093.9 |  | 4118 | 73.19 | 0.40484 | 62.273 | 0.0012774 | 41.29 | 1093.9 | 1052.61
4119 | 0.40498 | 73.2 | 62.273 | 0.0012778 | 41.3 | 1093.9 |  | 4119 | 73.2 | 0.40498 | 62.273 | 0.0012778 | 41.3 | 1093.9 | 1052.6
4120 | 0.40511 | 73.21 | 62.273 | 0.0012782 | 41.31 | 1093.9 |  | 4120 | 73.21 | 0.40511 | 62.273 | 0.0012782 | 41.31 | 1093.9 | 1052.59
4121 | 0.40525 | 73.22 | 62.273 | 0.0012786 | 41.32 | 1093.9 |  | 4121 | 73.22 | 0.40525 | 62.273 | 0.0012786 | 41.32 | 1093.9 | 1052.58
4122 | 0.40539 | 73.23 | 62.273 | 0.001279 | 41.33 | 1093.9 |  | 4122 | 73.23 | 0.40539 | 62.273 | 0.001279 | 41.33 | 1093.9 | 1052.57
4123 | 0.40552 | 73.24 | 62.273 | 0.0012794 | 41.34 | 1093.9 |  | 4123 | 73.24 | 0.40552 | 62.273 | 0.0012794 | 41.34 | 1093.9 | 1052.56
4124 | 0.40566 | 73.25 | 62.273 | 0.0012798 | 41.35 | 1093.9 |  | 4124 | 73.25 | 0.40566 | 62.273 | 0.0012798 | 41.35 | 1093.9 | 1052.55
4125 | 0.4058 | 73.26 | 62.273 | 0.0012802 | 41.36 | 1093.9 |  | 4125 | 73.26 | 0.4058 | 62.273 | 0.0012802 | 41.36 | 1093.9 | 1052.54
4126 | 0.40593 | 73.27 | 62.273 | 0.0012806 | 41.37 | 1093.9 |  | 4126 | 73.27 | 0.40593 | 62.273 | 0.0012806 | 41.37 | 1093.9 | 1052.53
4127 | 0.40607 | 73.28 | 62.273 | 0.001281 | 41.38 | 1093.9 |  | 4127 | 73.28 | 0.40607 | 62.273 | 0.001281 | 41.38 | 1093.9 | 1052.52
4128 | 0.40621 | 73.29 | 62.273 | 0.0012814 | 41.39 | 1093.9 |  | 4128 | 73.29 | 0.40621 | 62.273 | 0.0012814 | 41.39 | 1093.9 | 1052.51
4129 | 0.40634 | 73.3 | 62.273 | 0.0012818 | 41.4 | 1093.9 |  | 4129 | 73.3 | 0.40634 | 62.273 | 0.0012818 | 41.4 | 1093.9 | 1052.5
4130 | 0.40648 | 73.31 | 62.272 | 0.0012822 | 41.41 | 1093.9 |  | 4130 | 73.31 | 0.40648 | 62.272 | 0.0012822 | 41.41 | 1093.9 | 1052.49
4131 | 0.40662 | 73.32 | 62.272 | 0.0012826 | 41.42 | 1093.9 |  | 4131 | 73.32 | 0.40662 | 62.272 | 0.0012826 | 41.42 | 1093.9 | 1052.48
4132 | 0.40675 | 73.33 | 62.272 | 0.0012831 | 41.43 | 1093.9 |  | 4132 | 73.33 | 0.40675 | 62.272 | 0.0012831 | 41.43 | 1093.9 | 1052.47
4133 | 0.40689 | 73.34 | 62.272 | 0.0012835 | 41.44 | 1093.9 |  | 4133 | 73.34 | 0.40689 | 62.272 | 0.0012835 | 41.44 | 1093.9 | 1052.46
4134 | 0.40703 | 73.35 | 62.272 | 0.0012839 | 41.45 | 1094 |  | 4134 | 73.35 | 0.40703 | 62.272 | 0.0012839 | 41.45 | 1094 | 1052.55
4135 | 0.40716 | 73.36 | 62.272 | 0.0012843 | 41.46 | 1094 |  | 4135 | 73.36 | 0.40716 | 62.272 | 0.0012843 | 41.46 | 1094 | 1052.54
4136 | 0.4073 | 73.37 | 62.272 | 0.0012847 | 41.47 | 1094 |  | 4136 | 73.37 | 0.4073 | 62.272 | 0.0012847 | 41.47 | 1094 | 1052.53
4137 | 0.40744 | 73.38 | 62.272 | 0.0012851 | 41.48 | 1094 |  | 4137 | 73.38 | 0.40744 | 62.272 | 0.0012851 | 41.48 | 1094 | 1052.52
4138 | 0.40757 | 73.39 | 62.272 | 0.0012855 | 41.49 | 1094 |  | 4138 | 73.39 | 0.40757 | 62.272 | 0.0012855 | 41.49 | 1094 | 1052.51
4139 | 0.40771 | 73.4 | 62.272 | 0.0012859 | 41.5 | 1094 |  | 4139 | 73.4 | 0.40771 | 62.272 | 0.0012859 | 41.5 | 1094 | 1052.5
4140 | 0.40785 | 73.41 | 62.272 | 0.0012863 | 41.51 | 1094 |  | 4140 | 73.41 | 0.40785 | 62.272 | 0.0012863 | 41.51 | 1094 | 1052.49
4141 | 0.40799 | 73.42 | 62.272 | 0.0012867 | 41.52 | 1094 |  | 4141 | 73.42 | 0.40799 | 62.272 | 0.0012867 | 41.52 | 1094 | 1052.48
4142 | 0.40812 | 73.43 | 62.271 | 0.0012871 | 41.53 | 1094 |  | 4142 | 73.43 | 0.40812 | 62.271 | 0.0012871 | 41.53 | 1094 | 1052.47
4143 | 0.40826 | 73.44 | 62.271 | 0.0012875 | 41.54 | 1094 |  | 4143 | 73.44 | 0.40826 | 62.271 | 0.0012875 | 41.54 | 1094 | 1052.46
4144 | 0.4084 | 73.45 | 62.271 | 0.001288 | 41.55 | 1094 |  | 4144 | 73.45 | 0.4084 | 62.271 | 0.001288 | 41.55 | 1094 | 1052.45
4145 | 0.40853 | 73.46 | 62.271 | 0.0012884 | 41.56 | 1094 |  | 4145 | 73.46 | 0.40853 | 62.271 | 0.0012884 | 41.56 | 1094 | 1052.44
4146 | 0.40867 | 73.47 | 62.271 | 0.0012888 | 41.57 | 1094 |  | 4146 | 73.47 | 0.40867 | 62.271 | 0.0012888 | 41.57 | 1094 | 1052.43
4147 | 0.40881 | 73.48 | 62.271 | 0.0012892 | 41.58 | 1094 |  | 4147 | 73.48 | 0.40881 | 62.271 | 0.0012892 | 41.58 | 1094 | 1052.42
4148 | 0.40895 | 73.49 | 62.271 | 0.0012896 | 41.59 | 1094 |  | 4148 | 73.49 | 0.40895 | 62.271 | 0.0012896 | 41.59 | 1094 | 1052.41
4149 | 0.40908 | 73.5 | 62.271 | 0.00129 | 41.6 | 1094 |  | 4149 | 73.5 | 0.40908 | 62.271 | 0.00129 | 41.6 | 1094 | 1052.4
4150 | 0.40922 | 73.51 | 62.271 | 0.0012904 | 41.61 | 1094 |  | 4150 | 73.51 | 0.40922 | 62.271 | 0.0012904 | 41.61 | 1094 | 1052.39
4151 | 0.40936 | 73.52 | 62.271 | 0.0012908 | 41.62 | 1094 |  | 4151 | 73.52 | 0.40936 | 62.271 | 0.0012908 | 41.62 | 1094 | 1052.38
4152 | 0.4095 | 73.53 | 62.271 | 0.0012912 | 41.63 | 1094 |  | 4152 | 73.53 | 0.4095 | 62.271 | 0.0012912 | 41.63 | 1094 | 1052.37
4153 | 0.40963 | 73.54 | 62.271 | 0.0012916 | 41.64 | 1094 |  | 4153 | 73.54 | 0.40963 | 62.271 | 0.0012916 | 41.64 | 1094 | 1052.36
4154 | 0.40977 | 73.55 | 62.27 | 0.0012921 | 41.65 | 1094 |  | 4154 | 73.55 | 0.40977 | 62.27 | 0.0012921 | 41.65 | 1094 | 1052.35
4155 | 0.40991 | 73.56 | 62.27 | 0.0012925 | 41.66 | 1094 |  | 4155 | 73.56 | 0.40991 | 62.27 | 0.0012925 | 41.66 | 1094 | 1052.34
4156 | 0.41005 | 73.57 | 62.27 | 0.0012929 | 41.67 | 1094 |  | 4156 | 73.57 | 0.41005 | 62.27 | 0.0012929 | 41.67 | 1094 | 1052.33
4157 | 0.41019 | 73.58 | 62.27 | 0.0012933 | 41.68 | 1094.1 |  | 4157 | 73.58 | 0.41019 | 62.27 | 0.0012933 | 41.68 | 1094.1 | 1052.42
4158 | 0.41032 | 73.59 | 62.27 | 0.0012937 | 41.69 | 1094.1 |  | 4158 | 73.59 | 0.41032 | 62.27 | 0.0012937 | 41.69 | 1094.1 | 1052.41
4159 | 0.41046 | 73.6 | 62.27 | 0.0012941 | 41.7 | 1094.1 |  | 4159 | 73.6 | 0.41046 | 62.27 | 0.0012941 | 41.7 | 1094.1 | 1052.4
4160 | 0.4106 | 73.61 | 62.27 | 0.0012945 | 41.71 | 1094.1 |  | 4160 | 73.61 | 0.4106 | 62.27 | 0.0012945 | 41.71 | 1094.1 | 1052.39
4161 | 0.41074 | 73.62 | 62.27 | 0.0012949 | 41.72 | 1094.1 |  | 4161 | 73.62 | 0.41074 | 62.27 | 0.0012949 | 41.72 | 1094.1 | 1052.38
4162 | 0.41088 | 73.63 | 62.27 | 0.0012953 | 41.73 | 1094.1 |  | 4162 | 73.63 | 0.41088 | 62.27 | 0.0012953 | 41.73 | 1094.1 | 1052.37
4163 | 0.41101 | 73.64 | 62.27 | 0.0012958 | 41.74 | 1094.1 |  | 4163 | 73.64 | 0.41101 | 62.27 | 0.0012958 | 41.74 | 1094.1 | 1052.36
4164 | 0.41115 | 73.65 | 62.27 | 0.0012962 | 41.75 | 1094.1 |  | 4164 | 73.65 | 0.41115 | 62.27 | 0.0012962 | 41.75 | 1094.1 | 1052.35
4165 | 0.41129 | 73.66 | 62.27 | 0.0012966 | 41.76 | 1094.1 |  | 4165 | 73.66 | 0.41129 | 62.27 | 0.0012966 | 41.76 | 1094.1 | 1052.34
4166 | 0.41143 | 73.67 | 62.269 | 0.001297 | 41.77 | 1094.1 |  | 4166 | 73.67 | 0.41143 | 62.269 | 0.001297 | 41.77 | 1094.1 | 1052.33
4167 | 0.41157 | 73.68 | 62.269 | 0.0012974 | 41.78 | 1094.1 |  | 4167 | 73.68 | 0.41157 | 62.269 | 0.0012974 | 41.78 | 1094.1 | 1052.32
4168 | 0.4117 | 73.69 | 62.269 | 0.0012978 | 41.79 | 1094.1 |  | 4168 | 73.69 | 0.4117 | 62.269 | 0.0012978 | 41.79 | 1094.1 | 1052.31
4169 | 0.41184 | 73.7 | 62.269 | 0.0012982 | 41.8 | 1094.1 |  | 4169 | 73.7 | 0.41184 | 62.269 | 0.0012982 | 41.8 | 1094.1 | 1052.3
4170 | 0.41198 | 73.71 | 62.269 | 0.0012986 | 41.81 | 1094.1 |  | 4170 | 73.71 | 0.41198 | 62.269 | 0.0012986 | 41.81 | 1094.1 | 1052.29
4171 | 0.41212 | 73.72 | 62.269 | 0.001299 | 41.82 | 1094.1 |  | 4171 | 73.72 | 0.41212 | 62.269 | 0.001299 | 41.82 | 1094.1 | 1052.28
4172 | 0.41226 | 73.73 | 62.269 | 0.0012995 | 41.83 | 1094.1 |  | 4172 | 73.73 | 0.41226 | 62.269 | 0.0012995 | 41.83 | 1094.1 | 1052.27
4173 | 0.4124 | 73.74 | 62.269 | 0.0012999 | 41.84 | 1094.1 |  | 4173 | 73.74 | 0.4124 | 62.269 | 0.0012999 | 41.84 | 1094.1 | 1052.26
4174 | 0.41254 | 73.75 | 62.269 | 0.0013003 | 41.85 | 1094.1 |  | 4174 | 73.75 | 0.41254 | 62.269 | 0.0013003 | 41.85 | 1094.1 | 1052.25
4175 | 0.41267 | 73.76 | 62.269 | 0.0013007 | 41.86 | 1094.1 |  | 4175 | 73.76 | 0.41267 | 62.269 | 0.0013007 | 41.86 | 1094.1 | 1052.24
4176 | 0.41281 | 73.77 | 62.269 | 0.0013011 | 41.87 | 1094.1 |  | 4176 | 73.77 | 0.41281 | 62.269 | 0.0013011 | 41.87 | 1094.1 | 1052.23
4177 | 0.41295 | 73.78 | 62.269 | 0.0013015 | 41.88 | 1094.1 |  | 4177 | 73.78 | 0.41295 | 62.269 | 0.0013015 | 41.88 | 1094.1 | 1052.22
4178 | 0.41309 | 73.79 | 62.268 | 0.0013019 | 41.89 | 1094.1 |  | 4178 | 73.79 | 0.41309 | 62.268 | 0.0013019 | 41.89 | 1094.1 | 1052.21
4179 | 0.41323 | 73.8 | 62.268 | 0.0013023 | 41.9 | 1094.1 |  | 4179 | 73.8 | 0.41323 | 62.268 | 0.0013023 | 41.9 | 1094.1 | 1052.2
4180 | 0.41337 | 73.81 | 62.268 | 0.0013028 | 41.91 | 1094.2 |  | 4180 | 73.81 | 0.41337 | 62.268 | 0.0013028 | 41.91 | 1094.2 | 1052.29
4181 | 0.41351 | 73.82 | 62.268 | 0.0013032 | 41.92 | 1094.2 |  | 4181 | 73.82 | 0.41351 | 62.268 | 0.0013032 | 41.92 | 1094.2 | 1052.28
4182 | 0.41364 | 73.83 | 62.268 | 0.0013036 | 41.93 | 1094.2 |  | 4182 | 73.83 | 0.41364 | 62.268 | 0.0013036 | 41.93 | 1094.2 | 1052.27
4183 | 0.41378 | 73.84 | 62.268 | 0.001304 | 41.94 | 1094.2 |  | 4183 | 73.84 | 0.41378 | 62.268 | 0.001304 | 41.94 | 1094.2 | 1052.26
4184 | 0.41392 | 73.85 | 62.268 | 0.0013044 | 41.95 | 1094.2 |  | 4184 | 73.85 | 0.41392 | 62.268 | 0.0013044 | 41.95 | 1094.2 | 1052.25
4185 | 0.41406 | 73.86 | 62.268 | 0.0013048 | 41.96 | 1094.2 |  | 4185 | 73.86 | 0.41406 | 62.268 | 0.0013048 | 41.96 | 1094.2 | 1052.24
4186 | 0.4142 | 73.87 | 62.268 | 0.0013052 | 41.97 | 1094.2 |  | 4186 | 73.87 | 0.4142 | 62.268 | 0.0013052 | 41.97 | 1094.2 | 1052.23
4187 | 0.41434 | 73.88 | 62.268 | 0.0013057 | 41.98 | 1094.2 |  | 4187 | 73.88 | 0.41434 | 62.268 | 0.0013057 | 41.98 | 1094.2 | 1052.22
4188 | 0.41448 | 73.89 | 62.268 | 0.0013061 | 41.99 | 1094.2 |  | 4188 | 73.89 | 0.41448 | 62.268 | 0.0013061 | 41.99 | 1094.2 | 1052.21
4189 | 0.41462 | 73.9 | 62.268 | 0.0013065 | 42 | 1094.2 |  | 4189 | 73.9 | 0.41462 | 62.268 | 0.0013065 | 42 | 1094.2 | 1052.2
4190 | 0.41476 | 73.91 | 62.267 | 0.0013069 | 42.01 | 1094.2 |  | 4190 | 73.91 | 0.41476 | 62.267 | 0.0013069 | 42.01 | 1094.2 | 1052.19
4191 | 0.4149 | 73.92 | 62.267 | 0.0013073 | 42.02 | 1094.2 |  | 4191 | 73.92 | 0.4149 | 62.267 | 0.0013073 | 42.02 | 1094.2 | 1052.18
4192 | 0.41504 | 73.93 | 62.267 | 0.0013077 | 42.03 | 1094.2 |  | 4192 | 73.93 | 0.41504 | 62.267 | 0.0013077 | 42.03 | 1094.2 | 1052.17
4193 | 0.41517 | 73.94 | 62.267 | 0.0013081 | 42.04 | 1094.2 |  | 4193 | 73.94 | 0.41517 | 62.267 | 0.0013081 | 42.04 | 1094.2 | 1052.16
4194 | 0.41531 | 73.95 | 62.267 | 0.0013086 | 42.05 | 1094.2 |  | 4194 | 73.95 | 0.41531 | 62.267 | 0.0013086 | 42.05 | 1094.2 | 1052.15
4195 | 0.41545 | 73.96 | 62.267 | 0.001309 | 42.06 | 1094.2 |  | 4195 | 73.96 | 0.41545 | 62.267 | 0.001309 | 42.06 | 1094.2 | 1052.14
4196 | 0.41559 | 73.97 | 62.267 | 0.0013094 | 42.07 | 1094.2 |  | 4196 | 73.97 | 0.41559 | 62.267 | 0.0013094 | 42.07 | 1094.2 | 1052.13
4197 | 0.41573 | 73.98 | 62.267 | 0.0013098 | 42.08 | 1094.2 |  | 4197 | 73.98 | 0.41573 | 62.267 | 0.0013098 | 42.08 | 1094.2 | 1052.12
4198 | 0.41587 | 73.99 | 62.267 | 0.0013102 | 42.09 | 1094.2 |  | 4198 | 73.99 | 0.41587 | 62.267 | 0.0013102 | 42.09 | 1094.2 | 1052.11
4199 | 0.41601 | 74 | 62.267 | 0.0013106 | 42.1 | 1094.2 |  | 4199 | 74 | 0.41601 | 62.267 | 0.0013106 | 42.1 | 1094.2 | 1052.1
4200 | 0.41615 | 74.01 | 62.267 | 0.0013111 | 42.11 | 1094.2 |  | 4200 | 74.01 | 0.41615 | 62.267 | 0.0013111 | 42.11 | 1094.2 | 1052.09
4201 | 0.41629 | 74.02 | 62.267 | 0.0013115 | 42.12 | 1094.2 |  | 4201 | 74.02 | 0.41629 | 62.267 | 0.0013115 | 42.12 | 1094.2 | 1052.08
4202 | 0.41643 | 74.03 | 62.266 | 0.0013119 | 42.13 | 1094.2 |  | 4202 | 74.03 | 0.41643 | 62.266 | 0.0013119 | 42.13 | 1094.2 | 1052.07
4203 | 0.41657 | 74.04 | 62.266 | 0.0013123 | 42.14 | 1094.3 |  | 4203 | 74.04 | 0.41657 | 62.266 | 0.0013123 | 42.14 | 1094.3 | 1052.16
4204 | 0.41671 | 74.05 | 62.266 | 0.0013127 | 42.15 | 1094.3 |  | 4204 | 74.05 | 0.41671 | 62.266 | 0.0013127 | 42.15 | 1094.3 | 1052.15
4205 | 0.41685 | 74.06 | 62.266 | 0.0013131 | 42.16 | 1094.3 |  | 4205 | 74.06 | 0.41685 | 62.266 | 0.0013131 | 42.16 | 1094.3 | 1052.14
4206 | 0.41699 | 74.07 | 62.266 | 0.0013135 | 42.17 | 1094.3 |  | 4206 | 74.07 | 0.41699 | 62.266 | 0.0013135 | 42.17 | 1094.3 | 1052.13
4207 | 0.41713 | 74.08 | 62.266 | 0.001314 | 42.18 | 1094.3 |  | 4207 | 74.08 | 0.41713 | 62.266 | 0.001314 | 42.18 | 1094.3 | 1052.12
4208 | 0.41727 | 74.09 | 62.266 | 0.0013144 | 42.19 | 1094.3 |  | 4208 | 74.09 | 0.41727 | 62.266 | 0.0013144 | 42.19 | 1094.3 | 1052.11
4209 | 0.41741 | 74.1 | 62.266 | 0.0013148 | 42.2 | 1094.3 |  | 4209 | 74.1 | 0.41741 | 62.266 | 0.0013148 | 42.2 | 1094.3 | 1052.1
4210 | 0.41755 | 74.11 | 62.266 | 0.0013152 | 42.21 | 1094.3 |  | 4210 | 74.11 | 0.41755 | 62.266 | 0.0013152 | 42.21 | 1094.3 | 1052.09
4211 | 0.41769 | 74.12 | 62.266 | 0.0013156 | 42.22 | 1094.3 |  | 4211 | 74.12 | 0.41769 | 62.266 | 0.0013156 | 42.22 | 1094.3 | 1052.08
4212 | 0.41783 | 74.13 | 62.266 | 0.001316 | 42.23 | 1094.3 |  | 4212 | 74.13 | 0.41783 | 62.266 | 0.001316 | 42.23 | 1094.3 | 1052.07
4213 | 0.41797 | 74.14 | 62.266 | 0.0013165 | 42.24 | 1094.3 |  | 4213 | 74.14 | 0.41797 | 62.266 | 0.0013165 | 42.24 | 1094.3 | 1052.06
4214 | 0.41811 | 74.15 | 62.265 | 0.0013169 | 42.25 | 1094.3 |  | 4214 | 74.15 | 0.41811 | 62.265 | 0.0013169 | 42.25 | 1094.3 | 1052.05
4215 | 0.41825 | 74.16 | 62.265 | 0.0013173 | 42.26 | 1094.3 |  | 4215 | 74.16 | 0.41825 | 62.265 | 0.0013173 | 42.26 | 1094.3 | 1052.04
4216 | 0.41839 | 74.17 | 62.265 | 0.0013177 | 42.27 | 1094.3 |  | 4216 | 74.17 | 0.41839 | 62.265 | 0.0013177 | 42.27 | 1094.3 | 1052.03
4217 | 0.41853 | 74.18 | 62.265 | 0.0013181 | 42.28 | 1094.3 |  | 4217 | 74.18 | 0.41853 | 62.265 | 0.0013181 | 42.28 | 1094.3 | 1052.02
4218 | 0.41867 | 74.19 | 62.265 | 0.0013186 | 42.29 | 1094.3 |  | 4218 | 74.19 | 0.41867 | 62.265 | 0.0013186 | 42.29 | 1094.3 | 1052.01
4219 | 0.41881 | 74.2 | 62.265 | 0.001319 | 42.3 | 1094.3 |  | 4219 | 74.2 | 0.41881 | 62.265 | 0.001319 | 42.3 | 1094.3 | 1052
4220 | 0.41895 | 74.21 | 62.265 | 0.0013194 | 42.31 | 1094.3 |  | 4220 | 74.21 | 0.41895 | 62.265 | 0.0013194 | 42.31 | 1094.3 | 1051.99
4221 | 0.41909 | 74.22 | 62.265 | 0.0013198 | 42.32 | 1094.3 |  | 4221 | 74.22 | 0.41909 | 62.265 | 0.0013198 | 42.32 | 1094.3 | 1051.98
4222 | 0.41923 | 74.23 | 62.265 | 0.0013202 | 42.33 | 1094.3 |  | 4222 | 74.23 | 0.41923 | 62.265 | 0.0013202 | 42.33 | 1094.3 | 1051.97
4223 | 0.41937 | 74.24 | 62.265 | 0.0013206 | 42.34 | 1094.3 |  | 4223 | 74.24 | 0.41937 | 62.265 | 0.0013206 | 42.34 | 1094.3 | 1051.96
4224 | 0.41951 | 74.25 | 62.265 | 0.0013211 | 42.35 | 1094.3 |  | 4224 | 74.25 | 0.41951 | 62.265 | 0.0013211 | 42.35 | 1094.3 | 1051.95
4225 | 0.41965 | 74.26 | 62.265 | 0.0013215 | 42.36 | 1094.3 |  | 4225 | 74.26 | 0.41965 | 62.265 | 0.0013215 | 42.36 | 1094.3 | 1051.94
4226 | 0.41979 | 74.27 | 62.264 | 0.0013219 | 42.37 | 1094.4 |  | 4226 | 74.27 | 0.41979 | 62.264 | 0.0013219 | 42.37 | 1094.4 | 1052.03
4227 | 0.41993 | 74.28 | 62.264 | 0.0013223 | 42.38 | 1094.4 |  | 4227 | 74.28 | 0.41993 | 62.264 | 0.0013223 | 42.38 | 1094.4 | 1052.02
4228 | 0.42007 | 74.29 | 62.264 | 0.0013227 | 42.39 | 1094.4 |  | 4228 | 74.29 | 0.42007 | 62.264 | 0.0013227 | 42.39 | 1094.4 | 1052.01
4229 | 0.42022 | 74.3 | 62.264 | 0.0013232 | 42.4 | 1094.4 |  | 4229 | 74.3 | 0.42022 | 62.264 | 0.0013232 | 42.4 | 1094.4 | 1052
4230 | 0.42036 | 74.31 | 62.264 | 0.0013236 | 42.41 | 1094.4 |  | 4230 | 74.31 | 0.42036 | 62.264 | 0.0013236 | 42.41 | 1094.4 | 1051.99
4231 | 0.4205 | 74.32 | 62.264 | 0.001324 | 42.42 | 1094.4 |  | 4231 | 74.32 | 0.4205 | 62.264 | 0.001324 | 42.42 | 1094.4 | 1051.98
4232 | 0.42064 | 74.33 | 62.264 | 0.0013244 | 42.43 | 1094.4 |  | 4232 | 74.33 | 0.42064 | 62.264 | 0.0013244 | 42.43 | 1094.4 | 1051.97
4233 | 0.42078 | 74.34 | 62.264 | 0.0013248 | 42.44 | 1094.4 |  | 4233 | 74.34 | 0.42078 | 62.264 | 0.0013248 | 42.44 | 1094.4 | 1051.96
4234 | 0.42092 | 74.35 | 62.264 | 0.0013252 | 42.45 | 1094.4 |  | 4234 | 74.35 | 0.42092 | 62.264 | 0.0013252 | 42.45 | 1094.4 | 1051.95
4235 | 0.42106 | 74.36 | 62.264 | 0.0013257 | 42.46 | 1094.4 |  | 4235 | 74.36 | 0.42106 | 62.264 | 0.0013257 | 42.46 | 1094.4 | 1051.94
4236 | 0.4212 | 74.37 | 62.264 | 0.0013261 | 42.47 | 1094.4 |  | 4236 | 74.37 | 0.4212 | 62.264 | 0.0013261 | 42.47 | 1094.4 | 1051.93
4237 | 0.42134 | 74.38 | 62.264 | 0.0013265 | 42.48 | 1094.4 |  | 4237 | 74.38 | 0.42134 | 62.264 | 0.0013265 | 42.48 | 1094.4 | 1051.92
4238 | 0.42148 | 74.39 | 62.263 | 0.0013269 | 42.49 | 1094.4 |  | 4238 | 74.39 | 0.42148 | 62.263 | 0.0013269 | 42.49 | 1094.4 | 1051.91
4239 | 0.42163 | 74.4 | 62.263 | 0.0013273 | 42.5 | 1094.4 |  | 4239 | 74.4 | 0.42163 | 62.263 | 0.0013273 | 42.5 | 1094.4 | 1051.9
4240 | 0.42177 | 74.41 | 62.263 | 0.0013278 | 42.51 | 1094.4 |  | 4240 | 74.41 | 0.42177 | 62.263 | 0.0013278 | 42.51 | 1094.4 | 1051.89
4241 | 0.42191 | 74.42 | 62.263 | 0.0013282 | 42.52 | 1094.4 |  | 4241 | 74.42 | 0.42191 | 62.263 | 0.0013282 | 42.52 | 1094.4 | 1051.88
4242 | 0.42205 | 74.43 | 62.263 | 0.0013286 | 42.53 | 1094.4 |  | 4242 | 74.43 | 0.42205 | 62.263 | 0.0013286 | 42.53 | 1094.4 | 1051.87
4243 | 0.42219 | 74.44 | 62.263 | 0.001329 | 42.54 | 1094.4 |  | 4243 | 74.44 | 0.42219 | 62.263 | 0.001329 | 42.54 | 1094.4 | 1051.86
4244 | 0.42233 | 74.45 | 62.263 | 0.0013294 | 42.55 | 1094.4 |  | 4244 | 74.45 | 0.42233 | 62.263 | 0.0013294 | 42.55 | 1094.4 | 1051.85
4245 | 0.42247 | 74.46 | 62.263 | 0.0013299 | 42.56 | 1094.4 |  | 4245 | 74.46 | 0.42247 | 62.263 | 0.0013299 | 42.56 | 1094.4 | 1051.84
4246 | 0.42261 | 74.47 | 62.263 | 0.0013303 | 42.57 | 1094.4 |  | 4246 | 74.47 | 0.42261 | 62.263 | 0.0013303 | 42.57 | 1094.4 | 1051.83
4247 | 0.42276 | 74.48 | 62.263 | 0.0013307 | 42.58 | 1094.4 |  | 4247 | 74.48 | 0.42276 | 62.263 | 0.0013307 | 42.58 | 1094.4 | 1051.82
4248 | 0.4229 | 74.49 | 62.263 | 0.0013311 | 42.59 | 1094.4 |  | 4248 | 74.49 | 0.4229 | 62.263 | 0.0013311 | 42.59 | 1094.4 | 1051.81
4249 | 0.42304 | 74.5 | 62.263 | 0.0013316 | 42.6 | 1094.5 |  | 4249 | 74.5 | 0.42304 | 62.263 | 0.0013316 | 42.6 | 1094.5 | 1051.9
4250 | 0.42318 | 74.51 | 62.262 | 0.001332 | 42.61 | 1094.5 |  | 4250 | 74.51 | 0.42318 | 62.262 | 0.001332 | 42.61 | 1094.5 | 1051.89
4251 | 0.42332 | 74.52 | 62.262 | 0.0013324 | 42.62 | 1094.5 |  | 4251 | 74.52 | 0.42332 | 62.262 | 0.0013324 | 42.62 | 1094.5 | 1051.88
4252 | 0.42346 | 74.53 | 62.262 | 0.0013328 | 42.63 | 1094.5 |  | 4252 | 74.53 | 0.42346 | 62.262 | 0.0013328 | 42.63 | 1094.5 | 1051.87
4253 | 0.42361 | 74.54 | 62.262 | 0.0013332 | 42.64 | 1094.5 |  | 4253 | 74.54 | 0.42361 | 62.262 | 0.0013332 | 42.64 | 1094.5 | 1051.86
4254 | 0.42375 | 74.55 | 62.262 | 0.0013337 | 42.65 | 1094.5 |  | 4254 | 74.55 | 0.42375 | 62.262 | 0.0013337 | 42.65 | 1094.5 | 1051.85
4255 | 0.42389 | 74.56 | 62.262 | 0.0013341 | 42.66 | 1094.5 |  | 4255 | 74.56 | 0.42389 | 62.262 | 0.0013341 | 42.66 | 1094.5 | 1051.84
4256 | 0.42403 | 74.57 | 62.262 | 0.0013345 | 42.67 | 1094.5 |  | 4256 | 74.57 | 0.42403 | 62.262 | 0.0013345 | 42.67 | 1094.5 | 1051.83
4257 | 0.42417 | 74.58 | 62.262 | 0.0013349 | 42.68 | 1094.5 |  | 4257 | 74.58 | 0.42417 | 62.262 | 0.0013349 | 42.68 | 1094.5 | 1051.82
4258 | 0.42432 | 74.59 | 62.262 | 0.0013353 | 42.69 | 1094.5 |  | 4258 | 74.59 | 0.42432 | 62.262 | 0.0013353 | 42.69 | 1094.5 | 1051.81
4259 | 0.42446 | 74.6 | 62.262 | 0.0013358 | 42.7 | 1094.5 |  | 4259 | 74.6 | 0.42446 | 62.262 | 0.0013358 | 42.7 | 1094.5 | 1051.8
4260 | 0.4246 | 74.61 | 62.262 | 0.0013362 | 42.71 | 1094.5 |  | 4260 | 74.61 | 0.4246 | 62.262 | 0.0013362 | 42.71 | 1094.5 | 1051.79
4261 | 0.42474 | 74.62 | 62.262 | 0.0013366 | 42.72 | 1094.5 |  | 4261 | 74.62 | 0.42474 | 62.262 | 0.0013366 | 42.72 | 1094.5 | 1051.78
4262 | 0.42488 | 74.63 | 62.261 | 0.001337 | 42.73 | 1094.5 |  | 4262 | 74.63 | 0.42488 | 62.261 | 0.001337 | 42.73 | 1094.5 | 1051.77
4263 | 0.42503 | 74.64 | 62.261 | 0.0013375 | 42.74 | 1094.5 |  | 4263 | 74.64 | 0.42503 | 62.261 | 0.0013375 | 42.74 | 1094.5 | 1051.76
4264 | 0.42517 | 74.65 | 62.261 | 0.0013379 | 42.75 | 1094.5 |  | 4264 | 74.65 | 0.42517 | 62.261 | 0.0013379 | 42.75 | 1094.5 | 1051.75
4265 | 0.42531 | 74.66 | 62.261 | 0.0013383 | 42.76 | 1094.5 |  | 4265 | 74.66 | 0.42531 | 62.261 | 0.0013383 | 42.76 | 1094.5 | 1051.74
4266 | 0.42545 | 74.67 | 62.261 | 0.0013387 | 42.77 | 1094.5 |  | 4266 | 74.67 | 0.42545 | 62.261 | 0.0013387 | 42.77 | 1094.5 | 1051.73
4267 | 0.42559 | 74.68 | 62.261 | 0.0013392 | 42.78 | 1094.5 |  | 4267 | 74.68 | 0.42559 | 62.261 | 0.0013392 | 42.78 | 1094.5 | 1051.72
4268 | 0.42574 | 74.69 | 62.261 | 0.0013396 | 42.79 | 1094.5 |  | 4268 | 74.69 | 0.42574 | 62.261 | 0.0013396 | 42.79 | 1094.5 | 1051.71
4269 | 0.42588 | 74.7 | 62.261 | 0.00134 | 42.8 | 1094.5 |  | 4269 | 74.7 | 0.42588 | 62.261 | 0.00134 | 42.8 | 1094.5 | 1051.7
4270 | 0.42602 | 74.71 | 62.261 | 0.0013404 | 42.81 | 1094.5 |  | 4270 | 74.71 | 0.42602 | 62.261 | 0.0013404 | 42.81 | 1094.5 | 1051.69
4271 | 0.42616 | 74.72 | 62.261 | 0.0013408 | 42.82 | 1094.5 |  | 4271 | 74.72 | 0.42616 | 62.261 | 0.0013408 | 42.82 | 1094.5 | 1051.68
4272 | 0.42631 | 74.73 | 62.261 | 0.0013413 | 42.83 | 1094.5 |  | 4272 | 74.73 | 0.42631 | 62.261 | 0.0013413 | 42.83 | 1094.5 | 1051.67
4273 | 0.42645 | 74.74 | 62.261 | 0.0013417 | 42.84 | 1094.6 |  | 4273 | 74.74 | 0.42645 | 62.261 | 0.0013417 | 42.84 | 1094.6 | 1051.76
4274 | 0.42659 | 74.75 | 62.26 | 0.0013421 | 42.85 | 1094.6 |  | 4274 | 74.75 | 0.42659 | 62.26 | 0.0013421 | 42.85 | 1094.6 | 1051.75
4275 | 0.42674 | 74.76 | 62.26 | 0.0013425 | 42.86 | 1094.6 |  | 4275 | 74.76 | 0.42674 | 62.26 | 0.0013425 | 42.86 | 1094.6 | 1051.74
4276 | 0.42688 | 74.77 | 62.26 | 0.001343 | 42.87 | 1094.6 |  | 4276 | 74.77 | 0.42688 | 62.26 | 0.001343 | 42.87 | 1094.6 | 1051.73
4277 | 0.42702 | 74.78 | 62.26 | 0.0013434 | 42.88 | 1094.6 |  | 4277 | 74.78 | 0.42702 | 62.26 | 0.0013434 | 42.88 | 1094.6 | 1051.72
4278 | 0.42716 | 74.79 | 62.26 | 0.0013438 | 42.89 | 1094.6 |  | 4278 | 74.79 | 0.42716 | 62.26 | 0.0013438 | 42.89 | 1094.6 | 1051.71
4279 | 0.42731 | 74.8 | 62.26 | 0.0013442 | 42.9 | 1094.6 |  | 4279 | 74.8 | 0.42731 | 62.26 | 0.0013442 | 42.9 | 1094.6 | 1051.7
4280 | 0.42745 | 74.81 | 62.26 | 0.0013447 | 42.91 | 1094.6 |  | 4280 | 74.81 | 0.42745 | 62.26 | 0.0013447 | 42.91 | 1094.6 | 1051.69
4281 | 0.42759 | 74.82 | 62.26 | 0.0013451 | 42.92 | 1094.6 |  | 4281 | 74.82 | 0.42759 | 62.26 | 0.0013451 | 42.92 | 1094.6 | 1051.68
4282 | 0.42773 | 74.83 | 62.26 | 0.0013455 | 42.93 | 1094.6 |  | 4282 | 74.83 | 0.42773 | 62.26 | 0.0013455 | 42.93 | 1094.6 | 1051.67
4283 | 0.42788 | 74.84 | 62.26 | 0.0013459 | 42.94 | 1094.6 |  | 4283 | 74.84 | 0.42788 | 62.26 | 0.0013459 | 42.94 | 1094.6 | 1051.66
4284 | 0.42802 | 74.85 | 62.26 | 0.0013464 | 42.95 | 1094.6 |  | 4284 | 74.85 | 0.42802 | 62.26 | 0.0013464 | 42.95 | 1094.6 | 1051.65
4285 | 0.42816 | 74.86 | 62.259 | 0.0013468 | 42.96 | 1094.6 |  | 4285 | 74.86 | 0.42816 | 62.259 | 0.0013468 | 42.96 | 1094.6 | 1051.64
4286 | 0.42831 | 74.87 | 62.259 | 0.0013472 | 42.97 | 1094.6 |  | 4286 | 74.87 | 0.42831 | 62.259 | 0.0013472 | 42.97 | 1094.6 | 1051.63
4287 | 0.42845 | 74.88 | 62.259 | 0.0013476 | 42.98 | 1094.6 |  | 4287 | 74.88 | 0.42845 | 62.259 | 0.0013476 | 42.98 | 1094.6 | 1051.62
4288 | 0.42859 | 74.89 | 62.259 | 0.0013481 | 42.99 | 1094.6 |  | 4288 | 74.89 | 0.42859 | 62.259 | 0.0013481 | 42.99 | 1094.6 | 1051.61
4289 | 0.42874 | 74.9 | 62.259 | 0.0013485 | 43 | 1094.6 |  | 4289 | 74.9 | 0.42874 | 62.259 | 0.0013485 | 43 | 1094.6 | 1051.6
4290 | 0.42888 | 74.91 | 62.259 | 0.0013489 | 43.01 | 1094.6 |  | 4290 | 74.91 | 0.42888 | 62.259 | 0.0013489 | 43.01 | 1094.6 | 1051.59
4291 | 0.42902 | 74.92 | 62.259 | 0.0013493 | 43.02 | 1094.6 |  | 4291 | 74.92 | 0.42902 | 62.259 | 0.0013493 | 43.02 | 1094.6 | 1051.58
4292 | 0.42917 | 74.93 | 62.259 | 0.0013498 | 43.03 | 1094.6 |  | 4292 | 74.93 | 0.42917 | 62.259 | 0.0013498 | 43.03 | 1094.6 | 1051.57
4293 | 0.42931 | 74.94 | 62.259 | 0.0013502 | 43.04 | 1094.6 |  | 4293 | 74.94 | 0.42931 | 62.259 | 0.0013502 | 43.04 | 1094.6 | 1051.56
4294 | 0.42945 | 74.95 | 62.259 | 0.0013506 | 43.05 | 1094.6 |  | 4294 | 74.95 | 0.42945 | 62.259 | 0.0013506 | 43.05 | 1094.6 | 1051.55
4295 | 0.4296 | 74.96 | 62.259 | 0.0013511 | 43.06 | 1094.6 |  | 4295 | 74.96 | 0.4296 | 62.259 | 0.0013511 | 43.06 | 1094.6 | 1051.54
4296 | 0.42974 | 74.97 | 62.259 | 0.0013515 | 43.07 | 1094.7 |  | 4296 | 74.97 | 0.42974 | 62.259 | 0.0013515 | 43.07 | 1094.7 | 1051.63
4297 | 0.42988 | 74.98 | 62.258 | 0.0013519 | 43.08 | 1094.7 |  | 4297 | 74.98 | 0.42988 | 62.258 | 0.0013519 | 43.08 | 1094.7 | 1051.62
4298 | 0.43003 | 74.99 | 62.258 | 0.0013523 | 43.09 | 1094.7 |  | 4298 | 74.99 | 0.43003 | 62.258 | 0.0013523 | 43.09 | 1094.7 | 1051.61
4299 | 0.43017 | 75 | 62.258 | 0.0013528 | 43.1 | 1094.7 |  | 4299 | 75 | 0.43017 | 62.258 | 0.0013528 | 43.1 | 1094.7 | 1051.6
4300 | 0.43032 | 75.01 | 62.258 | 0.0013532 | 43.11 | 1094.7 |  | 4300 | 75.01 | 0.43032 | 62.258 | 0.0013532 | 43.11 | 1094.7 | 1051.59
4301 | 0.43046 | 75.02 | 62.258 | 0.0013536 | 43.12 | 1094.7 |  | 4301 | 75.02 | 0.43046 | 62.258 | 0.0013536 | 43.12 | 1094.7 | 1051.58
4302 | 0.4306 | 75.03 | 62.258 | 0.001354 | 43.13 | 1094.7 |  | 4302 | 75.03 | 0.4306 | 62.258 | 0.001354 | 43.13 | 1094.7 | 1051.57
4303 | 0.43075 | 75.04 | 62.258 | 0.0013545 | 43.14 | 1094.7 |  | 4303 | 75.04 | 0.43075 | 62.258 | 0.0013545 | 43.14 | 1094.7 | 1051.56
4304 | 0.43089 | 75.05 | 62.258 | 0.0013549 | 43.15 | 1094.7 |  | 4304 | 75.05 | 0.43089 | 62.258 | 0.0013549 | 43.15 | 1094.7 | 1051.55
4305 | 0.43103 | 75.06 | 62.258 | 0.0013553 | 43.16 | 1094.7 |  | 4305 | 75.06 | 0.43103 | 62.258 | 0.0013553 | 43.16 | 1094.7 | 1051.54
4306 | 0.43118 | 75.07 | 62.258 | 0.0013557 | 43.17 | 1094.7 |  | 4306 | 75.07 | 0.43118 | 62.258 | 0.0013557 | 43.17 | 1094.7 | 1051.53
4307 | 0.43132 | 75.08 | 62.258 | 0.0013562 | 43.18 | 1094.7 |  | 4307 | 75.08 | 0.43132 | 62.258 | 0.0013562 | 43.18 | 1094.7 | 1051.52
4308 | 0.43147 | 75.09 | 62.258 | 0.0013566 | 43.19 | 1094.7 |  | 4308 | 75.09 | 0.43147 | 62.258 | 0.0013566 | 43.19 | 1094.7 | 1051.51
4309 | 0.43161 | 75.1 | 62.257 | 0.001357 | 43.2 | 1094.7 |  | 4309 | 75.1 | 0.43161 | 62.257 | 0.001357 | 43.2 | 1094.7 | 1051.5
4310 | 0.43175 | 75.11 | 62.257 | 0.0013575 | 43.21 | 1094.7 |  | 4310 | 75.11 | 0.43175 | 62.257 | 0.0013575 | 43.21 | 1094.7 | 1051.49
4311 | 0.4319 | 75.12 | 62.257 | 0.0013579 | 43.22 | 1094.7 |  | 4311 | 75.12 | 0.4319 | 62.257 | 0.0013579 | 43.22 | 1094.7 | 1051.48
4312 | 0.43204 | 75.13 | 62.257 | 0.0013583 | 43.23 | 1094.7 |  | 4312 | 75.13 | 0.43204 | 62.257 | 0.0013583 | 43.23 | 1094.7 | 1051.47
4313 | 0.43219 | 75.14 | 62.257 | 0.0013587 | 43.24 | 1094.7 |  | 4313 | 75.14 | 0.43219 | 62.257 | 0.0013587 | 43.24 | 1094.7 | 1051.46
4314 | 0.43233 | 75.15 | 62.257 | 0.0013592 | 43.25 | 1094.7 |  | 4314 | 75.15 | 0.43233 | 62.257 | 0.0013592 | 43.25 | 1094.7 | 1051.45
4315 | 0.43248 | 75.16 | 62.257 | 0.0013596 | 43.259 | 1094.7 |  | 4315 | 75.16 | 0.43248 | 62.257 | 0.0013596 | 43.259 | 1094.7 | 1051.441
4316 | 0.43262 | 75.17 | 62.257 | 0.00136 | 43.269 | 1094.7 |  | 4316 | 75.17 | 0.43262 | 62.257 | 0.00136 | 43.269 | 1094.7 | 1051.431
4317 | 0.43276 | 75.18 | 62.257 | 0.0013605 | 43.279 | 1094.7 |  | 4317 | 75.18 | 0.43276 | 62.257 | 0.0013605 | 43.279 | 1094.7 | 1051.421
4318 | 0.43291 | 75.19 | 62.257 | 0.0013609 | 43.289 | 1094.7 |  | 4318 | 75.19 | 0.43291 | 62.257 | 0.0013609 | 43.289 | 1094.7 | 1051.411
4319 | 0.43305 | 75.2 | 62.257 | 0.0013613 | 43.299 | 1094.8 |  | 4319 | 75.2 | 0.43305 | 62.257 | 0.0013613 | 43.299 | 1094.8 | 1051.501
4320 | 0.4332 | 75.21 | 62.257 | 0.0013618 | 43.309 | 1094.8 |  | 4320 | 75.21 | 0.4332 | 62.257 | 0.0013618 | 43.309 | 1094.8 | 1051.491
4321 | 0.43334 | 75.22 | 62.256 | 0.0013622 | 43.319 | 1094.8 |  | 4321 | 75.22 | 0.43334 | 62.256 | 0.0013622 | 43.319 | 1094.8 | 1051.481
4322 | 0.43349 | 75.23 | 62.256 | 0.0013626 | 43.329 | 1094.8 |  | 4322 | 75.23 | 0.43349 | 62.256 | 0.0013626 | 43.329 | 1094.8 | 1051.471
4323 | 0.43363 | 75.24 | 62.256 | 0.001363 | 43.339 | 1094.8 |  | 4323 | 75.24 | 0.43363 | 62.256 | 0.001363 | 43.339 | 1094.8 | 1051.461
4324 | 0.43378 | 75.25 | 62.256 | 0.0013635 | 43.349 | 1094.8 |  | 4324 | 75.25 | 0.43378 | 62.256 | 0.0013635 | 43.349 | 1094.8 | 1051.451
4325 | 0.43392 | 75.26 | 62.256 | 0.0013639 | 43.359 | 1094.8 |  | 4325 | 75.26 | 0.43392 | 62.256 | 0.0013639 | 43.359 | 1094.8 | 1051.441
4326 | 0.43407 | 75.27 | 62.256 | 0.0013643 | 43.369 | 1094.8 |  | 4326 | 75.27 | 0.43407 | 62.256 | 0.0013643 | 43.369 | 1094.8 | 1051.431
4327 | 0.43421 | 75.28 | 62.256 | 0.0013648 | 43.379 | 1094.8 |  | 4327 | 75.28 | 0.43421 | 62.256 | 0.0013648 | 43.379 | 1094.8 | 1051.421
4328 | 0.43436 | 75.29 | 62.256 | 0.0013652 | 43.389 | 1094.8 |  | 4328 | 75.29 | 0.43436 | 62.256 | 0.0013652 | 43.389 | 1094.8 | 1051.411
4329 | 0.4345 | 75.3 | 62.256 | 0.0013656 | 43.399 | 1094.8 |  | 4329 | 75.3 | 0.4345 | 62.256 | 0.0013656 | 43.399 | 1094.8 | 1051.401
4330 | 0.43465 | 75.31 | 62.256 | 0.0013661 | 43.409 | 1094.8 |  | 4330 | 75.31 | 0.43465 | 62.256 | 0.0013661 | 43.409 | 1094.8 | 1051.391
4331 | 0.43479 | 75.32 | 62.256 | 0.0013665 | 43.419 | 1094.8 |  | 4331 | 75.32 | 0.43479 | 62.256 | 0.0013665 | 43.419 | 1094.8 | 1051.381
4332 | 0.43494 | 75.33 | 62.255 | 0.0013669 | 43.429 | 1094.8 |  | 4332 | 75.33 | 0.43494 | 62.255 | 0.0013669 | 43.429 | 1094.8 | 1051.371
4333 | 0.43508 | 75.34 | 62.255 | 0.0013673 | 43.439 | 1094.8 |  | 4333 | 75.34 | 0.43508 | 62.255 | 0.0013673 | 43.439 | 1094.8 | 1051.361
4334 | 0.43523 | 75.35 | 62.255 | 0.0013678 | 43.449 | 1094.8 |  | 4334 | 75.35 | 0.43523 | 62.255 | 0.0013678 | 43.449 | 1094.8 | 1051.351
4335 | 0.43537 | 75.36 | 62.255 | 0.0013682 | 43.459 | 1094.8 |  | 4335 | 75.36 | 0.43537 | 62.255 | 0.0013682 | 43.459 | 1094.8 | 1051.341
4336 | 0.43552 | 75.37 | 62.255 | 0.0013686 | 43.469 | 1094.8 |  | 4336 | 75.37 | 0.43552 | 62.255 | 0.0013686 | 43.469 | 1094.8 | 1051.331
4337 | 0.43566 | 75.38 | 62.255 | 0.0013691 | 43.479 | 1094.8 |  | 4337 | 75.38 | 0.43566 | 62.255 | 0.0013691 | 43.479 | 1094.8 | 1051.321
4338 | 0.43581 | 75.39 | 62.255 | 0.0013695 | 43.489 | 1094.8 |  | 4338 | 75.39 | 0.43581 | 62.255 | 0.0013695 | 43.489 | 1094.8 | 1051.311
4339 | 0.43595 | 75.4 | 62.255 | 0.0013699 | 43.499 | 1094.8 |  | 4339 | 75.4 | 0.43595 | 62.255 | 0.0013699 | 43.499 | 1094.8 | 1051.301
4340 | 0.4361 | 75.41 | 62.255 | 0.0013704 | 43.509 | 1094.8 |  | 4340 | 75.41 | 0.4361 | 62.255 | 0.0013704 | 43.509 | 1094.8 | 1051.291
4341 | 0.43624 | 75.42 | 62.255 | 0.0013708 | 43.519 | 1094.8 |  | 4341 | 75.42 | 0.43624 | 62.255 | 0.0013708 | 43.519 | 1094.8 | 1051.281
4342 | 0.43639 | 75.43 | 62.255 | 0.0013712 | 43.529 | 1094.9 |  | 4342 | 75.43 | 0.43639 | 62.255 | 0.0013712 | 43.529 | 1094.9 | 1051.371
4343 | 0.43653 | 75.44 | 62.255 | 0.0013717 | 43.539 | 1094.9 |  | 4343 | 75.44 | 0.43653 | 62.255 | 0.0013717 | 43.539 | 1094.9 | 1051.361
4344 | 0.43668 | 75.45 | 62.254 | 0.0013721 | 43.549 | 1094.9 |  | 4344 | 75.45 | 0.43668 | 62.254 | 0.0013721 | 43.549 | 1094.9 | 1051.351
4345 | 0.43683 | 75.46 | 62.254 | 0.0013725 | 43.559 | 1094.9 |  | 4345 | 75.46 | 0.43683 | 62.254 | 0.0013725 | 43.559 | 1094.9 | 1051.341
4346 | 0.43697 | 75.47 | 62.254 | 0.001373 | 43.569 | 1094.9 |  | 4346 | 75.47 | 0.43697 | 62.254 | 0.001373 | 43.569 | 1094.9 | 1051.331
4347 | 0.43712 | 75.48 | 62.254 | 0.0013734 | 43.579 | 1094.9 |  | 4347 | 75.48 | 0.43712 | 62.254 | 0.0013734 | 43.579 | 1094.9 | 1051.321
4348 | 0.43726 | 75.49 | 62.254 | 0.0013738 | 43.589 | 1094.9 |  | 4348 | 75.49 | 0.43726 | 62.254 | 0.0013738 | 43.589 | 1094.9 | 1051.311
4349 | 0.43741 | 75.5 | 62.254 | 0.0013743 | 43.599 | 1094.9 |  | 4349 | 75.5 | 0.43741 | 62.254 | 0.0013743 | 43.599 | 1094.9 | 1051.301
4350 | 0.43755 | 75.51 | 62.254 | 0.0013747 | 43.609 | 1094.9 |  | 4350 | 75.51 | 0.43755 | 62.254 | 0.0013747 | 43.609 | 1094.9 | 1051.291
4351 | 0.4377 | 75.52 | 62.254 | 0.0013751 | 43.619 | 1094.9 |  | 4351 | 75.52 | 0.4377 | 62.254 | 0.0013751 | 43.619 | 1094.9 | 1051.281
4352 | 0.43785 | 75.53 | 62.254 | 0.0013756 | 43.629 | 1094.9 |  | 4352 | 75.53 | 0.43785 | 62.254 | 0.0013756 | 43.629 | 1094.9 | 1051.271
4353 | 0.43799 | 75.54 | 62.254 | 0.001376 | 43.639 | 1094.9 |  | 4353 | 75.54 | 0.43799 | 62.254 | 0.001376 | 43.639 | 1094.9 | 1051.261
4354 | 0.43814 | 75.55 | 62.254 | 0.0013764 | 43.649 | 1094.9 |  | 4354 | 75.55 | 0.43814 | 62.254 | 0.0013764 | 43.649 | 1094.9 | 1051.251
4355 | 0.43828 | 75.56 | 62.253 | 0.0013769 | 43.659 | 1094.9 |  | 4355 | 75.56 | 0.43828 | 62.253 | 0.0013769 | 43.659 | 1094.9 | 1051.241
4356 | 0.43843 | 75.57 | 62.253 | 0.0013773 | 43.669 | 1094.9 |  | 4356 | 75.57 | 0.43843 | 62.253 | 0.0013773 | 43.669 | 1094.9 | 1051.231
4357 | 0.43858 | 75.58 | 62.253 | 0.0013777 | 43.679 | 1094.9 |  | 4357 | 75.58 | 0.43858 | 62.253 | 0.0013777 | 43.679 | 1094.9 | 1051.221
4358 | 0.43872 | 75.59 | 62.253 | 0.0013782 | 43.689 | 1094.9 |  | 4358 | 75.59 | 0.43872 | 62.253 | 0.0013782 | 43.689 | 1094.9 | 1051.211
4359 | 0.43887 | 75.6 | 62.253 | 0.0013786 | 43.699 | 1094.9 |  | 4359 | 75.6 | 0.43887 | 62.253 | 0.0013786 | 43.699 | 1094.9 | 1051.201
4360 | 0.43901 | 75.61 | 62.253 | 0.001379 | 43.709 | 1094.9 |  | 4360 | 75.61 | 0.43901 | 62.253 | 0.001379 | 43.709 | 1094.9 | 1051.191
4361 | 0.43916 | 75.62 | 62.253 | 0.0013795 | 43.719 | 1094.9 |  | 4361 | 75.62 | 0.43916 | 62.253 | 0.0013795 | 43.719 | 1094.9 | 1051.181
4362 | 0.43931 | 75.63 | 62.253 | 0.0013799 | 43.729 | 1094.9 |  | 4362 | 75.63 | 0.43931 | 62.253 | 0.0013799 | 43.729 | 1094.9 | 1051.171
4363 | 0.43945 | 75.64 | 62.253 | 0.0013803 | 43.739 | 1094.9 |  | 4363 | 75.64 | 0.43945 | 62.253 | 0.0013803 | 43.739 | 1094.9 | 1051.161
4364 | 0.4396 | 75.65 | 62.253 | 0.0013808 | 43.749 | 1094.9 |  | 4364 | 75.65 | 0.4396 | 62.253 | 0.0013808 | 43.749 | 1094.9 | 1051.151
4365 | 0.43975 | 75.66 | 62.253 | 0.0013812 | 43.759 | 1095 |  | 4365 | 75.66 | 0.43975 | 62.253 | 0.0013812 | 43.759 | 1095 | 1051.241
4366 | 0.43989 | 75.67 | 62.253 | 0.0013816 | 43.769 | 1095 |  | 4366 | 75.67 | 0.43989 | 62.253 | 0.0013816 | 43.769 | 1095 | 1051.231
4367 | 0.44004 | 75.68 | 62.252 | 0.0013821 | 43.779 | 1095 |  | 4367 | 75.68 | 0.44004 | 62.252 | 0.0013821 | 43.779 | 1095 | 1051.221
4368 | 0.44019 | 75.69 | 62.252 | 0.0013825 | 43.789 | 1095 |  | 4368 | 75.69 | 0.44019 | 62.252 | 0.0013825 | 43.789 | 1095 | 1051.211
4369 | 0.44033 | 75.7 | 62.252 | 0.0013829 | 43.799 | 1095 |  | 4369 | 75.7 | 0.44033 | 62.252 | 0.0013829 | 43.799 | 1095 | 1051.201
4370 | 0.44048 | 75.71 | 62.252 | 0.0013834 | 43.809 | 1095 |  | 4370 | 75.71 | 0.44048 | 62.252 | 0.0013834 | 43.809 | 1095 | 1051.191
4371 | 0.44063 | 75.72 | 62.252 | 0.0013838 | 43.819 | 1095 |  | 4371 | 75.72 | 0.44063 | 62.252 | 0.0013838 | 43.819 | 1095 | 1051.181
4372 | 0.44077 | 75.73 | 62.252 | 0.0013842 | 43.829 | 1095 |  | 4372 | 75.73 | 0.44077 | 62.252 | 0.0013842 | 43.829 | 1095 | 1051.171
4373 | 0.44092 | 75.74 | 62.252 | 0.0013847 | 43.839 | 1095 |  | 4373 | 75.74 | 0.44092 | 62.252 | 0.0013847 | 43.839 | 1095 | 1051.161
4374 | 0.44107 | 75.75 | 62.252 | 0.0013851 | 43.849 | 1095 |  | 4374 | 75.75 | 0.44107 | 62.252 | 0.0013851 | 43.849 | 1095 | 1051.151
4375 | 0.44121 | 75.76 | 62.252 | 0.0013855 | 43.859 | 1095 |  | 4375 | 75.76 | 0.44121 | 62.252 | 0.0013855 | 43.859 | 1095 | 1051.141
4376 | 0.44136 | 75.77 | 62.252 | 0.001386 | 43.869 | 1095 |  | 4376 | 75.77 | 0.44136 | 62.252 | 0.001386 | 43.869 | 1095 | 1051.131
4377 | 0.44151 | 75.78 | 62.252 | 0.0013864 | 43.879 | 1095 |  | 4377 | 75.78 | 0.44151 | 62.252 | 0.0013864 | 43.879 | 1095 | 1051.121
4378 | 0.44165 | 75.79 | 62.252 | 0.0013869 | 43.889 | 1095 |  | 4378 | 75.79 | 0.44165 | 62.252 | 0.0013869 | 43.889 | 1095 | 1051.111
4379 | 0.4418 | 75.8 | 62.251 | 0.0013873 | 43.899 | 1095 |  | 4379 | 75.8 | 0.4418 | 62.251 | 0.0013873 | 43.899 | 1095 | 1051.101
4380 | 0.44195 | 75.81 | 62.251 | 0.0013877 | 43.909 | 1095 |  | 4380 | 75.81 | 0.44195 | 62.251 | 0.0013877 | 43.909 | 1095 | 1051.091
4381 | 0.4421 | 75.82 | 62.251 | 0.0013882 | 43.919 | 1095 |  | 4381 | 75.82 | 0.4421 | 62.251 | 0.0013882 | 43.919 | 1095 | 1051.081
4382 | 0.44224 | 75.83 | 62.251 | 0.0013886 | 43.929 | 1095 |  | 4382 | 75.83 | 0.44224 | 62.251 | 0.0013886 | 43.929 | 1095 | 1051.071
4383 | 0.44239 | 75.84 | 62.251 | 0.001389 | 43.939 | 1095 |  | 4383 | 75.84 | 0.44239 | 62.251 | 0.001389 | 43.939 | 1095 | 1051.061
4384 | 0.44254 | 75.85 | 62.251 | 0.0013895 | 43.949 | 1095 |  | 4384 | 75.85 | 0.44254 | 62.251 | 0.0013895 | 43.949 | 1095 | 1051.051
4385 | 0.44268 | 75.86 | 62.251 | 0.0013899 | 43.959 | 1095 |  | 4385 | 75.86 | 0.44268 | 62.251 | 0.0013899 | 43.959 | 1095 | 1051.041
4386 | 0.44283 | 75.87 | 62.251 | 0.0013903 | 43.969 | 1095 |  | 4386 | 75.87 | 0.44283 | 62.251 | 0.0013903 | 43.969 | 1095 | 1051.031
4387 | 0.44298 | 75.88 | 62.251 | 0.0013908 | 43.979 | 1095 |  | 4387 | 75.88 | 0.44298 | 62.251 | 0.0013908 | 43.979 | 1095 | 1051.021
4388 | 0.44313 | 75.89 | 62.251 | 0.0013912 | 43.989 | 1095.1 |  | 4388 | 75.89 | 0.44313 | 62.251 | 0.0013912 | 43.989 | 1095.1 | 1051.111
4389 | 0.44327 | 75.9 | 62.251 | 0.0013917 | 43.999 | 1095.1 |  | 4389 | 75.9 | 0.44327 | 62.251 | 0.0013917 | 43.999 | 1095.1 | 1051.101
4390 | 0.44342 | 75.91 | 62.25 | 0.0013921 | 44.009 | 1095.1 |  | 4390 | 75.91 | 0.44342 | 62.25 | 0.0013921 | 44.009 | 1095.1 | 1051.091
4391 | 0.44357 | 75.92 | 62.25 | 0.0013925 | 44.019 | 1095.1 |  | 4391 | 75.92 | 0.44357 | 62.25 | 0.0013925 | 44.019 | 1095.1 | 1051.081
4392 | 0.44372 | 75.93 | 62.25 | 0.001393 | 44.029 | 1095.1 |  | 4392 | 75.93 | 0.44372 | 62.25 | 0.001393 | 44.029 | 1095.1 | 1051.071
4393 | 0.44386 | 75.94 | 62.25 | 0.0013934 | 44.039 | 1095.1 |  | 4393 | 75.94 | 0.44386 | 62.25 | 0.0013934 | 44.039 | 1095.1 | 1051.061
4394 | 0.44401 | 75.95 | 62.25 | 0.0013938 | 44.049 | 1095.1 |  | 4394 | 75.95 | 0.44401 | 62.25 | 0.0013938 | 44.049 | 1095.1 | 1051.051
4395 | 0.44416 | 75.96 | 62.25 | 0.0013943 | 44.059 | 1095.1 |  | 4395 | 75.96 | 0.44416 | 62.25 | 0.0013943 | 44.059 | 1095.1 | 1051.041
4396 | 0.44431 | 75.97 | 62.25 | 0.0013947 | 44.069 | 1095.1 |  | 4396 | 75.97 | 0.44431 | 62.25 | 0.0013947 | 44.069 | 1095.1 | 1051.031
4397 | 0.44445 | 75.98 | 62.25 | 0.0013952 | 44.079 | 1095.1 |  | 4397 | 75.98 | 0.44445 | 62.25 | 0.0013952 | 44.079 | 1095.1 | 1051.021
4398 | 0.4446 | 75.99 | 62.25 | 0.0013956 | 44.089 | 1095.1 |  | 4398 | 75.99 | 0.4446 | 62.25 | 0.0013956 | 44.089 | 1095.1 | 1051.011
4399 | 0.44475 | 76 | 62.25 | 0.001396 | 44.099 | 1095.1 |  | 4399 | 76 | 0.44475 | 62.25 | 0.001396 | 44.099 | 1095.1 | 1051.001
4400 | 0.4449 | 76.01 | 62.25 | 0.0013965 | 44.109 | 1095.1 |  | 4400 | 76.01 | 0.4449 | 62.25 | 0.0013965 | 44.109 | 1095.1 | 1050.991
4401 | 0.44505 | 76.02 | 62.25 | 0.0013969 | 44.119 | 1095.1 |  | 4401 | 76.02 | 0.44505 | 62.25 | 0.0013969 | 44.119 | 1095.1 | 1050.981
4402 | 0.44519 | 76.03 | 62.249 | 0.0013974 | 44.129 | 1095.1 |  | 4402 | 76.03 | 0.44519 | 62.249 | 0.0013974 | 44.129 | 1095.1 | 1050.971
4403 | 0.44534 | 76.04 | 62.249 | 0.0013978 | 44.139 | 1095.1 |  | 4403 | 76.04 | 0.44534 | 62.249 | 0.0013978 | 44.139 | 1095.1 | 1050.961
4404 | 0.44549 | 76.05 | 62.249 | 0.0013982 | 44.149 | 1095.1 |  | 4404 | 76.05 | 0.44549 | 62.249 | 0.0013982 | 44.149 | 1095.1 | 1050.951
4405 | 0.44564 | 76.06 | 62.249 | 0.0013987 | 44.159 | 1095.1 |  | 4405 | 76.06 | 0.44564 | 62.249 | 0.0013987 | 44.159 | 1095.1 | 1050.941
4406 | 0.44579 | 76.07 | 62.249 | 0.0013991 | 44.169 | 1095.1 |  | 4406 | 76.07 | 0.44579 | 62.249 | 0.0013991 | 44.169 | 1095.1 | 1050.931
4407 | 0.44594 | 76.08 | 62.249 | 0.0013996 | 44.179 | 1095.1 |  | 4407 | 76.08 | 0.44594 | 62.249 | 0.0013996 | 44.179 | 1095.1 | 1050.921
4408 | 0.44608 | 76.09 | 62.249 | 0.0014 | 44.189 | 1095.1 |  | 4408 | 76.09 | 0.44608 | 62.249 | 0.0014 | 44.189 | 1095.1 | 1050.911
4409 | 0.44623 | 76.1 | 62.249 | 0.0014004 | 44.199 | 1095.1 |  | 4409 | 76.1 | 0.44623 | 62.249 | 0.0014004 | 44.199 | 1095.1 | 1050.901
4410 | 0.44638 | 76.11 | 62.249 | 0.0014009 | 44.209 | 1095.1 |  | 4410 | 76.11 | 0.44638 | 62.249 | 0.0014009 | 44.209 | 1095.1 | 1050.891
4411 | 0.44653 | 76.12 | 62.249 | 0.0014013 | 44.219 | 1095.2 |  | 4411 | 76.12 | 0.44653 | 62.249 | 0.0014013 | 44.219 | 1095.2 | 1050.981
4412 | 0.44668 | 76.13 | 62.249 | 0.0014018 | 44.229 | 1095.2 |  | 4412 | 76.13 | 0.44668 | 62.249 | 0.0014018 | 44.229 | 1095.2 | 1050.971
4413 | 0.44683 | 76.14 | 62.248 | 0.0014022 | 44.239 | 1095.2 |  | 4413 | 76.14 | 0.44683 | 62.248 | 0.0014022 | 44.239 | 1095.2 | 1050.961
4414 | 0.44697 | 76.15 | 62.248 | 0.0014026 | 44.249 | 1095.2 |  | 4414 | 76.15 | 0.44697 | 62.248 | 0.0014026 | 44.249 | 1095.2 | 1050.951
4415 | 0.44712 | 76.16 | 62.248 | 0.0014031 | 44.259 | 1095.2 |  | 4415 | 76.16 | 0.44712 | 62.248 | 0.0014031 | 44.259 | 1095.2 | 1050.941
4416 | 0.44727 | 76.17 | 62.248 | 0.0014035 | 44.269 | 1095.2 |  | 4416 | 76.17 | 0.44727 | 62.248 | 0.0014035 | 44.269 | 1095.2 | 1050.931
4417 | 0.44742 | 76.18 | 62.248 | 0.001404 | 44.279 | 1095.2 |  | 4417 | 76.18 | 0.44742 | 62.248 | 0.001404 | 44.279 | 1095.2 | 1050.921
4418 | 0.44757 | 76.19 | 62.248 | 0.0014044 | 44.289 | 1095.2 |  | 4418 | 76.19 | 0.44757 | 62.248 | 0.0014044 | 44.289 | 1095.2 | 1050.911
4419 | 0.44772 | 76.2 | 62.248 | 0.0014048 | 44.299 | 1095.2 |  | 4419 | 76.2 | 0.44772 | 62.248 | 0.0014048 | 44.299 | 1095.2 | 1050.901
4420 | 0.44787 | 76.21 | 62.248 | 0.0014053 | 44.309 | 1095.2 |  | 4420 | 76.21 | 0.44787 | 62.248 | 0.0014053 | 44.309 | 1095.2 | 1050.891
4421 | 0.44802 | 76.22 | 62.248 | 0.0014057 | 44.319 | 1095.2 |  | 4421 | 76.22 | 0.44802 | 62.248 | 0.0014057 | 44.319 | 1095.2 | 1050.881
4422 | 0.44816 | 76.23 | 62.248 | 0.0014062 | 44.329 | 1095.2 |  | 4422 | 76.23 | 0.44816 | 62.248 | 0.0014062 | 44.329 | 1095.2 | 1050.871
4423 | 0.44831 | 76.24 | 62.248 | 0.0014066 | 44.339 | 1095.2 |  | 4423 | 76.24 | 0.44831 | 62.248 | 0.0014066 | 44.339 | 1095.2 | 1050.861
4424 | 0.44846 | 76.25 | 62.248 | 0.001407 | 44.349 | 1095.2 |  | 4424 | 76.25 | 0.44846 | 62.248 | 0.001407 | 44.349 | 1095.2 | 1050.851
4425 | 0.44861 | 76.26 | 62.247 | 0.0014075 | 44.359 | 1095.2 |  | 4425 | 76.26 | 0.44861 | 62.247 | 0.0014075 | 44.359 | 1095.2 | 1050.841
4426 | 0.44876 | 76.27 | 62.247 | 0.0014079 | 44.369 | 1095.2 |  | 4426 | 76.27 | 0.44876 | 62.247 | 0.0014079 | 44.369 | 1095.2 | 1050.831
4427 | 0.44891 | 76.28 | 62.247 | 0.0014084 | 44.379 | 1095.2 |  | 4427 | 76.28 | 0.44891 | 62.247 | 0.0014084 | 44.379 | 1095.2 | 1050.821
4428 | 0.44906 | 76.29 | 62.247 | 0.0014088 | 44.389 | 1095.2 |  | 4428 | 76.29 | 0.44906 | 62.247 | 0.0014088 | 44.389 | 1095.2 | 1050.811
4429 | 0.44921 | 76.3 | 62.247 | 0.0014093 | 44.399 | 1095.2 |  | 4429 | 76.3 | 0.44921 | 62.247 | 0.0014093 | 44.399 | 1095.2 | 1050.801
4430 | 0.44936 | 76.31 | 62.247 | 0.0014097 | 44.409 | 1095.2 |  | 4430 | 76.31 | 0.44936 | 62.247 | 0.0014097 | 44.409 | 1095.2 | 1050.791
4431 | 0.44951 | 76.32 | 62.247 | 0.0014101 | 44.419 | 1095.2 |  | 4431 | 76.32 | 0.44951 | 62.247 | 0.0014101 | 44.419 | 1095.2 | 1050.781
4432 | 0.44966 | 76.33 | 62.247 | 0.0014106 | 44.429 | 1095.2 |  | 4432 | 76.33 | 0.44966 | 62.247 | 0.0014106 | 44.429 | 1095.2 | 1050.771
4433 | 0.4498 | 76.34 | 62.247 | 0.001411 | 44.439 | 1095.2 |  | 4433 | 76.34 | 0.4498 | 62.247 | 0.001411 | 44.439 | 1095.2 | 1050.761
4434 | 0.44995 | 76.35 | 62.247 | 0.0014115 | 44.449 | 1095.3 |  | 4434 | 76.35 | 0.44995 | 62.247 | 0.0014115 | 44.449 | 1095.3 | 1050.851
4435 | 0.4501 | 76.36 | 62.247 | 0.0014119 | 44.459 | 1095.3 |  | 4435 | 76.36 | 0.4501 | 62.247 | 0.0014119 | 44.459 | 1095.3 | 1050.841
4436 | 0.45025 | 76.37 | 62.246 | 0.0014124 | 44.469 | 1095.3 |  | 4436 | 76.37 | 0.45025 | 62.246 | 0.0014124 | 44.469 | 1095.3 | 1050.831
4437 | 0.4504 | 76.38 | 62.246 | 0.0014128 | 44.479 | 1095.3 |  | 4437 | 76.38 | 0.4504 | 62.246 | 0.0014128 | 44.479 | 1095.3 | 1050.821
4438 | 0.45055 | 76.39 | 62.246 | 0.0014132 | 44.489 | 1095.3 |  | 4438 | 76.39 | 0.45055 | 62.246 | 0.0014132 | 44.489 | 1095.3 | 1050.811
4439 | 0.4507 | 76.4 | 62.246 | 0.0014137 | 44.499 | 1095.3 |  | 4439 | 76.4 | 0.4507 | 62.246 | 0.0014137 | 44.499 | 1095.3 | 1050.801
4440 | 0.45085 | 76.41 | 62.246 | 0.0014141 | 44.509 | 1095.3 |  | 4440 | 76.41 | 0.45085 | 62.246 | 0.0014141 | 44.509 | 1095.3 | 1050.791
4441 | 0.451 | 76.42 | 62.246 | 0.0014146 | 44.519 | 1095.3 |  | 4441 | 76.42 | 0.451 | 62.246 | 0.0014146 | 44.519 | 1095.3 | 1050.781
4442 | 0.45115 | 76.43 | 62.246 | 0.001415 | 44.529 | 1095.3 |  | 4442 | 76.43 | 0.45115 | 62.246 | 0.001415 | 44.529 | 1095.3 | 1050.771
4443 | 0.4513 | 76.44 | 62.246 | 0.0014155 | 44.539 | 1095.3 |  | 4443 | 76.44 | 0.4513 | 62.246 | 0.0014155 | 44.539 | 1095.3 | 1050.761
4444 | 0.45145 | 76.45 | 62.246 | 0.0014159 | 44.549 | 1095.3 |  | 4444 | 76.45 | 0.45145 | 62.246 | 0.0014159 | 44.549 | 1095.3 | 1050.751
4445 | 0.4516 | 76.46 | 62.246 | 0.0014163 | 44.559 | 1095.3 |  | 4445 | 76.46 | 0.4516 | 62.246 | 0.0014163 | 44.559 | 1095.3 | 1050.741
4446 | 0.45175 | 76.47 | 62.246 | 0.0014168 | 44.569 | 1095.3 |  | 4446 | 76.47 | 0.45175 | 62.246 | 0.0014168 | 44.569 | 1095.3 | 1050.731
4447 | 0.4519 | 76.48 | 62.245 | 0.0014172 | 44.579 | 1095.3 |  | 4447 | 76.48 | 0.4519 | 62.245 | 0.0014172 | 44.579 | 1095.3 | 1050.721
4448 | 0.45205 | 76.49 | 62.245 | 0.0014177 | 44.589 | 1095.3 |  | 4448 | 76.49 | 0.45205 | 62.245 | 0.0014177 | 44.589 | 1095.3 | 1050.711
4449 | 0.4522 | 76.5 | 62.245 | 0.0014181 | 44.599 | 1095.3 |  | 4449 | 76.5 | 0.4522 | 62.245 | 0.0014181 | 44.599 | 1095.3 | 1050.701
4450 | 0.45235 | 76.51 | 62.245 | 0.0014186 | 44.609 | 1095.3 |  | 4450 | 76.51 | 0.45235 | 62.245 | 0.0014186 | 44.609 | 1095.3 | 1050.691
4451 | 0.4525 | 76.52 | 62.245 | 0.001419 | 44.619 | 1095.3 |  | 4451 | 76.52 | 0.4525 | 62.245 | 0.001419 | 44.619 | 1095.3 | 1050.681
4452 | 0.45265 | 76.53 | 62.245 | 0.0014195 | 44.629 | 1095.3 |  | 4452 | 76.53 | 0.45265 | 62.245 | 0.0014195 | 44.629 | 1095.3 | 1050.671
4453 | 0.4528 | 76.54 | 62.245 | 0.0014199 | 44.639 | 1095.3 |  | 4453 | 76.54 | 0.4528 | 62.245 | 0.0014199 | 44.639 | 1095.3 | 1050.661
4454 | 0.45295 | 76.55 | 62.245 | 0.0014204 | 44.649 | 1095.3 |  | 4454 | 76.55 | 0.45295 | 62.245 | 0.0014204 | 44.649 | 1095.3 | 1050.651
4455 | 0.4531 | 76.56 | 62.245 | 0.0014208 | 44.659 | 1095.3 |  | 4455 | 76.56 | 0.4531 | 62.245 | 0.0014208 | 44.659 | 1095.3 | 1050.641
4456 | 0.45325 | 76.57 | 62.245 | 0.0014212 | 44.669 | 1095.3 |  | 4456 | 76.57 | 0.45325 | 62.245 | 0.0014212 | 44.669 | 1095.3 | 1050.631
4457 | 0.4534 | 76.58 | 62.245 | 0.0014217 | 44.679 | 1095.4 |  | 4457 | 76.58 | 0.4534 | 62.245 | 0.0014217 | 44.679 | 1095.4 | 1050.721
4458 | 0.45355 | 76.59 | 62.245 | 0.0014221 | 44.689 | 1095.4 |  | 4458 | 76.59 | 0.45355 | 62.245 | 0.0014221 | 44.689 | 1095.4 | 1050.711
4459 | 0.4537 | 76.6 | 62.244 | 0.0014226 | 44.699 | 1095.4 |  | 4459 | 76.6 | 0.4537 | 62.244 | 0.0014226 | 44.699 | 1095.4 | 1050.701
4460 | 0.45385 | 76.61 | 62.244 | 0.001423 | 44.709 | 1095.4 |  | 4460 | 76.61 | 0.45385 | 62.244 | 0.001423 | 44.709 | 1095.4 | 1050.691
4461 | 0.454 | 76.62 | 62.244 | 0.0014235 | 44.719 | 1095.4 |  | 4461 | 76.62 | 0.454 | 62.244 | 0.0014235 | 44.719 | 1095.4 | 1050.681
4462 | 0.45416 | 76.63 | 62.244 | 0.0014239 | 44.729 | 1095.4 |  | 4462 | 76.63 | 0.45416 | 62.244 | 0.0014239 | 44.729 | 1095.4 | 1050.671
4463 | 0.45431 | 76.64 | 62.244 | 0.0014244 | 44.739 | 1095.4 |  | 4463 | 76.64 | 0.45431 | 62.244 | 0.0014244 | 44.739 | 1095.4 | 1050.661
4464 | 0.45446 | 76.65 | 62.244 | 0.0014248 | 44.749 | 1095.4 |  | 4464 | 76.65 | 0.45446 | 62.244 | 0.0014248 | 44.749 | 1095.4 | 1050.651
4465 | 0.45461 | 76.66 | 62.244 | 0.0014253 | 44.759 | 1095.4 |  | 4465 | 76.66 | 0.45461 | 62.244 | 0.0014253 | 44.759 | 1095.4 | 1050.641
4466 | 0.45476 | 76.67 | 62.244 | 0.0014257 | 44.769 | 1095.4 |  | 4466 | 76.67 | 0.45476 | 62.244 | 0.0014257 | 44.769 | 1095.4 | 1050.631
4467 | 0.45491 | 76.68 | 62.244 | 0.0014262 | 44.779 | 1095.4 |  | 4467 | 76.68 | 0.45491 | 62.244 | 0.0014262 | 44.779 | 1095.4 | 1050.621
4468 | 0.45506 | 76.69 | 62.244 | 0.0014266 | 44.789 | 1095.4 |  | 4468 | 76.69 | 0.45506 | 62.244 | 0.0014266 | 44.789 | 1095.4 | 1050.611
4469 | 0.45521 | 76.7 | 62.244 | 0.001427 | 44.799 | 1095.4 |  | 4469 | 76.7 | 0.45521 | 62.244 | 0.001427 | 44.799 | 1095.4 | 1050.601
4470 | 0.45536 | 76.71 | 62.243 | 0.0014275 | 44.809 | 1095.4 |  | 4470 | 76.71 | 0.45536 | 62.243 | 0.0014275 | 44.809 | 1095.4 | 1050.591
4471 | 0.45551 | 76.72 | 62.243 | 0.0014279 | 44.819 | 1095.4 |  | 4471 | 76.72 | 0.45551 | 62.243 | 0.0014279 | 44.819 | 1095.4 | 1050.581
4472 | 0.45566 | 76.73 | 62.243 | 0.0014284 | 44.829 | 1095.4 |  | 4472 | 76.73 | 0.45566 | 62.243 | 0.0014284 | 44.829 | 1095.4 | 1050.571
4473 | 0.45582 | 76.74 | 62.243 | 0.0014288 | 44.839 | 1095.4 |  | 4473 | 76.74 | 0.45582 | 62.243 | 0.0014288 | 44.839 | 1095.4 | 1050.561
4474 | 0.45597 | 76.75 | 62.243 | 0.0014293 | 44.849 | 1095.4 |  | 4474 | 76.75 | 0.45597 | 62.243 | 0.0014293 | 44.849 | 1095.4 | 1050.551
4475 | 0.45612 | 76.76 | 62.243 | 0.0014297 | 44.859 | 1095.4 |  | 4475 | 76.76 | 0.45612 | 62.243 | 0.0014297 | 44.859 | 1095.4 | 1050.541
4476 | 0.45627 | 76.77 | 62.243 | 0.0014302 | 44.869 | 1095.4 |  | 4476 | 76.77 | 0.45627 | 62.243 | 0.0014302 | 44.869 | 1095.4 | 1050.531
4477 | 0.45642 | 76.78 | 62.243 | 0.0014306 | 44.879 | 1095.4 |  | 4477 | 76.78 | 0.45642 | 62.243 | 0.0014306 | 44.879 | 1095.4 | 1050.521
4478 | 0.45657 | 76.79 | 62.243 | 0.0014311 | 44.889 | 1095.4 |  | 4478 | 76.79 | 0.45657 | 62.243 | 0.0014311 | 44.889 | 1095.4 | 1050.511
4479 | 0.45672 | 76.8 | 62.243 | 0.0014315 | 44.899 | 1095.4 |  | 4479 | 76.8 | 0.45672 | 62.243 | 0.0014315 | 44.899 | 1095.4 | 1050.501
4480 | 0.45687 | 76.81 | 62.243 | 0.001432 | 44.909 | 1095.5 |  | 4480 | 76.81 | 0.45687 | 62.243 | 0.001432 | 44.909 | 1095.5 | 1050.591
4481 | 0.45703 | 76.82 | 62.242 | 0.0014324 | 44.919 | 1095.5 |  | 4481 | 76.82 | 0.45703 | 62.242 | 0.0014324 | 44.919 | 1095.5 | 1050.581
4482 | 0.45718 | 76.83 | 62.242 | 0.0014329 | 44.929 | 1095.5 |  | 4482 | 76.83 | 0.45718 | 62.242 | 0.0014329 | 44.929 | 1095.5 | 1050.571
4483 | 0.45733 | 76.84 | 62.242 | 0.0014333 | 44.939 | 1095.5 |  | 4483 | 76.84 | 0.45733 | 62.242 | 0.0014333 | 44.939 | 1095.5 | 1050.561
4484 | 0.45748 | 76.85 | 62.242 | 0.0014338 | 44.949 | 1095.5 |  | 4484 | 76.85 | 0.45748 | 62.242 | 0.0014338 | 44.949 | 1095.5 | 1050.551
4485 | 0.45763 | 76.86 | 62.242 | 0.0014342 | 44.959 | 1095.5 |  | 4485 | 76.86 | 0.45763 | 62.242 | 0.0014342 | 44.959 | 1095.5 | 1050.541
4486 | 0.45778 | 76.87 | 62.242 | 0.0014347 | 44.969 | 1095.5 |  | 4486 | 76.87 | 0.45778 | 62.242 | 0.0014347 | 44.969 | 1095.5 | 1050.531
4487 | 0.45794 | 76.88 | 62.242 | 0.0014351 | 44.979 | 1095.5 |  | 4487 | 76.88 | 0.45794 | 62.242 | 0.0014351 | 44.979 | 1095.5 | 1050.521
4488 | 0.45809 | 76.89 | 62.242 | 0.0014356 | 44.989 | 1095.5 |  | 4488 | 76.89 | 0.45809 | 62.242 | 0.0014356 | 44.989 | 1095.5 | 1050.511
4489 | 0.45824 | 76.9 | 62.242 | 0.001436 | 44.999 | 1095.5 |  | 4489 | 76.9 | 0.45824 | 62.242 | 0.001436 | 44.999 | 1095.5 | 1050.501
4490 | 0.45839 | 76.91 | 62.242 | 0.0014365 | 45.009 | 1095.5 |  | 4490 | 76.91 | 0.45839 | 62.242 | 0.0014365 | 45.009 | 1095.5 | 1050.491
4491 | 0.45854 | 76.92 | 62.242 | 0.0014369 | 45.019 | 1095.5 |  | 4491 | 76.92 | 0.45854 | 62.242 | 0.0014369 | 45.019 | 1095.5 | 1050.481
4492 | 0.45869 | 76.93 | 62.242 | 0.0014374 | 45.029 | 1095.5 |  | 4492 | 76.93 | 0.45869 | 62.242 | 0.0014374 | 45.029 | 1095.5 | 1050.471
4493 | 0.45885 | 76.94 | 62.241 | 0.0014378 | 45.039 | 1095.5 |  | 4493 | 76.94 | 0.45885 | 62.241 | 0.0014378 | 45.039 | 1095.5 | 1050.461
4494 | 0.459 | 76.95 | 62.241 | 0.0014383 | 45.049 | 1095.5 |  | 4494 | 76.95 | 0.459 | 62.241 | 0.0014383 | 45.049 | 1095.5 | 1050.451
4495 | 0.45915 | 76.96 | 62.241 | 0.0014387 | 45.059 | 1095.5 |  | 4495 | 76.96 | 0.45915 | 62.241 | 0.0014387 | 45.059 | 1095.5 | 1050.441
4496 | 0.4593 | 76.97 | 62.241 | 0.0014392 | 45.069 | 1095.5 |  | 4496 | 76.97 | 0.4593 | 62.241 | 0.0014392 | 45.069 | 1095.5 | 1050.431
4497 | 0.45945 | 76.98 | 62.241 | 0.0014396 | 45.079 | 1095.5 |  | 4497 | 76.98 | 0.45945 | 62.241 | 0.0014396 | 45.079 | 1095.5 | 1050.421
4498 | 0.45961 | 76.99 | 62.241 | 0.0014401 | 45.089 | 1095.5 |  | 4498 | 76.99 | 0.45961 | 62.241 | 0.0014401 | 45.089 | 1095.5 | 1050.411
4499 | 0.45976 | 77 | 62.241 | 0.0014405 | 45.099 | 1095.5 |  | 4499 | 77 | 0.45976 | 62.241 | 0.0014405 | 45.099 | 1095.5 | 1050.401
4500 | 0.45991 | 77.01 | 62.241 | 0.001441 | 45.109 | 1095.5 |  | 4500 | 77.01 | 0.45991 | 62.241 | 0.001441 | 45.109 | 1095.5 | 1050.391
4501 | 0.46006 | 77.02 | 62.241 | 0.0014414 | 45.119 | 1095.5 |  | 4501 | 77.02 | 0.46006 | 62.241 | 0.0014414 | 45.119 | 1095.5 | 1050.381
4502 | 0.46022 | 77.03 | 62.241 | 0.0014419 | 45.129 | 1095.5 |  | 4502 | 77.03 | 0.46022 | 62.241 | 0.0014419 | 45.129 | 1095.5 | 1050.371
4503 | 0.46037 | 77.04 | 62.241 | 0.0014423 | 45.139 | 1095.6 |  | 4503 | 77.04 | 0.46037 | 62.241 | 0.0014423 | 45.139 | 1095.6 | 1050.461
4504 | 0.46052 | 77.05 | 62.24 | 0.0014428 | 45.149 | 1095.6 |  | 4504 | 77.05 | 0.46052 | 62.24 | 0.0014428 | 45.149 | 1095.6 | 1050.451
4505 | 0.46067 | 77.06 | 62.24 | 0.0014432 | 45.159 | 1095.6 |  | 4505 | 77.06 | 0.46067 | 62.24 | 0.0014432 | 45.159 | 1095.6 | 1050.441
4506 | 0.46083 | 77.07 | 62.24 | 0.0014437 | 45.169 | 1095.6 |  | 4506 | 77.07 | 0.46083 | 62.24 | 0.0014437 | 45.169 | 1095.6 | 1050.431
4507 | 0.46098 | 77.08 | 62.24 | 0.0014441 | 45.179 | 1095.6 |  | 4507 | 77.08 | 0.46098 | 62.24 | 0.0014441 | 45.179 | 1095.6 | 1050.421
4508 | 0.46113 | 77.09 | 62.24 | 0.0014446 | 45.189 | 1095.6 |  | 4508 | 77.09 | 0.46113 | 62.24 | 0.0014446 | 45.189 | 1095.6 | 1050.411
4509 | 0.46128 | 77.1 | 62.24 | 0.001445 | 45.199 | 1095.6 |  | 4509 | 77.1 | 0.46128 | 62.24 | 0.001445 | 45.199 | 1095.6 | 1050.401
4510 | 0.46144 | 77.11 | 62.24 | 0.0014455 | 45.209 | 1095.6 |  | 4510 | 77.11 | 0.46144 | 62.24 | 0.0014455 | 45.209 | 1095.6 | 1050.391
4511 | 0.46159 | 77.12 | 62.24 | 0.0014459 | 45.219 | 1095.6 |  | 4511 | 77.12 | 0.46159 | 62.24 | 0.0014459 | 45.219 | 1095.6 | 1050.381
4512 | 0.46174 | 77.13 | 62.24 | 0.0014464 | 45.229 | 1095.6 |  | 4512 | 77.13 | 0.46174 | 62.24 | 0.0014464 | 45.229 | 1095.6 | 1050.371
4513 | 0.4619 | 77.14 | 62.24 | 0.0014468 | 45.239 | 1095.6 |  | 4513 | 77.14 | 0.4619 | 62.24 | 0.0014468 | 45.239 | 1095.6 | 1050.361
4514 | 0.46205 | 77.15 | 62.24 | 0.0014473 | 45.249 | 1095.6 |  | 4514 | 77.15 | 0.46205 | 62.24 | 0.0014473 | 45.249 | 1095.6 | 1050.351
4515 | 0.4622 | 77.16 | 62.239 | 0.0014477 | 45.259 | 1095.6 |  | 4515 | 77.16 | 0.4622 | 62.239 | 0.0014477 | 45.259 | 1095.6 | 1050.341
4516 | 0.46235 | 77.17 | 62.239 | 0.0014482 | 45.269 | 1095.6 |  | 4516 | 77.17 | 0.46235 | 62.239 | 0.0014482 | 45.269 | 1095.6 | 1050.331
4517 | 0.46251 | 77.18 | 62.239 | 0.0014486 | 45.279 | 1095.6 |  | 4517 | 77.18 | 0.46251 | 62.239 | 0.0014486 | 45.279 | 1095.6 | 1050.321
4518 | 0.46266 | 77.19 | 62.239 | 0.0014491 | 45.289 | 1095.6 |  | 4518 | 77.19 | 0.46266 | 62.239 | 0.0014491 | 45.289 | 1095.6 | 1050.311
4519 | 0.46281 | 77.2 | 62.239 | 0.0014496 | 45.299 | 1095.6 |  | 4519 | 77.2 | 0.46281 | 62.239 | 0.0014496 | 45.299 | 1095.6 | 1050.301
4520 | 0.46297 | 77.21 | 62.239 | 0.00145 | 45.309 | 1095.6 |  | 4520 | 77.21 | 0.46297 | 62.239 | 0.00145 | 45.309 | 1095.6 | 1050.291
4521 | 0.46312 | 77.22 | 62.239 | 0.0014505 | 45.318 | 1095.6 |  | 4521 | 77.22 | 0.46312 | 62.239 | 0.0014505 | 45.318 | 1095.6 | 1050.282
4522 | 0.46327 | 77.23 | 62.239 | 0.0014509 | 45.328 | 1095.6 |  | 4522 | 77.23 | 0.46327 | 62.239 | 0.0014509 | 45.328 | 1095.6 | 1050.272
4523 | 0.46343 | 77.24 | 62.239 | 0.0014514 | 45.338 | 1095.6 |  | 4523 | 77.24 | 0.46343 | 62.239 | 0.0014514 | 45.338 | 1095.6 | 1050.262
4524 | 0.46358 | 77.25 | 62.239 | 0.0014518 | 45.348 | 1095.6 |  | 4524 | 77.25 | 0.46358 | 62.239 | 0.0014518 | 45.348 | 1095.6 | 1050.252
4525 | 0.46373 | 77.26 | 62.239 | 0.0014523 | 45.358 | 1095.6 |  | 4525 | 77.26 | 0.46373 | 62.239 | 0.0014523 | 45.358 | 1095.6 | 1050.242
4526 | 0.46389 | 77.27 | 62.238 | 0.0014527 | 45.368 | 1095.6 |  | 4526 | 77.27 | 0.46389 | 62.238 | 0.0014527 | 45.368 | 1095.6 | 1050.232
4527 | 0.46404 | 77.28 | 62.238 | 0.0014532 | 45.378 | 1095.7 |  | 4527 | 77.28 | 0.46404 | 62.238 | 0.0014532 | 45.378 | 1095.7 | 1050.322
4528 | 0.46419 | 77.29 | 62.238 | 0.0014536 | 45.388 | 1095.7 |  | 4528 | 77.29 | 0.46419 | 62.238 | 0.0014536 | 45.388 | 1095.7 | 1050.312
4529 | 0.46435 | 77.3 | 62.238 | 0.0014541 | 45.398 | 1095.7 |  | 4529 | 77.3 | 0.46435 | 62.238 | 0.0014541 | 45.398 | 1095.7 | 1050.302
4530 | 0.4645 | 77.31 | 62.238 | 0.0014545 | 45.408 | 1095.7 |  | 4530 | 77.31 | 0.4645 | 62.238 | 0.0014545 | 45.408 | 1095.7 | 1050.292
4531 | 0.46465 | 77.32 | 62.238 | 0.001455 | 45.418 | 1095.7 |  | 4531 | 77.32 | 0.46465 | 62.238 | 0.001455 | 45.418 | 1095.7 | 1050.282
4532 | 0.46481 | 77.33 | 62.238 | 0.0014555 | 45.428 | 1095.7 |  | 4532 | 77.33 | 0.46481 | 62.238 | 0.0014555 | 45.428 | 1095.7 | 1050.272
4533 | 0.46496 | 77.34 | 62.238 | 0.0014559 | 45.438 | 1095.7 |  | 4533 | 77.34 | 0.46496 | 62.238 | 0.0014559 | 45.438 | 1095.7 | 1050.262
4534 | 0.46512 | 77.35 | 62.238 | 0.0014564 | 45.448 | 1095.7 |  | 4534 | 77.35 | 0.46512 | 62.238 | 0.0014564 | 45.448 | 1095.7 | 1050.252
4535 | 0.46527 | 77.36 | 62.238 | 0.0014568 | 45.458 | 1095.7 |  | 4535 | 77.36 | 0.46527 | 62.238 | 0.0014568 | 45.458 | 1095.7 | 1050.242
4536 | 0.46542 | 77.37 | 62.238 | 0.0014573 | 45.468 | 1095.7 |  | 4536 | 77.37 | 0.46542 | 62.238 | 0.0014573 | 45.468 | 1095.7 | 1050.232
4537 | 0.46558 | 77.38 | 62.237 | 0.0014577 | 45.478 | 1095.7 |  | 4537 | 77.38 | 0.46558 | 62.237 | 0.0014577 | 45.478 | 1095.7 | 1050.222
4538 | 0.46573 | 77.39 | 62.237 | 0.0014582 | 45.488 | 1095.7 |  | 4538 | 77.39 | 0.46573 | 62.237 | 0.0014582 | 45.488 | 1095.7 | 1050.212
4539 | 0.46589 | 77.4 | 62.237 | 0.0014586 | 45.498 | 1095.7 |  | 4539 | 77.4 | 0.46589 | 62.237 | 0.0014586 | 45.498 | 1095.7 | 1050.202
4540 | 0.46604 | 77.41 | 62.237 | 0.0014591 | 45.508 | 1095.7 |  | 4540 | 77.41 | 0.46604 | 62.237 | 0.0014591 | 45.508 | 1095.7 | 1050.192
4541 | 0.46619 | 77.42 | 62.237 | 0.0014596 | 45.518 | 1095.7 |  | 4541 | 77.42 | 0.46619 | 62.237 | 0.0014596 | 45.518 | 1095.7 | 1050.182
4542 | 0.46635 | 77.43 | 62.237 | 0.00146 | 45.528 | 1095.7 |  | 4542 | 77.43 | 0.46635 | 62.237 | 0.00146 | 45.528 | 1095.7 | 1050.172
4543 | 0.4665 | 77.44 | 62.237 | 0.0014605 | 45.538 | 1095.7 |  | 4543 | 77.44 | 0.4665 | 62.237 | 0.0014605 | 45.538 | 1095.7 | 1050.162
4544 | 0.46666 | 77.45 | 62.237 | 0.0014609 | 45.548 | 1095.7 |  | 4544 | 77.45 | 0.46666 | 62.237 | 0.0014609 | 45.548 | 1095.7 | 1050.152
4545 | 0.46681 | 77.46 | 62.237 | 0.0014614 | 45.558 | 1095.7 |  | 4545 | 77.46 | 0.46681 | 62.237 | 0.0014614 | 45.558 | 1095.7 | 1050.142
4546 | 0.46696 | 77.47 | 62.237 | 0.0014618 | 45.568 | 1095.7 |  | 4546 | 77.47 | 0.46696 | 62.237 | 0.0014618 | 45.568 | 1095.7 | 1050.132
4547 | 0.46712 | 77.48 | 62.237 | 0.0014623 | 45.578 | 1095.7 |  | 4547 | 77.48 | 0.46712 | 62.237 | 0.0014623 | 45.578 | 1095.7 | 1050.122
4548 | 0.46727 | 77.49 | 62.237 | 0.0014627 | 45.588 | 1095.7 |  | 4548 | 77.49 | 0.46727 | 62.237 | 0.0014627 | 45.588 | 1095.7 | 1050.112
4549 | 0.46743 | 77.5 | 62.236 | 0.0014632 | 45.598 | 1095.7 |  | 4549 | 77.5 | 0.46743 | 62.236 | 0.0014632 | 45.598 | 1095.7 | 1050.102
4550 | 0.46758 | 77.51 | 62.236 | 0.0014637 | 45.608 | 1095.8 |  | 4550 | 77.51 | 0.46758 | 62.236 | 0.0014637 | 45.608 | 1095.8 | 1050.192
4551 | 0.46774 | 77.52 | 62.236 | 0.0014641 | 45.618 | 1095.8 |  | 4551 | 77.52 | 0.46774 | 62.236 | 0.0014641 | 45.618 | 1095.8 | 1050.182
4552 | 0.46789 | 77.53 | 62.236 | 0.0014646 | 45.628 | 1095.8 |  | 4552 | 77.53 | 0.46789 | 62.236 | 0.0014646 | 45.628 | 1095.8 | 1050.172
4553 | 0.46805 | 77.54 | 62.236 | 0.001465 | 45.638 | 1095.8 |  | 4553 | 77.54 | 0.46805 | 62.236 | 0.001465 | 45.638 | 1095.8 | 1050.162
4554 | 0.4682 | 77.55 | 62.236 | 0.0014655 | 45.648 | 1095.8 |  | 4554 | 77.55 | 0.4682 | 62.236 | 0.0014655 | 45.648 | 1095.8 | 1050.152
4555 | 0.46836 | 77.56 | 62.236 | 0.0014659 | 45.658 | 1095.8 |  | 4555 | 77.56 | 0.46836 | 62.236 | 0.0014659 | 45.658 | 1095.8 | 1050.142
4556 | 0.46851 | 77.57 | 62.236 | 0.0014664 | 45.668 | 1095.8 |  | 4556 | 77.57 | 0.46851 | 62.236 | 0.0014664 | 45.668 | 1095.8 | 1050.132
4557 | 0.46867 | 77.58 | 62.236 | 0.0014669 | 45.678 | 1095.8 |  | 4557 | 77.58 | 0.46867 | 62.236 | 0.0014669 | 45.678 | 1095.8 | 1050.122
4558 | 0.46882 | 77.59 | 62.236 | 0.0014673 | 45.688 | 1095.8 |  | 4558 | 77.59 | 0.46882 | 62.236 | 0.0014673 | 45.688 | 1095.8 | 1050.112
4559 | 0.46898 | 77.6 | 62.236 | 0.0014678 | 45.698 | 1095.8 |  | 4559 | 77.6 | 0.46898 | 62.236 | 0.0014678 | 45.698 | 1095.8 | 1050.102
4560 | 0.46913 | 77.61 | 62.235 | 0.0014682 | 45.708 | 1095.8 |  | 4560 | 77.61 | 0.46913 | 62.235 | 0.0014682 | 45.708 | 1095.8 | 1050.092
4561 | 0.46928 | 77.62 | 62.235 | 0.0014687 | 45.718 | 1095.8 |  | 4561 | 77.62 | 0.46928 | 62.235 | 0.0014687 | 45.718 | 1095.8 | 1050.082
4562 | 0.46944 | 77.63 | 62.235 | 0.0014692 | 45.728 | 1095.8 |  | 4562 | 77.63 | 0.46944 | 62.235 | 0.0014692 | 45.728 | 1095.8 | 1050.072
4563 | 0.4696 | 77.64 | 62.235 | 0.0014696 | 45.738 | 1095.8 |  | 4563 | 77.64 | 0.4696 | 62.235 | 0.0014696 | 45.738 | 1095.8 | 1050.062
4564 | 0.46975 | 77.65 | 62.235 | 0.0014701 | 45.748 | 1095.8 |  | 4564 | 77.65 | 0.46975 | 62.235 | 0.0014701 | 45.748 | 1095.8 | 1050.052
4565 | 0.46991 | 77.66 | 62.235 | 0.0014705 | 45.758 | 1095.8 |  | 4565 | 77.66 | 0.46991 | 62.235 | 0.0014705 | 45.758 | 1095.8 | 1050.042
4566 | 0.47006 | 77.67 | 62.235 | 0.001471 | 45.768 | 1095.8 |  | 4566 | 77.67 | 0.47006 | 62.235 | 0.001471 | 45.768 | 1095.8 | 1050.032
4567 | 0.47022 | 77.68 | 62.235 | 0.0014714 | 45.778 | 1095.8 |  | 4567 | 77.68 | 0.47022 | 62.235 | 0.0014714 | 45.778 | 1095.8 | 1050.022
4568 | 0.47037 | 77.69 | 62.235 | 0.0014719 | 45.788 | 1095.8 |  | 4568 | 77.69 | 0.47037 | 62.235 | 0.0014719 | 45.788 | 1095.8 | 1050.012
4569 | 0.47053 | 77.7 | 62.235 | 0.0014724 | 45.798 | 1095.8 |  | 4569 | 77.7 | 0.47053 | 62.235 | 0.0014724 | 45.798 | 1095.8 | 1050.002
4570 | 0.47068 | 77.71 | 62.235 | 0.0014728 | 45.808 | 1095.8 |  | 4570 | 77.71 | 0.47068 | 62.235 | 0.0014728 | 45.808 | 1095.8 | 1049.992
4571 | 0.47084 | 77.72 | 62.234 | 0.0014733 | 45.818 | 1095.8 |  | 4571 | 77.72 | 0.47084 | 62.234 | 0.0014733 | 45.818 | 1095.8 | 1049.982
4572 | 0.47099 | 77.73 | 62.234 | 0.0014737 | 45.828 | 1095.8 |  | 4572 | 77.73 | 0.47099 | 62.234 | 0.0014737 | 45.828 | 1095.8 | 1049.972
4573 | 0.47115 | 77.74 | 62.234 | 0.0014742 | 45.838 | 1095.9 |  | 4573 | 77.74 | 0.47115 | 62.234 | 0.0014742 | 45.838 | 1095.9 | 1050.062
4574 | 0.4713 | 77.75 | 62.234 | 0.0014747 | 45.848 | 1095.9 |  | 4574 | 77.75 | 0.4713 | 62.234 | 0.0014747 | 45.848 | 1095.9 | 1050.052
4575 | 0.47146 | 77.76 | 62.234 | 0.0014751 | 45.858 | 1095.9 |  | 4575 | 77.76 | 0.47146 | 62.234 | 0.0014751 | 45.858 | 1095.9 | 1050.042
4576 | 0.47162 | 77.77 | 62.234 | 0.0014756 | 45.868 | 1095.9 |  | 4576 | 77.77 | 0.47162 | 62.234 | 0.0014756 | 45.868 | 1095.9 | 1050.032
4577 | 0.47177 | 77.78 | 62.234 | 0.001476 | 45.878 | 1095.9 |  | 4577 | 77.78 | 0.47177 | 62.234 | 0.001476 | 45.878 | 1095.9 | 1050.022
4578 | 0.47193 | 77.79 | 62.234 | 0.0014765 | 45.888 | 1095.9 |  | 4578 | 77.79 | 0.47193 | 62.234 | 0.0014765 | 45.888 | 1095.9 | 1050.012
4579 | 0.47208 | 77.8 | 62.234 | 0.001477 | 45.898 | 1095.9 |  | 4579 | 77.8 | 0.47208 | 62.234 | 0.001477 | 45.898 | 1095.9 | 1050.002
4580 | 0.47224 | 77.81 | 62.234 | 0.0014774 | 45.908 | 1095.9 |  | 4580 | 77.81 | 0.47224 | 62.234 | 0.0014774 | 45.908 | 1095.9 | 1049.992
4581 | 0.47239 | 77.82 | 62.234 | 0.0014779 | 45.918 | 1095.9 |  | 4581 | 77.82 | 0.47239 | 62.234 | 0.0014779 | 45.918 | 1095.9 | 1049.982
4582 | 0.47255 | 77.83 | 62.233 | 0.0014783 | 45.928 | 1095.9 |  | 4582 | 77.83 | 0.47255 | 62.233 | 0.0014783 | 45.928 | 1095.9 | 1049.972
4583 | 0.47271 | 77.84 | 62.233 | 0.0014788 | 45.938 | 1095.9 |  | 4583 | 77.84 | 0.47271 | 62.233 | 0.0014788 | 45.938 | 1095.9 | 1049.962
4584 | 0.47286 | 77.85 | 62.233 | 0.0014793 | 45.948 | 1095.9 |  | 4584 | 77.85 | 0.47286 | 62.233 | 0.0014793 | 45.948 | 1095.9 | 1049.952
4585 | 0.47302 | 77.86 | 62.233 | 0.0014797 | 45.958 | 1095.9 |  | 4585 | 77.86 | 0.47302 | 62.233 | 0.0014797 | 45.958 | 1095.9 | 1049.942
4586 | 0.47317 | 77.87 | 62.233 | 0.0014802 | 45.968 | 1095.9 |  | 4586 | 77.87 | 0.47317 | 62.233 | 0.0014802 | 45.968 | 1095.9 | 1049.932
4587 | 0.47333 | 77.88 | 62.233 | 0.0014807 | 45.978 | 1095.9 |  | 4587 | 77.88 | 0.47333 | 62.233 | 0.0014807 | 45.978 | 1095.9 | 1049.922
4588 | 0.47349 | 77.89 | 62.233 | 0.0014811 | 45.988 | 1095.9 |  | 4588 | 77.89 | 0.47349 | 62.233 | 0.0014811 | 45.988 | 1095.9 | 1049.912
4589 | 0.47364 | 77.9 | 62.233 | 0.0014816 | 45.998 | 1095.9 |  | 4589 | 77.9 | 0.47364 | 62.233 | 0.0014816 | 45.998 | 1095.9 | 1049.902
4590 | 0.4738 | 77.91 | 62.233 | 0.001482 | 46.008 | 1095.9 |  | 4590 | 77.91 | 0.4738 | 62.233 | 0.001482 | 46.008 | 1095.9 | 1049.892
4591 | 0.47396 | 77.92 | 62.233 | 0.0014825 | 46.018 | 1095.9 |  | 4591 | 77.92 | 0.47396 | 62.233 | 0.0014825 | 46.018 | 1095.9 | 1049.882
4592 | 0.47411 | 77.93 | 62.233 | 0.001483 | 46.028 | 1095.9 |  | 4592 | 77.93 | 0.47411 | 62.233 | 0.001483 | 46.028 | 1095.9 | 1049.872
4593 | 0.47427 | 77.94 | 62.232 | 0.0014834 | 46.038 | 1095.9 |  | 4593 | 77.94 | 0.47427 | 62.232 | 0.0014834 | 46.038 | 1095.9 | 1049.862
4594 | 0.47442 | 77.95 | 62.232 | 0.0014839 | 46.048 | 1095.9 |  | 4594 | 77.95 | 0.47442 | 62.232 | 0.0014839 | 46.048 | 1095.9 | 1049.852
4595 | 0.47458 | 77.96 | 62.232 | 0.0014843 | 46.058 | 1095.9 |  | 4595 | 77.96 | 0.47458 | 62.232 | 0.0014843 | 46.058 | 1095.9 | 1049.842
4596 | 0.47474 | 77.97 | 62.232 | 0.0014848 | 46.068 | 1096 |  | 4596 | 77.97 | 0.47474 | 62.232 | 0.0014848 | 46.068 | 1096 | 1049.932
4597 | 0.47489 | 77.98 | 62.232 | 0.0014853 | 46.078 | 1096 |  | 4597 | 77.98 | 0.47489 | 62.232 | 0.0014853 | 46.078 | 1096 | 1049.922
4598 | 0.47505 | 77.99 | 62.232 | 0.0014857 | 46.088 | 1096 |  | 4598 | 77.99 | 0.47505 | 62.232 | 0.0014857 | 46.088 | 1096 | 1049.912
4599 | 0.47521 | 78 | 62.232 | 0.0014862 | 46.098 | 1096 |  | 4599 | 78 | 0.47521 | 62.232 | 0.0014862 | 46.098 | 1096 | 1049.902
4600 | 0.47536 | 78.01 | 62.232 | 0.0014867 | 46.108 | 1096 |  | 4600 | 78.01 | 0.47536 | 62.232 | 0.0014867 | 46.108 | 1096 | 1049.892
4601 | 0.47552 | 78.02 | 62.232 | 0.0014871 | 46.118 | 1096 |  | 4601 | 78.02 | 0.47552 | 62.232 | 0.0014871 | 46.118 | 1096 | 1049.882
4602 | 0.47568 | 78.03 | 62.232 | 0.0014876 | 46.128 | 1096 |  | 4602 | 78.03 | 0.47568 | 62.232 | 0.0014876 | 46.128 | 1096 | 1049.872
4603 | 0.47584 | 78.04 | 62.232 | 0.0014881 | 46.138 | 1096 |  | 4603 | 78.04 | 0.47584 | 62.232 | 0.0014881 | 46.138 | 1096 | 1049.862
4604 | 0.47599 | 78.05 | 62.231 | 0.0014885 | 46.148 | 1096 |  | 4604 | 78.05 | 0.47599 | 62.231 | 0.0014885 | 46.148 | 1096 | 1049.852
4605 | 0.47615 | 78.06 | 62.231 | 0.001489 | 46.158 | 1096 |  | 4605 | 78.06 | 0.47615 | 62.231 | 0.001489 | 46.158 | 1096 | 1049.842
4606 | 0.47631 | 78.07 | 62.231 | 0.0014894 | 46.168 | 1096 |  | 4606 | 78.07 | 0.47631 | 62.231 | 0.0014894 | 46.168 | 1096 | 1049.832
4607 | 0.47646 | 78.08 | 62.231 | 0.0014899 | 46.178 | 1096 |  | 4607 | 78.08 | 0.47646 | 62.231 | 0.0014899 | 46.178 | 1096 | 1049.822
4608 | 0.47662 | 78.09 | 62.231 | 0.0014904 | 46.188 | 1096 |  | 4608 | 78.09 | 0.47662 | 62.231 | 0.0014904 | 46.188 | 1096 | 1049.812
4609 | 0.47678 | 78.1 | 62.231 | 0.0014908 | 46.198 | 1096 |  | 4609 | 78.1 | 0.47678 | 62.231 | 0.0014908 | 46.198 | 1096 | 1049.802
4610 | 0.47693 | 78.11 | 62.231 | 0.0014913 | 46.208 | 1096 |  | 4610 | 78.11 | 0.47693 | 62.231 | 0.0014913 | 46.208 | 1096 | 1049.792
4611 | 0.47709 | 78.12 | 62.231 | 0.0014918 | 46.218 | 1096 |  | 4611 | 78.12 | 0.47709 | 62.231 | 0.0014918 | 46.218 | 1096 | 1049.782
4612 | 0.47725 | 78.13 | 62.231 | 0.0014922 | 46.228 | 1096 |  | 4612 | 78.13 | 0.47725 | 62.231 | 0.0014922 | 46.228 | 1096 | 1049.772
4613 | 0.47741 | 78.14 | 62.231 | 0.0014927 | 46.238 | 1096 |  | 4613 | 78.14 | 0.47741 | 62.231 | 0.0014927 | 46.238 | 1096 | 1049.762
4614 | 0.47756 | 78.15 | 62.231 | 0.0014932 | 46.248 | 1096 |  | 4614 | 78.15 | 0.47756 | 62.231 | 0.0014932 | 46.248 | 1096 | 1049.752
4615 | 0.47772 | 78.16 | 62.23 | 0.0014936 | 46.258 | 1096 |  | 4615 | 78.16 | 0.47772 | 62.23 | 0.0014936 | 46.258 | 1096 | 1049.742
4616 | 0.47788 | 78.17 | 62.23 | 0.0014941 | 46.268 | 1096 |  | 4616 | 78.17 | 0.47788 | 62.23 | 0.0014941 | 46.268 | 1096 | 1049.732
4617 | 0.47804 | 78.18 | 62.23 | 0.0014946 | 46.278 | 1096 |  | 4617 | 78.18 | 0.47804 | 62.23 | 0.0014946 | 46.278 | 1096 | 1049.722
4618 | 0.47819 | 78.19 | 62.23 | 0.001495 | 46.288 | 1096 |  | 4618 | 78.19 | 0.47819 | 62.23 | 0.001495 | 46.288 | 1096 | 1049.712
4619 | 0.47835 | 78.2 | 62.23 | 0.0014955 | 46.298 | 1096.1 |  | 4619 | 78.2 | 0.47835 | 62.23 | 0.0014955 | 46.298 | 1096.1 | 1049.802
4620 | 0.47851 | 78.21 | 62.23 | 0.0014959 | 46.308 | 1096.1 |  | 4620 | 78.21 | 0.47851 | 62.23 | 0.0014959 | 46.308 | 1096.1 | 1049.792
4621 | 0.47867 | 78.22 | 62.23 | 0.0014964 | 46.318 | 1096.1 |  | 4621 | 78.22 | 0.47867 | 62.23 | 0.0014964 | 46.318 | 1096.1 | 1049.782
4622 | 0.47882 | 78.23 | 62.23 | 0.0014969 | 46.328 | 1096.1 |  | 4622 | 78.23 | 0.47882 | 62.23 | 0.0014969 | 46.328 | 1096.1 | 1049.772
4623 | 0.47898 | 78.24 | 62.23 | 0.0014973 | 46.338 | 1096.1 |  | 4623 | 78.24 | 0.47898 | 62.23 | 0.0014973 | 46.338 | 1096.1 | 1049.762
4624 | 0.47914 | 78.25 | 62.23 | 0.0014978 | 46.348 | 1096.1 |  | 4624 | 78.25 | 0.47914 | 62.23 | 0.0014978 | 46.348 | 1096.1 | 1049.752
4625 | 0.4793 | 78.26 | 62.23 | 0.0014983 | 46.358 | 1096.1 |  | 4625 | 78.26 | 0.4793 | 62.23 | 0.0014983 | 46.358 | 1096.1 | 1049.742
4626 | 0.47946 | 78.27 | 62.229 | 0.0014987 | 46.368 | 1096.1 |  | 4626 | 78.27 | 0.47946 | 62.229 | 0.0014987 | 46.368 | 1096.1 | 1049.732
4627 | 0.47961 | 78.28 | 62.229 | 0.0014992 | 46.378 | 1096.1 |  | 4627 | 78.28 | 0.47961 | 62.229 | 0.0014992 | 46.378 | 1096.1 | 1049.722
4628 | 0.47977 | 78.29 | 62.229 | 0.0014997 | 46.388 | 1096.1 |  | 4628 | 78.29 | 0.47977 | 62.229 | 0.0014997 | 46.388 | 1096.1 | 1049.712
4629 | 0.47993 | 78.3 | 62.229 | 0.0015001 | 46.398 | 1096.1 |  | 4629 | 78.3 | 0.47993 | 62.229 | 0.0015001 | 46.398 | 1096.1 | 1049.702
4630 | 0.48009 | 78.31 | 62.229 | 0.0015006 | 46.408 | 1096.1 |  | 4630 | 78.31 | 0.48009 | 62.229 | 0.0015006 | 46.408 | 1096.1 | 1049.692
4631 | 0.48025 | 78.32 | 62.229 | 0.0015011 | 46.418 | 1096.1 |  | 4631 | 78.32 | 0.48025 | 62.229 | 0.0015011 | 46.418 | 1096.1 | 1049.682
4632 | 0.4804 | 78.33 | 62.229 | 0.0015015 | 46.428 | 1096.1 |  | 4632 | 78.33 | 0.4804 | 62.229 | 0.0015015 | 46.428 | 1096.1 | 1049.672
4633 | 0.48056 | 78.34 | 62.229 | 0.001502 | 46.438 | 1096.1 |  | 4633 | 78.34 | 0.48056 | 62.229 | 0.001502 | 46.438 | 1096.1 | 1049.662
4634 | 0.48072 | 78.35 | 62.229 | 0.0015025 | 46.448 | 1096.1 |  | 4634 | 78.35 | 0.48072 | 62.229 | 0.0015025 | 46.448 | 1096.1 | 1049.652
4635 | 0.48088 | 78.36 | 62.229 | 0.0015029 | 46.458 | 1096.1 |  | 4635 | 78.36 | 0.48088 | 62.229 | 0.0015029 | 46.458 | 1096.1 | 1049.642
4636 | 0.48104 | 78.37 | 62.229 | 0.0015034 | 46.468 | 1096.1 |  | 4636 | 78.37 | 0.48104 | 62.229 | 0.0015034 | 46.468 | 1096.1 | 1049.632
4637 | 0.4812 | 78.38 | 62.228 | 0.0015039 | 46.478 | 1096.1 |  | 4637 | 78.38 | 0.4812 | 62.228 | 0.0015039 | 46.478 | 1096.1 | 1049.622
4638 | 0.48135 | 78.39 | 62.228 | 0.0015044 | 46.488 | 1096.1 |  | 4638 | 78.39 | 0.48135 | 62.228 | 0.0015044 | 46.488 | 1096.1 | 1049.612
4639 | 0.48151 | 78.4 | 62.228 | 0.0015048 | 46.498 | 1096.1 |  | 4639 | 78.4 | 0.48151 | 62.228 | 0.0015048 | 46.498 | 1096.1 | 1049.602
4640 | 0.48167 | 78.41 | 62.228 | 0.0015053 | 46.508 | 1096.1 |  | 4640 | 78.41 | 0.48167 | 62.228 | 0.0015053 | 46.508 | 1096.1 | 1049.592
4641 | 0.48183 | 78.42 | 62.228 | 0.0015058 | 46.518 | 1096.1 |  | 4641 | 78.42 | 0.48183 | 62.228 | 0.0015058 | 46.518 | 1096.1 | 1049.582
4642 | 0.48199 | 78.43 | 62.228 | 0.0015062 | 46.528 | 1096.2 |  | 4642 | 78.43 | 0.48199 | 62.228 | 0.0015062 | 46.528 | 1096.2 | 1049.672
4643 | 0.48215 | 78.44 | 62.228 | 0.0015067 | 46.538 | 1096.2 |  | 4643 | 78.44 | 0.48215 | 62.228 | 0.0015067 | 46.538 | 1096.2 | 1049.662
4644 | 0.48231 | 78.45 | 62.228 | 0.0015072 | 46.548 | 1096.2 |  | 4644 | 78.45 | 0.48231 | 62.228 | 0.0015072 | 46.548 | 1096.2 | 1049.652
4645 | 0.48246 | 78.46 | 62.228 | 0.0015076 | 46.558 | 1096.2 |  | 4645 | 78.46 | 0.48246 | 62.228 | 0.0015076 | 46.558 | 1096.2 | 1049.642
4646 | 0.48262 | 78.47 | 62.228 | 0.0015081 | 46.568 | 1096.2 |  | 4646 | 78.47 | 0.48262 | 62.228 | 0.0015081 | 46.568 | 1096.2 | 1049.632
4647 | 0.48278 | 78.48 | 62.228 | 0.0015086 | 46.578 | 1096.2 |  | 4647 | 78.48 | 0.48278 | 62.228 | 0.0015086 | 46.578 | 1096.2 | 1049.622
4648 | 0.48294 | 78.49 | 62.227 | 0.001509 | 46.588 | 1096.2 |  | 4648 | 78.49 | 0.48294 | 62.227 | 0.001509 | 46.588 | 1096.2 | 1049.612
4649 | 0.4831 | 78.5 | 62.227 | 0.0015095 | 46.598 | 1096.2 |  | 4649 | 78.5 | 0.4831 | 62.227 | 0.0015095 | 46.598 | 1096.2 | 1049.602
4650 | 0.48326 | 78.51 | 62.227 | 0.00151 | 46.608 | 1096.2 |  | 4650 | 78.51 | 0.48326 | 62.227 | 0.00151 | 46.608 | 1096.2 | 1049.592
4651 | 0.48342 | 78.52 | 62.227 | 0.0015104 | 46.618 | 1096.2 |  | 4651 | 78.52 | 0.48342 | 62.227 | 0.0015104 | 46.618 | 1096.2 | 1049.582
4652 | 0.48358 | 78.53 | 62.227 | 0.0015109 | 46.628 | 1096.2 |  | 4652 | 78.53 | 0.48358 | 62.227 | 0.0015109 | 46.628 | 1096.2 | 1049.572
4653 | 0.48374 | 78.54 | 62.227 | 0.0015114 | 46.638 | 1096.2 |  | 4653 | 78.54 | 0.48374 | 62.227 | 0.0015114 | 46.638 | 1096.2 | 1049.562
4654 | 0.4839 | 78.55 | 62.227 | 0.0015119 | 46.648 | 1096.2 |  | 4654 | 78.55 | 0.4839 | 62.227 | 0.0015119 | 46.648 | 1096.2 | 1049.552
4655 | 0.48406 | 78.56 | 62.227 | 0.0015123 | 46.658 | 1096.2 |  | 4655 | 78.56 | 0.48406 | 62.227 | 0.0015123 | 46.658 | 1096.2 | 1049.542
4656 | 0.48421 | 78.57 | 62.227 | 0.0015128 | 46.668 | 1096.2 |  | 4656 | 78.57 | 0.48421 | 62.227 | 0.0015128 | 46.668 | 1096.2 | 1049.532
4657 | 0.48437 | 78.58 | 62.227 | 0.0015133 | 46.678 | 1096.2 |  | 4657 | 78.58 | 0.48437 | 62.227 | 0.0015133 | 46.678 | 1096.2 | 1049.522
4658 | 0.48453 | 78.59 | 62.227 | 0.0015137 | 46.688 | 1096.2 |  | 4658 | 78.59 | 0.48453 | 62.227 | 0.0015137 | 46.688 | 1096.2 | 1049.512
4659 | 0.48469 | 78.6 | 62.226 | 0.0015142 | 46.698 | 1096.2 |  | 4659 | 78.6 | 0.48469 | 62.226 | 0.0015142 | 46.698 | 1096.2 | 1049.502
4660 | 0.48485 | 78.61 | 62.226 | 0.0015147 | 46.708 | 1096.2 |  | 4660 | 78.61 | 0.48485 | 62.226 | 0.0015147 | 46.708 | 1096.2 | 1049.492
4661 | 0.48501 | 78.62 | 62.226 | 0.0015151 | 46.718 | 1096.2 |  | 4661 | 78.62 | 0.48501 | 62.226 | 0.0015151 | 46.718 | 1096.2 | 1049.482
4662 | 0.48517 | 78.63 | 62.226 | 0.0015156 | 46.728 | 1096.2 |  | 4662 | 78.63 | 0.48517 | 62.226 | 0.0015156 | 46.728 | 1096.2 | 1049.472
4663 | 0.48533 | 78.64 | 62.226 | 0.0015161 | 46.738 | 1096.2 |  | 4663 | 78.64 | 0.48533 | 62.226 | 0.0015161 | 46.738 | 1096.2 | 1049.462
4664 | 0.48549 | 78.65 | 62.226 | 0.0015166 | 46.748 | 1096.2 |  | 4664 | 78.65 | 0.48549 | 62.226 | 0.0015166 | 46.748 | 1096.2 | 1049.452
4665 | 0.48565 | 78.66 | 62.226 | 0.001517 | 46.758 | 1096.3 |  | 4665 | 78.66 | 0.48565 | 62.226 | 0.001517 | 46.758 | 1096.3 | 1049.542
4666 | 0.48581 | 78.67 | 62.226 | 0.0015175 | 46.768 | 1096.3 |  | 4666 | 78.67 | 0.48581 | 62.226 | 0.0015175 | 46.768 | 1096.3 | 1049.532
4667 | 0.48597 | 78.68 | 62.226 | 0.001518 | 46.778 | 1096.3 |  | 4667 | 78.68 | 0.48597 | 62.226 | 0.001518 | 46.778 | 1096.3 | 1049.522
4668 | 0.48613 | 78.69 | 62.226 | 0.0015184 | 46.788 | 1096.3 |  | 4668 | 78.69 | 0.48613 | 62.226 | 0.0015184 | 46.788 | 1096.3 | 1049.512
4669 | 0.48629 | 78.7 | 62.226 | 0.0015189 | 46.798 | 1096.3 |  | 4669 | 78.7 | 0.48629 | 62.226 | 0.0015189 | 46.798 | 1096.3 | 1049.502
4670 | 0.48645 | 78.71 | 62.225 | 0.0015194 | 46.808 | 1096.3 |  | 4670 | 78.71 | 0.48645 | 62.225 | 0.0015194 | 46.808 | 1096.3 | 1049.492
4671 | 0.48661 | 78.72 | 62.225 | 0.0015199 | 46.818 | 1096.3 |  | 4671 | 78.72 | 0.48661 | 62.225 | 0.0015199 | 46.818 | 1096.3 | 1049.482
4672 | 0.48677 | 78.73 | 62.225 | 0.0015203 | 46.828 | 1096.3 |  | 4672 | 78.73 | 0.48677 | 62.225 | 0.0015203 | 46.828 | 1096.3 | 1049.472
4673 | 0.48693 | 78.74 | 62.225 | 0.0015208 | 46.838 | 1096.3 |  | 4673 | 78.74 | 0.48693 | 62.225 | 0.0015208 | 46.838 | 1096.3 | 1049.462
4674 | 0.48709 | 78.75 | 62.225 | 0.0015213 | 46.848 | 1096.3 |  | 4674 | 78.75 | 0.48709 | 62.225 | 0.0015213 | 46.848 | 1096.3 | 1049.452
4675 | 0.48725 | 78.76 | 62.225 | 0.0015217 | 46.858 | 1096.3 |  | 4675 | 78.76 | 0.48725 | 62.225 | 0.0015217 | 46.858 | 1096.3 | 1049.442
4676 | 0.48741 | 78.77 | 62.225 | 0.0015222 | 46.868 | 1096.3 |  | 4676 | 78.77 | 0.48741 | 62.225 | 0.0015222 | 46.868 | 1096.3 | 1049.432
4677 | 0.48757 | 78.78 | 62.225 | 0.0015227 | 46.878 | 1096.3 |  | 4677 | 78.78 | 0.48757 | 62.225 | 0.0015227 | 46.878 | 1096.3 | 1049.422
4678 | 0.48773 | 78.79 | 62.225 | 0.0015232 | 46.888 | 1096.3 |  | 4678 | 78.79 | 0.48773 | 62.225 | 0.0015232 | 46.888 | 1096.3 | 1049.412
4679 | 0.48789 | 78.8 | 62.225 | 0.0015236 | 46.898 | 1096.3 |  | 4679 | 78.8 | 0.48789 | 62.225 | 0.0015236 | 46.898 | 1096.3 | 1049.402
4680 | 0.48805 | 78.81 | 62.224 | 0.0015241 | 46.908 | 1096.3 |  | 4680 | 78.81 | 0.48805 | 62.224 | 0.0015241 | 46.908 | 1096.3 | 1049.392
4681 | 0.48821 | 78.82 | 62.224 | 0.0015246 | 46.918 | 1096.3 |  | 4681 | 78.82 | 0.48821 | 62.224 | 0.0015246 | 46.918 | 1096.3 | 1049.382
4682 | 0.48837 | 78.83 | 62.224 | 0.0015251 | 46.928 | 1096.3 |  | 4682 | 78.83 | 0.48837 | 62.224 | 0.0015251 | 46.928 | 1096.3 | 1049.372
4683 | 0.48853 | 78.84 | 62.224 | 0.0015255 | 46.938 | 1096.3 |  | 4683 | 78.84 | 0.48853 | 62.224 | 0.0015255 | 46.938 | 1096.3 | 1049.362
4684 | 0.48869 | 78.85 | 62.224 | 0.001526 | 46.948 | 1096.3 |  | 4684 | 78.85 | 0.48869 | 62.224 | 0.001526 | 46.948 | 1096.3 | 1049.352
4685 | 0.48885 | 78.86 | 62.224 | 0.0015265 | 46.958 | 1096.3 |  | 4685 | 78.86 | 0.48885 | 62.224 | 0.0015265 | 46.958 | 1096.3 | 1049.342
4686 | 0.48901 | 78.87 | 62.224 | 0.001527 | 46.968 | 1096.3 |  | 4686 | 78.87 | 0.48901 | 62.224 | 0.001527 | 46.968 | 1096.3 | 1049.332
4687 | 0.48918 | 78.88 | 62.224 | 0.0015274 | 46.978 | 1096.3 |  | 4687 | 78.88 | 0.48918 | 62.224 | 0.0015274 | 46.978 | 1096.3 | 1049.322
4688 | 0.48934 | 78.89 | 62.224 | 0.0015279 | 46.988 | 1096.4 |  | 4688 | 78.89 | 0.48934 | 62.224 | 0.0015279 | 46.988 | 1096.4 | 1049.412
4689 | 0.4895 | 78.9 | 62.224 | 0.0015284 | 46.998 | 1096.4 |  | 4689 | 78.9 | 0.4895 | 62.224 | 0.0015284 | 46.998 | 1096.4 | 1049.402
4690 | 0.48966 | 78.91 | 62.224 | 0.0015289 | 47.008 | 1096.4 |  | 4690 | 78.91 | 0.48966 | 62.224 | 0.0015289 | 47.008 | 1096.4 | 1049.392
4691 | 0.48982 | 78.92 | 62.223 | 0.0015293 | 47.017 | 1096.4 |  | 4691 | 78.92 | 0.48982 | 62.223 | 0.0015293 | 47.017 | 1096.4 | 1049.383
4692 | 0.48998 | 78.93 | 62.223 | 0.0015298 | 47.027 | 1096.4 |  | 4692 | 78.93 | 0.48998 | 62.223 | 0.0015298 | 47.027 | 1096.4 | 1049.373
4693 | 0.49014 | 78.94 | 62.223 | 0.0015303 | 47.037 | 1096.4 |  | 4693 | 78.94 | 0.49014 | 62.223 | 0.0015303 | 47.037 | 1096.4 | 1049.363
4694 | 0.4903 | 78.95 | 62.223 | 0.0015308 | 47.047 | 1096.4 |  | 4694 | 78.95 | 0.4903 | 62.223 | 0.0015308 | 47.047 | 1096.4 | 1049.353
4695 | 0.49046 | 78.96 | 62.223 | 0.0015312 | 47.057 | 1096.4 |  | 4695 | 78.96 | 0.49046 | 62.223 | 0.0015312 | 47.057 | 1096.4 | 1049.343
4696 | 0.49062 | 78.97 | 62.223 | 0.0015317 | 47.067 | 1096.4 |  | 4696 | 78.97 | 0.49062 | 62.223 | 0.0015317 | 47.067 | 1096.4 | 1049.333
4697 | 0.49078 | 78.98 | 62.223 | 0.0015322 | 47.077 | 1096.4 |  | 4697 | 78.98 | 0.49078 | 62.223 | 0.0015322 | 47.077 | 1096.4 | 1049.323
4698 | 0.49095 | 78.99 | 62.223 | 0.0015327 | 47.087 | 1096.4 |  | 4698 | 78.99 | 0.49095 | 62.223 | 0.0015327 | 47.087 | 1096.4 | 1049.313
4699 | 0.49111 | 79 | 62.223 | 0.0015331 | 47.097 | 1096.4 |  | 4699 | 79 | 0.49111 | 62.223 | 0.0015331 | 47.097 | 1096.4 | 1049.303
4700 | 0.49127 | 79.01 | 62.223 | 0.0015336 | 47.107 | 1096.4 |  | 4700 | 79.01 | 0.49127 | 62.223 | 0.0015336 | 47.107 | 1096.4 | 1049.293
4701 | 0.49143 | 79.02 | 62.223 | 0.0015341 | 47.117 | 1096.4 |  | 4701 | 79.02 | 0.49143 | 62.223 | 0.0015341 | 47.117 | 1096.4 | 1049.283
4702 | 0.49159 | 79.03 | 62.222 | 0.0015346 | 47.127 | 1096.4 |  | 4702 | 79.03 | 0.49159 | 62.222 | 0.0015346 | 47.127 | 1096.4 | 1049.273
4703 | 0.49175 | 79.04 | 62.222 | 0.001535 | 47.137 | 1096.4 |  | 4703 | 79.04 | 0.49175 | 62.222 | 0.001535 | 47.137 | 1096.4 | 1049.263
4704 | 0.49191 | 79.05 | 62.222 | 0.0015355 | 47.147 | 1096.4 |  | 4704 | 79.05 | 0.49191 | 62.222 | 0.0015355 | 47.147 | 1096.4 | 1049.253
4705 | 0.49208 | 79.06 | 62.222 | 0.001536 | 47.157 | 1096.4 |  | 4705 | 79.06 | 0.49208 | 62.222 | 0.001536 | 47.157 | 1096.4 | 1049.243
4706 | 0.49224 | 79.07 | 62.222 | 0.0015365 | 47.167 | 1096.4 |  | 4706 | 79.07 | 0.49224 | 62.222 | 0.0015365 | 47.167 | 1096.4 | 1049.233
4707 | 0.4924 | 79.08 | 62.222 | 0.0015369 | 47.177 | 1096.4 |  | 4707 | 79.08 | 0.4924 | 62.222 | 0.0015369 | 47.177 | 1096.4 | 1049.223
4708 | 0.49256 | 79.09 | 62.222 | 0.0015374 | 47.187 | 1096.4 |  | 4708 | 79.09 | 0.49256 | 62.222 | 0.0015374 | 47.187 | 1096.4 | 1049.213
4709 | 0.49272 | 79.1 | 62.222 | 0.0015379 | 47.197 | 1096.4 |  | 4709 | 79.1 | 0.49272 | 62.222 | 0.0015379 | 47.197 | 1096.4 | 1049.203
4710 | 0.49288 | 79.11 | 62.222 | 0.0015384 | 47.207 | 1096.4 |  | 4710 | 79.11 | 0.49288 | 62.222 | 0.0015384 | 47.207 | 1096.4 | 1049.193
4711 | 0.49305 | 79.12 | 62.222 | 0.0015388 | 47.217 | 1096.5 |  | 4711 | 79.12 | 0.49305 | 62.222 | 0.0015388 | 47.217 | 1096.5 | 1049.283
4712 | 0.49321 | 79.13 | 62.222 | 0.0015393 | 47.227 | 1096.5 |  | 4712 | 79.13 | 0.49321 | 62.222 | 0.0015393 | 47.227 | 1096.5 | 1049.273
4713 | 0.49337 | 79.14 | 62.221 | 0.0015398 | 47.237 | 1096.5 |  | 4713 | 79.14 | 0.49337 | 62.221 | 0.0015398 | 47.237 | 1096.5 | 1049.263
4714 | 0.49353 | 79.15 | 62.221 | 0.0015403 | 47.247 | 1096.5 |  | 4714 | 79.15 | 0.49353 | 62.221 | 0.0015403 | 47.247 | 1096.5 | 1049.253
4715 | 0.49369 | 79.16 | 62.221 | 0.0015408 | 47.257 | 1096.5 |  | 4715 | 79.16 | 0.49369 | 62.221 | 0.0015408 | 47.257 | 1096.5 | 1049.243
4716 | 0.49386 | 79.17 | 62.221 | 0.0015412 | 47.267 | 1096.5 |  | 4716 | 79.17 | 0.49386 | 62.221 | 0.0015412 | 47.267 | 1096.5 | 1049.233
4717 | 0.49402 | 79.18 | 62.221 | 0.0015417 | 47.277 | 1096.5 |  | 4717 | 79.18 | 0.49402 | 62.221 | 0.0015417 | 47.277 | 1096.5 | 1049.223
4718 | 0.49418 | 79.19 | 62.221 | 0.0015422 | 47.287 | 1096.5 |  | 4718 | 79.19 | 0.49418 | 62.221 | 0.0015422 | 47.287 | 1096.5 | 1049.213
4719 | 0.49434 | 79.2 | 62.221 | 0.0015427 | 47.297 | 1096.5 |  | 4719 | 79.2 | 0.49434 | 62.221 | 0.0015427 | 47.297 | 1096.5 | 1049.203
4720 | 0.4945 | 79.21 | 62.221 | 0.0015431 | 47.307 | 1096.5 |  | 4720 | 79.21 | 0.4945 | 62.221 | 0.0015431 | 47.307 | 1096.5 | 1049.193
4721 | 0.49467 | 79.22 | 62.221 | 0.0015436 | 47.317 | 1096.5 |  | 4721 | 79.22 | 0.49467 | 62.221 | 0.0015436 | 47.317 | 1096.5 | 1049.183
4722 | 0.49483 | 79.23 | 62.221 | 0.0015441 | 47.327 | 1096.5 |  | 4722 | 79.23 | 0.49483 | 62.221 | 0.0015441 | 47.327 | 1096.5 | 1049.173
4723 | 0.49499 | 79.24 | 62.221 | 0.0015446 | 47.337 | 1096.5 |  | 4723 | 79.24 | 0.49499 | 62.221 | 0.0015446 | 47.337 | 1096.5 | 1049.163
4724 | 0.49515 | 79.25 | 62.22 | 0.0015451 | 47.347 | 1096.5 |  | 4724 | 79.25 | 0.49515 | 62.22 | 0.0015451 | 47.347 | 1096.5 | 1049.153
4725 | 0.49532 | 79.26 | 62.22 | 0.0015455 | 47.357 | 1096.5 |  | 4725 | 79.26 | 0.49532 | 62.22 | 0.0015455 | 47.357 | 1096.5 | 1049.143
4726 | 0.49548 | 79.27 | 62.22 | 0.001546 | 47.367 | 1096.5 |  | 4726 | 79.27 | 0.49548 | 62.22 | 0.001546 | 47.367 | 1096.5 | 1049.133
4727 | 0.49564 | 79.28 | 62.22 | 0.0015465 | 47.377 | 1096.5 |  | 4727 | 79.28 | 0.49564 | 62.22 | 0.0015465 | 47.377 | 1096.5 | 1049.123
4728 | 0.4958 | 79.29 | 62.22 | 0.001547 | 47.387 | 1096.5 |  | 4728 | 79.29 | 0.4958 | 62.22 | 0.001547 | 47.387 | 1096.5 | 1049.113
4729 | 0.49597 | 79.3 | 62.22 | 0.0015475 | 47.397 | 1096.5 |  | 4729 | 79.3 | 0.49597 | 62.22 | 0.0015475 | 47.397 | 1096.5 | 1049.103
4730 | 0.49613 | 79.31 | 62.22 | 0.0015479 | 47.407 | 1096.5 |  | 4730 | 79.31 | 0.49613 | 62.22 | 0.0015479 | 47.407 | 1096.5 | 1049.093
4731 | 0.49629 | 79.32 | 62.22 | 0.0015484 | 47.417 | 1096.5 |  | 4731 | 79.32 | 0.49629 | 62.22 | 0.0015484 | 47.417 | 1096.5 | 1049.083
4732 | 0.49645 | 79.33 | 62.22 | 0.0015489 | 47.427 | 1096.5 |  | 4732 | 79.33 | 0.49645 | 62.22 | 0.0015489 | 47.427 | 1096.5 | 1049.073
4733 | 0.49662 | 79.34 | 62.22 | 0.0015494 | 47.437 | 1096.5 |  | 4733 | 79.34 | 0.49662 | 62.22 | 0.0015494 | 47.437 | 1096.5 | 1049.063
4734 | 0.49678 | 79.35 | 62.219 | 0.0015498 | 47.447 | 1096.5 |  | 4734 | 79.35 | 0.49678 | 62.219 | 0.0015498 | 47.447 | 1096.5 | 1049.053
4735 | 0.49694 | 79.36 | 62.219 | 0.0015503 | 47.457 | 1096.6 |  | 4735 | 79.36 | 0.49694 | 62.219 | 0.0015503 | 47.457 | 1096.6 | 1049.143
4736 | 0.49711 | 79.37 | 62.219 | 0.0015508 | 47.467 | 1096.6 |  | 4736 | 79.37 | 0.49711 | 62.219 | 0.0015508 | 47.467 | 1096.6 | 1049.133
4737 | 0.49727 | 79.38 | 62.219 | 0.0015513 | 47.477 | 1096.6 |  | 4737 | 79.38 | 0.49727 | 62.219 | 0.0015513 | 47.477 | 1096.6 | 1049.123
4738 | 0.49743 | 79.39 | 62.219 | 0.0015518 | 47.487 | 1096.6 |  | 4738 | 79.39 | 0.49743 | 62.219 | 0.0015518 | 47.487 | 1096.6 | 1049.113
4739 | 0.4976 | 79.4 | 62.219 | 0.0015523 | 47.497 | 1096.6 |  | 4739 | 79.4 | 0.4976 | 62.219 | 0.0015523 | 47.497 | 1096.6 | 1049.103
4740 | 0.49776 | 79.41 | 62.219 | 0.0015527 | 47.507 | 1096.6 |  | 4740 | 79.41 | 0.49776 | 62.219 | 0.0015527 | 47.507 | 1096.6 | 1049.093
4741 | 0.49792 | 79.42 | 62.219 | 0.0015532 | 47.517 | 1096.6 |  | 4741 | 79.42 | 0.49792 | 62.219 | 0.0015532 | 47.517 | 1096.6 | 1049.083
4742 | 0.49809 | 79.43 | 62.219 | 0.0015537 | 47.527 | 1096.6 |  | 4742 | 79.43 | 0.49809 | 62.219 | 0.0015537 | 47.527 | 1096.6 | 1049.073
4743 | 0.49825 | 79.44 | 62.219 | 0.0015542 | 47.537 | 1096.6 |  | 4743 | 79.44 | 0.49825 | 62.219 | 0.0015542 | 47.537 | 1096.6 | 1049.063
4744 | 0.49841 | 79.45 | 62.219 | 0.0015547 | 47.547 | 1096.6 |  | 4744 | 79.45 | 0.49841 | 62.219 | 0.0015547 | 47.547 | 1096.6 | 1049.053
4745 | 0.49858 | 79.46 | 62.218 | 0.0015551 | 47.557 | 1096.6 |  | 4745 | 79.46 | 0.49858 | 62.218 | 0.0015551 | 47.557 | 1096.6 | 1049.043
4746 | 0.49874 | 79.47 | 62.218 | 0.0015556 | 47.567 | 1096.6 |  | 4746 | 79.47 | 0.49874 | 62.218 | 0.0015556 | 47.567 | 1096.6 | 1049.033
4747 | 0.4989 | 79.48 | 62.218 | 0.0015561 | 47.577 | 1096.6 |  | 4747 | 79.48 | 0.4989 | 62.218 | 0.0015561 | 47.577 | 1096.6 | 1049.023
4748 | 0.49907 | 79.49 | 62.218 | 0.0015566 | 47.587 | 1096.6 |  | 4748 | 79.49 | 0.49907 | 62.218 | 0.0015566 | 47.587 | 1096.6 | 1049.013
4749 | 0.49923 | 79.5 | 62.218 | 0.0015571 | 47.597 | 1096.6 |  | 4749 | 79.5 | 0.49923 | 62.218 | 0.0015571 | 47.597 | 1096.6 | 1049.003
4750 | 0.49939 | 79.51 | 62.218 | 0.0015575 | 47.607 | 1096.6 |  | 4750 | 79.51 | 0.49939 | 62.218 | 0.0015575 | 47.607 | 1096.6 | 1048.993
4751 | 0.49956 | 79.52 | 62.218 | 0.001558 | 47.617 | 1096.6 |  | 4751 | 79.52 | 0.49956 | 62.218 | 0.001558 | 47.617 | 1096.6 | 1048.983
4752 | 0.49972 | 79.53 | 62.218 | 0.0015585 | 47.627 | 1096.6 |  | 4752 | 79.53 | 0.49972 | 62.218 | 0.0015585 | 47.627 | 1096.6 | 1048.973
4753 | 0.49988 | 79.54 | 62.218 | 0.001559 | 47.637 | 1096.6 |  | 4753 | 79.54 | 0.49988 | 62.218 | 0.001559 | 47.637 | 1096.6 | 1048.963
4754 | 0.50005 | 79.55 | 62.218 | 0.0015595 | 47.647 | 1096.6 |  | 4754 | 79.55 | 0.50005 | 62.218 | 0.0015595 | 47.647 | 1096.6 | 1048.953
4755 | 0.50021 | 79.56 | 62.218 | 0.00156 | 47.657 | 1096.6 |  | 4755 | 79.56 | 0.50021 | 62.218 | 0.00156 | 47.657 | 1096.6 | 1048.943
4756 | 0.50038 | 79.57 | 62.217 | 0.0015604 | 47.667 | 1096.6 |  | 4756 | 79.57 | 0.50038 | 62.217 | 0.0015604 | 47.667 | 1096.6 | 1048.933
4757 | 0.50054 | 79.58 | 62.217 | 0.0015609 | 47.677 | 1096.6 |  | 4757 | 79.58 | 0.50054 | 62.217 | 0.0015609 | 47.677 | 1096.6 | 1048.923
4758 | 0.5007 | 79.59 | 62.217 | 0.0015614 | 47.687 | 1096.7 |  | 4758 | 79.59 | 0.5007 | 62.217 | 0.0015614 | 47.687 | 1096.7 | 1049.013
4759 | 0.50087 | 79.6 | 62.217 | 0.0015619 | 47.697 | 1096.7 |  | 4759 | 79.6 | 0.50087 | 62.217 | 0.0015619 | 47.697 | 1096.7 | 1049.003
4760 | 0.50103 | 79.61 | 62.217 | 0.0015624 | 47.707 | 1096.7 |  | 4760 | 79.61 | 0.50103 | 62.217 | 0.0015624 | 47.707 | 1096.7 | 1048.993
4761 | 0.5012 | 79.62 | 62.217 | 0.0015629 | 47.717 | 1096.7 |  | 4761 | 79.62 | 0.5012 | 62.217 | 0.0015629 | 47.717 | 1096.7 | 1048.983
4762 | 0.50136 | 79.63 | 62.217 | 0.0015633 | 47.727 | 1096.7 |  | 4762 | 79.63 | 0.50136 | 62.217 | 0.0015633 | 47.727 | 1096.7 | 1048.973
4763 | 0.50152 | 79.64 | 62.217 | 0.0015638 | 47.737 | 1096.7 |  | 4763 | 79.64 | 0.50152 | 62.217 | 0.0015638 | 47.737 | 1096.7 | 1048.963
4764 | 0.50169 | 79.65 | 62.217 | 0.0015643 | 47.747 | 1096.7 |  | 4764 | 79.65 | 0.50169 | 62.217 | 0.0015643 | 47.747 | 1096.7 | 1048.953
4765 | 0.50185 | 79.66 | 62.217 | 0.0015648 | 47.757 | 1096.7 |  | 4765 | 79.66 | 0.50185 | 62.217 | 0.0015648 | 47.757 | 1096.7 | 1048.943
4766 | 0.50202 | 79.67 | 62.217 | 0.0015653 | 47.767 | 1096.7 |  | 4766 | 79.67 | 0.50202 | 62.217 | 0.0015653 | 47.767 | 1096.7 | 1048.933
4767 | 0.50218 | 79.68 | 62.216 | 0.0015658 | 47.777 | 1096.7 |  | 4767 | 79.68 | 0.50218 | 62.216 | 0.0015658 | 47.777 | 1096.7 | 1048.923
4768 | 0.50235 | 79.69 | 62.216 | 0.0015662 | 47.787 | 1096.7 |  | 4768 | 79.69 | 0.50235 | 62.216 | 0.0015662 | 47.787 | 1096.7 | 1048.913
4769 | 0.50251 | 79.7 | 62.216 | 0.0015667 | 47.797 | 1096.7 |  | 4769 | 79.7 | 0.50251 | 62.216 | 0.0015667 | 47.797 | 1096.7 | 1048.903
4770 | 0.50268 | 79.71 | 62.216 | 0.0015672 | 47.807 | 1096.7 |  | 4770 | 79.71 | 0.50268 | 62.216 | 0.0015672 | 47.807 | 1096.7 | 1048.893
4771 | 0.50284 | 79.72 | 62.216 | 0.0015677 | 47.817 | 1096.7 |  | 4771 | 79.72 | 0.50284 | 62.216 | 0.0015677 | 47.817 | 1096.7 | 1048.883
4772 | 0.503 | 79.73 | 62.216 | 0.0015682 | 47.827 | 1096.7 |  | 4772 | 79.73 | 0.503 | 62.216 | 0.0015682 | 47.827 | 1096.7 | 1048.873
4773 | 0.50317 | 79.74 | 62.216 | 0.0015687 | 47.837 | 1096.7 |  | 4773 | 79.74 | 0.50317 | 62.216 | 0.0015687 | 47.837 | 1096.7 | 1048.863
4774 | 0.50333 | 79.75 | 62.216 | 0.0015692 | 47.847 | 1096.7 |  | 4774 | 79.75 | 0.50333 | 62.216 | 0.0015692 | 47.847 | 1096.7 | 1048.853
4775 | 0.5035 | 79.76 | 62.216 | 0.0015696 | 47.857 | 1096.7 |  | 4775 | 79.76 | 0.5035 | 62.216 | 0.0015696 | 47.857 | 1096.7 | 1048.843
4776 | 0.50366 | 79.77 | 62.216 | 0.0015701 | 47.867 | 1096.7 |  | 4776 | 79.77 | 0.50366 | 62.216 | 0.0015701 | 47.867 | 1096.7 | 1048.833
4777 | 0.50383 | 79.78 | 62.215 | 0.0015706 | 47.877 | 1096.7 |  | 4777 | 79.78 | 0.50383 | 62.215 | 0.0015706 | 47.877 | 1096.7 | 1048.823
4778 | 0.50399 | 79.79 | 62.215 | 0.0015711 | 47.887 | 1096.7 |  | 4778 | 79.79 | 0.50399 | 62.215 | 0.0015711 | 47.887 | 1096.7 | 1048.813
4779 | 0.50416 | 79.8 | 62.215 | 0.0015716 | 47.897 | 1096.7 |  | 4779 | 79.8 | 0.50416 | 62.215 | 0.0015716 | 47.897 | 1096.7 | 1048.803
4780 | 0.50432 | 79.81 | 62.215 | 0.0015721 | 47.907 | 1096.7 |  | 4780 | 79.81 | 0.50432 | 62.215 | 0.0015721 | 47.907 | 1096.7 | 1048.793
4781 | 0.50449 | 79.82 | 62.215 | 0.0015726 | 47.917 | 1096.8 |  | 4781 | 79.82 | 0.50449 | 62.215 | 0.0015726 | 47.917 | 1096.8 | 1048.883
4782 | 0.50465 | 79.83 | 62.215 | 0.001573 | 47.927 | 1096.8 |  | 4782 | 79.83 | 0.50465 | 62.215 | 0.001573 | 47.927 | 1096.8 | 1048.873
4783 | 0.50482 | 79.84 | 62.215 | 0.0015735 | 47.937 | 1096.8 |  | 4783 | 79.84 | 0.50482 | 62.215 | 0.0015735 | 47.937 | 1096.8 | 1048.863
4784 | 0.50498 | 79.85 | 62.215 | 0.001574 | 47.947 | 1096.8 |  | 4784 | 79.85 | 0.50498 | 62.215 | 0.001574 | 47.947 | 1096.8 | 1048.853
4785 | 0.50515 | 79.86 | 62.215 | 0.0015745 | 47.957 | 1096.8 |  | 4785 | 79.86 | 0.50515 | 62.215 | 0.0015745 | 47.957 | 1096.8 | 1048.843
4786 | 0.50531 | 79.87 | 62.215 | 0.001575 | 47.967 | 1096.8 |  | 4786 | 79.87 | 0.50531 | 62.215 | 0.001575 | 47.967 | 1096.8 | 1048.833
4787 | 0.50548 | 79.88 | 62.215 | 0.0015755 | 47.977 | 1096.8 |  | 4787 | 79.88 | 0.50548 | 62.215 | 0.0015755 | 47.977 | 1096.8 | 1048.823
4788 | 0.50565 | 79.89 | 62.214 | 0.001576 | 47.987 | 1096.8 |  | 4788 | 79.89 | 0.50565 | 62.214 | 0.001576 | 47.987 | 1096.8 | 1048.813
4789 | 0.50581 | 79.9 | 62.214 | 0.0015764 | 47.997 | 1096.8 |  | 4789 | 79.9 | 0.50581 | 62.214 | 0.0015764 | 47.997 | 1096.8 | 1048.803
4790 | 0.50598 | 79.91 | 62.214 | 0.0015769 | 48.007 | 1096.8 |  | 4790 | 79.91 | 0.50598 | 62.214 | 0.0015769 | 48.007 | 1096.8 | 1048.793
4791 | 0.50614 | 79.92 | 62.214 | 0.0015774 | 48.017 | 1096.8 |  | 4791 | 79.92 | 0.50614 | 62.214 | 0.0015774 | 48.017 | 1096.8 | 1048.783
4792 | 0.50631 | 79.93 | 62.214 | 0.0015779 | 48.027 | 1096.8 |  | 4792 | 79.93 | 0.50631 | 62.214 | 0.0015779 | 48.027 | 1096.8 | 1048.773
4793 | 0.50647 | 79.94 | 62.214 | 0.0015784 | 48.037 | 1096.8 |  | 4793 | 79.94 | 0.50647 | 62.214 | 0.0015784 | 48.037 | 1096.8 | 1048.763
4794 | 0.50664 | 79.95 | 62.214 | 0.0015789 | 48.047 | 1096.8 |  | 4794 | 79.95 | 0.50664 | 62.214 | 0.0015789 | 48.047 | 1096.8 | 1048.753
4795 | 0.5068 | 79.96 | 62.214 | 0.0015794 | 48.057 | 1096.8 |  | 4795 | 79.96 | 0.5068 | 62.214 | 0.0015794 | 48.057 | 1096.8 | 1048.743
4796 | 0.50697 | 79.97 | 62.214 | 0.0015799 | 48.067 | 1096.8 |  | 4796 | 79.97 | 0.50697 | 62.214 | 0.0015799 | 48.067 | 1096.8 | 1048.733
4797 | 0.50714 | 79.98 | 62.214 | 0.0015803 | 48.077 | 1096.8 |  | 4797 | 79.98 | 0.50714 | 62.214 | 0.0015803 | 48.077 | 1096.8 | 1048.723
4798 | 0.5073 | 79.99 | 62.213 | 0.0015808 | 48.087 | 1096.8 |  | 4798 | 79.99 | 0.5073 | 62.213 | 0.0015808 | 48.087 | 1096.8 | 1048.713
4799 | 0.50747 | 80 | 62.213 | 0.0015813 | 48.097 | 1096.8 |  | 4799 | 80 | 0.50747 | 62.213 | 0.0015813 | 48.097 | 1096.8 | 1048.703
4800 | 0.50763 | 80.01 | 62.213 | 0.0015818 | 48.107 | 1096.8 |  | 4800 | 80.01 | 0.50763 | 62.213 | 0.0015818 | 48.107 | 1096.8 | 1048.693
4801 | 0.5078 | 80.02 | 62.213 | 0.0015823 | 48.117 | 1096.8 |  | 4801 | 80.02 | 0.5078 | 62.213 | 0.0015823 | 48.117 | 1096.8 | 1048.683
4802 | 0.50797 | 80.03 | 62.213 | 0.0015828 | 48.127 | 1096.8 |  | 4802 | 80.03 | 0.50797 | 62.213 | 0.0015828 | 48.127 | 1096.8 | 1048.673
4803 | 0.50813 | 80.04 | 62.213 | 0.0015833 | 48.137 | 1096.8 |  | 4803 | 80.04 | 0.50813 | 62.213 | 0.0015833 | 48.137 | 1096.8 | 1048.663
4804 | 0.5083 | 80.05 | 62.213 | 0.0015838 | 48.147 | 1096.9 |  | 4804 | 80.05 | 0.5083 | 62.213 | 0.0015838 | 48.147 | 1096.9 | 1048.753
4805 | 0.50846 | 80.06 | 62.213 | 0.0015843 | 48.157 | 1096.9 |  | 4805 | 80.06 | 0.50846 | 62.213 | 0.0015843 | 48.157 | 1096.9 | 1048.743
4806 | 0.50863 | 80.07 | 62.213 | 0.0015847 | 48.167 | 1096.9 |  | 4806 | 80.07 | 0.50863 | 62.213 | 0.0015847 | 48.167 | 1096.9 | 1048.733
4807 | 0.5088 | 80.08 | 62.213 | 0.0015852 | 48.177 | 1096.9 |  | 4807 | 80.08 | 0.5088 | 62.213 | 0.0015852 | 48.177 | 1096.9 | 1048.723
4808 | 0.50896 | 80.09 | 62.213 | 0.0015857 | 48.187 | 1096.9 |  | 4808 | 80.09 | 0.50896 | 62.213 | 0.0015857 | 48.187 | 1096.9 | 1048.713
4809 | 0.50913 | 80.1 | 62.212 | 0.0015862 | 48.197 | 1096.9 |  | 4809 | 80.1 | 0.50913 | 62.212 | 0.0015862 | 48.197 | 1096.9 | 1048.703
4810 | 0.5093 | 80.11 | 62.212 | 0.0015867 | 48.207 | 1096.9 |  | 4810 | 80.11 | 0.5093 | 62.212 | 0.0015867 | 48.207 | 1096.9 | 1048.693
4811 | 0.50946 | 80.12 | 62.212 | 0.0015872 | 48.217 | 1096.9 |  | 4811 | 80.12 | 0.50946 | 62.212 | 0.0015872 | 48.217 | 1096.9 | 1048.683
4812 | 0.50963 | 80.13 | 62.212 | 0.0015877 | 48.227 | 1096.9 |  | 4812 | 80.13 | 0.50963 | 62.212 | 0.0015877 | 48.227 | 1096.9 | 1048.673
4813 | 0.5098 | 80.14 | 62.212 | 0.0015882 | 48.237 | 1096.9 |  | 4813 | 80.14 | 0.5098 | 62.212 | 0.0015882 | 48.237 | 1096.9 | 1048.663
4814 | 0.50996 | 80.15 | 62.212 | 0.0015887 | 48.247 | 1096.9 |  | 4814 | 80.15 | 0.50996 | 62.212 | 0.0015887 | 48.247 | 1096.9 | 1048.653
4815 | 0.51013 | 80.16 | 62.212 | 0.0015892 | 48.257 | 1096.9 |  | 4815 | 80.16 | 0.51013 | 62.212 | 0.0015892 | 48.257 | 1096.9 | 1048.643
4816 | 0.5103 | 80.17 | 62.212 | 0.0015896 | 48.267 | 1096.9 |  | 4816 | 80.17 | 0.5103 | 62.212 | 0.0015896 | 48.267 | 1096.9 | 1048.633
4817 | 0.51046 | 80.18 | 62.212 | 0.0015901 | 48.277 | 1096.9 |  | 4817 | 80.18 | 0.51046 | 62.212 | 0.0015901 | 48.277 | 1096.9 | 1048.623
4818 | 0.51063 | 80.19 | 62.212 | 0.0015906 | 48.287 | 1096.9 |  | 4818 | 80.19 | 0.51063 | 62.212 | 0.0015906 | 48.287 | 1096.9 | 1048.613
4819 | 0.5108 | 80.2 | 62.212 | 0.0015911 | 48.297 | 1096.9 |  | 4819 | 80.2 | 0.5108 | 62.212 | 0.0015911 | 48.297 | 1096.9 | 1048.603
4820 | 0.51096 | 80.21 | 62.211 | 0.0015916 | 48.307 | 1096.9 |  | 4820 | 80.21 | 0.51096 | 62.211 | 0.0015916 | 48.307 | 1096.9 | 1048.593
4821 | 0.51113 | 80.22 | 62.211 | 0.0015921 | 48.317 | 1096.9 |  | 4821 | 80.22 | 0.51113 | 62.211 | 0.0015921 | 48.317 | 1096.9 | 1048.583
4822 | 0.5113 | 80.23 | 62.211 | 0.0015926 | 48.327 | 1096.9 |  | 4822 | 80.23 | 0.5113 | 62.211 | 0.0015926 | 48.327 | 1096.9 | 1048.573
4823 | 0.51146 | 80.24 | 62.211 | 0.0015931 | 48.337 | 1096.9 |  | 4823 | 80.24 | 0.51146 | 62.211 | 0.0015931 | 48.337 | 1096.9 | 1048.563
4824 | 0.51163 | 80.25 | 62.211 | 0.0015936 | 48.347 | 1096.9 |  | 4824 | 80.25 | 0.51163 | 62.211 | 0.0015936 | 48.347 | 1096.9 | 1048.553
4825 | 0.5118 | 80.26 | 62.211 | 0.0015941 | 48.357 | 1096.9 |  | 4825 | 80.26 | 0.5118 | 62.211 | 0.0015941 | 48.357 | 1096.9 | 1048.543
4826 | 0.51197 | 80.27 | 62.211 | 0.0015946 | 48.367 | 1096.9 |  | 4826 | 80.27 | 0.51197 | 62.211 | 0.0015946 | 48.367 | 1096.9 | 1048.533
4827 | 0.51213 | 80.28 | 62.211 | 0.001595 | 48.377 | 1097 |  | 4827 | 80.28 | 0.51213 | 62.211 | 0.001595 | 48.377 | 1097 | 1048.623
4828 | 0.5123 | 80.29 | 62.211 | 0.0015955 | 48.387 | 1097 |  | 4828 | 80.29 | 0.5123 | 62.211 | 0.0015955 | 48.387 | 1097 | 1048.613
4829 | 0.51247 | 80.3 | 62.211 | 0.001596 | 48.397 | 1097 |  | 4829 | 80.3 | 0.51247 | 62.211 | 0.001596 | 48.397 | 1097 | 1048.603
4830 | 0.51264 | 80.31 | 62.21 | 0.0015965 | 48.407 | 1097 |  | 4830 | 80.31 | 0.51264 | 62.21 | 0.0015965 | 48.407 | 1097 | 1048.593
4831 | 0.5128 | 80.32 | 62.21 | 0.001597 | 48.417 | 1097 |  | 4831 | 80.32 | 0.5128 | 62.21 | 0.001597 | 48.417 | 1097 | 1048.583
4832 | 0.51297 | 80.33 | 62.21 | 0.0015975 | 48.427 | 1097 |  | 4832 | 80.33 | 0.51297 | 62.21 | 0.0015975 | 48.427 | 1097 | 1048.573
4833 | 0.51314 | 80.34 | 62.21 | 0.001598 | 48.437 | 1097 |  | 4833 | 80.34 | 0.51314 | 62.21 | 0.001598 | 48.437 | 1097 | 1048.563
4834 | 0.51331 | 80.35 | 62.21 | 0.0015985 | 48.447 | 1097 |  | 4834 | 80.35 | 0.51331 | 62.21 | 0.0015985 | 48.447 | 1097 | 1048.553
4835 | 0.51347 | 80.36 | 62.21 | 0.001599 | 48.457 | 1097 |  | 4835 | 80.36 | 0.51347 | 62.21 | 0.001599 | 48.457 | 1097 | 1048.543
4836 | 0.51364 | 80.37 | 62.21 | 0.0015995 | 48.467 | 1097 |  | 4836 | 80.37 | 0.51364 | 62.21 | 0.0015995 | 48.467 | 1097 | 1048.533
4837 | 0.51381 | 80.38 | 62.21 | 0.0016 | 48.477 | 1097 |  | 4837 | 80.38 | 0.51381 | 62.21 | 0.0016 | 48.477 | 1097 | 1048.523
4838 | 0.51398 | 80.39 | 62.21 | 0.0016005 | 48.487 | 1097 |  | 4838 | 80.39 | 0.51398 | 62.21 | 0.0016005 | 48.487 | 1097 | 1048.513
4839 | 0.51414 | 80.4 | 62.21 | 0.001601 | 48.497 | 1097 |  | 4839 | 80.4 | 0.51414 | 62.21 | 0.001601 | 48.497 | 1097 | 1048.503
4840 | 0.51431 | 80.41 | 62.21 | 0.0016015 | 48.507 | 1097 |  | 4840 | 80.41 | 0.51431 | 62.21 | 0.0016015 | 48.507 | 1097 | 1048.493
4841 | 0.51448 | 80.42 | 62.209 | 0.001602 | 48.517 | 1097 |  | 4841 | 80.42 | 0.51448 | 62.209 | 0.001602 | 48.517 | 1097 | 1048.483
4842 | 0.51465 | 80.43 | 62.209 | 0.0016024 | 48.526 | 1097 |  | 4842 | 80.43 | 0.51465 | 62.209 | 0.0016024 | 48.526 | 1097 | 1048.474
4843 | 0.51482 | 80.44 | 62.209 | 0.0016029 | 48.536 | 1097 |  | 4843 | 80.44 | 0.51482 | 62.209 | 0.0016029 | 48.536 | 1097 | 1048.464
4844 | 0.51498 | 80.45 | 62.209 | 0.0016034 | 48.546 | 1097 |  | 4844 | 80.45 | 0.51498 | 62.209 | 0.0016034 | 48.546 | 1097 | 1048.454
4845 | 0.51515 | 80.46 | 62.209 | 0.0016039 | 48.556 | 1097 |  | 4845 | 80.46 | 0.51515 | 62.209 | 0.0016039 | 48.556 | 1097 | 1048.444
4846 | 0.51532 | 80.47 | 62.209 | 0.0016044 | 48.566 | 1097 |  | 4846 | 80.47 | 0.51532 | 62.209 | 0.0016044 | 48.566 | 1097 | 1048.434
4847 | 0.51549 | 80.48 | 62.209 | 0.0016049 | 48.576 | 1097 |  | 4847 | 80.48 | 0.51549 | 62.209 | 0.0016049 | 48.576 | 1097 | 1048.424
4848 | 0.51566 | 80.49 | 62.209 | 0.0016054 | 48.586 | 1097 |  | 4848 | 80.49 | 0.51566 | 62.209 | 0.0016054 | 48.586 | 1097 | 1048.414
4849 | 0.51583 | 80.5 | 62.209 | 0.0016059 | 48.596 | 1097 |  | 4849 | 80.5 | 0.51583 | 62.209 | 0.0016059 | 48.596 | 1097 | 1048.404
4850 | 0.51599 | 80.51 | 62.209 | 0.0016064 | 48.606 | 1097.1 |  | 4850 | 80.51 | 0.51599 | 62.209 | 0.0016064 | 48.606 | 1097.1 | 1048.494
4851 | 0.51616 | 80.52 | 62.208 | 0.0016069 | 48.616 | 1097.1 |  | 4851 | 80.52 | 0.51616 | 62.208 | 0.0016069 | 48.616 | 1097.1 | 1048.484
4852 | 0.51633 | 80.53 | 62.208 | 0.0016074 | 48.626 | 1097.1 |  | 4852 | 80.53 | 0.51633 | 62.208 | 0.0016074 | 48.626 | 1097.1 | 1048.474
4853 | 0.5165 | 80.54 | 62.208 | 0.0016079 | 48.636 | 1097.1 |  | 4853 | 80.54 | 0.5165 | 62.208 | 0.0016079 | 48.636 | 1097.1 | 1048.464
4854 | 0.51667 | 80.55 | 62.208 | 0.0016084 | 48.646 | 1097.1 |  | 4854 | 80.55 | 0.51667 | 62.208 | 0.0016084 | 48.646 | 1097.1 | 1048.454
4855 | 0.51684 | 80.56 | 62.208 | 0.0016089 | 48.656 | 1097.1 |  | 4855 | 80.56 | 0.51684 | 62.208 | 0.0016089 | 48.656 | 1097.1 | 1048.444
4856 | 0.517 | 80.57 | 62.208 | 0.0016094 | 48.666 | 1097.1 |  | 4856 | 80.57 | 0.517 | 62.208 | 0.0016094 | 48.666 | 1097.1 | 1048.434
4857 | 0.51717 | 80.58 | 62.208 | 0.0016099 | 48.676 | 1097.1 |  | 4857 | 80.58 | 0.51717 | 62.208 | 0.0016099 | 48.676 | 1097.1 | 1048.424
4858 | 0.51734 | 80.59 | 62.208 | 0.0016104 | 48.686 | 1097.1 |  | 4858 | 80.59 | 0.51734 | 62.208 | 0.0016104 | 48.686 | 1097.1 | 1048.414
4859 | 0.51751 | 80.6 | 62.208 | 0.0016109 | 48.696 | 1097.1 |  | 4859 | 80.6 | 0.51751 | 62.208 | 0.0016109 | 48.696 | 1097.1 | 1048.404
4860 | 0.51768 | 80.61 | 62.208 | 0.0016114 | 48.706 | 1097.1 |  | 4860 | 80.61 | 0.51768 | 62.208 | 0.0016114 | 48.706 | 1097.1 | 1048.394
4861 | 0.51785 | 80.62 | 62.208 | 0.0016119 | 48.716 | 1097.1 |  | 4861 | 80.62 | 0.51785 | 62.208 | 0.0016119 | 48.716 | 1097.1 | 1048.384
4862 | 0.51802 | 80.63 | 62.207 | 0.0016124 | 48.726 | 1097.1 |  | 4862 | 80.63 | 0.51802 | 62.207 | 0.0016124 | 48.726 | 1097.1 | 1048.374
4863 | 0.51819 | 80.64 | 62.207 | 0.0016128 | 48.736 | 1097.1 |  | 4863 | 80.64 | 0.51819 | 62.207 | 0.0016128 | 48.736 | 1097.1 | 1048.364
4864 | 0.51836 | 80.65 | 62.207 | 0.0016133 | 48.746 | 1097.1 |  | 4864 | 80.65 | 0.51836 | 62.207 | 0.0016133 | 48.746 | 1097.1 | 1048.354
4865 | 0.51852 | 80.66 | 62.207 | 0.0016138 | 48.756 | 1097.1 |  | 4865 | 80.66 | 0.51852 | 62.207 | 0.0016138 | 48.756 | 1097.1 | 1048.344
4866 | 0.51869 | 80.67 | 62.207 | 0.0016143 | 48.766 | 1097.1 |  | 4866 | 80.67 | 0.51869 | 62.207 | 0.0016143 | 48.766 | 1097.1 | 1048.334
4867 | 0.51886 | 80.68 | 62.207 | 0.0016148 | 48.776 | 1097.1 |  | 4867 | 80.68 | 0.51886 | 62.207 | 0.0016148 | 48.776 | 1097.1 | 1048.324
4868 | 0.51903 | 80.69 | 62.207 | 0.0016153 | 48.786 | 1097.1 |  | 4868 | 80.69 | 0.51903 | 62.207 | 0.0016153 | 48.786 | 1097.1 | 1048.314
4869 | 0.5192 | 80.7 | 62.207 | 0.0016158 | 48.796 | 1097.1 |  | 4869 | 80.7 | 0.5192 | 62.207 | 0.0016158 | 48.796 | 1097.1 | 1048.304
4870 | 0.51937 | 80.71 | 62.207 | 0.0016163 | 48.806 | 1097.1 |  | 4870 | 80.71 | 0.51937 | 62.207 | 0.0016163 | 48.806 | 1097.1 | 1048.294
4871 | 0.51954 | 80.72 | 62.207 | 0.0016168 | 48.816 | 1097.1 |  | 4871 | 80.72 | 0.51954 | 62.207 | 0.0016168 | 48.816 | 1097.1 | 1048.284
4872 | 0.51971 | 80.73 | 62.206 | 0.0016173 | 48.826 | 1097.1 |  | 4872 | 80.73 | 0.51971 | 62.206 | 0.0016173 | 48.826 | 1097.1 | 1048.274
4873 | 0.51988 | 80.74 | 62.206 | 0.0016178 | 48.836 | 1097.2 |  | 4873 | 80.74 | 0.51988 | 62.206 | 0.0016178 | 48.836 | 1097.2 | 1048.364
4874 | 0.52005 | 80.75 | 62.206 | 0.0016183 | 48.846 | 1097.2 |  | 4874 | 80.75 | 0.52005 | 62.206 | 0.0016183 | 48.846 | 1097.2 | 1048.354
4875 | 0.52022 | 80.76 | 62.206 | 0.0016188 | 48.856 | 1097.2 |  | 4875 | 80.76 | 0.52022 | 62.206 | 0.0016188 | 48.856 | 1097.2 | 1048.344
4876 | 0.52039 | 80.77 | 62.206 | 0.0016193 | 48.866 | 1097.2 |  | 4876 | 80.77 | 0.52039 | 62.206 | 0.0016193 | 48.866 | 1097.2 | 1048.334
4877 | 0.52056 | 80.78 | 62.206 | 0.0016198 | 48.876 | 1097.2 |  | 4877 | 80.78 | 0.52056 | 62.206 | 0.0016198 | 48.876 | 1097.2 | 1048.324
4878 | 0.52073 | 80.79 | 62.206 | 0.0016203 | 48.886 | 1097.2 |  | 4878 | 80.79 | 0.52073 | 62.206 | 0.0016203 | 48.886 | 1097.2 | 1048.314
4879 | 0.5209 | 80.8 | 62.206 | 0.0016208 | 48.896 | 1097.2 |  | 4879 | 80.8 | 0.5209 | 62.206 | 0.0016208 | 48.896 | 1097.2 | 1048.304
4880 | 0.52107 | 80.81 | 62.206 | 0.0016213 | 48.906 | 1097.2 |  | 4880 | 80.81 | 0.52107 | 62.206 | 0.0016213 | 48.906 | 1097.2 | 1048.294
4881 | 0.52124 | 80.82 | 62.206 | 0.0016218 | 48.916 | 1097.2 |  | 4881 | 80.82 | 0.52124 | 62.206 | 0.0016218 | 48.916 | 1097.2 | 1048.284
4882 | 0.52141 | 80.83 | 62.206 | 0.0016223 | 48.926 | 1097.2 |  | 4882 | 80.83 | 0.52141 | 62.206 | 0.0016223 | 48.926 | 1097.2 | 1048.274
4883 | 0.52158 | 80.84 | 62.205 | 0.0016228 | 48.936 | 1097.2 |  | 4883 | 80.84 | 0.52158 | 62.205 | 0.0016228 | 48.936 | 1097.2 | 1048.264
4884 | 0.52175 | 80.85 | 62.205 | 0.0016233 | 48.946 | 1097.2 |  | 4884 | 80.85 | 0.52175 | 62.205 | 0.0016233 | 48.946 | 1097.2 | 1048.254
4885 | 0.52192 | 80.86 | 62.205 | 0.0016238 | 48.956 | 1097.2 |  | 4885 | 80.86 | 0.52192 | 62.205 | 0.0016238 | 48.956 | 1097.2 | 1048.244
4886 | 0.52209 | 80.87 | 62.205 | 0.0016243 | 48.966 | 1097.2 |  | 4886 | 80.87 | 0.52209 | 62.205 | 0.0016243 | 48.966 | 1097.2 | 1048.234
4887 | 0.52226 | 80.88 | 62.205 | 0.0016248 | 48.976 | 1097.2 |  | 4887 | 80.88 | 0.52226 | 62.205 | 0.0016248 | 48.976 | 1097.2 | 1048.224
4888 | 0.52243 | 80.89 | 62.205 | 0.0016253 | 48.986 | 1097.2 |  | 4888 | 80.89 | 0.52243 | 62.205 | 0.0016253 | 48.986 | 1097.2 | 1048.214
4889 | 0.5226 | 80.9 | 62.205 | 0.0016258 | 48.996 | 1097.2 |  | 4889 | 80.9 | 0.5226 | 62.205 | 0.0016258 | 48.996 | 1097.2 | 1048.204
4890 | 0.52277 | 80.91 | 62.205 | 0.0016263 | 49.006 | 1097.2 |  | 4890 | 80.91 | 0.52277 | 62.205 | 0.0016263 | 49.006 | 1097.2 | 1048.194
4891 | 0.52294 | 80.92 | 62.205 | 0.0016268 | 49.016 | 1097.2 |  | 4891 | 80.92 | 0.52294 | 62.205 | 0.0016268 | 49.016 | 1097.2 | 1048.184
4892 | 0.52311 | 80.93 | 62.205 | 0.0016273 | 49.026 | 1097.2 |  | 4892 | 80.93 | 0.52311 | 62.205 | 0.0016273 | 49.026 | 1097.2 | 1048.174
4893 | 0.52328 | 80.94 | 62.204 | 0.0016278 | 49.036 | 1097.2 |  | 4893 | 80.94 | 0.52328 | 62.204 | 0.0016278 | 49.036 | 1097.2 | 1048.164
4894 | 0.52345 | 80.95 | 62.204 | 0.0016283 | 49.046 | 1097.2 |  | 4894 | 80.95 | 0.52345 | 62.204 | 0.0016283 | 49.046 | 1097.2 | 1048.154
4895 | 0.52362 | 80.96 | 62.204 | 0.0016288 | 49.056 | 1097.2 |  | 4895 | 80.96 | 0.52362 | 62.204 | 0.0016288 | 49.056 | 1097.2 | 1048.144
4896 | 0.52379 | 80.97 | 62.204 | 0.0016293 | 49.066 | 1097.3 |  | 4896 | 80.97 | 0.52379 | 62.204 | 0.0016293 | 49.066 | 1097.3 | 1048.234
4897 | 0.52396 | 80.98 | 62.204 | 0.0016298 | 49.076 | 1097.3 |  | 4897 | 80.98 | 0.52396 | 62.204 | 0.0016298 | 49.076 | 1097.3 | 1048.224
4898 | 0.52413 | 80.99 | 62.204 | 0.0016303 | 49.086 | 1097.3 |  | 4898 | 80.99 | 0.52413 | 62.204 | 0.0016303 | 49.086 | 1097.3 | 1048.214
4899 | 0.5243 | 81 | 62.204 | 0.0016308 | 49.096 | 1097.3 |  | 4899 | 81 | 0.5243 | 62.204 | 0.0016308 | 49.096 | 1097.3 | 1048.204
4900 | 0.52447 | 81.01 | 62.204 | 0.0016313 | 49.106 | 1097.3 |  | 4900 | 81.01 | 0.52447 | 62.204 | 0.0016313 | 49.106 | 1097.3 | 1048.194
4901 | 0.52464 | 81.02 | 62.204 | 0.0016318 | 49.116 | 1097.3 |  | 4901 | 81.02 | 0.52464 | 62.204 | 0.0016318 | 49.116 | 1097.3 | 1048.184
4902 | 0.52481 | 81.03 | 62.204 | 0.0016323 | 49.126 | 1097.3 |  | 4902 | 81.03 | 0.52481 | 62.204 | 0.0016323 | 49.126 | 1097.3 | 1048.174
4903 | 0.52499 | 81.04 | 62.203 | 0.0016328 | 49.136 | 1097.3 |  | 4903 | 81.04 | 0.52499 | 62.203 | 0.0016328 | 49.136 | 1097.3 | 1048.164
4904 | 0.52516 | 81.05 | 62.203 | 0.0016333 | 49.146 | 1097.3 |  | 4904 | 81.05 | 0.52516 | 62.203 | 0.0016333 | 49.146 | 1097.3 | 1048.154
4905 | 0.52533 | 81.06 | 62.203 | 0.0016338 | 49.156 | 1097.3 |  | 4905 | 81.06 | 0.52533 | 62.203 | 0.0016338 | 49.156 | 1097.3 | 1048.144
4906 | 0.5255 | 81.07 | 62.203 | 0.0016343 | 49.166 | 1097.3 |  | 4906 | 81.07 | 0.5255 | 62.203 | 0.0016343 | 49.166 | 1097.3 | 1048.134
4907 | 0.52567 | 81.08 | 62.203 | 0.0016348 | 49.176 | 1097.3 |  | 4907 | 81.08 | 0.52567 | 62.203 | 0.0016348 | 49.176 | 1097.3 | 1048.124
4908 | 0.52584 | 81.09 | 62.203 | 0.0016353 | 49.186 | 1097.3 |  | 4908 | 81.09 | 0.52584 | 62.203 | 0.0016353 | 49.186 | 1097.3 | 1048.114
4909 | 0.52601 | 81.1 | 62.203 | 0.0016358 | 49.196 | 1097.3 |  | 4909 | 81.1 | 0.52601 | 62.203 | 0.0016358 | 49.196 | 1097.3 | 1048.104
4910 | 0.52618 | 81.11 | 62.203 | 0.0016363 | 49.206 | 1097.3 |  | 4910 | 81.11 | 0.52618 | 62.203 | 0.0016363 | 49.206 | 1097.3 | 1048.094
4911 | 0.52635 | 81.12 | 62.203 | 0.0016368 | 49.216 | 1097.3 |  | 4911 | 81.12 | 0.52635 | 62.203 | 0.0016368 | 49.216 | 1097.3 | 1048.084
4912 | 0.52653 | 81.13 | 62.203 | 0.0016373 | 49.226 | 1097.3 |  | 4912 | 81.13 | 0.52653 | 62.203 | 0.0016373 | 49.226 | 1097.3 | 1048.074
4913 | 0.5267 | 81.14 | 62.203 | 0.0016379 | 49.236 | 1097.3 |  | 4913 | 81.14 | 0.5267 | 62.203 | 0.0016379 | 49.236 | 1097.3 | 1048.064
4914 | 0.52687 | 81.15 | 62.202 | 0.0016384 | 49.246 | 1097.3 |  | 4914 | 81.15 | 0.52687 | 62.202 | 0.0016384 | 49.246 | 1097.3 | 1048.054
4915 | 0.52704 | 81.16 | 62.202 | 0.0016389 | 49.256 | 1097.3 |  | 4915 | 81.16 | 0.52704 | 62.202 | 0.0016389 | 49.256 | 1097.3 | 1048.044
4916 | 0.52721 | 81.17 | 62.202 | 0.0016394 | 49.266 | 1097.3 |  | 4916 | 81.17 | 0.52721 | 62.202 | 0.0016394 | 49.266 | 1097.3 | 1048.034
4917 | 0.52738 | 81.18 | 62.202 | 0.0016399 | 49.276 | 1097.3 |  | 4917 | 81.18 | 0.52738 | 62.202 | 0.0016399 | 49.276 | 1097.3 | 1048.024
4918 | 0.52755 | 81.19 | 62.202 | 0.0016404 | 49.286 | 1097.3 |  | 4918 | 81.19 | 0.52755 | 62.202 | 0.0016404 | 49.286 | 1097.3 | 1048.014
4919 | 0.52773 | 81.2 | 62.202 | 0.0016409 | 49.296 | 1097.3 |  | 4919 | 81.2 | 0.52773 | 62.202 | 0.0016409 | 49.296 | 1097.3 | 1048.004
4920 | 0.5279 | 81.21 | 62.202 | 0.0016414 | 49.306 | 1097.4 |  | 4920 | 81.21 | 0.5279 | 62.202 | 0.0016414 | 49.306 | 1097.4 | 1048.094
4921 | 0.52807 | 81.22 | 62.202 | 0.0016419 | 49.316 | 1097.4 |  | 4921 | 81.22 | 0.52807 | 62.202 | 0.0016419 | 49.316 | 1097.4 | 1048.084
4922 | 0.52824 | 81.23 | 62.202 | 0.0016424 | 49.326 | 1097.4 |  | 4922 | 81.23 | 0.52824 | 62.202 | 0.0016424 | 49.326 | 1097.4 | 1048.074
4923 | 0.52841 | 81.24 | 62.202 | 0.0016429 | 49.336 | 1097.4 |  | 4923 | 81.24 | 0.52841 | 62.202 | 0.0016429 | 49.336 | 1097.4 | 1048.064
4924 | 0.52859 | 81.25 | 62.201 | 0.0016434 | 49.346 | 1097.4 |  | 4924 | 81.25 | 0.52859 | 62.201 | 0.0016434 | 49.346 | 1097.4 | 1048.054
4925 | 0.52876 | 81.26 | 62.201 | 0.0016439 | 49.356 | 1097.4 |  | 4925 | 81.26 | 0.52876 | 62.201 | 0.0016439 | 49.356 | 1097.4 | 1048.044
4926 | 0.52893 | 81.27 | 62.201 | 0.0016444 | 49.366 | 1097.4 |  | 4926 | 81.27 | 0.52893 | 62.201 | 0.0016444 | 49.366 | 1097.4 | 1048.034
4927 | 0.5291 | 81.28 | 62.201 | 0.0016449 | 49.376 | 1097.4 |  | 4927 | 81.28 | 0.5291 | 62.201 | 0.0016449 | 49.376 | 1097.4 | 1048.024
4928 | 0.52927 | 81.29 | 62.201 | 0.0016454 | 49.386 | 1097.4 |  | 4928 | 81.29 | 0.52927 | 62.201 | 0.0016454 | 49.386 | 1097.4 | 1048.014
4929 | 0.52945 | 81.3 | 62.201 | 0.0016459 | 49.396 | 1097.4 |  | 4929 | 81.3 | 0.52945 | 62.201 | 0.0016459 | 49.396 | 1097.4 | 1048.004
4930 | 0.52962 | 81.31 | 62.201 | 0.0016464 | 49.406 | 1097.4 |  | 4930 | 81.31 | 0.52962 | 62.201 | 0.0016464 | 49.406 | 1097.4 | 1047.994
4931 | 0.52979 | 81.32 | 62.201 | 0.0016469 | 49.416 | 1097.4 |  | 4931 | 81.32 | 0.52979 | 62.201 | 0.0016469 | 49.416 | 1097.4 | 1047.984
4932 | 0.52996 | 81.33 | 62.201 | 0.0016474 | 49.426 | 1097.4 |  | 4932 | 81.33 | 0.52996 | 62.201 | 0.0016474 | 49.426 | 1097.4 | 1047.974
4933 | 0.53014 | 81.34 | 62.201 | 0.0016479 | 49.436 | 1097.4 |  | 4933 | 81.34 | 0.53014 | 62.201 | 0.0016479 | 49.436 | 1097.4 | 1047.964
4934 | 0.53031 | 81.35 | 62.201 | 0.0016485 | 49.446 | 1097.4 |  | 4934 | 81.35 | 0.53031 | 62.201 | 0.0016485 | 49.446 | 1097.4 | 1047.954
4935 | 0.53048 | 81.36 | 62.2 | 0.001649 | 49.456 | 1097.4 |  | 4935 | 81.36 | 0.53048 | 62.2 | 0.001649 | 49.456 | 1097.4 | 1047.944
4936 | 0.53065 | 81.37 | 62.2 | 0.0016495 | 49.466 | 1097.4 |  | 4936 | 81.37 | 0.53065 | 62.2 | 0.0016495 | 49.466 | 1097.4 | 1047.934
4937 | 0.53083 | 81.38 | 62.2 | 0.00165 | 49.476 | 1097.4 |  | 4937 | 81.38 | 0.53083 | 62.2 | 0.00165 | 49.476 | 1097.4 | 1047.924
4938 | 0.531 | 81.39 | 62.2 | 0.0016505 | 49.486 | 1097.4 |  | 4938 | 81.39 | 0.531 | 62.2 | 0.0016505 | 49.486 | 1097.4 | 1047.914
4939 | 0.53117 | 81.4 | 62.2 | 0.001651 | 49.496 | 1097.4 |  | 4939 | 81.4 | 0.53117 | 62.2 | 0.001651 | 49.496 | 1097.4 | 1047.904
4940 | 0.53134 | 81.41 | 62.2 | 0.0016515 | 49.506 | 1097.4 |  | 4940 | 81.41 | 0.53134 | 62.2 | 0.0016515 | 49.506 | 1097.4 | 1047.894
4941 | 0.53152 | 81.42 | 62.2 | 0.001652 | 49.516 | 1097.4 |  | 4941 | 81.42 | 0.53152 | 62.2 | 0.001652 | 49.516 | 1097.4 | 1047.884
4942 | 0.53169 | 81.43 | 62.2 | 0.0016525 | 49.526 | 1097.4 |  | 4942 | 81.43 | 0.53169 | 62.2 | 0.0016525 | 49.526 | 1097.4 | 1047.874
4943 | 0.53186 | 81.44 | 62.2 | 0.001653 | 49.536 | 1097.5 |  | 4943 | 81.44 | 0.53186 | 62.2 | 0.001653 | 49.536 | 1097.5 | 1047.964
4944 | 0.53203 | 81.45 | 62.2 | 0.0016535 | 49.546 | 1097.5 |  | 4944 | 81.45 | 0.53203 | 62.2 | 0.0016535 | 49.546 | 1097.5 | 1047.954
4945 | 0.53221 | 81.46 | 62.199 | 0.001654 | 49.556 | 1097.5 |  | 4945 | 81.46 | 0.53221 | 62.199 | 0.001654 | 49.556 | 1097.5 | 1047.944
4946 | 0.53238 | 81.47 | 62.199 | 0.0016545 | 49.566 | 1097.5 |  | 4946 | 81.47 | 0.53238 | 62.199 | 0.0016545 | 49.566 | 1097.5 | 1047.934
4947 | 0.53255 | 81.48 | 62.199 | 0.001655 | 49.576 | 1097.5 |  | 4947 | 81.48 | 0.53255 | 62.199 | 0.001655 | 49.576 | 1097.5 | 1047.924
4948 | 0.53273 | 81.49 | 62.199 | 0.0016556 | 49.586 | 1097.5 |  | 4948 | 81.49 | 0.53273 | 62.199 | 0.0016556 | 49.586 | 1097.5 | 1047.914
4949 | 0.5329 | 81.5 | 62.199 | 0.0016561 | 49.596 | 1097.5 |  | 4949 | 81.5 | 0.5329 | 62.199 | 0.0016561 | 49.596 | 1097.5 | 1047.904
4950 | 0.53307 | 81.51 | 62.199 | 0.0016566 | 49.606 | 1097.5 |  | 4950 | 81.51 | 0.53307 | 62.199 | 0.0016566 | 49.606 | 1097.5 | 1047.894
4951 | 0.53325 | 81.52 | 62.199 | 0.0016571 | 49.616 | 1097.5 |  | 4951 | 81.52 | 0.53325 | 62.199 | 0.0016571 | 49.616 | 1097.5 | 1047.884
4952 | 0.53342 | 81.53 | 62.199 | 0.0016576 | 49.626 | 1097.5 |  | 4952 | 81.53 | 0.53342 | 62.199 | 0.0016576 | 49.626 | 1097.5 | 1047.874
4953 | 0.53359 | 81.54 | 62.199 | 0.0016581 | 49.636 | 1097.5 |  | 4953 | 81.54 | 0.53359 | 62.199 | 0.0016581 | 49.636 | 1097.5 | 1047.864
4954 | 0.53377 | 81.55 | 62.199 | 0.0016586 | 49.646 | 1097.5 |  | 4954 | 81.55 | 0.53377 | 62.199 | 0.0016586 | 49.646 | 1097.5 | 1047.854
4955 | 0.53394 | 81.56 | 62.198 | 0.0016591 | 49.656 | 1097.5 |  | 4955 | 81.56 | 0.53394 | 62.198 | 0.0016591 | 49.656 | 1097.5 | 1047.844
4956 | 0.53411 | 81.57 | 62.198 | 0.0016596 | 49.666 | 1097.5 |  | 4956 | 81.57 | 0.53411 | 62.198 | 0.0016596 | 49.666 | 1097.5 | 1047.834
4957 | 0.53429 | 81.58 | 62.198 | 0.0016601 | 49.676 | 1097.5 |  | 4957 | 81.58 | 0.53429 | 62.198 | 0.0016601 | 49.676 | 1097.5 | 1047.824
4958 | 0.53446 | 81.59 | 62.198 | 0.0016606 | 49.686 | 1097.5 |  | 4958 | 81.59 | 0.53446 | 62.198 | 0.0016606 | 49.686 | 1097.5 | 1047.814
4959 | 0.53463 | 81.6 | 62.198 | 0.0016611 | 49.696 | 1097.5 |  | 4959 | 81.6 | 0.53463 | 62.198 | 0.0016611 | 49.696 | 1097.5 | 1047.804
4960 | 0.53481 | 81.61 | 62.198 | 0.0016617 | 49.706 | 1097.5 |  | 4960 | 81.61 | 0.53481 | 62.198 | 0.0016617 | 49.706 | 1097.5 | 1047.794
4961 | 0.53498 | 81.62 | 62.198 | 0.0016622 | 49.716 | 1097.5 |  | 4961 | 81.62 | 0.53498 | 62.198 | 0.0016622 | 49.716 | 1097.5 | 1047.784
4962 | 0.53516 | 81.63 | 62.198 | 0.0016627 | 49.726 | 1097.5 |  | 4962 | 81.63 | 0.53516 | 62.198 | 0.0016627 | 49.726 | 1097.5 | 1047.774
4963 | 0.53533 | 81.64 | 62.198 | 0.0016632 | 49.736 | 1097.5 |  | 4963 | 81.64 | 0.53533 | 62.198 | 0.0016632 | 49.736 | 1097.5 | 1047.764
4964 | 0.5355 | 81.65 | 62.198 | 0.0016637 | 49.746 | 1097.5 |  | 4964 | 81.65 | 0.5355 | 62.198 | 0.0016637 | 49.746 | 1097.5 | 1047.754
4965 | 0.53568 | 81.66 | 62.197 | 0.0016642 | 49.756 | 1097.5 |  | 4965 | 81.66 | 0.53568 | 62.197 | 0.0016642 | 49.756 | 1097.5 | 1047.744
4966 | 0.53585 | 81.67 | 62.197 | 0.0016647 | 49.766 | 1097.6 |  | 4966 | 81.67 | 0.53585 | 62.197 | 0.0016647 | 49.766 | 1097.6 | 1047.834
4967 | 0.53602 | 81.68 | 62.197 | 0.0016652 | 49.776 | 1097.6 |  | 4967 | 81.68 | 0.53602 | 62.197 | 0.0016652 | 49.776 | 1097.6 | 1047.824
4968 | 0.5362 | 81.69 | 62.197 | 0.0016657 | 49.786 | 1097.6 |  | 4968 | 81.69 | 0.5362 | 62.197 | 0.0016657 | 49.786 | 1097.6 | 1047.814
4969 | 0.53637 | 81.7 | 62.197 | 0.0016662 | 49.796 | 1097.6 |  | 4969 | 81.7 | 0.53637 | 62.197 | 0.0016662 | 49.796 | 1097.6 | 1047.804
4970 | 0.53655 | 81.71 | 62.197 | 0.0016668 | 49.806 | 1097.6 |  | 4970 | 81.71 | 0.53655 | 62.197 | 0.0016668 | 49.806 | 1097.6 | 1047.794
4971 | 0.53672 | 81.72 | 62.197 | 0.0016673 | 49.816 | 1097.6 |  | 4971 | 81.72 | 0.53672 | 62.197 | 0.0016673 | 49.816 | 1097.6 | 1047.784
4972 | 0.5369 | 81.73 | 62.197 | 0.0016678 | 49.826 | 1097.6 |  | 4972 | 81.73 | 0.5369 | 62.197 | 0.0016678 | 49.826 | 1097.6 | 1047.774
4973 | 0.53707 | 81.74 | 62.197 | 0.0016683 | 49.836 | 1097.6 |  | 4973 | 81.74 | 0.53707 | 62.197 | 0.0016683 | 49.836 | 1097.6 | 1047.764
4974 | 0.53724 | 81.75 | 62.197 | 0.0016688 | 49.846 | 1097.6 |  | 4974 | 81.75 | 0.53724 | 62.197 | 0.0016688 | 49.846 | 1097.6 | 1047.754
4975 | 0.53742 | 81.76 | 62.197 | 0.0016693 | 49.856 | 1097.6 |  | 4975 | 81.76 | 0.53742 | 62.197 | 0.0016693 | 49.856 | 1097.6 | 1047.744
4976 | 0.53759 | 81.77 | 62.196 | 0.0016698 | 49.866 | 1097.6 |  | 4976 | 81.77 | 0.53759 | 62.196 | 0.0016698 | 49.866 | 1097.6 | 1047.734
4977 | 0.53777 | 81.78 | 62.196 | 0.0016703 | 49.876 | 1097.6 |  | 4977 | 81.78 | 0.53777 | 62.196 | 0.0016703 | 49.876 | 1097.6 | 1047.724
4978 | 0.53794 | 81.79 | 62.196 | 0.0016709 | 49.886 | 1097.6 |  | 4978 | 81.79 | 0.53794 | 62.196 | 0.0016709 | 49.886 | 1097.6 | 1047.714
4979 | 0.53812 | 81.8 | 62.196 | 0.0016714 | 49.896 | 1097.6 |  | 4979 | 81.8 | 0.53812 | 62.196 | 0.0016714 | 49.896 | 1097.6 | 1047.704
4980 | 0.53829 | 81.81 | 62.196 | 0.0016719 | 49.905 | 1097.6 |  | 4980 | 81.81 | 0.53829 | 62.196 | 0.0016719 | 49.905 | 1097.6 | 1047.695
4981 | 0.53847 | 81.82 | 62.196 | 0.0016724 | 49.915 | 1097.6 |  | 4981 | 81.82 | 0.53847 | 62.196 | 0.0016724 | 49.915 | 1097.6 | 1047.685
4982 | 0.53864 | 81.83 | 62.196 | 0.0016729 | 49.925 | 1097.6 |  | 4982 | 81.83 | 0.53864 | 62.196 | 0.0016729 | 49.925 | 1097.6 | 1047.675
4983 | 0.53882 | 81.84 | 62.196 | 0.0016734 | 49.935 | 1097.6 |  | 4983 | 81.84 | 0.53882 | 62.196 | 0.0016734 | 49.935 | 1097.6 | 1047.665
4984 | 0.53899 | 81.85 | 62.196 | 0.0016739 | 49.945 | 1097.6 |  | 4984 | 81.85 | 0.53899 | 62.196 | 0.0016739 | 49.945 | 1097.6 | 1047.655
4985 | 0.53917 | 81.86 | 62.196 | 0.0016744 | 49.955 | 1097.6 |  | 4985 | 81.86 | 0.53917 | 62.196 | 0.0016744 | 49.955 | 1097.6 | 1047.645
4986 | 0.53934 | 81.87 | 62.195 | 0.001675 | 49.965 | 1097.6 |  | 4986 | 81.87 | 0.53934 | 62.195 | 0.001675 | 49.965 | 1097.6 | 1047.635
4987 | 0.53952 | 81.88 | 62.195 | 0.0016755 | 49.975 | 1097.6 |  | 4987 | 81.88 | 0.53952 | 62.195 | 0.0016755 | 49.975 | 1097.6 | 1047.625
4988 | 0.53969 | 81.89 | 62.195 | 0.001676 | 49.985 | 1097.6 |  | 4988 | 81.89 | 0.53969 | 62.195 | 0.001676 | 49.985 | 1097.6 | 1047.615
4989 | 0.53987 | 81.9 | 62.195 | 0.0016765 | 49.995 | 1097.7 |  | 4989 | 81.9 | 0.53987 | 62.195 | 0.0016765 | 49.995 | 1097.7 | 1047.705
4990 | 0.54004 | 81.91 | 62.195 | 0.001677 | 50.005 | 1097.7 |  | 4990 | 81.91 | 0.54004 | 62.195 | 0.001677 | 50.005 | 1097.7 | 1047.695
4991 | 0.54022 | 81.92 | 62.195 | 0.0016775 | 50.015 | 1097.7 |  | 4991 | 81.92 | 0.54022 | 62.195 | 0.0016775 | 50.015 | 1097.7 | 1047.685
4992 | 0.54039 | 81.93 | 62.195 | 0.001678 | 50.025 | 1097.7 |  | 4992 | 81.93 | 0.54039 | 62.195 | 0.001678 | 50.025 | 1097.7 | 1047.675
4993 | 0.54057 | 81.94 | 62.195 | 0.0016785 | 50.035 | 1097.7 |  | 4993 | 81.94 | 0.54057 | 62.195 | 0.0016785 | 50.035 | 1097.7 | 1047.665
4994 | 0.54074 | 81.95 | 62.195 | 0.0016791 | 50.045 | 1097.7 |  | 4994 | 81.95 | 0.54074 | 62.195 | 0.0016791 | 50.045 | 1097.7 | 1047.655
4995 | 0.54092 | 81.96 | 62.195 | 0.0016796 | 50.055 | 1097.7 |  | 4995 | 81.96 | 0.54092 | 62.195 | 0.0016796 | 50.055 | 1097.7 | 1047.645
4996 | 0.54109 | 81.97 | 62.194 | 0.0016801 | 50.065 | 1097.7 |  | 4996 | 81.97 | 0.54109 | 62.194 | 0.0016801 | 50.065 | 1097.7 | 1047.635
4997 | 0.54127 | 81.98 | 62.194 | 0.0016806 | 50.075 | 1097.7 |  | 4997 | 81.98 | 0.54127 | 62.194 | 0.0016806 | 50.075 | 1097.7 | 1047.625
4998 | 0.54144 | 81.99 | 62.194 | 0.0016811 | 50.085 | 1097.7 |  | 4998 | 81.99 | 0.54144 | 62.194 | 0.0016811 | 50.085 | 1097.7 | 1047.615
4999 | 0.54162 | 82 | 62.194 | 0.0016816 | 50.095 | 1097.7 |  | 4999 | 82 | 0.54162 | 62.194 | 0.0016816 | 50.095 | 1097.7 | 1047.605
5000 | 0.5418 | 82.01 | 62.194 | 0.0016822 | 50.105 | 1097.7 |  | 5000 | 82.01 | 0.5418 | 62.194 | 0.0016822 | 50.105 | 1097.7 | 1047.595
5001 | 0.54197 | 82.02 | 62.194 | 0.0016827 | 50.115 | 1097.7 |  | 5001 | 82.02 | 0.54197 | 62.194 | 0.0016827 | 50.115 | 1097.7 | 1047.585
5002 | 0.54215 | 82.03 | 62.194 | 0.0016832 | 50.125 | 1097.7 |  | 5002 | 82.03 | 0.54215 | 62.194 | 0.0016832 | 50.125 | 1097.7 | 1047.575
5003 | 0.54232 | 82.04 | 62.194 | 0.0016837 | 50.135 | 1097.7 |  | 5003 | 82.04 | 0.54232 | 62.194 | 0.0016837 | 50.135 | 1097.7 | 1047.565
5004 | 0.5425 | 82.05 | 62.194 | 0.0016842 | 50.145 | 1097.7 |  | 5004 | 82.05 | 0.5425 | 62.194 | 0.0016842 | 50.145 | 1097.7 | 1047.555
5005 | 0.54267 | 82.06 | 62.194 | 0.0016847 | 50.155 | 1097.7 |  | 5005 | 82.06 | 0.54267 | 62.194 | 0.0016847 | 50.155 | 1097.7 | 1047.545
5006 | 0.54285 | 82.07 | 62.193 | 0.0016852 | 50.165 | 1097.7 |  | 5006 | 82.07 | 0.54285 | 62.193 | 0.0016852 | 50.165 | 1097.7 | 1047.535
5007 | 0.54303 | 82.08 | 62.193 | 0.0016858 | 50.175 | 1097.7 |  | 5007 | 82.08 | 0.54303 | 62.193 | 0.0016858 | 50.175 | 1097.7 | 1047.525
5008 | 0.5432 | 82.09 | 62.193 | 0.0016863 | 50.185 | 1097.7 |  | 5008 | 82.09 | 0.5432 | 62.193 | 0.0016863 | 50.185 | 1097.7 | 1047.515
5009 | 0.54338 | 82.1 | 62.193 | 0.0016868 | 50.195 | 1097.7 |  | 5009 | 82.1 | 0.54338 | 62.193 | 0.0016868 | 50.195 | 1097.7 | 1047.505
5010 | 0.54356 | 82.11 | 62.193 | 0.0016873 | 50.205 | 1097.7 |  | 5010 | 82.11 | 0.54356 | 62.193 | 0.0016873 | 50.205 | 1097.7 | 1047.495
5011 | 0.54373 | 82.12 | 62.193 | 0.0016878 | 50.215 | 1097.7 |  | 5011 | 82.12 | 0.54373 | 62.193 | 0.0016878 | 50.215 | 1097.7 | 1047.485
5012 | 0.54391 | 82.13 | 62.193 | 0.0016883 | 50.225 | 1097.8 |  | 5012 | 82.13 | 0.54391 | 62.193 | 0.0016883 | 50.225 | 1097.8 | 1047.575
5013 | 0.54408 | 82.14 | 62.193 | 0.0016889 | 50.235 | 1097.8 |  | 5013 | 82.14 | 0.54408 | 62.193 | 0.0016889 | 50.235 | 1097.8 | 1047.565
5014 | 0.54426 | 82.15 | 62.193 | 0.0016894 | 50.245 | 1097.8 |  | 5014 | 82.15 | 0.54426 | 62.193 | 0.0016894 | 50.245 | 1097.8 | 1047.555
5015 | 0.54444 | 82.16 | 62.193 | 0.0016899 | 50.255 | 1097.8 |  | 5015 | 82.16 | 0.54444 | 62.193 | 0.0016899 | 50.255 | 1097.8 | 1047.545
5016 | 0.54461 | 82.17 | 62.193 | 0.0016904 | 50.265 | 1097.8 |  | 5016 | 82.17 | 0.54461 | 62.193 | 0.0016904 | 50.265 | 1097.8 | 1047.535
5017 | 0.54479 | 82.18 | 62.192 | 0.0016909 | 50.275 | 1097.8 |  | 5017 | 82.18 | 0.54479 | 62.192 | 0.0016909 | 50.275 | 1097.8 | 1047.525
5018 | 0.54497 | 82.19 | 62.192 | 0.0016914 | 50.285 | 1097.8 |  | 5018 | 82.19 | 0.54497 | 62.192 | 0.0016914 | 50.285 | 1097.8 | 1047.515
5019 | 0.54514 | 82.2 | 62.192 | 0.001692 | 50.295 | 1097.8 |  | 5019 | 82.2 | 0.54514 | 62.192 | 0.001692 | 50.295 | 1097.8 | 1047.505
5020 | 0.54532 | 82.21 | 62.192 | 0.0016925 | 50.305 | 1097.8 |  | 5020 | 82.21 | 0.54532 | 62.192 | 0.0016925 | 50.305 | 1097.8 | 1047.495
5021 | 0.5455 | 82.22 | 62.192 | 0.001693 | 50.315 | 1097.8 |  | 5021 | 82.22 | 0.5455 | 62.192 | 0.001693 | 50.315 | 1097.8 | 1047.485
5022 | 0.54567 | 82.23 | 62.192 | 0.0016935 | 50.325 | 1097.8 |  | 5022 | 82.23 | 0.54567 | 62.192 | 0.0016935 | 50.325 | 1097.8 | 1047.475
5023 | 0.54585 | 82.24 | 62.192 | 0.001694 | 50.335 | 1097.8 |  | 5023 | 82.24 | 0.54585 | 62.192 | 0.001694 | 50.335 | 1097.8 | 1047.465
5024 | 0.54603 | 82.25 | 62.192 | 0.0016946 | 50.345 | 1097.8 |  | 5024 | 82.25 | 0.54603 | 62.192 | 0.0016946 | 50.345 | 1097.8 | 1047.455
5025 | 0.5462 | 82.26 | 62.192 | 0.0016951 | 50.355 | 1097.8 |  | 5025 | 82.26 | 0.5462 | 62.192 | 0.0016951 | 50.355 | 1097.8 | 1047.445
5026 | 0.54638 | 82.27 | 62.192 | 0.0016956 | 50.365 | 1097.8 |  | 5026 | 82.27 | 0.54638 | 62.192 | 0.0016956 | 50.365 | 1097.8 | 1047.435
5027 | 0.54656 | 82.28 | 62.191 | 0.0016961 | 50.375 | 1097.8 |  | 5027 | 82.28 | 0.54656 | 62.191 | 0.0016961 | 50.375 | 1097.8 | 1047.425
5028 | 0.54673 | 82.29 | 62.191 | 0.0016966 | 50.385 | 1097.8 |  | 5028 | 82.29 | 0.54673 | 62.191 | 0.0016966 | 50.385 | 1097.8 | 1047.415
5029 | 0.54691 | 82.3 | 62.191 | 0.0016971 | 50.395 | 1097.8 |  | 5029 | 82.3 | 0.54691 | 62.191 | 0.0016971 | 50.395 | 1097.8 | 1047.405
5030 | 0.54709 | 82.31 | 62.191 | 0.0016977 | 50.405 | 1097.8 |  | 5030 | 82.31 | 0.54709 | 62.191 | 0.0016977 | 50.405 | 1097.8 | 1047.395
5031 | 0.54727 | 82.32 | 62.191 | 0.0016982 | 50.415 | 1097.8 |  | 5031 | 82.32 | 0.54727 | 62.191 | 0.0016982 | 50.415 | 1097.8 | 1047.385
5032 | 0.54744 | 82.33 | 62.191 | 0.0016987 | 50.425 | 1097.8 |  | 5032 | 82.33 | 0.54744 | 62.191 | 0.0016987 | 50.425 | 1097.8 | 1047.375
5033 | 0.54762 | 82.34 | 62.191 | 0.0016992 | 50.435 | 1097.8 |  | 5033 | 82.34 | 0.54762 | 62.191 | 0.0016992 | 50.435 | 1097.8 | 1047.365
5034 | 0.5478 | 82.35 | 62.191 | 0.0016997 | 50.445 | 1097.8 |  | 5034 | 82.35 | 0.5478 | 62.191 | 0.0016997 | 50.445 | 1097.8 | 1047.355
5035 | 0.54798 | 82.36 | 62.191 | 0.0017003 | 50.455 | 1097.9 |  | 5035 | 82.36 | 0.54798 | 62.191 | 0.0017003 | 50.455 | 1097.9 | 1047.445
5036 | 0.54815 | 82.37 | 62.191 | 0.0017008 | 50.465 | 1097.9 |  | 5036 | 82.37 | 0.54815 | 62.191 | 0.0017008 | 50.465 | 1097.9 | 1047.435
5037 | 0.54833 | 82.38 | 62.19 | 0.0017013 | 50.475 | 1097.9 |  | 5037 | 82.38 | 0.54833 | 62.19 | 0.0017013 | 50.475 | 1097.9 | 1047.425
5038 | 0.54851 | 82.39 | 62.19 | 0.0017018 | 50.485 | 1097.9 |  | 5038 | 82.39 | 0.54851 | 62.19 | 0.0017018 | 50.485 | 1097.9 | 1047.415
5039 | 0.54869 | 82.4 | 62.19 | 0.0017023 | 50.495 | 1097.9 |  | 5039 | 82.4 | 0.54869 | 62.19 | 0.0017023 | 50.495 | 1097.9 | 1047.405
5040 | 0.54886 | 82.41 | 62.19 | 0.0017029 | 50.505 | 1097.9 |  | 5040 | 82.41 | 0.54886 | 62.19 | 0.0017029 | 50.505 | 1097.9 | 1047.395
5041 | 0.54904 | 82.42 | 62.19 | 0.0017034 | 50.515 | 1097.9 |  | 5041 | 82.42 | 0.54904 | 62.19 | 0.0017034 | 50.515 | 1097.9 | 1047.385
5042 | 0.54922 | 82.43 | 62.19 | 0.0017039 | 50.525 | 1097.9 |  | 5042 | 82.43 | 0.54922 | 62.19 | 0.0017039 | 50.525 | 1097.9 | 1047.375
5043 | 0.5494 | 82.44 | 62.19 | 0.0017044 | 50.535 | 1097.9 |  | 5043 | 82.44 | 0.5494 | 62.19 | 0.0017044 | 50.535 | 1097.9 | 1047.365
5044 | 0.54957 | 82.45 | 62.19 | 0.0017049 | 50.545 | 1097.9 |  | 5044 | 82.45 | 0.54957 | 62.19 | 0.0017049 | 50.545 | 1097.9 | 1047.355
5045 | 0.54975 | 82.46 | 62.19 | 0.0017055 | 50.555 | 1097.9 |  | 5045 | 82.46 | 0.54975 | 62.19 | 0.0017055 | 50.555 | 1097.9 | 1047.345
5046 | 0.54993 | 82.47 | 62.19 | 0.001706 | 50.565 | 1097.9 |  | 5046 | 82.47 | 0.54993 | 62.19 | 0.001706 | 50.565 | 1097.9 | 1047.335
5047 | 0.55011 | 82.48 | 62.189 | 0.0017065 | 50.575 | 1097.9 |  | 5047 | 82.48 | 0.55011 | 62.189 | 0.0017065 | 50.575 | 1097.9 | 1047.325
5048 | 0.55029 | 82.49 | 62.189 | 0.001707 | 50.585 | 1097.9 |  | 5048 | 82.49 | 0.55029 | 62.189 | 0.001707 | 50.585 | 1097.9 | 1047.315
5049 | 0.55046 | 82.5 | 62.189 | 0.0017076 | 50.595 | 1097.9 |  | 5049 | 82.5 | 0.55046 | 62.189 | 0.0017076 | 50.595 | 1097.9 | 1047.305
5050 | 0.55064 | 82.51 | 62.189 | 0.0017081 | 50.605 | 1097.9 |  | 5050 | 82.51 | 0.55064 | 62.189 | 0.0017081 | 50.605 | 1097.9 | 1047.295
5051 | 0.55082 | 82.52 | 62.189 | 0.0017086 | 50.615 | 1097.9 |  | 5051 | 82.52 | 0.55082 | 62.189 | 0.0017086 | 50.615 | 1097.9 | 1047.285
5052 | 0.551 | 82.53 | 62.189 | 0.0017091 | 50.625 | 1097.9 |  | 5052 | 82.53 | 0.551 | 62.189 | 0.0017091 | 50.625 | 1097.9 | 1047.275
5053 | 0.55118 | 82.54 | 62.189 | 0.0017096 | 50.635 | 1097.9 |  | 5053 | 82.54 | 0.55118 | 62.189 | 0.0017096 | 50.635 | 1097.9 | 1047.265
5054 | 0.55136 | 82.55 | 62.189 | 0.0017102 | 50.645 | 1097.9 |  | 5054 | 82.55 | 0.55136 | 62.189 | 0.0017102 | 50.645 | 1097.9 | 1047.255
5055 | 0.55153 | 82.56 | 62.189 | 0.0017107 | 50.655 | 1097.9 |  | 5055 | 82.56 | 0.55153 | 62.189 | 0.0017107 | 50.655 | 1097.9 | 1047.245
5056 | 0.55171 | 82.57 | 62.189 | 0.0017112 | 50.665 | 1097.9 |  | 5056 | 82.57 | 0.55171 | 62.189 | 0.0017112 | 50.665 | 1097.9 | 1047.235
5057 | 0.55189 | 82.58 | 62.188 | 0.0017117 | 50.675 | 1097.9 |  | 5057 | 82.58 | 0.55189 | 62.188 | 0.0017117 | 50.675 | 1097.9 | 1047.225
5058 | 0.55207 | 82.59 | 62.188 | 0.0017123 | 50.685 | 1098 |  | 5058 | 82.59 | 0.55207 | 62.188 | 0.0017123 | 50.685 | 1098 | 1047.315
5059 | 0.55225 | 82.6 | 62.188 | 0.0017128 | 50.695 | 1098 |  | 5059 | 82.6 | 0.55225 | 62.188 | 0.0017128 | 50.695 | 1098 | 1047.305
5060 | 0.55243 | 82.61 | 62.188 | 0.0017133 | 50.705 | 1098 |  | 5060 | 82.61 | 0.55243 | 62.188 | 0.0017133 | 50.705 | 1098 | 1047.295
5061 | 0.55261 | 82.62 | 62.188 | 0.0017138 | 50.715 | 1098 |  | 5061 | 82.62 | 0.55261 | 62.188 | 0.0017138 | 50.715 | 1098 | 1047.285
5062 | 0.55278 | 82.63 | 62.188 | 0.0017143 | 50.725 | 1098 |  | 5062 | 82.63 | 0.55278 | 62.188 | 0.0017143 | 50.725 | 1098 | 1047.275
5063 | 0.55296 | 82.64 | 62.188 | 0.0017149 | 50.735 | 1098 |  | 5063 | 82.64 | 0.55296 | 62.188 | 0.0017149 | 50.735 | 1098 | 1047.265
5064 | 0.55314 | 82.65 | 62.188 | 0.0017154 | 50.745 | 1098 |  | 5064 | 82.65 | 0.55314 | 62.188 | 0.0017154 | 50.745 | 1098 | 1047.255
5065 | 0.55332 | 82.66 | 62.188 | 0.0017159 | 50.755 | 1098 |  | 5065 | 82.66 | 0.55332 | 62.188 | 0.0017159 | 50.755 | 1098 | 1047.245
5066 | 0.5535 | 82.67 | 62.188 | 0.0017164 | 50.765 | 1098 |  | 5066 | 82.67 | 0.5535 | 62.188 | 0.0017164 | 50.765 | 1098 | 1047.235
5067 | 0.55368 | 82.68 | 62.187 | 0.001717 | 50.775 | 1098 |  | 5067 | 82.68 | 0.55368 | 62.187 | 0.001717 | 50.775 | 1098 | 1047.225
5068 | 0.55386 | 82.69 | 62.187 | 0.0017175 | 50.785 | 1098 |  | 5068 | 82.69 | 0.55386 | 62.187 | 0.0017175 | 50.785 | 1098 | 1047.215
5069 | 0.55404 | 82.7 | 62.187 | 0.001718 | 50.795 | 1098 |  | 5069 | 82.7 | 0.55404 | 62.187 | 0.001718 | 50.795 | 1098 | 1047.205
5070 | 0.55422 | 82.71 | 62.187 | 0.0017185 | 50.805 | 1098 |  | 5070 | 82.71 | 0.55422 | 62.187 | 0.0017185 | 50.805 | 1098 | 1047.195
5071 | 0.5544 | 82.72 | 62.187 | 0.0017191 | 50.815 | 1098 |  | 5071 | 82.72 | 0.5544 | 62.187 | 0.0017191 | 50.815 | 1098 | 1047.185
5072 | 0.55457 | 82.73 | 62.187 | 0.0017196 | 50.825 | 1098 |  | 5072 | 82.73 | 0.55457 | 62.187 | 0.0017196 | 50.825 | 1098 | 1047.175
5073 | 0.55475 | 82.74 | 62.187 | 0.0017201 | 50.835 | 1098 |  | 5073 | 82.74 | 0.55475 | 62.187 | 0.0017201 | 50.835 | 1098 | 1047.165
5074 | 0.55493 | 82.75 | 62.187 | 0.0017206 | 50.845 | 1098 |  | 5074 | 82.75 | 0.55493 | 62.187 | 0.0017206 | 50.845 | 1098 | 1047.155
5075 | 0.55511 | 82.76 | 62.187 | 0.0017212 | 50.855 | 1098 |  | 5075 | 82.76 | 0.55511 | 62.187 | 0.0017212 | 50.855 | 1098 | 1047.145
5076 | 0.55529 | 82.77 | 62.187 | 0.0017217 | 50.865 | 1098 |  | 5076 | 82.77 | 0.55529 | 62.187 | 0.0017217 | 50.865 | 1098 | 1047.135
5077 | 0.55547 | 82.78 | 62.186 | 0.0017222 | 50.875 | 1098 |  | 5077 | 82.78 | 0.55547 | 62.186 | 0.0017222 | 50.875 | 1098 | 1047.125
5078 | 0.55565 | 82.79 | 62.186 | 0.0017227 | 50.885 | 1098 |  | 5078 | 82.79 | 0.55565 | 62.186 | 0.0017227 | 50.885 | 1098 | 1047.115
5079 | 0.55583 | 82.8 | 62.186 | 0.0017233 | 50.895 | 1098 |  | 5079 | 82.8 | 0.55583 | 62.186 | 0.0017233 | 50.895 | 1098 | 1047.105
5080 | 0.55601 | 82.81 | 62.186 | 0.0017238 | 50.905 | 1098 |  | 5080 | 82.81 | 0.55601 | 62.186 | 0.0017238 | 50.905 | 1098 | 1047.095
5081 | 0.55619 | 82.82 | 62.186 | 0.0017243 | 50.915 | 1098 |  | 5081 | 82.82 | 0.55619 | 62.186 | 0.0017243 | 50.915 | 1098 | 1047.085
5082 | 0.55637 | 82.83 | 62.186 | 0.0017248 | 50.925 | 1098.1 |  | 5082 | 82.83 | 0.55637 | 62.186 | 0.0017248 | 50.925 | 1098.1 | 1047.175
5083 | 0.55655 | 82.84 | 62.186 | 0.0017254 | 50.935 | 1098.1 |  | 5083 | 82.84 | 0.55655 | 62.186 | 0.0017254 | 50.935 | 1098.1 | 1047.165
5084 | 0.55673 | 82.85 | 62.186 | 0.0017259 | 50.945 | 1098.1 |  | 5084 | 82.85 | 0.55673 | 62.186 | 0.0017259 | 50.945 | 1098.1 | 1047.155
5085 | 0.55691 | 82.86 | 62.186 | 0.0017264 | 50.955 | 1098.1 |  | 5085 | 82.86 | 0.55691 | 62.186 | 0.0017264 | 50.955 | 1098.1 | 1047.145
5086 | 0.55709 | 82.87 | 62.186 | 0.001727 | 50.965 | 1098.1 |  | 5086 | 82.87 | 0.55709 | 62.186 | 0.001727 | 50.965 | 1098.1 | 1047.135
5087 | 0.55727 | 82.88 | 62.186 | 0.0017275 | 50.975 | 1098.1 |  | 5087 | 82.88 | 0.55727 | 62.186 | 0.0017275 | 50.975 | 1098.1 | 1047.125
5088 | 0.55745 | 82.89 | 62.185 | 0.001728 | 50.985 | 1098.1 |  | 5088 | 82.89 | 0.55745 | 62.185 | 0.001728 | 50.985 | 1098.1 | 1047.115
5089 | 0.55763 | 82.9 | 62.185 | 0.0017285 | 50.995 | 1098.1 |  | 5089 | 82.9 | 0.55763 | 62.185 | 0.0017285 | 50.995 | 1098.1 | 1047.105
5090 | 0.55781 | 82.91 | 62.185 | 0.0017291 | 51.005 | 1098.1 |  | 5090 | 82.91 | 0.55781 | 62.185 | 0.0017291 | 51.005 | 1098.1 | 1047.095
5091 | 0.55799 | 82.92 | 62.185 | 0.0017296 | 51.015 | 1098.1 |  | 5091 | 82.92 | 0.55799 | 62.185 | 0.0017296 | 51.015 | 1098.1 | 1047.085
5092 | 0.55817 | 82.93 | 62.185 | 0.0017301 | 51.025 | 1098.1 |  | 5092 | 82.93 | 0.55817 | 62.185 | 0.0017301 | 51.025 | 1098.1 | 1047.075
5093 | 0.55835 | 82.94 | 62.185 | 0.0017306 | 51.035 | 1098.1 |  | 5093 | 82.94 | 0.55835 | 62.185 | 0.0017306 | 51.035 | 1098.1 | 1047.065
5094 | 0.55853 | 82.95 | 62.185 | 0.0017312 | 51.045 | 1098.1 |  | 5094 | 82.95 | 0.55853 | 62.185 | 0.0017312 | 51.045 | 1098.1 | 1047.055
5095 | 0.55871 | 82.96 | 62.185 | 0.0017317 | 51.055 | 1098.1 |  | 5095 | 82.96 | 0.55871 | 62.185 | 0.0017317 | 51.055 | 1098.1 | 1047.045
5096 | 0.55889 | 82.97 | 62.185 | 0.0017322 | 51.065 | 1098.1 |  | 5096 | 82.97 | 0.55889 | 62.185 | 0.0017322 | 51.065 | 1098.1 | 1047.035
5097 | 0.55907 | 82.98 | 62.185 | 0.0017328 | 51.075 | 1098.1 |  | 5097 | 82.98 | 0.55907 | 62.185 | 0.0017328 | 51.075 | 1098.1 | 1047.025
5098 | 0.55925 | 82.99 | 62.184 | 0.0017333 | 51.085 | 1098.1 |  | 5098 | 82.99 | 0.55925 | 62.184 | 0.0017333 | 51.085 | 1098.1 | 1047.015
5099 | 0.55943 | 83 | 62.184 | 0.0017338 | 51.095 | 1098.1 |  | 5099 | 83 | 0.55943 | 62.184 | 0.0017338 | 51.095 | 1098.1 | 1047.005
5100 | 0.55961 | 83.01 | 62.184 | 0.0017343 | 51.105 | 1098.1 |  | 5100 | 83.01 | 0.55961 | 62.184 | 0.0017343 | 51.105 | 1098.1 | 1046.995
5101 | 0.5598 | 83.02 | 62.184 | 0.0017349 | 51.115 | 1098.1 |  | 5101 | 83.02 | 0.5598 | 62.184 | 0.0017349 | 51.115 | 1098.1 | 1046.985
5102 | 0.55998 | 83.03 | 62.184 | 0.0017354 | 51.125 | 1098.1 |  | 5102 | 83.03 | 0.55998 | 62.184 | 0.0017354 | 51.125 | 1098.1 | 1046.975
5103 | 0.56016 | 83.04 | 62.184 | 0.0017359 | 51.135 | 1098.1 |  | 5103 | 83.04 | 0.56016 | 62.184 | 0.0017359 | 51.135 | 1098.1 | 1046.965
5104 | 0.56034 | 83.05 | 62.184 | 0.0017365 | 51.145 | 1098.1 |  | 5104 | 83.05 | 0.56034 | 62.184 | 0.0017365 | 51.145 | 1098.1 | 1046.955
5105 | 0.56052 | 83.06 | 62.184 | 0.001737 | 51.155 | 1098.2 |  | 5105 | 83.06 | 0.56052 | 62.184 | 0.001737 | 51.155 | 1098.2 | 1047.045
5106 | 0.5607 | 83.07 | 62.184 | 0.0017375 | 51.165 | 1098.2 |  | 5106 | 83.07 | 0.5607 | 62.184 | 0.0017375 | 51.165 | 1098.2 | 1047.035
5107 | 0.56088 | 83.08 | 62.184 | 0.001738 | 51.175 | 1098.2 |  | 5107 | 83.08 | 0.56088 | 62.184 | 0.001738 | 51.175 | 1098.2 | 1047.025
5108 | 0.56106 | 83.09 | 62.183 | 0.0017386 | 51.185 | 1098.2 |  | 5108 | 83.09 | 0.56106 | 62.183 | 0.0017386 | 51.185 | 1098.2 | 1047.015
5109 | 0.56124 | 83.1 | 62.183 | 0.0017391 | 51.194 | 1098.2 |  | 5109 | 83.1 | 0.56124 | 62.183 | 0.0017391 | 51.194 | 1098.2 | 1047.006
5110 | 0.56142 | 83.11 | 62.183 | 0.0017396 | 51.204 | 1098.2 |  | 5110 | 83.11 | 0.56142 | 62.183 | 0.0017396 | 51.204 | 1098.2 | 1046.996
5111 | 0.56161 | 83.12 | 62.183 | 0.0017402 | 51.214 | 1098.2 |  | 5111 | 83.12 | 0.56161 | 62.183 | 0.0017402 | 51.214 | 1098.2 | 1046.986
5112 | 0.56179 | 83.13 | 62.183 | 0.0017407 | 51.224 | 1098.2 |  | 5112 | 83.13 | 0.56179 | 62.183 | 0.0017407 | 51.224 | 1098.2 | 1046.976
5113 | 0.56197 | 83.14 | 62.183 | 0.0017412 | 51.234 | 1098.2 |  | 5113 | 83.14 | 0.56197 | 62.183 | 0.0017412 | 51.234 | 1098.2 | 1046.966
5114 | 0.56215 | 83.15 | 62.183 | 0.0017418 | 51.244 | 1098.2 |  | 5114 | 83.15 | 0.56215 | 62.183 | 0.0017418 | 51.244 | 1098.2 | 1046.956
5115 | 0.56233 | 83.16 | 62.183 | 0.0017423 | 51.254 | 1098.2 |  | 5115 | 83.16 | 0.56233 | 62.183 | 0.0017423 | 51.254 | 1098.2 | 1046.946
5116 | 0.56251 | 83.17 | 62.183 | 0.0017428 | 51.264 | 1098.2 |  | 5116 | 83.17 | 0.56251 | 62.183 | 0.0017428 | 51.264 | 1098.2 | 1046.936
5117 | 0.56269 | 83.18 | 62.183 | 0.0017433 | 51.274 | 1098.2 |  | 5117 | 83.18 | 0.56269 | 62.183 | 0.0017433 | 51.274 | 1098.2 | 1046.926
5118 | 0.56288 | 83.19 | 62.182 | 0.0017439 | 51.284 | 1098.2 |  | 5118 | 83.19 | 0.56288 | 62.182 | 0.0017439 | 51.284 | 1098.2 | 1046.916
5119 | 0.56306 | 83.2 | 62.182 | 0.0017444 | 51.294 | 1098.2 |  | 5119 | 83.2 | 0.56306 | 62.182 | 0.0017444 | 51.294 | 1098.2 | 1046.906
5120 | 0.56324 | 83.21 | 62.182 | 0.0017449 | 51.304 | 1098.2 |  | 5120 | 83.21 | 0.56324 | 62.182 | 0.0017449 | 51.304 | 1098.2 | 1046.896
5121 | 0.56342 | 83.22 | 62.182 | 0.0017455 | 51.314 | 1098.2 |  | 5121 | 83.22 | 0.56342 | 62.182 | 0.0017455 | 51.314 | 1098.2 | 1046.886
5122 | 0.5636 | 83.23 | 62.182 | 0.001746 | 51.324 | 1098.2 |  | 5122 | 83.23 | 0.5636 | 62.182 | 0.001746 | 51.324 | 1098.2 | 1046.876
5123 | 0.56378 | 83.24 | 62.182 | 0.0017465 | 51.334 | 1098.2 |  | 5123 | 83.24 | 0.56378 | 62.182 | 0.0017465 | 51.334 | 1098.2 | 1046.866
5124 | 0.56397 | 83.25 | 62.182 | 0.0017471 | 51.344 | 1098.2 |  | 5124 | 83.25 | 0.56397 | 62.182 | 0.0017471 | 51.344 | 1098.2 | 1046.856
5125 | 0.56415 | 83.26 | 62.182 | 0.0017476 | 51.354 | 1098.2 |  | 5125 | 83.26 | 0.56415 | 62.182 | 0.0017476 | 51.354 | 1098.2 | 1046.846
5126 | 0.56433 | 83.27 | 62.182 | 0.0017481 | 51.364 | 1098.2 |  | 5126 | 83.27 | 0.56433 | 62.182 | 0.0017481 | 51.364 | 1098.2 | 1046.836
5127 | 0.56451 | 83.28 | 62.182 | 0.0017487 | 51.374 | 1098.2 |  | 5127 | 83.28 | 0.56451 | 62.182 | 0.0017487 | 51.374 | 1098.2 | 1046.826
5128 | 0.56469 | 83.29 | 62.181 | 0.0017492 | 51.384 | 1098.3 |  | 5128 | 83.29 | 0.56469 | 62.181 | 0.0017492 | 51.384 | 1098.3 | 1046.916
5129 | 0.56488 | 83.3 | 62.181 | 0.0017497 | 51.394 | 1098.3 |  | 5129 | 83.3 | 0.56488 | 62.181 | 0.0017497 | 51.394 | 1098.3 | 1046.906
5130 | 0.56506 | 83.31 | 62.181 | 0.0017503 | 51.404 | 1098.3 |  | 5130 | 83.31 | 0.56506 | 62.181 | 0.0017503 | 51.404 | 1098.3 | 1046.896
5131 | 0.56524 | 83.32 | 62.181 | 0.0017508 | 51.414 | 1098.3 |  | 5131 | 83.32 | 0.56524 | 62.181 | 0.0017508 | 51.414 | 1098.3 | 1046.886
5132 | 0.56542 | 83.33 | 62.181 | 0.0017513 | 51.424 | 1098.3 |  | 5132 | 83.33 | 0.56542 | 62.181 | 0.0017513 | 51.424 | 1098.3 | 1046.876
5133 | 0.56561 | 83.34 | 62.181 | 0.0017519 | 51.434 | 1098.3 |  | 5133 | 83.34 | 0.56561 | 62.181 | 0.0017519 | 51.434 | 1098.3 | 1046.866
5134 | 0.56579 | 83.35 | 62.181 | 0.0017524 | 51.444 | 1098.3 |  | 5134 | 83.35 | 0.56579 | 62.181 | 0.0017524 | 51.444 | 1098.3 | 1046.856
5135 | 0.56597 | 83.36 | 62.181 | 0.0017529 | 51.454 | 1098.3 |  | 5135 | 83.36 | 0.56597 | 62.181 | 0.0017529 | 51.454 | 1098.3 | 1046.846
5136 | 0.56615 | 83.37 | 62.181 | 0.0017535 | 51.464 | 1098.3 |  | 5136 | 83.37 | 0.56615 | 62.181 | 0.0017535 | 51.464 | 1098.3 | 1046.836
5137 | 0.56634 | 83.38 | 62.181 | 0.001754 | 51.474 | 1098.3 |  | 5137 | 83.38 | 0.56634 | 62.181 | 0.001754 | 51.474 | 1098.3 | 1046.826
5138 | 0.56652 | 83.39 | 62.18 | 0.0017545 | 51.484 | 1098.3 |  | 5138 | 83.39 | 0.56652 | 62.18 | 0.0017545 | 51.484 | 1098.3 | 1046.816
5139 | 0.5667 | 83.4 | 62.18 | 0.0017551 | 51.494 | 1098.3 |  | 5139 | 83.4 | 0.5667 | 62.18 | 0.0017551 | 51.494 | 1098.3 | 1046.806
5140 | 0.56688 | 83.41 | 62.18 | 0.0017556 | 51.504 | 1098.3 |  | 5140 | 83.41 | 0.56688 | 62.18 | 0.0017556 | 51.504 | 1098.3 | 1046.796
5141 | 0.56707 | 83.42 | 62.18 | 0.0017561 | 51.514 | 1098.3 |  | 5141 | 83.42 | 0.56707 | 62.18 | 0.0017561 | 51.514 | 1098.3 | 1046.786
5142 | 0.56725 | 83.43 | 62.18 | 0.0017567 | 51.524 | 1098.3 |  | 5142 | 83.43 | 0.56725 | 62.18 | 0.0017567 | 51.524 | 1098.3 | 1046.776
5143 | 0.56743 | 83.44 | 62.18 | 0.0017572 | 51.534 | 1098.3 |  | 5143 | 83.44 | 0.56743 | 62.18 | 0.0017572 | 51.534 | 1098.3 | 1046.766
5144 | 0.56762 | 83.45 | 62.18 | 0.0017577 | 51.544 | 1098.3 |  | 5144 | 83.45 | 0.56762 | 62.18 | 0.0017577 | 51.544 | 1098.3 | 1046.756
5145 | 0.5678 | 83.46 | 62.18 | 0.0017583 | 51.554 | 1098.3 |  | 5145 | 83.46 | 0.5678 | 62.18 | 0.0017583 | 51.554 | 1098.3 | 1046.746
5146 | 0.56798 | 83.47 | 62.18 | 0.0017588 | 51.564 | 1098.3 |  | 5146 | 83.47 | 0.56798 | 62.18 | 0.0017588 | 51.564 | 1098.3 | 1046.736
5147 | 0.56816 | 83.48 | 62.18 | 0.0017593 | 51.574 | 1098.3 |  | 5147 | 83.48 | 0.56816 | 62.18 | 0.0017593 | 51.574 | 1098.3 | 1046.726
5148 | 0.56835 | 83.49 | 62.179 | 0.0017599 | 51.584 | 1098.3 |  | 5148 | 83.49 | 0.56835 | 62.179 | 0.0017599 | 51.584 | 1098.3 | 1046.716
5149 | 0.56853 | 83.5 | 62.179 | 0.0017604 | 51.594 | 1098.3 |  | 5149 | 83.5 | 0.56853 | 62.179 | 0.0017604 | 51.594 | 1098.3 | 1046.706
5150 | 0.56871 | 83.51 | 62.179 | 0.001761 | 51.604 | 1098.3 |  | 5150 | 83.51 | 0.56871 | 62.179 | 0.001761 | 51.604 | 1098.3 | 1046.696
5151 | 0.5689 | 83.52 | 62.179 | 0.0017615 | 51.614 | 1098.4 |  | 5151 | 83.52 | 0.5689 | 62.179 | 0.0017615 | 51.614 | 1098.4 | 1046.786
5152 | 0.56908 | 83.53 | 62.179 | 0.001762 | 51.624 | 1098.4 |  | 5152 | 83.53 | 0.56908 | 62.179 | 0.001762 | 51.624 | 1098.4 | 1046.776
5153 | 0.56926 | 83.54 | 62.179 | 0.0017626 | 51.634 | 1098.4 |  | 5153 | 83.54 | 0.56926 | 62.179 | 0.0017626 | 51.634 | 1098.4 | 1046.766
5154 | 0.56945 | 83.55 | 62.179 | 0.0017631 | 51.644 | 1098.4 |  | 5154 | 83.55 | 0.56945 | 62.179 | 0.0017631 | 51.644 | 1098.4 | 1046.756
5155 | 0.56963 | 83.56 | 62.179 | 0.0017636 | 51.654 | 1098.4 |  | 5155 | 83.56 | 0.56963 | 62.179 | 0.0017636 | 51.654 | 1098.4 | 1046.746
5156 | 0.56981 | 83.57 | 62.179 | 0.0017642 | 51.664 | 1098.4 |  | 5156 | 83.57 | 0.56981 | 62.179 | 0.0017642 | 51.664 | 1098.4 | 1046.736
5157 | 0.57 | 83.58 | 62.179 | 0.0017647 | 51.674 | 1098.4 |  | 5157 | 83.58 | 0.57 | 62.179 | 0.0017647 | 51.674 | 1098.4 | 1046.726
5158 | 0.57018 | 83.59 | 62.178 | 0.0017652 | 51.684 | 1098.4 |  | 5158 | 83.59 | 0.57018 | 62.178 | 0.0017652 | 51.684 | 1098.4 | 1046.716
5159 | 0.57037 | 83.6 | 62.178 | 0.0017658 | 51.694 | 1098.4 |  | 5159 | 83.6 | 0.57037 | 62.178 | 0.0017658 | 51.694 | 1098.4 | 1046.706
5160 | 0.57055 | 83.61 | 62.178 | 0.0017663 | 51.704 | 1098.4 |  | 5160 | 83.61 | 0.57055 | 62.178 | 0.0017663 | 51.704 | 1098.4 | 1046.696
5161 | 0.57073 | 83.62 | 62.178 | 0.0017669 | 51.714 | 1098.4 |  | 5161 | 83.62 | 0.57073 | 62.178 | 0.0017669 | 51.714 | 1098.4 | 1046.686
5162 | 0.57092 | 83.63 | 62.178 | 0.0017674 | 51.724 | 1098.4 |  | 5162 | 83.63 | 0.57092 | 62.178 | 0.0017674 | 51.724 | 1098.4 | 1046.676
5163 | 0.5711 | 83.64 | 62.178 | 0.0017679 | 51.734 | 1098.4 |  | 5163 | 83.64 | 0.5711 | 62.178 | 0.0017679 | 51.734 | 1098.4 | 1046.666
5164 | 0.57128 | 83.65 | 62.178 | 0.0017685 | 51.744 | 1098.4 |  | 5164 | 83.65 | 0.57128 | 62.178 | 0.0017685 | 51.744 | 1098.4 | 1046.656
5165 | 0.57147 | 83.66 | 62.178 | 0.001769 | 51.754 | 1098.4 |  | 5165 | 83.66 | 0.57147 | 62.178 | 0.001769 | 51.754 | 1098.4 | 1046.646
5166 | 0.57165 | 83.67 | 62.178 | 0.0017695 | 51.764 | 1098.4 |  | 5166 | 83.67 | 0.57165 | 62.178 | 0.0017695 | 51.764 | 1098.4 | 1046.636
5167 | 0.57184 | 83.68 | 62.177 | 0.0017701 | 51.774 | 1098.4 |  | 5167 | 83.68 | 0.57184 | 62.177 | 0.0017701 | 51.774 | 1098.4 | 1046.626
5168 | 0.57202 | 83.69 | 62.177 | 0.0017706 | 51.784 | 1098.4 |  | 5168 | 83.69 | 0.57202 | 62.177 | 0.0017706 | 51.784 | 1098.4 | 1046.616
5169 | 0.57221 | 83.7 | 62.177 | 0.0017712 | 51.794 | 1098.4 |  | 5169 | 83.7 | 0.57221 | 62.177 | 0.0017712 | 51.794 | 1098.4 | 1046.606
5170 | 0.57239 | 83.71 | 62.177 | 0.0017717 | 51.804 | 1098.4 |  | 5170 | 83.71 | 0.57239 | 62.177 | 0.0017717 | 51.804 | 1098.4 | 1046.596
5171 | 0.57257 | 83.72 | 62.177 | 0.0017722 | 51.814 | 1098.4 |  | 5171 | 83.72 | 0.57257 | 62.177 | 0.0017722 | 51.814 | 1098.4 | 1046.586
5172 | 0.57276 | 83.73 | 62.177 | 0.0017728 | 51.824 | 1098.4 |  | 5172 | 83.73 | 0.57276 | 62.177 | 0.0017728 | 51.824 | 1098.4 | 1046.576
5173 | 0.57294 | 83.74 | 62.177 | 0.0017733 | 51.834 | 1098.4 |  | 5173 | 83.74 | 0.57294 | 62.177 | 0.0017733 | 51.834 | 1098.4 | 1046.566
5174 | 0.57313 | 83.75 | 62.177 | 0.0017738 | 51.844 | 1098.5 |  | 5174 | 83.75 | 0.57313 | 62.177 | 0.0017738 | 51.844 | 1098.5 | 1046.656
5175 | 0.57331 | 83.76 | 62.177 | 0.0017744 | 51.854 | 1098.5 |  | 5175 | 83.76 | 0.57331 | 62.177 | 0.0017744 | 51.854 | 1098.5 | 1046.646
5176 | 0.5735 | 83.77 | 62.177 | 0.0017749 | 51.864 | 1098.5 |  | 5176 | 83.77 | 0.5735 | 62.177 | 0.0017749 | 51.864 | 1098.5 | 1046.636
5177 | 0.57368 | 83.78 | 62.176 | 0.0017755 | 51.874 | 1098.5 |  | 5177 | 83.78 | 0.57368 | 62.176 | 0.0017755 | 51.874 | 1098.5 | 1046.626
5178 | 0.57387 | 83.79 | 62.176 | 0.001776 | 51.884 | 1098.5 |  | 5178 | 83.79 | 0.57387 | 62.176 | 0.001776 | 51.884 | 1098.5 | 1046.616
5179 | 0.57405 | 83.8 | 62.176 | 0.0017765 | 51.894 | 1098.5 |  | 5179 | 83.8 | 0.57405 | 62.176 | 0.0017765 | 51.894 | 1098.5 | 1046.606
5180 | 0.57424 | 83.81 | 62.176 | 0.0017771 | 51.904 | 1098.5 |  | 5180 | 83.81 | 0.57424 | 62.176 | 0.0017771 | 51.904 | 1098.5 | 1046.596
5181 | 0.57442 | 83.82 | 62.176 | 0.0017776 | 51.914 | 1098.5 |  | 5181 | 83.82 | 0.57442 | 62.176 | 0.0017776 | 51.914 | 1098.5 | 1046.586
5182 | 0.5746 | 83.83 | 62.176 | 0.0017782 | 51.924 | 1098.5 |  | 5182 | 83.83 | 0.5746 | 62.176 | 0.0017782 | 51.924 | 1098.5 | 1046.576
5183 | 0.57479 | 83.84 | 62.176 | 0.0017787 | 51.934 | 1098.5 |  | 5183 | 83.84 | 0.57479 | 62.176 | 0.0017787 | 51.934 | 1098.5 | 1046.566
5184 | 0.57497 | 83.85 | 62.176 | 0.0017792 | 51.944 | 1098.5 |  | 5184 | 83.85 | 0.57497 | 62.176 | 0.0017792 | 51.944 | 1098.5 | 1046.556
5185 | 0.57516 | 83.86 | 62.176 | 0.0017798 | 51.954 | 1098.5 |  | 5185 | 83.86 | 0.57516 | 62.176 | 0.0017798 | 51.954 | 1098.5 | 1046.546
5186 | 0.57534 | 83.87 | 62.176 | 0.0017803 | 51.964 | 1098.5 |  | 5186 | 83.87 | 0.57534 | 62.176 | 0.0017803 | 51.964 | 1098.5 | 1046.536
5187 | 0.57553 | 83.88 | 62.175 | 0.0017809 | 51.974 | 1098.5 |  | 5187 | 83.88 | 0.57553 | 62.175 | 0.0017809 | 51.974 | 1098.5 | 1046.526
5188 | 0.57572 | 83.89 | 62.175 | 0.0017814 | 51.984 | 1098.5 |  | 5188 | 83.89 | 0.57572 | 62.175 | 0.0017814 | 51.984 | 1098.5 | 1046.516
5189 | 0.5759 | 83.9 | 62.175 | 0.001782 | 51.994 | 1098.5 |  | 5189 | 83.9 | 0.5759 | 62.175 | 0.001782 | 51.994 | 1098.5 | 1046.506
5190 | 0.57609 | 83.91 | 62.175 | 0.0017825 | 52.004 | 1098.5 |  | 5190 | 83.91 | 0.57609 | 62.175 | 0.0017825 | 52.004 | 1098.5 | 1046.496
5191 | 0.57627 | 83.92 | 62.175 | 0.001783 | 52.014 | 1098.5 |  | 5191 | 83.92 | 0.57627 | 62.175 | 0.001783 | 52.014 | 1098.5 | 1046.486
5192 | 0.57646 | 83.93 | 62.175 | 0.0017836 | 52.024 | 1098.5 |  | 5192 | 83.93 | 0.57646 | 62.175 | 0.0017836 | 52.024 | 1098.5 | 1046.476
5193 | 0.57664 | 83.94 | 62.175 | 0.0017841 | 52.034 | 1098.5 |  | 5193 | 83.94 | 0.57664 | 62.175 | 0.0017841 | 52.034 | 1098.5 | 1046.466
5194 | 0.57683 | 83.95 | 62.175 | 0.0017847 | 52.044 | 1098.5 |  | 5194 | 83.95 | 0.57683 | 62.175 | 0.0017847 | 52.044 | 1098.5 | 1046.456
5195 | 0.57701 | 83.96 | 62.175 | 0.0017852 | 52.054 | 1098.5 |  | 5195 | 83.96 | 0.57701 | 62.175 | 0.0017852 | 52.054 | 1098.5 | 1046.446
5196 | 0.5772 | 83.97 | 62.175 | 0.0017857 | 52.064 | 1098.5 |  | 5196 | 83.97 | 0.5772 | 62.175 | 0.0017857 | 52.064 | 1098.5 | 1046.436
5197 | 0.57738 | 83.98 | 62.174 | 0.0017863 | 52.074 | 1098.6 |  | 5197 | 83.98 | 0.57738 | 62.174 | 0.0017863 | 52.074 | 1098.6 | 1046.526
5198 | 0.57757 | 83.99 | 62.174 | 0.0017868 | 52.084 | 1098.6 |  | 5198 | 83.99 | 0.57757 | 62.174 | 0.0017868 | 52.084 | 1098.6 | 1046.516
5199 | 0.57776 | 84 | 62.174 | 0.0017874 | 52.094 | 1098.6 |  | 5199 | 84 | 0.57776 | 62.174 | 0.0017874 | 52.094 | 1098.6 | 1046.506
5200 | 0.57794 | 84.01 | 62.174 | 0.0017879 | 52.104 | 1098.6 |  | 5200 | 84.01 | 0.57794 | 62.174 | 0.0017879 | 52.104 | 1098.6 | 1046.496
5201 | 0.57813 | 84.02 | 62.174 | 0.0017885 | 52.114 | 1098.6 |  | 5201 | 84.02 | 0.57813 | 62.174 | 0.0017885 | 52.114 | 1098.6 | 1046.486
5202 | 0.57831 | 84.03 | 62.174 | 0.001789 | 52.124 | 1098.6 |  | 5202 | 84.03 | 0.57831 | 62.174 | 0.001789 | 52.124 | 1098.6 | 1046.476
5203 | 0.5785 | 84.04 | 62.174 | 0.0017895 | 52.134 | 1098.6 |  | 5203 | 84.04 | 0.5785 | 62.174 | 0.0017895 | 52.134 | 1098.6 | 1046.466
5204 | 0.57869 | 84.05 | 62.174 | 0.0017901 | 52.144 | 1098.6 |  | 5204 | 84.05 | 0.57869 | 62.174 | 0.0017901 | 52.144 | 1098.6 | 1046.456
5205 | 0.57887 | 84.06 | 62.174 | 0.0017906 | 52.154 | 1098.6 |  | 5205 | 84.06 | 0.57887 | 62.174 | 0.0017906 | 52.154 | 1098.6 | 1046.446
5206 | 0.57906 | 84.07 | 62.174 | 0.0017912 | 52.164 | 1098.6 |  | 5206 | 84.07 | 0.57906 | 62.174 | 0.0017912 | 52.164 | 1098.6 | 1046.436
5207 | 0.57924 | 84.08 | 62.173 | 0.0017917 | 52.174 | 1098.6 |  | 5207 | 84.08 | 0.57924 | 62.173 | 0.0017917 | 52.174 | 1098.6 | 1046.426
5208 | 0.57943 | 84.09 | 62.173 | 0.0017923 | 52.184 | 1098.6 |  | 5208 | 84.09 | 0.57943 | 62.173 | 0.0017923 | 52.184 | 1098.6 | 1046.416
5209 | 0.57962 | 84.1 | 62.173 | 0.0017928 | 52.194 | 1098.6 |  | 5209 | 84.1 | 0.57962 | 62.173 | 0.0017928 | 52.194 | 1098.6 | 1046.406
5210 | 0.5798 | 84.11 | 62.173 | 0.0017933 | 52.204 | 1098.6 |  | 5210 | 84.11 | 0.5798 | 62.173 | 0.0017933 | 52.204 | 1098.6 | 1046.396
5211 | 0.57999 | 84.12 | 62.173 | 0.0017939 | 52.214 | 1098.6 |  | 5211 | 84.12 | 0.57999 | 62.173 | 0.0017939 | 52.214 | 1098.6 | 1046.386
5212 | 0.58018 | 84.13 | 62.173 | 0.0017944 | 52.224 | 1098.6 |  | 5212 | 84.13 | 0.58018 | 62.173 | 0.0017944 | 52.224 | 1098.6 | 1046.376
5213 | 0.58036 | 84.14 | 62.173 | 0.001795 | 52.234 | 1098.6 |  | 5213 | 84.14 | 0.58036 | 62.173 | 0.001795 | 52.234 | 1098.6 | 1046.366
5214 | 0.58055 | 84.15 | 62.173 | 0.0017955 | 52.244 | 1098.6 |  | 5214 | 84.15 | 0.58055 | 62.173 | 0.0017955 | 52.244 | 1098.6 | 1046.356
5215 | 0.58074 | 84.16 | 62.173 | 0.0017961 | 52.254 | 1098.6 |  | 5215 | 84.16 | 0.58074 | 62.173 | 0.0017961 | 52.254 | 1098.6 | 1046.346
5216 | 0.58092 | 84.17 | 62.173 | 0.0017966 | 52.264 | 1098.6 |  | 5216 | 84.17 | 0.58092 | 62.173 | 0.0017966 | 52.264 | 1098.6 | 1046.336
5217 | 0.58111 | 84.18 | 62.172 | 0.0017972 | 52.274 | 1098.6 |  | 5217 | 84.18 | 0.58111 | 62.172 | 0.0017972 | 52.274 | 1098.6 | 1046.326
5218 | 0.5813 | 84.19 | 62.172 | 0.0017977 | 52.284 | 1098.6 |  | 5218 | 84.19 | 0.5813 | 62.172 | 0.0017977 | 52.284 | 1098.6 | 1046.316
5219 | 0.58148 | 84.2 | 62.172 | 0.0017982 | 52.294 | 1098.6 |  | 5219 | 84.2 | 0.58148 | 62.172 | 0.0017982 | 52.294 | 1098.6 | 1046.306
5220 | 0.58167 | 84.21 | 62.172 | 0.0017988 | 52.304 | 1098.6 |  | 5220 | 84.21 | 0.58167 | 62.172 | 0.0017988 | 52.304 | 1098.6 | 1046.296
5221 | 0.58186 | 84.22 | 62.172 | 0.0017993 | 52.314 | 1098.7 |  | 5221 | 84.22 | 0.58186 | 62.172 | 0.0017993 | 52.314 | 1098.7 | 1046.386
5222 | 0.58204 | 84.23 | 62.172 | 0.0017999 | 52.324 | 1098.7 |  | 5222 | 84.23 | 0.58204 | 62.172 | 0.0017999 | 52.324 | 1098.7 | 1046.376
5223 | 0.58223 | 84.24 | 62.172 | 0.0018004 | 52.334 | 1098.7 |  | 5223 | 84.24 | 0.58223 | 62.172 | 0.0018004 | 52.334 | 1098.7 | 1046.366
5224 | 0.58242 | 84.25 | 62.172 | 0.001801 | 52.344 | 1098.7 |  | 5224 | 84.25 | 0.58242 | 62.172 | 0.001801 | 52.344 | 1098.7 | 1046.356
5225 | 0.5826 | 84.26 | 62.172 | 0.0018015 | 52.354 | 1098.7 |  | 5225 | 84.26 | 0.5826 | 62.172 | 0.0018015 | 52.354 | 1098.7 | 1046.346
5226 | 0.58279 | 84.27 | 62.172 | 0.0018021 | 52.364 | 1098.7 |  | 5226 | 84.27 | 0.58279 | 62.172 | 0.0018021 | 52.364 | 1098.7 | 1046.336
5227 | 0.58298 | 84.28 | 62.171 | 0.0018026 | 52.374 | 1098.7 |  | 5227 | 84.28 | 0.58298 | 62.171 | 0.0018026 | 52.374 | 1098.7 | 1046.326
5228 | 0.58317 | 84.29 | 62.171 | 0.0018032 | 52.384 | 1098.7 |  | 5228 | 84.29 | 0.58317 | 62.171 | 0.0018032 | 52.384 | 1098.7 | 1046.316
5229 | 0.58335 | 84.3 | 62.171 | 0.0018037 | 52.394 | 1098.7 |  | 5229 | 84.3 | 0.58335 | 62.171 | 0.0018037 | 52.394 | 1098.7 | 1046.306
5230 | 0.58354 | 84.31 | 62.171 | 0.0018043 | 52.404 | 1098.7 |  | 5230 | 84.31 | 0.58354 | 62.171 | 0.0018043 | 52.404 | 1098.7 | 1046.296
5231 | 0.58373 | 84.32 | 62.171 | 0.0018048 | 52.413 | 1098.7 |  | 5231 | 84.32 | 0.58373 | 62.171 | 0.0018048 | 52.413 | 1098.7 | 1046.287
5232 | 0.58392 | 84.33 | 62.171 | 0.0018054 | 52.423 | 1098.7 |  | 5232 | 84.33 | 0.58392 | 62.171 | 0.0018054 | 52.423 | 1098.7 | 1046.277
5233 | 0.5841 | 84.34 | 62.171 | 0.0018059 | 52.433 | 1098.7 |  | 5233 | 84.34 | 0.5841 | 62.171 | 0.0018059 | 52.433 | 1098.7 | 1046.267
5234 | 0.58429 | 84.35 | 62.171 | 0.0018064 | 52.443 | 1098.7 |  | 5234 | 84.35 | 0.58429 | 62.171 | 0.0018064 | 52.443 | 1098.7 | 1046.257
5235 | 0.58448 | 84.36 | 62.171 | 0.001807 | 52.453 | 1098.7 |  | 5235 | 84.36 | 0.58448 | 62.171 | 0.001807 | 52.453 | 1098.7 | 1046.247
5236 | 0.58467 | 84.37 | 62.171 | 0.0018075 | 52.463 | 1098.7 |  | 5236 | 84.37 | 0.58467 | 62.171 | 0.0018075 | 52.463 | 1098.7 | 1046.237
5237 | 0.58485 | 84.38 | 62.17 | 0.0018081 | 52.473 | 1098.7 |  | 5237 | 84.38 | 0.58485 | 62.17 | 0.0018081 | 52.473 | 1098.7 | 1046.227
5238 | 0.58504 | 84.39 | 62.17 | 0.0018086 | 52.483 | 1098.7 |  | 5238 | 84.39 | 0.58504 | 62.17 | 0.0018086 | 52.483 | 1098.7 | 1046.217
5239 | 0.58523 | 84.4 | 62.17 | 0.0018092 | 52.493 | 1098.7 |  | 5239 | 84.4 | 0.58523 | 62.17 | 0.0018092 | 52.493 | 1098.7 | 1046.207
5240 | 0.58542 | 84.41 | 62.17 | 0.0018097 | 52.503 | 1098.7 |  | 5240 | 84.41 | 0.58542 | 62.17 | 0.0018097 | 52.503 | 1098.7 | 1046.197
5241 | 0.58561 | 84.42 | 62.17 | 0.0018103 | 52.513 | 1098.7 |  | 5241 | 84.42 | 0.58561 | 62.17 | 0.0018103 | 52.513 | 1098.7 | 1046.187
5242 | 0.58579 | 84.43 | 62.17 | 0.0018108 | 52.523 | 1098.7 |  | 5242 | 84.43 | 0.58579 | 62.17 | 0.0018108 | 52.523 | 1098.7 | 1046.177
5243 | 0.58598 | 84.44 | 62.17 | 0.0018114 | 52.533 | 1098.7 |  | 5243 | 84.44 | 0.58598 | 62.17 | 0.0018114 | 52.533 | 1098.7 | 1046.167
5244 | 0.58617 | 84.45 | 62.17 | 0.0018119 | 52.543 | 1098.8 |  | 5244 | 84.45 | 0.58617 | 62.17 | 0.0018119 | 52.543 | 1098.8 | 1046.257
5245 | 0.58636 | 84.46 | 62.17 | 0.0018125 | 52.553 | 1098.8 |  | 5245 | 84.46 | 0.58636 | 62.17 | 0.0018125 | 52.553 | 1098.8 | 1046.247
5246 | 0.58655 | 84.47 | 62.169 | 0.001813 | 52.563 | 1098.8 |  | 5246 | 84.47 | 0.58655 | 62.169 | 0.001813 | 52.563 | 1098.8 | 1046.237
5247 | 0.58673 | 84.48 | 62.169 | 0.0018136 | 52.573 | 1098.8 |  | 5247 | 84.48 | 0.58673 | 62.169 | 0.0018136 | 52.573 | 1098.8 | 1046.227
5248 | 0.58692 | 84.49 | 62.169 | 0.0018141 | 52.583 | 1098.8 |  | 5248 | 84.49 | 0.58692 | 62.169 | 0.0018141 | 52.583 | 1098.8 | 1046.217
5249 | 0.58711 | 84.5 | 62.169 | 0.0018147 | 52.593 | 1098.8 |  | 5249 | 84.5 | 0.58711 | 62.169 | 0.0018147 | 52.593 | 1098.8 | 1046.207
5250 | 0.5873 | 84.51 | 62.169 | 0.0018152 | 52.603 | 1098.8 |  | 5250 | 84.51 | 0.5873 | 62.169 | 0.0018152 | 52.603 | 1098.8 | 1046.197
5251 | 0.58749 | 84.52 | 62.169 | 0.0018158 | 52.613 | 1098.8 |  | 5251 | 84.52 | 0.58749 | 62.169 | 0.0018158 | 52.613 | 1098.8 | 1046.187
5252 | 0.58768 | 84.53 | 62.169 | 0.0018163 | 52.623 | 1098.8 |  | 5252 | 84.53 | 0.58768 | 62.169 | 0.0018163 | 52.623 | 1098.8 | 1046.177
5253 | 0.58786 | 84.54 | 62.169 | 0.0018169 | 52.633 | 1098.8 |  | 5253 | 84.54 | 0.58786 | 62.169 | 0.0018169 | 52.633 | 1098.8 | 1046.167
5254 | 0.58805 | 84.55 | 62.169 | 0.0018174 | 52.643 | 1098.8 |  | 5254 | 84.55 | 0.58805 | 62.169 | 0.0018174 | 52.643 | 1098.8 | 1046.157
5255 | 0.58824 | 84.56 | 62.169 | 0.001818 | 52.653 | 1098.8 |  | 5255 | 84.56 | 0.58824 | 62.169 | 0.001818 | 52.653 | 1098.8 | 1046.147
5256 | 0.58843 | 84.57 | 62.168 | 0.0018185 | 52.663 | 1098.8 |  | 5256 | 84.57 | 0.58843 | 62.168 | 0.0018185 | 52.663 | 1098.8 | 1046.137
5257 | 0.58862 | 84.58 | 62.168 | 0.0018191 | 52.673 | 1098.8 |  | 5257 | 84.58 | 0.58862 | 62.168 | 0.0018191 | 52.673 | 1098.8 | 1046.127
5258 | 0.58881 | 84.59 | 62.168 | 0.0018196 | 52.683 | 1098.8 |  | 5258 | 84.59 | 0.58881 | 62.168 | 0.0018196 | 52.683 | 1098.8 | 1046.117
5259 | 0.589 | 84.6 | 62.168 | 0.0018202 | 52.693 | 1098.8 |  | 5259 | 84.6 | 0.589 | 62.168 | 0.0018202 | 52.693 | 1098.8 | 1046.107
5260 | 0.58919 | 84.61 | 62.168 | 0.0018207 | 52.703 | 1098.8 |  | 5260 | 84.61 | 0.58919 | 62.168 | 0.0018207 | 52.703 | 1098.8 | 1046.097
5261 | 0.58938 | 84.62 | 62.168 | 0.0018213 | 52.713 | 1098.8 |  | 5261 | 84.62 | 0.58938 | 62.168 | 0.0018213 | 52.713 | 1098.8 | 1046.087
5262 | 0.58956 | 84.63 | 62.168 | 0.0018218 | 52.723 | 1098.8 |  | 5262 | 84.63 | 0.58956 | 62.168 | 0.0018218 | 52.723 | 1098.8 | 1046.077
5263 | 0.58975 | 84.64 | 62.168 | 0.0018224 | 52.733 | 1098.8 |  | 5263 | 84.64 | 0.58975 | 62.168 | 0.0018224 | 52.733 | 1098.8 | 1046.067
5264 | 0.58994 | 84.65 | 62.168 | 0.0018229 | 52.743 | 1098.8 |  | 5264 | 84.65 | 0.58994 | 62.168 | 0.0018229 | 52.743 | 1098.8 | 1046.057
5265 | 0.59013 | 84.66 | 62.168 | 0.0018235 | 52.753 | 1098.8 |  | 5265 | 84.66 | 0.59013 | 62.168 | 0.0018235 | 52.753 | 1098.8 | 1046.047
5266 | 0.59032 | 84.67 | 62.167 | 0.001824 | 52.763 | 1098.8 |  | 5266 | 84.67 | 0.59032 | 62.167 | 0.001824 | 52.763 | 1098.8 | 1046.037
5267 | 0.59051 | 84.68 | 62.167 | 0.0018246 | 52.773 | 1098.9 |  | 5267 | 84.68 | 0.59051 | 62.167 | 0.0018246 | 52.773 | 1098.9 | 1046.127
5268 | 0.5907 | 84.69 | 62.167 | 0.0018251 | 52.783 | 1098.9 |  | 5268 | 84.69 | 0.5907 | 62.167 | 0.0018251 | 52.783 | 1098.9 | 1046.117
5269 | 0.59089 | 84.7 | 62.167 | 0.0018257 | 52.793 | 1098.9 |  | 5269 | 84.7 | 0.59089 | 62.167 | 0.0018257 | 52.793 | 1098.9 | 1046.107
5270 | 0.59108 | 84.71 | 62.167 | 0.0018263 | 52.803 | 1098.9 |  | 5270 | 84.71 | 0.59108 | 62.167 | 0.0018263 | 52.803 | 1098.9 | 1046.097
5271 | 0.59127 | 84.72 | 62.167 | 0.0018268 | 52.813 | 1098.9 |  | 5271 | 84.72 | 0.59127 | 62.167 | 0.0018268 | 52.813 | 1098.9 | 1046.087
5272 | 0.59146 | 84.73 | 62.167 | 0.0018274 | 52.823 | 1098.9 |  | 5272 | 84.73 | 0.59146 | 62.167 | 0.0018274 | 52.823 | 1098.9 | 1046.077
5273 | 0.59165 | 84.74 | 62.167 | 0.0018279 | 52.833 | 1098.9 |  | 5273 | 84.74 | 0.59165 | 62.167 | 0.0018279 | 52.833 | 1098.9 | 1046.067
5274 | 0.59184 | 84.75 | 62.167 | 0.0018285 | 52.843 | 1098.9 |  | 5274 | 84.75 | 0.59184 | 62.167 | 0.0018285 | 52.843 | 1098.9 | 1046.057
5275 | 0.59203 | 84.76 | 62.167 | 0.001829 | 52.853 | 1098.9 |  | 5275 | 84.76 | 0.59203 | 62.167 | 0.001829 | 52.853 | 1098.9 | 1046.047
5276 | 0.59222 | 84.77 | 62.166 | 0.0018296 | 52.863 | 1098.9 |  | 5276 | 84.77 | 0.59222 | 62.166 | 0.0018296 | 52.863 | 1098.9 | 1046.037
5277 | 0.59241 | 84.78 | 62.166 | 0.0018301 | 52.873 | 1098.9 |  | 5277 | 84.78 | 0.59241 | 62.166 | 0.0018301 | 52.873 | 1098.9 | 1046.027
5278 | 0.5926 | 84.79 | 62.166 | 0.0018307 | 52.883 | 1098.9 |  | 5278 | 84.79 | 0.5926 | 62.166 | 0.0018307 | 52.883 | 1098.9 | 1046.017
5279 | 0.59279 | 84.8 | 62.166 | 0.0018312 | 52.893 | 1098.9 |  | 5279 | 84.8 | 0.59279 | 62.166 | 0.0018312 | 52.893 | 1098.9 | 1046.007
5280 | 0.59298 | 84.81 | 62.166 | 0.0018318 | 52.903 | 1098.9 |  | 5280 | 84.81 | 0.59298 | 62.166 | 0.0018318 | 52.903 | 1098.9 | 1045.997
5281 | 0.59317 | 84.82 | 62.166 | 0.0018323 | 52.913 | 1098.9 |  | 5281 | 84.82 | 0.59317 | 62.166 | 0.0018323 | 52.913 | 1098.9 | 1045.987
5282 | 0.59336 | 84.83 | 62.166 | 0.0018329 | 52.923 | 1098.9 |  | 5282 | 84.83 | 0.59336 | 62.166 | 0.0018329 | 52.923 | 1098.9 | 1045.977
5283 | 0.59355 | 84.84 | 62.166 | 0.0018335 | 52.933 | 1098.9 |  | 5283 | 84.84 | 0.59355 | 62.166 | 0.0018335 | 52.933 | 1098.9 | 1045.967
5284 | 0.59374 | 84.85 | 62.166 | 0.001834 | 52.943 | 1098.9 |  | 5284 | 84.85 | 0.59374 | 62.166 | 0.001834 | 52.943 | 1098.9 | 1045.957
5285 | 0.59393 | 84.86 | 62.165 | 0.0018346 | 52.953 | 1098.9 |  | 5285 | 84.86 | 0.59393 | 62.165 | 0.0018346 | 52.953 | 1098.9 | 1045.947
5286 | 0.59412 | 84.87 | 62.165 | 0.0018351 | 52.963 | 1098.9 |  | 5286 | 84.87 | 0.59412 | 62.165 | 0.0018351 | 52.963 | 1098.9 | 1045.937
5287 | 0.59431 | 84.88 | 62.165 | 0.0018357 | 52.973 | 1098.9 |  | 5287 | 84.88 | 0.59431 | 62.165 | 0.0018357 | 52.973 | 1098.9 | 1045.927
5288 | 0.5945 | 84.89 | 62.165 | 0.0018362 | 52.983 | 1098.9 |  | 5288 | 84.89 | 0.5945 | 62.165 | 0.0018362 | 52.983 | 1098.9 | 1045.917
5289 | 0.59469 | 84.9 | 62.165 | 0.0018368 | 52.993 | 1098.9 |  | 5289 | 84.9 | 0.59469 | 62.165 | 0.0018368 | 52.993 | 1098.9 | 1045.907
5290 | 0.59488 | 84.91 | 62.165 | 0.0018373 | 53.003 | 1099 |  | 5290 | 84.91 | 0.59488 | 62.165 | 0.0018373 | 53.003 | 1099 | 1045.997
5291 | 0.59507 | 84.92 | 62.165 | 0.0018379 | 53.013 | 1099 |  | 5291 | 84.92 | 0.59507 | 62.165 | 0.0018379 | 53.013 | 1099 | 1045.987
5292 | 0.59526 | 84.93 | 62.165 | 0.0018384 | 53.023 | 1099 |  | 5292 | 84.93 | 0.59526 | 62.165 | 0.0018384 | 53.023 | 1099 | 1045.977
5293 | 0.59545 | 84.94 | 62.165 | 0.001839 | 53.033 | 1099 |  | 5293 | 84.94 | 0.59545 | 62.165 | 0.001839 | 53.033 | 1099 | 1045.967
5294 | 0.59564 | 84.95 | 62.165 | 0.0018396 | 53.043 | 1099 |  | 5294 | 84.95 | 0.59564 | 62.165 | 0.0018396 | 53.043 | 1099 | 1045.957
5295 | 0.59583 | 84.96 | 62.164 | 0.0018401 | 53.053 | 1099 |  | 5295 | 84.96 | 0.59583 | 62.164 | 0.0018401 | 53.053 | 1099 | 1045.947
5296 | 0.59602 | 84.97 | 62.164 | 0.0018407 | 53.063 | 1099 |  | 5296 | 84.97 | 0.59602 | 62.164 | 0.0018407 | 53.063 | 1099 | 1045.937
5297 | 0.59622 | 84.98 | 62.164 | 0.0018412 | 53.073 | 1099 |  | 5297 | 84.98 | 0.59622 | 62.164 | 0.0018412 | 53.073 | 1099 | 1045.927
5298 | 0.59641 | 84.99 | 62.164 | 0.0018418 | 53.083 | 1099 |  | 5298 | 84.99 | 0.59641 | 62.164 | 0.0018418 | 53.083 | 1099 | 1045.917
5299 | 0.5966 | 85 | 62.164 | 0.0018423 | 53.093 | 1099 |  | 5299 | 85 | 0.5966 | 62.164 | 0.0018423 | 53.093 | 1099 | 1045.907
5300 | 0.59679 | 85.01 | 62.164 | 0.0018429 | 53.103 | 1099 |  | 5300 | 85.01 | 0.59679 | 62.164 | 0.0018429 | 53.103 | 1099 | 1045.897
5301 | 0.59698 | 85.02 | 62.164 | 0.0018435 | 53.113 | 1099 |  | 5301 | 85.02 | 0.59698 | 62.164 | 0.0018435 | 53.113 | 1099 | 1045.887
5302 | 0.59717 | 85.03 | 62.164 | 0.001844 | 53.123 | 1099 |  | 5302 | 85.03 | 0.59717 | 62.164 | 0.001844 | 53.123 | 1099 | 1045.877
5303 | 0.59736 | 85.04 | 62.164 | 0.0018446 | 53.133 | 1099 |  | 5303 | 85.04 | 0.59736 | 62.164 | 0.0018446 | 53.133 | 1099 | 1045.867
5304 | 0.59755 | 85.05 | 62.164 | 0.0018451 | 53.143 | 1099 |  | 5304 | 85.05 | 0.59755 | 62.164 | 0.0018451 | 53.143 | 1099 | 1045.857
5305 | 0.59774 | 85.06 | 62.163 | 0.0018457 | 53.153 | 1099 |  | 5305 | 85.06 | 0.59774 | 62.163 | 0.0018457 | 53.153 | 1099 | 1045.847
5306 | 0.59794 | 85.07 | 62.163 | 0.0018462 | 53.163 | 1099 |  | 5306 | 85.07 | 0.59794 | 62.163 | 0.0018462 | 53.163 | 1099 | 1045.837
5307 | 0.59813 | 85.08 | 62.163 | 0.0018468 | 53.173 | 1099 |  | 5307 | 85.08 | 0.59813 | 62.163 | 0.0018468 | 53.173 | 1099 | 1045.827
5308 | 0.59832 | 85.09 | 62.163 | 0.0018474 | 53.183 | 1099 |  | 5308 | 85.09 | 0.59832 | 62.163 | 0.0018474 | 53.183 | 1099 | 1045.817
5309 | 0.59851 | 85.1 | 62.163 | 0.0018479 | 53.193 | 1099 |  | 5309 | 85.1 | 0.59851 | 62.163 | 0.0018479 | 53.193 | 1099 | 1045.807
5310 | 0.5987 | 85.11 | 62.163 | 0.0018485 | 53.203 | 1099 |  | 5310 | 85.11 | 0.5987 | 62.163 | 0.0018485 | 53.203 | 1099 | 1045.797
5311 | 0.59889 | 85.12 | 62.163 | 0.001849 | 53.213 | 1099 |  | 5311 | 85.12 | 0.59889 | 62.163 | 0.001849 | 53.213 | 1099 | 1045.787
5312 | 0.59909 | 85.13 | 62.163 | 0.0018496 | 53.223 | 1099 |  | 5312 | 85.13 | 0.59909 | 62.163 | 0.0018496 | 53.223 | 1099 | 1045.777
5313 | 0.59928 | 85.14 | 62.163 | 0.0018502 | 53.233 | 1099.1 |  | 5313 | 85.14 | 0.59928 | 62.163 | 0.0018502 | 53.233 | 1099.1 | 1045.867
5314 | 0.59947 | 85.15 | 62.163 | 0.0018507 | 53.243 | 1099.1 |  | 5314 | 85.15 | 0.59947 | 62.163 | 0.0018507 | 53.243 | 1099.1 | 1045.857
5315 | 0.59966 | 85.16 | 62.162 | 0.0018513 | 53.253 | 1099.1 |  | 5315 | 85.16 | 0.59966 | 62.162 | 0.0018513 | 53.253 | 1099.1 | 1045.847
5316 | 0.59985 | 85.17 | 62.162 | 0.0018518 | 53.263 | 1099.1 |  | 5316 | 85.17 | 0.59985 | 62.162 | 0.0018518 | 53.263 | 1099.1 | 1045.837
5317 | 0.60004 | 85.18 | 62.162 | 0.0018524 | 53.273 | 1099.1 |  | 5317 | 85.18 | 0.60004 | 62.162 | 0.0018524 | 53.273 | 1099.1 | 1045.827
5318 | 0.60024 | 85.19 | 62.162 | 0.0018529 | 53.283 | 1099.1 |  | 5318 | 85.19 | 0.60024 | 62.162 | 0.0018529 | 53.283 | 1099.1 | 1045.817
5319 | 0.60043 | 85.2 | 62.162 | 0.0018535 | 53.293 | 1099.1 |  | 5319 | 85.2 | 0.60043 | 62.162 | 0.0018535 | 53.293 | 1099.1 | 1045.807
5320 | 0.60062 | 85.21 | 62.162 | 0.0018541 | 53.303 | 1099.1 |  | 5320 | 85.21 | 0.60062 | 62.162 | 0.0018541 | 53.303 | 1099.1 | 1045.797
5321 | 0.60081 | 85.22 | 62.162 | 0.0018546 | 53.313 | 1099.1 |  | 5321 | 85.22 | 0.60081 | 62.162 | 0.0018546 | 53.313 | 1099.1 | 1045.787
5322 | 0.60101 | 85.23 | 62.162 | 0.0018552 | 53.323 | 1099.1 |  | 5322 | 85.23 | 0.60101 | 62.162 | 0.0018552 | 53.323 | 1099.1 | 1045.777
5323 | 0.6012 | 85.24 | 62.162 | 0.0018557 | 53.333 | 1099.1 |  | 5323 | 85.24 | 0.6012 | 62.162 | 0.0018557 | 53.333 | 1099.1 | 1045.767
5324 | 0.60139 | 85.25 | 62.161 | 0.0018563 | 53.343 | 1099.1 |  | 5324 | 85.25 | 0.60139 | 62.161 | 0.0018563 | 53.343 | 1099.1 | 1045.757
5325 | 0.60158 | 85.26 | 62.161 | 0.0018569 | 53.353 | 1099.1 |  | 5325 | 85.26 | 0.60158 | 62.161 | 0.0018569 | 53.353 | 1099.1 | 1045.747
5326 | 0.60178 | 85.27 | 62.161 | 0.0018574 | 53.363 | 1099.1 |  | 5326 | 85.27 | 0.60178 | 62.161 | 0.0018574 | 53.363 | 1099.1 | 1045.737
5327 | 0.60197 | 85.28 | 62.161 | 0.001858 | 53.373 | 1099.1 |  | 5327 | 85.28 | 0.60197 | 62.161 | 0.001858 | 53.373 | 1099.1 | 1045.727
5328 | 0.60216 | 85.29 | 62.161 | 0.0018586 | 53.383 | 1099.1 |  | 5328 | 85.29 | 0.60216 | 62.161 | 0.0018586 | 53.383 | 1099.1 | 1045.717
5329 | 0.60235 | 85.3 | 62.161 | 0.0018591 | 53.393 | 1099.1 |  | 5329 | 85.3 | 0.60235 | 62.161 | 0.0018591 | 53.393 | 1099.1 | 1045.707
5330 | 0.60255 | 85.31 | 62.161 | 0.0018597 | 53.403 | 1099.1 |  | 5330 | 85.31 | 0.60255 | 62.161 | 0.0018597 | 53.403 | 1099.1 | 1045.697
5331 | 0.60274 | 85.32 | 62.161 | 0.0018602 | 53.413 | 1099.1 |  | 5331 | 85.32 | 0.60274 | 62.161 | 0.0018602 | 53.413 | 1099.1 | 1045.687
5332 | 0.60293 | 85.33 | 62.161 | 0.0018608 | 53.423 | 1099.1 |  | 5332 | 85.33 | 0.60293 | 62.161 | 0.0018608 | 53.423 | 1099.1 | 1045.677
5333 | 0.60312 | 85.34 | 62.161 | 0.0018614 | 53.433 | 1099.1 |  | 5333 | 85.34 | 0.60312 | 62.161 | 0.0018614 | 53.433 | 1099.1 | 1045.667
5334 | 0.60332 | 85.35 | 62.16 | 0.0018619 | 53.443 | 1099.1 |  | 5334 | 85.35 | 0.60332 | 62.16 | 0.0018619 | 53.443 | 1099.1 | 1045.657
5335 | 0.60351 | 85.36 | 62.16 | 0.0018625 | 53.453 | 1099.1 |  | 5335 | 85.36 | 0.60351 | 62.16 | 0.0018625 | 53.453 | 1099.1 | 1045.647
5336 | 0.6037 | 85.37 | 62.16 | 0.001863 | 53.463 | 1099.2 |  | 5336 | 85.37 | 0.6037 | 62.16 | 0.001863 | 53.463 | 1099.2 | 1045.737
5337 | 0.6039 | 85.38 | 62.16 | 0.0018636 | 53.473 | 1099.2 |  | 5337 | 85.38 | 0.6039 | 62.16 | 0.0018636 | 53.473 | 1099.2 | 1045.727
5338 | 0.60409 | 85.39 | 62.16 | 0.0018642 | 53.483 | 1099.2 |  | 5338 | 85.39 | 0.60409 | 62.16 | 0.0018642 | 53.483 | 1099.2 | 1045.717
5339 | 0.60428 | 85.4 | 62.16 | 0.0018647 | 53.493 | 1099.2 |  | 5339 | 85.4 | 0.60428 | 62.16 | 0.0018647 | 53.493 | 1099.2 | 1045.707
5340 | 0.60448 | 85.41 | 62.16 | 0.0018653 | 53.503 | 1099.2 |  | 5340 | 85.41 | 0.60448 | 62.16 | 0.0018653 | 53.503 | 1099.2 | 1045.697
5341 | 0.60467 | 85.42 | 62.16 | 0.0018659 | 53.513 | 1099.2 |  | 5341 | 85.42 | 0.60467 | 62.16 | 0.0018659 | 53.513 | 1099.2 | 1045.687
5342 | 0.60486 | 85.43 | 62.16 | 0.0018664 | 53.523 | 1099.2 |  | 5342 | 85.43 | 0.60486 | 62.16 | 0.0018664 | 53.523 | 1099.2 | 1045.677
5343 | 0.60506 | 85.44 | 62.159 | 0.001867 | 53.533 | 1099.2 |  | 5343 | 85.44 | 0.60506 | 62.159 | 0.001867 | 53.533 | 1099.2 | 1045.667
5344 | 0.60525 | 85.45 | 62.159 | 0.0018675 | 53.543 | 1099.2 |  | 5344 | 85.45 | 0.60525 | 62.159 | 0.0018675 | 53.543 | 1099.2 | 1045.657
5345 | 0.60544 | 85.46 | 62.159 | 0.0018681 | 53.553 | 1099.2 |  | 5345 | 85.46 | 0.60544 | 62.159 | 0.0018681 | 53.553 | 1099.2 | 1045.647
5346 | 0.60564 | 85.47 | 62.159 | 0.0018687 | 53.563 | 1099.2 |  | 5346 | 85.47 | 0.60564 | 62.159 | 0.0018687 | 53.563 | 1099.2 | 1045.637
5347 | 0.60583 | 85.48 | 62.159 | 0.0018692 | 53.573 | 1099.2 |  | 5347 | 85.48 | 0.60583 | 62.159 | 0.0018692 | 53.573 | 1099.2 | 1045.627
5348 | 0.60602 | 85.49 | 62.159 | 0.0018698 | 53.583 | 1099.2 |  | 5348 | 85.49 | 0.60602 | 62.159 | 0.0018698 | 53.583 | 1099.2 | 1045.617
5349 | 0.60622 | 85.5 | 62.159 | 0.0018704 | 53.592 | 1099.2 |  | 5349 | 85.5 | 0.60622 | 62.159 | 0.0018704 | 53.592 | 1099.2 | 1045.608
5350 | 0.60641 | 85.51 | 62.159 | 0.0018709 | 53.602 | 1099.2 |  | 5350 | 85.51 | 0.60641 | 62.159 | 0.0018709 | 53.602 | 1099.2 | 1045.598
5351 | 0.6066 | 85.52 | 62.159 | 0.0018715 | 53.612 | 1099.2 |  | 5351 | 85.52 | 0.6066 | 62.159 | 0.0018715 | 53.612 | 1099.2 | 1045.588
5352 | 0.6068 | 85.53 | 62.159 | 0.0018721 | 53.622 | 1099.2 |  | 5352 | 85.53 | 0.6068 | 62.159 | 0.0018721 | 53.622 | 1099.2 | 1045.578
5353 | 0.60699 | 85.54 | 62.158 | 0.0018726 | 53.632 | 1099.2 |  | 5353 | 85.54 | 0.60699 | 62.158 | 0.0018726 | 53.632 | 1099.2 | 1045.568
5354 | 0.60719 | 85.55 | 62.158 | 0.0018732 | 53.642 | 1099.2 |  | 5354 | 85.55 | 0.60719 | 62.158 | 0.0018732 | 53.642 | 1099.2 | 1045.558
5355 | 0.60738 | 85.56 | 62.158 | 0.0018738 | 53.652 | 1099.2 |  | 5355 | 85.56 | 0.60738 | 62.158 | 0.0018738 | 53.652 | 1099.2 | 1045.548
5356 | 0.60757 | 85.57 | 62.158 | 0.0018743 | 53.662 | 1099.2 |  | 5356 | 85.57 | 0.60757 | 62.158 | 0.0018743 | 53.662 | 1099.2 | 1045.538
5357 | 0.60777 | 85.58 | 62.158 | 0.0018749 | 53.672 | 1099.2 |  | 5357 | 85.58 | 0.60777 | 62.158 | 0.0018749 | 53.672 | 1099.2 | 1045.528
5358 | 0.60796 | 85.59 | 62.158 | 0.0018755 | 53.682 | 1099.2 |  | 5358 | 85.59 | 0.60796 | 62.158 | 0.0018755 | 53.682 | 1099.2 | 1045.518
5359 | 0.60816 | 85.6 | 62.158 | 0.001876 | 53.692 | 1099.2 |  | 5359 | 85.6 | 0.60816 | 62.158 | 0.001876 | 53.692 | 1099.2 | 1045.508
5360 | 0.60835 | 85.61 | 62.158 | 0.0018766 | 53.702 | 1099.3 |  | 5360 | 85.61 | 0.60835 | 62.158 | 0.0018766 | 53.702 | 1099.3 | 1045.598
5361 | 0.60855 | 85.62 | 62.158 | 0.0018771 | 53.712 | 1099.3 |  | 5361 | 85.62 | 0.60855 | 62.158 | 0.0018771 | 53.712 | 1099.3 | 1045.588
5362 | 0.60874 | 85.63 | 62.158 | 0.0018777 | 53.722 | 1099.3 |  | 5362 | 85.63 | 0.60874 | 62.158 | 0.0018777 | 53.722 | 1099.3 | 1045.578
5363 | 0.60893 | 85.64 | 62.157 | 0.0018783 | 53.732 | 1099.3 |  | 5363 | 85.64 | 0.60893 | 62.157 | 0.0018783 | 53.732 | 1099.3 | 1045.568
5364 | 0.60913 | 85.65 | 62.157 | 0.0018788 | 53.742 | 1099.3 |  | 5364 | 85.65 | 0.60913 | 62.157 | 0.0018788 | 53.742 | 1099.3 | 1045.558
5365 | 0.60932 | 85.66 | 62.157 | 0.0018794 | 53.752 | 1099.3 |  | 5365 | 85.66 | 0.60932 | 62.157 | 0.0018794 | 53.752 | 1099.3 | 1045.548
5366 | 0.60952 | 85.67 | 62.157 | 0.00188 | 53.762 | 1099.3 |  | 5366 | 85.67 | 0.60952 | 62.157 | 0.00188 | 53.762 | 1099.3 | 1045.538
5367 | 0.60971 | 85.68 | 62.157 | 0.0018805 | 53.772 | 1099.3 |  | 5367 | 85.68 | 0.60971 | 62.157 | 0.0018805 | 53.772 | 1099.3 | 1045.528
5368 | 0.60991 | 85.69 | 62.157 | 0.0018811 | 53.782 | 1099.3 |  | 5368 | 85.69 | 0.60991 | 62.157 | 0.0018811 | 53.782 | 1099.3 | 1045.518
5369 | 0.6101 | 85.7 | 62.157 | 0.0018817 | 53.792 | 1099.3 |  | 5369 | 85.7 | 0.6101 | 62.157 | 0.0018817 | 53.792 | 1099.3 | 1045.508
5370 | 0.6103 | 85.71 | 62.157 | 0.0018822 | 53.802 | 1099.3 |  | 5370 | 85.71 | 0.6103 | 62.157 | 0.0018822 | 53.802 | 1099.3 | 1045.498
5371 | 0.61049 | 85.72 | 62.157 | 0.0018828 | 53.812 | 1099.3 |  | 5371 | 85.72 | 0.61049 | 62.157 | 0.0018828 | 53.812 | 1099.3 | 1045.488
5372 | 0.61069 | 85.73 | 62.156 | 0.0018834 | 53.822 | 1099.3 |  | 5372 | 85.73 | 0.61069 | 62.156 | 0.0018834 | 53.822 | 1099.3 | 1045.478
5373 | 0.61088 | 85.74 | 62.156 | 0.001884 | 53.832 | 1099.3 |  | 5373 | 85.74 | 0.61088 | 62.156 | 0.001884 | 53.832 | 1099.3 | 1045.468
5374 | 0.61108 | 85.75 | 62.156 | 0.0018845 | 53.842 | 1099.3 |  | 5374 | 85.75 | 0.61108 | 62.156 | 0.0018845 | 53.842 | 1099.3 | 1045.458
5375 | 0.61127 | 85.76 | 62.156 | 0.0018851 | 53.852 | 1099.3 |  | 5375 | 85.76 | 0.61127 | 62.156 | 0.0018851 | 53.852 | 1099.3 | 1045.448
5376 | 0.61147 | 85.77 | 62.156 | 0.0018857 | 53.862 | 1099.3 |  | 5376 | 85.77 | 0.61147 | 62.156 | 0.0018857 | 53.862 | 1099.3 | 1045.438
5377 | 0.61166 | 85.78 | 62.156 | 0.0018862 | 53.872 | 1099.3 |  | 5377 | 85.78 | 0.61166 | 62.156 | 0.0018862 | 53.872 | 1099.3 | 1045.428
5378 | 0.61186 | 85.79 | 62.156 | 0.0018868 | 53.882 | 1099.3 |  | 5378 | 85.79 | 0.61186 | 62.156 | 0.0018868 | 53.882 | 1099.3 | 1045.418
5379 | 0.61205 | 85.8 | 62.156 | 0.0018874 | 53.892 | 1099.3 |  | 5379 | 85.8 | 0.61205 | 62.156 | 0.0018874 | 53.892 | 1099.3 | 1045.408
5380 | 0.61225 | 85.81 | 62.156 | 0.0018879 | 53.902 | 1099.3 |  | 5380 | 85.81 | 0.61225 | 62.156 | 0.0018879 | 53.902 | 1099.3 | 1045.398
5381 | 0.61244 | 85.82 | 62.156 | 0.0018885 | 53.912 | 1099.3 |  | 5381 | 85.82 | 0.61244 | 62.156 | 0.0018885 | 53.912 | 1099.3 | 1045.388
5382 | 0.61264 | 85.83 | 62.155 | 0.0018891 | 53.922 | 1099.3 |  | 5382 | 85.83 | 0.61264 | 62.155 | 0.0018891 | 53.922 | 1099.3 | 1045.378
5383 | 0.61283 | 85.84 | 62.155 | 0.0018896 | 53.932 | 1099.4 |  | 5383 | 85.84 | 0.61283 | 62.155 | 0.0018896 | 53.932 | 1099.4 | 1045.468
5384 | 0.61303 | 85.85 | 62.155 | 0.0018902 | 53.942 | 1099.4 |  | 5384 | 85.85 | 0.61303 | 62.155 | 0.0018902 | 53.942 | 1099.4 | 1045.458
5385 | 0.61323 | 85.86 | 62.155 | 0.0018908 | 53.952 | 1099.4 |  | 5385 | 85.86 | 0.61323 | 62.155 | 0.0018908 | 53.952 | 1099.4 | 1045.448
5386 | 0.61342 | 85.87 | 62.155 | 0.0018913 | 53.962 | 1099.4 |  | 5386 | 85.87 | 0.61342 | 62.155 | 0.0018913 | 53.962 | 1099.4 | 1045.438
5387 | 0.61362 | 85.88 | 62.155 | 0.0018919 | 53.972 | 1099.4 |  | 5387 | 85.88 | 0.61362 | 62.155 | 0.0018919 | 53.972 | 1099.4 | 1045.428
5388 | 0.61381 | 85.89 | 62.155 | 0.0018925 | 53.982 | 1099.4 |  | 5388 | 85.89 | 0.61381 | 62.155 | 0.0018925 | 53.982 | 1099.4 | 1045.418
5389 | 0.61401 | 85.9 | 62.155 | 0.0018931 | 53.992 | 1099.4 |  | 5389 | 85.9 | 0.61401 | 62.155 | 0.0018931 | 53.992 | 1099.4 | 1045.408
5390 | 0.61421 | 85.91 | 62.155 | 0.0018936 | 54.002 | 1099.4 |  | 5390 | 85.91 | 0.61421 | 62.155 | 0.0018936 | 54.002 | 1099.4 | 1045.398
5391 | 0.6144 | 85.92 | 62.155 | 0.0018942 | 54.012 | 1099.4 |  | 5391 | 85.92 | 0.6144 | 62.155 | 0.0018942 | 54.012 | 1099.4 | 1045.388
5392 | 0.6146 | 85.93 | 62.154 | 0.0018948 | 54.022 | 1099.4 |  | 5392 | 85.93 | 0.6146 | 62.154 | 0.0018948 | 54.022 | 1099.4 | 1045.378
5393 | 0.61479 | 85.94 | 62.154 | 0.0018953 | 54.032 | 1099.4 |  | 5393 | 85.94 | 0.61479 | 62.154 | 0.0018953 | 54.032 | 1099.4 | 1045.368
5394 | 0.61499 | 85.95 | 62.154 | 0.0018959 | 54.042 | 1099.4 |  | 5394 | 85.95 | 0.61499 | 62.154 | 0.0018959 | 54.042 | 1099.4 | 1045.358
5395 | 0.61519 | 85.96 | 62.154 | 0.0018965 | 54.052 | 1099.4 |  | 5395 | 85.96 | 0.61519 | 62.154 | 0.0018965 | 54.052 | 1099.4 | 1045.348
5396 | 0.61538 | 85.97 | 62.154 | 0.001897 | 54.062 | 1099.4 |  | 5396 | 85.97 | 0.61538 | 62.154 | 0.001897 | 54.062 | 1099.4 | 1045.338
5397 | 0.61558 | 85.98 | 62.154 | 0.0018976 | 54.072 | 1099.4 |  | 5397 | 85.98 | 0.61558 | 62.154 | 0.0018976 | 54.072 | 1099.4 | 1045.328
5398 | 0.61577 | 85.99 | 62.154 | 0.0018982 | 54.082 | 1099.4 |  | 5398 | 85.99 | 0.61577 | 62.154 | 0.0018982 | 54.082 | 1099.4 | 1045.318
5399 | 0.61597 | 86 | 62.154 | 0.0018988 | 54.092 | 1099.4 |  | 5399 | 86 | 0.61597 | 62.154 | 0.0018988 | 54.092 | 1099.4 | 1045.308
5400 | 0.61617 | 86.01 | 62.154 | 0.0018993 | 54.102 | 1099.4 |  | 5400 | 86.01 | 0.61617 | 62.154 | 0.0018993 | 54.102 | 1099.4 | 1045.298
5401 | 0.61636 | 86.02 | 62.153 | 0.0018999 | 54.112 | 1099.4 |  | 5401 | 86.02 | 0.61636 | 62.153 | 0.0018999 | 54.112 | 1099.4 | 1045.288
5402 | 0.61656 | 86.03 | 62.153 | 0.0019005 | 54.122 | 1099.4 |  | 5402 | 86.03 | 0.61656 | 62.153 | 0.0019005 | 54.122 | 1099.4 | 1045.278
5403 | 0.61676 | 86.04 | 62.153 | 0.001901 | 54.132 | 1099.4 |  | 5403 | 86.04 | 0.61676 | 62.153 | 0.001901 | 54.132 | 1099.4 | 1045.268
5404 | 0.61695 | 86.05 | 62.153 | 0.0019016 | 54.142 | 1099.4 |  | 5404 | 86.05 | 0.61695 | 62.153 | 0.0019016 | 54.142 | 1099.4 | 1045.258
5405 | 0.61715 | 86.06 | 62.153 | 0.0019022 | 54.152 | 1099.4 |  | 5405 | 86.06 | 0.61715 | 62.153 | 0.0019022 | 54.152 | 1099.4 | 1045.248
5406 | 0.61735 | 86.07 | 62.153 | 0.0019028 | 54.162 | 1099.5 |  | 5406 | 86.07 | 0.61735 | 62.153 | 0.0019028 | 54.162 | 1099.5 | 1045.338
5407 | 0.61754 | 86.08 | 62.153 | 0.0019033 | 54.172 | 1099.5 |  | 5407 | 86.08 | 0.61754 | 62.153 | 0.0019033 | 54.172 | 1099.5 | 1045.328
5408 | 0.61774 | 86.09 | 62.153 | 0.0019039 | 54.182 | 1099.5 |  | 5408 | 86.09 | 0.61774 | 62.153 | 0.0019039 | 54.182 | 1099.5 | 1045.318
5409 | 0.61794 | 86.1 | 62.153 | 0.0019045 | 54.192 | 1099.5 |  | 5409 | 86.1 | 0.61794 | 62.153 | 0.0019045 | 54.192 | 1099.5 | 1045.308
5410 | 0.61814 | 86.11 | 62.153 | 0.0019051 | 54.202 | 1099.5 |  | 5410 | 86.11 | 0.61814 | 62.153 | 0.0019051 | 54.202 | 1099.5 | 1045.298
5411 | 0.61833 | 86.12 | 62.152 | 0.0019056 | 54.212 | 1099.5 |  | 5411 | 86.12 | 0.61833 | 62.152 | 0.0019056 | 54.212 | 1099.5 | 1045.288
5412 | 0.61853 | 86.13 | 62.152 | 0.0019062 | 54.222 | 1099.5 |  | 5412 | 86.13 | 0.61853 | 62.152 | 0.0019062 | 54.222 | 1099.5 | 1045.278
5413 | 0.61873 | 86.14 | 62.152 | 0.0019068 | 54.232 | 1099.5 |  | 5413 | 86.14 | 0.61873 | 62.152 | 0.0019068 | 54.232 | 1099.5 | 1045.268
5414 | 0.61892 | 86.15 | 62.152 | 0.0019073 | 54.242 | 1099.5 |  | 5414 | 86.15 | 0.61892 | 62.152 | 0.0019073 | 54.242 | 1099.5 | 1045.258
5415 | 0.61912 | 86.16 | 62.152 | 0.0019079 | 54.252 | 1099.5 |  | 5415 | 86.16 | 0.61912 | 62.152 | 0.0019079 | 54.252 | 1099.5 | 1045.248
5416 | 0.61932 | 86.17 | 62.152 | 0.0019085 | 54.262 | 1099.5 |  | 5416 | 86.17 | 0.61932 | 62.152 | 0.0019085 | 54.262 | 1099.5 | 1045.238
5417 | 0.61952 | 86.18 | 62.152 | 0.0019091 | 54.272 | 1099.5 |  | 5417 | 86.18 | 0.61952 | 62.152 | 0.0019091 | 54.272 | 1099.5 | 1045.228
5418 | 0.61971 | 86.19 | 62.152 | 0.0019096 | 54.282 | 1099.5 |  | 5418 | 86.19 | 0.61971 | 62.152 | 0.0019096 | 54.282 | 1099.5 | 1045.218
5419 | 0.61991 | 86.2 | 62.152 | 0.0019102 | 54.292 | 1099.5 |  | 5419 | 86.2 | 0.61991 | 62.152 | 0.0019102 | 54.292 | 1099.5 | 1045.208
5420 | 0.62011 | 86.21 | 62.151 | 0.0019108 | 54.302 | 1099.5 |  | 5420 | 86.21 | 0.62011 | 62.151 | 0.0019108 | 54.302 | 1099.5 | 1045.198
5421 | 0.62031 | 86.22 | 62.151 | 0.0019114 | 54.312 | 1099.5 |  | 5421 | 86.22 | 0.62031 | 62.151 | 0.0019114 | 54.312 | 1099.5 | 1045.188
5422 | 0.6205 | 86.23 | 62.151 | 0.0019119 | 54.322 | 1099.5 |  | 5422 | 86.23 | 0.6205 | 62.151 | 0.0019119 | 54.322 | 1099.5 | 1045.178
5423 | 0.6207 | 86.24 | 62.151 | 0.0019125 | 54.332 | 1099.5 |  | 5423 | 86.24 | 0.6207 | 62.151 | 0.0019125 | 54.332 | 1099.5 | 1045.168
5424 | 0.6209 | 86.25 | 62.151 | 0.0019131 | 54.342 | 1099.5 |  | 5424 | 86.25 | 0.6209 | 62.151 | 0.0019131 | 54.342 | 1099.5 | 1045.158
5425 | 0.6211 | 86.26 | 62.151 | 0.0019137 | 54.352 | 1099.5 |  | 5425 | 86.26 | 0.6211 | 62.151 | 0.0019137 | 54.352 | 1099.5 | 1045.148
5426 | 0.62129 | 86.27 | 62.151 | 0.0019142 | 54.362 | 1099.5 |  | 5426 | 86.27 | 0.62129 | 62.151 | 0.0019142 | 54.362 | 1099.5 | 1045.138
5427 | 0.62149 | 86.28 | 62.151 | 0.0019148 | 54.372 | 1099.5 |  | 5427 | 86.28 | 0.62149 | 62.151 | 0.0019148 | 54.372 | 1099.5 | 1045.128
5428 | 0.62169 | 86.29 | 62.151 | 0.0019154 | 54.382 | 1099.5 |  | 5428 | 86.29 | 0.62169 | 62.151 | 0.0019154 | 54.382 | 1099.5 | 1045.118
5429 | 0.62189 | 86.3 | 62.151 | 0.001916 | 54.392 | 1099.6 |  | 5429 | 86.3 | 0.62189 | 62.151 | 0.001916 | 54.392 | 1099.6 | 1045.208
5430 | 0.62209 | 86.31 | 62.15 | 0.0019165 | 54.402 | 1099.6 |  | 5430 | 86.31 | 0.62209 | 62.15 | 0.0019165 | 54.402 | 1099.6 | 1045.198
5431 | 0.62229 | 86.32 | 62.15 | 0.0019171 | 54.412 | 1099.6 |  | 5431 | 86.32 | 0.62229 | 62.15 | 0.0019171 | 54.412 | 1099.6 | 1045.188
5432 | 0.62248 | 86.33 | 62.15 | 0.0019177 | 54.422 | 1099.6 |  | 5432 | 86.33 | 0.62248 | 62.15 | 0.0019177 | 54.422 | 1099.6 | 1045.178
5433 | 0.62268 | 86.34 | 62.15 | 0.0019183 | 54.432 | 1099.6 |  | 5433 | 86.34 | 0.62268 | 62.15 | 0.0019183 | 54.432 | 1099.6 | 1045.168
5434 | 0.62288 | 86.35 | 62.15 | 0.0019189 | 54.442 | 1099.6 |  | 5434 | 86.35 | 0.62288 | 62.15 | 0.0019189 | 54.442 | 1099.6 | 1045.158
5435 | 0.62308 | 86.36 | 62.15 | 0.0019194 | 54.452 | 1099.6 |  | 5435 | 86.36 | 0.62308 | 62.15 | 0.0019194 | 54.452 | 1099.6 | 1045.148
5436 | 0.62328 | 86.37 | 62.15 | 0.00192 | 54.462 | 1099.6 |  | 5436 | 86.37 | 0.62328 | 62.15 | 0.00192 | 54.462 | 1099.6 | 1045.138
5437 | 0.62348 | 86.38 | 62.15 | 0.0019206 | 54.472 | 1099.6 |  | 5437 | 86.38 | 0.62348 | 62.15 | 0.0019206 | 54.472 | 1099.6 | 1045.128
5438 | 0.62367 | 86.39 | 62.15 | 0.0019212 | 54.482 | 1099.6 |  | 5438 | 86.39 | 0.62367 | 62.15 | 0.0019212 | 54.482 | 1099.6 | 1045.118
5439 | 0.62387 | 86.4 | 62.149 | 0.0019217 | 54.492 | 1099.6 |  | 5439 | 86.4 | 0.62387 | 62.149 | 0.0019217 | 54.492 | 1099.6 | 1045.108
5440 | 0.62407 | 86.41 | 62.149 | 0.0019223 | 54.502 | 1099.6 |  | 5440 | 86.41 | 0.62407 | 62.149 | 0.0019223 | 54.502 | 1099.6 | 1045.098
5441 | 0.62427 | 86.42 | 62.149 | 0.0019229 | 54.512 | 1099.6 |  | 5441 | 86.42 | 0.62427 | 62.149 | 0.0019229 | 54.512 | 1099.6 | 1045.088
5442 | 0.62447 | 86.43 | 62.149 | 0.0019235 | 54.522 | 1099.6 |  | 5442 | 86.43 | 0.62447 | 62.149 | 0.0019235 | 54.522 | 1099.6 | 1045.078
5443 | 0.62467 | 86.44 | 62.149 | 0.001924 | 54.532 | 1099.6 |  | 5443 | 86.44 | 0.62467 | 62.149 | 0.001924 | 54.532 | 1099.6 | 1045.068
5444 | 0.62487 | 86.45 | 62.149 | 0.0019246 | 54.542 | 1099.6 |  | 5444 | 86.45 | 0.62487 | 62.149 | 0.0019246 | 54.542 | 1099.6 | 1045.058
5445 | 0.62507 | 86.46 | 62.149 | 0.0019252 | 54.552 | 1099.6 |  | 5445 | 86.46 | 0.62507 | 62.149 | 0.0019252 | 54.552 | 1099.6 | 1045.048
5446 | 0.62526 | 86.47 | 62.149 | 0.0019258 | 54.562 | 1099.6 |  | 5446 | 86.47 | 0.62526 | 62.149 | 0.0019258 | 54.562 | 1099.6 | 1045.038
5447 | 0.62546 | 86.48 | 62.149 | 0.0019264 | 54.572 | 1099.6 |  | 5447 | 86.48 | 0.62546 | 62.149 | 0.0019264 | 54.572 | 1099.6 | 1045.028
5448 | 0.62566 | 86.49 | 62.149 | 0.0019269 | 54.582 | 1099.6 |  | 5448 | 86.49 | 0.62566 | 62.149 | 0.0019269 | 54.582 | 1099.6 | 1045.018
5449 | 0.62586 | 86.5 | 62.148 | 0.0019275 | 54.592 | 1099.6 |  | 5449 | 86.5 | 0.62586 | 62.148 | 0.0019275 | 54.592 | 1099.6 | 1045.008
5450 | 0.62606 | 86.51 | 62.148 | 0.0019281 | 54.602 | 1099.6 |  | 5450 | 86.51 | 0.62606 | 62.148 | 0.0019281 | 54.602 | 1099.6 | 1044.998
5451 | 0.62626 | 86.52 | 62.148 | 0.0019287 | 54.612 | 1099.6 |  | 5451 | 86.52 | 0.62626 | 62.148 | 0.0019287 | 54.612 | 1099.6 | 1044.988
5452 | 0.62646 | 86.53 | 62.148 | 0.0019293 | 54.622 | 1099.7 |  | 5452 | 86.53 | 0.62646 | 62.148 | 0.0019293 | 54.622 | 1099.7 | 1045.078
5453 | 0.62666 | 86.54 | 62.148 | 0.0019298 | 54.632 | 1099.7 |  | 5453 | 86.54 | 0.62666 | 62.148 | 0.0019298 | 54.632 | 1099.7 | 1045.068
5454 | 0.62686 | 86.55 | 62.148 | 0.0019304 | 54.642 | 1099.7 |  | 5454 | 86.55 | 0.62686 | 62.148 | 0.0019304 | 54.642 | 1099.7 | 1045.058
5455 | 0.62706 | 86.56 | 62.148 | 0.001931 | 54.652 | 1099.7 |  | 5455 | 86.56 | 0.62706 | 62.148 | 0.001931 | 54.652 | 1099.7 | 1045.048
5456 | 0.62726 | 86.57 | 62.148 | 0.0019316 | 54.662 | 1099.7 |  | 5456 | 86.57 | 0.62726 | 62.148 | 0.0019316 | 54.662 | 1099.7 | 1045.038
5457 | 0.62746 | 86.58 | 62.148 | 0.0019322 | 54.672 | 1099.7 |  | 5457 | 86.58 | 0.62746 | 62.148 | 0.0019322 | 54.672 | 1099.7 | 1045.028
5458 | 0.62766 | 86.59 | 62.147 | 0.0019327 | 54.682 | 1099.7 |  | 5458 | 86.59 | 0.62766 | 62.147 | 0.0019327 | 54.682 | 1099.7 | 1045.018
5459 | 0.62786 | 86.6 | 62.147 | 0.0019333 | 54.692 | 1099.7 |  | 5459 | 86.6 | 0.62786 | 62.147 | 0.0019333 | 54.692 | 1099.7 | 1045.008
5460 | 0.62806 | 86.61 | 62.147 | 0.0019339 | 54.702 | 1099.7 |  | 5460 | 86.61 | 0.62806 | 62.147 | 0.0019339 | 54.702 | 1099.7 | 1044.998
5461 | 0.62826 | 86.62 | 62.147 | 0.0019345 | 54.712 | 1099.7 |  | 5461 | 86.62 | 0.62826 | 62.147 | 0.0019345 | 54.712 | 1099.7 | 1044.988
5462 | 0.62846 | 86.63 | 62.147 | 0.0019351 | 54.721 | 1099.7 |  | 5462 | 86.63 | 0.62846 | 62.147 | 0.0019351 | 54.721 | 1099.7 | 1044.979
5463 | 0.62866 | 86.64 | 62.147 | 0.0019356 | 54.731 | 1099.7 |  | 5463 | 86.64 | 0.62866 | 62.147 | 0.0019356 | 54.731 | 1099.7 | 1044.969
5464 | 0.62886 | 86.65 | 62.147 | 0.0019362 | 54.741 | 1099.7 |  | 5464 | 86.65 | 0.62886 | 62.147 | 0.0019362 | 54.741 | 1099.7 | 1044.959
5465 | 0.62906 | 86.66 | 62.147 | 0.0019368 | 54.751 | 1099.7 |  | 5465 | 86.66 | 0.62906 | 62.147 | 0.0019368 | 54.751 | 1099.7 | 1044.949
5466 | 0.62926 | 86.67 | 62.147 | 0.0019374 | 54.761 | 1099.7 |  | 5466 | 86.67 | 0.62926 | 62.147 | 0.0019374 | 54.761 | 1099.7 | 1044.939
5467 | 0.62946 | 86.68 | 62.147 | 0.001938 | 54.771 | 1099.7 |  | 5467 | 86.68 | 0.62946 | 62.147 | 0.001938 | 54.771 | 1099.7 | 1044.929
5468 | 0.62966 | 86.69 | 62.146 | 0.0019385 | 54.781 | 1099.7 |  | 5468 | 86.69 | 0.62966 | 62.146 | 0.0019385 | 54.781 | 1099.7 | 1044.919
5469 | 0.62986 | 86.7 | 62.146 | 0.0019391 | 54.791 | 1099.7 |  | 5469 | 86.7 | 0.62986 | 62.146 | 0.0019391 | 54.791 | 1099.7 | 1044.909
5470 | 0.63006 | 86.71 | 62.146 | 0.0019397 | 54.801 | 1099.7 |  | 5470 | 86.71 | 0.63006 | 62.146 | 0.0019397 | 54.801 | 1099.7 | 1044.899
5471 | 0.63026 | 86.72 | 62.146 | 0.0019403 | 54.811 | 1099.7 |  | 5471 | 86.72 | 0.63026 | 62.146 | 0.0019403 | 54.811 | 1099.7 | 1044.889
5472 | 0.63046 | 86.73 | 62.146 | 0.0019409 | 54.821 | 1099.7 |  | 5472 | 86.73 | 0.63046 | 62.146 | 0.0019409 | 54.821 | 1099.7 | 1044.879
5473 | 0.63066 | 86.74 | 62.146 | 0.0019415 | 54.831 | 1099.7 |  | 5473 | 86.74 | 0.63066 | 62.146 | 0.0019415 | 54.831 | 1099.7 | 1044.869
5474 | 0.63086 | 86.75 | 62.146 | 0.001942 | 54.841 | 1099.7 |  | 5474 | 86.75 | 0.63086 | 62.146 | 0.001942 | 54.841 | 1099.7 | 1044.859
5475 | 0.63106 | 86.76 | 62.146 | 0.0019426 | 54.851 | 1099.7 |  | 5475 | 86.76 | 0.63106 | 62.146 | 0.0019426 | 54.851 | 1099.7 | 1044.849
5476 | 0.63126 | 86.77 | 62.146 | 0.0019432 | 54.861 | 1099.8 |  | 5476 | 86.77 | 0.63126 | 62.146 | 0.0019432 | 54.861 | 1099.8 | 1044.939
5477 | 0.63146 | 86.78 | 62.145 | 0.0019438 | 54.871 | 1099.8 |  | 5477 | 86.78 | 0.63146 | 62.145 | 0.0019438 | 54.871 | 1099.8 | 1044.929
5478 | 0.63166 | 86.79 | 62.145 | 0.0019444 | 54.881 | 1099.8 |  | 5478 | 86.79 | 0.63166 | 62.145 | 0.0019444 | 54.881 | 1099.8 | 1044.919
5479 | 0.63186 | 86.8 | 62.145 | 0.001945 | 54.891 | 1099.8 |  | 5479 | 86.8 | 0.63186 | 62.145 | 0.001945 | 54.891 | 1099.8 | 1044.909
5480 | 0.63206 | 86.81 | 62.145 | 0.0019455 | 54.901 | 1099.8 |  | 5480 | 86.81 | 0.63206 | 62.145 | 0.0019455 | 54.901 | 1099.8 | 1044.899
5481 | 0.63226 | 86.82 | 62.145 | 0.0019461 | 54.911 | 1099.8 |  | 5481 | 86.82 | 0.63226 | 62.145 | 0.0019461 | 54.911 | 1099.8 | 1044.889
5482 | 0.63246 | 86.83 | 62.145 | 0.0019467 | 54.921 | 1099.8 |  | 5482 | 86.83 | 0.63246 | 62.145 | 0.0019467 | 54.921 | 1099.8 | 1044.879
5483 | 0.63267 | 86.84 | 62.145 | 0.0019473 | 54.931 | 1099.8 |  | 5483 | 86.84 | 0.63267 | 62.145 | 0.0019473 | 54.931 | 1099.8 | 1044.869
5484 | 0.63287 | 86.85 | 62.145 | 0.0019479 | 54.941 | 1099.8 |  | 5484 | 86.85 | 0.63287 | 62.145 | 0.0019479 | 54.941 | 1099.8 | 1044.859
5485 | 0.63307 | 86.86 | 62.145 | 0.0019485 | 54.951 | 1099.8 |  | 5485 | 86.86 | 0.63307 | 62.145 | 0.0019485 | 54.951 | 1099.8 | 1044.849
5486 | 0.63327 | 86.87 | 62.144 | 0.001949 | 54.961 | 1099.8 |  | 5486 | 86.87 | 0.63327 | 62.144 | 0.001949 | 54.961 | 1099.8 | 1044.839
5487 | 0.63347 | 86.88 | 62.144 | 0.0019496 | 54.971 | 1099.8 |  | 5487 | 86.88 | 0.63347 | 62.144 | 0.0019496 | 54.971 | 1099.8 | 1044.829
5488 | 0.63367 | 86.89 | 62.144 | 0.0019502 | 54.981 | 1099.8 |  | 5488 | 86.89 | 0.63367 | 62.144 | 0.0019502 | 54.981 | 1099.8 | 1044.819
5489 | 0.63387 | 86.9 | 62.144 | 0.0019508 | 54.991 | 1099.8 |  | 5489 | 86.9 | 0.63387 | 62.144 | 0.0019508 | 54.991 | 1099.8 | 1044.809
5490 | 0.63407 | 86.91 | 62.144 | 0.0019514 | 55.001 | 1099.8 |  | 5490 | 86.91 | 0.63407 | 62.144 | 0.0019514 | 55.001 | 1099.8 | 1044.799
5491 | 0.63428 | 86.92 | 62.144 | 0.001952 | 55.011 | 1099.8 |  | 5491 | 86.92 | 0.63428 | 62.144 | 0.001952 | 55.011 | 1099.8 | 1044.789
5492 | 0.63448 | 86.93 | 62.144 | 0.0019526 | 55.021 | 1099.8 |  | 5492 | 86.93 | 0.63448 | 62.144 | 0.0019526 | 55.021 | 1099.8 | 1044.779
5493 | 0.63468 | 86.94 | 62.144 | 0.0019531 | 55.031 | 1099.8 |  | 5493 | 86.94 | 0.63468 | 62.144 | 0.0019531 | 55.031 | 1099.8 | 1044.769
5494 | 0.63488 | 86.95 | 62.144 | 0.0019537 | 55.041 | 1099.8 |  | 5494 | 86.95 | 0.63488 | 62.144 | 0.0019537 | 55.041 | 1099.8 | 1044.759
5495 | 0.63508 | 86.96 | 62.144 | 0.0019543 | 55.051 | 1099.8 |  | 5495 | 86.96 | 0.63508 | 62.144 | 0.0019543 | 55.051 | 1099.8 | 1044.749
5496 | 0.63528 | 86.97 | 62.143 | 0.0019549 | 55.061 | 1099.8 |  | 5496 | 86.97 | 0.63528 | 62.143 | 0.0019549 | 55.061 | 1099.8 | 1044.739
5497 | 0.63549 | 86.98 | 62.143 | 0.0019555 | 55.071 | 1099.8 |  | 5497 | 86.98 | 0.63549 | 62.143 | 0.0019555 | 55.071 | 1099.8 | 1044.729
5498 | 0.63569 | 86.99 | 62.143 | 0.0019561 | 55.081 | 1099.8 |  | 5498 | 86.99 | 0.63569 | 62.143 | 0.0019561 | 55.081 | 1099.8 | 1044.719
5499 | 0.63589 | 87 | 62.143 | 0.0019567 | 55.091 | 1099.9 |  | 5499 | 87 | 0.63589 | 62.143 | 0.0019567 | 55.091 | 1099.9 | 1044.809
5500 | 0.63609 | 87.01 | 62.143 | 0.0019572 | 55.101 | 1099.9 |  | 5500 | 87.01 | 0.63609 | 62.143 | 0.0019572 | 55.101 | 1099.9 | 1044.799
5501 | 0.63629 | 87.02 | 62.143 | 0.0019578 | 55.111 | 1099.9 |  | 5501 | 87.02 | 0.63629 | 62.143 | 0.0019578 | 55.111 | 1099.9 | 1044.789
5502 | 0.6365 | 87.03 | 62.143 | 0.0019584 | 55.121 | 1099.9 |  | 5502 | 87.03 | 0.6365 | 62.143 | 0.0019584 | 55.121 | 1099.9 | 1044.779
5503 | 0.6367 | 87.04 | 62.143 | 0.001959 | 55.131 | 1099.9 |  | 5503 | 87.04 | 0.6367 | 62.143 | 0.001959 | 55.131 | 1099.9 | 1044.769
5504 | 0.6369 | 87.05 | 62.143 | 0.0019596 | 55.141 | 1099.9 |  | 5504 | 87.05 | 0.6369 | 62.143 | 0.0019596 | 55.141 | 1099.9 | 1044.759
5505 | 0.6371 | 87.06 | 62.142 | 0.0019602 | 55.151 | 1099.9 |  | 5505 | 87.06 | 0.6371 | 62.142 | 0.0019602 | 55.151 | 1099.9 | 1044.749
5506 | 0.6373 | 87.07 | 62.142 | 0.0019608 | 55.161 | 1099.9 |  | 5506 | 87.07 | 0.6373 | 62.142 | 0.0019608 | 55.161 | 1099.9 | 1044.739
5507 | 0.63751 | 87.08 | 62.142 | 0.0019613 | 55.171 | 1099.9 |  | 5507 | 87.08 | 0.63751 | 62.142 | 0.0019613 | 55.171 | 1099.9 | 1044.729
5508 | 0.63771 | 87.09 | 62.142 | 0.0019619 | 55.181 | 1099.9 |  | 5508 | 87.09 | 0.63771 | 62.142 | 0.0019619 | 55.181 | 1099.9 | 1044.719
5509 | 0.63791 | 87.1 | 62.142 | 0.0019625 | 55.191 | 1099.9 |  | 5509 | 87.1 | 0.63791 | 62.142 | 0.0019625 | 55.191 | 1099.9 | 1044.709
5510 | 0.63811 | 87.11 | 62.142 | 0.0019631 | 55.201 | 1099.9 |  | 5510 | 87.11 | 0.63811 | 62.142 | 0.0019631 | 55.201 | 1099.9 | 1044.699
5511 | 0.63832 | 87.12 | 62.142 | 0.0019637 | 55.211 | 1099.9 |  | 5511 | 87.12 | 0.63832 | 62.142 | 0.0019637 | 55.211 | 1099.9 | 1044.689
5512 | 0.63852 | 87.13 | 62.142 | 0.0019643 | 55.221 | 1099.9 |  | 5512 | 87.13 | 0.63852 | 62.142 | 0.0019643 | 55.221 | 1099.9 | 1044.679
5513 | 0.63872 | 87.14 | 62.142 | 0.0019649 | 55.231 | 1099.9 |  | 5513 | 87.14 | 0.63872 | 62.142 | 0.0019649 | 55.231 | 1099.9 | 1044.669
5514 | 0.63892 | 87.15 | 62.142 | 0.0019655 | 55.241 | 1099.9 |  | 5514 | 87.15 | 0.63892 | 62.142 | 0.0019655 | 55.241 | 1099.9 | 1044.659
5515 | 0.63913 | 87.16 | 62.141 | 0.0019661 | 55.251 | 1099.9 |  | 5515 | 87.16 | 0.63913 | 62.141 | 0.0019661 | 55.251 | 1099.9 | 1044.649
5516 | 0.63933 | 87.17 | 62.141 | 0.0019666 | 55.261 | 1099.9 |  | 5516 | 87.17 | 0.63933 | 62.141 | 0.0019666 | 55.261 | 1099.9 | 1044.639
5517 | 0.63953 | 87.18 | 62.141 | 0.0019672 | 55.271 | 1099.9 |  | 5517 | 87.18 | 0.63953 | 62.141 | 0.0019672 | 55.271 | 1099.9 | 1044.629
5518 | 0.63974 | 87.19 | 62.141 | 0.0019678 | 55.281 | 1099.9 |  | 5518 | 87.19 | 0.63974 | 62.141 | 0.0019678 | 55.281 | 1099.9 | 1044.619
5519 | 0.63994 | 87.2 | 62.141 | 0.0019684 | 55.291 | 1099.9 |  | 5519 | 87.2 | 0.63994 | 62.141 | 0.0019684 | 55.291 | 1099.9 | 1044.609
5520 | 0.64014 | 87.21 | 62.141 | 0.001969 | 55.301 | 1099.9 |  | 5520 | 87.21 | 0.64014 | 62.141 | 0.001969 | 55.301 | 1099.9 | 1044.599
5521 | 0.64035 | 87.22 | 62.141 | 0.0019696 | 55.311 | 1099.9 |  | 5521 | 87.22 | 0.64035 | 62.141 | 0.0019696 | 55.311 | 1099.9 | 1044.589
5522 | 0.64055 | 87.23 | 62.141 | 0.0019702 | 55.321 | 1100 |  | 5522 | 87.23 | 0.64055 | 62.141 | 0.0019702 | 55.321 | 1100 | 1044.679
5523 | 0.64075 | 87.24 | 62.141 | 0.0019708 | 55.331 | 1100 |  | 5523 | 87.24 | 0.64075 | 62.141 | 0.0019708 | 55.331 | 1100 | 1044.669
5524 | 0.64096 | 87.25 | 62.14 | 0.0019714 | 55.341 | 1100 |  | 5524 | 87.25 | 0.64096 | 62.14 | 0.0019714 | 55.341 | 1100 | 1044.659
5525 | 0.64116 | 87.26 | 62.14 | 0.001972 | 55.351 | 1100 |  | 5525 | 87.26 | 0.64116 | 62.14 | 0.001972 | 55.351 | 1100 | 1044.649
5526 | 0.64136 | 87.27 | 62.14 | 0.0019725 | 55.361 | 1100 |  | 5526 | 87.27 | 0.64136 | 62.14 | 0.0019725 | 55.361 | 1100 | 1044.639
5527 | 0.64157 | 87.28 | 62.14 | 0.0019731 | 55.371 | 1100 |  | 5527 | 87.28 | 0.64157 | 62.14 | 0.0019731 | 55.371 | 1100 | 1044.629
5528 | 0.64177 | 87.29 | 62.14 | 0.0019737 | 55.381 | 1100 |  | 5528 | 87.29 | 0.64177 | 62.14 | 0.0019737 | 55.381 | 1100 | 1044.619
5529 | 0.64197 | 87.3 | 62.14 | 0.0019743 | 55.391 | 1100 |  | 5529 | 87.3 | 0.64197 | 62.14 | 0.0019743 | 55.391 | 1100 | 1044.609
5530 | 0.64218 | 87.31 | 62.14 | 0.0019749 | 55.401 | 1100 |  | 5530 | 87.31 | 0.64218 | 62.14 | 0.0019749 | 55.401 | 1100 | 1044.599
5531 | 0.64238 | 87.32 | 62.14 | 0.0019755 | 55.411 | 1100 |  | 5531 | 87.32 | 0.64238 | 62.14 | 0.0019755 | 55.411 | 1100 | 1044.589
5532 | 0.64258 | 87.33 | 62.14 | 0.0019761 | 55.421 | 1100 |  | 5532 | 87.33 | 0.64258 | 62.14 | 0.0019761 | 55.421 | 1100 | 1044.579
5533 | 0.64279 | 87.34 | 62.139 | 0.0019767 | 55.431 | 1100 |  | 5533 | 87.34 | 0.64279 | 62.139 | 0.0019767 | 55.431 | 1100 | 1044.569
5534 | 0.64299 | 87.35 | 62.139 | 0.0019773 | 55.441 | 1100 |  | 5534 | 87.35 | 0.64299 | 62.139 | 0.0019773 | 55.441 | 1100 | 1044.559
5535 | 0.6432 | 87.36 | 62.139 | 0.0019779 | 55.451 | 1100 |  | 5535 | 87.36 | 0.6432 | 62.139 | 0.0019779 | 55.451 | 1100 | 1044.549
5536 | 0.6434 | 87.37 | 62.139 | 0.0019785 | 55.461 | 1100 |  | 5536 | 87.37 | 0.6434 | 62.139 | 0.0019785 | 55.461 | 1100 | 1044.539
5537 | 0.6436 | 87.38 | 62.139 | 0.001979 | 55.471 | 1100 |  | 5537 | 87.38 | 0.6436 | 62.139 | 0.001979 | 55.471 | 1100 | 1044.529
5538 | 0.64381 | 87.39 | 62.139 | 0.0019796 | 55.481 | 1100 |  | 5538 | 87.39 | 0.64381 | 62.139 | 0.0019796 | 55.481 | 1100 | 1044.519
5539 | 0.64401 | 87.4 | 62.139 | 0.0019802 | 55.491 | 1100 |  | 5539 | 87.4 | 0.64401 | 62.139 | 0.0019802 | 55.491 | 1100 | 1044.509
5540 | 0.64422 | 87.41 | 62.139 | 0.0019808 | 55.501 | 1100 |  | 5540 | 87.41 | 0.64422 | 62.139 | 0.0019808 | 55.501 | 1100 | 1044.499
5541 | 0.64442 | 87.42 | 62.139 | 0.0019814 | 55.511 | 1100 |  | 5541 | 87.42 | 0.64442 | 62.139 | 0.0019814 | 55.511 | 1100 | 1044.489
5542 | 0.64462 | 87.43 | 62.139 | 0.001982 | 55.521 | 1100 |  | 5542 | 87.43 | 0.64462 | 62.139 | 0.001982 | 55.521 | 1100 | 1044.479
5543 | 0.64483 | 87.44 | 62.138 | 0.0019826 | 55.531 | 1100 |  | 5543 | 87.44 | 0.64483 | 62.138 | 0.0019826 | 55.531 | 1100 | 1044.469
5544 | 0.64503 | 87.45 | 62.138 | 0.0019832 | 55.541 | 1100 |  | 5544 | 87.45 | 0.64503 | 62.138 | 0.0019832 | 55.541 | 1100 | 1044.459
5545 | 0.64524 | 87.46 | 62.138 | 0.0019838 | 55.551 | 1100.1 |  | 5545 | 87.46 | 0.64524 | 62.138 | 0.0019838 | 55.551 | 1100.1 | 1044.549
5546 | 0.64544 | 87.47 | 62.138 | 0.0019844 | 55.561 | 1100.1 |  | 5546 | 87.47 | 0.64544 | 62.138 | 0.0019844 | 55.561 | 1100.1 | 1044.539
5547 | 0.64565 | 87.48 | 62.138 | 0.001985 | 55.571 | 1100.1 |  | 5547 | 87.48 | 0.64565 | 62.138 | 0.001985 | 55.571 | 1100.1 | 1044.529
5548 | 0.64585 | 87.49 | 62.138 | 0.0019856 | 55.581 | 1100.1 |  | 5548 | 87.49 | 0.64585 | 62.138 | 0.0019856 | 55.581 | 1100.1 | 1044.519
5549 | 0.64606 | 87.5 | 62.138 | 0.0019862 | 55.591 | 1100.1 |  | 5549 | 87.5 | 0.64606 | 62.138 | 0.0019862 | 55.591 | 1100.1 | 1044.509
5550 | 0.64626 | 87.51 | 62.138 | 0.0019868 | 55.601 | 1100.1 |  | 5550 | 87.51 | 0.64626 | 62.138 | 0.0019868 | 55.601 | 1100.1 | 1044.499
5551 | 0.64647 | 87.52 | 62.138 | 0.0019874 | 55.611 | 1100.1 |  | 5551 | 87.52 | 0.64647 | 62.138 | 0.0019874 | 55.611 | 1100.1 | 1044.489
5552 | 0.64667 | 87.53 | 62.137 | 0.0019879 | 55.621 | 1100.1 |  | 5552 | 87.53 | 0.64667 | 62.137 | 0.0019879 | 55.621 | 1100.1 | 1044.479
5553 | 0.64688 | 87.54 | 62.137 | 0.0019885 | 55.631 | 1100.1 |  | 5553 | 87.54 | 0.64688 | 62.137 | 0.0019885 | 55.631 | 1100.1 | 1044.469
5554 | 0.64708 | 87.55 | 62.137 | 0.0019891 | 55.641 | 1100.1 |  | 5554 | 87.55 | 0.64708 | 62.137 | 0.0019891 | 55.641 | 1100.1 | 1044.459
5555 | 0.64729 | 87.56 | 62.137 | 0.0019897 | 55.651 | 1100.1 |  | 5555 | 87.56 | 0.64729 | 62.137 | 0.0019897 | 55.651 | 1100.1 | 1044.449
5556 | 0.64749 | 87.57 | 62.137 | 0.0019903 | 55.661 | 1100.1 |  | 5556 | 87.57 | 0.64749 | 62.137 | 0.0019903 | 55.661 | 1100.1 | 1044.439
5557 | 0.6477 | 87.58 | 62.137 | 0.0019909 | 55.671 | 1100.1 |  | 5557 | 87.58 | 0.6477 | 62.137 | 0.0019909 | 55.671 | 1100.1 | 1044.429
5558 | 0.6479 | 87.59 | 62.137 | 0.0019915 | 55.681 | 1100.1 |  | 5558 | 87.59 | 0.6479 | 62.137 | 0.0019915 | 55.681 | 1100.1 | 1044.419
5559 | 0.64811 | 87.6 | 62.137 | 0.0019921 | 55.691 | 1100.1 |  | 5559 | 87.6 | 0.64811 | 62.137 | 0.0019921 | 55.691 | 1100.1 | 1044.409
5560 | 0.64831 | 87.61 | 62.137 | 0.0019927 | 55.701 | 1100.1 |  | 5560 | 87.61 | 0.64831 | 62.137 | 0.0019927 | 55.701 | 1100.1 | 1044.399
5561 | 0.64852 | 87.62 | 62.136 | 0.0019933 | 55.711 | 1100.1 |  | 5561 | 87.62 | 0.64852 | 62.136 | 0.0019933 | 55.711 | 1100.1 | 1044.389
5562 | 0.64872 | 87.63 | 62.136 | 0.0019939 | 55.721 | 1100.1 |  | 5562 | 87.63 | 0.64872 | 62.136 | 0.0019939 | 55.721 | 1100.1 | 1044.379
5563 | 0.64893 | 87.64 | 62.136 | 0.0019945 | 55.731 | 1100.1 |  | 5563 | 87.64 | 0.64893 | 62.136 | 0.0019945 | 55.731 | 1100.1 | 1044.369
5564 | 0.64913 | 87.65 | 62.136 | 0.0019951 | 55.741 | 1100.1 |  | 5564 | 87.65 | 0.64913 | 62.136 | 0.0019951 | 55.741 | 1100.1 | 1044.359
5565 | 0.64934 | 87.66 | 62.136 | 0.0019957 | 55.751 | 1100.1 |  | 5565 | 87.66 | 0.64934 | 62.136 | 0.0019957 | 55.751 | 1100.1 | 1044.349
5566 | 0.64955 | 87.67 | 62.136 | 0.0019963 | 55.761 | 1100.1 |  | 5566 | 87.67 | 0.64955 | 62.136 | 0.0019963 | 55.761 | 1100.1 | 1044.339
5567 | 0.64975 | 87.68 | 62.136 | 0.0019969 | 55.771 | 1100.1 |  | 5567 | 87.68 | 0.64975 | 62.136 | 0.0019969 | 55.771 | 1100.1 | 1044.329
5568 | 0.64996 | 87.69 | 62.136 | 0.0019975 | 55.781 | 1100.2 |  | 5568 | 87.69 | 0.64996 | 62.136 | 0.0019975 | 55.781 | 1100.2 | 1044.419
5569 | 0.65016 | 87.7 | 62.136 | 0.0019981 | 55.791 | 1100.2 |  | 5569 | 87.7 | 0.65016 | 62.136 | 0.0019981 | 55.791 | 1100.2 | 1044.409
5570 | 0.65037 | 87.71 | 62.136 | 0.0019987 | 55.801 | 1100.2 |  | 5570 | 87.71 | 0.65037 | 62.136 | 0.0019987 | 55.801 | 1100.2 | 1044.399
5571 | 0.65057 | 87.72 | 62.135 | 0.0019993 | 55.81 | 1100.2 |  | 5571 | 87.72 | 0.65057 | 62.135 | 0.0019993 | 55.81 | 1100.2 | 1044.39
5572 | 0.65078 | 87.73 | 62.135 | 0.0019999 | 55.82 | 1100.2 |  | 5572 | 87.73 | 0.65078 | 62.135 | 0.0019999 | 55.82 | 1100.2 | 1044.38
5573 | 0.65099 | 87.74 | 62.135 | 0.0020005 | 55.83 | 1100.2 |  | 5573 | 87.74 | 0.65099 | 62.135 | 0.0020005 | 55.83 | 1100.2 | 1044.37
5574 | 0.65119 | 87.75 | 62.135 | 0.0020011 | 55.84 | 1100.2 |  | 5574 | 87.75 | 0.65119 | 62.135 | 0.0020011 | 55.84 | 1100.2 | 1044.36
5575 | 0.6514 | 87.76 | 62.135 | 0.0020017 | 55.85 | 1100.2 |  | 5575 | 87.76 | 0.6514 | 62.135 | 0.0020017 | 55.85 | 1100.2 | 1044.35
5576 | 0.65161 | 87.77 | 62.135 | 0.0020023 | 55.86 | 1100.2 |  | 5576 | 87.77 | 0.65161 | 62.135 | 0.0020023 | 55.86 | 1100.2 | 1044.34
5577 | 0.65181 | 87.78 | 62.135 | 0.0020029 | 55.87 | 1100.2 |  | 5577 | 87.78 | 0.65181 | 62.135 | 0.0020029 | 55.87 | 1100.2 | 1044.33
5578 | 0.65202 | 87.79 | 62.135 | 0.0020035 | 55.88 | 1100.2 |  | 5578 | 87.79 | 0.65202 | 62.135 | 0.0020035 | 55.88 | 1100.2 | 1044.32
5579 | 0.65222 | 87.8 | 62.135 | 0.0020041 | 55.89 | 1100.2 |  | 5579 | 87.8 | 0.65222 | 62.135 | 0.0020041 | 55.89 | 1100.2 | 1044.31
5580 | 0.65243 | 87.81 | 62.134 | 0.0020046 | 55.9 | 1100.2 |  | 5580 | 87.81 | 0.65243 | 62.134 | 0.0020046 | 55.9 | 1100.2 | 1044.3
5581 | 0.65264 | 87.82 | 62.134 | 0.0020052 | 55.91 | 1100.2 |  | 5581 | 87.82 | 0.65264 | 62.134 | 0.0020052 | 55.91 | 1100.2 | 1044.29
5582 | 0.65284 | 87.83 | 62.134 | 0.0020058 | 55.92 | 1100.2 |  | 5582 | 87.83 | 0.65284 | 62.134 | 0.0020058 | 55.92 | 1100.2 | 1044.28
5583 | 0.65305 | 87.84 | 62.134 | 0.0020064 | 55.93 | 1100.2 |  | 5583 | 87.84 | 0.65305 | 62.134 | 0.0020064 | 55.93 | 1100.2 | 1044.27
5584 | 0.65326 | 87.85 | 62.134 | 0.002007 | 55.94 | 1100.2 |  | 5584 | 87.85 | 0.65326 | 62.134 | 0.002007 | 55.94 | 1100.2 | 1044.26
5585 | 0.65346 | 87.86 | 62.134 | 0.0020076 | 55.95 | 1100.2 |  | 5585 | 87.86 | 0.65346 | 62.134 | 0.0020076 | 55.95 | 1100.2 | 1044.25
5586 | 0.65367 | 87.87 | 62.134 | 0.0020082 | 55.96 | 1100.2 |  | 5586 | 87.87 | 0.65367 | 62.134 | 0.0020082 | 55.96 | 1100.2 | 1044.24
5587 | 0.65388 | 87.88 | 62.134 | 0.0020088 | 55.97 | 1100.2 |  | 5587 | 87.88 | 0.65388 | 62.134 | 0.0020088 | 55.97 | 1100.2 | 1044.23
5588 | 0.65409 | 87.89 | 62.134 | 0.0020094 | 55.98 | 1100.2 |  | 5588 | 87.89 | 0.65409 | 62.134 | 0.0020094 | 55.98 | 1100.2 | 1044.22
5589 | 0.65429 | 87.9 | 62.133 | 0.00201 | 55.99 | 1100.2 |  | 5589 | 87.9 | 0.65429 | 62.133 | 0.00201 | 55.99 | 1100.2 | 1044.21
5590 | 0.6545 | 87.91 | 62.133 | 0.0020106 | 56 | 1100.2 |  | 5590 | 87.91 | 0.6545 | 62.133 | 0.0020106 | 56 | 1100.2 | 1044.2
5591 | 0.65471 | 87.92 | 62.133 | 0.0020112 | 56.01 | 1100.2 |  | 5591 | 87.92 | 0.65471 | 62.133 | 0.0020112 | 56.01 | 1100.2 | 1044.19
5592 | 0.65491 | 87.93 | 62.133 | 0.0020118 | 56.02 | 1100.3 |  | 5592 | 87.93 | 0.65491 | 62.133 | 0.0020118 | 56.02 | 1100.3 | 1044.28
5593 | 0.65512 | 87.94 | 62.133 | 0.0020124 | 56.03 | 1100.3 |  | 5593 | 87.94 | 0.65512 | 62.133 | 0.0020124 | 56.03 | 1100.3 | 1044.27
5594 | 0.65533 | 87.95 | 62.133 | 0.002013 | 56.04 | 1100.3 |  | 5594 | 87.95 | 0.65533 | 62.133 | 0.002013 | 56.04 | 1100.3 | 1044.26
5595 | 0.65554 | 87.96 | 62.133 | 0.0020136 | 56.05 | 1100.3 |  | 5595 | 87.96 | 0.65554 | 62.133 | 0.0020136 | 56.05 | 1100.3 | 1044.25
5596 | 0.65574 | 87.97 | 62.133 | 0.0020142 | 56.06 | 1100.3 |  | 5596 | 87.97 | 0.65574 | 62.133 | 0.0020142 | 56.06 | 1100.3 | 1044.24
5597 | 0.65595 | 87.98 | 62.133 | 0.0020148 | 56.07 | 1100.3 |  | 5597 | 87.98 | 0.65595 | 62.133 | 0.0020148 | 56.07 | 1100.3 | 1044.23
5598 | 0.65616 | 87.99 | 62.132 | 0.0020155 | 56.08 | 1100.3 |  | 5598 | 87.99 | 0.65616 | 62.132 | 0.0020155 | 56.08 | 1100.3 | 1044.22
5599 | 0.65637 | 88 | 62.132 | 0.0020161 | 56.09 | 1100.3 |  | 5599 | 88 | 0.65637 | 62.132 | 0.0020161 | 56.09 | 1100.3 | 1044.21
5600 | 0.65657 | 88.01 | 62.132 | 0.0020167 | 56.1 | 1100.3 |  | 5600 | 88.01 | 0.65657 | 62.132 | 0.0020167 | 56.1 | 1100.3 | 1044.2
5601 | 0.65678 | 88.02 | 62.132 | 0.0020173 | 56.11 | 1100.3 |  | 5601 | 88.02 | 0.65678 | 62.132 | 0.0020173 | 56.11 | 1100.3 | 1044.19
5602 | 0.65699 | 88.03 | 62.132 | 0.0020179 | 56.12 | 1100.3 |  | 5602 | 88.03 | 0.65699 | 62.132 | 0.0020179 | 56.12 | 1100.3 | 1044.18
5603 | 0.6572 | 88.04 | 62.132 | 0.0020185 | 56.13 | 1100.3 |  | 5603 | 88.04 | 0.6572 | 62.132 | 0.0020185 | 56.13 | 1100.3 | 1044.17
5604 | 0.6574 | 88.05 | 62.132 | 0.0020191 | 56.14 | 1100.3 |  | 5604 | 88.05 | 0.6574 | 62.132 | 0.0020191 | 56.14 | 1100.3 | 1044.16
5605 | 0.65761 | 88.06 | 62.132 | 0.0020197 | 56.15 | 1100.3 |  | 5605 | 88.06 | 0.65761 | 62.132 | 0.0020197 | 56.15 | 1100.3 | 1044.15
5606 | 0.65782 | 88.07 | 62.132 | 0.0020203 | 56.16 | 1100.3 |  | 5606 | 88.07 | 0.65782 | 62.132 | 0.0020203 | 56.16 | 1100.3 | 1044.14
5607 | 0.65803 | 88.08 | 62.132 | 0.0020209 | 56.17 | 1100.3 |  | 5607 | 88.08 | 0.65803 | 62.132 | 0.0020209 | 56.17 | 1100.3 | 1044.13
5608 | 0.65824 | 88.09 | 62.131 | 0.0020215 | 56.18 | 1100.3 |  | 5608 | 88.09 | 0.65824 | 62.131 | 0.0020215 | 56.18 | 1100.3 | 1044.12
5609 | 0.65844 | 88.1 | 62.131 | 0.0020221 | 56.19 | 1100.3 |  | 5609 | 88.1 | 0.65844 | 62.131 | 0.0020221 | 56.19 | 1100.3 | 1044.11
5610 | 0.65865 | 88.11 | 62.131 | 0.0020227 | 56.2 | 1100.3 |  | 5610 | 88.11 | 0.65865 | 62.131 | 0.0020227 | 56.2 | 1100.3 | 1044.1
5611 | 0.65886 | 88.12 | 62.131 | 0.0020233 | 56.21 | 1100.3 |  | 5611 | 88.12 | 0.65886 | 62.131 | 0.0020233 | 56.21 | 1100.3 | 1044.09
5612 | 0.65907 | 88.13 | 62.131 | 0.0020239 | 56.22 | 1100.3 |  | 5612 | 88.13 | 0.65907 | 62.131 | 0.0020239 | 56.22 | 1100.3 | 1044.08
5613 | 0.65928 | 88.14 | 62.131 | 0.0020245 | 56.23 | 1100.3 |  | 5613 | 88.14 | 0.65928 | 62.131 | 0.0020245 | 56.23 | 1100.3 | 1044.07
5614 | 0.65949 | 88.15 | 62.131 | 0.0020251 | 56.24 | 1100.3 |  | 5614 | 88.15 | 0.65949 | 62.131 | 0.0020251 | 56.24 | 1100.3 | 1044.06
5615 | 0.65969 | 88.16 | 62.131 | 0.0020257 | 56.25 | 1100.4 |  | 5615 | 88.16 | 0.65969 | 62.131 | 0.0020257 | 56.25 | 1100.4 | 1044.15
5616 | 0.6599 | 88.17 | 62.131 | 0.0020263 | 56.26 | 1100.4 |  | 5616 | 88.17 | 0.6599 | 62.131 | 0.0020263 | 56.26 | 1100.4 | 1044.14
5617 | 0.66011 | 88.18 | 62.13 | 0.0020269 | 56.27 | 1100.4 |  | 5617 | 88.18 | 0.66011 | 62.13 | 0.0020269 | 56.27 | 1100.4 | 1044.13
5618 | 0.66032 | 88.19 | 62.13 | 0.0020275 | 56.28 | 1100.4 |  | 5618 | 88.19 | 0.66032 | 62.13 | 0.0020275 | 56.28 | 1100.4 | 1044.12
5619 | 0.66053 | 88.2 | 62.13 | 0.0020281 | 56.29 | 1100.4 |  | 5619 | 88.2 | 0.66053 | 62.13 | 0.0020281 | 56.29 | 1100.4 | 1044.11
5620 | 0.66074 | 88.21 | 62.13 | 0.0020287 | 56.3 | 1100.4 |  | 5620 | 88.21 | 0.66074 | 62.13 | 0.0020287 | 56.3 | 1100.4 | 1044.1
5621 | 0.66095 | 88.22 | 62.13 | 0.0020293 | 56.31 | 1100.4 |  | 5621 | 88.22 | 0.66095 | 62.13 | 0.0020293 | 56.31 | 1100.4 | 1044.09
5622 | 0.66115 | 88.23 | 62.13 | 0.0020299 | 56.32 | 1100.4 |  | 5622 | 88.23 | 0.66115 | 62.13 | 0.0020299 | 56.32 | 1100.4 | 1044.08
5623 | 0.66136 | 88.24 | 62.13 | 0.0020305 | 56.33 | 1100.4 |  | 5623 | 88.24 | 0.66136 | 62.13 | 0.0020305 | 56.33 | 1100.4 | 1044.07
5624 | 0.66157 | 88.25 | 62.13 | 0.0020311 | 56.34 | 1100.4 |  | 5624 | 88.25 | 0.66157 | 62.13 | 0.0020311 | 56.34 | 1100.4 | 1044.06
5625 | 0.66178 | 88.26 | 62.13 | 0.0020317 | 56.35 | 1100.4 |  | 5625 | 88.26 | 0.66178 | 62.13 | 0.0020317 | 56.35 | 1100.4 | 1044.05
5626 | 0.66199 | 88.27 | 62.129 | 0.0020324 | 56.36 | 1100.4 |  | 5626 | 88.27 | 0.66199 | 62.129 | 0.0020324 | 56.36 | 1100.4 | 1044.04
5627 | 0.6622 | 88.28 | 62.129 | 0.002033 | 56.37 | 1100.4 |  | 5627 | 88.28 | 0.6622 | 62.129 | 0.002033 | 56.37 | 1100.4 | 1044.03
5628 | 0.66241 | 88.29 | 62.129 | 0.0020336 | 56.38 | 1100.4 |  | 5628 | 88.29 | 0.66241 | 62.129 | 0.0020336 | 56.38 | 1100.4 | 1044.02
5629 | 0.66262 | 88.3 | 62.129 | 0.0020342 | 56.39 | 1100.4 |  | 5629 | 88.3 | 0.66262 | 62.129 | 0.0020342 | 56.39 | 1100.4 | 1044.01
5630 | 0.66283 | 88.31 | 62.129 | 0.0020348 | 56.4 | 1100.4 |  | 5630 | 88.31 | 0.66283 | 62.129 | 0.0020348 | 56.4 | 1100.4 | 1044
5631 | 0.66304 | 88.32 | 62.129 | 0.0020354 | 56.41 | 1100.4 |  | 5631 | 88.32 | 0.66304 | 62.129 | 0.0020354 | 56.41 | 1100.4 | 1043.99
5632 | 0.66325 | 88.33 | 62.129 | 0.002036 | 56.42 | 1100.4 |  | 5632 | 88.33 | 0.66325 | 62.129 | 0.002036 | 56.42 | 1100.4 | 1043.98
5633 | 0.66346 | 88.34 | 62.129 | 0.0020366 | 56.43 | 1100.4 |  | 5633 | 88.34 | 0.66346 | 62.129 | 0.0020366 | 56.43 | 1100.4 | 1043.97
5634 | 0.66367 | 88.35 | 62.129 | 0.0020372 | 56.44 | 1100.4 |  | 5634 | 88.35 | 0.66367 | 62.129 | 0.0020372 | 56.44 | 1100.4 | 1043.96
5635 | 0.66388 | 88.36 | 62.128 | 0.0020378 | 56.45 | 1100.4 |  | 5635 | 88.36 | 0.66388 | 62.128 | 0.0020378 | 56.45 | 1100.4 | 1043.95
5636 | 0.66408 | 88.37 | 62.128 | 0.0020384 | 56.46 | 1100.4 |  | 5636 | 88.37 | 0.66408 | 62.128 | 0.0020384 | 56.46 | 1100.4 | 1043.94
5637 | 0.66429 | 88.38 | 62.128 | 0.002039 | 56.47 | 1100.4 |  | 5637 | 88.38 | 0.66429 | 62.128 | 0.002039 | 56.47 | 1100.4 | 1043.93
5638 | 0.6645 | 88.39 | 62.128 | 0.0020396 | 56.48 | 1100.5 |  | 5638 | 88.39 | 0.6645 | 62.128 | 0.0020396 | 56.48 | 1100.5 | 1044.02
5639 | 0.66471 | 88.4 | 62.128 | 0.0020402 | 56.49 | 1100.5 |  | 5639 | 88.4 | 0.66471 | 62.128 | 0.0020402 | 56.49 | 1100.5 | 1044.01
5640 | 0.66492 | 88.41 | 62.128 | 0.0020408 | 56.5 | 1100.5 |  | 5640 | 88.41 | 0.66492 | 62.128 | 0.0020408 | 56.5 | 1100.5 | 1044
5641 | 0.66513 | 88.42 | 62.128 | 0.0020415 | 56.51 | 1100.5 |  | 5641 | 88.42 | 0.66513 | 62.128 | 0.0020415 | 56.51 | 1100.5 | 1043.99
5642 | 0.66534 | 88.43 | 62.128 | 0.0020421 | 56.52 | 1100.5 |  | 5642 | 88.43 | 0.66534 | 62.128 | 0.0020421 | 56.52 | 1100.5 | 1043.98
5643 | 0.66555 | 88.44 | 62.128 | 0.0020427 | 56.53 | 1100.5 |  | 5643 | 88.44 | 0.66555 | 62.128 | 0.0020427 | 56.53 | 1100.5 | 1043.97
5644 | 0.66576 | 88.45 | 62.128 | 0.0020433 | 56.54 | 1100.5 |  | 5644 | 88.45 | 0.66576 | 62.128 | 0.0020433 | 56.54 | 1100.5 | 1043.96
5645 | 0.66597 | 88.46 | 62.127 | 0.0020439 | 56.55 | 1100.5 |  | 5645 | 88.46 | 0.66597 | 62.127 | 0.0020439 | 56.55 | 1100.5 | 1043.95
5646 | 0.66618 | 88.47 | 62.127 | 0.0020445 | 56.56 | 1100.5 |  | 5646 | 88.47 | 0.66618 | 62.127 | 0.0020445 | 56.56 | 1100.5 | 1043.94
5647 | 0.6664 | 88.48 | 62.127 | 0.0020451 | 56.57 | 1100.5 |  | 5647 | 88.48 | 0.6664 | 62.127 | 0.0020451 | 56.57 | 1100.5 | 1043.93
5648 | 0.66661 | 88.49 | 62.127 | 0.0020457 | 56.58 | 1100.5 |  | 5648 | 88.49 | 0.66661 | 62.127 | 0.0020457 | 56.58 | 1100.5 | 1043.92
5649 | 0.66682 | 88.5 | 62.127 | 0.0020463 | 56.59 | 1100.5 |  | 5649 | 88.5 | 0.66682 | 62.127 | 0.0020463 | 56.59 | 1100.5 | 1043.91
5650 | 0.66703 | 88.51 | 62.127 | 0.0020469 | 56.6 | 1100.5 |  | 5650 | 88.51 | 0.66703 | 62.127 | 0.0020469 | 56.6 | 1100.5 | 1043.9
5651 | 0.66724 | 88.52 | 62.127 | 0.0020475 | 56.61 | 1100.5 |  | 5651 | 88.52 | 0.66724 | 62.127 | 0.0020475 | 56.61 | 1100.5 | 1043.89
5652 | 0.66745 | 88.53 | 62.127 | 0.0020482 | 56.62 | 1100.5 |  | 5652 | 88.53 | 0.66745 | 62.127 | 0.0020482 | 56.62 | 1100.5 | 1043.88
5653 | 0.66766 | 88.54 | 62.127 | 0.0020488 | 56.63 | 1100.5 |  | 5653 | 88.54 | 0.66766 | 62.127 | 0.0020488 | 56.63 | 1100.5 | 1043.87
5654 | 0.66787 | 88.55 | 62.126 | 0.0020494 | 56.64 | 1100.5 |  | 5654 | 88.55 | 0.66787 | 62.126 | 0.0020494 | 56.64 | 1100.5 | 1043.86
5655 | 0.66808 | 88.56 | 62.126 | 0.00205 | 56.65 | 1100.5 |  | 5655 | 88.56 | 0.66808 | 62.126 | 0.00205 | 56.65 | 1100.5 | 1043.85
5656 | 0.66829 | 88.57 | 62.126 | 0.0020506 | 56.66 | 1100.5 |  | 5656 | 88.57 | 0.66829 | 62.126 | 0.0020506 | 56.66 | 1100.5 | 1043.84
5657 | 0.6685 | 88.58 | 62.126 | 0.0020512 | 56.67 | 1100.5 |  | 5657 | 88.58 | 0.6685 | 62.126 | 0.0020512 | 56.67 | 1100.5 | 1043.83
5658 | 0.66871 | 88.59 | 62.126 | 0.0020518 | 56.68 | 1100.5 |  | 5658 | 88.59 | 0.66871 | 62.126 | 0.0020518 | 56.68 | 1100.5 | 1043.82
5659 | 0.66892 | 88.6 | 62.126 | 0.0020524 | 56.69 | 1100.5 |  | 5659 | 88.6 | 0.66892 | 62.126 | 0.0020524 | 56.69 | 1100.5 | 1043.81
5660 | 0.66913 | 88.61 | 62.126 | 0.002053 | 56.7 | 1100.5 |  | 5660 | 88.61 | 0.66913 | 62.126 | 0.002053 | 56.7 | 1100.5 | 1043.8
5661 | 0.66935 | 88.62 | 62.126 | 0.0020537 | 56.71 | 1100.6 |  | 5661 | 88.62 | 0.66935 | 62.126 | 0.0020537 | 56.71 | 1100.6 | 1043.89
5662 | 0.66956 | 88.63 | 62.126 | 0.0020543 | 56.72 | 1100.6 |  | 5662 | 88.63 | 0.66956 | 62.126 | 0.0020543 | 56.72 | 1100.6 | 1043.88
5663 | 0.66977 | 88.64 | 62.125 | 0.0020549 | 56.73 | 1100.6 |  | 5663 | 88.64 | 0.66977 | 62.125 | 0.0020549 | 56.73 | 1100.6 | 1043.87
5664 | 0.66998 | 88.65 | 62.125 | 0.0020555 | 56.74 | 1100.6 |  | 5664 | 88.65 | 0.66998 | 62.125 | 0.0020555 | 56.74 | 1100.6 | 1043.86
5665 | 0.67019 | 88.66 | 62.125 | 0.0020561 | 56.75 | 1100.6 |  | 5665 | 88.66 | 0.67019 | 62.125 | 0.0020561 | 56.75 | 1100.6 | 1043.85
5666 | 0.6704 | 88.67 | 62.125 | 0.0020567 | 56.76 | 1100.6 |  | 5666 | 88.67 | 0.6704 | 62.125 | 0.0020567 | 56.76 | 1100.6 | 1043.84
5667 | 0.67061 | 88.68 | 62.125 | 0.0020573 | 56.77 | 1100.6 |  | 5667 | 88.68 | 0.67061 | 62.125 | 0.0020573 | 56.77 | 1100.6 | 1043.83
5668 | 0.67082 | 88.69 | 62.125 | 0.0020579 | 56.78 | 1100.6 |  | 5668 | 88.69 | 0.67082 | 62.125 | 0.0020579 | 56.78 | 1100.6 | 1043.82
5669 | 0.67104 | 88.7 | 62.125 | 0.0020585 | 56.79 | 1100.6 |  | 5669 | 88.7 | 0.67104 | 62.125 | 0.0020585 | 56.79 | 1100.6 | 1043.81
5670 | 0.67125 | 88.71 | 62.125 | 0.0020592 | 56.8 | 1100.6 |  | 5670 | 88.71 | 0.67125 | 62.125 | 0.0020592 | 56.8 | 1100.6 | 1043.8
5671 | 0.67146 | 88.72 | 62.125 | 0.0020598 | 56.81 | 1100.6 |  | 5671 | 88.72 | 0.67146 | 62.125 | 0.0020598 | 56.81 | 1100.6 | 1043.79
5672 | 0.67167 | 88.73 | 62.124 | 0.0020604 | 56.82 | 1100.6 |  | 5672 | 88.73 | 0.67167 | 62.124 | 0.0020604 | 56.82 | 1100.6 | 1043.78
5673 | 0.67188 | 88.74 | 62.124 | 0.002061 | 56.83 | 1100.6 |  | 5673 | 88.74 | 0.67188 | 62.124 | 0.002061 | 56.83 | 1100.6 | 1043.77
5674 | 0.6721 | 88.75 | 62.124 | 0.0020616 | 56.84 | 1100.6 |  | 5674 | 88.75 | 0.6721 | 62.124 | 0.0020616 | 56.84 | 1100.6 | 1043.76
5675 | 0.67231 | 88.76 | 62.124 | 0.0020622 | 56.85 | 1100.6 |  | 5675 | 88.76 | 0.67231 | 62.124 | 0.0020622 | 56.85 | 1100.6 | 1043.75
5676 | 0.67252 | 88.77 | 62.124 | 0.0020628 | 56.86 | 1100.6 |  | 5676 | 88.77 | 0.67252 | 62.124 | 0.0020628 | 56.86 | 1100.6 | 1043.74
5677 | 0.67273 | 88.78 | 62.124 | 0.0020635 | 56.87 | 1100.6 |  | 5677 | 88.78 | 0.67273 | 62.124 | 0.0020635 | 56.87 | 1100.6 | 1043.73
5678 | 0.67294 | 88.79 | 62.124 | 0.0020641 | 56.88 | 1100.6 |  | 5678 | 88.79 | 0.67294 | 62.124 | 0.0020641 | 56.88 | 1100.6 | 1043.72
5679 | 0.67316 | 88.8 | 62.124 | 0.0020647 | 56.889 | 1100.6 |  | 5679 | 88.8 | 0.67316 | 62.124 | 0.0020647 | 56.889 | 1100.6 | 1043.711
5680 | 0.67337 | 88.81 | 62.124 | 0.0020653 | 56.899 | 1100.6 |  | 5680 | 88.81 | 0.67337 | 62.124 | 0.0020653 | 56.899 | 1100.6 | 1043.701
5681 | 0.67358 | 88.82 | 62.123 | 0.0020659 | 56.909 | 1100.6 |  | 5681 | 88.82 | 0.67358 | 62.123 | 0.0020659 | 56.909 | 1100.6 | 1043.691
5682 | 0.67379 | 88.83 | 62.123 | 0.0020665 | 56.919 | 1100.6 |  | 5682 | 88.83 | 0.67379 | 62.123 | 0.0020665 | 56.919 | 1100.6 | 1043.681
5683 | 0.674 | 88.84 | 62.123 | 0.0020671 | 56.929 | 1100.6 |  | 5683 | 88.84 | 0.674 | 62.123 | 0.0020671 | 56.929 | 1100.6 | 1043.671
5684 | 0.67422 | 88.85 | 62.123 | 0.0020678 | 56.939 | 1100.7 |  | 5684 | 88.85 | 0.67422 | 62.123 | 0.0020678 | 56.939 | 1100.7 | 1043.761
5685 | 0.67443 | 88.86 | 62.123 | 0.0020684 | 56.949 | 1100.7 |  | 5685 | 88.86 | 0.67443 | 62.123 | 0.0020684 | 56.949 | 1100.7 | 1043.751
5686 | 0.67464 | 88.87 | 62.123 | 0.002069 | 56.959 | 1100.7 |  | 5686 | 88.87 | 0.67464 | 62.123 | 0.002069 | 56.959 | 1100.7 | 1043.741
5687 | 0.67485 | 88.88 | 62.123 | 0.0020696 | 56.969 | 1100.7 |  | 5687 | 88.88 | 0.67485 | 62.123 | 0.0020696 | 56.969 | 1100.7 | 1043.731
5688 | 0.67507 | 88.89 | 62.123 | 0.0020702 | 56.979 | 1100.7 |  | 5688 | 88.89 | 0.67507 | 62.123 | 0.0020702 | 56.979 | 1100.7 | 1043.721
5689 | 0.67528 | 88.9 | 62.123 | 0.0020708 | 56.989 | 1100.7 |  | 5689 | 88.9 | 0.67528 | 62.123 | 0.0020708 | 56.989 | 1100.7 | 1043.711
5690 | 0.67549 | 88.91 | 62.122 | 0.0020714 | 56.999 | 1100.7 |  | 5690 | 88.91 | 0.67549 | 62.122 | 0.0020714 | 56.999 | 1100.7 | 1043.701
5691 | 0.67571 | 88.92 | 62.122 | 0.0020721 | 57.009 | 1100.7 |  | 5691 | 88.92 | 0.67571 | 62.122 | 0.0020721 | 57.009 | 1100.7 | 1043.691
5692 | 0.67592 | 88.93 | 62.122 | 0.0020727 | 57.019 | 1100.7 |  | 5692 | 88.93 | 0.67592 | 62.122 | 0.0020727 | 57.019 | 1100.7 | 1043.681
5693 | 0.67613 | 88.94 | 62.122 | 0.0020733 | 57.029 | 1100.7 |  | 5693 | 88.94 | 0.67613 | 62.122 | 0.0020733 | 57.029 | 1100.7 | 1043.671
5694 | 0.67634 | 88.95 | 62.122 | 0.0020739 | 57.039 | 1100.7 |  | 5694 | 88.95 | 0.67634 | 62.122 | 0.0020739 | 57.039 | 1100.7 | 1043.661
5695 | 0.67656 | 88.96 | 62.122 | 0.0020745 | 57.049 | 1100.7 |  | 5695 | 88.96 | 0.67656 | 62.122 | 0.0020745 | 57.049 | 1100.7 | 1043.651
5696 | 0.67677 | 88.97 | 62.122 | 0.0020751 | 57.059 | 1100.7 |  | 5696 | 88.97 | 0.67677 | 62.122 | 0.0020751 | 57.059 | 1100.7 | 1043.641
5697 | 0.67698 | 88.98 | 62.122 | 0.0020758 | 57.069 | 1100.7 |  | 5697 | 88.98 | 0.67698 | 62.122 | 0.0020758 | 57.069 | 1100.7 | 1043.631
5698 | 0.6772 | 88.99 | 62.122 | 0.0020764 | 57.079 | 1100.7 |  | 5698 | 88.99 | 0.6772 | 62.122 | 0.0020764 | 57.079 | 1100.7 | 1043.621
5699 | 0.67741 | 89 | 62.122 | 0.002077 | 57.089 | 1100.7 |  | 5699 | 89 | 0.67741 | 62.122 | 0.002077 | 57.089 | 1100.7 | 1043.611
5700 | 0.67762 | 89.01 | 62.121 | 0.0020776 | 57.099 | 1100.7 |  | 5700 | 89.01 | 0.67762 | 62.121 | 0.0020776 | 57.099 | 1100.7 | 1043.601
5701 | 0.67784 | 89.02 | 62.121 | 0.0020782 | 57.109 | 1100.7 |  | 5701 | 89.02 | 0.67784 | 62.121 | 0.0020782 | 57.109 | 1100.7 | 1043.591
5702 | 0.67805 | 89.03 | 62.121 | 0.0020788 | 57.119 | 1100.7 |  | 5702 | 89.03 | 0.67805 | 62.121 | 0.0020788 | 57.119 | 1100.7 | 1043.581
5703 | 0.67826 | 89.04 | 62.121 | 0.0020795 | 57.129 | 1100.7 |  | 5703 | 89.04 | 0.67826 | 62.121 | 0.0020795 | 57.129 | 1100.7 | 1043.571
5704 | 0.67848 | 89.05 | 62.121 | 0.0020801 | 57.139 | 1100.7 |  | 5704 | 89.05 | 0.67848 | 62.121 | 0.0020801 | 57.139 | 1100.7 | 1043.561
5705 | 0.67869 | 89.06 | 62.121 | 0.0020807 | 57.149 | 1100.7 |  | 5705 | 89.06 | 0.67869 | 62.121 | 0.0020807 | 57.149 | 1100.7 | 1043.551
5706 | 0.67891 | 89.07 | 62.121 | 0.0020813 | 57.159 | 1100.7 |  | 5706 | 89.07 | 0.67891 | 62.121 | 0.0020813 | 57.159 | 1100.7 | 1043.541
5707 | 0.67912 | 89.08 | 62.121 | 0.0020819 | 57.169 | 1100.7 |  | 5707 | 89.08 | 0.67912 | 62.121 | 0.0020819 | 57.169 | 1100.7 | 1043.531
5708 | 0.67933 | 89.09 | 62.121 | 0.0020826 | 57.179 | 1100.8 |  | 5708 | 89.09 | 0.67933 | 62.121 | 0.0020826 | 57.179 | 1100.8 | 1043.621
5709 | 0.67955 | 89.1 | 62.12 | 0.0020832 | 57.189 | 1100.8 |  | 5709 | 89.1 | 0.67955 | 62.12 | 0.0020832 | 57.189 | 1100.8 | 1043.611
5710 | 0.67976 | 89.11 | 62.12 | 0.0020838 | 57.199 | 1100.8 |  | 5710 | 89.11 | 0.67976 | 62.12 | 0.0020838 | 57.199 | 1100.8 | 1043.601
5711 | 0.67998 | 89.12 | 62.12 | 0.0020844 | 57.209 | 1100.8 |  | 5711 | 89.12 | 0.67998 | 62.12 | 0.0020844 | 57.209 | 1100.8 | 1043.591
5712 | 0.68019 | 89.13 | 62.12 | 0.002085 | 57.219 | 1100.8 |  | 5712 | 89.13 | 0.68019 | 62.12 | 0.002085 | 57.219 | 1100.8 | 1043.581
5713 | 0.6804 | 89.14 | 62.12 | 0.0020856 | 57.229 | 1100.8 |  | 5713 | 89.14 | 0.6804 | 62.12 | 0.0020856 | 57.229 | 1100.8 | 1043.571
5714 | 0.68062 | 89.15 | 62.12 | 0.0020863 | 57.239 | 1100.8 |  | 5714 | 89.15 | 0.68062 | 62.12 | 0.0020863 | 57.239 | 1100.8 | 1043.561
5715 | 0.68083 | 89.16 | 62.12 | 0.0020869 | 57.249 | 1100.8 |  | 5715 | 89.16 | 0.68083 | 62.12 | 0.0020869 | 57.249 | 1100.8 | 1043.551
5716 | 0.68105 | 89.17 | 62.12 | 0.0020875 | 57.259 | 1100.8 |  | 5716 | 89.17 | 0.68105 | 62.12 | 0.0020875 | 57.259 | 1100.8 | 1043.541
5717 | 0.68126 | 89.18 | 62.12 | 0.0020881 | 57.269 | 1100.8 |  | 5717 | 89.18 | 0.68126 | 62.12 | 0.0020881 | 57.269 | 1100.8 | 1043.531
5718 | 0.68148 | 89.19 | 62.119 | 0.0020887 | 57.279 | 1100.8 |  | 5718 | 89.19 | 0.68148 | 62.119 | 0.0020887 | 57.279 | 1100.8 | 1043.521
5719 | 0.68169 | 89.2 | 62.119 | 0.0020894 | 57.289 | 1100.8 |  | 5719 | 89.2 | 0.68169 | 62.119 | 0.0020894 | 57.289 | 1100.8 | 1043.511
5720 | 0.6819 | 89.21 | 62.119 | 0.00209 | 57.299 | 1100.8 |  | 5720 | 89.21 | 0.6819 | 62.119 | 0.00209 | 57.299 | 1100.8 | 1043.501
5721 | 0.68212 | 89.22 | 62.119 | 0.0020906 | 57.309 | 1100.8 |  | 5721 | 89.22 | 0.68212 | 62.119 | 0.0020906 | 57.309 | 1100.8 | 1043.491
5722 | 0.68233 | 89.23 | 62.119 | 0.0020912 | 57.319 | 1100.8 |  | 5722 | 89.23 | 0.68233 | 62.119 | 0.0020912 | 57.319 | 1100.8 | 1043.481
5723 | 0.68255 | 89.24 | 62.119 | 0.0020918 | 57.329 | 1100.8 |  | 5723 | 89.24 | 0.68255 | 62.119 | 0.0020918 | 57.329 | 1100.8 | 1043.471
5724 | 0.68276 | 89.25 | 62.119 | 0.0020925 | 57.339 | 1100.8 |  | 5724 | 89.25 | 0.68276 | 62.119 | 0.0020925 | 57.339 | 1100.8 | 1043.461
5725 | 0.68298 | 89.26 | 62.119 | 0.0020931 | 57.349 | 1100.8 |  | 5725 | 89.26 | 0.68298 | 62.119 | 0.0020931 | 57.349 | 1100.8 | 1043.451
5726 | 0.68319 | 89.27 | 62.119 | 0.0020937 | 57.359 | 1100.8 |  | 5726 | 89.27 | 0.68319 | 62.119 | 0.0020937 | 57.359 | 1100.8 | 1043.441
5727 | 0.68341 | 89.28 | 62.118 | 0.0020943 | 57.369 | 1100.8 |  | 5727 | 89.28 | 0.68341 | 62.118 | 0.0020943 | 57.369 | 1100.8 | 1043.431
5728 | 0.68362 | 89.29 | 62.118 | 0.002095 | 57.379 | 1100.8 |  | 5728 | 89.29 | 0.68362 | 62.118 | 0.002095 | 57.379 | 1100.8 | 1043.421
5729 | 0.68384 | 89.3 | 62.118 | 0.0020956 | 57.389 | 1100.8 |  | 5729 | 89.3 | 0.68384 | 62.118 | 0.0020956 | 57.389 | 1100.8 | 1043.411
5730 | 0.68405 | 89.31 | 62.118 | 0.0020962 | 57.399 | 1100.8 |  | 5730 | 89.31 | 0.68405 | 62.118 | 0.0020962 | 57.399 | 1100.8 | 1043.401
5731 | 0.68427 | 89.32 | 62.118 | 0.0020968 | 57.409 | 1100.9 |  | 5731 | 89.32 | 0.68427 | 62.118 | 0.0020968 | 57.409 | 1100.9 | 1043.491
5732 | 0.68448 | 89.33 | 62.118 | 0.0020974 | 57.419 | 1100.9 |  | 5732 | 89.33 | 0.68448 | 62.118 | 0.0020974 | 57.419 | 1100.9 | 1043.481
5733 | 0.6847 | 89.34 | 62.118 | 0.0020981 | 57.429 | 1100.9 |  | 5733 | 89.34 | 0.6847 | 62.118 | 0.0020981 | 57.429 | 1100.9 | 1043.471
5734 | 0.68491 | 89.35 | 62.118 | 0.0020987 | 57.439 | 1100.9 |  | 5734 | 89.35 | 0.68491 | 62.118 | 0.0020987 | 57.439 | 1100.9 | 1043.461
5735 | 0.68513 | 89.36 | 62.118 | 0.0020993 | 57.449 | 1100.9 |  | 5735 | 89.36 | 0.68513 | 62.118 | 0.0020993 | 57.449 | 1100.9 | 1043.451
5736 | 0.68535 | 89.37 | 62.117 | 0.0020999 | 57.459 | 1100.9 |  | 5736 | 89.37 | 0.68535 | 62.117 | 0.0020999 | 57.459 | 1100.9 | 1043.441
5737 | 0.68556 | 89.38 | 62.117 | 0.0021006 | 57.469 | 1100.9 |  | 5737 | 89.38 | 0.68556 | 62.117 | 0.0021006 | 57.469 | 1100.9 | 1043.431
5738 | 0.68578 | 89.39 | 62.117 | 0.0021012 | 57.479 | 1100.9 |  | 5738 | 89.39 | 0.68578 | 62.117 | 0.0021012 | 57.479 | 1100.9 | 1043.421
5739 | 0.68599 | 89.4 | 62.117 | 0.0021018 | 57.489 | 1100.9 |  | 5739 | 89.4 | 0.68599 | 62.117 | 0.0021018 | 57.489 | 1100.9 | 1043.411
5740 | 0.68621 | 89.41 | 62.117 | 0.0021024 | 57.499 | 1100.9 |  | 5740 | 89.41 | 0.68621 | 62.117 | 0.0021024 | 57.499 | 1100.9 | 1043.401
5741 | 0.68642 | 89.42 | 62.117 | 0.0021031 | 57.509 | 1100.9 |  | 5741 | 89.42 | 0.68642 | 62.117 | 0.0021031 | 57.509 | 1100.9 | 1043.391
5742 | 0.68664 | 89.43 | 62.117 | 0.0021037 | 57.519 | 1100.9 |  | 5742 | 89.43 | 0.68664 | 62.117 | 0.0021037 | 57.519 | 1100.9 | 1043.381
5743 | 0.68686 | 89.44 | 62.117 | 0.0021043 | 57.529 | 1100.9 |  | 5743 | 89.44 | 0.68686 | 62.117 | 0.0021043 | 57.529 | 1100.9 | 1043.371
5744 | 0.68707 | 89.45 | 62.117 | 0.0021049 | 57.539 | 1100.9 |  | 5744 | 89.45 | 0.68707 | 62.117 | 0.0021049 | 57.539 | 1100.9 | 1043.361
5745 | 0.68729 | 89.46 | 62.116 | 0.0021055 | 57.549 | 1100.9 |  | 5745 | 89.46 | 0.68729 | 62.116 | 0.0021055 | 57.549 | 1100.9 | 1043.351
5746 | 0.6875 | 89.47 | 62.116 | 0.0021062 | 57.559 | 1100.9 |  | 5746 | 89.47 | 0.6875 | 62.116 | 0.0021062 | 57.559 | 1100.9 | 1043.341
5747 | 0.68772 | 89.48 | 62.116 | 0.0021068 | 57.569 | 1100.9 |  | 5747 | 89.48 | 0.68772 | 62.116 | 0.0021068 | 57.569 | 1100.9 | 1043.331
5748 | 0.68794 | 89.49 | 62.116 | 0.0021074 | 57.579 | 1100.9 |  | 5748 | 89.49 | 0.68794 | 62.116 | 0.0021074 | 57.579 | 1100.9 | 1043.321
5749 | 0.68815 | 89.5 | 62.116 | 0.002108 | 57.589 | 1100.9 |  | 5749 | 89.5 | 0.68815 | 62.116 | 0.002108 | 57.589 | 1100.9 | 1043.311
5750 | 0.68837 | 89.51 | 62.116 | 0.0021087 | 57.599 | 1100.9 |  | 5750 | 89.51 | 0.68837 | 62.116 | 0.0021087 | 57.599 | 1100.9 | 1043.301
5751 | 0.68858 | 89.52 | 62.116 | 0.0021093 | 57.609 | 1100.9 |  | 5751 | 89.52 | 0.68858 | 62.116 | 0.0021093 | 57.609 | 1100.9 | 1043.291
5752 | 0.6888 | 89.53 | 62.116 | 0.0021099 | 57.619 | 1100.9 |  | 5752 | 89.53 | 0.6888 | 62.116 | 0.0021099 | 57.619 | 1100.9 | 1043.281
5753 | 0.68902 | 89.54 | 62.116 | 0.0021105 | 57.629 | 1100.9 |  | 5753 | 89.54 | 0.68902 | 62.116 | 0.0021105 | 57.629 | 1100.9 | 1043.271
5754 | 0.68923 | 89.55 | 62.115 | 0.0021112 | 57.639 | 1101 |  | 5754 | 89.55 | 0.68923 | 62.115 | 0.0021112 | 57.639 | 1101 | 1043.361
5755 | 0.68945 | 89.56 | 62.115 | 0.0021118 | 57.649 | 1101 |  | 5755 | 89.56 | 0.68945 | 62.115 | 0.0021118 | 57.649 | 1101 | 1043.351
5756 | 0.68967 | 89.57 | 62.115 | 0.0021124 | 57.659 | 1101 |  | 5756 | 89.57 | 0.68967 | 62.115 | 0.0021124 | 57.659 | 1101 | 1043.341
5757 | 0.68988 | 89.58 | 62.115 | 0.0021131 | 57.669 | 1101 |  | 5757 | 89.58 | 0.68988 | 62.115 | 0.0021131 | 57.669 | 1101 | 1043.331
5758 | 0.6901 | 89.59 | 62.115 | 0.0021137 | 57.679 | 1101 |  | 5758 | 89.59 | 0.6901 | 62.115 | 0.0021137 | 57.679 | 1101 | 1043.321
5759 | 0.69032 | 89.6 | 62.115 | 0.0021143 | 57.689 | 1101 |  | 5759 | 89.6 | 0.69032 | 62.115 | 0.0021143 | 57.689 | 1101 | 1043.311
5760 | 0.69053 | 89.61 | 62.115 | 0.0021149 | 57.699 | 1101 |  | 5760 | 89.61 | 0.69053 | 62.115 | 0.0021149 | 57.699 | 1101 | 1043.301
5761 | 0.69075 | 89.62 | 62.115 | 0.0021156 | 57.709 | 1101 |  | 5761 | 89.62 | 0.69075 | 62.115 | 0.0021156 | 57.709 | 1101 | 1043.291
5762 | 0.69097 | 89.63 | 62.115 | 0.0021162 | 57.719 | 1101 |  | 5762 | 89.63 | 0.69097 | 62.115 | 0.0021162 | 57.719 | 1101 | 1043.281
5763 | 0.69119 | 89.64 | 62.114 | 0.0021168 | 57.729 | 1101 |  | 5763 | 89.64 | 0.69119 | 62.114 | 0.0021168 | 57.729 | 1101 | 1043.271
5764 | 0.6914 | 89.65 | 62.114 | 0.0021174 | 57.739 | 1101 |  | 5764 | 89.65 | 0.6914 | 62.114 | 0.0021174 | 57.739 | 1101 | 1043.261
5765 | 0.69162 | 89.66 | 62.114 | 0.0021181 | 57.749 | 1101 |  | 5765 | 89.66 | 0.69162 | 62.114 | 0.0021181 | 57.749 | 1101 | 1043.251
5766 | 0.69184 | 89.67 | 62.114 | 0.0021187 | 57.759 | 1101 |  | 5766 | 89.67 | 0.69184 | 62.114 | 0.0021187 | 57.759 | 1101 | 1043.241
5767 | 0.69205 | 89.68 | 62.114 | 0.0021193 | 57.769 | 1101 |  | 5767 | 89.68 | 0.69205 | 62.114 | 0.0021193 | 57.769 | 1101 | 1043.231
5768 | 0.69227 | 89.69 | 62.114 | 0.00212 | 57.779 | 1101 |  | 5768 | 89.69 | 0.69227 | 62.114 | 0.00212 | 57.779 | 1101 | 1043.221
5769 | 0.69249 | 89.7 | 62.114 | 0.0021206 | 57.789 | 1101 |  | 5769 | 89.7 | 0.69249 | 62.114 | 0.0021206 | 57.789 | 1101 | 1043.211
5770 | 0.69271 | 89.71 | 62.114 | 0.0021212 | 57.799 | 1101 |  | 5770 | 89.71 | 0.69271 | 62.114 | 0.0021212 | 57.799 | 1101 | 1043.201
5771 | 0.69292 | 89.72 | 62.114 | 0.0021218 | 57.809 | 1101 |  | 5771 | 89.72 | 0.69292 | 62.114 | 0.0021218 | 57.809 | 1101 | 1043.191
5772 | 0.69314 | 89.73 | 62.113 | 0.0021225 | 57.819 | 1101 |  | 5772 | 89.73 | 0.69314 | 62.113 | 0.0021225 | 57.819 | 1101 | 1043.181
5773 | 0.69336 | 89.74 | 62.113 | 0.0021231 | 57.829 | 1101 |  | 5773 | 89.74 | 0.69336 | 62.113 | 0.0021231 | 57.829 | 1101 | 1043.171
5774 | 0.69358 | 89.75 | 62.113 | 0.0021237 | 57.839 | 1101 |  | 5774 | 89.75 | 0.69358 | 62.113 | 0.0021237 | 57.839 | 1101 | 1043.161
5775 | 0.6938 | 89.76 | 62.113 | 0.0021244 | 57.849 | 1101 |  | 5775 | 89.76 | 0.6938 | 62.113 | 0.0021244 | 57.849 | 1101 | 1043.151
5776 | 0.69401 | 89.77 | 62.113 | 0.002125 | 57.859 | 1101 |  | 5776 | 89.77 | 0.69401 | 62.113 | 0.002125 | 57.859 | 1101 | 1043.141
5777 | 0.69423 | 89.78 | 62.113 | 0.0021256 | 57.869 | 1101.1 |  | 5777 | 89.78 | 0.69423 | 62.113 | 0.0021256 | 57.869 | 1101.1 | 1043.231
5778 | 0.69445 | 89.79 | 62.113 | 0.0021262 | 57.879 | 1101.1 |  | 5778 | 89.79 | 0.69445 | 62.113 | 0.0021262 | 57.879 | 1101.1 | 1043.221
5779 | 0.69467 | 89.8 | 62.113 | 0.0021269 | 57.889 | 1101.1 |  | 5779 | 89.8 | 0.69467 | 62.113 | 0.0021269 | 57.889 | 1101.1 | 1043.211
5780 | 0.69489 | 89.81 | 62.113 | 0.0021275 | 57.899 | 1101.1 |  | 5780 | 89.81 | 0.69489 | 62.113 | 0.0021275 | 57.899 | 1101.1 | 1043.201
5781 | 0.6951 | 89.82 | 62.112 | 0.0021281 | 57.909 | 1101.1 |  | 5781 | 89.82 | 0.6951 | 62.112 | 0.0021281 | 57.909 | 1101.1 | 1043.191
5782 | 0.69532 | 89.83 | 62.112 | 0.0021288 | 57.919 | 1101.1 |  | 5782 | 89.83 | 0.69532 | 62.112 | 0.0021288 | 57.919 | 1101.1 | 1043.181
5783 | 0.69554 | 89.84 | 62.112 | 0.0021294 | 57.929 | 1101.1 |  | 5783 | 89.84 | 0.69554 | 62.112 | 0.0021294 | 57.929 | 1101.1 | 1043.171
5784 | 0.69576 | 89.85 | 62.112 | 0.00213 | 57.938 | 1101.1 |  | 5784 | 89.85 | 0.69576 | 62.112 | 0.00213 | 57.938 | 1101.1 | 1043.162
5785 | 0.69598 | 89.86 | 62.112 | 0.0021307 | 57.948 | 1101.1 |  | 5785 | 89.86 | 0.69598 | 62.112 | 0.0021307 | 57.948 | 1101.1 | 1043.152
5786 | 0.6962 | 89.87 | 62.112 | 0.0021313 | 57.958 | 1101.1 |  | 5786 | 89.87 | 0.6962 | 62.112 | 0.0021313 | 57.958 | 1101.1 | 1043.142
5787 | 0.69641 | 89.88 | 62.112 | 0.0021319 | 57.968 | 1101.1 |  | 5787 | 89.88 | 0.69641 | 62.112 | 0.0021319 | 57.968 | 1101.1 | 1043.132
5788 | 0.69663 | 89.89 | 62.112 | 0.0021325 | 57.978 | 1101.1 |  | 5788 | 89.89 | 0.69663 | 62.112 | 0.0021325 | 57.978 | 1101.1 | 1043.122
5789 | 0.69685 | 89.9 | 62.112 | 0.0021332 | 57.988 | 1101.1 |  | 5789 | 89.9 | 0.69685 | 62.112 | 0.0021332 | 57.988 | 1101.1 | 1043.112
5790 | 0.69707 | 89.91 | 62.111 | 0.0021338 | 57.998 | 1101.1 |  | 5790 | 89.91 | 0.69707 | 62.111 | 0.0021338 | 57.998 | 1101.1 | 1043.102
5791 | 0.69729 | 89.92 | 62.111 | 0.0021344 | 58.008 | 1101.1 |  | 5791 | 89.92 | 0.69729 | 62.111 | 0.0021344 | 58.008 | 1101.1 | 1043.092
5792 | 0.69751 | 89.93 | 62.111 | 0.0021351 | 58.018 | 1101.1 |  | 5792 | 89.93 | 0.69751 | 62.111 | 0.0021351 | 58.018 | 1101.1 | 1043.082
5793 | 0.69773 | 89.94 | 62.111 | 0.0021357 | 58.028 | 1101.1 |  | 5793 | 89.94 | 0.69773 | 62.111 | 0.0021357 | 58.028 | 1101.1 | 1043.072
5794 | 0.69794 | 89.95 | 62.111 | 0.0021363 | 58.038 | 1101.1 |  | 5794 | 89.95 | 0.69794 | 62.111 | 0.0021363 | 58.038 | 1101.1 | 1043.062
5795 | 0.69816 | 89.96 | 62.111 | 0.002137 | 58.048 | 1101.1 |  | 5795 | 89.96 | 0.69816 | 62.111 | 0.002137 | 58.048 | 1101.1 | 1043.052
5796 | 0.69838 | 89.97 | 62.111 | 0.0021376 | 58.058 | 1101.1 |  | 5796 | 89.97 | 0.69838 | 62.111 | 0.0021376 | 58.058 | 1101.1 | 1043.042
5797 | 0.6986 | 89.98 | 62.111 | 0.0021382 | 58.068 | 1101.1 |  | 5797 | 89.98 | 0.6986 | 62.111 | 0.0021382 | 58.068 | 1101.1 | 1043.032
5798 | 0.69882 | 89.99 | 62.111 | 0.0021389 | 58.078 | 1101.1 |  | 5798 | 89.99 | 0.69882 | 62.111 | 0.0021389 | 58.078 | 1101.1 | 1043.022
5799 | 0.69904 | 90 | 62.11 | 0.0021395 | 58.088 | 1101.1 |  | 5799 | 90 | 0.69904 | 62.11 | 0.0021395 | 58.088 | 1101.1 | 1043.012
5800 | 0.69926 | 90.01 | 62.11 | 0.0021401 | 58.098 | 1101.1 |  | 5800 | 90.01 | 0.69926 | 62.11 | 0.0021401 | 58.098 | 1101.1 | 1043.002
5801 | 0.69948 | 90.02 | 62.11 | 0.0021408 | 58.108 | 1101.2 |  | 5801 | 90.02 | 0.69948 | 62.11 | 0.0021408 | 58.108 | 1101.2 | 1043.092
5802 | 0.6997 | 90.03 | 62.11 | 0.0021414 | 58.118 | 1101.2 |  | 5802 | 90.03 | 0.6997 | 62.11 | 0.0021414 | 58.118 | 1101.2 | 1043.082
5803 | 0.69992 | 90.04 | 62.11 | 0.002142 | 58.128 | 1101.2 |  | 5803 | 90.04 | 0.69992 | 62.11 | 0.002142 | 58.128 | 1101.2 | 1043.072
5804 | 0.70014 | 90.05 | 62.11 | 0.0021427 | 58.138 | 1101.2 |  | 5804 | 90.05 | 0.70014 | 62.11 | 0.0021427 | 58.138 | 1101.2 | 1043.062
5805 | 0.70036 | 90.06 | 62.11 | 0.0021433 | 58.148 | 1101.2 |  | 5805 | 90.06 | 0.70036 | 62.11 | 0.0021433 | 58.148 | 1101.2 | 1043.052
5806 | 0.70058 | 90.07 | 62.11 | 0.0021439 | 58.158 | 1101.2 |  | 5806 | 90.07 | 0.70058 | 62.11 | 0.0021439 | 58.158 | 1101.2 | 1043.042
5807 | 0.7008 | 90.08 | 62.11 | 0.0021446 | 58.168 | 1101.2 |  | 5807 | 90.08 | 0.7008 | 62.11 | 0.0021446 | 58.168 | 1101.2 | 1043.032
5808 | 0.70102 | 90.09 | 62.109 | 0.0021452 | 58.178 | 1101.2 |  | 5808 | 90.09 | 0.70102 | 62.109 | 0.0021452 | 58.178 | 1101.2 | 1043.022
5809 | 0.70124 | 90.1 | 62.109 | 0.0021458 | 58.188 | 1101.2 |  | 5809 | 90.1 | 0.70124 | 62.109 | 0.0021458 | 58.188 | 1101.2 | 1043.012
5810 | 0.70146 | 90.11 | 62.109 | 0.0021465 | 58.198 | 1101.2 |  | 5810 | 90.11 | 0.70146 | 62.109 | 0.0021465 | 58.198 | 1101.2 | 1043.002
5811 | 0.70168 | 90.12 | 62.109 | 0.0021471 | 58.208 | 1101.2 |  | 5811 | 90.12 | 0.70168 | 62.109 | 0.0021471 | 58.208 | 1101.2 | 1042.992
5812 | 0.7019 | 90.13 | 62.109 | 0.0021477 | 58.218 | 1101.2 |  | 5812 | 90.13 | 0.7019 | 62.109 | 0.0021477 | 58.218 | 1101.2 | 1042.982
5813 | 0.70212 | 90.14 | 62.109 | 0.0021484 | 58.228 | 1101.2 |  | 5813 | 90.14 | 0.70212 | 62.109 | 0.0021484 | 58.228 | 1101.2 | 1042.972
5814 | 0.70234 | 90.15 | 62.109 | 0.002149 | 58.238 | 1101.2 |  | 5814 | 90.15 | 0.70234 | 62.109 | 0.002149 | 58.238 | 1101.2 | 1042.962
5815 | 0.70256 | 90.16 | 62.109 | 0.0021496 | 58.248 | 1101.2 |  | 5815 | 90.16 | 0.70256 | 62.109 | 0.0021496 | 58.248 | 1101.2 | 1042.952
5816 | 0.70278 | 90.17 | 62.109 | 0.0021503 | 58.258 | 1101.2 |  | 5816 | 90.17 | 0.70278 | 62.109 | 0.0021503 | 58.258 | 1101.2 | 1042.942
5817 | 0.703 | 90.18 | 62.108 | 0.0021509 | 58.268 | 1101.2 |  | 5817 | 90.18 | 0.703 | 62.108 | 0.0021509 | 58.268 | 1101.2 | 1042.932
5818 | 0.70322 | 90.19 | 62.108 | 0.0021516 | 58.278 | 1101.2 |  | 5818 | 90.19 | 0.70322 | 62.108 | 0.0021516 | 58.278 | 1101.2 | 1042.922
5819 | 0.70344 | 90.2 | 62.108 | 0.0021522 | 58.288 | 1101.2 |  | 5819 | 90.2 | 0.70344 | 62.108 | 0.0021522 | 58.288 | 1101.2 | 1042.912
5820 | 0.70366 | 90.21 | 62.108 | 0.0021528 | 58.298 | 1101.2 |  | 5820 | 90.21 | 0.70366 | 62.108 | 0.0021528 | 58.298 | 1101.2 | 1042.902
5821 | 0.70388 | 90.22 | 62.108 | 0.0021535 | 58.308 | 1101.2 |  | 5821 | 90.22 | 0.70388 | 62.108 | 0.0021535 | 58.308 | 1101.2 | 1042.892
5822 | 0.7041 | 90.23 | 62.108 | 0.0021541 | 58.318 | 1101.2 |  | 5822 | 90.23 | 0.7041 | 62.108 | 0.0021541 | 58.318 | 1101.2 | 1042.882
5823 | 0.70432 | 90.24 | 62.108 | 0.0021547 | 58.328 | 1101.2 |  | 5823 | 90.24 | 0.70432 | 62.108 | 0.0021547 | 58.328 | 1101.2 | 1042.872
5824 | 0.70454 | 90.25 | 62.108 | 0.0021554 | 58.338 | 1101.3 |  | 5824 | 90.25 | 0.70454 | 62.108 | 0.0021554 | 58.338 | 1101.3 | 1042.962
5825 | 0.70476 | 90.26 | 62.108 | 0.002156 | 58.348 | 1101.3 |  | 5825 | 90.26 | 0.70476 | 62.108 | 0.002156 | 58.348 | 1101.3 | 1042.952
5826 | 0.70498 | 90.27 | 62.107 | 0.0021567 | 58.358 | 1101.3 |  | 5826 | 90.27 | 0.70498 | 62.107 | 0.0021567 | 58.358 | 1101.3 | 1042.942
5827 | 0.7052 | 90.28 | 62.107 | 0.0021573 | 58.368 | 1101.3 |  | 5827 | 90.28 | 0.7052 | 62.107 | 0.0021573 | 58.368 | 1101.3 | 1042.932
5828 | 0.70542 | 90.29 | 62.107 | 0.0021579 | 58.378 | 1101.3 |  | 5828 | 90.29 | 0.70542 | 62.107 | 0.0021579 | 58.378 | 1101.3 | 1042.922
5829 | 0.70565 | 90.3 | 62.107 | 0.0021586 | 58.388 | 1101.3 |  | 5829 | 90.3 | 0.70565 | 62.107 | 0.0021586 | 58.388 | 1101.3 | 1042.912
5830 | 0.70587 | 90.31 | 62.107 | 0.0021592 | 58.398 | 1101.3 |  | 5830 | 90.31 | 0.70587 | 62.107 | 0.0021592 | 58.398 | 1101.3 | 1042.902
5831 | 0.70609 | 90.32 | 62.107 | 0.0021598 | 58.408 | 1101.3 |  | 5831 | 90.32 | 0.70609 | 62.107 | 0.0021598 | 58.408 | 1101.3 | 1042.892
5832 | 0.70631 | 90.33 | 62.107 | 0.0021605 | 58.418 | 1101.3 |  | 5832 | 90.33 | 0.70631 | 62.107 | 0.0021605 | 58.418 | 1101.3 | 1042.882
5833 | 0.70653 | 90.34 | 62.107 | 0.0021611 | 58.428 | 1101.3 |  | 5833 | 90.34 | 0.70653 | 62.107 | 0.0021611 | 58.428 | 1101.3 | 1042.872
5834 | 0.70675 | 90.35 | 62.107 | 0.0021618 | 58.438 | 1101.3 |  | 5834 | 90.35 | 0.70675 | 62.107 | 0.0021618 | 58.438 | 1101.3 | 1042.862
5835 | 0.70697 | 90.36 | 62.106 | 0.0021624 | 58.448 | 1101.3 |  | 5835 | 90.36 | 0.70697 | 62.106 | 0.0021624 | 58.448 | 1101.3 | 1042.852
5836 | 0.70719 | 90.37 | 62.106 | 0.002163 | 58.458 | 1101.3 |  | 5836 | 90.37 | 0.70719 | 62.106 | 0.002163 | 58.458 | 1101.3 | 1042.842
5837 | 0.70742 | 90.38 | 62.106 | 0.0021637 | 58.468 | 1101.3 |  | 5837 | 90.38 | 0.70742 | 62.106 | 0.0021637 | 58.468 | 1101.3 | 1042.832
5838 | 0.70764 | 90.39 | 62.106 | 0.0021643 | 58.478 | 1101.3 |  | 5838 | 90.39 | 0.70764 | 62.106 | 0.0021643 | 58.478 | 1101.3 | 1042.822
5839 | 0.70786 | 90.4 | 62.106 | 0.002165 | 58.488 | 1101.3 |  | 5839 | 90.4 | 0.70786 | 62.106 | 0.002165 | 58.488 | 1101.3 | 1042.812
5840 | 0.70808 | 90.41 | 62.106 | 0.0021656 | 58.498 | 1101.3 |  | 5840 | 90.41 | 0.70808 | 62.106 | 0.0021656 | 58.498 | 1101.3 | 1042.802
5841 | 0.7083 | 90.42 | 62.106 | 0.0021662 | 58.508 | 1101.3 |  | 5841 | 90.42 | 0.7083 | 62.106 | 0.0021662 | 58.508 | 1101.3 | 1042.792
5842 | 0.70852 | 90.43 | 62.106 | 0.0021669 | 58.518 | 1101.3 |  | 5842 | 90.43 | 0.70852 | 62.106 | 0.0021669 | 58.518 | 1101.3 | 1042.782
5843 | 0.70875 | 90.44 | 62.106 | 0.0021675 | 58.528 | 1101.3 |  | 5843 | 90.44 | 0.70875 | 62.106 | 0.0021675 | 58.528 | 1101.3 | 1042.772
5844 | 0.70897 | 90.45 | 62.105 | 0.0021682 | 58.538 | 1101.3 |  | 5844 | 90.45 | 0.70897 | 62.105 | 0.0021682 | 58.538 | 1101.3 | 1042.762
5845 | 0.70919 | 90.46 | 62.105 | 0.0021688 | 58.548 | 1101.3 |  | 5845 | 90.46 | 0.70919 | 62.105 | 0.0021688 | 58.548 | 1101.3 | 1042.752
5846 | 0.70941 | 90.47 | 62.105 | 0.0021694 | 58.558 | 1101.3 |  | 5846 | 90.47 | 0.70941 | 62.105 | 0.0021694 | 58.558 | 1101.3 | 1042.742
5847 | 0.70963 | 90.48 | 62.105 | 0.0021701 | 58.568 | 1101.4 |  | 5847 | 90.48 | 0.70963 | 62.105 | 0.0021701 | 58.568 | 1101.4 | 1042.832
5848 | 0.70986 | 90.49 | 62.105 | 0.0021707 | 58.578 | 1101.4 |  | 5848 | 90.49 | 0.70986 | 62.105 | 0.0021707 | 58.578 | 1101.4 | 1042.822
5849 | 0.71008 | 90.5 | 62.105 | 0.0021714 | 58.588 | 1101.4 |  | 5849 | 90.5 | 0.71008 | 62.105 | 0.0021714 | 58.588 | 1101.4 | 1042.812
5850 | 0.7103 | 90.51 | 62.105 | 0.002172 | 58.598 | 1101.4 |  | 5850 | 90.51 | 0.7103 | 62.105 | 0.002172 | 58.598 | 1101.4 | 1042.802
5851 | 0.71052 | 90.52 | 62.105 | 0.0021726 | 58.608 | 1101.4 |  | 5851 | 90.52 | 0.71052 | 62.105 | 0.0021726 | 58.608 | 1101.4 | 1042.792
5852 | 0.71075 | 90.53 | 62.105 | 0.0021733 | 58.618 | 1101.4 |  | 5852 | 90.53 | 0.71075 | 62.105 | 0.0021733 | 58.618 | 1101.4 | 1042.782
5853 | 0.71097 | 90.54 | 62.104 | 0.0021739 | 58.628 | 1101.4 |  | 5853 | 90.54 | 0.71097 | 62.104 | 0.0021739 | 58.628 | 1101.4 | 1042.772
5854 | 0.71119 | 90.55 | 62.104 | 0.0021746 | 58.638 | 1101.4 |  | 5854 | 90.55 | 0.71119 | 62.104 | 0.0021746 | 58.638 | 1101.4 | 1042.762
5855 | 0.71141 | 90.56 | 62.104 | 0.0021752 | 58.648 | 1101.4 |  | 5855 | 90.56 | 0.71141 | 62.104 | 0.0021752 | 58.648 | 1101.4 | 1042.752
5856 | 0.71164 | 90.57 | 62.104 | 0.0021758 | 58.658 | 1101.4 |  | 5856 | 90.57 | 0.71164 | 62.104 | 0.0021758 | 58.658 | 1101.4 | 1042.742
5857 | 0.71186 | 90.58 | 62.104 | 0.0021765 | 58.668 | 1101.4 |  | 5857 | 90.58 | 0.71186 | 62.104 | 0.0021765 | 58.668 | 1101.4 | 1042.732
5858 | 0.71208 | 90.59 | 62.104 | 0.0021771 | 58.678 | 1101.4 |  | 5858 | 90.59 | 0.71208 | 62.104 | 0.0021771 | 58.678 | 1101.4 | 1042.722
5859 | 0.7123 | 90.6 | 62.104 | 0.0021778 | 58.688 | 1101.4 |  | 5859 | 90.6 | 0.7123 | 62.104 | 0.0021778 | 58.688 | 1101.4 | 1042.712
5860 | 0.71253 | 90.61 | 62.104 | 0.0021784 | 58.698 | 1101.4 |  | 5860 | 90.61 | 0.71253 | 62.104 | 0.0021784 | 58.698 | 1101.4 | 1042.702
5861 | 0.71275 | 90.62 | 62.104 | 0.0021791 | 58.708 | 1101.4 |  | 5861 | 90.62 | 0.71275 | 62.104 | 0.0021791 | 58.708 | 1101.4 | 1042.692
5862 | 0.71297 | 90.63 | 62.103 | 0.0021797 | 58.718 | 1101.4 |  | 5862 | 90.63 | 0.71297 | 62.103 | 0.0021797 | 58.718 | 1101.4 | 1042.682
5863 | 0.7132 | 90.64 | 62.103 | 0.0021803 | 58.728 | 1101.4 |  | 5863 | 90.64 | 0.7132 | 62.103 | 0.0021803 | 58.728 | 1101.4 | 1042.672
5864 | 0.71342 | 90.65 | 62.103 | 0.002181 | 58.738 | 1101.4 |  | 5864 | 90.65 | 0.71342 | 62.103 | 0.002181 | 58.738 | 1101.4 | 1042.662
5865 | 0.71364 | 90.66 | 62.103 | 0.0021816 | 58.748 | 1101.4 |  | 5865 | 90.66 | 0.71364 | 62.103 | 0.0021816 | 58.748 | 1101.4 | 1042.652
5866 | 0.71387 | 90.67 | 62.103 | 0.0021823 | 58.758 | 1101.4 |  | 5866 | 90.67 | 0.71387 | 62.103 | 0.0021823 | 58.758 | 1101.4 | 1042.642
5867 | 0.71409 | 90.68 | 62.103 | 0.0021829 | 58.768 | 1101.4 |  | 5867 | 90.68 | 0.71409 | 62.103 | 0.0021829 | 58.768 | 1101.4 | 1042.632
5868 | 0.71431 | 90.69 | 62.103 | 0.0021836 | 58.778 | 1101.4 |  | 5868 | 90.69 | 0.71431 | 62.103 | 0.0021836 | 58.778 | 1101.4 | 1042.622
5869 | 0.71454 | 90.7 | 62.103 | 0.0021842 | 58.788 | 1101.4 |  | 5869 | 90.7 | 0.71454 | 62.103 | 0.0021842 | 58.788 | 1101.4 | 1042.612
5870 | 0.71476 | 90.71 | 62.103 | 0.0021849 | 58.798 | 1101.5 |  | 5870 | 90.71 | 0.71476 | 62.103 | 0.0021849 | 58.798 | 1101.5 | 1042.702
5871 | 0.71498 | 90.72 | 62.102 | 0.0021855 | 58.808 | 1101.5 |  | 5871 | 90.72 | 0.71498 | 62.102 | 0.0021855 | 58.808 | 1101.5 | 1042.692
5872 | 0.71521 | 90.73 | 62.102 | 0.0021861 | 58.818 | 1101.5 |  | 5872 | 90.73 | 0.71521 | 62.102 | 0.0021861 | 58.818 | 1101.5 | 1042.682
5873 | 0.71543 | 90.74 | 62.102 | 0.0021868 | 58.828 | 1101.5 |  | 5873 | 90.74 | 0.71543 | 62.102 | 0.0021868 | 58.828 | 1101.5 | 1042.672
5874 | 0.71565 | 90.75 | 62.102 | 0.0021874 | 58.838 | 1101.5 |  | 5874 | 90.75 | 0.71565 | 62.102 | 0.0021874 | 58.838 | 1101.5 | 1042.662
5875 | 0.71588 | 90.76 | 62.102 | 0.0021881 | 58.848 | 1101.5 |  | 5875 | 90.76 | 0.71588 | 62.102 | 0.0021881 | 58.848 | 1101.5 | 1042.652
5876 | 0.7161 | 90.77 | 62.102 | 0.0021887 | 58.858 | 1101.5 |  | 5876 | 90.77 | 0.7161 | 62.102 | 0.0021887 | 58.858 | 1101.5 | 1042.642
5877 | 0.71633 | 90.78 | 62.102 | 0.0021894 | 58.868 | 1101.5 |  | 5877 | 90.78 | 0.71633 | 62.102 | 0.0021894 | 58.868 | 1101.5 | 1042.632
5878 | 0.71655 | 90.79 | 62.102 | 0.00219 | 58.878 | 1101.5 |  | 5878 | 90.79 | 0.71655 | 62.102 | 0.00219 | 58.878 | 1101.5 | 1042.622
5879 | 0.71677 | 90.8 | 62.102 | 0.0021907 | 58.888 | 1101.5 |  | 5879 | 90.8 | 0.71677 | 62.102 | 0.0021907 | 58.888 | 1101.5 | 1042.612
5880 | 0.717 | 90.81 | 62.101 | 0.0021913 | 58.898 | 1101.5 |  | 5880 | 90.81 | 0.717 | 62.101 | 0.0021913 | 58.898 | 1101.5 | 1042.602
5881 | 0.71722 | 90.82 | 62.101 | 0.002192 | 58.908 | 1101.5 |  | 5881 | 90.82 | 0.71722 | 62.101 | 0.002192 | 58.908 | 1101.5 | 1042.592
5882 | 0.71745 | 90.83 | 62.101 | 0.0021926 | 58.918 | 1101.5 |  | 5882 | 90.83 | 0.71745 | 62.101 | 0.0021926 | 58.918 | 1101.5 | 1042.582
5883 | 0.71767 | 90.84 | 62.101 | 0.0021932 | 58.928 | 1101.5 |  | 5883 | 90.84 | 0.71767 | 62.101 | 0.0021932 | 58.928 | 1101.5 | 1042.572
5884 | 0.71789 | 90.85 | 62.101 | 0.0021939 | 58.938 | 1101.5 |  | 5884 | 90.85 | 0.71789 | 62.101 | 0.0021939 | 58.938 | 1101.5 | 1042.562
5885 | 0.71812 | 90.86 | 62.101 | 0.0021945 | 58.948 | 1101.5 |  | 5885 | 90.86 | 0.71812 | 62.101 | 0.0021945 | 58.948 | 1101.5 | 1042.552
5886 | 0.71834 | 90.87 | 62.101 | 0.0021952 | 58.958 | 1101.5 |  | 5886 | 90.87 | 0.71834 | 62.101 | 0.0021952 | 58.958 | 1101.5 | 1042.542
5887 | 0.71857 | 90.88 | 62.101 | 0.0021958 | 58.967 | 1101.5 |  | 5887 | 90.88 | 0.71857 | 62.101 | 0.0021958 | 58.967 | 1101.5 | 1042.533
5888 | 0.71879 | 90.89 | 62.1 | 0.0021965 | 58.977 | 1101.5 |  | 5888 | 90.89 | 0.71879 | 62.1 | 0.0021965 | 58.977 | 1101.5 | 1042.523
5889 | 0.71902 | 90.9 | 62.1 | 0.0021971 | 58.987 | 1101.5 |  | 5889 | 90.9 | 0.71902 | 62.1 | 0.0021971 | 58.987 | 1101.5 | 1042.513
5890 | 0.71924 | 90.91 | 62.1 | 0.0021978 | 58.997 | 1101.5 |  | 5890 | 90.91 | 0.71924 | 62.1 | 0.0021978 | 58.997 | 1101.5 | 1042.503
5891 | 0.71947 | 90.92 | 62.1 | 0.0021984 | 59.007 | 1101.5 |  | 5891 | 90.92 | 0.71947 | 62.1 | 0.0021984 | 59.007 | 1101.5 | 1042.493
5892 | 0.71969 | 90.93 | 62.1 | 0.0021991 | 59.017 | 1101.5 |  | 5892 | 90.93 | 0.71969 | 62.1 | 0.0021991 | 59.017 | 1101.5 | 1042.483
5893 | 0.71992 | 90.94 | 62.1 | 0.0021997 | 59.027 | 1101.6 |  | 5893 | 90.94 | 0.71992 | 62.1 | 0.0021997 | 59.027 | 1101.6 | 1042.573
5894 | 0.72014 | 90.95 | 62.1 | 0.0022004 | 59.037 | 1101.6 |  | 5894 | 90.95 | 0.72014 | 62.1 | 0.0022004 | 59.037 | 1101.6 | 1042.563
5895 | 0.72037 | 90.96 | 62.1 | 0.002201 | 59.047 | 1101.6 |  | 5895 | 90.96 | 0.72037 | 62.1 | 0.002201 | 59.047 | 1101.6 | 1042.553
5896 | 0.72059 | 90.97 | 62.1 | 0.0022017 | 59.057 | 1101.6 |  | 5896 | 90.97 | 0.72059 | 62.1 | 0.0022017 | 59.057 | 1101.6 | 1042.543
5897 | 0.72082 | 90.98 | 62.099 | 0.0022023 | 59.067 | 1101.6 |  | 5897 | 90.98 | 0.72082 | 62.099 | 0.0022023 | 59.067 | 1101.6 | 1042.533
5898 | 0.72104 | 90.99 | 62.099 | 0.002203 | 59.077 | 1101.6 |  | 5898 | 90.99 | 0.72104 | 62.099 | 0.002203 | 59.077 | 1101.6 | 1042.523
5899 | 0.72127 | 91 | 62.099 | 0.0022036 | 59.087 | 1101.6 |  | 5899 | 91 | 0.72127 | 62.099 | 0.0022036 | 59.087 | 1101.6 | 1042.513
5900 | 0.72149 | 91.01 | 62.099 | 0.0022043 | 59.097 | 1101.6 |  | 5900 | 91.01 | 0.72149 | 62.099 | 0.0022043 | 59.097 | 1101.6 | 1042.503
5901 | 0.72172 | 91.02 | 62.099 | 0.0022049 | 59.107 | 1101.6 |  | 5901 | 91.02 | 0.72172 | 62.099 | 0.0022049 | 59.107 | 1101.6 | 1042.493
5902 | 0.72194 | 91.03 | 62.099 | 0.0022056 | 59.117 | 1101.6 |  | 5902 | 91.03 | 0.72194 | 62.099 | 0.0022056 | 59.117 | 1101.6 | 1042.483
5903 | 0.72217 | 91.04 | 62.099 | 0.0022062 | 59.127 | 1101.6 |  | 5903 | 91.04 | 0.72217 | 62.099 | 0.0022062 | 59.127 | 1101.6 | 1042.473
5904 | 0.72239 | 91.05 | 62.099 | 0.0022069 | 59.137 | 1101.6 |  | 5904 | 91.05 | 0.72239 | 62.099 | 0.0022069 | 59.137 | 1101.6 | 1042.463
5905 | 0.72262 | 91.06 | 62.099 | 0.0022075 | 59.147 | 1101.6 |  | 5905 | 91.06 | 0.72262 | 62.099 | 0.0022075 | 59.147 | 1101.6 | 1042.453
5906 | 0.72285 | 91.07 | 62.098 | 0.0022082 | 59.157 | 1101.6 |  | 5906 | 91.07 | 0.72285 | 62.098 | 0.0022082 | 59.157 | 1101.6 | 1042.443
5907 | 0.72307 | 91.08 | 62.098 | 0.0022088 | 59.167 | 1101.6 |  | 5907 | 91.08 | 0.72307 | 62.098 | 0.0022088 | 59.167 | 1101.6 | 1042.433
5908 | 0.7233 | 91.09 | 62.098 | 0.0022095 | 59.177 | 1101.6 |  | 5908 | 91.09 | 0.7233 | 62.098 | 0.0022095 | 59.177 | 1101.6 | 1042.423
5909 | 0.72352 | 91.1 | 62.098 | 0.0022101 | 59.187 | 1101.6 |  | 5909 | 91.1 | 0.72352 | 62.098 | 0.0022101 | 59.187 | 1101.6 | 1042.413
5910 | 0.72375 | 91.11 | 62.098 | 0.0022108 | 59.197 | 1101.6 |  | 5910 | 91.11 | 0.72375 | 62.098 | 0.0022108 | 59.197 | 1101.6 | 1042.403
5911 | 0.72397 | 91.12 | 62.098 | 0.0022114 | 59.207 | 1101.6 |  | 5911 | 91.12 | 0.72397 | 62.098 | 0.0022114 | 59.207 | 1101.6 | 1042.393
5912 | 0.7242 | 91.13 | 62.098 | 0.0022121 | 59.217 | 1101.6 |  | 5912 | 91.13 | 0.7242 | 62.098 | 0.0022121 | 59.217 | 1101.6 | 1042.383
5913 | 0.72443 | 91.14 | 62.098 | 0.0022127 | 59.227 | 1101.6 |  | 5913 | 91.14 | 0.72443 | 62.098 | 0.0022127 | 59.227 | 1101.6 | 1042.373
5914 | 0.72465 | 91.15 | 62.098 | 0.0022134 | 59.237 | 1101.6 |  | 5914 | 91.15 | 0.72465 | 62.098 | 0.0022134 | 59.237 | 1101.6 | 1042.363
5915 | 0.72488 | 91.16 | 62.097 | 0.002214 | 59.247 | 1101.6 |  | 5915 | 91.16 | 0.72488 | 62.097 | 0.002214 | 59.247 | 1101.6 | 1042.353
5916 | 0.72511 | 91.17 | 62.097 | 0.0022147 | 59.257 | 1101.6 |  | 5916 | 91.17 | 0.72511 | 62.097 | 0.0022147 | 59.257 | 1101.6 | 1042.343
5917 | 0.72533 | 91.18 | 62.097 | 0.0022153 | 59.267 | 1101.7 |  | 5917 | 91.18 | 0.72533 | 62.097 | 0.0022153 | 59.267 | 1101.7 | 1042.433
5918 | 0.72556 | 91.19 | 62.097 | 0.002216 | 59.277 | 1101.7 |  | 5918 | 91.19 | 0.72556 | 62.097 | 0.002216 | 59.277 | 1101.7 | 1042.423
5919 | 0.72579 | 91.2 | 62.097 | 0.0022166 | 59.287 | 1101.7 |  | 5919 | 91.2 | 0.72579 | 62.097 | 0.0022166 | 59.287 | 1101.7 | 1042.413
5920 | 0.72601 | 91.21 | 62.097 | 0.0022173 | 59.297 | 1101.7 |  | 5920 | 91.21 | 0.72601 | 62.097 | 0.0022173 | 59.297 | 1101.7 | 1042.403
5921 | 0.72624 | 91.22 | 62.097 | 0.0022179 | 59.307 | 1101.7 |  | 5921 | 91.22 | 0.72624 | 62.097 | 0.0022179 | 59.307 | 1101.7 | 1042.393
5922 | 0.72646 | 91.23 | 62.097 | 0.0022186 | 59.317 | 1101.7 |  | 5922 | 91.23 | 0.72646 | 62.097 | 0.0022186 | 59.317 | 1101.7 | 1042.383
5923 | 0.72669 | 91.24 | 62.097 | 0.0022192 | 59.327 | 1101.7 |  | 5923 | 91.24 | 0.72669 | 62.097 | 0.0022192 | 59.327 | 1101.7 | 1042.373
5924 | 0.72692 | 91.25 | 62.096 | 0.0022199 | 59.337 | 1101.7 |  | 5924 | 91.25 | 0.72692 | 62.096 | 0.0022199 | 59.337 | 1101.7 | 1042.363
5925 | 0.72715 | 91.26 | 62.096 | 0.0022205 | 59.347 | 1101.7 |  | 5925 | 91.26 | 0.72715 | 62.096 | 0.0022205 | 59.347 | 1101.7 | 1042.353
5926 | 0.72737 | 91.27 | 62.096 | 0.0022212 | 59.357 | 1101.7 |  | 5926 | 91.27 | 0.72737 | 62.096 | 0.0022212 | 59.357 | 1101.7 | 1042.343
5927 | 0.7276 | 91.28 | 62.096 | 0.0022219 | 59.367 | 1101.7 |  | 5927 | 91.28 | 0.7276 | 62.096 | 0.0022219 | 59.367 | 1101.7 | 1042.333
5928 | 0.72783 | 91.29 | 62.096 | 0.0022225 | 59.377 | 1101.7 |  | 5928 | 91.29 | 0.72783 | 62.096 | 0.0022225 | 59.377 | 1101.7 | 1042.323
5929 | 0.72805 | 91.3 | 62.096 | 0.0022232 | 59.387 | 1101.7 |  | 5929 | 91.3 | 0.72805 | 62.096 | 0.0022232 | 59.387 | 1101.7 | 1042.313
5930 | 0.72828 | 91.31 | 62.096 | 0.0022238 | 59.397 | 1101.7 |  | 5930 | 91.31 | 0.72828 | 62.096 | 0.0022238 | 59.397 | 1101.7 | 1042.303
5931 | 0.72851 | 91.32 | 62.096 | 0.0022245 | 59.407 | 1101.7 |  | 5931 | 91.32 | 0.72851 | 62.096 | 0.0022245 | 59.407 | 1101.7 | 1042.293
5932 | 0.72874 | 91.33 | 62.096 | 0.0022251 | 59.417 | 1101.7 |  | 5932 | 91.33 | 0.72874 | 62.096 | 0.0022251 | 59.417 | 1101.7 | 1042.283
5933 | 0.72896 | 91.34 | 62.095 | 0.0022258 | 59.427 | 1101.7 |  | 5933 | 91.34 | 0.72896 | 62.095 | 0.0022258 | 59.427 | 1101.7 | 1042.273
5934 | 0.72919 | 91.35 | 62.095 | 0.0022264 | 59.437 | 1101.7 |  | 5934 | 91.35 | 0.72919 | 62.095 | 0.0022264 | 59.437 | 1101.7 | 1042.263
5935 | 0.72942 | 91.36 | 62.095 | 0.0022271 | 59.447 | 1101.7 |  | 5935 | 91.36 | 0.72942 | 62.095 | 0.0022271 | 59.447 | 1101.7 | 1042.253
5936 | 0.72964 | 91.37 | 62.095 | 0.0022277 | 59.457 | 1101.7 |  | 5936 | 91.37 | 0.72964 | 62.095 | 0.0022277 | 59.457 | 1101.7 | 1042.243
5937 | 0.72987 | 91.38 | 62.095 | 0.0022284 | 59.467 | 1101.7 |  | 5937 | 91.38 | 0.72987 | 62.095 | 0.0022284 | 59.467 | 1101.7 | 1042.233
5938 | 0.7301 | 91.39 | 62.095 | 0.0022291 | 59.477 | 1101.7 |  | 5938 | 91.39 | 0.7301 | 62.095 | 0.0022291 | 59.477 | 1101.7 | 1042.223
5939 | 0.73033 | 91.4 | 62.095 | 0.0022297 | 59.487 | 1101.7 |  | 5939 | 91.4 | 0.73033 | 62.095 | 0.0022297 | 59.487 | 1101.7 | 1042.213
5940 | 0.73056 | 91.41 | 62.095 | 0.0022304 | 59.497 | 1101.8 |  | 5940 | 91.41 | 0.73056 | 62.095 | 0.0022304 | 59.497 | 1101.8 | 1042.303
5941 | 0.73078 | 91.42 | 62.094 | 0.002231 | 59.507 | 1101.8 |  | 5941 | 91.42 | 0.73078 | 62.094 | 0.002231 | 59.507 | 1101.8 | 1042.293
5942 | 0.73101 | 91.43 | 62.094 | 0.0022317 | 59.517 | 1101.8 |  | 5942 | 91.43 | 0.73101 | 62.094 | 0.0022317 | 59.517 | 1101.8 | 1042.283
5943 | 0.73124 | 91.44 | 62.094 | 0.0022323 | 59.527 | 1101.8 |  | 5943 | 91.44 | 0.73124 | 62.094 | 0.0022323 | 59.527 | 1101.8 | 1042.273
5944 | 0.73147 | 91.45 | 62.094 | 0.002233 | 59.537 | 1101.8 |  | 5944 | 91.45 | 0.73147 | 62.094 | 0.002233 | 59.537 | 1101.8 | 1042.263
5945 | 0.7317 | 91.46 | 62.094 | 0.0022337 | 59.547 | 1101.8 |  | 5945 | 91.46 | 0.7317 | 62.094 | 0.0022337 | 59.547 | 1101.8 | 1042.253
5946 | 0.73192 | 91.47 | 62.094 | 0.0022343 | 59.557 | 1101.8 |  | 5946 | 91.47 | 0.73192 | 62.094 | 0.0022343 | 59.557 | 1101.8 | 1042.243
5947 | 0.73215 | 91.48 | 62.094 | 0.002235 | 59.567 | 1101.8 |  | 5947 | 91.48 | 0.73215 | 62.094 | 0.002235 | 59.567 | 1101.8 | 1042.233
5948 | 0.73238 | 91.49 | 62.094 | 0.0022356 | 59.577 | 1101.8 |  | 5948 | 91.49 | 0.73238 | 62.094 | 0.0022356 | 59.577 | 1101.8 | 1042.223
5949 | 0.73261 | 91.5 | 62.094 | 0.0022363 | 59.587 | 1101.8 |  | 5949 | 91.5 | 0.73261 | 62.094 | 0.0022363 | 59.587 | 1101.8 | 1042.213
5950 | 0.73284 | 91.51 | 62.093 | 0.0022369 | 59.597 | 1101.8 |  | 5950 | 91.51 | 0.73284 | 62.093 | 0.0022369 | 59.597 | 1101.8 | 1042.203
5951 | 0.73307 | 91.52 | 62.093 | 0.0022376 | 59.607 | 1101.8 |  | 5951 | 91.52 | 0.73307 | 62.093 | 0.0022376 | 59.607 | 1101.8 | 1042.193
5952 | 0.73329 | 91.53 | 62.093 | 0.0022383 | 59.617 | 1101.8 |  | 5952 | 91.53 | 0.73329 | 62.093 | 0.0022383 | 59.617 | 1101.8 | 1042.183
5953 | 0.73352 | 91.54 | 62.093 | 0.0022389 | 59.627 | 1101.8 |  | 5953 | 91.54 | 0.73352 | 62.093 | 0.0022389 | 59.627 | 1101.8 | 1042.173
5954 | 0.73375 | 91.55 | 62.093 | 0.0022396 | 59.637 | 1101.8 |  | 5954 | 91.55 | 0.73375 | 62.093 | 0.0022396 | 59.637 | 1101.8 | 1042.163
5955 | 0.73398 | 91.56 | 62.093 | 0.0022402 | 59.647 | 1101.8 |  | 5955 | 91.56 | 0.73398 | 62.093 | 0.0022402 | 59.647 | 1101.8 | 1042.153
5956 | 0.73421 | 91.57 | 62.093 | 0.0022409 | 59.657 | 1101.8 |  | 5956 | 91.57 | 0.73421 | 62.093 | 0.0022409 | 59.657 | 1101.8 | 1042.143
5957 | 0.73444 | 91.58 | 62.093 | 0.0022415 | 59.667 | 1101.8 |  | 5957 | 91.58 | 0.73444 | 62.093 | 0.0022415 | 59.667 | 1101.8 | 1042.133
5958 | 0.73467 | 91.59 | 62.093 | 0.0022422 | 59.677 | 1101.8 |  | 5958 | 91.59 | 0.73467 | 62.093 | 0.0022422 | 59.677 | 1101.8 | 1042.123
5959 | 0.7349 | 91.6 | 62.092 | 0.0022429 | 59.687 | 1101.8 |  | 5959 | 91.6 | 0.7349 | 62.092 | 0.0022429 | 59.687 | 1101.8 | 1042.113
5960 | 0.73512 | 91.61 | 62.092 | 0.0022435 | 59.697 | 1101.8 |  | 5960 | 91.61 | 0.73512 | 62.092 | 0.0022435 | 59.697 | 1101.8 | 1042.103
5961 | 0.73535 | 91.62 | 62.092 | 0.0022442 | 59.707 | 1101.8 |  | 5961 | 91.62 | 0.73535 | 62.092 | 0.0022442 | 59.707 | 1101.8 | 1042.093
5962 | 0.73558 | 91.63 | 62.092 | 0.0022448 | 59.717 | 1101.8 |  | 5962 | 91.63 | 0.73558 | 62.092 | 0.0022448 | 59.717 | 1101.8 | 1042.083
5963 | 0.73581 | 91.64 | 62.092 | 0.0022455 | 59.727 | 1101.9 |  | 5963 | 91.64 | 0.73581 | 62.092 | 0.0022455 | 59.727 | 1101.9 | 1042.173
5964 | 0.73604 | 91.65 | 62.092 | 0.0022462 | 59.737 | 1101.9 |  | 5964 | 91.65 | 0.73604 | 62.092 | 0.0022462 | 59.737 | 1101.9 | 1042.163
5965 | 0.73627 | 91.66 | 62.092 | 0.0022468 | 59.747 | 1101.9 |  | 5965 | 91.66 | 0.73627 | 62.092 | 0.0022468 | 59.747 | 1101.9 | 1042.153
5966 | 0.7365 | 91.67 | 62.092 | 0.0022475 | 59.757 | 1101.9 |  | 5966 | 91.67 | 0.7365 | 62.092 | 0.0022475 | 59.757 | 1101.9 | 1042.143
5967 | 0.73673 | 91.68 | 62.092 | 0.0022481 | 59.767 | 1101.9 |  | 5967 | 91.68 | 0.73673 | 62.092 | 0.0022481 | 59.767 | 1101.9 | 1042.133
5968 | 0.73696 | 91.69 | 62.091 | 0.0022488 | 59.777 | 1101.9 |  | 5968 | 91.69 | 0.73696 | 62.091 | 0.0022488 | 59.777 | 1101.9 | 1042.123
5969 | 0.73719 | 91.7 | 62.091 | 0.0022495 | 59.787 | 1101.9 |  | 5969 | 91.7 | 0.73719 | 62.091 | 0.0022495 | 59.787 | 1101.9 | 1042.113
5970 | 0.73742 | 91.71 | 62.091 | 0.0022501 | 59.797 | 1101.9 |  | 5970 | 91.71 | 0.73742 | 62.091 | 0.0022501 | 59.797 | 1101.9 | 1042.103
5971 | 0.73765 | 91.72 | 62.091 | 0.0022508 | 59.807 | 1101.9 |  | 5971 | 91.72 | 0.73765 | 62.091 | 0.0022508 | 59.807 | 1101.9 | 1042.093
5972 | 0.73788 | 91.73 | 62.091 | 0.0022514 | 59.817 | 1101.9 |  | 5972 | 91.73 | 0.73788 | 62.091 | 0.0022514 | 59.817 | 1101.9 | 1042.083
5973 | 0.73811 | 91.74 | 62.091 | 0.0022521 | 59.827 | 1101.9 |  | 5973 | 91.74 | 0.73811 | 62.091 | 0.0022521 | 59.827 | 1101.9 | 1042.073
5974 | 0.73834 | 91.75 | 62.091 | 0.0022528 | 59.837 | 1101.9 |  | 5974 | 91.75 | 0.73834 | 62.091 | 0.0022528 | 59.837 | 1101.9 | 1042.063
5975 | 0.73857 | 91.76 | 62.091 | 0.0022534 | 59.847 | 1101.9 |  | 5975 | 91.76 | 0.73857 | 62.091 | 0.0022534 | 59.847 | 1101.9 | 1042.053
5976 | 0.7388 | 91.77 | 62.091 | 0.0022541 | 59.857 | 1101.9 |  | 5976 | 91.77 | 0.7388 | 62.091 | 0.0022541 | 59.857 | 1101.9 | 1042.043
5977 | 0.73903 | 91.78 | 62.09 | 0.0022548 | 59.867 | 1101.9 |  | 5977 | 91.78 | 0.73903 | 62.09 | 0.0022548 | 59.867 | 1101.9 | 1042.033
5978 | 0.73926 | 91.79 | 62.09 | 0.0022554 | 59.877 | 1101.9 |  | 5978 | 91.79 | 0.73926 | 62.09 | 0.0022554 | 59.877 | 1101.9 | 1042.023
5979 | 0.73949 | 91.8 | 62.09 | 0.0022561 | 59.887 | 1101.9 |  | 5979 | 91.8 | 0.73949 | 62.09 | 0.0022561 | 59.887 | 1101.9 | 1042.013
5980 | 0.73972 | 91.81 | 62.09 | 0.0022567 | 59.897 | 1101.9 |  | 5980 | 91.81 | 0.73972 | 62.09 | 0.0022567 | 59.897 | 1101.9 | 1042.003
5981 | 0.73995 | 91.82 | 62.09 | 0.0022574 | 59.907 | 1101.9 |  | 5981 | 91.82 | 0.73995 | 62.09 | 0.0022574 | 59.907 | 1101.9 | 1041.993
5982 | 0.74018 | 91.83 | 62.09 | 0.0022581 | 59.917 | 1101.9 |  | 5982 | 91.83 | 0.74018 | 62.09 | 0.0022581 | 59.917 | 1101.9 | 1041.983
5983 | 0.74041 | 91.84 | 62.09 | 0.0022587 | 59.927 | 1101.9 |  | 5983 | 91.84 | 0.74041 | 62.09 | 0.0022587 | 59.927 | 1101.9 | 1041.973
5984 | 0.74064 | 91.85 | 62.09 | 0.0022594 | 59.937 | 1101.9 |  | 5984 | 91.85 | 0.74064 | 62.09 | 0.0022594 | 59.937 | 1101.9 | 1041.963
5985 | 0.74087 | 91.86 | 62.089 | 0.0022601 | 59.947 | 1101.9 |  | 5985 | 91.86 | 0.74087 | 62.089 | 0.0022601 | 59.947 | 1101.9 | 1041.953
5986 | 0.7411 | 91.87 | 62.089 | 0.0022607 | 59.957 | 1102 |  | 5986 | 91.87 | 0.7411 | 62.089 | 0.0022607 | 59.957 | 1102 | 1042.043
5987 | 0.74133 | 91.88 | 62.089 | 0.0022614 | 59.967 | 1102 |  | 5987 | 91.88 | 0.74133 | 62.089 | 0.0022614 | 59.967 | 1102 | 1042.033
5988 | 0.74156 | 91.89 | 62.089 | 0.0022621 | 59.977 | 1102 |  | 5988 | 91.89 | 0.74156 | 62.089 | 0.0022621 | 59.977 | 1102 | 1042.023
5989 | 0.74179 | 91.9 | 62.089 | 0.0022627 | 59.986 | 1102 |  | 5989 | 91.9 | 0.74179 | 62.089 | 0.0022627 | 59.986 | 1102 | 1042.014
5990 | 0.74202 | 91.91 | 62.089 | 0.0022634 | 59.996 | 1102 |  | 5990 | 91.91 | 0.74202 | 62.089 | 0.0022634 | 59.996 | 1102 | 1042.004
5991 | 0.74225 | 91.92 | 62.089 | 0.002264 | 60.006 | 1102 |  | 5991 | 91.92 | 0.74225 | 62.089 | 0.002264 | 60.006 | 1102 | 1041.994
5992 | 0.74249 | 91.93 | 62.089 | 0.0022647 | 60.016 | 1102 |  | 5992 | 91.93 | 0.74249 | 62.089 | 0.0022647 | 60.016 | 1102 | 1041.984
5993 | 0.74272 | 91.94 | 62.089 | 0.0022654 | 60.026 | 1102 |  | 5993 | 91.94 | 0.74272 | 62.089 | 0.0022654 | 60.026 | 1102 | 1041.974
5994 | 0.74295 | 91.95 | 62.088 | 0.002266 | 60.036 | 1102 |  | 5994 | 91.95 | 0.74295 | 62.088 | 0.002266 | 60.036 | 1102 | 1041.964
5995 | 0.74318 | 91.96 | 62.088 | 0.0022667 | 60.046 | 1102 |  | 5995 | 91.96 | 0.74318 | 62.088 | 0.0022667 | 60.046 | 1102 | 1041.954
5996 | 0.74341 | 91.97 | 62.088 | 0.0022674 | 60.056 | 1102 |  | 5996 | 91.97 | 0.74341 | 62.088 | 0.0022674 | 60.056 | 1102 | 1041.944
5997 | 0.74364 | 91.98 | 62.088 | 0.002268 | 60.066 | 1102 |  | 5997 | 91.98 | 0.74364 | 62.088 | 0.002268 | 60.066 | 1102 | 1041.934
5998 | 0.74387 | 91.99 | 62.088 | 0.0022687 | 60.076 | 1102 |  | 5998 | 91.99 | 0.74387 | 62.088 | 0.0022687 | 60.076 | 1102 | 1041.924
5999 | 0.7441 | 92 | 62.088 | 0.0022694 | 60.086 | 1102 |  | 5999 | 92 | 0.7441 | 62.088 | 0.0022694 | 60.086 | 1102 | 1041.914
6000 | 0.74434 | 92.01 | 62.088 | 0.00227 | 60.096 | 1102 |  | 6000 | 92.01 | 0.74434 | 62.088 | 0.00227 | 60.096 | 1102 | 1041.904
6001 | 0.74457 | 92.02 | 62.088 | 0.0022707 | 60.106 | 1102 |  | 6001 | 92.02 | 0.74457 | 62.088 | 0.0022707 | 60.106 | 1102 | 1041.894
6002 | 0.7448 | 92.03 | 62.088 | 0.0022714 | 60.116 | 1102 |  | 6002 | 92.03 | 0.7448 | 62.088 | 0.0022714 | 60.116 | 1102 | 1041.884
6003 | 0.74503 | 92.04 | 62.087 | 0.002272 | 60.126 | 1102 |  | 6003 | 92.04 | 0.74503 | 62.087 | 0.002272 | 60.126 | 1102 | 1041.874
6004 | 0.74526 | 92.05 | 62.087 | 0.0022727 | 60.136 | 1102 |  | 6004 | 92.05 | 0.74526 | 62.087 | 0.0022727 | 60.136 | 1102 | 1041.864
6005 | 0.74549 | 92.06 | 62.087 | 0.0022734 | 60.146 | 1102 |  | 6005 | 92.06 | 0.74549 | 62.087 | 0.0022734 | 60.146 | 1102 | 1041.854
6006 | 0.74573 | 92.07 | 62.087 | 0.002274 | 60.156 | 1102 |  | 6006 | 92.07 | 0.74573 | 62.087 | 0.002274 | 60.156 | 1102 | 1041.844
6007 | 0.74596 | 92.08 | 62.087 | 0.0022747 | 60.166 | 1102 |  | 6007 | 92.08 | 0.74596 | 62.087 | 0.0022747 | 60.166 | 1102 | 1041.834
6008 | 0.74619 | 92.09 | 62.087 | 0.0022754 | 60.176 | 1102 |  | 6008 | 92.09 | 0.74619 | 62.087 | 0.0022754 | 60.176 | 1102 | 1041.824
6009 | 0.74642 | 92.1 | 62.087 | 0.002276 | 60.186 | 1102 |  | 6009 | 92.1 | 0.74642 | 62.087 | 0.002276 | 60.186 | 1102 | 1041.814
6010 | 0.74665 | 92.11 | 62.087 | 0.0022767 | 60.196 | 1102.1 |  | 6010 | 92.11 | 0.74665 | 62.087 | 0.0022767 | 60.196 | 1102.1 | 1041.904
6011 | 0.74689 | 92.12 | 62.087 | 0.0022774 | 60.206 | 1102.1 |  | 6011 | 92.12 | 0.74689 | 62.087 | 0.0022774 | 60.206 | 1102.1 | 1041.894
6012 | 0.74712 | 92.13 | 62.086 | 0.002278 | 60.216 | 1102.1 |  | 6012 | 92.13 | 0.74712 | 62.086 | 0.002278 | 60.216 | 1102.1 | 1041.884
6013 | 0.74735 | 92.14 | 62.086 | 0.0022787 | 60.226 | 1102.1 |  | 6013 | 92.14 | 0.74735 | 62.086 | 0.0022787 | 60.226 | 1102.1 | 1041.874
6014 | 0.74758 | 92.15 | 62.086 | 0.0022794 | 60.236 | 1102.1 |  | 6014 | 92.15 | 0.74758 | 62.086 | 0.0022794 | 60.236 | 1102.1 | 1041.864
6015 | 0.74782 | 92.16 | 62.086 | 0.00228 | 60.246 | 1102.1 |  | 6015 | 92.16 | 0.74782 | 62.086 | 0.00228 | 60.246 | 1102.1 | 1041.854
6016 | 0.74805 | 92.17 | 62.086 | 0.0022807 | 60.256 | 1102.1 |  | 6016 | 92.17 | 0.74805 | 62.086 | 0.0022807 | 60.256 | 1102.1 | 1041.844
6017 | 0.74828 | 92.18 | 62.086 | 0.0022814 | 60.266 | 1102.1 |  | 6017 | 92.18 | 0.74828 | 62.086 | 0.0022814 | 60.266 | 1102.1 | 1041.834
6018 | 0.74851 | 92.19 | 62.086 | 0.002282 | 60.276 | 1102.1 |  | 6018 | 92.19 | 0.74851 | 62.086 | 0.002282 | 60.276 | 1102.1 | 1041.824
6019 | 0.74875 | 92.2 | 62.086 | 0.0022827 | 60.286 | 1102.1 |  | 6019 | 92.2 | 0.74875 | 62.086 | 0.0022827 | 60.286 | 1102.1 | 1041.814
6020 | 0.74898 | 92.21 | 62.085 | 0.0022834 | 60.296 | 1102.1 |  | 6020 | 92.21 | 0.74898 | 62.085 | 0.0022834 | 60.296 | 1102.1 | 1041.804
6021 | 0.74921 | 92.22 | 62.085 | 0.0022841 | 60.306 | 1102.1 |  | 6021 | 92.22 | 0.74921 | 62.085 | 0.0022841 | 60.306 | 1102.1 | 1041.794
6022 | 0.74944 | 92.23 | 62.085 | 0.0022847 | 60.316 | 1102.1 |  | 6022 | 92.23 | 0.74944 | 62.085 | 0.0022847 | 60.316 | 1102.1 | 1041.784
6023 | 0.74968 | 92.24 | 62.085 | 0.0022854 | 60.326 | 1102.1 |  | 6023 | 92.24 | 0.74968 | 62.085 | 0.0022854 | 60.326 | 1102.1 | 1041.774
6024 | 0.74991 | 92.25 | 62.085 | 0.0022861 | 60.336 | 1102.1 |  | 6024 | 92.25 | 0.74991 | 62.085 | 0.0022861 | 60.336 | 1102.1 | 1041.764
6025 | 0.75014 | 92.26 | 62.085 | 0.0022867 | 60.346 | 1102.1 |  | 6025 | 92.26 | 0.75014 | 62.085 | 0.0022867 | 60.346 | 1102.1 | 1041.754
6026 | 0.75038 | 92.27 | 62.085 | 0.0022874 | 60.356 | 1102.1 |  | 6026 | 92.27 | 0.75038 | 62.085 | 0.0022874 | 60.356 | 1102.1 | 1041.744
6027 | 0.75061 | 92.28 | 62.085 | 0.0022881 | 60.366 | 1102.1 |  | 6027 | 92.28 | 0.75061 | 62.085 | 0.0022881 | 60.366 | 1102.1 | 1041.734
6028 | 0.75084 | 92.29 | 62.085 | 0.0022887 | 60.376 | 1102.1 |  | 6028 | 92.29 | 0.75084 | 62.085 | 0.0022887 | 60.376 | 1102.1 | 1041.724
6029 | 0.75108 | 92.3 | 62.084 | 0.0022894 | 60.386 | 1102.1 |  | 6029 | 92.3 | 0.75108 | 62.084 | 0.0022894 | 60.386 | 1102.1 | 1041.714
6030 | 0.75131 | 92.31 | 62.084 | 0.0022901 | 60.396 | 1102.1 |  | 6030 | 92.31 | 0.75131 | 62.084 | 0.0022901 | 60.396 | 1102.1 | 1041.704
6031 | 0.75154 | 92.32 | 62.084 | 0.0022908 | 60.406 | 1102.1 |  | 6031 | 92.32 | 0.75154 | 62.084 | 0.0022908 | 60.406 | 1102.1 | 1041.694
6032 | 0.75178 | 92.33 | 62.084 | 0.0022914 | 60.416 | 1102.1 |  | 6032 | 92.33 | 0.75178 | 62.084 | 0.0022914 | 60.416 | 1102.1 | 1041.684
6033 | 0.75201 | 92.34 | 62.084 | 0.0022921 | 60.426 | 1102.2 |  | 6033 | 92.34 | 0.75201 | 62.084 | 0.0022921 | 60.426 | 1102.2 | 1041.774
6034 | 0.75224 | 92.35 | 62.084 | 0.0022928 | 60.436 | 1102.2 |  | 6034 | 92.35 | 0.75224 | 62.084 | 0.0022928 | 60.436 | 1102.2 | 1041.764
6035 | 0.75248 | 92.36 | 62.084 | 0.0022934 | 60.446 | 1102.2 |  | 6035 | 92.36 | 0.75248 | 62.084 | 0.0022934 | 60.446 | 1102.2 | 1041.754
6036 | 0.75271 | 92.37 | 62.084 | 0.0022941 | 60.456 | 1102.2 |  | 6036 | 92.37 | 0.75271 | 62.084 | 0.0022941 | 60.456 | 1102.2 | 1041.744
6037 | 0.75295 | 92.38 | 62.084 | 0.0022948 | 60.466 | 1102.2 |  | 6037 | 92.38 | 0.75295 | 62.084 | 0.0022948 | 60.466 | 1102.2 | 1041.734
6038 | 0.75318 | 92.39 | 62.083 | 0.0022955 | 60.476 | 1102.2 |  | 6038 | 92.39 | 0.75318 | 62.083 | 0.0022955 | 60.476 | 1102.2 | 1041.724
6039 | 0.75341 | 92.4 | 62.083 | 0.0022961 | 60.486 | 1102.2 |  | 6039 | 92.4 | 0.75341 | 62.083 | 0.0022961 | 60.486 | 1102.2 | 1041.714
6040 | 0.75365 | 92.41 | 62.083 | 0.0022968 | 60.496 | 1102.2 |  | 6040 | 92.41 | 0.75365 | 62.083 | 0.0022968 | 60.496 | 1102.2 | 1041.704
6041 | 0.75388 | 92.42 | 62.083 | 0.0022975 | 60.506 | 1102.2 |  | 6041 | 92.42 | 0.75388 | 62.083 | 0.0022975 | 60.506 | 1102.2 | 1041.694
6042 | 0.75412 | 92.43 | 62.083 | 0.0022981 | 60.516 | 1102.2 |  | 6042 | 92.43 | 0.75412 | 62.083 | 0.0022981 | 60.516 | 1102.2 | 1041.684
6043 | 0.75435 | 92.44 | 62.083 | 0.0022988 | 60.526 | 1102.2 |  | 6043 | 92.44 | 0.75435 | 62.083 | 0.0022988 | 60.526 | 1102.2 | 1041.674
6044 | 0.75458 | 92.45 | 62.083 | 0.0022995 | 60.536 | 1102.2 |  | 6044 | 92.45 | 0.75458 | 62.083 | 0.0022995 | 60.536 | 1102.2 | 1041.664
6045 | 0.75482 | 92.46 | 62.083 | 0.0023002 | 60.546 | 1102.2 |  | 6045 | 92.46 | 0.75482 | 62.083 | 0.0023002 | 60.546 | 1102.2 | 1041.654
6046 | 0.75505 | 92.47 | 62.082 | 0.0023008 | 60.556 | 1102.2 |  | 6046 | 92.47 | 0.75505 | 62.082 | 0.0023008 | 60.556 | 1102.2 | 1041.644
6047 | 0.75529 | 92.48 | 62.082 | 0.0023015 | 60.566 | 1102.2 |  | 6047 | 92.48 | 0.75529 | 62.082 | 0.0023015 | 60.566 | 1102.2 | 1041.634
6048 | 0.75552 | 92.49 | 62.082 | 0.0023022 | 60.576 | 1102.2 |  | 6048 | 92.49 | 0.75552 | 62.082 | 0.0023022 | 60.576 | 1102.2 | 1041.624
6049 | 0.75576 | 92.5 | 62.082 | 0.0023029 | 60.586 | 1102.2 |  | 6049 | 92.5 | 0.75576 | 62.082 | 0.0023029 | 60.586 | 1102.2 | 1041.614
6050 | 0.75599 | 92.51 | 62.082 | 0.0023035 | 60.596 | 1102.2 |  | 6050 | 92.51 | 0.75599 | 62.082 | 0.0023035 | 60.596 | 1102.2 | 1041.604
6051 | 0.75623 | 92.52 | 62.082 | 0.0023042 | 60.606 | 1102.2 |  | 6051 | 92.52 | 0.75623 | 62.082 | 0.0023042 | 60.606 | 1102.2 | 1041.594
6052 | 0.75646 | 92.53 | 62.082 | 0.0023049 | 60.616 | 1102.2 |  | 6052 | 92.53 | 0.75646 | 62.082 | 0.0023049 | 60.616 | 1102.2 | 1041.584
6053 | 0.75669 | 92.54 | 62.082 | 0.0023056 | 60.626 | 1102.2 |  | 6053 | 92.54 | 0.75669 | 62.082 | 0.0023056 | 60.626 | 1102.2 | 1041.574
6054 | 0.75693 | 92.55 | 62.082 | 0.0023062 | 60.636 | 1102.2 |  | 6054 | 92.55 | 0.75693 | 62.082 | 0.0023062 | 60.636 | 1102.2 | 1041.564
6055 | 0.75716 | 92.56 | 62.081 | 0.0023069 | 60.646 | 1102.2 |  | 6055 | 92.56 | 0.75716 | 62.081 | 0.0023069 | 60.646 | 1102.2 | 1041.554
6056 | 0.7574 | 92.57 | 62.081 | 0.0023076 | 60.656 | 1102.3 |  | 6056 | 92.57 | 0.7574 | 62.081 | 0.0023076 | 60.656 | 1102.3 | 1041.644
6057 | 0.75763 | 92.58 | 62.081 | 0.0023083 | 60.666 | 1102.3 |  | 6057 | 92.58 | 0.75763 | 62.081 | 0.0023083 | 60.666 | 1102.3 | 1041.634
6058 | 0.75787 | 92.59 | 62.081 | 0.0023089 | 60.676 | 1102.3 |  | 6058 | 92.59 | 0.75787 | 62.081 | 0.0023089 | 60.676 | 1102.3 | 1041.624
6059 | 0.75811 | 92.6 | 62.081 | 0.0023096 | 60.686 | 1102.3 |  | 6059 | 92.6 | 0.75811 | 62.081 | 0.0023096 | 60.686 | 1102.3 | 1041.614
6060 | 0.75834 | 92.61 | 62.081 | 0.0023103 | 60.696 | 1102.3 |  | 6060 | 92.61 | 0.75834 | 62.081 | 0.0023103 | 60.696 | 1102.3 | 1041.604
6061 | 0.75858 | 92.62 | 62.081 | 0.002311 | 60.706 | 1102.3 |  | 6061 | 92.62 | 0.75858 | 62.081 | 0.002311 | 60.706 | 1102.3 | 1041.594
6062 | 0.75881 | 92.63 | 62.081 | 0.0023116 | 60.716 | 1102.3 |  | 6062 | 92.63 | 0.75881 | 62.081 | 0.0023116 | 60.716 | 1102.3 | 1041.584
6063 | 0.75905 | 92.64 | 62.081 | 0.0023123 | 60.726 | 1102.3 |  | 6063 | 92.64 | 0.75905 | 62.081 | 0.0023123 | 60.726 | 1102.3 | 1041.574
6064 | 0.75928 | 92.65 | 62.08 | 0.002313 | 60.736 | 1102.3 |  | 6064 | 92.65 | 0.75928 | 62.08 | 0.002313 | 60.736 | 1102.3 | 1041.564
6065 | 0.75952 | 92.66 | 62.08 | 0.0023137 | 60.746 | 1102.3 |  | 6065 | 92.66 | 0.75952 | 62.08 | 0.0023137 | 60.746 | 1102.3 | 1041.554
6066 | 0.75975 | 92.67 | 62.08 | 0.0023144 | 60.756 | 1102.3 |  | 6066 | 92.67 | 0.75975 | 62.08 | 0.0023144 | 60.756 | 1102.3 | 1041.544
6067 | 0.75999 | 92.68 | 62.08 | 0.002315 | 60.766 | 1102.3 |  | 6067 | 92.68 | 0.75999 | 62.08 | 0.002315 | 60.766 | 1102.3 | 1041.534
6068 | 0.76023 | 92.69 | 62.08 | 0.0023157 | 60.776 | 1102.3 |  | 6068 | 92.69 | 0.76023 | 62.08 | 0.0023157 | 60.776 | 1102.3 | 1041.524
6069 | 0.76046 | 92.7 | 62.08 | 0.0023164 | 60.786 | 1102.3 |  | 6069 | 92.7 | 0.76046 | 62.08 | 0.0023164 | 60.786 | 1102.3 | 1041.514
6070 | 0.7607 | 92.71 | 62.08 | 0.0023171 | 60.796 | 1102.3 |  | 6070 | 92.71 | 0.7607 | 62.08 | 0.0023171 | 60.796 | 1102.3 | 1041.504
6071 | 0.76093 | 92.72 | 62.08 | 0.0023177 | 60.806 | 1102.3 |  | 6071 | 92.72 | 0.76093 | 62.08 | 0.0023177 | 60.806 | 1102.3 | 1041.494
6072 | 0.76117 | 92.73 | 62.079 | 0.0023184 | 60.816 | 1102.3 |  | 6072 | 92.73 | 0.76117 | 62.079 | 0.0023184 | 60.816 | 1102.3 | 1041.484
6073 | 0.7614 | 92.74 | 62.079 | 0.0023191 | 60.826 | 1102.3 |  | 6073 | 92.74 | 0.7614 | 62.079 | 0.0023191 | 60.826 | 1102.3 | 1041.474
6074 | 0.76164 | 92.75 | 62.079 | 0.0023198 | 60.836 | 1102.3 |  | 6074 | 92.75 | 0.76164 | 62.079 | 0.0023198 | 60.836 | 1102.3 | 1041.464
6075 | 0.76188 | 92.76 | 62.079 | 0.0023205 | 60.846 | 1102.3 |  | 6075 | 92.76 | 0.76188 | 62.079 | 0.0023205 | 60.846 | 1102.3 | 1041.454
6076 | 0.76211 | 92.77 | 62.079 | 0.0023211 | 60.856 | 1102.3 |  | 6076 | 92.77 | 0.76211 | 62.079 | 0.0023211 | 60.856 | 1102.3 | 1041.444
6077 | 0.76235 | 92.78 | 62.079 | 0.0023218 | 60.866 | 1102.3 |  | 6077 | 92.78 | 0.76235 | 62.079 | 0.0023218 | 60.866 | 1102.3 | 1041.434
6078 | 0.76259 | 92.79 | 62.079 | 0.0023225 | 60.876 | 1102.3 |  | 6078 | 92.79 | 0.76259 | 62.079 | 0.0023225 | 60.876 | 1102.3 | 1041.424
6079 | 0.76282 | 92.8 | 62.079 | 0.0023232 | 60.886 | 1102.3 |  | 6079 | 92.8 | 0.76282 | 62.079 | 0.0023232 | 60.886 | 1102.3 | 1041.414
6080 | 0.76306 | 92.81 | 62.079 | 0.0023238 | 60.896 | 1102.4 |  | 6080 | 92.81 | 0.76306 | 62.079 | 0.0023238 | 60.896 | 1102.4 | 1041.504
6081 | 0.7633 | 92.82 | 62.078 | 0.0023245 | 60.906 | 1102.4 |  | 6081 | 92.82 | 0.7633 | 62.078 | 0.0023245 | 60.906 | 1102.4 | 1041.494
6082 | 0.76353 | 92.83 | 62.078 | 0.0023252 | 60.916 | 1102.4 |  | 6082 | 92.83 | 0.76353 | 62.078 | 0.0023252 | 60.916 | 1102.4 | 1041.484
6083 | 0.76377 | 92.84 | 62.078 | 0.0023259 | 60.926 | 1102.4 |  | 6083 | 92.84 | 0.76377 | 62.078 | 0.0023259 | 60.926 | 1102.4 | 1041.474
6084 | 0.76401 | 92.85 | 62.078 | 0.0023266 | 60.936 | 1102.4 |  | 6084 | 92.85 | 0.76401 | 62.078 | 0.0023266 | 60.936 | 1102.4 | 1041.464
6085 | 0.76424 | 92.86 | 62.078 | 0.0023272 | 60.946 | 1102.4 |  | 6085 | 92.86 | 0.76424 | 62.078 | 0.0023272 | 60.946 | 1102.4 | 1041.454
6086 | 0.76448 | 92.87 | 62.078 | 0.0023279 | 60.956 | 1102.4 |  | 6086 | 92.87 | 0.76448 | 62.078 | 0.0023279 | 60.956 | 1102.4 | 1041.444
6087 | 0.76472 | 92.88 | 62.078 | 0.0023286 | 60.966 | 1102.4 |  | 6087 | 92.88 | 0.76472 | 62.078 | 0.0023286 | 60.966 | 1102.4 | 1041.434
6088 | 0.76495 | 92.89 | 62.078 | 0.0023293 | 60.976 | 1102.4 |  | 6088 | 92.89 | 0.76495 | 62.078 | 0.0023293 | 60.976 | 1102.4 | 1041.424
6089 | 0.76519 | 92.9 | 62.078 | 0.00233 | 60.986 | 1102.4 |  | 6089 | 92.9 | 0.76519 | 62.078 | 0.00233 | 60.986 | 1102.4 | 1041.414
6090 | 0.76543 | 92.91 | 62.077 | 0.0023306 | 60.995 | 1102.4 |  | 6090 | 92.91 | 0.76543 | 62.077 | 0.0023306 | 60.995 | 1102.4 | 1041.405
6091 | 0.76567 | 92.92 | 62.077 | 0.0023313 | 61.005 | 1102.4 |  | 6091 | 92.92 | 0.76567 | 62.077 | 0.0023313 | 61.005 | 1102.4 | 1041.395
6092 | 0.7659 | 92.93 | 62.077 | 0.002332 | 61.015 | 1102.4 |  | 6092 | 92.93 | 0.7659 | 62.077 | 0.002332 | 61.015 | 1102.4 | 1041.385
6093 | 0.76614 | 92.94 | 62.077 | 0.0023327 | 61.025 | 1102.4 |  | 6093 | 92.94 | 0.76614 | 62.077 | 0.0023327 | 61.025 | 1102.4 | 1041.375
6094 | 0.76638 | 92.95 | 62.077 | 0.0023334 | 61.035 | 1102.4 |  | 6094 | 92.95 | 0.76638 | 62.077 | 0.0023334 | 61.035 | 1102.4 | 1041.365
6095 | 0.76662 | 92.96 | 62.077 | 0.0023341 | 61.045 | 1102.4 |  | 6095 | 92.96 | 0.76662 | 62.077 | 0.0023341 | 61.045 | 1102.4 | 1041.355
6096 | 0.76685 | 92.97 | 62.077 | 0.0023347 | 61.055 | 1102.4 |  | 6096 | 92.97 | 0.76685 | 62.077 | 0.0023347 | 61.055 | 1102.4 | 1041.345
6097 | 0.76709 | 92.98 | 62.077 | 0.0023354 | 61.065 | 1102.4 |  | 6097 | 92.98 | 0.76709 | 62.077 | 0.0023354 | 61.065 | 1102.4 | 1041.335
6098 | 0.76733 | 92.99 | 62.076 | 0.0023361 | 61.075 | 1102.4 |  | 6098 | 92.99 | 0.76733 | 62.076 | 0.0023361 | 61.075 | 1102.4 | 1041.325
6099 | 0.76757 | 93 | 62.076 | 0.0023368 | 61.085 | 1102.4 |  | 6099 | 93 | 0.76757 | 62.076 | 0.0023368 | 61.085 | 1102.4 | 1041.315
6100 | 0.7678 | 93.01 | 62.076 | 0.0023375 | 61.095 | 1102.4 |  | 6100 | 93.01 | 0.7678 | 62.076 | 0.0023375 | 61.095 | 1102.4 | 1041.305
6101 | 0.76804 | 93.02 | 62.076 | 0.0023382 | 61.105 | 1102.4 |  | 6101 | 93.02 | 0.76804 | 62.076 | 0.0023382 | 61.105 | 1102.4 | 1041.295
6102 | 0.76828 | 93.03 | 62.076 | 0.0023388 | 61.115 | 1102.4 |  | 6102 | 93.03 | 0.76828 | 62.076 | 0.0023388 | 61.115 | 1102.4 | 1041.285
6103 | 0.76852 | 93.04 | 62.076 | 0.0023395 | 61.125 | 1102.5 |  | 6103 | 93.04 | 0.76852 | 62.076 | 0.0023395 | 61.125 | 1102.5 | 1041.375
6104 | 0.76876 | 93.05 | 62.076 | 0.0023402 | 61.135 | 1102.5 |  | 6104 | 93.05 | 0.76876 | 62.076 | 0.0023402 | 61.135 | 1102.5 | 1041.365
6105 | 0.76899 | 93.06 | 62.076 | 0.0023409 | 61.145 | 1102.5 |  | 6105 | 93.06 | 0.76899 | 62.076 | 0.0023409 | 61.145 | 1102.5 | 1041.355
6106 | 0.76923 | 93.07 | 62.076 | 0.0023416 | 61.155 | 1102.5 |  | 6106 | 93.07 | 0.76923 | 62.076 | 0.0023416 | 61.155 | 1102.5 | 1041.345
6107 | 0.76947 | 93.08 | 62.075 | 0.0023423 | 61.165 | 1102.5 |  | 6107 | 93.08 | 0.76947 | 62.075 | 0.0023423 | 61.165 | 1102.5 | 1041.335
6108 | 0.76971 | 93.09 | 62.075 | 0.0023429 | 61.175 | 1102.5 |  | 6108 | 93.09 | 0.76971 | 62.075 | 0.0023429 | 61.175 | 1102.5 | 1041.325
6109 | 0.76995 | 93.1 | 62.075 | 0.0023436 | 61.185 | 1102.5 |  | 6109 | 93.1 | 0.76995 | 62.075 | 0.0023436 | 61.185 | 1102.5 | 1041.315
6110 | 0.77019 | 93.11 | 62.075 | 0.0023443 | 61.195 | 1102.5 |  | 6110 | 93.11 | 0.77019 | 62.075 | 0.0023443 | 61.195 | 1102.5 | 1041.305
6111 | 0.77042 | 93.12 | 62.075 | 0.002345 | 61.205 | 1102.5 |  | 6111 | 93.12 | 0.77042 | 62.075 | 0.002345 | 61.205 | 1102.5 | 1041.295
6112 | 0.77066 | 93.13 | 62.075 | 0.0023457 | 61.215 | 1102.5 |  | 6112 | 93.13 | 0.77066 | 62.075 | 0.0023457 | 61.215 | 1102.5 | 1041.285
6113 | 0.7709 | 93.14 | 62.075 | 0.0023464 | 61.225 | 1102.5 |  | 6113 | 93.14 | 0.7709 | 62.075 | 0.0023464 | 61.225 | 1102.5 | 1041.275
6114 | 0.77114 | 93.15 | 62.075 | 0.002347 | 61.235 | 1102.5 |  | 6114 | 93.15 | 0.77114 | 62.075 | 0.002347 | 61.235 | 1102.5 | 1041.265
6115 | 0.77138 | 93.16 | 62.074 | 0.0023477 | 61.245 | 1102.5 |  | 6115 | 93.16 | 0.77138 | 62.074 | 0.0023477 | 61.245 | 1102.5 | 1041.255
6116 | 0.77162 | 93.17 | 62.074 | 0.0023484 | 61.255 | 1102.5 |  | 6116 | 93.17 | 0.77162 | 62.074 | 0.0023484 | 61.255 | 1102.5 | 1041.245
6117 | 0.77186 | 93.18 | 62.074 | 0.0023491 | 61.265 | 1102.5 |  | 6117 | 93.18 | 0.77186 | 62.074 | 0.0023491 | 61.265 | 1102.5 | 1041.235
6118 | 0.7721 | 93.19 | 62.074 | 0.0023498 | 61.275 | 1102.5 |  | 6118 | 93.19 | 0.7721 | 62.074 | 0.0023498 | 61.275 | 1102.5 | 1041.225
6119 | 0.77233 | 93.2 | 62.074 | 0.0023505 | 61.285 | 1102.5 |  | 6119 | 93.2 | 0.77233 | 62.074 | 0.0023505 | 61.285 | 1102.5 | 1041.215
6120 | 0.77257 | 93.21 | 62.074 | 0.0023512 | 61.295 | 1102.5 |  | 6120 | 93.21 | 0.77257 | 62.074 | 0.0023512 | 61.295 | 1102.5 | 1041.205
6121 | 0.77281 | 93.22 | 62.074 | 0.0023518 | 61.305 | 1102.5 |  | 6121 | 93.22 | 0.77281 | 62.074 | 0.0023518 | 61.305 | 1102.5 | 1041.195
6122 | 0.77305 | 93.23 | 62.074 | 0.0023525 | 61.315 | 1102.5 |  | 6122 | 93.23 | 0.77305 | 62.074 | 0.0023525 | 61.315 | 1102.5 | 1041.185
6123 | 0.77329 | 93.24 | 62.074 | 0.0023532 | 61.325 | 1102.5 |  | 6123 | 93.24 | 0.77329 | 62.074 | 0.0023532 | 61.325 | 1102.5 | 1041.175
6124 | 0.77353 | 93.25 | 62.073 | 0.0023539 | 61.335 | 1102.5 |  | 6124 | 93.25 | 0.77353 | 62.073 | 0.0023539 | 61.335 | 1102.5 | 1041.165
6125 | 0.77377 | 93.26 | 62.073 | 0.0023546 | 61.345 | 1102.5 |  | 6125 | 93.26 | 0.77377 | 62.073 | 0.0023546 | 61.345 | 1102.5 | 1041.155
6126 | 0.77401 | 93.27 | 62.073 | 0.0023553 | 61.355 | 1102.6 |  | 6126 | 93.27 | 0.77401 | 62.073 | 0.0023553 | 61.355 | 1102.6 | 1041.245
6127 | 0.77425 | 93.28 | 62.073 | 0.002356 | 61.365 | 1102.6 |  | 6127 | 93.28 | 0.77425 | 62.073 | 0.002356 | 61.365 | 1102.6 | 1041.235
6128 | 0.77449 | 93.29 | 62.073 | 0.0023567 | 61.375 | 1102.6 |  | 6128 | 93.29 | 0.77449 | 62.073 | 0.0023567 | 61.375 | 1102.6 | 1041.225
6129 | 0.77473 | 93.3 | 62.073 | 0.0023573 | 61.385 | 1102.6 |  | 6129 | 93.3 | 0.77473 | 62.073 | 0.0023573 | 61.385 | 1102.6 | 1041.215
6130 | 0.77497 | 93.31 | 62.073 | 0.002358 | 61.395 | 1102.6 |  | 6130 | 93.31 | 0.77497 | 62.073 | 0.002358 | 61.395 | 1102.6 | 1041.205
6131 | 0.77521 | 93.32 | 62.073 | 0.0023587 | 61.405 | 1102.6 |  | 6131 | 93.32 | 0.77521 | 62.073 | 0.0023587 | 61.405 | 1102.6 | 1041.195
6132 | 0.77545 | 93.33 | 62.073 | 0.0023594 | 61.415 | 1102.6 |  | 6132 | 93.33 | 0.77545 | 62.073 | 0.0023594 | 61.415 | 1102.6 | 1041.185
6133 | 0.77569 | 93.34 | 62.072 | 0.0023601 | 61.425 | 1102.6 |  | 6133 | 93.34 | 0.77569 | 62.072 | 0.0023601 | 61.425 | 1102.6 | 1041.175
6134 | 0.77593 | 93.35 | 62.072 | 0.0023608 | 61.435 | 1102.6 |  | 6134 | 93.35 | 0.77593 | 62.072 | 0.0023608 | 61.435 | 1102.6 | 1041.165
6135 | 0.77617 | 93.36 | 62.072 | 0.0023615 | 61.445 | 1102.6 |  | 6135 | 93.36 | 0.77617 | 62.072 | 0.0023615 | 61.445 | 1102.6 | 1041.155
6136 | 0.77641 | 93.37 | 62.072 | 0.0023622 | 61.455 | 1102.6 |  | 6136 | 93.37 | 0.77641 | 62.072 | 0.0023622 | 61.455 | 1102.6 | 1041.145
6137 | 0.77665 | 93.38 | 62.072 | 0.0023629 | 61.465 | 1102.6 |  | 6137 | 93.38 | 0.77665 | 62.072 | 0.0023629 | 61.465 | 1102.6 | 1041.135
6138 | 0.77689 | 93.39 | 62.072 | 0.0023635 | 61.475 | 1102.6 |  | 6138 | 93.39 | 0.77689 | 62.072 | 0.0023635 | 61.475 | 1102.6 | 1041.125
6139 | 0.77713 | 93.4 | 62.072 | 0.0023642 | 61.485 | 1102.6 |  | 6139 | 93.4 | 0.77713 | 62.072 | 0.0023642 | 61.485 | 1102.6 | 1041.115
6140 | 0.77737 | 93.41 | 62.072 | 0.0023649 | 61.495 | 1102.6 |  | 6140 | 93.41 | 0.77737 | 62.072 | 0.0023649 | 61.495 | 1102.6 | 1041.105
6141 | 0.77761 | 93.42 | 62.071 | 0.0023656 | 61.505 | 1102.6 |  | 6141 | 93.42 | 0.77761 | 62.071 | 0.0023656 | 61.505 | 1102.6 | 1041.095
6142 | 0.77785 | 93.43 | 62.071 | 0.0023663 | 61.515 | 1102.6 |  | 6142 | 93.43 | 0.77785 | 62.071 | 0.0023663 | 61.515 | 1102.6 | 1041.085
6143 | 0.77809 | 93.44 | 62.071 | 0.002367 | 61.525 | 1102.6 |  | 6143 | 93.44 | 0.77809 | 62.071 | 0.002367 | 61.525 | 1102.6 | 1041.075
6144 | 0.77833 | 93.45 | 62.071 | 0.0023677 | 61.535 | 1102.6 |  | 6144 | 93.45 | 0.77833 | 62.071 | 0.0023677 | 61.535 | 1102.6 | 1041.065
6145 | 0.77857 | 93.46 | 62.071 | 0.0023684 | 61.545 | 1102.6 |  | 6145 | 93.46 | 0.77857 | 62.071 | 0.0023684 | 61.545 | 1102.6 | 1041.055
6146 | 0.77881 | 93.47 | 62.071 | 0.0023691 | 61.555 | 1102.6 |  | 6146 | 93.47 | 0.77881 | 62.071 | 0.0023691 | 61.555 | 1102.6 | 1041.045
6147 | 0.77905 | 93.48 | 62.071 | 0.0023698 | 61.565 | 1102.6 |  | 6147 | 93.48 | 0.77905 | 62.071 | 0.0023698 | 61.565 | 1102.6 | 1041.035
6148 | 0.77929 | 93.49 | 62.071 | 0.0023704 | 61.575 | 1102.6 |  | 6148 | 93.49 | 0.77929 | 62.071 | 0.0023704 | 61.575 | 1102.6 | 1041.025
6149 | 0.77954 | 93.5 | 62.071 | 0.0023711 | 61.585 | 1102.7 |  | 6149 | 93.5 | 0.77954 | 62.071 | 0.0023711 | 61.585 | 1102.7 | 1041.115
6150 | 0.77978 | 93.51 | 62.07 | 0.0023718 | 61.595 | 1102.7 |  | 6150 | 93.51 | 0.77978 | 62.07 | 0.0023718 | 61.595 | 1102.7 | 1041.105
6151 | 0.78002 | 93.52 | 62.07 | 0.0023725 | 61.605 | 1102.7 |  | 6151 | 93.52 | 0.78002 | 62.07 | 0.0023725 | 61.605 | 1102.7 | 1041.095
6152 | 0.78026 | 93.53 | 62.07 | 0.0023732 | 61.615 | 1102.7 |  | 6152 | 93.53 | 0.78026 | 62.07 | 0.0023732 | 61.615 | 1102.7 | 1041.085
6153 | 0.7805 | 93.54 | 62.07 | 0.0023739 | 61.625 | 1102.7 |  | 6153 | 93.54 | 0.7805 | 62.07 | 0.0023739 | 61.625 | 1102.7 | 1041.075
6154 | 0.78074 | 93.55 | 62.07 | 0.0023746 | 61.635 | 1102.7 |  | 6154 | 93.55 | 0.78074 | 62.07 | 0.0023746 | 61.635 | 1102.7 | 1041.065
6155 | 0.78098 | 93.56 | 62.07 | 0.0023753 | 61.645 | 1102.7 |  | 6155 | 93.56 | 0.78098 | 62.07 | 0.0023753 | 61.645 | 1102.7 | 1041.055
6156 | 0.78122 | 93.57 | 62.07 | 0.002376 | 61.655 | 1102.7 |  | 6156 | 93.57 | 0.78122 | 62.07 | 0.002376 | 61.655 | 1102.7 | 1041.045
6157 | 0.78147 | 93.58 | 62.07 | 0.0023767 | 61.665 | 1102.7 |  | 6157 | 93.58 | 0.78147 | 62.07 | 0.0023767 | 61.665 | 1102.7 | 1041.035
6158 | 0.78171 | 93.59 | 62.069 | 0.0023774 | 61.675 | 1102.7 |  | 6158 | 93.59 | 0.78171 | 62.069 | 0.0023774 | 61.675 | 1102.7 | 1041.025
6159 | 0.78195 | 93.6 | 62.069 | 0.0023781 | 61.685 | 1102.7 |  | 6159 | 93.6 | 0.78195 | 62.069 | 0.0023781 | 61.685 | 1102.7 | 1041.015
6160 | 0.78219 | 93.61 | 62.069 | 0.0023787 | 61.695 | 1102.7 |  | 6160 | 93.61 | 0.78219 | 62.069 | 0.0023787 | 61.695 | 1102.7 | 1041.005
6161 | 0.78243 | 93.62 | 62.069 | 0.0023794 | 61.705 | 1102.7 |  | 6161 | 93.62 | 0.78243 | 62.069 | 0.0023794 | 61.705 | 1102.7 | 1040.995
6162 | 0.78267 | 93.63 | 62.069 | 0.0023801 | 61.715 | 1102.7 |  | 6162 | 93.63 | 0.78267 | 62.069 | 0.0023801 | 61.715 | 1102.7 | 1040.985
6163 | 0.78292 | 93.64 | 62.069 | 0.0023808 | 61.725 | 1102.7 |  | 6163 | 93.64 | 0.78292 | 62.069 | 0.0023808 | 61.725 | 1102.7 | 1040.975
6164 | 0.78316 | 93.65 | 62.069 | 0.0023815 | 61.735 | 1102.7 |  | 6164 | 93.65 | 0.78316 | 62.069 | 0.0023815 | 61.735 | 1102.7 | 1040.965
6165 | 0.7834 | 93.66 | 62.069 | 0.0023822 | 61.745 | 1102.7 |  | 6165 | 93.66 | 0.7834 | 62.069 | 0.0023822 | 61.745 | 1102.7 | 1040.955
6166 | 0.78364 | 93.67 | 62.069 | 0.0023829 | 61.755 | 1102.7 |  | 6166 | 93.67 | 0.78364 | 62.069 | 0.0023829 | 61.755 | 1102.7 | 1040.945
6167 | 0.78388 | 93.68 | 62.068 | 0.0023836 | 61.765 | 1102.7 |  | 6167 | 93.68 | 0.78388 | 62.068 | 0.0023836 | 61.765 | 1102.7 | 1040.935
6168 | 0.78413 | 93.69 | 62.068 | 0.0023843 | 61.775 | 1102.7 |  | 6168 | 93.69 | 0.78413 | 62.068 | 0.0023843 | 61.775 | 1102.7 | 1040.925
6169 | 0.78437 | 93.7 | 62.068 | 0.002385 | 61.785 | 1102.7 |  | 6169 | 93.7 | 0.78437 | 62.068 | 0.002385 | 61.785 | 1102.7 | 1040.915
6170 | 0.78461 | 93.71 | 62.068 | 0.0023857 | 61.795 | 1102.7 |  | 6170 | 93.71 | 0.78461 | 62.068 | 0.0023857 | 61.795 | 1102.7 | 1040.905
6171 | 0.78485 | 93.72 | 62.068 | 0.0023864 | 61.805 | 1102.7 |  | 6171 | 93.72 | 0.78485 | 62.068 | 0.0023864 | 61.805 | 1102.7 | 1040.895
6172 | 0.7851 | 93.73 | 62.068 | 0.0023871 | 61.815 | 1102.7 |  | 6172 | 93.73 | 0.7851 | 62.068 | 0.0023871 | 61.815 | 1102.7 | 1040.885
6173 | 0.78534 | 93.74 | 62.068 | 0.0023878 | 61.825 | 1102.8 |  | 6173 | 93.74 | 0.78534 | 62.068 | 0.0023878 | 61.825 | 1102.8 | 1040.975
6174 | 0.78558 | 93.75 | 62.068 | 0.0023885 | 61.835 | 1102.8 |  | 6174 | 93.75 | 0.78558 | 62.068 | 0.0023885 | 61.835 | 1102.8 | 1040.965
6175 | 0.78582 | 93.76 | 62.067 | 0.0023892 | 61.845 | 1102.8 |  | 6175 | 93.76 | 0.78582 | 62.067 | 0.0023892 | 61.845 | 1102.8 | 1040.955
6176 | 0.78607 | 93.77 | 62.067 | 0.0023899 | 61.855 | 1102.8 |  | 6176 | 93.77 | 0.78607 | 62.067 | 0.0023899 | 61.855 | 1102.8 | 1040.945
6177 | 0.78631 | 93.78 | 62.067 | 0.0023906 | 61.865 | 1102.8 |  | 6177 | 93.78 | 0.78631 | 62.067 | 0.0023906 | 61.865 | 1102.8 | 1040.935
6178 | 0.78655 | 93.79 | 62.067 | 0.0023913 | 61.875 | 1102.8 |  | 6178 | 93.79 | 0.78655 | 62.067 | 0.0023913 | 61.875 | 1102.8 | 1040.925
6179 | 0.78679 | 93.8 | 62.067 | 0.002392 | 61.885 | 1102.8 |  | 6179 | 93.8 | 0.78679 | 62.067 | 0.002392 | 61.885 | 1102.8 | 1040.915
6180 | 0.78704 | 93.81 | 62.067 | 0.0023926 | 61.895 | 1102.8 |  | 6180 | 93.81 | 0.78704 | 62.067 | 0.0023926 | 61.895 | 1102.8 | 1040.905
6181 | 0.78728 | 93.82 | 62.067 | 0.0023933 | 61.905 | 1102.8 |  | 6181 | 93.82 | 0.78728 | 62.067 | 0.0023933 | 61.905 | 1102.8 | 1040.895
6182 | 0.78752 | 93.83 | 62.067 | 0.002394 | 61.915 | 1102.8 |  | 6182 | 93.83 | 0.78752 | 62.067 | 0.002394 | 61.915 | 1102.8 | 1040.885
6183 | 0.78777 | 93.84 | 62.067 | 0.0023947 | 61.925 | 1102.8 |  | 6183 | 93.84 | 0.78777 | 62.067 | 0.0023947 | 61.925 | 1102.8 | 1040.875
6184 | 0.78801 | 93.85 | 62.066 | 0.0023954 | 61.935 | 1102.8 |  | 6184 | 93.85 | 0.78801 | 62.066 | 0.0023954 | 61.935 | 1102.8 | 1040.865
6185 | 0.78825 | 93.86 | 62.066 | 0.0023961 | 61.945 | 1102.8 |  | 6185 | 93.86 | 0.78825 | 62.066 | 0.0023961 | 61.945 | 1102.8 | 1040.855
6186 | 0.7885 | 93.87 | 62.066 | 0.0023968 | 61.955 | 1102.8 |  | 6186 | 93.87 | 0.7885 | 62.066 | 0.0023968 | 61.955 | 1102.8 | 1040.845
6187 | 0.78874 | 93.88 | 62.066 | 0.0023975 | 61.965 | 1102.8 |  | 6187 | 93.88 | 0.78874 | 62.066 | 0.0023975 | 61.965 | 1102.8 | 1040.835
6188 | 0.78898 | 93.89 | 62.066 | 0.0023982 | 61.975 | 1102.8 |  | 6188 | 93.89 | 0.78898 | 62.066 | 0.0023982 | 61.975 | 1102.8 | 1040.825
6189 | 0.78923 | 93.9 | 62.066 | 0.0023989 | 61.985 | 1102.8 |  | 6189 | 93.9 | 0.78923 | 62.066 | 0.0023989 | 61.985 | 1102.8 | 1040.815
6190 | 0.78947 | 93.91 | 62.066 | 0.0023996 | 61.994 | 1102.8 |  | 6190 | 93.91 | 0.78947 | 62.066 | 0.0023996 | 61.994 | 1102.8 | 1040.806
6191 | 0.78971 | 93.92 | 62.066 | 0.0024003 | 62.004 | 1102.8 |  | 6191 | 93.92 | 0.78971 | 62.066 | 0.0024003 | 62.004 | 1102.8 | 1040.796
6192 | 0.78996 | 93.93 | 62.065 | 0.002401 | 62.014 | 1102.8 |  | 6192 | 93.93 | 0.78996 | 62.065 | 0.002401 | 62.014 | 1102.8 | 1040.786
6193 | 0.7902 | 93.94 | 62.065 | 0.0024017 | 62.024 | 1102.8 |  | 6193 | 93.94 | 0.7902 | 62.065 | 0.0024017 | 62.024 | 1102.8 | 1040.776
6194 | 0.79045 | 93.95 | 62.065 | 0.0024024 | 62.034 | 1102.8 |  | 6194 | 93.95 | 0.79045 | 62.065 | 0.0024024 | 62.034 | 1102.8 | 1040.766
6195 | 0.79069 | 93.96 | 62.065 | 0.0024031 | 62.044 | 1102.8 |  | 6195 | 93.96 | 0.79069 | 62.065 | 0.0024031 | 62.044 | 1102.8 | 1040.756
6196 | 0.79093 | 93.97 | 62.065 | 0.0024038 | 62.054 | 1102.9 |  | 6196 | 93.97 | 0.79093 | 62.065 | 0.0024038 | 62.054 | 1102.9 | 1040.846
6197 | 0.79118 | 93.98 | 62.065 | 0.0024045 | 62.064 | 1102.9 |  | 6197 | 93.98 | 0.79118 | 62.065 | 0.0024045 | 62.064 | 1102.9 | 1040.836
6198 | 0.79142 | 93.99 | 62.065 | 0.0024052 | 62.074 | 1102.9 |  | 6198 | 93.99 | 0.79142 | 62.065 | 0.0024052 | 62.074 | 1102.9 | 1040.826
6199 | 0.79167 | 94 | 62.065 | 0.0024059 | 62.084 | 1102.9 |  | 6199 | 94 | 0.79167 | 62.065 | 0.0024059 | 62.084 | 1102.9 | 1040.816
6200 | 0.79191 | 94.01 | 62.065 | 0.0024066 | 62.094 | 1102.9 |  | 6200 | 94.01 | 0.79191 | 62.065 | 0.0024066 | 62.094 | 1102.9 | 1040.806
6201 | 0.79215 | 94.02 | 62.064 | 0.0024073 | 62.104 | 1102.9 |  | 6201 | 94.02 | 0.79215 | 62.064 | 0.0024073 | 62.104 | 1102.9 | 1040.796
6202 | 0.7924 | 94.03 | 62.064 | 0.002408 | 62.114 | 1102.9 |  | 6202 | 94.03 | 0.7924 | 62.064 | 0.002408 | 62.114 | 1102.9 | 1040.786
6203 | 0.79264 | 94.04 | 62.064 | 0.0024087 | 62.124 | 1102.9 |  | 6203 | 94.04 | 0.79264 | 62.064 | 0.0024087 | 62.124 | 1102.9 | 1040.776
6204 | 0.79289 | 94.05 | 62.064 | 0.0024094 | 62.134 | 1102.9 |  | 6204 | 94.05 | 0.79289 | 62.064 | 0.0024094 | 62.134 | 1102.9 | 1040.766
6205 | 0.79313 | 94.06 | 62.064 | 0.0024101 | 62.144 | 1102.9 |  | 6205 | 94.06 | 0.79313 | 62.064 | 0.0024101 | 62.144 | 1102.9 | 1040.756
6206 | 0.79338 | 94.07 | 62.064 | 0.0024108 | 62.154 | 1102.9 |  | 6206 | 94.07 | 0.79338 | 62.064 | 0.0024108 | 62.154 | 1102.9 | 1040.746
6207 | 0.79362 | 94.08 | 62.064 | 0.0024115 | 62.164 | 1102.9 |  | 6207 | 94.08 | 0.79362 | 62.064 | 0.0024115 | 62.164 | 1102.9 | 1040.736
6208 | 0.79387 | 94.09 | 62.064 | 0.0024122 | 62.174 | 1102.9 |  | 6208 | 94.09 | 0.79387 | 62.064 | 0.0024122 | 62.174 | 1102.9 | 1040.726
6209 | 0.79411 | 94.1 | 62.063 | 0.0024129 | 62.184 | 1102.9 |  | 6209 | 94.1 | 0.79411 | 62.063 | 0.0024129 | 62.184 | 1102.9 | 1040.716
6210 | 0.79436 | 94.11 | 62.063 | 0.0024136 | 62.194 | 1102.9 |  | 6210 | 94.11 | 0.79436 | 62.063 | 0.0024136 | 62.194 | 1102.9 | 1040.706
6211 | 0.7946 | 94.12 | 62.063 | 0.0024143 | 62.204 | 1102.9 |  | 6211 | 94.12 | 0.7946 | 62.063 | 0.0024143 | 62.204 | 1102.9 | 1040.696
6212 | 0.79485 | 94.13 | 62.063 | 0.002415 | 62.214 | 1102.9 |  | 6212 | 94.13 | 0.79485 | 62.063 | 0.002415 | 62.214 | 1102.9 | 1040.686
6213 | 0.79509 | 94.14 | 62.063 | 0.0024157 | 62.224 | 1102.9 |  | 6213 | 94.14 | 0.79509 | 62.063 | 0.0024157 | 62.224 | 1102.9 | 1040.676
6214 | 0.79534 | 94.15 | 62.063 | 0.0024164 | 62.234 | 1102.9 |  | 6214 | 94.15 | 0.79534 | 62.063 | 0.0024164 | 62.234 | 1102.9 | 1040.666
6215 | 0.79558 | 94.16 | 62.063 | 0.0024171 | 62.244 | 1102.9 |  | 6215 | 94.16 | 0.79558 | 62.063 | 0.0024171 | 62.244 | 1102.9 | 1040.656
6216 | 0.79583 | 94.17 | 62.063 | 0.0024178 | 62.254 | 1102.9 |  | 6216 | 94.17 | 0.79583 | 62.063 | 0.0024178 | 62.254 | 1102.9 | 1040.646
6217 | 0.79607 | 94.18 | 62.063 | 0.0024185 | 62.264 | 1102.9 |  | 6217 | 94.18 | 0.79607 | 62.063 | 0.0024185 | 62.264 | 1102.9 | 1040.636
6218 | 0.79632 | 94.19 | 62.062 | 0.0024192 | 62.274 | 1102.9 |  | 6218 | 94.19 | 0.79632 | 62.062 | 0.0024192 | 62.274 | 1102.9 | 1040.626
6219 | 0.79656 | 94.2 | 62.062 | 0.0024199 | 62.284 | 1103 |  | 6219 | 94.2 | 0.79656 | 62.062 | 0.0024199 | 62.284 | 1103 | 1040.716
6220 | 0.79681 | 94.21 | 62.062 | 0.0024207 | 62.294 | 1103 |  | 6220 | 94.21 | 0.79681 | 62.062 | 0.0024207 | 62.294 | 1103 | 1040.706
6221 | 0.79706 | 94.22 | 62.062 | 0.0024214 | 62.304 | 1103 |  | 6221 | 94.22 | 0.79706 | 62.062 | 0.0024214 | 62.304 | 1103 | 1040.696
6222 | 0.7973 | 94.23 | 62.062 | 0.0024221 | 62.314 | 1103 |  | 6222 | 94.23 | 0.7973 | 62.062 | 0.0024221 | 62.314 | 1103 | 1040.686
6223 | 0.79755 | 94.24 | 62.062 | 0.0024228 | 62.324 | 1103 |  | 6223 | 94.24 | 0.79755 | 62.062 | 0.0024228 | 62.324 | 1103 | 1040.676
6224 | 0.79779 | 94.25 | 62.062 | 0.0024235 | 62.334 | 1103 |  | 6224 | 94.25 | 0.79779 | 62.062 | 0.0024235 | 62.334 | 1103 | 1040.666
6225 | 0.79804 | 94.26 | 62.062 | 0.0024242 | 62.344 | 1103 |  | 6225 | 94.26 | 0.79804 | 62.062 | 0.0024242 | 62.344 | 1103 | 1040.656
6226 | 0.79828 | 94.27 | 62.061 | 0.0024249 | 62.354 | 1103 |  | 6226 | 94.27 | 0.79828 | 62.061 | 0.0024249 | 62.354 | 1103 | 1040.646
6227 | 0.79853 | 94.28 | 62.061 | 0.0024256 | 62.364 | 1103 |  | 6227 | 94.28 | 0.79853 | 62.061 | 0.0024256 | 62.364 | 1103 | 1040.636
6228 | 0.79878 | 94.29 | 62.061 | 0.0024263 | 62.374 | 1103 |  | 6228 | 94.29 | 0.79878 | 62.061 | 0.0024263 | 62.374 | 1103 | 1040.626
6229 | 0.79902 | 94.3 | 62.061 | 0.002427 | 62.384 | 1103 |  | 6229 | 94.3 | 0.79902 | 62.061 | 0.002427 | 62.384 | 1103 | 1040.616
6230 | 0.79927 | 94.31 | 62.061 | 0.0024277 | 62.394 | 1103 |  | 6230 | 94.31 | 0.79927 | 62.061 | 0.0024277 | 62.394 | 1103 | 1040.606
6231 | 0.79952 | 94.32 | 62.061 | 0.0024284 | 62.404 | 1103 |  | 6231 | 94.32 | 0.79952 | 62.061 | 0.0024284 | 62.404 | 1103 | 1040.596
6232 | 0.79976 | 94.33 | 62.061 | 0.0024291 | 62.414 | 1103 |  | 6232 | 94.33 | 0.79976 | 62.061 | 0.0024291 | 62.414 | 1103 | 1040.586
6233 | 0.80001 | 94.34 | 62.061 | 0.0024298 | 62.424 | 1103 |  | 6233 | 94.34 | 0.80001 | 62.061 | 0.0024298 | 62.424 | 1103 | 1040.576
6234 | 0.80025 | 94.35 | 62.061 | 0.0024305 | 62.434 | 1103 |  | 6234 | 94.35 | 0.80025 | 62.061 | 0.0024305 | 62.434 | 1103 | 1040.566
6235 | 0.8005 | 94.36 | 62.06 | 0.0024312 | 62.444 | 1103 |  | 6235 | 94.36 | 0.8005 | 62.06 | 0.0024312 | 62.444 | 1103 | 1040.556
6236 | 0.80075 | 94.37 | 62.06 | 0.0024319 | 62.454 | 1103 |  | 6236 | 94.37 | 0.80075 | 62.06 | 0.0024319 | 62.454 | 1103 | 1040.546
6237 | 0.80099 | 94.38 | 62.06 | 0.0024326 | 62.464 | 1103 |  | 6237 | 94.38 | 0.80099 | 62.06 | 0.0024326 | 62.464 | 1103 | 1040.536
6238 | 0.80124 | 94.39 | 62.06 | 0.0024333 | 62.474 | 1103 |  | 6238 | 94.39 | 0.80124 | 62.06 | 0.0024333 | 62.474 | 1103 | 1040.526
6239 | 0.80149 | 94.4 | 62.06 | 0.0024341 | 62.484 | 1103 |  | 6239 | 94.4 | 0.80149 | 62.06 | 0.0024341 | 62.484 | 1103 | 1040.516
6240 | 0.80174 | 94.41 | 62.06 | 0.0024348 | 62.494 | 1103 |  | 6240 | 94.41 | 0.80174 | 62.06 | 0.0024348 | 62.494 | 1103 | 1040.506
6241 | 0.80198 | 94.42 | 62.06 | 0.0024355 | 62.504 | 1103 |  | 6241 | 94.42 | 0.80198 | 62.06 | 0.0024355 | 62.504 | 1103 | 1040.496
6242 | 0.80223 | 94.43 | 62.06 | 0.0024362 | 62.514 | 1103.1 |  | 6242 | 94.43 | 0.80223 | 62.06 | 0.0024362 | 62.514 | 1103.1 | 1040.586
6243 | 0.80248 | 94.44 | 62.059 | 0.0024369 | 62.524 | 1103.1 |  | 6243 | 94.44 | 0.80248 | 62.059 | 0.0024369 | 62.524 | 1103.1 | 1040.576
6244 | 0.80272 | 94.45 | 62.059 | 0.0024376 | 62.534 | 1103.1 |  | 6244 | 94.45 | 0.80272 | 62.059 | 0.0024376 | 62.534 | 1103.1 | 1040.566
6245 | 0.80297 | 94.46 | 62.059 | 0.0024383 | 62.544 | 1103.1 |  | 6245 | 94.46 | 0.80297 | 62.059 | 0.0024383 | 62.544 | 1103.1 | 1040.556
6246 | 0.80322 | 94.47 | 62.059 | 0.002439 | 62.554 | 1103.1 |  | 6246 | 94.47 | 0.80322 | 62.059 | 0.002439 | 62.554 | 1103.1 | 1040.546
6247 | 0.80347 | 94.48 | 62.059 | 0.0024397 | 62.564 | 1103.1 |  | 6247 | 94.48 | 0.80347 | 62.059 | 0.0024397 | 62.564 | 1103.1 | 1040.536
6248 | 0.80371 | 94.49 | 62.059 | 0.0024404 | 62.574 | 1103.1 |  | 6248 | 94.49 | 0.80371 | 62.059 | 0.0024404 | 62.574 | 1103.1 | 1040.526
6249 | 0.80396 | 94.5 | 62.059 | 0.0024411 | 62.584 | 1103.1 |  | 6249 | 94.5 | 0.80396 | 62.059 | 0.0024411 | 62.584 | 1103.1 | 1040.516
6250 | 0.80421 | 94.51 | 62.059 | 0.0024418 | 62.594 | 1103.1 |  | 6250 | 94.51 | 0.80421 | 62.059 | 0.0024418 | 62.594 | 1103.1 | 1040.506
6251 | 0.80446 | 94.52 | 62.059 | 0.0024425 | 62.604 | 1103.1 |  | 6251 | 94.52 | 0.80446 | 62.059 | 0.0024425 | 62.604 | 1103.1 | 1040.496
6252 | 0.8047 | 94.53 | 62.058 | 0.0024433 | 62.614 | 1103.1 |  | 6252 | 94.53 | 0.8047 | 62.058 | 0.0024433 | 62.614 | 1103.1 | 1040.486
6253 | 0.80495 | 94.54 | 62.058 | 0.002444 | 62.624 | 1103.1 |  | 6253 | 94.54 | 0.80495 | 62.058 | 0.002444 | 62.624 | 1103.1 | 1040.476
6254 | 0.8052 | 94.55 | 62.058 | 0.0024447 | 62.634 | 1103.1 |  | 6254 | 94.55 | 0.8052 | 62.058 | 0.0024447 | 62.634 | 1103.1 | 1040.466
6255 | 0.80545 | 94.56 | 62.058 | 0.0024454 | 62.644 | 1103.1 |  | 6255 | 94.56 | 0.80545 | 62.058 | 0.0024454 | 62.644 | 1103.1 | 1040.456
6256 | 0.80569 | 94.57 | 62.058 | 0.0024461 | 62.654 | 1103.1 |  | 6256 | 94.57 | 0.80569 | 62.058 | 0.0024461 | 62.654 | 1103.1 | 1040.446
6257 | 0.80594 | 94.58 | 62.058 | 0.0024468 | 62.664 | 1103.1 |  | 6257 | 94.58 | 0.80594 | 62.058 | 0.0024468 | 62.664 | 1103.1 | 1040.436
6258 | 0.80619 | 94.59 | 62.058 | 0.0024475 | 62.674 | 1103.1 |  | 6258 | 94.59 | 0.80619 | 62.058 | 0.0024475 | 62.674 | 1103.1 | 1040.426
6259 | 0.80644 | 94.6 | 62.058 | 0.0024482 | 62.684 | 1103.1 |  | 6259 | 94.6 | 0.80644 | 62.058 | 0.0024482 | 62.684 | 1103.1 | 1040.416
6260 | 0.80669 | 94.61 | 62.057 | 0.0024489 | 62.694 | 1103.1 |  | 6260 | 94.61 | 0.80669 | 62.057 | 0.0024489 | 62.694 | 1103.1 | 1040.406
6261 | 0.80694 | 94.62 | 62.057 | 0.0024496 | 62.704 | 1103.1 |  | 6261 | 94.62 | 0.80694 | 62.057 | 0.0024496 | 62.704 | 1103.1 | 1040.396
6262 | 0.80718 | 94.63 | 62.057 | 0.0024504 | 62.714 | 1103.1 |  | 6262 | 94.63 | 0.80718 | 62.057 | 0.0024504 | 62.714 | 1103.1 | 1040.386
6263 | 0.80743 | 94.64 | 62.057 | 0.0024511 | 62.724 | 1103.1 |  | 6263 | 94.64 | 0.80743 | 62.057 | 0.0024511 | 62.724 | 1103.1 | 1040.376
6264 | 0.80768 | 94.65 | 62.057 | 0.0024518 | 62.734 | 1103.1 |  | 6264 | 94.65 | 0.80768 | 62.057 | 0.0024518 | 62.734 | 1103.1 | 1040.366
6265 | 0.80793 | 94.66 | 62.057 | 0.0024525 | 62.744 | 1103.1 |  | 6265 | 94.66 | 0.80793 | 62.057 | 0.0024525 | 62.744 | 1103.1 | 1040.356
6266 | 0.80818 | 94.67 | 62.057 | 0.0024532 | 62.754 | 1103.2 |  | 6266 | 94.67 | 0.80818 | 62.057 | 0.0024532 | 62.754 | 1103.2 | 1040.446
6267 | 0.80843 | 94.68 | 62.057 | 0.0024539 | 62.764 | 1103.2 |  | 6267 | 94.68 | 0.80843 | 62.057 | 0.0024539 | 62.764 | 1103.2 | 1040.436
6268 | 0.80868 | 94.69 | 62.057 | 0.0024546 | 62.774 | 1103.2 |  | 6268 | 94.69 | 0.80868 | 62.057 | 0.0024546 | 62.774 | 1103.2 | 1040.426
6269 | 0.80892 | 94.7 | 62.056 | 0.0024553 | 62.784 | 1103.2 |  | 6269 | 94.7 | 0.80892 | 62.056 | 0.0024553 | 62.784 | 1103.2 | 1040.416
6270 | 0.80917 | 94.71 | 62.056 | 0.002456 | 62.794 | 1103.2 |  | 6270 | 94.71 | 0.80917 | 62.056 | 0.002456 | 62.794 | 1103.2 | 1040.406
6271 | 0.80942 | 94.72 | 62.056 | 0.0024568 | 62.804 | 1103.2 |  | 6271 | 94.72 | 0.80942 | 62.056 | 0.0024568 | 62.804 | 1103.2 | 1040.396
6272 | 0.80967 | 94.73 | 62.056 | 0.0024575 | 62.814 | 1103.2 |  | 6272 | 94.73 | 0.80967 | 62.056 | 0.0024575 | 62.814 | 1103.2 | 1040.386
6273 | 0.80992 | 94.74 | 62.056 | 0.0024582 | 62.824 | 1103.2 |  | 6273 | 94.74 | 0.80992 | 62.056 | 0.0024582 | 62.824 | 1103.2 | 1040.376
6274 | 0.81017 | 94.75 | 62.056 | 0.0024589 | 62.834 | 1103.2 |  | 6274 | 94.75 | 0.81017 | 62.056 | 0.0024589 | 62.834 | 1103.2 | 1040.366
6275 | 0.81042 | 94.76 | 62.056 | 0.0024596 | 62.844 | 1103.2 |  | 6275 | 94.76 | 0.81042 | 62.056 | 0.0024596 | 62.844 | 1103.2 | 1040.356
6276 | 0.81067 | 94.77 | 62.056 | 0.0024603 | 62.854 | 1103.2 |  | 6276 | 94.77 | 0.81067 | 62.056 | 0.0024603 | 62.854 | 1103.2 | 1040.346
6277 | 0.81092 | 94.78 | 62.055 | 0.002461 | 62.864 | 1103.2 |  | 6277 | 94.78 | 0.81092 | 62.055 | 0.002461 | 62.864 | 1103.2 | 1040.336
6278 | 0.81117 | 94.79 | 62.055 | 0.0024618 | 62.874 | 1103.2 |  | 6278 | 94.79 | 0.81117 | 62.055 | 0.0024618 | 62.874 | 1103.2 | 1040.326
6279 | 0.81142 | 94.8 | 62.055 | 0.0024625 | 62.884 | 1103.2 |  | 6279 | 94.8 | 0.81142 | 62.055 | 0.0024625 | 62.884 | 1103.2 | 1040.316
6280 | 0.81167 | 94.81 | 62.055 | 0.0024632 | 62.894 | 1103.2 |  | 6280 | 94.81 | 0.81167 | 62.055 | 0.0024632 | 62.894 | 1103.2 | 1040.306
6281 | 0.81192 | 94.82 | 62.055 | 0.0024639 | 62.904 | 1103.2 |  | 6281 | 94.82 | 0.81192 | 62.055 | 0.0024639 | 62.904 | 1103.2 | 1040.296
6282 | 0.81216 | 94.83 | 62.055 | 0.0024646 | 62.914 | 1103.2 |  | 6282 | 94.83 | 0.81216 | 62.055 | 0.0024646 | 62.914 | 1103.2 | 1040.286
6283 | 0.81241 | 94.84 | 62.055 | 0.0024653 | 62.924 | 1103.2 |  | 6283 | 94.84 | 0.81241 | 62.055 | 0.0024653 | 62.924 | 1103.2 | 1040.276
6284 | 0.81266 | 94.85 | 62.055 | 0.002466 | 62.934 | 1103.2 |  | 6284 | 94.85 | 0.81266 | 62.055 | 0.002466 | 62.934 | 1103.2 | 1040.266
6285 | 0.81291 | 94.86 | 62.055 | 0.0024668 | 62.944 | 1103.2 |  | 6285 | 94.86 | 0.81291 | 62.055 | 0.0024668 | 62.944 | 1103.2 | 1040.256
6286 | 0.81316 | 94.87 | 62.054 | 0.0024675 | 62.954 | 1103.2 |  | 6286 | 94.87 | 0.81316 | 62.054 | 0.0024675 | 62.954 | 1103.2 | 1040.246
6287 | 0.81341 | 94.88 | 62.054 | 0.0024682 | 62.964 | 1103.2 |  | 6287 | 94.88 | 0.81341 | 62.054 | 0.0024682 | 62.964 | 1103.2 | 1040.236
6288 | 0.81366 | 94.89 | 62.054 | 0.0024689 | 62.974 | 1103.2 |  | 6288 | 94.89 | 0.81366 | 62.054 | 0.0024689 | 62.974 | 1103.2 | 1040.226
6289 | 0.81391 | 94.9 | 62.054 | 0.0024696 | 62.983 | 1103.3 |  | 6289 | 94.9 | 0.81391 | 62.054 | 0.0024696 | 62.983 | 1103.3 | 1040.317
6290 | 0.81416 | 94.91 | 62.054 | 0.0024703 | 62.993 | 1103.3 |  | 6290 | 94.91 | 0.81416 | 62.054 | 0.0024703 | 62.993 | 1103.3 | 1040.307
6291 | 0.81442 | 94.92 | 62.054 | 0.002471 | 63.003 | 1103.3 |  | 6291 | 94.92 | 0.81442 | 62.054 | 0.002471 | 63.003 | 1103.3 | 1040.297
6292 | 0.81467 | 94.93 | 62.054 | 0.0024718 | 63.013 | 1103.3 |  | 6292 | 94.93 | 0.81467 | 62.054 | 0.0024718 | 63.013 | 1103.3 | 1040.287
6293 | 0.81492 | 94.94 | 62.054 | 0.0024725 | 63.023 | 1103.3 |  | 6293 | 94.94 | 0.81492 | 62.054 | 0.0024725 | 63.023 | 1103.3 | 1040.277
6294 | 0.81517 | 94.95 | 62.053 | 0.0024732 | 63.033 | 1103.3 |  | 6294 | 94.95 | 0.81517 | 62.053 | 0.0024732 | 63.033 | 1103.3 | 1040.267
6295 | 0.81542 | 94.96 | 62.053 | 0.0024739 | 63.043 | 1103.3 |  | 6295 | 94.96 | 0.81542 | 62.053 | 0.0024739 | 63.043 | 1103.3 | 1040.257
6296 | 0.81567 | 94.97 | 62.053 | 0.0024746 | 63.053 | 1103.3 |  | 6296 | 94.97 | 0.81567 | 62.053 | 0.0024746 | 63.053 | 1103.3 | 1040.247
6297 | 0.81592 | 94.98 | 62.053 | 0.0024753 | 63.063 | 1103.3 |  | 6297 | 94.98 | 0.81592 | 62.053 | 0.0024753 | 63.063 | 1103.3 | 1040.237
6298 | 0.81617 | 94.99 | 62.053 | 0.0024761 | 63.073 | 1103.3 |  | 6298 | 94.99 | 0.81617 | 62.053 | 0.0024761 | 63.073 | 1103.3 | 1040.227
6299 | 0.81642 | 95 | 62.053 | 0.0024768 | 63.083 | 1103.3 |  | 6299 | 95 | 0.81642 | 62.053 | 0.0024768 | 63.083 | 1103.3 | 1040.217
6300 | 0.81667 | 95.01 | 62.053 | 0.0024775 | 63.093 | 1103.3 |  | 6300 | 95.01 | 0.81667 | 62.053 | 0.0024775 | 63.093 | 1103.3 | 1040.207
6301 | 0.81692 | 95.02 | 62.053 | 0.0024782 | 63.103 | 1103.3 |  | 6301 | 95.02 | 0.81692 | 62.053 | 0.0024782 | 63.103 | 1103.3 | 1040.197
6302 | 0.81717 | 95.03 | 62.052 | 0.0024789 | 63.113 | 1103.3 |  | 6302 | 95.03 | 0.81717 | 62.052 | 0.0024789 | 63.113 | 1103.3 | 1040.187
6303 | 0.81742 | 95.04 | 62.052 | 0.0024797 | 63.123 | 1103.3 |  | 6303 | 95.04 | 0.81742 | 62.052 | 0.0024797 | 63.123 | 1103.3 | 1040.177
6304 | 0.81767 | 95.05 | 62.052 | 0.0024804 | 63.133 | 1103.3 |  | 6304 | 95.05 | 0.81767 | 62.052 | 0.0024804 | 63.133 | 1103.3 | 1040.167
6305 | 0.81793 | 95.06 | 62.052 | 0.0024811 | 63.143 | 1103.3 |  | 6305 | 95.06 | 0.81793 | 62.052 | 0.0024811 | 63.143 | 1103.3 | 1040.157
6306 | 0.81818 | 95.07 | 62.052 | 0.0024818 | 63.153 | 1103.3 |  | 6306 | 95.07 | 0.81818 | 62.052 | 0.0024818 | 63.153 | 1103.3 | 1040.147
6307 | 0.81843 | 95.08 | 62.052 | 0.0024825 | 63.163 | 1103.3 |  | 6307 | 95.08 | 0.81843 | 62.052 | 0.0024825 | 63.163 | 1103.3 | 1040.137
6308 | 0.81868 | 95.09 | 62.052 | 0.0024832 | 63.173 | 1103.3 |  | 6308 | 95.09 | 0.81868 | 62.052 | 0.0024832 | 63.173 | 1103.3 | 1040.127
6309 | 0.81893 | 95.1 | 62.052 | 0.002484 | 63.183 | 1103.3 |  | 6309 | 95.1 | 0.81893 | 62.052 | 0.002484 | 63.183 | 1103.3 | 1040.117
6310 | 0.81918 | 95.11 | 62.052 | 0.0024847 | 63.193 | 1103.3 |  | 6310 | 95.11 | 0.81918 | 62.052 | 0.0024847 | 63.193 | 1103.3 | 1040.107
6311 | 0.81943 | 95.12 | 62.051 | 0.0024854 | 63.203 | 1103.3 |  | 6311 | 95.12 | 0.81943 | 62.051 | 0.0024854 | 63.203 | 1103.3 | 1040.097
6312 | 0.81969 | 95.13 | 62.051 | 0.0024861 | 63.213 | 1103.4 |  | 6312 | 95.13 | 0.81969 | 62.051 | 0.0024861 | 63.213 | 1103.4 | 1040.187
6313 | 0.81994 | 95.14 | 62.051 | 0.0024868 | 63.223 | 1103.4 |  | 6313 | 95.14 | 0.81994 | 62.051 | 0.0024868 | 63.223 | 1103.4 | 1040.177
6314 | 0.82019 | 95.15 | 62.051 | 0.0024876 | 63.233 | 1103.4 |  | 6314 | 95.15 | 0.82019 | 62.051 | 0.0024876 | 63.233 | 1103.4 | 1040.167
6315 | 0.82044 | 95.16 | 62.051 | 0.0024883 | 63.243 | 1103.4 |  | 6315 | 95.16 | 0.82044 | 62.051 | 0.0024883 | 63.243 | 1103.4 | 1040.157
6316 | 0.82069 | 95.17 | 62.051 | 0.002489 | 63.253 | 1103.4 |  | 6316 | 95.17 | 0.82069 | 62.051 | 0.002489 | 63.253 | 1103.4 | 1040.147
6317 | 0.82095 | 95.18 | 62.051 | 0.0024897 | 63.263 | 1103.4 |  | 6317 | 95.18 | 0.82095 | 62.051 | 0.0024897 | 63.263 | 1103.4 | 1040.137
6318 | 0.8212 | 95.19 | 62.051 | 0.0024904 | 63.273 | 1103.4 |  | 6318 | 95.19 | 0.8212 | 62.051 | 0.0024904 | 63.273 | 1103.4 | 1040.127
6319 | 0.82145 | 95.2 | 62.05 | 0.0024912 | 63.283 | 1103.4 |  | 6319 | 95.2 | 0.82145 | 62.05 | 0.0024912 | 63.283 | 1103.4 | 1040.117
6320 | 0.8217 | 95.21 | 62.05 | 0.0024919 | 63.293 | 1103.4 |  | 6320 | 95.21 | 0.8217 | 62.05 | 0.0024919 | 63.293 | 1103.4 | 1040.107
6321 | 0.82195 | 95.22 | 62.05 | 0.0024926 | 63.303 | 1103.4 |  | 6321 | 95.22 | 0.82195 | 62.05 | 0.0024926 | 63.303 | 1103.4 | 1040.097
6322 | 0.82221 | 95.23 | 62.05 | 0.0024933 | 63.313 | 1103.4 |  | 6322 | 95.23 | 0.82221 | 62.05 | 0.0024933 | 63.313 | 1103.4 | 1040.087
6323 | 0.82246 | 95.24 | 62.05 | 0.0024941 | 63.323 | 1103.4 |  | 6323 | 95.24 | 0.82246 | 62.05 | 0.0024941 | 63.323 | 1103.4 | 1040.077
6324 | 0.82271 | 95.25 | 62.05 | 0.0024948 | 63.333 | 1103.4 |  | 6324 | 95.25 | 0.82271 | 62.05 | 0.0024948 | 63.333 | 1103.4 | 1040.067
6325 | 0.82296 | 95.26 | 62.05 | 0.0024955 | 63.343 | 1103.4 |  | 6325 | 95.26 | 0.82296 | 62.05 | 0.0024955 | 63.343 | 1103.4 | 1040.057
6326 | 0.82322 | 95.27 | 62.05 | 0.0024962 | 63.353 | 1103.4 |  | 6326 | 95.27 | 0.82322 | 62.05 | 0.0024962 | 63.353 | 1103.4 | 1040.047
6327 | 0.82347 | 95.28 | 62.049 | 0.0024969 | 63.363 | 1103.4 |  | 6327 | 95.28 | 0.82347 | 62.049 | 0.0024969 | 63.363 | 1103.4 | 1040.037
6328 | 0.82372 | 95.29 | 62.049 | 0.0024977 | 63.373 | 1103.4 |  | 6328 | 95.29 | 0.82372 | 62.049 | 0.0024977 | 63.373 | 1103.4 | 1040.027
6329 | 0.82398 | 95.3 | 62.049 | 0.0024984 | 63.383 | 1103.4 |  | 6329 | 95.3 | 0.82398 | 62.049 | 0.0024984 | 63.383 | 1103.4 | 1040.017
6330 | 0.82423 | 95.31 | 62.049 | 0.0024991 | 63.393 | 1103.4 |  | 6330 | 95.31 | 0.82423 | 62.049 | 0.0024991 | 63.393 | 1103.4 | 1040.007
6331 | 0.82448 | 95.32 | 62.049 | 0.0024998 | 63.403 | 1103.4 |  | 6331 | 95.32 | 0.82448 | 62.049 | 0.0024998 | 63.403 | 1103.4 | 1039.997
6332 | 0.82473 | 95.33 | 62.049 | 0.0025006 | 63.413 | 1103.4 |  | 6332 | 95.33 | 0.82473 | 62.049 | 0.0025006 | 63.413 | 1103.4 | 1039.987
6333 | 0.82499 | 95.34 | 62.049 | 0.0025013 | 63.423 | 1103.4 |  | 6333 | 95.34 | 0.82499 | 62.049 | 0.0025013 | 63.423 | 1103.4 | 1039.977
6334 | 0.82524 | 95.35 | 62.049 | 0.002502 | 63.433 | 1103.4 |  | 6334 | 95.35 | 0.82524 | 62.049 | 0.002502 | 63.433 | 1103.4 | 1039.967
6335 | 0.82549 | 95.36 | 62.049 | 0.0025027 | 63.443 | 1103.4 |  | 6335 | 95.36 | 0.82549 | 62.049 | 0.0025027 | 63.443 | 1103.4 | 1039.957
6336 | 0.82575 | 95.37 | 62.048 | 0.0025035 | 63.453 | 1103.5 |  | 6336 | 95.37 | 0.82575 | 62.048 | 0.0025035 | 63.453 | 1103.5 | 1040.047
6337 | 0.826 | 95.38 | 62.048 | 0.0025042 | 63.463 | 1103.5 |  | 6337 | 95.38 | 0.826 | 62.048 | 0.0025042 | 63.463 | 1103.5 | 1040.037
6338 | 0.82625 | 95.39 | 62.048 | 0.0025049 | 63.473 | 1103.5 |  | 6338 | 95.39 | 0.82625 | 62.048 | 0.0025049 | 63.473 | 1103.5 | 1040.027
6339 | 0.82651 | 95.4 | 62.048 | 0.0025056 | 63.483 | 1103.5 |  | 6339 | 95.4 | 0.82651 | 62.048 | 0.0025056 | 63.483 | 1103.5 | 1040.017
6340 | 0.82676 | 95.41 | 62.048 | 0.0025063 | 63.493 | 1103.5 |  | 6340 | 95.41 | 0.82676 | 62.048 | 0.0025063 | 63.493 | 1103.5 | 1040.007
6341 | 0.82701 | 95.42 | 62.048 | 0.0025071 | 63.503 | 1103.5 |  | 6341 | 95.42 | 0.82701 | 62.048 | 0.0025071 | 63.503 | 1103.5 | 1039.997
6342 | 0.82727 | 95.43 | 62.048 | 0.0025078 | 63.513 | 1103.5 |  | 6342 | 95.43 | 0.82727 | 62.048 | 0.0025078 | 63.513 | 1103.5 | 1039.987
6343 | 0.82752 | 95.44 | 62.048 | 0.0025085 | 63.523 | 1103.5 |  | 6343 | 95.44 | 0.82752 | 62.048 | 0.0025085 | 63.523 | 1103.5 | 1039.977
6344 | 0.82778 | 95.45 | 62.047 | 0.0025093 | 63.533 | 1103.5 |  | 6344 | 95.45 | 0.82778 | 62.047 | 0.0025093 | 63.533 | 1103.5 | 1039.967
6345 | 0.82803 | 95.46 | 62.047 | 0.00251 | 63.543 | 1103.5 |  | 6345 | 95.46 | 0.82803 | 62.047 | 0.00251 | 63.543 | 1103.5 | 1039.957
6346 | 0.82828 | 95.47 | 62.047 | 0.0025107 | 63.553 | 1103.5 |  | 6346 | 95.47 | 0.82828 | 62.047 | 0.0025107 | 63.553 | 1103.5 | 1039.947
6347 | 0.82854 | 95.48 | 62.047 | 0.0025114 | 63.563 | 1103.5 |  | 6347 | 95.48 | 0.82854 | 62.047 | 0.0025114 | 63.563 | 1103.5 | 1039.937
6348 | 0.82879 | 95.49 | 62.047 | 0.0025122 | 63.573 | 1103.5 |  | 6348 | 95.49 | 0.82879 | 62.047 | 0.0025122 | 63.573 | 1103.5 | 1039.927
6349 | 0.82905 | 95.5 | 62.047 | 0.0025129 | 63.583 | 1103.5 |  | 6349 | 95.5 | 0.82905 | 62.047 | 0.0025129 | 63.583 | 1103.5 | 1039.917
6350 | 0.8293 | 95.51 | 62.047 | 0.0025136 | 63.593 | 1103.5 |  | 6350 | 95.51 | 0.8293 | 62.047 | 0.0025136 | 63.593 | 1103.5 | 1039.907
6351 | 0.82955 | 95.52 | 62.047 | 0.0025143 | 63.603 | 1103.5 |  | 6351 | 95.52 | 0.82955 | 62.047 | 0.0025143 | 63.603 | 1103.5 | 1039.897
6352 | 0.82981 | 95.53 | 62.046 | 0.0025151 | 63.613 | 1103.5 |  | 6352 | 95.53 | 0.82981 | 62.046 | 0.0025151 | 63.613 | 1103.5 | 1039.887
6353 | 0.83006 | 95.54 | 62.046 | 0.0025158 | 63.623 | 1103.5 |  | 6353 | 95.54 | 0.83006 | 62.046 | 0.0025158 | 63.623 | 1103.5 | 1039.877
6354 | 0.83032 | 95.55 | 62.046 | 0.0025165 | 63.633 | 1103.5 |  | 6354 | 95.55 | 0.83032 | 62.046 | 0.0025165 | 63.633 | 1103.5 | 1039.867
6355 | 0.83057 | 95.56 | 62.046 | 0.0025172 | 63.643 | 1103.5 |  | 6355 | 95.56 | 0.83057 | 62.046 | 0.0025172 | 63.643 | 1103.5 | 1039.857
6356 | 0.83083 | 95.57 | 62.046 | 0.002518 | 63.653 | 1103.5 |  | 6356 | 95.57 | 0.83083 | 62.046 | 0.002518 | 63.653 | 1103.5 | 1039.847
6357 | 0.83108 | 95.58 | 62.046 | 0.0025187 | 63.663 | 1103.5 |  | 6357 | 95.58 | 0.83108 | 62.046 | 0.0025187 | 63.663 | 1103.5 | 1039.837
6358 | 0.83134 | 95.59 | 62.046 | 0.0025194 | 63.673 | 1103.5 |  | 6358 | 95.59 | 0.83134 | 62.046 | 0.0025194 | 63.673 | 1103.5 | 1039.827
6359 | 0.83159 | 95.6 | 62.046 | 0.0025202 | 63.683 | 1103.6 |  | 6359 | 95.6 | 0.83159 | 62.046 | 0.0025202 | 63.683 | 1103.6 | 1039.917
6360 | 0.83185 | 95.61 | 62.046 | 0.0025209 | 63.693 | 1103.6 |  | 6360 | 95.61 | 0.83185 | 62.046 | 0.0025209 | 63.693 | 1103.6 | 1039.907
6361 | 0.8321 | 95.62 | 62.045 | 0.0025216 | 63.703 | 1103.6 |  | 6361 | 95.62 | 0.8321 | 62.045 | 0.0025216 | 63.703 | 1103.6 | 1039.897
6362 | 0.83236 | 95.63 | 62.045 | 0.0025223 | 63.713 | 1103.6 |  | 6362 | 95.63 | 0.83236 | 62.045 | 0.0025223 | 63.713 | 1103.6 | 1039.887
6363 | 0.83261 | 95.64 | 62.045 | 0.0025231 | 63.723 | 1103.6 |  | 6363 | 95.64 | 0.83261 | 62.045 | 0.0025231 | 63.723 | 1103.6 | 1039.877
6364 | 0.83287 | 95.65 | 62.045 | 0.0025238 | 63.733 | 1103.6 |  | 6364 | 95.65 | 0.83287 | 62.045 | 0.0025238 | 63.733 | 1103.6 | 1039.867
6365 | 0.83312 | 95.66 | 62.045 | 0.0025245 | 63.743 | 1103.6 |  | 6365 | 95.66 | 0.83312 | 62.045 | 0.0025245 | 63.743 | 1103.6 | 1039.857
6366 | 0.83338 | 95.67 | 62.045 | 0.0025253 | 63.753 | 1103.6 |  | 6366 | 95.67 | 0.83338 | 62.045 | 0.0025253 | 63.753 | 1103.6 | 1039.847
6367 | 0.83363 | 95.68 | 62.045 | 0.002526 | 63.763 | 1103.6 |  | 6367 | 95.68 | 0.83363 | 62.045 | 0.002526 | 63.763 | 1103.6 | 1039.837
6368 | 0.83389 | 95.69 | 62.045 | 0.0025267 | 63.773 | 1103.6 |  | 6368 | 95.69 | 0.83389 | 62.045 | 0.0025267 | 63.773 | 1103.6 | 1039.827
6369 | 0.83414 | 95.7 | 62.044 | 0.0025274 | 63.783 | 1103.6 |  | 6369 | 95.7 | 0.83414 | 62.044 | 0.0025274 | 63.783 | 1103.6 | 1039.817
6370 | 0.8344 | 95.71 | 62.044 | 0.0025282 | 63.793 | 1103.6 |  | 6370 | 95.71 | 0.8344 | 62.044 | 0.0025282 | 63.793 | 1103.6 | 1039.807
6371 | 0.83465 | 95.72 | 62.044 | 0.0025289 | 63.803 | 1103.6 |  | 6371 | 95.72 | 0.83465 | 62.044 | 0.0025289 | 63.803 | 1103.6 | 1039.797
6372 | 0.83491 | 95.73 | 62.044 | 0.0025296 | 63.813 | 1103.6 |  | 6372 | 95.73 | 0.83491 | 62.044 | 0.0025296 | 63.813 | 1103.6 | 1039.787
6373 | 0.83517 | 95.74 | 62.044 | 0.0025304 | 63.823 | 1103.6 |  | 6373 | 95.74 | 0.83517 | 62.044 | 0.0025304 | 63.823 | 1103.6 | 1039.777
6374 | 0.83542 | 95.75 | 62.044 | 0.0025311 | 63.833 | 1103.6 |  | 6374 | 95.75 | 0.83542 | 62.044 | 0.0025311 | 63.833 | 1103.6 | 1039.767
6375 | 0.83568 | 95.76 | 62.044 | 0.0025318 | 63.843 | 1103.6 |  | 6375 | 95.76 | 0.83568 | 62.044 | 0.0025318 | 63.843 | 1103.6 | 1039.757
6376 | 0.83593 | 95.77 | 62.044 | 0.0025326 | 63.853 | 1103.6 |  | 6376 | 95.77 | 0.83593 | 62.044 | 0.0025326 | 63.853 | 1103.6 | 1039.747
6377 | 0.83619 | 95.78 | 62.043 | 0.0025333 | 63.863 | 1103.6 |  | 6377 | 95.78 | 0.83619 | 62.043 | 0.0025333 | 63.863 | 1103.6 | 1039.737
6378 | 0.83645 | 95.79 | 62.043 | 0.002534 | 63.873 | 1103.6 |  | 6378 | 95.79 | 0.83645 | 62.043 | 0.002534 | 63.873 | 1103.6 | 1039.727
6379 | 0.8367 | 95.8 | 62.043 | 0.0025348 | 63.883 | 1103.6 |  | 6379 | 95.8 | 0.8367 | 62.043 | 0.0025348 | 63.883 | 1103.6 | 1039.717
6380 | 0.83696 | 95.81 | 62.043 | 0.0025355 | 63.893 | 1103.6 |  | 6380 | 95.81 | 0.83696 | 62.043 | 0.0025355 | 63.893 | 1103.6 | 1039.707
6381 | 0.83722 | 95.82 | 62.043 | 0.0025362 | 63.903 | 1103.6 |  | 6381 | 95.82 | 0.83722 | 62.043 | 0.0025362 | 63.903 | 1103.6 | 1039.697
6382 | 0.83747 | 95.83 | 62.043 | 0.002537 | 63.913 | 1103.7 |  | 6382 | 95.83 | 0.83747 | 62.043 | 0.002537 | 63.913 | 1103.7 | 1039.787
6383 | 0.83773 | 95.84 | 62.043 | 0.0025377 | 63.923 | 1103.7 |  | 6383 | 95.84 | 0.83773 | 62.043 | 0.0025377 | 63.923 | 1103.7 | 1039.777
6384 | 0.83798 | 95.85 | 62.043 | 0.0025384 | 63.933 | 1103.7 |  | 6384 | 95.85 | 0.83798 | 62.043 | 0.0025384 | 63.933 | 1103.7 | 1039.767
6385 | 0.83824 | 95.86 | 62.043 | 0.0025391 | 63.943 | 1103.7 |  | 6385 | 95.86 | 0.83824 | 62.043 | 0.0025391 | 63.943 | 1103.7 | 1039.757
6386 | 0.8385 | 95.87 | 62.042 | 0.0025399 | 63.953 | 1103.7 |  | 6386 | 95.87 | 0.8385 | 62.042 | 0.0025399 | 63.953 | 1103.7 | 1039.747
6387 | 0.83875 | 95.88 | 62.042 | 0.0025406 | 63.963 | 1103.7 |  | 6387 | 95.88 | 0.83875 | 62.042 | 0.0025406 | 63.963 | 1103.7 | 1039.737
6388 | 0.83901 | 95.89 | 62.042 | 0.0025413 | 63.973 | 1103.7 |  | 6388 | 95.89 | 0.83901 | 62.042 | 0.0025413 | 63.973 | 1103.7 | 1039.727
6389 | 0.83927 | 95.9 | 62.042 | 0.0025421 | 63.982 | 1103.7 |  | 6389 | 95.9 | 0.83927 | 62.042 | 0.0025421 | 63.982 | 1103.7 | 1039.718
6390 | 0.83953 | 95.91 | 62.042 | 0.0025428 | 63.992 | 1103.7 |  | 6390 | 95.91 | 0.83953 | 62.042 | 0.0025428 | 63.992 | 1103.7 | 1039.708
6391 | 0.83978 | 95.92 | 62.042 | 0.0025435 | 64.002 | 1103.7 |  | 6391 | 95.92 | 0.83978 | 62.042 | 0.0025435 | 64.002 | 1103.7 | 1039.698
6392 | 0.84004 | 95.93 | 62.042 | 0.0025443 | 64.012 | 1103.7 |  | 6392 | 95.93 | 0.84004 | 62.042 | 0.0025443 | 64.012 | 1103.7 | 1039.688
6393 | 0.8403 | 95.94 | 62.042 | 0.002545 | 64.022 | 1103.7 |  | 6393 | 95.94 | 0.8403 | 62.042 | 0.002545 | 64.022 | 1103.7 | 1039.678
6394 | 0.84055 | 95.95 | 62.041 | 0.0025458 | 64.032 | 1103.7 |  | 6394 | 95.95 | 0.84055 | 62.041 | 0.0025458 | 64.032 | 1103.7 | 1039.668
6395 | 0.84081 | 95.96 | 62.041 | 0.0025465 | 64.042 | 1103.7 |  | 6395 | 95.96 | 0.84081 | 62.041 | 0.0025465 | 64.042 | 1103.7 | 1039.658
6396 | 0.84107 | 95.97 | 62.041 | 0.0025472 | 64.052 | 1103.7 |  | 6396 | 95.97 | 0.84107 | 62.041 | 0.0025472 | 64.052 | 1103.7 | 1039.648
6397 | 0.84133 | 95.98 | 62.041 | 0.002548 | 64.062 | 1103.7 |  | 6397 | 95.98 | 0.84133 | 62.041 | 0.002548 | 64.062 | 1103.7 | 1039.638
6398 | 0.84158 | 95.99 | 62.041 | 0.0025487 | 64.072 | 1103.7 |  | 6398 | 95.99 | 0.84158 | 62.041 | 0.0025487 | 64.072 | 1103.7 | 1039.628
6399 | 0.84184 | 96 | 62.041 | 0.0025494 | 64.082 | 1103.7 |  | 6399 | 96 | 0.84184 | 62.041 | 0.0025494 | 64.082 | 1103.7 | 1039.618
6400 | 0.8421 | 96.01 | 62.041 | 0.0025502 | 64.092 | 1103.7 |  | 6400 | 96.01 | 0.8421 | 62.041 | 0.0025502 | 64.092 | 1103.7 | 1039.608
6401 | 0.84236 | 96.02 | 62.041 | 0.0025509 | 64.102 | 1103.7 |  | 6401 | 96.02 | 0.84236 | 62.041 | 0.0025509 | 64.102 | 1103.7 | 1039.598
6402 | 0.84261 | 96.03 | 62.04 | 0.0025516 | 64.112 | 1103.7 |  | 6402 | 96.03 | 0.84261 | 62.04 | 0.0025516 | 64.112 | 1103.7 | 1039.588
6403 | 0.84287 | 96.04 | 62.04 | 0.0025524 | 64.122 | 1103.7 |  | 6403 | 96.04 | 0.84287 | 62.04 | 0.0025524 | 64.122 | 1103.7 | 1039.578
6404 | 0.84313 | 96.05 | 62.04 | 0.0025531 | 64.132 | 1103.7 |  | 6404 | 96.05 | 0.84313 | 62.04 | 0.0025531 | 64.132 | 1103.7 | 1039.568
6405 | 0.84339 | 96.06 | 62.04 | 0.0025538 | 64.142 | 1103.8 |  | 6405 | 96.06 | 0.84339 | 62.04 | 0.0025538 | 64.142 | 1103.8 | 1039.658
6406 | 0.84365 | 96.07 | 62.04 | 0.0025546 | 64.152 | 1103.8 |  | 6406 | 96.07 | 0.84365 | 62.04 | 0.0025546 | 64.152 | 1103.8 | 1039.648
6407 | 0.8439 | 96.08 | 62.04 | 0.0025553 | 64.162 | 1103.8 |  | 6407 | 96.08 | 0.8439 | 62.04 | 0.0025553 | 64.162 | 1103.8 | 1039.638
6408 | 0.84416 | 96.09 | 62.04 | 0.0025561 | 64.172 | 1103.8 |  | 6408 | 96.09 | 0.84416 | 62.04 | 0.0025561 | 64.172 | 1103.8 | 1039.628
6409 | 0.84442 | 96.1 | 62.04 | 0.0025568 | 64.182 | 1103.8 |  | 6409 | 96.1 | 0.84442 | 62.04 | 0.0025568 | 64.182 | 1103.8 | 1039.618
6410 | 0.84468 | 96.11 | 62.04 | 0.0025575 | 64.192 | 1103.8 |  | 6410 | 96.11 | 0.84468 | 62.04 | 0.0025575 | 64.192 | 1103.8 | 1039.608
6411 | 0.84494 | 96.12 | 62.039 | 0.0025583 | 64.202 | 1103.8 |  | 6411 | 96.12 | 0.84494 | 62.039 | 0.0025583 | 64.202 | 1103.8 | 1039.598
6412 | 0.8452 | 96.13 | 62.039 | 0.002559 | 64.212 | 1103.8 |  | 6412 | 96.13 | 0.8452 | 62.039 | 0.002559 | 64.212 | 1103.8 | 1039.588
6413 | 0.84545 | 96.14 | 62.039 | 0.0025597 | 64.222 | 1103.8 |  | 6413 | 96.14 | 0.84545 | 62.039 | 0.0025597 | 64.222 | 1103.8 | 1039.578
6414 | 0.84571 | 96.15 | 62.039 | 0.0025605 | 64.232 | 1103.8 |  | 6414 | 96.15 | 0.84571 | 62.039 | 0.0025605 | 64.232 | 1103.8 | 1039.568
6415 | 0.84597 | 96.16 | 62.039 | 0.0025612 | 64.242 | 1103.8 |  | 6415 | 96.16 | 0.84597 | 62.039 | 0.0025612 | 64.242 | 1103.8 | 1039.558
6416 | 0.84623 | 96.17 | 62.039 | 0.002562 | 64.252 | 1103.8 |  | 6416 | 96.17 | 0.84623 | 62.039 | 0.002562 | 64.252 | 1103.8 | 1039.548
6417 | 0.84649 | 96.18 | 62.039 | 0.0025627 | 64.262 | 1103.8 |  | 6417 | 96.18 | 0.84649 | 62.039 | 0.0025627 | 64.262 | 1103.8 | 1039.538
6418 | 0.84675 | 96.19 | 62.039 | 0.0025634 | 64.272 | 1103.8 |  | 6418 | 96.19 | 0.84675 | 62.039 | 0.0025634 | 64.272 | 1103.8 | 1039.528
6419 | 0.84701 | 96.2 | 62.038 | 0.0025642 | 64.282 | 1103.8 |  | 6419 | 96.2 | 0.84701 | 62.038 | 0.0025642 | 64.282 | 1103.8 | 1039.518
6420 | 0.84727 | 96.21 | 62.038 | 0.0025649 | 64.292 | 1103.8 |  | 6420 | 96.21 | 0.84727 | 62.038 | 0.0025649 | 64.292 | 1103.8 | 1039.508
6421 | 0.84752 | 96.22 | 62.038 | 0.0025657 | 64.302 | 1103.8 |  | 6421 | 96.22 | 0.84752 | 62.038 | 0.0025657 | 64.302 | 1103.8 | 1039.498
6422 | 0.84778 | 96.23 | 62.038 | 0.0025664 | 64.312 | 1103.8 |  | 6422 | 96.23 | 0.84778 | 62.038 | 0.0025664 | 64.312 | 1103.8 | 1039.488
6423 | 0.84804 | 96.24 | 62.038 | 0.0025671 | 64.322 | 1103.8 |  | 6423 | 96.24 | 0.84804 | 62.038 | 0.0025671 | 64.322 | 1103.8 | 1039.478
6424 | 0.8483 | 96.25 | 62.038 | 0.0025679 | 64.332 | 1103.8 |  | 6424 | 96.25 | 0.8483 | 62.038 | 0.0025679 | 64.332 | 1103.8 | 1039.468
6425 | 0.84856 | 96.26 | 62.038 | 0.0025686 | 64.342 | 1103.8 |  | 6425 | 96.26 | 0.84856 | 62.038 | 0.0025686 | 64.342 | 1103.8 | 1039.458
6426 | 0.84882 | 96.27 | 62.038 | 0.0025694 | 64.352 | 1103.8 |  | 6426 | 96.27 | 0.84882 | 62.038 | 0.0025694 | 64.352 | 1103.8 | 1039.448
6427 | 0.84908 | 96.28 | 62.037 | 0.0025701 | 64.362 | 1103.8 |  | 6427 | 96.28 | 0.84908 | 62.037 | 0.0025701 | 64.362 | 1103.8 | 1039.438
6428 | 0.84934 | 96.29 | 62.037 | 0.0025708 | 64.372 | 1103.8 |  | 6428 | 96.29 | 0.84934 | 62.037 | 0.0025708 | 64.372 | 1103.8 | 1039.428
6429 | 0.8496 | 96.3 | 62.037 | 0.0025716 | 64.382 | 1103.9 |  | 6429 | 96.3 | 0.8496 | 62.037 | 0.0025716 | 64.382 | 1103.9 | 1039.518
6430 | 0.84986 | 96.31 | 62.037 | 0.0025723 | 64.392 | 1103.9 |  | 6430 | 96.31 | 0.84986 | 62.037 | 0.0025723 | 64.392 | 1103.9 | 1039.508
6431 | 0.85012 | 96.32 | 62.037 | 0.0025731 | 64.402 | 1103.9 |  | 6431 | 96.32 | 0.85012 | 62.037 | 0.0025731 | 64.402 | 1103.9 | 1039.498
6432 | 0.85038 | 96.33 | 62.037 | 0.0025738 | 64.412 | 1103.9 |  | 6432 | 96.33 | 0.85038 | 62.037 | 0.0025738 | 64.412 | 1103.9 | 1039.488
6433 | 0.85064 | 96.34 | 62.037 | 0.0025745 | 64.422 | 1103.9 |  | 6433 | 96.34 | 0.85064 | 62.037 | 0.0025745 | 64.422 | 1103.9 | 1039.478
6434 | 0.8509 | 96.35 | 62.037 | 0.0025753 | 64.432 | 1103.9 |  | 6434 | 96.35 | 0.8509 | 62.037 | 0.0025753 | 64.432 | 1103.9 | 1039.468
6435 | 0.85116 | 96.36 | 62.036 | 0.002576 | 64.442 | 1103.9 |  | 6435 | 96.36 | 0.85116 | 62.036 | 0.002576 | 64.442 | 1103.9 | 1039.458
6436 | 0.85142 | 96.37 | 62.036 | 0.0025768 | 64.452 | 1103.9 |  | 6436 | 96.37 | 0.85142 | 62.036 | 0.0025768 | 64.452 | 1103.9 | 1039.448
6437 | 0.85168 | 96.38 | 62.036 | 0.0025775 | 64.462 | 1103.9 |  | 6437 | 96.38 | 0.85168 | 62.036 | 0.0025775 | 64.462 | 1103.9 | 1039.438
6438 | 0.85194 | 96.39 | 62.036 | 0.0025782 | 64.472 | 1103.9 |  | 6438 | 96.39 | 0.85194 | 62.036 | 0.0025782 | 64.472 | 1103.9 | 1039.428
6439 | 0.8522 | 96.4 | 62.036 | 0.002579 | 64.482 | 1103.9 |  | 6439 | 96.4 | 0.8522 | 62.036 | 0.002579 | 64.482 | 1103.9 | 1039.418
6440 | 0.85246 | 96.41 | 62.036 | 0.0025797 | 64.492 | 1103.9 |  | 6440 | 96.41 | 0.85246 | 62.036 | 0.0025797 | 64.492 | 1103.9 | 1039.408
6441 | 0.85272 | 96.42 | 62.036 | 0.0025805 | 64.502 | 1103.9 |  | 6441 | 96.42 | 0.85272 | 62.036 | 0.0025805 | 64.502 | 1103.9 | 1039.398
6442 | 0.85298 | 96.43 | 62.036 | 0.0025812 | 64.512 | 1103.9 |  | 6442 | 96.43 | 0.85298 | 62.036 | 0.0025812 | 64.512 | 1103.9 | 1039.388
6443 | 0.85324 | 96.44 | 62.036 | 0.002582 | 64.522 | 1103.9 |  | 6443 | 96.44 | 0.85324 | 62.036 | 0.002582 | 64.522 | 1103.9 | 1039.378
6444 | 0.8535 | 96.45 | 62.035 | 0.0025827 | 64.532 | 1103.9 |  | 6444 | 96.45 | 0.8535 | 62.035 | 0.0025827 | 64.532 | 1103.9 | 1039.368
6445 | 0.85376 | 96.46 | 62.035 | 0.0025834 | 64.542 | 1103.9 |  | 6445 | 96.46 | 0.85376 | 62.035 | 0.0025834 | 64.542 | 1103.9 | 1039.358
6446 | 0.85402 | 96.47 | 62.035 | 0.0025842 | 64.552 | 1103.9 |  | 6446 | 96.47 | 0.85402 | 62.035 | 0.0025842 | 64.552 | 1103.9 | 1039.348
6447 | 0.85428 | 96.48 | 62.035 | 0.0025849 | 64.562 | 1103.9 |  | 6447 | 96.48 | 0.85428 | 62.035 | 0.0025849 | 64.562 | 1103.9 | 1039.338
6448 | 0.85455 | 96.49 | 62.035 | 0.0025857 | 64.572 | 1103.9 |  | 6448 | 96.49 | 0.85455 | 62.035 | 0.0025857 | 64.572 | 1103.9 | 1039.328
6449 | 0.85481 | 96.5 | 62.035 | 0.0025864 | 64.582 | 1103.9 |  | 6449 | 96.5 | 0.85481 | 62.035 | 0.0025864 | 64.582 | 1103.9 | 1039.318
6450 | 0.85507 | 96.51 | 62.035 | 0.0025872 | 64.592 | 1103.9 |  | 6450 | 96.51 | 0.85507 | 62.035 | 0.0025872 | 64.592 | 1103.9 | 1039.308
6451 | 0.85533 | 96.52 | 62.035 | 0.0025879 | 64.602 | 1103.9 |  | 6451 | 96.52 | 0.85533 | 62.035 | 0.0025879 | 64.602 | 1103.9 | 1039.298
6452 | 0.85559 | 96.53 | 62.034 | 0.0025887 | 64.612 | 1104 |  | 6452 | 96.53 | 0.85559 | 62.034 | 0.0025887 | 64.612 | 1104 | 1039.388
6453 | 0.85585 | 96.54 | 62.034 | 0.0025894 | 64.622 | 1104 |  | 6453 | 96.54 | 0.85585 | 62.034 | 0.0025894 | 64.622 | 1104 | 1039.378
6454 | 0.85611 | 96.55 | 62.034 | 0.0025902 | 64.632 | 1104 |  | 6454 | 96.55 | 0.85611 | 62.034 | 0.0025902 | 64.632 | 1104 | 1039.368
6455 | 0.85637 | 96.56 | 62.034 | 0.0025909 | 64.642 | 1104 |  | 6455 | 96.56 | 0.85637 | 62.034 | 0.0025909 | 64.642 | 1104 | 1039.358
6456 | 0.85664 | 96.57 | 62.034 | 0.0025916 | 64.652 | 1104 |  | 6456 | 96.57 | 0.85664 | 62.034 | 0.0025916 | 64.652 | 1104 | 1039.348
6457 | 0.8569 | 96.58 | 62.034 | 0.0025924 | 64.662 | 1104 |  | 6457 | 96.58 | 0.8569 | 62.034 | 0.0025924 | 64.662 | 1104 | 1039.338
6458 | 0.85716 | 96.59 | 62.034 | 0.0025931 | 64.672 | 1104 |  | 6458 | 96.59 | 0.85716 | 62.034 | 0.0025931 | 64.672 | 1104 | 1039.328
6459 | 0.85742 | 96.6 | 62.034 | 0.0025939 | 64.682 | 1104 |  | 6459 | 96.6 | 0.85742 | 62.034 | 0.0025939 | 64.682 | 1104 | 1039.318
6460 | 0.85768 | 96.61 | 62.033 | 0.0025946 | 64.692 | 1104 |  | 6460 | 96.61 | 0.85768 | 62.033 | 0.0025946 | 64.692 | 1104 | 1039.308
6461 | 0.85794 | 96.62 | 62.033 | 0.0025954 | 64.702 | 1104 |  | 6461 | 96.62 | 0.85794 | 62.033 | 0.0025954 | 64.702 | 1104 | 1039.298
6462 | 0.85821 | 96.63 | 62.033 | 0.0025961 | 64.712 | 1104 |  | 6462 | 96.63 | 0.85821 | 62.033 | 0.0025961 | 64.712 | 1104 | 1039.288
6463 | 0.85847 | 96.64 | 62.033 | 0.0025969 | 64.722 | 1104 |  | 6463 | 96.64 | 0.85847 | 62.033 | 0.0025969 | 64.722 | 1104 | 1039.278
6464 | 0.85873 | 96.65 | 62.033 | 0.0025976 | 64.732 | 1104 |  | 6464 | 96.65 | 0.85873 | 62.033 | 0.0025976 | 64.732 | 1104 | 1039.268
6465 | 0.85899 | 96.66 | 62.033 | 0.0025984 | 64.742 | 1104 |  | 6465 | 96.66 | 0.85899 | 62.033 | 0.0025984 | 64.742 | 1104 | 1039.258
6466 | 0.85925 | 96.67 | 62.033 | 0.0025991 | 64.752 | 1104 |  | 6466 | 96.67 | 0.85925 | 62.033 | 0.0025991 | 64.752 | 1104 | 1039.248
6467 | 0.85952 | 96.68 | 62.033 | 0.0025999 | 64.762 | 1104 |  | 6467 | 96.68 | 0.85952 | 62.033 | 0.0025999 | 64.762 | 1104 | 1039.238
6468 | 0.85978 | 96.69 | 62.032 | 0.0026006 | 64.772 | 1104 |  | 6468 | 96.69 | 0.85978 | 62.032 | 0.0026006 | 64.772 | 1104 | 1039.228
6469 | 0.86004 | 96.7 | 62.032 | 0.0026014 | 64.782 | 1104 |  | 6469 | 96.7 | 0.86004 | 62.032 | 0.0026014 | 64.782 | 1104 | 1039.218
6470 | 0.8603 | 96.71 | 62.032 | 0.0026021 | 64.792 | 1104 |  | 6470 | 96.71 | 0.8603 | 62.032 | 0.0026021 | 64.792 | 1104 | 1039.208
6471 | 0.86057 | 96.72 | 62.032 | 0.0026029 | 64.802 | 1104 |  | 6471 | 96.72 | 0.86057 | 62.032 | 0.0026029 | 64.802 | 1104 | 1039.198
6472 | 0.86083 | 96.73 | 62.032 | 0.0026036 | 64.812 | 1104 |  | 6472 | 96.73 | 0.86083 | 62.032 | 0.0026036 | 64.812 | 1104 | 1039.188
6473 | 0.86109 | 96.74 | 62.032 | 0.0026043 | 64.822 | 1104 |  | 6473 | 96.74 | 0.86109 | 62.032 | 0.0026043 | 64.822 | 1104 | 1039.178
6474 | 0.86135 | 96.75 | 62.032 | 0.0026051 | 64.832 | 1104 |  | 6474 | 96.75 | 0.86135 | 62.032 | 0.0026051 | 64.832 | 1104 | 1039.168
6475 | 0.86162 | 96.76 | 62.032 | 0.0026058 | 64.842 | 1104.1 |  | 6475 | 96.76 | 0.86162 | 62.032 | 0.0026058 | 64.842 | 1104.1 | 1039.258
6476 | 0.86188 | 96.77 | 62.031 | 0.0026066 | 64.852 | 1104.1 |  | 6476 | 96.77 | 0.86188 | 62.031 | 0.0026066 | 64.852 | 1104.1 | 1039.248
6477 | 0.86214 | 96.78 | 62.031 | 0.0026073 | 64.862 | 1104.1 |  | 6477 | 96.78 | 0.86214 | 62.031 | 0.0026073 | 64.862 | 1104.1 | 1039.238
6478 | 0.86241 | 96.79 | 62.031 | 0.0026081 | 64.872 | 1104.1 |  | 6478 | 96.79 | 0.86241 | 62.031 | 0.0026081 | 64.872 | 1104.1 | 1039.228
6479 | 0.86267 | 96.8 | 62.031 | 0.0026088 | 64.882 | 1104.1 |  | 6479 | 96.8 | 0.86267 | 62.031 | 0.0026088 | 64.882 | 1104.1 | 1039.218
6480 | 0.86293 | 96.81 | 62.031 | 0.0026096 | 64.892 | 1104.1 |  | 6480 | 96.81 | 0.86293 | 62.031 | 0.0026096 | 64.892 | 1104.1 | 1039.208
6481 | 0.8632 | 96.82 | 62.031 | 0.0026103 | 64.902 | 1104.1 |  | 6481 | 96.82 | 0.8632 | 62.031 | 0.0026103 | 64.902 | 1104.1 | 1039.198
6482 | 0.86346 | 96.83 | 62.031 | 0.0026111 | 64.912 | 1104.1 |  | 6482 | 96.83 | 0.86346 | 62.031 | 0.0026111 | 64.912 | 1104.1 | 1039.188
6483 | 0.86372 | 96.84 | 62.031 | 0.0026118 | 64.922 | 1104.1 |  | 6483 | 96.84 | 0.86372 | 62.031 | 0.0026118 | 64.922 | 1104.1 | 1039.178
6484 | 0.86399 | 96.85 | 62.031 | 0.0026126 | 64.932 | 1104.1 |  | 6484 | 96.85 | 0.86399 | 62.031 | 0.0026126 | 64.932 | 1104.1 | 1039.168
6485 | 0.86425 | 96.86 | 62.03 | 0.0026133 | 64.942 | 1104.1 |  | 6485 | 96.86 | 0.86425 | 62.03 | 0.0026133 | 64.942 | 1104.1 | 1039.158
6486 | 0.86451 | 96.87 | 62.03 | 0.0026141 | 64.952 | 1104.1 |  | 6486 | 96.87 | 0.86451 | 62.03 | 0.0026141 | 64.952 | 1104.1 | 1039.148
6487 | 0.86478 | 96.88 | 62.03 | 0.0026149 | 64.962 | 1104.1 |  | 6487 | 96.88 | 0.86478 | 62.03 | 0.0026149 | 64.962 | 1104.1 | 1039.138
6488 | 0.86504 | 96.89 | 62.03 | 0.0026156 | 64.971 | 1104.1 |  | 6488 | 96.89 | 0.86504 | 62.03 | 0.0026156 | 64.971 | 1104.1 | 1039.129
6489 | 0.8653 | 96.9 | 62.03 | 0.0026164 | 64.981 | 1104.1 |  | 6489 | 96.9 | 0.8653 | 62.03 | 0.0026164 | 64.981 | 1104.1 | 1039.119
6490 | 0.86557 | 96.91 | 62.03 | 0.0026171 | 64.991 | 1104.1 |  | 6490 | 96.91 | 0.86557 | 62.03 | 0.0026171 | 64.991 | 1104.1 | 1039.109
6491 | 0.86583 | 96.92 | 62.03 | 0.0026179 | 65.001 | 1104.1 |  | 6491 | 96.92 | 0.86583 | 62.03 | 0.0026179 | 65.001 | 1104.1 | 1039.099
6492 | 0.8661 | 96.93 | 62.03 | 0.0026186 | 65.011 | 1104.1 |  | 6492 | 96.93 | 0.8661 | 62.03 | 0.0026186 | 65.011 | 1104.1 | 1039.089
6493 | 0.86636 | 96.94 | 62.029 | 0.0026194 | 65.021 | 1104.1 |  | 6493 | 96.94 | 0.86636 | 62.029 | 0.0026194 | 65.021 | 1104.1 | 1039.079
6494 | 0.86662 | 96.95 | 62.029 | 0.0026201 | 65.031 | 1104.1 |  | 6494 | 96.95 | 0.86662 | 62.029 | 0.0026201 | 65.031 | 1104.1 | 1039.069
6495 | 0.86689 | 96.96 | 62.029 | 0.0026209 | 65.041 | 1104.1 |  | 6495 | 96.96 | 0.86689 | 62.029 | 0.0026209 | 65.041 | 1104.1 | 1039.059
6496 | 0.86715 | 96.97 | 62.029 | 0.0026216 | 65.051 | 1104.1 |  | 6496 | 96.97 | 0.86715 | 62.029 | 0.0026216 | 65.051 | 1104.1 | 1039.049
6497 | 0.86742 | 96.98 | 62.029 | 0.0026224 | 65.061 | 1104.1 |  | 6497 | 96.98 | 0.86742 | 62.029 | 0.0026224 | 65.061 | 1104.1 | 1039.039
6498 | 0.86768 | 96.99 | 62.029 | 0.0026231 | 65.071 | 1104.1 |  | 6498 | 96.99 | 0.86768 | 62.029 | 0.0026231 | 65.071 | 1104.1 | 1039.029
6499 | 0.86795 | 97 | 62.029 | 0.0026239 | 65.081 | 1104.2 |  | 6499 | 97 | 0.86795 | 62.029 | 0.0026239 | 65.081 | 1104.2 | 1039.119
6500 | 0.86821 | 97.01 | 62.029 | 0.0026246 | 65.091 | 1104.2 |  | 6500 | 97.01 | 0.86821 | 62.029 | 0.0026246 | 65.091 | 1104.2 | 1039.109
6501 | 0.86847 | 97.02 | 62.028 | 0.0026254 | 65.101 | 1104.2 |  | 6501 | 97.02 | 0.86847 | 62.028 | 0.0026254 | 65.101 | 1104.2 | 1039.099
6502 | 0.86874 | 97.03 | 62.028 | 0.0026261 | 65.111 | 1104.2 |  | 6502 | 97.03 | 0.86874 | 62.028 | 0.0026261 | 65.111 | 1104.2 | 1039.089
6503 | 0.869 | 97.04 | 62.028 | 0.0026269 | 65.121 | 1104.2 |  | 6503 | 97.04 | 0.869 | 62.028 | 0.0026269 | 65.121 | 1104.2 | 1039.079
6504 | 0.86927 | 97.05 | 62.028 | 0.0026277 | 65.131 | 1104.2 |  | 6504 | 97.05 | 0.86927 | 62.028 | 0.0026277 | 65.131 | 1104.2 | 1039.069
6505 | 0.86953 | 97.06 | 62.028 | 0.0026284 | 65.141 | 1104.2 |  | 6505 | 97.06 | 0.86953 | 62.028 | 0.0026284 | 65.141 | 1104.2 | 1039.059
6506 | 0.8698 | 97.07 | 62.028 | 0.0026292 | 65.151 | 1104.2 |  | 6506 | 97.07 | 0.8698 | 62.028 | 0.0026292 | 65.151 | 1104.2 | 1039.049
6507 | 0.87006 | 97.08 | 62.028 | 0.0026299 | 65.161 | 1104.2 |  | 6507 | 97.08 | 0.87006 | 62.028 | 0.0026299 | 65.161 | 1104.2 | 1039.039
6508 | 0.87033 | 97.09 | 62.028 | 0.0026307 | 65.171 | 1104.2 |  | 6508 | 97.09 | 0.87033 | 62.028 | 0.0026307 | 65.171 | 1104.2 | 1039.029
6509 | 0.87059 | 97.1 | 62.027 | 0.0026314 | 65.181 | 1104.2 |  | 6509 | 97.1 | 0.87059 | 62.027 | 0.0026314 | 65.181 | 1104.2 | 1039.019
6510 | 0.87086 | 97.11 | 62.027 | 0.0026322 | 65.191 | 1104.2 |  | 6510 | 97.11 | 0.87086 | 62.027 | 0.0026322 | 65.191 | 1104.2 | 1039.009
6511 | 0.87112 | 97.12 | 62.027 | 0.0026329 | 65.201 | 1104.2 |  | 6511 | 97.12 | 0.87112 | 62.027 | 0.0026329 | 65.201 | 1104.2 | 1038.999
6512 | 0.87139 | 97.13 | 62.027 | 0.0026337 | 65.211 | 1104.2 |  | 6512 | 97.13 | 0.87139 | 62.027 | 0.0026337 | 65.211 | 1104.2 | 1038.989
6513 | 0.87165 | 97.14 | 62.027 | 0.0026345 | 65.221 | 1104.2 |  | 6513 | 97.14 | 0.87165 | 62.027 | 0.0026345 | 65.221 | 1104.2 | 1038.979
6514 | 0.87192 | 97.15 | 62.027 | 0.0026352 | 65.231 | 1104.2 |  | 6514 | 97.15 | 0.87192 | 62.027 | 0.0026352 | 65.231 | 1104.2 | 1038.969
6515 | 0.87219 | 97.16 | 62.027 | 0.002636 | 65.241 | 1104.2 |  | 6515 | 97.16 | 0.87219 | 62.027 | 0.002636 | 65.241 | 1104.2 | 1038.959
6516 | 0.87245 | 97.17 | 62.027 | 0.0026367 | 65.251 | 1104.2 |  | 6516 | 97.17 | 0.87245 | 62.027 | 0.0026367 | 65.251 | 1104.2 | 1038.949
6517 | 0.87272 | 97.18 | 62.026 | 0.0026375 | 65.261 | 1104.2 |  | 6517 | 97.18 | 0.87272 | 62.026 | 0.0026375 | 65.261 | 1104.2 | 1038.939
6518 | 0.87298 | 97.19 | 62.026 | 0.0026382 | 65.271 | 1104.2 |  | 6518 | 97.19 | 0.87298 | 62.026 | 0.0026382 | 65.271 | 1104.2 | 1038.929
6519 | 0.87325 | 97.2 | 62.026 | 0.002639 | 65.281 | 1104.2 |  | 6519 | 97.2 | 0.87325 | 62.026 | 0.002639 | 65.281 | 1104.2 | 1038.919
6520 | 0.87352 | 97.21 | 62.026 | 0.0026398 | 65.291 | 1104.2 |  | 6520 | 97.21 | 0.87352 | 62.026 | 0.0026398 | 65.291 | 1104.2 | 1038.909
6521 | 0.87378 | 97.22 | 62.026 | 0.0026405 | 65.301 | 1104.2 |  | 6521 | 97.22 | 0.87378 | 62.026 | 0.0026405 | 65.301 | 1104.2 | 1038.899
6522 | 0.87405 | 97.23 | 62.026 | 0.0026413 | 65.311 | 1104.3 |  | 6522 | 97.23 | 0.87405 | 62.026 | 0.0026413 | 65.311 | 1104.3 | 1038.989
6523 | 0.87431 | 97.24 | 62.026 | 0.002642 | 65.321 | 1104.3 |  | 6523 | 97.24 | 0.87431 | 62.026 | 0.002642 | 65.321 | 1104.3 | 1038.979
6524 | 0.87458 | 97.25 | 62.026 | 0.0026428 | 65.331 | 1104.3 |  | 6524 | 97.25 | 0.87458 | 62.026 | 0.0026428 | 65.331 | 1104.3 | 1038.969
6525 | 0.87485 | 97.26 | 62.026 | 0.0026435 | 65.341 | 1104.3 |  | 6525 | 97.26 | 0.87485 | 62.026 | 0.0026435 | 65.341 | 1104.3 | 1038.959
6526 | 0.87511 | 97.27 | 62.025 | 0.0026443 | 65.351 | 1104.3 |  | 6526 | 97.27 | 0.87511 | 62.025 | 0.0026443 | 65.351 | 1104.3 | 1038.949
6527 | 0.87538 | 97.28 | 62.025 | 0.0026451 | 65.361 | 1104.3 |  | 6527 | 97.28 | 0.87538 | 62.025 | 0.0026451 | 65.361 | 1104.3 | 1038.939
6528 | 0.87565 | 97.29 | 62.025 | 0.0026458 | 65.371 | 1104.3 |  | 6528 | 97.29 | 0.87565 | 62.025 | 0.0026458 | 65.371 | 1104.3 | 1038.929
6529 | 0.87591 | 97.3 | 62.025 | 0.0026466 | 65.381 | 1104.3 |  | 6529 | 97.3 | 0.87591 | 62.025 | 0.0026466 | 65.381 | 1104.3 | 1038.919
6530 | 0.87618 | 97.31 | 62.025 | 0.0026473 | 65.391 | 1104.3 |  | 6530 | 97.31 | 0.87618 | 62.025 | 0.0026473 | 65.391 | 1104.3 | 1038.909
6531 | 0.87644 | 97.32 | 62.025 | 0.0026481 | 65.401 | 1104.3 |  | 6531 | 97.32 | 0.87644 | 62.025 | 0.0026481 | 65.401 | 1104.3 | 1038.899
6532 | 0.87671 | 97.33 | 62.025 | 0.0026489 | 65.411 | 1104.3 |  | 6532 | 97.33 | 0.87671 | 62.025 | 0.0026489 | 65.411 | 1104.3 | 1038.889
6533 | 0.87698 | 97.34 | 62.025 | 0.0026496 | 65.421 | 1104.3 |  | 6533 | 97.34 | 0.87698 | 62.025 | 0.0026496 | 65.421 | 1104.3 | 1038.879
6534 | 0.87725 | 97.35 | 62.024 | 0.0026504 | 65.431 | 1104.3 |  | 6534 | 97.35 | 0.87725 | 62.024 | 0.0026504 | 65.431 | 1104.3 | 1038.869
6535 | 0.87751 | 97.36 | 62.024 | 0.0026511 | 65.441 | 1104.3 |  | 6535 | 97.36 | 0.87751 | 62.024 | 0.0026511 | 65.441 | 1104.3 | 1038.859
6536 | 0.87778 | 97.37 | 62.024 | 0.0026519 | 65.451 | 1104.3 |  | 6536 | 97.37 | 0.87778 | 62.024 | 0.0026519 | 65.451 | 1104.3 | 1038.849
6537 | 0.87805 | 97.38 | 62.024 | 0.0026527 | 65.461 | 1104.3 |  | 6537 | 97.38 | 0.87805 | 62.024 | 0.0026527 | 65.461 | 1104.3 | 1038.839
6538 | 0.87831 | 97.39 | 62.024 | 0.0026534 | 65.471 | 1104.3 |  | 6538 | 97.39 | 0.87831 | 62.024 | 0.0026534 | 65.471 | 1104.3 | 1038.829
6539 | 0.87858 | 97.4 | 62.024 | 0.0026542 | 65.481 | 1104.3 |  | 6539 | 97.4 | 0.87858 | 62.024 | 0.0026542 | 65.481 | 1104.3 | 1038.819
6540 | 0.87885 | 97.41 | 62.024 | 0.0026549 | 65.491 | 1104.3 |  | 6540 | 97.41 | 0.87885 | 62.024 | 0.0026549 | 65.491 | 1104.3 | 1038.809
6541 | 0.87912 | 97.42 | 62.024 | 0.0026557 | 65.501 | 1104.3 |  | 6541 | 97.42 | 0.87912 | 62.024 | 0.0026557 | 65.501 | 1104.3 | 1038.799
6542 | 0.87938 | 97.43 | 62.023 | 0.0026565 | 65.511 | 1104.3 |  | 6542 | 97.43 | 0.87938 | 62.023 | 0.0026565 | 65.511 | 1104.3 | 1038.789
6543 | 0.87965 | 97.44 | 62.023 | 0.0026572 | 65.521 | 1104.3 |  | 6543 | 97.44 | 0.87965 | 62.023 | 0.0026572 | 65.521 | 1104.3 | 1038.779
6544 | 0.87992 | 97.45 | 62.023 | 0.002658 | 65.531 | 1104.3 |  | 6544 | 97.45 | 0.87992 | 62.023 | 0.002658 | 65.531 | 1104.3 | 1038.769
6545 | 0.88019 | 97.46 | 62.023 | 0.0026588 | 65.541 | 1104.4 |  | 6545 | 97.46 | 0.88019 | 62.023 | 0.0026588 | 65.541 | 1104.4 | 1038.859
6546 | 0.88045 | 97.47 | 62.023 | 0.0026595 | 65.551 | 1104.4 |  | 6546 | 97.47 | 0.88045 | 62.023 | 0.0026595 | 65.551 | 1104.4 | 1038.849
6547 | 0.88072 | 97.48 | 62.023 | 0.0026603 | 65.561 | 1104.4 |  | 6547 | 97.48 | 0.88072 | 62.023 | 0.0026603 | 65.561 | 1104.4 | 1038.839
6548 | 0.88099 | 97.49 | 62.023 | 0.002661 | 65.571 | 1104.4 |  | 6548 | 97.49 | 0.88099 | 62.023 | 0.002661 | 65.571 | 1104.4 | 1038.829
6549 | 0.88126 | 97.5 | 62.023 | 0.0026618 | 65.581 | 1104.4 |  | 6549 | 97.5 | 0.88126 | 62.023 | 0.0026618 | 65.581 | 1104.4 | 1038.819
6550 | 0.88153 | 97.51 | 62.022 | 0.0026626 | 65.591 | 1104.4 |  | 6550 | 97.51 | 0.88153 | 62.022 | 0.0026626 | 65.591 | 1104.4 | 1038.809
6551 | 0.88179 | 97.52 | 62.022 | 0.0026633 | 65.601 | 1104.4 |  | 6551 | 97.52 | 0.88179 | 62.022 | 0.0026633 | 65.601 | 1104.4 | 1038.799
6552 | 0.88206 | 97.53 | 62.022 | 0.0026641 | 65.611 | 1104.4 |  | 6552 | 97.53 | 0.88206 | 62.022 | 0.0026641 | 65.611 | 1104.4 | 1038.789
6553 | 0.88233 | 97.54 | 62.022 | 0.0026649 | 65.621 | 1104.4 |  | 6553 | 97.54 | 0.88233 | 62.022 | 0.0026649 | 65.621 | 1104.4 | 1038.779
6554 | 0.8826 | 97.55 | 62.022 | 0.0026656 | 65.631 | 1104.4 |  | 6554 | 97.55 | 0.8826 | 62.022 | 0.0026656 | 65.631 | 1104.4 | 1038.769
6555 | 0.88287 | 97.56 | 62.022 | 0.0026664 | 65.641 | 1104.4 |  | 6555 | 97.56 | 0.88287 | 62.022 | 0.0026664 | 65.641 | 1104.4 | 1038.759
6556 | 0.88314 | 97.57 | 62.022 | 0.0026671 | 65.651 | 1104.4 |  | 6556 | 97.57 | 0.88314 | 62.022 | 0.0026671 | 65.651 | 1104.4 | 1038.749
6557 | 0.8834 | 97.58 | 62.022 | 0.0026679 | 65.661 | 1104.4 |  | 6557 | 97.58 | 0.8834 | 62.022 | 0.0026679 | 65.661 | 1104.4 | 1038.739
6558 | 0.88367 | 97.59 | 62.021 | 0.0026687 | 65.671 | 1104.4 |  | 6558 | 97.59 | 0.88367 | 62.021 | 0.0026687 | 65.671 | 1104.4 | 1038.729
6559 | 0.88394 | 97.6 | 62.021 | 0.0026694 | 65.681 | 1104.4 |  | 6559 | 97.6 | 0.88394 | 62.021 | 0.0026694 | 65.681 | 1104.4 | 1038.719
6560 | 0.88421 | 97.61 | 62.021 | 0.0026702 | 65.691 | 1104.4 |  | 6560 | 97.61 | 0.88421 | 62.021 | 0.0026702 | 65.691 | 1104.4 | 1038.709
6561 | 0.88448 | 97.62 | 62.021 | 0.002671 | 65.701 | 1104.4 |  | 6561 | 97.62 | 0.88448 | 62.021 | 0.002671 | 65.701 | 1104.4 | 1038.699
6562 | 0.88475 | 97.63 | 62.021 | 0.0026717 | 65.711 | 1104.4 |  | 6562 | 97.63 | 0.88475 | 62.021 | 0.0026717 | 65.711 | 1104.4 | 1038.689
6563 | 0.88502 | 97.64 | 62.021 | 0.0026725 | 65.721 | 1104.4 |  | 6563 | 97.64 | 0.88502 | 62.021 | 0.0026725 | 65.721 | 1104.4 | 1038.679
6564 | 0.88529 | 97.65 | 62.021 | 0.0026733 | 65.731 | 1104.4 |  | 6564 | 97.65 | 0.88529 | 62.021 | 0.0026733 | 65.731 | 1104.4 | 1038.669
6565 | 0.88556 | 97.66 | 62.021 | 0.002674 | 65.741 | 1104.4 |  | 6565 | 97.66 | 0.88556 | 62.021 | 0.002674 | 65.741 | 1104.4 | 1038.659
6566 | 0.88582 | 97.67 | 62.02 | 0.0026748 | 65.751 | 1104.4 |  | 6566 | 97.67 | 0.88582 | 62.02 | 0.0026748 | 65.751 | 1104.4 | 1038.649
6567 | 0.88609 | 97.68 | 62.02 | 0.0026756 | 65.761 | 1104.4 |  | 6567 | 97.68 | 0.88609 | 62.02 | 0.0026756 | 65.761 | 1104.4 | 1038.639
6568 | 0.88636 | 97.69 | 62.02 | 0.0026763 | 65.771 | 1104.4 |  | 6568 | 97.69 | 0.88636 | 62.02 | 0.0026763 | 65.771 | 1104.4 | 1038.629
6569 | 0.88663 | 97.7 | 62.02 | 0.0026771 | 65.781 | 1104.5 |  | 6569 | 97.7 | 0.88663 | 62.02 | 0.0026771 | 65.781 | 1104.5 | 1038.719
6570 | 0.8869 | 97.71 | 62.02 | 0.0026779 | 65.791 | 1104.5 |  | 6570 | 97.71 | 0.8869 | 62.02 | 0.0026779 | 65.791 | 1104.5 | 1038.709
6571 | 0.88717 | 97.72 | 62.02 | 0.0026786 | 65.801 | 1104.5 |  | 6571 | 97.72 | 0.88717 | 62.02 | 0.0026786 | 65.801 | 1104.5 | 1038.699
6572 | 0.88744 | 97.73 | 62.02 | 0.0026794 | 65.811 | 1104.5 |  | 6572 | 97.73 | 0.88744 | 62.02 | 0.0026794 | 65.811 | 1104.5 | 1038.689
6573 | 0.88771 | 97.74 | 62.02 | 0.0026802 | 65.821 | 1104.5 |  | 6573 | 97.74 | 0.88771 | 62.02 | 0.0026802 | 65.821 | 1104.5 | 1038.679
6574 | 0.88798 | 97.75 | 62.019 | 0.0026809 | 65.831 | 1104.5 |  | 6574 | 97.75 | 0.88798 | 62.019 | 0.0026809 | 65.831 | 1104.5 | 1038.669
6575 | 0.88825 | 97.76 | 62.019 | 0.0026817 | 65.841 | 1104.5 |  | 6575 | 97.76 | 0.88825 | 62.019 | 0.0026817 | 65.841 | 1104.5 | 1038.659
6576 | 0.88852 | 97.77 | 62.019 | 0.0026825 | 65.851 | 1104.5 |  | 6576 | 97.77 | 0.88852 | 62.019 | 0.0026825 | 65.851 | 1104.5 | 1038.649
6577 | 0.88879 | 97.78 | 62.019 | 0.0026832 | 65.861 | 1104.5 |  | 6577 | 97.78 | 0.88879 | 62.019 | 0.0026832 | 65.861 | 1104.5 | 1038.639
6578 | 0.88906 | 97.79 | 62.019 | 0.002684 | 65.871 | 1104.5 |  | 6578 | 97.79 | 0.88906 | 62.019 | 0.002684 | 65.871 | 1104.5 | 1038.629
6579 | 0.88933 | 97.8 | 62.019 | 0.0026848 | 65.881 | 1104.5 |  | 6579 | 97.8 | 0.88933 | 62.019 | 0.0026848 | 65.881 | 1104.5 | 1038.619
6580 | 0.8896 | 97.81 | 62.019 | 0.0026855 | 65.891 | 1104.5 |  | 6580 | 97.81 | 0.8896 | 62.019 | 0.0026855 | 65.891 | 1104.5 | 1038.609
6581 | 0.88987 | 97.82 | 62.019 | 0.0026863 | 65.901 | 1104.5 |  | 6581 | 97.82 | 0.88987 | 62.019 | 0.0026863 | 65.901 | 1104.5 | 1038.599
6582 | 0.89014 | 97.83 | 62.018 | 0.0026871 | 65.911 | 1104.5 |  | 6582 | 97.83 | 0.89014 | 62.018 | 0.0026871 | 65.911 | 1104.5 | 1038.589
6583 | 0.89041 | 97.84 | 62.018 | 0.0026879 | 65.921 | 1104.5 |  | 6583 | 97.84 | 0.89041 | 62.018 | 0.0026879 | 65.921 | 1104.5 | 1038.579
6584 | 0.89068 | 97.85 | 62.018 | 0.0026886 | 65.931 | 1104.5 |  | 6584 | 97.85 | 0.89068 | 62.018 | 0.0026886 | 65.931 | 1104.5 | 1038.569
6585 | 0.89095 | 97.86 | 62.018 | 0.0026894 | 65.941 | 1104.5 |  | 6585 | 97.86 | 0.89095 | 62.018 | 0.0026894 | 65.941 | 1104.5 | 1038.559
6586 | 0.89122 | 97.87 | 62.018 | 0.0026902 | 65.951 | 1104.5 |  | 6586 | 97.87 | 0.89122 | 62.018 | 0.0026902 | 65.951 | 1104.5 | 1038.549
6587 | 0.89149 | 97.88 | 62.018 | 0.0026909 | 65.96 | 1104.5 |  | 6587 | 97.88 | 0.89149 | 62.018 | 0.0026909 | 65.96 | 1104.5 | 1038.54
6588 | 0.89176 | 97.89 | 62.018 | 0.0026917 | 65.97 | 1104.5 |  | 6588 | 97.89 | 0.89176 | 62.018 | 0.0026917 | 65.97 | 1104.5 | 1038.53
6589 | 0.89203 | 97.9 | 62.018 | 0.0026925 | 65.98 | 1104.5 |  | 6589 | 97.9 | 0.89203 | 62.018 | 0.0026925 | 65.98 | 1104.5 | 1038.52
6590 | 0.89231 | 97.91 | 62.018 | 0.0026932 | 65.99 | 1104.5 |  | 6590 | 97.91 | 0.89231 | 62.018 | 0.0026932 | 65.99 | 1104.5 | 1038.51
6591 | 0.89258 | 97.92 | 62.017 | 0.002694 | 66 | 1104.5 |  | 6591 | 97.92 | 0.89258 | 62.017 | 0.002694 | 66 | 1104.5 | 1038.5
6592 | 0.89285 | 97.93 | 62.017 | 0.0026948 | 66.01 | 1104.6 |  | 6592 | 97.93 | 0.89285 | 62.017 | 0.0026948 | 66.01 | 1104.6 | 1038.59
6593 | 0.89312 | 97.94 | 62.017 | 0.0026956 | 66.02 | 1104.6 |  | 6593 | 97.94 | 0.89312 | 62.017 | 0.0026956 | 66.02 | 1104.6 | 1038.58
6594 | 0.89339 | 97.95 | 62.017 | 0.0026963 | 66.03 | 1104.6 |  | 6594 | 97.95 | 0.89339 | 62.017 | 0.0026963 | 66.03 | 1104.6 | 1038.57
6595 | 0.89366 | 97.96 | 62.017 | 0.0026971 | 66.04 | 1104.6 |  | 6595 | 97.96 | 0.89366 | 62.017 | 0.0026971 | 66.04 | 1104.6 | 1038.56
6596 | 0.89393 | 97.97 | 62.017 | 0.0026979 | 66.05 | 1104.6 |  | 6596 | 97.97 | 0.89393 | 62.017 | 0.0026979 | 66.05 | 1104.6 | 1038.55
6597 | 0.8942 | 97.98 | 62.017 | 0.0026986 | 66.06 | 1104.6 |  | 6597 | 97.98 | 0.8942 | 62.017 | 0.0026986 | 66.06 | 1104.6 | 1038.54
6598 | 0.89448 | 97.99 | 62.017 | 0.0026994 | 66.07 | 1104.6 |  | 6598 | 97.99 | 0.89448 | 62.017 | 0.0026994 | 66.07 | 1104.6 | 1038.53
6599 | 0.89475 | 98 | 62.016 | 0.0027002 | 66.08 | 1104.6 |  | 6599 | 98 | 0.89475 | 62.016 | 0.0027002 | 66.08 | 1104.6 | 1038.52
6600 | 0.89502 | 98.01 | 62.016 | 0.002701 | 66.09 | 1104.6 |  | 6600 | 98.01 | 0.89502 | 62.016 | 0.002701 | 66.09 | 1104.6 | 1038.51
6601 | 0.89529 | 98.02 | 62.016 | 0.0027017 | 66.1 | 1104.6 |  | 6601 | 98.02 | 0.89529 | 62.016 | 0.0027017 | 66.1 | 1104.6 | 1038.5
6602 | 0.89556 | 98.03 | 62.016 | 0.0027025 | 66.11 | 1104.6 |  | 6602 | 98.03 | 0.89556 | 62.016 | 0.0027025 | 66.11 | 1104.6 | 1038.49
6603 | 0.89583 | 98.04 | 62.016 | 0.0027033 | 66.12 | 1104.6 |  | 6603 | 98.04 | 0.89583 | 62.016 | 0.0027033 | 66.12 | 1104.6 | 1038.48
6604 | 0.89611 | 98.05 | 62.016 | 0.0027041 | 66.13 | 1104.6 |  | 6604 | 98.05 | 0.89611 | 62.016 | 0.0027041 | 66.13 | 1104.6 | 1038.47
6605 | 0.89638 | 98.06 | 62.016 | 0.0027048 | 66.14 | 1104.6 |  | 6605 | 98.06 | 0.89638 | 62.016 | 0.0027048 | 66.14 | 1104.6 | 1038.46
6606 | 0.89665 | 98.07 | 62.016 | 0.0027056 | 66.15 | 1104.6 |  | 6606 | 98.07 | 0.89665 | 62.016 | 0.0027056 | 66.15 | 1104.6 | 1038.45
6607 | 0.89692 | 98.08 | 62.015 | 0.0027064 | 66.16 | 1104.6 |  | 6607 | 98.08 | 0.89692 | 62.015 | 0.0027064 | 66.16 | 1104.6 | 1038.44
6608 | 0.89719 | 98.09 | 62.015 | 0.0027071 | 66.17 | 1104.6 |  | 6608 | 98.09 | 0.89719 | 62.015 | 0.0027071 | 66.17 | 1104.6 | 1038.43
6609 | 0.89747 | 98.1 | 62.015 | 0.0027079 | 66.18 | 1104.6 |  | 6609 | 98.1 | 0.89747 | 62.015 | 0.0027079 | 66.18 | 1104.6 | 1038.42
6610 | 0.89774 | 98.11 | 62.015 | 0.0027087 | 66.19 | 1104.6 |  | 6610 | 98.11 | 0.89774 | 62.015 | 0.0027087 | 66.19 | 1104.6 | 1038.41
6611 | 0.89801 | 98.12 | 62.015 | 0.0027095 | 66.2 | 1104.6 |  | 6611 | 98.12 | 0.89801 | 62.015 | 0.0027095 | 66.2 | 1104.6 | 1038.4
6612 | 0.89828 | 98.13 | 62.015 | 0.0027102 | 66.21 | 1104.6 |  | 6612 | 98.13 | 0.89828 | 62.015 | 0.0027102 | 66.21 | 1104.6 | 1038.39
6613 | 0.89856 | 98.14 | 62.015 | 0.002711 | 66.22 | 1104.6 |  | 6613 | 98.14 | 0.89856 | 62.015 | 0.002711 | 66.22 | 1104.6 | 1038.38
6614 | 0.89883 | 98.15 | 62.015 | 0.0027118 | 66.23 | 1104.6 |  | 6614 | 98.15 | 0.89883 | 62.015 | 0.0027118 | 66.23 | 1104.6 | 1038.37
6615 | 0.8991 | 98.16 | 62.014 | 0.0027126 | 66.24 | 1104.7 |  | 6615 | 98.16 | 0.8991 | 62.014 | 0.0027126 | 66.24 | 1104.7 | 1038.46
6616 | 0.89937 | 98.17 | 62.014 | 0.0027133 | 66.25 | 1104.7 |  | 6616 | 98.17 | 0.89937 | 62.014 | 0.0027133 | 66.25 | 1104.7 | 1038.45
6617 | 0.89965 | 98.18 | 62.014 | 0.0027141 | 66.26 | 1104.7 |  | 6617 | 98.18 | 0.89965 | 62.014 | 0.0027141 | 66.26 | 1104.7 | 1038.44
6618 | 0.89992 | 98.19 | 62.014 | 0.0027149 | 66.27 | 1104.7 |  | 6618 | 98.19 | 0.89992 | 62.014 | 0.0027149 | 66.27 | 1104.7 | 1038.43
6619 | 0.90019 | 98.2 | 62.014 | 0.0027157 | 66.28 | 1104.7 |  | 6619 | 98.2 | 0.90019 | 62.014 | 0.0027157 | 66.28 | 1104.7 | 1038.42
6620 | 0.90047 | 98.21 | 62.014 | 0.0027165 | 66.29 | 1104.7 |  | 6620 | 98.21 | 0.90047 | 62.014 | 0.0027165 | 66.29 | 1104.7 | 1038.41
6621 | 0.90074 | 98.22 | 62.014 | 0.0027172 | 66.3 | 1104.7 |  | 6621 | 98.22 | 0.90074 | 62.014 | 0.0027172 | 66.3 | 1104.7 | 1038.4
6622 | 0.90101 | 98.23 | 62.014 | 0.002718 | 66.31 | 1104.7 |  | 6622 | 98.23 | 0.90101 | 62.014 | 0.002718 | 66.31 | 1104.7 | 1038.39
6623 | 0.90128 | 98.24 | 62.013 | 0.0027188 | 66.32 | 1104.7 |  | 6623 | 98.24 | 0.90128 | 62.013 | 0.0027188 | 66.32 | 1104.7 | 1038.38
6624 | 0.90156 | 98.25 | 62.013 | 0.0027196 | 66.33 | 1104.7 |  | 6624 | 98.25 | 0.90156 | 62.013 | 0.0027196 | 66.33 | 1104.7 | 1038.37
6625 | 0.90183 | 98.26 | 62.013 | 0.0027203 | 66.34 | 1104.7 |  | 6625 | 98.26 | 0.90183 | 62.013 | 0.0027203 | 66.34 | 1104.7 | 1038.36
6626 | 0.90211 | 98.27 | 62.013 | 0.0027211 | 66.35 | 1104.7 |  | 6626 | 98.27 | 0.90211 | 62.013 | 0.0027211 | 66.35 | 1104.7 | 1038.35
6627 | 0.90238 | 98.28 | 62.013 | 0.0027219 | 66.36 | 1104.7 |  | 6627 | 98.28 | 0.90238 | 62.013 | 0.0027219 | 66.36 | 1104.7 | 1038.34
6628 | 0.90265 | 98.29 | 62.013 | 0.0027227 | 66.37 | 1104.7 |  | 6628 | 98.29 | 0.90265 | 62.013 | 0.0027227 | 66.37 | 1104.7 | 1038.33
6629 | 0.90293 | 98.3 | 62.013 | 0.0027234 | 66.38 | 1104.7 |  | 6629 | 98.3 | 0.90293 | 62.013 | 0.0027234 | 66.38 | 1104.7 | 1038.32
6630 | 0.9032 | 98.31 | 62.013 | 0.0027242 | 66.39 | 1104.7 |  | 6630 | 98.31 | 0.9032 | 62.013 | 0.0027242 | 66.39 | 1104.7 | 1038.31
6631 | 0.90347 | 98.32 | 62.012 | 0.002725 | 66.4 | 1104.7 |  | 6631 | 98.32 | 0.90347 | 62.012 | 0.002725 | 66.4 | 1104.7 | 1038.3
6632 | 0.90375 | 98.33 | 62.012 | 0.0027258 | 66.41 | 1104.7 |  | 6632 | 98.33 | 0.90375 | 62.012 | 0.0027258 | 66.41 | 1104.7 | 1038.29
6633 | 0.90402 | 98.34 | 62.012 | 0.0027266 | 66.42 | 1104.7 |  | 6633 | 98.34 | 0.90402 | 62.012 | 0.0027266 | 66.42 | 1104.7 | 1038.28
6634 | 0.9043 | 98.35 | 62.012 | 0.0027273 | 66.43 | 1104.7 |  | 6634 | 98.35 | 0.9043 | 62.012 | 0.0027273 | 66.43 | 1104.7 | 1038.27
6635 | 0.90457 | 98.36 | 62.012 | 0.0027281 | 66.44 | 1104.7 |  | 6635 | 98.36 | 0.90457 | 62.012 | 0.0027281 | 66.44 | 1104.7 | 1038.26
6636 | 0.90484 | 98.37 | 62.012 | 0.0027289 | 66.45 | 1104.7 |  | 6636 | 98.37 | 0.90484 | 62.012 | 0.0027289 | 66.45 | 1104.7 | 1038.25
6637 | 0.90512 | 98.38 | 62.012 | 0.0027297 | 66.46 | 1104.7 |  | 6637 | 98.38 | 0.90512 | 62.012 | 0.0027297 | 66.46 | 1104.7 | 1038.24
6638 | 0.90539 | 98.39 | 62.012 | 0.0027305 | 66.47 | 1104.7 |  | 6638 | 98.39 | 0.90539 | 62.012 | 0.0027305 | 66.47 | 1104.7 | 1038.23
6639 | 0.90567 | 98.4 | 62.011 | 0.0027312 | 66.48 | 1104.8 |  | 6639 | 98.4 | 0.90567 | 62.011 | 0.0027312 | 66.48 | 1104.8 | 1038.32
6640 | 0.90594 | 98.41 | 62.011 | 0.002732 | 66.49 | 1104.8 |  | 6640 | 98.41 | 0.90594 | 62.011 | 0.002732 | 66.49 | 1104.8 | 1038.31
6641 | 0.90622 | 98.42 | 62.011 | 0.0027328 | 66.5 | 1104.8 |  | 6641 | 98.42 | 0.90622 | 62.011 | 0.0027328 | 66.5 | 1104.8 | 1038.3
6642 | 0.90649 | 98.43 | 62.011 | 0.0027336 | 66.51 | 1104.8 |  | 6642 | 98.43 | 0.90649 | 62.011 | 0.0027336 | 66.51 | 1104.8 | 1038.29
6643 | 0.90676 | 98.44 | 62.011 | 0.0027344 | 66.52 | 1104.8 |  | 6643 | 98.44 | 0.90676 | 62.011 | 0.0027344 | 66.52 | 1104.8 | 1038.28
6644 | 0.90704 | 98.45 | 62.011 | 0.0027351 | 66.53 | 1104.8 |  | 6644 | 98.45 | 0.90704 | 62.011 | 0.0027351 | 66.53 | 1104.8 | 1038.27
6645 | 0.90731 | 98.46 | 62.011 | 0.0027359 | 66.54 | 1104.8 |  | 6645 | 98.46 | 0.90731 | 62.011 | 0.0027359 | 66.54 | 1104.8 | 1038.26
6646 | 0.90759 | 98.47 | 62.011 | 0.0027367 | 66.55 | 1104.8 |  | 6646 | 98.47 | 0.90759 | 62.011 | 0.0027367 | 66.55 | 1104.8 | 1038.25
6647 | 0.90786 | 98.48 | 62.01 | 0.0027375 | 66.56 | 1104.8 |  | 6647 | 98.48 | 0.90786 | 62.01 | 0.0027375 | 66.56 | 1104.8 | 1038.24
6648 | 0.90814 | 98.49 | 62.01 | 0.0027383 | 66.57 | 1104.8 |  | 6648 | 98.49 | 0.90814 | 62.01 | 0.0027383 | 66.57 | 1104.8 | 1038.23
6649 | 0.90841 | 98.5 | 62.01 | 0.002739 | 66.58 | 1104.8 |  | 6649 | 98.5 | 0.90841 | 62.01 | 0.002739 | 66.58 | 1104.8 | 1038.22
6650 | 0.90869 | 98.51 | 62.01 | 0.0027398 | 66.59 | 1104.8 |  | 6650 | 98.51 | 0.90869 | 62.01 | 0.0027398 | 66.59 | 1104.8 | 1038.21
6651 | 0.90896 | 98.52 | 62.01 | 0.0027406 | 66.6 | 1104.8 |  | 6651 | 98.52 | 0.90896 | 62.01 | 0.0027406 | 66.6 | 1104.8 | 1038.2
6652 | 0.90924 | 98.53 | 62.01 | 0.0027414 | 66.61 | 1104.8 |  | 6652 | 98.53 | 0.90924 | 62.01 | 0.0027414 | 66.61 | 1104.8 | 1038.19
6653 | 0.90952 | 98.54 | 62.01 | 0.0027422 | 66.62 | 1104.8 |  | 6653 | 98.54 | 0.90952 | 62.01 | 0.0027422 | 66.62 | 1104.8 | 1038.18
6654 | 0.90979 | 98.55 | 62.01 | 0.002743 | 66.63 | 1104.8 |  | 6654 | 98.55 | 0.90979 | 62.01 | 0.002743 | 66.63 | 1104.8 | 1038.17
6655 | 0.91007 | 98.56 | 62.009 | 0.0027437 | 66.64 | 1104.8 |  | 6655 | 98.56 | 0.91007 | 62.009 | 0.0027437 | 66.64 | 1104.8 | 1038.16
6656 | 0.91034 | 98.57 | 62.009 | 0.0027445 | 66.65 | 1104.8 |  | 6656 | 98.57 | 0.91034 | 62.009 | 0.0027445 | 66.65 | 1104.8 | 1038.15
6657 | 0.91062 | 98.58 | 62.009 | 0.0027453 | 66.66 | 1104.8 |  | 6657 | 98.58 | 0.91062 | 62.009 | 0.0027453 | 66.66 | 1104.8 | 1038.14
6658 | 0.91089 | 98.59 | 62.009 | 0.0027461 | 66.67 | 1104.8 |  | 6658 | 98.59 | 0.91089 | 62.009 | 0.0027461 | 66.67 | 1104.8 | 1038.13
6659 | 0.91117 | 98.6 | 62.009 | 0.0027469 | 66.68 | 1104.8 |  | 6659 | 98.6 | 0.91117 | 62.009 | 0.0027469 | 66.68 | 1104.8 | 1038.12
6660 | 0.91145 | 98.61 | 62.009 | 0.0027477 | 66.69 | 1104.8 |  | 6660 | 98.61 | 0.91145 | 62.009 | 0.0027477 | 66.69 | 1104.8 | 1038.11
6661 | 0.91172 | 98.62 | 62.009 | 0.0027484 | 66.7 | 1104.8 |  | 6661 | 98.62 | 0.91172 | 62.009 | 0.0027484 | 66.7 | 1104.8 | 1038.1
6662 | 0.912 | 98.63 | 62.009 | 0.0027492 | 66.71 | 1104.9 |  | 6662 | 98.63 | 0.912 | 62.009 | 0.0027492 | 66.71 | 1104.9 | 1038.19
6663 | 0.91227 | 98.64 | 62.008 | 0.00275 | 66.72 | 1104.9 |  | 6663 | 98.64 | 0.91227 | 62.008 | 0.00275 | 66.72 | 1104.9 | 1038.18
6664 | 0.91255 | 98.65 | 62.008 | 0.0027508 | 66.73 | 1104.9 |  | 6664 | 98.65 | 0.91255 | 62.008 | 0.0027508 | 66.73 | 1104.9 | 1038.17
6665 | 0.91283 | 98.66 | 62.008 | 0.0027516 | 66.74 | 1104.9 |  | 6665 | 98.66 | 0.91283 | 62.008 | 0.0027516 | 66.74 | 1104.9 | 1038.16
6666 | 0.9131 | 98.67 | 62.008 | 0.0027524 | 66.75 | 1104.9 |  | 6666 | 98.67 | 0.9131 | 62.008 | 0.0027524 | 66.75 | 1104.9 | 1038.15
6667 | 0.91338 | 98.68 | 62.008 | 0.0027532 | 66.76 | 1104.9 |  | 6667 | 98.68 | 0.91338 | 62.008 | 0.0027532 | 66.76 | 1104.9 | 1038.14
6668 | 0.91366 | 98.69 | 62.008 | 0.0027539 | 66.77 | 1104.9 |  | 6668 | 98.69 | 0.91366 | 62.008 | 0.0027539 | 66.77 | 1104.9 | 1038.13
6669 | 0.91393 | 98.7 | 62.008 | 0.0027547 | 66.78 | 1104.9 |  | 6669 | 98.7 | 0.91393 | 62.008 | 0.0027547 | 66.78 | 1104.9 | 1038.12
6670 | 0.91421 | 98.71 | 62.008 | 0.0027555 | 66.79 | 1104.9 |  | 6670 | 98.71 | 0.91421 | 62.008 | 0.0027555 | 66.79 | 1104.9 | 1038.11
6671 | 0.91449 | 98.72 | 62.007 | 0.0027563 | 66.8 | 1104.9 |  | 6671 | 98.72 | 0.91449 | 62.007 | 0.0027563 | 66.8 | 1104.9 | 1038.1
6672 | 0.91476 | 98.73 | 62.007 | 0.0027571 | 66.81 | 1104.9 |  | 6672 | 98.73 | 0.91476 | 62.007 | 0.0027571 | 66.81 | 1104.9 | 1038.09
6673 | 0.91504 | 98.74 | 62.007 | 0.0027579 | 66.82 | 1104.9 |  | 6673 | 98.74 | 0.91504 | 62.007 | 0.0027579 | 66.82 | 1104.9 | 1038.08
6674 | 0.91532 | 98.75 | 62.007 | 0.0027587 | 66.83 | 1104.9 |  | 6674 | 98.75 | 0.91532 | 62.007 | 0.0027587 | 66.83 | 1104.9 | 1038.07
6675 | 0.91559 | 98.76 | 62.007 | 0.0027594 | 66.84 | 1104.9 |  | 6675 | 98.76 | 0.91559 | 62.007 | 0.0027594 | 66.84 | 1104.9 | 1038.06
6676 | 0.91587 | 98.77 | 62.007 | 0.0027602 | 66.85 | 1104.9 |  | 6676 | 98.77 | 0.91587 | 62.007 | 0.0027602 | 66.85 | 1104.9 | 1038.05
6677 | 0.91615 | 98.78 | 62.007 | 0.002761 | 66.86 | 1104.9 |  | 6677 | 98.78 | 0.91615 | 62.007 | 0.002761 | 66.86 | 1104.9 | 1038.04
6678 | 0.91642 | 98.79 | 62.007 | 0.0027618 | 66.87 | 1104.9 |  | 6678 | 98.79 | 0.91642 | 62.007 | 0.0027618 | 66.87 | 1104.9 | 1038.03
6679 | 0.9167 | 98.8 | 62.006 | 0.0027626 | 66.88 | 1104.9 |  | 6679 | 98.8 | 0.9167 | 62.006 | 0.0027626 | 66.88 | 1104.9 | 1038.02
6680 | 0.91698 | 98.81 | 62.006 | 0.0027634 | 66.89 | 1104.9 |  | 6680 | 98.81 | 0.91698 | 62.006 | 0.0027634 | 66.89 | 1104.9 | 1038.01
6681 | 0.91726 | 98.82 | 62.006 | 0.0027642 | 66.9 | 1104.9 |  | 6681 | 98.82 | 0.91726 | 62.006 | 0.0027642 | 66.9 | 1104.9 | 1038
6682 | 0.91753 | 98.83 | 62.006 | 0.002765 | 66.91 | 1104.9 |  | 6682 | 98.83 | 0.91753 | 62.006 | 0.002765 | 66.91 | 1104.9 | 1037.99
6683 | 0.91781 | 98.84 | 62.006 | 0.0027657 | 66.92 | 1104.9 |  | 6683 | 98.84 | 0.91781 | 62.006 | 0.0027657 | 66.92 | 1104.9 | 1037.98
6684 | 0.91809 | 98.85 | 62.006 | 0.0027665 | 66.93 | 1104.9 |  | 6684 | 98.85 | 0.91809 | 62.006 | 0.0027665 | 66.93 | 1104.9 | 1037.97
6685 | 0.91837 | 98.86 | 62.006 | 0.0027673 | 66.94 | 1105 |  | 6685 | 98.86 | 0.91837 | 62.006 | 0.0027673 | 66.94 | 1105 | 1038.06
6686 | 0.91864 | 98.87 | 62.006 | 0.0027681 | 66.949 | 1105 |  | 6686 | 98.87 | 0.91864 | 62.006 | 0.0027681 | 66.949 | 1105 | 1038.051
6687 | 0.91892 | 98.88 | 62.005 | 0.0027689 | 66.959 | 1105 |  | 6687 | 98.88 | 0.91892 | 62.005 | 0.0027689 | 66.959 | 1105 | 1038.041
6688 | 0.9192 | 98.89 | 62.005 | 0.0027697 | 66.969 | 1105 |  | 6688 | 98.89 | 0.9192 | 62.005 | 0.0027697 | 66.969 | 1105 | 1038.031
6689 | 0.91948 | 98.9 | 62.005 | 0.0027705 | 66.979 | 1105 |  | 6689 | 98.9 | 0.91948 | 62.005 | 0.0027705 | 66.979 | 1105 | 1038.021
6690 | 0.91976 | 98.91 | 62.005 | 0.0027713 | 66.989 | 1105 |  | 6690 | 98.91 | 0.91976 | 62.005 | 0.0027713 | 66.989 | 1105 | 1038.011
6691 | 0.92003 | 98.92 | 62.005 | 0.0027721 | 66.999 | 1105 |  | 6691 | 98.92 | 0.92003 | 62.005 | 0.0027721 | 66.999 | 1105 | 1038.001
6692 | 0.92031 | 98.93 | 62.005 | 0.0027728 | 67.009 | 1105 |  | 6692 | 98.93 | 0.92031 | 62.005 | 0.0027728 | 67.009 | 1105 | 1037.991
6693 | 0.92059 | 98.94 | 62.005 | 0.0027736 | 67.019 | 1105 |  | 6693 | 98.94 | 0.92059 | 62.005 | 0.0027736 | 67.019 | 1105 | 1037.981
6694 | 0.92087 | 98.95 | 62.005 | 0.0027744 | 67.029 | 1105 |  | 6694 | 98.95 | 0.92087 | 62.005 | 0.0027744 | 67.029 | 1105 | 1037.971
6695 | 0.92115 | 98.96 | 62.004 | 0.0027752 | 67.039 | 1105 |  | 6695 | 98.96 | 0.92115 | 62.004 | 0.0027752 | 67.039 | 1105 | 1037.961
6696 | 0.92143 | 98.97 | 62.004 | 0.002776 | 67.049 | 1105 |  | 6696 | 98.97 | 0.92143 | 62.004 | 0.002776 | 67.049 | 1105 | 1037.951
6697 | 0.9217 | 98.98 | 62.004 | 0.0027768 | 67.059 | 1105 |  | 6697 | 98.98 | 0.9217 | 62.004 | 0.0027768 | 67.059 | 1105 | 1037.941
6698 | 0.92198 | 98.99 | 62.004 | 0.0027776 | 67.069 | 1105 |  | 6698 | 98.99 | 0.92198 | 62.004 | 0.0027776 | 67.069 | 1105 | 1037.931
6699 | 0.92226 | 99 | 62.004 | 0.0027784 | 67.079 | 1105 |  | 6699 | 99 | 0.92226 | 62.004 | 0.0027784 | 67.079 | 1105 | 1037.921
6700 | 0.92254 | 99.01 | 62.004 | 0.0027792 | 67.089 | 1105 |  | 6700 | 99.01 | 0.92254 | 62.004 | 0.0027792 | 67.089 | 1105 | 1037.911
6701 | 0.92282 | 99.02 | 62.004 | 0.00278 | 67.099 | 1105 |  | 6701 | 99.02 | 0.92282 | 62.004 | 0.00278 | 67.099 | 1105 | 1037.901
6702 | 0.9231 | 99.03 | 62.004 | 0.0027808 | 67.109 | 1105 |  | 6702 | 99.03 | 0.9231 | 62.004 | 0.0027808 | 67.109 | 1105 | 1037.891
6703 | 0.92338 | 99.04 | 62.003 | 0.0027815 | 67.119 | 1105 |  | 6703 | 99.04 | 0.92338 | 62.003 | 0.0027815 | 67.119 | 1105 | 1037.881
6704 | 0.92366 | 99.05 | 62.003 | 0.0027823 | 67.129 | 1105 |  | 6704 | 99.05 | 0.92366 | 62.003 | 0.0027823 | 67.129 | 1105 | 1037.871
6705 | 0.92394 | 99.06 | 62.003 | 0.0027831 | 67.139 | 1105 |  | 6705 | 99.06 | 0.92394 | 62.003 | 0.0027831 | 67.139 | 1105 | 1037.861
6706 | 0.92422 | 99.07 | 62.003 | 0.0027839 | 67.149 | 1105 |  | 6706 | 99.07 | 0.92422 | 62.003 | 0.0027839 | 67.149 | 1105 | 1037.851
6707 | 0.92449 | 99.08 | 62.003 | 0.0027847 | 67.159 | 1105 |  | 6707 | 99.08 | 0.92449 | 62.003 | 0.0027847 | 67.159 | 1105 | 1037.841
6708 | 0.92477 | 99.09 | 62.003 | 0.0027855 | 67.169 | 1105 |  | 6708 | 99.09 | 0.92477 | 62.003 | 0.0027855 | 67.169 | 1105 | 1037.831
6709 | 0.92505 | 99.1 | 62.003 | 0.0027863 | 67.179 | 1105.1 |  | 6709 | 99.1 | 0.92505 | 62.003 | 0.0027863 | 67.179 | 1105.1 | 1037.921
6710 | 0.92533 | 99.11 | 62.003 | 0.0027871 | 67.189 | 1105.1 |  | 6710 | 99.11 | 0.92533 | 62.003 | 0.0027871 | 67.189 | 1105.1 | 1037.911
6711 | 0.92561 | 99.12 | 62.002 | 0.0027879 | 67.199 | 1105.1 |  | 6711 | 99.12 | 0.92561 | 62.002 | 0.0027879 | 67.199 | 1105.1 | 1037.901
6712 | 0.92589 | 99.13 | 62.002 | 0.0027887 | 67.209 | 1105.1 |  | 6712 | 99.13 | 0.92589 | 62.002 | 0.0027887 | 67.209 | 1105.1 | 1037.891
6713 | 0.92617 | 99.14 | 62.002 | 0.0027895 | 67.219 | 1105.1 |  | 6713 | 99.14 | 0.92617 | 62.002 | 0.0027895 | 67.219 | 1105.1 | 1037.881
6714 | 0.92645 | 99.15 | 62.002 | 0.0027903 | 67.229 | 1105.1 |  | 6714 | 99.15 | 0.92645 | 62.002 | 0.0027903 | 67.229 | 1105.1 | 1037.871
6715 | 0.92673 | 99.16 | 62.002 | 0.0027911 | 67.239 | 1105.1 |  | 6715 | 99.16 | 0.92673 | 62.002 | 0.0027911 | 67.239 | 1105.1 | 1037.861
6716 | 0.92701 | 99.17 | 62.002 | 0.0027919 | 67.249 | 1105.1 |  | 6716 | 99.17 | 0.92701 | 62.002 | 0.0027919 | 67.249 | 1105.1 | 1037.851
6717 | 0.92729 | 99.18 | 62.002 | 0.0027927 | 67.259 | 1105.1 |  | 6717 | 99.18 | 0.92729 | 62.002 | 0.0027927 | 67.259 | 1105.1 | 1037.841
6718 | 0.92757 | 99.19 | 62.002 | 0.0027935 | 67.269 | 1105.1 |  | 6718 | 99.19 | 0.92757 | 62.002 | 0.0027935 | 67.269 | 1105.1 | 1037.831
6719 | 0.92785 | 99.2 | 62.001 | 0.0027942 | 67.279 | 1105.1 |  | 6719 | 99.2 | 0.92785 | 62.001 | 0.0027942 | 67.279 | 1105.1 | 1037.821
6720 | 0.92813 | 99.21 | 62.001 | 0.002795 | 67.289 | 1105.1 |  | 6720 | 99.21 | 0.92813 | 62.001 | 0.002795 | 67.289 | 1105.1 | 1037.811
6721 | 0.92841 | 99.22 | 62.001 | 0.0027958 | 67.299 | 1105.1 |  | 6721 | 99.22 | 0.92841 | 62.001 | 0.0027958 | 67.299 | 1105.1 | 1037.801
6722 | 0.92869 | 99.23 | 62.001 | 0.0027966 | 67.309 | 1105.1 |  | 6722 | 99.23 | 0.92869 | 62.001 | 0.0027966 | 67.309 | 1105.1 | 1037.791
6723 | 0.92897 | 99.24 | 62.001 | 0.0027974 | 67.319 | 1105.1 |  | 6723 | 99.24 | 0.92897 | 62.001 | 0.0027974 | 67.319 | 1105.1 | 1037.781
6724 | 0.92925 | 99.25 | 62.001 | 0.0027982 | 67.329 | 1105.1 |  | 6724 | 99.25 | 0.92925 | 62.001 | 0.0027982 | 67.329 | 1105.1 | 1037.771
6725 | 0.92953 | 99.26 | 62.001 | 0.002799 | 67.339 | 1105.1 |  | 6725 | 99.26 | 0.92953 | 62.001 | 0.002799 | 67.339 | 1105.1 | 1037.761
6726 | 0.92982 | 99.27 | 62.001 | 0.0027998 | 67.349 | 1105.1 |  | 6726 | 99.27 | 0.92982 | 62.001 | 0.0027998 | 67.349 | 1105.1 | 1037.751
6727 | 0.9301 | 99.28 | 62 | 0.0028006 | 67.359 | 1105.1 |  | 6727 | 99.28 | 0.9301 | 62 | 0.0028006 | 67.359 | 1105.1 | 1037.741
6728 | 0.93038 | 99.29 | 62 | 0.0028014 | 67.369 | 1105.1 |  | 6728 | 99.29 | 0.93038 | 62 | 0.0028014 | 67.369 | 1105.1 | 1037.731
6729 | 0.93066 | 99.3 | 62 | 0.0028022 | 67.379 | 1105.1 |  | 6729 | 99.3 | 0.93066 | 62 | 0.0028022 | 67.379 | 1105.1 | 1037.721
6730 | 0.93094 | 99.31 | 62 | 0.002803 | 67.389 | 1105.1 |  | 6730 | 99.31 | 0.93094 | 62 | 0.002803 | 67.389 | 1105.1 | 1037.711
6731 | 0.93122 | 99.32 | 62 | 0.0028038 | 67.399 | 1105.1 |  | 6731 | 99.32 | 0.93122 | 62 | 0.0028038 | 67.399 | 1105.1 | 1037.701
6732 | 0.9315 | 99.33 | 62 | 0.0028046 | 67.409 | 1105.2 |  | 6732 | 99.33 | 0.9315 | 62 | 0.0028046 | 67.409 | 1105.2 | 1037.791
6733 | 0.93178 | 99.34 | 62 | 0.0028054 | 67.419 | 1105.2 |  | 6733 | 99.34 | 0.93178 | 62 | 0.0028054 | 67.419 | 1105.2 | 1037.781
6734 | 0.93206 | 99.35 | 62 | 0.0028062 | 67.429 | 1105.2 |  | 6734 | 99.35 | 0.93206 | 62 | 0.0028062 | 67.429 | 1105.2 | 1037.771
6735 | 0.93235 | 99.36 | 61.999 | 0.002807 | 67.439 | 1105.2 |  | 6735 | 99.36 | 0.93235 | 61.999 | 0.002807 | 67.439 | 1105.2 | 1037.761
6736 | 0.93263 | 99.37 | 61.999 | 0.0028078 | 67.449 | 1105.2 |  | 6736 | 99.37 | 0.93263 | 61.999 | 0.0028078 | 67.449 | 1105.2 | 1037.751
6737 | 0.93291 | 99.38 | 61.999 | 0.0028086 | 67.459 | 1105.2 |  | 6737 | 99.38 | 0.93291 | 61.999 | 0.0028086 | 67.459 | 1105.2 | 1037.741
6738 | 0.93319 | 99.39 | 61.999 | 0.0028094 | 67.469 | 1105.2 |  | 6738 | 99.39 | 0.93319 | 61.999 | 0.0028094 | 67.469 | 1105.2 | 1037.731
6739 | 0.93347 | 99.4 | 61.999 | 0.0028102 | 67.479 | 1105.2 |  | 6739 | 99.4 | 0.93347 | 61.999 | 0.0028102 | 67.479 | 1105.2 | 1037.721
6740 | 0.93375 | 99.41 | 61.999 | 0.002811 | 67.489 | 1105.2 |  | 6740 | 99.41 | 0.93375 | 61.999 | 0.002811 | 67.489 | 1105.2 | 1037.711
6741 | 0.93403 | 99.42 | 61.999 | 0.0028118 | 67.499 | 1105.2 |  | 6741 | 99.42 | 0.93403 | 61.999 | 0.0028118 | 67.499 | 1105.2 | 1037.701
6742 | 0.93432 | 99.43 | 61.999 | 0.0028126 | 67.509 | 1105.2 |  | 6742 | 99.43 | 0.93432 | 61.999 | 0.0028126 | 67.509 | 1105.2 | 1037.691
6743 | 0.9346 | 99.44 | 61.998 | 0.0028134 | 67.519 | 1105.2 |  | 6743 | 99.44 | 0.9346 | 61.998 | 0.0028134 | 67.519 | 1105.2 | 1037.681
6744 | 0.93488 | 99.45 | 61.998 | 0.0028142 | 67.529 | 1105.2 |  | 6744 | 99.45 | 0.93488 | 61.998 | 0.0028142 | 67.529 | 1105.2 | 1037.671
6745 | 0.93516 | 99.46 | 61.998 | 0.002815 | 67.539 | 1105.2 |  | 6745 | 99.46 | 0.93516 | 61.998 | 0.002815 | 67.539 | 1105.2 | 1037.661
6746 | 0.93545 | 99.47 | 61.998 | 0.0028158 | 67.549 | 1105.2 |  | 6746 | 99.47 | 0.93545 | 61.998 | 0.0028158 | 67.549 | 1105.2 | 1037.651
6747 | 0.93573 | 99.48 | 61.998 | 0.0028166 | 67.559 | 1105.2 |  | 6747 | 99.48 | 0.93573 | 61.998 | 0.0028166 | 67.559 | 1105.2 | 1037.641
6748 | 0.93601 | 99.49 | 61.998 | 0.0028174 | 67.569 | 1105.2 |  | 6748 | 99.49 | 0.93601 | 61.998 | 0.0028174 | 67.569 | 1105.2 | 1037.631
6749 | 0.93629 | 99.5 | 61.998 | 0.0028182 | 67.579 | 1105.2 |  | 6749 | 99.5 | 0.93629 | 61.998 | 0.0028182 | 67.579 | 1105.2 | 1037.621
6750 | 0.93657 | 99.51 | 61.998 | 0.002819 | 67.589 | 1105.2 |  | 6750 | 99.51 | 0.93657 | 61.998 | 0.002819 | 67.589 | 1105.2 | 1037.611
6751 | 0.93686 | 99.52 | 61.997 | 0.0028198 | 67.599 | 1105.2 |  | 6751 | 99.52 | 0.93686 | 61.997 | 0.0028198 | 67.599 | 1105.2 | 1037.601
6752 | 0.93714 | 99.53 | 61.997 | 0.0028206 | 67.609 | 1105.2 |  | 6752 | 99.53 | 0.93714 | 61.997 | 0.0028206 | 67.609 | 1105.2 | 1037.591
6753 | 0.93742 | 99.54 | 61.997 | 0.0028214 | 67.619 | 1105.2 |  | 6753 | 99.54 | 0.93742 | 61.997 | 0.0028214 | 67.619 | 1105.2 | 1037.581
6754 | 0.93771 | 99.55 | 61.997 | 0.0028222 | 67.629 | 1105.2 |  | 6754 | 99.55 | 0.93771 | 61.997 | 0.0028222 | 67.629 | 1105.2 | 1037.571
6755 | 0.93799 | 99.56 | 61.997 | 0.002823 | 67.639 | 1105.3 |  | 6755 | 99.56 | 0.93799 | 61.997 | 0.002823 | 67.639 | 1105.3 | 1037.661
6756 | 0.93827 | 99.57 | 61.997 | 0.0028238 | 67.649 | 1105.3 |  | 6756 | 99.57 | 0.93827 | 61.997 | 0.0028238 | 67.649 | 1105.3 | 1037.651
6757 | 0.93855 | 99.58 | 61.997 | 0.0028246 | 67.659 | 1105.3 |  | 6757 | 99.58 | 0.93855 | 61.997 | 0.0028246 | 67.659 | 1105.3 | 1037.641
6758 | 0.93884 | 99.59 | 61.997 | 0.0028254 | 67.669 | 1105.3 |  | 6758 | 99.59 | 0.93884 | 61.997 | 0.0028254 | 67.669 | 1105.3 | 1037.631
6759 | 0.93912 | 99.6 | 61.996 | 0.0028262 | 67.679 | 1105.3 |  | 6759 | 99.6 | 0.93912 | 61.996 | 0.0028262 | 67.679 | 1105.3 | 1037.621
6760 | 0.9394 | 99.61 | 61.996 | 0.002827 | 67.689 | 1105.3 |  | 6760 | 99.61 | 0.9394 | 61.996 | 0.002827 | 67.689 | 1105.3 | 1037.611
6761 | 0.93969 | 99.62 | 61.996 | 0.0028278 | 67.699 | 1105.3 |  | 6761 | 99.62 | 0.93969 | 61.996 | 0.0028278 | 67.699 | 1105.3 | 1037.601
6762 | 0.93997 | 99.63 | 61.996 | 0.0028286 | 67.709 | 1105.3 |  | 6762 | 99.63 | 0.93997 | 61.996 | 0.0028286 | 67.709 | 1105.3 | 1037.591
6763 | 0.94025 | 99.64 | 61.996 | 0.0028294 | 67.719 | 1105.3 |  | 6763 | 99.64 | 0.94025 | 61.996 | 0.0028294 | 67.719 | 1105.3 | 1037.581
6764 | 0.94054 | 99.65 | 61.996 | 0.0028302 | 67.729 | 1105.3 |  | 6764 | 99.65 | 0.94054 | 61.996 | 0.0028302 | 67.729 | 1105.3 | 1037.571
6765 | 0.94082 | 99.66 | 61.996 | 0.002831 | 67.739 | 1105.3 |  | 6765 | 99.66 | 0.94082 | 61.996 | 0.002831 | 67.739 | 1105.3 | 1037.561
6766 | 0.9411 | 99.67 | 61.996 | 0.0028318 | 67.749 | 1105.3 |  | 6766 | 99.67 | 0.9411 | 61.996 | 0.0028318 | 67.749 | 1105.3 | 1037.551
6767 | 0.94139 | 99.68 | 61.995 | 0.0028326 | 67.759 | 1105.3 |  | 6767 | 99.68 | 0.94139 | 61.995 | 0.0028326 | 67.759 | 1105.3 | 1037.541
6768 | 0.94167 | 99.69 | 61.995 | 0.0028334 | 67.769 | 1105.3 |  | 6768 | 99.69 | 0.94167 | 61.995 | 0.0028334 | 67.769 | 1105.3 | 1037.531
6769 | 0.94196 | 99.7 | 61.995 | 0.0028343 | 67.779 | 1105.3 |  | 6769 | 99.7 | 0.94196 | 61.995 | 0.0028343 | 67.779 | 1105.3 | 1037.521
6770 | 0.94224 | 99.71 | 61.995 | 0.0028351 | 67.789 | 1105.3 |  | 6770 | 99.71 | 0.94224 | 61.995 | 0.0028351 | 67.789 | 1105.3 | 1037.511
6771 | 0.94252 | 99.72 | 61.995 | 0.0028359 | 67.799 | 1105.3 |  | 6771 | 99.72 | 0.94252 | 61.995 | 0.0028359 | 67.799 | 1105.3 | 1037.501
6772 | 0.94281 | 99.73 | 61.995 | 0.0028367 | 67.809 | 1105.3 |  | 6772 | 99.73 | 0.94281 | 61.995 | 0.0028367 | 67.809 | 1105.3 | 1037.491
6773 | 0.94309 | 99.74 | 61.995 | 0.0028375 | 67.819 | 1105.3 |  | 6773 | 99.74 | 0.94309 | 61.995 | 0.0028375 | 67.819 | 1105.3 | 1037.481
6774 | 0.94338 | 99.75 | 61.995 | 0.0028383 | 67.829 | 1105.3 |  | 6774 | 99.75 | 0.94338 | 61.995 | 0.0028383 | 67.829 | 1105.3 | 1037.471
6775 | 0.94366 | 99.76 | 61.994 | 0.0028391 | 67.839 | 1105.3 |  | 6775 | 99.76 | 0.94366 | 61.994 | 0.0028391 | 67.839 | 1105.3 | 1037.461
6776 | 0.94394 | 99.77 | 61.994 | 0.0028399 | 67.849 | 1105.3 |  | 6776 | 99.77 | 0.94394 | 61.994 | 0.0028399 | 67.849 | 1105.3 | 1037.451
6777 | 0.94423 | 99.78 | 61.994 | 0.0028407 | 67.859 | 1105.3 |  | 6777 | 99.78 | 0.94423 | 61.994 | 0.0028407 | 67.859 | 1105.3 | 1037.441
6778 | 0.94451 | 99.79 | 61.994 | 0.0028415 | 67.869 | 1105.3 |  | 6778 | 99.79 | 0.94451 | 61.994 | 0.0028415 | 67.869 | 1105.3 | 1037.431
6779 | 0.9448 | 99.8 | 61.994 | 0.0028423 | 67.879 | 1105.4 |  | 6779 | 99.8 | 0.9448 | 61.994 | 0.0028423 | 67.879 | 1105.4 | 1037.521
6780 | 0.94508 | 99.81 | 61.994 | 0.0028431 | 67.889 | 1105.4 |  | 6780 | 99.81 | 0.94508 | 61.994 | 0.0028431 | 67.889 | 1105.4 | 1037.511
6781 | 0.94537 | 99.82 | 61.994 | 0.0028439 | 67.899 | 1105.4 |  | 6781 | 99.82 | 0.94537 | 61.994 | 0.0028439 | 67.899 | 1105.4 | 1037.501
6782 | 0.94565 | 99.83 | 61.993 | 0.0028447 | 67.909 | 1105.4 |  | 6782 | 99.83 | 0.94565 | 61.993 | 0.0028447 | 67.909 | 1105.4 | 1037.491
6783 | 0.94594 | 99.84 | 61.993 | 0.0028455 | 67.919 | 1105.4 |  | 6783 | 99.84 | 0.94594 | 61.993 | 0.0028455 | 67.919 | 1105.4 | 1037.481
6784 | 0.94622 | 99.85 | 61.993 | 0.0028464 | 67.929 | 1105.4 |  | 6784 | 99.85 | 0.94622 | 61.993 | 0.0028464 | 67.929 | 1105.4 | 1037.471
6785 | 0.94651 | 99.86 | 61.993 | 0.0028472 | 67.939 | 1105.4 |  | 6785 | 99.86 | 0.94651 | 61.993 | 0.0028472 | 67.939 | 1105.4 | 1037.461
6786 | 0.94679 | 99.87 | 61.993 | 0.002848 | 67.948 | 1105.4 |  | 6786 | 99.87 | 0.94679 | 61.993 | 0.002848 | 67.948 | 1105.4 | 1037.452
6787 | 0.94708 | 99.88 | 61.993 | 0.0028488 | 67.958 | 1105.4 |  | 6787 | 99.88 | 0.94708 | 61.993 | 0.0028488 | 67.958 | 1105.4 | 1037.442
6788 | 0.94736 | 99.89 | 61.993 | 0.0028496 | 67.968 | 1105.4 |  | 6788 | 99.89 | 0.94736 | 61.993 | 0.0028496 | 67.968 | 1105.4 | 1037.432
6789 | 0.94765 | 99.9 | 61.993 | 0.0028504 | 67.978 | 1105.4 |  | 6789 | 99.9 | 0.94765 | 61.993 | 0.0028504 | 67.978 | 1105.4 | 1037.422
6790 | 0.94793 | 99.91 | 61.992 | 0.0028512 | 67.988 | 1105.4 |  | 6790 | 99.91 | 0.94793 | 61.992 | 0.0028512 | 67.988 | 1105.4 | 1037.412
6791 | 0.94822 | 99.92 | 61.992 | 0.002852 | 67.998 | 1105.4 |  | 6791 | 99.92 | 0.94822 | 61.992 | 0.002852 | 67.998 | 1105.4 | 1037.402
6792 | 0.9485 | 99.93 | 61.992 | 0.0028528 | 68.008 | 1105.4 |  | 6792 | 99.93 | 0.9485 | 61.992 | 0.0028528 | 68.008 | 1105.4 | 1037.392
6793 | 0.94879 | 99.94 | 61.992 | 0.0028536 | 68.018 | 1105.4 |  | 6793 | 99.94 | 0.94879 | 61.992 | 0.0028536 | 68.018 | 1105.4 | 1037.382
6794 | 0.94908 | 99.95 | 61.992 | 0.0028544 | 68.028 | 1105.4 |  | 6794 | 99.95 | 0.94908 | 61.992 | 0.0028544 | 68.028 | 1105.4 | 1037.372
6795 | 0.94936 | 99.96 | 61.992 | 0.0028553 | 68.038 | 1105.4 |  | 6795 | 99.96 | 0.94936 | 61.992 | 0.0028553 | 68.038 | 1105.4 | 1037.362
6796 | 0.94965 | 99.97 | 61.992 | 0.0028561 | 68.048 | 1105.4 |  | 6796 | 99.97 | 0.94965 | 61.992 | 0.0028561 | 68.048 | 1105.4 | 1037.352
6797 | 0.94993 | 99.98 | 61.992 | 0.0028569 | 68.058 | 1105.4 |  | 6797 | 99.98 | 0.94993 | 61.992 | 0.0028569 | 68.058 | 1105.4 | 1037.342
6798 | 0.95022 | 99.99 | 61.991 | 0.0028577 | 68.068 | 1105.4 |  | 6798 | 99.99 | 0.95022 | 61.991 | 0.0028577 | 68.068 | 1105.4 | 1037.332
6799 | 0.95051 | 100 | 61.991 | 0.0028585 | 68.078 | 1105.4 |  | 6799 | 100 | 0.95051 | 61.991 | 0.0028585 | 68.078 | 1105.4 | 1037.322
6800 | 0.95079 | 100.01 | 61.991 | 0.0028593 | 68.088 | 1105.4 |  | 6800 | 100.01 | 0.95079 | 61.991 | 0.0028593 | 68.088 | 1105.4 | 1037.312
6801 | 0.95108 | 100.02 | 61.991 | 0.0028601 | 68.098 | 1105.4 |  | 6801 | 100.02 | 0.95108 | 61.991 | 0.0028601 | 68.098 | 1105.4 | 1037.302
6802 | 0.95136 | 100.03 | 61.991 | 0.0028609 | 68.108 | 1105.5 |  | 6802 | 100.03 | 0.95136 | 61.991 | 0.0028609 | 68.108 | 1105.5 | 1037.392
6803 | 0.95165 | 100.04 | 61.991 | 0.0028617 | 68.118 | 1105.5 |  | 6803 | 100.04 | 0.95165 | 61.991 | 0.0028617 | 68.118 | 1105.5 | 1037.382
6804 | 0.95194 | 100.05 | 61.991 | 0.0028625 | 68.128 | 1105.5 |  | 6804 | 100.05 | 0.95194 | 61.991 | 0.0028625 | 68.128 | 1105.5 | 1037.372
6805 | 0.95222 | 100.06 | 61.991 | 0.0028634 | 68.138 | 1105.5 |  | 6805 | 100.06 | 0.95222 | 61.991 | 0.0028634 | 68.138 | 1105.5 | 1037.362
6806 | 0.95251 | 100.07 | 61.99 | 0.0028642 | 68.148 | 1105.5 |  | 6806 | 100.07 | 0.95251 | 61.99 | 0.0028642 | 68.148 | 1105.5 | 1037.352
6807 | 0.9528 | 100.08 | 61.99 | 0.002865 | 68.158 | 1105.5 |  | 6807 | 100.08 | 0.9528 | 61.99 | 0.002865 | 68.158 | 1105.5 | 1037.342
6808 | 0.95308 | 100.09 | 61.99 | 0.0028658 | 68.168 | 1105.5 |  | 6808 | 100.09 | 0.95308 | 61.99 | 0.0028658 | 68.168 | 1105.5 | 1037.332
6809 | 0.95337 | 100.1 | 61.99 | 0.0028666 | 68.178 | 1105.5 |  | 6809 | 100.1 | 0.95337 | 61.99 | 0.0028666 | 68.178 | 1105.5 | 1037.322
6810 | 0.95366 | 100.11 | 61.99 | 0.0028674 | 68.188 | 1105.5 |  | 6810 | 100.11 | 0.95366 | 61.99 | 0.0028674 | 68.188 | 1105.5 | 1037.312
6811 | 0.95395 | 100.12 | 61.99 | 0.0028682 | 68.198 | 1105.5 |  | 6811 | 100.12 | 0.95395 | 61.99 | 0.0028682 | 68.198 | 1105.5 | 1037.302
6812 | 0.95423 | 100.13 | 61.99 | 0.0028691 | 68.208 | 1105.5 |  | 6812 | 100.13 | 0.95423 | 61.99 | 0.0028691 | 68.208 | 1105.5 | 1037.292
6813 | 0.95452 | 100.14 | 61.99 | 0.0028699 | 68.218 | 1105.5 |  | 6813 | 100.14 | 0.95452 | 61.99 | 0.0028699 | 68.218 | 1105.5 | 1037.282
6814 | 0.95481 | 100.15 | 61.989 | 0.0028707 | 68.228 | 1105.5 |  | 6814 | 100.15 | 0.95481 | 61.989 | 0.0028707 | 68.228 | 1105.5 | 1037.272
6815 | 0.95509 | 100.16 | 61.989 | 0.0028715 | 68.238 | 1105.5 |  | 6815 | 100.16 | 0.95509 | 61.989 | 0.0028715 | 68.238 | 1105.5 | 1037.262
6816 | 0.95538 | 100.17 | 61.989 | 0.0028723 | 68.248 | 1105.5 |  | 6816 | 100.17 | 0.95538 | 61.989 | 0.0028723 | 68.248 | 1105.5 | 1037.252
6817 | 0.95567 | 100.18 | 61.989 | 0.0028731 | 68.258 | 1105.5 |  | 6817 | 100.18 | 0.95567 | 61.989 | 0.0028731 | 68.258 | 1105.5 | 1037.242
6818 | 0.95596 | 100.19 | 61.989 | 0.0028739 | 68.268 | 1105.5 |  | 6818 | 100.19 | 0.95596 | 61.989 | 0.0028739 | 68.268 | 1105.5 | 1037.232
6819 | 0.95624 | 100.2 | 61.989 | 0.0028747 | 68.278 | 1105.5 |  | 6819 | 100.2 | 0.95624 | 61.989 | 0.0028747 | 68.278 | 1105.5 | 1037.222
6820 | 0.95653 | 100.21 | 61.989 | 0.0028756 | 68.288 | 1105.5 |  | 6820 | 100.21 | 0.95653 | 61.989 | 0.0028756 | 68.288 | 1105.5 | 1037.212
6821 | 0.95682 | 100.22 | 61.989 | 0.0028764 | 68.298 | 1105.5 |  | 6821 | 100.22 | 0.95682 | 61.989 | 0.0028764 | 68.298 | 1105.5 | 1037.202
6822 | 0.95711 | 100.23 | 61.988 | 0.0028772 | 68.308 | 1105.5 |  | 6822 | 100.23 | 0.95711 | 61.988 | 0.0028772 | 68.308 | 1105.5 | 1037.192
6823 | 0.95739 | 100.24 | 61.988 | 0.002878 | 68.318 | 1105.5 |  | 6823 | 100.24 | 0.95739 | 61.988 | 0.002878 | 68.318 | 1105.5 | 1037.182
6824 | 0.95768 | 100.25 | 61.988 | 0.0028788 | 68.328 | 1105.5 |  | 6824 | 100.25 | 0.95768 | 61.988 | 0.0028788 | 68.328 | 1105.5 | 1037.172
6825 | 0.95797 | 100.26 | 61.988 | 0.0028796 | 68.338 | 1105.6 |  | 6825 | 100.26 | 0.95797 | 61.988 | 0.0028796 | 68.338 | 1105.6 | 1037.262
6826 | 0.95826 | 100.27 | 61.988 | 0.0028805 | 68.348 | 1105.6 |  | 6826 | 100.27 | 0.95826 | 61.988 | 0.0028805 | 68.348 | 1105.6 | 1037.252
6827 | 0.95855 | 100.28 | 61.988 | 0.0028813 | 68.358 | 1105.6 |  | 6827 | 100.28 | 0.95855 | 61.988 | 0.0028813 | 68.358 | 1105.6 | 1037.242
6828 | 0.95884 | 100.29 | 61.988 | 0.0028821 | 68.368 | 1105.6 |  | 6828 | 100.29 | 0.95884 | 61.988 | 0.0028821 | 68.368 | 1105.6 | 1037.232
6829 | 0.95912 | 100.3 | 61.988 | 0.0028829 | 68.378 | 1105.6 |  | 6829 | 100.3 | 0.95912 | 61.988 | 0.0028829 | 68.378 | 1105.6 | 1037.222
6830 | 0.95941 | 100.31 | 61.987 | 0.0028837 | 68.388 | 1105.6 |  | 6830 | 100.31 | 0.95941 | 61.987 | 0.0028837 | 68.388 | 1105.6 | 1037.212
6831 | 0.9597 | 100.32 | 61.987 | 0.0028845 | 68.398 | 1105.6 |  | 6831 | 100.32 | 0.9597 | 61.987 | 0.0028845 | 68.398 | 1105.6 | 1037.202
6832 | 0.95999 | 100.33 | 61.987 | 0.0028854 | 68.408 | 1105.6 |  | 6832 | 100.33 | 0.95999 | 61.987 | 0.0028854 | 68.408 | 1105.6 | 1037.192
6833 | 0.96028 | 100.34 | 61.987 | 0.0028862 | 68.418 | 1105.6 |  | 6833 | 100.34 | 0.96028 | 61.987 | 0.0028862 | 68.418 | 1105.6 | 1037.182
6834 | 0.96057 | 100.35 | 61.987 | 0.002887 | 68.428 | 1105.6 |  | 6834 | 100.35 | 0.96057 | 61.987 | 0.002887 | 68.428 | 1105.6 | 1037.172
6835 | 0.96086 | 100.36 | 61.987 | 0.0028878 | 68.438 | 1105.6 |  | 6835 | 100.36 | 0.96086 | 61.987 | 0.0028878 | 68.438 | 1105.6 | 1037.162
6836 | 0.96114 | 100.37 | 61.987 | 0.0028886 | 68.448 | 1105.6 |  | 6836 | 100.37 | 0.96114 | 61.987 | 0.0028886 | 68.448 | 1105.6 | 1037.152
6837 | 0.96143 | 100.38 | 61.987 | 0.0028894 | 68.458 | 1105.6 |  | 6837 | 100.38 | 0.96143 | 61.987 | 0.0028894 | 68.458 | 1105.6 | 1037.142
6838 | 0.96172 | 100.39 | 61.986 | 0.0028903 | 68.468 | 1105.6 |  | 6838 | 100.39 | 0.96172 | 61.986 | 0.0028903 | 68.468 | 1105.6 | 1037.132
6839 | 0.96201 | 100.4 | 61.986 | 0.0028911 | 68.478 | 1105.6 |  | 6839 | 100.4 | 0.96201 | 61.986 | 0.0028911 | 68.478 | 1105.6 | 1037.122
6840 | 0.9623 | 100.41 | 61.986 | 0.0028919 | 68.488 | 1105.6 |  | 6840 | 100.41 | 0.9623 | 61.986 | 0.0028919 | 68.488 | 1105.6 | 1037.112
6841 | 0.96259 | 100.42 | 61.986 | 0.0028927 | 68.498 | 1105.6 |  | 6841 | 100.42 | 0.96259 | 61.986 | 0.0028927 | 68.498 | 1105.6 | 1037.102
6842 | 0.96288 | 100.43 | 61.986 | 0.0028935 | 68.508 | 1105.6 |  | 6842 | 100.43 | 0.96288 | 61.986 | 0.0028935 | 68.508 | 1105.6 | 1037.092
6843 | 0.96317 | 100.44 | 61.986 | 0.0028944 | 68.518 | 1105.6 |  | 6843 | 100.44 | 0.96317 | 61.986 | 0.0028944 | 68.518 | 1105.6 | 1037.082
6844 | 0.96346 | 100.45 | 61.986 | 0.0028952 | 68.528 | 1105.6 |  | 6844 | 100.45 | 0.96346 | 61.986 | 0.0028952 | 68.528 | 1105.6 | 1037.072
6845 | 0.96375 | 100.46 | 61.985 | 0.002896 | 68.538 | 1105.6 |  | 6845 | 100.46 | 0.96375 | 61.985 | 0.002896 | 68.538 | 1105.6 | 1037.062
6846 | 0.96404 | 100.47 | 61.985 | 0.0028968 | 68.548 | 1105.6 |  | 6846 | 100.47 | 0.96404 | 61.985 | 0.0028968 | 68.548 | 1105.6 | 1037.052
6847 | 0.96433 | 100.48 | 61.985 | 0.0028976 | 68.558 | 1105.6 |  | 6847 | 100.48 | 0.96433 | 61.985 | 0.0028976 | 68.558 | 1105.6 | 1037.042
6848 | 0.96462 | 100.49 | 61.985 | 0.0028985 | 68.568 | 1105.6 |  | 6848 | 100.49 | 0.96462 | 61.985 | 0.0028985 | 68.568 | 1105.6 | 1037.032
6849 | 0.96491 | 100.5 | 61.985 | 0.0028993 | 68.578 | 1105.7 |  | 6849 | 100.5 | 0.96491 | 61.985 | 0.0028993 | 68.578 | 1105.7 | 1037.122
6850 | 0.9652 | 100.51 | 61.985 | 0.0029001 | 68.588 | 1105.7 |  | 6850 | 100.51 | 0.9652 | 61.985 | 0.0029001 | 68.588 | 1105.7 | 1037.112
6851 | 0.96549 | 100.52 | 61.985 | 0.0029009 | 68.598 | 1105.7 |  | 6851 | 100.52 | 0.96549 | 61.985 | 0.0029009 | 68.598 | 1105.7 | 1037.102
6852 | 0.96578 | 100.53 | 61.985 | 0.0029017 | 68.608 | 1105.7 |  | 6852 | 100.53 | 0.96578 | 61.985 | 0.0029017 | 68.608 | 1105.7 | 1037.092
6853 | 0.96607 | 100.54 | 61.984 | 0.0029026 | 68.618 | 1105.7 |  | 6853 | 100.54 | 0.96607 | 61.984 | 0.0029026 | 68.618 | 1105.7 | 1037.082
6854 | 0.96636 | 100.55 | 61.984 | 0.0029034 | 68.628 | 1105.7 |  | 6854 | 100.55 | 0.96636 | 61.984 | 0.0029034 | 68.628 | 1105.7 | 1037.072
6855 | 0.96665 | 100.56 | 61.984 | 0.0029042 | 68.638 | 1105.7 |  | 6855 | 100.56 | 0.96665 | 61.984 | 0.0029042 | 68.638 | 1105.7 | 1037.062
6856 | 0.96694 | 100.57 | 61.984 | 0.002905 | 68.648 | 1105.7 |  | 6856 | 100.57 | 0.96694 | 61.984 | 0.002905 | 68.648 | 1105.7 | 1037.052
6857 | 0.96723 | 100.58 | 61.984 | 0.0029059 | 68.658 | 1105.7 |  | 6857 | 100.58 | 0.96723 | 61.984 | 0.0029059 | 68.658 | 1105.7 | 1037.042
6858 | 0.96752 | 100.59 | 61.984 | 0.0029067 | 68.668 | 1105.7 |  | 6858 | 100.59 | 0.96752 | 61.984 | 0.0029067 | 68.668 | 1105.7 | 1037.032
6859 | 0.96781 | 100.6 | 61.984 | 0.0029075 | 68.678 | 1105.7 |  | 6859 | 100.6 | 0.96781 | 61.984 | 0.0029075 | 68.678 | 1105.7 | 1037.022
6860 | 0.9681 | 100.61 | 61.984 | 0.0029083 | 68.688 | 1105.7 |  | 6860 | 100.61 | 0.9681 | 61.984 | 0.0029083 | 68.688 | 1105.7 | 1037.012
6861 | 0.96839 | 100.62 | 61.983 | 0.0029091 | 68.698 | 1105.7 |  | 6861 | 100.62 | 0.96839 | 61.983 | 0.0029091 | 68.698 | 1105.7 | 1037.002
6862 | 0.96868 | 100.63 | 61.983 | 0.00291 | 68.708 | 1105.7 |  | 6862 | 100.63 | 0.96868 | 61.983 | 0.00291 | 68.708 | 1105.7 | 1036.992
6863 | 0.96897 | 100.64 | 61.983 | 0.0029108 | 68.718 | 1105.7 |  | 6863 | 100.64 | 0.96897 | 61.983 | 0.0029108 | 68.718 | 1105.7 | 1036.982
6864 | 0.96926 | 100.65 | 61.983 | 0.0029116 | 68.728 | 1105.7 |  | 6864 | 100.65 | 0.96926 | 61.983 | 0.0029116 | 68.728 | 1105.7 | 1036.972
6865 | 0.96955 | 100.66 | 61.983 | 0.0029124 | 68.738 | 1105.7 |  | 6865 | 100.66 | 0.96955 | 61.983 | 0.0029124 | 68.738 | 1105.7 | 1036.962
6866 | 0.96985 | 100.67 | 61.983 | 0.0029133 | 68.748 | 1105.7 |  | 6866 | 100.67 | 0.96985 | 61.983 | 0.0029133 | 68.748 | 1105.7 | 1036.952
6867 | 0.97014 | 100.68 | 61.983 | 0.0029141 | 68.758 | 1105.7 |  | 6867 | 100.68 | 0.97014 | 61.983 | 0.0029141 | 68.758 | 1105.7 | 1036.942
6868 | 0.97043 | 100.69 | 61.983 | 0.0029149 | 68.768 | 1105.7 |  | 6868 | 100.69 | 0.97043 | 61.983 | 0.0029149 | 68.768 | 1105.7 | 1036.932
6869 | 0.97072 | 100.7 | 61.982 | 0.0029157 | 68.778 | 1105.7 |  | 6869 | 100.7 | 0.97072 | 61.982 | 0.0029157 | 68.778 | 1105.7 | 1036.922
6870 | 0.97101 | 100.71 | 61.982 | 0.0029166 | 68.788 | 1105.7 |  | 6870 | 100.71 | 0.97101 | 61.982 | 0.0029166 | 68.788 | 1105.7 | 1036.912
6871 | 0.9713 | 100.72 | 61.982 | 0.0029174 | 68.798 | 1105.7 |  | 6871 | 100.72 | 0.9713 | 61.982 | 0.0029174 | 68.798 | 1105.7 | 1036.902
6872 | 0.97159 | 100.73 | 61.982 | 0.0029182 | 68.808 | 1105.8 |  | 6872 | 100.73 | 0.97159 | 61.982 | 0.0029182 | 68.808 | 1105.8 | 1036.992
6873 | 0.97189 | 100.74 | 61.982 | 0.002919 | 68.818 | 1105.8 |  | 6873 | 100.74 | 0.97189 | 61.982 | 0.002919 | 68.818 | 1105.8 | 1036.982
6874 | 0.97218 | 100.75 | 61.982 | 0.0029199 | 68.828 | 1105.8 |  | 6874 | 100.75 | 0.97218 | 61.982 | 0.0029199 | 68.828 | 1105.8 | 1036.972
6875 | 0.97247 | 100.76 | 61.982 | 0.0029207 | 68.838 | 1105.8 |  | 6875 | 100.76 | 0.97247 | 61.982 | 0.0029207 | 68.838 | 1105.8 | 1036.962
6876 | 0.97276 | 100.77 | 61.982 | 0.0029215 | 68.848 | 1105.8 |  | 6876 | 100.77 | 0.97276 | 61.982 | 0.0029215 | 68.848 | 1105.8 | 1036.952
6877 | 0.97305 | 100.78 | 61.981 | 0.0029223 | 68.858 | 1105.8 |  | 6877 | 100.78 | 0.97305 | 61.981 | 0.0029223 | 68.858 | 1105.8 | 1036.942
6878 | 0.97334 | 100.79 | 61.981 | 0.0029232 | 68.868 | 1105.8 |  | 6878 | 100.79 | 0.97334 | 61.981 | 0.0029232 | 68.868 | 1105.8 | 1036.932
6879 | 0.97364 | 100.8 | 61.981 | 0.002924 | 68.878 | 1105.8 |  | 6879 | 100.8 | 0.97364 | 61.981 | 0.002924 | 68.878 | 1105.8 | 1036.922
6880 | 0.97393 | 100.81 | 61.981 | 0.0029248 | 68.888 | 1105.8 |  | 6880 | 100.81 | 0.97393 | 61.981 | 0.0029248 | 68.888 | 1105.8 | 1036.912
6881 | 0.97422 | 100.82 | 61.981 | 0.0029256 | 68.898 | 1105.8 |  | 6881 | 100.82 | 0.97422 | 61.981 | 0.0029256 | 68.898 | 1105.8 | 1036.902
6882 | 0.97451 | 100.83 | 61.981 | 0.0029265 | 68.908 | 1105.8 |  | 6882 | 100.83 | 0.97451 | 61.981 | 0.0029265 | 68.908 | 1105.8 | 1036.892
6883 | 0.97481 | 100.84 | 61.981 | 0.0029273 | 68.918 | 1105.8 |  | 6883 | 100.84 | 0.97481 | 61.981 | 0.0029273 | 68.918 | 1105.8 | 1036.882
6884 | 0.9751 | 100.85 | 61.981 | 0.0029281 | 68.928 | 1105.8 |  | 6884 | 100.85 | 0.9751 | 61.981 | 0.0029281 | 68.928 | 1105.8 | 1036.872
6885 | 0.97539 | 100.86 | 61.98 | 0.002929 | 68.938 | 1105.8 |  | 6885 | 100.86 | 0.97539 | 61.98 | 0.002929 | 68.938 | 1105.8 | 1036.862
6886 | 0.97568 | 100.87 | 61.98 | 0.0029298 | 68.947 | 1105.8 |  | 6886 | 100.87 | 0.97568 | 61.98 | 0.0029298 | 68.947 | 1105.8 | 1036.853
6887 | 0.97598 | 100.88 | 61.98 | 0.0029306 | 68.957 | 1105.8 |  | 6887 | 100.88 | 0.97598 | 61.98 | 0.0029306 | 68.957 | 1105.8 | 1036.843
6888 | 0.97627 | 100.89 | 61.98 | 0.0029314 | 68.967 | 1105.8 |  | 6888 | 100.89 | 0.97627 | 61.98 | 0.0029314 | 68.967 | 1105.8 | 1036.833
6889 | 0.97656 | 100.9 | 61.98 | 0.0029323 | 68.977 | 1105.8 |  | 6889 | 100.9 | 0.97656 | 61.98 | 0.0029323 | 68.977 | 1105.8 | 1036.823
6890 | 0.97686 | 100.91 | 61.98 | 0.0029331 | 68.987 | 1105.8 |  | 6890 | 100.91 | 0.97686 | 61.98 | 0.0029331 | 68.987 | 1105.8 | 1036.813
6891 | 0.97715 | 100.92 | 61.98 | 0.0029339 | 68.997 | 1105.8 |  | 6891 | 100.92 | 0.97715 | 61.98 | 0.0029339 | 68.997 | 1105.8 | 1036.803
6892 | 0.97744 | 100.93 | 61.979 | 0.0029348 | 69.007 | 1105.8 |  | 6892 | 100.93 | 0.97744 | 61.979 | 0.0029348 | 69.007 | 1105.8 | 1036.793
6893 | 0.97773 | 100.94 | 61.979 | 0.0029356 | 69.017 | 1105.8 |  | 6893 | 100.94 | 0.97773 | 61.979 | 0.0029356 | 69.017 | 1105.8 | 1036.783
6894 | 0.97803 | 100.95 | 61.979 | 0.0029364 | 69.027 | 1105.8 |  | 6894 | 100.95 | 0.97803 | 61.979 | 0.0029364 | 69.027 | 1105.8 | 1036.773
6895 | 0.97832 | 100.96 | 61.979 | 0.0029372 | 69.037 | 1105.9 |  | 6895 | 100.96 | 0.97832 | 61.979 | 0.0029372 | 69.037 | 1105.9 | 1036.863
6896 | 0.97861 | 100.97 | 61.979 | 0.0029381 | 69.047 | 1105.9 |  | 6896 | 100.97 | 0.97861 | 61.979 | 0.0029381 | 69.047 | 1105.9 | 1036.853
6897 | 0.97891 | 100.98 | 61.979 | 0.0029389 | 69.057 | 1105.9 |  | 6897 | 100.98 | 0.97891 | 61.979 | 0.0029389 | 69.057 | 1105.9 | 1036.843
6898 | 0.9792 | 100.99 | 61.979 | 0.0029397 | 69.067 | 1105.9 |  | 6898 | 100.99 | 0.9792 | 61.979 | 0.0029397 | 69.067 | 1105.9 | 1036.833
6899 | 0.9795 | 101 | 61.979 | 0.0029406 | 69.077 | 1105.9 |  | 6899 | 101 | 0.9795 | 61.979 | 0.0029406 | 69.077 | 1105.9 | 1036.823
6900 | 0.97979 | 101.01 | 61.978 | 0.0029414 | 69.087 | 1105.9 |  | 6900 | 101.01 | 0.97979 | 61.978 | 0.0029414 | 69.087 | 1105.9 | 1036.813
6901 | 0.98008 | 101.02 | 61.978 | 0.0029422 | 69.097 | 1105.9 |  | 6901 | 101.02 | 0.98008 | 61.978 | 0.0029422 | 69.097 | 1105.9 | 1036.803
6902 | 0.98038 | 101.03 | 61.978 | 0.0029431 | 69.107 | 1105.9 |  | 6902 | 101.03 | 0.98038 | 61.978 | 0.0029431 | 69.107 | 1105.9 | 1036.793
6903 | 0.98067 | 101.04 | 61.978 | 0.0029439 | 69.117 | 1105.9 |  | 6903 | 101.04 | 0.98067 | 61.978 | 0.0029439 | 69.117 | 1105.9 | 1036.783
6904 | 0.98096 | 101.05 | 61.978 | 0.0029447 | 69.127 | 1105.9 |  | 6904 | 101.05 | 0.98096 | 61.978 | 0.0029447 | 69.127 | 1105.9 | 1036.773
6905 | 0.98126 | 101.06 | 61.978 | 0.0029456 | 69.137 | 1105.9 |  | 6905 | 101.06 | 0.98126 | 61.978 | 0.0029456 | 69.137 | 1105.9 | 1036.763
6906 | 0.98155 | 101.07 | 61.978 | 0.0029464 | 69.147 | 1105.9 |  | 6906 | 101.07 | 0.98155 | 61.978 | 0.0029464 | 69.147 | 1105.9 | 1036.753
6907 | 0.98185 | 101.08 | 61.978 | 0.0029472 | 69.157 | 1105.9 |  | 6907 | 101.08 | 0.98185 | 61.978 | 0.0029472 | 69.157 | 1105.9 | 1036.743
6908 | 0.98214 | 101.09 | 61.977 | 0.0029481 | 69.167 | 1105.9 |  | 6908 | 101.09 | 0.98214 | 61.977 | 0.0029481 | 69.167 | 1105.9 | 1036.733
6909 | 0.98244 | 101.1 | 61.977 | 0.0029489 | 69.177 | 1105.9 |  | 6909 | 101.1 | 0.98244 | 61.977 | 0.0029489 | 69.177 | 1105.9 | 1036.723
6910 | 0.98273 | 101.11 | 61.977 | 0.0029497 | 69.187 | 1105.9 |  | 6910 | 101.11 | 0.98273 | 61.977 | 0.0029497 | 69.187 | 1105.9 | 1036.713
6911 | 0.98302 | 101.12 | 61.977 | 0.0029506 | 69.197 | 1105.9 |  | 6911 | 101.12 | 0.98302 | 61.977 | 0.0029506 | 69.197 | 1105.9 | 1036.703
6912 | 0.98332 | 101.13 | 61.977 | 0.0029514 | 69.207 | 1105.9 |  | 6912 | 101.13 | 0.98332 | 61.977 | 0.0029514 | 69.207 | 1105.9 | 1036.693
6913 | 0.98361 | 101.14 | 61.977 | 0.0029522 | 69.217 | 1105.9 |  | 6913 | 101.14 | 0.98361 | 61.977 | 0.0029522 | 69.217 | 1105.9 | 1036.683
6914 | 0.98391 | 101.15 | 61.977 | 0.0029531 | 69.227 | 1105.9 |  | 6914 | 101.15 | 0.98391 | 61.977 | 0.0029531 | 69.227 | 1105.9 | 1036.673
6915 | 0.9842 | 101.16 | 61.977 | 0.0029539 | 69.237 | 1105.9 |  | 6915 | 101.16 | 0.9842 | 61.977 | 0.0029539 | 69.237 | 1105.9 | 1036.663
6916 | 0.9845 | 101.17 | 61.976 | 0.0029547 | 69.247 | 1105.9 |  | 6916 | 101.17 | 0.9845 | 61.976 | 0.0029547 | 69.247 | 1105.9 | 1036.653
6917 | 0.98479 | 101.18 | 61.976 | 0.0029556 | 69.257 | 1105.9 |  | 6917 | 101.18 | 0.98479 | 61.976 | 0.0029556 | 69.257 | 1105.9 | 1036.643
6918 | 0.98509 | 101.19 | 61.976 | 0.0029564 | 69.267 | 1105.9 |  | 6918 | 101.19 | 0.98509 | 61.976 | 0.0029564 | 69.267 | 1105.9 | 1036.633
6919 | 0.98538 | 101.2 | 61.976 | 0.0029572 | 69.277 | 1106 |  | 6919 | 101.2 | 0.98538 | 61.976 | 0.0029572 | 69.277 | 1106 | 1036.723
6920 | 0.98568 | 101.21 | 61.976 | 0.0029581 | 69.287 | 1106 |  | 6920 | 101.21 | 0.98568 | 61.976 | 0.0029581 | 69.287 | 1106 | 1036.713
6921 | 0.98597 | 101.22 | 61.976 | 0.0029589 | 69.297 | 1106 |  | 6921 | 101.22 | 0.98597 | 61.976 | 0.0029589 | 69.297 | 1106 | 1036.703
6922 | 0.98627 | 101.23 | 61.976 | 0.0029597 | 69.307 | 1106 |  | 6922 | 101.23 | 0.98627 | 61.976 | 0.0029597 | 69.307 | 1106 | 1036.693
6923 | 0.98657 | 101.24 | 61.976 | 0.0029606 | 69.317 | 1106 |  | 6923 | 101.24 | 0.98657 | 61.976 | 0.0029606 | 69.317 | 1106 | 1036.683
6924 | 0.98686 | 101.25 | 61.975 | 0.0029614 | 69.327 | 1106 |  | 6924 | 101.25 | 0.98686 | 61.975 | 0.0029614 | 69.327 | 1106 | 1036.673
6925 | 0.98716 | 101.26 | 61.975 | 0.0029622 | 69.337 | 1106 |  | 6925 | 101.26 | 0.98716 | 61.975 | 0.0029622 | 69.337 | 1106 | 1036.663
6926 | 0.98745 | 101.27 | 61.975 | 0.0029631 | 69.347 | 1106 |  | 6926 | 101.27 | 0.98745 | 61.975 | 0.0029631 | 69.347 | 1106 | 1036.653
6927 | 0.98775 | 101.28 | 61.975 | 0.0029639 | 69.357 | 1106 |  | 6927 | 101.28 | 0.98775 | 61.975 | 0.0029639 | 69.357 | 1106 | 1036.643
6928 | 0.98804 | 101.29 | 61.975 | 0.0029647 | 69.367 | 1106 |  | 6928 | 101.29 | 0.98804 | 61.975 | 0.0029647 | 69.367 | 1106 | 1036.633
6929 | 0.98834 | 101.3 | 61.975 | 0.0029656 | 69.377 | 1106 |  | 6929 | 101.3 | 0.98834 | 61.975 | 0.0029656 | 69.377 | 1106 | 1036.623
6930 | 0.98864 | 101.31 | 61.975 | 0.0029664 | 69.387 | 1106 |  | 6930 | 101.31 | 0.98864 | 61.975 | 0.0029664 | 69.387 | 1106 | 1036.613
6931 | 0.98893 | 101.32 | 61.974 | 0.0029673 | 69.397 | 1106 |  | 6931 | 101.32 | 0.98893 | 61.974 | 0.0029673 | 69.397 | 1106 | 1036.603
6932 | 0.98923 | 101.33 | 61.974 | 0.0029681 | 69.407 | 1106 |  | 6932 | 101.33 | 0.98923 | 61.974 | 0.0029681 | 69.407 | 1106 | 1036.593
6933 | 0.98952 | 101.34 | 61.974 | 0.0029689 | 69.417 | 1106 |  | 6933 | 101.34 | 0.98952 | 61.974 | 0.0029689 | 69.417 | 1106 | 1036.583
6934 | 0.98982 | 101.35 | 61.974 | 0.0029698 | 69.427 | 1106 |  | 6934 | 101.35 | 0.98982 | 61.974 | 0.0029698 | 69.427 | 1106 | 1036.573
6935 | 0.99012 | 101.36 | 61.974 | 0.0029706 | 69.437 | 1106 |  | 6935 | 101.36 | 0.99012 | 61.974 | 0.0029706 | 69.437 | 1106 | 1036.563
6936 | 0.99041 | 101.37 | 61.974 | 0.0029714 | 69.447 | 1106 |  | 6936 | 101.37 | 0.99041 | 61.974 | 0.0029714 | 69.447 | 1106 | 1036.553
6937 | 0.99071 | 101.38 | 61.974 | 0.0029723 | 69.457 | 1106 |  | 6937 | 101.38 | 0.99071 | 61.974 | 0.0029723 | 69.457 | 1106 | 1036.543
6938 | 0.99101 | 101.39 | 61.974 | 0.0029731 | 69.467 | 1106 |  | 6938 | 101.39 | 0.99101 | 61.974 | 0.0029731 | 69.467 | 1106 | 1036.533
6939 | 0.9913 | 101.4 | 61.973 | 0.002974 | 69.477 | 1106 |  | 6939 | 101.4 | 0.9913 | 61.973 | 0.002974 | 69.477 | 1106 | 1036.523
6940 | 0.9916 | 101.41 | 61.973 | 0.0029748 | 69.487 | 1106 |  | 6940 | 101.41 | 0.9916 | 61.973 | 0.0029748 | 69.487 | 1106 | 1036.513
6941 | 0.9919 | 101.42 | 61.973 | 0.0029756 | 69.497 | 1106 |  | 6941 | 101.42 | 0.9919 | 61.973 | 0.0029756 | 69.497 | 1106 | 1036.503
6942 | 0.99219 | 101.43 | 61.973 | 0.0029765 | 69.507 | 1106.1 |  | 6942 | 101.43 | 0.99219 | 61.973 | 0.0029765 | 69.507 | 1106.1 | 1036.593
6943 | 0.99249 | 101.44 | 61.973 | 0.0029773 | 69.517 | 1106.1 |  | 6943 | 101.44 | 0.99249 | 61.973 | 0.0029773 | 69.517 | 1106.1 | 1036.583
6944 | 0.99279 | 101.45 | 61.973 | 0.0029782 | 69.527 | 1106.1 |  | 6944 | 101.45 | 0.99279 | 61.973 | 0.0029782 | 69.527 | 1106.1 | 1036.573
6945 | 0.99308 | 101.46 | 61.973 | 0.002979 | 69.537 | 1106.1 |  | 6945 | 101.46 | 0.99308 | 61.973 | 0.002979 | 69.537 | 1106.1 | 1036.563
6946 | 0.99338 | 101.47 | 61.973 | 0.0029798 | 69.547 | 1106.1 |  | 6946 | 101.47 | 0.99338 | 61.973 | 0.0029798 | 69.547 | 1106.1 | 1036.553
6947 | 0.99368 | 101.48 | 61.972 | 0.0029807 | 69.557 | 1106.1 |  | 6947 | 101.48 | 0.99368 | 61.972 | 0.0029807 | 69.557 | 1106.1 | 1036.543
6948 | 0.99398 | 101.49 | 61.972 | 0.0029815 | 69.567 | 1106.1 |  | 6948 | 101.49 | 0.99398 | 61.972 | 0.0029815 | 69.567 | 1106.1 | 1036.533
6949 | 0.99427 | 101.5 | 61.972 | 0.0029824 | 69.577 | 1106.1 |  | 6949 | 101.5 | 0.99427 | 61.972 | 0.0029824 | 69.577 | 1106.1 | 1036.523
6950 | 0.99457 | 101.51 | 61.972 | 0.0029832 | 69.587 | 1106.1 |  | 6950 | 101.51 | 0.99457 | 61.972 | 0.0029832 | 69.587 | 1106.1 | 1036.513
6951 | 0.99487 | 101.52 | 61.972 | 0.002984 | 69.597 | 1106.1 |  | 6951 | 101.52 | 0.99487 | 61.972 | 0.002984 | 69.597 | 1106.1 | 1036.503
6952 | 0.99517 | 101.53 | 61.972 | 0.0029849 | 69.607 | 1106.1 |  | 6952 | 101.53 | 0.99517 | 61.972 | 0.0029849 | 69.607 | 1106.1 | 1036.493
6953 | 0.99546 | 101.54 | 61.972 | 0.0029857 | 69.617 | 1106.1 |  | 6953 | 101.54 | 0.99546 | 61.972 | 0.0029857 | 69.617 | 1106.1 | 1036.483
6954 | 0.99576 | 101.55 | 61.972 | 0.0029866 | 69.627 | 1106.1 |  | 6954 | 101.55 | 0.99576 | 61.972 | 0.0029866 | 69.627 | 1106.1 | 1036.473
6955 | 0.99606 | 101.56 | 61.971 | 0.0029874 | 69.637 | 1106.1 |  | 6955 | 101.56 | 0.99606 | 61.971 | 0.0029874 | 69.637 | 1106.1 | 1036.463
6956 | 0.99636 | 101.57 | 61.971 | 0.0029882 | 69.647 | 1106.1 |  | 6956 | 101.57 | 0.99636 | 61.971 | 0.0029882 | 69.647 | 1106.1 | 1036.453
6957 | 0.99666 | 101.58 | 61.971 | 0.0029891 | 69.657 | 1106.1 |  | 6957 | 101.58 | 0.99666 | 61.971 | 0.0029891 | 69.657 | 1106.1 | 1036.443
6958 | 0.99695 | 101.59 | 61.971 | 0.0029899 | 69.667 | 1106.1 |  | 6958 | 101.59 | 0.99695 | 61.971 | 0.0029899 | 69.667 | 1106.1 | 1036.433
6959 | 0.99725 | 101.6 | 61.971 | 0.0029908 | 69.677 | 1106.1 |  | 6959 | 101.6 | 0.99725 | 61.971 | 0.0029908 | 69.677 | 1106.1 | 1036.423
6960 | 0.99755 | 101.61 | 61.971 | 0.0029916 | 69.687 | 1106.1 |  | 6960 | 101.61 | 0.99755 | 61.971 | 0.0029916 | 69.687 | 1106.1 | 1036.413
6961 | 0.99785 | 101.62 | 61.971 | 0.0029925 | 69.697 | 1106.1 |  | 6961 | 101.62 | 0.99785 | 61.971 | 0.0029925 | 69.697 | 1106.1 | 1036.403
6962 | 0.99815 | 101.63 | 61.97 | 0.0029933 | 69.707 | 1106.1 |  | 6962 | 101.63 | 0.99815 | 61.97 | 0.0029933 | 69.707 | 1106.1 | 1036.393
6963 | 0.99845 | 101.64 | 61.97 | 0.0029941 | 69.717 | 1106.1 |  | 6963 | 101.64 | 0.99845 | 61.97 | 0.0029941 | 69.717 | 1106.1 | 1036.383
6964 | 0.99875 | 101.65 | 61.97 | 0.002995 | 69.727 | 1106.1 |  | 6964 | 101.65 | 0.99875 | 61.97 | 0.002995 | 69.727 | 1106.1 | 1036.373
6965 | 0.99904 | 101.66 | 61.97 | 0.0029958 | 69.737 | 1106.2 |  | 6965 | 101.66 | 0.99904 | 61.97 | 0.0029958 | 69.737 | 1106.2 | 1036.463
6966 | 0.99934 | 101.67 | 61.97 | 0.0029967 | 69.747 | 1106.2 |  | 6966 | 101.67 | 0.99934 | 61.97 | 0.0029967 | 69.747 | 1106.2 | 1036.453
6967 | 0.99964 | 101.68 | 61.97 | 0.0029975 | 69.757 | 1106.2 |  | 6967 | 101.68 | 0.99964 | 61.97 | 0.0029975 | 69.757 | 1106.2 | 1036.443
6968 | 0.99994 | 101.69 | 61.97 | 0.0029984 | 69.767 | 1106.2 |  | 6968 | 101.69 | 0.99994 | 61.97 | 0.0029984 | 69.767 | 1106.2 | 1036.433
6969 | 1.0002 | 101.7 | 61.97 | 0.0029992 | 69.777 | 1106.2 |  | 6969 | 101.7 | 1.0002 | 61.97 | 0.0029992 | 69.777 | 1106.2 | 1036.423
6970 | 1.0005 | 101.71 | 61.969 | 0.0030001 | 69.787 | 1106.2 |  | 6970 | 101.71 | 1.0005 | 61.969 | 0.0030001 | 69.787 | 1106.2 | 1036.413
6971 | 1.0008 | 101.72 | 61.969 | 0.0030009 | 69.797 | 1106.2 |  | 6971 | 101.72 | 1.0008 | 61.969 | 0.0030009 | 69.797 | 1106.2 | 1036.403
6972 | 1.0011 | 101.73 | 61.969 | 0.0030017 | 69.807 | 1106.2 |  | 6972 | 101.73 | 1.0011 | 61.969 | 0.0030017 | 69.807 | 1106.2 | 1036.393
6973 | 1.0014 | 101.74 | 61.969 | 0.0030026 | 69.817 | 1106.2 |  | 6973 | 101.74 | 1.0014 | 61.969 | 0.0030026 | 69.817 | 1106.2 | 1036.383
6974 | 1.0017 | 101.75 | 61.969 | 0.0030034 | 69.827 | 1106.2 |  | 6974 | 101.75 | 1.0017 | 61.969 | 0.0030034 | 69.827 | 1106.2 | 1036.373
6975 | 1.002 | 101.76 | 61.969 | 0.0030043 | 69.837 | 1106.2 |  | 6975 | 101.76 | 1.002 | 61.969 | 0.0030043 | 69.837 | 1106.2 | 1036.363
6976 | 1.0023 | 101.77 | 61.969 | 0.0030051 | 69.847 | 1106.2 |  | 6976 | 101.77 | 1.0023 | 61.969 | 0.0030051 | 69.847 | 1106.2 | 1036.353
6977 | 1.0026 | 101.78 | 61.969 | 0.003006 | 69.857 | 1106.2 |  | 6977 | 101.78 | 1.0026 | 61.969 | 0.003006 | 69.857 | 1106.2 | 1036.343
6978 | 1.0029 | 101.79 | 61.968 | 0.0030068 | 69.867 | 1106.2 |  | 6978 | 101.79 | 1.0029 | 61.968 | 0.0030068 | 69.867 | 1106.2 | 1036.333
6979 | 1.0032 | 101.8 | 61.968 | 0.0030077 | 69.877 | 1106.2 |  | 6979 | 101.8 | 1.0032 | 61.968 | 0.0030077 | 69.877 | 1106.2 | 1036.323
6980 | 1.0035 | 101.81 | 61.968 | 0.0030085 | 69.887 | 1106.2 |  | 6980 | 101.81 | 1.0035 | 61.968 | 0.0030085 | 69.887 | 1106.2 | 1036.313
6981 | 1.0038 | 101.82 | 61.968 | 0.0030094 | 69.897 | 1106.2 |  | 6981 | 101.82 | 1.0038 | 61.968 | 0.0030094 | 69.897 | 1106.2 | 1036.303
6982 | 1.0041 | 101.83 | 61.968 | 0.0030102 | 69.907 | 1106.2 |  | 6982 | 101.83 | 1.0041 | 61.968 | 0.0030102 | 69.907 | 1106.2 | 1036.293
6983 | 1.0044 | 101.84 | 61.968 | 0.0030111 | 69.917 | 1106.2 |  | 6983 | 101.84 | 1.0044 | 61.968 | 0.0030111 | 69.917 | 1106.2 | 1036.283
6984 | 1.0047 | 101.85 | 61.968 | 0.0030119 | 69.927 | 1106.2 |  | 6984 | 101.85 | 1.0047 | 61.968 | 0.0030119 | 69.927 | 1106.2 | 1036.273
6985 | 1.005 | 101.86 | 61.968 | 0.0030128 | 69.937 | 1106.2 |  | 6985 | 101.86 | 1.005 | 61.968 | 0.0030128 | 69.937 | 1106.2 | 1036.263
6986 | 1.0053 | 101.87 | 61.967 | 0.0030136 | 69.947 | 1106.2 |  | 6986 | 101.87 | 1.0053 | 61.967 | 0.0030136 | 69.947 | 1106.2 | 1036.253
6987 | 1.0056 | 101.88 | 61.967 | 0.0030144 | 69.956 | 1106.2 |  | 6987 | 101.88 | 1.0056 | 61.967 | 0.0030144 | 69.956 | 1106.2 | 1036.244
6988 | 1.0059 | 101.89 | 61.967 | 0.0030153 | 69.966 | 1106.2 |  | 6988 | 101.89 | 1.0059 | 61.967 | 0.0030153 | 69.966 | 1106.2 | 1036.234
6989 | 1.0062 | 101.9 | 61.967 | 0.0030161 | 69.976 | 1106.3 |  | 6989 | 101.9 | 1.0062 | 61.967 | 0.0030161 | 69.976 | 1106.3 | 1036.324
6990 | 1.0065 | 101.91 | 61.967 | 0.003017 | 69.986 | 1106.3 |  | 6990 | 101.91 | 1.0065 | 61.967 | 0.003017 | 69.986 | 1106.3 | 1036.314
6991 | 1.0068 | 101.92 | 61.967 | 0.0030178 | 69.996 | 1106.3 |  | 6991 | 101.92 | 1.0068 | 61.967 | 0.0030178 | 69.996 | 1106.3 | 1036.304
6992 | 1.0071 | 101.93 | 61.967 | 0.0030187 | 70.006 | 1106.3 |  | 6992 | 101.93 | 1.0071 | 61.967 | 0.0030187 | 70.006 | 1106.3 | 1036.294
6993 | 1.0074 | 101.94 | 61.966 | 0.0030195 | 70.016 | 1106.3 |  | 6993 | 101.94 | 1.0074 | 61.966 | 0.0030195 | 70.016 | 1106.3 | 1036.284
6994 | 1.0077 | 101.95 | 61.966 | 0.0030204 | 70.026 | 1106.3 |  | 6994 | 101.95 | 1.0077 | 61.966 | 0.0030204 | 70.026 | 1106.3 | 1036.274
6995 | 1.008 | 101.96 | 61.966 | 0.0030212 | 70.036 | 1106.3 |  | 6995 | 101.96 | 1.008 | 61.966 | 0.0030212 | 70.036 | 1106.3 | 1036.264
6996 | 1.0083 | 101.97 | 61.966 | 0.0030221 | 70.046 | 1106.3 |  | 6996 | 101.97 | 1.0083 | 61.966 | 0.0030221 | 70.046 | 1106.3 | 1036.254
6997 | 1.0086 | 101.98 | 61.966 | 0.0030229 | 70.056 | 1106.3 |  | 6997 | 101.98 | 1.0086 | 61.966 | 0.0030229 | 70.056 | 1106.3 | 1036.244
6998 | 1.0089 | 101.99 | 61.966 | 0.0030238 | 70.066 | 1106.3 |  | 6998 | 101.99 | 1.0089 | 61.966 | 0.0030238 | 70.066 | 1106.3 | 1036.234
6999 | 1.0092 | 102 | 61.966 | 0.0030246 | 70.076 | 1106.3 |  | 6999 | 102 | 1.0092 | 61.966 | 0.0030246 | 70.076 | 1106.3 | 1036.224
7000 | 1.0095 | 102.01 | 61.966 | 0.0030255 | 70.086 | 1106.3 |  | 7000 | 102.01 | 1.0095 | 61.966 | 0.0030255 | 70.086 | 1106.3 | 1036.214
7001 | 1.0098 | 102.02 | 61.965 | 0.0030263 | 70.096 | 1106.3 |  | 7001 | 102.02 | 1.0098 | 61.965 | 0.0030263 | 70.096 | 1106.3 | 1036.204
7002 | 1.0101 | 102.03 | 61.965 | 0.0030272 | 70.106 | 1106.3 |  | 7002 | 102.03 | 1.0101 | 61.965 | 0.0030272 | 70.106 | 1106.3 | 1036.194
7003 | 1.0105 | 102.04 | 61.965 | 0.003028 | 70.116 | 1106.3 |  | 7003 | 102.04 | 1.0105 | 61.965 | 0.003028 | 70.116 | 1106.3 | 1036.184
7004 | 1.0108 | 102.05 | 61.965 | 0.0030289 | 70.126 | 1106.3 |  | 7004 | 102.05 | 1.0108 | 61.965 | 0.0030289 | 70.126 | 1106.3 | 1036.174
7005 | 1.0111 | 102.06 | 61.965 | 0.0030298 | 70.136 | 1106.3 |  | 7005 | 102.06 | 1.0111 | 61.965 | 0.0030298 | 70.136 | 1106.3 | 1036.164
7006 | 1.0114 | 102.07 | 61.965 | 0.0030306 | 70.146 | 1106.3 |  | 7006 | 102.07 | 1.0114 | 61.965 | 0.0030306 | 70.146 | 1106.3 | 1036.154
7007 | 1.0117 | 102.08 | 61.965 | 0.0030315 | 70.156 | 1106.3 |  | 7007 | 102.08 | 1.0117 | 61.965 | 0.0030315 | 70.156 | 1106.3 | 1036.144
7008 | 1.012 | 102.09 | 61.965 | 0.0030323 | 70.166 | 1106.3 |  | 7008 | 102.09 | 1.012 | 61.965 | 0.0030323 | 70.166 | 1106.3 | 1036.134
7009 | 1.0123 | 102.1 | 61.964 | 0.0030332 | 70.176 | 1106.3 |  | 7009 | 102.1 | 1.0123 | 61.964 | 0.0030332 | 70.176 | 1106.3 | 1036.124
7010 | 1.0126 | 102.11 | 61.964 | 0.003034 | 70.186 | 1106.3 |  | 7010 | 102.11 | 1.0126 | 61.964 | 0.003034 | 70.186 | 1106.3 | 1036.114
7011 | 1.0129 | 102.12 | 61.964 | 0.0030349 | 70.196 | 1106.3 |  | 7011 | 102.12 | 1.0129 | 61.964 | 0.0030349 | 70.196 | 1106.3 | 1036.104
7012 | 1.0132 | 102.13 | 61.964 | 0.0030357 | 70.206 | 1106.4 |  | 7012 | 102.13 | 1.0132 | 61.964 | 0.0030357 | 70.206 | 1106.4 | 1036.194
7013 | 1.0135 | 102.14 | 61.964 | 0.0030366 | 70.216 | 1106.4 |  | 7013 | 102.14 | 1.0135 | 61.964 | 0.0030366 | 70.216 | 1106.4 | 1036.184
7014 | 1.0138 | 102.15 | 61.964 | 0.0030374 | 70.226 | 1106.4 |  | 7014 | 102.15 | 1.0138 | 61.964 | 0.0030374 | 70.226 | 1106.4 | 1036.174
7015 | 1.0141 | 102.16 | 61.964 | 0.0030383 | 70.236 | 1106.4 |  | 7015 | 102.16 | 1.0141 | 61.964 | 0.0030383 | 70.236 | 1106.4 | 1036.164
7016 | 1.0144 | 102.17 | 61.963 | 0.0030391 | 70.246 | 1106.4 |  | 7016 | 102.17 | 1.0144 | 61.963 | 0.0030391 | 70.246 | 1106.4 | 1036.154
7017 | 1.0147 | 102.18 | 61.963 | 0.00304 | 70.256 | 1106.4 |  | 7017 | 102.18 | 1.0147 | 61.963 | 0.00304 | 70.256 | 1106.4 | 1036.144
7018 | 1.015 | 102.19 | 61.963 | 0.0030408 | 70.266 | 1106.4 |  | 7018 | 102.19 | 1.015 | 61.963 | 0.0030408 | 70.266 | 1106.4 | 1036.134
7019 | 1.0153 | 102.2 | 61.963 | 0.0030417 | 70.276 | 1106.4 |  | 7019 | 102.2 | 1.0153 | 61.963 | 0.0030417 | 70.276 | 1106.4 | 1036.124
7020 | 1.0156 | 102.21 | 61.963 | 0.0030426 | 70.286 | 1106.4 |  | 7020 | 102.21 | 1.0156 | 61.963 | 0.0030426 | 70.286 | 1106.4 | 1036.114
7021 | 1.0159 | 102.22 | 61.963 | 0.0030434 | 70.296 | 1106.4 |  | 7021 | 102.22 | 1.0159 | 61.963 | 0.0030434 | 70.296 | 1106.4 | 1036.104
7022 | 1.0162 | 102.23 | 61.963 | 0.0030443 | 70.306 | 1106.4 |  | 7022 | 102.23 | 1.0162 | 61.963 | 0.0030443 | 70.306 | 1106.4 | 1036.094
7023 | 1.0165 | 102.24 | 61.963 | 0.0030451 | 70.316 | 1106.4 |  | 7023 | 102.24 | 1.0165 | 61.963 | 0.0030451 | 70.316 | 1106.4 | 1036.084
7024 | 1.0168 | 102.25 | 61.962 | 0.003046 | 70.326 | 1106.4 |  | 7024 | 102.25 | 1.0168 | 61.962 | 0.003046 | 70.326 | 1106.4 | 1036.074
7025 | 1.0171 | 102.26 | 61.962 | 0.0030468 | 70.336 | 1106.4 |  | 7025 | 102.26 | 1.0171 | 61.962 | 0.0030468 | 70.336 | 1106.4 | 1036.064
7026 | 1.0174 | 102.27 | 61.962 | 0.0030477 | 70.346 | 1106.4 |  | 7026 | 102.27 | 1.0174 | 61.962 | 0.0030477 | 70.346 | 1106.4 | 1036.054
7027 | 1.0177 | 102.28 | 61.962 | 0.0030485 | 70.356 | 1106.4 |  | 7027 | 102.28 | 1.0177 | 61.962 | 0.0030485 | 70.356 | 1106.4 | 1036.044
7028 | 1.018 | 102.29 | 61.962 | 0.0030494 | 70.366 | 1106.4 |  | 7028 | 102.29 | 1.018 | 61.962 | 0.0030494 | 70.366 | 1106.4 | 1036.034
7029 | 1.0183 | 102.3 | 61.962 | 0.0030503 | 70.376 | 1106.4 |  | 7029 | 102.3 | 1.0183 | 61.962 | 0.0030503 | 70.376 | 1106.4 | 1036.024
7030 | 1.0186 | 102.31 | 61.962 | 0.0030511 | 70.386 | 1106.4 |  | 7030 | 102.31 | 1.0186 | 61.962 | 0.0030511 | 70.386 | 1106.4 | 1036.014
7031 | 1.0189 | 102.32 | 61.962 | 0.003052 | 70.396 | 1106.4 |  | 7031 | 102.32 | 1.0189 | 61.962 | 0.003052 | 70.396 | 1106.4 | 1036.004
7032 | 1.0192 | 102.33 | 61.961 | 0.0030528 | 70.406 | 1106.4 |  | 7032 | 102.33 | 1.0192 | 61.961 | 0.0030528 | 70.406 | 1106.4 | 1035.994
7033 | 1.0195 | 102.34 | 61.961 | 0.0030537 | 70.416 | 1106.4 |  | 7033 | 102.34 | 1.0195 | 61.961 | 0.0030537 | 70.416 | 1106.4 | 1035.984
7034 | 1.0198 | 102.35 | 61.961 | 0.0030545 | 70.426 | 1106.4 |  | 7034 | 102.35 | 1.0198 | 61.961 | 0.0030545 | 70.426 | 1106.4 | 1035.974
7035 | 1.0201 | 102.36 | 61.961 | 0.0030554 | 70.436 | 1106.4 |  | 7035 | 102.36 | 1.0201 | 61.961 | 0.0030554 | 70.436 | 1106.4 | 1035.964
7036 | 1.0204 | 102.37 | 61.961 | 0.0030563 | 70.446 | 1106.5 |  | 7036 | 102.37 | 1.0204 | 61.961 | 0.0030563 | 70.446 | 1106.5 | 1036.054
7037 | 1.0208 | 102.38 | 61.961 | 0.0030571 | 70.456 | 1106.5 |  | 7037 | 102.38 | 1.0208 | 61.961 | 0.0030571 | 70.456 | 1106.5 | 1036.044
7038 | 1.0211 | 102.39 | 61.961 | 0.003058 | 70.466 | 1106.5 |  | 7038 | 102.39 | 1.0211 | 61.961 | 0.003058 | 70.466 | 1106.5 | 1036.034
7039 | 1.0214 | 102.4 | 61.96 | 0.0030588 | 70.476 | 1106.5 |  | 7039 | 102.4 | 1.0214 | 61.96 | 0.0030588 | 70.476 | 1106.5 | 1036.024
7040 | 1.0217 | 102.41 | 61.96 | 0.0030597 | 70.486 | 1106.5 |  | 7040 | 102.41 | 1.0217 | 61.96 | 0.0030597 | 70.486 | 1106.5 | 1036.014
7041 | 1.022 | 102.42 | 61.96 | 0.0030606 | 70.496 | 1106.5 |  | 7041 | 102.42 | 1.022 | 61.96 | 0.0030606 | 70.496 | 1106.5 | 1036.004
7042 | 1.0223 | 102.43 | 61.96 | 0.0030614 | 70.506 | 1106.5 |  | 7042 | 102.43 | 1.0223 | 61.96 | 0.0030614 | 70.506 | 1106.5 | 1035.994
7043 | 1.0226 | 102.44 | 61.96 | 0.0030623 | 70.516 | 1106.5 |  | 7043 | 102.44 | 1.0226 | 61.96 | 0.0030623 | 70.516 | 1106.5 | 1035.984
7044 | 1.0229 | 102.45 | 61.96 | 0.0030631 | 70.526 | 1106.5 |  | 7044 | 102.45 | 1.0229 | 61.96 | 0.0030631 | 70.526 | 1106.5 | 1035.974
7045 | 1.0232 | 102.46 | 61.96 | 0.003064 | 70.536 | 1106.5 |  | 7045 | 102.46 | 1.0232 | 61.96 | 0.003064 | 70.536 | 1106.5 | 1035.964
7046 | 1.0235 | 102.47 | 61.96 | 0.0030649 | 70.546 | 1106.5 |  | 7046 | 102.47 | 1.0235 | 61.96 | 0.0030649 | 70.546 | 1106.5 | 1035.954
7047 | 1.0238 | 102.48 | 61.959 | 0.0030657 | 70.556 | 1106.5 |  | 7047 | 102.48 | 1.0238 | 61.959 | 0.0030657 | 70.556 | 1106.5 | 1035.944
7048 | 1.0241 | 102.49 | 61.959 | 0.0030666 | 70.566 | 1106.5 |  | 7048 | 102.49 | 1.0241 | 61.959 | 0.0030666 | 70.566 | 1106.5 | 1035.934
7049 | 1.0244 | 102.5 | 61.959 | 0.0030674 | 70.576 | 1106.5 |  | 7049 | 102.5 | 1.0244 | 61.959 | 0.0030674 | 70.576 | 1106.5 | 1035.924
7050 | 1.0247 | 102.51 | 61.959 | 0.0030683 | 70.586 | 1106.5 |  | 7050 | 102.51 | 1.0247 | 61.959 | 0.0030683 | 70.586 | 1106.5 | 1035.914
7051 | 1.025 | 102.52 | 61.959 | 0.0030692 | 70.596 | 1106.5 |  | 7051 | 102.52 | 1.025 | 61.959 | 0.0030692 | 70.596 | 1106.5 | 1035.904
7052 | 1.0253 | 102.53 | 61.959 | 0.00307 | 70.606 | 1106.5 |  | 7052 | 102.53 | 1.0253 | 61.959 | 0.00307 | 70.606 | 1106.5 | 1035.894
7053 | 1.0256 | 102.54 | 61.959 | 0.0030709 | 70.616 | 1106.5 |  | 7053 | 102.54 | 1.0256 | 61.959 | 0.0030709 | 70.616 | 1106.5 | 1035.884
7054 | 1.0259 | 102.55 | 61.959 | 0.0030718 | 70.626 | 1106.5 |  | 7054 | 102.55 | 1.0259 | 61.959 | 0.0030718 | 70.626 | 1106.5 | 1035.874
7055 | 1.0262 | 102.56 | 61.958 | 0.0030726 | 70.636 | 1106.5 |  | 7055 | 102.56 | 1.0262 | 61.958 | 0.0030726 | 70.636 | 1106.5 | 1035.864
7056 | 1.0265 | 102.57 | 61.958 | 0.0030735 | 70.646 | 1106.5 |  | 7056 | 102.57 | 1.0265 | 61.958 | 0.0030735 | 70.646 | 1106.5 | 1035.854
7057 | 1.0269 | 102.58 | 61.958 | 0.0030743 | 70.656 | 1106.5 |  | 7057 | 102.58 | 1.0269 | 61.958 | 0.0030743 | 70.656 | 1106.5 | 1035.844
7058 | 1.0272 | 102.59 | 61.958 | 0.0030752 | 70.666 | 1106.5 |  | 7058 | 102.59 | 1.0272 | 61.958 | 0.0030752 | 70.666 | 1106.5 | 1035.834
7059 | 1.0275 | 102.6 | 61.958 | 0.0030761 | 70.676 | 1106.6 |  | 7059 | 102.6 | 1.0275 | 61.958 | 0.0030761 | 70.676 | 1106.6 | 1035.924
7060 | 1.0278 | 102.61 | 61.958 | 0.0030769 | 70.686 | 1106.6 |  | 7060 | 102.61 | 1.0278 | 61.958 | 0.0030769 | 70.686 | 1106.6 | 1035.914
7061 | 1.0281 | 102.62 | 61.958 | 0.0030778 | 70.696 | 1106.6 |  | 7061 | 102.62 | 1.0281 | 61.958 | 0.0030778 | 70.696 | 1106.6 | 1035.904
7062 | 1.0284 | 102.63 | 61.957 | 0.0030787 | 70.706 | 1106.6 |  | 7062 | 102.63 | 1.0284 | 61.957 | 0.0030787 | 70.706 | 1106.6 | 1035.894
7063 | 1.0287 | 102.64 | 61.957 | 0.0030795 | 70.716 | 1106.6 |  | 7063 | 102.64 | 1.0287 | 61.957 | 0.0030795 | 70.716 | 1106.6 | 1035.884
7064 | 1.029 | 102.65 | 61.957 | 0.0030804 | 70.726 | 1106.6 |  | 7064 | 102.65 | 1.029 | 61.957 | 0.0030804 | 70.726 | 1106.6 | 1035.874
7065 | 1.0293 | 102.66 | 61.957 | 0.0030812 | 70.736 | 1106.6 |  | 7065 | 102.66 | 1.0293 | 61.957 | 0.0030812 | 70.736 | 1106.6 | 1035.864
7066 | 1.0296 | 102.67 | 61.957 | 0.0030821 | 70.746 | 1106.6 |  | 7066 | 102.67 | 1.0296 | 61.957 | 0.0030821 | 70.746 | 1106.6 | 1035.854
7067 | 1.0299 | 102.68 | 61.957 | 0.003083 | 70.756 | 1106.6 |  | 7067 | 102.68 | 1.0299 | 61.957 | 0.003083 | 70.756 | 1106.6 | 1035.844
7068 | 1.0302 | 102.69 | 61.957 | 0.0030838 | 70.766 | 1106.6 |  | 7068 | 102.69 | 1.0302 | 61.957 | 0.0030838 | 70.766 | 1106.6 | 1035.834
7069 | 1.0305 | 102.7 | 61.957 | 0.0030847 | 70.776 | 1106.6 |  | 7069 | 102.7 | 1.0305 | 61.957 | 0.0030847 | 70.776 | 1106.6 | 1035.824
7070 | 1.0308 | 102.71 | 61.956 | 0.0030856 | 70.786 | 1106.6 |  | 7070 | 102.71 | 1.0308 | 61.956 | 0.0030856 | 70.786 | 1106.6 | 1035.814
7071 | 1.0311 | 102.72 | 61.956 | 0.0030864 | 70.796 | 1106.6 |  | 7071 | 102.72 | 1.0311 | 61.956 | 0.0030864 | 70.796 | 1106.6 | 1035.804
7072 | 1.0315 | 102.73 | 61.956 | 0.0030873 | 70.806 | 1106.6 |  | 7072 | 102.73 | 1.0315 | 61.956 | 0.0030873 | 70.806 | 1106.6 | 1035.794
7073 | 1.0318 | 102.74 | 61.956 | 0.0030882 | 70.816 | 1106.6 |  | 7073 | 102.74 | 1.0318 | 61.956 | 0.0030882 | 70.816 | 1106.6 | 1035.784
7074 | 1.0321 | 102.75 | 61.956 | 0.003089 | 70.826 | 1106.6 |  | 7074 | 102.75 | 1.0321 | 61.956 | 0.003089 | 70.826 | 1106.6 | 1035.774
7075 | 1.0324 | 102.76 | 61.956 | 0.0030899 | 70.836 | 1106.6 |  | 7075 | 102.76 | 1.0324 | 61.956 | 0.0030899 | 70.836 | 1106.6 | 1035.764
7076 | 1.0327 | 102.77 | 61.956 | 0.0030908 | 70.846 | 1106.6 |  | 7076 | 102.77 | 1.0327 | 61.956 | 0.0030908 | 70.846 | 1106.6 | 1035.754
7077 | 1.033 | 102.78 | 61.956 | 0.0030916 | 70.856 | 1106.6 |  | 7077 | 102.78 | 1.033 | 61.956 | 0.0030916 | 70.856 | 1106.6 | 1035.744
7078 | 1.0333 | 102.79 | 61.955 | 0.0030925 | 70.866 | 1106.6 |  | 7078 | 102.79 | 1.0333 | 61.955 | 0.0030925 | 70.866 | 1106.6 | 1035.734
7079 | 1.0336 | 102.8 | 61.955 | 0.0030934 | 70.876 | 1106.6 |  | 7079 | 102.8 | 1.0336 | 61.955 | 0.0030934 | 70.876 | 1106.6 | 1035.724
7080 | 1.0339 | 102.81 | 61.955 | 0.0030942 | 70.886 | 1106.6 |  | 7080 | 102.81 | 1.0339 | 61.955 | 0.0030942 | 70.886 | 1106.6 | 1035.714
7081 | 1.0342 | 102.82 | 61.955 | 0.0030951 | 70.896 | 1106.6 |  | 7081 | 102.82 | 1.0342 | 61.955 | 0.0030951 | 70.896 | 1106.6 | 1035.704
7082 | 1.0345 | 102.83 | 61.955 | 0.003096 | 70.906 | 1106.7 |  | 7082 | 102.83 | 1.0345 | 61.955 | 0.003096 | 70.906 | 1106.7 | 1035.794
7083 | 1.0348 | 102.84 | 61.955 | 0.0030968 | 70.916 | 1106.7 |  | 7083 | 102.84 | 1.0348 | 61.955 | 0.0030968 | 70.916 | 1106.7 | 1035.784
7084 | 1.0351 | 102.85 | 61.955 | 0.0030977 | 70.926 | 1106.7 |  | 7084 | 102.85 | 1.0351 | 61.955 | 0.0030977 | 70.926 | 1106.7 | 1035.774
7085 | 1.0355 | 102.86 | 61.954 | 0.0030986 | 70.936 | 1106.7 |  | 7085 | 102.86 | 1.0355 | 61.954 | 0.0030986 | 70.936 | 1106.7 | 1035.764
7086 | 1.0358 | 102.87 | 61.954 | 0.0030994 | 70.946 | 1106.7 |  | 7086 | 102.87 | 1.0358 | 61.954 | 0.0030994 | 70.946 | 1106.7 | 1035.754
7087 | 1.0361 | 102.88 | 61.954 | 0.0031003 | 70.956 | 1106.7 |  | 7087 | 102.88 | 1.0361 | 61.954 | 0.0031003 | 70.956 | 1106.7 | 1035.744
7088 | 1.0364 | 102.89 | 61.954 | 0.0031012 | 70.966 | 1106.7 |  | 7088 | 102.89 | 1.0364 | 61.954 | 0.0031012 | 70.966 | 1106.7 | 1035.734
7089 | 1.0367 | 102.9 | 61.954 | 0.0031021 | 70.976 | 1106.7 |  | 7089 | 102.9 | 1.0367 | 61.954 | 0.0031021 | 70.976 | 1106.7 | 1035.724
7090 | 1.037 | 102.91 | 61.954 | 0.0031029 | 70.985 | 1106.7 |  | 7090 | 102.91 | 1.037 | 61.954 | 0.0031029 | 70.985 | 1106.7 | 1035.715
7091 | 1.0373 | 102.92 | 61.954 | 0.0031038 | 70.995 | 1106.7 |  | 7091 | 102.92 | 1.0373 | 61.954 | 0.0031038 | 70.995 | 1106.7 | 1035.705
7092 | 1.0376 | 102.93 | 61.954 | 0.0031047 | 71.005 | 1106.7 |  | 7092 | 102.93 | 1.0376 | 61.954 | 0.0031047 | 71.005 | 1106.7 | 1035.695
7093 | 1.0379 | 102.94 | 61.953 | 0.0031055 | 71.015 | 1106.7 |  | 7093 | 102.94 | 1.0379 | 61.953 | 0.0031055 | 71.015 | 1106.7 | 1035.685
7094 | 1.0382 | 102.95 | 61.953 | 0.0031064 | 71.025 | 1106.7 |  | 7094 | 102.95 | 1.0382 | 61.953 | 0.0031064 | 71.025 | 1106.7 | 1035.675
7095 | 1.0385 | 102.96 | 61.953 | 0.0031073 | 71.035 | 1106.7 |  | 7095 | 102.96 | 1.0385 | 61.953 | 0.0031073 | 71.035 | 1106.7 | 1035.665
7096 | 1.0388 | 102.97 | 61.953 | 0.0031081 | 71.045 | 1106.7 |  | 7096 | 102.97 | 1.0388 | 61.953 | 0.0031081 | 71.045 | 1106.7 | 1035.655
7097 | 1.0392 | 102.98 | 61.953 | 0.003109 | 71.055 | 1106.7 |  | 7097 | 102.98 | 1.0392 | 61.953 | 0.003109 | 71.055 | 1106.7 | 1035.645
7098 | 1.0395 | 102.99 | 61.953 | 0.0031099 | 71.065 | 1106.7 |  | 7098 | 102.99 | 1.0395 | 61.953 | 0.0031099 | 71.065 | 1106.7 | 1035.635
7099 | 1.0398 | 103 | 61.953 | 0.0031108 | 71.075 | 1106.7 |  | 7099 | 103 | 1.0398 | 61.953 | 0.0031108 | 71.075 | 1106.7 | 1035.625
7100 | 1.0401 | 103.01 | 61.953 | 0.0031116 | 71.085 | 1106.7 |  | 7100 | 103.01 | 1.0401 | 61.953 | 0.0031116 | 71.085 | 1106.7 | 1035.615
7101 | 1.0404 | 103.02 | 61.952 | 0.0031125 | 71.095 | 1106.7 |  | 7101 | 103.02 | 1.0404 | 61.952 | 0.0031125 | 71.095 | 1106.7 | 1035.605
7102 | 1.0407 | 103.03 | 61.952 | 0.0031134 | 71.105 | 1106.7 |  | 7102 | 103.03 | 1.0407 | 61.952 | 0.0031134 | 71.105 | 1106.7 | 1035.595
7103 | 1.041 | 103.04 | 61.952 | 0.0031142 | 71.115 | 1106.7 |  | 7103 | 103.04 | 1.041 | 61.952 | 0.0031142 | 71.115 | 1106.7 | 1035.585
7104 | 1.0413 | 103.05 | 61.952 | 0.0031151 | 71.125 | 1106.7 |  | 7104 | 103.05 | 1.0413 | 61.952 | 0.0031151 | 71.125 | 1106.7 | 1035.575
7105 | 1.0416 | 103.06 | 61.952 | 0.003116 | 71.135 | 1106.7 |  | 7105 | 103.06 | 1.0416 | 61.952 | 0.003116 | 71.135 | 1106.7 | 1035.565
7106 | 1.0419 | 103.07 | 61.952 | 0.0031169 | 71.145 | 1106.8 |  | 7106 | 103.07 | 1.0419 | 61.952 | 0.0031169 | 71.145 | 1106.8 | 1035.655
7107 | 1.0422 | 103.08 | 61.952 | 0.0031177 | 71.155 | 1106.8 |  | 7107 | 103.08 | 1.0422 | 61.952 | 0.0031177 | 71.155 | 1106.8 | 1035.645
7108 | 1.0426 | 103.09 | 61.951 | 0.0031186 | 71.165 | 1106.8 |  | 7108 | 103.09 | 1.0426 | 61.951 | 0.0031186 | 71.165 | 1106.8 | 1035.635
7109 | 1.0429 | 103.1 | 61.951 | 0.0031195 | 71.175 | 1106.8 |  | 7109 | 103.1 | 1.0429 | 61.951 | 0.0031195 | 71.175 | 1106.8 | 1035.625
7110 | 1.0432 | 103.11 | 61.951 | 0.0031204 | 71.185 | 1106.8 |  | 7110 | 103.11 | 1.0432 | 61.951 | 0.0031204 | 71.185 | 1106.8 | 1035.615
7111 | 1.0435 | 103.12 | 61.951 | 0.0031212 | 71.195 | 1106.8 |  | 7111 | 103.12 | 1.0435 | 61.951 | 0.0031212 | 71.195 | 1106.8 | 1035.605
7112 | 1.0438 | 103.13 | 61.951 | 0.0031221 | 71.205 | 1106.8 |  | 7112 | 103.13 | 1.0438 | 61.951 | 0.0031221 | 71.205 | 1106.8 | 1035.595
7113 | 1.0441 | 103.14 | 61.951 | 0.003123 | 71.215 | 1106.8 |  | 7113 | 103.14 | 1.0441 | 61.951 | 0.003123 | 71.215 | 1106.8 | 1035.585
7114 | 1.0444 | 103.15 | 61.951 | 0.0031239 | 71.225 | 1106.8 |  | 7114 | 103.15 | 1.0444 | 61.951 | 0.0031239 | 71.225 | 1106.8 | 1035.575
7115 | 1.0447 | 103.16 | 61.951 | 0.0031247 | 71.235 | 1106.8 |  | 7115 | 103.16 | 1.0447 | 61.951 | 0.0031247 | 71.235 | 1106.8 | 1035.565
7116 | 1.045 | 103.17 | 61.95 | 0.0031256 | 71.245 | 1106.8 |  | 7116 | 103.17 | 1.045 | 61.95 | 0.0031256 | 71.245 | 1106.8 | 1035.555
7117 | 1.0454 | 103.18 | 61.95 | 0.0031265 | 71.255 | 1106.8 |  | 7117 | 103.18 | 1.0454 | 61.95 | 0.0031265 | 71.255 | 1106.8 | 1035.545
7118 | 1.0457 | 103.19 | 61.95 | 0.0031274 | 71.265 | 1106.8 |  | 7118 | 103.19 | 1.0457 | 61.95 | 0.0031274 | 71.265 | 1106.8 | 1035.535
7119 | 1.046 | 103.2 | 61.95 | 0.0031282 | 71.275 | 1106.8 |  | 7119 | 103.2 | 1.046 | 61.95 | 0.0031282 | 71.275 | 1106.8 | 1035.525
7120 | 1.0463 | 103.21 | 61.95 | 0.0031291 | 71.285 | 1106.8 |  | 7120 | 103.21 | 1.0463 | 61.95 | 0.0031291 | 71.285 | 1106.8 | 1035.515
7121 | 1.0466 | 103.22 | 61.95 | 0.00313 | 71.295 | 1106.8 |  | 7121 | 103.22 | 1.0466 | 61.95 | 0.00313 | 71.295 | 1106.8 | 1035.505
7122 | 1.0469 | 103.23 | 61.95 | 0.0031309 | 71.305 | 1106.8 |  | 7122 | 103.23 | 1.0469 | 61.95 | 0.0031309 | 71.305 | 1106.8 | 1035.495
7123 | 1.0472 | 103.24 | 61.95 | 0.0031317 | 71.315 | 1106.8 |  | 7123 | 103.24 | 1.0472 | 61.95 | 0.0031317 | 71.315 | 1106.8 | 1035.485
7124 | 1.0475 | 103.25 | 61.949 | 0.0031326 | 71.325 | 1106.8 |  | 7124 | 103.25 | 1.0475 | 61.949 | 0.0031326 | 71.325 | 1106.8 | 1035.475
7125 | 1.0478 | 103.26 | 61.949 | 0.0031335 | 71.335 | 1106.8 |  | 7125 | 103.26 | 1.0478 | 61.949 | 0.0031335 | 71.335 | 1106.8 | 1035.465
7126 | 1.0482 | 103.27 | 61.949 | 0.0031344 | 71.345 | 1106.8 |  | 7126 | 103.27 | 1.0482 | 61.949 | 0.0031344 | 71.345 | 1106.8 | 1035.455
7127 | 1.0485 | 103.28 | 61.949 | 0.0031352 | 71.355 | 1106.8 |  | 7127 | 103.28 | 1.0485 | 61.949 | 0.0031352 | 71.355 | 1106.8 | 1035.445
7128 | 1.0488 | 103.29 | 61.949 | 0.0031361 | 71.365 | 1106.8 |  | 7128 | 103.29 | 1.0488 | 61.949 | 0.0031361 | 71.365 | 1106.8 | 1035.435
7129 | 1.0491 | 103.3 | 61.949 | 0.003137 | 71.375 | 1106.9 |  | 7129 | 103.3 | 1.0491 | 61.949 | 0.003137 | 71.375 | 1106.9 | 1035.525
7130 | 1.0494 | 103.31 | 61.949 | 0.0031379 | 71.385 | 1106.9 |  | 7130 | 103.31 | 1.0494 | 61.949 | 0.0031379 | 71.385 | 1106.9 | 1035.515
7131 | 1.0497 | 103.32 | 61.948 | 0.0031388 | 71.395 | 1106.9 |  | 7131 | 103.32 | 1.0497 | 61.948 | 0.0031388 | 71.395 | 1106.9 | 1035.505
7132 | 1.05 | 103.33 | 61.948 | 0.0031396 | 71.405 | 1106.9 |  | 7132 | 103.33 | 1.05 | 61.948 | 0.0031396 | 71.405 | 1106.9 | 1035.495
7133 | 1.0503 | 103.34 | 61.948 | 0.0031405 | 71.415 | 1106.9 |  | 7133 | 103.34 | 1.0503 | 61.948 | 0.0031405 | 71.415 | 1106.9 | 1035.485
7134 | 1.0506 | 103.35 | 61.948 | 0.0031414 | 71.425 | 1106.9 |  | 7134 | 103.35 | 1.0506 | 61.948 | 0.0031414 | 71.425 | 1106.9 | 1035.475
7135 | 1.051 | 103.36 | 61.948 | 0.0031423 | 71.435 | 1106.9 |  | 7135 | 103.36 | 1.051 | 61.948 | 0.0031423 | 71.435 | 1106.9 | 1035.465
7136 | 1.0513 | 103.37 | 61.948 | 0.0031431 | 71.445 | 1106.9 |  | 7136 | 103.37 | 1.0513 | 61.948 | 0.0031431 | 71.445 | 1106.9 | 1035.455
7137 | 1.0516 | 103.38 | 61.948 | 0.003144 | 71.455 | 1106.9 |  | 7137 | 103.38 | 1.0516 | 61.948 | 0.003144 | 71.455 | 1106.9 | 1035.445
7138 | 1.0519 | 103.39 | 61.948 | 0.0031449 | 71.465 | 1106.9 |  | 7138 | 103.39 | 1.0519 | 61.948 | 0.0031449 | 71.465 | 1106.9 | 1035.435
7139 | 1.0522 | 103.4 | 61.947 | 0.0031458 | 71.475 | 1106.9 |  | 7139 | 103.4 | 1.0522 | 61.947 | 0.0031458 | 71.475 | 1106.9 | 1035.425
7140 | 1.0525 | 103.41 | 61.947 | 0.0031467 | 71.485 | 1106.9 |  | 7140 | 103.41 | 1.0525 | 61.947 | 0.0031467 | 71.485 | 1106.9 | 1035.415
7141 | 1.0528 | 103.42 | 61.947 | 0.0031475 | 71.495 | 1106.9 |  | 7141 | 103.42 | 1.0528 | 61.947 | 0.0031475 | 71.495 | 1106.9 | 1035.405
7142 | 1.0531 | 103.43 | 61.947 | 0.0031484 | 71.505 | 1106.9 |  | 7142 | 103.43 | 1.0531 | 61.947 | 0.0031484 | 71.505 | 1106.9 | 1035.395
7143 | 1.0535 | 103.44 | 61.947 | 0.0031493 | 71.515 | 1106.9 |  | 7143 | 103.44 | 1.0535 | 61.947 | 0.0031493 | 71.515 | 1106.9 | 1035.385
7144 | 1.0538 | 103.45 | 61.947 | 0.0031502 | 71.525 | 1106.9 |  | 7144 | 103.45 | 1.0538 | 61.947 | 0.0031502 | 71.525 | 1106.9 | 1035.375
7145 | 1.0541 | 103.46 | 61.947 | 0.0031511 | 71.535 | 1106.9 |  | 7145 | 103.46 | 1.0541 | 61.947 | 0.0031511 | 71.535 | 1106.9 | 1035.365
7146 | 1.0544 | 103.47 | 61.946 | 0.0031519 | 71.545 | 1106.9 |  | 7146 | 103.47 | 1.0544 | 61.946 | 0.0031519 | 71.545 | 1106.9 | 1035.355
7147 | 1.0547 | 103.48 | 61.946 | 0.0031528 | 71.555 | 1106.9 |  | 7147 | 103.48 | 1.0547 | 61.946 | 0.0031528 | 71.555 | 1106.9 | 1035.345
7148 | 1.055 | 103.49 | 61.946 | 0.0031537 | 71.565 | 1106.9 |  | 7148 | 103.49 | 1.055 | 61.946 | 0.0031537 | 71.565 | 1106.9 | 1035.335
7149 | 1.0553 | 103.5 | 61.946 | 0.0031546 | 71.575 | 1106.9 |  | 7149 | 103.5 | 1.0553 | 61.946 | 0.0031546 | 71.575 | 1106.9 | 1035.325
7150 | 1.0556 | 103.51 | 61.946 | 0.0031555 | 71.585 | 1106.9 |  | 7150 | 103.51 | 1.0556 | 61.946 | 0.0031555 | 71.585 | 1106.9 | 1035.315
7151 | 1.056 | 103.52 | 61.946 | 0.0031564 | 71.595 | 1106.9 |  | 7151 | 103.52 | 1.056 | 61.946 | 0.0031564 | 71.595 | 1106.9 | 1035.305
7152 | 1.0563 | 103.53 | 61.946 | 0.0031572 | 71.605 | 1106.9 |  | 7152 | 103.53 | 1.0563 | 61.946 | 0.0031572 | 71.605 | 1106.9 | 1035.295
7153 | 1.0566 | 103.54 | 61.946 | 0.0031581 | 71.615 | 1107 |  | 7153 | 103.54 | 1.0566 | 61.946 | 0.0031581 | 71.615 | 1107 | 1035.385
7154 | 1.0569 | 103.55 | 61.945 | 0.003159 | 71.625 | 1107 |  | 7154 | 103.55 | 1.0569 | 61.945 | 0.003159 | 71.625 | 1107 | 1035.375
7155 | 1.0572 | 103.56 | 61.945 | 0.0031599 | 71.635 | 1107 |  | 7155 | 103.56 | 1.0572 | 61.945 | 0.0031599 | 71.635 | 1107 | 1035.365
7156 | 1.0575 | 103.57 | 61.945 | 0.0031608 | 71.645 | 1107 |  | 7156 | 103.57 | 1.0575 | 61.945 | 0.0031608 | 71.645 | 1107 | 1035.355
7157 | 1.0578 | 103.58 | 61.945 | 0.0031617 | 71.655 | 1107 |  | 7157 | 103.58 | 1.0578 | 61.945 | 0.0031617 | 71.655 | 1107 | 1035.345
7158 | 1.0582 | 103.59 | 61.945 | 0.0031625 | 71.665 | 1107 |  | 7158 | 103.59 | 1.0582 | 61.945 | 0.0031625 | 71.665 | 1107 | 1035.335
7159 | 1.0585 | 103.6 | 61.945 | 0.0031634 | 71.675 | 1107 |  | 7159 | 103.6 | 1.0585 | 61.945 | 0.0031634 | 71.675 | 1107 | 1035.325
7160 | 1.0588 | 103.61 | 61.945 | 0.0031643 | 71.685 | 1107 |  | 7160 | 103.61 | 1.0588 | 61.945 | 0.0031643 | 71.685 | 1107 | 1035.315
7161 | 1.0591 | 103.62 | 61.944 | 0.0031652 | 71.695 | 1107 |  | 7161 | 103.62 | 1.0591 | 61.944 | 0.0031652 | 71.695 | 1107 | 1035.305
7162 | 1.0594 | 103.63 | 61.944 | 0.0031661 | 71.705 | 1107 |  | 7162 | 103.63 | 1.0594 | 61.944 | 0.0031661 | 71.705 | 1107 | 1035.295
7163 | 1.0597 | 103.64 | 61.944 | 0.003167 | 71.715 | 1107 |  | 7163 | 103.64 | 1.0597 | 61.944 | 0.003167 | 71.715 | 1107 | 1035.285
7164 | 1.06 | 103.65 | 61.944 | 0.0031678 | 71.725 | 1107 |  | 7164 | 103.65 | 1.06 | 61.944 | 0.0031678 | 71.725 | 1107 | 1035.275
7165 | 1.0604 | 103.66 | 61.944 | 0.0031687 | 71.735 | 1107 |  | 7165 | 103.66 | 1.0604 | 61.944 | 0.0031687 | 71.735 | 1107 | 1035.265
7166 | 1.0607 | 103.67 | 61.944 | 0.0031696 | 71.745 | 1107 |  | 7166 | 103.67 | 1.0607 | 61.944 | 0.0031696 | 71.745 | 1107 | 1035.255
7167 | 1.061 | 103.68 | 61.944 | 0.0031705 | 71.755 | 1107 |  | 7167 | 103.68 | 1.061 | 61.944 | 0.0031705 | 71.755 | 1107 | 1035.245
7168 | 1.0613 | 103.69 | 61.944 | 0.0031714 | 71.765 | 1107 |  | 7168 | 103.69 | 1.0613 | 61.944 | 0.0031714 | 71.765 | 1107 | 1035.235
7169 | 1.0616 | 103.7 | 61.943 | 0.0031723 | 71.775 | 1107 |  | 7169 | 103.7 | 1.0616 | 61.943 | 0.0031723 | 71.775 | 1107 | 1035.225
7170 | 1.0619 | 103.71 | 61.943 | 0.0031732 | 71.785 | 1107 |  | 7170 | 103.71 | 1.0619 | 61.943 | 0.0031732 | 71.785 | 1107 | 1035.215
7171 | 1.0622 | 103.72 | 61.943 | 0.003174 | 71.795 | 1107 |  | 7171 | 103.72 | 1.0622 | 61.943 | 0.003174 | 71.795 | 1107 | 1035.205
7172 | 1.0626 | 103.73 | 61.943 | 0.0031749 | 71.805 | 1107 |  | 7172 | 103.73 | 1.0626 | 61.943 | 0.0031749 | 71.805 | 1107 | 1035.195
7173 | 1.0629 | 103.74 | 61.943 | 0.0031758 | 71.815 | 1107 |  | 7173 | 103.74 | 1.0629 | 61.943 | 0.0031758 | 71.815 | 1107 | 1035.185
7174 | 1.0632 | 103.75 | 61.943 | 0.0031767 | 71.825 | 1107 |  | 7174 | 103.75 | 1.0632 | 61.943 | 0.0031767 | 71.825 | 1107 | 1035.175
7175 | 1.0635 | 103.76 | 61.943 | 0.0031776 | 71.835 | 1107 |  | 7175 | 103.76 | 1.0635 | 61.943 | 0.0031776 | 71.835 | 1107 | 1035.165
7176 | 1.0638 | 103.77 | 61.943 | 0.0031785 | 71.845 | 1107.1 |  | 7176 | 103.77 | 1.0638 | 61.943 | 0.0031785 | 71.845 | 1107.1 | 1035.255
7177 | 1.0641 | 103.78 | 61.942 | 0.0031794 | 71.855 | 1107.1 |  | 7177 | 103.78 | 1.0641 | 61.942 | 0.0031794 | 71.855 | 1107.1 | 1035.245
7178 | 1.0645 | 103.79 | 61.942 | 0.0031803 | 71.865 | 1107.1 |  | 7178 | 103.79 | 1.0645 | 61.942 | 0.0031803 | 71.865 | 1107.1 | 1035.235
7179 | 1.0648 | 103.8 | 61.942 | 0.0031811 | 71.875 | 1107.1 |  | 7179 | 103.8 | 1.0648 | 61.942 | 0.0031811 | 71.875 | 1107.1 | 1035.225
7180 | 1.0651 | 103.81 | 61.942 | 0.003182 | 71.885 | 1107.1 |  | 7180 | 103.81 | 1.0651 | 61.942 | 0.003182 | 71.885 | 1107.1 | 1035.215
7181 | 1.0654 | 103.82 | 61.942 | 0.0031829 | 71.895 | 1107.1 |  | 7181 | 103.82 | 1.0654 | 61.942 | 0.0031829 | 71.895 | 1107.1 | 1035.205
7182 | 1.0657 | 103.83 | 61.942 | 0.0031838 | 71.905 | 1107.1 |  | 7182 | 103.83 | 1.0657 | 61.942 | 0.0031838 | 71.905 | 1107.1 | 1035.195
7183 | 1.066 | 103.84 | 61.942 | 0.0031847 | 71.915 | 1107.1 |  | 7183 | 103.84 | 1.066 | 61.942 | 0.0031847 | 71.915 | 1107.1 | 1035.185
7184 | 1.0663 | 103.85 | 61.941 | 0.0031856 | 71.925 | 1107.1 |  | 7184 | 103.85 | 1.0663 | 61.941 | 0.0031856 | 71.925 | 1107.1 | 1035.175
7185 | 1.0667 | 103.86 | 61.941 | 0.0031865 | 71.935 | 1107.1 |  | 7185 | 103.86 | 1.0667 | 61.941 | 0.0031865 | 71.935 | 1107.1 | 1035.165
7186 | 1.067 | 103.87 | 61.941 | 0.0031874 | 71.945 | 1107.1 |  | 7186 | 103.87 | 1.067 | 61.941 | 0.0031874 | 71.945 | 1107.1 | 1035.155
7187 | 1.0673 | 103.88 | 61.941 | 0.0031883 | 71.955 | 1107.1 |  | 7187 | 103.88 | 1.0673 | 61.941 | 0.0031883 | 71.955 | 1107.1 | 1035.145
7188 | 1.0676 | 103.89 | 61.941 | 0.0031891 | 71.965 | 1107.1 |  | 7188 | 103.89 | 1.0676 | 61.941 | 0.0031891 | 71.965 | 1107.1 | 1035.135
7189 | 1.0679 | 103.9 | 61.941 | 0.00319 | 71.975 | 1107.1 |  | 7189 | 103.9 | 1.0679 | 61.941 | 0.00319 | 71.975 | 1107.1 | 1035.125
7190 | 1.0682 | 103.91 | 61.941 | 0.0031909 | 71.985 | 1107.1 |  | 7190 | 103.91 | 1.0682 | 61.941 | 0.0031909 | 71.985 | 1107.1 | 1035.115
7191 | 1.0686 | 103.92 | 61.941 | 0.0031918 | 71.995 | 1107.1 |  | 7191 | 103.92 | 1.0686 | 61.941 | 0.0031918 | 71.995 | 1107.1 | 1035.105
7192 | 1.0689 | 103.93 | 61.94 | 0.0031927 | 72.005 | 1107.1 |  | 7192 | 103.93 | 1.0689 | 61.94 | 0.0031927 | 72.005 | 1107.1 | 1035.095
7193 | 1.0692 | 103.94 | 61.94 | 0.0031936 | 72.014 | 1107.1 |  | 7193 | 103.94 | 1.0692 | 61.94 | 0.0031936 | 72.014 | 1107.1 | 1035.086
7194 | 1.0695 | 103.95 | 61.94 | 0.0031945 | 72.024 | 1107.1 |  | 7194 | 103.95 | 1.0695 | 61.94 | 0.0031945 | 72.024 | 1107.1 | 1035.076
7195 | 1.0698 | 103.96 | 61.94 | 0.0031954 | 72.034 | 1107.1 |  | 7195 | 103.96 | 1.0698 | 61.94 | 0.0031954 | 72.034 | 1107.1 | 1035.066
7196 | 1.0701 | 103.97 | 61.94 | 0.0031963 | 72.044 | 1107.1 |  | 7196 | 103.97 | 1.0701 | 61.94 | 0.0031963 | 72.044 | 1107.1 | 1035.056
7197 | 1.0705 | 103.98 | 61.94 | 0.0031972 | 72.054 | 1107.1 |  | 7197 | 103.98 | 1.0705 | 61.94 | 0.0031972 | 72.054 | 1107.1 | 1035.046
7198 | 1.0708 | 103.99 | 61.94 | 0.0031981 | 72.064 | 1107.1 |  | 7198 | 103.99 | 1.0708 | 61.94 | 0.0031981 | 72.064 | 1107.1 | 1035.036
7199 | 1.0711 | 104 | 61.939 | 0.0031989 | 72.074 | 1107.2 |  | 7199 | 104 | 1.0711 | 61.939 | 0.0031989 | 72.074 | 1107.2 | 1035.126
7200 | 1.0714 | 104.01 | 61.939 | 0.0031998 | 72.084 | 1107.2 |  | 7200 | 104.01 | 1.0714 | 61.939 | 0.0031998 | 72.084 | 1107.2 | 1035.116
7201 | 1.0717 | 104.02 | 61.939 | 0.0032007 | 72.094 | 1107.2 |  | 7201 | 104.02 | 1.0717 | 61.939 | 0.0032007 | 72.094 | 1107.2 | 1035.106
7202 | 1.072 | 104.03 | 61.939 | 0.0032016 | 72.104 | 1107.2 |  | 7202 | 104.03 | 1.072 | 61.939 | 0.0032016 | 72.104 | 1107.2 | 1035.096
7203 | 1.0724 | 104.04 | 61.939 | 0.0032025 | 72.114 | 1107.2 |  | 7203 | 104.04 | 1.0724 | 61.939 | 0.0032025 | 72.114 | 1107.2 | 1035.086
7204 | 1.0727 | 104.05 | 61.939 | 0.0032034 | 72.124 | 1107.2 |  | 7204 | 104.05 | 1.0727 | 61.939 | 0.0032034 | 72.124 | 1107.2 | 1035.076
7205 | 1.073 | 104.06 | 61.939 | 0.0032043 | 72.134 | 1107.2 |  | 7205 | 104.06 | 1.073 | 61.939 | 0.0032043 | 72.134 | 1107.2 | 1035.066
7206 | 1.0733 | 104.07 | 61.939 | 0.0032052 | 72.144 | 1107.2 |  | 7206 | 104.07 | 1.0733 | 61.939 | 0.0032052 | 72.144 | 1107.2 | 1035.056
7207 | 1.0736 | 104.08 | 61.938 | 0.0032061 | 72.154 | 1107.2 |  | 7207 | 104.08 | 1.0736 | 61.938 | 0.0032061 | 72.154 | 1107.2 | 1035.046
7208 | 1.074 | 104.09 | 61.938 | 0.003207 | 72.164 | 1107.2 |  | 7208 | 104.09 | 1.074 | 61.938 | 0.003207 | 72.164 | 1107.2 | 1035.036
7209 | 1.0743 | 104.1 | 61.938 | 0.0032079 | 72.174 | 1107.2 |  | 7209 | 104.1 | 1.0743 | 61.938 | 0.0032079 | 72.174 | 1107.2 | 1035.026
7210 | 1.0746 | 104.11 | 61.938 | 0.0032088 | 72.184 | 1107.2 |  | 7210 | 104.11 | 1.0746 | 61.938 | 0.0032088 | 72.184 | 1107.2 | 1035.016
7211 | 1.0749 | 104.12 | 61.938 | 0.0032097 | 72.194 | 1107.2 |  | 7211 | 104.12 | 1.0749 | 61.938 | 0.0032097 | 72.194 | 1107.2 | 1035.006
7212 | 1.0752 | 104.13 | 61.938 | 0.0032106 | 72.204 | 1107.2 |  | 7212 | 104.13 | 1.0752 | 61.938 | 0.0032106 | 72.204 | 1107.2 | 1034.996
7213 | 1.0755 | 104.14 | 61.938 | 0.0032115 | 72.214 | 1107.2 |  | 7213 | 104.14 | 1.0755 | 61.938 | 0.0032115 | 72.214 | 1107.2 | 1034.986
7214 | 1.0759 | 104.15 | 61.937 | 0.0032124 | 72.224 | 1107.2 |  | 7214 | 104.15 | 1.0759 | 61.937 | 0.0032124 | 72.224 | 1107.2 | 1034.976
7215 | 1.0762 | 104.16 | 61.937 | 0.0032133 | 72.234 | 1107.2 |  | 7215 | 104.16 | 1.0762 | 61.937 | 0.0032133 | 72.234 | 1107.2 | 1034.966
7216 | 1.0765 | 104.17 | 61.937 | 0.0032142 | 72.244 | 1107.2 |  | 7216 | 104.17 | 1.0765 | 61.937 | 0.0032142 | 72.244 | 1107.2 | 1034.956
7217 | 1.0768 | 104.18 | 61.937 | 0.003215 | 72.254 | 1107.2 |  | 7217 | 104.18 | 1.0768 | 61.937 | 0.003215 | 72.254 | 1107.2 | 1034.946
7218 | 1.0771 | 104.19 | 61.937 | 0.0032159 | 72.264 | 1107.2 |  | 7218 | 104.19 | 1.0771 | 61.937 | 0.0032159 | 72.264 | 1107.2 | 1034.936
7219 | 1.0775 | 104.2 | 61.937 | 0.0032168 | 72.274 | 1107.2 |  | 7219 | 104.2 | 1.0775 | 61.937 | 0.0032168 | 72.274 | 1107.2 | 1034.926
7220 | 1.0778 | 104.21 | 61.937 | 0.0032177 | 72.284 | 1107.2 |  | 7220 | 104.21 | 1.0778 | 61.937 | 0.0032177 | 72.284 | 1107.2 | 1034.916
7221 | 1.0781 | 104.22 | 61.937 | 0.0032186 | 72.294 | 1107.2 |  | 7221 | 104.22 | 1.0781 | 61.937 | 0.0032186 | 72.294 | 1107.2 | 1034.906
7222 | 1.0784 | 104.23 | 61.936 | 0.0032195 | 72.304 | 1107.2 |  | 7222 | 104.23 | 1.0784 | 61.936 | 0.0032195 | 72.304 | 1107.2 | 1034.896
7223 | 1.0787 | 104.24 | 61.936 | 0.0032204 | 72.314 | 1107.3 |  | 7223 | 104.24 | 1.0787 | 61.936 | 0.0032204 | 72.314 | 1107.3 | 1034.986
7224 | 1.0791 | 104.25 | 61.936 | 0.0032213 | 72.324 | 1107.3 |  | 7224 | 104.25 | 1.0791 | 61.936 | 0.0032213 | 72.324 | 1107.3 | 1034.976
7225 | 1.0794 | 104.26 | 61.936 | 0.0032222 | 72.334 | 1107.3 |  | 7225 | 104.26 | 1.0794 | 61.936 | 0.0032222 | 72.334 | 1107.3 | 1034.966
7226 | 1.0797 | 104.27 | 61.936 | 0.0032231 | 72.344 | 1107.3 |  | 7226 | 104.27 | 1.0797 | 61.936 | 0.0032231 | 72.344 | 1107.3 | 1034.956
7227 | 1.08 | 104.28 | 61.936 | 0.003224 | 72.354 | 1107.3 |  | 7227 | 104.28 | 1.08 | 61.936 | 0.003224 | 72.354 | 1107.3 | 1034.946
7228 | 1.0803 | 104.29 | 61.936 | 0.0032249 | 72.364 | 1107.3 |  | 7228 | 104.29 | 1.0803 | 61.936 | 0.0032249 | 72.364 | 1107.3 | 1034.936
7229 | 1.0806 | 104.3 | 61.935 | 0.0032258 | 72.374 | 1107.3 |  | 7229 | 104.3 | 1.0806 | 61.935 | 0.0032258 | 72.374 | 1107.3 | 1034.926
7230 | 1.081 | 104.31 | 61.935 | 0.0032267 | 72.384 | 1107.3 |  | 7230 | 104.31 | 1.081 | 61.935 | 0.0032267 | 72.384 | 1107.3 | 1034.916
7231 | 1.0813 | 104.32 | 61.935 | 0.0032276 | 72.394 | 1107.3 |  | 7231 | 104.32 | 1.0813 | 61.935 | 0.0032276 | 72.394 | 1107.3 | 1034.906
7232 | 1.0816 | 104.33 | 61.935 | 0.0032285 | 72.404 | 1107.3 |  | 7232 | 104.33 | 1.0816 | 61.935 | 0.0032285 | 72.404 | 1107.3 | 1034.896
7233 | 1.0819 | 104.34 | 61.935 | 0.0032294 | 72.414 | 1107.3 |  | 7233 | 104.34 | 1.0819 | 61.935 | 0.0032294 | 72.414 | 1107.3 | 1034.886
7234 | 1.0822 | 104.35 | 61.935 | 0.0032303 | 72.424 | 1107.3 |  | 7234 | 104.35 | 1.0822 | 61.935 | 0.0032303 | 72.424 | 1107.3 | 1034.876
7235 | 1.0826 | 104.36 | 61.935 | 0.0032312 | 72.434 | 1107.3 |  | 7235 | 104.36 | 1.0826 | 61.935 | 0.0032312 | 72.434 | 1107.3 | 1034.866
7236 | 1.0829 | 104.37 | 61.935 | 0.0032321 | 72.444 | 1107.3 |  | 7236 | 104.37 | 1.0829 | 61.935 | 0.0032321 | 72.444 | 1107.3 | 1034.856
7237 | 1.0832 | 104.38 | 61.934 | 0.003233 | 72.454 | 1107.3 |  | 7237 | 104.38 | 1.0832 | 61.934 | 0.003233 | 72.454 | 1107.3 | 1034.846
7238 | 1.0835 | 104.39 | 61.934 | 0.0032339 | 72.464 | 1107.3 |  | 7238 | 104.39 | 1.0835 | 61.934 | 0.0032339 | 72.464 | 1107.3 | 1034.836
7239 | 1.0838 | 104.4 | 61.934 | 0.0032348 | 72.474 | 1107.3 |  | 7239 | 104.4 | 1.0838 | 61.934 | 0.0032348 | 72.474 | 1107.3 | 1034.826
7240 | 1.0842 | 104.41 | 61.934 | 0.0032357 | 72.484 | 1107.3 |  | 7240 | 104.41 | 1.0842 | 61.934 | 0.0032357 | 72.484 | 1107.3 | 1034.816
7241 | 1.0845 | 104.42 | 61.934 | 0.0032366 | 72.494 | 1107.3 |  | 7241 | 104.42 | 1.0845 | 61.934 | 0.0032366 | 72.494 | 1107.3 | 1034.806
7242 | 1.0848 | 104.43 | 61.934 | 0.0032375 | 72.504 | 1107.3 |  | 7242 | 104.43 | 1.0848 | 61.934 | 0.0032375 | 72.504 | 1107.3 | 1034.796
7243 | 1.0851 | 104.44 | 61.934 | 0.0032384 | 72.514 | 1107.3 |  | 7243 | 104.44 | 1.0851 | 61.934 | 0.0032384 | 72.514 | 1107.3 | 1034.786
7244 | 1.0855 | 104.45 | 61.933 | 0.0032393 | 72.524 | 1107.3 |  | 7244 | 104.45 | 1.0855 | 61.933 | 0.0032393 | 72.524 | 1107.3 | 1034.776
7245 | 1.0858 | 104.46 | 61.933 | 0.0032402 | 72.534 | 1107.3 |  | 7245 | 104.46 | 1.0858 | 61.933 | 0.0032402 | 72.534 | 1107.3 | 1034.766
7246 | 1.0861 | 104.47 | 61.933 | 0.0032411 | 72.544 | 1107.4 |  | 7246 | 104.47 | 1.0861 | 61.933 | 0.0032411 | 72.544 | 1107.4 | 1034.856
7247 | 1.0864 | 104.48 | 61.933 | 0.003242 | 72.554 | 1107.4 |  | 7247 | 104.48 | 1.0864 | 61.933 | 0.003242 | 72.554 | 1107.4 | 1034.846
7248 | 1.0867 | 104.49 | 61.933 | 0.0032429 | 72.564 | 1107.4 |  | 7248 | 104.49 | 1.0867 | 61.933 | 0.0032429 | 72.564 | 1107.4 | 1034.836
7249 | 1.0871 | 104.5 | 61.933 | 0.0032438 | 72.574 | 1107.4 |  | 7249 | 104.5 | 1.0871 | 61.933 | 0.0032438 | 72.574 | 1107.4 | 1034.826
7250 | 1.0874 | 104.51 | 61.933 | 0.0032447 | 72.584 | 1107.4 |  | 7250 | 104.51 | 1.0874 | 61.933 | 0.0032447 | 72.584 | 1107.4 | 1034.816
7251 | 1.0877 | 104.52 | 61.933 | 0.0032456 | 72.594 | 1107.4 |  | 7251 | 104.52 | 1.0877 | 61.933 | 0.0032456 | 72.594 | 1107.4 | 1034.806
7252 | 1.088 | 104.53 | 61.932 | 0.0032465 | 72.604 | 1107.4 |  | 7252 | 104.53 | 1.088 | 61.932 | 0.0032465 | 72.604 | 1107.4 | 1034.796
7253 | 1.0883 | 104.54 | 61.932 | 0.0032475 | 72.614 | 1107.4 |  | 7253 | 104.54 | 1.0883 | 61.932 | 0.0032475 | 72.614 | 1107.4 | 1034.786
7254 | 1.0887 | 104.55 | 61.932 | 0.0032484 | 72.624 | 1107.4 |  | 7254 | 104.55 | 1.0887 | 61.932 | 0.0032484 | 72.624 | 1107.4 | 1034.776
7255 | 1.089 | 104.56 | 61.932 | 0.0032493 | 72.634 | 1107.4 |  | 7255 | 104.56 | 1.089 | 61.932 | 0.0032493 | 72.634 | 1107.4 | 1034.766
7256 | 1.0893 | 104.57 | 61.932 | 0.0032502 | 72.644 | 1107.4 |  | 7256 | 104.57 | 1.0893 | 61.932 | 0.0032502 | 72.644 | 1107.4 | 1034.756
7257 | 1.0896 | 104.58 | 61.932 | 0.0032511 | 72.654 | 1107.4 |  | 7257 | 104.58 | 1.0896 | 61.932 | 0.0032511 | 72.654 | 1107.4 | 1034.746
7258 | 1.09 | 104.59 | 61.932 | 0.003252 | 72.664 | 1107.4 |  | 7258 | 104.59 | 1.09 | 61.932 | 0.003252 | 72.664 | 1107.4 | 1034.736
7259 | 1.0903 | 104.6 | 61.931 | 0.0032529 | 72.674 | 1107.4 |  | 7259 | 104.6 | 1.0903 | 61.931 | 0.0032529 | 72.674 | 1107.4 | 1034.726
7260 | 1.0906 | 104.61 | 61.931 | 0.0032538 | 72.684 | 1107.4 |  | 7260 | 104.61 | 1.0906 | 61.931 | 0.0032538 | 72.684 | 1107.4 | 1034.716
7261 | 1.0909 | 104.62 | 61.931 | 0.0032547 | 72.694 | 1107.4 |  | 7261 | 104.62 | 1.0909 | 61.931 | 0.0032547 | 72.694 | 1107.4 | 1034.706
7262 | 1.0912 | 104.63 | 61.931 | 0.0032556 | 72.704 | 1107.4 |  | 7262 | 104.63 | 1.0912 | 61.931 | 0.0032556 | 72.704 | 1107.4 | 1034.696
7263 | 1.0916 | 104.64 | 61.931 | 0.0032565 | 72.714 | 1107.4 |  | 7263 | 104.64 | 1.0916 | 61.931 | 0.0032565 | 72.714 | 1107.4 | 1034.686
7264 | 1.0919 | 104.65 | 61.931 | 0.0032574 | 72.724 | 1107.4 |  | 7264 | 104.65 | 1.0919 | 61.931 | 0.0032574 | 72.724 | 1107.4 | 1034.676
7265 | 1.0922 | 104.66 | 61.931 | 0.0032583 | 72.734 | 1107.4 |  | 7265 | 104.66 | 1.0922 | 61.931 | 0.0032583 | 72.734 | 1107.4 | 1034.666
7266 | 1.0925 | 104.67 | 61.931 | 0.0032592 | 72.744 | 1107.4 |  | 7266 | 104.67 | 1.0925 | 61.931 | 0.0032592 | 72.744 | 1107.4 | 1034.656
7267 | 1.0929 | 104.68 | 61.93 | 0.0032601 | 72.754 | 1107.4 |  | 7267 | 104.68 | 1.0929 | 61.93 | 0.0032601 | 72.754 | 1107.4 | 1034.646
7268 | 1.0932 | 104.69 | 61.93 | 0.003261 | 72.764 | 1107.4 |  | 7268 | 104.69 | 1.0932 | 61.93 | 0.003261 | 72.764 | 1107.4 | 1034.636
7269 | 1.0935 | 104.7 | 61.93 | 0.0032619 | 72.774 | 1107.4 |  | 7269 | 104.7 | 1.0935 | 61.93 | 0.0032619 | 72.774 | 1107.4 | 1034.626
7270 | 1.0938 | 104.71 | 61.93 | 0.0032629 | 72.784 | 1107.5 |  | 7270 | 104.71 | 1.0938 | 61.93 | 0.0032629 | 72.784 | 1107.5 | 1034.716
7271 | 1.0941 | 104.72 | 61.93 | 0.0032638 | 72.794 | 1107.5 |  | 7271 | 104.72 | 1.0941 | 61.93 | 0.0032638 | 72.794 | 1107.5 | 1034.706
7272 | 1.0945 | 104.73 | 61.93 | 0.0032647 | 72.804 | 1107.5 |  | 7272 | 104.73 | 1.0945 | 61.93 | 0.0032647 | 72.804 | 1107.5 | 1034.696
7273 | 1.0948 | 104.74 | 61.93 | 0.0032656 | 72.814 | 1107.5 |  | 7273 | 104.74 | 1.0948 | 61.93 | 0.0032656 | 72.814 | 1107.5 | 1034.686
7274 | 1.0951 | 104.75 | 61.929 | 0.0032665 | 72.824 | 1107.5 |  | 7274 | 104.75 | 1.0951 | 61.929 | 0.0032665 | 72.824 | 1107.5 | 1034.676
7275 | 1.0954 | 104.76 | 61.929 | 0.0032674 | 72.834 | 1107.5 |  | 7275 | 104.76 | 1.0954 | 61.929 | 0.0032674 | 72.834 | 1107.5 | 1034.666
7276 | 1.0958 | 104.77 | 61.929 | 0.0032683 | 72.844 | 1107.5 |  | 7276 | 104.77 | 1.0958 | 61.929 | 0.0032683 | 72.844 | 1107.5 | 1034.656
7277 | 1.0961 | 104.78 | 61.929 | 0.0032692 | 72.854 | 1107.5 |  | 7277 | 104.78 | 1.0961 | 61.929 | 0.0032692 | 72.854 | 1107.5 | 1034.646
7278 | 1.0964 | 104.79 | 61.929 | 0.0032701 | 72.864 | 1107.5 |  | 7278 | 104.79 | 1.0964 | 61.929 | 0.0032701 | 72.864 | 1107.5 | 1034.636
7279 | 1.0967 | 104.8 | 61.929 | 0.003271 | 72.874 | 1107.5 |  | 7279 | 104.8 | 1.0967 | 61.929 | 0.003271 | 72.874 | 1107.5 | 1034.626
7280 | 1.0971 | 104.81 | 61.929 | 0.0032719 | 72.884 | 1107.5 |  | 7280 | 104.81 | 1.0971 | 61.929 | 0.0032719 | 72.884 | 1107.5 | 1034.616
7281 | 1.0974 | 104.82 | 61.929 | 0.0032728 | 72.894 | 1107.5 |  | 7281 | 104.82 | 1.0974 | 61.929 | 0.0032728 | 72.894 | 1107.5 | 1034.606
7282 | 1.0977 | 104.83 | 61.928 | 0.0032738 | 72.904 | 1107.5 |  | 7282 | 104.83 | 1.0977 | 61.928 | 0.0032738 | 72.904 | 1107.5 | 1034.596
7283 | 1.098 | 104.84 | 61.928 | 0.0032747 | 72.914 | 1107.5 |  | 7283 | 104.84 | 1.098 | 61.928 | 0.0032747 | 72.914 | 1107.5 | 1034.586
7284 | 1.0984 | 104.85 | 61.928 | 0.0032756 | 72.924 | 1107.5 |  | 7284 | 104.85 | 1.0984 | 61.928 | 0.0032756 | 72.924 | 1107.5 | 1034.576
7285 | 1.0987 | 104.86 | 61.928 | 0.0032765 | 72.934 | 1107.5 |  | 7285 | 104.86 | 1.0987 | 61.928 | 0.0032765 | 72.934 | 1107.5 | 1034.566
7286 | 1.099 | 104.87 | 61.928 | 0.0032774 | 72.944 | 1107.5 |  | 7286 | 104.87 | 1.099 | 61.928 | 0.0032774 | 72.944 | 1107.5 | 1034.556
7287 | 1.0993 | 104.88 | 61.928 | 0.0032783 | 72.954 | 1107.5 |  | 7287 | 104.88 | 1.0993 | 61.928 | 0.0032783 | 72.954 | 1107.5 | 1034.546
7288 | 1.0997 | 104.89 | 61.928 | 0.0032792 | 72.964 | 1107.5 |  | 7288 | 104.89 | 1.0997 | 61.928 | 0.0032792 | 72.964 | 1107.5 | 1034.536
7289 | 1.1 | 104.9 | 61.927 | 0.0032801 | 72.974 | 1107.5 |  | 7289 | 104.9 | 1.1 | 61.927 | 0.0032801 | 72.974 | 1107.5 | 1034.526
7290 | 1.1003 | 104.91 | 61.927 | 0.003281 | 72.984 | 1107.5 |  | 7290 | 104.91 | 1.1003 | 61.927 | 0.003281 | 72.984 | 1107.5 | 1034.516
7291 | 1.1006 | 104.92 | 61.927 | 0.003282 | 72.994 | 1107.5 |  | 7291 | 104.92 | 1.1006 | 61.927 | 0.003282 | 72.994 | 1107.5 | 1034.506
7292 | 1.101 | 104.93 | 61.927 | 0.0032829 | 73.004 | 1107.5 |  | 7292 | 104.93 | 1.101 | 61.927 | 0.0032829 | 73.004 | 1107.5 | 1034.496
7293 | 1.1013 | 104.94 | 61.927 | 0.0032838 | 73.014 | 1107.6 |  | 7293 | 104.94 | 1.1013 | 61.927 | 0.0032838 | 73.014 | 1107.6 | 1034.586
7294 | 1.1016 | 104.95 | 61.927 | 0.0032847 | 73.024 | 1107.6 |  | 7294 | 104.95 | 1.1016 | 61.927 | 0.0032847 | 73.024 | 1107.6 | 1034.576
7295 | 1.1019 | 104.96 | 61.927 | 0.0032856 | 73.034 | 1107.6 |  | 7295 | 104.96 | 1.1019 | 61.927 | 0.0032856 | 73.034 | 1107.6 | 1034.566
7296 | 1.1023 | 104.97 | 61.927 | 0.0032865 | 73.044 | 1107.6 |  | 7296 | 104.97 | 1.1023 | 61.927 | 0.0032865 | 73.044 | 1107.6 | 1034.556
7297 | 1.1026 | 104.98 | 61.926 | 0.0032874 | 73.054 | 1107.6 |  | 7297 | 104.98 | 1.1026 | 61.926 | 0.0032874 | 73.054 | 1107.6 | 1034.546
7298 | 1.1029 | 104.99 | 61.926 | 0.0032883 | 73.064 | 1107.6 |  | 7298 | 104.99 | 1.1029 | 61.926 | 0.0032883 | 73.064 | 1107.6 | 1034.536
7299 | 1.1032 | 105 | 61.926 | 0.0032893 | 73.073 | 1107.6 |  | 7299 | 105 | 1.1032 | 61.926 | 0.0032893 | 73.073 | 1107.6 | 1034.527
7300 | 1.1036 | 105.01 | 61.926 | 0.0032902 | 73.083 | 1107.6 |  | 7300 | 105.01 | 1.1036 | 61.926 | 0.0032902 | 73.083 | 1107.6 | 1034.517
7301 | 1.1039 | 105.02 | 61.926 | 0.0032911 | 73.093 | 1107.6 |  | 7301 | 105.02 | 1.1039 | 61.926 | 0.0032911 | 73.093 | 1107.6 | 1034.507
7302 | 1.1042 | 105.03 | 61.926 | 0.003292 | 73.103 | 1107.6 |  | 7302 | 105.03 | 1.1042 | 61.926 | 0.003292 | 73.103 | 1107.6 | 1034.497
7303 | 1.1045 | 105.04 | 61.926 | 0.0032929 | 73.113 | 1107.6 |  | 7303 | 105.04 | 1.1045 | 61.926 | 0.0032929 | 73.113 | 1107.6 | 1034.487
7304 | 1.1049 | 105.05 | 61.925 | 0.0032938 | 73.123 | 1107.6 |  | 7304 | 105.05 | 1.1049 | 61.925 | 0.0032938 | 73.123 | 1107.6 | 1034.477
7305 | 1.1052 | 105.06 | 61.925 | 0.0032947 | 73.133 | 1107.6 |  | 7305 | 105.06 | 1.1052 | 61.925 | 0.0032947 | 73.133 | 1107.6 | 1034.467
7306 | 1.1055 | 105.07 | 61.925 | 0.0032957 | 73.143 | 1107.6 |  | 7306 | 105.07 | 1.1055 | 61.925 | 0.0032957 | 73.143 | 1107.6 | 1034.457
7307 | 1.1058 | 105.08 | 61.925 | 0.0032966 | 73.153 | 1107.6 |  | 7307 | 105.08 | 1.1058 | 61.925 | 0.0032966 | 73.153 | 1107.6 | 1034.447
7308 | 1.1062 | 105.09 | 61.925 | 0.0032975 | 73.163 | 1107.6 |  | 7308 | 105.09 | 1.1062 | 61.925 | 0.0032975 | 73.163 | 1107.6 | 1034.437
7309 | 1.1065 | 105.1 | 61.925 | 0.0032984 | 73.173 | 1107.6 |  | 7309 | 105.1 | 1.1065 | 61.925 | 0.0032984 | 73.173 | 1107.6 | 1034.427
7310 | 1.1068 | 105.11 | 61.925 | 0.0032993 | 73.183 | 1107.6 |  | 7310 | 105.11 | 1.1068 | 61.925 | 0.0032993 | 73.183 | 1107.6 | 1034.417
7311 | 1.1071 | 105.12 | 61.925 | 0.0033002 | 73.193 | 1107.6 |  | 7311 | 105.12 | 1.1071 | 61.925 | 0.0033002 | 73.193 | 1107.6 | 1034.407
7312 | 1.1075 | 105.13 | 61.924 | 0.0033012 | 73.203 | 1107.6 |  | 7312 | 105.13 | 1.1075 | 61.924 | 0.0033012 | 73.203 | 1107.6 | 1034.397
7313 | 1.1078 | 105.14 | 61.924 | 0.0033021 | 73.213 | 1107.6 |  | 7313 | 105.14 | 1.1078 | 61.924 | 0.0033021 | 73.213 | 1107.6 | 1034.387
7314 | 1.1081 | 105.15 | 61.924 | 0.003303 | 73.223 | 1107.6 |  | 7314 | 105.15 | 1.1081 | 61.924 | 0.003303 | 73.223 | 1107.6 | 1034.377
7315 | 1.1084 | 105.16 | 61.924 | 0.0033039 | 73.233 | 1107.6 |  | 7315 | 105.16 | 1.1084 | 61.924 | 0.0033039 | 73.233 | 1107.6 | 1034.367
7316 | 1.1088 | 105.17 | 61.924 | 0.0033048 | 73.243 | 1107.7 |  | 7316 | 105.17 | 1.1088 | 61.924 | 0.0033048 | 73.243 | 1107.7 | 1034.457
7317 | 1.1091 | 105.18 | 61.924 | 0.0033057 | 73.253 | 1107.7 |  | 7317 | 105.18 | 1.1091 | 61.924 | 0.0033057 | 73.253 | 1107.7 | 1034.447
7318 | 1.1094 | 105.19 | 61.924 | 0.0033067 | 73.263 | 1107.7 |  | 7318 | 105.19 | 1.1094 | 61.924 | 0.0033067 | 73.263 | 1107.7 | 1034.437
7319 | 1.1098 | 105.2 | 61.923 | 0.0033076 | 73.273 | 1107.7 |  | 7319 | 105.2 | 1.1098 | 61.923 | 0.0033076 | 73.273 | 1107.7 | 1034.427
7320 | 1.1101 | 105.21 | 61.923 | 0.0033085 | 73.283 | 1107.7 |  | 7320 | 105.21 | 1.1101 | 61.923 | 0.0033085 | 73.283 | 1107.7 | 1034.417
7321 | 1.1104 | 105.22 | 61.923 | 0.0033094 | 73.293 | 1107.7 |  | 7321 | 105.22 | 1.1104 | 61.923 | 0.0033094 | 73.293 | 1107.7 | 1034.407
7322 | 1.1107 | 105.23 | 61.923 | 0.0033103 | 73.303 | 1107.7 |  | 7322 | 105.23 | 1.1107 | 61.923 | 0.0033103 | 73.303 | 1107.7 | 1034.397
7323 | 1.1111 | 105.24 | 61.923 | 0.0033113 | 73.313 | 1107.7 |  | 7323 | 105.24 | 1.1111 | 61.923 | 0.0033113 | 73.313 | 1107.7 | 1034.387
7324 | 1.1114 | 105.25 | 61.923 | 0.0033122 | 73.323 | 1107.7 |  | 7324 | 105.25 | 1.1114 | 61.923 | 0.0033122 | 73.323 | 1107.7 | 1034.377
7325 | 1.1117 | 105.26 | 61.923 | 0.0033131 | 73.333 | 1107.7 |  | 7325 | 105.26 | 1.1117 | 61.923 | 0.0033131 | 73.333 | 1107.7 | 1034.367
7326 | 1.112 | 105.27 | 61.923 | 0.003314 | 73.343 | 1107.7 |  | 7326 | 105.27 | 1.112 | 61.923 | 0.003314 | 73.343 | 1107.7 | 1034.357
7327 | 1.1124 | 105.28 | 61.922 | 0.0033149 | 73.353 | 1107.7 |  | 7327 | 105.28 | 1.1124 | 61.922 | 0.0033149 | 73.353 | 1107.7 | 1034.347
7328 | 1.1127 | 105.29 | 61.922 | 0.0033159 | 73.363 | 1107.7 |  | 7328 | 105.29 | 1.1127 | 61.922 | 0.0033159 | 73.363 | 1107.7 | 1034.337
7329 | 1.113 | 105.3 | 61.922 | 0.0033168 | 73.373 | 1107.7 |  | 7329 | 105.3 | 1.113 | 61.922 | 0.0033168 | 73.373 | 1107.7 | 1034.327
7330 | 1.1134 | 105.31 | 61.922 | 0.0033177 | 73.383 | 1107.7 |  | 7330 | 105.31 | 1.1134 | 61.922 | 0.0033177 | 73.383 | 1107.7 | 1034.317
7331 | 1.1137 | 105.32 | 61.922 | 0.0033186 | 73.393 | 1107.7 |  | 7331 | 105.32 | 1.1137 | 61.922 | 0.0033186 | 73.393 | 1107.7 | 1034.307
7332 | 1.114 | 105.33 | 61.922 | 0.0033195 | 73.403 | 1107.7 |  | 7332 | 105.33 | 1.114 | 61.922 | 0.0033195 | 73.403 | 1107.7 | 1034.297
7333 | 1.1143 | 105.34 | 61.922 | 0.0033205 | 73.413 | 1107.7 |  | 7333 | 105.34 | 1.1143 | 61.922 | 0.0033205 | 73.413 | 1107.7 | 1034.287
7334 | 1.1147 | 105.35 | 61.921 | 0.0033214 | 73.423 | 1107.7 |  | 7334 | 105.35 | 1.1147 | 61.921 | 0.0033214 | 73.423 | 1107.7 | 1034.277
7335 | 1.115 | 105.36 | 61.921 | 0.0033223 | 73.433 | 1107.7 |  | 7335 | 105.36 | 1.115 | 61.921 | 0.0033223 | 73.433 | 1107.7 | 1034.267
7336 | 1.1153 | 105.37 | 61.921 | 0.0033232 | 73.443 | 1107.7 |  | 7336 | 105.37 | 1.1153 | 61.921 | 0.0033232 | 73.443 | 1107.7 | 1034.257
7337 | 1.1157 | 105.38 | 61.921 | 0.0033241 | 73.453 | 1107.7 |  | 7337 | 105.38 | 1.1157 | 61.921 | 0.0033241 | 73.453 | 1107.7 | 1034.247
7338 | 1.116 | 105.39 | 61.921 | 0.0033251 | 73.463 | 1107.7 |  | 7338 | 105.39 | 1.116 | 61.921 | 0.0033251 | 73.463 | 1107.7 | 1034.237
7339 | 1.1163 | 105.4 | 61.921 | 0.003326 | 73.473 | 1107.7 |  | 7339 | 105.4 | 1.1163 | 61.921 | 0.003326 | 73.473 | 1107.7 | 1034.227
7340 | 1.1166 | 105.41 | 61.921 | 0.0033269 | 73.483 | 1107.8 |  | 7340 | 105.41 | 1.1166 | 61.921 | 0.0033269 | 73.483 | 1107.8 | 1034.317
7341 | 1.117 | 105.42 | 61.92 | 0.0033278 | 73.493 | 1107.8 |  | 7341 | 105.42 | 1.117 | 61.92 | 0.0033278 | 73.493 | 1107.8 | 1034.307
7342 | 1.1173 | 105.43 | 61.92 | 0.0033288 | 73.503 | 1107.8 |  | 7342 | 105.43 | 1.1173 | 61.92 | 0.0033288 | 73.503 | 1107.8 | 1034.297
7343 | 1.1176 | 105.44 | 61.92 | 0.0033297 | 73.513 | 1107.8 |  | 7343 | 105.44 | 1.1176 | 61.92 | 0.0033297 | 73.513 | 1107.8 | 1034.287
7344 | 1.118 | 105.45 | 61.92 | 0.0033306 | 73.523 | 1107.8 |  | 7344 | 105.45 | 1.118 | 61.92 | 0.0033306 | 73.523 | 1107.8 | 1034.277
7345 | 1.1183 | 105.46 | 61.92 | 0.0033315 | 73.533 | 1107.8 |  | 7345 | 105.46 | 1.1183 | 61.92 | 0.0033315 | 73.533 | 1107.8 | 1034.267
7346 | 1.1186 | 105.47 | 61.92 | 0.0033325 | 73.543 | 1107.8 |  | 7346 | 105.47 | 1.1186 | 61.92 | 0.0033325 | 73.543 | 1107.8 | 1034.257
7347 | 1.1189 | 105.48 | 61.92 | 0.0033334 | 73.553 | 1107.8 |  | 7347 | 105.48 | 1.1189 | 61.92 | 0.0033334 | 73.553 | 1107.8 | 1034.247
7348 | 1.1193 | 105.49 | 61.92 | 0.0033343 | 73.563 | 1107.8 |  | 7348 | 105.49 | 1.1193 | 61.92 | 0.0033343 | 73.563 | 1107.8 | 1034.237
7349 | 1.1196 | 105.5 | 61.919 | 0.0033352 | 73.573 | 1107.8 |  | 7349 | 105.5 | 1.1196 | 61.919 | 0.0033352 | 73.573 | 1107.8 | 1034.227
7350 | 1.1199 | 105.51 | 61.919 | 0.0033362 | 73.583 | 1107.8 |  | 7350 | 105.51 | 1.1199 | 61.919 | 0.0033362 | 73.583 | 1107.8 | 1034.217
7351 | 1.1203 | 105.52 | 61.919 | 0.0033371 | 73.593 | 1107.8 |  | 7351 | 105.52 | 1.1203 | 61.919 | 0.0033371 | 73.593 | 1107.8 | 1034.207
7352 | 1.1206 | 105.53 | 61.919 | 0.003338 | 73.603 | 1107.8 |  | 7352 | 105.53 | 1.1206 | 61.919 | 0.003338 | 73.603 | 1107.8 | 1034.197
7353 | 1.1209 | 105.54 | 61.919 | 0.0033389 | 73.613 | 1107.8 |  | 7353 | 105.54 | 1.1209 | 61.919 | 0.0033389 | 73.613 | 1107.8 | 1034.187
7354 | 1.1213 | 105.55 | 61.919 | 0.0033399 | 73.623 | 1107.8 |  | 7354 | 105.55 | 1.1213 | 61.919 | 0.0033399 | 73.623 | 1107.8 | 1034.177
7355 | 1.1216 | 105.56 | 61.919 | 0.0033408 | 73.633 | 1107.8 |  | 7355 | 105.56 | 1.1216 | 61.919 | 0.0033408 | 73.633 | 1107.8 | 1034.167
7356 | 1.1219 | 105.57 | 61.918 | 0.0033417 | 73.643 | 1107.8 |  | 7356 | 105.57 | 1.1219 | 61.918 | 0.0033417 | 73.643 | 1107.8 | 1034.157
7357 | 1.1222 | 105.58 | 61.918 | 0.0033426 | 73.653 | 1107.8 |  | 7357 | 105.58 | 1.1222 | 61.918 | 0.0033426 | 73.653 | 1107.8 | 1034.147
7358 | 1.1226 | 105.59 | 61.918 | 0.0033436 | 73.663 | 1107.8 |  | 7358 | 105.59 | 1.1226 | 61.918 | 0.0033436 | 73.663 | 1107.8 | 1034.137
7359 | 1.1229 | 105.6 | 61.918 | 0.0033445 | 73.673 | 1107.8 |  | 7359 | 105.6 | 1.1229 | 61.918 | 0.0033445 | 73.673 | 1107.8 | 1034.127
7360 | 1.1232 | 105.61 | 61.918 | 0.0033454 | 73.683 | 1107.8 |  | 7360 | 105.61 | 1.1232 | 61.918 | 0.0033454 | 73.683 | 1107.8 | 1034.117
7361 | 1.1236 | 105.62 | 61.918 | 0.0033463 | 73.693 | 1107.8 |  | 7361 | 105.62 | 1.1236 | 61.918 | 0.0033463 | 73.693 | 1107.8 | 1034.107
7362 | 1.1239 | 105.63 | 61.918 | 0.0033473 | 73.703 | 1107.8 |  | 7362 | 105.63 | 1.1239 | 61.918 | 0.0033473 | 73.703 | 1107.8 | 1034.097
7363 | 1.1242 | 105.64 | 61.918 | 0.0033482 | 73.713 | 1107.9 |  | 7363 | 105.64 | 1.1242 | 61.918 | 0.0033482 | 73.713 | 1107.9 | 1034.187
7364 | 1.1246 | 105.65 | 61.917 | 0.0033491 | 73.723 | 1107.9 |  | 7364 | 105.65 | 1.1246 | 61.917 | 0.0033491 | 73.723 | 1107.9 | 1034.177
7365 | 1.1249 | 105.66 | 61.917 | 0.00335 | 73.733 | 1107.9 |  | 7365 | 105.66 | 1.1249 | 61.917 | 0.00335 | 73.733 | 1107.9 | 1034.167
7366 | 1.1252 | 105.67 | 61.917 | 0.003351 | 73.743 | 1107.9 |  | 7366 | 105.67 | 1.1252 | 61.917 | 0.003351 | 73.743 | 1107.9 | 1034.157
7367 | 1.1256 | 105.68 | 61.917 | 0.0033519 | 73.753 | 1107.9 |  | 7367 | 105.68 | 1.1256 | 61.917 | 0.0033519 | 73.753 | 1107.9 | 1034.147
7368 | 1.1259 | 105.69 | 61.917 | 0.0033528 | 73.763 | 1107.9 |  | 7368 | 105.69 | 1.1259 | 61.917 | 0.0033528 | 73.763 | 1107.9 | 1034.137
7369 | 1.1262 | 105.7 | 61.917 | 0.0033538 | 73.773 | 1107.9 |  | 7369 | 105.7 | 1.1262 | 61.917 | 0.0033538 | 73.773 | 1107.9 | 1034.127
7370 | 1.1265 | 105.71 | 61.917 | 0.0033547 | 73.783 | 1107.9 |  | 7370 | 105.71 | 1.1265 | 61.917 | 0.0033547 | 73.783 | 1107.9 | 1034.117
7371 | 1.1269 | 105.72 | 61.916 | 0.0033556 | 73.793 | 1107.9 |  | 7371 | 105.72 | 1.1269 | 61.916 | 0.0033556 | 73.793 | 1107.9 | 1034.107
7372 | 1.1272 | 105.73 | 61.916 | 0.0033566 | 73.803 | 1107.9 |  | 7372 | 105.73 | 1.1272 | 61.916 | 0.0033566 | 73.803 | 1107.9 | 1034.097
7373 | 1.1275 | 105.74 | 61.916 | 0.0033575 | 73.813 | 1107.9 |  | 7373 | 105.74 | 1.1275 | 61.916 | 0.0033575 | 73.813 | 1107.9 | 1034.087
7374 | 1.1279 | 105.75 | 61.916 | 0.0033584 | 73.823 | 1107.9 |  | 7374 | 105.75 | 1.1279 | 61.916 | 0.0033584 | 73.823 | 1107.9 | 1034.077
7375 | 1.1282 | 105.76 | 61.916 | 0.0033593 | 73.833 | 1107.9 |  | 7375 | 105.76 | 1.1282 | 61.916 | 0.0033593 | 73.833 | 1107.9 | 1034.067
7376 | 1.1285 | 105.77 | 61.916 | 0.0033603 | 73.843 | 1107.9 |  | 7376 | 105.77 | 1.1285 | 61.916 | 0.0033603 | 73.843 | 1107.9 | 1034.057
7377 | 1.1289 | 105.78 | 61.916 | 0.0033612 | 73.853 | 1107.9 |  | 7377 | 105.78 | 1.1289 | 61.916 | 0.0033612 | 73.853 | 1107.9 | 1034.047
7378 | 1.1292 | 105.79 | 61.916 | 0.0033621 | 73.863 | 1107.9 |  | 7378 | 105.79 | 1.1292 | 61.916 | 0.0033621 | 73.863 | 1107.9 | 1034.037
7379 | 1.1295 | 105.8 | 61.915 | 0.0033631 | 73.873 | 1107.9 |  | 7379 | 105.8 | 1.1295 | 61.915 | 0.0033631 | 73.873 | 1107.9 | 1034.027
7380 | 1.1299 | 105.81 | 61.915 | 0.003364 | 73.883 | 1107.9 |  | 7380 | 105.81 | 1.1299 | 61.915 | 0.003364 | 73.883 | 1107.9 | 1034.017
7381 | 1.1302 | 105.82 | 61.915 | 0.0033649 | 73.893 | 1107.9 |  | 7381 | 105.82 | 1.1302 | 61.915 | 0.0033649 | 73.893 | 1107.9 | 1034.007
7382 | 1.1305 | 105.83 | 61.915 | 0.0033659 | 73.903 | 1107.9 |  | 7382 | 105.83 | 1.1305 | 61.915 | 0.0033659 | 73.903 | 1107.9 | 1033.997
7383 | 1.1309 | 105.84 | 61.915 | 0.0033668 | 73.913 | 1107.9 |  | 7383 | 105.84 | 1.1309 | 61.915 | 0.0033668 | 73.913 | 1107.9 | 1033.987
7384 | 1.1312 | 105.85 | 61.915 | 0.0033677 | 73.923 | 1107.9 |  | 7384 | 105.85 | 1.1312 | 61.915 | 0.0033677 | 73.923 | 1107.9 | 1033.977
7385 | 1.1315 | 105.86 | 61.915 | 0.0033687 | 73.933 | 1107.9 |  | 7385 | 105.86 | 1.1315 | 61.915 | 0.0033687 | 73.933 | 1107.9 | 1033.967
7386 | 1.1319 | 105.87 | 61.914 | 0.0033696 | 73.943 | 1107.9 |  | 7386 | 105.87 | 1.1319 | 61.914 | 0.0033696 | 73.943 | 1107.9 | 1033.957
7387 | 1.1322 | 105.88 | 61.914 | 0.0033705 | 73.953 | 1108 |  | 7387 | 105.88 | 1.1322 | 61.914 | 0.0033705 | 73.953 | 1108 | 1034.047
7388 | 1.1325 | 105.89 | 61.914 | 0.0033715 | 73.963 | 1108 |  | 7388 | 105.89 | 1.1325 | 61.914 | 0.0033715 | 73.963 | 1108 | 1034.037
7389 | 1.1329 | 105.9 | 61.914 | 0.0033724 | 73.973 | 1108 |  | 7389 | 105.9 | 1.1329 | 61.914 | 0.0033724 | 73.973 | 1108 | 1034.027
7390 | 1.1332 | 105.91 | 61.914 | 0.0033733 | 73.983 | 1108 |  | 7390 | 105.91 | 1.1332 | 61.914 | 0.0033733 | 73.983 | 1108 | 1034.017
7391 | 1.1335 | 105.92 | 61.914 | 0.0033743 | 73.993 | 1108 |  | 7391 | 105.92 | 1.1335 | 61.914 | 0.0033743 | 73.993 | 1108 | 1034.007
7392 | 1.1339 | 105.93 | 61.914 | 0.0033752 | 74.003 | 1108 |  | 7392 | 105.93 | 1.1339 | 61.914 | 0.0033752 | 74.003 | 1108 | 1033.997
7393 | 1.1342 | 105.94 | 61.913 | 0.0033761 | 74.013 | 1108 |  | 7393 | 105.94 | 1.1342 | 61.913 | 0.0033761 | 74.013 | 1108 | 1033.987
7394 | 1.1345 | 105.95 | 61.913 | 0.0033771 | 74.023 | 1108 |  | 7394 | 105.95 | 1.1345 | 61.913 | 0.0033771 | 74.023 | 1108 | 1033.977
7395 | 1.1349 | 105.96 | 61.913 | 0.003378 | 74.033 | 1108 |  | 7395 | 105.96 | 1.1349 | 61.913 | 0.003378 | 74.033 | 1108 | 1033.967
7396 | 1.1352 | 105.97 | 61.913 | 0.0033789 | 74.043 | 1108 |  | 7396 | 105.97 | 1.1352 | 61.913 | 0.0033789 | 74.043 | 1108 | 1033.957
7397 | 1.1355 | 105.98 | 61.913 | 0.0033799 | 74.053 | 1108 |  | 7397 | 105.98 | 1.1355 | 61.913 | 0.0033799 | 74.053 | 1108 | 1033.947
7398 | 1.1359 | 105.99 | 61.913 | 0.0033808 | 74.063 | 1108 |  | 7398 | 105.99 | 1.1359 | 61.913 | 0.0033808 | 74.063 | 1108 | 1033.937
7399 | 1.1362 | 106 | 61.913 | 0.0033817 | 74.073 | 1108 |  | 7399 | 106 | 1.1362 | 61.913 | 0.0033817 | 74.073 | 1108 | 1033.927
7400 | 1.1365 | 106.01 | 61.913 | 0.0033827 | 74.083 | 1108 |  | 7400 | 106.01 | 1.1365 | 61.913 | 0.0033827 | 74.083 | 1108 | 1033.917
7401 | 1.1369 | 106.02 | 61.912 | 0.0033836 | 74.093 | 1108 |  | 7401 | 106.02 | 1.1369 | 61.912 | 0.0033836 | 74.093 | 1108 | 1033.907
7402 | 1.1372 | 106.03 | 61.912 | 0.0033845 | 74.103 | 1108 |  | 7402 | 106.03 | 1.1372 | 61.912 | 0.0033845 | 74.103 | 1108 | 1033.897
7403 | 1.1375 | 106.04 | 61.912 | 0.0033855 | 74.113 | 1108 |  | 7403 | 106.04 | 1.1375 | 61.912 | 0.0033855 | 74.113 | 1108 | 1033.887
7404 | 1.1379 | 106.05 | 61.912 | 0.0033864 | 74.123 | 1108 |  | 7404 | 106.05 | 1.1379 | 61.912 | 0.0033864 | 74.123 | 1108 | 1033.877
7405 | 1.1382 | 106.06 | 61.912 | 0.0033874 | 74.133 | 1108 |  | 7405 | 106.06 | 1.1382 | 61.912 | 0.0033874 | 74.133 | 1108 | 1033.867
7406 | 1.1385 | 106.07 | 61.912 | 0.0033883 | 74.142 | 1108 |  | 7406 | 106.07 | 1.1385 | 61.912 | 0.0033883 | 74.142 | 1108 | 1033.858
7407 | 1.1389 | 106.08 | 61.912 | 0.0033892 | 74.152 | 1108 |  | 7407 | 106.08 | 1.1389 | 61.912 | 0.0033892 | 74.152 | 1108 | 1033.848
7408 | 1.1392 | 106.09 | 61.911 | 0.0033902 | 74.162 | 1108 |  | 7408 | 106.09 | 1.1392 | 61.911 | 0.0033902 | 74.162 | 1108 | 1033.838
7409 | 1.1395 | 106.1 | 61.911 | 0.0033911 | 74.172 | 1108 |  | 7409 | 106.1 | 1.1395 | 61.911 | 0.0033911 | 74.172 | 1108 | 1033.828
7410 | 1.1399 | 106.11 | 61.911 | 0.003392 | 74.182 | 1108.1 |  | 7410 | 106.11 | 1.1399 | 61.911 | 0.003392 | 74.182 | 1108.1 | 1033.918
7411 | 1.1402 | 106.12 | 61.911 | 0.003393 | 74.192 | 1108.1 |  | 7411 | 106.12 | 1.1402 | 61.911 | 0.003393 | 74.192 | 1108.1 | 1033.908
7412 | 1.1405 | 106.13 | 61.911 | 0.0033939 | 74.202 | 1108.1 |  | 7412 | 106.13 | 1.1405 | 61.911 | 0.0033939 | 74.202 | 1108.1 | 1033.898
7413 | 1.1409 | 106.14 | 61.911 | 0.0033949 | 74.212 | 1108.1 |  | 7413 | 106.14 | 1.1409 | 61.911 | 0.0033949 | 74.212 | 1108.1 | 1033.888
7414 | 1.1412 | 106.15 | 61.911 | 0.0033958 | 74.222 | 1108.1 |  | 7414 | 106.15 | 1.1412 | 61.911 | 0.0033958 | 74.222 | 1108.1 | 1033.878
7415 | 1.1415 | 106.16 | 61.91 | 0.0033967 | 74.232 | 1108.1 |  | 7415 | 106.16 | 1.1415 | 61.91 | 0.0033967 | 74.232 | 1108.1 | 1033.868
7416 | 1.1419 | 106.17 | 61.91 | 0.0033977 | 74.242 | 1108.1 |  | 7416 | 106.17 | 1.1419 | 61.91 | 0.0033977 | 74.242 | 1108.1 | 1033.858
7417 | 1.1422 | 106.18 | 61.91 | 0.0033986 | 74.252 | 1108.1 |  | 7417 | 106.18 | 1.1422 | 61.91 | 0.0033986 | 74.252 | 1108.1 | 1033.848
7418 | 1.1425 | 106.19 | 61.91 | 0.0033996 | 74.262 | 1108.1 |  | 7418 | 106.19 | 1.1425 | 61.91 | 0.0033996 | 74.262 | 1108.1 | 1033.838
7419 | 1.1429 | 106.2 | 61.91 | 0.0034005 | 74.272 | 1108.1 |  | 7419 | 106.2 | 1.1429 | 61.91 | 0.0034005 | 74.272 | 1108.1 | 1033.828
7420 | 1.1432 | 106.21 | 61.91 | 0.0034014 | 74.282 | 1108.1 |  | 7420 | 106.21 | 1.1432 | 61.91 | 0.0034014 | 74.282 | 1108.1 | 1033.818
7421 | 1.1436 | 106.22 | 61.91 | 0.0034024 | 74.292 | 1108.1 |  | 7421 | 106.22 | 1.1436 | 61.91 | 0.0034024 | 74.292 | 1108.1 | 1033.808
7422 | 1.1439 | 106.23 | 61.91 | 0.0034033 | 74.302 | 1108.1 |  | 7422 | 106.23 | 1.1439 | 61.91 | 0.0034033 | 74.302 | 1108.1 | 1033.798
7423 | 1.1442 | 106.24 | 61.909 | 0.0034043 | 74.312 | 1108.1 |  | 7423 | 106.24 | 1.1442 | 61.909 | 0.0034043 | 74.312 | 1108.1 | 1033.788
7424 | 1.1446 | 106.25 | 61.909 | 0.0034052 | 74.322 | 1108.1 |  | 7424 | 106.25 | 1.1446 | 61.909 | 0.0034052 | 74.322 | 1108.1 | 1033.778
7425 | 1.1449 | 106.26 | 61.909 | 0.0034061 | 74.332 | 1108.1 |  | 7425 | 106.26 | 1.1449 | 61.909 | 0.0034061 | 74.332 | 1108.1 | 1033.768
7426 | 1.1452 | 106.27 | 61.909 | 0.0034071 | 74.342 | 1108.1 |  | 7426 | 106.27 | 1.1452 | 61.909 | 0.0034071 | 74.342 | 1108.1 | 1033.758
7427 | 1.1456 | 106.28 | 61.909 | 0.003408 | 74.352 | 1108.1 |  | 7427 | 106.28 | 1.1456 | 61.909 | 0.003408 | 74.352 | 1108.1 | 1033.748
7428 | 1.1459 | 106.29 | 61.909 | 0.003409 | 74.362 | 1108.1 |  | 7428 | 106.29 | 1.1459 | 61.909 | 0.003409 | 74.362 | 1108.1 | 1033.738
7429 | 1.1462 | 106.3 | 61.909 | 0.0034099 | 74.372 | 1108.1 |  | 7429 | 106.3 | 1.1462 | 61.909 | 0.0034099 | 74.372 | 1108.1 | 1033.728
7430 | 1.1466 | 106.31 | 61.908 | 0.0034108 | 74.382 | 1108.1 |  | 7430 | 106.31 | 1.1466 | 61.908 | 0.0034108 | 74.382 | 1108.1 | 1033.718
7431 | 1.1469 | 106.32 | 61.908 | 0.0034118 | 74.392 | 1108.1 |  | 7431 | 106.32 | 1.1469 | 61.908 | 0.0034118 | 74.392 | 1108.1 | 1033.708
7432 | 1.1473 | 106.33 | 61.908 | 0.0034127 | 74.402 | 1108.1 |  | 7432 | 106.33 | 1.1473 | 61.908 | 0.0034127 | 74.402 | 1108.1 | 1033.698
7433 | 1.1476 | 106.34 | 61.908 | 0.0034137 | 74.412 | 1108.1 |  | 7433 | 106.34 | 1.1476 | 61.908 | 0.0034137 | 74.412 | 1108.1 | 1033.688
7434 | 1.1479 | 106.35 | 61.908 | 0.0034146 | 74.422 | 1108.2 |  | 7434 | 106.35 | 1.1479 | 61.908 | 0.0034146 | 74.422 | 1108.2 | 1033.778
7435 | 1.1483 | 106.36 | 61.908 | 0.0034156 | 74.432 | 1108.2 |  | 7435 | 106.36 | 1.1483 | 61.908 | 0.0034156 | 74.432 | 1108.2 | 1033.768
7436 | 1.1486 | 106.37 | 61.908 | 0.0034165 | 74.442 | 1108.2 |  | 7436 | 106.37 | 1.1486 | 61.908 | 0.0034165 | 74.442 | 1108.2 | 1033.758
7437 | 1.1489 | 106.38 | 61.908 | 0.0034174 | 74.452 | 1108.2 |  | 7437 | 106.38 | 1.1489 | 61.908 | 0.0034174 | 74.452 | 1108.2 | 1033.748
7438 | 1.1493 | 106.39 | 61.907 | 0.0034184 | 74.462 | 1108.2 |  | 7438 | 106.39 | 1.1493 | 61.907 | 0.0034184 | 74.462 | 1108.2 | 1033.738
7439 | 1.1496 | 106.4 | 61.907 | 0.0034193 | 74.472 | 1108.2 |  | 7439 | 106.4 | 1.1496 | 61.907 | 0.0034193 | 74.472 | 1108.2 | 1033.728
7440 | 1.1499 | 106.41 | 61.907 | 0.0034203 | 74.482 | 1108.2 |  | 7440 | 106.41 | 1.1499 | 61.907 | 0.0034203 | 74.482 | 1108.2 | 1033.718
7441 | 1.1503 | 106.42 | 61.907 | 0.0034212 | 74.492 | 1108.2 |  | 7441 | 106.42 | 1.1503 | 61.907 | 0.0034212 | 74.492 | 1108.2 | 1033.708
7442 | 1.1506 | 106.43 | 61.907 | 0.0034222 | 74.502 | 1108.2 |  | 7442 | 106.43 | 1.1506 | 61.907 | 0.0034222 | 74.502 | 1108.2 | 1033.698
7443 | 1.151 | 106.44 | 61.907 | 0.0034231 | 74.512 | 1108.2 |  | 7443 | 106.44 | 1.151 | 61.907 | 0.0034231 | 74.512 | 1108.2 | 1033.688
7444 | 1.1513 | 106.45 | 61.907 | 0.0034241 | 74.522 | 1108.2 |  | 7444 | 106.45 | 1.1513 | 61.907 | 0.0034241 | 74.522 | 1108.2 | 1033.678
7445 | 1.1516 | 106.46 | 61.906 | 0.003425 | 74.532 | 1108.2 |  | 7445 | 106.46 | 1.1516 | 61.906 | 0.003425 | 74.532 | 1108.2 | 1033.668
7446 | 1.152 | 106.47 | 61.906 | 0.003426 | 74.542 | 1108.2 |  | 7446 | 106.47 | 1.152 | 61.906 | 0.003426 | 74.542 | 1108.2 | 1033.658
7447 | 1.1523 | 106.48 | 61.906 | 0.0034269 | 74.552 | 1108.2 |  | 7447 | 106.48 | 1.1523 | 61.906 | 0.0034269 | 74.552 | 1108.2 | 1033.648
7448 | 1.1526 | 106.49 | 61.906 | 0.0034278 | 74.562 | 1108.2 |  | 7448 | 106.49 | 1.1526 | 61.906 | 0.0034278 | 74.562 | 1108.2 | 1033.638
7449 | 1.153 | 106.5 | 61.906 | 0.0034288 | 74.572 | 1108.2 |  | 7449 | 106.5 | 1.153 | 61.906 | 0.0034288 | 74.572 | 1108.2 | 1033.628
7450 | 1.1533 | 106.51 | 61.906 | 0.0034297 | 74.582 | 1108.2 |  | 7450 | 106.51 | 1.1533 | 61.906 | 0.0034297 | 74.582 | 1108.2 | 1033.618
7451 | 1.1537 | 106.52 | 61.906 | 0.0034307 | 74.592 | 1108.2 |  | 7451 | 106.52 | 1.1537 | 61.906 | 0.0034307 | 74.592 | 1108.2 | 1033.608
7452 | 1.154 | 106.53 | 61.905 | 0.0034316 | 74.602 | 1108.2 |  | 7452 | 106.53 | 1.154 | 61.905 | 0.0034316 | 74.602 | 1108.2 | 1033.598
7453 | 1.1543 | 106.54 | 61.905 | 0.0034326 | 74.612 | 1108.2 |  | 7453 | 106.54 | 1.1543 | 61.905 | 0.0034326 | 74.612 | 1108.2 | 1033.588
7454 | 1.1547 | 106.55 | 61.905 | 0.0034335 | 74.622 | 1108.2 |  | 7454 | 106.55 | 1.1547 | 61.905 | 0.0034335 | 74.622 | 1108.2 | 1033.578
7455 | 1.155 | 106.56 | 61.905 | 0.0034345 | 74.632 | 1108.2 |  | 7455 | 106.56 | 1.155 | 61.905 | 0.0034345 | 74.632 | 1108.2 | 1033.568
7456 | 1.1554 | 106.57 | 61.905 | 0.0034354 | 74.642 | 1108.2 |  | 7456 | 106.57 | 1.1554 | 61.905 | 0.0034354 | 74.642 | 1108.2 | 1033.558
7457 | 1.1557 | 106.58 | 61.905 | 0.0034364 | 74.652 | 1108.3 |  | 7457 | 106.58 | 1.1557 | 61.905 | 0.0034364 | 74.652 | 1108.3 | 1033.648
7458 | 1.156 | 106.59 | 61.905 | 0.0034373 | 74.662 | 1108.3 |  | 7458 | 106.59 | 1.156 | 61.905 | 0.0034373 | 74.662 | 1108.3 | 1033.638
7459 | 1.1564 | 106.6 | 61.905 | 0.0034383 | 74.672 | 1108.3 |  | 7459 | 106.6 | 1.1564 | 61.905 | 0.0034383 | 74.672 | 1108.3 | 1033.628
7460 | 1.1567 | 106.61 | 61.904 | 0.0034392 | 74.682 | 1108.3 |  | 7460 | 106.61 | 1.1567 | 61.904 | 0.0034392 | 74.682 | 1108.3 | 1033.618
7461 | 1.1571 | 106.62 | 61.904 | 0.0034402 | 74.692 | 1108.3 |  | 7461 | 106.62 | 1.1571 | 61.904 | 0.0034402 | 74.692 | 1108.3 | 1033.608
7462 | 1.1574 | 106.63 | 61.904 | 0.0034411 | 74.702 | 1108.3 |  | 7462 | 106.63 | 1.1574 | 61.904 | 0.0034411 | 74.702 | 1108.3 | 1033.598
7463 | 1.1577 | 106.64 | 61.904 | 0.0034421 | 74.712 | 1108.3 |  | 7463 | 106.64 | 1.1577 | 61.904 | 0.0034421 | 74.712 | 1108.3 | 1033.588
7464 | 1.1581 | 106.65 | 61.904 | 0.003443 | 74.722 | 1108.3 |  | 7464 | 106.65 | 1.1581 | 61.904 | 0.003443 | 74.722 | 1108.3 | 1033.578
7465 | 1.1584 | 106.66 | 61.904 | 0.003444 | 74.732 | 1108.3 |  | 7465 | 106.66 | 1.1584 | 61.904 | 0.003444 | 74.732 | 1108.3 | 1033.568
7466 | 1.1587 | 106.67 | 61.904 | 0.0034449 | 74.742 | 1108.3 |  | 7466 | 106.67 | 1.1587 | 61.904 | 0.0034449 | 74.742 | 1108.3 | 1033.558
7467 | 1.1591 | 106.68 | 61.903 | 0.0034459 | 74.752 | 1108.3 |  | 7467 | 106.68 | 1.1591 | 61.903 | 0.0034459 | 74.752 | 1108.3 | 1033.548
7468 | 1.1594 | 106.69 | 61.903 | 0.0034468 | 74.762 | 1108.3 |  | 7468 | 106.69 | 1.1594 | 61.903 | 0.0034468 | 74.762 | 1108.3 | 1033.538
7469 | 1.1598 | 106.7 | 61.903 | 0.0034478 | 74.772 | 1108.3 |  | 7469 | 106.7 | 1.1598 | 61.903 | 0.0034478 | 74.772 | 1108.3 | 1033.528
7470 | 1.1601 | 106.71 | 61.903 | 0.0034487 | 74.782 | 1108.3 |  | 7470 | 106.71 | 1.1601 | 61.903 | 0.0034487 | 74.782 | 1108.3 | 1033.518
7471 | 1.1604 | 106.72 | 61.903 | 0.0034497 | 74.792 | 1108.3 |  | 7471 | 106.72 | 1.1604 | 61.903 | 0.0034497 | 74.792 | 1108.3 | 1033.508
7472 | 1.1608 | 106.73 | 61.903 | 0.0034506 | 74.802 | 1108.3 |  | 7472 | 106.73 | 1.1608 | 61.903 | 0.0034506 | 74.802 | 1108.3 | 1033.498
7473 | 1.1611 | 106.74 | 61.903 | 0.0034516 | 74.812 | 1108.3 |  | 7473 | 106.74 | 1.1611 | 61.903 | 0.0034516 | 74.812 | 1108.3 | 1033.488
7474 | 1.1615 | 106.75 | 61.902 | 0.0034525 | 74.822 | 1108.3 |  | 7474 | 106.75 | 1.1615 | 61.902 | 0.0034525 | 74.822 | 1108.3 | 1033.478
7475 | 1.1618 | 106.76 | 61.902 | 0.0034535 | 74.832 | 1108.3 |  | 7475 | 106.76 | 1.1618 | 61.902 | 0.0034535 | 74.832 | 1108.3 | 1033.468
7476 | 1.1621 | 106.77 | 61.902 | 0.0034544 | 74.842 | 1108.3 |  | 7476 | 106.77 | 1.1621 | 61.902 | 0.0034544 | 74.842 | 1108.3 | 1033.458
7477 | 1.1625 | 106.78 | 61.902 | 0.0034554 | 74.852 | 1108.3 |  | 7477 | 106.78 | 1.1625 | 61.902 | 0.0034554 | 74.852 | 1108.3 | 1033.448
7478 | 1.1628 | 106.79 | 61.902 | 0.0034563 | 74.862 | 1108.3 |  | 7478 | 106.79 | 1.1628 | 61.902 | 0.0034563 | 74.862 | 1108.3 | 1033.438
7479 | 1.1632 | 106.8 | 61.902 | 0.0034573 | 74.872 | 1108.3 |  | 7479 | 106.8 | 1.1632 | 61.902 | 0.0034573 | 74.872 | 1108.3 | 1033.428
7480 | 1.1635 | 106.81 | 61.902 | 0.0034582 | 74.882 | 1108.4 |  | 7480 | 106.81 | 1.1635 | 61.902 | 0.0034582 | 74.882 | 1108.4 | 1033.518
7481 | 1.1638 | 106.82 | 61.902 | 0.0034592 | 74.892 | 1108.4 |  | 7481 | 106.82 | 1.1638 | 61.902 | 0.0034592 | 74.892 | 1108.4 | 1033.508
7482 | 1.1642 | 106.83 | 61.901 | 0.0034602 | 74.902 | 1108.4 |  | 7482 | 106.83 | 1.1642 | 61.901 | 0.0034602 | 74.902 | 1108.4 | 1033.498
7483 | 1.1645 | 106.84 | 61.901 | 0.0034611 | 74.912 | 1108.4 |  | 7483 | 106.84 | 1.1645 | 61.901 | 0.0034611 | 74.912 | 1108.4 | 1033.488
7484 | 1.1649 | 106.85 | 61.901 | 0.0034621 | 74.922 | 1108.4 |  | 7484 | 106.85 | 1.1649 | 61.901 | 0.0034621 | 74.922 | 1108.4 | 1033.478
7485 | 1.1652 | 106.86 | 61.901 | 0.003463 | 74.932 | 1108.4 |  | 7485 | 106.86 | 1.1652 | 61.901 | 0.003463 | 74.932 | 1108.4 | 1033.468
7486 | 1.1656 | 106.87 | 61.901 | 0.003464 | 74.942 | 1108.4 |  | 7486 | 106.87 | 1.1656 | 61.901 | 0.003464 | 74.942 | 1108.4 | 1033.458
7487 | 1.1659 | 106.88 | 61.901 | 0.0034649 | 74.952 | 1108.4 |  | 7487 | 106.88 | 1.1659 | 61.901 | 0.0034649 | 74.952 | 1108.4 | 1033.448
7488 | 1.1662 | 106.89 | 61.901 | 0.0034659 | 74.962 | 1108.4 |  | 7488 | 106.89 | 1.1662 | 61.901 | 0.0034659 | 74.962 | 1108.4 | 1033.438
7489 | 1.1666 | 106.9 | 61.9 | 0.0034668 | 74.972 | 1108.4 |  | 7489 | 106.9 | 1.1666 | 61.9 | 0.0034668 | 74.972 | 1108.4 | 1033.428
7490 | 1.1669 | 106.91 | 61.9 | 0.0034678 | 74.982 | 1108.4 |  | 7490 | 106.91 | 1.1669 | 61.9 | 0.0034678 | 74.982 | 1108.4 | 1033.418
7491 | 1.1673 | 106.92 | 61.9 | 0.0034688 | 74.992 | 1108.4 |  | 7491 | 106.92 | 1.1673 | 61.9 | 0.0034688 | 74.992 | 1108.4 | 1033.408
7492 | 1.1676 | 106.93 | 61.9 | 0.0034697 | 75.002 | 1108.4 |  | 7492 | 106.93 | 1.1676 | 61.9 | 0.0034697 | 75.002 | 1108.4 | 1033.398
7493 | 1.1679 | 106.94 | 61.9 | 0.0034707 | 75.012 | 1108.4 |  | 7493 | 106.94 | 1.1679 | 61.9 | 0.0034707 | 75.012 | 1108.4 | 1033.388
7494 | 1.1683 | 106.95 | 61.9 | 0.0034716 | 75.022 | 1108.4 |  | 7494 | 106.95 | 1.1683 | 61.9 | 0.0034716 | 75.022 | 1108.4 | 1033.378
7495 | 1.1686 | 106.96 | 61.9 | 0.0034726 | 75.032 | 1108.4 |  | 7495 | 106.96 | 1.1686 | 61.9 | 0.0034726 | 75.032 | 1108.4 | 1033.368
7496 | 1.169 | 106.97 | 61.899 | 0.0034735 | 75.042 | 1108.4 |  | 7496 | 106.97 | 1.169 | 61.899 | 0.0034735 | 75.042 | 1108.4 | 1033.358
7497 | 1.1693 | 106.98 | 61.899 | 0.0034745 | 75.052 | 1108.4 |  | 7497 | 106.98 | 1.1693 | 61.899 | 0.0034745 | 75.052 | 1108.4 | 1033.348
7498 | 1.1697 | 106.99 | 61.899 | 0.0034755 | 75.062 | 1108.4 |  | 7498 | 106.99 | 1.1697 | 61.899 | 0.0034755 | 75.062 | 1108.4 | 1033.338
7499 | 1.17 | 107 | 61.899 | 0.0034764 | 75.072 | 1108.4 |  | 7499 | 107 | 1.17 | 61.899 | 0.0034764 | 75.072 | 1108.4 | 1033.328
7500 | 1.1703 | 107.01 | 61.899 | 0.0034774 | 75.082 | 1108.4 |  | 7500 | 107.01 | 1.1703 | 61.899 | 0.0034774 | 75.082 | 1108.4 | 1033.318
7501 | 1.1707 | 107.02 | 61.899 | 0.0034783 | 75.092 | 1108.4 |  | 7501 | 107.02 | 1.1707 | 61.899 | 0.0034783 | 75.092 | 1108.4 | 1033.308
7502 | 1.171 | 107.03 | 61.899 | 0.0034793 | 75.102 | 1108.4 |  | 7502 | 107.03 | 1.171 | 61.899 | 0.0034793 | 75.102 | 1108.4 | 1033.298
7503 | 1.1714 | 107.04 | 61.899 | 0.0034802 | 75.112 | 1108.4 |  | 7503 | 107.04 | 1.1714 | 61.899 | 0.0034802 | 75.112 | 1108.4 | 1033.288
7504 | 1.1717 | 107.05 | 61.898 | 0.0034812 | 75.122 | 1108.5 |  | 7504 | 107.05 | 1.1717 | 61.898 | 0.0034812 | 75.122 | 1108.5 | 1033.378
7505 | 1.1721 | 107.06 | 61.898 | 0.0034822 | 75.132 | 1108.5 |  | 7505 | 107.06 | 1.1721 | 61.898 | 0.0034822 | 75.132 | 1108.5 | 1033.368
7506 | 1.1724 | 107.07 | 61.898 | 0.0034831 | 75.142 | 1108.5 |  | 7506 | 107.07 | 1.1724 | 61.898 | 0.0034831 | 75.142 | 1108.5 | 1033.358
7507 | 1.1727 | 107.08 | 61.898 | 0.0034841 | 75.152 | 1108.5 |  | 7507 | 107.08 | 1.1727 | 61.898 | 0.0034841 | 75.152 | 1108.5 | 1033.348
7508 | 1.1731 | 107.09 | 61.898 | 0.003485 | 75.162 | 1108.5 |  | 7508 | 107.09 | 1.1731 | 61.898 | 0.003485 | 75.162 | 1108.5 | 1033.338
7509 | 1.1734 | 107.1 | 61.898 | 0.003486 | 75.172 | 1108.5 |  | 7509 | 107.1 | 1.1734 | 61.898 | 0.003486 | 75.172 | 1108.5 | 1033.328
7510 | 1.1738 | 107.11 | 61.898 | 0.003487 | 75.182 | 1108.5 |  | 7510 | 107.11 | 1.1738 | 61.898 | 0.003487 | 75.182 | 1108.5 | 1033.318
7511 | 1.1741 | 107.12 | 61.897 | 0.0034879 | 75.192 | 1108.5 |  | 7511 | 107.12 | 1.1741 | 61.897 | 0.0034879 | 75.192 | 1108.5 | 1033.308
7512 | 1.1745 | 107.13 | 61.897 | 0.0034889 | 75.202 | 1108.5 |  | 7512 | 107.13 | 1.1745 | 61.897 | 0.0034889 | 75.202 | 1108.5 | 1033.298
7513 | 1.1748 | 107.14 | 61.897 | 0.0034898 | 75.212 | 1108.5 |  | 7513 | 107.14 | 1.1748 | 61.897 | 0.0034898 | 75.212 | 1108.5 | 1033.288
7514 | 1.1751 | 107.15 | 61.897 | 0.0034908 | 75.222 | 1108.5 |  | 7514 | 107.15 | 1.1751 | 61.897 | 0.0034908 | 75.222 | 1108.5 | 1033.278
7515 | 1.1755 | 107.16 | 61.897 | 0.0034918 | 75.231 | 1108.5 |  | 7515 | 107.16 | 1.1755 | 61.897 | 0.0034918 | 75.231 | 1108.5 | 1033.269
7516 | 1.1758 | 107.17 | 61.897 | 0.0034927 | 75.241 | 1108.5 |  | 7516 | 107.17 | 1.1758 | 61.897 | 0.0034927 | 75.241 | 1108.5 | 1033.259
7517 | 1.1762 | 107.18 | 61.897 | 0.0034937 | 75.251 | 1108.5 |  | 7517 | 107.18 | 1.1762 | 61.897 | 0.0034937 | 75.251 | 1108.5 | 1033.249
7518 | 1.1765 | 107.19 | 61.896 | 0.0034946 | 75.261 | 1108.5 |  | 7518 | 107.19 | 1.1765 | 61.896 | 0.0034946 | 75.261 | 1108.5 | 1033.239
7519 | 1.1769 | 107.2 | 61.896 | 0.0034956 | 75.271 | 1108.5 |  | 7519 | 107.2 | 1.1769 | 61.896 | 0.0034956 | 75.271 | 1108.5 | 1033.229
7520 | 1.1772 | 107.21 | 61.896 | 0.0034966 | 75.281 | 1108.5 |  | 7520 | 107.21 | 1.1772 | 61.896 | 0.0034966 | 75.281 | 1108.5 | 1033.219
7521 | 1.1776 | 107.22 | 61.896 | 0.0034975 | 75.291 | 1108.5 |  | 7521 | 107.22 | 1.1776 | 61.896 | 0.0034975 | 75.291 | 1108.5 | 1033.209
7522 | 1.1779 | 107.23 | 61.896 | 0.0034985 | 75.301 | 1108.5 |  | 7522 | 107.23 | 1.1779 | 61.896 | 0.0034985 | 75.301 | 1108.5 | 1033.199
7523 | 1.1782 | 107.24 | 61.896 | 0.0034995 | 75.311 | 1108.5 |  | 7523 | 107.24 | 1.1782 | 61.896 | 0.0034995 | 75.311 | 1108.5 | 1033.189
7524 | 1.1786 | 107.25 | 61.896 | 0.0035004 | 75.321 | 1108.5 |  | 7524 | 107.25 | 1.1786 | 61.896 | 0.0035004 | 75.321 | 1108.5 | 1033.179
7525 | 1.1789 | 107.26 | 61.895 | 0.0035014 | 75.331 | 1108.5 |  | 7525 | 107.26 | 1.1789 | 61.895 | 0.0035014 | 75.331 | 1108.5 | 1033.169
7526 | 1.1793 | 107.27 | 61.895 | 0.0035024 | 75.341 | 1108.5 |  | 7526 | 107.27 | 1.1793 | 61.895 | 0.0035024 | 75.341 | 1108.5 | 1033.159
7527 | 1.1796 | 107.28 | 61.895 | 0.0035033 | 75.351 | 1108.6 |  | 7527 | 107.28 | 1.1796 | 61.895 | 0.0035033 | 75.351 | 1108.6 | 1033.249
7528 | 1.18 | 107.29 | 61.895 | 0.0035043 | 75.361 | 1108.6 |  | 7528 | 107.29 | 1.18 | 61.895 | 0.0035043 | 75.361 | 1108.6 | 1033.239
7529 | 1.1803 | 107.3 | 61.895 | 0.0035052 | 75.371 | 1108.6 |  | 7529 | 107.3 | 1.1803 | 61.895 | 0.0035052 | 75.371 | 1108.6 | 1033.229
7530 | 1.1807 | 107.31 | 61.895 | 0.0035062 | 75.381 | 1108.6 |  | 7530 | 107.31 | 1.1807 | 61.895 | 0.0035062 | 75.381 | 1108.6 | 1033.219
7531 | 1.181 | 107.32 | 61.895 | 0.0035072 | 75.391 | 1108.6 |  | 7531 | 107.32 | 1.181 | 61.895 | 0.0035072 | 75.391 | 1108.6 | 1033.209
7532 | 1.1813 | 107.33 | 61.895 | 0.0035081 | 75.401 | 1108.6 |  | 7532 | 107.33 | 1.1813 | 61.895 | 0.0035081 | 75.401 | 1108.6 | 1033.199
7533 | 1.1817 | 107.34 | 61.894 | 0.0035091 | 75.411 | 1108.6 |  | 7533 | 107.34 | 1.1817 | 61.894 | 0.0035091 | 75.411 | 1108.6 | 1033.189
7534 | 1.182 | 107.35 | 61.894 | 0.0035101 | 75.421 | 1108.6 |  | 7534 | 107.35 | 1.182 | 61.894 | 0.0035101 | 75.421 | 1108.6 | 1033.179
7535 | 1.1824 | 107.36 | 61.894 | 0.003511 | 75.431 | 1108.6 |  | 7535 | 107.36 | 1.1824 | 61.894 | 0.003511 | 75.431 | 1108.6 | 1033.169
7536 | 1.1827 | 107.37 | 61.894 | 0.003512 | 75.441 | 1108.6 |  | 7536 | 107.37 | 1.1827 | 61.894 | 0.003512 | 75.441 | 1108.6 | 1033.159
7537 | 1.1831 | 107.38 | 61.894 | 0.003513 | 75.451 | 1108.6 |  | 7537 | 107.38 | 1.1831 | 61.894 | 0.003513 | 75.451 | 1108.6 | 1033.149
7538 | 1.1834 | 107.39 | 61.894 | 0.0035139 | 75.461 | 1108.6 |  | 7538 | 107.39 | 1.1834 | 61.894 | 0.0035139 | 75.461 | 1108.6 | 1033.139
7539 | 1.1838 | 107.4 | 61.894 | 0.0035149 | 75.471 | 1108.6 |  | 7539 | 107.4 | 1.1838 | 61.894 | 0.0035149 | 75.471 | 1108.6 | 1033.129
7540 | 1.1841 | 107.41 | 61.893 | 0.0035159 | 75.481 | 1108.6 |  | 7540 | 107.41 | 1.1841 | 61.893 | 0.0035159 | 75.481 | 1108.6 | 1033.119
7541 | 1.1845 | 107.42 | 61.893 | 0.0035168 | 75.491 | 1108.6 |  | 7541 | 107.42 | 1.1845 | 61.893 | 0.0035168 | 75.491 | 1108.6 | 1033.109
7542 | 1.1848 | 107.43 | 61.893 | 0.0035178 | 75.501 | 1108.6 |  | 7542 | 107.43 | 1.1848 | 61.893 | 0.0035178 | 75.501 | 1108.6 | 1033.099
7543 | 1.1851 | 107.44 | 61.893 | 0.0035188 | 75.511 | 1108.6 |  | 7543 | 107.44 | 1.1851 | 61.893 | 0.0035188 | 75.511 | 1108.6 | 1033.089
7544 | 1.1855 | 107.45 | 61.893 | 0.0035197 | 75.521 | 1108.6 |  | 7544 | 107.45 | 1.1855 | 61.893 | 0.0035197 | 75.521 | 1108.6 | 1033.079
7545 | 1.1858 | 107.46 | 61.893 | 0.0035207 | 75.531 | 1108.6 |  | 7545 | 107.46 | 1.1858 | 61.893 | 0.0035207 | 75.531 | 1108.6 | 1033.069
7546 | 1.1862 | 107.47 | 61.893 | 0.0035217 | 75.541 | 1108.6 |  | 7546 | 107.47 | 1.1862 | 61.893 | 0.0035217 | 75.541 | 1108.6 | 1033.059
7547 | 1.1865 | 107.48 | 61.892 | 0.0035226 | 75.551 | 1108.6 |  | 7547 | 107.48 | 1.1865 | 61.892 | 0.0035226 | 75.551 | 1108.6 | 1033.049
7548 | 1.1869 | 107.49 | 61.892 | 0.0035236 | 75.561 | 1108.6 |  | 7548 | 107.49 | 1.1869 | 61.892 | 0.0035236 | 75.561 | 1108.6 | 1033.039
7549 | 1.1872 | 107.5 | 61.892 | 0.0035246 | 75.571 | 1108.6 |  | 7549 | 107.5 | 1.1872 | 61.892 | 0.0035246 | 75.571 | 1108.6 | 1033.029
7550 | 1.1876 | 107.51 | 61.892 | 0.0035256 | 75.581 | 1108.6 |  | 7550 | 107.51 | 1.1876 | 61.892 | 0.0035256 | 75.581 | 1108.6 | 1033.019
7551 | 1.1879 | 107.52 | 61.892 | 0.0035265 | 75.591 | 1108.7 |  | 7551 | 107.52 | 1.1879 | 61.892 | 0.0035265 | 75.591 | 1108.7 | 1033.109
7552 | 1.1883 | 107.53 | 61.892 | 0.0035275 | 75.601 | 1108.7 |  | 7552 | 107.53 | 1.1883 | 61.892 | 0.0035275 | 75.601 | 1108.7 | 1033.099
7553 | 1.1886 | 107.54 | 61.892 | 0.0035285 | 75.611 | 1108.7 |  | 7553 | 107.54 | 1.1886 | 61.892 | 0.0035285 | 75.611 | 1108.7 | 1033.089
7554 | 1.189 | 107.55 | 61.892 | 0.0035294 | 75.621 | 1108.7 |  | 7554 | 107.55 | 1.189 | 61.892 | 0.0035294 | 75.621 | 1108.7 | 1033.079
7555 | 1.1893 | 107.56 | 61.891 | 0.0035304 | 75.631 | 1108.7 |  | 7555 | 107.56 | 1.1893 | 61.891 | 0.0035304 | 75.631 | 1108.7 | 1033.069
7556 | 1.1897 | 107.57 | 61.891 | 0.0035314 | 75.641 | 1108.7 |  | 7556 | 107.57 | 1.1897 | 61.891 | 0.0035314 | 75.641 | 1108.7 | 1033.059
7557 | 1.19 | 107.58 | 61.891 | 0.0035323 | 75.651 | 1108.7 |  | 7557 | 107.58 | 1.19 | 61.891 | 0.0035323 | 75.651 | 1108.7 | 1033.049
7558 | 1.1903 | 107.59 | 61.891 | 0.0035333 | 75.661 | 1108.7 |  | 7558 | 107.59 | 1.1903 | 61.891 | 0.0035333 | 75.661 | 1108.7 | 1033.039
7559 | 1.1907 | 107.6 | 61.891 | 0.0035343 | 75.671 | 1108.7 |  | 7559 | 107.6 | 1.1907 | 61.891 | 0.0035343 | 75.671 | 1108.7 | 1033.029
7560 | 1.191 | 107.61 | 61.891 | 0.0035353 | 75.681 | 1108.7 |  | 7560 | 107.61 | 1.191 | 61.891 | 0.0035353 | 75.681 | 1108.7 | 1033.019
7561 | 1.1914 | 107.62 | 61.891 | 0.0035362 | 75.691 | 1108.7 |  | 7561 | 107.62 | 1.1914 | 61.891 | 0.0035362 | 75.691 | 1108.7 | 1033.009
7562 | 1.1917 | 107.63 | 61.89 | 0.0035372 | 75.701 | 1108.7 |  | 7562 | 107.63 | 1.1917 | 61.89 | 0.0035372 | 75.701 | 1108.7 | 1032.999
7563 | 1.1921 | 107.64 | 61.89 | 0.0035382 | 75.711 | 1108.7 |  | 7563 | 107.64 | 1.1921 | 61.89 | 0.0035382 | 75.711 | 1108.7 | 1032.989
7564 | 1.1924 | 107.65 | 61.89 | 0.0035391 | 75.721 | 1108.7 |  | 7564 | 107.65 | 1.1924 | 61.89 | 0.0035391 | 75.721 | 1108.7 | 1032.979
7565 | 1.1928 | 107.66 | 61.89 | 0.0035401 | 75.731 | 1108.7 |  | 7565 | 107.66 | 1.1928 | 61.89 | 0.0035401 | 75.731 | 1108.7 | 1032.969
7566 | 1.1931 | 107.67 | 61.89 | 0.0035411 | 75.741 | 1108.7 |  | 7566 | 107.67 | 1.1931 | 61.89 | 0.0035411 | 75.741 | 1108.7 | 1032.959
7567 | 1.1935 | 107.68 | 61.89 | 0.0035421 | 75.751 | 1108.7 |  | 7567 | 107.68 | 1.1935 | 61.89 | 0.0035421 | 75.751 | 1108.7 | 1032.949
7568 | 1.1938 | 107.69 | 61.89 | 0.003543 | 75.761 | 1108.7 |  | 7568 | 107.69 | 1.1938 | 61.89 | 0.003543 | 75.761 | 1108.7 | 1032.939
7569 | 1.1942 | 107.7 | 61.889 | 0.003544 | 75.771 | 1108.7 |  | 7569 | 107.7 | 1.1942 | 61.889 | 0.003544 | 75.771 | 1108.7 | 1032.929
7570 | 1.1945 | 107.71 | 61.889 | 0.003545 | 75.781 | 1108.7 |  | 7570 | 107.71 | 1.1945 | 61.889 | 0.003545 | 75.781 | 1108.7 | 1032.919
7571 | 1.1949 | 107.72 | 61.889 | 0.003546 | 75.791 | 1108.7 |  | 7571 | 107.72 | 1.1949 | 61.889 | 0.003546 | 75.791 | 1108.7 | 1032.909
7572 | 1.1952 | 107.73 | 61.889 | 0.0035469 | 75.801 | 1108.7 |  | 7572 | 107.73 | 1.1952 | 61.889 | 0.0035469 | 75.801 | 1108.7 | 1032.899
7573 | 1.1956 | 107.74 | 61.889 | 0.0035479 | 75.811 | 1108.7 |  | 7573 | 107.74 | 1.1956 | 61.889 | 0.0035479 | 75.811 | 1108.7 | 1032.889
7574 | 1.1959 | 107.75 | 61.889 | 0.0035489 | 75.821 | 1108.8 |  | 7574 | 107.75 | 1.1959 | 61.889 | 0.0035489 | 75.821 | 1108.8 | 1032.979
7575 | 1.1963 | 107.76 | 61.889 | 0.0035499 | 75.831 | 1108.8 |  | 7575 | 107.76 | 1.1963 | 61.889 | 0.0035499 | 75.831 | 1108.8 | 1032.969
7576 | 1.1966 | 107.77 | 61.888 | 0.0035508 | 75.841 | 1108.8 |  | 7576 | 107.77 | 1.1966 | 61.888 | 0.0035508 | 75.841 | 1108.8 | 1032.959
7577 | 1.197 | 107.78 | 61.888 | 0.0035518 | 75.851 | 1108.8 |  | 7577 | 107.78 | 1.197 | 61.888 | 0.0035518 | 75.851 | 1108.8 | 1032.949
7578 | 1.1973 | 107.79 | 61.888 | 0.0035528 | 75.861 | 1108.8 |  | 7578 | 107.79 | 1.1973 | 61.888 | 0.0035528 | 75.861 | 1108.8 | 1032.939
7579 | 1.1977 | 107.8 | 61.888 | 0.0035538 | 75.871 | 1108.8 |  | 7579 | 107.8 | 1.1977 | 61.888 | 0.0035538 | 75.871 | 1108.8 | 1032.929
7580 | 1.198 | 107.81 | 61.888 | 0.0035547 | 75.881 | 1108.8 |  | 7580 | 107.81 | 1.198 | 61.888 | 0.0035547 | 75.881 | 1108.8 | 1032.919
7581 | 1.1984 | 107.82 | 61.888 | 0.0035557 | 75.891 | 1108.8 |  | 7581 | 107.82 | 1.1984 | 61.888 | 0.0035557 | 75.891 | 1108.8 | 1032.909
7582 | 1.1987 | 107.83 | 61.888 | 0.0035567 | 75.901 | 1108.8 |  | 7582 | 107.83 | 1.1987 | 61.888 | 0.0035567 | 75.901 | 1108.8 | 1032.899
7583 | 1.1991 | 107.84 | 61.888 | 0.0035577 | 75.911 | 1108.8 |  | 7583 | 107.84 | 1.1991 | 61.888 | 0.0035577 | 75.911 | 1108.8 | 1032.889
7584 | 1.1994 | 107.85 | 61.887 | 0.0035586 | 75.921 | 1108.8 |  | 7584 | 107.85 | 1.1994 | 61.887 | 0.0035586 | 75.921 | 1108.8 | 1032.879
7585 | 1.1998 | 107.86 | 61.887 | 0.0035596 | 75.931 | 1108.8 |  | 7585 | 107.86 | 1.1998 | 61.887 | 0.0035596 | 75.931 | 1108.8 | 1032.869
7586 | 1.2001 | 107.87 | 61.887 | 0.0035606 | 75.941 | 1108.8 |  | 7586 | 107.87 | 1.2001 | 61.887 | 0.0035606 | 75.941 | 1108.8 | 1032.859
7587 | 1.2005 | 107.88 | 61.887 | 0.0035616 | 75.951 | 1108.8 |  | 7587 | 107.88 | 1.2005 | 61.887 | 0.0035616 | 75.951 | 1108.8 | 1032.849
7588 | 1.2008 | 107.89 | 61.887 | 0.0035626 | 75.961 | 1108.8 |  | 7588 | 107.89 | 1.2008 | 61.887 | 0.0035626 | 75.961 | 1108.8 | 1032.839
7589 | 1.2012 | 107.9 | 61.887 | 0.0035635 | 75.971 | 1108.8 |  | 7589 | 107.9 | 1.2012 | 61.887 | 0.0035635 | 75.971 | 1108.8 | 1032.829
7590 | 1.2015 | 107.91 | 61.887 | 0.0035645 | 75.981 | 1108.8 |  | 7590 | 107.91 | 1.2015 | 61.887 | 0.0035645 | 75.981 | 1108.8 | 1032.819
7591 | 1.2019 | 107.92 | 61.886 | 0.0035655 | 75.991 | 1108.8 |  | 7591 | 107.92 | 1.2019 | 61.886 | 0.0035655 | 75.991 | 1108.8 | 1032.809
7592 | 1.2022 | 107.93 | 61.886 | 0.0035665 | 76.001 | 1108.8 |  | 7592 | 107.93 | 1.2022 | 61.886 | 0.0035665 | 76.001 | 1108.8 | 1032.799
7593 | 1.2026 | 107.94 | 61.886 | 0.0035674 | 76.011 | 1108.8 |  | 7593 | 107.94 | 1.2026 | 61.886 | 0.0035674 | 76.011 | 1108.8 | 1032.789
7594 | 1.2029 | 107.95 | 61.886 | 0.0035684 | 76.021 | 1108.8 |  | 7594 | 107.95 | 1.2029 | 61.886 | 0.0035684 | 76.021 | 1108.8 | 1032.779
7595 | 1.2033 | 107.96 | 61.886 | 0.0035694 | 76.031 | 1108.8 |  | 7595 | 107.96 | 1.2033 | 61.886 | 0.0035694 | 76.031 | 1108.8 | 1032.769
7596 | 1.2036 | 107.97 | 61.886 | 0.0035704 | 76.041 | 1108.8 |  | 7596 | 107.97 | 1.2036 | 61.886 | 0.0035704 | 76.041 | 1108.8 | 1032.759
7597 | 1.204 | 107.98 | 61.886 | 0.0035714 | 76.051 | 1108.8 |  | 7597 | 107.98 | 1.204 | 61.886 | 0.0035714 | 76.051 | 1108.8 | 1032.749
7598 | 1.2043 | 107.99 | 61.885 | 0.0035723 | 76.061 | 1108.9 |  | 7598 | 107.99 | 1.2043 | 61.885 | 0.0035723 | 76.061 | 1108.9 | 1032.839
7599 | 1.2047 | 108 | 61.885 | 0.0035733 | 76.071 | 1108.9 |  | 7599 | 108 | 1.2047 | 61.885 | 0.0035733 | 76.071 | 1108.9 | 1032.829
7600 | 1.205 | 108.01 | 61.885 | 0.0035743 | 76.081 | 1108.9 |  | 7600 | 108.01 | 1.205 | 61.885 | 0.0035743 | 76.081 | 1108.9 | 1032.819
7601 | 1.2054 | 108.02 | 61.885 | 0.0035753 | 76.091 | 1108.9 |  | 7601 | 108.02 | 1.2054 | 61.885 | 0.0035753 | 76.091 | 1108.9 | 1032.809
7602 | 1.2057 | 108.03 | 61.885 | 0.0035763 | 76.101 | 1108.9 |  | 7602 | 108.03 | 1.2057 | 61.885 | 0.0035763 | 76.101 | 1108.9 | 1032.799
7603 | 1.2061 | 108.04 | 61.885 | 0.0035772 | 76.111 | 1108.9 |  | 7603 | 108.04 | 1.2061 | 61.885 | 0.0035772 | 76.111 | 1108.9 | 1032.789
7604 | 1.2064 | 108.05 | 61.885 | 0.0035782 | 76.121 | 1108.9 |  | 7604 | 108.05 | 1.2064 | 61.885 | 0.0035782 | 76.121 | 1108.9 | 1032.779
7605 | 1.2068 | 108.06 | 61.884 | 0.0035792 | 76.131 | 1108.9 |  | 7605 | 108.06 | 1.2068 | 61.884 | 0.0035792 | 76.131 | 1108.9 | 1032.769
7606 | 1.2071 | 108.07 | 61.884 | 0.0035802 | 76.141 | 1108.9 |  | 7606 | 108.07 | 1.2071 | 61.884 | 0.0035802 | 76.141 | 1108.9 | 1032.759
7607 | 1.2075 | 108.08 | 61.884 | 0.0035812 | 76.151 | 1108.9 |  | 7607 | 108.08 | 1.2075 | 61.884 | 0.0035812 | 76.151 | 1108.9 | 1032.749
7608 | 1.2078 | 108.09 | 61.884 | 0.0035822 | 76.161 | 1108.9 |  | 7608 | 108.09 | 1.2078 | 61.884 | 0.0035822 | 76.161 | 1108.9 | 1032.739
7609 | 1.2082 | 108.1 | 61.884 | 0.0035831 | 76.171 | 1108.9 |  | 7609 | 108.1 | 1.2082 | 61.884 | 0.0035831 | 76.171 | 1108.9 | 1032.729
7610 | 1.2085 | 108.11 | 61.884 | 0.0035841 | 76.181 | 1108.9 |  | 7610 | 108.11 | 1.2085 | 61.884 | 0.0035841 | 76.181 | 1108.9 | 1032.719
7611 | 1.2089 | 108.12 | 61.884 | 0.0035851 | 76.191 | 1108.9 |  | 7611 | 108.12 | 1.2089 | 61.884 | 0.0035851 | 76.191 | 1108.9 | 1032.709
7612 | 1.2092 | 108.13 | 61.884 | 0.0035861 | 76.201 | 1108.9 |  | 7612 | 108.13 | 1.2092 | 61.884 | 0.0035861 | 76.201 | 1108.9 | 1032.699
7613 | 1.2096 | 108.14 | 61.883 | 0.0035871 | 76.211 | 1108.9 |  | 7613 | 108.14 | 1.2096 | 61.883 | 0.0035871 | 76.211 | 1108.9 | 1032.689
7614 | 1.2099 | 108.15 | 61.883 | 0.0035881 | 76.221 | 1108.9 |  | 7614 | 108.15 | 1.2099 | 61.883 | 0.0035881 | 76.221 | 1108.9 | 1032.679
7615 | 1.2103 | 108.16 | 61.883 | 0.003589 | 76.231 | 1108.9 |  | 7615 | 108.16 | 1.2103 | 61.883 | 0.003589 | 76.231 | 1108.9 | 1032.669
7616 | 1.2107 | 108.17 | 61.883 | 0.00359 | 76.241 | 1108.9 |  | 7616 | 108.17 | 1.2107 | 61.883 | 0.00359 | 76.241 | 1108.9 | 1032.659
7617 | 1.211 | 108.18 | 61.883 | 0.003591 | 76.251 | 1108.9 |  | 7617 | 108.18 | 1.211 | 61.883 | 0.003591 | 76.251 | 1108.9 | 1032.649
7618 | 1.2114 | 108.19 | 61.883 | 0.003592 | 76.261 | 1108.9 |  | 7618 | 108.19 | 1.2114 | 61.883 | 0.003592 | 76.261 | 1108.9 | 1032.639
7619 | 1.2117 | 108.2 | 61.883 | 0.003593 | 76.271 | 1108.9 |  | 7619 | 108.2 | 1.2117 | 61.883 | 0.003593 | 76.271 | 1108.9 | 1032.629
7620 | 1.2121 | 108.21 | 61.882 | 0.003594 | 76.281 | 1108.9 |  | 7620 | 108.21 | 1.2121 | 61.882 | 0.003594 | 76.281 | 1108.9 | 1032.619
7621 | 1.2124 | 108.22 | 61.882 | 0.003595 | 76.291 | 1109 |  | 7621 | 108.22 | 1.2124 | 61.882 | 0.003595 | 76.291 | 1109 | 1032.709
7622 | 1.2128 | 108.23 | 61.882 | 0.0035959 | 76.301 | 1109 |  | 7622 | 108.23 | 1.2128 | 61.882 | 0.0035959 | 76.301 | 1109 | 1032.699
7623 | 1.2131 | 108.24 | 61.882 | 0.0035969 | 76.311 | 1109 |  | 7623 | 108.24 | 1.2131 | 61.882 | 0.0035969 | 76.311 | 1109 | 1032.689
7624 | 1.2135 | 108.25 | 61.882 | 0.0035979 | 76.321 | 1109 |  | 7624 | 108.25 | 1.2135 | 61.882 | 0.0035979 | 76.321 | 1109 | 1032.679
7625 | 1.2138 | 108.26 | 61.882 | 0.0035989 | 76.331 | 1109 |  | 7625 | 108.26 | 1.2138 | 61.882 | 0.0035989 | 76.331 | 1109 | 1032.669
7626 | 1.2142 | 108.27 | 61.882 | 0.0035999 | 76.341 | 1109 |  | 7626 | 108.27 | 1.2142 | 61.882 | 0.0035999 | 76.341 | 1109 | 1032.659
7627 | 1.2145 | 108.28 | 61.881 | 0.0036009 | 76.35 | 1109 |  | 7627 | 108.28 | 1.2145 | 61.881 | 0.0036009 | 76.35 | 1109 | 1032.65
7628 | 1.2149 | 108.29 | 61.881 | 0.0036019 | 76.36 | 1109 |  | 7628 | 108.29 | 1.2149 | 61.881 | 0.0036019 | 76.36 | 1109 | 1032.64
7629 | 1.2152 | 108.3 | 61.881 | 0.0036028 | 76.37 | 1109 |  | 7629 | 108.3 | 1.2152 | 61.881 | 0.0036028 | 76.37 | 1109 | 1032.63
7630 | 1.2156 | 108.31 | 61.881 | 0.0036038 | 76.38 | 1109 |  | 7630 | 108.31 | 1.2156 | 61.881 | 0.0036038 | 76.38 | 1109 | 1032.62
7631 | 1.216 | 108.32 | 61.881 | 0.0036048 | 76.39 | 1109 |  | 7631 | 108.32 | 1.216 | 61.881 | 0.0036048 | 76.39 | 1109 | 1032.61
7632 | 1.2163 | 108.33 | 61.881 | 0.0036058 | 76.4 | 1109 |  | 7632 | 108.33 | 1.2163 | 61.881 | 0.0036058 | 76.4 | 1109 | 1032.6
7633 | 1.2167 | 108.34 | 61.881 | 0.0036068 | 76.41 | 1109 |  | 7633 | 108.34 | 1.2167 | 61.881 | 0.0036068 | 76.41 | 1109 | 1032.59
7634 | 1.217 | 108.35 | 61.88 | 0.0036078 | 76.42 | 1109 |  | 7634 | 108.35 | 1.217 | 61.88 | 0.0036078 | 76.42 | 1109 | 1032.58
7635 | 1.2174 | 108.36 | 61.88 | 0.0036088 | 76.43 | 1109 |  | 7635 | 108.36 | 1.2174 | 61.88 | 0.0036088 | 76.43 | 1109 | 1032.57
7636 | 1.2177 | 108.37 | 61.88 | 0.0036098 | 76.44 | 1109 |  | 7636 | 108.37 | 1.2177 | 61.88 | 0.0036098 | 76.44 | 1109 | 1032.56
7637 | 1.2181 | 108.38 | 61.88 | 0.0036108 | 76.45 | 1109 |  | 7637 | 108.38 | 1.2181 | 61.88 | 0.0036108 | 76.45 | 1109 | 1032.55
7638 | 1.2184 | 108.39 | 61.88 | 0.0036117 | 76.46 | 1109 |  | 7638 | 108.39 | 1.2184 | 61.88 | 0.0036117 | 76.46 | 1109 | 1032.54
7639 | 1.2188 | 108.4 | 61.88 | 0.0036127 | 76.47 | 1109 |  | 7639 | 108.4 | 1.2188 | 61.88 | 0.0036127 | 76.47 | 1109 | 1032.53
7640 | 1.2191 | 108.41 | 61.88 | 0.0036137 | 76.48 | 1109 |  | 7640 | 108.41 | 1.2191 | 61.88 | 0.0036137 | 76.48 | 1109 | 1032.52
7641 | 1.2195 | 108.42 | 61.879 | 0.0036147 | 76.49 | 1109 |  | 7641 | 108.42 | 1.2195 | 61.879 | 0.0036147 | 76.49 | 1109 | 1032.51
7642 | 1.2198 | 108.43 | 61.879 | 0.0036157 | 76.5 | 1109 |  | 7642 | 108.43 | 1.2198 | 61.879 | 0.0036157 | 76.5 | 1109 | 1032.5
7643 | 1.2202 | 108.44 | 61.879 | 0.0036167 | 76.51 | 1109 |  | 7643 | 108.44 | 1.2202 | 61.879 | 0.0036167 | 76.51 | 1109 | 1032.49
7644 | 1.2206 | 108.45 | 61.879 | 0.0036177 | 76.52 | 1109 |  | 7644 | 108.45 | 1.2206 | 61.879 | 0.0036177 | 76.52 | 1109 | 1032.48
7645 | 1.2209 | 108.46 | 61.879 | 0.0036187 | 76.53 | 1109.1 |  | 7645 | 108.46 | 1.2209 | 61.879 | 0.0036187 | 76.53 | 1109.1 | 1032.57
7646 | 1.2213 | 108.47 | 61.879 | 0.0036197 | 76.54 | 1109.1 |  | 7646 | 108.47 | 1.2213 | 61.879 | 0.0036197 | 76.54 | 1109.1 | 1032.56
7647 | 1.2216 | 108.48 | 61.879 | 0.0036207 | 76.55 | 1109.1 |  | 7647 | 108.48 | 1.2216 | 61.879 | 0.0036207 | 76.55 | 1109.1 | 1032.55
7648 | 1.222 | 108.49 | 61.879 | 0.0036216 | 76.56 | 1109.1 |  | 7648 | 108.49 | 1.222 | 61.879 | 0.0036216 | 76.56 | 1109.1 | 1032.54
7649 | 1.2223 | 108.5 | 61.878 | 0.0036226 | 76.57 | 1109.1 |  | 7649 | 108.5 | 1.2223 | 61.878 | 0.0036226 | 76.57 | 1109.1 | 1032.53
7650 | 1.2227 | 108.51 | 61.878 | 0.0036236 | 76.58 | 1109.1 |  | 7650 | 108.51 | 1.2227 | 61.878 | 0.0036236 | 76.58 | 1109.1 | 1032.52
7651 | 1.223 | 108.52 | 61.878 | 0.0036246 | 76.59 | 1109.1 |  | 7651 | 108.52 | 1.223 | 61.878 | 0.0036246 | 76.59 | 1109.1 | 1032.51
7652 | 1.2234 | 108.53 | 61.878 | 0.0036256 | 76.6 | 1109.1 |  | 7652 | 108.53 | 1.2234 | 61.878 | 0.0036256 | 76.6 | 1109.1 | 1032.5
7653 | 1.2238 | 108.54 | 61.878 | 0.0036266 | 76.61 | 1109.1 |  | 7653 | 108.54 | 1.2238 | 61.878 | 0.0036266 | 76.61 | 1109.1 | 1032.49
7654 | 1.2241 | 108.55 | 61.878 | 0.0036276 | 76.62 | 1109.1 |  | 7654 | 108.55 | 1.2241 | 61.878 | 0.0036276 | 76.62 | 1109.1 | 1032.48
7655 | 1.2245 | 108.56 | 61.878 | 0.0036286 | 76.63 | 1109.1 |  | 7655 | 108.56 | 1.2245 | 61.878 | 0.0036286 | 76.63 | 1109.1 | 1032.47
7656 | 1.2248 | 108.57 | 61.877 | 0.0036296 | 76.64 | 1109.1 |  | 7656 | 108.57 | 1.2248 | 61.877 | 0.0036296 | 76.64 | 1109.1 | 1032.46
7657 | 1.2252 | 108.58 | 61.877 | 0.0036306 | 76.65 | 1109.1 |  | 7657 | 108.58 | 1.2252 | 61.877 | 0.0036306 | 76.65 | 1109.1 | 1032.45
7658 | 1.2255 | 108.59 | 61.877 | 0.0036316 | 76.66 | 1109.1 |  | 7658 | 108.59 | 1.2255 | 61.877 | 0.0036316 | 76.66 | 1109.1 | 1032.44
7659 | 1.2259 | 108.6 | 61.877 | 0.0036326 | 76.67 | 1109.1 |  | 7659 | 108.6 | 1.2259 | 61.877 | 0.0036326 | 76.67 | 1109.1 | 1032.43
7660 | 1.2263 | 108.61 | 61.877 | 0.0036336 | 76.68 | 1109.1 |  | 7660 | 108.61 | 1.2263 | 61.877 | 0.0036336 | 76.68 | 1109.1 | 1032.42
7661 | 1.2266 | 108.62 | 61.877 | 0.0036346 | 76.69 | 1109.1 |  | 7661 | 108.62 | 1.2266 | 61.877 | 0.0036346 | 76.69 | 1109.1 | 1032.41
7662 | 1.227 | 108.63 | 61.877 | 0.0036356 | 76.7 | 1109.1 |  | 7662 | 108.63 | 1.227 | 61.877 | 0.0036356 | 76.7 | 1109.1 | 1032.4
7663 | 1.2273 | 108.64 | 61.876 | 0.0036366 | 76.71 | 1109.1 |  | 7663 | 108.64 | 1.2273 | 61.876 | 0.0036366 | 76.71 | 1109.1 | 1032.39
7664 | 1.2277 | 108.65 | 61.876 | 0.0036375 | 76.72 | 1109.1 |  | 7664 | 108.65 | 1.2277 | 61.876 | 0.0036375 | 76.72 | 1109.1 | 1032.38
7665 | 1.228 | 108.66 | 61.876 | 0.0036385 | 76.73 | 1109.1 |  | 7665 | 108.66 | 1.228 | 61.876 | 0.0036385 | 76.73 | 1109.1 | 1032.37
7666 | 1.2284 | 108.67 | 61.876 | 0.0036395 | 76.74 | 1109.1 |  | 7666 | 108.67 | 1.2284 | 61.876 | 0.0036395 | 76.74 | 1109.1 | 1032.36
7667 | 1.2288 | 108.68 | 61.876 | 0.0036405 | 76.75 | 1109.1 |  | 7667 | 108.68 | 1.2288 | 61.876 | 0.0036405 | 76.75 | 1109.1 | 1032.35
7668 | 1.2291 | 108.69 | 61.876 | 0.0036415 | 76.76 | 1109.2 |  | 7668 | 108.69 | 1.2291 | 61.876 | 0.0036415 | 76.76 | 1109.2 | 1032.44
7669 | 1.2295 | 108.7 | 61.876 | 0.0036425 | 76.77 | 1109.2 |  | 7669 | 108.7 | 1.2295 | 61.876 | 0.0036425 | 76.77 | 1109.2 | 1032.43
7670 | 1.2298 | 108.71 | 61.875 | 0.0036435 | 76.78 | 1109.2 |  | 7670 | 108.71 | 1.2298 | 61.875 | 0.0036435 | 76.78 | 1109.2 | 1032.42
7671 | 1.2302 | 108.72 | 61.875 | 0.0036445 | 76.79 | 1109.2 |  | 7671 | 108.72 | 1.2302 | 61.875 | 0.0036445 | 76.79 | 1109.2 | 1032.41
7672 | 1.2305 | 108.73 | 61.875 | 0.0036455 | 76.8 | 1109.2 |  | 7672 | 108.73 | 1.2305 | 61.875 | 0.0036455 | 76.8 | 1109.2 | 1032.4
7673 | 1.2309 | 108.74 | 61.875 | 0.0036465 | 76.81 | 1109.2 |  | 7673 | 108.74 | 1.2309 | 61.875 | 0.0036465 | 76.81 | 1109.2 | 1032.39
7674 | 1.2313 | 108.75 | 61.875 | 0.0036475 | 76.82 | 1109.2 |  | 7674 | 108.75 | 1.2313 | 61.875 | 0.0036475 | 76.82 | 1109.2 | 1032.38
7675 | 1.2316 | 108.76 | 61.875 | 0.0036485 | 76.83 | 1109.2 |  | 7675 | 108.76 | 1.2316 | 61.875 | 0.0036485 | 76.83 | 1109.2 | 1032.37
7676 | 1.232 | 108.77 | 61.875 | 0.0036495 | 76.84 | 1109.2 |  | 7676 | 108.77 | 1.232 | 61.875 | 0.0036495 | 76.84 | 1109.2 | 1032.36
7677 | 1.2323 | 108.78 | 61.874 | 0.0036505 | 76.85 | 1109.2 |  | 7677 | 108.78 | 1.2323 | 61.874 | 0.0036505 | 76.85 | 1109.2 | 1032.35
7678 | 1.2327 | 108.79 | 61.874 | 0.0036515 | 76.86 | 1109.2 |  | 7678 | 108.79 | 1.2327 | 61.874 | 0.0036515 | 76.86 | 1109.2 | 1032.34
7679 | 1.233 | 108.8 | 61.874 | 0.0036525 | 76.87 | 1109.2 |  | 7679 | 108.8 | 1.233 | 61.874 | 0.0036525 | 76.87 | 1109.2 | 1032.33
7680 | 1.2334 | 108.81 | 61.874 | 0.0036535 | 76.88 | 1109.2 |  | 7680 | 108.81 | 1.2334 | 61.874 | 0.0036535 | 76.88 | 1109.2 | 1032.32
7681 | 1.2338 | 108.82 | 61.874 | 0.0036545 | 76.89 | 1109.2 |  | 7681 | 108.82 | 1.2338 | 61.874 | 0.0036545 | 76.89 | 1109.2 | 1032.31
7682 | 1.2341 | 108.83 | 61.874 | 0.0036555 | 76.9 | 1109.2 |  | 7682 | 108.83 | 1.2341 | 61.874 | 0.0036555 | 76.9 | 1109.2 | 1032.3
7683 | 1.2345 | 108.84 | 61.874 | 0.0036565 | 76.91 | 1109.2 |  | 7683 | 108.84 | 1.2345 | 61.874 | 0.0036565 | 76.91 | 1109.2 | 1032.29
7684 | 1.2348 | 108.85 | 61.874 | 0.0036575 | 76.92 | 1109.2 |  | 7684 | 108.85 | 1.2348 | 61.874 | 0.0036575 | 76.92 | 1109.2 | 1032.28
7685 | 1.2352 | 108.86 | 61.873 | 0.0036585 | 76.93 | 1109.2 |  | 7685 | 108.86 | 1.2352 | 61.873 | 0.0036585 | 76.93 | 1109.2 | 1032.27
7686 | 1.2356 | 108.87 | 61.873 | 0.0036595 | 76.94 | 1109.2 |  | 7686 | 108.87 | 1.2356 | 61.873 | 0.0036595 | 76.94 | 1109.2 | 1032.26
7687 | 1.2359 | 108.88 | 61.873 | 0.0036605 | 76.95 | 1109.2 |  | 7687 | 108.88 | 1.2359 | 61.873 | 0.0036605 | 76.95 | 1109.2 | 1032.25
7688 | 1.2363 | 108.89 | 61.873 | 0.0036615 | 76.96 | 1109.2 |  | 7688 | 108.89 | 1.2363 | 61.873 | 0.0036615 | 76.96 | 1109.2 | 1032.24
7689 | 1.2366 | 108.9 | 61.873 | 0.0036625 | 76.97 | 1109.2 |  | 7689 | 108.9 | 1.2366 | 61.873 | 0.0036625 | 76.97 | 1109.2 | 1032.23
7690 | 1.237 | 108.91 | 61.873 | 0.0036635 | 76.98 | 1109.2 |  | 7690 | 108.91 | 1.237 | 61.873 | 0.0036635 | 76.98 | 1109.2 | 1032.22
7691 | 1.2373 | 108.92 | 61.873 | 0.0036645 | 76.99 | 1109.3 |  | 7691 | 108.92 | 1.2373 | 61.873 | 0.0036645 | 76.99 | 1109.3 | 1032.31
7692 | 1.2377 | 108.93 | 61.872 | 0.0036655 | 77 | 1109.3 |  | 7692 | 108.93 | 1.2377 | 61.872 | 0.0036655 | 77 | 1109.3 | 1032.3
7693 | 1.2381 | 108.94 | 61.872 | 0.0036665 | 77.01 | 1109.3 |  | 7693 | 108.94 | 1.2381 | 61.872 | 0.0036665 | 77.01 | 1109.3 | 1032.29
7694 | 1.2384 | 108.95 | 61.872 | 0.0036675 | 77.02 | 1109.3 |  | 7694 | 108.95 | 1.2384 | 61.872 | 0.0036675 | 77.02 | 1109.3 | 1032.28
7695 | 1.2388 | 108.96 | 61.872 | 0.0036685 | 77.03 | 1109.3 |  | 7695 | 108.96 | 1.2388 | 61.872 | 0.0036685 | 77.03 | 1109.3 | 1032.27
7696 | 1.2391 | 108.97 | 61.872 | 0.0036695 | 77.04 | 1109.3 |  | 7696 | 108.97 | 1.2391 | 61.872 | 0.0036695 | 77.04 | 1109.3 | 1032.26
7697 | 1.2395 | 108.98 | 61.872 | 0.0036705 | 77.05 | 1109.3 |  | 7697 | 108.98 | 1.2395 | 61.872 | 0.0036705 | 77.05 | 1109.3 | 1032.25
7698 | 1.2399 | 108.99 | 61.872 | 0.0036715 | 77.06 | 1109.3 |  | 7698 | 108.99 | 1.2399 | 61.872 | 0.0036715 | 77.06 | 1109.3 | 1032.24
7699 | 1.2402 | 109 | 61.871 | 0.0036725 | 77.07 | 1109.3 |  | 7699 | 109 | 1.2402 | 61.871 | 0.0036725 | 77.07 | 1109.3 | 1032.23
7700 | 1.2406 | 109.01 | 61.871 | 0.0036735 | 77.08 | 1109.3 |  | 7700 | 109.01 | 1.2406 | 61.871 | 0.0036735 | 77.08 | 1109.3 | 1032.22
7701 | 1.2409 | 109.02 | 61.871 | 0.0036745 | 77.09 | 1109.3 |  | 7701 | 109.02 | 1.2409 | 61.871 | 0.0036745 | 77.09 | 1109.3 | 1032.21
7702 | 1.2413 | 109.03 | 61.871 | 0.0036755 | 77.1 | 1109.3 |  | 7702 | 109.03 | 1.2413 | 61.871 | 0.0036755 | 77.1 | 1109.3 | 1032.2
7703 | 1.2417 | 109.04 | 61.871 | 0.0036765 | 77.11 | 1109.3 |  | 7703 | 109.04 | 1.2417 | 61.871 | 0.0036765 | 77.11 | 1109.3 | 1032.19
7704 | 1.242 | 109.05 | 61.871 | 0.0036776 | 77.12 | 1109.3 |  | 7704 | 109.05 | 1.242 | 61.871 | 0.0036776 | 77.12 | 1109.3 | 1032.18
7705 | 1.2424 | 109.06 | 61.871 | 0.0036786 | 77.13 | 1109.3 |  | 7705 | 109.06 | 1.2424 | 61.871 | 0.0036786 | 77.13 | 1109.3 | 1032.17
7706 | 1.2427 | 109.07 | 61.87 | 0.0036796 | 77.14 | 1109.3 |  | 7706 | 109.07 | 1.2427 | 61.87 | 0.0036796 | 77.14 | 1109.3 | 1032.16
7707 | 1.2431 | 109.08 | 61.87 | 0.0036806 | 77.15 | 1109.3 |  | 7707 | 109.08 | 1.2431 | 61.87 | 0.0036806 | 77.15 | 1109.3 | 1032.15
7708 | 1.2435 | 109.09 | 61.87 | 0.0036816 | 77.16 | 1109.3 |  | 7708 | 109.09 | 1.2435 | 61.87 | 0.0036816 | 77.16 | 1109.3 | 1032.14
7709 | 1.2438 | 109.1 | 61.87 | 0.0036826 | 77.17 | 1109.3 |  | 7709 | 109.1 | 1.2438 | 61.87 | 0.0036826 | 77.17 | 1109.3 | 1032.13
7710 | 1.2442 | 109.11 | 61.87 | 0.0036836 | 77.18 | 1109.3 |  | 7710 | 109.11 | 1.2442 | 61.87 | 0.0036836 | 77.18 | 1109.3 | 1032.12
7711 | 1.2446 | 109.12 | 61.87 | 0.0036846 | 77.19 | 1109.3 |  | 7711 | 109.12 | 1.2446 | 61.87 | 0.0036846 | 77.19 | 1109.3 | 1032.11
7712 | 1.2449 | 109.13 | 61.87 | 0.0036856 | 77.2 | 1109.3 |  | 7712 | 109.13 | 1.2449 | 61.87 | 0.0036856 | 77.2 | 1109.3 | 1032.1
7713 | 1.2453 | 109.14 | 61.869 | 0.0036866 | 77.21 | 1109.3 |  | 7713 | 109.14 | 1.2453 | 61.869 | 0.0036866 | 77.21 | 1109.3 | 1032.09
7714 | 1.2456 | 109.15 | 61.869 | 0.0036876 | 77.22 | 1109.3 |  | 7714 | 109.15 | 1.2456 | 61.869 | 0.0036876 | 77.22 | 1109.3 | 1032.08
7715 | 1.246 | 109.16 | 61.869 | 0.0036886 | 77.23 | 1109.4 |  | 7715 | 109.16 | 1.246 | 61.869 | 0.0036886 | 77.23 | 1109.4 | 1032.17
7716 | 1.2464 | 109.17 | 61.869 | 0.0036896 | 77.24 | 1109.4 |  | 7716 | 109.17 | 1.2464 | 61.869 | 0.0036896 | 77.24 | 1109.4 | 1032.16
7717 | 1.2467 | 109.18 | 61.869 | 0.0036906 | 77.25 | 1109.4 |  | 7717 | 109.18 | 1.2467 | 61.869 | 0.0036906 | 77.25 | 1109.4 | 1032.15
7718 | 1.2471 | 109.19 | 61.869 | 0.0036916 | 77.26 | 1109.4 |  | 7718 | 109.19 | 1.2471 | 61.869 | 0.0036916 | 77.26 | 1109.4 | 1032.14
7719 | 1.2474 | 109.2 | 61.869 | 0.0036926 | 77.27 | 1109.4 |  | 7719 | 109.2 | 1.2474 | 61.869 | 0.0036926 | 77.27 | 1109.4 | 1032.13
7720 | 1.2478 | 109.21 | 61.868 | 0.0036937 | 77.28 | 1109.4 |  | 7720 | 109.21 | 1.2478 | 61.868 | 0.0036937 | 77.28 | 1109.4 | 1032.12
7721 | 1.2482 | 109.22 | 61.868 | 0.0036947 | 77.29 | 1109.4 |  | 7721 | 109.22 | 1.2482 | 61.868 | 0.0036947 | 77.29 | 1109.4 | 1032.11
7722 | 1.2485 | 109.23 | 61.868 | 0.0036957 | 77.3 | 1109.4 |  | 7722 | 109.23 | 1.2485 | 61.868 | 0.0036957 | 77.3 | 1109.4 | 1032.1
7723 | 1.2489 | 109.24 | 61.868 | 0.0036967 | 77.31 | 1109.4 |  | 7723 | 109.24 | 1.2489 | 61.868 | 0.0036967 | 77.31 | 1109.4 | 1032.09
7724 | 1.2493 | 109.25 | 61.868 | 0.0036977 | 77.32 | 1109.4 |  | 7724 | 109.25 | 1.2493 | 61.868 | 0.0036977 | 77.32 | 1109.4 | 1032.08
7725 | 1.2496 | 109.26 | 61.868 | 0.0036987 | 77.33 | 1109.4 |  | 7725 | 109.26 | 1.2496 | 61.868 | 0.0036987 | 77.33 | 1109.4 | 1032.07
7726 | 1.25 | 109.27 | 61.868 | 0.0036997 | 77.34 | 1109.4 |  | 7726 | 109.27 | 1.25 | 61.868 | 0.0036997 | 77.34 | 1109.4 | 1032.06
7727 | 1.2503 | 109.28 | 61.867 | 0.0037007 | 77.35 | 1109.4 |  | 7727 | 109.28 | 1.2503 | 61.867 | 0.0037007 | 77.35 | 1109.4 | 1032.05
7728 | 1.2507 | 109.29 | 61.867 | 0.0037017 | 77.36 | 1109.4 |  | 7728 | 109.29 | 1.2507 | 61.867 | 0.0037017 | 77.36 | 1109.4 | 1032.04
7729 | 1.2511 | 109.3 | 61.867 | 0.0037027 | 77.37 | 1109.4 |  | 7729 | 109.3 | 1.2511 | 61.867 | 0.0037027 | 77.37 | 1109.4 | 1032.03
7730 | 1.2514 | 109.31 | 61.867 | 0.0037038 | 77.38 | 1109.4 |  | 7730 | 109.31 | 1.2514 | 61.867 | 0.0037038 | 77.38 | 1109.4 | 1032.02
7731 | 1.2518 | 109.32 | 61.867 | 0.0037048 | 77.39 | 1109.4 |  | 7731 | 109.32 | 1.2518 | 61.867 | 0.0037048 | 77.39 | 1109.4 | 1032.01
7732 | 1.2522 | 109.33 | 61.867 | 0.0037058 | 77.4 | 1109.4 |  | 7732 | 109.33 | 1.2522 | 61.867 | 0.0037058 | 77.4 | 1109.4 | 1032
7733 | 1.2525 | 109.34 | 61.867 | 0.0037068 | 77.41 | 1109.4 |  | 7733 | 109.34 | 1.2525 | 61.867 | 0.0037068 | 77.41 | 1109.4 | 1031.99
7734 | 1.2529 | 109.35 | 61.867 | 0.0037078 | 77.42 | 1109.4 |  | 7734 | 109.35 | 1.2529 | 61.867 | 0.0037078 | 77.42 | 1109.4 | 1031.98
7735 | 1.2532 | 109.36 | 61.866 | 0.0037088 | 77.43 | 1109.4 |  | 7735 | 109.36 | 1.2532 | 61.866 | 0.0037088 | 77.43 | 1109.4 | 1031.97
7736 | 1.2536 | 109.37 | 61.866 | 0.0037098 | 77.44 | 1109.4 |  | 7736 | 109.37 | 1.2536 | 61.866 | 0.0037098 | 77.44 | 1109.4 | 1031.96
7737 | 1.254 | 109.38 | 61.866 | 0.0037108 | 77.45 | 1109.4 |  | 7737 | 109.38 | 1.254 | 61.866 | 0.0037108 | 77.45 | 1109.4 | 1031.95
7738 | 1.2543 | 109.39 | 61.866 | 0.0037118 | 77.46 | 1109.5 |  | 7738 | 109.39 | 1.2543 | 61.866 | 0.0037118 | 77.46 | 1109.5 | 1032.04
7739 | 1.2547 | 109.4 | 61.866 | 0.0037129 | 77.47 | 1109.5 |  | 7739 | 109.4 | 1.2547 | 61.866 | 0.0037129 | 77.47 | 1109.5 | 1032.03
7740 | 1.2551 | 109.41 | 61.866 | 0.0037139 | 77.48 | 1109.5 |  | 7740 | 109.41 | 1.2551 | 61.866 | 0.0037139 | 77.48 | 1109.5 | 1032.02
7741 | 1.2554 | 109.42 | 61.866 | 0.0037149 | 77.49 | 1109.5 |  | 7741 | 109.42 | 1.2554 | 61.866 | 0.0037149 | 77.49 | 1109.5 | 1032.01
7742 | 1.2558 | 109.43 | 61.865 | 0.0037159 | 77.499 | 1109.5 |  | 7742 | 109.43 | 1.2558 | 61.865 | 0.0037159 | 77.499 | 1109.5 | 1032.001
7743 | 1.2562 | 109.44 | 61.865 | 0.0037169 | 77.509 | 1109.5 |  | 7743 | 109.44 | 1.2562 | 61.865 | 0.0037169 | 77.509 | 1109.5 | 1031.991
7744 | 1.2565 | 109.45 | 61.865 | 0.0037179 | 77.519 | 1109.5 |  | 7744 | 109.45 | 1.2565 | 61.865 | 0.0037179 | 77.519 | 1109.5 | 1031.981
7745 | 1.2569 | 109.46 | 61.865 | 0.0037189 | 77.529 | 1109.5 |  | 7745 | 109.46 | 1.2569 | 61.865 | 0.0037189 | 77.529 | 1109.5 | 1031.971
7746 | 1.2572 | 109.47 | 61.865 | 0.00372 | 77.539 | 1109.5 |  | 7746 | 109.47 | 1.2572 | 61.865 | 0.00372 | 77.539 | 1109.5 | 1031.961
7747 | 1.2576 | 109.48 | 61.865 | 0.003721 | 77.549 | 1109.5 |  | 7747 | 109.48 | 1.2576 | 61.865 | 0.003721 | 77.549 | 1109.5 | 1031.951
7748 | 1.258 | 109.49 | 61.865 | 0.003722 | 77.559 | 1109.5 |  | 7748 | 109.49 | 1.258 | 61.865 | 0.003722 | 77.559 | 1109.5 | 1031.941
7749 | 1.2583 | 109.5 | 61.864 | 0.003723 | 77.569 | 1109.5 |  | 7749 | 109.5 | 1.2583 | 61.864 | 0.003723 | 77.569 | 1109.5 | 1031.931
7750 | 1.2587 | 109.51 | 61.864 | 0.003724 | 77.579 | 1109.5 |  | 7750 | 109.51 | 1.2587 | 61.864 | 0.003724 | 77.579 | 1109.5 | 1031.921
7751 | 1.2591 | 109.52 | 61.864 | 0.003725 | 77.589 | 1109.5 |  | 7751 | 109.52 | 1.2591 | 61.864 | 0.003725 | 77.589 | 1109.5 | 1031.911
7752 | 1.2594 | 109.53 | 61.864 | 0.003726 | 77.599 | 1109.5 |  | 7752 | 109.53 | 1.2594 | 61.864 | 0.003726 | 77.599 | 1109.5 | 1031.901
7753 | 1.2598 | 109.54 | 61.864 | 0.0037271 | 77.609 | 1109.5 |  | 7753 | 109.54 | 1.2598 | 61.864 | 0.0037271 | 77.609 | 1109.5 | 1031.891
7754 | 1.2602 | 109.55 | 61.864 | 0.0037281 | 77.619 | 1109.5 |  | 7754 | 109.55 | 1.2602 | 61.864 | 0.0037281 | 77.619 | 1109.5 | 1031.881
7755 | 1.2605 | 109.56 | 61.864 | 0.0037291 | 77.629 | 1109.5 |  | 7755 | 109.56 | 1.2605 | 61.864 | 0.0037291 | 77.629 | 1109.5 | 1031.871
7756 | 1.2609 | 109.57 | 61.863 | 0.0037301 | 77.639 | 1109.5 |  | 7756 | 109.57 | 1.2609 | 61.863 | 0.0037301 | 77.639 | 1109.5 | 1031.861
7757 | 1.2613 | 109.58 | 61.863 | 0.0037311 | 77.649 | 1109.5 |  | 7757 | 109.58 | 1.2613 | 61.863 | 0.0037311 | 77.649 | 1109.5 | 1031.851
7758 | 1.2616 | 109.59 | 61.863 | 0.0037321 | 77.659 | 1109.5 |  | 7758 | 109.59 | 1.2616 | 61.863 | 0.0037321 | 77.659 | 1109.5 | 1031.841
7759 | 1.262 | 109.6 | 61.863 | 0.0037332 | 77.669 | 1109.5 |  | 7759 | 109.6 | 1.262 | 61.863 | 0.0037332 | 77.669 | 1109.5 | 1031.831
7760 | 1.2624 | 109.61 | 61.863 | 0.0037342 | 77.679 | 1109.5 |  | 7760 | 109.61 | 1.2624 | 61.863 | 0.0037342 | 77.679 | 1109.5 | 1031.821
7761 | 1.2627 | 109.62 | 61.863 | 0.0037352 | 77.689 | 1109.5 |  | 7761 | 109.62 | 1.2627 | 61.863 | 0.0037352 | 77.689 | 1109.5 | 1031.811
7762 | 1.2631 | 109.63 | 61.863 | 0.0037362 | 77.699 | 1109.6 |  | 7762 | 109.63 | 1.2631 | 61.863 | 0.0037362 | 77.699 | 1109.6 | 1031.901
7763 | 1.2635 | 109.64 | 61.862 | 0.0037372 | 77.709 | 1109.6 |  | 7763 | 109.64 | 1.2635 | 61.862 | 0.0037372 | 77.709 | 1109.6 | 1031.891
7764 | 1.2638 | 109.65 | 61.862 | 0.0037383 | 77.719 | 1109.6 |  | 7764 | 109.65 | 1.2638 | 61.862 | 0.0037383 | 77.719 | 1109.6 | 1031.881
7765 | 1.2642 | 109.66 | 61.862 | 0.0037393 | 77.729 | 1109.6 |  | 7765 | 109.66 | 1.2642 | 61.862 | 0.0037393 | 77.729 | 1109.6 | 1031.871
7766 | 1.2645 | 109.67 | 61.862 | 0.0037403 | 77.739 | 1109.6 |  | 7766 | 109.67 | 1.2645 | 61.862 | 0.0037403 | 77.739 | 1109.6 | 1031.861
7767 | 1.2649 | 109.68 | 61.862 | 0.0037413 | 77.749 | 1109.6 |  | 7767 | 109.68 | 1.2649 | 61.862 | 0.0037413 | 77.749 | 1109.6 | 1031.851
7768 | 1.2653 | 109.69 | 61.862 | 0.0037423 | 77.759 | 1109.6 |  | 7768 | 109.69 | 1.2653 | 61.862 | 0.0037423 | 77.759 | 1109.6 | 1031.841
7769 | 1.2656 | 109.7 | 61.862 | 0.0037434 | 77.769 | 1109.6 |  | 7769 | 109.7 | 1.2656 | 61.862 | 0.0037434 | 77.769 | 1109.6 | 1031.831
7770 | 1.266 | 109.71 | 61.861 | 0.0037444 | 77.779 | 1109.6 |  | 7770 | 109.71 | 1.266 | 61.861 | 0.0037444 | 77.779 | 1109.6 | 1031.821
7771 | 1.2664 | 109.72 | 61.861 | 0.0037454 | 77.789 | 1109.6 |  | 7771 | 109.72 | 1.2664 | 61.861 | 0.0037454 | 77.789 | 1109.6 | 1031.811
7772 | 1.2667 | 109.73 | 61.861 | 0.0037464 | 77.799 | 1109.6 |  | 7772 | 109.73 | 1.2667 | 61.861 | 0.0037464 | 77.799 | 1109.6 | 1031.801
7773 | 1.2671 | 109.74 | 61.861 | 0.0037474 | 77.809 | 1109.6 |  | 7773 | 109.74 | 1.2671 | 61.861 | 0.0037474 | 77.809 | 1109.6 | 1031.791
7774 | 1.2675 | 109.75 | 61.861 | 0.0037485 | 77.819 | 1109.6 |  | 7774 | 109.75 | 1.2675 | 61.861 | 0.0037485 | 77.819 | 1109.6 | 1031.781
7775 | 1.2678 | 109.76 | 61.861 | 0.0037495 | 77.829 | 1109.6 |  | 7775 | 109.76 | 1.2678 | 61.861 | 0.0037495 | 77.829 | 1109.6 | 1031.771
7776 | 1.2682 | 109.77 | 61.861 | 0.0037505 | 77.839 | 1109.6 |  | 7776 | 109.77 | 1.2682 | 61.861 | 0.0037505 | 77.839 | 1109.6 | 1031.761
7777 | 1.2686 | 109.78 | 61.86 | 0.0037515 | 77.849 | 1109.6 |  | 7777 | 109.78 | 1.2686 | 61.86 | 0.0037515 | 77.849 | 1109.6 | 1031.751
7778 | 1.2689 | 109.79 | 61.86 | 0.0037525 | 77.859 | 1109.6 |  | 7778 | 109.79 | 1.2689 | 61.86 | 0.0037525 | 77.859 | 1109.6 | 1031.741
7779 | 1.2693 | 109.8 | 61.86 | 0.0037536 | 77.869 | 1109.6 |  | 7779 | 109.8 | 1.2693 | 61.86 | 0.0037536 | 77.869 | 1109.6 | 1031.731
7780 | 1.2697 | 109.81 | 61.86 | 0.0037546 | 77.879 | 1109.6 |  | 7780 | 109.81 | 1.2697 | 61.86 | 0.0037546 | 77.879 | 1109.6 | 1031.721
7781 | 1.2701 | 109.82 | 61.86 | 0.0037556 | 77.889 | 1109.6 |  | 7781 | 109.82 | 1.2701 | 61.86 | 0.0037556 | 77.889 | 1109.6 | 1031.711
7782 | 1.2704 | 109.83 | 61.86 | 0.0037566 | 77.899 | 1109.6 |  | 7782 | 109.83 | 1.2704 | 61.86 | 0.0037566 | 77.899 | 1109.6 | 1031.701
7783 | 1.2708 | 109.84 | 61.86 | 0.0037577 | 77.909 | 1109.6 |  | 7783 | 109.84 | 1.2708 | 61.86 | 0.0037577 | 77.909 | 1109.6 | 1031.691
7784 | 1.2712 | 109.85 | 61.859 | 0.0037587 | 77.919 | 1109.6 |  | 7784 | 109.85 | 1.2712 | 61.859 | 0.0037587 | 77.919 | 1109.6 | 1031.681
7785 | 1.2715 | 109.86 | 61.859 | 0.0037597 | 77.929 | 1109.7 |  | 7785 | 109.86 | 1.2715 | 61.859 | 0.0037597 | 77.929 | 1109.7 | 1031.771
7786 | 1.2719 | 109.87 | 61.859 | 0.0037607 | 77.939 | 1109.7 |  | 7786 | 109.87 | 1.2719 | 61.859 | 0.0037607 | 77.939 | 1109.7 | 1031.761
7787 | 1.2723 | 109.88 | 61.859 | 0.0037618 | 77.949 | 1109.7 |  | 7787 | 109.88 | 1.2723 | 61.859 | 0.0037618 | 77.949 | 1109.7 | 1031.751
7788 | 1.2726 | 109.89 | 61.859 | 0.0037628 | 77.959 | 1109.7 |  | 7788 | 109.89 | 1.2726 | 61.859 | 0.0037628 | 77.959 | 1109.7 | 1031.741
7789 | 1.273 | 109.9 | 61.859 | 0.0037638 | 77.969 | 1109.7 |  | 7789 | 109.9 | 1.273 | 61.859 | 0.0037638 | 77.969 | 1109.7 | 1031.731
7790 | 1.2734 | 109.91 | 61.859 | 0.0037648 | 77.979 | 1109.7 |  | 7790 | 109.91 | 1.2734 | 61.859 | 0.0037648 | 77.979 | 1109.7 | 1031.721
7791 | 1.2737 | 109.92 | 61.859 | 0.0037659 | 77.989 | 1109.7 |  | 7791 | 109.92 | 1.2737 | 61.859 | 0.0037659 | 77.989 | 1109.7 | 1031.711
7792 | 1.2741 | 109.93 | 61.858 | 0.0037669 | 77.999 | 1109.7 |  | 7792 | 109.93 | 1.2741 | 61.858 | 0.0037669 | 77.999 | 1109.7 | 1031.701
7793 | 1.2745 | 109.94 | 61.858 | 0.0037679 | 78.009 | 1109.7 |  | 7793 | 109.94 | 1.2745 | 61.858 | 0.0037679 | 78.009 | 1109.7 | 1031.691
7794 | 1.2748 | 109.95 | 61.858 | 0.0037689 | 78.019 | 1109.7 |  | 7794 | 109.95 | 1.2748 | 61.858 | 0.0037689 | 78.019 | 1109.7 | 1031.681
7795 | 1.2752 | 109.96 | 61.858 | 0.00377 | 78.029 | 1109.7 |  | 7795 | 109.96 | 1.2752 | 61.858 | 0.00377 | 78.029 | 1109.7 | 1031.671
7796 | 1.2756 | 109.97 | 61.858 | 0.003771 | 78.039 | 1109.7 |  | 7796 | 109.97 | 1.2756 | 61.858 | 0.003771 | 78.039 | 1109.7 | 1031.661
7797 | 1.2759 | 109.98 | 61.858 | 0.003772 | 78.049 | 1109.7 |  | 7797 | 109.98 | 1.2759 | 61.858 | 0.003772 | 78.049 | 1109.7 | 1031.651
7798 | 1.2763 | 109.99 | 61.858 | 0.003773 | 78.059 | 1109.7 |  | 7798 | 109.99 | 1.2763 | 61.858 | 0.003773 | 78.059 | 1109.7 | 1031.641
7799 | 1.2767 | 110 | 61.857 | 0.0037741 | 78.069 | 1109.7 |  | 7799 | 110 | 1.2767 | 61.857 | 0.0037741 | 78.069 | 1109.7 | 1031.631
7800 | 1.277 | 110.01 | 61.857 | 0.0037751 | 78.079 | 1109.7 |  | 7800 | 110.01 | 1.277 | 61.857 | 0.0037751 | 78.079 | 1109.7 | 1031.621
7801 | 1.2774 | 110.02 | 61.857 | 0.0037761 | 78.089 | 1109.7 |  | 7801 | 110.02 | 1.2774 | 61.857 | 0.0037761 | 78.089 | 1109.7 | 1031.611
7802 | 1.2778 | 110.03 | 61.857 | 0.0037771 | 78.099 | 1109.7 |  | 7802 | 110.03 | 1.2778 | 61.857 | 0.0037771 | 78.099 | 1109.7 | 1031.601
7803 | 1.2782 | 110.04 | 61.857 | 0.0037782 | 78.109 | 1109.7 |  | 7803 | 110.04 | 1.2782 | 61.857 | 0.0037782 | 78.109 | 1109.7 | 1031.591
7804 | 1.2785 | 110.05 | 61.857 | 0.0037792 | 78.119 | 1109.7 |  | 7804 | 110.05 | 1.2785 | 61.857 | 0.0037792 | 78.119 | 1109.7 | 1031.581
7805 | 1.2789 | 110.06 | 61.857 | 0.0037802 | 78.129 | 1109.7 |  | 7805 | 110.06 | 1.2789 | 61.857 | 0.0037802 | 78.129 | 1109.7 | 1031.571
7806 | 1.2793 | 110.07 | 61.856 | 0.0037813 | 78.139 | 1109.7 |  | 7806 | 110.07 | 1.2793 | 61.856 | 0.0037813 | 78.139 | 1109.7 | 1031.561
7807 | 1.2796 | 110.08 | 61.856 | 0.0037823 | 78.149 | 1109.7 |  | 7807 | 110.08 | 1.2796 | 61.856 | 0.0037823 | 78.149 | 1109.7 | 1031.551
7808 | 1.28 | 110.09 | 61.856 | 0.0037833 | 78.159 | 1109.7 |  | 7808 | 110.09 | 1.28 | 61.856 | 0.0037833 | 78.159 | 1109.7 | 1031.541
7809 | 1.2804 | 110.1 | 61.856 | 0.0037843 | 78.169 | 1109.8 |  | 7809 | 110.1 | 1.2804 | 61.856 | 0.0037843 | 78.169 | 1109.8 | 1031.631
7810 | 1.2807 | 110.11 | 61.856 | 0.0037854 | 78.179 | 1109.8 |  | 7810 | 110.11 | 1.2807 | 61.856 | 0.0037854 | 78.179 | 1109.8 | 1031.621
7811 | 1.2811 | 110.12 | 61.856 | 0.0037864 | 78.189 | 1109.8 |  | 7811 | 110.12 | 1.2811 | 61.856 | 0.0037864 | 78.189 | 1109.8 | 1031.611
7812 | 1.2815 | 110.13 | 61.856 | 0.0037874 | 78.199 | 1109.8 |  | 7812 | 110.13 | 1.2815 | 61.856 | 0.0037874 | 78.199 | 1109.8 | 1031.601
7813 | 1.2819 | 110.14 | 61.855 | 0.0037885 | 78.209 | 1109.8 |  | 7813 | 110.14 | 1.2819 | 61.855 | 0.0037885 | 78.209 | 1109.8 | 1031.591
7814 | 1.2822 | 110.15 | 61.855 | 0.0037895 | 78.219 | 1109.8 |  | 7814 | 110.15 | 1.2822 | 61.855 | 0.0037895 | 78.219 | 1109.8 | 1031.581
7815 | 1.2826 | 110.16 | 61.855 | 0.0037905 | 78.229 | 1109.8 |  | 7815 | 110.16 | 1.2826 | 61.855 | 0.0037905 | 78.229 | 1109.8 | 1031.571
7816 | 1.283 | 110.17 | 61.855 | 0.0037916 | 78.239 | 1109.8 |  | 7816 | 110.17 | 1.283 | 61.855 | 0.0037916 | 78.239 | 1109.8 | 1031.561
7817 | 1.2833 | 110.18 | 61.855 | 0.0037926 | 78.249 | 1109.8 |  | 7817 | 110.18 | 1.2833 | 61.855 | 0.0037926 | 78.249 | 1109.8 | 1031.551
7818 | 1.2837 | 110.19 | 61.855 | 0.0037936 | 78.259 | 1109.8 |  | 7818 | 110.19 | 1.2837 | 61.855 | 0.0037936 | 78.259 | 1109.8 | 1031.541
7819 | 1.2841 | 110.2 | 61.855 | 0.0037947 | 78.269 | 1109.8 |  | 7819 | 110.2 | 1.2841 | 61.855 | 0.0037947 | 78.269 | 1109.8 | 1031.531
7820 | 1.2845 | 110.21 | 61.854 | 0.0037957 | 78.279 | 1109.8 |  | 7820 | 110.21 | 1.2845 | 61.854 | 0.0037957 | 78.279 | 1109.8 | 1031.521
7821 | 1.2848 | 110.22 | 61.854 | 0.0037967 | 78.289 | 1109.8 |  | 7821 | 110.22 | 1.2848 | 61.854 | 0.0037967 | 78.289 | 1109.8 | 1031.511
7822 | 1.2852 | 110.23 | 61.854 | 0.0037977 | 78.299 | 1109.8 |  | 7822 | 110.23 | 1.2852 | 61.854 | 0.0037977 | 78.299 | 1109.8 | 1031.501
7823 | 1.2856 | 110.24 | 61.854 | 0.0037988 | 78.309 | 1109.8 |  | 7823 | 110.24 | 1.2856 | 61.854 | 0.0037988 | 78.309 | 1109.8 | 1031.491
7824 | 1.2859 | 110.25 | 61.854 | 0.0037998 | 78.319 | 1109.8 |  | 7824 | 110.25 | 1.2859 | 61.854 | 0.0037998 | 78.319 | 1109.8 | 1031.481
7825 | 1.2863 | 110.26 | 61.854 | 0.0038008 | 78.329 | 1109.8 |  | 7825 | 110.26 | 1.2863 | 61.854 | 0.0038008 | 78.329 | 1109.8 | 1031.471
7826 | 1.2867 | 110.27 | 61.854 | 0.0038019 | 78.339 | 1109.8 |  | 7826 | 110.27 | 1.2867 | 61.854 | 0.0038019 | 78.339 | 1109.8 | 1031.461
7827 | 1.2871 | 110.28 | 61.853 | 0.0038029 | 78.349 | 1109.8 |  | 7827 | 110.28 | 1.2871 | 61.853 | 0.0038029 | 78.349 | 1109.8 | 1031.451
7828 | 1.2874 | 110.29 | 61.853 | 0.0038039 | 78.359 | 1109.8 |  | 7828 | 110.29 | 1.2874 | 61.853 | 0.0038039 | 78.359 | 1109.8 | 1031.441
7829 | 1.2878 | 110.3 | 61.853 | 0.003805 | 78.369 | 1109.8 |  | 7829 | 110.3 | 1.2878 | 61.853 | 0.003805 | 78.369 | 1109.8 | 1031.431
7830 | 1.2882 | 110.31 | 61.853 | 0.003806 | 78.379 | 1109.8 |  | 7830 | 110.31 | 1.2882 | 61.853 | 0.003806 | 78.379 | 1109.8 | 1031.421
7831 | 1.2885 | 110.32 | 61.853 | 0.0038071 | 78.389 | 1109.8 |  | 7831 | 110.32 | 1.2885 | 61.853 | 0.0038071 | 78.389 | 1109.8 | 1031.411
7832 | 1.2889 | 110.33 | 61.853 | 0.0038081 | 78.399 | 1109.9 |  | 7832 | 110.33 | 1.2889 | 61.853 | 0.0038081 | 78.399 | 1109.9 | 1031.501
7833 | 1.2893 | 110.34 | 61.853 | 0.0038091 | 78.409 | 1109.9 |  | 7833 | 110.34 | 1.2893 | 61.853 | 0.0038091 | 78.409 | 1109.9 | 1031.491
7834 | 1.2897 | 110.35 | 61.852 | 0.0038102 | 78.419 | 1109.9 |  | 7834 | 110.35 | 1.2897 | 61.852 | 0.0038102 | 78.419 | 1109.9 | 1031.481
7835 | 1.29 | 110.36 | 61.852 | 0.0038112 | 78.429 | 1109.9 |  | 7835 | 110.36 | 1.29 | 61.852 | 0.0038112 | 78.429 | 1109.9 | 1031.471
7836 | 1.2904 | 110.37 | 61.852 | 0.0038122 | 78.439 | 1109.9 |  | 7836 | 110.37 | 1.2904 | 61.852 | 0.0038122 | 78.439 | 1109.9 | 1031.461
7837 | 1.2908 | 110.38 | 61.852 | 0.0038133 | 78.449 | 1109.9 |  | 7837 | 110.38 | 1.2908 | 61.852 | 0.0038133 | 78.449 | 1109.9 | 1031.451
7838 | 1.2911 | 110.39 | 61.852 | 0.0038143 | 78.459 | 1109.9 |  | 7838 | 110.39 | 1.2911 | 61.852 | 0.0038143 | 78.459 | 1109.9 | 1031.441
7839 | 1.2915 | 110.4 | 61.852 | 0.0038153 | 78.469 | 1109.9 |  | 7839 | 110.4 | 1.2915 | 61.852 | 0.0038153 | 78.469 | 1109.9 | 1031.431
7840 | 1.2919 | 110.41 | 61.852 | 0.0038164 | 78.479 | 1109.9 |  | 7840 | 110.41 | 1.2919 | 61.852 | 0.0038164 | 78.479 | 1109.9 | 1031.421
7841 | 1.2923 | 110.42 | 61.851 | 0.0038174 | 78.489 | 1109.9 |  | 7841 | 110.42 | 1.2923 | 61.851 | 0.0038174 | 78.489 | 1109.9 | 1031.411
7842 | 1.2926 | 110.43 | 61.851 | 0.0038184 | 78.499 | 1109.9 |  | 7842 | 110.43 | 1.2926 | 61.851 | 0.0038184 | 78.499 | 1109.9 | 1031.401
7843 | 1.293 | 110.44 | 61.851 | 0.0038195 | 78.509 | 1109.9 |  | 7843 | 110.44 | 1.293 | 61.851 | 0.0038195 | 78.509 | 1109.9 | 1031.391
7844 | 1.2934 | 110.45 | 61.851 | 0.0038205 | 78.519 | 1109.9 |  | 7844 | 110.45 | 1.2934 | 61.851 | 0.0038205 | 78.519 | 1109.9 | 1031.381
7845 | 1.2938 | 110.46 | 61.851 | 0.0038216 | 78.529 | 1109.9 |  | 7845 | 110.46 | 1.2938 | 61.851 | 0.0038216 | 78.529 | 1109.9 | 1031.371
7846 | 1.2941 | 110.47 | 61.851 | 0.0038226 | 78.539 | 1109.9 |  | 7846 | 110.47 | 1.2941 | 61.851 | 0.0038226 | 78.539 | 1109.9 | 1031.361
7847 | 1.2945 | 110.48 | 61.851 | 0.0038236 | 78.549 | 1109.9 |  | 7847 | 110.48 | 1.2945 | 61.851 | 0.0038236 | 78.549 | 1109.9 | 1031.351
7848 | 1.2949 | 110.49 | 61.85 | 0.0038247 | 78.559 | 1109.9 |  | 7848 | 110.49 | 1.2949 | 61.85 | 0.0038247 | 78.559 | 1109.9 | 1031.341
7849 | 1.2953 | 110.5 | 61.85 | 0.0038257 | 78.569 | 1109.9 |  | 7849 | 110.5 | 1.2953 | 61.85 | 0.0038257 | 78.569 | 1109.9 | 1031.331
7850 | 1.2956 | 110.51 | 61.85 | 0.0038268 | 78.579 | 1109.9 |  | 7850 | 110.51 | 1.2956 | 61.85 | 0.0038268 | 78.579 | 1109.9 | 1031.321
7851 | 1.296 | 110.52 | 61.85 | 0.0038278 | 78.589 | 1109.9 |  | 7851 | 110.52 | 1.296 | 61.85 | 0.0038278 | 78.589 | 1109.9 | 1031.311
7852 | 1.2964 | 110.53 | 61.85 | 0.0038288 | 78.599 | 1109.9 |  | 7852 | 110.53 | 1.2964 | 61.85 | 0.0038288 | 78.599 | 1109.9 | 1031.301
7853 | 1.2967 | 110.54 | 61.85 | 0.0038299 | 78.609 | 1109.9 |  | 7853 | 110.54 | 1.2967 | 61.85 | 0.0038299 | 78.609 | 1109.9 | 1031.291
7854 | 1.2971 | 110.55 | 61.85 | 0.0038309 | 78.619 | 1109.9 |  | 7854 | 110.55 | 1.2971 | 61.85 | 0.0038309 | 78.619 | 1109.9 | 1031.281
7855 | 1.2975 | 110.56 | 61.849 | 0.003832 | 78.629 | 1109.9 |  | 7855 | 110.56 | 1.2975 | 61.849 | 0.003832 | 78.629 | 1109.9 | 1031.271
7856 | 1.2979 | 110.57 | 61.849 | 0.003833 | 78.639 | 1110 |  | 7856 | 110.57 | 1.2979 | 61.849 | 0.003833 | 78.639 | 1110 | 1031.361
7857 | 1.2982 | 110.58 | 61.849 | 0.003834 | 78.649 | 1110 |  | 7857 | 110.58 | 1.2982 | 61.849 | 0.003834 | 78.649 | 1110 | 1031.351
7858 | 1.2986 | 110.59 | 61.849 | 0.0038351 | 78.659 | 1110 |  | 7858 | 110.59 | 1.2986 | 61.849 | 0.0038351 | 78.659 | 1110 | 1031.341
7859 | 1.299 | 110.6 | 61.849 | 0.0038361 | 78.669 | 1110 |  | 7859 | 110.6 | 1.299 | 61.849 | 0.0038361 | 78.669 | 1110 | 1031.331
7860 | 1.2994 | 110.61 | 61.849 | 0.0038372 | 78.678 | 1110 |  | 7860 | 110.61 | 1.2994 | 61.849 | 0.0038372 | 78.678 | 1110 | 1031.322
7861 | 1.2997 | 110.62 | 61.849 | 0.0038382 | 78.688 | 1110 |  | 7861 | 110.62 | 1.2997 | 61.849 | 0.0038382 | 78.688 | 1110 | 1031.312
7862 | 1.3001 | 110.63 | 61.848 | 0.0038392 | 78.698 | 1110 |  | 7862 | 110.63 | 1.3001 | 61.848 | 0.0038392 | 78.698 | 1110 | 1031.302
7863 | 1.3005 | 110.64 | 61.848 | 0.0038403 | 78.708 | 1110 |  | 7863 | 110.64 | 1.3005 | 61.848 | 0.0038403 | 78.708 | 1110 | 1031.292
7864 | 1.3009 | 110.65 | 61.848 | 0.0038413 | 78.718 | 1110 |  | 7864 | 110.65 | 1.3009 | 61.848 | 0.0038413 | 78.718 | 1110 | 1031.282
7865 | 1.3012 | 110.66 | 61.848 | 0.0038424 | 78.728 | 1110 |  | 7865 | 110.66 | 1.3012 | 61.848 | 0.0038424 | 78.728 | 1110 | 1031.272
7866 | 1.3016 | 110.67 | 61.848 | 0.0038434 | 78.738 | 1110 |  | 7866 | 110.67 | 1.3016 | 61.848 | 0.0038434 | 78.738 | 1110 | 1031.262
7867 | 1.302 | 110.68 | 61.848 | 0.0038445 | 78.748 | 1110 |  | 7867 | 110.68 | 1.302 | 61.848 | 0.0038445 | 78.748 | 1110 | 1031.252
7868 | 1.3024 | 110.69 | 61.848 | 0.0038455 | 78.758 | 1110 |  | 7868 | 110.69 | 1.3024 | 61.848 | 0.0038455 | 78.758 | 1110 | 1031.242
7869 | 1.3027 | 110.7 | 61.847 | 0.0038465 | 78.768 | 1110 |  | 7869 | 110.7 | 1.3027 | 61.847 | 0.0038465 | 78.768 | 1110 | 1031.232
7870 | 1.3031 | 110.71 | 61.847 | 0.0038476 | 78.778 | 1110 |  | 7870 | 110.71 | 1.3031 | 61.847 | 0.0038476 | 78.778 | 1110 | 1031.222
7871 | 1.3035 | 110.72 | 61.847 | 0.0038486 | 78.788 | 1110 |  | 7871 | 110.72 | 1.3035 | 61.847 | 0.0038486 | 78.788 | 1110 | 1031.212
7872 | 1.3039 | 110.73 | 61.847 | 0.0038497 | 78.798 | 1110 |  | 7872 | 110.73 | 1.3039 | 61.847 | 0.0038497 | 78.798 | 1110 | 1031.202
7873 | 1.3042 | 110.74 | 61.847 | 0.0038507 | 78.808 | 1110 |  | 7873 | 110.74 | 1.3042 | 61.847 | 0.0038507 | 78.808 | 1110 | 1031.192
7874 | 1.3046 | 110.75 | 61.847 | 0.0038518 | 78.818 | 1110 |  | 7874 | 110.75 | 1.3046 | 61.847 | 0.0038518 | 78.818 | 1110 | 1031.182
7875 | 1.305 | 110.76 | 61.847 | 0.0038528 | 78.828 | 1110 |  | 7875 | 110.76 | 1.305 | 61.847 | 0.0038528 | 78.828 | 1110 | 1031.172
7876 | 1.3054 | 110.77 | 61.846 | 0.0038539 | 78.838 | 1110 |  | 7876 | 110.77 | 1.3054 | 61.846 | 0.0038539 | 78.838 | 1110 | 1031.162
7877 | 1.3058 | 110.78 | 61.846 | 0.0038549 | 78.848 | 1110 |  | 7877 | 110.78 | 1.3058 | 61.846 | 0.0038549 | 78.848 | 1110 | 1031.152
7878 | 1.3061 | 110.79 | 61.846 | 0.003856 | 78.858 | 1110 |  | 7878 | 110.79 | 1.3061 | 61.846 | 0.003856 | 78.858 | 1110 | 1031.142
7879 | 1.3065 | 110.8 | 61.846 | 0.003857 | 78.868 | 1110.1 |  | 7879 | 110.8 | 1.3065 | 61.846 | 0.003857 | 78.868 | 1110.1 | 1031.232
7880 | 1.3069 | 110.81 | 61.846 | 0.003858 | 78.878 | 1110.1 |  | 7880 | 110.81 | 1.3069 | 61.846 | 0.003858 | 78.878 | 1110.1 | 1031.222
7881 | 1.3073 | 110.82 | 61.846 | 0.0038591 | 78.888 | 1110.1 |  | 7881 | 110.82 | 1.3073 | 61.846 | 0.0038591 | 78.888 | 1110.1 | 1031.212
7882 | 1.3076 | 110.83 | 61.846 | 0.0038601 | 78.898 | 1110.1 |  | 7882 | 110.83 | 1.3076 | 61.846 | 0.0038601 | 78.898 | 1110.1 | 1031.202
7883 | 1.308 | 110.84 | 61.845 | 0.0038612 | 78.908 | 1110.1 |  | 7883 | 110.84 | 1.308 | 61.845 | 0.0038612 | 78.908 | 1110.1 | 1031.192
7884 | 1.3084 | 110.85 | 61.845 | 0.0038622 | 78.918 | 1110.1 |  | 7884 | 110.85 | 1.3084 | 61.845 | 0.0038622 | 78.918 | 1110.1 | 1031.182
7885 | 1.3088 | 110.86 | 61.845 | 0.0038633 | 78.928 | 1110.1 |  | 7885 | 110.86 | 1.3088 | 61.845 | 0.0038633 | 78.928 | 1110.1 | 1031.172
7886 | 1.3091 | 110.87 | 61.845 | 0.0038643 | 78.938 | 1110.1 |  | 7886 | 110.87 | 1.3091 | 61.845 | 0.0038643 | 78.938 | 1110.1 | 1031.162
7887 | 1.3095 | 110.88 | 61.845 | 0.0038654 | 78.948 | 1110.1 |  | 7887 | 110.88 | 1.3095 | 61.845 | 0.0038654 | 78.948 | 1110.1 | 1031.152
7888 | 1.3099 | 110.89 | 61.845 | 0.0038664 | 78.958 | 1110.1 |  | 7888 | 110.89 | 1.3099 | 61.845 | 0.0038664 | 78.958 | 1110.1 | 1031.142
7889 | 1.3103 | 110.9 | 61.845 | 0.0038675 | 78.968 | 1110.1 |  | 7889 | 110.9 | 1.3103 | 61.845 | 0.0038675 | 78.968 | 1110.1 | 1031.132
7890 | 1.3107 | 110.91 | 61.844 | 0.0038685 | 78.978 | 1110.1 |  | 7890 | 110.91 | 1.3107 | 61.844 | 0.0038685 | 78.978 | 1110.1 | 1031.122
7891 | 1.311 | 110.92 | 61.844 | 0.0038696 | 78.988 | 1110.1 |  | 7891 | 110.92 | 1.311 | 61.844 | 0.0038696 | 78.988 | 1110.1 | 1031.112
7892 | 1.3114 | 110.93 | 61.844 | 0.0038706 | 78.998 | 1110.1 |  | 7892 | 110.93 | 1.3114 | 61.844 | 0.0038706 | 78.998 | 1110.1 | 1031.102
7893 | 1.3118 | 110.94 | 61.844 | 0.0038717 | 79.008 | 1110.1 |  | 7893 | 110.94 | 1.3118 | 61.844 | 0.0038717 | 79.008 | 1110.1 | 1031.092
7894 | 1.3122 | 110.95 | 61.844 | 0.0038727 | 79.018 | 1110.1 |  | 7894 | 110.95 | 1.3122 | 61.844 | 0.0038727 | 79.018 | 1110.1 | 1031.082
7895 | 1.3125 | 110.96 | 61.844 | 0.0038738 | 79.028 | 1110.1 |  | 7895 | 110.96 | 1.3125 | 61.844 | 0.0038738 | 79.028 | 1110.1 | 1031.072
7896 | 1.3129 | 110.97 | 61.844 | 0.0038748 | 79.038 | 1110.1 |  | 7896 | 110.97 | 1.3129 | 61.844 | 0.0038748 | 79.038 | 1110.1 | 1031.062
7897 | 1.3133 | 110.98 | 61.843 | 0.0038759 | 79.048 | 1110.1 |  | 7897 | 110.98 | 1.3133 | 61.843 | 0.0038759 | 79.048 | 1110.1 | 1031.052
7898 | 1.3137 | 110.99 | 61.843 | 0.0038769 | 79.058 | 1110.1 |  | 7898 | 110.99 | 1.3137 | 61.843 | 0.0038769 | 79.058 | 1110.1 | 1031.042
7899 | 1.3141 | 111 | 61.843 | 0.003878 | 79.068 | 1110.1 |  | 7899 | 111 | 1.3141 | 61.843 | 0.003878 | 79.068 | 1110.1 | 1031.032
7900 | 1.3144 | 111.01 | 61.843 | 0.003879 | 79.078 | 1110.1 |  | 7900 | 111.01 | 1.3144 | 61.843 | 0.003879 | 79.078 | 1110.1 | 1031.022
7901 | 1.3148 | 111.02 | 61.843 | 0.0038801 | 79.088 | 1110.1 |  | 7901 | 111.02 | 1.3148 | 61.843 | 0.0038801 | 79.088 | 1110.1 | 1031.012
7902 | 1.3152 | 111.03 | 61.843 | 0.0038811 | 79.098 | 1110.1 |  | 7902 | 111.03 | 1.3152 | 61.843 | 0.0038811 | 79.098 | 1110.1 | 1031.002
7903 | 1.3156 | 111.04 | 61.843 | 0.0038822 | 79.108 | 1110.2 |  | 7903 | 111.04 | 1.3156 | 61.843 | 0.0038822 | 79.108 | 1110.2 | 1031.092
7904 | 1.3159 | 111.05 | 61.842 | 0.0038832 | 79.118 | 1110.2 |  | 7904 | 111.05 | 1.3159 | 61.842 | 0.0038832 | 79.118 | 1110.2 | 1031.082
7905 | 1.3163 | 111.06 | 61.842 | 0.0038843 | 79.128 | 1110.2 |  | 7905 | 111.06 | 1.3163 | 61.842 | 0.0038843 | 79.128 | 1110.2 | 1031.072
7906 | 1.3167 | 111.07 | 61.842 | 0.0038853 | 79.138 | 1110.2 |  | 7906 | 111.07 | 1.3167 | 61.842 | 0.0038853 | 79.138 | 1110.2 | 1031.062
7907 | 1.3171 | 111.08 | 61.842 | 0.0038864 | 79.148 | 1110.2 |  | 7907 | 111.08 | 1.3171 | 61.842 | 0.0038864 | 79.148 | 1110.2 | 1031.052
7908 | 1.3175 | 111.09 | 61.842 | 0.0038874 | 79.158 | 1110.2 |  | 7908 | 111.09 | 1.3175 | 61.842 | 0.0038874 | 79.158 | 1110.2 | 1031.042
7909 | 1.3178 | 111.1 | 61.842 | 0.0038885 | 79.168 | 1110.2 |  | 7909 | 111.1 | 1.3178 | 61.842 | 0.0038885 | 79.168 | 1110.2 | 1031.032
7910 | 1.3182 | 111.11 | 61.842 | 0.0038895 | 79.178 | 1110.2 |  | 7910 | 111.11 | 1.3182 | 61.842 | 0.0038895 | 79.178 | 1110.2 | 1031.022
7911 | 1.3186 | 111.12 | 61.842 | 0.0038906 | 79.188 | 1110.2 |  | 7911 | 111.12 | 1.3186 | 61.842 | 0.0038906 | 79.188 | 1110.2 | 1031.012
7912 | 1.319 | 111.13 | 61.841 | 0.0038917 | 79.198 | 1110.2 |  | 7912 | 111.13 | 1.319 | 61.841 | 0.0038917 | 79.198 | 1110.2 | 1031.002
7913 | 1.3194 | 111.14 | 61.841 | 0.0038927 | 79.208 | 1110.2 |  | 7913 | 111.14 | 1.3194 | 61.841 | 0.0038927 | 79.208 | 1110.2 | 1030.992
7914 | 1.3197 | 111.15 | 61.841 | 0.0038938 | 79.218 | 1110.2 |  | 7914 | 111.15 | 1.3197 | 61.841 | 0.0038938 | 79.218 | 1110.2 | 1030.982
7915 | 1.3201 | 111.16 | 61.841 | 0.0038948 | 79.228 | 1110.2 |  | 7915 | 111.16 | 1.3201 | 61.841 | 0.0038948 | 79.228 | 1110.2 | 1030.972
7916 | 1.3205 | 111.17 | 61.841 | 0.0038959 | 79.238 | 1110.2 |  | 7916 | 111.17 | 1.3205 | 61.841 | 0.0038959 | 79.238 | 1110.2 | 1030.962
7917 | 1.3209 | 111.18 | 61.841 | 0.0038969 | 79.248 | 1110.2 |  | 7917 | 111.18 | 1.3209 | 61.841 | 0.0038969 | 79.248 | 1110.2 | 1030.952
7918 | 1.3213 | 111.19 | 61.841 | 0.003898 | 79.258 | 1110.2 |  | 7918 | 111.19 | 1.3213 | 61.841 | 0.003898 | 79.258 | 1110.2 | 1030.942
7919 | 1.3216 | 111.2 | 61.84 | 0.003899 | 79.268 | 1110.2 |  | 7919 | 111.2 | 1.3216 | 61.84 | 0.003899 | 79.268 | 1110.2 | 1030.932
7920 | 1.322 | 111.21 | 61.84 | 0.0039001 | 79.278 | 1110.2 |  | 7920 | 111.21 | 1.322 | 61.84 | 0.0039001 | 79.278 | 1110.2 | 1030.922
7921 | 1.3224 | 111.22 | 61.84 | 0.0039012 | 79.288 | 1110.2 |  | 7921 | 111.22 | 1.3224 | 61.84 | 0.0039012 | 79.288 | 1110.2 | 1030.912
7922 | 1.3228 | 111.23 | 61.84 | 0.0039022 | 79.298 | 1110.2 |  | 7922 | 111.23 | 1.3228 | 61.84 | 0.0039022 | 79.298 | 1110.2 | 1030.902
7923 | 1.3232 | 111.24 | 61.84 | 0.0039033 | 79.308 | 1110.2 |  | 7923 | 111.24 | 1.3232 | 61.84 | 0.0039033 | 79.308 | 1110.2 | 1030.892
7924 | 1.3235 | 111.25 | 61.84 | 0.0039043 | 79.318 | 1110.2 |  | 7924 | 111.25 | 1.3235 | 61.84 | 0.0039043 | 79.318 | 1110.2 | 1030.882
7925 | 1.3239 | 111.26 | 61.84 | 0.0039054 | 79.328 | 1110.2 |  | 7925 | 111.26 | 1.3239 | 61.84 | 0.0039054 | 79.328 | 1110.2 | 1030.872
7926 | 1.3243 | 111.27 | 61.839 | 0.0039064 | 79.338 | 1110.3 |  | 7926 | 111.27 | 1.3243 | 61.839 | 0.0039064 | 79.338 | 1110.3 | 1030.962
7927 | 1.3247 | 111.28 | 61.839 | 0.0039075 | 79.348 | 1110.3 |  | 7927 | 111.28 | 1.3247 | 61.839 | 0.0039075 | 79.348 | 1110.3 | 1030.952
7928 | 1.3251 | 111.29 | 61.839 | 0.0039086 | 79.358 | 1110.3 |  | 7928 | 111.29 | 1.3251 | 61.839 | 0.0039086 | 79.358 | 1110.3 | 1030.942
7929 | 1.3254 | 111.3 | 61.839 | 0.0039096 | 79.368 | 1110.3 |  | 7929 | 111.3 | 1.3254 | 61.839 | 0.0039096 | 79.368 | 1110.3 | 1030.932
7930 | 1.3258 | 111.31 | 61.839 | 0.0039107 | 79.378 | 1110.3 |  | 7930 | 111.31 | 1.3258 | 61.839 | 0.0039107 | 79.378 | 1110.3 | 1030.922
7931 | 1.3262 | 111.32 | 61.839 | 0.0039117 | 79.388 | 1110.3 |  | 7931 | 111.32 | 1.3262 | 61.839 | 0.0039117 | 79.388 | 1110.3 | 1030.912
7932 | 1.3266 | 111.33 | 61.839 | 0.0039128 | 79.398 | 1110.3 |  | 7932 | 111.33 | 1.3266 | 61.839 | 0.0039128 | 79.398 | 1110.3 | 1030.902
7933 | 1.327 | 111.34 | 61.838 | 0.0039138 | 79.408 | 1110.3 |  | 7933 | 111.34 | 1.327 | 61.838 | 0.0039138 | 79.408 | 1110.3 | 1030.892
7934 | 1.3274 | 111.35 | 61.838 | 0.0039149 | 79.418 | 1110.3 |  | 7934 | 111.35 | 1.3274 | 61.838 | 0.0039149 | 79.418 | 1110.3 | 1030.882
7935 | 1.3277 | 111.36 | 61.838 | 0.003916 | 79.428 | 1110.3 |  | 7935 | 111.36 | 1.3277 | 61.838 | 0.003916 | 79.428 | 1110.3 | 1030.872
7936 | 1.3281 | 111.37 | 61.838 | 0.003917 | 79.438 | 1110.3 |  | 7936 | 111.37 | 1.3281 | 61.838 | 0.003917 | 79.438 | 1110.3 | 1030.862
7937 | 1.3285 | 111.38 | 61.838 | 0.0039181 | 79.448 | 1110.3 |  | 7937 | 111.38 | 1.3285 | 61.838 | 0.0039181 | 79.448 | 1110.3 | 1030.852
7938 | 1.3289 | 111.39 | 61.838 | 0.0039191 | 79.458 | 1110.3 |  | 7938 | 111.39 | 1.3289 | 61.838 | 0.0039191 | 79.458 | 1110.3 | 1030.842
7939 | 1.3293 | 111.4 | 61.838 | 0.0039202 | 79.468 | 1110.3 |  | 7939 | 111.4 | 1.3293 | 61.838 | 0.0039202 | 79.468 | 1110.3 | 1030.832
7940 | 1.3296 | 111.41 | 61.837 | 0.0039213 | 79.478 | 1110.3 |  | 7940 | 111.41 | 1.3296 | 61.837 | 0.0039213 | 79.478 | 1110.3 | 1030.822
7941 | 1.33 | 111.42 | 61.837 | 0.0039223 | 79.488 | 1110.3 |  | 7941 | 111.42 | 1.33 | 61.837 | 0.0039223 | 79.488 | 1110.3 | 1030.812
7942 | 1.3304 | 111.43 | 61.837 | 0.0039234 | 79.498 | 1110.3 |  | 7942 | 111.43 | 1.3304 | 61.837 | 0.0039234 | 79.498 | 1110.3 | 1030.802
7943 | 1.3308 | 111.44 | 61.837 | 0.0039245 | 79.508 | 1110.3 |  | 7943 | 111.44 | 1.3308 | 61.837 | 0.0039245 | 79.508 | 1110.3 | 1030.792
7944 | 1.3312 | 111.45 | 61.837 | 0.0039255 | 79.518 | 1110.3 |  | 7944 | 111.45 | 1.3312 | 61.837 | 0.0039255 | 79.518 | 1110.3 | 1030.782
7945 | 1.3316 | 111.46 | 61.837 | 0.0039266 | 79.528 | 1110.3 |  | 7945 | 111.46 | 1.3316 | 61.837 | 0.0039266 | 79.528 | 1110.3 | 1030.772
7946 | 1.3319 | 111.47 | 61.837 | 0.0039276 | 79.538 | 1110.3 |  | 7946 | 111.47 | 1.3319 | 61.837 | 0.0039276 | 79.538 | 1110.3 | 1030.762
7947 | 1.3323 | 111.48 | 61.836 | 0.0039287 | 79.548 | 1110.3 |  | 7947 | 111.48 | 1.3323 | 61.836 | 0.0039287 | 79.548 | 1110.3 | 1030.752
7948 | 1.3327 | 111.49 | 61.836 | 0.0039298 | 79.558 | 1110.3 |  | 7948 | 111.49 | 1.3327 | 61.836 | 0.0039298 | 79.558 | 1110.3 | 1030.742
7949 | 1.3331 | 111.5 | 61.836 | 0.0039308 | 79.568 | 1110.3 |  | 7949 | 111.5 | 1.3331 | 61.836 | 0.0039308 | 79.568 | 1110.3 | 1030.732
7950 | 1.3335 | 111.51 | 61.836 | 0.0039319 | 79.578 | 1110.4 |  | 7950 | 111.51 | 1.3335 | 61.836 | 0.0039319 | 79.578 | 1110.4 | 1030.822
7951 | 1.3339 | 111.52 | 61.836 | 0.003933 | 79.588 | 1110.4 |  | 7951 | 111.52 | 1.3339 | 61.836 | 0.003933 | 79.588 | 1110.4 | 1030.812
7952 | 1.3342 | 111.53 | 61.836 | 0.003934 | 79.598 | 1110.4 |  | 7952 | 111.53 | 1.3342 | 61.836 | 0.003934 | 79.598 | 1110.4 | 1030.802
7953 | 1.3346 | 111.54 | 61.836 | 0.0039351 | 79.608 | 1110.4 |  | 7953 | 111.54 | 1.3346 | 61.836 | 0.0039351 | 79.608 | 1110.4 | 1030.792
7954 | 1.335 | 111.55 | 61.835 | 0.0039361 | 79.618 | 1110.4 |  | 7954 | 111.55 | 1.335 | 61.835 | 0.0039361 | 79.618 | 1110.4 | 1030.782
7955 | 1.3354 | 111.56 | 61.835 | 0.0039372 | 79.628 | 1110.4 |  | 7955 | 111.56 | 1.3354 | 61.835 | 0.0039372 | 79.628 | 1110.4 | 1030.772
7956 | 1.3358 | 111.57 | 61.835 | 0.0039383 | 79.638 | 1110.4 |  | 7956 | 111.57 | 1.3358 | 61.835 | 0.0039383 | 79.638 | 1110.4 | 1030.762
7957 | 1.3362 | 111.58 | 61.835 | 0.0039393 | 79.648 | 1110.4 |  | 7957 | 111.58 | 1.3362 | 61.835 | 0.0039393 | 79.648 | 1110.4 | 1030.752
7958 | 1.3365 | 111.59 | 61.835 | 0.0039404 | 79.658 | 1110.4 |  | 7958 | 111.59 | 1.3365 | 61.835 | 0.0039404 | 79.658 | 1110.4 | 1030.742
7959 | 1.3369 | 111.6 | 61.835 | 0.0039415 | 79.668 | 1110.4 |  | 7959 | 111.6 | 1.3369 | 61.835 | 0.0039415 | 79.668 | 1110.4 | 1030.732
7960 | 1.3373 | 111.61 | 61.835 | 0.0039425 | 79.678 | 1110.4 |  | 7960 | 111.61 | 1.3373 | 61.835 | 0.0039425 | 79.678 | 1110.4 | 1030.722
7961 | 1.3377 | 111.62 | 61.834 | 0.0039436 | 79.688 | 1110.4 |  | 7961 | 111.62 | 1.3377 | 61.834 | 0.0039436 | 79.688 | 1110.4 | 1030.712
7962 | 1.3381 | 111.63 | 61.834 | 0.0039447 | 79.698 | 1110.4 |  | 7962 | 111.63 | 1.3381 | 61.834 | 0.0039447 | 79.698 | 1110.4 | 1030.702
7963 | 1.3385 | 111.64 | 61.834 | 0.0039457 | 79.708 | 1110.4 |  | 7963 | 111.64 | 1.3385 | 61.834 | 0.0039457 | 79.708 | 1110.4 | 1030.692
7964 | 1.3388 | 111.65 | 61.834 | 0.0039468 | 79.718 | 1110.4 |  | 7964 | 111.65 | 1.3388 | 61.834 | 0.0039468 | 79.718 | 1110.4 | 1030.682
7965 | 1.3392 | 111.66 | 61.834 | 0.0039479 | 79.728 | 1110.4 |  | 7965 | 111.66 | 1.3392 | 61.834 | 0.0039479 | 79.728 | 1110.4 | 1030.672
7966 | 1.3396 | 111.67 | 61.834 | 0.0039489 | 79.738 | 1110.4 |  | 7966 | 111.67 | 1.3396 | 61.834 | 0.0039489 | 79.738 | 1110.4 | 1030.662
7967 | 1.34 | 111.68 | 61.833 | 0.00395 | 79.748 | 1110.4 |  | 7967 | 111.68 | 1.34 | 61.833 | 0.00395 | 79.748 | 1110.4 | 1030.652
7968 | 1.3404 | 111.69 | 61.833 | 0.0039511 | 79.758 | 1110.4 |  | 7968 | 111.69 | 1.3404 | 61.833 | 0.0039511 | 79.758 | 1110.4 | 1030.642
7969 | 1.3408 | 111.7 | 61.833 | 0.0039521 | 79.768 | 1110.4 |  | 7969 | 111.7 | 1.3408 | 61.833 | 0.0039521 | 79.768 | 1110.4 | 1030.632
7970 | 1.3412 | 111.71 | 61.833 | 0.0039532 | 79.778 | 1110.4 |  | 7970 | 111.71 | 1.3412 | 61.833 | 0.0039532 | 79.778 | 1110.4 | 1030.622
7971 | 1.3415 | 111.72 | 61.833 | 0.0039543 | 79.788 | 1110.4 |  | 7971 | 111.72 | 1.3415 | 61.833 | 0.0039543 | 79.788 | 1110.4 | 1030.612
7972 | 1.3419 | 111.73 | 61.833 | 0.0039553 | 79.798 | 1110.4 |  | 7972 | 111.73 | 1.3419 | 61.833 | 0.0039553 | 79.798 | 1110.4 | 1030.602
7973 | 1.3423 | 111.74 | 61.833 | 0.0039564 | 79.808 | 1110.5 |  | 7973 | 111.74 | 1.3423 | 61.833 | 0.0039564 | 79.808 | 1110.5 | 1030.692
7974 | 1.3427 | 111.75 | 61.832 | 0.0039575 | 79.818 | 1110.5 |  | 7974 | 111.75 | 1.3427 | 61.832 | 0.0039575 | 79.818 | 1110.5 | 1030.682
7975 | 1.3431 | 111.76 | 61.832 | 0.0039586 | 79.828 | 1110.5 |  | 7975 | 111.76 | 1.3431 | 61.832 | 0.0039586 | 79.828 | 1110.5 | 1030.672
7976 | 1.3435 | 111.77 | 61.832 | 0.0039596 | 79.838 | 1110.5 |  | 7976 | 111.77 | 1.3435 | 61.832 | 0.0039596 | 79.838 | 1110.5 | 1030.662
7977 | 1.3439 | 111.78 | 61.832 | 0.0039607 | 79.848 | 1110.5 |  | 7977 | 111.78 | 1.3439 | 61.832 | 0.0039607 | 79.848 | 1110.5 | 1030.652
7978 | 1.3442 | 111.79 | 61.832 | 0.0039618 | 79.858 | 1110.5 |  | 7978 | 111.79 | 1.3442 | 61.832 | 0.0039618 | 79.858 | 1110.5 | 1030.642
7979 | 1.3446 | 111.8 | 61.832 | 0.0039628 | 79.868 | 1110.5 |  | 7979 | 111.8 | 1.3446 | 61.832 | 0.0039628 | 79.868 | 1110.5 | 1030.632
7980 | 1.345 | 111.81 | 61.832 | 0.0039639 | 79.878 | 1110.5 |  | 7980 | 111.81 | 1.345 | 61.832 | 0.0039639 | 79.878 | 1110.5 | 1030.622
7981 | 1.3454 | 111.82 | 61.831 | 0.003965 | 79.888 | 1110.5 |  | 7981 | 111.82 | 1.3454 | 61.831 | 0.003965 | 79.888 | 1110.5 | 1030.612
7982 | 1.3458 | 111.83 | 61.831 | 0.003966 | 79.898 | 1110.5 |  | 7982 | 111.83 | 1.3458 | 61.831 | 0.003966 | 79.898 | 1110.5 | 1030.602
7983 | 1.3462 | 111.84 | 61.831 | 0.0039671 | 79.907 | 1110.5 |  | 7983 | 111.84 | 1.3462 | 61.831 | 0.0039671 | 79.907 | 1110.5 | 1030.593
7984 | 1.3466 | 111.85 | 61.831 | 0.0039682 | 79.917 | 1110.5 |  | 7984 | 111.85 | 1.3466 | 61.831 | 0.0039682 | 79.917 | 1110.5 | 1030.583
7985 | 1.3469 | 111.86 | 61.831 | 0.0039693 | 79.927 | 1110.5 |  | 7985 | 111.86 | 1.3469 | 61.831 | 0.0039693 | 79.927 | 1110.5 | 1030.573
7986 | 1.3473 | 111.87 | 61.831 | 0.0039703 | 79.937 | 1110.5 |  | 7986 | 111.87 | 1.3473 | 61.831 | 0.0039703 | 79.937 | 1110.5 | 1030.563
7987 | 1.3477 | 111.88 | 61.831 | 0.0039714 | 79.947 | 1110.5 |  | 7987 | 111.88 | 1.3477 | 61.831 | 0.0039714 | 79.947 | 1110.5 | 1030.553
7988 | 1.3481 | 111.89 | 61.83 | 0.0039725 | 79.957 | 1110.5 |  | 7988 | 111.89 | 1.3481 | 61.83 | 0.0039725 | 79.957 | 1110.5 | 1030.543
7989 | 1.3485 | 111.9 | 61.83 | 0.0039736 | 79.967 | 1110.5 |  | 7989 | 111.9 | 1.3485 | 61.83 | 0.0039736 | 79.967 | 1110.5 | 1030.533
7990 | 1.3489 | 111.91 | 61.83 | 0.0039746 | 79.977 | 1110.5 |  | 7990 | 111.91 | 1.3489 | 61.83 | 0.0039746 | 79.977 | 1110.5 | 1030.523
7991 | 1.3493 | 111.92 | 61.83 | 0.0039757 | 79.987 | 1110.5 |  | 7991 | 111.92 | 1.3493 | 61.83 | 0.0039757 | 79.987 | 1110.5 | 1030.513
7992 | 1.3497 | 111.93 | 61.83 | 0.0039768 | 79.997 | 1110.5 |  | 7992 | 111.93 | 1.3497 | 61.83 | 0.0039768 | 79.997 | 1110.5 | 1030.503
7993 | 1.35 | 111.94 | 61.83 | 0.0039778 | 80.007 | 1110.5 |  | 7993 | 111.94 | 1.35 | 61.83 | 0.0039778 | 80.007 | 1110.5 | 1030.493
7994 | 1.3504 | 111.95 | 61.83 | 0.0039789 | 80.017 | 1110.5 |  | 7994 | 111.95 | 1.3504 | 61.83 | 0.0039789 | 80.017 | 1110.5 | 1030.483
7995 | 1.3508 | 111.96 | 61.829 | 0.00398 | 80.027 | 1110.5 |  | 7995 | 111.96 | 1.3508 | 61.829 | 0.00398 | 80.027 | 1110.5 | 1030.473
7996 | 1.3512 | 111.97 | 61.829 | 0.0039811 | 80.037 | 1110.5 |  | 7996 | 111.97 | 1.3512 | 61.829 | 0.0039811 | 80.037 | 1110.5 | 1030.463
7997 | 1.3516 | 111.98 | 61.829 | 0.0039821 | 80.047 | 1110.6 |  | 7997 | 111.98 | 1.3516 | 61.829 | 0.0039821 | 80.047 | 1110.6 | 1030.553
7998 | 1.352 | 111.99 | 61.829 | 0.0039832 | 80.057 | 1110.6 |  | 7998 | 111.99 | 1.352 | 61.829 | 0.0039832 | 80.057 | 1110.6 | 1030.543
7999 | 1.3524 | 112 | 61.829 | 0.0039843 | 80.067 | 1110.6 |  | 7999 | 112 | 1.3524 | 61.829 | 0.0039843 | 80.067 | 1110.6 | 1030.533
8000 | 1.3528 | 112.01 | 61.829 | 0.0039854 | 80.077 | 1110.6 |  | 8000 | 112.01 | 1.3528 | 61.829 | 0.0039854 | 80.077 | 1110.6 | 1030.523
8001 | 1.3531 | 112.02 | 61.829 | 0.0039864 | 80.087 | 1110.6 |  | 8001 | 112.02 | 1.3531 | 61.829 | 0.0039864 | 80.087 | 1110.6 | 1030.513
8002 | 1.3535 | 112.03 | 61.828 | 0.0039875 | 80.097 | 1110.6 |  | 8002 | 112.03 | 1.3535 | 61.828 | 0.0039875 | 80.097 | 1110.6 | 1030.503
8003 | 1.3539 | 112.04 | 61.828 | 0.0039886 | 80.107 | 1110.6 |  | 8003 | 112.04 | 1.3539 | 61.828 | 0.0039886 | 80.107 | 1110.6 | 1030.493
8004 | 1.3543 | 112.05 | 61.828 | 0.0039897 | 80.117 | 1110.6 |  | 8004 | 112.05 | 1.3543 | 61.828 | 0.0039897 | 80.117 | 1110.6 | 1030.483
8005 | 1.3547 | 112.06 | 61.828 | 0.0039908 | 80.127 | 1110.6 |  | 8005 | 112.06 | 1.3547 | 61.828 | 0.0039908 | 80.127 | 1110.6 | 1030.473
8006 | 1.3551 | 112.07 | 61.828 | 0.0039918 | 80.137 | 1110.6 |  | 8006 | 112.07 | 1.3551 | 61.828 | 0.0039918 | 80.137 | 1110.6 | 1030.463
8007 | 1.3555 | 112.08 | 61.828 | 0.0039929 | 80.147 | 1110.6 |  | 8007 | 112.08 | 1.3555 | 61.828 | 0.0039929 | 80.147 | 1110.6 | 1030.453
8008 | 1.3559 | 112.09 | 61.828 | 0.003994 | 80.157 | 1110.6 |  | 8008 | 112.09 | 1.3559 | 61.828 | 0.003994 | 80.157 | 1110.6 | 1030.443
8009 | 1.3563 | 112.1 | 61.827 | 0.0039951 | 80.167 | 1110.6 |  | 8009 | 112.1 | 1.3563 | 61.827 | 0.0039951 | 80.167 | 1110.6 | 1030.433
8010 | 1.3566 | 112.11 | 61.827 | 0.0039961 | 80.177 | 1110.6 |  | 8010 | 112.11 | 1.3566 | 61.827 | 0.0039961 | 80.177 | 1110.6 | 1030.423
8011 | 1.357 | 112.12 | 61.827 | 0.0039972 | 80.187 | 1110.6 |  | 8011 | 112.12 | 1.357 | 61.827 | 0.0039972 | 80.187 | 1110.6 | 1030.413
8012 | 1.3574 | 112.13 | 61.827 | 0.0039983 | 80.197 | 1110.6 |  | 8012 | 112.13 | 1.3574 | 61.827 | 0.0039983 | 80.197 | 1110.6 | 1030.403
8013 | 1.3578 | 112.14 | 61.827 | 0.0039994 | 80.207 | 1110.6 |  | 8013 | 112.14 | 1.3578 | 61.827 | 0.0039994 | 80.207 | 1110.6 | 1030.393
8014 | 1.3582 | 112.15 | 61.827 | 0.0040005 | 80.217 | 1110.6 |  | 8014 | 112.15 | 1.3582 | 61.827 | 0.0040005 | 80.217 | 1110.6 | 1030.383
8015 | 1.3586 | 112.16 | 61.827 | 0.0040015 | 80.227 | 1110.6 |  | 8015 | 112.16 | 1.3586 | 61.827 | 0.0040015 | 80.227 | 1110.6 | 1030.373
8016 | 1.359 | 112.17 | 61.826 | 0.0040026 | 80.237 | 1110.6 |  | 8016 | 112.17 | 1.359 | 61.826 | 0.0040026 | 80.237 | 1110.6 | 1030.363
8017 | 1.3594 | 112.18 | 61.826 | 0.0040037 | 80.247 | 1110.6 |  | 8017 | 112.18 | 1.3594 | 61.826 | 0.0040037 | 80.247 | 1110.6 | 1030.353
8018 | 1.3598 | 112.19 | 61.826 | 0.0040048 | 80.257 | 1110.6 |  | 8018 | 112.19 | 1.3598 | 61.826 | 0.0040048 | 80.257 | 1110.6 | 1030.343
8019 | 1.3601 | 112.2 | 61.826 | 0.0040059 | 80.267 | 1110.6 |  | 8019 | 112.2 | 1.3601 | 61.826 | 0.0040059 | 80.267 | 1110.6 | 1030.333
8020 | 1.3605 | 112.21 | 61.826 | 0.0040069 | 80.277 | 1110.7 |  | 8020 | 112.21 | 1.3605 | 61.826 | 0.0040069 | 80.277 | 1110.7 | 1030.423
8021 | 1.3609 | 112.22 | 61.826 | 0.004008 | 80.287 | 1110.7 |  | 8021 | 112.22 | 1.3609 | 61.826 | 0.004008 | 80.287 | 1110.7 | 1030.413
8022 | 1.3613 | 112.23 | 61.826 | 0.0040091 | 80.297 | 1110.7 |  | 8022 | 112.23 | 1.3613 | 61.826 | 0.0040091 | 80.297 | 1110.7 | 1030.403
8023 | 1.3617 | 112.24 | 61.825 | 0.0040102 | 80.307 | 1110.7 |  | 8023 | 112.24 | 1.3617 | 61.825 | 0.0040102 | 80.307 | 1110.7 | 1030.393
8024 | 1.3621 | 112.25 | 61.825 | 0.0040113 | 80.317 | 1110.7 |  | 8024 | 112.25 | 1.3621 | 61.825 | 0.0040113 | 80.317 | 1110.7 | 1030.383
8025 | 1.3625 | 112.26 | 61.825 | 0.0040123 | 80.327 | 1110.7 |  | 8025 | 112.26 | 1.3625 | 61.825 | 0.0040123 | 80.327 | 1110.7 | 1030.373
8026 | 1.3629 | 112.27 | 61.825 | 0.0040134 | 80.337 | 1110.7 |  | 8026 | 112.27 | 1.3629 | 61.825 | 0.0040134 | 80.337 | 1110.7 | 1030.363
8027 | 1.3633 | 112.28 | 61.825 | 0.0040145 | 80.347 | 1110.7 |  | 8027 | 112.28 | 1.3633 | 61.825 | 0.0040145 | 80.347 | 1110.7 | 1030.353
8028 | 1.3637 | 112.29 | 61.825 | 0.0040156 | 80.357 | 1110.7 |  | 8028 | 112.29 | 1.3637 | 61.825 | 0.0040156 | 80.357 | 1110.7 | 1030.343
8029 | 1.364 | 112.3 | 61.825 | 0.0040167 | 80.367 | 1110.7 |  | 8029 | 112.3 | 1.364 | 61.825 | 0.0040167 | 80.367 | 1110.7 | 1030.333
8030 | 1.3644 | 112.31 | 61.824 | 0.0040178 | 80.377 | 1110.7 |  | 8030 | 112.31 | 1.3644 | 61.824 | 0.0040178 | 80.377 | 1110.7 | 1030.323
8031 | 1.3648 | 112.32 | 61.824 | 0.0040188 | 80.387 | 1110.7 |  | 8031 | 112.32 | 1.3648 | 61.824 | 0.0040188 | 80.387 | 1110.7 | 1030.313
8032 | 1.3652 | 112.33 | 61.824 | 0.0040199 | 80.397 | 1110.7 |  | 8032 | 112.33 | 1.3652 | 61.824 | 0.0040199 | 80.397 | 1110.7 | 1030.303
8033 | 1.3656 | 112.34 | 61.824 | 0.004021 | 80.407 | 1110.7 |  | 8033 | 112.34 | 1.3656 | 61.824 | 0.004021 | 80.407 | 1110.7 | 1030.293
8034 | 1.366 | 112.35 | 61.824 | 0.0040221 | 80.417 | 1110.7 |  | 8034 | 112.35 | 1.366 | 61.824 | 0.0040221 | 80.417 | 1110.7 | 1030.283
8035 | 1.3664 | 112.36 | 61.824 | 0.0040232 | 80.427 | 1110.7 |  | 8035 | 112.36 | 1.3664 | 61.824 | 0.0040232 | 80.427 | 1110.7 | 1030.273
8036 | 1.3668 | 112.37 | 61.824 | 0.0040243 | 80.437 | 1110.7 |  | 8036 | 112.37 | 1.3668 | 61.824 | 0.0040243 | 80.437 | 1110.7 | 1030.263
8037 | 1.3672 | 112.38 | 61.823 | 0.0040253 | 80.447 | 1110.7 |  | 8037 | 112.38 | 1.3672 | 61.823 | 0.0040253 | 80.447 | 1110.7 | 1030.253
8038 | 1.3676 | 112.39 | 61.823 | 0.0040264 | 80.457 | 1110.7 |  | 8038 | 112.39 | 1.3676 | 61.823 | 0.0040264 | 80.457 | 1110.7 | 1030.243
8039 | 1.368 | 112.4 | 61.823 | 0.0040275 | 80.467 | 1110.7 |  | 8039 | 112.4 | 1.368 | 61.823 | 0.0040275 | 80.467 | 1110.7 | 1030.233
8040 | 1.3684 | 112.41 | 61.823 | 0.0040286 | 80.477 | 1110.7 |  | 8040 | 112.41 | 1.3684 | 61.823 | 0.0040286 | 80.477 | 1110.7 | 1030.223
8041 | 1.3687 | 112.42 | 61.823 | 0.0040297 | 80.487 | 1110.7 |  | 8041 | 112.42 | 1.3687 | 61.823 | 0.0040297 | 80.487 | 1110.7 | 1030.213
8042 | 1.3691 | 112.43 | 61.823 | 0.0040308 | 80.497 | 1110.7 |  | 8042 | 112.43 | 1.3691 | 61.823 | 0.0040308 | 80.497 | 1110.7 | 1030.203
8043 | 1.3695 | 112.44 | 61.823 | 0.0040319 | 80.507 | 1110.7 |  | 8043 | 112.44 | 1.3695 | 61.823 | 0.0040319 | 80.507 | 1110.7 | 1030.193
8044 | 1.3699 | 112.45 | 61.822 | 0.0040329 | 80.517 | 1110.8 |  | 8044 | 112.45 | 1.3699 | 61.822 | 0.0040329 | 80.517 | 1110.8 | 1030.283
8045 | 1.3703 | 112.46 | 61.822 | 0.004034 | 80.527 | 1110.8 |  | 8045 | 112.46 | 1.3703 | 61.822 | 0.004034 | 80.527 | 1110.8 | 1030.273
8046 | 1.3707 | 112.47 | 61.822 | 0.0040351 | 80.537 | 1110.8 |  | 8046 | 112.47 | 1.3707 | 61.822 | 0.0040351 | 80.537 | 1110.8 | 1030.263
8047 | 1.3711 | 112.48 | 61.822 | 0.0040362 | 80.547 | 1110.8 |  | 8047 | 112.48 | 1.3711 | 61.822 | 0.0040362 | 80.547 | 1110.8 | 1030.253
8048 | 1.3715 | 112.49 | 61.822 | 0.0040373 | 80.557 | 1110.8 |  | 8048 | 112.49 | 1.3715 | 61.822 | 0.0040373 | 80.557 | 1110.8 | 1030.243
8049 | 1.3719 | 112.5 | 61.822 | 0.0040384 | 80.567 | 1110.8 |  | 8049 | 112.5 | 1.3719 | 61.822 | 0.0040384 | 80.567 | 1110.8 | 1030.233
8050 | 1.3723 | 112.51 | 61.822 | 0.0040395 | 80.577 | 1110.8 |  | 8050 | 112.51 | 1.3723 | 61.822 | 0.0040395 | 80.577 | 1110.8 | 1030.223
8051 | 1.3727 | 112.52 | 61.821 | 0.0040406 | 80.587 | 1110.8 |  | 8051 | 112.52 | 1.3727 | 61.821 | 0.0040406 | 80.587 | 1110.8 | 1030.213
8052 | 1.3731 | 112.53 | 61.821 | 0.0040416 | 80.597 | 1110.8 |  | 8052 | 112.53 | 1.3731 | 61.821 | 0.0040416 | 80.597 | 1110.8 | 1030.203
8053 | 1.3735 | 112.54 | 61.821 | 0.0040427 | 80.607 | 1110.8 |  | 8053 | 112.54 | 1.3735 | 61.821 | 0.0040427 | 80.607 | 1110.8 | 1030.193
8054 | 1.3738 | 112.55 | 61.821 | 0.0040438 | 80.617 | 1110.8 |  | 8054 | 112.55 | 1.3738 | 61.821 | 0.0040438 | 80.617 | 1110.8 | 1030.183
8055 | 1.3742 | 112.56 | 61.821 | 0.0040449 | 80.627 | 1110.8 |  | 8055 | 112.56 | 1.3742 | 61.821 | 0.0040449 | 80.627 | 1110.8 | 1030.173
8056 | 1.3746 | 112.57 | 61.821 | 0.004046 | 80.637 | 1110.8 |  | 8056 | 112.57 | 1.3746 | 61.821 | 0.004046 | 80.637 | 1110.8 | 1030.163
8057 | 1.375 | 112.58 | 61.821 | 0.0040471 | 80.647 | 1110.8 |  | 8057 | 112.58 | 1.375 | 61.821 | 0.0040471 | 80.647 | 1110.8 | 1030.153
8058 | 1.3754 | 112.59 | 61.82 | 0.0040482 | 80.657 | 1110.8 |  | 8058 | 112.59 | 1.3754 | 61.82 | 0.0040482 | 80.657 | 1110.8 | 1030.143
8059 | 1.3758 | 112.6 | 61.82 | 0.0040493 | 80.667 | 1110.8 |  | 8059 | 112.6 | 1.3758 | 61.82 | 0.0040493 | 80.667 | 1110.8 | 1030.133
8060 | 1.3762 | 112.61 | 61.82 | 0.0040504 | 80.677 | 1110.8 |  | 8060 | 112.61 | 1.3762 | 61.82 | 0.0040504 | 80.677 | 1110.8 | 1030.123
8061 | 1.3766 | 112.62 | 61.82 | 0.0040514 | 80.687 | 1110.8 |  | 8061 | 112.62 | 1.3766 | 61.82 | 0.0040514 | 80.687 | 1110.8 | 1030.113
8062 | 1.377 | 112.63 | 61.82 | 0.0040525 | 80.697 | 1110.8 |  | 8062 | 112.63 | 1.377 | 61.82 | 0.0040525 | 80.697 | 1110.8 | 1030.103
8063 | 1.3774 | 112.64 | 61.82 | 0.0040536 | 80.707 | 1110.8 |  | 8063 | 112.64 | 1.3774 | 61.82 | 0.0040536 | 80.707 | 1110.8 | 1030.093
8064 | 1.3778 | 112.65 | 61.82 | 0.0040547 | 80.717 | 1110.8 |  | 8064 | 112.65 | 1.3778 | 61.82 | 0.0040547 | 80.717 | 1110.8 | 1030.083
8065 | 1.3782 | 112.66 | 61.819 | 0.0040558 | 80.727 | 1110.8 |  | 8065 | 112.66 | 1.3782 | 61.819 | 0.0040558 | 80.727 | 1110.8 | 1030.073
8066 | 1.3786 | 112.67 | 61.819 | 0.0040569 | 80.737 | 1110.8 |  | 8066 | 112.67 | 1.3786 | 61.819 | 0.0040569 | 80.737 | 1110.8 | 1030.063
8067 | 1.379 | 112.68 | 61.819 | 0.004058 | 80.747 | 1110.9 |  | 8067 | 112.68 | 1.379 | 61.819 | 0.004058 | 80.747 | 1110.9 | 1030.153
8068 | 1.3794 | 112.69 | 61.819 | 0.0040591 | 80.757 | 1110.9 |  | 8068 | 112.69 | 1.3794 | 61.819 | 0.0040591 | 80.757 | 1110.9 | 1030.143
8069 | 1.3798 | 112.7 | 61.819 | 0.0040602 | 80.767 | 1110.9 |  | 8069 | 112.7 | 1.3798 | 61.819 | 0.0040602 | 80.767 | 1110.9 | 1030.133
8070 | 1.3801 | 112.71 | 61.819 | 0.0040613 | 80.777 | 1110.9 |  | 8070 | 112.71 | 1.3801 | 61.819 | 0.0040613 | 80.777 | 1110.9 | 1030.123
8071 | 1.3805 | 112.72 | 61.819 | 0.0040624 | 80.787 | 1110.9 |  | 8071 | 112.72 | 1.3805 | 61.819 | 0.0040624 | 80.787 | 1110.9 | 1030.113
8072 | 1.3809 | 112.73 | 61.818 | 0.0040635 | 80.797 | 1110.9 |  | 8072 | 112.73 | 1.3809 | 61.818 | 0.0040635 | 80.797 | 1110.9 | 1030.103
8073 | 1.3813 | 112.74 | 61.818 | 0.0040646 | 80.807 | 1110.9 |  | 8073 | 112.74 | 1.3813 | 61.818 | 0.0040646 | 80.807 | 1110.9 | 1030.093
8074 | 1.3817 | 112.75 | 61.818 | 0.0040657 | 80.817 | 1110.9 |  | 8074 | 112.75 | 1.3817 | 61.818 | 0.0040657 | 80.817 | 1110.9 | 1030.083
8075 | 1.3821 | 112.76 | 61.818 | 0.0040667 | 80.827 | 1110.9 |  | 8075 | 112.76 | 1.3821 | 61.818 | 0.0040667 | 80.827 | 1110.9 | 1030.073
8076 | 1.3825 | 112.77 | 61.818 | 0.0040678 | 80.837 | 1110.9 |  | 8076 | 112.77 | 1.3825 | 61.818 | 0.0040678 | 80.837 | 1110.9 | 1030.063
8077 | 1.3829 | 112.78 | 61.818 | 0.0040689 | 80.847 | 1110.9 |  | 8077 | 112.78 | 1.3829 | 61.818 | 0.0040689 | 80.847 | 1110.9 | 1030.053
8078 | 1.3833 | 112.79 | 61.818 | 0.00407 | 80.857 | 1110.9 |  | 8078 | 112.79 | 1.3833 | 61.818 | 0.00407 | 80.857 | 1110.9 | 1030.043
8079 | 1.3837 | 112.8 | 61.817 | 0.0040711 | 80.867 | 1110.9 |  | 8079 | 112.8 | 1.3837 | 61.817 | 0.0040711 | 80.867 | 1110.9 | 1030.033
8080 | 1.3841 | 112.81 | 61.817 | 0.0040722 | 80.877 | 1110.9 |  | 8080 | 112.81 | 1.3841 | 61.817 | 0.0040722 | 80.877 | 1110.9 | 1030.023
8081 | 1.3845 | 112.82 | 61.817 | 0.0040733 | 80.887 | 1110.9 |  | 8081 | 112.82 | 1.3845 | 61.817 | 0.0040733 | 80.887 | 1110.9 | 1030.013
8082 | 1.3849 | 112.83 | 61.817 | 0.0040744 | 80.897 | 1110.9 |  | 8082 | 112.83 | 1.3849 | 61.817 | 0.0040744 | 80.897 | 1110.9 | 1030.003
8083 | 1.3853 | 112.84 | 61.817 | 0.0040755 | 80.907 | 1110.9 |  | 8083 | 112.84 | 1.3853 | 61.817 | 0.0040755 | 80.907 | 1110.9 | 1029.993
8084 | 1.3857 | 112.85 | 61.817 | 0.0040766 | 80.917 | 1110.9 |  | 8084 | 112.85 | 1.3857 | 61.817 | 0.0040766 | 80.917 | 1110.9 | 1029.983
8085 | 1.3861 | 112.86 | 61.816 | 0.0040777 | 80.927 | 1110.9 |  | 8085 | 112.86 | 1.3861 | 61.816 | 0.0040777 | 80.927 | 1110.9 | 1029.973
8086 | 1.3865 | 112.87 | 61.816 | 0.0040788 | 80.937 | 1110.9 |  | 8086 | 112.87 | 1.3865 | 61.816 | 0.0040788 | 80.937 | 1110.9 | 1029.963
8087 | 1.3869 | 112.88 | 61.816 | 0.0040799 | 80.947 | 1110.9 |  | 8087 | 112.88 | 1.3869 | 61.816 | 0.0040799 | 80.947 | 1110.9 | 1029.953
8088 | 1.3873 | 112.89 | 61.816 | 0.004081 | 80.957 | 1110.9 |  | 8088 | 112.89 | 1.3873 | 61.816 | 0.004081 | 80.957 | 1110.9 | 1029.943
8089 | 1.3877 | 112.9 | 61.816 | 0.0040821 | 80.967 | 1110.9 |  | 8089 | 112.9 | 1.3877 | 61.816 | 0.0040821 | 80.967 | 1110.9 | 1029.933
8090 | 1.3881 | 112.91 | 61.816 | 0.0040832 | 80.977 | 1110.9 |  | 8090 | 112.91 | 1.3881 | 61.816 | 0.0040832 | 80.977 | 1110.9 | 1029.923
8091 | 1.3885 | 112.92 | 61.816 | 0.0040843 | 80.987 | 1111 |  | 8091 | 112.92 | 1.3885 | 61.816 | 0.0040843 | 80.987 | 1111 | 1030.013
8092 | 1.3889 | 112.93 | 61.815 | 0.0040854 | 80.997 | 1111 |  | 8092 | 112.93 | 1.3889 | 61.815 | 0.0040854 | 80.997 | 1111 | 1030.003
8093 | 1.3893 | 112.94 | 61.815 | 0.0040865 | 81.007 | 1111 |  | 8093 | 112.94 | 1.3893 | 61.815 | 0.0040865 | 81.007 | 1111 | 1029.993
8094 | 1.3897 | 112.95 | 61.815 | 0.0040876 | 81.017 | 1111 |  | 8094 | 112.95 | 1.3897 | 61.815 | 0.0040876 | 81.017 | 1111 | 1029.983
8095 | 1.39 | 112.96 | 61.815 | 0.0040887 | 81.027 | 1111 |  | 8095 | 112.96 | 1.39 | 61.815 | 0.0040887 | 81.027 | 1111 | 1029.973
8096 | 1.3904 | 112.97 | 61.815 | 0.0040898 | 81.037 | 1111 |  | 8096 | 112.97 | 1.3904 | 61.815 | 0.0040898 | 81.037 | 1111 | 1029.963
8097 | 1.3908 | 112.98 | 61.815 | 0.0040909 | 81.047 | 1111 |  | 8097 | 112.98 | 1.3908 | 61.815 | 0.0040909 | 81.047 | 1111 | 1029.953
8098 | 1.3912 | 112.99 | 61.815 | 0.004092 | 81.057 | 1111 |  | 8098 | 112.99 | 1.3912 | 61.815 | 0.004092 | 81.057 | 1111 | 1029.943
8099 | 1.3916 | 113 | 61.814 | 0.0040931 | 81.067 | 1111 |  | 8099 | 113 | 1.3916 | 61.814 | 0.0040931 | 81.067 | 1111 | 1029.933
8100 | 1.392 | 113.01 | 61.814 | 0.0040942 | 81.077 | 1111 |  | 8100 | 113.01 | 1.392 | 61.814 | 0.0040942 | 81.077 | 1111 | 1029.923
8101 | 1.3924 | 113.02 | 61.814 | 0.0040953 | 81.087 | 1111 |  | 8101 | 113.02 | 1.3924 | 61.814 | 0.0040953 | 81.087 | 1111 | 1029.913
8102 | 1.3928 | 113.03 | 61.814 | 0.0040964 | 81.097 | 1111 |  | 8102 | 113.03 | 1.3928 | 61.814 | 0.0040964 | 81.097 | 1111 | 1029.903
8103 | 1.3932 | 113.04 | 61.814 | 0.0040975 | 81.107 | 1111 |  | 8103 | 113.04 | 1.3932 | 61.814 | 0.0040975 | 81.107 | 1111 | 1029.893
8104 | 1.3936 | 113.05 | 61.814 | 0.0040986 | 81.117 | 1111 |  | 8104 | 113.05 | 1.3936 | 61.814 | 0.0040986 | 81.117 | 1111 | 1029.883
8105 | 1.394 | 113.06 | 61.814 | 0.0040997 | 81.127 | 1111 |  | 8105 | 113.06 | 1.394 | 61.814 | 0.0040997 | 81.127 | 1111 | 1029.873
8106 | 1.3944 | 113.07 | 61.813 | 0.0041008 | 81.137 | 1111 |  | 8106 | 113.07 | 1.3944 | 61.813 | 0.0041008 | 81.137 | 1111 | 1029.863
8107 | 1.3948 | 113.08 | 61.813 | 0.0041019 | 81.147 | 1111 |  | 8107 | 113.08 | 1.3948 | 61.813 | 0.0041019 | 81.147 | 1111 | 1029.853
8108 | 1.3952 | 113.09 | 61.813 | 0.004103 | 81.157 | 1111 |  | 8108 | 113.09 | 1.3952 | 61.813 | 0.004103 | 81.157 | 1111 | 1029.843
8109 | 1.3956 | 113.1 | 61.813 | 0.0041041 | 81.167 | 1111 |  | 8109 | 113.1 | 1.3956 | 61.813 | 0.0041041 | 81.167 | 1111 | 1029.833
8110 | 1.396 | 113.11 | 61.813 | 0.0041052 | 81.177 | 1111 |  | 8110 | 113.11 | 1.396 | 61.813 | 0.0041052 | 81.177 | 1111 | 1029.823
8111 | 1.3964 | 113.12 | 61.813 | 0.0041063 | 81.186 | 1111 |  | 8111 | 113.12 | 1.3964 | 61.813 | 0.0041063 | 81.186 | 1111 | 1029.814
8112 | 1.3968 | 113.13 | 61.813 | 0.0041074 | 81.196 | 1111 |  | 8112 | 113.13 | 1.3968 | 61.813 | 0.0041074 | 81.196 | 1111 | 1029.804
8113 | 1.3972 | 113.14 | 61.812 | 0.0041085 | 81.206 | 1111 |  | 8113 | 113.14 | 1.3972 | 61.812 | 0.0041085 | 81.206 | 1111 | 1029.794
8114 | 1.3976 | 113.15 | 61.812 | 0.0041096 | 81.216 | 1111 |  | 8114 | 113.15 | 1.3976 | 61.812 | 0.0041096 | 81.216 | 1111 | 1029.784
8115 | 1.398 | 113.16 | 61.812 | 0.0041107 | 81.226 | 1111.1 |  | 8115 | 113.16 | 1.398 | 61.812 | 0.0041107 | 81.226 | 1111.1 | 1029.874
8116 | 1.3984 | 113.17 | 61.812 | 0.0041118 | 81.236 | 1111.1 |  | 8116 | 113.17 | 1.3984 | 61.812 | 0.0041118 | 81.236 | 1111.1 | 1029.864
8117 | 1.3988 | 113.18 | 61.812 | 0.0041129 | 81.246 | 1111.1 |  | 8117 | 113.18 | 1.3988 | 61.812 | 0.0041129 | 81.246 | 1111.1 | 1029.854
8118 | 1.3992 | 113.19 | 61.812 | 0.004114 | 81.256 | 1111.1 |  | 8118 | 113.19 | 1.3992 | 61.812 | 0.004114 | 81.256 | 1111.1 | 1029.844
8119 | 1.3996 | 113.2 | 61.812 | 0.0041151 | 81.266 | 1111.1 |  | 8119 | 113.2 | 1.3996 | 61.812 | 0.0041151 | 81.266 | 1111.1 | 1029.834
8120 | 1.4 | 113.21 | 61.811 | 0.0041162 | 81.276 | 1111.1 |  | 8120 | 113.21 | 1.4 | 61.811 | 0.0041162 | 81.276 | 1111.1 | 1029.824
8121 | 1.4004 | 113.22 | 61.811 | 0.0041173 | 81.286 | 1111.1 |  | 8121 | 113.22 | 1.4004 | 61.811 | 0.0041173 | 81.286 | 1111.1 | 1029.814
8122 | 1.4008 | 113.23 | 61.811 | 0.0041185 | 81.296 | 1111.1 |  | 8122 | 113.23 | 1.4008 | 61.811 | 0.0041185 | 81.296 | 1111.1 | 1029.804
8123 | 1.4012 | 113.24 | 61.811 | 0.0041196 | 81.306 | 1111.1 |  | 8123 | 113.24 | 1.4012 | 61.811 | 0.0041196 | 81.306 | 1111.1 | 1029.794
8124 | 1.4016 | 113.25 | 61.811 | 0.0041207 | 81.316 | 1111.1 |  | 8124 | 113.25 | 1.4016 | 61.811 | 0.0041207 | 81.316 | 1111.1 | 1029.784
8125 | 1.402 | 113.26 | 61.811 | 0.0041218 | 81.326 | 1111.1 |  | 8125 | 113.26 | 1.402 | 61.811 | 0.0041218 | 81.326 | 1111.1 | 1029.774
8126 | 1.4024 | 113.27 | 61.811 | 0.0041229 | 81.336 | 1111.1 |  | 8126 | 113.27 | 1.4024 | 61.811 | 0.0041229 | 81.336 | 1111.1 | 1029.764
8127 | 1.4028 | 113.28 | 61.81 | 0.004124 | 81.346 | 1111.1 |  | 8127 | 113.28 | 1.4028 | 61.81 | 0.004124 | 81.346 | 1111.1 | 1029.754
8128 | 1.4032 | 113.29 | 61.81 | 0.0041251 | 81.356 | 1111.1 |  | 8128 | 113.29 | 1.4032 | 61.81 | 0.0041251 | 81.356 | 1111.1 | 1029.744
8129 | 1.4036 | 113.3 | 61.81 | 0.0041262 | 81.366 | 1111.1 |  | 8129 | 113.3 | 1.4036 | 61.81 | 0.0041262 | 81.366 | 1111.1 | 1029.734
8130 | 1.404 | 113.31 | 61.81 | 0.0041273 | 81.376 | 1111.1 |  | 8130 | 113.31 | 1.404 | 61.81 | 0.0041273 | 81.376 | 1111.1 | 1029.724
8131 | 1.4044 | 113.32 | 61.81 | 0.0041284 | 81.386 | 1111.1 |  | 8131 | 113.32 | 1.4044 | 61.81 | 0.0041284 | 81.386 | 1111.1 | 1029.714
8132 | 1.4048 | 113.33 | 61.81 | 0.0041295 | 81.396 | 1111.1 |  | 8132 | 113.33 | 1.4048 | 61.81 | 0.0041295 | 81.396 | 1111.1 | 1029.704
8133 | 1.4052 | 113.34 | 61.81 | 0.0041306 | 81.406 | 1111.1 |  | 8133 | 113.34 | 1.4052 | 61.81 | 0.0041306 | 81.406 | 1111.1 | 1029.694
8134 | 1.4056 | 113.35 | 61.809 | 0.0041317 | 81.416 | 1111.1 |  | 8134 | 113.35 | 1.4056 | 61.809 | 0.0041317 | 81.416 | 1111.1 | 1029.684
8135 | 1.406 | 113.36 | 61.809 | 0.0041329 | 81.426 | 1111.1 |  | 8135 | 113.36 | 1.406 | 61.809 | 0.0041329 | 81.426 | 1111.1 | 1029.674
8136 | 1.4064 | 113.37 | 61.809 | 0.004134 | 81.436 | 1111.1 |  | 8136 | 113.37 | 1.4064 | 61.809 | 0.004134 | 81.436 | 1111.1 | 1029.664
8137 | 1.4068 | 113.38 | 61.809 | 0.0041351 | 81.446 | 1111.1 |  | 8137 | 113.38 | 1.4068 | 61.809 | 0.0041351 | 81.446 | 1111.1 | 1029.654
8138 | 1.4072 | 113.39 | 61.809 | 0.0041362 | 81.456 | 1111.2 |  | 8138 | 113.39 | 1.4072 | 61.809 | 0.0041362 | 81.456 | 1111.2 | 1029.744
8139 | 1.4076 | 113.4 | 61.809 | 0.0041373 | 81.466 | 1111.2 |  | 8139 | 113.4 | 1.4076 | 61.809 | 0.0041373 | 81.466 | 1111.2 | 1029.734
8140 | 1.408 | 113.41 | 61.809 | 0.0041384 | 81.476 | 1111.2 |  | 8140 | 113.41 | 1.408 | 61.809 | 0.0041384 | 81.476 | 1111.2 | 1029.724
8141 | 1.4084 | 113.42 | 61.808 | 0.0041395 | 81.486 | 1111.2 |  | 8141 | 113.42 | 1.4084 | 61.808 | 0.0041395 | 81.486 | 1111.2 | 1029.714
8142 | 1.4088 | 113.43 | 61.808 | 0.0041406 | 81.496 | 1111.2 |  | 8142 | 113.43 | 1.4088 | 61.808 | 0.0041406 | 81.496 | 1111.2 | 1029.704
8143 | 1.4092 | 113.44 | 61.808 | 0.0041417 | 81.506 | 1111.2 |  | 8143 | 113.44 | 1.4092 | 61.808 | 0.0041417 | 81.506 | 1111.2 | 1029.694
8144 | 1.4096 | 113.45 | 61.808 | 0.0041429 | 81.516 | 1111.2 |  | 8144 | 113.45 | 1.4096 | 61.808 | 0.0041429 | 81.516 | 1111.2 | 1029.684
8145 | 1.41 | 113.46 | 61.808 | 0.004144 | 81.526 | 1111.2 |  | 8145 | 113.46 | 1.41 | 61.808 | 0.004144 | 81.526 | 1111.2 | 1029.674
8146 | 1.4104 | 113.47 | 61.808 | 0.0041451 | 81.536 | 1111.2 |  | 8146 | 113.47 | 1.4104 | 61.808 | 0.0041451 | 81.536 | 1111.2 | 1029.664
8147 | 1.4108 | 113.48 | 61.807 | 0.0041462 | 81.546 | 1111.2 |  | 8147 | 113.48 | 1.4108 | 61.807 | 0.0041462 | 81.546 | 1111.2 | 1029.654
8148 | 1.4112 | 113.49 | 61.807 | 0.0041473 | 81.556 | 1111.2 |  | 8148 | 113.49 | 1.4112 | 61.807 | 0.0041473 | 81.556 | 1111.2 | 1029.644
8149 | 1.4116 | 113.5 | 61.807 | 0.0041484 | 81.566 | 1111.2 |  | 8149 | 113.5 | 1.4116 | 61.807 | 0.0041484 | 81.566 | 1111.2 | 1029.634
8150 | 1.412 | 113.51 | 61.807 | 0.0041495 | 81.576 | 1111.2 |  | 8150 | 113.51 | 1.412 | 61.807 | 0.0041495 | 81.576 | 1111.2 | 1029.624
8151 | 1.4124 | 113.52 | 61.807 | 0.0041506 | 81.586 | 1111.2 |  | 8151 | 113.52 | 1.4124 | 61.807 | 0.0041506 | 81.586 | 1111.2 | 1029.614
8152 | 1.4128 | 113.53 | 61.807 | 0.0041518 | 81.596 | 1111.2 |  | 8152 | 113.53 | 1.4128 | 61.807 | 0.0041518 | 81.596 | 1111.2 | 1029.604
8153 | 1.4132 | 113.54 | 61.807 | 0.0041529 | 81.606 | 1111.2 |  | 8153 | 113.54 | 1.4132 | 61.807 | 0.0041529 | 81.606 | 1111.2 | 1029.594
8154 | 1.4137 | 113.55 | 61.806 | 0.004154 | 81.616 | 1111.2 |  | 8154 | 113.55 | 1.4137 | 61.806 | 0.004154 | 81.616 | 1111.2 | 1029.584
8155 | 1.4141 | 113.56 | 61.806 | 0.0041551 | 81.626 | 1111.2 |  | 8155 | 113.56 | 1.4141 | 61.806 | 0.0041551 | 81.626 | 1111.2 | 1029.574
8156 | 1.4145 | 113.57 | 61.806 | 0.0041562 | 81.636 | 1111.2 |  | 8156 | 113.57 | 1.4145 | 61.806 | 0.0041562 | 81.636 | 1111.2 | 1029.564
8157 | 1.4149 | 113.58 | 61.806 | 0.0041573 | 81.646 | 1111.2 |  | 8157 | 113.58 | 1.4149 | 61.806 | 0.0041573 | 81.646 | 1111.2 | 1029.554
8158 | 1.4153 | 113.59 | 61.806 | 0.0041584 | 81.656 | 1111.2 |  | 8158 | 113.59 | 1.4153 | 61.806 | 0.0041584 | 81.656 | 1111.2 | 1029.544
8159 | 1.4157 | 113.6 | 61.806 | 0.0041596 | 81.666 | 1111.2 |  | 8159 | 113.6 | 1.4157 | 61.806 | 0.0041596 | 81.666 | 1111.2 | 1029.534
8160 | 1.4161 | 113.61 | 61.806 | 0.0041607 | 81.676 | 1111.2 |  | 8160 | 113.61 | 1.4161 | 61.806 | 0.0041607 | 81.676 | 1111.2 | 1029.524
8161 | 1.4165 | 113.62 | 61.805 | 0.0041618 | 81.686 | 1111.2 |  | 8161 | 113.62 | 1.4165 | 61.805 | 0.0041618 | 81.686 | 1111.2 | 1029.514
8162 | 1.4169 | 113.63 | 61.805 | 0.0041629 | 81.696 | 1111.3 |  | 8162 | 113.63 | 1.4169 | 61.805 | 0.0041629 | 81.696 | 1111.3 | 1029.604
8163 | 1.4173 | 113.64 | 61.805 | 0.004164 | 81.706 | 1111.3 |  | 8163 | 113.64 | 1.4173 | 61.805 | 0.004164 | 81.706 | 1111.3 | 1029.594
8164 | 1.4177 | 113.65 | 61.805 | 0.0041651 | 81.716 | 1111.3 |  | 8164 | 113.65 | 1.4177 | 61.805 | 0.0041651 | 81.716 | 1111.3 | 1029.584
8165 | 1.4181 | 113.66 | 61.805 | 0.0041663 | 81.726 | 1111.3 |  | 8165 | 113.66 | 1.4181 | 61.805 | 0.0041663 | 81.726 | 1111.3 | 1029.574
8166 | 1.4185 | 113.67 | 61.805 | 0.0041674 | 81.736 | 1111.3 |  | 8166 | 113.67 | 1.4185 | 61.805 | 0.0041674 | 81.736 | 1111.3 | 1029.564
8167 | 1.4189 | 113.68 | 61.805 | 0.0041685 | 81.746 | 1111.3 |  | 8167 | 113.68 | 1.4189 | 61.805 | 0.0041685 | 81.746 | 1111.3 | 1029.554
8168 | 1.4193 | 113.69 | 61.804 | 0.0041696 | 81.756 | 1111.3 |  | 8168 | 113.69 | 1.4193 | 61.804 | 0.0041696 | 81.756 | 1111.3 | 1029.544
8169 | 1.4197 | 113.7 | 61.804 | 0.0041707 | 81.766 | 1111.3 |  | 8169 | 113.7 | 1.4197 | 61.804 | 0.0041707 | 81.766 | 1111.3 | 1029.534
8170 | 1.4201 | 113.71 | 61.804 | 0.0041718 | 81.776 | 1111.3 |  | 8170 | 113.71 | 1.4201 | 61.804 | 0.0041718 | 81.776 | 1111.3 | 1029.524
8171 | 1.4205 | 113.72 | 61.804 | 0.004173 | 81.786 | 1111.3 |  | 8171 | 113.72 | 1.4205 | 61.804 | 0.004173 | 81.786 | 1111.3 | 1029.514
8172 | 1.4209 | 113.73 | 61.804 | 0.0041741 | 81.796 | 1111.3 |  | 8172 | 113.73 | 1.4209 | 61.804 | 0.0041741 | 81.796 | 1111.3 | 1029.504
8173 | 1.4213 | 113.74 | 61.804 | 0.0041752 | 81.806 | 1111.3 |  | 8173 | 113.74 | 1.4213 | 61.804 | 0.0041752 | 81.806 | 1111.3 | 1029.494
8174 | 1.4217 | 113.75 | 61.804 | 0.0041763 | 81.816 | 1111.3 |  | 8174 | 113.75 | 1.4217 | 61.804 | 0.0041763 | 81.816 | 1111.3 | 1029.484
8175 | 1.4221 | 113.76 | 61.803 | 0.0041774 | 81.826 | 1111.3 |  | 8175 | 113.76 | 1.4221 | 61.803 | 0.0041774 | 81.826 | 1111.3 | 1029.474
8176 | 1.4225 | 113.77 | 61.803 | 0.0041786 | 81.836 | 1111.3 |  | 8176 | 113.77 | 1.4225 | 61.803 | 0.0041786 | 81.836 | 1111.3 | 1029.464
8177 | 1.4229 | 113.78 | 61.803 | 0.0041797 | 81.846 | 1111.3 |  | 8177 | 113.78 | 1.4229 | 61.803 | 0.0041797 | 81.846 | 1111.3 | 1029.454
8178 | 1.4234 | 113.79 | 61.803 | 0.0041808 | 81.856 | 1111.3 |  | 8178 | 113.79 | 1.4234 | 61.803 | 0.0041808 | 81.856 | 1111.3 | 1029.444
8179 | 1.4238 | 113.8 | 61.803 | 0.0041819 | 81.866 | 1111.3 |  | 8179 | 113.8 | 1.4238 | 61.803 | 0.0041819 | 81.866 | 1111.3 | 1029.434
8180 | 1.4242 | 113.81 | 61.803 | 0.004183 | 81.876 | 1111.3 |  | 8180 | 113.81 | 1.4242 | 61.803 | 0.004183 | 81.876 | 1111.3 | 1029.424
8181 | 1.4246 | 113.82 | 61.803 | 0.0041842 | 81.886 | 1111.3 |  | 8181 | 113.82 | 1.4246 | 61.803 | 0.0041842 | 81.886 | 1111.3 | 1029.414
8182 | 1.425 | 113.83 | 61.802 | 0.0041853 | 81.896 | 1111.3 |  | 8182 | 113.83 | 1.425 | 61.802 | 0.0041853 | 81.896 | 1111.3 | 1029.404
8183 | 1.4254 | 113.84 | 61.802 | 0.0041864 | 81.906 | 1111.3 |  | 8183 | 113.84 | 1.4254 | 61.802 | 0.0041864 | 81.906 | 1111.3 | 1029.394
8184 | 1.4258 | 113.85 | 61.802 | 0.0041875 | 81.916 | 1111.3 |  | 8184 | 113.85 | 1.4258 | 61.802 | 0.0041875 | 81.916 | 1111.3 | 1029.384
8185 | 1.4262 | 113.86 | 61.802 | 0.0041886 | 81.926 | 1111.4 |  | 8185 | 113.86 | 1.4262 | 61.802 | 0.0041886 | 81.926 | 1111.4 | 1029.474
8186 | 1.4266 | 113.87 | 61.802 | 0.0041898 | 81.936 | 1111.4 |  | 8186 | 113.87 | 1.4266 | 61.802 | 0.0041898 | 81.936 | 1111.4 | 1029.464
8187 | 1.427 | 113.88 | 61.802 | 0.0041909 | 81.946 | 1111.4 |  | 8187 | 113.88 | 1.427 | 61.802 | 0.0041909 | 81.946 | 1111.4 | 1029.454
8188 | 1.4274 | 113.89 | 61.802 | 0.004192 | 81.956 | 1111.4 |  | 8188 | 113.89 | 1.4274 | 61.802 | 0.004192 | 81.956 | 1111.4 | 1029.444
8189 | 1.4278 | 113.9 | 61.801 | 0.0041931 | 81.966 | 1111.4 |  | 8189 | 113.9 | 1.4278 | 61.801 | 0.0041931 | 81.966 | 1111.4 | 1029.434
8190 | 1.4282 | 113.91 | 61.801 | 0.0041943 | 81.976 | 1111.4 |  | 8190 | 113.91 | 1.4282 | 61.801 | 0.0041943 | 81.976 | 1111.4 | 1029.424
8191 | 1.4286 | 113.92 | 61.801 | 0.0041954 | 81.986 | 1111.4 |  | 8191 | 113.92 | 1.4286 | 61.801 | 0.0041954 | 81.986 | 1111.4 | 1029.414
8192 | 1.429 | 113.93 | 61.801 | 0.0041965 | 81.996 | 1111.4 |  | 8192 | 113.93 | 1.429 | 61.801 | 0.0041965 | 81.996 | 1111.4 | 1029.404
8193 | 1.4294 | 113.94 | 61.801 | 0.0041976 | 82.006 | 1111.4 |  | 8193 | 113.94 | 1.4294 | 61.801 | 0.0041976 | 82.006 | 1111.4 | 1029.394
8194 | 1.4298 | 113.95 | 61.801 | 0.0041988 | 82.016 | 1111.4 |  | 8194 | 113.95 | 1.4298 | 61.801 | 0.0041988 | 82.016 | 1111.4 | 1029.384
8195 | 1.4303 | 113.96 | 61.8 | 0.0041999 | 82.026 | 1111.4 |  | 8195 | 113.96 | 1.4303 | 61.8 | 0.0041999 | 82.026 | 1111.4 | 1029.374
8196 | 1.4307 | 113.97 | 61.8 | 0.004201 | 82.036 | 1111.4 |  | 8196 | 113.97 | 1.4307 | 61.8 | 0.004201 | 82.036 | 1111.4 | 1029.364
8197 | 1.4311 | 113.98 | 61.8 | 0.0042021 | 82.046 | 1111.4 |  | 8197 | 113.98 | 1.4311 | 61.8 | 0.0042021 | 82.046 | 1111.4 | 1029.354
8198 | 1.4315 | 113.99 | 61.8 | 0.0042033 | 82.056 | 1111.4 |  | 8198 | 113.99 | 1.4315 | 61.8 | 0.0042033 | 82.056 | 1111.4 | 1029.344
8199 | 1.4319 | 114 | 61.8 | 0.0042044 | 82.066 | 1111.4 |  | 8199 | 114 | 1.4319 | 61.8 | 0.0042044 | 82.066 | 1111.4 | 1029.334
8200 | 1.4323 | 114.01 | 61.8 | 0.0042055 | 82.076 | 1111.4 |  | 8200 | 114.01 | 1.4323 | 61.8 | 0.0042055 | 82.076 | 1111.4 | 1029.324
8201 | 1.4327 | 114.02 | 61.8 | 0.0042066 | 82.086 | 1111.4 |  | 8201 | 114.02 | 1.4327 | 61.8 | 0.0042066 | 82.086 | 1111.4 | 1029.314
8202 | 1.4331 | 114.03 | 61.799 | 0.0042078 | 82.096 | 1111.4 |  | 8202 | 114.03 | 1.4331 | 61.799 | 0.0042078 | 82.096 | 1111.4 | 1029.304
8203 | 1.4335 | 114.04 | 61.799 | 0.0042089 | 82.106 | 1111.4 |  | 8203 | 114.04 | 1.4335 | 61.799 | 0.0042089 | 82.106 | 1111.4 | 1029.294
8204 | 1.4339 | 114.05 | 61.799 | 0.00421 | 82.116 | 1111.4 |  | 8204 | 114.05 | 1.4339 | 61.799 | 0.00421 | 82.116 | 1111.4 | 1029.284
8205 | 1.4343 | 114.06 | 61.799 | 0.0042111 | 82.126 | 1111.4 |  | 8205 | 114.06 | 1.4343 | 61.799 | 0.0042111 | 82.126 | 1111.4 | 1029.274
8206 | 1.4347 | 114.07 | 61.799 | 0.0042123 | 82.136 | 1111.4 |  | 8206 | 114.07 | 1.4347 | 61.799 | 0.0042123 | 82.136 | 1111.4 | 1029.264
8207 | 1.4351 | 114.08 | 61.799 | 0.0042134 | 82.146 | 1111.4 |  | 8207 | 114.08 | 1.4351 | 61.799 | 0.0042134 | 82.146 | 1111.4 | 1029.254
8208 | 1.4356 | 114.09 | 61.799 | 0.0042145 | 82.156 | 1111.4 |  | 8208 | 114.09 | 1.4356 | 61.799 | 0.0042145 | 82.156 | 1111.4 | 1029.244
8209 | 1.436 | 114.1 | 61.798 | 0.0042156 | 82.166 | 1111.5 |  | 8209 | 114.1 | 1.436 | 61.798 | 0.0042156 | 82.166 | 1111.5 | 1029.334
8210 | 1.4364 | 114.11 | 61.798 | 0.0042168 | 82.176 | 1111.5 |  | 8210 | 114.11 | 1.4364 | 61.798 | 0.0042168 | 82.176 | 1111.5 | 1029.324
8211 | 1.4368 | 114.12 | 61.798 | 0.0042179 | 82.186 | 1111.5 |  | 8211 | 114.12 | 1.4368 | 61.798 | 0.0042179 | 82.186 | 1111.5 | 1029.314
8212 | 1.4372 | 114.13 | 61.798 | 0.004219 | 82.196 | 1111.5 |  | 8212 | 114.13 | 1.4372 | 61.798 | 0.004219 | 82.196 | 1111.5 | 1029.304
8213 | 1.4376 | 114.14 | 61.798 | 0.0042202 | 82.206 | 1111.5 |  | 8213 | 114.14 | 1.4376 | 61.798 | 0.0042202 | 82.206 | 1111.5 | 1029.294
8214 | 1.438 | 114.15 | 61.798 | 0.0042213 | 82.216 | 1111.5 |  | 8214 | 114.15 | 1.438 | 61.798 | 0.0042213 | 82.216 | 1111.5 | 1029.284
8215 | 1.4384 | 114.16 | 61.798 | 0.0042224 | 82.226 | 1111.5 |  | 8215 | 114.16 | 1.4384 | 61.798 | 0.0042224 | 82.226 | 1111.5 | 1029.274
8216 | 1.4388 | 114.17 | 61.797 | 0.0042235 | 82.236 | 1111.5 |  | 8216 | 114.17 | 1.4388 | 61.797 | 0.0042235 | 82.236 | 1111.5 | 1029.264
8217 | 1.4392 | 114.18 | 61.797 | 0.0042247 | 82.246 | 1111.5 |  | 8217 | 114.18 | 1.4392 | 61.797 | 0.0042247 | 82.246 | 1111.5 | 1029.254
8218 | 1.4396 | 114.19 | 61.797 | 0.0042258 | 82.256 | 1111.5 |  | 8218 | 114.19 | 1.4396 | 61.797 | 0.0042258 | 82.256 | 1111.5 | 1029.244
8219 | 1.4401 | 114.2 | 61.797 | 0.0042269 | 82.266 | 1111.5 |  | 8219 | 114.2 | 1.4401 | 61.797 | 0.0042269 | 82.266 | 1111.5 | 1029.234
8220 | 1.4405 | 114.21 | 61.797 | 0.0042281 | 82.276 | 1111.5 |  | 8220 | 114.21 | 1.4405 | 61.797 | 0.0042281 | 82.276 | 1111.5 | 1029.224
8221 | 1.4409 | 114.22 | 61.797 | 0.0042292 | 82.286 | 1111.5 |  | 8221 | 114.22 | 1.4409 | 61.797 | 0.0042292 | 82.286 | 1111.5 | 1029.214
8222 | 1.4413 | 114.23 | 61.797 | 0.0042303 | 82.296 | 1111.5 |  | 8222 | 114.23 | 1.4413 | 61.797 | 0.0042303 | 82.296 | 1111.5 | 1029.204
8223 | 1.4417 | 114.24 | 61.796 | 0.0042315 | 82.306 | 1111.5 |  | 8223 | 114.24 | 1.4417 | 61.796 | 0.0042315 | 82.306 | 1111.5 | 1029.194
8224 | 1.4421 | 114.25 | 61.796 | 0.0042326 | 82.316 | 1111.5 |  | 8224 | 114.25 | 1.4421 | 61.796 | 0.0042326 | 82.316 | 1111.5 | 1029.184
8225 | 1.4425 | 114.26 | 61.796 | 0.0042337 | 82.326 | 1111.5 |  | 8225 | 114.26 | 1.4425 | 61.796 | 0.0042337 | 82.326 | 1111.5 | 1029.174
8226 | 1.4429 | 114.27 | 61.796 | 0.0042349 | 82.336 | 1111.5 |  | 8226 | 114.27 | 1.4429 | 61.796 | 0.0042349 | 82.336 | 1111.5 | 1029.164
8227 | 1.4433 | 114.28 | 61.796 | 0.004236 | 82.346 | 1111.5 |  | 8227 | 114.28 | 1.4433 | 61.796 | 0.004236 | 82.346 | 1111.5 | 1029.154
8228 | 1.4437 | 114.29 | 61.796 | 0.0042371 | 82.356 | 1111.5 |  | 8228 | 114.29 | 1.4437 | 61.796 | 0.0042371 | 82.356 | 1111.5 | 1029.144
8229 | 1.4442 | 114.3 | 61.795 | 0.0042383 | 82.366 | 1111.5 |  | 8229 | 114.3 | 1.4442 | 61.795 | 0.0042383 | 82.366 | 1111.5 | 1029.134
8230 | 1.4446 | 114.31 | 61.795 | 0.0042394 | 82.376 | 1111.5 |  | 8230 | 114.31 | 1.4446 | 61.795 | 0.0042394 | 82.376 | 1111.5 | 1029.124
8231 | 1.445 | 114.32 | 61.795 | 0.0042405 | 82.386 | 1111.5 |  | 8231 | 114.32 | 1.445 | 61.795 | 0.0042405 | 82.386 | 1111.5 | 1029.114
8232 | 1.4454 | 114.33 | 61.795 | 0.0042417 | 82.396 | 1111.6 |  | 8232 | 114.33 | 1.4454 | 61.795 | 0.0042417 | 82.396 | 1111.6 | 1029.204
8233 | 1.4458 | 114.34 | 61.795 | 0.0042428 | 82.406 | 1111.6 |  | 8233 | 114.34 | 1.4458 | 61.795 | 0.0042428 | 82.406 | 1111.6 | 1029.194
8234 | 1.4462 | 114.35 | 61.795 | 0.0042439 | 82.416 | 1111.6 |  | 8234 | 114.35 | 1.4462 | 61.795 | 0.0042439 | 82.416 | 1111.6 | 1029.184
8235 | 1.4466 | 114.36 | 61.795 | 0.0042451 | 82.426 | 1111.6 |  | 8235 | 114.36 | 1.4466 | 61.795 | 0.0042451 | 82.426 | 1111.6 | 1029.174
8236 | 1.447 | 114.37 | 61.794 | 0.0042462 | 82.436 | 1111.6 |  | 8236 | 114.37 | 1.447 | 61.794 | 0.0042462 | 82.436 | 1111.6 | 1029.164
8237 | 1.4474 | 114.38 | 61.794 | 0.0042473 | 82.446 | 1111.6 |  | 8237 | 114.38 | 1.4474 | 61.794 | 0.0042473 | 82.446 | 1111.6 | 1029.154
8238 | 1.4479 | 114.39 | 61.794 | 0.0042485 | 82.456 | 1111.6 |  | 8238 | 114.39 | 1.4479 | 61.794 | 0.0042485 | 82.456 | 1111.6 | 1029.144
8239 | 1.4483 | 114.4 | 61.794 | 0.0042496 | 82.466 | 1111.6 |  | 8239 | 114.4 | 1.4483 | 61.794 | 0.0042496 | 82.466 | 1111.6 | 1029.134
8240 | 1.4487 | 114.41 | 61.794 | 0.0042507 | 82.476 | 1111.6 |  | 8240 | 114.41 | 1.4487 | 61.794 | 0.0042507 | 82.476 | 1111.6 | 1029.124
8241 | 1.4491 | 114.42 | 61.794 | 0.0042519 | 82.486 | 1111.6 |  | 8241 | 114.42 | 1.4491 | 61.794 | 0.0042519 | 82.486 | 1111.6 | 1029.114
8242 | 1.4495 | 114.43 | 61.794 | 0.004253 | 82.496 | 1111.6 |  | 8242 | 114.43 | 1.4495 | 61.794 | 0.004253 | 82.496 | 1111.6 | 1029.104
8243 | 1.4499 | 114.44 | 61.793 | 0.0042542 | 82.506 | 1111.6 |  | 8243 | 114.44 | 1.4499 | 61.793 | 0.0042542 | 82.506 | 1111.6 | 1029.094
8244 | 1.4503 | 114.45 | 61.793 | 0.0042553 | 82.516 | 1111.6 |  | 8244 | 114.45 | 1.4503 | 61.793 | 0.0042553 | 82.516 | 1111.6 | 1029.084
8245 | 1.4507 | 114.46 | 61.793 | 0.0042564 | 82.525 | 1111.6 |  | 8245 | 114.46 | 1.4507 | 61.793 | 0.0042564 | 82.525 | 1111.6 | 1029.075
8246 | 1.4511 | 114.47 | 61.793 | 0.0042576 | 82.535 | 1111.6 |  | 8246 | 114.47 | 1.4511 | 61.793 | 0.0042576 | 82.535 | 1111.6 | 1029.065
8247 | 1.4516 | 114.48 | 61.793 | 0.0042587 | 82.545 | 1111.6 |  | 8247 | 114.48 | 1.4516 | 61.793 | 0.0042587 | 82.545 | 1111.6 | 1029.055
8248 | 1.452 | 114.49 | 61.793 | 0.0042598 | 82.555 | 1111.6 |  | 8248 | 114.49 | 1.452 | 61.793 | 0.0042598 | 82.555 | 1111.6 | 1029.045
8249 | 1.4524 | 114.5 | 61.793 | 0.004261 | 82.565 | 1111.6 |  | 8249 | 114.5 | 1.4524 | 61.793 | 0.004261 | 82.565 | 1111.6 | 1029.035
8250 | 1.4528 | 114.51 | 61.792 | 0.0042621 | 82.575 | 1111.6 |  | 8250 | 114.51 | 1.4528 | 61.792 | 0.0042621 | 82.575 | 1111.6 | 1029.025
8251 | 1.4532 | 114.52 | 61.792 | 0.0042633 | 82.585 | 1111.6 |  | 8251 | 114.52 | 1.4532 | 61.792 | 0.0042633 | 82.585 | 1111.6 | 1029.015
8252 | 1.4536 | 114.53 | 61.792 | 0.0042644 | 82.595 | 1111.6 |  | 8252 | 114.53 | 1.4536 | 61.792 | 0.0042644 | 82.595 | 1111.6 | 1029.005
8253 | 1.454 | 114.54 | 61.792 | 0.0042655 | 82.605 | 1111.6 |  | 8253 | 114.54 | 1.454 | 61.792 | 0.0042655 | 82.605 | 1111.6 | 1028.995
8254 | 1.4544 | 114.55 | 61.792 | 0.0042667 | 82.615 | 1111.6 |  | 8254 | 114.55 | 1.4544 | 61.792 | 0.0042667 | 82.615 | 1111.6 | 1028.985
8255 | 1.4549 | 114.56 | 61.792 | 0.0042678 | 82.625 | 1111.6 |  | 8255 | 114.56 | 1.4549 | 61.792 | 0.0042678 | 82.625 | 1111.6 | 1028.975
8256 | 1.4553 | 114.57 | 61.792 | 0.004269 | 82.635 | 1111.7 |  | 8256 | 114.57 | 1.4553 | 61.792 | 0.004269 | 82.635 | 1111.7 | 1029.065
8257 | 1.4557 | 114.58 | 61.791 | 0.0042701 | 82.645 | 1111.7 |  | 8257 | 114.58 | 1.4557 | 61.791 | 0.0042701 | 82.645 | 1111.7 | 1029.055
8258 | 1.4561 | 114.59 | 61.791 | 0.0042712 | 82.655 | 1111.7 |  | 8258 | 114.59 | 1.4561 | 61.791 | 0.0042712 | 82.655 | 1111.7 | 1029.045
8259 | 1.4565 | 114.6 | 61.791 | 0.0042724 | 82.665 | 1111.7 |  | 8259 | 114.6 | 1.4565 | 61.791 | 0.0042724 | 82.665 | 1111.7 | 1029.035
8260 | 1.4569 | 114.61 | 61.791 | 0.0042735 | 82.675 | 1111.7 |  | 8260 | 114.61 | 1.4569 | 61.791 | 0.0042735 | 82.675 | 1111.7 | 1029.025
8261 | 1.4573 | 114.62 | 61.791 | 0.0042747 | 82.685 | 1111.7 |  | 8261 | 114.62 | 1.4573 | 61.791 | 0.0042747 | 82.685 | 1111.7 | 1029.015
8262 | 1.4578 | 114.63 | 61.791 | 0.0042758 | 82.695 | 1111.7 |  | 8262 | 114.63 | 1.4578 | 61.791 | 0.0042758 | 82.695 | 1111.7 | 1029.005
8263 | 1.4582 | 114.64 | 61.79 | 0.0042769 | 82.705 | 1111.7 |  | 8263 | 114.64 | 1.4582 | 61.79 | 0.0042769 | 82.705 | 1111.7 | 1028.995
8264 | 1.4586 | 114.65 | 61.79 | 0.0042781 | 82.715 | 1111.7 |  | 8264 | 114.65 | 1.4586 | 61.79 | 0.0042781 | 82.715 | 1111.7 | 1028.985
8265 | 1.459 | 114.66 | 61.79 | 0.0042792 | 82.725 | 1111.7 |  | 8265 | 114.66 | 1.459 | 61.79 | 0.0042792 | 82.725 | 1111.7 | 1028.975
8266 | 1.4594 | 114.67 | 61.79 | 0.0042804 | 82.735 | 1111.7 |  | 8266 | 114.67 | 1.4594 | 61.79 | 0.0042804 | 82.735 | 1111.7 | 1028.965
8267 | 1.4598 | 114.68 | 61.79 | 0.0042815 | 82.745 | 1111.7 |  | 8267 | 114.68 | 1.4598 | 61.79 | 0.0042815 | 82.745 | 1111.7 | 1028.955
8268 | 1.4602 | 114.69 | 61.79 | 0.0042827 | 82.755 | 1111.7 |  | 8268 | 114.69 | 1.4602 | 61.79 | 0.0042827 | 82.755 | 1111.7 | 1028.945
8269 | 1.4606 | 114.7 | 61.79 | 0.0042838 | 82.765 | 1111.7 |  | 8269 | 114.7 | 1.4606 | 61.79 | 0.0042838 | 82.765 | 1111.7 | 1028.935
8270 | 1.4611 | 114.71 | 61.789 | 0.0042849 | 82.775 | 1111.7 |  | 8270 | 114.71 | 1.4611 | 61.789 | 0.0042849 | 82.775 | 1111.7 | 1028.925
8271 | 1.4615 | 114.72 | 61.789 | 0.0042861 | 82.785 | 1111.7 |  | 8271 | 114.72 | 1.4615 | 61.789 | 0.0042861 | 82.785 | 1111.7 | 1028.915
8272 | 1.4619 | 114.73 | 61.789 | 0.0042872 | 82.795 | 1111.7 |  | 8272 | 114.73 | 1.4619 | 61.789 | 0.0042872 | 82.795 | 1111.7 | 1028.905
8273 | 1.4623 | 114.74 | 61.789 | 0.0042884 | 82.805 | 1111.7 |  | 8273 | 114.74 | 1.4623 | 61.789 | 0.0042884 | 82.805 | 1111.7 | 1028.895
8274 | 1.4627 | 114.75 | 61.789 | 0.0042895 | 82.815 | 1111.7 |  | 8274 | 114.75 | 1.4627 | 61.789 | 0.0042895 | 82.815 | 1111.7 | 1028.885
8275 | 1.4631 | 114.76 | 61.789 | 0.0042907 | 82.825 | 1111.7 |  | 8275 | 114.76 | 1.4631 | 61.789 | 0.0042907 | 82.825 | 1111.7 | 1028.875
8276 | 1.4636 | 114.77 | 61.789 | 0.0042918 | 82.835 | 1111.7 |  | 8276 | 114.77 | 1.4636 | 61.789 | 0.0042918 | 82.835 | 1111.7 | 1028.865
8277 | 1.464 | 114.78 | 61.788 | 0.004293 | 82.845 | 1111.7 |  | 8277 | 114.78 | 1.464 | 61.788 | 0.004293 | 82.845 | 1111.7 | 1028.855
8278 | 1.4644 | 114.79 | 61.788 | 0.0042941 | 82.855 | 1111.7 |  | 8278 | 114.79 | 1.4644 | 61.788 | 0.0042941 | 82.855 | 1111.7 | 1028.845
8279 | 1.4648 | 114.8 | 61.788 | 0.0042952 | 82.865 | 1111.8 |  | 8279 | 114.8 | 1.4648 | 61.788 | 0.0042952 | 82.865 | 1111.8 | 1028.935
8280 | 1.4652 | 114.81 | 61.788 | 0.0042964 | 82.875 | 1111.8 |  | 8280 | 114.81 | 1.4652 | 61.788 | 0.0042964 | 82.875 | 1111.8 | 1028.925
8281 | 1.4656 | 114.82 | 61.788 | 0.0042975 | 82.885 | 1111.8 |  | 8281 | 114.82 | 1.4656 | 61.788 | 0.0042975 | 82.885 | 1111.8 | 1028.915
8282 | 1.466 | 114.83 | 61.788 | 0.0042987 | 82.895 | 1111.8 |  | 8282 | 114.83 | 1.466 | 61.788 | 0.0042987 | 82.895 | 1111.8 | 1028.905
8283 | 1.4665 | 114.84 | 61.788 | 0.0042998 | 82.905 | 1111.8 |  | 8283 | 114.84 | 1.4665 | 61.788 | 0.0042998 | 82.905 | 1111.8 | 1028.895
8284 | 1.4669 | 114.85 | 61.787 | 0.004301 | 82.915 | 1111.8 |  | 8284 | 114.85 | 1.4669 | 61.787 | 0.004301 | 82.915 | 1111.8 | 1028.885
8285 | 1.4673 | 114.86 | 61.787 | 0.0043021 | 82.925 | 1111.8 |  | 8285 | 114.86 | 1.4673 | 61.787 | 0.0043021 | 82.925 | 1111.8 | 1028.875
8286 | 1.4677 | 114.87 | 61.787 | 0.0043033 | 82.935 | 1111.8 |  | 8286 | 114.87 | 1.4677 | 61.787 | 0.0043033 | 82.935 | 1111.8 | 1028.865
8287 | 1.4681 | 114.88 | 61.787 | 0.0043044 | 82.945 | 1111.8 |  | 8287 | 114.88 | 1.4681 | 61.787 | 0.0043044 | 82.945 | 1111.8 | 1028.855
8288 | 1.4685 | 114.89 | 61.787 | 0.0043056 | 82.955 | 1111.8 |  | 8288 | 114.89 | 1.4685 | 61.787 | 0.0043056 | 82.955 | 1111.8 | 1028.845
8289 | 1.469 | 114.9 | 61.787 | 0.0043067 | 82.965 | 1111.8 |  | 8289 | 114.9 | 1.469 | 61.787 | 0.0043067 | 82.965 | 1111.8 | 1028.835
8290 | 1.4694 | 114.91 | 61.787 | 0.0043079 | 82.975 | 1111.8 |  | 8290 | 114.91 | 1.4694 | 61.787 | 0.0043079 | 82.975 | 1111.8 | 1028.825
8291 | 1.4698 | 114.92 | 61.786 | 0.004309 | 82.985 | 1111.8 |  | 8291 | 114.92 | 1.4698 | 61.786 | 0.004309 | 82.985 | 1111.8 | 1028.815
8292 | 1.4702 | 114.93 | 61.786 | 0.0043102 | 82.995 | 1111.8 |  | 8292 | 114.93 | 1.4702 | 61.786 | 0.0043102 | 82.995 | 1111.8 | 1028.805
8293 | 1.4706 | 114.94 | 61.786 | 0.0043113 | 83.005 | 1111.8 |  | 8293 | 114.94 | 1.4706 | 61.786 | 0.0043113 | 83.005 | 1111.8 | 1028.795
8294 | 1.471 | 114.95 | 61.786 | 0.0043125 | 83.015 | 1111.8 |  | 8294 | 114.95 | 1.471 | 61.786 | 0.0043125 | 83.015 | 1111.8 | 1028.785
8295 | 1.4715 | 114.96 | 61.786 | 0.0043136 | 83.025 | 1111.8 |  | 8295 | 114.96 | 1.4715 | 61.786 | 0.0043136 | 83.025 | 1111.8 | 1028.775
8296 | 1.4719 | 114.97 | 61.786 | 0.0043148 | 83.035 | 1111.8 |  | 8296 | 114.97 | 1.4719 | 61.786 | 0.0043148 | 83.035 | 1111.8 | 1028.765
8297 | 1.4723 | 114.98 | 61.785 | 0.0043159 | 83.045 | 1111.8 |  | 8297 | 114.98 | 1.4723 | 61.785 | 0.0043159 | 83.045 | 1111.8 | 1028.755
8298 | 1.4727 | 114.99 | 61.785 | 0.0043171 | 83.055 | 1111.8 |  | 8298 | 114.99 | 1.4727 | 61.785 | 0.0043171 | 83.055 | 1111.8 | 1028.745
8299 | 1.4731 | 115 | 61.785 | 0.0043182 | 83.065 | 1111.8 |  | 8299 | 115 | 1.4731 | 61.785 | 0.0043182 | 83.065 | 1111.8 | 1028.735
8300 | 1.4735 | 115.01 | 61.785 | 0.0043194 | 83.075 | 1111.8 |  | 8300 | 115.01 | 1.4735 | 61.785 | 0.0043194 | 83.075 | 1111.8 | 1028.725
8301 | 1.474 | 115.02 | 61.785 | 0.0043205 | 83.085 | 1111.8 |  | 8301 | 115.02 | 1.474 | 61.785 | 0.0043205 | 83.085 | 1111.8 | 1028.715
8302 | 1.4744 | 115.03 | 61.785 | 0.0043217 | 83.095 | 1111.8 |  | 8302 | 115.03 | 1.4744 | 61.785 | 0.0043217 | 83.095 | 1111.8 | 1028.705
8303 | 1.4748 | 115.04 | 61.785 | 0.0043228 | 83.105 | 1111.9 |  | 8303 | 115.04 | 1.4748 | 61.785 | 0.0043228 | 83.105 | 1111.9 | 1028.795
8304 | 1.4752 | 115.05 | 61.784 | 0.004324 | 83.115 | 1111.9 |  | 8304 | 115.05 | 1.4752 | 61.784 | 0.004324 | 83.115 | 1111.9 | 1028.785
8305 | 1.4756 | 115.06 | 61.784 | 0.0043251 | 83.125 | 1111.9 |  | 8305 | 115.06 | 1.4756 | 61.784 | 0.0043251 | 83.125 | 1111.9 | 1028.775
8306 | 1.4761 | 115.07 | 61.784 | 0.0043263 | 83.135 | 1111.9 |  | 8306 | 115.07 | 1.4761 | 61.784 | 0.0043263 | 83.135 | 1111.9 | 1028.765
8307 | 1.4765 | 115.08 | 61.784 | 0.0043274 | 83.145 | 1111.9 |  | 8307 | 115.08 | 1.4765 | 61.784 | 0.0043274 | 83.145 | 1111.9 | 1028.755
8308 | 1.4769 | 115.09 | 61.784 | 0.0043286 | 83.155 | 1111.9 |  | 8308 | 115.09 | 1.4769 | 61.784 | 0.0043286 | 83.155 | 1111.9 | 1028.745
8309 | 1.4773 | 115.1 | 61.784 | 0.0043298 | 83.165 | 1111.9 |  | 8309 | 115.1 | 1.4773 | 61.784 | 0.0043298 | 83.165 | 1111.9 | 1028.735
8310 | 1.4777 | 115.11 | 61.784 | 0.0043309 | 83.175 | 1111.9 |  | 8310 | 115.11 | 1.4777 | 61.784 | 0.0043309 | 83.175 | 1111.9 | 1028.725
8311 | 1.4781 | 115.12 | 61.783 | 0.0043321 | 83.185 | 1111.9 |  | 8311 | 115.12 | 1.4781 | 61.783 | 0.0043321 | 83.185 | 1111.9 | 1028.715
8312 | 1.4786 | 115.13 | 61.783 | 0.0043332 | 83.195 | 1111.9 |  | 8312 | 115.13 | 1.4786 | 61.783 | 0.0043332 | 83.195 | 1111.9 | 1028.705
8313 | 1.479 | 115.14 | 61.783 | 0.0043344 | 83.205 | 1111.9 |  | 8313 | 115.14 | 1.479 | 61.783 | 0.0043344 | 83.205 | 1111.9 | 1028.695
8314 | 1.4794 | 115.15 | 61.783 | 0.0043355 | 83.215 | 1111.9 |  | 8314 | 115.15 | 1.4794 | 61.783 | 0.0043355 | 83.215 | 1111.9 | 1028.685
8315 | 1.4798 | 115.16 | 61.783 | 0.0043367 | 83.225 | 1111.9 |  | 8315 | 115.16 | 1.4798 | 61.783 | 0.0043367 | 83.225 | 1111.9 | 1028.675
8316 | 1.4802 | 115.17 | 61.783 | 0.0043378 | 83.235 | 1111.9 |  | 8316 | 115.17 | 1.4802 | 61.783 | 0.0043378 | 83.235 | 1111.9 | 1028.665
8317 | 1.4807 | 115.18 | 61.783 | 0.004339 | 83.245 | 1111.9 |  | 8317 | 115.18 | 1.4807 | 61.783 | 0.004339 | 83.245 | 1111.9 | 1028.655
8318 | 1.4811 | 115.19 | 61.782 | 0.0043401 | 83.255 | 1111.9 |  | 8318 | 115.19 | 1.4811 | 61.782 | 0.0043401 | 83.255 | 1111.9 | 1028.645
8319 | 1.4815 | 115.2 | 61.782 | 0.0043413 | 83.265 | 1111.9 |  | 8319 | 115.2 | 1.4815 | 61.782 | 0.0043413 | 83.265 | 1111.9 | 1028.635
8320 | 1.4819 | 115.21 | 61.782 | 0.0043425 | 83.275 | 1111.9 |  | 8320 | 115.21 | 1.4819 | 61.782 | 0.0043425 | 83.275 | 1111.9 | 1028.625
8321 | 1.4823 | 115.22 | 61.782 | 0.0043436 | 83.285 | 1111.9 |  | 8321 | 115.22 | 1.4823 | 61.782 | 0.0043436 | 83.285 | 1111.9 | 1028.615
8322 | 1.4828 | 115.23 | 61.782 | 0.0043448 | 83.295 | 1111.9 |  | 8322 | 115.23 | 1.4828 | 61.782 | 0.0043448 | 83.295 | 1111.9 | 1028.605
8323 | 1.4832 | 115.24 | 61.782 | 0.0043459 | 83.305 | 1111.9 |  | 8323 | 115.24 | 1.4832 | 61.782 | 0.0043459 | 83.305 | 1111.9 | 1028.595
8324 | 1.4836 | 115.25 | 61.781 | 0.0043471 | 83.315 | 1111.9 |  | 8324 | 115.25 | 1.4836 | 61.781 | 0.0043471 | 83.315 | 1111.9 | 1028.585
8325 | 1.484 | 115.26 | 61.781 | 0.0043482 | 83.325 | 1111.9 |  | 8325 | 115.26 | 1.484 | 61.781 | 0.0043482 | 83.325 | 1111.9 | 1028.575
8326 | 1.4844 | 115.27 | 61.781 | 0.0043494 | 83.335 | 1112 |  | 8326 | 115.27 | 1.4844 | 61.781 | 0.0043494 | 83.335 | 1112 | 1028.665
8327 | 1.4849 | 115.28 | 61.781 | 0.0043506 | 83.345 | 1112 |  | 8327 | 115.28 | 1.4849 | 61.781 | 0.0043506 | 83.345 | 1112 | 1028.655
8328 | 1.4853 | 115.29 | 61.781 | 0.0043517 | 83.355 | 1112 |  | 8328 | 115.29 | 1.4853 | 61.781 | 0.0043517 | 83.355 | 1112 | 1028.645
8329 | 1.4857 | 115.3 | 61.781 | 0.0043529 | 83.365 | 1112 |  | 8329 | 115.3 | 1.4857 | 61.781 | 0.0043529 | 83.365 | 1112 | 1028.635
8330 | 1.4861 | 115.31 | 61.781 | 0.004354 | 83.375 | 1112 |  | 8330 | 115.31 | 1.4861 | 61.781 | 0.004354 | 83.375 | 1112 | 1028.625
8331 | 1.4865 | 115.32 | 61.78 | 0.0043552 | 83.385 | 1112 |  | 8331 | 115.32 | 1.4865 | 61.78 | 0.0043552 | 83.385 | 1112 | 1028.615
8332 | 1.487 | 115.33 | 61.78 | 0.0043564 | 83.395 | 1112 |  | 8332 | 115.33 | 1.487 | 61.78 | 0.0043564 | 83.395 | 1112 | 1028.605
8333 | 1.4874 | 115.34 | 61.78 | 0.0043575 | 83.405 | 1112 |  | 8333 | 115.34 | 1.4874 | 61.78 | 0.0043575 | 83.405 | 1112 | 1028.595
8334 | 1.4878 | 115.35 | 61.78 | 0.0043587 | 83.415 | 1112 |  | 8334 | 115.35 | 1.4878 | 61.78 | 0.0043587 | 83.415 | 1112 | 1028.585
8335 | 1.4882 | 115.36 | 61.78 | 0.0043598 | 83.425 | 1112 |  | 8335 | 115.36 | 1.4882 | 61.78 | 0.0043598 | 83.425 | 1112 | 1028.575
8336 | 1.4886 | 115.37 | 61.78 | 0.004361 | 83.435 | 1112 |  | 8336 | 115.37 | 1.4886 | 61.78 | 0.004361 | 83.435 | 1112 | 1028.565
8337 | 1.4891 | 115.38 | 61.78 | 0.0043622 | 83.445 | 1112 |  | 8337 | 115.38 | 1.4891 | 61.78 | 0.0043622 | 83.445 | 1112 | 1028.555
8338 | 1.4895 | 115.39 | 61.779 | 0.0043633 | 83.455 | 1112 |  | 8338 | 115.39 | 1.4895 | 61.779 | 0.0043633 | 83.455 | 1112 | 1028.545
8339 | 1.4899 | 115.4 | 61.779 | 0.0043645 | 83.465 | 1112 |  | 8339 | 115.4 | 1.4899 | 61.779 | 0.0043645 | 83.465 | 1112 | 1028.535
8340 | 1.4903 | 115.41 | 61.779 | 0.0043657 | 83.475 | 1112 |  | 8340 | 115.41 | 1.4903 | 61.779 | 0.0043657 | 83.475 | 1112 | 1028.525
8341 | 1.4908 | 115.42 | 61.779 | 0.0043668 | 83.485 | 1112 |  | 8341 | 115.42 | 1.4908 | 61.779 | 0.0043668 | 83.485 | 1112 | 1028.515
8342 | 1.4912 | 115.43 | 61.779 | 0.004368 | 83.495 | 1112 |  | 8342 | 115.43 | 1.4912 | 61.779 | 0.004368 | 83.495 | 1112 | 1028.505
8343 | 1.4916 | 115.44 | 61.779 | 0.0043691 | 83.505 | 1112 |  | 8343 | 115.44 | 1.4916 | 61.779 | 0.0043691 | 83.505 | 1112 | 1028.495
8344 | 1.492 | 115.45 | 61.779 | 0.0043703 | 83.515 | 1112 |  | 8344 | 115.45 | 1.492 | 61.779 | 0.0043703 | 83.515 | 1112 | 1028.485
8345 | 1.4924 | 115.46 | 61.778 | 0.0043715 | 83.525 | 1112 |  | 8345 | 115.46 | 1.4924 | 61.778 | 0.0043715 | 83.525 | 1112 | 1028.475
8346 | 1.4929 | 115.47 | 61.778 | 0.0043726 | 83.535 | 1112 |  | 8346 | 115.47 | 1.4929 | 61.778 | 0.0043726 | 83.535 | 1112 | 1028.465
8347 | 1.4933 | 115.48 | 61.778 | 0.0043738 | 83.545 | 1112 |  | 8347 | 115.48 | 1.4933 | 61.778 | 0.0043738 | 83.545 | 1112 | 1028.455
8348 | 1.4937 | 115.49 | 61.778 | 0.004375 | 83.555 | 1112 |  | 8348 | 115.49 | 1.4937 | 61.778 | 0.004375 | 83.555 | 1112 | 1028.445
8349 | 1.4941 | 115.5 | 61.778 | 0.0043761 | 83.565 | 1112 |  | 8349 | 115.5 | 1.4941 | 61.778 | 0.0043761 | 83.565 | 1112 | 1028.435
8350 | 1.4946 | 115.51 | 61.778 | 0.0043773 | 83.575 | 1112.1 |  | 8350 | 115.51 | 1.4946 | 61.778 | 0.0043773 | 83.575 | 1112.1 | 1028.525
8351 | 1.495 | 115.52 | 61.777 | 0.0043785 | 83.585 | 1112.1 |  | 8351 | 115.52 | 1.495 | 61.777 | 0.0043785 | 83.585 | 1112.1 | 1028.515
8352 | 1.4954 | 115.53 | 61.777 | 0.0043796 | 83.595 | 1112.1 |  | 8352 | 115.53 | 1.4954 | 61.777 | 0.0043796 | 83.595 | 1112.1 | 1028.505
8353 | 1.4958 | 115.54 | 61.777 | 0.0043808 | 83.605 | 1112.1 |  | 8353 | 115.54 | 1.4958 | 61.777 | 0.0043808 | 83.605 | 1112.1 | 1028.495
8354 | 1.4962 | 115.55 | 61.777 | 0.0043819 | 83.615 | 1112.1 |  | 8354 | 115.55 | 1.4962 | 61.777 | 0.0043819 | 83.615 | 1112.1 | 1028.485
8355 | 1.4967 | 115.56 | 61.777 | 0.0043831 | 83.625 | 1112.1 |  | 8355 | 115.56 | 1.4967 | 61.777 | 0.0043831 | 83.625 | 1112.1 | 1028.475
8356 | 1.4971 | 115.57 | 61.777 | 0.0043843 | 83.635 | 1112.1 |  | 8356 | 115.57 | 1.4971 | 61.777 | 0.0043843 | 83.635 | 1112.1 | 1028.465
8357 | 1.4975 | 115.58 | 61.777 | 0.0043854 | 83.645 | 1112.1 |  | 8357 | 115.58 | 1.4975 | 61.777 | 0.0043854 | 83.645 | 1112.1 | 1028.455
8358 | 1.4979 | 115.59 | 61.776 | 0.0043866 | 83.655 | 1112.1 |  | 8358 | 115.59 | 1.4979 | 61.776 | 0.0043866 | 83.655 | 1112.1 | 1028.445
8359 | 1.4984 | 115.6 | 61.776 | 0.0043878 | 83.665 | 1112.1 |  | 8359 | 115.6 | 1.4984 | 61.776 | 0.0043878 | 83.665 | 1112.1 | 1028.435
8360 | 1.4988 | 115.61 | 61.776 | 0.0043889 | 83.675 | 1112.1 |  | 8360 | 115.61 | 1.4988 | 61.776 | 0.0043889 | 83.675 | 1112.1 | 1028.425
8361 | 1.4992 | 115.62 | 61.776 | 0.0043901 | 83.685 | 1112.1 |  | 8361 | 115.62 | 1.4992 | 61.776 | 0.0043901 | 83.685 | 1112.1 | 1028.415
8362 | 1.4996 | 115.63 | 61.776 | 0.0043913 | 83.695 | 1112.1 |  | 8362 | 115.63 | 1.4996 | 61.776 | 0.0043913 | 83.695 | 1112.1 | 1028.405
8363 | 1.5001 | 115.64 | 61.776 | 0.0043924 | 83.705 | 1112.1 |  | 8363 | 115.64 | 1.5001 | 61.776 | 0.0043924 | 83.705 | 1112.1 | 1028.395
8364 | 1.5005 | 115.65 | 61.776 | 0.0043936 | 83.715 | 1112.1 |  | 8364 | 115.65 | 1.5005 | 61.776 | 0.0043936 | 83.715 | 1112.1 | 1028.385
8365 | 1.5009 | 115.66 | 61.775 | 0.0043948 | 83.725 | 1112.1 |  | 8365 | 115.66 | 1.5009 | 61.775 | 0.0043948 | 83.725 | 1112.1 | 1028.375
8366 | 1.5013 | 115.67 | 61.775 | 0.004396 | 83.735 | 1112.1 |  | 8366 | 115.67 | 1.5013 | 61.775 | 0.004396 | 83.735 | 1112.1 | 1028.365
8367 | 1.5018 | 115.68 | 61.775 | 0.0043971 | 83.745 | 1112.1 |  | 8367 | 115.68 | 1.5018 | 61.775 | 0.0043971 | 83.745 | 1112.1 | 1028.355
8368 | 1.5022 | 115.69 | 61.775 | 0.0043983 | 83.755 | 1112.1 |  | 8368 | 115.69 | 1.5022 | 61.775 | 0.0043983 | 83.755 | 1112.1 | 1028.345
8369 | 1.5026 | 115.7 | 61.775 | 0.0043995 | 83.765 | 1112.1 |  | 8369 | 115.7 | 1.5026 | 61.775 | 0.0043995 | 83.765 | 1112.1 | 1028.335
8370 | 1.503 | 115.71 | 61.775 | 0.0044006 | 83.775 | 1112.1 |  | 8370 | 115.71 | 1.503 | 61.775 | 0.0044006 | 83.775 | 1112.1 | 1028.325
8371 | 1.5035 | 115.72 | 61.775 | 0.0044018 | 83.785 | 1112.1 |  | 8371 | 115.72 | 1.5035 | 61.775 | 0.0044018 | 83.785 | 1112.1 | 1028.315
8372 | 1.5039 | 115.73 | 61.774 | 0.004403 | 83.795 | 1112.1 |  | 8372 | 115.73 | 1.5039 | 61.774 | 0.004403 | 83.795 | 1112.1 | 1028.305
8373 | 1.5043 | 115.74 | 61.774 | 0.0044041 | 83.805 | 1112.1 |  | 8373 | 115.74 | 1.5043 | 61.774 | 0.0044041 | 83.805 | 1112.1 | 1028.295
8374 | 1.5047 | 115.75 | 61.774 | 0.0044053 | 83.815 | 1112.2 |  | 8374 | 115.75 | 1.5047 | 61.774 | 0.0044053 | 83.815 | 1112.2 | 1028.385
8375 | 1.5052 | 115.76 | 61.774 | 0.0044065 | 83.825 | 1112.2 |  | 8375 | 115.76 | 1.5052 | 61.774 | 0.0044065 | 83.825 | 1112.2 | 1028.375
8376 | 1.5056 | 115.77 | 61.774 | 0.0044077 | 83.835 | 1112.2 |  | 8376 | 115.77 | 1.5056 | 61.774 | 0.0044077 | 83.835 | 1112.2 | 1028.365
8377 | 1.506 | 115.78 | 61.774 | 0.0044088 | 83.845 | 1112.2 |  | 8377 | 115.78 | 1.506 | 61.774 | 0.0044088 | 83.845 | 1112.2 | 1028.355
8378 | 1.5064 | 115.79 | 61.773 | 0.00441 | 83.855 | 1112.2 |  | 8378 | 115.79 | 1.5064 | 61.773 | 0.00441 | 83.855 | 1112.2 | 1028.345
8379 | 1.5069 | 115.8 | 61.773 | 0.0044112 | 83.865 | 1112.2 |  | 8379 | 115.8 | 1.5069 | 61.773 | 0.0044112 | 83.865 | 1112.2 | 1028.335
8380 | 1.5073 | 115.81 | 61.773 | 0.0044123 | 83.875 | 1112.2 |  | 8380 | 115.81 | 1.5073 | 61.773 | 0.0044123 | 83.875 | 1112.2 | 1028.325
8381 | 1.5077 | 115.82 | 61.773 | 0.0044135 | 83.885 | 1112.2 |  | 8381 | 115.82 | 1.5077 | 61.773 | 0.0044135 | 83.885 | 1112.2 | 1028.315
8382 | 1.5081 | 115.83 | 61.773 | 0.0044147 | 83.895 | 1112.2 |  | 8382 | 115.83 | 1.5081 | 61.773 | 0.0044147 | 83.895 | 1112.2 | 1028.305
8383 | 1.5086 | 115.84 | 61.773 | 0.0044159 | 83.905 | 1112.2 |  | 8383 | 115.84 | 1.5086 | 61.773 | 0.0044159 | 83.905 | 1112.2 | 1028.295
8384 | 1.509 | 115.85 | 61.773 | 0.004417 | 83.915 | 1112.2 |  | 8384 | 115.85 | 1.509 | 61.773 | 0.004417 | 83.915 | 1112.2 | 1028.285
8385 | 1.5094 | 115.86 | 61.772 | 0.0044182 | 83.925 | 1112.2 |  | 8385 | 115.86 | 1.5094 | 61.772 | 0.0044182 | 83.925 | 1112.2 | 1028.275
8386 | 1.5098 | 115.87 | 61.772 | 0.0044194 | 83.935 | 1112.2 |  | 8386 | 115.87 | 1.5098 | 61.772 | 0.0044194 | 83.935 | 1112.2 | 1028.265
8387 | 1.5103 | 115.88 | 61.772 | 0.0044206 | 83.945 | 1112.2 |  | 8387 | 115.88 | 1.5103 | 61.772 | 0.0044206 | 83.945 | 1112.2 | 1028.255
8388 | 1.5107 | 115.89 | 61.772 | 0.0044217 | 83.954 | 1112.2 |  | 8388 | 115.89 | 1.5107 | 61.772 | 0.0044217 | 83.954 | 1112.2 | 1028.246
8389 | 1.5111 | 115.9 | 61.772 | 0.0044229 | 83.964 | 1112.2 |  | 8389 | 115.9 | 1.5111 | 61.772 | 0.0044229 | 83.964 | 1112.2 | 1028.236
8390 | 1.5115 | 115.91 | 61.772 | 0.0044241 | 83.974 | 1112.2 |  | 8390 | 115.91 | 1.5115 | 61.772 | 0.0044241 | 83.974 | 1112.2 | 1028.226
8391 | 1.512 | 115.92 | 61.772 | 0.0044253 | 83.984 | 1112.2 |  | 8391 | 115.92 | 1.512 | 61.772 | 0.0044253 | 83.984 | 1112.2 | 1028.216
8392 | 1.5124 | 115.93 | 61.771 | 0.0044264 | 83.994 | 1112.2 |  | 8392 | 115.93 | 1.5124 | 61.771 | 0.0044264 | 83.994 | 1112.2 | 1028.206
8393 | 1.5128 | 115.94 | 61.771 | 0.0044276 | 84.004 | 1112.2 |  | 8393 | 115.94 | 1.5128 | 61.771 | 0.0044276 | 84.004 | 1112.2 | 1028.196
8394 | 1.5133 | 115.95 | 61.771 | 0.0044288 | 84.014 | 1112.2 |  | 8394 | 115.95 | 1.5133 | 61.771 | 0.0044288 | 84.014 | 1112.2 | 1028.186
8395 | 1.5137 | 115.96 | 61.771 | 0.00443 | 84.024 | 1112.2 |  | 8395 | 115.96 | 1.5137 | 61.771 | 0.00443 | 84.024 | 1112.2 | 1028.176
8396 | 1.5141 | 115.97 | 61.771 | 0.0044311 | 84.034 | 1112.2 |  | 8396 | 115.97 | 1.5141 | 61.771 | 0.0044311 | 84.034 | 1112.2 | 1028.166
8397 | 1.5145 | 115.98 | 61.771 | 0.0044323 | 84.044 | 1112.3 |  | 8397 | 115.98 | 1.5145 | 61.771 | 0.0044323 | 84.044 | 1112.3 | 1028.256
8398 | 1.515 | 115.99 | 61.77 | 0.0044335 | 84.054 | 1112.3 |  | 8398 | 115.99 | 1.515 | 61.77 | 0.0044335 | 84.054 | 1112.3 | 1028.246
8399 | 1.5154 | 116 | 61.77 | 0.0044347 | 84.064 | 1112.3 |  | 8399 | 116 | 1.5154 | 61.77 | 0.0044347 | 84.064 | 1112.3 | 1028.236
8400 | 1.5158 | 116.01 | 61.77 | 0.0044359 | 84.074 | 1112.3 |  | 8400 | 116.01 | 1.5158 | 61.77 | 0.0044359 | 84.074 | 1112.3 | 1028.226
8401 | 1.5162 | 116.02 | 61.77 | 0.004437 | 84.084 | 1112.3 |  | 8401 | 116.02 | 1.5162 | 61.77 | 0.004437 | 84.084 | 1112.3 | 1028.216
8402 | 1.5167 | 116.03 | 61.77 | 0.0044382 | 84.094 | 1112.3 |  | 8402 | 116.03 | 1.5167 | 61.77 | 0.0044382 | 84.094 | 1112.3 | 1028.206
8403 | 1.5171 | 116.04 | 61.77 | 0.0044394 | 84.104 | 1112.3 |  | 8403 | 116.04 | 1.5171 | 61.77 | 0.0044394 | 84.104 | 1112.3 | 1028.196
8404 | 1.5175 | 116.05 | 61.77 | 0.0044406 | 84.114 | 1112.3 |  | 8404 | 116.05 | 1.5175 | 61.77 | 0.0044406 | 84.114 | 1112.3 | 1028.186
8405 | 1.518 | 116.06 | 61.769 | 0.0044417 | 84.124 | 1112.3 |  | 8405 | 116.06 | 1.518 | 61.769 | 0.0044417 | 84.124 | 1112.3 | 1028.176
8406 | 1.5184 | 116.07 | 61.769 | 0.0044429 | 84.134 | 1112.3 |  | 8406 | 116.07 | 1.5184 | 61.769 | 0.0044429 | 84.134 | 1112.3 | 1028.166
8407 | 1.5188 | 116.08 | 61.769 | 0.0044441 | 84.144 | 1112.3 |  | 8407 | 116.08 | 1.5188 | 61.769 | 0.0044441 | 84.144 | 1112.3 | 1028.156
8408 | 1.5192 | 116.09 | 61.769 | 0.0044453 | 84.154 | 1112.3 |  | 8408 | 116.09 | 1.5192 | 61.769 | 0.0044453 | 84.154 | 1112.3 | 1028.146
8409 | 1.5197 | 116.1 | 61.769 | 0.0044465 | 84.164 | 1112.3 |  | 8409 | 116.1 | 1.5197 | 61.769 | 0.0044465 | 84.164 | 1112.3 | 1028.136
8410 | 1.5201 | 116.11 | 61.769 | 0.0044476 | 84.174 | 1112.3 |  | 8410 | 116.11 | 1.5201 | 61.769 | 0.0044476 | 84.174 | 1112.3 | 1028.126
8411 | 1.5205 | 116.12 | 61.769 | 0.0044488 | 84.184 | 1112.3 |  | 8411 | 116.12 | 1.5205 | 61.769 | 0.0044488 | 84.184 | 1112.3 | 1028.116
8412 | 1.521 | 116.13 | 61.768 | 0.00445 | 84.194 | 1112.3 |  | 8412 | 116.13 | 1.521 | 61.768 | 0.00445 | 84.194 | 1112.3 | 1028.106
8413 | 1.5214 | 116.14 | 61.768 | 0.0044512 | 84.204 | 1112.3 |  | 8413 | 116.14 | 1.5214 | 61.768 | 0.0044512 | 84.204 | 1112.3 | 1028.096
8414 | 1.5218 | 116.15 | 61.768 | 0.0044524 | 84.214 | 1112.3 |  | 8414 | 116.15 | 1.5218 | 61.768 | 0.0044524 | 84.214 | 1112.3 | 1028.086
8415 | 1.5222 | 116.16 | 61.768 | 0.0044536 | 84.224 | 1112.3 |  | 8415 | 116.16 | 1.5222 | 61.768 | 0.0044536 | 84.224 | 1112.3 | 1028.076
8416 | 1.5227 | 116.17 | 61.768 | 0.0044547 | 84.234 | 1112.3 |  | 8416 | 116.17 | 1.5227 | 61.768 | 0.0044547 | 84.234 | 1112.3 | 1028.066
8417 | 1.5231 | 116.18 | 61.768 | 0.0044559 | 84.244 | 1112.3 |  | 8417 | 116.18 | 1.5231 | 61.768 | 0.0044559 | 84.244 | 1112.3 | 1028.056
8418 | 1.5235 | 116.19 | 61.768 | 0.0044571 | 84.254 | 1112.3 |  | 8418 | 116.19 | 1.5235 | 61.768 | 0.0044571 | 84.254 | 1112.3 | 1028.046
8419 | 1.524 | 116.2 | 61.767 | 0.0044583 | 84.264 | 1112.3 |  | 8419 | 116.2 | 1.524 | 61.767 | 0.0044583 | 84.264 | 1112.3 | 1028.036
8420 | 1.5244 | 116.21 | 61.767 | 0.0044595 | 84.274 | 1112.3 |  | 8420 | 116.21 | 1.5244 | 61.767 | 0.0044595 | 84.274 | 1112.3 | 1028.026
8421 | 1.5248 | 116.22 | 61.767 | 0.0044606 | 84.284 | 1112.4 |  | 8421 | 116.22 | 1.5248 | 61.767 | 0.0044606 | 84.284 | 1112.4 | 1028.116
8422 | 1.5253 | 116.23 | 61.767 | 0.0044618 | 84.294 | 1112.4 |  | 8422 | 116.23 | 1.5253 | 61.767 | 0.0044618 | 84.294 | 1112.4 | 1028.106
8423 | 1.5257 | 116.24 | 61.767 | 0.004463 | 84.304 | 1112.4 |  | 8423 | 116.24 | 1.5257 | 61.767 | 0.004463 | 84.304 | 1112.4 | 1028.096
8424 | 1.5261 | 116.25 | 61.767 | 0.0044642 | 84.314 | 1112.4 |  | 8424 | 116.25 | 1.5261 | 61.767 | 0.0044642 | 84.314 | 1112.4 | 1028.086
8425 | 1.5265 | 116.26 | 61.766 | 0.0044654 | 84.324 | 1112.4 |  | 8425 | 116.26 | 1.5265 | 61.766 | 0.0044654 | 84.324 | 1112.4 | 1028.076
8426 | 1.527 | 116.27 | 61.766 | 0.0044666 | 84.334 | 1112.4 |  | 8426 | 116.27 | 1.527 | 61.766 | 0.0044666 | 84.334 | 1112.4 | 1028.066
8427 | 1.5274 | 116.28 | 61.766 | 0.0044678 | 84.344 | 1112.4 |  | 8427 | 116.28 | 1.5274 | 61.766 | 0.0044678 | 84.344 | 1112.4 | 1028.056
8428 | 1.5278 | 116.29 | 61.766 | 0.0044689 | 84.354 | 1112.4 |  | 8428 | 116.29 | 1.5278 | 61.766 | 0.0044689 | 84.354 | 1112.4 | 1028.046
8429 | 1.5283 | 116.3 | 61.766 | 0.0044701 | 84.364 | 1112.4 |  | 8429 | 116.3 | 1.5283 | 61.766 | 0.0044701 | 84.364 | 1112.4 | 1028.036
8430 | 1.5287 | 116.31 | 61.766 | 0.0044713 | 84.374 | 1112.4 |  | 8430 | 116.31 | 1.5287 | 61.766 | 0.0044713 | 84.374 | 1112.4 | 1028.026
8431 | 1.5291 | 116.32 | 61.766 | 0.0044725 | 84.384 | 1112.4 |  | 8431 | 116.32 | 1.5291 | 61.766 | 0.0044725 | 84.384 | 1112.4 | 1028.016
8432 | 1.5296 | 116.33 | 61.765 | 0.0044737 | 84.394 | 1112.4 |  | 8432 | 116.33 | 1.5296 | 61.765 | 0.0044737 | 84.394 | 1112.4 | 1028.006
8433 | 1.53 | 116.34 | 61.765 | 0.0044749 | 84.404 | 1112.4 |  | 8433 | 116.34 | 1.53 | 61.765 | 0.0044749 | 84.404 | 1112.4 | 1027.996
8434 | 1.5304 | 116.35 | 61.765 | 0.0044761 | 84.414 | 1112.4 |  | 8434 | 116.35 | 1.5304 | 61.765 | 0.0044761 | 84.414 | 1112.4 | 1027.986
8435 | 1.5309 | 116.36 | 61.765 | 0.0044772 | 84.424 | 1112.4 |  | 8435 | 116.36 | 1.5309 | 61.765 | 0.0044772 | 84.424 | 1112.4 | 1027.976
8436 | 1.5313 | 116.37 | 61.765 | 0.0044784 | 84.434 | 1112.4 |  | 8436 | 116.37 | 1.5313 | 61.765 | 0.0044784 | 84.434 | 1112.4 | 1027.966
8437 | 1.5317 | 116.38 | 61.765 | 0.0044796 | 84.444 | 1112.4 |  | 8437 | 116.38 | 1.5317 | 61.765 | 0.0044796 | 84.444 | 1112.4 | 1027.956
8438 | 1.5322 | 116.39 | 61.765 | 0.0044808 | 84.454 | 1112.4 |  | 8438 | 116.39 | 1.5322 | 61.765 | 0.0044808 | 84.454 | 1112.4 | 1027.946
8439 | 1.5326 | 116.4 | 61.764 | 0.004482 | 84.464 | 1112.4 |  | 8439 | 116.4 | 1.5326 | 61.764 | 0.004482 | 84.464 | 1112.4 | 1027.936
8440 | 1.533 | 116.41 | 61.764 | 0.0044832 | 84.474 | 1112.4 |  | 8440 | 116.41 | 1.533 | 61.764 | 0.0044832 | 84.474 | 1112.4 | 1027.926
8441 | 1.5334 | 116.42 | 61.764 | 0.0044844 | 84.484 | 1112.4 |  | 8441 | 116.42 | 1.5334 | 61.764 | 0.0044844 | 84.484 | 1112.4 | 1027.916
8442 | 1.5339 | 116.43 | 61.764 | 0.0044856 | 84.494 | 1112.4 |  | 8442 | 116.43 | 1.5339 | 61.764 | 0.0044856 | 84.494 | 1112.4 | 1027.906
8443 | 1.5343 | 116.44 | 61.764 | 0.0044867 | 84.504 | 1112.4 |  | 8443 | 116.44 | 1.5343 | 61.764 | 0.0044867 | 84.504 | 1112.4 | 1027.896
8444 | 1.5347 | 116.45 | 61.764 | 0.0044879 | 84.514 | 1112.5 |  | 8444 | 116.45 | 1.5347 | 61.764 | 0.0044879 | 84.514 | 1112.5 | 1027.986
8445 | 1.5352 | 116.46 | 61.763 | 0.0044891 | 84.524 | 1112.5 |  | 8445 | 116.46 | 1.5352 | 61.763 | 0.0044891 | 84.524 | 1112.5 | 1027.976
8446 | 1.5356 | 116.47 | 61.763 | 0.0044903 | 84.534 | 1112.5 |  | 8446 | 116.47 | 1.5356 | 61.763 | 0.0044903 | 84.534 | 1112.5 | 1027.966
8447 | 1.536 | 116.48 | 61.763 | 0.0044915 | 84.544 | 1112.5 |  | 8447 | 116.48 | 1.536 | 61.763 | 0.0044915 | 84.544 | 1112.5 | 1027.956
8448 | 1.5365 | 116.49 | 61.763 | 0.0044927 | 84.554 | 1112.5 |  | 8448 | 116.49 | 1.5365 | 61.763 | 0.0044927 | 84.554 | 1112.5 | 1027.946
8449 | 1.5369 | 116.5 | 61.763 | 0.0044939 | 84.564 | 1112.5 |  | 8449 | 116.5 | 1.5369 | 61.763 | 0.0044939 | 84.564 | 1112.5 | 1027.936
8450 | 1.5373 | 116.51 | 61.763 | 0.0044951 | 84.574 | 1112.5 |  | 8450 | 116.51 | 1.5373 | 61.763 | 0.0044951 | 84.574 | 1112.5 | 1027.926
8451 | 1.5378 | 116.52 | 61.763 | 0.0044963 | 84.584 | 1112.5 |  | 8451 | 116.52 | 1.5378 | 61.763 | 0.0044963 | 84.584 | 1112.5 | 1027.916
8452 | 1.5382 | 116.53 | 61.762 | 0.0044975 | 84.594 | 1112.5 |  | 8452 | 116.53 | 1.5382 | 61.762 | 0.0044975 | 84.594 | 1112.5 | 1027.906
8453 | 1.5386 | 116.54 | 61.762 | 0.0044987 | 84.604 | 1112.5 |  | 8453 | 116.54 | 1.5386 | 61.762 | 0.0044987 | 84.604 | 1112.5 | 1027.896
8454 | 1.5391 | 116.55 | 61.762 | 0.0044998 | 84.614 | 1112.5 |  | 8454 | 116.55 | 1.5391 | 61.762 | 0.0044998 | 84.614 | 1112.5 | 1027.886
8455 | 1.5395 | 116.56 | 61.762 | 0.004501 | 84.624 | 1112.5 |  | 8455 | 116.56 | 1.5395 | 61.762 | 0.004501 | 84.624 | 1112.5 | 1027.876
8456 | 1.5399 | 116.57 | 61.762 | 0.0045022 | 84.634 | 1112.5 |  | 8456 | 116.57 | 1.5399 | 61.762 | 0.0045022 | 84.634 | 1112.5 | 1027.866
8457 | 1.5404 | 116.58 | 61.762 | 0.0045034 | 84.644 | 1112.5 |  | 8457 | 116.58 | 1.5404 | 61.762 | 0.0045034 | 84.644 | 1112.5 | 1027.856
8458 | 1.5408 | 116.59 | 61.762 | 0.0045046 | 84.654 | 1112.5 |  | 8458 | 116.59 | 1.5408 | 61.762 | 0.0045046 | 84.654 | 1112.5 | 1027.846
8459 | 1.5412 | 116.6 | 61.761 | 0.0045058 | 84.664 | 1112.5 |  | 8459 | 116.6 | 1.5412 | 61.761 | 0.0045058 | 84.664 | 1112.5 | 1027.836
8460 | 1.5417 | 116.61 | 61.761 | 0.004507 | 84.674 | 1112.5 |  | 8460 | 116.61 | 1.5417 | 61.761 | 0.004507 | 84.674 | 1112.5 | 1027.826
8461 | 1.5421 | 116.62 | 61.761 | 0.0045082 | 84.684 | 1112.5 |  | 8461 | 116.62 | 1.5421 | 61.761 | 0.0045082 | 84.684 | 1112.5 | 1027.816
8462 | 1.5425 | 116.63 | 61.761 | 0.0045094 | 84.694 | 1112.5 |  | 8462 | 116.63 | 1.5425 | 61.761 | 0.0045094 | 84.694 | 1112.5 | 1027.806
8463 | 1.543 | 116.64 | 61.761 | 0.0045106 | 84.704 | 1112.5 |  | 8463 | 116.64 | 1.543 | 61.761 | 0.0045106 | 84.704 | 1112.5 | 1027.796
8464 | 1.5434 | 116.65 | 61.761 | 0.0045118 | 84.714 | 1112.5 |  | 8464 | 116.65 | 1.5434 | 61.761 | 0.0045118 | 84.714 | 1112.5 | 1027.786
8465 | 1.5439 | 116.66 | 61.76 | 0.004513 | 84.724 | 1112.5 |  | 8465 | 116.66 | 1.5439 | 61.76 | 0.004513 | 84.724 | 1112.5 | 1027.776
8466 | 1.5443 | 116.67 | 61.76 | 0.0045142 | 84.734 | 1112.5 |  | 8466 | 116.67 | 1.5443 | 61.76 | 0.0045142 | 84.734 | 1112.5 | 1027.766
8467 | 1.5447 | 116.68 | 61.76 | 0.0045154 | 84.744 | 1112.5 |  | 8467 | 116.68 | 1.5447 | 61.76 | 0.0045154 | 84.744 | 1112.5 | 1027.756
8468 | 1.5452 | 116.69 | 61.76 | 0.0045166 | 84.754 | 1112.6 |  | 8468 | 116.69 | 1.5452 | 61.76 | 0.0045166 | 84.754 | 1112.6 | 1027.846
8469 | 1.5456 | 116.7 | 61.76 | 0.0045178 | 84.764 | 1112.6 |  | 8469 | 116.7 | 1.5456 | 61.76 | 0.0045178 | 84.764 | 1112.6 | 1027.836
8470 | 1.546 | 116.71 | 61.76 | 0.004519 | 84.774 | 1112.6 |  | 8470 | 116.71 | 1.546 | 61.76 | 0.004519 | 84.774 | 1112.6 | 1027.826
8471 | 1.5465 | 116.72 | 61.76 | 0.0045202 | 84.784 | 1112.6 |  | 8471 | 116.72 | 1.5465 | 61.76 | 0.0045202 | 84.784 | 1112.6 | 1027.816
8472 | 1.5469 | 116.73 | 61.759 | 0.0045214 | 84.794 | 1112.6 |  | 8472 | 116.73 | 1.5469 | 61.759 | 0.0045214 | 84.794 | 1112.6 | 1027.806
8473 | 1.5473 | 116.74 | 61.759 | 0.0045225 | 84.804 | 1112.6 |  | 8473 | 116.74 | 1.5473 | 61.759 | 0.0045225 | 84.804 | 1112.6 | 1027.796
8474 | 1.5478 | 116.75 | 61.759 | 0.0045237 | 84.814 | 1112.6 |  | 8474 | 116.75 | 1.5478 | 61.759 | 0.0045237 | 84.814 | 1112.6 | 1027.786
8475 | 1.5482 | 116.76 | 61.759 | 0.0045249 | 84.824 | 1112.6 |  | 8475 | 116.76 | 1.5482 | 61.759 | 0.0045249 | 84.824 | 1112.6 | 1027.776
8476 | 1.5486 | 116.77 | 61.759 | 0.0045261 | 84.834 | 1112.6 |  | 8476 | 116.77 | 1.5486 | 61.759 | 0.0045261 | 84.834 | 1112.6 | 1027.766
8477 | 1.5491 | 116.78 | 61.759 | 0.0045273 | 84.844 | 1112.6 |  | 8477 | 116.78 | 1.5491 | 61.759 | 0.0045273 | 84.844 | 1112.6 | 1027.756
8478 | 1.5495 | 116.79 | 61.759 | 0.0045285 | 84.854 | 1112.6 |  | 8478 | 116.79 | 1.5495 | 61.759 | 0.0045285 | 84.854 | 1112.6 | 1027.746
8479 | 1.5499 | 116.8 | 61.758 | 0.0045297 | 84.864 | 1112.6 |  | 8479 | 116.8 | 1.5499 | 61.758 | 0.0045297 | 84.864 | 1112.6 | 1027.736
8480 | 1.5504 | 116.81 | 61.758 | 0.0045309 | 84.874 | 1112.6 |  | 8480 | 116.81 | 1.5504 | 61.758 | 0.0045309 | 84.874 | 1112.6 | 1027.726
8481 | 1.5508 | 116.82 | 61.758 | 0.0045321 | 84.884 | 1112.6 |  | 8481 | 116.82 | 1.5508 | 61.758 | 0.0045321 | 84.884 | 1112.6 | 1027.716
8482 | 1.5513 | 116.83 | 61.758 | 0.0045333 | 84.894 | 1112.6 |  | 8482 | 116.83 | 1.5513 | 61.758 | 0.0045333 | 84.894 | 1112.6 | 1027.706
8483 | 1.5517 | 116.84 | 61.758 | 0.0045345 | 84.904 | 1112.6 |  | 8483 | 116.84 | 1.5517 | 61.758 | 0.0045345 | 84.904 | 1112.6 | 1027.696
8484 | 1.5521 | 116.85 | 61.758 | 0.0045357 | 84.914 | 1112.6 |  | 8484 | 116.85 | 1.5521 | 61.758 | 0.0045357 | 84.914 | 1112.6 | 1027.686
8485 | 1.5526 | 116.86 | 61.757 | 0.0045369 | 84.924 | 1112.6 |  | 8485 | 116.86 | 1.5526 | 61.757 | 0.0045369 | 84.924 | 1112.6 | 1027.676
8486 | 1.553 | 116.87 | 61.757 | 0.0045381 | 84.934 | 1112.6 |  | 8486 | 116.87 | 1.553 | 61.757 | 0.0045381 | 84.934 | 1112.6 | 1027.666
8487 | 1.5534 | 116.88 | 61.757 | 0.0045393 | 84.944 | 1112.6 |  | 8487 | 116.88 | 1.5534 | 61.757 | 0.0045393 | 84.944 | 1112.6 | 1027.656
8488 | 1.5539 | 116.89 | 61.757 | 0.0045405 | 84.954 | 1112.6 |  | 8488 | 116.89 | 1.5539 | 61.757 | 0.0045405 | 84.954 | 1112.6 | 1027.646
8489 | 1.5543 | 116.9 | 61.757 | 0.0045417 | 84.964 | 1112.6 |  | 8489 | 116.9 | 1.5543 | 61.757 | 0.0045417 | 84.964 | 1112.6 | 1027.636
8490 | 1.5548 | 116.91 | 61.757 | 0.0045429 | 84.974 | 1112.6 |  | 8490 | 116.91 | 1.5548 | 61.757 | 0.0045429 | 84.974 | 1112.6 | 1027.626
8491 | 1.5552 | 116.92 | 61.757 | 0.0045441 | 84.984 | 1112.6 |  | 8491 | 116.92 | 1.5552 | 61.757 | 0.0045441 | 84.984 | 1112.6 | 1027.616
8492 | 1.5556 | 116.93 | 61.756 | 0.0045453 | 84.994 | 1112.7 |  | 8492 | 116.93 | 1.5556 | 61.756 | 0.0045453 | 84.994 | 1112.7 | 1027.706
8493 | 1.5561 | 116.94 | 61.756 | 0.0045466 | 85.004 | 1112.7 |  | 8493 | 116.94 | 1.5561 | 61.756 | 0.0045466 | 85.004 | 1112.7 | 1027.696
8494 | 1.5565 | 116.95 | 61.756 | 0.0045478 | 85.014 | 1112.7 |  | 8494 | 116.95 | 1.5565 | 61.756 | 0.0045478 | 85.014 | 1112.7 | 1027.686
8495 | 1.5569 | 116.96 | 61.756 | 0.004549 | 85.024 | 1112.7 |  | 8495 | 116.96 | 1.5569 | 61.756 | 0.004549 | 85.024 | 1112.7 | 1027.676
8496 | 1.5574 | 116.97 | 61.756 | 0.0045502 | 85.034 | 1112.7 |  | 8496 | 116.97 | 1.5574 | 61.756 | 0.0045502 | 85.034 | 1112.7 | 1027.666
8497 | 1.5578 | 116.98 | 61.756 | 0.0045514 | 85.044 | 1112.7 |  | 8497 | 116.98 | 1.5578 | 61.756 | 0.0045514 | 85.044 | 1112.7 | 1027.656
8498 | 1.5583 | 116.99 | 61.756 | 0.0045526 | 85.054 | 1112.7 |  | 8498 | 116.99 | 1.5583 | 61.756 | 0.0045526 | 85.054 | 1112.7 | 1027.646
8499 | 1.5587 | 117 | 61.755 | 0.0045538 | 85.064 | 1112.7 |  | 8499 | 117 | 1.5587 | 61.755 | 0.0045538 | 85.064 | 1112.7 | 1027.636
8500 | 1.5591 | 117.01 | 61.755 | 0.004555 | 85.074 | 1112.7 |  | 8500 | 117.01 | 1.5591 | 61.755 | 0.004555 | 85.074 | 1112.7 | 1027.626
8501 | 1.5596 | 117.02 | 61.755 | 0.0045562 | 85.084 | 1112.7 |  | 8501 | 117.02 | 1.5596 | 61.755 | 0.0045562 | 85.084 | 1112.7 | 1027.616
8502 | 1.56 | 117.03 | 61.755 | 0.0045574 | 85.094 | 1112.7 |  | 8502 | 117.03 | 1.56 | 61.755 | 0.0045574 | 85.094 | 1112.7 | 1027.606
8503 | 1.5604 | 117.04 | 61.755 | 0.0045586 | 85.104 | 1112.7 |  | 8503 | 117.04 | 1.5604 | 61.755 | 0.0045586 | 85.104 | 1112.7 | 1027.596
8504 | 1.5609 | 117.05 | 61.755 | 0.0045598 | 85.114 | 1112.7 |  | 8504 | 117.05 | 1.5609 | 61.755 | 0.0045598 | 85.114 | 1112.7 | 1027.586
8505 | 1.5613 | 117.06 | 61.754 | 0.004561 | 85.124 | 1112.7 |  | 8505 | 117.06 | 1.5613 | 61.754 | 0.004561 | 85.124 | 1112.7 | 1027.576
8506 | 1.5618 | 117.07 | 61.754 | 0.0045622 | 85.134 | 1112.7 |  | 8506 | 117.07 | 1.5618 | 61.754 | 0.0045622 | 85.134 | 1112.7 | 1027.566
8507 | 1.5622 | 117.08 | 61.754 | 0.0045634 | 85.144 | 1112.7 |  | 8507 | 117.08 | 1.5622 | 61.754 | 0.0045634 | 85.144 | 1112.7 | 1027.556
8508 | 1.5626 | 117.09 | 61.754 | 0.0045646 | 85.154 | 1112.7 |  | 8508 | 117.09 | 1.5626 | 61.754 | 0.0045646 | 85.154 | 1112.7 | 1027.546
8509 | 1.5631 | 117.1 | 61.754 | 0.0045658 | 85.164 | 1112.7 |  | 8509 | 117.1 | 1.5631 | 61.754 | 0.0045658 | 85.164 | 1112.7 | 1027.536
8510 | 1.5635 | 117.11 | 61.754 | 0.004567 | 85.174 | 1112.7 |  | 8510 | 117.11 | 1.5635 | 61.754 | 0.004567 | 85.174 | 1112.7 | 1027.526
8511 | 1.564 | 117.12 | 61.754 | 0.0045682 | 85.184 | 1112.7 |  | 8511 | 117.12 | 1.564 | 61.754 | 0.0045682 | 85.184 | 1112.7 | 1027.516
8512 | 1.5644 | 117.13 | 61.753 | 0.0045695 | 85.194 | 1112.7 |  | 8512 | 117.13 | 1.5644 | 61.753 | 0.0045695 | 85.194 | 1112.7 | 1027.506
8513 | 1.5648 | 117.14 | 61.753 | 0.0045707 | 85.204 | 1112.7 |  | 8513 | 117.14 | 1.5648 | 61.753 | 0.0045707 | 85.204 | 1112.7 | 1027.496
8514 | 1.5653 | 117.15 | 61.753 | 0.0045719 | 85.214 | 1112.7 |  | 8514 | 117.15 | 1.5653 | 61.753 | 0.0045719 | 85.214 | 1112.7 | 1027.486
8515 | 1.5657 | 117.16 | 61.753 | 0.0045731 | 85.224 | 1112.8 |  | 8515 | 117.16 | 1.5657 | 61.753 | 0.0045731 | 85.224 | 1112.8 | 1027.576
8516 | 1.5662 | 117.17 | 61.753 | 0.0045743 | 85.234 | 1112.8 |  | 8516 | 117.17 | 1.5662 | 61.753 | 0.0045743 | 85.234 | 1112.8 | 1027.566
8517 | 1.5666 | 117.18 | 61.753 | 0.0045755 | 85.244 | 1112.8 |  | 8517 | 117.18 | 1.5666 | 61.753 | 0.0045755 | 85.244 | 1112.8 | 1027.556
8518 | 1.567 | 117.19 | 61.753 | 0.0045767 | 85.254 | 1112.8 |  | 8518 | 117.19 | 1.567 | 61.753 | 0.0045767 | 85.254 | 1112.8 | 1027.546
8519 | 1.5675 | 117.2 | 61.752 | 0.0045779 | 85.264 | 1112.8 |  | 8519 | 117.2 | 1.5675 | 61.752 | 0.0045779 | 85.264 | 1112.8 | 1027.536
8520 | 1.5679 | 117.21 | 61.752 | 0.0045791 | 85.274 | 1112.8 |  | 8520 | 117.21 | 1.5679 | 61.752 | 0.0045791 | 85.274 | 1112.8 | 1027.526
8521 | 1.5684 | 117.22 | 61.752 | 0.0045803 | 85.284 | 1112.8 |  | 8521 | 117.22 | 1.5684 | 61.752 | 0.0045803 | 85.284 | 1112.8 | 1027.516
8522 | 1.5688 | 117.23 | 61.752 | 0.0045815 | 85.294 | 1112.8 |  | 8522 | 117.23 | 1.5688 | 61.752 | 0.0045815 | 85.294 | 1112.8 | 1027.506
8523 | 1.5692 | 117.24 | 61.752 | 0.0045828 | 85.304 | 1112.8 |  | 8523 | 117.24 | 1.5692 | 61.752 | 0.0045828 | 85.304 | 1112.8 | 1027.496
8524 | 1.5697 | 117.25 | 61.752 | 0.004584 | 85.314 | 1112.8 |  | 8524 | 117.25 | 1.5697 | 61.752 | 0.004584 | 85.314 | 1112.8 | 1027.486
8525 | 1.5701 | 117.26 | 61.751 | 0.0045852 | 85.324 | 1112.8 |  | 8525 | 117.26 | 1.5701 | 61.751 | 0.0045852 | 85.324 | 1112.8 | 1027.476
8526 | 1.5706 | 117.27 | 61.751 | 0.0045864 | 85.334 | 1112.8 |  | 8526 | 117.27 | 1.5706 | 61.751 | 0.0045864 | 85.334 | 1112.8 | 1027.466
8527 | 1.571 | 117.28 | 61.751 | 0.0045876 | 85.344 | 1112.8 |  | 8527 | 117.28 | 1.571 | 61.751 | 0.0045876 | 85.344 | 1112.8 | 1027.456
8528 | 1.5714 | 117.29 | 61.751 | 0.0045888 | 85.354 | 1112.8 |  | 8528 | 117.29 | 1.5714 | 61.751 | 0.0045888 | 85.354 | 1112.8 | 1027.446
8529 | 1.5719 | 117.3 | 61.751 | 0.00459 | 85.364 | 1112.8 |  | 8529 | 117.3 | 1.5719 | 61.751 | 0.00459 | 85.364 | 1112.8 | 1027.436
8530 | 1.5723 | 117.31 | 61.751 | 0.0045912 | 85.374 | 1112.8 |  | 8530 | 117.31 | 1.5723 | 61.751 | 0.0045912 | 85.374 | 1112.8 | 1027.426
8531 | 1.5728 | 117.32 | 61.751 | 0.0045925 | 85.384 | 1112.8 |  | 8531 | 117.32 | 1.5728 | 61.751 | 0.0045925 | 85.384 | 1112.8 | 1027.416
8532 | 1.5732 | 117.33 | 61.75 | 0.0045937 | 85.394 | 1112.8 |  | 8532 | 117.33 | 1.5732 | 61.75 | 0.0045937 | 85.394 | 1112.8 | 1027.406
8533 | 1.5737 | 117.34 | 61.75 | 0.0045949 | 85.404 | 1112.8 |  | 8533 | 117.34 | 1.5737 | 61.75 | 0.0045949 | 85.404 | 1112.8 | 1027.396
8534 | 1.5741 | 117.35 | 61.75 | 0.0045961 | 85.414 | 1112.8 |  | 8534 | 117.35 | 1.5741 | 61.75 | 0.0045961 | 85.414 | 1112.8 | 1027.386
8535 | 1.5745 | 117.36 | 61.75 | 0.0045973 | 85.424 | 1112.8 |  | 8535 | 117.36 | 1.5745 | 61.75 | 0.0045973 | 85.424 | 1112.8 | 1027.376
8536 | 1.575 | 117.37 | 61.75 | 0.0045985 | 85.434 | 1112.8 |  | 8536 | 117.37 | 1.575 | 61.75 | 0.0045985 | 85.434 | 1112.8 | 1027.366
8537 | 1.5754 | 117.38 | 61.75 | 0.0045997 | 85.444 | 1112.8 |  | 8537 | 117.38 | 1.5754 | 61.75 | 0.0045997 | 85.444 | 1112.8 | 1027.356
8538 | 1.5759 | 117.39 | 61.75 | 0.0046009 | 85.454 | 1112.8 |  | 8538 | 117.39 | 1.5759 | 61.75 | 0.0046009 | 85.454 | 1112.8 | 1027.346
8539 | 1.5763 | 117.4 | 61.749 | 0.0046022 | 85.464 | 1112.9 |  | 8539 | 117.4 | 1.5763 | 61.749 | 0.0046022 | 85.464 | 1112.9 | 1027.436
8540 | 1.5767 | 117.41 | 61.749 | 0.0046034 | 85.473 | 1112.9 |  | 8540 | 117.41 | 1.5767 | 61.749 | 0.0046034 | 85.473 | 1112.9 | 1027.427
8541 | 1.5772 | 117.42 | 61.749 | 0.0046046 | 85.483 | 1112.9 |  | 8541 | 117.42 | 1.5772 | 61.749 | 0.0046046 | 85.483 | 1112.9 | 1027.417
8542 | 1.5776 | 117.43 | 61.749 | 0.0046058 | 85.493 | 1112.9 |  | 8542 | 117.43 | 1.5776 | 61.749 | 0.0046058 | 85.493 | 1112.9 | 1027.407
8543 | 1.5781 | 117.44 | 61.749 | 0.004607 | 85.503 | 1112.9 |  | 8543 | 117.44 | 1.5781 | 61.749 | 0.004607 | 85.503 | 1112.9 | 1027.397
8544 | 1.5785 | 117.45 | 61.749 | 0.0046082 | 85.513 | 1112.9 |  | 8544 | 117.45 | 1.5785 | 61.749 | 0.0046082 | 85.513 | 1112.9 | 1027.387
8545 | 1.579 | 117.46 | 61.748 | 0.0046095 | 85.523 | 1112.9 |  | 8545 | 117.46 | 1.579 | 61.748 | 0.0046095 | 85.523 | 1112.9 | 1027.377
8546 | 1.5794 | 117.47 | 61.748 | 0.0046107 | 85.533 | 1112.9 |  | 8546 | 117.47 | 1.5794 | 61.748 | 0.0046107 | 85.533 | 1112.9 | 1027.367
8547 | 1.5798 | 117.48 | 61.748 | 0.0046119 | 85.543 | 1112.9 |  | 8547 | 117.48 | 1.5798 | 61.748 | 0.0046119 | 85.543 | 1112.9 | 1027.357
8548 | 1.5803 | 117.49 | 61.748 | 0.0046131 | 85.553 | 1112.9 |  | 8548 | 117.49 | 1.5803 | 61.748 | 0.0046131 | 85.553 | 1112.9 | 1027.347
8549 | 1.5807 | 117.5 | 61.748 | 0.0046143 | 85.563 | 1112.9 |  | 8549 | 117.5 | 1.5807 | 61.748 | 0.0046143 | 85.563 | 1112.9 | 1027.337
8550 | 1.5812 | 117.51 | 61.748 | 0.0046155 | 85.573 | 1112.9 |  | 8550 | 117.51 | 1.5812 | 61.748 | 0.0046155 | 85.573 | 1112.9 | 1027.327
8551 | 1.5816 | 117.52 | 61.748 | 0.0046168 | 85.583 | 1112.9 |  | 8551 | 117.52 | 1.5816 | 61.748 | 0.0046168 | 85.583 | 1112.9 | 1027.317
8552 | 1.5821 | 117.53 | 61.747 | 0.004618 | 85.593 | 1112.9 |  | 8552 | 117.53 | 1.5821 | 61.747 | 0.004618 | 85.593 | 1112.9 | 1027.307
8553 | 1.5825 | 117.54 | 61.747 | 0.0046192 | 85.603 | 1112.9 |  | 8553 | 117.54 | 1.5825 | 61.747 | 0.0046192 | 85.603 | 1112.9 | 1027.297
8554 | 1.583 | 117.55 | 61.747 | 0.0046204 | 85.613 | 1112.9 |  | 8554 | 117.55 | 1.583 | 61.747 | 0.0046204 | 85.613 | 1112.9 | 1027.287
8555 | 1.5834 | 117.56 | 61.747 | 0.0046216 | 85.623 | 1112.9 |  | 8555 | 117.56 | 1.5834 | 61.747 | 0.0046216 | 85.623 | 1112.9 | 1027.277
8556 | 1.5838 | 117.57 | 61.747 | 0.0046229 | 85.633 | 1112.9 |  | 8556 | 117.57 | 1.5838 | 61.747 | 0.0046229 | 85.633 | 1112.9 | 1027.267
8557 | 1.5843 | 117.58 | 61.747 | 0.0046241 | 85.643 | 1112.9 |  | 8557 | 117.58 | 1.5843 | 61.747 | 0.0046241 | 85.643 | 1112.9 | 1027.257
8558 | 1.5847 | 117.59 | 61.746 | 0.0046253 | 85.653 | 1112.9 |  | 8558 | 117.59 | 1.5847 | 61.746 | 0.0046253 | 85.653 | 1112.9 | 1027.247
8559 | 1.5852 | 117.6 | 61.746 | 0.0046265 | 85.663 | 1112.9 |  | 8559 | 117.6 | 1.5852 | 61.746 | 0.0046265 | 85.663 | 1112.9 | 1027.237
8560 | 1.5856 | 117.61 | 61.746 | 0.0046277 | 85.673 | 1112.9 |  | 8560 | 117.61 | 1.5856 | 61.746 | 0.0046277 | 85.673 | 1112.9 | 1027.227
8561 | 1.5861 | 117.62 | 61.746 | 0.004629 | 85.683 | 1112.9 |  | 8561 | 117.62 | 1.5861 | 61.746 | 0.004629 | 85.683 | 1112.9 | 1027.217
8562 | 1.5865 | 117.63 | 61.746 | 0.0046302 | 85.693 | 1113 |  | 8562 | 117.63 | 1.5865 | 61.746 | 0.0046302 | 85.693 | 1113 | 1027.307
8563 | 1.587 | 117.64 | 61.746 | 0.0046314 | 85.703 | 1113 |  | 8563 | 117.64 | 1.587 | 61.746 | 0.0046314 | 85.703 | 1113 | 1027.297
8564 | 1.5874 | 117.65 | 61.746 | 0.0046326 | 85.713 | 1113 |  | 8564 | 117.65 | 1.5874 | 61.746 | 0.0046326 | 85.713 | 1113 | 1027.287
8565 | 1.5878 | 117.66 | 61.745 | 0.0046339 | 85.723 | 1113 |  | 8565 | 117.66 | 1.5878 | 61.745 | 0.0046339 | 85.723 | 1113 | 1027.277
8566 | 1.5883 | 117.67 | 61.745 | 0.0046351 | 85.733 | 1113 |  | 8566 | 117.67 | 1.5883 | 61.745 | 0.0046351 | 85.733 | 1113 | 1027.267
8567 | 1.5887 | 117.68 | 61.745 | 0.0046363 | 85.743 | 1113 |  | 8567 | 117.68 | 1.5887 | 61.745 | 0.0046363 | 85.743 | 1113 | 1027.257
8568 | 1.5892 | 117.69 | 61.745 | 0.0046375 | 85.753 | 1113 |  | 8568 | 117.69 | 1.5892 | 61.745 | 0.0046375 | 85.753 | 1113 | 1027.247
8569 | 1.5896 | 117.7 | 61.745 | 0.0046387 | 85.763 | 1113 |  | 8569 | 117.7 | 1.5896 | 61.745 | 0.0046387 | 85.763 | 1113 | 1027.237
8570 | 1.5901 | 117.71 | 61.745 | 0.00464 | 85.773 | 1113 |  | 8570 | 117.71 | 1.5901 | 61.745 | 0.00464 | 85.773 | 1113 | 1027.227
8571 | 1.5905 | 117.72 | 61.745 | 0.0046412 | 85.783 | 1113 |  | 8571 | 117.72 | 1.5905 | 61.745 | 0.0046412 | 85.783 | 1113 | 1027.217
8572 | 1.591 | 117.73 | 61.744 | 0.0046424 | 85.793 | 1113 |  | 8572 | 117.73 | 1.591 | 61.744 | 0.0046424 | 85.793 | 1113 | 1027.207
8573 | 1.5914 | 117.74 | 61.744 | 0.0046436 | 85.803 | 1113 |  | 8573 | 117.74 | 1.5914 | 61.744 | 0.0046436 | 85.803 | 1113 | 1027.197
8574 | 1.5919 | 117.75 | 61.744 | 0.0046449 | 85.813 | 1113 |  | 8574 | 117.75 | 1.5919 | 61.744 | 0.0046449 | 85.813 | 1113 | 1027.187
8575 | 1.5923 | 117.76 | 61.744 | 0.0046461 | 85.823 | 1113 |  | 8575 | 117.76 | 1.5923 | 61.744 | 0.0046461 | 85.823 | 1113 | 1027.177
8576 | 1.5928 | 117.77 | 61.744 | 0.0046473 | 85.833 | 1113 |  | 8576 | 117.77 | 1.5928 | 61.744 | 0.0046473 | 85.833 | 1113 | 1027.167
8577 | 1.5932 | 117.78 | 61.744 | 0.0046485 | 85.843 | 1113 |  | 8577 | 117.78 | 1.5932 | 61.744 | 0.0046485 | 85.843 | 1113 | 1027.157
8578 | 1.5936 | 117.79 | 61.743 | 0.0046498 | 85.853 | 1113 |  | 8578 | 117.79 | 1.5936 | 61.743 | 0.0046498 | 85.853 | 1113 | 1027.147
8579 | 1.5941 | 117.8 | 61.743 | 0.004651 | 85.863 | 1113 |  | 8579 | 117.8 | 1.5941 | 61.743 | 0.004651 | 85.863 | 1113 | 1027.137
8580 | 1.5945 | 117.81 | 61.743 | 0.0046522 | 85.873 | 1113 |  | 8580 | 117.81 | 1.5945 | 61.743 | 0.0046522 | 85.873 | 1113 | 1027.127
8581 | 1.595 | 117.82 | 61.743 | 0.0046534 | 85.883 | 1113 |  | 8581 | 117.82 | 1.595 | 61.743 | 0.0046534 | 85.883 | 1113 | 1027.117
8582 | 1.5954 | 117.83 | 61.743 | 0.0046547 | 85.893 | 1113 |  | 8582 | 117.83 | 1.5954 | 61.743 | 0.0046547 | 85.893 | 1113 | 1027.107
8583 | 1.5959 | 117.84 | 61.743 | 0.0046559 | 85.903 | 1113 |  | 8583 | 117.84 | 1.5959 | 61.743 | 0.0046559 | 85.903 | 1113 | 1027.097
8584 | 1.5963 | 117.85 | 61.743 | 0.0046571 | 85.913 | 1113 |  | 8584 | 117.85 | 1.5963 | 61.743 | 0.0046571 | 85.913 | 1113 | 1027.087
8585 | 1.5968 | 117.86 | 61.742 | 0.0046584 | 85.923 | 1113 |  | 8585 | 117.86 | 1.5968 | 61.742 | 0.0046584 | 85.923 | 1113 | 1027.077
8586 | 1.5972 | 117.87 | 61.742 | 0.0046596 | 85.933 | 1113.1 |  | 8586 | 117.87 | 1.5972 | 61.742 | 0.0046596 | 85.933 | 1113.1 | 1027.167
8587 | 1.5977 | 117.88 | 61.742 | 0.0046608 | 85.943 | 1113.1 |  | 8587 | 117.88 | 1.5977 | 61.742 | 0.0046608 | 85.943 | 1113.1 | 1027.157
8588 | 1.5981 | 117.89 | 61.742 | 0.004662 | 85.953 | 1113.1 |  | 8588 | 117.89 | 1.5981 | 61.742 | 0.004662 | 85.953 | 1113.1 | 1027.147
8589 | 1.5986 | 117.9 | 61.742 | 0.0046633 | 85.963 | 1113.1 |  | 8589 | 117.9 | 1.5986 | 61.742 | 0.0046633 | 85.963 | 1113.1 | 1027.137
8590 | 1.599 | 117.91 | 61.742 | 0.0046645 | 85.973 | 1113.1 |  | 8590 | 117.91 | 1.599 | 61.742 | 0.0046645 | 85.973 | 1113.1 | 1027.127
8591 | 1.5995 | 117.92 | 61.741 | 0.0046657 | 85.983 | 1113.1 |  | 8591 | 117.92 | 1.5995 | 61.741 | 0.0046657 | 85.983 | 1113.1 | 1027.117
8592 | 1.5999 | 117.93 | 61.741 | 0.004667 | 85.993 | 1113.1 |  | 8592 | 117.93 | 1.5999 | 61.741 | 0.004667 | 85.993 | 1113.1 | 1027.107
8593 | 1.6004 | 117.94 | 61.741 | 0.0046682 | 86.003 | 1113.1 |  | 8593 | 117.94 | 1.6004 | 61.741 | 0.0046682 | 86.003 | 1113.1 | 1027.097
8594 | 1.6008 | 117.95 | 61.741 | 0.0046694 | 86.013 | 1113.1 |  | 8594 | 117.95 | 1.6008 | 61.741 | 0.0046694 | 86.013 | 1113.1 | 1027.087
8595 | 1.6013 | 117.96 | 61.741 | 0.0046706 | 86.023 | 1113.1 |  | 8595 | 117.96 | 1.6013 | 61.741 | 0.0046706 | 86.023 | 1113.1 | 1027.077
8596 | 1.6017 | 117.97 | 61.741 | 0.0046719 | 86.033 | 1113.1 |  | 8596 | 117.97 | 1.6017 | 61.741 | 0.0046719 | 86.033 | 1113.1 | 1027.067
8597 | 1.6022 | 117.98 | 61.741 | 0.0046731 | 86.043 | 1113.1 |  | 8597 | 117.98 | 1.6022 | 61.741 | 0.0046731 | 86.043 | 1113.1 | 1027.057
8598 | 1.6026 | 117.99 | 61.74 | 0.0046743 | 86.053 | 1113.1 |  | 8598 | 117.99 | 1.6026 | 61.74 | 0.0046743 | 86.053 | 1113.1 | 1027.047
8599 | 1.603 | 118 | 61.74 | 0.0046756 | 86.063 | 1113.1 |  | 8599 | 118 | 1.603 | 61.74 | 0.0046756 | 86.063 | 1113.1 | 1027.037
8600 | 1.6035 | 118.01 | 61.74 | 0.0046768 | 86.073 | 1113.1 |  | 8600 | 118.01 | 1.6035 | 61.74 | 0.0046768 | 86.073 | 1113.1 | 1027.027
8601 | 1.6039 | 118.02 | 61.74 | 0.004678 | 86.083 | 1113.1 |  | 8601 | 118.02 | 1.6039 | 61.74 | 0.004678 | 86.083 | 1113.1 | 1027.017
8602 | 1.6044 | 118.03 | 61.74 | 0.0046793 | 86.093 | 1113.1 |  | 8602 | 118.03 | 1.6044 | 61.74 | 0.0046793 | 86.093 | 1113.1 | 1027.007
8603 | 1.6048 | 118.04 | 61.74 | 0.0046805 | 86.103 | 1113.1 |  | 8603 | 118.04 | 1.6048 | 61.74 | 0.0046805 | 86.103 | 1113.1 | 1026.997
8604 | 1.6053 | 118.05 | 61.74 | 0.0046817 | 86.113 | 1113.1 |  | 8604 | 118.05 | 1.6053 | 61.74 | 0.0046817 | 86.113 | 1113.1 | 1026.987
8605 | 1.6057 | 118.06 | 61.739 | 0.004683 | 86.123 | 1113.1 |  | 8605 | 118.06 | 1.6057 | 61.739 | 0.004683 | 86.123 | 1113.1 | 1026.977
8606 | 1.6062 | 118.07 | 61.739 | 0.0046842 | 86.133 | 1113.1 |  | 8606 | 118.07 | 1.6062 | 61.739 | 0.0046842 | 86.133 | 1113.1 | 1026.967
8607 | 1.6066 | 118.08 | 61.739 | 0.0046854 | 86.143 | 1113.1 |  | 8607 | 118.08 | 1.6066 | 61.739 | 0.0046854 | 86.143 | 1113.1 | 1026.957
8608 | 1.6071 | 118.09 | 61.739 | 0.0046867 | 86.153 | 1113.1 |  | 8608 | 118.09 | 1.6071 | 61.739 | 0.0046867 | 86.153 | 1113.1 | 1026.947
8609 | 1.6075 | 118.1 | 61.739 | 0.0046879 | 86.163 | 1113.1 |  | 8609 | 118.1 | 1.6075 | 61.739 | 0.0046879 | 86.163 | 1113.1 | 1026.937
8610 | 1.608 | 118.11 | 61.739 | 0.0046891 | 86.173 | 1113.2 |  | 8610 | 118.11 | 1.608 | 61.739 | 0.0046891 | 86.173 | 1113.2 | 1027.027
8611 | 1.6084 | 118.12 | 61.738 | 0.0046904 | 86.183 | 1113.2 |  | 8611 | 118.12 | 1.6084 | 61.738 | 0.0046904 | 86.183 | 1113.2 | 1027.017
8612 | 1.6089 | 118.13 | 61.738 | 0.0046916 | 86.193 | 1113.2 |  | 8612 | 118.13 | 1.6089 | 61.738 | 0.0046916 | 86.193 | 1113.2 | 1027.007
8613 | 1.6093 | 118.14 | 61.738 | 0.0046928 | 86.203 | 1113.2 |  | 8613 | 118.14 | 1.6093 | 61.738 | 0.0046928 | 86.203 | 1113.2 | 1026.997
8614 | 1.6098 | 118.15 | 61.738 | 0.0046941 | 86.213 | 1113.2 |  | 8614 | 118.15 | 1.6098 | 61.738 | 0.0046941 | 86.213 | 1113.2 | 1026.987
8615 | 1.6102 | 118.16 | 61.738 | 0.0046953 | 86.223 | 1113.2 |  | 8615 | 118.16 | 1.6102 | 61.738 | 0.0046953 | 86.223 | 1113.2 | 1026.977
8616 | 1.6107 | 118.17 | 61.738 | 0.0046965 | 86.233 | 1113.2 |  | 8616 | 118.17 | 1.6107 | 61.738 | 0.0046965 | 86.233 | 1113.2 | 1026.967
8617 | 1.6111 | 118.18 | 61.738 | 0.0046978 | 86.243 | 1113.2 |  | 8617 | 118.18 | 1.6111 | 61.738 | 0.0046978 | 86.243 | 1113.2 | 1026.957
8618 | 1.6116 | 118.19 | 61.737 | 0.004699 | 86.253 | 1113.2 |  | 8618 | 118.19 | 1.6116 | 61.737 | 0.004699 | 86.253 | 1113.2 | 1026.947
8619 | 1.6121 | 118.2 | 61.737 | 0.0047003 | 86.263 | 1113.2 |  | 8619 | 118.2 | 1.6121 | 61.737 | 0.0047003 | 86.263 | 1113.2 | 1026.937
8620 | 1.6125 | 118.21 | 61.737 | 0.0047015 | 86.273 | 1113.2 |  | 8620 | 118.21 | 1.6125 | 61.737 | 0.0047015 | 86.273 | 1113.2 | 1026.927
8621 | 1.613 | 118.22 | 61.737 | 0.0047027 | 86.283 | 1113.2 |  | 8621 | 118.22 | 1.613 | 61.737 | 0.0047027 | 86.283 | 1113.2 | 1026.917
8622 | 1.6134 | 118.23 | 61.737 | 0.004704 | 86.293 | 1113.2 |  | 8622 | 118.23 | 1.6134 | 61.737 | 0.004704 | 86.293 | 1113.2 | 1026.907
8623 | 1.6139 | 118.24 | 61.737 | 0.0047052 | 86.303 | 1113.2 |  | 8623 | 118.24 | 1.6139 | 61.737 | 0.0047052 | 86.303 | 1113.2 | 1026.897
8624 | 1.6143 | 118.25 | 61.736 | 0.0047064 | 86.313 | 1113.2 |  | 8624 | 118.25 | 1.6143 | 61.736 | 0.0047064 | 86.313 | 1113.2 | 1026.887
8625 | 1.6148 | 118.26 | 61.736 | 0.0047077 | 86.323 | 1113.2 |  | 8625 | 118.26 | 1.6148 | 61.736 | 0.0047077 | 86.323 | 1113.2 | 1026.877
8626 | 1.6152 | 118.27 | 61.736 | 0.0047089 | 86.333 | 1113.2 |  | 8626 | 118.27 | 1.6152 | 61.736 | 0.0047089 | 86.333 | 1113.2 | 1026.867
8627 | 1.6157 | 118.28 | 61.736 | 0.0047102 | 86.343 | 1113.2 |  | 8627 | 118.28 | 1.6157 | 61.736 | 0.0047102 | 86.343 | 1113.2 | 1026.857
8628 | 1.6161 | 118.29 | 61.736 | 0.0047114 | 86.353 | 1113.2 |  | 8628 | 118.29 | 1.6161 | 61.736 | 0.0047114 | 86.353 | 1113.2 | 1026.847
8629 | 1.6166 | 118.3 | 61.736 | 0.0047126 | 86.363 | 1113.2 |  | 8629 | 118.3 | 1.6166 | 61.736 | 0.0047126 | 86.363 | 1113.2 | 1026.837
8630 | 1.617 | 118.31 | 61.736 | 0.0047139 | 86.373 | 1113.2 |  | 8630 | 118.31 | 1.617 | 61.736 | 0.0047139 | 86.373 | 1113.2 | 1026.827
8631 | 1.6175 | 118.32 | 61.735 | 0.0047151 | 86.383 | 1113.2 |  | 8631 | 118.32 | 1.6175 | 61.735 | 0.0047151 | 86.383 | 1113.2 | 1026.817
8632 | 1.6179 | 118.33 | 61.735 | 0.0047164 | 86.393 | 1113.2 |  | 8632 | 118.33 | 1.6179 | 61.735 | 0.0047164 | 86.393 | 1113.2 | 1026.807
8633 | 1.6184 | 118.34 | 61.735 | 0.0047176 | 86.403 | 1113.3 |  | 8633 | 118.34 | 1.6184 | 61.735 | 0.0047176 | 86.403 | 1113.3 | 1026.897
8634 | 1.6188 | 118.35 | 61.735 | 0.0047188 | 86.413 | 1113.3 |  | 8634 | 118.35 | 1.6188 | 61.735 | 0.0047188 | 86.413 | 1113.3 | 1026.887
8635 | 1.6193 | 118.36 | 61.735 | 0.0047201 | 86.423 | 1113.3 |  | 8635 | 118.36 | 1.6193 | 61.735 | 0.0047201 | 86.423 | 1113.3 | 1026.877
8636 | 1.6197 | 118.37 | 61.735 | 0.0047213 | 86.433 | 1113.3 |  | 8636 | 118.37 | 1.6197 | 61.735 | 0.0047213 | 86.433 | 1113.3 | 1026.867
8637 | 1.6202 | 118.38 | 61.735 | 0.0047226 | 86.443 | 1113.3 |  | 8637 | 118.38 | 1.6202 | 61.735 | 0.0047226 | 86.443 | 1113.3 | 1026.857
8638 | 1.6206 | 118.39 | 61.734 | 0.0047238 | 86.453 | 1113.3 |  | 8638 | 118.39 | 1.6206 | 61.734 | 0.0047238 | 86.453 | 1113.3 | 1026.847
8639 | 1.6211 | 118.4 | 61.734 | 0.0047251 | 86.463 | 1113.3 |  | 8639 | 118.4 | 1.6211 | 61.734 | 0.0047251 | 86.463 | 1113.3 | 1026.837
8640 | 1.6215 | 118.41 | 61.734 | 0.0047263 | 86.473 | 1113.3 |  | 8640 | 118.41 | 1.6215 | 61.734 | 0.0047263 | 86.473 | 1113.3 | 1026.827
8641 | 1.622 | 118.42 | 61.734 | 0.0047275 | 86.483 | 1113.3 |  | 8641 | 118.42 | 1.622 | 61.734 | 0.0047275 | 86.483 | 1113.3 | 1026.817
8642 | 1.6225 | 118.43 | 61.734 | 0.0047288 | 86.493 | 1113.3 |  | 8642 | 118.43 | 1.6225 | 61.734 | 0.0047288 | 86.493 | 1113.3 | 1026.807
8643 | 1.6229 | 118.44 | 61.734 | 0.00473 | 86.503 | 1113.3 |  | 8643 | 118.44 | 1.6229 | 61.734 | 0.00473 | 86.503 | 1113.3 | 1026.797
8644 | 1.6234 | 118.45 | 61.733 | 0.0047313 | 86.513 | 1113.3 |  | 8644 | 118.45 | 1.6234 | 61.733 | 0.0047313 | 86.513 | 1113.3 | 1026.787
8645 | 1.6238 | 118.46 | 61.733 | 0.0047325 | 86.523 | 1113.3 |  | 8645 | 118.46 | 1.6238 | 61.733 | 0.0047325 | 86.523 | 1113.3 | 1026.777
8646 | 1.6243 | 118.47 | 61.733 | 0.0047338 | 86.533 | 1113.3 |  | 8646 | 118.47 | 1.6243 | 61.733 | 0.0047338 | 86.533 | 1113.3 | 1026.767
8647 | 1.6247 | 118.48 | 61.733 | 0.004735 | 86.543 | 1113.3 |  | 8647 | 118.48 | 1.6247 | 61.733 | 0.004735 | 86.543 | 1113.3 | 1026.757
8648 | 1.6252 | 118.49 | 61.733 | 0.0047362 | 86.553 | 1113.3 |  | 8648 | 118.49 | 1.6252 | 61.733 | 0.0047362 | 86.553 | 1113.3 | 1026.747
8649 | 1.6256 | 118.5 | 61.733 | 0.0047375 | 86.563 | 1113.3 |  | 8649 | 118.5 | 1.6256 | 61.733 | 0.0047375 | 86.563 | 1113.3 | 1026.737
8650 | 1.6261 | 118.51 | 61.733 | 0.0047387 | 86.573 | 1113.3 |  | 8650 | 118.51 | 1.6261 | 61.733 | 0.0047387 | 86.573 | 1113.3 | 1026.727
8651 | 1.6265 | 118.52 | 61.732 | 0.00474 | 86.583 | 1113.3 |  | 8651 | 118.52 | 1.6265 | 61.732 | 0.00474 | 86.583 | 1113.3 | 1026.717
8652 | 1.627 | 118.53 | 61.732 | 0.0047412 | 86.593 | 1113.3 |  | 8652 | 118.53 | 1.627 | 61.732 | 0.0047412 | 86.593 | 1113.3 | 1026.707
8653 | 1.6275 | 118.54 | 61.732 | 0.0047425 | 86.603 | 1113.3 |  | 8653 | 118.54 | 1.6275 | 61.732 | 0.0047425 | 86.603 | 1113.3 | 1026.697
8654 | 1.6279 | 118.55 | 61.732 | 0.0047437 | 86.613 | 1113.3 |  | 8654 | 118.55 | 1.6279 | 61.732 | 0.0047437 | 86.613 | 1113.3 | 1026.687
8655 | 1.6284 | 118.56 | 61.732 | 0.004745 | 86.623 | 1113.3 |  | 8655 | 118.56 | 1.6284 | 61.732 | 0.004745 | 86.623 | 1113.3 | 1026.677
8656 | 1.6288 | 118.57 | 61.732 | 0.0047462 | 86.633 | 1113.3 |  | 8656 | 118.57 | 1.6288 | 61.732 | 0.0047462 | 86.633 | 1113.3 | 1026.667
8657 | 1.6293 | 118.58 | 61.731 | 0.0047475 | 86.643 | 1113.4 |  | 8657 | 118.58 | 1.6293 | 61.731 | 0.0047475 | 86.643 | 1113.4 | 1026.757
8658 | 1.6297 | 118.59 | 61.731 | 0.0047487 | 86.653 | 1113.4 |  | 8658 | 118.59 | 1.6297 | 61.731 | 0.0047487 | 86.653 | 1113.4 | 1026.747
8659 | 1.6302 | 118.6 | 61.731 | 0.00475 | 86.663 | 1113.4 |  | 8659 | 118.6 | 1.6302 | 61.731 | 0.00475 | 86.663 | 1113.4 | 1026.737
8660 | 1.6306 | 118.61 | 61.731 | 0.0047512 | 86.673 | 1113.4 |  | 8660 | 118.61 | 1.6306 | 61.731 | 0.0047512 | 86.673 | 1113.4 | 1026.727
8661 | 1.6311 | 118.62 | 61.731 | 0.0047525 | 86.683 | 1113.4 |  | 8661 | 118.62 | 1.6311 | 61.731 | 0.0047525 | 86.683 | 1113.4 | 1026.717
8662 | 1.6315 | 118.63 | 61.731 | 0.0047537 | 86.693 | 1113.4 |  | 8662 | 118.63 | 1.6315 | 61.731 | 0.0047537 | 86.693 | 1113.4 | 1026.707
8663 | 1.632 | 118.64 | 61.731 | 0.004755 | 86.703 | 1113.4 |  | 8663 | 118.64 | 1.632 | 61.731 | 0.004755 | 86.703 | 1113.4 | 1026.697
8664 | 1.6325 | 118.65 | 61.73 | 0.0047562 | 86.713 | 1113.4 |  | 8664 | 118.65 | 1.6325 | 61.73 | 0.0047562 | 86.713 | 1113.4 | 1026.687
8665 | 1.6329 | 118.66 | 61.73 | 0.0047575 | 86.723 | 1113.4 |  | 8665 | 118.66 | 1.6329 | 61.73 | 0.0047575 | 86.723 | 1113.4 | 1026.677
8666 | 1.6334 | 118.67 | 61.73 | 0.0047587 | 86.733 | 1113.4 |  | 8666 | 118.67 | 1.6334 | 61.73 | 0.0047587 | 86.733 | 1113.4 | 1026.667
8667 | 1.6338 | 118.68 | 61.73 | 0.00476 | 86.743 | 1113.4 |  | 8667 | 118.68 | 1.6338 | 61.73 | 0.00476 | 86.743 | 1113.4 | 1026.657
8668 | 1.6343 | 118.69 | 61.73 | 0.0047612 | 86.753 | 1113.4 |  | 8668 | 118.69 | 1.6343 | 61.73 | 0.0047612 | 86.753 | 1113.4 | 1026.647
8669 | 1.6347 | 118.7 | 61.73 | 0.0047625 | 86.763 | 1113.4 |  | 8669 | 118.7 | 1.6347 | 61.73 | 0.0047625 | 86.763 | 1113.4 | 1026.637
8670 | 1.6352 | 118.71 | 61.729 | 0.0047637 | 86.773 | 1113.4 |  | 8670 | 118.71 | 1.6352 | 61.729 | 0.0047637 | 86.773 | 1113.4 | 1026.627
8671 | 1.6357 | 118.72 | 61.729 | 0.004765 | 86.783 | 1113.4 |  | 8671 | 118.72 | 1.6357 | 61.729 | 0.004765 | 86.783 | 1113.4 | 1026.617
8672 | 1.6361 | 118.73 | 61.729 | 0.0047662 | 86.793 | 1113.4 |  | 8672 | 118.73 | 1.6361 | 61.729 | 0.0047662 | 86.793 | 1113.4 | 1026.607
8673 | 1.6366 | 118.74 | 61.729 | 0.0047675 | 86.803 | 1113.4 |  | 8673 | 118.74 | 1.6366 | 61.729 | 0.0047675 | 86.803 | 1113.4 | 1026.597
8674 | 1.637 | 118.75 | 61.729 | 0.0047687 | 86.813 | 1113.4 |  | 8674 | 118.75 | 1.637 | 61.729 | 0.0047687 | 86.813 | 1113.4 | 1026.587
8675 | 1.6375 | 118.76 | 61.729 | 0.00477 | 86.823 | 1113.4 |  | 8675 | 118.76 | 1.6375 | 61.729 | 0.00477 | 86.823 | 1113.4 | 1026.577
8676 | 1.6379 | 118.77 | 61.729 | 0.0047712 | 86.833 | 1113.4 |  | 8676 | 118.77 | 1.6379 | 61.729 | 0.0047712 | 86.833 | 1113.4 | 1026.567
8677 | 1.6384 | 118.78 | 61.728 | 0.0047725 | 86.843 | 1113.4 |  | 8677 | 118.78 | 1.6384 | 61.728 | 0.0047725 | 86.843 | 1113.4 | 1026.557
8678 | 1.6389 | 118.79 | 61.728 | 0.0047737 | 86.853 | 1113.4 |  | 8678 | 118.79 | 1.6389 | 61.728 | 0.0047737 | 86.853 | 1113.4 | 1026.547
8679 | 1.6393 | 118.8 | 61.728 | 0.004775 | 86.863 | 1113.4 |  | 8679 | 118.8 | 1.6393 | 61.728 | 0.004775 | 86.863 | 1113.4 | 1026.537
8680 | 1.6398 | 118.81 | 61.728 | 0.0047762 | 86.873 | 1113.5 |  | 8680 | 118.81 | 1.6398 | 61.728 | 0.0047762 | 86.873 | 1113.5 | 1026.627
8681 | 1.6402 | 118.82 | 61.728 | 0.0047775 | 86.883 | 1113.5 |  | 8681 | 118.82 | 1.6402 | 61.728 | 0.0047775 | 86.883 | 1113.5 | 1026.617
8682 | 1.6407 | 118.83 | 61.728 | 0.0047787 | 86.893 | 1113.5 |  | 8682 | 118.83 | 1.6407 | 61.728 | 0.0047787 | 86.893 | 1113.5 | 1026.607
8683 | 1.6411 | 118.84 | 61.727 | 0.00478 | 86.903 | 1113.5 |  | 8683 | 118.84 | 1.6411 | 61.727 | 0.00478 | 86.903 | 1113.5 | 1026.597
8684 | 1.6416 | 118.85 | 61.727 | 0.0047812 | 86.913 | 1113.5 |  | 8684 | 118.85 | 1.6416 | 61.727 | 0.0047812 | 86.913 | 1113.5 | 1026.587
8685 | 1.6421 | 118.86 | 61.727 | 0.0047825 | 86.923 | 1113.5 |  | 8685 | 118.86 | 1.6421 | 61.727 | 0.0047825 | 86.923 | 1113.5 | 1026.577
8686 | 1.6425 | 118.87 | 61.727 | 0.0047838 | 86.933 | 1113.5 |  | 8686 | 118.87 | 1.6425 | 61.727 | 0.0047838 | 86.933 | 1113.5 | 1026.567
8687 | 1.643 | 118.88 | 61.727 | 0.004785 | 86.943 | 1113.5 |  | 8687 | 118.88 | 1.643 | 61.727 | 0.004785 | 86.943 | 1113.5 | 1026.557
8688 | 1.6434 | 118.89 | 61.727 | 0.0047863 | 86.953 | 1113.5 |  | 8688 | 118.89 | 1.6434 | 61.727 | 0.0047863 | 86.953 | 1113.5 | 1026.547
8689 | 1.6439 | 118.9 | 61.727 | 0.0047875 | 86.963 | 1113.5 |  | 8689 | 118.9 | 1.6439 | 61.727 | 0.0047875 | 86.963 | 1113.5 | 1026.537
8690 | 1.6444 | 118.91 | 61.726 | 0.0047888 | 86.973 | 1113.5 |  | 8690 | 118.91 | 1.6444 | 61.726 | 0.0047888 | 86.973 | 1113.5 | 1026.527
8691 | 1.6448 | 118.92 | 61.726 | 0.00479 | 86.983 | 1113.5 |  | 8691 | 118.92 | 1.6448 | 61.726 | 0.00479 | 86.983 | 1113.5 | 1026.517
8692 | 1.6453 | 118.93 | 61.726 | 0.0047913 | 86.993 | 1113.5 |  | 8692 | 118.93 | 1.6453 | 61.726 | 0.0047913 | 86.993 | 1113.5 | 1026.507
8693 | 1.6457 | 118.94 | 61.726 | 0.0047926 | 87.003 | 1113.5 |  | 8693 | 118.94 | 1.6457 | 61.726 | 0.0047926 | 87.003 | 1113.5 | 1026.497
8694 | 1.6462 | 118.95 | 61.726 | 0.0047938 | 87.013 | 1113.5 |  | 8694 | 118.95 | 1.6462 | 61.726 | 0.0047938 | 87.013 | 1113.5 | 1026.487
8695 | 1.6466 | 118.96 | 61.726 | 0.0047951 | 87.023 | 1113.5 |  | 8695 | 118.96 | 1.6466 | 61.726 | 0.0047951 | 87.023 | 1113.5 | 1026.477
8696 | 1.6471 | 118.97 | 61.726 | 0.0047963 | 87.033 | 1113.5 |  | 8696 | 118.97 | 1.6471 | 61.726 | 0.0047963 | 87.033 | 1113.5 | 1026.467
8697 | 1.6476 | 118.98 | 61.725 | 0.0047976 | 87.043 | 1113.5 |  | 8697 | 118.98 | 1.6476 | 61.725 | 0.0047976 | 87.043 | 1113.5 | 1026.457
8698 | 1.648 | 118.99 | 61.725 | 0.0047988 | 87.053 | 1113.5 |  | 8698 | 118.99 | 1.648 | 61.725 | 0.0047988 | 87.053 | 1113.5 | 1026.447
8699 | 1.6485 | 119 | 61.725 | 0.0048001 | 87.063 | 1113.5 |  | 8699 | 119 | 1.6485 | 61.725 | 0.0048001 | 87.063 | 1113.5 | 1026.437
8700 | 1.6489 | 119.01 | 61.725 | 0.0048014 | 87.073 | 1113.5 |  | 8700 | 119.01 | 1.6489 | 61.725 | 0.0048014 | 87.073 | 1113.5 | 1026.427
8701 | 1.6494 | 119.02 | 61.725 | 0.0048026 | 87.083 | 1113.5 |  | 8701 | 119.02 | 1.6494 | 61.725 | 0.0048026 | 87.083 | 1113.5 | 1026.417
8702 | 1.6499 | 119.03 | 61.725 | 0.0048039 | 87.093 | 1113.5 |  | 8702 | 119.03 | 1.6499 | 61.725 | 0.0048039 | 87.093 | 1113.5 | 1026.407
8703 | 1.6503 | 119.04 | 61.724 | 0.0048051 | 87.103 | 1113.5 |  | 8703 | 119.04 | 1.6503 | 61.724 | 0.0048051 | 87.103 | 1113.5 | 1026.397
8704 | 1.6508 | 119.05 | 61.724 | 0.0048064 | 87.113 | 1113.6 |  | 8704 | 119.05 | 1.6508 | 61.724 | 0.0048064 | 87.113 | 1113.6 | 1026.487
8705 | 1.6512 | 119.06 | 61.724 | 0.0048077 | 87.123 | 1113.6 |  | 8705 | 119.06 | 1.6512 | 61.724 | 0.0048077 | 87.123 | 1113.6 | 1026.477
8706 | 1.6517 | 119.07 | 61.724 | 0.0048089 | 87.133 | 1113.6 |  | 8706 | 119.07 | 1.6517 | 61.724 | 0.0048089 | 87.133 | 1113.6 | 1026.467
8707 | 1.6522 | 119.08 | 61.724 | 0.0048102 | 87.142 | 1113.6 |  | 8707 | 119.08 | 1.6522 | 61.724 | 0.0048102 | 87.142 | 1113.6 | 1026.458
8708 | 1.6526 | 119.09 | 61.724 | 0.0048115 | 87.152 | 1113.6 |  | 8708 | 119.09 | 1.6526 | 61.724 | 0.0048115 | 87.152 | 1113.6 | 1026.448
8709 | 1.6531 | 119.1 | 61.724 | 0.0048127 | 87.162 | 1113.6 |  | 8709 | 119.1 | 1.6531 | 61.724 | 0.0048127 | 87.162 | 1113.6 | 1026.438
8710 | 1.6536 | 119.11 | 61.723 | 0.004814 | 87.172 | 1113.6 |  | 8710 | 119.11 | 1.6536 | 61.723 | 0.004814 | 87.172 | 1113.6 | 1026.428
8711 | 1.654 | 119.12 | 61.723 | 0.0048152 | 87.182 | 1113.6 |  | 8711 | 119.12 | 1.654 | 61.723 | 0.0048152 | 87.182 | 1113.6 | 1026.418
8712 | 1.6545 | 119.13 | 61.723 | 0.0048165 | 87.192 | 1113.6 |  | 8712 | 119.13 | 1.6545 | 61.723 | 0.0048165 | 87.192 | 1113.6 | 1026.408
8713 | 1.6549 | 119.14 | 61.723 | 0.0048178 | 87.202 | 1113.6 |  | 8713 | 119.14 | 1.6549 | 61.723 | 0.0048178 | 87.202 | 1113.6 | 1026.398
8714 | 1.6554 | 119.15 | 61.723 | 0.004819 | 87.212 | 1113.6 |  | 8714 | 119.15 | 1.6554 | 61.723 | 0.004819 | 87.212 | 1113.6 | 1026.388
8715 | 1.6559 | 119.16 | 61.723 | 0.0048203 | 87.222 | 1113.6 |  | 8715 | 119.16 | 1.6559 | 61.723 | 0.0048203 | 87.222 | 1113.6 | 1026.378
8716 | 1.6563 | 119.17 | 61.722 | 0.0048216 | 87.232 | 1113.6 |  | 8716 | 119.17 | 1.6563 | 61.722 | 0.0048216 | 87.232 | 1113.6 | 1026.368
8717 | 1.6568 | 119.18 | 61.722 | 0.0048228 | 87.242 | 1113.6 |  | 8717 | 119.18 | 1.6568 | 61.722 | 0.0048228 | 87.242 | 1113.6 | 1026.358
8718 | 1.6572 | 119.19 | 61.722 | 0.0048241 | 87.252 | 1113.6 |  | 8718 | 119.19 | 1.6572 | 61.722 | 0.0048241 | 87.252 | 1113.6 | 1026.348
8719 | 1.6577 | 119.2 | 61.722 | 0.0048253 | 87.262 | 1113.6 |  | 8719 | 119.2 | 1.6577 | 61.722 | 0.0048253 | 87.262 | 1113.6 | 1026.338
8720 | 1.6582 | 119.21 | 61.722 | 0.0048266 | 87.272 | 1113.6 |  | 8720 | 119.21 | 1.6582 | 61.722 | 0.0048266 | 87.272 | 1113.6 | 1026.328
8721 | 1.6586 | 119.22 | 61.722 | 0.0048279 | 87.282 | 1113.6 |  | 8721 | 119.22 | 1.6586 | 61.722 | 0.0048279 | 87.282 | 1113.6 | 1026.318
8722 | 1.6591 | 119.23 | 61.722 | 0.0048291 | 87.292 | 1113.6 |  | 8722 | 119.23 | 1.6591 | 61.722 | 0.0048291 | 87.292 | 1113.6 | 1026.308
8723 | 1.6596 | 119.24 | 61.721 | 0.0048304 | 87.302 | 1113.6 |  | 8723 | 119.24 | 1.6596 | 61.721 | 0.0048304 | 87.302 | 1113.6 | 1026.298
8724 | 1.66 | 119.25 | 61.721 | 0.0048317 | 87.312 | 1113.6 |  | 8724 | 119.25 | 1.66 | 61.721 | 0.0048317 | 87.312 | 1113.6 | 1026.288
8725 | 1.6605 | 119.26 | 61.721 | 0.0048329 | 87.322 | 1113.6 |  | 8725 | 119.26 | 1.6605 | 61.721 | 0.0048329 | 87.322 | 1113.6 | 1026.278
8726 | 1.6609 | 119.27 | 61.721 | 0.0048342 | 87.332 | 1113.6 |  | 8726 | 119.27 | 1.6609 | 61.721 | 0.0048342 | 87.332 | 1113.6 | 1026.268
8727 | 1.6614 | 119.28 | 61.721 | 0.0048355 | 87.342 | 1113.6 |  | 8727 | 119.28 | 1.6614 | 61.721 | 0.0048355 | 87.342 | 1113.6 | 1026.258
8728 | 1.6619 | 119.29 | 61.721 | 0.0048367 | 87.352 | 1113.7 |  | 8728 | 119.29 | 1.6619 | 61.721 | 0.0048367 | 87.352 | 1113.7 | 1026.348
8729 | 1.6623 | 119.3 | 61.72 | 0.004838 | 87.362 | 1113.7 |  | 8729 | 119.3 | 1.6623 | 61.72 | 0.004838 | 87.362 | 1113.7 | 1026.338
8730 | 1.6628 | 119.31 | 61.72 | 0.0048393 | 87.372 | 1113.7 |  | 8730 | 119.31 | 1.6628 | 61.72 | 0.0048393 | 87.372 | 1113.7 | 1026.328
8731 | 1.6633 | 119.32 | 61.72 | 0.0048405 | 87.382 | 1113.7 |  | 8731 | 119.32 | 1.6633 | 61.72 | 0.0048405 | 87.382 | 1113.7 | 1026.318
8732 | 1.6637 | 119.33 | 61.72 | 0.0048418 | 87.392 | 1113.7 |  | 8732 | 119.33 | 1.6637 | 61.72 | 0.0048418 | 87.392 | 1113.7 | 1026.308
8733 | 1.6642 | 119.34 | 61.72 | 0.0048431 | 87.402 | 1113.7 |  | 8733 | 119.34 | 1.6642 | 61.72 | 0.0048431 | 87.402 | 1113.7 | 1026.298
8734 | 1.6647 | 119.35 | 61.72 | 0.0048444 | 87.412 | 1113.7 |  | 8734 | 119.35 | 1.6647 | 61.72 | 0.0048444 | 87.412 | 1113.7 | 1026.288
8735 | 1.6651 | 119.36 | 61.72 | 0.0048456 | 87.422 | 1113.7 |  | 8735 | 119.36 | 1.6651 | 61.72 | 0.0048456 | 87.422 | 1113.7 | 1026.278
8736 | 1.6656 | 119.37 | 61.719 | 0.0048469 | 87.432 | 1113.7 |  | 8736 | 119.37 | 1.6656 | 61.719 | 0.0048469 | 87.432 | 1113.7 | 1026.268
8737 | 1.666 | 119.38 | 61.719 | 0.0048482 | 87.442 | 1113.7 |  | 8737 | 119.38 | 1.666 | 61.719 | 0.0048482 | 87.442 | 1113.7 | 1026.258
8738 | 1.6665 | 119.39 | 61.719 | 0.0048494 | 87.452 | 1113.7 |  | 8738 | 119.39 | 1.6665 | 61.719 | 0.0048494 | 87.452 | 1113.7 | 1026.248
8739 | 1.667 | 119.4 | 61.719 | 0.0048507 | 87.462 | 1113.7 |  | 8739 | 119.4 | 1.667 | 61.719 | 0.0048507 | 87.462 | 1113.7 | 1026.238
8740 | 1.6674 | 119.41 | 61.719 | 0.004852 | 87.472 | 1113.7 |  | 8740 | 119.41 | 1.6674 | 61.719 | 0.004852 | 87.472 | 1113.7 | 1026.228
8741 | 1.6679 | 119.42 | 61.719 | 0.0048532 | 87.482 | 1113.7 |  | 8741 | 119.42 | 1.6679 | 61.719 | 0.0048532 | 87.482 | 1113.7 | 1026.218
8742 | 1.6684 | 119.43 | 61.718 | 0.0048545 | 87.492 | 1113.7 |  | 8742 | 119.43 | 1.6684 | 61.718 | 0.0048545 | 87.492 | 1113.7 | 1026.208
8743 | 1.6688 | 119.44 | 61.718 | 0.0048558 | 87.502 | 1113.7 |  | 8743 | 119.44 | 1.6688 | 61.718 | 0.0048558 | 87.502 | 1113.7 | 1026.198
8744 | 1.6693 | 119.45 | 61.718 | 0.0048571 | 87.512 | 1113.7 |  | 8744 | 119.45 | 1.6693 | 61.718 | 0.0048571 | 87.512 | 1113.7 | 1026.188
8745 | 1.6698 | 119.46 | 61.718 | 0.0048583 | 87.522 | 1113.7 |  | 8745 | 119.46 | 1.6698 | 61.718 | 0.0048583 | 87.522 | 1113.7 | 1026.178
8746 | 1.6702 | 119.47 | 61.718 | 0.0048596 | 87.532 | 1113.7 |  | 8746 | 119.47 | 1.6702 | 61.718 | 0.0048596 | 87.532 | 1113.7 | 1026.168
8747 | 1.6707 | 119.48 | 61.718 | 0.0048609 | 87.542 | 1113.7 |  | 8747 | 119.48 | 1.6707 | 61.718 | 0.0048609 | 87.542 | 1113.7 | 1026.158
8748 | 1.6712 | 119.49 | 61.718 | 0.0048621 | 87.552 | 1113.7 |  | 8748 | 119.49 | 1.6712 | 61.718 | 0.0048621 | 87.552 | 1113.7 | 1026.148
8749 | 1.6716 | 119.5 | 61.717 | 0.0048634 | 87.562 | 1113.7 |  | 8749 | 119.5 | 1.6716 | 61.717 | 0.0048634 | 87.562 | 1113.7 | 1026.138
8750 | 1.6721 | 119.51 | 61.717 | 0.0048647 | 87.572 | 1113.7 |  | 8750 | 119.51 | 1.6721 | 61.717 | 0.0048647 | 87.572 | 1113.7 | 1026.128
8751 | 1.6726 | 119.52 | 61.717 | 0.004866 | 87.582 | 1113.8 |  | 8751 | 119.52 | 1.6726 | 61.717 | 0.004866 | 87.582 | 1113.8 | 1026.218
8752 | 1.673 | 119.53 | 61.717 | 0.0048672 | 87.592 | 1113.8 |  | 8752 | 119.53 | 1.673 | 61.717 | 0.0048672 | 87.592 | 1113.8 | 1026.208
8753 | 1.6735 | 119.54 | 61.717 | 0.0048685 | 87.602 | 1113.8 |  | 8753 | 119.54 | 1.6735 | 61.717 | 0.0048685 | 87.602 | 1113.8 | 1026.198
8754 | 1.6739 | 119.55 | 61.717 | 0.0048698 | 87.612 | 1113.8 |  | 8754 | 119.55 | 1.6739 | 61.717 | 0.0048698 | 87.612 | 1113.8 | 1026.188
8755 | 1.6744 | 119.56 | 61.716 | 0.0048711 | 87.622 | 1113.8 |  | 8755 | 119.56 | 1.6744 | 61.716 | 0.0048711 | 87.622 | 1113.8 | 1026.178
8756 | 1.6749 | 119.57 | 61.716 | 0.0048723 | 87.632 | 1113.8 |  | 8756 | 119.57 | 1.6749 | 61.716 | 0.0048723 | 87.632 | 1113.8 | 1026.168
8757 | 1.6753 | 119.58 | 61.716 | 0.0048736 | 87.642 | 1113.8 |  | 8757 | 119.58 | 1.6753 | 61.716 | 0.0048736 | 87.642 | 1113.8 | 1026.158
8758 | 1.6758 | 119.59 | 61.716 | 0.0048749 | 87.652 | 1113.8 |  | 8758 | 119.59 | 1.6758 | 61.716 | 0.0048749 | 87.652 | 1113.8 | 1026.148
8759 | 1.6763 | 119.6 | 61.716 | 0.0048762 | 87.662 | 1113.8 |  | 8759 | 119.6 | 1.6763 | 61.716 | 0.0048762 | 87.662 | 1113.8 | 1026.138
8760 | 1.6767 | 119.61 | 61.716 | 0.0048774 | 87.672 | 1113.8 |  | 8760 | 119.61 | 1.6767 | 61.716 | 0.0048774 | 87.672 | 1113.8 | 1026.128
8761 | 1.6772 | 119.62 | 61.716 | 0.0048787 | 87.682 | 1113.8 |  | 8761 | 119.62 | 1.6772 | 61.716 | 0.0048787 | 87.682 | 1113.8 | 1026.118
8762 | 1.6777 | 119.63 | 61.715 | 0.00488 | 87.692 | 1113.8 |  | 8762 | 119.63 | 1.6777 | 61.715 | 0.00488 | 87.692 | 1113.8 | 1026.108
8763 | 1.6781 | 119.64 | 61.715 | 0.0048813 | 87.702 | 1113.8 |  | 8763 | 119.64 | 1.6781 | 61.715 | 0.0048813 | 87.702 | 1113.8 | 1026.098
8764 | 1.6786 | 119.65 | 61.715 | 0.0048826 | 87.712 | 1113.8 |  | 8764 | 119.65 | 1.6786 | 61.715 | 0.0048826 | 87.712 | 1113.8 | 1026.088
8765 | 1.6791 | 119.66 | 61.715 | 0.0048838 | 87.722 | 1113.8 |  | 8765 | 119.66 | 1.6791 | 61.715 | 0.0048838 | 87.722 | 1113.8 | 1026.078
8766 | 1.6795 | 119.67 | 61.715 | 0.0048851 | 87.732 | 1113.8 |  | 8766 | 119.67 | 1.6795 | 61.715 | 0.0048851 | 87.732 | 1113.8 | 1026.068
8767 | 1.68 | 119.68 | 61.715 | 0.0048864 | 87.742 | 1113.8 |  | 8767 | 119.68 | 1.68 | 61.715 | 0.0048864 | 87.742 | 1113.8 | 1026.058
8768 | 1.6805 | 119.69 | 61.714 | 0.0048877 | 87.752 | 1113.8 |  | 8768 | 119.69 | 1.6805 | 61.714 | 0.0048877 | 87.752 | 1113.8 | 1026.048
8769 | 1.6809 | 119.7 | 61.714 | 0.0048889 | 87.762 | 1113.8 |  | 8769 | 119.7 | 1.6809 | 61.714 | 0.0048889 | 87.762 | 1113.8 | 1026.038
8770 | 1.6814 | 119.71 | 61.714 | 0.0048902 | 87.772 | 1113.8 |  | 8770 | 119.71 | 1.6814 | 61.714 | 0.0048902 | 87.772 | 1113.8 | 1026.028
8771 | 1.6819 | 119.72 | 61.714 | 0.0048915 | 87.782 | 1113.8 |  | 8771 | 119.72 | 1.6819 | 61.714 | 0.0048915 | 87.782 | 1113.8 | 1026.018
8772 | 1.6824 | 119.73 | 61.714 | 0.0048928 | 87.792 | 1113.8 |  | 8772 | 119.73 | 1.6824 | 61.714 | 0.0048928 | 87.792 | 1113.8 | 1026.008
8773 | 1.6828 | 119.74 | 61.714 | 0.0048941 | 87.802 | 1113.8 |  | 8773 | 119.74 | 1.6828 | 61.714 | 0.0048941 | 87.802 | 1113.8 | 1025.998
8774 | 1.6833 | 119.75 | 61.714 | 0.0048953 | 87.812 | 1113.8 |  | 8774 | 119.75 | 1.6833 | 61.714 | 0.0048953 | 87.812 | 1113.8 | 1025.988
8775 | 1.6838 | 119.76 | 61.713 | 0.0048966 | 87.822 | 1113.9 |  | 8775 | 119.76 | 1.6838 | 61.713 | 0.0048966 | 87.822 | 1113.9 | 1026.078
8776 | 1.6842 | 119.77 | 61.713 | 0.0048979 | 87.832 | 1113.9 |  | 8776 | 119.77 | 1.6842 | 61.713 | 0.0048979 | 87.832 | 1113.9 | 1026.068
8777 | 1.6847 | 119.78 | 61.713 | 0.0048992 | 87.842 | 1113.9 |  | 8777 | 119.78 | 1.6847 | 61.713 | 0.0048992 | 87.842 | 1113.9 | 1026.058
8778 | 1.6852 | 119.79 | 61.713 | 0.0049005 | 87.852 | 1113.9 |  | 8778 | 119.79 | 1.6852 | 61.713 | 0.0049005 | 87.852 | 1113.9 | 1026.048
8779 | 1.6856 | 119.8 | 61.713 | 0.0049017 | 87.862 | 1113.9 |  | 8779 | 119.8 | 1.6856 | 61.713 | 0.0049017 | 87.862 | 1113.9 | 1026.038
8780 | 1.6861 | 119.81 | 61.713 | 0.004903 | 87.872 | 1113.9 |  | 8780 | 119.81 | 1.6861 | 61.713 | 0.004903 | 87.872 | 1113.9 | 1026.028
8781 | 1.6866 | 119.82 | 61.712 | 0.0049043 | 87.882 | 1113.9 |  | 8781 | 119.82 | 1.6866 | 61.712 | 0.0049043 | 87.882 | 1113.9 | 1026.018
8782 | 1.687 | 119.83 | 61.712 | 0.0049056 | 87.892 | 1113.9 |  | 8782 | 119.83 | 1.687 | 61.712 | 0.0049056 | 87.892 | 1113.9 | 1026.008
8783 | 1.6875 | 119.84 | 61.712 | 0.0049069 | 87.902 | 1113.9 |  | 8783 | 119.84 | 1.6875 | 61.712 | 0.0049069 | 87.902 | 1113.9 | 1025.998
8784 | 1.688 | 119.85 | 61.712 | 0.0049082 | 87.912 | 1113.9 |  | 8784 | 119.85 | 1.688 | 61.712 | 0.0049082 | 87.912 | 1113.9 | 1025.988
8785 | 1.6884 | 119.86 | 61.712 | 0.0049094 | 87.922 | 1113.9 |  | 8785 | 119.86 | 1.6884 | 61.712 | 0.0049094 | 87.922 | 1113.9 | 1025.978
8786 | 1.6889 | 119.87 | 61.712 | 0.0049107 | 87.932 | 1113.9 |  | 8786 | 119.87 | 1.6889 | 61.712 | 0.0049107 | 87.932 | 1113.9 | 1025.968
8787 | 1.6894 | 119.88 | 61.712 | 0.004912 | 87.942 | 1113.9 |  | 8787 | 119.88 | 1.6894 | 61.712 | 0.004912 | 87.942 | 1113.9 | 1025.958
8788 | 1.6899 | 119.89 | 61.711 | 0.0049133 | 87.952 | 1113.9 |  | 8788 | 119.89 | 1.6899 | 61.711 | 0.0049133 | 87.952 | 1113.9 | 1025.948
8789 | 1.6903 | 119.9 | 61.711 | 0.0049146 | 87.962 | 1113.9 |  | 8789 | 119.9 | 1.6903 | 61.711 | 0.0049146 | 87.962 | 1113.9 | 1025.938
8790 | 1.6908 | 119.91 | 61.711 | 0.0049159 | 87.972 | 1113.9 |  | 8790 | 119.91 | 1.6908 | 61.711 | 0.0049159 | 87.972 | 1113.9 | 1025.928
8791 | 1.6913 | 119.92 | 61.711 | 0.0049171 | 87.982 | 1113.9 |  | 8791 | 119.92 | 1.6913 | 61.711 | 0.0049171 | 87.982 | 1113.9 | 1025.918
8792 | 1.6917 | 119.93 | 61.711 | 0.0049184 | 87.992 | 1113.9 |  | 8792 | 119.93 | 1.6917 | 61.711 | 0.0049184 | 87.992 | 1113.9 | 1025.908
8793 | 1.6922 | 119.94 | 61.711 | 0.0049197 | 88.002 | 1113.9 |  | 8793 | 119.94 | 1.6922 | 61.711 | 0.0049197 | 88.002 | 1113.9 | 1025.898
8794 | 1.6927 | 119.95 | 61.71 | 0.004921 | 88.012 | 1113.9 |  | 8794 | 119.95 | 1.6927 | 61.71 | 0.004921 | 88.012 | 1113.9 | 1025.888
8795 | 1.6931 | 119.96 | 61.71 | 0.0049223 | 88.022 | 1113.9 |  | 8795 | 119.96 | 1.6931 | 61.71 | 0.0049223 | 88.022 | 1113.9 | 1025.878
8796 | 1.6936 | 119.97 | 61.71 | 0.0049236 | 88.032 | 1113.9 |  | 8796 | 119.97 | 1.6936 | 61.71 | 0.0049236 | 88.032 | 1113.9 | 1025.868
8797 | 1.6941 | 119.98 | 61.71 | 0.0049249 | 88.042 | 1113.9 |  | 8797 | 119.98 | 1.6941 | 61.71 | 0.0049249 | 88.042 | 1113.9 | 1025.858
8798 | 1.6946 | 119.99 | 61.71 | 0.0049262 | 88.052 | 1113.9 |  | 8798 | 119.99 | 1.6946 | 61.71 | 0.0049262 | 88.052 | 1113.9 | 1025.848
8799 | 1.695 | 120 | 61.71 | 0.0049274 | 88.062 | 1114 |  | 8799 | 120 | 1.695 | 61.71 | 0.0049274 | 88.062 | 1114 | 1025.938
8800 | 1.6955 | 120.01 | 61.71 | 0.0049287 | 88.072 | 1114 |  | 8800 | 120.01 | 1.6955 | 61.71 | 0.0049287 | 88.072 | 1114 | 1025.928
8801 | 1.696 | 120.02 | 61.709 | 0.00493 | 88.082 | 1114 |  | 8801 | 120.02 | 1.696 | 61.709 | 0.00493 | 88.082 | 1114 | 1025.918
8802 | 1.6964 | 120.03 | 61.709 | 0.0049313 | 88.092 | 1114 |  | 8802 | 120.03 | 1.6964 | 61.709 | 0.0049313 | 88.092 | 1114 | 1025.908
8803 | 1.6969 | 120.04 | 61.709 | 0.0049326 | 88.102 | 1114 |  | 8803 | 120.04 | 1.6969 | 61.709 | 0.0049326 | 88.102 | 1114 | 1025.898
8804 | 1.6974 | 120.05 | 61.709 | 0.0049339 | 88.112 | 1114 |  | 8804 | 120.05 | 1.6974 | 61.709 | 0.0049339 | 88.112 | 1114 | 1025.888
8805 | 1.6979 | 120.06 | 61.709 | 0.0049352 | 88.122 | 1114 |  | 8805 | 120.06 | 1.6979 | 61.709 | 0.0049352 | 88.122 | 1114 | 1025.878
8806 | 1.6983 | 120.07 | 61.709 | 0.0049365 | 88.132 | 1114 |  | 8806 | 120.07 | 1.6983 | 61.709 | 0.0049365 | 88.132 | 1114 | 1025.868
8807 | 1.6988 | 120.08 | 61.708 | 0.0049377 | 88.142 | 1114 |  | 8807 | 120.08 | 1.6988 | 61.708 | 0.0049377 | 88.142 | 1114 | 1025.858
8808 | 1.6993 | 120.09 | 61.708 | 0.004939 | 88.152 | 1114 |  | 8808 | 120.09 | 1.6993 | 61.708 | 0.004939 | 88.152 | 1114 | 1025.848
8809 | 1.6997 | 120.1 | 61.708 | 0.0049403 | 88.162 | 1114 |  | 8809 | 120.1 | 1.6997 | 61.708 | 0.0049403 | 88.162 | 1114 | 1025.838
8810 | 1.7002 | 120.11 | 61.708 | 0.0049416 | 88.172 | 1114 |  | 8810 | 120.11 | 1.7002 | 61.708 | 0.0049416 | 88.172 | 1114 | 1025.828
8811 | 1.7007 | 120.12 | 61.708 | 0.0049429 | 88.182 | 1114 |  | 8811 | 120.12 | 1.7007 | 61.708 | 0.0049429 | 88.182 | 1114 | 1025.818
8812 | 1.7012 | 120.13 | 61.708 | 0.0049442 | 88.192 | 1114 |  | 8812 | 120.13 | 1.7012 | 61.708 | 0.0049442 | 88.192 | 1114 | 1025.808
8813 | 1.7016 | 120.14 | 61.708 | 0.0049455 | 88.202 | 1114 |  | 8813 | 120.14 | 1.7016 | 61.708 | 0.0049455 | 88.202 | 1114 | 1025.798
8814 | 1.7021 | 120.15 | 61.707 | 0.0049468 | 88.212 | 1114 |  | 8814 | 120.15 | 1.7021 | 61.707 | 0.0049468 | 88.212 | 1114 | 1025.788
8815 | 1.7026 | 120.16 | 61.707 | 0.0049481 | 88.222 | 1114 |  | 8815 | 120.16 | 1.7026 | 61.707 | 0.0049481 | 88.222 | 1114 | 1025.778
8816 | 1.7031 | 120.17 | 61.707 | 0.0049494 | 88.232 | 1114 |  | 8816 | 120.17 | 1.7031 | 61.707 | 0.0049494 | 88.232 | 1114 | 1025.768
8817 | 1.7035 | 120.18 | 61.707 | 0.0049507 | 88.242 | 1114 |  | 8817 | 120.18 | 1.7035 | 61.707 | 0.0049507 | 88.242 | 1114 | 1025.758
8818 | 1.704 | 120.19 | 61.707 | 0.004952 | 88.252 | 1114 |  | 8818 | 120.19 | 1.704 | 61.707 | 0.004952 | 88.252 | 1114 | 1025.748
8819 | 1.7045 | 120.2 | 61.707 | 0.0049532 | 88.262 | 1114 |  | 8819 | 120.2 | 1.7045 | 61.707 | 0.0049532 | 88.262 | 1114 | 1025.738
8820 | 1.7049 | 120.21 | 61.706 | 0.0049545 | 88.272 | 1114 |  | 8820 | 120.21 | 1.7049 | 61.706 | 0.0049545 | 88.272 | 1114 | 1025.728
8821 | 1.7054 | 120.22 | 61.706 | 0.0049558 | 88.282 | 1114 |  | 8821 | 120.22 | 1.7054 | 61.706 | 0.0049558 | 88.282 | 1114 | 1025.718
8822 | 1.7059 | 120.23 | 61.706 | 0.0049571 | 88.292 | 1114.1 |  | 8822 | 120.23 | 1.7059 | 61.706 | 0.0049571 | 88.292 | 1114.1 | 1025.808
8823 | 1.7064 | 120.24 | 61.706 | 0.0049584 | 88.302 | 1114.1 |  | 8823 | 120.24 | 1.7064 | 61.706 | 0.0049584 | 88.302 | 1114.1 | 1025.798
8824 | 1.7068 | 120.25 | 61.706 | 0.0049597 | 88.312 | 1114.1 |  | 8824 | 120.25 | 1.7068 | 61.706 | 0.0049597 | 88.312 | 1114.1 | 1025.788
8825 | 1.7073 | 120.26 | 61.706 | 0.004961 | 88.322 | 1114.1 |  | 8825 | 120.26 | 1.7073 | 61.706 | 0.004961 | 88.322 | 1114.1 | 1025.778
8826 | 1.7078 | 120.27 | 61.706 | 0.0049623 | 88.332 | 1114.1 |  | 8826 | 120.27 | 1.7078 | 61.706 | 0.0049623 | 88.332 | 1114.1 | 1025.768
8827 | 1.7083 | 120.28 | 61.705 | 0.0049636 | 88.342 | 1114.1 |  | 8827 | 120.28 | 1.7083 | 61.705 | 0.0049636 | 88.342 | 1114.1 | 1025.758
8828 | 1.7087 | 120.29 | 61.705 | 0.0049649 | 88.352 | 1114.1 |  | 8828 | 120.29 | 1.7087 | 61.705 | 0.0049649 | 88.352 | 1114.1 | 1025.748
8829 | 1.7092 | 120.3 | 61.705 | 0.0049662 | 88.362 | 1114.1 |  | 8829 | 120.3 | 1.7092 | 61.705 | 0.0049662 | 88.362 | 1114.1 | 1025.738
8830 | 1.7097 | 120.31 | 61.705 | 0.0049675 | 88.372 | 1114.1 |  | 8830 | 120.31 | 1.7097 | 61.705 | 0.0049675 | 88.372 | 1114.1 | 1025.728
8831 | 1.7102 | 120.32 | 61.705 | 0.0049688 | 88.382 | 1114.1 |  | 8831 | 120.32 | 1.7102 | 61.705 | 0.0049688 | 88.382 | 1114.1 | 1025.718
8832 | 1.7106 | 120.33 | 61.705 | 0.0049701 | 88.392 | 1114.1 |  | 8832 | 120.33 | 1.7106 | 61.705 | 0.0049701 | 88.392 | 1114.1 | 1025.708
8833 | 1.7111 | 120.34 | 61.704 | 0.0049714 | 88.402 | 1114.1 |  | 8833 | 120.34 | 1.7111 | 61.704 | 0.0049714 | 88.402 | 1114.1 | 1025.698
8834 | 1.7116 | 120.35 | 61.704 | 0.0049727 | 88.412 | 1114.1 |  | 8834 | 120.35 | 1.7116 | 61.704 | 0.0049727 | 88.412 | 1114.1 | 1025.688
8835 | 1.7121 | 120.36 | 61.704 | 0.004974 | 88.422 | 1114.1 |  | 8835 | 120.36 | 1.7121 | 61.704 | 0.004974 | 88.422 | 1114.1 | 1025.678
8836 | 1.7125 | 120.37 | 61.704 | 0.0049753 | 88.432 | 1114.1 |  | 8836 | 120.37 | 1.7125 | 61.704 | 0.0049753 | 88.432 | 1114.1 | 1025.668
8837 | 1.713 | 120.38 | 61.704 | 0.0049766 | 88.442 | 1114.1 |  | 8837 | 120.38 | 1.713 | 61.704 | 0.0049766 | 88.442 | 1114.1 | 1025.658
8838 | 1.7135 | 120.39 | 61.704 | 0.0049779 | 88.452 | 1114.1 |  | 8838 | 120.39 | 1.7135 | 61.704 | 0.0049779 | 88.452 | 1114.1 | 1025.648
8839 | 1.714 | 120.4 | 61.704 | 0.0049792 | 88.462 | 1114.1 |  | 8839 | 120.4 | 1.714 | 61.704 | 0.0049792 | 88.462 | 1114.1 | 1025.638
8840 | 1.7144 | 120.41 | 61.703 | 0.0049805 | 88.472 | 1114.1 |  | 8840 | 120.41 | 1.7144 | 61.703 | 0.0049805 | 88.472 | 1114.1 | 1025.628
8841 | 1.7149 | 120.42 | 61.703 | 0.0049818 | 88.482 | 1114.1 |  | 8841 | 120.42 | 1.7149 | 61.703 | 0.0049818 | 88.482 | 1114.1 | 1025.618
8842 | 1.7154 | 120.43 | 61.703 | 0.0049831 | 88.492 | 1114.1 |  | 8842 | 120.43 | 1.7154 | 61.703 | 0.0049831 | 88.492 | 1114.1 | 1025.608
8843 | 1.7159 | 120.44 | 61.703 | 0.0049844 | 88.502 | 1114.1 |  | 8843 | 120.44 | 1.7159 | 61.703 | 0.0049844 | 88.502 | 1114.1 | 1025.598
8844 | 1.7163 | 120.45 | 61.703 | 0.0049857 | 88.512 | 1114.1 |  | 8844 | 120.45 | 1.7163 | 61.703 | 0.0049857 | 88.512 | 1114.1 | 1025.588
8845 | 1.7168 | 120.46 | 61.703 | 0.004987 | 88.522 | 1114.1 |  | 8845 | 120.46 | 1.7168 | 61.703 | 0.004987 | 88.522 | 1114.1 | 1025.578
8846 | 1.7173 | 120.47 | 61.702 | 0.0049883 | 88.532 | 1114.2 |  | 8846 | 120.47 | 1.7173 | 61.702 | 0.0049883 | 88.532 | 1114.2 | 1025.668
8847 | 1.7178 | 120.48 | 61.702 | 0.0049896 | 88.542 | 1114.2 |  | 8847 | 120.48 | 1.7178 | 61.702 | 0.0049896 | 88.542 | 1114.2 | 1025.658
8848 | 1.7182 | 120.49 | 61.702 | 0.0049909 | 88.552 | 1114.2 |  | 8848 | 120.49 | 1.7182 | 61.702 | 0.0049909 | 88.552 | 1114.2 | 1025.648
8849 | 1.7187 | 120.5 | 61.702 | 0.0049922 | 88.562 | 1114.2 |  | 8849 | 120.5 | 1.7187 | 61.702 | 0.0049922 | 88.562 | 1114.2 | 1025.638
8850 | 1.7192 | 120.51 | 61.702 | 0.0049935 | 88.572 | 1114.2 |  | 8850 | 120.51 | 1.7192 | 61.702 | 0.0049935 | 88.572 | 1114.2 | 1025.628
8851 | 1.7197 | 120.52 | 61.702 | 0.0049948 | 88.582 | 1114.2 |  | 8851 | 120.52 | 1.7197 | 61.702 | 0.0049948 | 88.582 | 1114.2 | 1025.618
8852 | 1.7201 | 120.53 | 61.701 | 0.0049961 | 88.592 | 1114.2 |  | 8852 | 120.53 | 1.7201 | 61.701 | 0.0049961 | 88.592 | 1114.2 | 1025.608
8853 | 1.7206 | 120.54 | 61.701 | 0.0049974 | 88.602 | 1114.2 |  | 8853 | 120.54 | 1.7206 | 61.701 | 0.0049974 | 88.602 | 1114.2 | 1025.598
8854 | 1.7211 | 120.55 | 61.701 | 0.0049987 | 88.612 | 1114.2 |  | 8854 | 120.55 | 1.7211 | 61.701 | 0.0049987 | 88.612 | 1114.2 | 1025.588
8855 | 1.7216 | 120.56 | 61.701 | 0.005 | 88.622 | 1114.2 |  | 8855 | 120.56 | 1.7216 | 61.701 | 0.005 | 88.622 | 1114.2 | 1025.578
8856 | 1.7221 | 120.57 | 61.701 | 0.0050013 | 88.632 | 1114.2 |  | 8856 | 120.57 | 1.7221 | 61.701 | 0.0050013 | 88.632 | 1114.2 | 1025.568
8857 | 1.7225 | 120.58 | 61.701 | 0.0050026 | 88.642 | 1114.2 |  | 8857 | 120.58 | 1.7225 | 61.701 | 0.0050026 | 88.642 | 1114.2 | 1025.558
8858 | 1.723 | 120.59 | 61.701 | 0.0050039 | 88.652 | 1114.2 |  | 8858 | 120.59 | 1.723 | 61.701 | 0.0050039 | 88.652 | 1114.2 | 1025.548
8859 | 1.7235 | 120.6 | 61.7 | 0.0050052 | 88.662 | 1114.2 |  | 8859 | 120.6 | 1.7235 | 61.7 | 0.0050052 | 88.662 | 1114.2 | 1025.538
8860 | 1.724 | 120.61 | 61.7 | 0.0050065 | 88.672 | 1114.2 |  | 8860 | 120.61 | 1.724 | 61.7 | 0.0050065 | 88.672 | 1114.2 | 1025.528
8861 | 1.7244 | 120.62 | 61.7 | 0.0050078 | 88.682 | 1114.2 |  | 8861 | 120.62 | 1.7244 | 61.7 | 0.0050078 | 88.682 | 1114.2 | 1025.518
8862 | 1.7249 | 120.63 | 61.7 | 0.0050091 | 88.692 | 1114.2 |  | 8862 | 120.63 | 1.7249 | 61.7 | 0.0050091 | 88.692 | 1114.2 | 1025.508
8863 | 1.7254 | 120.64 | 61.7 | 0.0050104 | 88.702 | 1114.2 |  | 8863 | 120.64 | 1.7254 | 61.7 | 0.0050104 | 88.702 | 1114.2 | 1025.498
8864 | 1.7259 | 120.65 | 61.7 | 0.0050117 | 88.712 | 1114.2 |  | 8864 | 120.65 | 1.7259 | 61.7 | 0.0050117 | 88.712 | 1114.2 | 1025.488
8865 | 1.7264 | 120.66 | 61.699 | 0.005013 | 88.722 | 1114.2 |  | 8865 | 120.66 | 1.7264 | 61.699 | 0.005013 | 88.722 | 1114.2 | 1025.478
8866 | 1.7268 | 120.67 | 61.699 | 0.0050143 | 88.732 | 1114.2 |  | 8866 | 120.67 | 1.7268 | 61.699 | 0.0050143 | 88.732 | 1114.2 | 1025.468
8867 | 1.7273 | 120.68 | 61.699 | 0.0050156 | 88.742 | 1114.2 |  | 8867 | 120.68 | 1.7273 | 61.699 | 0.0050156 | 88.742 | 1114.2 | 1025.458
8868 | 1.7278 | 120.69 | 61.699 | 0.005017 | 88.752 | 1114.2 |  | 8868 | 120.69 | 1.7278 | 61.699 | 0.005017 | 88.752 | 1114.2 | 1025.448
8869 | 1.7283 | 120.7 | 61.699 | 0.0050183 | 88.762 | 1114.2 |  | 8869 | 120.7 | 1.7283 | 61.699 | 0.0050183 | 88.762 | 1114.2 | 1025.438
8870 | 1.7288 | 120.71 | 61.699 | 0.0050196 | 88.772 | 1114.3 |  | 8870 | 120.71 | 1.7288 | 61.699 | 0.0050196 | 88.772 | 1114.3 | 1025.528
8871 | 1.7292 | 120.72 | 61.699 | 0.0050209 | 88.782 | 1114.3 |  | 8871 | 120.72 | 1.7292 | 61.699 | 0.0050209 | 88.782 | 1114.3 | 1025.518
8872 | 1.7297 | 120.73 | 61.698 | 0.0050222 | 88.792 | 1114.3 |  | 8872 | 120.73 | 1.7297 | 61.698 | 0.0050222 | 88.792 | 1114.3 | 1025.508
8873 | 1.7302 | 120.74 | 61.698 | 0.0050235 | 88.802 | 1114.3 |  | 8873 | 120.74 | 1.7302 | 61.698 | 0.0050235 | 88.802 | 1114.3 | 1025.498
8874 | 1.7307 | 120.75 | 61.698 | 0.0050248 | 88.812 | 1114.3 |  | 8874 | 120.75 | 1.7307 | 61.698 | 0.0050248 | 88.812 | 1114.3 | 1025.488
8875 | 1.7311 | 120.76 | 61.698 | 0.0050261 | 88.822 | 1114.3 |  | 8875 | 120.76 | 1.7311 | 61.698 | 0.0050261 | 88.822 | 1114.3 | 1025.478
8876 | 1.7316 | 120.77 | 61.698 | 0.0050274 | 88.832 | 1114.3 |  | 8876 | 120.77 | 1.7316 | 61.698 | 0.0050274 | 88.832 | 1114.3 | 1025.468
8877 | 1.7321 | 120.78 | 61.698 | 0.0050287 | 88.842 | 1114.3 |  | 8877 | 120.78 | 1.7321 | 61.698 | 0.0050287 | 88.842 | 1114.3 | 1025.458
8878 | 1.7326 | 120.79 | 61.697 | 0.00503 | 88.852 | 1114.3 |  | 8878 | 120.79 | 1.7326 | 61.697 | 0.00503 | 88.852 | 1114.3 | 1025.448
8879 | 1.7331 | 120.8 | 61.697 | 0.0050314 | 88.862 | 1114.3 |  | 8879 | 120.8 | 1.7331 | 61.697 | 0.0050314 | 88.862 | 1114.3 | 1025.438
8880 | 1.7335 | 120.81 | 61.697 | 0.0050327 | 88.872 | 1114.3 |  | 8880 | 120.81 | 1.7335 | 61.697 | 0.0050327 | 88.872 | 1114.3 | 1025.428
8881 | 1.734 | 120.82 | 61.697 | 0.005034 | 88.882 | 1114.3 |  | 8881 | 120.82 | 1.734 | 61.697 | 0.005034 | 88.882 | 1114.3 | 1025.418
8882 | 1.7345 | 120.83 | 61.697 | 0.0050353 | 88.892 | 1114.3 |  | 8882 | 120.83 | 1.7345 | 61.697 | 0.0050353 | 88.892 | 1114.3 | 1025.408
8883 | 1.735 | 120.84 | 61.697 | 0.0050366 | 88.902 | 1114.3 |  | 8883 | 120.84 | 1.735 | 61.697 | 0.0050366 | 88.902 | 1114.3 | 1025.398
8884 | 1.7355 | 120.85 | 61.697 | 0.0050379 | 88.912 | 1114.3 |  | 8884 | 120.85 | 1.7355 | 61.697 | 0.0050379 | 88.912 | 1114.3 | 1025.388
8885 | 1.7359 | 120.86 | 61.696 | 0.0050392 | 88.922 | 1114.3 |  | 8885 | 120.86 | 1.7359 | 61.696 | 0.0050392 | 88.922 | 1114.3 | 1025.378
8886 | 1.7364 | 120.87 | 61.696 | 0.0050405 | 88.932 | 1114.3 |  | 8886 | 120.87 | 1.7364 | 61.696 | 0.0050405 | 88.932 | 1114.3 | 1025.368
8887 | 1.7369 | 120.88 | 61.696 | 0.0050418 | 88.942 | 1114.3 |  | 8887 | 120.88 | 1.7369 | 61.696 | 0.0050418 | 88.942 | 1114.3 | 1025.358
8888 | 1.7374 | 120.89 | 61.696 | 0.0050432 | 88.952 | 1114.3 |  | 8888 | 120.89 | 1.7374 | 61.696 | 0.0050432 | 88.952 | 1114.3 | 1025.348
8889 | 1.7379 | 120.9 | 61.696 | 0.0050445 | 88.962 | 1114.3 |  | 8889 | 120.9 | 1.7379 | 61.696 | 0.0050445 | 88.962 | 1114.3 | 1025.338
8890 | 1.7384 | 120.91 | 61.696 | 0.0050458 | 88.972 | 1114.3 |  | 8890 | 120.91 | 1.7384 | 61.696 | 0.0050458 | 88.972 | 1114.3 | 1025.328
8891 | 1.7388 | 120.92 | 61.695 | 0.0050471 | 88.982 | 1114.3 |  | 8891 | 120.92 | 1.7388 | 61.695 | 0.0050471 | 88.982 | 1114.3 | 1025.318
8892 | 1.7393 | 120.93 | 61.695 | 0.0050484 | 88.992 | 1114.3 |  | 8892 | 120.93 | 1.7393 | 61.695 | 0.0050484 | 88.992 | 1114.3 | 1025.308
8893 | 1.7398 | 120.94 | 61.695 | 0.0050497 | 89.001 | 1114.4 |  | 8893 | 120.94 | 1.7398 | 61.695 | 0.0050497 | 89.001 | 1114.4 | 1025.399
8894 | 1.7403 | 120.95 | 61.695 | 0.005051 | 89.011 | 1114.4 |  | 8894 | 120.95 | 1.7403 | 61.695 | 0.005051 | 89.011 | 1114.4 | 1025.389
8895 | 1.7408 | 120.96 | 61.695 | 0.0050524 | 89.021 | 1114.4 |  | 8895 | 120.96 | 1.7408 | 61.695 | 0.0050524 | 89.021 | 1114.4 | 1025.379
8896 | 1.7412 | 120.97 | 61.695 | 0.0050537 | 89.031 | 1114.4 |  | 8896 | 120.97 | 1.7412 | 61.695 | 0.0050537 | 89.031 | 1114.4 | 1025.369
8897 | 1.7417 | 120.98 | 61.695 | 0.005055 | 89.041 | 1114.4 |  | 8897 | 120.98 | 1.7417 | 61.695 | 0.005055 | 89.041 | 1114.4 | 1025.359
8898 | 1.7422 | 120.99 | 61.694 | 0.0050563 | 89.051 | 1114.4 |  | 8898 | 120.99 | 1.7422 | 61.694 | 0.0050563 | 89.051 | 1114.4 | 1025.349
8899 | 1.7427 | 121 | 61.694 | 0.0050576 | 89.061 | 1114.4 |  | 8899 | 121 | 1.7427 | 61.694 | 0.0050576 | 89.061 | 1114.4 | 1025.339
8900 | 1.7432 | 121.01 | 61.694 | 0.0050589 | 89.071 | 1114.4 |  | 8900 | 121.01 | 1.7432 | 61.694 | 0.0050589 | 89.071 | 1114.4 | 1025.329
8901 | 1.7437 | 121.02 | 61.694 | 0.0050602 | 89.081 | 1114.4 |  | 8901 | 121.02 | 1.7437 | 61.694 | 0.0050602 | 89.081 | 1114.4 | 1025.319
8902 | 1.7441 | 121.03 | 61.694 | 0.0050616 | 89.091 | 1114.4 |  | 8902 | 121.03 | 1.7441 | 61.694 | 0.0050616 | 89.091 | 1114.4 | 1025.309
8903 | 1.7446 | 121.04 | 61.694 | 0.0050629 | 89.101 | 1114.4 |  | 8903 | 121.04 | 1.7446 | 61.694 | 0.0050629 | 89.101 | 1114.4 | 1025.299
8904 | 1.7451 | 121.05 | 61.693 | 0.0050642 | 89.111 | 1114.4 |  | 8904 | 121.05 | 1.7451 | 61.693 | 0.0050642 | 89.111 | 1114.4 | 1025.289
8905 | 1.7456 | 121.06 | 61.693 | 0.0050655 | 89.121 | 1114.4 |  | 8905 | 121.06 | 1.7456 | 61.693 | 0.0050655 | 89.121 | 1114.4 | 1025.279
8906 | 1.7461 | 121.07 | 61.693 | 0.0050668 | 89.131 | 1114.4 |  | 8906 | 121.07 | 1.7461 | 61.693 | 0.0050668 | 89.131 | 1114.4 | 1025.269
8907 | 1.7466 | 121.08 | 61.693 | 0.0050682 | 89.141 | 1114.4 |  | 8907 | 121.08 | 1.7466 | 61.693 | 0.0050682 | 89.141 | 1114.4 | 1025.259
8908 | 1.747 | 121.09 | 61.693 | 0.0050695 | 89.151 | 1114.4 |  | 8908 | 121.09 | 1.747 | 61.693 | 0.0050695 | 89.151 | 1114.4 | 1025.249
8909 | 1.7475 | 121.1 | 61.693 | 0.0050708 | 89.161 | 1114.4 |  | 8909 | 121.1 | 1.7475 | 61.693 | 0.0050708 | 89.161 | 1114.4 | 1025.239
8910 | 1.748 | 121.11 | 61.692 | 0.0050721 | 89.171 | 1114.4 |  | 8910 | 121.11 | 1.748 | 61.692 | 0.0050721 | 89.171 | 1114.4 | 1025.229
8911 | 1.7485 | 121.12 | 61.692 | 0.0050734 | 89.181 | 1114.4 |  | 8911 | 121.12 | 1.7485 | 61.692 | 0.0050734 | 89.181 | 1114.4 | 1025.219
8912 | 1.749 | 121.13 | 61.692 | 0.0050748 | 89.191 | 1114.4 |  | 8912 | 121.13 | 1.749 | 61.692 | 0.0050748 | 89.191 | 1114.4 | 1025.209
8913 | 1.7495 | 121.14 | 61.692 | 0.0050761 | 89.201 | 1114.4 |  | 8913 | 121.14 | 1.7495 | 61.692 | 0.0050761 | 89.201 | 1114.4 | 1025.199
8914 | 1.7499 | 121.15 | 61.692 | 0.0050774 | 89.211 | 1114.4 |  | 8914 | 121.15 | 1.7499 | 61.692 | 0.0050774 | 89.211 | 1114.4 | 1025.189
8915 | 1.7504 | 121.16 | 61.692 | 0.0050787 | 89.221 | 1114.4 |  | 8915 | 121.16 | 1.7504 | 61.692 | 0.0050787 | 89.221 | 1114.4 | 1025.179
8916 | 1.7509 | 121.17 | 61.692 | 0.00508 | 89.231 | 1114.4 |  | 8916 | 121.17 | 1.7509 | 61.692 | 0.00508 | 89.231 | 1114.4 | 1025.169
8917 | 1.7514 | 121.18 | 61.691 | 0.0050814 | 89.241 | 1114.5 |  | 8917 | 121.18 | 1.7514 | 61.691 | 0.0050814 | 89.241 | 1114.5 | 1025.259
8918 | 1.7519 | 121.19 | 61.691 | 0.0050827 | 89.251 | 1114.5 |  | 8918 | 121.19 | 1.7519 | 61.691 | 0.0050827 | 89.251 | 1114.5 | 1025.249
8919 | 1.7524 | 121.2 | 61.691 | 0.005084 | 89.261 | 1114.5 |  | 8919 | 121.2 | 1.7524 | 61.691 | 0.005084 | 89.261 | 1114.5 | 1025.239
8920 | 1.7528 | 121.21 | 61.691 | 0.0050853 | 89.271 | 1114.5 |  | 8920 | 121.21 | 1.7528 | 61.691 | 0.0050853 | 89.271 | 1114.5 | 1025.229
8921 | 1.7533 | 121.22 | 61.691 | 0.0050866 | 89.281 | 1114.5 |  | 8921 | 121.22 | 1.7533 | 61.691 | 0.0050866 | 89.281 | 1114.5 | 1025.219
8922 | 1.7538 | 121.23 | 61.691 | 0.005088 | 89.291 | 1114.5 |  | 8922 | 121.23 | 1.7538 | 61.691 | 0.005088 | 89.291 | 1114.5 | 1025.209
8923 | 1.7543 | 121.24 | 61.69 | 0.0050893 | 89.301 | 1114.5 |  | 8923 | 121.24 | 1.7543 | 61.69 | 0.0050893 | 89.301 | 1114.5 | 1025.199
8924 | 1.7548 | 121.25 | 61.69 | 0.0050906 | 89.311 | 1114.5 |  | 8924 | 121.25 | 1.7548 | 61.69 | 0.0050906 | 89.311 | 1114.5 | 1025.189
8925 | 1.7553 | 121.26 | 61.69 | 0.0050919 | 89.321 | 1114.5 |  | 8925 | 121.26 | 1.7553 | 61.69 | 0.0050919 | 89.321 | 1114.5 | 1025.179
8926 | 1.7558 | 121.27 | 61.69 | 0.0050933 | 89.331 | 1114.5 |  | 8926 | 121.27 | 1.7558 | 61.69 | 0.0050933 | 89.331 | 1114.5 | 1025.169
8927 | 1.7562 | 121.28 | 61.69 | 0.0050946 | 89.341 | 1114.5 |  | 8927 | 121.28 | 1.7562 | 61.69 | 0.0050946 | 89.341 | 1114.5 | 1025.159
8928 | 1.7567 | 121.29 | 61.69 | 0.0050959 | 89.351 | 1114.5 |  | 8928 | 121.29 | 1.7567 | 61.69 | 0.0050959 | 89.351 | 1114.5 | 1025.149
8929 | 1.7572 | 121.3 | 61.69 | 0.0050972 | 89.361 | 1114.5 |  | 8929 | 121.3 | 1.7572 | 61.69 | 0.0050972 | 89.361 | 1114.5 | 1025.139
8930 | 1.7577 | 121.31 | 61.689 | 0.0050986 | 89.371 | 1114.5 |  | 8930 | 121.31 | 1.7577 | 61.689 | 0.0050986 | 89.371 | 1114.5 | 1025.129
8931 | 1.7582 | 121.32 | 61.689 | 0.0050999 | 89.381 | 1114.5 |  | 8931 | 121.32 | 1.7582 | 61.689 | 0.0050999 | 89.381 | 1114.5 | 1025.119
8932 | 1.7587 | 121.33 | 61.689 | 0.0051012 | 89.391 | 1114.5 |  | 8932 | 121.33 | 1.7587 | 61.689 | 0.0051012 | 89.391 | 1114.5 | 1025.109
8933 | 1.7592 | 121.34 | 61.689 | 0.0051025 | 89.401 | 1114.5 |  | 8933 | 121.34 | 1.7592 | 61.689 | 0.0051025 | 89.401 | 1114.5 | 1025.099
8934 | 1.7596 | 121.35 | 61.689 | 0.0051039 | 89.411 | 1114.5 |  | 8934 | 121.35 | 1.7596 | 61.689 | 0.0051039 | 89.411 | 1114.5 | 1025.089
8935 | 1.7601 | 121.36 | 61.689 | 0.0051052 | 89.421 | 1114.5 |  | 8935 | 121.36 | 1.7601 | 61.689 | 0.0051052 | 89.421 | 1114.5 | 1025.079
8936 | 1.7606 | 121.37 | 61.688 | 0.0051065 | 89.431 | 1114.5 |  | 8936 | 121.37 | 1.7606 | 61.688 | 0.0051065 | 89.431 | 1114.5 | 1025.069
8937 | 1.7611 | 121.38 | 61.688 | 0.0051078 | 89.441 | 1114.5 |  | 8937 | 121.38 | 1.7611 | 61.688 | 0.0051078 | 89.441 | 1114.5 | 1025.059
8938 | 1.7616 | 121.39 | 61.688 | 0.0051092 | 89.451 | 1114.5 |  | 8938 | 121.39 | 1.7616 | 61.688 | 0.0051092 | 89.451 | 1114.5 | 1025.049
8939 | 1.7621 | 121.4 | 61.688 | 0.0051105 | 89.461 | 1114.5 |  | 8939 | 121.4 | 1.7621 | 61.688 | 0.0051105 | 89.461 | 1114.5 | 1025.039
8940 | 1.7626 | 121.41 | 61.688 | 0.0051118 | 89.471 | 1114.6 |  | 8940 | 121.41 | 1.7626 | 61.688 | 0.0051118 | 89.471 | 1114.6 | 1025.129
8941 | 1.763 | 121.42 | 61.688 | 0.0051132 | 89.481 | 1114.6 |  | 8941 | 121.42 | 1.763 | 61.688 | 0.0051132 | 89.481 | 1114.6 | 1025.119
8942 | 1.7635 | 121.43 | 61.688 | 0.0051145 | 89.491 | 1114.6 |  | 8942 | 121.43 | 1.7635 | 61.688 | 0.0051145 | 89.491 | 1114.6 | 1025.109
8943 | 1.764 | 121.44 | 61.687 | 0.0051158 | 89.501 | 1114.6 |  | 8943 | 121.44 | 1.764 | 61.687 | 0.0051158 | 89.501 | 1114.6 | 1025.099
8944 | 1.7645 | 121.45 | 61.687 | 0.0051171 | 89.511 | 1114.6 |  | 8944 | 121.45 | 1.7645 | 61.687 | 0.0051171 | 89.511 | 1114.6 | 1025.089
8945 | 1.765 | 121.46 | 61.687 | 0.0051185 | 89.521 | 1114.6 |  | 8945 | 121.46 | 1.765 | 61.687 | 0.0051185 | 89.521 | 1114.6 | 1025.079
8946 | 1.7655 | 121.47 | 61.687 | 0.0051198 | 89.531 | 1114.6 |  | 8946 | 121.47 | 1.7655 | 61.687 | 0.0051198 | 89.531 | 1114.6 | 1025.069
8947 | 1.766 | 121.48 | 61.687 | 0.0051211 | 89.541 | 1114.6 |  | 8947 | 121.48 | 1.766 | 61.687 | 0.0051211 | 89.541 | 1114.6 | 1025.059
8948 | 1.7665 | 121.49 | 61.687 | 0.0051225 | 89.551 | 1114.6 |  | 8948 | 121.49 | 1.7665 | 61.687 | 0.0051225 | 89.551 | 1114.6 | 1025.049
8949 | 1.7669 | 121.5 | 61.686 | 0.0051238 | 89.561 | 1114.6 |  | 8949 | 121.5 | 1.7669 | 61.686 | 0.0051238 | 89.561 | 1114.6 | 1025.039
8950 | 1.7674 | 121.51 | 61.686 | 0.0051251 | 89.571 | 1114.6 |  | 8950 | 121.51 | 1.7674 | 61.686 | 0.0051251 | 89.571 | 1114.6 | 1025.029
8951 | 1.7679 | 121.52 | 61.686 | 0.0051264 | 89.581 | 1114.6 |  | 8951 | 121.52 | 1.7679 | 61.686 | 0.0051264 | 89.581 | 1114.6 | 1025.019
8952 | 1.7684 | 121.53 | 61.686 | 0.0051278 | 89.591 | 1114.6 |  | 8952 | 121.53 | 1.7684 | 61.686 | 0.0051278 | 89.591 | 1114.6 | 1025.009
8953 | 1.7689 | 121.54 | 61.686 | 0.0051291 | 89.601 | 1114.6 |  | 8953 | 121.54 | 1.7689 | 61.686 | 0.0051291 | 89.601 | 1114.6 | 1024.999
8954 | 1.7694 | 121.55 | 61.686 | 0.0051304 | 89.611 | 1114.6 |  | 8954 | 121.55 | 1.7694 | 61.686 | 0.0051304 | 89.611 | 1114.6 | 1024.989
8955 | 1.7699 | 121.56 | 61.685 | 0.0051318 | 89.621 | 1114.6 |  | 8955 | 121.56 | 1.7699 | 61.685 | 0.0051318 | 89.621 | 1114.6 | 1024.979
8956 | 1.7704 | 121.57 | 61.685 | 0.0051331 | 89.631 | 1114.6 |  | 8956 | 121.57 | 1.7704 | 61.685 | 0.0051331 | 89.631 | 1114.6 | 1024.969
8957 | 1.7709 | 121.58 | 61.685 | 0.0051344 | 89.641 | 1114.6 |  | 8957 | 121.58 | 1.7709 | 61.685 | 0.0051344 | 89.641 | 1114.6 | 1024.959
8958 | 1.7713 | 121.59 | 61.685 | 0.0051358 | 89.651 | 1114.6 |  | 8958 | 121.59 | 1.7713 | 61.685 | 0.0051358 | 89.651 | 1114.6 | 1024.949
8959 | 1.7718 | 121.6 | 61.685 | 0.0051371 | 89.661 | 1114.6 |  | 8959 | 121.6 | 1.7718 | 61.685 | 0.0051371 | 89.661 | 1114.6 | 1024.939
8960 | 1.7723 | 121.61 | 61.685 | 0.0051384 | 89.671 | 1114.6 |  | 8960 | 121.61 | 1.7723 | 61.685 | 0.0051384 | 89.671 | 1114.6 | 1024.929
8961 | 1.7728 | 121.62 | 61.685 | 0.0051398 | 89.681 | 1114.6 |  | 8961 | 121.62 | 1.7728 | 61.685 | 0.0051398 | 89.681 | 1114.6 | 1024.919
8962 | 1.7733 | 121.63 | 61.684 | 0.0051411 | 89.691 | 1114.6 |  | 8962 | 121.63 | 1.7733 | 61.684 | 0.0051411 | 89.691 | 1114.6 | 1024.909
8963 | 1.7738 | 121.64 | 61.684 | 0.0051424 | 89.701 | 1114.6 |  | 8963 | 121.64 | 1.7738 | 61.684 | 0.0051424 | 89.701 | 1114.6 | 1024.899
8964 | 1.7743 | 121.65 | 61.684 | 0.0051438 | 89.711 | 1114.7 |  | 8964 | 121.65 | 1.7743 | 61.684 | 0.0051438 | 89.711 | 1114.7 | 1024.989
8965 | 1.7748 | 121.66 | 61.684 | 0.0051451 | 89.721 | 1114.7 |  | 8965 | 121.66 | 1.7748 | 61.684 | 0.0051451 | 89.721 | 1114.7 | 1024.979
8966 | 1.7753 | 121.67 | 61.684 | 0.0051465 | 89.731 | 1114.7 |  | 8966 | 121.67 | 1.7753 | 61.684 | 0.0051465 | 89.731 | 1114.7 | 1024.969
8967 | 1.7758 | 121.68 | 61.684 | 0.0051478 | 89.741 | 1114.7 |  | 8967 | 121.68 | 1.7758 | 61.684 | 0.0051478 | 89.741 | 1114.7 | 1024.959
8968 | 1.7762 | 121.69 | 61.683 | 0.0051491 | 89.751 | 1114.7 |  | 8968 | 121.69 | 1.7762 | 61.683 | 0.0051491 | 89.751 | 1114.7 | 1024.949
8969 | 1.7767 | 121.7 | 61.683 | 0.0051505 | 89.761 | 1114.7 |  | 8969 | 121.7 | 1.7767 | 61.683 | 0.0051505 | 89.761 | 1114.7 | 1024.939
8970 | 1.7772 | 121.71 | 61.683 | 0.0051518 | 89.771 | 1114.7 |  | 8970 | 121.71 | 1.7772 | 61.683 | 0.0051518 | 89.771 | 1114.7 | 1024.929
8971 | 1.7777 | 121.72 | 61.683 | 0.0051531 | 89.781 | 1114.7 |  | 8971 | 121.72 | 1.7777 | 61.683 | 0.0051531 | 89.781 | 1114.7 | 1024.919
8972 | 1.7782 | 121.73 | 61.683 | 0.0051545 | 89.791 | 1114.7 |  | 8972 | 121.73 | 1.7782 | 61.683 | 0.0051545 | 89.791 | 1114.7 | 1024.909
8973 | 1.7787 | 121.74 | 61.683 | 0.0051558 | 89.801 | 1114.7 |  | 8973 | 121.74 | 1.7787 | 61.683 | 0.0051558 | 89.801 | 1114.7 | 1024.899
8974 | 1.7792 | 121.75 | 61.683 | 0.0051571 | 89.811 | 1114.7 |  | 8974 | 121.75 | 1.7792 | 61.683 | 0.0051571 | 89.811 | 1114.7 | 1024.889
8975 | 1.7797 | 121.76 | 61.682 | 0.0051585 | 89.821 | 1114.7 |  | 8975 | 121.76 | 1.7797 | 61.682 | 0.0051585 | 89.821 | 1114.7 | 1024.879
8976 | 1.7802 | 121.77 | 61.682 | 0.0051598 | 89.831 | 1114.7 |  | 8976 | 121.77 | 1.7802 | 61.682 | 0.0051598 | 89.831 | 1114.7 | 1024.869
8977 | 1.7807 | 121.78 | 61.682 | 0.0051612 | 89.841 | 1114.7 |  | 8977 | 121.78 | 1.7807 | 61.682 | 0.0051612 | 89.841 | 1114.7 | 1024.859
8978 | 1.7812 | 121.79 | 61.682 | 0.0051625 | 89.851 | 1114.7 |  | 8978 | 121.79 | 1.7812 | 61.682 | 0.0051625 | 89.851 | 1114.7 | 1024.849
8979 | 1.7816 | 121.8 | 61.682 | 0.0051638 | 89.861 | 1114.7 |  | 8979 | 121.8 | 1.7816 | 61.682 | 0.0051638 | 89.861 | 1114.7 | 1024.839
8980 | 1.7821 | 121.81 | 61.682 | 0.0051652 | 89.871 | 1114.7 |  | 8980 | 121.81 | 1.7821 | 61.682 | 0.0051652 | 89.871 | 1114.7 | 1024.829
8981 | 1.7826 | 121.82 | 61.681 | 0.0051665 | 89.881 | 1114.7 |  | 8981 | 121.82 | 1.7826 | 61.681 | 0.0051665 | 89.881 | 1114.7 | 1024.819
8982 | 1.7831 | 121.83 | 61.681 | 0.0051679 | 89.891 | 1114.7 |  | 8982 | 121.83 | 1.7831 | 61.681 | 0.0051679 | 89.891 | 1114.7 | 1024.809
8983 | 1.7836 | 121.84 | 61.681 | 0.0051692 | 89.901 | 1114.7 |  | 8983 | 121.84 | 1.7836 | 61.681 | 0.0051692 | 89.901 | 1114.7 | 1024.799
8984 | 1.7841 | 121.85 | 61.681 | 0.0051705 | 89.911 | 1114.7 |  | 8984 | 121.85 | 1.7841 | 61.681 | 0.0051705 | 89.911 | 1114.7 | 1024.789
8985 | 1.7846 | 121.86 | 61.681 | 0.0051719 | 89.921 | 1114.7 |  | 8985 | 121.86 | 1.7846 | 61.681 | 0.0051719 | 89.921 | 1114.7 | 1024.779
8986 | 1.7851 | 121.87 | 61.681 | 0.0051732 | 89.931 | 1114.7 |  | 8986 | 121.87 | 1.7851 | 61.681 | 0.0051732 | 89.931 | 1114.7 | 1024.769
8987 | 1.7856 | 121.88 | 61.68 | 0.0051746 | 89.941 | 1114.7 |  | 8987 | 121.88 | 1.7856 | 61.68 | 0.0051746 | 89.941 | 1114.7 | 1024.759
8988 | 1.7861 | 121.89 | 61.68 | 0.0051759 | 89.951 | 1114.8 |  | 8988 | 121.89 | 1.7861 | 61.68 | 0.0051759 | 89.951 | 1114.8 | 1024.849
8989 | 1.7866 | 121.9 | 61.68 | 0.0051772 | 89.961 | 1114.8 |  | 8989 | 121.9 | 1.7866 | 61.68 | 0.0051772 | 89.961 | 1114.8 | 1024.839
8990 | 1.7871 | 121.91 | 61.68 | 0.0051786 | 89.971 | 1114.8 |  | 8990 | 121.91 | 1.7871 | 61.68 | 0.0051786 | 89.971 | 1114.8 | 1024.829
8991 | 1.7876 | 121.92 | 61.68 | 0.0051799 | 89.981 | 1114.8 |  | 8991 | 121.92 | 1.7876 | 61.68 | 0.0051799 | 89.981 | 1114.8 | 1024.819
8992 | 1.788 | 121.93 | 61.68 | 0.0051813 | 89.991 | 1114.8 |  | 8992 | 121.93 | 1.788 | 61.68 | 0.0051813 | 89.991 | 1114.8 | 1024.809
8993 | 1.7885 | 121.94 | 61.68 | 0.0051826 | 90.001 | 1114.8 |  | 8993 | 121.94 | 1.7885 | 61.68 | 0.0051826 | 90.001 | 1114.8 | 1024.799
8994 | 1.789 | 121.95 | 61.679 | 0.005184 | 90.011 | 1114.8 |  | 8994 | 121.95 | 1.789 | 61.679 | 0.005184 | 90.011 | 1114.8 | 1024.789
8995 | 1.7895 | 121.96 | 61.679 | 0.0051853 | 90.021 | 1114.8 |  | 8995 | 121.96 | 1.7895 | 61.679 | 0.0051853 | 90.021 | 1114.8 | 1024.779
8996 | 1.79 | 121.97 | 61.679 | 0.0051867 | 90.031 | 1114.8 |  | 8996 | 121.97 | 1.79 | 61.679 | 0.0051867 | 90.031 | 1114.8 | 1024.769
8997 | 1.7905 | 121.98 | 61.679 | 0.005188 | 90.041 | 1114.8 |  | 8997 | 121.98 | 1.7905 | 61.679 | 0.005188 | 90.041 | 1114.8 | 1024.759
8998 | 1.791 | 121.99 | 61.679 | 0.0051893 | 90.051 | 1114.8 |  | 8998 | 121.99 | 1.791 | 61.679 | 0.0051893 | 90.051 | 1114.8 | 1024.749
8999 | 1.7915 | 122 | 61.679 | 0.0051907 | 90.061 | 1114.8 |  | 8999 | 122 | 1.7915 | 61.679 | 0.0051907 | 90.061 | 1114.8 | 1024.739
9000 | 1.792 | 122.01 | 61.678 | 0.005192 | 90.071 | 1114.8 |  | 9000 | 122.01 | 1.792 | 61.678 | 0.005192 | 90.071 | 1114.8 | 1024.729
9001 | 1.7925 | 122.02 | 61.678 | 0.0051934 | 90.081 | 1114.8 |  | 9001 | 122.02 | 1.7925 | 61.678 | 0.0051934 | 90.081 | 1114.8 | 1024.719
9002 | 1.793 | 122.03 | 61.678 | 0.0051947 | 90.091 | 1114.8 |  | 9002 | 122.03 | 1.793 | 61.678 | 0.0051947 | 90.091 | 1114.8 | 1024.709
9003 | 1.7935 | 122.04 | 61.678 | 0.0051961 | 90.101 | 1114.8 |  | 9003 | 122.04 | 1.7935 | 61.678 | 0.0051961 | 90.101 | 1114.8 | 1024.699
9004 | 1.794 | 122.05 | 61.678 | 0.0051974 | 90.111 | 1114.8 |  | 9004 | 122.05 | 1.794 | 61.678 | 0.0051974 | 90.111 | 1114.8 | 1024.689
9005 | 1.7945 | 122.06 | 61.678 | 0.0051988 | 90.121 | 1114.8 |  | 9005 | 122.06 | 1.7945 | 61.678 | 0.0051988 | 90.121 | 1114.8 | 1024.679
9006 | 1.795 | 122.07 | 61.677 | 0.0052001 | 90.131 | 1114.8 |  | 9006 | 122.07 | 1.795 | 61.677 | 0.0052001 | 90.131 | 1114.8 | 1024.669
9007 | 1.7955 | 122.08 | 61.677 | 0.0052015 | 90.141 | 1114.8 |  | 9007 | 122.08 | 1.7955 | 61.677 | 0.0052015 | 90.141 | 1114.8 | 1024.659
9008 | 1.7959 | 122.09 | 61.677 | 0.0052028 | 90.151 | 1114.8 |  | 9008 | 122.09 | 1.7959 | 61.677 | 0.0052028 | 90.151 | 1114.8 | 1024.649
9009 | 1.7964 | 122.1 | 61.677 | 0.0052042 | 90.161 | 1114.8 |  | 9009 | 122.1 | 1.7964 | 61.677 | 0.0052042 | 90.161 | 1114.8 | 1024.639
9010 | 1.7969 | 122.11 | 61.677 | 0.0052055 | 90.171 | 1114.8 |  | 9010 | 122.11 | 1.7969 | 61.677 | 0.0052055 | 90.171 | 1114.8 | 1024.629
9011 | 1.7974 | 122.12 | 61.677 | 0.0052069 | 90.181 | 1114.8 |  | 9011 | 122.12 | 1.7974 | 61.677 | 0.0052069 | 90.181 | 1114.8 | 1024.619
9012 | 1.7979 | 122.13 | 61.677 | 0.0052082 | 90.191 | 1114.9 |  | 9012 | 122.13 | 1.7979 | 61.677 | 0.0052082 | 90.191 | 1114.9 | 1024.709
9013 | 1.7984 | 122.14 | 61.676 | 0.0052096 | 90.201 | 1114.9 |  | 9013 | 122.14 | 1.7984 | 61.676 | 0.0052096 | 90.201 | 1114.9 | 1024.699
9014 | 1.7989 | 122.15 | 61.676 | 0.0052109 | 90.211 | 1114.9 |  | 9014 | 122.15 | 1.7989 | 61.676 | 0.0052109 | 90.211 | 1114.9 | 1024.689
9015 | 1.7994 | 122.16 | 61.676 | 0.0052123 | 90.221 | 1114.9 |  | 9015 | 122.16 | 1.7994 | 61.676 | 0.0052123 | 90.221 | 1114.9 | 1024.679
9016 | 1.7999 | 122.17 | 61.676 | 0.0052136 | 90.231 | 1114.9 |  | 9016 | 122.17 | 1.7999 | 61.676 | 0.0052136 | 90.231 | 1114.9 | 1024.669
9017 | 1.8004 | 122.18 | 61.676 | 0.005215 | 90.241 | 1114.9 |  | 9017 | 122.18 | 1.8004 | 61.676 | 0.005215 | 90.241 | 1114.9 | 1024.659
9018 | 1.8009 | 122.19 | 61.676 | 0.0052163 | 90.251 | 1114.9 |  | 9018 | 122.19 | 1.8009 | 61.676 | 0.0052163 | 90.251 | 1114.9 | 1024.649
9019 | 1.8014 | 122.2 | 61.675 | 0.0052177 | 90.261 | 1114.9 |  | 9019 | 122.2 | 1.8014 | 61.675 | 0.0052177 | 90.261 | 1114.9 | 1024.639
9020 | 1.8019 | 122.21 | 61.675 | 0.005219 | 90.271 | 1114.9 |  | 9020 | 122.21 | 1.8019 | 61.675 | 0.005219 | 90.271 | 1114.9 | 1024.629
9021 | 1.8024 | 122.22 | 61.675 | 0.0052204 | 90.281 | 1114.9 |  | 9021 | 122.22 | 1.8024 | 61.675 | 0.0052204 | 90.281 | 1114.9 | 1024.619
9022 | 1.8029 | 122.23 | 61.675 | 0.0052217 | 90.291 | 1114.9 |  | 9022 | 122.23 | 1.8029 | 61.675 | 0.0052217 | 90.291 | 1114.9 | 1024.609
9023 | 1.8034 | 122.24 | 61.675 | 0.0052231 | 90.301 | 1114.9 |  | 9023 | 122.24 | 1.8034 | 61.675 | 0.0052231 | 90.301 | 1114.9 | 1024.599
9024 | 1.8039 | 122.25 | 61.675 | 0.0052244 | 90.311 | 1114.9 |  | 9024 | 122.25 | 1.8039 | 61.675 | 0.0052244 | 90.311 | 1114.9 | 1024.589
9025 | 1.8044 | 122.26 | 61.675 | 0.0052258 | 90.321 | 1114.9 |  | 9025 | 122.26 | 1.8044 | 61.675 | 0.0052258 | 90.321 | 1114.9 | 1024.579
9026 | 1.8049 | 122.27 | 61.674 | 0.0052271 | 90.331 | 1114.9 |  | 9026 | 122.27 | 1.8049 | 61.674 | 0.0052271 | 90.331 | 1114.9 | 1024.569
9027 | 1.8054 | 122.28 | 61.674 | 0.0052285 | 90.341 | 1114.9 |  | 9027 | 122.28 | 1.8054 | 61.674 | 0.0052285 | 90.341 | 1114.9 | 1024.559
9028 | 1.8059 | 122.29 | 61.674 | 0.0052298 | 90.351 | 1114.9 |  | 9028 | 122.29 | 1.8059 | 61.674 | 0.0052298 | 90.351 | 1114.9 | 1024.549
9029 | 1.8064 | 122.3 | 61.674 | 0.0052312 | 90.361 | 1114.9 |  | 9029 | 122.3 | 1.8064 | 61.674 | 0.0052312 | 90.361 | 1114.9 | 1024.539
9030 | 1.8069 | 122.31 | 61.674 | 0.0052325 | 90.371 | 1114.9 |  | 9030 | 122.31 | 1.8069 | 61.674 | 0.0052325 | 90.371 | 1114.9 | 1024.529
9031 | 1.8074 | 122.32 | 61.674 | 0.0052339 | 90.381 | 1114.9 |  | 9031 | 122.32 | 1.8074 | 61.674 | 0.0052339 | 90.381 | 1114.9 | 1024.519
9032 | 1.8079 | 122.33 | 61.673 | 0.0052352 | 90.391 | 1114.9 |  | 9032 | 122.33 | 1.8079 | 61.673 | 0.0052352 | 90.391 | 1114.9 | 1024.509
9033 | 1.8084 | 122.34 | 61.673 | 0.0052366 | 90.401 | 1114.9 |  | 9033 | 122.34 | 1.8084 | 61.673 | 0.0052366 | 90.401 | 1114.9 | 1024.499
9034 | 1.8089 | 122.35 | 61.673 | 0.005238 | 90.411 | 1114.9 |  | 9034 | 122.35 | 1.8089 | 61.673 | 0.005238 | 90.411 | 1114.9 | 1024.489
9035 | 1.8094 | 122.36 | 61.673 | 0.0052393 | 90.421 | 1115 |  | 9035 | 122.36 | 1.8094 | 61.673 | 0.0052393 | 90.421 | 1115 | 1024.579
9036 | 1.8099 | 122.37 | 61.673 | 0.0052407 | 90.431 | 1115 |  | 9036 | 122.37 | 1.8099 | 61.673 | 0.0052407 | 90.431 | 1115 | 1024.569
9037 | 1.8104 | 122.38 | 61.673 | 0.005242 | 90.441 | 1115 |  | 9037 | 122.38 | 1.8104 | 61.673 | 0.005242 | 90.441 | 1115 | 1024.559
9038 | 1.8108 | 122.39 | 61.672 | 0.0052434 | 90.451 | 1115 |  | 9038 | 122.39 | 1.8108 | 61.672 | 0.0052434 | 90.451 | 1115 | 1024.549
9039 | 1.8113 | 122.4 | 61.672 | 0.0052447 | 90.461 | 1115 |  | 9039 | 122.4 | 1.8113 | 61.672 | 0.0052447 | 90.461 | 1115 | 1024.539
9040 | 1.8118 | 122.41 | 61.672 | 0.0052461 | 90.471 | 1115 |  | 9040 | 122.41 | 1.8118 | 61.672 | 0.0052461 | 90.471 | 1115 | 1024.529
9041 | 1.8123 | 122.42 | 61.672 | 0.0052475 | 90.481 | 1115 |  | 9041 | 122.42 | 1.8123 | 61.672 | 0.0052475 | 90.481 | 1115 | 1024.519
9042 | 1.8128 | 122.43 | 61.672 | 0.0052488 | 90.491 | 1115 |  | 9042 | 122.43 | 1.8128 | 61.672 | 0.0052488 | 90.491 | 1115 | 1024.509
9043 | 1.8133 | 122.44 | 61.672 | 0.0052502 | 90.501 | 1115 |  | 9043 | 122.44 | 1.8133 | 61.672 | 0.0052502 | 90.501 | 1115 | 1024.499
9044 | 1.8138 | 122.45 | 61.672 | 0.0052515 | 90.511 | 1115 |  | 9044 | 122.45 | 1.8138 | 61.672 | 0.0052515 | 90.511 | 1115 | 1024.489
9045 | 1.8143 | 122.46 | 61.671 | 0.0052529 | 90.521 | 1115 |  | 9045 | 122.46 | 1.8143 | 61.671 | 0.0052529 | 90.521 | 1115 | 1024.479
9046 | 1.8148 | 122.47 | 61.671 | 0.0052542 | 90.531 | 1115 |  | 9046 | 122.47 | 1.8148 | 61.671 | 0.0052542 | 90.531 | 1115 | 1024.469
9047 | 1.8153 | 122.48 | 61.671 | 0.0052556 | 90.541 | 1115 |  | 9047 | 122.48 | 1.8153 | 61.671 | 0.0052556 | 90.541 | 1115 | 1024.459
9048 | 1.8158 | 122.49 | 61.671 | 0.005257 | 90.551 | 1115 |  | 9048 | 122.49 | 1.8158 | 61.671 | 0.005257 | 90.551 | 1115 | 1024.449
9049 | 1.8163 | 122.5 | 61.671 | 0.0052583 | 90.561 | 1115 |  | 9049 | 122.5 | 1.8163 | 61.671 | 0.0052583 | 90.561 | 1115 | 1024.439
9050 | 1.8168 | 122.51 | 61.671 | 0.0052597 | 90.571 | 1115 |  | 9050 | 122.51 | 1.8168 | 61.671 | 0.0052597 | 90.571 | 1115 | 1024.429
9051 | 1.8173 | 122.52 | 61.67 | 0.005261 | 90.581 | 1115 |  | 9051 | 122.52 | 1.8173 | 61.67 | 0.005261 | 90.581 | 1115 | 1024.419
9052 | 1.8178 | 122.53 | 61.67 | 0.0052624 | 90.591 | 1115 |  | 9052 | 122.53 | 1.8178 | 61.67 | 0.0052624 | 90.591 | 1115 | 1024.409
9053 | 1.8183 | 122.54 | 61.67 | 0.0052638 | 90.601 | 1115 |  | 9053 | 122.54 | 1.8183 | 61.67 | 0.0052638 | 90.601 | 1115 | 1024.399
9054 | 1.8188 | 122.55 | 61.67 | 0.0052651 | 90.611 | 1115 |  | 9054 | 122.55 | 1.8188 | 61.67 | 0.0052651 | 90.611 | 1115 | 1024.389
9055 | 1.8193 | 122.56 | 61.67 | 0.0052665 | 90.621 | 1115 |  | 9055 | 122.56 | 1.8193 | 61.67 | 0.0052665 | 90.621 | 1115 | 1024.379
9056 | 1.8198 | 122.57 | 61.67 | 0.0052679 | 90.631 | 1115 |  | 9056 | 122.57 | 1.8198 | 61.67 | 0.0052679 | 90.631 | 1115 | 1024.369
9057 | 1.8203 | 122.58 | 61.669 | 0.0052692 | 90.641 | 1115 |  | 9057 | 122.58 | 1.8203 | 61.669 | 0.0052692 | 90.641 | 1115 | 1024.359
9058 | 1.8208 | 122.59 | 61.669 | 0.0052706 | 90.651 | 1115 |  | 9058 | 122.59 | 1.8208 | 61.669 | 0.0052706 | 90.651 | 1115 | 1024.349
9059 | 1.8213 | 122.6 | 61.669 | 0.0052719 | 90.661 | 1115.1 |  | 9059 | 122.6 | 1.8213 | 61.669 | 0.0052719 | 90.661 | 1115.1 | 1024.439
9060 | 1.8218 | 122.61 | 61.669 | 0.0052733 | 90.671 | 1115.1 |  | 9060 | 122.61 | 1.8218 | 61.669 | 0.0052733 | 90.671 | 1115.1 | 1024.429
9061 | 1.8223 | 122.62 | 61.669 | 0.0052747 | 90.681 | 1115.1 |  | 9061 | 122.62 | 1.8223 | 61.669 | 0.0052747 | 90.681 | 1115.1 | 1024.419
9062 | 1.8228 | 122.63 | 61.669 | 0.005276 | 90.691 | 1115.1 |  | 9062 | 122.63 | 1.8228 | 61.669 | 0.005276 | 90.691 | 1115.1 | 1024.409
9063 | 1.8233 | 122.64 | 61.669 | 0.0052774 | 90.701 | 1115.1 |  | 9063 | 122.64 | 1.8233 | 61.669 | 0.0052774 | 90.701 | 1115.1 | 1024.399
9064 | 1.8238 | 122.65 | 61.668 | 0.0052788 | 90.711 | 1115.1 |  | 9064 | 122.65 | 1.8238 | 61.668 | 0.0052788 | 90.711 | 1115.1 | 1024.389
9065 | 1.8243 | 122.66 | 61.668 | 0.0052801 | 90.721 | 1115.1 |  | 9065 | 122.66 | 1.8243 | 61.668 | 0.0052801 | 90.721 | 1115.1 | 1024.379
9066 | 1.8249 | 122.67 | 61.668 | 0.0052815 | 90.731 | 1115.1 |  | 9066 | 122.67 | 1.8249 | 61.668 | 0.0052815 | 90.731 | 1115.1 | 1024.369
9067 | 1.8254 | 122.68 | 61.668 | 0.0052829 | 90.741 | 1115.1 |  | 9067 | 122.68 | 1.8254 | 61.668 | 0.0052829 | 90.741 | 1115.1 | 1024.359
9068 | 1.8259 | 122.69 | 61.668 | 0.0052842 | 90.751 | 1115.1 |  | 9068 | 122.69 | 1.8259 | 61.668 | 0.0052842 | 90.751 | 1115.1 | 1024.349
9069 | 1.8264 | 122.7 | 61.668 | 0.0052856 | 90.761 | 1115.1 |  | 9069 | 122.7 | 1.8264 | 61.668 | 0.0052856 | 90.761 | 1115.1 | 1024.339
9070 | 1.8269 | 122.71 | 61.667 | 0.005287 | 90.771 | 1115.1 |  | 9070 | 122.71 | 1.8269 | 61.667 | 0.005287 | 90.771 | 1115.1 | 1024.329
9071 | 1.8274 | 122.72 | 61.667 | 0.0052883 | 90.781 | 1115.1 |  | 9071 | 122.72 | 1.8274 | 61.667 | 0.0052883 | 90.781 | 1115.1 | 1024.319
9072 | 1.8279 | 122.73 | 61.667 | 0.0052897 | 90.791 | 1115.1 |  | 9072 | 122.73 | 1.8279 | 61.667 | 0.0052897 | 90.791 | 1115.1 | 1024.309
9073 | 1.8284 | 122.74 | 61.667 | 0.0052911 | 90.801 | 1115.1 |  | 9073 | 122.74 | 1.8284 | 61.667 | 0.0052911 | 90.801 | 1115.1 | 1024.299
9074 | 1.8289 | 122.75 | 61.667 | 0.0052924 | 90.811 | 1115.1 |  | 9074 | 122.75 | 1.8289 | 61.667 | 0.0052924 | 90.811 | 1115.1 | 1024.289
9075 | 1.8294 | 122.76 | 61.667 | 0.0052938 | 90.821 | 1115.1 |  | 9075 | 122.76 | 1.8294 | 61.667 | 0.0052938 | 90.821 | 1115.1 | 1024.279
9076 | 1.8299 | 122.77 | 61.666 | 0.0052952 | 90.831 | 1115.1 |  | 9076 | 122.77 | 1.8299 | 61.666 | 0.0052952 | 90.831 | 1115.1 | 1024.269
9077 | 1.8304 | 122.78 | 61.666 | 0.0052965 | 90.841 | 1115.1 |  | 9077 | 122.78 | 1.8304 | 61.666 | 0.0052965 | 90.841 | 1115.1 | 1024.259
9078 | 1.8309 | 122.79 | 61.666 | 0.0052979 | 90.851 | 1115.1 |  | 9078 | 122.79 | 1.8309 | 61.666 | 0.0052979 | 90.851 | 1115.1 | 1024.249
9079 | 1.8314 | 122.8 | 61.666 | 0.0052993 | 90.861 | 1115.1 |  | 9079 | 122.8 | 1.8314 | 61.666 | 0.0052993 | 90.861 | 1115.1 | 1024.239
9080 | 1.8319 | 122.81 | 61.666 | 0.0053006 | 90.871 | 1115.1 |  | 9080 | 122.81 | 1.8319 | 61.666 | 0.0053006 | 90.871 | 1115.1 | 1024.229
9081 | 1.8324 | 122.82 | 61.666 | 0.005302 | 90.881 | 1115.1 |  | 9081 | 122.82 | 1.8324 | 61.666 | 0.005302 | 90.881 | 1115.1 | 1024.219
9082 | 1.8329 | 122.83 | 61.666 | 0.0053034 | 90.891 | 1115.1 |  | 9082 | 122.83 | 1.8329 | 61.666 | 0.0053034 | 90.891 | 1115.1 | 1024.209
9083 | 1.8334 | 122.84 | 61.665 | 0.0053047 | 90.901 | 1115.2 |  | 9083 | 122.84 | 1.8334 | 61.665 | 0.0053047 | 90.901 | 1115.2 | 1024.299
9084 | 1.8339 | 122.85 | 61.665 | 0.0053061 | 90.911 | 1115.2 |  | 9084 | 122.85 | 1.8339 | 61.665 | 0.0053061 | 90.911 | 1115.2 | 1024.289
9085 | 1.8344 | 122.86 | 61.665 | 0.0053075 | 90.921 | 1115.2 |  | 9085 | 122.86 | 1.8344 | 61.665 | 0.0053075 | 90.921 | 1115.2 | 1024.279
9086 | 1.8349 | 122.87 | 61.665 | 0.0053089 | 90.931 | 1115.2 |  | 9086 | 122.87 | 1.8349 | 61.665 | 0.0053089 | 90.931 | 1115.2 | 1024.269
9087 | 1.8354 | 122.88 | 61.665 | 0.0053102 | 90.941 | 1115.2 |  | 9087 | 122.88 | 1.8354 | 61.665 | 0.0053102 | 90.941 | 1115.2 | 1024.259
9088 | 1.8359 | 122.89 | 61.665 | 0.0053116 | 90.951 | 1115.2 |  | 9088 | 122.89 | 1.8359 | 61.665 | 0.0053116 | 90.951 | 1115.2 | 1024.249
9089 | 1.8364 | 122.9 | 61.664 | 0.005313 | 90.961 | 1115.2 |  | 9089 | 122.9 | 1.8364 | 61.664 | 0.005313 | 90.961 | 1115.2 | 1024.239
9090 | 1.8369 | 122.91 | 61.664 | 0.0053143 | 90.971 | 1115.2 |  | 9090 | 122.91 | 1.8369 | 61.664 | 0.0053143 | 90.971 | 1115.2 | 1024.229
9091 | 1.8374 | 122.92 | 61.664 | 0.0053157 | 90.981 | 1115.2 |  | 9091 | 122.92 | 1.8374 | 61.664 | 0.0053157 | 90.981 | 1115.2 | 1024.219
9092 | 1.8379 | 122.93 | 61.664 | 0.0053171 | 90.991 | 1115.2 |  | 9092 | 122.93 | 1.8379 | 61.664 | 0.0053171 | 90.991 | 1115.2 | 1024.209
9093 | 1.8384 | 122.94 | 61.664 | 0.0053185 | 91.001 | 1115.2 |  | 9093 | 122.94 | 1.8384 | 61.664 | 0.0053185 | 91.001 | 1115.2 | 1024.199
9094 | 1.8389 | 122.95 | 61.664 | 0.0053198 | 91.011 | 1115.2 |  | 9094 | 122.95 | 1.8389 | 61.664 | 0.0053198 | 91.011 | 1115.2 | 1024.189
9095 | 1.8395 | 122.96 | 61.663 | 0.0053212 | 91.021 | 1115.2 |  | 9095 | 122.96 | 1.8395 | 61.663 | 0.0053212 | 91.021 | 1115.2 | 1024.179
9096 | 1.84 | 122.97 | 61.663 | 0.0053226 | 91.031 | 1115.2 |  | 9096 | 122.97 | 1.84 | 61.663 | 0.0053226 | 91.031 | 1115.2 | 1024.169
9097 | 1.8405 | 122.98 | 61.663 | 0.005324 | 91.041 | 1115.2 |  | 9097 | 122.98 | 1.8405 | 61.663 | 0.005324 | 91.041 | 1115.2 | 1024.159
9098 | 1.841 | 122.99 | 61.663 | 0.0053253 | 91.051 | 1115.2 |  | 9098 | 122.99 | 1.841 | 61.663 | 0.0053253 | 91.051 | 1115.2 | 1024.149
9099 | 1.8415 | 123 | 61.663 | 0.0053267 | 91.061 | 1115.2 |  | 9099 | 123 | 1.8415 | 61.663 | 0.0053267 | 91.061 | 1115.2 | 1024.139
9100 | 1.842 | 123.01 | 61.663 | 0.0053281 | 91.071 | 1115.2 |  | 9100 | 123.01 | 1.842 | 61.663 | 0.0053281 | 91.071 | 1115.2 | 1024.129
9101 | 1.8425 | 123.02 | 61.663 | 0.0053295 | 91.081 | 1115.2 |  | 9101 | 123.02 | 1.8425 | 61.663 | 0.0053295 | 91.081 | 1115.2 | 1024.119
9102 | 1.843 | 123.03 | 61.662 | 0.0053308 | 91.091 | 1115.2 |  | 9102 | 123.03 | 1.843 | 61.662 | 0.0053308 | 91.091 | 1115.2 | 1024.109
9103 | 1.8435 | 123.04 | 61.662 | 0.0053322 | 91.101 | 1115.2 |  | 9103 | 123.04 | 1.8435 | 61.662 | 0.0053322 | 91.101 | 1115.2 | 1024.099
9104 | 1.844 | 123.05 | 61.662 | 0.0053336 | 91.111 | 1115.2 |  | 9104 | 123.05 | 1.844 | 61.662 | 0.0053336 | 91.111 | 1115.2 | 1024.089
9105 | 1.8445 | 123.06 | 61.662 | 0.005335 | 91.121 | 1115.2 |  | 9105 | 123.06 | 1.8445 | 61.662 | 0.005335 | 91.121 | 1115.2 | 1024.079
9106 | 1.845 | 123.07 | 61.662 | 0.0053363 | 91.131 | 1115.3 |  | 9106 | 123.07 | 1.845 | 61.662 | 0.0053363 | 91.131 | 1115.3 | 1024.169
9107 | 1.8455 | 123.08 | 61.662 | 0.0053377 | 91.141 | 1115.3 |  | 9107 | 123.08 | 1.8455 | 61.662 | 0.0053377 | 91.141 | 1115.3 | 1024.159
9108 | 1.846 | 123.09 | 61.661 | 0.0053391 | 91.151 | 1115.3 |  | 9108 | 123.09 | 1.846 | 61.661 | 0.0053391 | 91.151 | 1115.3 | 1024.149
9109 | 1.8465 | 123.1 | 61.661 | 0.0053405 | 91.161 | 1115.3 |  | 9109 | 123.1 | 1.8465 | 61.661 | 0.0053405 | 91.161 | 1115.3 | 1024.139
9110 | 1.847 | 123.11 | 61.661 | 0.0053418 | 91.171 | 1115.3 |  | 9110 | 123.11 | 1.847 | 61.661 | 0.0053418 | 91.171 | 1115.3 | 1024.129
9111 | 1.8476 | 123.12 | 61.661 | 0.0053432 | 91.18 | 1115.3 |  | 9111 | 123.12 | 1.8476 | 61.661 | 0.0053432 | 91.18 | 1115.3 | 1024.12
9112 | 1.8481 | 123.13 | 61.661 | 0.0053446 | 91.19 | 1115.3 |  | 9112 | 123.13 | 1.8481 | 61.661 | 0.0053446 | 91.19 | 1115.3 | 1024.11
9113 | 1.8486 | 123.14 | 61.661 | 0.005346 | 91.2 | 1115.3 |  | 9113 | 123.14 | 1.8486 | 61.661 | 0.005346 | 91.2 | 1115.3 | 1024.1
9114 | 1.8491 | 123.15 | 61.66 | 0.0053474 | 91.21 | 1115.3 |  | 9114 | 123.15 | 1.8491 | 61.66 | 0.0053474 | 91.21 | 1115.3 | 1024.09
9115 | 1.8496 | 123.16 | 61.66 | 0.0053487 | 91.22 | 1115.3 |  | 9115 | 123.16 | 1.8496 | 61.66 | 0.0053487 | 91.22 | 1115.3 | 1024.08
9116 | 1.8501 | 123.17 | 61.66 | 0.0053501 | 91.23 | 1115.3 |  | 9116 | 123.17 | 1.8501 | 61.66 | 0.0053501 | 91.23 | 1115.3 | 1024.07
9117 | 1.8506 | 123.18 | 61.66 | 0.0053515 | 91.24 | 1115.3 |  | 9117 | 123.18 | 1.8506 | 61.66 | 0.0053515 | 91.24 | 1115.3 | 1024.06
9118 | 1.8511 | 123.19 | 61.66 | 0.0053529 | 91.25 | 1115.3 |  | 9118 | 123.19 | 1.8511 | 61.66 | 0.0053529 | 91.25 | 1115.3 | 1024.05
9119 | 1.8516 | 123.2 | 61.66 | 0.0053543 | 91.26 | 1115.3 |  | 9119 | 123.2 | 1.8516 | 61.66 | 0.0053543 | 91.26 | 1115.3 | 1024.04
9120 | 1.8521 | 123.21 | 61.66 | 0.0053556 | 91.27 | 1115.3 |  | 9120 | 123.21 | 1.8521 | 61.66 | 0.0053556 | 91.27 | 1115.3 | 1024.03
9121 | 1.8526 | 123.22 | 61.659 | 0.005357 | 91.28 | 1115.3 |  | 9121 | 123.22 | 1.8526 | 61.659 | 0.005357 | 91.28 | 1115.3 | 1024.02
9122 | 1.8531 | 123.23 | 61.659 | 0.0053584 | 91.29 | 1115.3 |  | 9122 | 123.23 | 1.8531 | 61.659 | 0.0053584 | 91.29 | 1115.3 | 1024.01
9123 | 1.8536 | 123.24 | 61.659 | 0.0053598 | 91.3 | 1115.3 |  | 9123 | 123.24 | 1.8536 | 61.659 | 0.0053598 | 91.3 | 1115.3 | 1024
9124 | 1.8542 | 123.25 | 61.659 | 0.0053612 | 91.31 | 1115.3 |  | 9124 | 123.25 | 1.8542 | 61.659 | 0.0053612 | 91.31 | 1115.3 | 1023.99
9125 | 1.8547 | 123.26 | 61.659 | 0.0053626 | 91.32 | 1115.3 |  | 9125 | 123.26 | 1.8547 | 61.659 | 0.0053626 | 91.32 | 1115.3 | 1023.98
9126 | 1.8552 | 123.27 | 61.659 | 0.0053639 | 91.33 | 1115.3 |  | 9126 | 123.27 | 1.8552 | 61.659 | 0.0053639 | 91.33 | 1115.3 | 1023.97
9127 | 1.8557 | 123.28 | 61.658 | 0.0053653 | 91.34 | 1115.3 |  | 9127 | 123.28 | 1.8557 | 61.658 | 0.0053653 | 91.34 | 1115.3 | 1023.96
9128 | 1.8562 | 123.29 | 61.658 | 0.0053667 | 91.35 | 1115.3 |  | 9128 | 123.29 | 1.8562 | 61.658 | 0.0053667 | 91.35 | 1115.3 | 1023.95
9129 | 1.8567 | 123.3 | 61.658 | 0.0053681 | 91.36 | 1115.3 |  | 9129 | 123.3 | 1.8567 | 61.658 | 0.0053681 | 91.36 | 1115.3 | 1023.94
9130 | 1.8572 | 123.31 | 61.658 | 0.0053695 | 91.37 | 1115.4 |  | 9130 | 123.31 | 1.8572 | 61.658 | 0.0053695 | 91.37 | 1115.4 | 1024.03
9131 | 1.8577 | 123.32 | 61.658 | 0.0053709 | 91.38 | 1115.4 |  | 9131 | 123.32 | 1.8577 | 61.658 | 0.0053709 | 91.38 | 1115.4 | 1024.02
9132 | 1.8582 | 123.33 | 61.658 | 0.0053722 | 91.39 | 1115.4 |  | 9132 | 123.33 | 1.8582 | 61.658 | 0.0053722 | 91.39 | 1115.4 | 1024.01
9133 | 1.8587 | 123.34 | 61.657 | 0.0053736 | 91.4 | 1115.4 |  | 9133 | 123.34 | 1.8587 | 61.657 | 0.0053736 | 91.4 | 1115.4 | 1024
9134 | 1.8592 | 123.35 | 61.657 | 0.005375 | 91.41 | 1115.4 |  | 9134 | 123.35 | 1.8592 | 61.657 | 0.005375 | 91.41 | 1115.4 | 1023.99
9135 | 1.8598 | 123.36 | 61.657 | 0.0053764 | 91.42 | 1115.4 |  | 9135 | 123.36 | 1.8598 | 61.657 | 0.0053764 | 91.42 | 1115.4 | 1023.98
9136 | 1.8603 | 123.37 | 61.657 | 0.0053778 | 91.43 | 1115.4 |  | 9136 | 123.37 | 1.8603 | 61.657 | 0.0053778 | 91.43 | 1115.4 | 1023.97
9137 | 1.8608 | 123.38 | 61.657 | 0.0053792 | 91.44 | 1115.4 |  | 9137 | 123.38 | 1.8608 | 61.657 | 0.0053792 | 91.44 | 1115.4 | 1023.96
9138 | 1.8613 | 123.39 | 61.657 | 0.0053806 | 91.45 | 1115.4 |  | 9138 | 123.39 | 1.8613 | 61.657 | 0.0053806 | 91.45 | 1115.4 | 1023.95
9139 | 1.8618 | 123.4 | 61.657 | 0.0053819 | 91.46 | 1115.4 |  | 9139 | 123.4 | 1.8618 | 61.657 | 0.0053819 | 91.46 | 1115.4 | 1023.94
9140 | 1.8623 | 123.41 | 61.656 | 0.0053833 | 91.47 | 1115.4 |  | 9140 | 123.41 | 1.8623 | 61.656 | 0.0053833 | 91.47 | 1115.4 | 1023.93
9141 | 1.8628 | 123.42 | 61.656 | 0.0053847 | 91.48 | 1115.4 |  | 9141 | 123.42 | 1.8628 | 61.656 | 0.0053847 | 91.48 | 1115.4 | 1023.92
9142 | 1.8633 | 123.43 | 61.656 | 0.0053861 | 91.49 | 1115.4 |  | 9142 | 123.43 | 1.8633 | 61.656 | 0.0053861 | 91.49 | 1115.4 | 1023.91
9143 | 1.8638 | 123.44 | 61.656 | 0.0053875 | 91.5 | 1115.4 |  | 9143 | 123.44 | 1.8638 | 61.656 | 0.0053875 | 91.5 | 1115.4 | 1023.9
9144 | 1.8643 | 123.45 | 61.656 | 0.0053889 | 91.51 | 1115.4 |  | 9144 | 123.45 | 1.8643 | 61.656 | 0.0053889 | 91.51 | 1115.4 | 1023.89
9145 | 1.8649 | 123.46 | 61.656 | 0.0053903 | 91.52 | 1115.4 |  | 9145 | 123.46 | 1.8649 | 61.656 | 0.0053903 | 91.52 | 1115.4 | 1023.88
9146 | 1.8654 | 123.47 | 61.655 | 0.0053917 | 91.53 | 1115.4 |  | 9146 | 123.47 | 1.8654 | 61.655 | 0.0053917 | 91.53 | 1115.4 | 1023.87
9147 | 1.8659 | 123.48 | 61.655 | 0.0053931 | 91.54 | 1115.4 |  | 9147 | 123.48 | 1.8659 | 61.655 | 0.0053931 | 91.54 | 1115.4 | 1023.86
9148 | 1.8664 | 123.49 | 61.655 | 0.0053944 | 91.55 | 1115.4 |  | 9148 | 123.49 | 1.8664 | 61.655 | 0.0053944 | 91.55 | 1115.4 | 1023.85
9149 | 1.8669 | 123.5 | 61.655 | 0.0053958 | 91.56 | 1115.4 |  | 9149 | 123.5 | 1.8669 | 61.655 | 0.0053958 | 91.56 | 1115.4 | 1023.84
9150 | 1.8674 | 123.51 | 61.655 | 0.0053972 | 91.57 | 1115.4 |  | 9150 | 123.51 | 1.8674 | 61.655 | 0.0053972 | 91.57 | 1115.4 | 1023.83
9151 | 1.8679 | 123.52 | 61.655 | 0.0053986 | 91.58 | 1115.4 |  | 9151 | 123.52 | 1.8679 | 61.655 | 0.0053986 | 91.58 | 1115.4 | 1023.82
9152 | 1.8684 | 123.53 | 61.654 | 0.0054 | 91.59 | 1115.4 |  | 9152 | 123.53 | 1.8684 | 61.654 | 0.0054 | 91.59 | 1115.4 | 1023.81
9153 | 1.869 | 123.54 | 61.654 | 0.0054014 | 91.6 | 1115.4 |  | 9153 | 123.54 | 1.869 | 61.654 | 0.0054014 | 91.6 | 1115.4 | 1023.8
9154 | 1.8695 | 123.55 | 61.654 | 0.0054028 | 91.61 | 1115.5 |  | 9154 | 123.55 | 1.8695 | 61.654 | 0.0054028 | 91.61 | 1115.5 | 1023.89
9155 | 1.87 | 123.56 | 61.654 | 0.0054042 | 91.62 | 1115.5 |  | 9155 | 123.56 | 1.87 | 61.654 | 0.0054042 | 91.62 | 1115.5 | 1023.88
9156 | 1.8705 | 123.57 | 61.654 | 0.0054056 | 91.63 | 1115.5 |  | 9156 | 123.57 | 1.8705 | 61.654 | 0.0054056 | 91.63 | 1115.5 | 1023.87
9157 | 1.871 | 123.58 | 61.654 | 0.005407 | 91.64 | 1115.5 |  | 9157 | 123.58 | 1.871 | 61.654 | 0.005407 | 91.64 | 1115.5 | 1023.86
9158 | 1.8715 | 123.59 | 61.654 | 0.0054084 | 91.65 | 1115.5 |  | 9158 | 123.59 | 1.8715 | 61.654 | 0.0054084 | 91.65 | 1115.5 | 1023.85
9159 | 1.872 | 123.6 | 61.653 | 0.0054097 | 91.66 | 1115.5 |  | 9159 | 123.6 | 1.872 | 61.653 | 0.0054097 | 91.66 | 1115.5 | 1023.84
9160 | 1.8725 | 123.61 | 61.653 | 0.0054111 | 91.67 | 1115.5 |  | 9160 | 123.61 | 1.8725 | 61.653 | 0.0054111 | 91.67 | 1115.5 | 1023.83
9161 | 1.8731 | 123.62 | 61.653 | 0.0054125 | 91.68 | 1115.5 |  | 9161 | 123.62 | 1.8731 | 61.653 | 0.0054125 | 91.68 | 1115.5 | 1023.82
9162 | 1.8736 | 123.63 | 61.653 | 0.0054139 | 91.69 | 1115.5 |  | 9162 | 123.63 | 1.8736 | 61.653 | 0.0054139 | 91.69 | 1115.5 | 1023.81
9163 | 1.8741 | 123.64 | 61.653 | 0.0054153 | 91.7 | 1115.5 |  | 9163 | 123.64 | 1.8741 | 61.653 | 0.0054153 | 91.7 | 1115.5 | 1023.8
9164 | 1.8746 | 123.65 | 61.653 | 0.0054167 | 91.71 | 1115.5 |  | 9164 | 123.65 | 1.8746 | 61.653 | 0.0054167 | 91.71 | 1115.5 | 1023.79
9165 | 1.8751 | 123.66 | 61.652 | 0.0054181 | 91.72 | 1115.5 |  | 9165 | 123.66 | 1.8751 | 61.652 | 0.0054181 | 91.72 | 1115.5 | 1023.78
9166 | 1.8756 | 123.67 | 61.652 | 0.0054195 | 91.73 | 1115.5 |  | 9166 | 123.67 | 1.8756 | 61.652 | 0.0054195 | 91.73 | 1115.5 | 1023.77
9167 | 1.8761 | 123.68 | 61.652 | 0.0054209 | 91.74 | 1115.5 |  | 9167 | 123.68 | 1.8761 | 61.652 | 0.0054209 | 91.74 | 1115.5 | 1023.76
9168 | 1.8766 | 123.69 | 61.652 | 0.0054223 | 91.75 | 1115.5 |  | 9168 | 123.69 | 1.8766 | 61.652 | 0.0054223 | 91.75 | 1115.5 | 1023.75
9169 | 1.8772 | 123.7 | 61.652 | 0.0054237 | 91.76 | 1115.5 |  | 9169 | 123.7 | 1.8772 | 61.652 | 0.0054237 | 91.76 | 1115.5 | 1023.74
9170 | 1.8777 | 123.71 | 61.652 | 0.0054251 | 91.77 | 1115.5 |  | 9170 | 123.71 | 1.8777 | 61.652 | 0.0054251 | 91.77 | 1115.5 | 1023.73
9171 | 1.8782 | 123.72 | 61.651 | 0.0054265 | 91.78 | 1115.5 |  | 9171 | 123.72 | 1.8782 | 61.651 | 0.0054265 | 91.78 | 1115.5 | 1023.72
9172 | 1.8787 | 123.73 | 61.651 | 0.0054279 | 91.79 | 1115.5 |  | 9172 | 123.73 | 1.8787 | 61.651 | 0.0054279 | 91.79 | 1115.5 | 1023.71
9173 | 1.8792 | 123.74 | 61.651 | 0.0054293 | 91.8 | 1115.5 |  | 9173 | 123.74 | 1.8792 | 61.651 | 0.0054293 | 91.8 | 1115.5 | 1023.7
9174 | 1.8797 | 123.75 | 61.651 | 0.0054307 | 91.81 | 1115.5 |  | 9174 | 123.75 | 1.8797 | 61.651 | 0.0054307 | 91.81 | 1115.5 | 1023.69
9175 | 1.8802 | 123.76 | 61.651 | 0.0054321 | 91.82 | 1115.5 |  | 9175 | 123.76 | 1.8802 | 61.651 | 0.0054321 | 91.82 | 1115.5 | 1023.68
9176 | 1.8808 | 123.77 | 61.651 | 0.0054335 | 91.83 | 1115.5 |  | 9176 | 123.77 | 1.8808 | 61.651 | 0.0054335 | 91.83 | 1115.5 | 1023.67
9177 | 1.8813 | 123.78 | 61.65 | 0.0054349 | 91.84 | 1115.6 |  | 9177 | 123.78 | 1.8813 | 61.65 | 0.0054349 | 91.84 | 1115.6 | 1023.76
9178 | 1.8818 | 123.79 | 61.65 | 0.0054363 | 91.85 | 1115.6 |  | 9178 | 123.79 | 1.8818 | 61.65 | 0.0054363 | 91.85 | 1115.6 | 1023.75
9179 | 1.8823 | 123.8 | 61.65 | 0.0054377 | 91.86 | 1115.6 |  | 9179 | 123.8 | 1.8823 | 61.65 | 0.0054377 | 91.86 | 1115.6 | 1023.74
9180 | 1.8828 | 123.81 | 61.65 | 0.0054391 | 91.87 | 1115.6 |  | 9180 | 123.81 | 1.8828 | 61.65 | 0.0054391 | 91.87 | 1115.6 | 1023.73
9181 | 1.8833 | 123.82 | 61.65 | 0.0054405 | 91.88 | 1115.6 |  | 9181 | 123.82 | 1.8833 | 61.65 | 0.0054405 | 91.88 | 1115.6 | 1023.72
9182 | 1.8839 | 123.83 | 61.65 | 0.0054419 | 91.89 | 1115.6 |  | 9182 | 123.83 | 1.8839 | 61.65 | 0.0054419 | 91.89 | 1115.6 | 1023.71
9183 | 1.8844 | 123.84 | 61.65 | 0.0054433 | 91.9 | 1115.6 |  | 9183 | 123.84 | 1.8844 | 61.65 | 0.0054433 | 91.9 | 1115.6 | 1023.7
9184 | 1.8849 | 123.85 | 61.649 | 0.0054447 | 91.91 | 1115.6 |  | 9184 | 123.85 | 1.8849 | 61.649 | 0.0054447 | 91.91 | 1115.6 | 1023.69
9185 | 1.8854 | 123.86 | 61.649 | 0.0054461 | 91.92 | 1115.6 |  | 9185 | 123.86 | 1.8854 | 61.649 | 0.0054461 | 91.92 | 1115.6 | 1023.68
9186 | 1.8859 | 123.87 | 61.649 | 0.0054475 | 91.93 | 1115.6 |  | 9186 | 123.87 | 1.8859 | 61.649 | 0.0054475 | 91.93 | 1115.6 | 1023.67
9187 | 1.8864 | 123.88 | 61.649 | 0.0054489 | 91.94 | 1115.6 |  | 9187 | 123.88 | 1.8864 | 61.649 | 0.0054489 | 91.94 | 1115.6 | 1023.66
9188 | 1.887 | 123.89 | 61.649 | 0.0054503 | 91.95 | 1115.6 |  | 9188 | 123.89 | 1.887 | 61.649 | 0.0054503 | 91.95 | 1115.6 | 1023.65
9189 | 1.8875 | 123.9 | 61.649 | 0.0054517 | 91.96 | 1115.6 |  | 9189 | 123.9 | 1.8875 | 61.649 | 0.0054517 | 91.96 | 1115.6 | 1023.64
9190 | 1.888 | 123.91 | 61.648 | 0.0054531 | 91.97 | 1115.6 |  | 9190 | 123.91 | 1.888 | 61.648 | 0.0054531 | 91.97 | 1115.6 | 1023.63
9191 | 1.8885 | 123.92 | 61.648 | 0.0054545 | 91.98 | 1115.6 |  | 9191 | 123.92 | 1.8885 | 61.648 | 0.0054545 | 91.98 | 1115.6 | 1023.62
9192 | 1.889 | 123.93 | 61.648 | 0.0054559 | 91.99 | 1115.6 |  | 9192 | 123.93 | 1.889 | 61.648 | 0.0054559 | 91.99 | 1115.6 | 1023.61
9193 | 1.8895 | 123.94 | 61.648 | 0.0054573 | 92 | 1115.6 |  | 9193 | 123.94 | 1.8895 | 61.648 | 0.0054573 | 92 | 1115.6 | 1023.6
9194 | 1.8901 | 123.95 | 61.648 | 0.0054587 | 92.01 | 1115.6 |  | 9194 | 123.95 | 1.8901 | 61.648 | 0.0054587 | 92.01 | 1115.6 | 1023.59
9195 | 1.8906 | 123.96 | 61.648 | 0.0054601 | 92.02 | 1115.6 |  | 9195 | 123.96 | 1.8906 | 61.648 | 0.0054601 | 92.02 | 1115.6 | 1023.58
9196 | 1.8911 | 123.97 | 61.647 | 0.0054615 | 92.03 | 1115.6 |  | 9196 | 123.97 | 1.8911 | 61.647 | 0.0054615 | 92.03 | 1115.6 | 1023.57
9197 | 1.8916 | 123.98 | 61.647 | 0.0054629 | 92.04 | 1115.6 |  | 9197 | 123.98 | 1.8916 | 61.647 | 0.0054629 | 92.04 | 1115.6 | 1023.56
9198 | 1.8921 | 123.99 | 61.647 | 0.0054643 | 92.05 | 1115.6 |  | 9198 | 123.99 | 1.8921 | 61.647 | 0.0054643 | 92.05 | 1115.6 | 1023.55
9199 | 1.8926 | 124 | 61.647 | 0.0054657 | 92.06 | 1115.6 |  | 9199 | 124 | 1.8926 | 61.647 | 0.0054657 | 92.06 | 1115.6 | 1023.54
9200 | 1.8932 | 124.01 | 61.647 | 0.0054671 | 92.07 | 1115.6 |  | 9200 | 124.01 | 1.8932 | 61.647 | 0.0054671 | 92.07 | 1115.6 | 1023.53
9201 | 1.8937 | 124.02 | 61.647 | 0.0054685 | 92.08 | 1115.7 |  | 9201 | 124.02 | 1.8937 | 61.647 | 0.0054685 | 92.08 | 1115.7 | 1023.62
9202 | 1.8942 | 124.03 | 61.647 | 0.0054699 | 92.09 | 1115.7 |  | 9202 | 124.03 | 1.8942 | 61.647 | 0.0054699 | 92.09 | 1115.7 | 1023.61
9203 | 1.8947 | 124.04 | 61.646 | 0.0054713 | 92.1 | 1115.7 |  | 9203 | 124.04 | 1.8947 | 61.646 | 0.0054713 | 92.1 | 1115.7 | 1023.6
9204 | 1.8952 | 124.05 | 61.646 | 0.0054727 | 92.11 | 1115.7 |  | 9204 | 124.05 | 1.8952 | 61.646 | 0.0054727 | 92.11 | 1115.7 | 1023.59
9205 | 1.8957 | 124.06 | 61.646 | 0.0054742 | 92.12 | 1115.7 |  | 9205 | 124.06 | 1.8957 | 61.646 | 0.0054742 | 92.12 | 1115.7 | 1023.58
9206 | 1.8963 | 124.07 | 61.646 | 0.0054756 | 92.13 | 1115.7 |  | 9206 | 124.07 | 1.8963 | 61.646 | 0.0054756 | 92.13 | 1115.7 | 1023.57
9207 | 1.8968 | 124.08 | 61.646 | 0.005477 | 92.14 | 1115.7 |  | 9207 | 124.08 | 1.8968 | 61.646 | 0.005477 | 92.14 | 1115.7 | 1023.56
9208 | 1.8973 | 124.09 | 61.646 | 0.0054784 | 92.15 | 1115.7 |  | 9208 | 124.09 | 1.8973 | 61.646 | 0.0054784 | 92.15 | 1115.7 | 1023.55
9209 | 1.8978 | 124.1 | 61.645 | 0.0054798 | 92.16 | 1115.7 |  | 9209 | 124.1 | 1.8978 | 61.645 | 0.0054798 | 92.16 | 1115.7 | 1023.54
9210 | 1.8983 | 124.11 | 61.645 | 0.0054812 | 92.17 | 1115.7 |  | 9210 | 124.11 | 1.8983 | 61.645 | 0.0054812 | 92.17 | 1115.7 | 1023.53
9211 | 1.8989 | 124.12 | 61.645 | 0.0054826 | 92.18 | 1115.7 |  | 9211 | 124.12 | 1.8989 | 61.645 | 0.0054826 | 92.18 | 1115.7 | 1023.52
9212 | 1.8994 | 124.13 | 61.645 | 0.005484 | 92.19 | 1115.7 |  | 9212 | 124.13 | 1.8994 | 61.645 | 0.005484 | 92.19 | 1115.7 | 1023.51
9213 | 1.8999 | 124.14 | 61.645 | 0.0054854 | 92.2 | 1115.7 |  | 9213 | 124.14 | 1.8999 | 61.645 | 0.0054854 | 92.2 | 1115.7 | 1023.5
9214 | 1.9004 | 124.15 | 61.645 | 0.0054868 | 92.21 | 1115.7 |  | 9214 | 124.15 | 1.9004 | 61.645 | 0.0054868 | 92.21 | 1115.7 | 1023.49
9215 | 1.9009 | 124.16 | 61.644 | 0.0054882 | 92.22 | 1115.7 |  | 9215 | 124.16 | 1.9009 | 61.644 | 0.0054882 | 92.22 | 1115.7 | 1023.48
9216 | 1.9015 | 124.17 | 61.644 | 0.0054897 | 92.23 | 1115.7 |  | 9216 | 124.17 | 1.9015 | 61.644 | 0.0054897 | 92.23 | 1115.7 | 1023.47
9217 | 1.902 | 124.18 | 61.644 | 0.0054911 | 92.24 | 1115.7 |  | 9217 | 124.18 | 1.902 | 61.644 | 0.0054911 | 92.24 | 1115.7 | 1023.46
9218 | 1.9025 | 124.19 | 61.644 | 0.0054925 | 92.25 | 1115.7 |  | 9218 | 124.19 | 1.9025 | 61.644 | 0.0054925 | 92.25 | 1115.7 | 1023.45
9219 | 1.903 | 124.2 | 61.644 | 0.0054939 | 92.26 | 1115.7 |  | 9219 | 124.2 | 1.903 | 61.644 | 0.0054939 | 92.26 | 1115.7 | 1023.44
9220 | 1.9035 | 124.21 | 61.644 | 0.0054953 | 92.27 | 1115.7 |  | 9220 | 124.21 | 1.9035 | 61.644 | 0.0054953 | 92.27 | 1115.7 | 1023.43
9221 | 1.9041 | 124.22 | 61.643 | 0.0054967 | 92.28 | 1115.7 |  | 9221 | 124.22 | 1.9041 | 61.643 | 0.0054967 | 92.28 | 1115.7 | 1023.42
9222 | 1.9046 | 124.23 | 61.643 | 0.0054981 | 92.29 | 1115.7 |  | 9222 | 124.23 | 1.9046 | 61.643 | 0.0054981 | 92.29 | 1115.7 | 1023.41
9223 | 1.9051 | 124.24 | 61.643 | 0.0054995 | 92.3 | 1115.7 |  | 9223 | 124.24 | 1.9051 | 61.643 | 0.0054995 | 92.3 | 1115.7 | 1023.4
9224 | 1.9056 | 124.25 | 61.643 | 0.0055009 | 92.31 | 1115.7 |  | 9224 | 124.25 | 1.9056 | 61.643 | 0.0055009 | 92.31 | 1115.7 | 1023.39
9225 | 1.9061 | 124.26 | 61.643 | 0.0055024 | 92.32 | 1115.8 |  | 9225 | 124.26 | 1.9061 | 61.643 | 0.0055024 | 92.32 | 1115.8 | 1023.48
9226 | 1.9067 | 124.27 | 61.643 | 0.0055038 | 92.33 | 1115.8 |  | 9226 | 124.27 | 1.9067 | 61.643 | 0.0055038 | 92.33 | 1115.8 | 1023.47
9227 | 1.9072 | 124.28 | 61.643 | 0.0055052 | 92.34 | 1115.8 |  | 9227 | 124.28 | 1.9072 | 61.643 | 0.0055052 | 92.34 | 1115.8 | 1023.46
9228 | 1.9077 | 124.29 | 61.642 | 0.0055066 | 92.35 | 1115.8 |  | 9228 | 124.29 | 1.9077 | 61.642 | 0.0055066 | 92.35 | 1115.8 | 1023.45
9229 | 1.9082 | 124.3 | 61.642 | 0.005508 | 92.36 | 1115.8 |  | 9229 | 124.3 | 1.9082 | 61.642 | 0.005508 | 92.36 | 1115.8 | 1023.44
9230 | 1.9087 | 124.31 | 61.642 | 0.0055094 | 92.37 | 1115.8 |  | 9230 | 124.31 | 1.9087 | 61.642 | 0.0055094 | 92.37 | 1115.8 | 1023.43
9231 | 1.9093 | 124.32 | 61.642 | 0.0055108 | 92.38 | 1115.8 |  | 9231 | 124.32 | 1.9093 | 61.642 | 0.0055108 | 92.38 | 1115.8 | 1023.42
9232 | 1.9098 | 124.33 | 61.642 | 0.0055123 | 92.39 | 1115.8 |  | 9232 | 124.33 | 1.9098 | 61.642 | 0.0055123 | 92.39 | 1115.8 | 1023.41
9233 | 1.9103 | 124.34 | 61.642 | 0.0055137 | 92.4 | 1115.8 |  | 9233 | 124.34 | 1.9103 | 61.642 | 0.0055137 | 92.4 | 1115.8 | 1023.4
9234 | 1.9108 | 124.35 | 61.641 | 0.0055151 | 92.41 | 1115.8 |  | 9234 | 124.35 | 1.9108 | 61.641 | 0.0055151 | 92.41 | 1115.8 | 1023.39
9235 | 1.9114 | 124.36 | 61.641 | 0.0055165 | 92.42 | 1115.8 |  | 9235 | 124.36 | 1.9114 | 61.641 | 0.0055165 | 92.42 | 1115.8 | 1023.38
9236 | 1.9119 | 124.37 | 61.641 | 0.0055179 | 92.43 | 1115.8 |  | 9236 | 124.37 | 1.9119 | 61.641 | 0.0055179 | 92.43 | 1115.8 | 1023.37
9237 | 1.9124 | 124.38 | 61.641 | 0.0055193 | 92.44 | 1115.8 |  | 9237 | 124.38 | 1.9124 | 61.641 | 0.0055193 | 92.44 | 1115.8 | 1023.36
9238 | 1.9129 | 124.39 | 61.641 | 0.0055208 | 92.45 | 1115.8 |  | 9238 | 124.39 | 1.9129 | 61.641 | 0.0055208 | 92.45 | 1115.8 | 1023.35
9239 | 1.9134 | 124.4 | 61.641 | 0.0055222 | 92.46 | 1115.8 |  | 9239 | 124.4 | 1.9134 | 61.641 | 0.0055222 | 92.46 | 1115.8 | 1023.34
9240 | 1.914 | 124.41 | 61.64 | 0.0055236 | 92.47 | 1115.8 |  | 9240 | 124.41 | 1.914 | 61.64 | 0.0055236 | 92.47 | 1115.8 | 1023.33
9241 | 1.9145 | 124.42 | 61.64 | 0.005525 | 92.48 | 1115.8 |  | 9241 | 124.42 | 1.9145 | 61.64 | 0.005525 | 92.48 | 1115.8 | 1023.32
9242 | 1.915 | 124.43 | 61.64 | 0.0055264 | 92.49 | 1115.8 |  | 9242 | 124.43 | 1.915 | 61.64 | 0.0055264 | 92.49 | 1115.8 | 1023.31
9243 | 1.9155 | 124.44 | 61.64 | 0.0055278 | 92.5 | 1115.8 |  | 9243 | 124.44 | 1.9155 | 61.64 | 0.0055278 | 92.5 | 1115.8 | 1023.3
9244 | 1.9161 | 124.45 | 61.64 | 0.0055293 | 92.51 | 1115.8 |  | 9244 | 124.45 | 1.9161 | 61.64 | 0.0055293 | 92.51 | 1115.8 | 1023.29
9245 | 1.9166 | 124.46 | 61.64 | 0.0055307 | 92.52 | 1115.8 |  | 9245 | 124.46 | 1.9166 | 61.64 | 0.0055307 | 92.52 | 1115.8 | 1023.28
9246 | 1.9171 | 124.47 | 61.639 | 0.0055321 | 92.53 | 1115.8 |  | 9246 | 124.47 | 1.9171 | 61.639 | 0.0055321 | 92.53 | 1115.8 | 1023.27
9247 | 1.9176 | 124.48 | 61.639 | 0.0055335 | 92.54 | 1115.8 |  | 9247 | 124.48 | 1.9176 | 61.639 | 0.0055335 | 92.54 | 1115.8 | 1023.26
9248 | 1.9182 | 124.49 | 61.639 | 0.0055349 | 92.55 | 1115.8 |  | 9248 | 124.49 | 1.9182 | 61.639 | 0.0055349 | 92.55 | 1115.8 | 1023.25
9249 | 1.9187 | 124.5 | 61.639 | 0.0055364 | 92.56 | 1115.9 |  | 9249 | 124.5 | 1.9187 | 61.639 | 0.0055364 | 92.56 | 1115.9 | 1023.34
9250 | 1.9192 | 124.51 | 61.639 | 0.0055378 | 92.57 | 1115.9 |  | 9250 | 124.51 | 1.9192 | 61.639 | 0.0055378 | 92.57 | 1115.9 | 1023.33
9251 | 1.9197 | 124.52 | 61.639 | 0.0055392 | 92.58 | 1115.9 |  | 9251 | 124.52 | 1.9197 | 61.639 | 0.0055392 | 92.58 | 1115.9 | 1023.32
9252 | 1.9202 | 124.53 | 61.639 | 0.0055406 | 92.59 | 1115.9 |  | 9252 | 124.53 | 1.9202 | 61.639 | 0.0055406 | 92.59 | 1115.9 | 1023.31
9253 | 1.9208 | 124.54 | 61.638 | 0.005542 | 92.6 | 1115.9 |  | 9253 | 124.54 | 1.9208 | 61.638 | 0.005542 | 92.6 | 1115.9 | 1023.3
9254 | 1.9213 | 124.55 | 61.638 | 0.0055435 | 92.61 | 1115.9 |  | 9254 | 124.55 | 1.9213 | 61.638 | 0.0055435 | 92.61 | 1115.9 | 1023.29
9255 | 1.9218 | 124.56 | 61.638 | 0.0055449 | 92.62 | 1115.9 |  | 9255 | 124.56 | 1.9218 | 61.638 | 0.0055449 | 92.62 | 1115.9 | 1023.28
9256 | 1.9223 | 124.57 | 61.638 | 0.0055463 | 92.63 | 1115.9 |  | 9256 | 124.57 | 1.9223 | 61.638 | 0.0055463 | 92.63 | 1115.9 | 1023.27
9257 | 1.9229 | 124.58 | 61.638 | 0.0055477 | 92.64 | 1115.9 |  | 9257 | 124.58 | 1.9229 | 61.638 | 0.0055477 | 92.64 | 1115.9 | 1023.26
9258 | 1.9234 | 124.59 | 61.638 | 0.0055492 | 92.65 | 1115.9 |  | 9258 | 124.59 | 1.9234 | 61.638 | 0.0055492 | 92.65 | 1115.9 | 1023.25
9259 | 1.9239 | 124.6 | 61.637 | 0.0055506 | 92.66 | 1115.9 |  | 9259 | 124.6 | 1.9239 | 61.637 | 0.0055506 | 92.66 | 1115.9 | 1023.24
9260 | 1.9244 | 124.61 | 61.637 | 0.005552 | 92.67 | 1115.9 |  | 9260 | 124.61 | 1.9244 | 61.637 | 0.005552 | 92.67 | 1115.9 | 1023.23
9261 | 1.925 | 124.62 | 61.637 | 0.0055534 | 92.68 | 1115.9 |  | 9261 | 124.62 | 1.925 | 61.637 | 0.0055534 | 92.68 | 1115.9 | 1023.22
9262 | 1.9255 | 124.63 | 61.637 | 0.0055549 | 92.69 | 1115.9 |  | 9262 | 124.63 | 1.9255 | 61.637 | 0.0055549 | 92.69 | 1115.9 | 1023.21
9263 | 1.926 | 124.64 | 61.637 | 0.0055563 | 92.7 | 1115.9 |  | 9263 | 124.64 | 1.926 | 61.637 | 0.0055563 | 92.7 | 1115.9 | 1023.2
9264 | 1.9265 | 124.65 | 61.637 | 0.0055577 | 92.71 | 1115.9 |  | 9264 | 124.65 | 1.9265 | 61.637 | 0.0055577 | 92.71 | 1115.9 | 1023.19
9265 | 1.9271 | 124.66 | 61.636 | 0.0055591 | 92.72 | 1115.9 |  | 9265 | 124.66 | 1.9271 | 61.636 | 0.0055591 | 92.72 | 1115.9 | 1023.18
9266 | 1.9276 | 124.67 | 61.636 | 0.0055606 | 92.73 | 1115.9 |  | 9266 | 124.67 | 1.9276 | 61.636 | 0.0055606 | 92.73 | 1115.9 | 1023.17
9267 | 1.9281 | 124.68 | 61.636 | 0.005562 | 92.74 | 1115.9 |  | 9267 | 124.68 | 1.9281 | 61.636 | 0.005562 | 92.74 | 1115.9 | 1023.16
9268 | 1.9286 | 124.69 | 61.636 | 0.0055634 | 92.75 | 1115.9 |  | 9268 | 124.69 | 1.9286 | 61.636 | 0.0055634 | 92.75 | 1115.9 | 1023.15
9269 | 1.9292 | 124.7 | 61.636 | 0.0055648 | 92.76 | 1115.9 |  | 9269 | 124.7 | 1.9292 | 61.636 | 0.0055648 | 92.76 | 1115.9 | 1023.14
9270 | 1.9297 | 124.71 | 61.636 | 0.0055663 | 92.77 | 1115.9 |  | 9270 | 124.71 | 1.9297 | 61.636 | 0.0055663 | 92.77 | 1115.9 | 1023.13
9271 | 1.9302 | 124.72 | 61.635 | 0.0055677 | 92.78 | 1115.9 |  | 9271 | 124.72 | 1.9302 | 61.635 | 0.0055677 | 92.78 | 1115.9 | 1023.12
9272 | 1.9308 | 124.73 | 61.635 | 0.0055691 | 92.79 | 1116 |  | 9272 | 124.73 | 1.9308 | 61.635 | 0.0055691 | 92.79 | 1116 | 1023.21
9273 | 1.9313 | 124.74 | 61.635 | 0.0055705 | 92.8 | 1116 |  | 9273 | 124.74 | 1.9313 | 61.635 | 0.0055705 | 92.8 | 1116 | 1023.2
9274 | 1.9318 | 124.75 | 61.635 | 0.005572 | 92.81 | 1116 |  | 9274 | 124.75 | 1.9318 | 61.635 | 0.005572 | 92.81 | 1116 | 1023.19
9275 | 1.9323 | 124.76 | 61.635 | 0.0055734 | 92.82 | 1116 |  | 9275 | 124.76 | 1.9323 | 61.635 | 0.0055734 | 92.82 | 1116 | 1023.18
9276 | 1.9329 | 124.77 | 61.635 | 0.0055748 | 92.83 | 1116 |  | 9276 | 124.77 | 1.9329 | 61.635 | 0.0055748 | 92.83 | 1116 | 1023.17
9277 | 1.9334 | 124.78 | 61.635 | 0.0055763 | 92.84 | 1116 |  | 9277 | 124.78 | 1.9334 | 61.635 | 0.0055763 | 92.84 | 1116 | 1023.16
9278 | 1.9339 | 124.79 | 61.634 | 0.0055777 | 92.85 | 1116 |  | 9278 | 124.79 | 1.9339 | 61.634 | 0.0055777 | 92.85 | 1116 | 1023.15
9279 | 1.9344 | 124.8 | 61.634 | 0.0055791 | 92.86 | 1116 |  | 9279 | 124.8 | 1.9344 | 61.634 | 0.0055791 | 92.86 | 1116 | 1023.14
9280 | 1.935 | 124.81 | 61.634 | 0.0055806 | 92.87 | 1116 |  | 9280 | 124.81 | 1.935 | 61.634 | 0.0055806 | 92.87 | 1116 | 1023.13
9281 | 1.9355 | 124.82 | 61.634 | 0.005582 | 92.88 | 1116 |  | 9281 | 124.82 | 1.9355 | 61.634 | 0.005582 | 92.88 | 1116 | 1023.12
9282 | 1.936 | 124.83 | 61.634 | 0.0055834 | 92.89 | 1116 |  | 9282 | 124.83 | 1.936 | 61.634 | 0.0055834 | 92.89 | 1116 | 1023.11
9283 | 1.9366 | 124.84 | 61.634 | 0.0055848 | 92.9 | 1116 |  | 9283 | 124.84 | 1.9366 | 61.634 | 0.0055848 | 92.9 | 1116 | 1023.1
9284 | 1.9371 | 124.85 | 61.633 | 0.0055863 | 92.91 | 1116 |  | 9284 | 124.85 | 1.9371 | 61.633 | 0.0055863 | 92.91 | 1116 | 1023.09
9285 | 1.9376 | 124.86 | 61.633 | 0.0055877 | 92.92 | 1116 |  | 9285 | 124.86 | 1.9376 | 61.633 | 0.0055877 | 92.92 | 1116 | 1023.08
9286 | 1.9381 | 124.87 | 61.633 | 0.0055891 | 92.93 | 1116 |  | 9286 | 124.87 | 1.9381 | 61.633 | 0.0055891 | 92.93 | 1116 | 1023.07
9287 | 1.9387 | 124.88 | 61.633 | 0.0055906 | 92.94 | 1116 |  | 9287 | 124.88 | 1.9387 | 61.633 | 0.0055906 | 92.94 | 1116 | 1023.06
9288 | 1.9392 | 124.89 | 61.633 | 0.005592 | 92.95 | 1116 |  | 9288 | 124.89 | 1.9392 | 61.633 | 0.005592 | 92.95 | 1116 | 1023.05
9289 | 1.9397 | 124.9 | 61.633 | 0.0055934 | 92.96 | 1116 |  | 9289 | 124.9 | 1.9397 | 61.633 | 0.0055934 | 92.96 | 1116 | 1023.04
9290 | 1.9403 | 124.91 | 61.632 | 0.0055949 | 92.97 | 1116 |  | 9290 | 124.91 | 1.9403 | 61.632 | 0.0055949 | 92.97 | 1116 | 1023.03
9291 | 1.9408 | 124.92 | 61.632 | 0.0055963 | 92.98 | 1116 |  | 9291 | 124.92 | 1.9408 | 61.632 | 0.0055963 | 92.98 | 1116 | 1023.02
9292 | 1.9413 | 124.93 | 61.632 | 0.0055977 | 92.99 | 1116 |  | 9292 | 124.93 | 1.9413 | 61.632 | 0.0055977 | 92.99 | 1116 | 1023.01
9293 | 1.9418 | 124.94 | 61.632 | 0.0055992 | 93 | 1116 |  | 9293 | 124.94 | 1.9418 | 61.632 | 0.0055992 | 93 | 1116 | 1023
9294 | 1.9424 | 124.95 | 61.632 | 0.0056006 | 93.01 | 1116 |  | 9294 | 124.95 | 1.9424 | 61.632 | 0.0056006 | 93.01 | 1116 | 1022.99
9295 | 1.9429 | 124.96 | 61.632 | 0.005602 | 93.02 | 1116 |  | 9295 | 124.96 | 1.9429 | 61.632 | 0.005602 | 93.02 | 1116 | 1022.98
9296 | 1.9434 | 124.97 | 61.631 | 0.0056035 | 93.03 | 1116.1 |  | 9296 | 124.97 | 1.9434 | 61.631 | 0.0056035 | 93.03 | 1116.1 | 1023.07
9297 | 1.944 | 124.98 | 61.631 | 0.0056049 | 93.04 | 1116.1 |  | 9297 | 124.98 | 1.944 | 61.631 | 0.0056049 | 93.04 | 1116.1 | 1023.06
9298 | 1.9445 | 124.99 | 61.631 | 0.0056063 | 93.05 | 1116.1 |  | 9298 | 124.99 | 1.9445 | 61.631 | 0.0056063 | 93.05 | 1116.1 | 1023.05
9299 | 1.945 | 125 | 61.631 | 0.0056078 | 93.06 | 1116.1 |  | 9299 | 125 | 1.945 | 61.631 | 0.0056078 | 93.06 | 1116.1 | 1023.04
9300 | 1.9455 | 125.01 | 61.631 | 0.0056092 | 93.07 | 1116.1 |  | 9300 | 125.01 | 1.9455 | 61.631 | 0.0056092 | 93.07 | 1116.1 | 1023.03
9301 | 1.9461 | 125.02 | 61.631 | 0.0056107 | 93.08 | 1116.1 |  | 9301 | 125.02 | 1.9461 | 61.631 | 0.0056107 | 93.08 | 1116.1 | 1023.02
9302 | 1.9466 | 125.03 | 61.631 | 0.0056121 | 93.09 | 1116.1 |  | 9302 | 125.03 | 1.9466 | 61.631 | 0.0056121 | 93.09 | 1116.1 | 1023.01
9303 | 1.9471 | 125.04 | 61.63 | 0.0056135 | 93.1 | 1116.1 |  | 9303 | 125.04 | 1.9471 | 61.63 | 0.0056135 | 93.1 | 1116.1 | 1023
9304 | 1.9477 | 125.05 | 61.63 | 0.005615 | 93.11 | 1116.1 |  | 9304 | 125.05 | 1.9477 | 61.63 | 0.005615 | 93.11 | 1116.1 | 1022.99
9305 | 1.9482 | 125.06 | 61.63 | 0.0056164 | 93.12 | 1116.1 |  | 9305 | 125.06 | 1.9482 | 61.63 | 0.0056164 | 93.12 | 1116.1 | 1022.98
9306 | 1.9487 | 125.07 | 61.63 | 0.0056178 | 93.13 | 1116.1 |  | 9306 | 125.07 | 1.9487 | 61.63 | 0.0056178 | 93.13 | 1116.1 | 1022.97
9307 | 1.9493 | 125.08 | 61.63 | 0.0056193 | 93.14 | 1116.1 |  | 9307 | 125.08 | 1.9493 | 61.63 | 0.0056193 | 93.14 | 1116.1 | 1022.96
9308 | 1.9498 | 125.09 | 61.63 | 0.0056207 | 93.15 | 1116.1 |  | 9308 | 125.09 | 1.9498 | 61.63 | 0.0056207 | 93.15 | 1116.1 | 1022.95
9309 | 1.9503 | 125.1 | 61.629 | 0.0056222 | 93.16 | 1116.1 |  | 9309 | 125.1 | 1.9503 | 61.629 | 0.0056222 | 93.16 | 1116.1 | 1022.94
9310 | 1.9509 | 125.11 | 61.629 | 0.0056236 | 93.17 | 1116.1 |  | 9310 | 125.11 | 1.9509 | 61.629 | 0.0056236 | 93.17 | 1116.1 | 1022.93
9311 | 1.9514 | 125.12 | 61.629 | 0.005625 | 93.18 | 1116.1 |  | 9311 | 125.12 | 1.9514 | 61.629 | 0.005625 | 93.18 | 1116.1 | 1022.92
9312 | 1.9519 | 125.13 | 61.629 | 0.0056265 | 93.19 | 1116.1 |  | 9312 | 125.13 | 1.9519 | 61.629 | 0.0056265 | 93.19 | 1116.1 | 1022.91
9313 | 1.9524 | 125.14 | 61.629 | 0.0056279 | 93.2 | 1116.1 |  | 9313 | 125.14 | 1.9524 | 61.629 | 0.0056279 | 93.2 | 1116.1 | 1022.9
9314 | 1.953 | 125.15 | 61.629 | 0.0056294 | 93.21 | 1116.1 |  | 9314 | 125.15 | 1.953 | 61.629 | 0.0056294 | 93.21 | 1116.1 | 1022.89
9315 | 1.9535 | 125.16 | 61.628 | 0.0056308 | 93.22 | 1116.1 |  | 9315 | 125.16 | 1.9535 | 61.628 | 0.0056308 | 93.22 | 1116.1 | 1022.88
9316 | 1.954 | 125.17 | 61.628 | 0.0056322 | 93.23 | 1116.1 |  | 9316 | 125.17 | 1.954 | 61.628 | 0.0056322 | 93.23 | 1116.1 | 1022.87
9317 | 1.9546 | 125.18 | 61.628 | 0.0056337 | 93.24 | 1116.1 |  | 9317 | 125.18 | 1.9546 | 61.628 | 0.0056337 | 93.24 | 1116.1 | 1022.86
9318 | 1.9551 | 125.19 | 61.628 | 0.0056351 | 93.25 | 1116.1 |  | 9318 | 125.19 | 1.9551 | 61.628 | 0.0056351 | 93.25 | 1116.1 | 1022.85
9319 | 1.9556 | 125.2 | 61.628 | 0.0056366 | 93.26 | 1116.1 |  | 9319 | 125.2 | 1.9556 | 61.628 | 0.0056366 | 93.26 | 1116.1 | 1022.84
9320 | 1.9562 | 125.21 | 61.628 | 0.005638 | 93.27 | 1116.2 |  | 9320 | 125.21 | 1.9562 | 61.628 | 0.005638 | 93.27 | 1116.2 | 1022.93
9321 | 1.9567 | 125.22 | 61.627 | 0.0056394 | 93.28 | 1116.2 |  | 9321 | 125.22 | 1.9567 | 61.627 | 0.0056394 | 93.28 | 1116.2 | 1022.92
9322 | 1.9572 | 125.23 | 61.627 | 0.0056409 | 93.29 | 1116.2 |  | 9322 | 125.23 | 1.9572 | 61.627 | 0.0056409 | 93.29 | 1116.2 | 1022.91
9323 | 1.9578 | 125.24 | 61.627 | 0.0056423 | 93.3 | 1116.2 |  | 9323 | 125.24 | 1.9578 | 61.627 | 0.0056423 | 93.3 | 1116.2 | 1022.9
9324 | 1.9583 | 125.25 | 61.627 | 0.0056438 | 93.31 | 1116.2 |  | 9324 | 125.25 | 1.9583 | 61.627 | 0.0056438 | 93.31 | 1116.2 | 1022.89
9325 | 1.9588 | 125.26 | 61.627 | 0.0056452 | 93.32 | 1116.2 |  | 9325 | 125.26 | 1.9588 | 61.627 | 0.0056452 | 93.32 | 1116.2 | 1022.88
9326 | 1.9594 | 125.27 | 61.627 | 0.0056467 | 93.33 | 1116.2 |  | 9326 | 125.27 | 1.9594 | 61.627 | 0.0056467 | 93.33 | 1116.2 | 1022.87
9327 | 1.9599 | 125.28 | 61.626 | 0.0056481 | 93.34 | 1116.2 |  | 9327 | 125.28 | 1.9599 | 61.626 | 0.0056481 | 93.34 | 1116.2 | 1022.86
9328 | 1.9604 | 125.29 | 61.626 | 0.0056496 | 93.35 | 1116.2 |  | 9328 | 125.29 | 1.9604 | 61.626 | 0.0056496 | 93.35 | 1116.2 | 1022.85
9329 | 1.961 | 125.3 | 61.626 | 0.005651 | 93.36 | 1116.2 |  | 9329 | 125.3 | 1.961 | 61.626 | 0.005651 | 93.36 | 1116.2 | 1022.84
9330 | 1.9615 | 125.31 | 61.626 | 0.0056524 | 93.37 | 1116.2 |  | 9330 | 125.31 | 1.9615 | 61.626 | 0.0056524 | 93.37 | 1116.2 | 1022.83
9331 | 1.962 | 125.32 | 61.626 | 0.0056539 | 93.38 | 1116.2 |  | 9331 | 125.32 | 1.962 | 61.626 | 0.0056539 | 93.38 | 1116.2 | 1022.82
9332 | 1.9626 | 125.33 | 61.626 | 0.0056553 | 93.39 | 1116.2 |  | 9332 | 125.33 | 1.9626 | 61.626 | 0.0056553 | 93.39 | 1116.2 | 1022.81
9333 | 1.9631 | 125.34 | 61.626 | 0.0056568 | 93.4 | 1116.2 |  | 9333 | 125.34 | 1.9631 | 61.626 | 0.0056568 | 93.4 | 1116.2 | 1022.8
9334 | 1.9636 | 125.35 | 61.625 | 0.0056582 | 93.41 | 1116.2 |  | 9334 | 125.35 | 1.9636 | 61.625 | 0.0056582 | 93.41 | 1116.2 | 1022.79
9335 | 1.9642 | 125.36 | 61.625 | 0.0056597 | 93.42 | 1116.2 |  | 9335 | 125.36 | 1.9642 | 61.625 | 0.0056597 | 93.42 | 1116.2 | 1022.78
9336 | 1.9647 | 125.37 | 61.625 | 0.0056611 | 93.43 | 1116.2 |  | 9336 | 125.37 | 1.9647 | 61.625 | 0.0056611 | 93.43 | 1116.2 | 1022.77
9337 | 1.9652 | 125.38 | 61.625 | 0.0056626 | 93.44 | 1116.2 |  | 9337 | 125.38 | 1.9652 | 61.625 | 0.0056626 | 93.44 | 1116.2 | 1022.76
9338 | 1.9658 | 125.39 | 61.625 | 0.005664 | 93.45 | 1116.2 |  | 9338 | 125.39 | 1.9658 | 61.625 | 0.005664 | 93.45 | 1116.2 | 1022.75
9339 | 1.9663 | 125.4 | 61.625 | 0.0056655 | 93.46 | 1116.2 |  | 9339 | 125.4 | 1.9663 | 61.625 | 0.0056655 | 93.46 | 1116.2 | 1022.74
9340 | 1.9668 | 125.41 | 61.624 | 0.0056669 | 93.47 | 1116.2 |  | 9340 | 125.41 | 1.9668 | 61.624 | 0.0056669 | 93.47 | 1116.2 | 1022.73
9341 | 1.9674 | 125.42 | 61.624 | 0.0056684 | 93.48 | 1116.2 |  | 9341 | 125.42 | 1.9674 | 61.624 | 0.0056684 | 93.48 | 1116.2 | 1022.72
9342 | 1.9679 | 125.43 | 61.624 | 0.0056698 | 93.49 | 1116.2 |  | 9342 | 125.43 | 1.9679 | 61.624 | 0.0056698 | 93.49 | 1116.2 | 1022.71
9343 | 1.9685 | 125.44 | 61.624 | 0.0056713 | 93.5 | 1116.3 |  | 9343 | 125.44 | 1.9685 | 61.624 | 0.0056713 | 93.5 | 1116.3 | 1022.8
9344 | 1.969 | 125.45 | 61.624 | 0.0056727 | 93.51 | 1116.3 |  | 9344 | 125.45 | 1.969 | 61.624 | 0.0056727 | 93.51 | 1116.3 | 1022.79
9345 | 1.9695 | 125.46 | 61.624 | 0.0056742 | 93.52 | 1116.3 |  | 9345 | 125.46 | 1.9695 | 61.624 | 0.0056742 | 93.52 | 1116.3 | 1022.78
9346 | 1.9701 | 125.47 | 61.623 | 0.0056756 | 93.53 | 1116.3 |  | 9346 | 125.47 | 1.9701 | 61.623 | 0.0056756 | 93.53 | 1116.3 | 1022.77
9347 | 1.9706 | 125.48 | 61.623 | 0.0056771 | 93.54 | 1116.3 |  | 9347 | 125.48 | 1.9706 | 61.623 | 0.0056771 | 93.54 | 1116.3 | 1022.76
9348 | 1.9711 | 125.49 | 61.623 | 0.0056785 | 93.55 | 1116.3 |  | 9348 | 125.49 | 1.9711 | 61.623 | 0.0056785 | 93.55 | 1116.3 | 1022.75
9349 | 1.9717 | 125.5 | 61.623 | 0.00568 | 93.56 | 1116.3 |  | 9349 | 125.5 | 1.9717 | 61.623 | 0.00568 | 93.56 | 1116.3 | 1022.74
9350 | 1.9722 | 125.51 | 61.623 | 0.0056814 | 93.57 | 1116.3 |  | 9350 | 125.51 | 1.9722 | 61.623 | 0.0056814 | 93.57 | 1116.3 | 1022.73
9351 | 1.9727 | 125.52 | 61.623 | 0.0056829 | 93.58 | 1116.3 |  | 9351 | 125.52 | 1.9727 | 61.623 | 0.0056829 | 93.58 | 1116.3 | 1022.72
9352 | 1.9733 | 125.53 | 61.622 | 0.0056843 | 93.59 | 1116.3 |  | 9352 | 125.53 | 1.9733 | 61.622 | 0.0056843 | 93.59 | 1116.3 | 1022.71
9353 | 1.9738 | 125.54 | 61.622 | 0.0056858 | 93.6 | 1116.3 |  | 9353 | 125.54 | 1.9738 | 61.622 | 0.0056858 | 93.6 | 1116.3 | 1022.7
9354 | 1.9744 | 125.55 | 61.622 | 0.0056872 | 93.61 | 1116.3 |  | 9354 | 125.55 | 1.9744 | 61.622 | 0.0056872 | 93.61 | 1116.3 | 1022.69
9355 | 1.9749 | 125.56 | 61.622 | 0.0056887 | 93.62 | 1116.3 |  | 9355 | 125.56 | 1.9749 | 61.622 | 0.0056887 | 93.62 | 1116.3 | 1022.68
9356 | 1.9754 | 125.57 | 61.622 | 0.0056901 | 93.63 | 1116.3 |  | 9356 | 125.57 | 1.9754 | 61.622 | 0.0056901 | 93.63 | 1116.3 | 1022.67
9357 | 1.976 | 125.58 | 61.622 | 0.0056916 | 93.64 | 1116.3 |  | 9357 | 125.58 | 1.976 | 61.622 | 0.0056916 | 93.64 | 1116.3 | 1022.66
9358 | 1.9765 | 125.59 | 61.622 | 0.005693 | 93.65 | 1116.3 |  | 9358 | 125.59 | 1.9765 | 61.622 | 0.005693 | 93.65 | 1116.3 | 1022.65
9359 | 1.977 | 125.6 | 61.621 | 0.0056945 | 93.66 | 1116.3 |  | 9359 | 125.6 | 1.977 | 61.621 | 0.0056945 | 93.66 | 1116.3 | 1022.64
9360 | 1.9776 | 125.61 | 61.621 | 0.005696 | 93.67 | 1116.3 |  | 9360 | 125.61 | 1.9776 | 61.621 | 0.005696 | 93.67 | 1116.3 | 1022.63
9361 | 1.9781 | 125.62 | 61.621 | 0.0056974 | 93.68 | 1116.3 |  | 9361 | 125.62 | 1.9781 | 61.621 | 0.0056974 | 93.68 | 1116.3 | 1022.62
9362 | 1.9786 | 125.63 | 61.621 | 0.0056989 | 93.69 | 1116.3 |  | 9362 | 125.63 | 1.9786 | 61.621 | 0.0056989 | 93.69 | 1116.3 | 1022.61
9363 | 1.9792 | 125.64 | 61.621 | 0.0057003 | 93.7 | 1116.3 |  | 9363 | 125.64 | 1.9792 | 61.621 | 0.0057003 | 93.7 | 1116.3 | 1022.6
9364 | 1.9797 | 125.65 | 61.621 | 0.0057018 | 93.71 | 1116.3 |  | 9364 | 125.65 | 1.9797 | 61.621 | 0.0057018 | 93.71 | 1116.3 | 1022.59
9365 | 1.9803 | 125.66 | 61.62 | 0.0057032 | 93.72 | 1116.3 |  | 9365 | 125.66 | 1.9803 | 61.62 | 0.0057032 | 93.72 | 1116.3 | 1022.58
9366 | 1.9808 | 125.67 | 61.62 | 0.0057047 | 93.73 | 1116.3 |  | 9366 | 125.67 | 1.9808 | 61.62 | 0.0057047 | 93.73 | 1116.3 | 1022.57
9367 | 1.9813 | 125.68 | 61.62 | 0.0057062 | 93.74 | 1116.4 |  | 9367 | 125.68 | 1.9813 | 61.62 | 0.0057062 | 93.74 | 1116.4 | 1022.66
9368 | 1.9819 | 125.69 | 61.62 | 0.0057076 | 93.75 | 1116.4 |  | 9368 | 125.69 | 1.9819 | 61.62 | 0.0057076 | 93.75 | 1116.4 | 1022.65
9369 | 1.9824 | 125.7 | 61.62 | 0.0057091 | 93.76 | 1116.4 |  | 9369 | 125.7 | 1.9824 | 61.62 | 0.0057091 | 93.76 | 1116.4 | 1022.64
9370 | 1.983 | 125.71 | 61.62 | 0.0057105 | 93.77 | 1116.4 |  | 9370 | 125.71 | 1.983 | 61.62 | 0.0057105 | 93.77 | 1116.4 | 1022.63
9371 | 1.9835 | 125.72 | 61.619 | 0.005712 | 93.78 | 1116.4 |  | 9371 | 125.72 | 1.9835 | 61.619 | 0.005712 | 93.78 | 1116.4 | 1022.62
9372 | 1.984 | 125.73 | 61.619 | 0.0057134 | 93.79 | 1116.4 |  | 9372 | 125.73 | 1.984 | 61.619 | 0.0057134 | 93.79 | 1116.4 | 1022.61
9373 | 1.9846 | 125.74 | 61.619 | 0.0057149 | 93.8 | 1116.4 |  | 9373 | 125.74 | 1.9846 | 61.619 | 0.0057149 | 93.8 | 1116.4 | 1022.6
9374 | 1.9851 | 125.75 | 61.619 | 0.0057164 | 93.81 | 1116.4 |  | 9374 | 125.75 | 1.9851 | 61.619 | 0.0057164 | 93.81 | 1116.4 | 1022.59
9375 | 1.9857 | 125.76 | 61.619 | 0.0057178 | 93.82 | 1116.4 |  | 9375 | 125.76 | 1.9857 | 61.619 | 0.0057178 | 93.82 | 1116.4 | 1022.58
9376 | 1.9862 | 125.77 | 61.619 | 0.0057193 | 93.83 | 1116.4 |  | 9376 | 125.77 | 1.9862 | 61.619 | 0.0057193 | 93.83 | 1116.4 | 1022.57
9377 | 1.9867 | 125.78 | 61.618 | 0.0057207 | 93.84 | 1116.4 |  | 9377 | 125.78 | 1.9867 | 61.618 | 0.0057207 | 93.84 | 1116.4 | 1022.56
9378 | 1.9873 | 125.79 | 61.618 | 0.0057222 | 93.85 | 1116.4 |  | 9378 | 125.79 | 1.9873 | 61.618 | 0.0057222 | 93.85 | 1116.4 | 1022.55
9379 | 1.9878 | 125.8 | 61.618 | 0.0057237 | 93.86 | 1116.4 |  | 9379 | 125.8 | 1.9878 | 61.618 | 0.0057237 | 93.86 | 1116.4 | 1022.54
9380 | 1.9883 | 125.81 | 61.618 | 0.0057251 | 93.87 | 1116.4 |  | 9380 | 125.81 | 1.9883 | 61.618 | 0.0057251 | 93.87 | 1116.4 | 1022.53
9381 | 1.9889 | 125.82 | 61.618 | 0.0057266 | 93.88 | 1116.4 |  | 9381 | 125.82 | 1.9889 | 61.618 | 0.0057266 | 93.88 | 1116.4 | 1022.52
9382 | 1.9894 | 125.83 | 61.618 | 0.005728 | 93.89 | 1116.4 |  | 9382 | 125.83 | 1.9894 | 61.618 | 0.005728 | 93.89 | 1116.4 | 1022.51
9383 | 1.99 | 125.84 | 61.617 | 0.0057295 | 93.9 | 1116.4 |  | 9383 | 125.84 | 1.99 | 61.617 | 0.0057295 | 93.9 | 1116.4 | 1022.5
9384 | 1.9905 | 125.85 | 61.617 | 0.005731 | 93.91 | 1116.4 |  | 9384 | 125.85 | 1.9905 | 61.617 | 0.005731 | 93.91 | 1116.4 | 1022.49
9385 | 1.9911 | 125.86 | 61.617 | 0.0057324 | 93.92 | 1116.4 |  | 9385 | 125.86 | 1.9911 | 61.617 | 0.0057324 | 93.92 | 1116.4 | 1022.48
9386 | 1.9916 | 125.87 | 61.617 | 0.0057339 | 93.93 | 1116.4 |  | 9386 | 125.87 | 1.9916 | 61.617 | 0.0057339 | 93.93 | 1116.4 | 1022.47
9387 | 1.9921 | 125.88 | 61.617 | 0.0057354 | 93.94 | 1116.4 |  | 9387 | 125.88 | 1.9921 | 61.617 | 0.0057354 | 93.94 | 1116.4 | 1022.46
9388 | 1.9927 | 125.89 | 61.617 | 0.0057368 | 93.95 | 1116.4 |  | 9388 | 125.89 | 1.9927 | 61.617 | 0.0057368 | 93.95 | 1116.4 | 1022.45
9389 | 1.9932 | 125.9 | 61.616 | 0.0057383 | 93.96 | 1116.4 |  | 9389 | 125.9 | 1.9932 | 61.616 | 0.0057383 | 93.96 | 1116.4 | 1022.44
9390 | 1.9938 | 125.91 | 61.616 | 0.0057398 | 93.97 | 1116.4 |  | 9390 | 125.91 | 1.9938 | 61.616 | 0.0057398 | 93.97 | 1116.4 | 1022.43
9391 | 1.9943 | 125.92 | 61.616 | 0.0057412 | 93.98 | 1116.5 |  | 9391 | 125.92 | 1.9943 | 61.616 | 0.0057412 | 93.98 | 1116.5 | 1022.52
9392 | 1.9948 | 125.93 | 61.616 | 0.0057427 | 93.99 | 1116.5 |  | 9392 | 125.93 | 1.9948 | 61.616 | 0.0057427 | 93.99 | 1116.5 | 1022.51
9393 | 1.9954 | 125.94 | 61.616 | 0.0057441 | 93.999 | 1116.5 |  | 9393 | 125.94 | 1.9954 | 61.616 | 0.0057441 | 93.999 | 1116.5 | 1022.501
9394 | 1.9959 | 125.95 | 61.616 | 0.0057456 | 94.009 | 1116.5 |  | 9394 | 125.95 | 1.9959 | 61.616 | 0.0057456 | 94.009 | 1116.5 | 1022.491
9395 | 1.9965 | 125.96 | 61.616 | 0.0057471 | 94.019 | 1116.5 |  | 9395 | 125.96 | 1.9965 | 61.616 | 0.0057471 | 94.019 | 1116.5 | 1022.481
9396 | 1.997 | 125.97 | 61.615 | 0.0057485 | 94.029 | 1116.5 |  | 9396 | 125.97 | 1.997 | 61.615 | 0.0057485 | 94.029 | 1116.5 | 1022.471
9397 | 1.9975 | 125.98 | 61.615 | 0.00575 | 94.039 | 1116.5 |  | 9397 | 125.98 | 1.9975 | 61.615 | 0.00575 | 94.039 | 1116.5 | 1022.461
9398 | 1.9981 | 125.99 | 61.615 | 0.0057515 | 94.049 | 1116.5 |  | 9398 | 125.99 | 1.9981 | 61.615 | 0.0057515 | 94.049 | 1116.5 | 1022.451
9399 | 1.9986 | 126 | 61.615 | 0.0057529 | 94.059 | 1116.5 |  | 9399 | 126 | 1.9986 | 61.615 | 0.0057529 | 94.059 | 1116.5 | 1022.441
9400 | 1.9992 | 126.01 | 61.615 | 0.0057544 | 94.069 | 1116.5 |  | 9400 | 126.01 | 1.9992 | 61.615 | 0.0057544 | 94.069 | 1116.5 | 1022.431
9401 | 1.9997 | 126.02 | 61.615 | 0.0057559 | 94.079 | 1116.5 |  | 9401 | 126.02 | 1.9997 | 61.615 | 0.0057559 | 94.079 | 1116.5 | 1022.421
9402 | 2.0003 | 126.03 | 61.614 | 0.0057573 | 94.089 | 1116.5 |  | 9402 | 126.03 | 2.0003 | 61.614 | 0.0057573 | 94.089 | 1116.5 | 1022.411
9403 | 2.0008 | 126.04 | 61.614 | 0.0057588 | 94.099 | 1116.5 |  | 9403 | 126.04 | 2.0008 | 61.614 | 0.0057588 | 94.099 | 1116.5 | 1022.401
9404 | 2.0013 | 126.05 | 61.614 | 0.0057603 | 94.109 | 1116.5 |  | 9404 | 126.05 | 2.0013 | 61.614 | 0.0057603 | 94.109 | 1116.5 | 1022.391
9405 | 2.0019 | 126.06 | 61.614 | 0.0057618 | 94.119 | 1116.5 |  | 9405 | 126.06 | 2.0019 | 61.614 | 0.0057618 | 94.119 | 1116.5 | 1022.381
9406 | 2.0024 | 126.07 | 61.614 | 0.0057632 | 94.129 | 1116.5 |  | 9406 | 126.07 | 2.0024 | 61.614 | 0.0057632 | 94.129 | 1116.5 | 1022.371
9407 | 2.003 | 126.08 | 61.614 | 0.0057647 | 94.139 | 1116.5 |  | 9407 | 126.08 | 2.003 | 61.614 | 0.0057647 | 94.139 | 1116.5 | 1022.361
9408 | 2.0035 | 126.09 | 61.613 | 0.0057662 | 94.149 | 1116.5 |  | 9408 | 126.09 | 2.0035 | 61.613 | 0.0057662 | 94.149 | 1116.5 | 1022.351
9409 | 2.0041 | 126.1 | 61.613 | 0.0057676 | 94.159 | 1116.5 |  | 9409 | 126.1 | 2.0041 | 61.613 | 0.0057676 | 94.159 | 1116.5 | 1022.341
9410 | 2.0046 | 126.11 | 61.613 | 0.0057691 | 94.169 | 1116.5 |  | 9410 | 126.11 | 2.0046 | 61.613 | 0.0057691 | 94.169 | 1116.5 | 1022.331
9411 | 2.0052 | 126.12 | 61.613 | 0.0057706 | 94.179 | 1116.5 |  | 9411 | 126.12 | 2.0052 | 61.613 | 0.0057706 | 94.179 | 1116.5 | 1022.321
9412 | 2.0057 | 126.13 | 61.613 | 0.005772 | 94.189 | 1116.5 |  | 9412 | 126.13 | 2.0057 | 61.613 | 0.005772 | 94.189 | 1116.5 | 1022.311
9413 | 2.0062 | 126.14 | 61.613 | 0.0057735 | 94.199 | 1116.5 |  | 9413 | 126.14 | 2.0062 | 61.613 | 0.0057735 | 94.199 | 1116.5 | 1022.301
9414 | 2.0068 | 126.15 | 61.612 | 0.005775 | 94.209 | 1116.5 |  | 9414 | 126.15 | 2.0068 | 61.612 | 0.005775 | 94.209 | 1116.5 | 1022.291
9415 | 2.0073 | 126.16 | 61.612 | 0.0057765 | 94.219 | 1116.6 |  | 9415 | 126.16 | 2.0073 | 61.612 | 0.0057765 | 94.219 | 1116.6 | 1022.381
9416 | 2.0079 | 126.17 | 61.612 | 0.0057779 | 94.229 | 1116.6 |  | 9416 | 126.17 | 2.0079 | 61.612 | 0.0057779 | 94.229 | 1116.6 | 1022.371
9417 | 2.0084 | 126.18 | 61.612 | 0.0057794 | 94.239 | 1116.6 |  | 9417 | 126.18 | 2.0084 | 61.612 | 0.0057794 | 94.239 | 1116.6 | 1022.361
9418 | 2.009 | 126.19 | 61.612 | 0.0057809 | 94.249 | 1116.6 |  | 9418 | 126.19 | 2.009 | 61.612 | 0.0057809 | 94.249 | 1116.6 | 1022.351
9419 | 2.0095 | 126.2 | 61.612 | 0.0057824 | 94.259 | 1116.6 |  | 9419 | 126.2 | 2.0095 | 61.612 | 0.0057824 | 94.259 | 1116.6 | 1022.341
9420 | 2.0101 | 126.21 | 61.611 | 0.0057838 | 94.269 | 1116.6 |  | 9420 | 126.21 | 2.0101 | 61.611 | 0.0057838 | 94.269 | 1116.6 | 1022.331
9421 | 2.0106 | 126.22 | 61.611 | 0.0057853 | 94.279 | 1116.6 |  | 9421 | 126.22 | 2.0106 | 61.611 | 0.0057853 | 94.279 | 1116.6 | 1022.321
9422 | 2.0111 | 126.23 | 61.611 | 0.0057868 | 94.289 | 1116.6 |  | 9422 | 126.23 | 2.0111 | 61.611 | 0.0057868 | 94.289 | 1116.6 | 1022.311
9423 | 2.0117 | 126.24 | 61.611 | 0.0057883 | 94.299 | 1116.6 |  | 9423 | 126.24 | 2.0117 | 61.611 | 0.0057883 | 94.299 | 1116.6 | 1022.301
9424 | 2.0122 | 126.25 | 61.611 | 0.0057897 | 94.309 | 1116.6 |  | 9424 | 126.25 | 2.0122 | 61.611 | 0.0057897 | 94.309 | 1116.6 | 1022.291
9425 | 2.0128 | 126.26 | 61.611 | 0.0057912 | 94.319 | 1116.6 |  | 9425 | 126.26 | 2.0128 | 61.611 | 0.0057912 | 94.319 | 1116.6 | 1022.281
9426 | 2.0133 | 126.27 | 61.611 | 0.0057927 | 94.329 | 1116.6 |  | 9426 | 126.27 | 2.0133 | 61.611 | 0.0057927 | 94.329 | 1116.6 | 1022.271
9427 | 2.0139 | 126.28 | 61.61 | 0.0057942 | 94.339 | 1116.6 |  | 9427 | 126.28 | 2.0139 | 61.61 | 0.0057942 | 94.339 | 1116.6 | 1022.261
9428 | 2.0144 | 126.29 | 61.61 | 0.0057956 | 94.349 | 1116.6 |  | 9428 | 126.29 | 2.0144 | 61.61 | 0.0057956 | 94.349 | 1116.6 | 1022.251
9429 | 2.015 | 126.3 | 61.61 | 0.0057971 | 94.359 | 1116.6 |  | 9429 | 126.3 | 2.015 | 61.61 | 0.0057971 | 94.359 | 1116.6 | 1022.241
9430 | 2.0155 | 126.31 | 61.61 | 0.0057986 | 94.369 | 1116.6 |  | 9430 | 126.31 | 2.0155 | 61.61 | 0.0057986 | 94.369 | 1116.6 | 1022.231
9431 | 2.0161 | 126.32 | 61.61 | 0.0058001 | 94.379 | 1116.6 |  | 9431 | 126.32 | 2.0161 | 61.61 | 0.0058001 | 94.379 | 1116.6 | 1022.221
9432 | 2.0166 | 126.33 | 61.61 | 0.0058015 | 94.389 | 1116.6 |  | 9432 | 126.33 | 2.0166 | 61.61 | 0.0058015 | 94.389 | 1116.6 | 1022.211
9433 | 2.0171 | 126.34 | 61.609 | 0.005803 | 94.399 | 1116.6 |  | 9433 | 126.34 | 2.0171 | 61.609 | 0.005803 | 94.399 | 1116.6 | 1022.201
9434 | 2.0177 | 126.35 | 61.609 | 0.0058045 | 94.409 | 1116.6 |  | 9434 | 126.35 | 2.0177 | 61.609 | 0.0058045 | 94.409 | 1116.6 | 1022.191
9435 | 2.0182 | 126.36 | 61.609 | 0.005806 | 94.419 | 1116.6 |  | 9435 | 126.36 | 2.0182 | 61.609 | 0.005806 | 94.419 | 1116.6 | 1022.181
9436 | 2.0188 | 126.37 | 61.609 | 0.0058075 | 94.429 | 1116.6 |  | 9436 | 126.37 | 2.0188 | 61.609 | 0.0058075 | 94.429 | 1116.6 | 1022.171
9437 | 2.0193 | 126.38 | 61.609 | 0.0058089 | 94.439 | 1116.6 |  | 9437 | 126.38 | 2.0193 | 61.609 | 0.0058089 | 94.439 | 1116.6 | 1022.161
9438 | 2.0199 | 126.39 | 61.609 | 0.0058104 | 94.449 | 1116.7 |  | 9438 | 126.39 | 2.0199 | 61.609 | 0.0058104 | 94.449 | 1116.7 | 1022.251
9439 | 2.0204 | 126.4 | 61.608 | 0.0058119 | 94.459 | 1116.7 |  | 9439 | 126.4 | 2.0204 | 61.608 | 0.0058119 | 94.459 | 1116.7 | 1022.241
9440 | 2.021 | 126.41 | 61.608 | 0.0058134 | 94.469 | 1116.7 |  | 9440 | 126.41 | 2.021 | 61.608 | 0.0058134 | 94.469 | 1116.7 | 1022.231
9441 | 2.0215 | 126.42 | 61.608 | 0.0058149 | 94.479 | 1116.7 |  | 9441 | 126.42 | 2.0215 | 61.608 | 0.0058149 | 94.479 | 1116.7 | 1022.221
9442 | 2.0221 | 126.43 | 61.608 | 0.0058163 | 94.489 | 1116.7 |  | 9442 | 126.43 | 2.0221 | 61.608 | 0.0058163 | 94.489 | 1116.7 | 1022.211
9443 | 2.0226 | 126.44 | 61.608 | 0.0058178 | 94.499 | 1116.7 |  | 9443 | 126.44 | 2.0226 | 61.608 | 0.0058178 | 94.499 | 1116.7 | 1022.201
9444 | 2.0232 | 126.45 | 61.608 | 0.0058193 | 94.509 | 1116.7 |  | 9444 | 126.45 | 2.0232 | 61.608 | 0.0058193 | 94.509 | 1116.7 | 1022.191
9445 | 2.0237 | 126.46 | 61.607 | 0.0058208 | 94.519 | 1116.7 |  | 9445 | 126.46 | 2.0237 | 61.607 | 0.0058208 | 94.519 | 1116.7 | 1022.181
9446 | 2.0243 | 126.47 | 61.607 | 0.0058223 | 94.529 | 1116.7 |  | 9446 | 126.47 | 2.0243 | 61.607 | 0.0058223 | 94.529 | 1116.7 | 1022.171
9447 | 2.0248 | 126.48 | 61.607 | 0.0058237 | 94.539 | 1116.7 |  | 9447 | 126.48 | 2.0248 | 61.607 | 0.0058237 | 94.539 | 1116.7 | 1022.161
9448 | 2.0254 | 126.49 | 61.607 | 0.0058252 | 94.549 | 1116.7 |  | 9448 | 126.49 | 2.0254 | 61.607 | 0.0058252 | 94.549 | 1116.7 | 1022.151
9449 | 2.0259 | 126.5 | 61.607 | 0.0058267 | 94.559 | 1116.7 |  | 9449 | 126.5 | 2.0259 | 61.607 | 0.0058267 | 94.559 | 1116.7 | 1022.141
9450 | 2.0265 | 126.51 | 61.607 | 0.0058282 | 94.569 | 1116.7 |  | 9450 | 126.51 | 2.0265 | 61.607 | 0.0058282 | 94.569 | 1116.7 | 1022.131
9451 | 2.027 | 126.52 | 61.606 | 0.0058297 | 94.579 | 1116.7 |  | 9451 | 126.52 | 2.027 | 61.606 | 0.0058297 | 94.579 | 1116.7 | 1022.121
9452 | 2.0276 | 126.53 | 61.606 | 0.0058312 | 94.589 | 1116.7 |  | 9452 | 126.53 | 2.0276 | 61.606 | 0.0058312 | 94.589 | 1116.7 | 1022.111
9453 | 2.0281 | 126.54 | 61.606 | 0.0058326 | 94.599 | 1116.7 |  | 9453 | 126.54 | 2.0281 | 61.606 | 0.0058326 | 94.599 | 1116.7 | 1022.101
9454 | 2.0287 | 126.55 | 61.606 | 0.0058341 | 94.609 | 1116.7 |  | 9454 | 126.55 | 2.0287 | 61.606 | 0.0058341 | 94.609 | 1116.7 | 1022.091
9455 | 2.0292 | 126.56 | 61.606 | 0.0058356 | 94.619 | 1116.7 |  | 9455 | 126.56 | 2.0292 | 61.606 | 0.0058356 | 94.619 | 1116.7 | 1022.081
9456 | 2.0298 | 126.57 | 61.606 | 0.0058371 | 94.629 | 1116.7 |  | 9456 | 126.57 | 2.0298 | 61.606 | 0.0058371 | 94.629 | 1116.7 | 1022.071
9457 | 2.0303 | 126.58 | 61.605 | 0.0058386 | 94.639 | 1116.7 |  | 9457 | 126.58 | 2.0303 | 61.605 | 0.0058386 | 94.639 | 1116.7 | 1022.061
9458 | 2.0309 | 126.59 | 61.605 | 0.0058401 | 94.649 | 1116.7 |  | 9458 | 126.59 | 2.0309 | 61.605 | 0.0058401 | 94.649 | 1116.7 | 1022.051
9459 | 2.0314 | 126.6 | 61.605 | 0.0058416 | 94.659 | 1116.7 |  | 9459 | 126.6 | 2.0314 | 61.605 | 0.0058416 | 94.659 | 1116.7 | 1022.041
9460 | 2.032 | 126.61 | 61.605 | 0.005843 | 94.669 | 1116.7 |  | 9460 | 126.61 | 2.032 | 61.605 | 0.005843 | 94.669 | 1116.7 | 1022.031
9461 | 2.0325 | 126.62 | 61.605 | 0.0058445 | 94.679 | 1116.7 |  | 9461 | 126.62 | 2.0325 | 61.605 | 0.0058445 | 94.679 | 1116.7 | 1022.021
9462 | 2.0331 | 126.63 | 61.605 | 0.005846 | 94.689 | 1116.8 |  | 9462 | 126.63 | 2.0331 | 61.605 | 0.005846 | 94.689 | 1116.8 | 1022.111
9463 | 2.0336 | 126.64 | 61.605 | 0.0058475 | 94.699 | 1116.8 |  | 9463 | 126.64 | 2.0336 | 61.605 | 0.0058475 | 94.699 | 1116.8 | 1022.101
9464 | 2.0342 | 126.65 | 61.604 | 0.005849 | 94.709 | 1116.8 |  | 9464 | 126.65 | 2.0342 | 61.604 | 0.005849 | 94.709 | 1116.8 | 1022.091
9465 | 2.0347 | 126.66 | 61.604 | 0.0058505 | 94.719 | 1116.8 |  | 9465 | 126.66 | 2.0347 | 61.604 | 0.0058505 | 94.719 | 1116.8 | 1022.081
9466 | 2.0353 | 126.67 | 61.604 | 0.005852 | 94.729 | 1116.8 |  | 9466 | 126.67 | 2.0353 | 61.604 | 0.005852 | 94.729 | 1116.8 | 1022.071
9467 | 2.0358 | 126.68 | 61.604 | 0.0058535 | 94.739 | 1116.8 |  | 9467 | 126.68 | 2.0358 | 61.604 | 0.0058535 | 94.739 | 1116.8 | 1022.061
9468 | 2.0364 | 126.69 | 61.604 | 0.0058549 | 94.749 | 1116.8 |  | 9468 | 126.69 | 2.0364 | 61.604 | 0.0058549 | 94.749 | 1116.8 | 1022.051
9469 | 2.0369 | 126.7 | 61.604 | 0.0058564 | 94.759 | 1116.8 |  | 9469 | 126.7 | 2.0369 | 61.604 | 0.0058564 | 94.759 | 1116.8 | 1022.041
9470 | 2.0375 | 126.71 | 61.603 | 0.0058579 | 94.769 | 1116.8 |  | 9470 | 126.71 | 2.0375 | 61.603 | 0.0058579 | 94.769 | 1116.8 | 1022.031
9471 | 2.038 | 126.72 | 61.603 | 0.0058594 | 94.779 | 1116.8 |  | 9471 | 126.72 | 2.038 | 61.603 | 0.0058594 | 94.779 | 1116.8 | 1022.021
9472 | 2.0386 | 126.73 | 61.603 | 0.0058609 | 94.789 | 1116.8 |  | 9472 | 126.73 | 2.0386 | 61.603 | 0.0058609 | 94.789 | 1116.8 | 1022.011
9473 | 2.0391 | 126.74 | 61.603 | 0.0058624 | 94.799 | 1116.8 |  | 9473 | 126.74 | 2.0391 | 61.603 | 0.0058624 | 94.799 | 1116.8 | 1022.001
9474 | 2.0397 | 126.75 | 61.603 | 0.0058639 | 94.809 | 1116.8 |  | 9474 | 126.75 | 2.0397 | 61.603 | 0.0058639 | 94.809 | 1116.8 | 1021.991
9475 | 2.0402 | 126.76 | 61.603 | 0.0058654 | 94.819 | 1116.8 |  | 9475 | 126.76 | 2.0402 | 61.603 | 0.0058654 | 94.819 | 1116.8 | 1021.981
9476 | 2.0408 | 126.77 | 61.602 | 0.0058669 | 94.829 | 1116.8 |  | 9476 | 126.77 | 2.0408 | 61.602 | 0.0058669 | 94.829 | 1116.8 | 1021.971
9477 | 2.0413 | 126.78 | 61.602 | 0.0058684 | 94.839 | 1116.8 |  | 9477 | 126.78 | 2.0413 | 61.602 | 0.0058684 | 94.839 | 1116.8 | 1021.961
9478 | 2.0419 | 126.79 | 61.602 | 0.0058699 | 94.849 | 1116.8 |  | 9478 | 126.79 | 2.0419 | 61.602 | 0.0058699 | 94.849 | 1116.8 | 1021.951
9479 | 2.0424 | 126.8 | 61.602 | 0.0058713 | 94.859 | 1116.8 |  | 9479 | 126.8 | 2.0424 | 61.602 | 0.0058713 | 94.859 | 1116.8 | 1021.941
9480 | 2.043 | 126.81 | 61.602 | 0.0058728 | 94.869 | 1116.8 |  | 9480 | 126.81 | 2.043 | 61.602 | 0.0058728 | 94.869 | 1116.8 | 1021.931
9481 | 2.0435 | 126.82 | 61.602 | 0.0058743 | 94.879 | 1116.8 |  | 9481 | 126.82 | 2.0435 | 61.602 | 0.0058743 | 94.879 | 1116.8 | 1021.921
9482 | 2.0441 | 126.83 | 61.601 | 0.0058758 | 94.889 | 1116.8 |  | 9482 | 126.83 | 2.0441 | 61.601 | 0.0058758 | 94.889 | 1116.8 | 1021.911
9483 | 2.0446 | 126.84 | 61.601 | 0.0058773 | 94.899 | 1116.8 |  | 9483 | 126.84 | 2.0446 | 61.601 | 0.0058773 | 94.899 | 1116.8 | 1021.901
9484 | 2.0452 | 126.85 | 61.601 | 0.0058788 | 94.909 | 1116.8 |  | 9484 | 126.85 | 2.0452 | 61.601 | 0.0058788 | 94.909 | 1116.8 | 1021.891
9485 | 2.0457 | 126.86 | 61.601 | 0.0058803 | 94.919 | 1116.8 |  | 9485 | 126.86 | 2.0457 | 61.601 | 0.0058803 | 94.919 | 1116.8 | 1021.881
9486 | 2.0463 | 126.87 | 61.601 | 0.0058818 | 94.929 | 1116.9 |  | 9486 | 126.87 | 2.0463 | 61.601 | 0.0058818 | 94.929 | 1116.9 | 1021.971
9487 | 2.0469 | 126.88 | 61.601 | 0.0058833 | 94.939 | 1116.9 |  | 9487 | 126.88 | 2.0469 | 61.601 | 0.0058833 | 94.939 | 1116.9 | 1021.961
9488 | 2.0474 | 126.89 | 61.6 | 0.0058848 | 94.949 | 1116.9 |  | 9488 | 126.89 | 2.0474 | 61.6 | 0.0058848 | 94.949 | 1116.9 | 1021.951
9489 | 2.048 | 126.9 | 61.6 | 0.0058863 | 94.959 | 1116.9 |  | 9489 | 126.9 | 2.048 | 61.6 | 0.0058863 | 94.959 | 1116.9 | 1021.941
9490 | 2.0485 | 126.91 | 61.6 | 0.0058878 | 94.969 | 1116.9 |  | 9490 | 126.91 | 2.0485 | 61.6 | 0.0058878 | 94.969 | 1116.9 | 1021.931
9491 | 2.0491 | 126.92 | 61.6 | 0.0058893 | 94.979 | 1116.9 |  | 9491 | 126.92 | 2.0491 | 61.6 | 0.0058893 | 94.979 | 1116.9 | 1021.921
9492 | 2.0496 | 126.93 | 61.6 | 0.0058908 | 94.989 | 1116.9 |  | 9492 | 126.93 | 2.0496 | 61.6 | 0.0058908 | 94.989 | 1116.9 | 1021.911
9493 | 2.0502 | 126.94 | 61.6 | 0.0058923 | 94.999 | 1116.9 |  | 9493 | 126.94 | 2.0502 | 61.6 | 0.0058923 | 94.999 | 1116.9 | 1021.901
9494 | 2.0507 | 126.95 | 61.599 | 0.0058938 | 95.009 | 1116.9 |  | 9494 | 126.95 | 2.0507 | 61.599 | 0.0058938 | 95.009 | 1116.9 | 1021.891
9495 | 2.0513 | 126.96 | 61.599 | 0.0058953 | 95.019 | 1116.9 |  | 9495 | 126.96 | 2.0513 | 61.599 | 0.0058953 | 95.019 | 1116.9 | 1021.881
9496 | 2.0518 | 126.97 | 61.599 | 0.0058968 | 95.029 | 1116.9 |  | 9496 | 126.97 | 2.0518 | 61.599 | 0.0058968 | 95.029 | 1116.9 | 1021.871
9497 | 2.0524 | 126.98 | 61.599 | 0.0058983 | 95.039 | 1116.9 |  | 9497 | 126.98 | 2.0524 | 61.599 | 0.0058983 | 95.039 | 1116.9 | 1021.861
9498 | 2.053 | 126.99 | 61.599 | 0.0058998 | 95.049 | 1116.9 |  | 9498 | 126.99 | 2.053 | 61.599 | 0.0058998 | 95.049 | 1116.9 | 1021.851
9499 | 2.0535 | 127 | 61.599 | 0.0059013 | 95.059 | 1116.9 |  | 9499 | 127 | 2.0535 | 61.599 | 0.0059013 | 95.059 | 1116.9 | 1021.841
9500 | 2.0541 | 127.01 | 61.598 | 0.0059028 | 95.069 | 1116.9 |  | 9500 | 127.01 | 2.0541 | 61.598 | 0.0059028 | 95.069 | 1116.9 | 1021.831
9501 | 2.0546 | 127.02 | 61.598 | 0.0059043 | 95.079 | 1116.9 |  | 9501 | 127.02 | 2.0546 | 61.598 | 0.0059043 | 95.079 | 1116.9 | 1021.821
9502 | 2.0552 | 127.03 | 61.598 | 0.0059058 | 95.089 | 1116.9 |  | 9502 | 127.03 | 2.0552 | 61.598 | 0.0059058 | 95.089 | 1116.9 | 1021.811
9503 | 2.0557 | 127.04 | 61.598 | 0.0059073 | 95.099 | 1116.9 |  | 9503 | 127.04 | 2.0557 | 61.598 | 0.0059073 | 95.099 | 1116.9 | 1021.801
9504 | 2.0563 | 127.05 | 61.598 | 0.0059088 | 95.109 | 1116.9 |  | 9504 | 127.05 | 2.0563 | 61.598 | 0.0059088 | 95.109 | 1116.9 | 1021.791
9505 | 2.0568 | 127.06 | 61.598 | 0.0059103 | 95.119 | 1116.9 |  | 9505 | 127.06 | 2.0568 | 61.598 | 0.0059103 | 95.119 | 1116.9 | 1021.781
9506 | 2.0574 | 127.07 | 61.598 | 0.0059118 | 95.129 | 1116.9 |  | 9506 | 127.07 | 2.0574 | 61.598 | 0.0059118 | 95.129 | 1116.9 | 1021.771
9507 | 2.058 | 127.08 | 61.597 | 0.0059133 | 95.139 | 1116.9 |  | 9507 | 127.08 | 2.058 | 61.597 | 0.0059133 | 95.139 | 1116.9 | 1021.761
9508 | 2.0585 | 127.09 | 61.597 | 0.0059148 | 95.149 | 1116.9 |  | 9508 | 127.09 | 2.0585 | 61.597 | 0.0059148 | 95.149 | 1116.9 | 1021.751
9509 | 2.0591 | 127.1 | 61.597 | 0.0059163 | 95.159 | 1116.9 |  | 9509 | 127.1 | 2.0591 | 61.597 | 0.0059163 | 95.159 | 1116.9 | 1021.741
9510 | 2.0596 | 127.11 | 61.597 | 0.0059178 | 95.169 | 1117 |  | 9510 | 127.11 | 2.0596 | 61.597 | 0.0059178 | 95.169 | 1117 | 1021.831
9511 | 2.0602 | 127.12 | 61.597 | 0.0059193 | 95.179 | 1117 |  | 9511 | 127.12 | 2.0602 | 61.597 | 0.0059193 | 95.179 | 1117 | 1021.821
9512 | 2.0607 | 127.13 | 61.597 | 0.0059208 | 95.189 | 1117 |  | 9512 | 127.13 | 2.0607 | 61.597 | 0.0059208 | 95.189 | 1117 | 1021.811
9513 | 2.0613 | 127.14 | 61.596 | 0.0059223 | 95.199 | 1117 |  | 9513 | 127.14 | 2.0613 | 61.596 | 0.0059223 | 95.199 | 1117 | 1021.801
9514 | 2.0618 | 127.15 | 61.596 | 0.0059238 | 95.209 | 1117 |  | 9514 | 127.15 | 2.0618 | 61.596 | 0.0059238 | 95.209 | 1117 | 1021.791
9515 | 2.0624 | 127.16 | 61.596 | 0.0059253 | 95.219 | 1117 |  | 9515 | 127.16 | 2.0624 | 61.596 | 0.0059253 | 95.219 | 1117 | 1021.781
9516 | 2.063 | 127.17 | 61.596 | 0.0059268 | 95.229 | 1117 |  | 9516 | 127.17 | 2.063 | 61.596 | 0.0059268 | 95.229 | 1117 | 1021.771
9517 | 2.0635 | 127.18 | 61.596 | 0.0059283 | 95.239 | 1117 |  | 9517 | 127.18 | 2.0635 | 61.596 | 0.0059283 | 95.239 | 1117 | 1021.761
9518 | 2.0641 | 127.19 | 61.596 | 0.0059298 | 95.249 | 1117 |  | 9518 | 127.19 | 2.0641 | 61.596 | 0.0059298 | 95.249 | 1117 | 1021.751
9519 | 2.0646 | 127.2 | 61.595 | 0.0059313 | 95.259 | 1117 |  | 9519 | 127.2 | 2.0646 | 61.595 | 0.0059313 | 95.259 | 1117 | 1021.741
9520 | 2.0652 | 127.21 | 61.595 | 0.0059328 | 95.269 | 1117 |  | 9520 | 127.21 | 2.0652 | 61.595 | 0.0059328 | 95.269 | 1117 | 1021.731
9521 | 2.0658 | 127.22 | 61.595 | 0.0059343 | 95.279 | 1117 |  | 9521 | 127.22 | 2.0658 | 61.595 | 0.0059343 | 95.279 | 1117 | 1021.721
9522 | 2.0663 | 127.23 | 61.595 | 0.0059358 | 95.289 | 1117 |  | 9522 | 127.23 | 2.0663 | 61.595 | 0.0059358 | 95.289 | 1117 | 1021.711
9523 | 2.0669 | 127.24 | 61.595 | 0.0059373 | 95.299 | 1117 |  | 9523 | 127.24 | 2.0669 | 61.595 | 0.0059373 | 95.299 | 1117 | 1021.701
9524 | 2.0674 | 127.25 | 61.595 | 0.0059388 | 95.309 | 1117 |  | 9524 | 127.25 | 2.0674 | 61.595 | 0.0059388 | 95.309 | 1117 | 1021.691
9525 | 2.068 | 127.26 | 61.594 | 0.0059404 | 95.319 | 1117 |  | 9525 | 127.26 | 2.068 | 61.594 | 0.0059404 | 95.319 | 1117 | 1021.681
9526 | 2.0685 | 127.27 | 61.594 | 0.0059419 | 95.329 | 1117 |  | 9526 | 127.27 | 2.0685 | 61.594 | 0.0059419 | 95.329 | 1117 | 1021.671
9527 | 2.0691 | 127.28 | 61.594 | 0.0059434 | 95.339 | 1117 |  | 9527 | 127.28 | 2.0691 | 61.594 | 0.0059434 | 95.339 | 1117 | 1021.661
9528 | 2.0697 | 127.29 | 61.594 | 0.0059449 | 95.349 | 1117 |  | 9528 | 127.29 | 2.0697 | 61.594 | 0.0059449 | 95.349 | 1117 | 1021.651
9529 | 2.0702 | 127.3 | 61.594 | 0.0059464 | 95.359 | 1117 |  | 9529 | 127.3 | 2.0702 | 61.594 | 0.0059464 | 95.359 | 1117 | 1021.641
9530 | 2.0708 | 127.31 | 61.594 | 0.0059479 | 95.369 | 1117 |  | 9530 | 127.31 | 2.0708 | 61.594 | 0.0059479 | 95.369 | 1117 | 1021.631
9531 | 2.0713 | 127.32 | 61.593 | 0.0059494 | 95.379 | 1117 |  | 9531 | 127.32 | 2.0713 | 61.593 | 0.0059494 | 95.379 | 1117 | 1021.621
9532 | 2.0719 | 127.33 | 61.593 | 0.0059509 | 95.389 | 1117 |  | 9532 | 127.33 | 2.0719 | 61.593 | 0.0059509 | 95.389 | 1117 | 1021.611
9533 | 2.0725 | 127.34 | 61.593 | 0.0059524 | 95.399 | 1117.1 |  | 9533 | 127.34 | 2.0725 | 61.593 | 0.0059524 | 95.399 | 1117.1 | 1021.701
9534 | 2.073 | 127.35 | 61.593 | 0.0059539 | 95.409 | 1117.1 |  | 9534 | 127.35 | 2.073 | 61.593 | 0.0059539 | 95.409 | 1117.1 | 1021.691
9535 | 2.0736 | 127.36 | 61.593 | 0.0059554 | 95.419 | 1117.1 |  | 9535 | 127.36 | 2.0736 | 61.593 | 0.0059554 | 95.419 | 1117.1 | 1021.681
9536 | 2.0741 | 127.37 | 61.593 | 0.005957 | 95.429 | 1117.1 |  | 9536 | 127.37 | 2.0741 | 61.593 | 0.005957 | 95.429 | 1117.1 | 1021.671
9537 | 2.0747 | 127.38 | 61.592 | 0.0059585 | 95.439 | 1117.1 |  | 9537 | 127.38 | 2.0747 | 61.592 | 0.0059585 | 95.439 | 1117.1 | 1021.661
9538 | 2.0753 | 127.39 | 61.592 | 0.00596 | 95.449 | 1117.1 |  | 9538 | 127.39 | 2.0753 | 61.592 | 0.00596 | 95.449 | 1117.1 | 1021.651
9539 | 2.0758 | 127.4 | 61.592 | 0.0059615 | 95.459 | 1117.1 |  | 9539 | 127.4 | 2.0758 | 61.592 | 0.0059615 | 95.459 | 1117.1 | 1021.641
9540 | 2.0764 | 127.41 | 61.592 | 0.005963 | 95.469 | 1117.1 |  | 9540 | 127.41 | 2.0764 | 61.592 | 0.005963 | 95.469 | 1117.1 | 1021.631
9541 | 2.0769 | 127.42 | 61.592 | 0.0059645 | 95.479 | 1117.1 |  | 9541 | 127.42 | 2.0769 | 61.592 | 0.0059645 | 95.479 | 1117.1 | 1021.621
9542 | 2.0775 | 127.43 | 61.592 | 0.005966 | 95.489 | 1117.1 |  | 9542 | 127.43 | 2.0775 | 61.592 | 0.005966 | 95.489 | 1117.1 | 1021.611
9543 | 2.0781 | 127.44 | 61.591 | 0.0059675 | 95.499 | 1117.1 |  | 9543 | 127.44 | 2.0781 | 61.591 | 0.0059675 | 95.499 | 1117.1 | 1021.601
9544 | 2.0786 | 127.45 | 61.591 | 0.0059691 | 95.509 | 1117.1 |  | 9544 | 127.45 | 2.0786 | 61.591 | 0.0059691 | 95.509 | 1117.1 | 1021.591
9545 | 2.0792 | 127.46 | 61.591 | 0.0059706 | 95.519 | 1117.1 |  | 9545 | 127.46 | 2.0792 | 61.591 | 0.0059706 | 95.519 | 1117.1 | 1021.581
9546 | 2.0797 | 127.47 | 61.591 | 0.0059721 | 95.529 | 1117.1 |  | 9546 | 127.47 | 2.0797 | 61.591 | 0.0059721 | 95.529 | 1117.1 | 1021.571
9547 | 2.0803 | 127.48 | 61.591 | 0.0059736 | 95.539 | 1117.1 |  | 9547 | 127.48 | 2.0803 | 61.591 | 0.0059736 | 95.539 | 1117.1 | 1021.561
9548 | 2.0809 | 127.49 | 61.591 | 0.0059751 | 95.549 | 1117.1 |  | 9548 | 127.49 | 2.0809 | 61.591 | 0.0059751 | 95.549 | 1117.1 | 1021.551
9549 | 2.0814 | 127.5 | 61.59 | 0.0059766 | 95.559 | 1117.1 |  | 9549 | 127.5 | 2.0814 | 61.59 | 0.0059766 | 95.559 | 1117.1 | 1021.541
9550 | 2.082 | 127.51 | 61.59 | 0.0059781 | 95.569 | 1117.1 |  | 9550 | 127.51 | 2.082 | 61.59 | 0.0059781 | 95.569 | 1117.1 | 1021.531
9551 | 2.0825 | 127.52 | 61.59 | 0.0059797 | 95.579 | 1117.1 |  | 9551 | 127.52 | 2.0825 | 61.59 | 0.0059797 | 95.579 | 1117.1 | 1021.521
9552 | 2.0831 | 127.53 | 61.59 | 0.0059812 | 95.589 | 1117.1 |  | 9552 | 127.53 | 2.0831 | 61.59 | 0.0059812 | 95.589 | 1117.1 | 1021.511
9553 | 2.0837 | 127.54 | 61.59 | 0.0059827 | 95.599 | 1117.1 |  | 9553 | 127.54 | 2.0837 | 61.59 | 0.0059827 | 95.599 | 1117.1 | 1021.501
9554 | 2.0842 | 127.55 | 61.59 | 0.0059842 | 95.609 | 1117.1 |  | 9554 | 127.55 | 2.0842 | 61.59 | 0.0059842 | 95.609 | 1117.1 | 1021.491
9555 | 2.0848 | 127.56 | 61.589 | 0.0059857 | 95.619 | 1117.1 |  | 9555 | 127.56 | 2.0848 | 61.589 | 0.0059857 | 95.619 | 1117.1 | 1021.481
9556 | 2.0854 | 127.57 | 61.589 | 0.0059872 | 95.629 | 1117.1 |  | 9556 | 127.57 | 2.0854 | 61.589 | 0.0059872 | 95.629 | 1117.1 | 1021.471
9557 | 2.0859 | 127.58 | 61.589 | 0.0059888 | 95.639 | 1117.2 |  | 9557 | 127.58 | 2.0859 | 61.589 | 0.0059888 | 95.639 | 1117.2 | 1021.561
9558 | 2.0865 | 127.59 | 61.589 | 0.0059903 | 95.649 | 1117.2 |  | 9558 | 127.59 | 2.0865 | 61.589 | 0.0059903 | 95.649 | 1117.2 | 1021.551
9559 | 2.087 | 127.6 | 61.589 | 0.0059918 | 95.659 | 1117.2 |  | 9559 | 127.6 | 2.087 | 61.589 | 0.0059918 | 95.659 | 1117.2 | 1021.541
9560 | 2.0876 | 127.61 | 61.589 | 0.0059933 | 95.669 | 1117.2 |  | 9560 | 127.61 | 2.0876 | 61.589 | 0.0059933 | 95.669 | 1117.2 | 1021.531
9561 | 2.0882 | 127.62 | 61.589 | 0.0059948 | 95.679 | 1117.2 |  | 9561 | 127.62 | 2.0882 | 61.589 | 0.0059948 | 95.679 | 1117.2 | 1021.521
9562 | 2.0887 | 127.63 | 61.588 | 0.0059964 | 95.689 | 1117.2 |  | 9562 | 127.63 | 2.0887 | 61.588 | 0.0059964 | 95.689 | 1117.2 | 1021.511
9563 | 2.0893 | 127.64 | 61.588 | 0.0059979 | 95.699 | 1117.2 |  | 9563 | 127.64 | 2.0893 | 61.588 | 0.0059979 | 95.699 | 1117.2 | 1021.501
9564 | 2.0899 | 127.65 | 61.588 | 0.0059994 | 95.709 | 1117.2 |  | 9564 | 127.65 | 2.0899 | 61.588 | 0.0059994 | 95.709 | 1117.2 | 1021.491
9565 | 2.0904 | 127.66 | 61.588 | 0.0060009 | 95.719 | 1117.2 |  | 9565 | 127.66 | 2.0904 | 61.588 | 0.0060009 | 95.719 | 1117.2 | 1021.481
9566 | 2.091 | 127.67 | 61.588 | 0.0060024 | 95.729 | 1117.2 |  | 9566 | 127.67 | 2.091 | 61.588 | 0.0060024 | 95.729 | 1117.2 | 1021.471
9567 | 2.0916 | 127.68 | 61.588 | 0.006004 | 95.739 | 1117.2 |  | 9567 | 127.68 | 2.0916 | 61.588 | 0.006004 | 95.739 | 1117.2 | 1021.461
9568 | 2.0921 | 127.69 | 61.587 | 0.0060055 | 95.749 | 1117.2 |  | 9568 | 127.69 | 2.0921 | 61.587 | 0.0060055 | 95.749 | 1117.2 | 1021.451
9569 | 2.0927 | 127.7 | 61.587 | 0.006007 | 95.759 | 1117.2 |  | 9569 | 127.7 | 2.0927 | 61.587 | 0.006007 | 95.759 | 1117.2 | 1021.441
9570 | 2.0932 | 127.71 | 61.587 | 0.0060085 | 95.769 | 1117.2 |  | 9570 | 127.71 | 2.0932 | 61.587 | 0.0060085 | 95.769 | 1117.2 | 1021.431
9571 | 2.0938 | 127.72 | 61.587 | 0.00601 | 95.779 | 1117.2 |  | 9571 | 127.72 | 2.0938 | 61.587 | 0.00601 | 95.779 | 1117.2 | 1021.421
9572 | 2.0944 | 127.73 | 61.587 | 0.0060116 | 95.789 | 1117.2 |  | 9572 | 127.73 | 2.0944 | 61.587 | 0.0060116 | 95.789 | 1117.2 | 1021.411
9573 | 2.0949 | 127.74 | 61.587 | 0.0060131 | 95.799 | 1117.2 |  | 9573 | 127.74 | 2.0949 | 61.587 | 0.0060131 | 95.799 | 1117.2 | 1021.401
9574 | 2.0955 | 127.75 | 61.586 | 0.0060146 | 95.809 | 1117.2 |  | 9574 | 127.75 | 2.0955 | 61.586 | 0.0060146 | 95.809 | 1117.2 | 1021.391
9575 | 2.0961 | 127.76 | 61.586 | 0.0060161 | 95.819 | 1117.2 |  | 9575 | 127.76 | 2.0961 | 61.586 | 0.0060161 | 95.819 | 1117.2 | 1021.381
9576 | 2.0966 | 127.77 | 61.586 | 0.0060177 | 95.829 | 1117.2 |  | 9576 | 127.77 | 2.0966 | 61.586 | 0.0060177 | 95.829 | 1117.2 | 1021.371
9577 | 2.0972 | 127.78 | 61.586 | 0.0060192 | 95.839 | 1117.2 |  | 9577 | 127.78 | 2.0972 | 61.586 | 0.0060192 | 95.839 | 1117.2 | 1021.361
9578 | 2.0978 | 127.79 | 61.586 | 0.0060207 | 95.849 | 1117.2 |  | 9578 | 127.79 | 2.0978 | 61.586 | 0.0060207 | 95.849 | 1117.2 | 1021.351
9579 | 2.0983 | 127.8 | 61.586 | 0.0060222 | 95.859 | 1117.2 |  | 9579 | 127.8 | 2.0983 | 61.586 | 0.0060222 | 95.859 | 1117.2 | 1021.341
9580 | 2.0989 | 127.81 | 61.585 | 0.0060238 | 95.869 | 1117.2 |  | 9580 | 127.81 | 2.0989 | 61.585 | 0.0060238 | 95.869 | 1117.2 | 1021.331
9581 | 2.0995 | 127.82 | 61.585 | 0.0060253 | 95.879 | 1117.3 |  | 9581 | 127.82 | 2.0995 | 61.585 | 0.0060253 | 95.879 | 1117.3 | 1021.421
9582 | 2.1 | 127.83 | 61.585 | 0.0060268 | 95.889 | 1117.3 |  | 9582 | 127.83 | 2.1 | 61.585 | 0.0060268 | 95.889 | 1117.3 | 1021.411
9583 | 2.1006 | 127.84 | 61.585 | 0.0060283 | 95.899 | 1117.3 |  | 9583 | 127.84 | 2.1006 | 61.585 | 0.0060283 | 95.899 | 1117.3 | 1021.401
9584 | 2.1012 | 127.85 | 61.585 | 0.0060299 | 95.909 | 1117.3 |  | 9584 | 127.85 | 2.1012 | 61.585 | 0.0060299 | 95.909 | 1117.3 | 1021.391
9585 | 2.1017 | 127.86 | 61.585 | 0.0060314 | 95.919 | 1117.3 |  | 9585 | 127.86 | 2.1017 | 61.585 | 0.0060314 | 95.919 | 1117.3 | 1021.381
9586 | 2.1023 | 127.87 | 61.584 | 0.0060329 | 95.929 | 1117.3 |  | 9586 | 127.87 | 2.1023 | 61.584 | 0.0060329 | 95.929 | 1117.3 | 1021.371
9587 | 2.1029 | 127.88 | 61.584 | 0.0060344 | 95.939 | 1117.3 |  | 9587 | 127.88 | 2.1029 | 61.584 | 0.0060344 | 95.939 | 1117.3 | 1021.361
9588 | 2.1034 | 127.89 | 61.584 | 0.006036 | 95.949 | 1117.3 |  | 9588 | 127.89 | 2.1034 | 61.584 | 0.006036 | 95.949 | 1117.3 | 1021.351
9589 | 2.104 | 127.9 | 61.584 | 0.0060375 | 95.959 | 1117.3 |  | 9589 | 127.9 | 2.104 | 61.584 | 0.0060375 | 95.959 | 1117.3 | 1021.341
9590 | 2.1046 | 127.91 | 61.584 | 0.006039 | 95.969 | 1117.3 |  | 9590 | 127.91 | 2.1046 | 61.584 | 0.006039 | 95.969 | 1117.3 | 1021.331
9591 | 2.1051 | 127.92 | 61.584 | 0.0060406 | 95.979 | 1117.3 |  | 9591 | 127.92 | 2.1051 | 61.584 | 0.0060406 | 95.979 | 1117.3 | 1021.321
9592 | 2.1057 | 127.93 | 61.583 | 0.0060421 | 95.989 | 1117.3 |  | 9592 | 127.93 | 2.1057 | 61.583 | 0.0060421 | 95.989 | 1117.3 | 1021.311
9593 | 2.1063 | 127.94 | 61.583 | 0.0060436 | 95.999 | 1117.3 |  | 9593 | 127.94 | 2.1063 | 61.583 | 0.0060436 | 95.999 | 1117.3 | 1021.301
9594 | 2.1068 | 127.95 | 61.583 | 0.0060451 | 96.009 | 1117.3 |  | 9594 | 127.95 | 2.1068 | 61.583 | 0.0060451 | 96.009 | 1117.3 | 1021.291
9595 | 2.1074 | 127.96 | 61.583 | 0.0060467 | 96.019 | 1117.3 |  | 9595 | 127.96 | 2.1074 | 61.583 | 0.0060467 | 96.019 | 1117.3 | 1021.281
9596 | 2.108 | 127.97 | 61.583 | 0.0060482 | 96.029 | 1117.3 |  | 9596 | 127.97 | 2.108 | 61.583 | 0.0060482 | 96.029 | 1117.3 | 1021.271
9597 | 2.1085 | 127.98 | 61.583 | 0.0060497 | 96.039 | 1117.3 |  | 9597 | 127.98 | 2.1085 | 61.583 | 0.0060497 | 96.039 | 1117.3 | 1021.261
9598 | 2.1091 | 127.99 | 61.582 | 0.0060513 | 96.049 | 1117.3 |  | 9598 | 127.99 | 2.1091 | 61.582 | 0.0060513 | 96.049 | 1117.3 | 1021.251
9599 | 2.1097 | 128 | 61.582 | 0.0060528 | 96.059 | 1117.3 |  | 9599 | 128 | 2.1097 | 61.582 | 0.0060528 | 96.059 | 1117.3 | 1021.241
9600 | 2.1102 | 128.01 | 61.582 | 0.0060543 | 96.069 | 1117.3 |  | 9600 | 128.01 | 2.1102 | 61.582 | 0.0060543 | 96.069 | 1117.3 | 1021.231
9601 | 2.1108 | 128.02 | 61.582 | 0.0060559 | 96.079 | 1117.3 |  | 9601 | 128.02 | 2.1108 | 61.582 | 0.0060559 | 96.079 | 1117.3 | 1021.221
9602 | 2.1114 | 128.03 | 61.582 | 0.0060574 | 96.089 | 1117.3 |  | 9602 | 128.03 | 2.1114 | 61.582 | 0.0060574 | 96.089 | 1117.3 | 1021.211
9603 | 2.1119 | 128.04 | 61.582 | 0.0060589 | 96.099 | 1117.3 |  | 9603 | 128.04 | 2.1119 | 61.582 | 0.0060589 | 96.099 | 1117.3 | 1021.201
9604 | 2.1125 | 128.05 | 61.581 | 0.0060605 | 96.109 | 1117.3 |  | 9604 | 128.05 | 2.1125 | 61.581 | 0.0060605 | 96.109 | 1117.3 | 1021.191
9605 | 2.1131 | 128.06 | 61.581 | 0.006062 | 96.119 | 1117.4 |  | 9605 | 128.06 | 2.1131 | 61.581 | 0.006062 | 96.119 | 1117.4 | 1021.281
9606 | 2.1136 | 128.07 | 61.581 | 0.0060635 | 96.129 | 1117.4 |  | 9606 | 128.07 | 2.1136 | 61.581 | 0.0060635 | 96.129 | 1117.4 | 1021.271
9607 | 2.1142 | 128.08 | 61.581 | 0.0060651 | 96.139 | 1117.4 |  | 9607 | 128.08 | 2.1142 | 61.581 | 0.0060651 | 96.139 | 1117.4 | 1021.261
9608 | 2.1148 | 128.09 | 61.581 | 0.0060666 | 96.149 | 1117.4 |  | 9608 | 128.09 | 2.1148 | 61.581 | 0.0060666 | 96.149 | 1117.4 | 1021.251
9609 | 2.1154 | 128.1 | 61.581 | 0.0060681 | 96.159 | 1117.4 |  | 9609 | 128.1 | 2.1154 | 61.581 | 0.0060681 | 96.159 | 1117.4 | 1021.241
9610 | 2.1159 | 128.11 | 61.58 | 0.0060697 | 96.169 | 1117.4 |  | 9610 | 128.11 | 2.1159 | 61.58 | 0.0060697 | 96.169 | 1117.4 | 1021.231
9611 | 2.1165 | 128.12 | 61.58 | 0.0060712 | 96.179 | 1117.4 |  | 9611 | 128.12 | 2.1165 | 61.58 | 0.0060712 | 96.179 | 1117.4 | 1021.221
9612 | 2.1171 | 128.13 | 61.58 | 0.0060727 | 96.189 | 1117.4 |  | 9612 | 128.13 | 2.1171 | 61.58 | 0.0060727 | 96.189 | 1117.4 | 1021.211
9613 | 2.1176 | 128.14 | 61.58 | 0.0060743 | 96.199 | 1117.4 |  | 9613 | 128.14 | 2.1176 | 61.58 | 0.0060743 | 96.199 | 1117.4 | 1021.201
9614 | 2.1182 | 128.15 | 61.58 | 0.0060758 | 96.209 | 1117.4 |  | 9614 | 128.15 | 2.1182 | 61.58 | 0.0060758 | 96.209 | 1117.4 | 1021.191
9615 | 2.1188 | 128.16 | 61.58 | 0.0060773 | 96.219 | 1117.4 |  | 9615 | 128.16 | 2.1188 | 61.58 | 0.0060773 | 96.219 | 1117.4 | 1021.181
9616 | 2.1193 | 128.17 | 61.579 | 0.0060789 | 96.229 | 1117.4 |  | 9616 | 128.17 | 2.1193 | 61.579 | 0.0060789 | 96.229 | 1117.4 | 1021.171
9617 | 2.1199 | 128.18 | 61.579 | 0.0060804 | 96.239 | 1117.4 |  | 9617 | 128.18 | 2.1199 | 61.579 | 0.0060804 | 96.239 | 1117.4 | 1021.161
9618 | 2.1205 | 128.19 | 61.579 | 0.006082 | 96.249 | 1117.4 |  | 9618 | 128.19 | 2.1205 | 61.579 | 0.006082 | 96.249 | 1117.4 | 1021.151
9619 | 2.1211 | 128.2 | 61.579 | 0.0060835 | 96.259 | 1117.4 |  | 9619 | 128.2 | 2.1211 | 61.579 | 0.0060835 | 96.259 | 1117.4 | 1021.141
9620 | 2.1216 | 128.21 | 61.579 | 0.006085 | 96.269 | 1117.4 |  | 9620 | 128.21 | 2.1216 | 61.579 | 0.006085 | 96.269 | 1117.4 | 1021.131
9621 | 2.1222 | 128.22 | 61.579 | 0.0060866 | 96.279 | 1117.4 |  | 9621 | 128.22 | 2.1222 | 61.579 | 0.0060866 | 96.279 | 1117.4 | 1021.121
9622 | 2.1228 | 128.23 | 61.579 | 0.0060881 | 96.289 | 1117.4 |  | 9622 | 128.23 | 2.1228 | 61.579 | 0.0060881 | 96.289 | 1117.4 | 1021.111
9623 | 2.1233 | 128.24 | 61.578 | 0.0060896 | 96.299 | 1117.4 |  | 9623 | 128.24 | 2.1233 | 61.578 | 0.0060896 | 96.299 | 1117.4 | 1021.101
9624 | 2.1239 | 128.25 | 61.578 | 0.0060912 | 96.309 | 1117.4 |  | 9624 | 128.25 | 2.1239 | 61.578 | 0.0060912 | 96.309 | 1117.4 | 1021.091
9625 | 2.1245 | 128.26 | 61.578 | 0.0060927 | 96.319 | 1117.4 |  | 9625 | 128.26 | 2.1245 | 61.578 | 0.0060927 | 96.319 | 1117.4 | 1021.081
9626 | 2.1251 | 128.27 | 61.578 | 0.0060943 | 96.329 | 1117.4 |  | 9626 | 128.27 | 2.1251 | 61.578 | 0.0060943 | 96.329 | 1117.4 | 1021.071
9627 | 2.1256 | 128.28 | 61.578 | 0.0060958 | 96.339 | 1117.4 |  | 9627 | 128.28 | 2.1256 | 61.578 | 0.0060958 | 96.339 | 1117.4 | 1021.061
9628 | 2.1262 | 128.29 | 61.578 | 0.0060973 | 96.349 | 1117.4 |  | 9628 | 128.29 | 2.1262 | 61.578 | 0.0060973 | 96.349 | 1117.4 | 1021.051
9629 | 2.1268 | 128.3 | 61.577 | 0.0060989 | 96.359 | 1117.5 |  | 9629 | 128.3 | 2.1268 | 61.577 | 0.0060989 | 96.359 | 1117.5 | 1021.141
9630 | 2.1273 | 128.31 | 61.577 | 0.0061004 | 96.369 | 1117.5 |  | 9630 | 128.31 | 2.1273 | 61.577 | 0.0061004 | 96.369 | 1117.5 | 1021.131
9631 | 2.1279 | 128.32 | 61.577 | 0.006102 | 96.379 | 1117.5 |  | 9631 | 128.32 | 2.1279 | 61.577 | 0.006102 | 96.379 | 1117.5 | 1021.121
9632 | 2.1285 | 128.33 | 61.577 | 0.0061035 | 96.389 | 1117.5 |  | 9632 | 128.33 | 2.1285 | 61.577 | 0.0061035 | 96.389 | 1117.5 | 1021.111
9633 | 2.1291 | 128.34 | 61.577 | 0.0061051 | 96.399 | 1117.5 |  | 9633 | 128.34 | 2.1291 | 61.577 | 0.0061051 | 96.399 | 1117.5 | 1021.101
9634 | 2.1296 | 128.35 | 61.577 | 0.0061066 | 96.409 | 1117.5 |  | 9634 | 128.35 | 2.1296 | 61.577 | 0.0061066 | 96.409 | 1117.5 | 1021.091
9635 | 2.1302 | 128.36 | 61.576 | 0.0061081 | 96.419 | 1117.5 |  | 9635 | 128.36 | 2.1302 | 61.576 | 0.0061081 | 96.419 | 1117.5 | 1021.081
9636 | 2.1308 | 128.37 | 61.576 | 0.0061097 | 96.429 | 1117.5 |  | 9636 | 128.37 | 2.1308 | 61.576 | 0.0061097 | 96.429 | 1117.5 | 1021.071
9637 | 2.1314 | 128.38 | 61.576 | 0.0061112 | 96.439 | 1117.5 |  | 9637 | 128.38 | 2.1314 | 61.576 | 0.0061112 | 96.439 | 1117.5 | 1021.061
9638 | 2.1319 | 128.39 | 61.576 | 0.0061128 | 96.449 | 1117.5 |  | 9638 | 128.39 | 2.1319 | 61.576 | 0.0061128 | 96.449 | 1117.5 | 1021.051
9639 | 2.1325 | 128.4 | 61.576 | 0.0061143 | 96.459 | 1117.5 |  | 9639 | 128.4 | 2.1325 | 61.576 | 0.0061143 | 96.459 | 1117.5 | 1021.041
9640 | 2.1331 | 128.41 | 61.576 | 0.0061159 | 96.469 | 1117.5 |  | 9640 | 128.41 | 2.1331 | 61.576 | 0.0061159 | 96.469 | 1117.5 | 1021.031
9641 | 2.1336 | 128.42 | 61.575 | 0.0061174 | 96.479 | 1117.5 |  | 9641 | 128.42 | 2.1336 | 61.575 | 0.0061174 | 96.479 | 1117.5 | 1021.021
9642 | 2.1342 | 128.43 | 61.575 | 0.006119 | 96.489 | 1117.5 |  | 9642 | 128.43 | 2.1342 | 61.575 | 0.006119 | 96.489 | 1117.5 | 1021.011
9643 | 2.1348 | 128.44 | 61.575 | 0.0061205 | 96.499 | 1117.5 |  | 9643 | 128.44 | 2.1348 | 61.575 | 0.0061205 | 96.499 | 1117.5 | 1021.001
9644 | 2.1354 | 128.45 | 61.575 | 0.006122 | 96.509 | 1117.5 |  | 9644 | 128.45 | 2.1354 | 61.575 | 0.006122 | 96.509 | 1117.5 | 1020.991
9645 | 2.1359 | 128.46 | 61.575 | 0.0061236 | 96.519 | 1117.5 |  | 9645 | 128.46 | 2.1359 | 61.575 | 0.0061236 | 96.519 | 1117.5 | 1020.981
9646 | 2.1365 | 128.47 | 61.575 | 0.0061251 | 96.529 | 1117.5 |  | 9646 | 128.47 | 2.1365 | 61.575 | 0.0061251 | 96.529 | 1117.5 | 1020.971
9647 | 2.1371 | 128.48 | 61.574 | 0.0061267 | 96.539 | 1117.5 |  | 9647 | 128.48 | 2.1371 | 61.574 | 0.0061267 | 96.539 | 1117.5 | 1020.961
9648 | 2.1377 | 128.49 | 61.574 | 0.0061282 | 96.549 | 1117.5 |  | 9648 | 128.49 | 2.1377 | 61.574 | 0.0061282 | 96.549 | 1117.5 | 1020.951
9649 | 2.1382 | 128.5 | 61.574 | 0.0061298 | 96.559 | 1117.5 |  | 9649 | 128.5 | 2.1382 | 61.574 | 0.0061298 | 96.559 | 1117.5 | 1020.941
9650 | 2.1388 | 128.51 | 61.574 | 0.0061313 | 96.569 | 1117.5 |  | 9650 | 128.51 | 2.1388 | 61.574 | 0.0061313 | 96.569 | 1117.5 | 1020.931
9651 | 2.1394 | 128.52 | 61.574 | 0.0061329 | 96.579 | 1117.5 |  | 9651 | 128.52 | 2.1394 | 61.574 | 0.0061329 | 96.579 | 1117.5 | 1020.921
9652 | 2.14 | 128.53 | 61.574 | 0.0061344 | 96.589 | 1117.6 |  | 9652 | 128.53 | 2.14 | 61.574 | 0.0061344 | 96.589 | 1117.6 | 1021.011
9653 | 2.1405 | 128.54 | 61.573 | 0.006136 | 96.599 | 1117.6 |  | 9653 | 128.54 | 2.1405 | 61.573 | 0.006136 | 96.599 | 1117.6 | 1021.001
9654 | 2.1411 | 128.55 | 61.573 | 0.0061375 | 96.609 | 1117.6 |  | 9654 | 128.55 | 2.1411 | 61.573 | 0.0061375 | 96.609 | 1117.6 | 1020.991
9655 | 2.1417 | 128.56 | 61.573 | 0.0061391 | 96.619 | 1117.6 |  | 9655 | 128.56 | 2.1417 | 61.573 | 0.0061391 | 96.619 | 1117.6 | 1020.981
9656 | 2.1423 | 128.57 | 61.573 | 0.0061406 | 96.629 | 1117.6 |  | 9656 | 128.57 | 2.1423 | 61.573 | 0.0061406 | 96.629 | 1117.6 | 1020.971
9657 | 2.1428 | 128.58 | 61.573 | 0.0061422 | 96.639 | 1117.6 |  | 9657 | 128.58 | 2.1428 | 61.573 | 0.0061422 | 96.639 | 1117.6 | 1020.961
9658 | 2.1434 | 128.59 | 61.573 | 0.0061437 | 96.649 | 1117.6 |  | 9658 | 128.59 | 2.1434 | 61.573 | 0.0061437 | 96.649 | 1117.6 | 1020.951
9659 | 2.144 | 128.6 | 61.572 | 0.0061453 | 96.659 | 1117.6 |  | 9659 | 128.6 | 2.144 | 61.572 | 0.0061453 | 96.659 | 1117.6 | 1020.941
9660 | 2.1446 | 128.61 | 61.572 | 0.0061468 | 96.669 | 1117.6 |  | 9660 | 128.61 | 2.1446 | 61.572 | 0.0061468 | 96.669 | 1117.6 | 1020.931
9661 | 2.1451 | 128.62 | 61.572 | 0.0061484 | 96.679 | 1117.6 |  | 9661 | 128.62 | 2.1451 | 61.572 | 0.0061484 | 96.679 | 1117.6 | 1020.921
9662 | 2.1457 | 128.63 | 61.572 | 0.0061499 | 96.689 | 1117.6 |  | 9662 | 128.63 | 2.1457 | 61.572 | 0.0061499 | 96.689 | 1117.6 | 1020.911
9663 | 2.1463 | 128.64 | 61.572 | 0.0061515 | 96.699 | 1117.6 |  | 9663 | 128.64 | 2.1463 | 61.572 | 0.0061515 | 96.699 | 1117.6 | 1020.901
9664 | 2.1469 | 128.65 | 61.572 | 0.006153 | 96.709 | 1117.6 |  | 9664 | 128.65 | 2.1469 | 61.572 | 0.006153 | 96.709 | 1117.6 | 1020.891
9665 | 2.1474 | 128.66 | 61.571 | 0.0061546 | 96.719 | 1117.6 |  | 9665 | 128.66 | 2.1474 | 61.571 | 0.0061546 | 96.719 | 1117.6 | 1020.881
9666 | 2.148 | 128.67 | 61.571 | 0.0061561 | 96.729 | 1117.6 |  | 9666 | 128.67 | 2.148 | 61.571 | 0.0061561 | 96.729 | 1117.6 | 1020.871
9667 | 2.1486 | 128.68 | 61.571 | 0.0061577 | 96.739 | 1117.6 |  | 9667 | 128.68 | 2.1486 | 61.571 | 0.0061577 | 96.739 | 1117.6 | 1020.861
9668 | 2.1492 | 128.69 | 61.571 | 0.0061593 | 96.749 | 1117.6 |  | 9668 | 128.69 | 2.1492 | 61.571 | 0.0061593 | 96.749 | 1117.6 | 1020.851
9669 | 2.1498 | 128.7 | 61.571 | 0.0061608 | 96.759 | 1117.6 |  | 9669 | 128.7 | 2.1498 | 61.571 | 0.0061608 | 96.759 | 1117.6 | 1020.841
9670 | 2.1503 | 128.71 | 61.571 | 0.0061624 | 96.769 | 1117.6 |  | 9670 | 128.71 | 2.1503 | 61.571 | 0.0061624 | 96.769 | 1117.6 | 1020.831
9671 | 2.1509 | 128.72 | 61.57 | 0.0061639 | 96.779 | 1117.6 |  | 9671 | 128.72 | 2.1509 | 61.57 | 0.0061639 | 96.779 | 1117.6 | 1020.821
9672 | 2.1515 | 128.73 | 61.57 | 0.0061655 | 96.789 | 1117.6 |  | 9672 | 128.73 | 2.1515 | 61.57 | 0.0061655 | 96.789 | 1117.6 | 1020.811
9673 | 2.1521 | 128.74 | 61.57 | 0.006167 | 96.799 | 1117.6 |  | 9673 | 128.74 | 2.1521 | 61.57 | 0.006167 | 96.799 | 1117.6 | 1020.801
9674 | 2.1526 | 128.75 | 61.57 | 0.0061686 | 96.809 | 1117.6 |  | 9674 | 128.75 | 2.1526 | 61.57 | 0.0061686 | 96.809 | 1117.6 | 1020.791
9675 | 2.1532 | 128.76 | 61.57 | 0.0061701 | 96.819 | 1117.6 |  | 9675 | 128.76 | 2.1532 | 61.57 | 0.0061701 | 96.819 | 1117.6 | 1020.781
9676 | 2.1538 | 128.77 | 61.57 | 0.0061717 | 96.829 | 1117.7 |  | 9676 | 128.77 | 2.1538 | 61.57 | 0.0061717 | 96.829 | 1117.7 | 1020.871
9677 | 2.1544 | 128.78 | 61.569 | 0.0061733 | 96.839 | 1117.7 |  | 9677 | 128.78 | 2.1544 | 61.569 | 0.0061733 | 96.839 | 1117.7 | 1020.861
9678 | 2.155 | 128.79 | 61.569 | 0.0061748 | 96.849 | 1117.7 |  | 9678 | 128.79 | 2.155 | 61.569 | 0.0061748 | 96.849 | 1117.7 | 1020.851
9679 | 2.1555 | 128.8 | 61.569 | 0.0061764 | 96.859 | 1117.7 |  | 9679 | 128.8 | 2.1555 | 61.569 | 0.0061764 | 96.859 | 1117.7 | 1020.841
9680 | 2.1561 | 128.81 | 61.569 | 0.0061779 | 96.869 | 1117.7 |  | 9680 | 128.81 | 2.1561 | 61.569 | 0.0061779 | 96.869 | 1117.7 | 1020.831
9681 | 2.1567 | 128.82 | 61.569 | 0.0061795 | 96.879 | 1117.7 |  | 9681 | 128.82 | 2.1567 | 61.569 | 0.0061795 | 96.879 | 1117.7 | 1020.821
9682 | 2.1573 | 128.83 | 61.569 | 0.006181 | 96.889 | 1117.7 |  | 9682 | 128.83 | 2.1573 | 61.569 | 0.006181 | 96.889 | 1117.7 | 1020.811
9683 | 2.1579 | 128.84 | 61.568 | 0.0061826 | 96.899 | 1117.7 |  | 9683 | 128.84 | 2.1579 | 61.568 | 0.0061826 | 96.899 | 1117.7 | 1020.801
9684 | 2.1584 | 128.85 | 61.568 | 0.0061842 | 96.909 | 1117.7 |  | 9684 | 128.85 | 2.1584 | 61.568 | 0.0061842 | 96.909 | 1117.7 | 1020.791
9685 | 2.159 | 128.86 | 61.568 | 0.0061857 | 96.919 | 1117.7 |  | 9685 | 128.86 | 2.159 | 61.568 | 0.0061857 | 96.919 | 1117.7 | 1020.781
9686 | 2.1596 | 128.87 | 61.568 | 0.0061873 | 96.929 | 1117.7 |  | 9686 | 128.87 | 2.1596 | 61.568 | 0.0061873 | 96.929 | 1117.7 | 1020.771
9687 | 2.1602 | 128.88 | 61.568 | 0.0061888 | 96.939 | 1117.7 |  | 9687 | 128.88 | 2.1602 | 61.568 | 0.0061888 | 96.939 | 1117.7 | 1020.761
9688 | 2.1608 | 128.89 | 61.568 | 0.0061904 | 96.949 | 1117.7 |  | 9688 | 128.89 | 2.1608 | 61.568 | 0.0061904 | 96.949 | 1117.7 | 1020.751
9689 | 2.1613 | 128.9 | 61.567 | 0.006192 | 96.959 | 1117.7 |  | 9689 | 128.9 | 2.1613 | 61.567 | 0.006192 | 96.959 | 1117.7 | 1020.741
9690 | 2.1619 | 128.91 | 61.567 | 0.0061935 | 96.969 | 1117.7 |  | 9690 | 128.91 | 2.1619 | 61.567 | 0.0061935 | 96.969 | 1117.7 | 1020.731
9691 | 2.1625 | 128.92 | 61.567 | 0.0061951 | 96.979 | 1117.7 |  | 9691 | 128.92 | 2.1625 | 61.567 | 0.0061951 | 96.979 | 1117.7 | 1020.721
9692 | 2.1631 | 128.93 | 61.567 | 0.0061966 | 96.989 | 1117.7 |  | 9692 | 128.93 | 2.1631 | 61.567 | 0.0061966 | 96.989 | 1117.7 | 1020.711
9693 | 2.1637 | 128.94 | 61.567 | 0.0061982 | 96.999 | 1117.7 |  | 9693 | 128.94 | 2.1637 | 61.567 | 0.0061982 | 96.999 | 1117.7 | 1020.701
9694 | 2.1642 | 128.95 | 61.567 | 0.0061998 | 97.009 | 1117.7 |  | 9694 | 128.95 | 2.1642 | 61.567 | 0.0061998 | 97.009 | 1117.7 | 1020.691
9695 | 2.1648 | 128.96 | 61.566 | 0.0062013 | 97.019 | 1117.7 |  | 9695 | 128.96 | 2.1648 | 61.566 | 0.0062013 | 97.019 | 1117.7 | 1020.681
9696 | 2.1654 | 128.97 | 61.566 | 0.0062029 | 97.029 | 1117.7 |  | 9696 | 128.97 | 2.1654 | 61.566 | 0.0062029 | 97.029 | 1117.7 | 1020.671
9697 | 2.166 | 128.98 | 61.566 | 0.0062045 | 97.039 | 1117.7 |  | 9697 | 128.98 | 2.166 | 61.566 | 0.0062045 | 97.039 | 1117.7 | 1020.661
9698 | 2.1666 | 128.99 | 61.566 | 0.006206 | 97.049 | 1117.7 |  | 9698 | 128.99 | 2.1666 | 61.566 | 0.006206 | 97.049 | 1117.7 | 1020.651
9699 | 2.1671 | 129 | 61.566 | 0.0062076 | 97.059 | 1117.7 |  | 9699 | 129 | 2.1671 | 61.566 | 0.0062076 | 97.059 | 1117.7 | 1020.641
9700 | 2.1677 | 129.01 | 61.566 | 0.0062092 | 97.069 | 1117.8 |  | 9700 | 129.01 | 2.1677 | 61.566 | 0.0062092 | 97.069 | 1117.8 | 1020.731
9701 | 2.1683 | 129.02 | 61.565 | 0.0062107 | 97.079 | 1117.8 |  | 9701 | 129.02 | 2.1683 | 61.565 | 0.0062107 | 97.079 | 1117.8 | 1020.721
9702 | 2.1689 | 129.03 | 61.565 | 0.0062123 | 97.089 | 1117.8 |  | 9702 | 129.03 | 2.1689 | 61.565 | 0.0062123 | 97.089 | 1117.8 | 1020.711
9703 | 2.1695 | 129.04 | 61.565 | 0.0062139 | 97.099 | 1117.8 |  | 9703 | 129.04 | 2.1695 | 61.565 | 0.0062139 | 97.099 | 1117.8 | 1020.701
9704 | 2.17 | 129.05 | 61.565 | 0.0062154 | 97.109 | 1117.8 |  | 9704 | 129.05 | 2.17 | 61.565 | 0.0062154 | 97.109 | 1117.8 | 1020.691
9705 | 2.1706 | 129.06 | 61.565 | 0.006217 | 97.119 | 1117.8 |  | 9705 | 129.06 | 2.1706 | 61.565 | 0.006217 | 97.119 | 1117.8 | 1020.681
9706 | 2.1712 | 129.07 | 61.565 | 0.0062186 | 97.129 | 1117.8 |  | 9706 | 129.07 | 2.1712 | 61.565 | 0.0062186 | 97.129 | 1117.8 | 1020.671
9707 | 2.1718 | 129.08 | 61.564 | 0.0062201 | 97.139 | 1117.8 |  | 9707 | 129.08 | 2.1718 | 61.564 | 0.0062201 | 97.139 | 1117.8 | 1020.661
9708 | 2.1724 | 129.09 | 61.564 | 0.0062217 | 97.149 | 1117.8 |  | 9708 | 129.09 | 2.1724 | 61.564 | 0.0062217 | 97.149 | 1117.8 | 1020.651
9709 | 2.173 | 129.1 | 61.564 | 0.0062233 | 97.159 | 1117.8 |  | 9709 | 129.1 | 2.173 | 61.564 | 0.0062233 | 97.159 | 1117.8 | 1020.641
9710 | 2.1735 | 129.11 | 61.564 | 0.0062248 | 97.169 | 1117.8 |  | 9710 | 129.11 | 2.1735 | 61.564 | 0.0062248 | 97.169 | 1117.8 | 1020.631
9711 | 2.1741 | 129.12 | 61.564 | 0.0062264 | 97.179 | 1117.8 |  | 9711 | 129.12 | 2.1741 | 61.564 | 0.0062264 | 97.179 | 1117.8 | 1020.621
9712 | 2.1747 | 129.13 | 61.564 | 0.006228 | 97.189 | 1117.8 |  | 9712 | 129.13 | 2.1747 | 61.564 | 0.006228 | 97.189 | 1117.8 | 1020.611
9713 | 2.1753 | 129.14 | 61.563 | 0.0062295 | 97.199 | 1117.8 |  | 9713 | 129.14 | 2.1753 | 61.563 | 0.0062295 | 97.199 | 1117.8 | 1020.601
9714 | 2.1759 | 129.15 | 61.563 | 0.0062311 | 97.209 | 1117.8 |  | 9714 | 129.15 | 2.1759 | 61.563 | 0.0062311 | 97.209 | 1117.8 | 1020.591
9715 | 2.1765 | 129.16 | 61.563 | 0.0062327 | 97.219 | 1117.8 |  | 9715 | 129.16 | 2.1765 | 61.563 | 0.0062327 | 97.219 | 1117.8 | 1020.581
9716 | 2.177 | 129.17 | 61.563 | 0.0062342 | 97.229 | 1117.8 |  | 9716 | 129.17 | 2.177 | 61.563 | 0.0062342 | 97.229 | 1117.8 | 1020.571
9717 | 2.1776 | 129.18 | 61.563 | 0.0062358 | 97.239 | 1117.8 |  | 9717 | 129.18 | 2.1776 | 61.563 | 0.0062358 | 97.239 | 1117.8 | 1020.561
9718 | 2.1782 | 129.19 | 61.563 | 0.0062374 | 97.249 | 1117.8 |  | 9718 | 129.19 | 2.1782 | 61.563 | 0.0062374 | 97.249 | 1117.8 | 1020.551
9719 | 2.1788 | 129.2 | 61.562 | 0.0062389 | 97.259 | 1117.8 |  | 9719 | 129.2 | 2.1788 | 61.562 | 0.0062389 | 97.259 | 1117.8 | 1020.541
9720 | 2.1794 | 129.21 | 61.562 | 0.0062405 | 97.269 | 1117.8 |  | 9720 | 129.21 | 2.1794 | 61.562 | 0.0062405 | 97.269 | 1117.8 | 1020.531
9721 | 2.18 | 129.22 | 61.562 | 0.0062421 | 97.279 | 1117.8 |  | 9721 | 129.22 | 2.18 | 61.562 | 0.0062421 | 97.279 | 1117.8 | 1020.521
9722 | 2.1805 | 129.23 | 61.562 | 0.0062437 | 97.289 | 1117.8 |  | 9722 | 129.23 | 2.1805 | 61.562 | 0.0062437 | 97.289 | 1117.8 | 1020.511
9723 | 2.1811 | 129.24 | 61.562 | 0.0062452 | 97.299 | 1117.8 |  | 9723 | 129.24 | 2.1811 | 61.562 | 0.0062452 | 97.299 | 1117.8 | 1020.501
9724 | 2.1817 | 129.25 | 61.562 | 0.0062468 | 97.309 | 1117.9 |  | 9724 | 129.25 | 2.1817 | 61.562 | 0.0062468 | 97.309 | 1117.9 | 1020.591
9725 | 2.1823 | 129.26 | 61.561 | 0.0062484 | 97.319 | 1117.9 |  | 9725 | 129.26 | 2.1823 | 61.561 | 0.0062484 | 97.319 | 1117.9 | 1020.581
9726 | 2.1829 | 129.27 | 61.561 | 0.00625 | 97.329 | 1117.9 |  | 9726 | 129.27 | 2.1829 | 61.561 | 0.00625 | 97.329 | 1117.9 | 1020.571
9727 | 2.1835 | 129.28 | 61.561 | 0.0062515 | 97.339 | 1117.9 |  | 9727 | 129.28 | 2.1835 | 61.561 | 0.0062515 | 97.339 | 1117.9 | 1020.561
9728 | 2.1841 | 129.29 | 61.561 | 0.0062531 | 97.349 | 1117.9 |  | 9728 | 129.29 | 2.1841 | 61.561 | 0.0062531 | 97.349 | 1117.9 | 1020.551
9729 | 2.1846 | 129.3 | 61.561 | 0.0062547 | 97.359 | 1117.9 |  | 9729 | 129.3 | 2.1846 | 61.561 | 0.0062547 | 97.359 | 1117.9 | 1020.541
9730 | 2.1852 | 129.31 | 61.561 | 0.0062563 | 97.369 | 1117.9 |  | 9730 | 129.31 | 2.1852 | 61.561 | 0.0062563 | 97.369 | 1117.9 | 1020.531
9731 | 2.1858 | 129.32 | 61.561 | 0.0062578 | 97.379 | 1117.9 |  | 9731 | 129.32 | 2.1858 | 61.561 | 0.0062578 | 97.379 | 1117.9 | 1020.521
9732 | 2.1864 | 129.33 | 61.56 | 0.0062594 | 97.389 | 1117.9 |  | 9732 | 129.33 | 2.1864 | 61.56 | 0.0062594 | 97.389 | 1117.9 | 1020.511
9733 | 2.187 | 129.34 | 61.56 | 0.006261 | 97.399 | 1117.9 |  | 9733 | 129.34 | 2.187 | 61.56 | 0.006261 | 97.399 | 1117.9 | 1020.501
9734 | 2.1876 | 129.35 | 61.56 | 0.0062626 | 97.409 | 1117.9 |  | 9734 | 129.35 | 2.1876 | 61.56 | 0.0062626 | 97.409 | 1117.9 | 1020.491
9735 | 2.1882 | 129.36 | 61.56 | 0.0062641 | 97.419 | 1117.9 |  | 9735 | 129.36 | 2.1882 | 61.56 | 0.0062641 | 97.419 | 1117.9 | 1020.481
9736 | 2.1887 | 129.37 | 61.56 | 0.0062657 | 97.429 | 1117.9 |  | 9736 | 129.37 | 2.1887 | 61.56 | 0.0062657 | 97.429 | 1117.9 | 1020.471
9737 | 2.1893 | 129.38 | 61.56 | 0.0062673 | 97.439 | 1117.9 |  | 9737 | 129.38 | 2.1893 | 61.56 | 0.0062673 | 97.439 | 1117.9 | 1020.461
9738 | 2.1899 | 129.39 | 61.559 | 0.0062689 | 97.449 | 1117.9 |  | 9738 | 129.39 | 2.1899 | 61.559 | 0.0062689 | 97.449 | 1117.9 | 1020.451
9739 | 2.1905 | 129.4 | 61.559 | 0.0062704 | 97.459 | 1117.9 |  | 9739 | 129.4 | 2.1905 | 61.559 | 0.0062704 | 97.459 | 1117.9 | 1020.441
9740 | 2.1911 | 129.41 | 61.559 | 0.006272 | 97.469 | 1117.9 |  | 9740 | 129.41 | 2.1911 | 61.559 | 0.006272 | 97.469 | 1117.9 | 1020.431
9741 | 2.1917 | 129.42 | 61.559 | 0.0062736 | 97.479 | 1117.9 |  | 9741 | 129.42 | 2.1917 | 61.559 | 0.0062736 | 97.479 | 1117.9 | 1020.421
9742 | 2.1923 | 129.43 | 61.559 | 0.0062752 | 97.489 | 1117.9 |  | 9742 | 129.43 | 2.1923 | 61.559 | 0.0062752 | 97.489 | 1117.9 | 1020.411
9743 | 2.1928 | 129.44 | 61.559 | 0.0062768 | 97.499 | 1117.9 |  | 9743 | 129.44 | 2.1928 | 61.559 | 0.0062768 | 97.499 | 1117.9 | 1020.401
9744 | 2.1934 | 129.45 | 61.558 | 0.0062783 | 97.509 | 1117.9 |  | 9744 | 129.45 | 2.1934 | 61.558 | 0.0062783 | 97.509 | 1117.9 | 1020.391
9745 | 2.194 | 129.46 | 61.558 | 0.0062799 | 97.519 | 1117.9 |  | 9745 | 129.46 | 2.194 | 61.558 | 0.0062799 | 97.519 | 1117.9 | 1020.381
9746 | 2.1946 | 129.47 | 61.558 | 0.0062815 | 97.529 | 1117.9 |  | 9746 | 129.47 | 2.1946 | 61.558 | 0.0062815 | 97.529 | 1117.9 | 1020.371
9747 | 2.1952 | 129.48 | 61.558 | 0.0062831 | 97.539 | 1117.9 |  | 9747 | 129.48 | 2.1952 | 61.558 | 0.0062831 | 97.539 | 1117.9 | 1020.361
9748 | 2.1958 | 129.49 | 61.558 | 0.0062847 | 97.549 | 1118 |  | 9748 | 129.49 | 2.1958 | 61.558 | 0.0062847 | 97.549 | 1118 | 1020.451
9749 | 2.1964 | 129.5 | 61.558 | 0.0062862 | 97.559 | 1118 |  | 9749 | 129.5 | 2.1964 | 61.558 | 0.0062862 | 97.559 | 1118 | 1020.441
9750 | 2.197 | 129.51 | 61.557 | 0.0062878 | 97.569 | 1118 |  | 9750 | 129.51 | 2.197 | 61.557 | 0.0062878 | 97.569 | 1118 | 1020.431
9751 | 2.1975 | 129.52 | 61.557 | 0.0062894 | 97.579 | 1118 |  | 9751 | 129.52 | 2.1975 | 61.557 | 0.0062894 | 97.579 | 1118 | 1020.421
9752 | 2.1981 | 129.53 | 61.557 | 0.006291 | 97.589 | 1118 |  | 9752 | 129.53 | 2.1981 | 61.557 | 0.006291 | 97.589 | 1118 | 1020.411
9753 | 2.1987 | 129.54 | 61.557 | 0.0062926 | 97.599 | 1118 |  | 9753 | 129.54 | 2.1987 | 61.557 | 0.0062926 | 97.599 | 1118 | 1020.401
9754 | 2.1993 | 129.55 | 61.557 | 0.0062941 | 97.609 | 1118 |  | 9754 | 129.55 | 2.1993 | 61.557 | 0.0062941 | 97.609 | 1118 | 1020.391
9755 | 2.1999 | 129.56 | 61.557 | 0.0062957 | 97.619 | 1118 |  | 9755 | 129.56 | 2.1999 | 61.557 | 0.0062957 | 97.619 | 1118 | 1020.381
9756 | 2.2005 | 129.57 | 61.556 | 0.0062973 | 97.629 | 1118 |  | 9756 | 129.57 | 2.2005 | 61.556 | 0.0062973 | 97.629 | 1118 | 1020.371
9757 | 2.2011 | 129.58 | 61.556 | 0.0062989 | 97.639 | 1118 |  | 9757 | 129.58 | 2.2011 | 61.556 | 0.0062989 | 97.639 | 1118 | 1020.361
9758 | 2.2017 | 129.59 | 61.556 | 0.0063005 | 97.649 | 1118 |  | 9758 | 129.59 | 2.2017 | 61.556 | 0.0063005 | 97.649 | 1118 | 1020.351
9759 | 2.2023 | 129.6 | 61.556 | 0.0063021 | 97.659 | 1118 |  | 9759 | 129.6 | 2.2023 | 61.556 | 0.0063021 | 97.659 | 1118 | 1020.341
9760 | 2.2028 | 129.61 | 61.556 | 0.0063036 | 97.669 | 1118 |  | 9760 | 129.61 | 2.2028 | 61.556 | 0.0063036 | 97.669 | 1118 | 1020.331
9761 | 2.2034 | 129.62 | 61.556 | 0.0063052 | 97.679 | 1118 |  | 9761 | 129.62 | 2.2034 | 61.556 | 0.0063052 | 97.679 | 1118 | 1020.321
9762 | 2.204 | 129.63 | 61.555 | 0.0063068 | 97.689 | 1118 |  | 9762 | 129.63 | 2.204 | 61.555 | 0.0063068 | 97.689 | 1118 | 1020.311
9763 | 2.2046 | 129.64 | 61.555 | 0.0063084 | 97.699 | 1118 |  | 9763 | 129.64 | 2.2046 | 61.555 | 0.0063084 | 97.699 | 1118 | 1020.301
9764 | 2.2052 | 129.65 | 61.555 | 0.00631 | 97.709 | 1118 |  | 9764 | 129.65 | 2.2052 | 61.555 | 0.00631 | 97.709 | 1118 | 1020.291
9765 | 2.2058 | 129.66 | 61.555 | 0.0063116 | 97.719 | 1118 |  | 9765 | 129.66 | 2.2058 | 61.555 | 0.0063116 | 97.719 | 1118 | 1020.281
9766 | 2.2064 | 129.67 | 61.555 | 0.0063132 | 97.729 | 1118 |  | 9766 | 129.67 | 2.2064 | 61.555 | 0.0063132 | 97.729 | 1118 | 1020.271
9767 | 2.207 | 129.68 | 61.555 | 0.0063147 | 97.739 | 1118 |  | 9767 | 129.68 | 2.207 | 61.555 | 0.0063147 | 97.739 | 1118 | 1020.261
9768 | 2.2076 | 129.69 | 61.554 | 0.0063163 | 97.749 | 1118 |  | 9768 | 129.69 | 2.2076 | 61.554 | 0.0063163 | 97.749 | 1118 | 1020.251
9769 | 2.2082 | 129.7 | 61.554 | 0.0063179 | 97.759 | 1118 |  | 9769 | 129.7 | 2.2082 | 61.554 | 0.0063179 | 97.759 | 1118 | 1020.241
9770 | 2.2087 | 129.71 | 61.554 | 0.0063195 | 97.769 | 1118 |  | 9770 | 129.71 | 2.2087 | 61.554 | 0.0063195 | 97.769 | 1118 | 1020.231
9771 | 2.2093 | 129.72 | 61.554 | 0.0063211 | 97.779 | 1118.1 |  | 9771 | 129.72 | 2.2093 | 61.554 | 0.0063211 | 97.779 | 1118.1 | 1020.321
9772 | 2.2099 | 129.73 | 61.554 | 0.0063227 | 97.789 | 1118.1 |  | 9772 | 129.73 | 2.2099 | 61.554 | 0.0063227 | 97.789 | 1118.1 | 1020.311
9773 | 2.2105 | 129.74 | 61.554 | 0.0063243 | 97.799 | 1118.1 |  | 9773 | 129.74 | 2.2105 | 61.554 | 0.0063243 | 97.799 | 1118.1 | 1020.301
9774 | 2.2111 | 129.75 | 61.553 | 0.0063259 | 97.809 | 1118.1 |  | 9774 | 129.75 | 2.2111 | 61.553 | 0.0063259 | 97.809 | 1118.1 | 1020.291
9775 | 2.2117 | 129.76 | 61.553 | 0.0063275 | 97.819 | 1118.1 |  | 9775 | 129.76 | 2.2117 | 61.553 | 0.0063275 | 97.819 | 1118.1 | 1020.281
9776 | 2.2123 | 129.77 | 61.553 | 0.006329 | 97.829 | 1118.1 |  | 9776 | 129.77 | 2.2123 | 61.553 | 0.006329 | 97.829 | 1118.1 | 1020.271
9777 | 2.2129 | 129.78 | 61.553 | 0.0063306 | 97.839 | 1118.1 |  | 9777 | 129.78 | 2.2129 | 61.553 | 0.0063306 | 97.839 | 1118.1 | 1020.261
9778 | 2.2135 | 129.79 | 61.553 | 0.0063322 | 97.849 | 1118.1 |  | 9778 | 129.79 | 2.2135 | 61.553 | 0.0063322 | 97.849 | 1118.1 | 1020.251
9779 | 2.2141 | 129.8 | 61.553 | 0.0063338 | 97.859 | 1118.1 |  | 9779 | 129.8 | 2.2141 | 61.553 | 0.0063338 | 97.859 | 1118.1 | 1020.241
9780 | 2.2147 | 129.81 | 61.552 | 0.0063354 | 97.869 | 1118.1 |  | 9780 | 129.81 | 2.2147 | 61.552 | 0.0063354 | 97.869 | 1118.1 | 1020.231
9781 | 2.2153 | 129.82 | 61.552 | 0.006337 | 97.879 | 1118.1 |  | 9781 | 129.82 | 2.2153 | 61.552 | 0.006337 | 97.879 | 1118.1 | 1020.221
9782 | 2.2158 | 129.83 | 61.552 | 0.0063386 | 97.889 | 1118.1 |  | 9782 | 129.83 | 2.2158 | 61.552 | 0.0063386 | 97.889 | 1118.1 | 1020.211
9783 | 2.2164 | 129.84 | 61.552 | 0.0063402 | 97.899 | 1118.1 |  | 9783 | 129.84 | 2.2164 | 61.552 | 0.0063402 | 97.899 | 1118.1 | 1020.201
9784 | 2.217 | 129.85 | 61.552 | 0.0063418 | 97.909 | 1118.1 |  | 9784 | 129.85 | 2.217 | 61.552 | 0.0063418 | 97.909 | 1118.1 | 1020.191
9785 | 2.2176 | 129.86 | 61.552 | 0.0063434 | 97.919 | 1118.1 |  | 9785 | 129.86 | 2.2176 | 61.552 | 0.0063434 | 97.919 | 1118.1 | 1020.181
9786 | 2.2182 | 129.87 | 61.551 | 0.006345 | 97.929 | 1118.1 |  | 9786 | 129.87 | 2.2182 | 61.551 | 0.006345 | 97.929 | 1118.1 | 1020.171
9787 | 2.2188 | 129.88 | 61.551 | 0.0063466 | 97.939 | 1118.1 |  | 9787 | 129.88 | 2.2188 | 61.551 | 0.0063466 | 97.939 | 1118.1 | 1020.161
9788 | 2.2194 | 129.89 | 61.551 | 0.0063482 | 97.949 | 1118.1 |  | 9788 | 129.89 | 2.2194 | 61.551 | 0.0063482 | 97.949 | 1118.1 | 1020.151
9789 | 2.22 | 129.9 | 61.551 | 0.0063497 | 97.959 | 1118.1 |  | 9789 | 129.9 | 2.22 | 61.551 | 0.0063497 | 97.959 | 1118.1 | 1020.141
9790 | 2.2206 | 129.91 | 61.551 | 0.0063513 | 97.969 | 1118.1 |  | 9790 | 129.91 | 2.2206 | 61.551 | 0.0063513 | 97.969 | 1118.1 | 1020.131
9791 | 2.2212 | 129.92 | 61.551 | 0.0063529 | 97.979 | 1118.1 |  | 9791 | 129.92 | 2.2212 | 61.551 | 0.0063529 | 97.979 | 1118.1 | 1020.121
9792 | 2.2218 | 129.93 | 61.55 | 0.0063545 | 97.989 | 1118.1 |  | 9792 | 129.93 | 2.2218 | 61.55 | 0.0063545 | 97.989 | 1118.1 | 1020.111
9793 | 2.2224 | 129.94 | 61.55 | 0.0063561 | 97.999 | 1118.1 |  | 9793 | 129.94 | 2.2224 | 61.55 | 0.0063561 | 97.999 | 1118.1 | 1020.101
9794 | 2.223 | 129.95 | 61.55 | 0.0063577 | 98.009 | 1118.1 |  | 9794 | 129.95 | 2.223 | 61.55 | 0.0063577 | 98.009 | 1118.1 | 1020.091
9795 | 2.2236 | 129.96 | 61.55 | 0.0063593 | 98.019 | 1118.2 |  | 9795 | 129.96 | 2.2236 | 61.55 | 0.0063593 | 98.019 | 1118.2 | 1020.181
9796 | 2.2242 | 129.97 | 61.55 | 0.0063609 | 98.029 | 1118.2 |  | 9796 | 129.97 | 2.2242 | 61.55 | 0.0063609 | 98.029 | 1118.2 | 1020.171
9797 | 2.2247 | 129.98 | 61.55 | 0.0063625 | 98.039 | 1118.2 |  | 9797 | 129.98 | 2.2247 | 61.55 | 0.0063625 | 98.039 | 1118.2 | 1020.161
9798 | 2.2253 | 129.99 | 61.549 | 0.0063641 | 98.049 | 1118.2 |  | 9798 | 129.99 | 2.2253 | 61.549 | 0.0063641 | 98.049 | 1118.2 | 1020.151
9799 | 2.2259 | 130 | 61.549 | 0.0063657 | 98.059 | 1118.2 |  | 9799 | 130 | 2.2259 | 61.549 | 0.0063657 | 98.059 | 1118.2 | 1020.141
9800 | 2.2265 | 130.01 | 61.549 | 0.0063673 | 98.069 | 1118.2 |  | 9800 | 130.01 | 2.2265 | 61.549 | 0.0063673 | 98.069 | 1118.2 | 1020.131
9801 | 2.2271 | 130.02 | 61.549 | 0.0063689 | 98.079 | 1118.2 |  | 9801 | 130.02 | 2.2271 | 61.549 | 0.0063689 | 98.079 | 1118.2 | 1020.121
9802 | 2.2277 | 130.03 | 61.549 | 0.0063705 | 98.089 | 1118.2 |  | 9802 | 130.03 | 2.2277 | 61.549 | 0.0063705 | 98.089 | 1118.2 | 1020.111
9803 | 2.2283 | 130.04 | 61.549 | 0.0063721 | 98.099 | 1118.2 |  | 9803 | 130.04 | 2.2283 | 61.549 | 0.0063721 | 98.099 | 1118.2 | 1020.101
9804 | 2.2289 | 130.05 | 61.548 | 0.0063737 | 98.109 | 1118.2 |  | 9804 | 130.05 | 2.2289 | 61.548 | 0.0063737 | 98.109 | 1118.2 | 1020.091
9805 | 2.2295 | 130.06 | 61.548 | 0.0063753 | 98.119 | 1118.2 |  | 9805 | 130.06 | 2.2295 | 61.548 | 0.0063753 | 98.119 | 1118.2 | 1020.081
9806 | 2.2301 | 130.07 | 61.548 | 0.0063769 | 98.129 | 1118.2 |  | 9806 | 130.07 | 2.2301 | 61.548 | 0.0063769 | 98.129 | 1118.2 | 1020.071
9807 | 2.2307 | 130.08 | 61.548 | 0.0063785 | 98.139 | 1118.2 |  | 9807 | 130.08 | 2.2307 | 61.548 | 0.0063785 | 98.139 | 1118.2 | 1020.061
9808 | 2.2313 | 130.09 | 61.548 | 0.0063801 | 98.149 | 1118.2 |  | 9808 | 130.09 | 2.2313 | 61.548 | 0.0063801 | 98.149 | 1118.2 | 1020.051
9809 | 2.2319 | 130.1 | 61.548 | 0.0063817 | 98.159 | 1118.2 |  | 9809 | 130.1 | 2.2319 | 61.548 | 0.0063817 | 98.159 | 1118.2 | 1020.041
9810 | 2.2325 | 130.11 | 61.547 | 0.0063833 | 98.169 | 1118.2 |  | 9810 | 130.11 | 2.2325 | 61.547 | 0.0063833 | 98.169 | 1118.2 | 1020.031
9811 | 2.2331 | 130.12 | 61.547 | 0.0063849 | 98.179 | 1118.2 |  | 9811 | 130.12 | 2.2331 | 61.547 | 0.0063849 | 98.179 | 1118.2 | 1020.021
9812 | 2.2337 | 130.13 | 61.547 | 0.0063865 | 98.189 | 1118.2 |  | 9812 | 130.13 | 2.2337 | 61.547 | 0.0063865 | 98.189 | 1118.2 | 1020.011
9813 | 2.2343 | 130.14 | 61.547 | 0.0063881 | 98.199 | 1118.2 |  | 9813 | 130.14 | 2.2343 | 61.547 | 0.0063881 | 98.199 | 1118.2 | 1020.001
9814 | 2.2349 | 130.15 | 61.547 | 0.0063897 | 98.209 | 1118.2 |  | 9814 | 130.15 | 2.2349 | 61.547 | 0.0063897 | 98.209 | 1118.2 | 1019.991
9815 | 2.2355 | 130.16 | 61.547 | 0.0063913 | 98.219 | 1118.2 |  | 9815 | 130.16 | 2.2355 | 61.547 | 0.0063913 | 98.219 | 1118.2 | 1019.981
9816 | 2.2361 | 130.17 | 61.546 | 0.0063929 | 98.229 | 1118.2 |  | 9816 | 130.17 | 2.2361 | 61.546 | 0.0063929 | 98.229 | 1118.2 | 1019.971
9817 | 2.2367 | 130.18 | 61.546 | 0.0063945 | 98.239 | 1118.2 |  | 9817 | 130.18 | 2.2367 | 61.546 | 0.0063945 | 98.239 | 1118.2 | 1019.961
9818 | 2.2373 | 130.19 | 61.546 | 0.0063961 | 98.249 | 1118.2 |  | 9818 | 130.19 | 2.2373 | 61.546 | 0.0063961 | 98.249 | 1118.2 | 1019.951
9819 | 2.2379 | 130.2 | 61.546 | 0.0063977 | 98.259 | 1118.3 |  | 9819 | 130.2 | 2.2379 | 61.546 | 0.0063977 | 98.259 | 1118.3 | 1020.041
9820 | 2.2385 | 130.21 | 61.546 | 0.0063993 | 98.269 | 1118.3 |  | 9820 | 130.21 | 2.2385 | 61.546 | 0.0063993 | 98.269 | 1118.3 | 1020.031
9821 | 2.2391 | 130.22 | 61.546 | 0.0064009 | 98.279 | 1118.3 |  | 9821 | 130.22 | 2.2391 | 61.546 | 0.0064009 | 98.279 | 1118.3 | 1020.021
9822 | 2.2397 | 130.23 | 61.545 | 0.0064026 | 98.289 | 1118.3 |  | 9822 | 130.23 | 2.2397 | 61.545 | 0.0064026 | 98.289 | 1118.3 | 1020.011
9823 | 2.2403 | 130.24 | 61.545 | 0.0064042 | 98.299 | 1118.3 |  | 9823 | 130.24 | 2.2403 | 61.545 | 0.0064042 | 98.299 | 1118.3 | 1020.001
9824 | 2.2409 | 130.25 | 61.545 | 0.0064058 | 98.309 | 1118.3 |  | 9824 | 130.25 | 2.2409 | 61.545 | 0.0064058 | 98.309 | 1118.3 | 1019.991
9825 | 2.2414 | 130.26 | 61.545 | 0.0064074 | 98.319 | 1118.3 |  | 9825 | 130.26 | 2.2414 | 61.545 | 0.0064074 | 98.319 | 1118.3 | 1019.981
9826 | 2.242 | 130.27 | 61.545 | 0.006409 | 98.329 | 1118.3 |  | 9826 | 130.27 | 2.242 | 61.545 | 0.006409 | 98.329 | 1118.3 | 1019.971
9827 | 2.2426 | 130.28 | 61.545 | 0.0064106 | 98.339 | 1118.3 |  | 9827 | 130.28 | 2.2426 | 61.545 | 0.0064106 | 98.339 | 1118.3 | 1019.961
9828 | 2.2432 | 130.29 | 61.544 | 0.0064122 | 98.349 | 1118.3 |  | 9828 | 130.29 | 2.2432 | 61.544 | 0.0064122 | 98.349 | 1118.3 | 1019.951
9829 | 2.2438 | 130.3 | 61.544 | 0.0064138 | 98.359 | 1118.3 |  | 9829 | 130.3 | 2.2438 | 61.544 | 0.0064138 | 98.359 | 1118.3 | 1019.941
9830 | 2.2444 | 130.31 | 61.544 | 0.0064154 | 98.369 | 1118.3 |  | 9830 | 130.31 | 2.2444 | 61.544 | 0.0064154 | 98.369 | 1118.3 | 1019.931
9831 | 2.245 | 130.32 | 61.544 | 0.006417 | 98.379 | 1118.3 |  | 9831 | 130.32 | 2.245 | 61.544 | 0.006417 | 98.379 | 1118.3 | 1019.921
9832 | 2.2456 | 130.33 | 61.544 | 0.0064186 | 98.389 | 1118.3 |  | 9832 | 130.33 | 2.2456 | 61.544 | 0.0064186 | 98.389 | 1118.3 | 1019.911
9833 | 2.2462 | 130.34 | 61.544 | 0.0064202 | 98.399 | 1118.3 |  | 9833 | 130.34 | 2.2462 | 61.544 | 0.0064202 | 98.399 | 1118.3 | 1019.901
9834 | 2.2468 | 130.35 | 61.543 | 0.0064218 | 98.409 | 1118.3 |  | 9834 | 130.35 | 2.2468 | 61.543 | 0.0064218 | 98.409 | 1118.3 | 1019.891
9835 | 2.2474 | 130.36 | 61.543 | 0.0064235 | 98.419 | 1118.3 |  | 9835 | 130.36 | 2.2474 | 61.543 | 0.0064235 | 98.419 | 1118.3 | 1019.881
9836 | 2.248 | 130.37 | 61.543 | 0.0064251 | 98.429 | 1118.3 |  | 9836 | 130.37 | 2.248 | 61.543 | 0.0064251 | 98.429 | 1118.3 | 1019.871
9837 | 2.2486 | 130.38 | 61.543 | 0.0064267 | 98.439 | 1118.3 |  | 9837 | 130.38 | 2.2486 | 61.543 | 0.0064267 | 98.439 | 1118.3 | 1019.861
9838 | 2.2492 | 130.39 | 61.543 | 0.0064283 | 98.449 | 1118.3 |  | 9838 | 130.39 | 2.2492 | 61.543 | 0.0064283 | 98.449 | 1118.3 | 1019.851
9839 | 2.2498 | 130.4 | 61.543 | 0.0064299 | 98.459 | 1118.3 |  | 9839 | 130.4 | 2.2498 | 61.543 | 0.0064299 | 98.459 | 1118.3 | 1019.841
9840 | 2.2504 | 130.41 | 61.542 | 0.0064315 | 98.469 | 1118.3 |  | 9840 | 130.41 | 2.2504 | 61.542 | 0.0064315 | 98.469 | 1118.3 | 1019.831
9841 | 2.251 | 130.42 | 61.542 | 0.0064331 | 98.479 | 1118.3 |  | 9841 | 130.42 | 2.251 | 61.542 | 0.0064331 | 98.479 | 1118.3 | 1019.821
9842 | 2.2516 | 130.43 | 61.542 | 0.0064347 | 98.489 | 1118.3 |  | 9842 | 130.43 | 2.2516 | 61.542 | 0.0064347 | 98.489 | 1118.3 | 1019.811
9843 | 2.2522 | 130.44 | 61.542 | 0.0064363 | 98.499 | 1118.4 |  | 9843 | 130.44 | 2.2522 | 61.542 | 0.0064363 | 98.499 | 1118.4 | 1019.901
9844 | 2.2528 | 130.45 | 61.542 | 0.006438 | 98.509 | 1118.4 |  | 9844 | 130.45 | 2.2528 | 61.542 | 0.006438 | 98.509 | 1118.4 | 1019.891
9845 | 2.2534 | 130.46 | 61.542 | 0.0064396 | 98.519 | 1118.4 |  | 9845 | 130.46 | 2.2534 | 61.542 | 0.0064396 | 98.519 | 1118.4 | 1019.881
9846 | 2.254 | 130.47 | 61.541 | 0.0064412 | 98.529 | 1118.4 |  | 9846 | 130.47 | 2.254 | 61.541 | 0.0064412 | 98.529 | 1118.4 | 1019.871
9847 | 2.2546 | 130.48 | 61.541 | 0.0064428 | 98.539 | 1118.4 |  | 9847 | 130.48 | 2.2546 | 61.541 | 0.0064428 | 98.539 | 1118.4 | 1019.861
9848 | 2.2552 | 130.49 | 61.541 | 0.0064444 | 98.549 | 1118.4 |  | 9848 | 130.49 | 2.2552 | 61.541 | 0.0064444 | 98.549 | 1118.4 | 1019.851
9849 | 2.2558 | 130.5 | 61.541 | 0.006446 | 98.559 | 1118.4 |  | 9849 | 130.5 | 2.2558 | 61.541 | 0.006446 | 98.559 | 1118.4 | 1019.841
9850 | 2.2564 | 130.51 | 61.541 | 0.0064476 | 98.569 | 1118.4 |  | 9850 | 130.51 | 2.2564 | 61.541 | 0.0064476 | 98.569 | 1118.4 | 1019.831
9851 | 2.2571 | 130.52 | 61.541 | 0.0064493 | 98.579 | 1118.4 |  | 9851 | 130.52 | 2.2571 | 61.541 | 0.0064493 | 98.579 | 1118.4 | 1019.821
9852 | 2.2577 | 130.53 | 61.54 | 0.0064509 | 98.589 | 1118.4 |  | 9852 | 130.53 | 2.2577 | 61.54 | 0.0064509 | 98.589 | 1118.4 | 1019.811
9853 | 2.2583 | 130.54 | 61.54 | 0.0064525 | 98.599 | 1118.4 |  | 9853 | 130.54 | 2.2583 | 61.54 | 0.0064525 | 98.599 | 1118.4 | 1019.801
9854 | 2.2589 | 130.55 | 61.54 | 0.0064541 | 98.609 | 1118.4 |  | 9854 | 130.55 | 2.2589 | 61.54 | 0.0064541 | 98.609 | 1118.4 | 1019.791
9855 | 2.2595 | 130.56 | 61.54 | 0.0064557 | 98.619 | 1118.4 |  | 9855 | 130.56 | 2.2595 | 61.54 | 0.0064557 | 98.619 | 1118.4 | 1019.781
9856 | 2.2601 | 130.57 | 61.54 | 0.0064573 | 98.629 | 1118.4 |  | 9856 | 130.57 | 2.2601 | 61.54 | 0.0064573 | 98.629 | 1118.4 | 1019.771
9857 | 2.2607 | 130.58 | 61.54 | 0.006459 | 98.639 | 1118.4 |  | 9857 | 130.58 | 2.2607 | 61.54 | 0.006459 | 98.639 | 1118.4 | 1019.761
9858 | 2.2613 | 130.59 | 61.539 | 0.0064606 | 98.649 | 1118.4 |  | 9858 | 130.59 | 2.2613 | 61.539 | 0.0064606 | 98.649 | 1118.4 | 1019.751
9859 | 2.2619 | 130.6 | 61.539 | 0.0064622 | 98.659 | 1118.4 |  | 9859 | 130.6 | 2.2619 | 61.539 | 0.0064622 | 98.659 | 1118.4 | 1019.741
9860 | 2.2625 | 130.61 | 61.539 | 0.0064638 | 98.669 | 1118.4 |  | 9860 | 130.61 | 2.2625 | 61.539 | 0.0064638 | 98.669 | 1118.4 | 1019.731
9861 | 2.2631 | 130.62 | 61.539 | 0.0064654 | 98.679 | 1118.4 |  | 9861 | 130.62 | 2.2631 | 61.539 | 0.0064654 | 98.679 | 1118.4 | 1019.721
9862 | 2.2637 | 130.63 | 61.539 | 0.0064671 | 98.689 | 1118.4 |  | 9862 | 130.63 | 2.2637 | 61.539 | 0.0064671 | 98.689 | 1118.4 | 1019.711
9863 | 2.2643 | 130.64 | 61.539 | 0.0064687 | 98.699 | 1118.4 |  | 9863 | 130.64 | 2.2643 | 61.539 | 0.0064687 | 98.699 | 1118.4 | 1019.701
9864 | 2.2649 | 130.65 | 61.538 | 0.0064703 | 98.709 | 1118.4 |  | 9864 | 130.65 | 2.2649 | 61.538 | 0.0064703 | 98.709 | 1118.4 | 1019.691
9865 | 2.2655 | 130.66 | 61.538 | 0.0064719 | 98.719 | 1118.4 |  | 9865 | 130.66 | 2.2655 | 61.538 | 0.0064719 | 98.719 | 1118.4 | 1019.681
9866 | 2.2661 | 130.67 | 61.538 | 0.0064735 | 98.729 | 1118.4 |  | 9866 | 130.67 | 2.2661 | 61.538 | 0.0064735 | 98.729 | 1118.4 | 1019.671
9867 | 2.2667 | 130.68 | 61.538 | 0.0064752 | 98.739 | 1118.5 |  | 9867 | 130.68 | 2.2667 | 61.538 | 0.0064752 | 98.739 | 1118.5 | 1019.761
9868 | 2.2673 | 130.69 | 61.538 | 0.0064768 | 98.749 | 1118.5 |  | 9868 | 130.69 | 2.2673 | 61.538 | 0.0064768 | 98.749 | 1118.5 | 1019.751
9869 | 2.2679 | 130.7 | 61.538 | 0.0064784 | 98.759 | 1118.5 |  | 9869 | 130.7 | 2.2679 | 61.538 | 0.0064784 | 98.759 | 1118.5 | 1019.741
9870 | 2.2685 | 130.71 | 61.537 | 0.00648 | 98.769 | 1118.5 |  | 9870 | 130.71 | 2.2685 | 61.537 | 0.00648 | 98.769 | 1118.5 | 1019.731
9871 | 2.2691 | 130.72 | 61.537 | 0.0064816 | 98.779 | 1118.5 |  | 9871 | 130.72 | 2.2691 | 61.537 | 0.0064816 | 98.779 | 1118.5 | 1019.721
9872 | 2.2697 | 130.73 | 61.537 | 0.0064833 | 98.789 | 1118.5 |  | 9872 | 130.73 | 2.2697 | 61.537 | 0.0064833 | 98.789 | 1118.5 | 1019.711
9873 | 2.2703 | 130.74 | 61.537 | 0.0064849 | 98.799 | 1118.5 |  | 9873 | 130.74 | 2.2703 | 61.537 | 0.0064849 | 98.799 | 1118.5 | 1019.701
9874 | 2.2709 | 130.75 | 61.537 | 0.0064865 | 98.809 | 1118.5 |  | 9874 | 130.75 | 2.2709 | 61.537 | 0.0064865 | 98.809 | 1118.5 | 1019.691
9875 | 2.2715 | 130.76 | 61.537 | 0.0064881 | 98.819 | 1118.5 |  | 9875 | 130.76 | 2.2715 | 61.537 | 0.0064881 | 98.819 | 1118.5 | 1019.681
9876 | 2.2721 | 130.77 | 61.536 | 0.0064898 | 98.829 | 1118.5 |  | 9876 | 130.77 | 2.2721 | 61.536 | 0.0064898 | 98.829 | 1118.5 | 1019.671
9877 | 2.2727 | 130.78 | 61.536 | 0.0064914 | 98.839 | 1118.5 |  | 9877 | 130.78 | 2.2727 | 61.536 | 0.0064914 | 98.839 | 1118.5 | 1019.661
9878 | 2.2734 | 130.79 | 61.536 | 0.006493 | 98.849 | 1118.5 |  | 9878 | 130.79 | 2.2734 | 61.536 | 0.006493 | 98.849 | 1118.5 | 1019.651
9879 | 2.274 | 130.8 | 61.536 | 0.0064946 | 98.859 | 1118.5 |  | 9879 | 130.8 | 2.274 | 61.536 | 0.0064946 | 98.859 | 1118.5 | 1019.641
9880 | 2.2746 | 130.81 | 61.536 | 0.0064963 | 98.869 | 1118.5 |  | 9880 | 130.81 | 2.2746 | 61.536 | 0.0064963 | 98.869 | 1118.5 | 1019.631
9881 | 2.2752 | 130.82 | 61.535 | 0.0064979 | 98.879 | 1118.5 |  | 9881 | 130.82 | 2.2752 | 61.535 | 0.0064979 | 98.879 | 1118.5 | 1019.621
9882 | 2.2758 | 130.83 | 61.535 | 0.0064995 | 98.889 | 1118.5 |  | 9882 | 130.83 | 2.2758 | 61.535 | 0.0064995 | 98.889 | 1118.5 | 1019.611
9883 | 2.2764 | 130.84 | 61.535 | 0.0065011 | 98.899 | 1118.5 |  | 9883 | 130.84 | 2.2764 | 61.535 | 0.0065011 | 98.899 | 1118.5 | 1019.601
9884 | 2.277 | 130.85 | 61.535 | 0.0065028 | 98.909 | 1118.5 |  | 9884 | 130.85 | 2.277 | 61.535 | 0.0065028 | 98.909 | 1118.5 | 1019.591
9885 | 2.2776 | 130.86 | 61.535 | 0.0065044 | 98.919 | 1118.5 |  | 9885 | 130.86 | 2.2776 | 61.535 | 0.0065044 | 98.919 | 1118.5 | 1019.581
9886 | 2.2782 | 130.87 | 61.535 | 0.006506 | 98.929 | 1118.5 |  | 9886 | 130.87 | 2.2782 | 61.535 | 0.006506 | 98.929 | 1118.5 | 1019.571
9887 | 2.2788 | 130.88 | 61.534 | 0.0065076 | 98.939 | 1118.5 |  | 9887 | 130.88 | 2.2788 | 61.534 | 0.0065076 | 98.939 | 1118.5 | 1019.561
9888 | 2.2794 | 130.89 | 61.534 | 0.0065093 | 98.949 | 1118.5 |  | 9888 | 130.89 | 2.2794 | 61.534 | 0.0065093 | 98.949 | 1118.5 | 1019.551
9889 | 2.28 | 130.9 | 61.534 | 0.0065109 | 98.959 | 1118.5 |  | 9889 | 130.9 | 2.28 | 61.534 | 0.0065109 | 98.959 | 1118.5 | 1019.541
9890 | 2.2806 | 130.91 | 61.534 | 0.0065125 | 98.969 | 1118.5 |  | 9890 | 130.91 | 2.2806 | 61.534 | 0.0065125 | 98.969 | 1118.5 | 1019.531
9891 | 2.2812 | 130.92 | 61.534 | 0.0065142 | 98.979 | 1118.6 |  | 9891 | 130.92 | 2.2812 | 61.534 | 0.0065142 | 98.979 | 1118.6 | 1019.621
9892 | 2.2818 | 130.93 | 61.534 | 0.0065158 | 98.989 | 1118.6 |  | 9892 | 130.93 | 2.2818 | 61.534 | 0.0065158 | 98.989 | 1118.6 | 1019.611
9893 | 2.2825 | 130.94 | 61.533 | 0.0065174 | 98.999 | 1118.6 |  | 9893 | 130.94 | 2.2825 | 61.533 | 0.0065174 | 98.999 | 1118.6 | 1019.601
9894 | 2.2831 | 130.95 | 61.533 | 0.006519 | 99.009 | 1118.6 |  | 9894 | 130.95 | 2.2831 | 61.533 | 0.006519 | 99.009 | 1118.6 | 1019.591
9895 | 2.2837 | 130.96 | 61.533 | 0.0065207 | 99.019 | 1118.6 |  | 9895 | 130.96 | 2.2837 | 61.533 | 0.0065207 | 99.019 | 1118.6 | 1019.581
9896 | 2.2843 | 130.97 | 61.533 | 0.0065223 | 99.029 | 1118.6 |  | 9896 | 130.97 | 2.2843 | 61.533 | 0.0065223 | 99.029 | 1118.6 | 1019.571
9897 | 2.2849 | 130.98 | 61.533 | 0.0065239 | 99.039 | 1118.6 |  | 9897 | 130.98 | 2.2849 | 61.533 | 0.0065239 | 99.039 | 1118.6 | 1019.561
9898 | 2.2855 | 130.99 | 61.533 | 0.0065256 | 99.049 | 1118.6 |  | 9898 | 130.99 | 2.2855 | 61.533 | 0.0065256 | 99.049 | 1118.6 | 1019.551
9899 | 2.2861 | 131 | 61.532 | 0.0065272 | 99.059 | 1118.6 |  | 9899 | 131 | 2.2861 | 61.532 | 0.0065272 | 99.059 | 1118.6 | 1019.541
9900 | 2.2867 | 131.01 | 61.532 | 0.0065288 | 99.069 | 1118.6 |  | 9900 | 131.01 | 2.2867 | 61.532 | 0.0065288 | 99.069 | 1118.6 | 1019.531
9901 | 2.2873 | 131.02 | 61.532 | 0.0065305 | 99.079 | 1118.6 |  | 9901 | 131.02 | 2.2873 | 61.532 | 0.0065305 | 99.079 | 1118.6 | 1019.521
9902 | 2.2879 | 131.03 | 61.532 | 0.0065321 | 99.089 | 1118.6 |  | 9902 | 131.03 | 2.2879 | 61.532 | 0.0065321 | 99.089 | 1118.6 | 1019.511
9903 | 2.2885 | 131.04 | 61.532 | 0.0065337 | 99.099 | 1118.6 |  | 9903 | 131.04 | 2.2885 | 61.532 | 0.0065337 | 99.099 | 1118.6 | 1019.501
9904 | 2.2891 | 131.05 | 61.532 | 0.0065354 | 99.109 | 1118.6 |  | 9904 | 131.05 | 2.2891 | 61.532 | 0.0065354 | 99.109 | 1118.6 | 1019.491
9905 | 2.2898 | 131.06 | 61.531 | 0.006537 | 99.119 | 1118.6 |  | 9905 | 131.06 | 2.2898 | 61.531 | 0.006537 | 99.119 | 1118.6 | 1019.481
9906 | 2.2904 | 131.07 | 61.531 | 0.0065386 | 99.129 | 1118.6 |  | 9906 | 131.07 | 2.2904 | 61.531 | 0.0065386 | 99.129 | 1118.6 | 1019.471
9907 | 2.291 | 131.08 | 61.531 | 0.0065403 | 99.139 | 1118.6 |  | 9907 | 131.08 | 2.291 | 61.531 | 0.0065403 | 99.139 | 1118.6 | 1019.461
9908 | 2.2916 | 131.09 | 61.531 | 0.0065419 | 99.149 | 1118.6 |  | 9908 | 131.09 | 2.2916 | 61.531 | 0.0065419 | 99.149 | 1118.6 | 1019.451
9909 | 2.2922 | 131.1 | 61.531 | 0.0065435 | 99.159 | 1118.6 |  | 9909 | 131.1 | 2.2922 | 61.531 | 0.0065435 | 99.159 | 1118.6 | 1019.441
9910 | 2.2928 | 131.11 | 61.531 | 0.0065452 | 99.169 | 1118.6 |  | 9910 | 131.11 | 2.2928 | 61.531 | 0.0065452 | 99.169 | 1118.6 | 1019.431
9911 | 2.2934 | 131.12 | 61.53 | 0.0065468 | 99.179 | 1118.6 |  | 9911 | 131.12 | 2.2934 | 61.53 | 0.0065468 | 99.179 | 1118.6 | 1019.421
9912 | 2.294 | 131.13 | 61.53 | 0.0065484 | 99.189 | 1118.6 |  | 9912 | 131.13 | 2.294 | 61.53 | 0.0065484 | 99.189 | 1118.6 | 1019.411
9913 | 2.2946 | 131.14 | 61.53 | 0.0065501 | 99.199 | 1118.6 |  | 9913 | 131.14 | 2.2946 | 61.53 | 0.0065501 | 99.199 | 1118.6 | 1019.401
9914 | 2.2952 | 131.15 | 61.53 | 0.0065517 | 99.209 | 1118.7 |  | 9914 | 131.15 | 2.2952 | 61.53 | 0.0065517 | 99.209 | 1118.7 | 1019.491
9915 | 2.2959 | 131.16 | 61.53 | 0.0065534 | 99.219 | 1118.7 |  | 9915 | 131.16 | 2.2959 | 61.53 | 0.0065534 | 99.219 | 1118.7 | 1019.481
9916 | 2.2965 | 131.17 | 61.53 | 0.006555 | 99.229 | 1118.7 |  | 9916 | 131.17 | 2.2965 | 61.53 | 0.006555 | 99.229 | 1118.7 | 1019.471
9917 | 2.2971 | 131.18 | 61.529 | 0.0065566 | 99.239 | 1118.7 |  | 9917 | 131.18 | 2.2971 | 61.529 | 0.0065566 | 99.239 | 1118.7 | 1019.461
9918 | 2.2977 | 131.19 | 61.529 | 0.0065583 | 99.249 | 1118.7 |  | 9918 | 131.19 | 2.2977 | 61.529 | 0.0065583 | 99.249 | 1118.7 | 1019.451
9919 | 2.2983 | 131.2 | 61.529 | 0.0065599 | 99.259 | 1118.7 |  | 9919 | 131.2 | 2.2983 | 61.529 | 0.0065599 | 99.259 | 1118.7 | 1019.441
9920 | 2.2989 | 131.21 | 61.529 | 0.0065615 | 99.269 | 1118.7 |  | 9920 | 131.21 | 2.2989 | 61.529 | 0.0065615 | 99.269 | 1118.7 | 1019.431
9921 | 2.2995 | 131.22 | 61.529 | 0.0065632 | 99.279 | 1118.7 |  | 9921 | 131.22 | 2.2995 | 61.529 | 0.0065632 | 99.279 | 1118.7 | 1019.421
9922 | 2.3001 | 131.23 | 61.529 | 0.0065648 | 99.289 | 1118.7 |  | 9922 | 131.23 | 2.3001 | 61.529 | 0.0065648 | 99.289 | 1118.7 | 1019.411
9923 | 2.3007 | 131.24 | 61.528 | 0.0065665 | 99.299 | 1118.7 |  | 9923 | 131.24 | 2.3007 | 61.528 | 0.0065665 | 99.299 | 1118.7 | 1019.401
9924 | 2.3014 | 131.25 | 61.528 | 0.0065681 | 99.309 | 1118.7 |  | 9924 | 131.25 | 2.3014 | 61.528 | 0.0065681 | 99.309 | 1118.7 | 1019.391
9925 | 2.302 | 131.26 | 61.528 | 0.0065697 | 99.319 | 1118.7 |  | 9925 | 131.26 | 2.302 | 61.528 | 0.0065697 | 99.319 | 1118.7 | 1019.381
9926 | 2.3026 | 131.27 | 61.528 | 0.0065714 | 99.329 | 1118.7 |  | 9926 | 131.27 | 2.3026 | 61.528 | 0.0065714 | 99.329 | 1118.7 | 1019.371
9927 | 2.3032 | 131.28 | 61.528 | 0.006573 | 99.339 | 1118.7 |  | 9927 | 131.28 | 2.3032 | 61.528 | 0.006573 | 99.339 | 1118.7 | 1019.361
9928 | 2.3038 | 131.29 | 61.528 | 0.0065747 | 99.349 | 1118.7 |  | 9928 | 131.29 | 2.3038 | 61.528 | 0.0065747 | 99.349 | 1118.7 | 1019.351
9929 | 2.3044 | 131.3 | 61.527 | 0.0065763 | 99.359 | 1118.7 |  | 9929 | 131.3 | 2.3044 | 61.527 | 0.0065763 | 99.359 | 1118.7 | 1019.341
9930 | 2.305 | 131.31 | 61.527 | 0.006578 | 99.369 | 1118.7 |  | 9930 | 131.31 | 2.305 | 61.527 | 0.006578 | 99.369 | 1118.7 | 1019.331
9931 | 2.3056 | 131.32 | 61.527 | 0.0065796 | 99.379 | 1118.7 |  | 9931 | 131.32 | 2.3056 | 61.527 | 0.0065796 | 99.379 | 1118.7 | 1019.321
9932 | 2.3063 | 131.33 | 61.527 | 0.0065812 | 99.389 | 1118.7 |  | 9932 | 131.33 | 2.3063 | 61.527 | 0.0065812 | 99.389 | 1118.7 | 1019.311
9933 | 2.3069 | 131.34 | 61.527 | 0.0065829 | 99.399 | 1118.7 |  | 9933 | 131.34 | 2.3069 | 61.527 | 0.0065829 | 99.399 | 1118.7 | 1019.301
9934 | 2.3075 | 131.35 | 61.527 | 0.0065845 | 99.409 | 1118.7 |  | 9934 | 131.35 | 2.3075 | 61.527 | 0.0065845 | 99.409 | 1118.7 | 1019.291
9935 | 2.3081 | 131.36 | 61.526 | 0.0065862 | 99.419 | 1118.7 |  | 9935 | 131.36 | 2.3081 | 61.526 | 0.0065862 | 99.419 | 1118.7 | 1019.281
9936 | 2.3087 | 131.37 | 61.526 | 0.0065878 | 99.429 | 1118.7 |  | 9936 | 131.37 | 2.3087 | 61.526 | 0.0065878 | 99.429 | 1118.7 | 1019.271
9937 | 2.3093 | 131.38 | 61.526 | 0.0065895 | 99.439 | 1118.7 |  | 9937 | 131.38 | 2.3093 | 61.526 | 0.0065895 | 99.439 | 1118.7 | 1019.261
9938 | 2.3099 | 131.39 | 61.526 | 0.0065911 | 99.449 | 1118.8 |  | 9938 | 131.39 | 2.3099 | 61.526 | 0.0065911 | 99.449 | 1118.8 | 1019.351
9939 | 2.3105 | 131.4 | 61.526 | 0.0065928 | 99.459 | 1118.8 |  | 9939 | 131.4 | 2.3105 | 61.526 | 0.0065928 | 99.459 | 1118.8 | 1019.341
9940 | 2.3112 | 131.41 | 61.526 | 0.0065944 | 99.469 | 1118.8 |  | 9940 | 131.41 | 2.3112 | 61.526 | 0.0065944 | 99.469 | 1118.8 | 1019.331
9941 | 2.3118 | 131.42 | 61.525 | 0.006596 | 99.479 | 1118.8 |  | 9941 | 131.42 | 2.3118 | 61.525 | 0.006596 | 99.479 | 1118.8 | 1019.321
9942 | 2.3124 | 131.43 | 61.525 | 0.0065977 | 99.489 | 1118.8 |  | 9942 | 131.43 | 2.3124 | 61.525 | 0.0065977 | 99.489 | 1118.8 | 1019.311
9943 | 2.313 | 131.44 | 61.525 | 0.0065993 | 99.499 | 1118.8 |  | 9943 | 131.44 | 2.313 | 61.525 | 0.0065993 | 99.499 | 1118.8 | 1019.301
9944 | 2.3136 | 131.45 | 61.525 | 0.006601 | 99.509 | 1118.8 |  | 9944 | 131.45 | 2.3136 | 61.525 | 0.006601 | 99.509 | 1118.8 | 1019.291
9945 | 2.3142 | 131.46 | 61.525 | 0.0066026 | 99.519 | 1118.8 |  | 9945 | 131.46 | 2.3142 | 61.525 | 0.0066026 | 99.519 | 1118.8 | 1019.281
9946 | 2.3149 | 131.47 | 61.525 | 0.0066043 | 99.529 | 1118.8 |  | 9946 | 131.47 | 2.3149 | 61.525 | 0.0066043 | 99.529 | 1118.8 | 1019.271
9947 | 2.3155 | 131.48 | 61.524 | 0.0066059 | 99.539 | 1118.8 |  | 9947 | 131.48 | 2.3155 | 61.524 | 0.0066059 | 99.539 | 1118.8 | 1019.261
9948 | 2.3161 | 131.49 | 61.524 | 0.0066076 | 99.549 | 1118.8 |  | 9948 | 131.49 | 2.3161 | 61.524 | 0.0066076 | 99.549 | 1118.8 | 1019.251
9949 | 2.3167 | 131.5 | 61.524 | 0.0066092 | 99.559 | 1118.8 |  | 9949 | 131.5 | 2.3167 | 61.524 | 0.0066092 | 99.559 | 1118.8 | 1019.241
9950 | 2.3173 | 131.51 | 61.524 | 0.0066109 | 99.569 | 1118.8 |  | 9950 | 131.51 | 2.3173 | 61.524 | 0.0066109 | 99.569 | 1118.8 | 1019.231
9951 | 2.3179 | 131.52 | 61.524 | 0.0066125 | 99.579 | 1118.8 |  | 9951 | 131.52 | 2.3179 | 61.524 | 0.0066125 | 99.579 | 1118.8 | 1019.221
9952 | 2.3185 | 131.53 | 61.524 | 0.0066142 | 99.589 | 1118.8 |  | 9952 | 131.53 | 2.3185 | 61.524 | 0.0066142 | 99.589 | 1118.8 | 1019.211
9953 | 2.3192 | 131.54 | 61.523 | 0.0066158 | 99.599 | 1118.8 |  | 9953 | 131.54 | 2.3192 | 61.523 | 0.0066158 | 99.599 | 1118.8 | 1019.201
9954 | 2.3198 | 131.55 | 61.523 | 0.0066175 | 99.609 | 1118.8 |  | 9954 | 131.55 | 2.3198 | 61.523 | 0.0066175 | 99.609 | 1118.8 | 1019.191
9955 | 2.3204 | 131.56 | 61.523 | 0.0066191 | 99.619 | 1118.8 |  | 9955 | 131.56 | 2.3204 | 61.523 | 0.0066191 | 99.619 | 1118.8 | 1019.181
9956 | 2.321 | 131.57 | 61.523 | 0.0066208 | 99.629 | 1118.8 |  | 9956 | 131.57 | 2.321 | 61.523 | 0.0066208 | 99.629 | 1118.8 | 1019.171
9957 | 2.3216 | 131.58 | 61.523 | 0.0066224 | 99.639 | 1118.8 |  | 9957 | 131.58 | 2.3216 | 61.523 | 0.0066224 | 99.639 | 1118.8 | 1019.161
9958 | 2.3222 | 131.59 | 61.523 | 0.0066241 | 99.649 | 1118.8 |  | 9958 | 131.59 | 2.3222 | 61.523 | 0.0066241 | 99.649 | 1118.8 | 1019.151
9959 | 2.3229 | 131.6 | 61.522 | 0.0066257 | 99.659 | 1118.8 |  | 9959 | 131.6 | 2.3229 | 61.522 | 0.0066257 | 99.659 | 1118.8 | 1019.141
9960 | 2.3235 | 131.61 | 61.522 | 0.0066274 | 99.669 | 1118.8 |  | 9960 | 131.61 | 2.3235 | 61.522 | 0.0066274 | 99.669 | 1118.8 | 1019.131
9961 | 2.3241 | 131.62 | 61.522 | 0.006629 | 99.679 | 1118.8 |  | 9961 | 131.62 | 2.3241 | 61.522 | 0.006629 | 99.679 | 1118.8 | 1019.121
9962 | 2.3247 | 131.63 | 61.522 | 0.0066307 | 99.689 | 1118.9 |  | 9962 | 131.63 | 2.3247 | 61.522 | 0.0066307 | 99.689 | 1118.9 | 1019.211
9963 | 2.3253 | 131.64 | 61.522 | 0.0066324 | 99.699 | 1118.9 |  | 9963 | 131.64 | 2.3253 | 61.522 | 0.0066324 | 99.699 | 1118.9 | 1019.201
9964 | 2.3259 | 131.65 | 61.522 | 0.006634 | 99.709 | 1118.9 |  | 9964 | 131.65 | 2.3259 | 61.522 | 0.006634 | 99.709 | 1118.9 | 1019.191
9965 | 2.3266 | 131.66 | 61.521 | 0.0066357 | 99.719 | 1118.9 |  | 9965 | 131.66 | 2.3266 | 61.521 | 0.0066357 | 99.719 | 1118.9 | 1019.181
9966 | 2.3272 | 131.67 | 61.521 | 0.0066373 | 99.729 | 1118.9 |  | 9966 | 131.67 | 2.3272 | 61.521 | 0.0066373 | 99.729 | 1118.9 | 1019.171
9967 | 2.3278 | 131.68 | 61.521 | 0.006639 | 99.739 | 1118.9 |  | 9967 | 131.68 | 2.3278 | 61.521 | 0.006639 | 99.739 | 1118.9 | 1019.161
9968 | 2.3284 | 131.69 | 61.521 | 0.0066406 | 99.749 | 1118.9 |  | 9968 | 131.69 | 2.3284 | 61.521 | 0.0066406 | 99.749 | 1118.9 | 1019.151
9969 | 2.329 | 131.7 | 61.521 | 0.0066423 | 99.759 | 1118.9 |  | 9969 | 131.7 | 2.329 | 61.521 | 0.0066423 | 99.759 | 1118.9 | 1019.141
9970 | 2.3297 | 131.71 | 61.521 | 0.0066439 | 99.769 | 1118.9 |  | 9970 | 131.71 | 2.3297 | 61.521 | 0.0066439 | 99.769 | 1118.9 | 1019.131
9971 | 2.3303 | 131.72 | 61.52 | 0.0066456 | 99.779 | 1118.9 |  | 9971 | 131.72 | 2.3303 | 61.52 | 0.0066456 | 99.779 | 1118.9 | 1019.121
9972 | 2.3309 | 131.73 | 61.52 | 0.0066473 | 99.789 | 1118.9 |  | 9972 | 131.73 | 2.3309 | 61.52 | 0.0066473 | 99.789 | 1118.9 | 1019.111
9973 | 2.3315 | 131.74 | 61.52 | 0.0066489 | 99.799 | 1118.9 |  | 9973 | 131.74 | 2.3315 | 61.52 | 0.0066489 | 99.799 | 1118.9 | 1019.101
9974 | 2.3321 | 131.75 | 61.52 | 0.0066506 | 99.809 | 1118.9 |  | 9974 | 131.75 | 2.3321 | 61.52 | 0.0066506 | 99.809 | 1118.9 | 1019.091
9975 | 2.3327 | 131.76 | 61.52 | 0.0066522 | 99.819 | 1118.9 |  | 9975 | 131.76 | 2.3327 | 61.52 | 0.0066522 | 99.819 | 1118.9 | 1019.081
9976 | 2.3334 | 131.77 | 61.52 | 0.0066539 | 99.829 | 1118.9 |  | 9976 | 131.77 | 2.3334 | 61.52 | 0.0066539 | 99.829 | 1118.9 | 1019.071
9977 | 2.334 | 131.78 | 61.519 | 0.0066555 | 99.839 | 1118.9 |  | 9977 | 131.78 | 2.334 | 61.519 | 0.0066555 | 99.839 | 1118.9 | 1019.061
9978 | 2.3346 | 131.79 | 61.519 | 0.0066572 | 99.849 | 1118.9 |  | 9978 | 131.79 | 2.3346 | 61.519 | 0.0066572 | 99.849 | 1118.9 | 1019.051
9979 | 2.3352 | 131.8 | 61.519 | 0.0066589 | 99.859 | 1118.9 |  | 9979 | 131.8 | 2.3352 | 61.519 | 0.0066589 | 99.859 | 1118.9 | 1019.041
9980 | 2.3358 | 131.81 | 61.519 | 0.0066605 | 99.869 | 1118.9 |  | 9980 | 131.81 | 2.3358 | 61.519 | 0.0066605 | 99.869 | 1118.9 | 1019.031
9981 | 2.3365 | 131.82 | 61.519 | 0.0066622 | 99.879 | 1118.9 |  | 9981 | 131.82 | 2.3365 | 61.519 | 0.0066622 | 99.879 | 1118.9 | 1019.021
9982 | 2.3371 | 131.83 | 61.519 | 0.0066638 | 99.889 | 1118.9 |  | 9982 | 131.83 | 2.3371 | 61.519 | 0.0066638 | 99.889 | 1118.9 | 1019.011
9983 | 2.3377 | 131.84 | 61.518 | 0.0066655 | 99.899 | 1118.9 |  | 9983 | 131.84 | 2.3377 | 61.518 | 0.0066655 | 99.899 | 1118.9 | 1019.001
9984 | 2.3383 | 131.85 | 61.518 | 0.0066672 | 99.909 | 1118.9 |  | 9984 | 131.85 | 2.3383 | 61.518 | 0.0066672 | 99.909 | 1118.9 | 1018.991
9985 | 2.3389 | 131.86 | 61.518 | 0.0066688 | 99.919 | 1118.9 |  | 9985 | 131.86 | 2.3389 | 61.518 | 0.0066688 | 99.919 | 1118.9 | 1018.981
9986 | 2.3396 | 131.87 | 61.518 | 0.0066705 | 99.929 | 1119 |  | 9986 | 131.87 | 2.3396 | 61.518 | 0.0066705 | 99.929 | 1119 | 1019.071
9987 | 2.3402 | 131.88 | 61.518 | 0.0066722 | 99.939 | 1119 |  | 9987 | 131.88 | 2.3402 | 61.518 | 0.0066722 | 99.939 | 1119 | 1019.061
9988 | 2.3408 | 131.89 | 61.517 | 0.0066738 | 99.949 | 1119 |  | 9988 | 131.89 | 2.3408 | 61.517 | 0.0066738 | 99.949 | 1119 | 1019.051
9989 | 2.3414 | 131.9 | 61.517 | 0.0066755 | 99.959 | 1119 |  | 9989 | 131.9 | 2.3414 | 61.517 | 0.0066755 | 99.959 | 1119 | 1019.041
9990 | 2.342 | 131.91 | 61.517 | 0.0066771 | 99.969 | 1119 |  | 9990 | 131.91 | 2.342 | 61.517 | 0.0066771 | 99.969 | 1119 | 1019.031
9991 | 2.3427 | 131.92 | 61.517 | 0.0066788 | 99.979 | 1119 |  | 9991 | 131.92 | 2.3427 | 61.517 | 0.0066788 | 99.979 | 1119 | 1019.021
9992 | 2.3433 | 131.93 | 61.517 | 0.0066805 | 99.989 | 1119 |  | 9992 | 131.93 | 2.3433 | 61.517 | 0.0066805 | 99.989 | 1119 | 1019.011
9993 | 2.3439 | 131.94 | 61.517 | 0.0066821 | 99.999 | 1119 |  | 9993 | 131.94 | 2.3439 | 61.517 | 0.0066821 | 99.999 | 1119 | 1019.001
9994 | 2.3445 | 131.95 | 61.516 | 0.0066838 | 100.01 | 1119 |  | 9994 | 131.95 | 2.3445 | 61.516 | 0.0066838 | 100.01 | 1119 | 1018.99
9995 | 2.3452 | 131.96 | 61.516 | 0.0066855 | 100.02 | 1119 |  | 9995 | 131.96 | 2.3452 | 61.516 | 0.0066855 | 100.02 | 1119 | 1018.98
9996 | 2.3458 | 131.97 | 61.516 | 0.0066871 | 100.03 | 1119 |  | 9996 | 131.97 | 2.3458 | 61.516 | 0.0066871 | 100.03 | 1119 | 1018.97
9997 | 2.3464 | 131.98 | 61.516 | 0.0066888 | 100.04 | 1119 |  | 9997 | 131.98 | 2.3464 | 61.516 | 0.0066888 | 100.04 | 1119 | 1018.96
9998 | 2.347 | 131.99 | 61.516 | 0.0066905 | 100.05 | 1119 |  | 9998 | 131.99 | 2.347 | 61.516 | 0.0066905 | 100.05 | 1119 | 1018.95
9999 | 2.3476 | 132 | 61.516 | 0.0066921 | 100.06 | 1119 |  | 9999 | 132 | 2.3476 | 61.516 | 0.0066921 | 100.06 | 1119 | 1018.94
10000 | 2.3483 | 132.01 | 61.515 | 0.0066938 | 100.07 | 1119 |  | 10000 | 132.01 | 2.3483 | 61.515 | 0.0066938 | 100.07 | 1119 | 1018.93
10001 | 2.3489 | 132.02 | 61.515 | 0.0066955 | 100.08 | 1119 |  | 10001 | 132.02 | 2.3489 | 61.515 | 0.0066955 | 100.08 | 1119 | 1018.92
10002 | 2.3495 | 132.03 | 61.515 | 0.0066971 | 100.09 | 1119 |  | 10002 | 132.03 | 2.3495 | 61.515 | 0.0066971 | 100.09 | 1119 | 1018.91
10003 | 2.3501 | 132.04 | 61.515 | 0.0066988 | 100.1 | 1119 |  | 10003 | 132.04 | 2.3501 | 61.515 | 0.0066988 | 100.1 | 1119 | 1018.9
10004 | 2.3508 | 132.05 | 61.515 | 0.0067005 | 100.11 | 1119 |  | 10004 | 132.05 | 2.3508 | 61.515 | 0.0067005 | 100.11 | 1119 | 1018.89
10005 | 2.3514 | 132.06 | 61.515 | 0.0067021 | 100.12 | 1119 |  | 10005 | 132.06 | 2.3514 | 61.515 | 0.0067021 | 100.12 | 1119 | 1018.88
10006 | 2.352 | 132.07 | 61.514 | 0.0067038 | 100.13 | 1119 |  | 10006 | 132.07 | 2.352 | 61.514 | 0.0067038 | 100.13 | 1119 | 1018.87
10007 | 2.3526 | 132.08 | 61.514 | 0.0067055 | 100.14 | 1119 |  | 10007 | 132.08 | 2.3526 | 61.514 | 0.0067055 | 100.14 | 1119 | 1018.86
10008 | 2.3533 | 132.09 | 61.514 | 0.0067071 | 100.15 | 1119 |  | 10008 | 132.09 | 2.3533 | 61.514 | 0.0067071 | 100.15 | 1119 | 1018.85
10009 | 2.3539 | 132.1 | 61.514 | 0.0067088 | 100.16 | 1119 |  | 10009 | 132.1 | 2.3539 | 61.514 | 0.0067088 | 100.16 | 1119 | 1018.84
10010 | 2.3545 | 132.11 | 61.514 | 0.0067105 | 100.17 | 1119.1 |  | 10010 | 132.11 | 2.3545 | 61.514 | 0.0067105 | 100.17 | 1119.1 | 1018.93
10011 | 2.3551 | 132.12 | 61.514 | 0.0067122 | 100.18 | 1119.1 |  | 10011 | 132.12 | 2.3551 | 61.514 | 0.0067122 | 100.18 | 1119.1 | 1018.92
10012 | 2.3557 | 132.13 | 61.513 | 0.0067138 | 100.19 | 1119.1 |  | 10012 | 132.13 | 2.3557 | 61.513 | 0.0067138 | 100.19 | 1119.1 | 1018.91
10013 | 2.3564 | 132.14 | 61.513 | 0.0067155 | 100.2 | 1119.1 |  | 10013 | 132.14 | 2.3564 | 61.513 | 0.0067155 | 100.2 | 1119.1 | 1018.9
10014 | 2.357 | 132.15 | 61.513 | 0.0067172 | 100.21 | 1119.1 |  | 10014 | 132.15 | 2.357 | 61.513 | 0.0067172 | 100.21 | 1119.1 | 1018.89
10015 | 2.3576 | 132.16 | 61.513 | 0.0067188 | 100.22 | 1119.1 |  | 10015 | 132.16 | 2.3576 | 61.513 | 0.0067188 | 100.22 | 1119.1 | 1018.88
10016 | 2.3582 | 132.17 | 61.513 | 0.0067205 | 100.23 | 1119.1 |  | 10016 | 132.17 | 2.3582 | 61.513 | 0.0067205 | 100.23 | 1119.1 | 1018.87
10017 | 2.3589 | 132.18 | 61.513 | 0.0067222 | 100.24 | 1119.1 |  | 10017 | 132.18 | 2.3589 | 61.513 | 0.0067222 | 100.24 | 1119.1 | 1018.86
10018 | 2.3595 | 132.19 | 61.512 | 0.0067239 | 100.25 | 1119.1 |  | 10018 | 132.19 | 2.3595 | 61.512 | 0.0067239 | 100.25 | 1119.1 | 1018.85
10019 | 2.3601 | 132.2 | 61.512 | 0.0067255 | 100.26 | 1119.1 |  | 10019 | 132.2 | 2.3601 | 61.512 | 0.0067255 | 100.26 | 1119.1 | 1018.84
10020 | 2.3607 | 132.21 | 61.512 | 0.0067272 | 100.27 | 1119.1 |  | 10020 | 132.21 | 2.3607 | 61.512 | 0.0067272 | 100.27 | 1119.1 | 1018.83
10021 | 2.3614 | 132.22 | 61.512 | 0.0067289 | 100.28 | 1119.1 |  | 10021 | 132.22 | 2.3614 | 61.512 | 0.0067289 | 100.28 | 1119.1 | 1018.82
10022 | 2.362 | 132.23 | 61.512 | 0.0067306 | 100.29 | 1119.1 |  | 10022 | 132.23 | 2.362 | 61.512 | 0.0067306 | 100.29 | 1119.1 | 1018.81
10023 | 2.3626 | 132.24 | 61.512 | 0.0067322 | 100.3 | 1119.1 |  | 10023 | 132.24 | 2.3626 | 61.512 | 0.0067322 | 100.3 | 1119.1 | 1018.8
10024 | 2.3632 | 132.25 | 61.511 | 0.0067339 | 100.31 | 1119.1 |  | 10024 | 132.25 | 2.3632 | 61.511 | 0.0067339 | 100.31 | 1119.1 | 1018.79
10025 | 2.3639 | 132.26 | 61.511 | 0.0067356 | 100.32 | 1119.1 |  | 10025 | 132.26 | 2.3639 | 61.511 | 0.0067356 | 100.32 | 1119.1 | 1018.78
10026 | 2.3645 | 132.27 | 61.511 | 0.0067373 | 100.33 | 1119.1 |  | 10026 | 132.27 | 2.3645 | 61.511 | 0.0067373 | 100.33 | 1119.1 | 1018.77
10027 | 2.3651 | 132.28 | 61.511 | 0.0067389 | 100.34 | 1119.1 |  | 10027 | 132.28 | 2.3651 | 61.511 | 0.0067389 | 100.34 | 1119.1 | 1018.76
10028 | 2.3658 | 132.29 | 61.511 | 0.0067406 | 100.35 | 1119.1 |  | 10028 | 132.29 | 2.3658 | 61.511 | 0.0067406 | 100.35 | 1119.1 | 1018.75
10029 | 2.3664 | 132.3 | 61.511 | 0.0067423 | 100.36 | 1119.1 |  | 10029 | 132.3 | 2.3664 | 61.511 | 0.0067423 | 100.36 | 1119.1 | 1018.74
10030 | 2.367 | 132.31 | 61.51 | 0.006744 | 100.37 | 1119.1 |  | 10030 | 132.31 | 2.367 | 61.51 | 0.006744 | 100.37 | 1119.1 | 1018.73
10031 | 2.3676 | 132.32 | 61.51 | 0.0067456 | 100.38 | 1119.1 |  | 10031 | 132.32 | 2.3676 | 61.51 | 0.0067456 | 100.38 | 1119.1 | 1018.72
10032 | 2.3683 | 132.33 | 61.51 | 0.0067473 | 100.39 | 1119.1 |  | 10032 | 132.33 | 2.3683 | 61.51 | 0.0067473 | 100.39 | 1119.1 | 1018.71
10033 | 2.3689 | 132.34 | 61.51 | 0.006749 | 100.4 | 1119.1 |  | 10033 | 132.34 | 2.3689 | 61.51 | 0.006749 | 100.4 | 1119.1 | 1018.7
10034 | 2.3695 | 132.35 | 61.51 | 0.0067507 | 100.41 | 1119.2 |  | 10034 | 132.35 | 2.3695 | 61.51 | 0.0067507 | 100.41 | 1119.2 | 1018.79
10035 | 2.3701 | 132.36 | 61.51 | 0.0067524 | 100.42 | 1119.2 |  | 10035 | 132.36 | 2.3701 | 61.51 | 0.0067524 | 100.42 | 1119.2 | 1018.78
10036 | 2.3708 | 132.37 | 61.509 | 0.006754 | 100.43 | 1119.2 |  | 10036 | 132.37 | 2.3708 | 61.509 | 0.006754 | 100.43 | 1119.2 | 1018.77
10037 | 2.3714 | 132.38 | 61.509 | 0.0067557 | 100.44 | 1119.2 |  | 10037 | 132.38 | 2.3714 | 61.509 | 0.0067557 | 100.44 | 1119.2 | 1018.76
10038 | 2.372 | 132.39 | 61.509 | 0.0067574 | 100.45 | 1119.2 |  | 10038 | 132.39 | 2.372 | 61.509 | 0.0067574 | 100.45 | 1119.2 | 1018.75
10039 | 2.3727 | 132.4 | 61.509 | 0.0067591 | 100.46 | 1119.2 |  | 10039 | 132.4 | 2.3727 | 61.509 | 0.0067591 | 100.46 | 1119.2 | 1018.74
10040 | 2.3733 | 132.41 | 61.509 | 0.0067608 | 100.47 | 1119.2 |  | 10040 | 132.41 | 2.3733 | 61.509 | 0.0067608 | 100.47 | 1119.2 | 1018.73
10041 | 2.3739 | 132.42 | 61.509 | 0.0067624 | 100.48 | 1119.2 |  | 10041 | 132.42 | 2.3739 | 61.509 | 0.0067624 | 100.48 | 1119.2 | 1018.72
10042 | 2.3745 | 132.43 | 61.508 | 0.0067641 | 100.49 | 1119.2 |  | 10042 | 132.43 | 2.3745 | 61.508 | 0.0067641 | 100.49 | 1119.2 | 1018.71
10043 | 2.3752 | 132.44 | 61.508 | 0.0067658 | 100.5 | 1119.2 |  | 10043 | 132.44 | 2.3752 | 61.508 | 0.0067658 | 100.5 | 1119.2 | 1018.7
10044 | 2.3758 | 132.45 | 61.508 | 0.0067675 | 100.51 | 1119.2 |  | 10044 | 132.45 | 2.3758 | 61.508 | 0.0067675 | 100.51 | 1119.2 | 1018.69
10045 | 2.3764 | 132.46 | 61.508 | 0.0067692 | 100.52 | 1119.2 |  | 10045 | 132.46 | 2.3764 | 61.508 | 0.0067692 | 100.52 | 1119.2 | 1018.68
10046 | 2.3771 | 132.47 | 61.508 | 0.0067708 | 100.53 | 1119.2 |  | 10046 | 132.47 | 2.3771 | 61.508 | 0.0067708 | 100.53 | 1119.2 | 1018.67
10047 | 2.3777 | 132.48 | 61.508 | 0.0067725 | 100.54 | 1119.2 |  | 10047 | 132.48 | 2.3777 | 61.508 | 0.0067725 | 100.54 | 1119.2 | 1018.66
10048 | 2.3783 | 132.49 | 61.507 | 0.0067742 | 100.55 | 1119.2 |  | 10048 | 132.49 | 2.3783 | 61.507 | 0.0067742 | 100.55 | 1119.2 | 1018.65
10049 | 2.3789 | 132.5 | 61.507 | 0.0067759 | 100.56 | 1119.2 |  | 10049 | 132.5 | 2.3789 | 61.507 | 0.0067759 | 100.56 | 1119.2 | 1018.64
10050 | 2.3796 | 132.51 | 61.507 | 0.0067776 | 100.57 | 1119.2 |  | 10050 | 132.51 | 2.3796 | 61.507 | 0.0067776 | 100.57 | 1119.2 | 1018.63
10051 | 2.3802 | 132.52 | 61.507 | 0.0067793 | 100.58 | 1119.2 |  | 10051 | 132.52 | 2.3802 | 61.507 | 0.0067793 | 100.58 | 1119.2 | 1018.62
10052 | 2.3808 | 132.53 | 61.507 | 0.0067809 | 100.59 | 1119.2 |  | 10052 | 132.53 | 2.3808 | 61.507 | 0.0067809 | 100.59 | 1119.2 | 1018.61
10053 | 2.3815 | 132.54 | 61.506 | 0.0067826 | 100.6 | 1119.2 |  | 10053 | 132.54 | 2.3815 | 61.506 | 0.0067826 | 100.6 | 1119.2 | 1018.6
10054 | 2.3821 | 132.55 | 61.506 | 0.0067843 | 100.61 | 1119.2 |  | 10054 | 132.55 | 2.3821 | 61.506 | 0.0067843 | 100.61 | 1119.2 | 1018.59
10055 | 2.3827 | 132.56 | 61.506 | 0.006786 | 100.62 | 1119.2 |  | 10055 | 132.56 | 2.3827 | 61.506 | 0.006786 | 100.62 | 1119.2 | 1018.58
10056 | 2.3834 | 132.57 | 61.506 | 0.0067877 | 100.63 | 1119.2 |  | 10056 | 132.57 | 2.3834 | 61.506 | 0.0067877 | 100.63 | 1119.2 | 1018.57
10057 | 2.384 | 132.58 | 61.506 | 0.0067894 | 100.64 | 1119.2 |  | 10057 | 132.58 | 2.384 | 61.506 | 0.0067894 | 100.64 | 1119.2 | 1018.56
10058 | 2.3846 | 132.59 | 61.506 | 0.0067911 | 100.65 | 1119.3 |  | 10058 | 132.59 | 2.3846 | 61.506 | 0.0067911 | 100.65 | 1119.3 | 1018.65
10059 | 2.3852 | 132.6 | 61.505 | 0.0067928 | 100.66 | 1119.3 |  | 10059 | 132.6 | 2.3852 | 61.505 | 0.0067928 | 100.66 | 1119.3 | 1018.64
10060 | 2.3859 | 132.61 | 61.505 | 0.0067944 | 100.67 | 1119.3 |  | 10060 | 132.61 | 2.3859 | 61.505 | 0.0067944 | 100.67 | 1119.3 | 1018.63
10061 | 2.3865 | 132.62 | 61.505 | 0.0067961 | 100.68 | 1119.3 |  | 10061 | 132.62 | 2.3865 | 61.505 | 0.0067961 | 100.68 | 1119.3 | 1018.62
10062 | 2.3871 | 132.63 | 61.505 | 0.0067978 | 100.69 | 1119.3 |  | 10062 | 132.63 | 2.3871 | 61.505 | 0.0067978 | 100.69 | 1119.3 | 1018.61
10063 | 2.3878 | 132.64 | 61.505 | 0.0067995 | 100.7 | 1119.3 |  | 10063 | 132.64 | 2.3878 | 61.505 | 0.0067995 | 100.7 | 1119.3 | 1018.6
10064 | 2.3884 | 132.65 | 61.505 | 0.0068012 | 100.71 | 1119.3 |  | 10064 | 132.65 | 2.3884 | 61.505 | 0.0068012 | 100.71 | 1119.3 | 1018.59
10065 | 2.389 | 132.66 | 61.504 | 0.0068029 | 100.72 | 1119.3 |  | 10065 | 132.66 | 2.389 | 61.504 | 0.0068029 | 100.72 | 1119.3 | 1018.58
10066 | 2.3897 | 132.67 | 61.504 | 0.0068046 | 100.73 | 1119.3 |  | 10066 | 132.67 | 2.3897 | 61.504 | 0.0068046 | 100.73 | 1119.3 | 1018.57
10067 | 2.3903 | 132.68 | 61.504 | 0.0068063 | 100.74 | 1119.3 |  | 10067 | 132.68 | 2.3903 | 61.504 | 0.0068063 | 100.74 | 1119.3 | 1018.56
10068 | 2.3909 | 132.69 | 61.504 | 0.006808 | 100.75 | 1119.3 |  | 10068 | 132.69 | 2.3909 | 61.504 | 0.006808 | 100.75 | 1119.3 | 1018.55
10069 | 2.3916 | 132.7 | 61.504 | 0.0068096 | 100.76 | 1119.3 |  | 10069 | 132.7 | 2.3916 | 61.504 | 0.0068096 | 100.76 | 1119.3 | 1018.54
10070 | 2.3922 | 132.71 | 61.504 | 0.0068113 | 100.77 | 1119.3 |  | 10070 | 132.71 | 2.3922 | 61.504 | 0.0068113 | 100.77 | 1119.3 | 1018.53
10071 | 2.3928 | 132.72 | 61.503 | 0.006813 | 100.78 | 1119.3 |  | 10071 | 132.72 | 2.3928 | 61.503 | 0.006813 | 100.78 | 1119.3 | 1018.52
10072 | 2.3935 | 132.73 | 61.503 | 0.0068147 | 100.79 | 1119.3 |  | 10072 | 132.73 | 2.3935 | 61.503 | 0.0068147 | 100.79 | 1119.3 | 1018.51
10073 | 2.3941 | 132.74 | 61.503 | 0.0068164 | 100.8 | 1119.3 |  | 10073 | 132.74 | 2.3941 | 61.503 | 0.0068164 | 100.8 | 1119.3 | 1018.5
10074 | 2.3947 | 132.75 | 61.503 | 0.0068181 | 100.81 | 1119.3 |  | 10074 | 132.75 | 2.3947 | 61.503 | 0.0068181 | 100.81 | 1119.3 | 1018.49
10075 | 2.3954 | 132.76 | 61.503 | 0.0068198 | 100.82 | 1119.3 |  | 10075 | 132.76 | 2.3954 | 61.503 | 0.0068198 | 100.82 | 1119.3 | 1018.48
10076 | 2.396 | 132.77 | 61.503 | 0.0068215 | 100.83 | 1119.3 |  | 10076 | 132.77 | 2.396 | 61.503 | 0.0068215 | 100.83 | 1119.3 | 1018.47
10077 | 2.3966 | 132.78 | 61.502 | 0.0068232 | 100.84 | 1119.3 |  | 10077 | 132.78 | 2.3966 | 61.502 | 0.0068232 | 100.84 | 1119.3 | 1018.46
10078 | 2.3973 | 132.79 | 61.502 | 0.0068249 | 100.85 | 1119.3 |  | 10078 | 132.79 | 2.3973 | 61.502 | 0.0068249 | 100.85 | 1119.3 | 1018.45
10079 | 2.3979 | 132.8 | 61.502 | 0.0068266 | 100.86 | 1119.3 |  | 10079 | 132.8 | 2.3979 | 61.502 | 0.0068266 | 100.86 | 1119.3 | 1018.44
10080 | 2.3985 | 132.81 | 61.502 | 0.0068283 | 100.87 | 1119.3 |  | 10080 | 132.81 | 2.3985 | 61.502 | 0.0068283 | 100.87 | 1119.3 | 1018.43
10081 | 2.3992 | 132.82 | 61.502 | 0.00683 | 100.88 | 1119.4 |  | 10081 | 132.82 | 2.3992 | 61.502 | 0.00683 | 100.88 | 1119.4 | 1018.52
10082 | 2.3998 | 132.83 | 61.502 | 0.0068317 | 100.89 | 1119.4 |  | 10082 | 132.83 | 2.3998 | 61.502 | 0.0068317 | 100.89 | 1119.4 | 1018.51
10083 | 2.4004 | 132.84 | 61.501 | 0.0068334 | 100.9 | 1119.4 |  | 10083 | 132.84 | 2.4004 | 61.501 | 0.0068334 | 100.9 | 1119.4 | 1018.5
10084 | 2.4011 | 132.85 | 61.501 | 0.0068351 | 100.91 | 1119.4 |  | 10084 | 132.85 | 2.4011 | 61.501 | 0.0068351 | 100.91 | 1119.4 | 1018.49
10085 | 2.4017 | 132.86 | 61.501 | 0.0068368 | 100.92 | 1119.4 |  | 10085 | 132.86 | 2.4017 | 61.501 | 0.0068368 | 100.92 | 1119.4 | 1018.48
10086 | 2.4023 | 132.87 | 61.501 | 0.0068385 | 100.93 | 1119.4 |  | 10086 | 132.87 | 2.4023 | 61.501 | 0.0068385 | 100.93 | 1119.4 | 1018.47
10087 | 2.403 | 132.88 | 61.501 | 0.0068401 | 100.94 | 1119.4 |  | 10087 | 132.88 | 2.403 | 61.501 | 0.0068401 | 100.94 | 1119.4 | 1018.46
10088 | 2.4036 | 132.89 | 61.501 | 0.0068418 | 100.95 | 1119.4 |  | 10088 | 132.89 | 2.4036 | 61.501 | 0.0068418 | 100.95 | 1119.4 | 1018.45
10089 | 2.4042 | 132.9 | 61.5 | 0.0068435 | 100.96 | 1119.4 |  | 10089 | 132.9 | 2.4042 | 61.5 | 0.0068435 | 100.96 | 1119.4 | 1018.44
10090 | 2.4049 | 132.91 | 61.5 | 0.0068452 | 100.97 | 1119.4 |  | 10090 | 132.91 | 2.4049 | 61.5 | 0.0068452 | 100.97 | 1119.4 | 1018.43
10091 | 2.4055 | 132.92 | 61.5 | 0.0068469 | 100.98 | 1119.4 |  | 10091 | 132.92 | 2.4055 | 61.5 | 0.0068469 | 100.98 | 1119.4 | 1018.42
10092 | 2.4061 | 132.93 | 61.5 | 0.0068486 | 100.99 | 1119.4 |  | 10092 | 132.93 | 2.4061 | 61.5 | 0.0068486 | 100.99 | 1119.4 | 1018.41
10093 | 2.4068 | 132.94 | 61.5 | 0.0068503 | 101 | 1119.4 |  | 10093 | 132.94 | 2.4068 | 61.5 | 0.0068503 | 101 | 1119.4 | 1018.4
10094 | 2.4074 | 132.95 | 61.5 | 0.006852 | 101.01 | 1119.4 |  | 10094 | 132.95 | 2.4074 | 61.5 | 0.006852 | 101.01 | 1119.4 | 1018.39
10095 | 2.4081 | 132.96 | 61.499 | 0.0068537 | 101.02 | 1119.4 |  | 10095 | 132.96 | 2.4081 | 61.499 | 0.0068537 | 101.02 | 1119.4 | 1018.38
10096 | 2.4087 | 132.97 | 61.499 | 0.0068554 | 101.03 | 1119.4 |  | 10096 | 132.97 | 2.4087 | 61.499 | 0.0068554 | 101.03 | 1119.4 | 1018.37
10097 | 2.4093 | 132.98 | 61.499 | 0.0068571 | 101.04 | 1119.4 |  | 10097 | 132.98 | 2.4093 | 61.499 | 0.0068571 | 101.04 | 1119.4 | 1018.36
10098 | 2.41 | 132.99 | 61.499 | 0.0068588 | 101.05 | 1119.4 |  | 10098 | 132.99 | 2.41 | 61.499 | 0.0068588 | 101.05 | 1119.4 | 1018.35
10099 | 2.4106 | 133 | 61.499 | 0.0068605 | 101.06 | 1119.4 |  | 10099 | 133 | 2.4106 | 61.499 | 0.0068605 | 101.06 | 1119.4 | 1018.34
10100 | 2.4112 | 133.01 | 61.499 | 0.0068622 | 101.07 | 1119.4 |  | 10100 | 133.01 | 2.4112 | 61.499 | 0.0068622 | 101.07 | 1119.4 | 1018.33
10101 | 2.4119 | 133.02 | 61.498 | 0.0068639 | 101.08 | 1119.4 |  | 10101 | 133.02 | 2.4119 | 61.498 | 0.0068639 | 101.08 | 1119.4 | 1018.32
10102 | 2.4125 | 133.03 | 61.498 | 0.0068657 | 101.09 | 1119.4 |  | 10102 | 133.03 | 2.4125 | 61.498 | 0.0068657 | 101.09 | 1119.4 | 1018.31
10103 | 2.4131 | 133.04 | 61.498 | 0.0068674 | 101.1 | 1119.4 |  | 10103 | 133.04 | 2.4131 | 61.498 | 0.0068674 | 101.1 | 1119.4 | 1018.3
10104 | 2.4138 | 133.05 | 61.498 | 0.0068691 | 101.11 | 1119.4 |  | 10104 | 133.05 | 2.4138 | 61.498 | 0.0068691 | 101.11 | 1119.4 | 1018.29
10105 | 2.4144 | 133.06 | 61.498 | 0.0068708 | 101.12 | 1119.5 |  | 10105 | 133.06 | 2.4144 | 61.498 | 0.0068708 | 101.12 | 1119.5 | 1018.38
10106 | 2.4151 | 133.07 | 61.497 | 0.0068725 | 101.13 | 1119.5 |  | 10106 | 133.07 | 2.4151 | 61.497 | 0.0068725 | 101.13 | 1119.5 | 1018.37
10107 | 2.4157 | 133.08 | 61.497 | 0.0068742 | 101.14 | 1119.5 |  | 10107 | 133.08 | 2.4157 | 61.497 | 0.0068742 | 101.14 | 1119.5 | 1018.36
10108 | 2.4163 | 133.09 | 61.497 | 0.0068759 | 101.15 | 1119.5 |  | 10108 | 133.09 | 2.4163 | 61.497 | 0.0068759 | 101.15 | 1119.5 | 1018.35
10109 | 2.417 | 133.1 | 61.497 | 0.0068776 | 101.16 | 1119.5 |  | 10109 | 133.1 | 2.417 | 61.497 | 0.0068776 | 101.16 | 1119.5 | 1018.34
10110 | 2.4176 | 133.11 | 61.497 | 0.0068793 | 101.17 | 1119.5 |  | 10110 | 133.11 | 2.4176 | 61.497 | 0.0068793 | 101.17 | 1119.5 | 1018.33
10111 | 2.4182 | 133.12 | 61.497 | 0.006881 | 101.18 | 1119.5 |  | 10111 | 133.12 | 2.4182 | 61.497 | 0.006881 | 101.18 | 1119.5 | 1018.32
10112 | 2.4189 | 133.13 | 61.496 | 0.0068827 | 101.19 | 1119.5 |  | 10112 | 133.13 | 2.4189 | 61.496 | 0.0068827 | 101.19 | 1119.5 | 1018.31
10113 | 2.4195 | 133.14 | 61.496 | 0.0068844 | 101.2 | 1119.5 |  | 10113 | 133.14 | 2.4195 | 61.496 | 0.0068844 | 101.2 | 1119.5 | 1018.3
10114 | 2.4202 | 133.15 | 61.496 | 0.0068861 | 101.21 | 1119.5 |  | 10114 | 133.15 | 2.4202 | 61.496 | 0.0068861 | 101.21 | 1119.5 | 1018.29
10115 | 2.4208 | 133.16 | 61.496 | 0.0068878 | 101.22 | 1119.5 |  | 10115 | 133.16 | 2.4208 | 61.496 | 0.0068878 | 101.22 | 1119.5 | 1018.28
10116 | 2.4214 | 133.17 | 61.496 | 0.0068895 | 101.23 | 1119.5 |  | 10116 | 133.17 | 2.4214 | 61.496 | 0.0068895 | 101.23 | 1119.5 | 1018.27
10117 | 2.4221 | 133.18 | 61.496 | 0.0068912 | 101.24 | 1119.5 |  | 10117 | 133.18 | 2.4221 | 61.496 | 0.0068912 | 101.24 | 1119.5 | 1018.26
10118 | 2.4227 | 133.19 | 61.495 | 0.0068929 | 101.25 | 1119.5 |  | 10118 | 133.19 | 2.4227 | 61.495 | 0.0068929 | 101.25 | 1119.5 | 1018.25
10119 | 2.4234 | 133.2 | 61.495 | 0.0068947 | 101.26 | 1119.5 |  | 10119 | 133.2 | 2.4234 | 61.495 | 0.0068947 | 101.26 | 1119.5 | 1018.24
10120 | 2.424 | 133.21 | 61.495 | 0.0068964 | 101.27 | 1119.5 |  | 10120 | 133.21 | 2.424 | 61.495 | 0.0068964 | 101.27 | 1119.5 | 1018.23
10121 | 2.4246 | 133.22 | 61.495 | 0.0068981 | 101.28 | 1119.5 |  | 10121 | 133.22 | 2.4246 | 61.495 | 0.0068981 | 101.28 | 1119.5 | 1018.22
10122 | 2.4253 | 133.23 | 61.495 | 0.0068998 | 101.29 | 1119.5 |  | 10122 | 133.23 | 2.4253 | 61.495 | 0.0068998 | 101.29 | 1119.5 | 1018.21
10123 | 2.4259 | 133.24 | 61.495 | 0.0069015 | 101.3 | 1119.5 |  | 10123 | 133.24 | 2.4259 | 61.495 | 0.0069015 | 101.3 | 1119.5 | 1018.2
10124 | 2.4266 | 133.25 | 61.494 | 0.0069032 | 101.31 | 1119.5 |  | 10124 | 133.25 | 2.4266 | 61.494 | 0.0069032 | 101.31 | 1119.5 | 1018.19
10125 | 2.4272 | 133.26 | 61.494 | 0.0069049 | 101.32 | 1119.5 |  | 10125 | 133.26 | 2.4272 | 61.494 | 0.0069049 | 101.32 | 1119.5 | 1018.18
10126 | 2.4278 | 133.27 | 61.494 | 0.0069066 | 101.33 | 1119.5 |  | 10126 | 133.27 | 2.4278 | 61.494 | 0.0069066 | 101.33 | 1119.5 | 1018.17
10127 | 2.4285 | 133.28 | 61.494 | 0.0069083 | 101.34 | 1119.5 |  | 10127 | 133.28 | 2.4285 | 61.494 | 0.0069083 | 101.34 | 1119.5 | 1018.16
10128 | 2.4291 | 133.29 | 61.494 | 0.00691 | 101.35 | 1119.5 |  | 10128 | 133.29 | 2.4291 | 61.494 | 0.00691 | 101.35 | 1119.5 | 1018.15
10129 | 2.4298 | 133.3 | 61.494 | 0.0069118 | 101.36 | 1119.6 |  | 10129 | 133.3 | 2.4298 | 61.494 | 0.0069118 | 101.36 | 1119.6 | 1018.24
10130 | 2.4304 | 133.31 | 61.493 | 0.0069135 | 101.37 | 1119.6 |  | 10130 | 133.31 | 2.4304 | 61.493 | 0.0069135 | 101.37 | 1119.6 | 1018.23
10131 | 2.431 | 133.32 | 61.493 | 0.0069152 | 101.38 | 1119.6 |  | 10131 | 133.32 | 2.431 | 61.493 | 0.0069152 | 101.38 | 1119.6 | 1018.22
10132 | 2.4317 | 133.33 | 61.493 | 0.0069169 | 101.39 | 1119.6 |  | 10132 | 133.33 | 2.4317 | 61.493 | 0.0069169 | 101.39 | 1119.6 | 1018.21
10133 | 2.4323 | 133.34 | 61.493 | 0.0069186 | 101.4 | 1119.6 |  | 10133 | 133.34 | 2.4323 | 61.493 | 0.0069186 | 101.4 | 1119.6 | 1018.2
10134 | 2.433 | 133.35 | 61.493 | 0.0069203 | 101.41 | 1119.6 |  | 10134 | 133.35 | 2.433 | 61.493 | 0.0069203 | 101.41 | 1119.6 | 1018.19
10135 | 2.4336 | 133.36 | 61.493 | 0.006922 | 101.42 | 1119.6 |  | 10135 | 133.36 | 2.4336 | 61.493 | 0.006922 | 101.42 | 1119.6 | 1018.18
10136 | 2.4343 | 133.37 | 61.492 | 0.0069238 | 101.43 | 1119.6 |  | 10136 | 133.37 | 2.4343 | 61.492 | 0.0069238 | 101.43 | 1119.6 | 1018.17
10137 | 2.4349 | 133.38 | 61.492 | 0.0069255 | 101.44 | 1119.6 |  | 10137 | 133.38 | 2.4349 | 61.492 | 0.0069255 | 101.44 | 1119.6 | 1018.16
10138 | 2.4355 | 133.39 | 61.492 | 0.0069272 | 101.45 | 1119.6 |  | 10138 | 133.39 | 2.4355 | 61.492 | 0.0069272 | 101.45 | 1119.6 | 1018.15
10139 | 2.4362 | 133.4 | 61.492 | 0.0069289 | 101.46 | 1119.6 |  | 10139 | 133.4 | 2.4362 | 61.492 | 0.0069289 | 101.46 | 1119.6 | 1018.14
10140 | 2.4368 | 133.41 | 61.492 | 0.0069306 | 101.47 | 1119.6 |  | 10140 | 133.41 | 2.4368 | 61.492 | 0.0069306 | 101.47 | 1119.6 | 1018.13
10141 | 2.4375 | 133.42 | 61.492 | 0.0069323 | 101.48 | 1119.6 |  | 10141 | 133.42 | 2.4375 | 61.492 | 0.0069323 | 101.48 | 1119.6 | 1018.12
10142 | 2.4381 | 133.43 | 61.491 | 0.0069341 | 101.49 | 1119.6 |  | 10142 | 133.43 | 2.4381 | 61.491 | 0.0069341 | 101.49 | 1119.6 | 1018.11
10143 | 2.4388 | 133.44 | 61.491 | 0.0069358 | 101.5 | 1119.6 |  | 10143 | 133.44 | 2.4388 | 61.491 | 0.0069358 | 101.5 | 1119.6 | 1018.1
10144 | 2.4394 | 133.45 | 61.491 | 0.0069375 | 101.51 | 1119.6 |  | 10144 | 133.45 | 2.4394 | 61.491 | 0.0069375 | 101.51 | 1119.6 | 1018.09
10145 | 2.44 | 133.46 | 61.491 | 0.0069392 | 101.52 | 1119.6 |  | 10145 | 133.46 | 2.44 | 61.491 | 0.0069392 | 101.52 | 1119.6 | 1018.08
10146 | 2.4407 | 133.47 | 61.491 | 0.0069409 | 101.53 | 1119.6 |  | 10146 | 133.47 | 2.4407 | 61.491 | 0.0069409 | 101.53 | 1119.6 | 1018.07
10147 | 2.4413 | 133.48 | 61.49 | 0.0069426 | 101.54 | 1119.6 |  | 10147 | 133.48 | 2.4413 | 61.49 | 0.0069426 | 101.54 | 1119.6 | 1018.06
10148 | 2.442 | 133.49 | 61.49 | 0.0069444 | 101.55 | 1119.6 |  | 10148 | 133.49 | 2.442 | 61.49 | 0.0069444 | 101.55 | 1119.6 | 1018.05
10149 | 2.4426 | 133.5 | 61.49 | 0.0069461 | 101.56 | 1119.6 |  | 10149 | 133.5 | 2.4426 | 61.49 | 0.0069461 | 101.56 | 1119.6 | 1018.04
10150 | 2.4433 | 133.51 | 61.49 | 0.0069478 | 101.57 | 1119.6 |  | 10150 | 133.51 | 2.4433 | 61.49 | 0.0069478 | 101.57 | 1119.6 | 1018.03
10151 | 2.4439 | 133.52 | 61.49 | 0.0069495 | 101.58 | 1119.6 |  | 10151 | 133.52 | 2.4439 | 61.49 | 0.0069495 | 101.58 | 1119.6 | 1018.02
10152 | 2.4445 | 133.53 | 61.49 | 0.0069512 | 101.59 | 1119.6 |  | 10152 | 133.53 | 2.4445 | 61.49 | 0.0069512 | 101.59 | 1119.6 | 1018.01
10153 | 2.4452 | 133.54 | 61.489 | 0.006953 | 101.6 | 1119.7 |  | 10153 | 133.54 | 2.4452 | 61.489 | 0.006953 | 101.6 | 1119.7 | 1018.1
10154 | 2.4458 | 133.55 | 61.489 | 0.0069547 | 101.61 | 1119.7 |  | 10154 | 133.55 | 2.4458 | 61.489 | 0.0069547 | 101.61 | 1119.7 | 1018.09
10155 | 2.4465 | 133.56 | 61.489 | 0.0069564 | 101.62 | 1119.7 |  | 10155 | 133.56 | 2.4465 | 61.489 | 0.0069564 | 101.62 | 1119.7 | 1018.08
10156 | 2.4471 | 133.57 | 61.489 | 0.0069581 | 101.63 | 1119.7 |  | 10156 | 133.57 | 2.4471 | 61.489 | 0.0069581 | 101.63 | 1119.7 | 1018.07
10157 | 2.4478 | 133.58 | 61.489 | 0.0069598 | 101.64 | 1119.7 |  | 10157 | 133.58 | 2.4478 | 61.489 | 0.0069598 | 101.64 | 1119.7 | 1018.06
10158 | 2.4484 | 133.59 | 61.489 | 0.0069616 | 101.65 | 1119.7 |  | 10158 | 133.59 | 2.4484 | 61.489 | 0.0069616 | 101.65 | 1119.7 | 1018.05
10159 | 2.4491 | 133.6 | 61.488 | 0.0069633 | 101.66 | 1119.7 |  | 10159 | 133.6 | 2.4491 | 61.488 | 0.0069633 | 101.66 | 1119.7 | 1018.04
10160 | 2.4497 | 133.61 | 61.488 | 0.006965 | 101.67 | 1119.7 |  | 10160 | 133.61 | 2.4497 | 61.488 | 0.006965 | 101.67 | 1119.7 | 1018.03
10161 | 2.4503 | 133.62 | 61.488 | 0.0069667 | 101.68 | 1119.7 |  | 10161 | 133.62 | 2.4503 | 61.488 | 0.0069667 | 101.68 | 1119.7 | 1018.02
10162 | 2.451 | 133.63 | 61.488 | 0.0069685 | 101.69 | 1119.7 |  | 10162 | 133.63 | 2.451 | 61.488 | 0.0069685 | 101.69 | 1119.7 | 1018.01
10163 | 2.4516 | 133.64 | 61.488 | 0.0069702 | 101.7 | 1119.7 |  | 10163 | 133.64 | 2.4516 | 61.488 | 0.0069702 | 101.7 | 1119.7 | 1018
10164 | 2.4523 | 133.65 | 61.488 | 0.0069719 | 101.71 | 1119.7 |  | 10164 | 133.65 | 2.4523 | 61.488 | 0.0069719 | 101.71 | 1119.7 | 1017.99
10165 | 2.4529 | 133.66 | 61.487 | 0.0069736 | 101.72 | 1119.7 |  | 10165 | 133.66 | 2.4529 | 61.487 | 0.0069736 | 101.72 | 1119.7 | 1017.98
10166 | 2.4536 | 133.67 | 61.487 | 0.0069754 | 101.73 | 1119.7 |  | 10166 | 133.67 | 2.4536 | 61.487 | 0.0069754 | 101.73 | 1119.7 | 1017.97
10167 | 2.4542 | 133.68 | 61.487 | 0.0069771 | 101.74 | 1119.7 |  | 10167 | 133.68 | 2.4542 | 61.487 | 0.0069771 | 101.74 | 1119.7 | 1017.96
10168 | 2.4549 | 133.69 | 61.487 | 0.0069788 | 101.75 | 1119.7 |  | 10168 | 133.69 | 2.4549 | 61.487 | 0.0069788 | 101.75 | 1119.7 | 1017.95
10169 | 2.4555 | 133.7 | 61.487 | 0.0069805 | 101.76 | 1119.7 |  | 10169 | 133.7 | 2.4555 | 61.487 | 0.0069805 | 101.76 | 1119.7 | 1017.94
10170 | 2.4562 | 133.71 | 61.487 | 0.0069823 | 101.77 | 1119.7 |  | 10170 | 133.71 | 2.4562 | 61.487 | 0.0069823 | 101.77 | 1119.7 | 1017.93
10171 | 2.4568 | 133.72 | 61.486 | 0.006984 | 101.78 | 1119.7 |  | 10171 | 133.72 | 2.4568 | 61.486 | 0.006984 | 101.78 | 1119.7 | 1017.92
10172 | 2.4575 | 133.73 | 61.486 | 0.0069857 | 101.79 | 1119.7 |  | 10172 | 133.73 | 2.4575 | 61.486 | 0.0069857 | 101.79 | 1119.7 | 1017.91
10173 | 2.4581 | 133.74 | 61.486 | 0.0069875 | 101.8 | 1119.7 |  | 10173 | 133.74 | 2.4581 | 61.486 | 0.0069875 | 101.8 | 1119.7 | 1017.9
10174 | 2.4588 | 133.75 | 61.486 | 0.0069892 | 101.81 | 1119.7 |  | 10174 | 133.75 | 2.4588 | 61.486 | 0.0069892 | 101.81 | 1119.7 | 1017.89
10175 | 2.4594 | 133.76 | 61.486 | 0.0069909 | 101.82 | 1119.7 |  | 10175 | 133.76 | 2.4594 | 61.486 | 0.0069909 | 101.82 | 1119.7 | 1017.88
10176 | 2.4601 | 133.77 | 61.486 | 0.0069926 | 101.83 | 1119.7 |  | 10176 | 133.77 | 2.4601 | 61.486 | 0.0069926 | 101.83 | 1119.7 | 1017.87
10177 | 2.4607 | 133.78 | 61.485 | 0.0069944 | 101.84 | 1119.8 |  | 10177 | 133.78 | 2.4607 | 61.485 | 0.0069944 | 101.84 | 1119.8 | 1017.96
10178 | 2.4613 | 133.79 | 61.485 | 0.0069961 | 101.85 | 1119.8 |  | 10178 | 133.79 | 2.4613 | 61.485 | 0.0069961 | 101.85 | 1119.8 | 1017.95
10179 | 2.462 | 133.8 | 61.485 | 0.0069978 | 101.86 | 1119.8 |  | 10179 | 133.8 | 2.462 | 61.485 | 0.0069978 | 101.86 | 1119.8 | 1017.94
10180 | 2.4626 | 133.81 | 61.485 | 0.0069996 | 101.87 | 1119.8 |  | 10180 | 133.81 | 2.4626 | 61.485 | 0.0069996 | 101.87 | 1119.8 | 1017.93
10181 | 2.4633 | 133.82 | 61.485 | 0.0070013 | 101.88 | 1119.8 |  | 10181 | 133.82 | 2.4633 | 61.485 | 0.0070013 | 101.88 | 1119.8 | 1017.92
10182 | 2.4639 | 133.83 | 61.485 | 0.007003 | 101.89 | 1119.8 |  | 10182 | 133.83 | 2.4639 | 61.485 | 0.007003 | 101.89 | 1119.8 | 1017.91
10183 | 2.4646 | 133.84 | 61.484 | 0.0070048 | 101.9 | 1119.8 |  | 10183 | 133.84 | 2.4646 | 61.484 | 0.0070048 | 101.9 | 1119.8 | 1017.9
10184 | 2.4652 | 133.85 | 61.484 | 0.0070065 | 101.91 | 1119.8 |  | 10184 | 133.85 | 2.4652 | 61.484 | 0.0070065 | 101.91 | 1119.8 | 1017.89
10185 | 2.4659 | 133.86 | 61.484 | 0.0070082 | 101.92 | 1119.8 |  | 10185 | 133.86 | 2.4659 | 61.484 | 0.0070082 | 101.92 | 1119.8 | 1017.88
10186 | 2.4665 | 133.87 | 61.484 | 0.00701 | 101.93 | 1119.8 |  | 10186 | 133.87 | 2.4665 | 61.484 | 0.00701 | 101.93 | 1119.8 | 1017.87
10187 | 2.4672 | 133.88 | 61.484 | 0.0070117 | 101.94 | 1119.8 |  | 10187 | 133.88 | 2.4672 | 61.484 | 0.0070117 | 101.94 | 1119.8 | 1017.86
10188 | 2.4678 | 133.89 | 61.483 | 0.0070134 | 101.95 | 1119.8 |  | 10188 | 133.89 | 2.4678 | 61.483 | 0.0070134 | 101.95 | 1119.8 | 1017.85
10189 | 2.4685 | 133.9 | 61.483 | 0.0070152 | 101.96 | 1119.8 |  | 10189 | 133.9 | 2.4685 | 61.483 | 0.0070152 | 101.96 | 1119.8 | 1017.84
10190 | 2.4691 | 133.91 | 61.483 | 0.0070169 | 101.97 | 1119.8 |  | 10190 | 133.91 | 2.4691 | 61.483 | 0.0070169 | 101.97 | 1119.8 | 1017.83
10191 | 2.4698 | 133.92 | 61.483 | 0.0070186 | 101.98 | 1119.8 |  | 10191 | 133.92 | 2.4698 | 61.483 | 0.0070186 | 101.98 | 1119.8 | 1017.82
10192 | 2.4704 | 133.93 | 61.483 | 0.0070204 | 101.99 | 1119.8 |  | 10192 | 133.93 | 2.4704 | 61.483 | 0.0070204 | 101.99 | 1119.8 | 1017.81
10193 | 2.4711 | 133.94 | 61.483 | 0.0070221 | 102 | 1119.8 |  | 10193 | 133.94 | 2.4711 | 61.483 | 0.0070221 | 102 | 1119.8 | 1017.8
10194 | 2.4717 | 133.95 | 61.482 | 0.0070238 | 102.01 | 1119.8 |  | 10194 | 133.95 | 2.4717 | 61.482 | 0.0070238 | 102.01 | 1119.8 | 1017.79
10195 | 2.4724 | 133.96 | 61.482 | 0.0070256 | 102.02 | 1119.8 |  | 10195 | 133.96 | 2.4724 | 61.482 | 0.0070256 | 102.02 | 1119.8 | 1017.78
10196 | 2.473 | 133.97 | 61.482 | 0.0070273 | 102.03 | 1119.8 |  | 10196 | 133.97 | 2.473 | 61.482 | 0.0070273 | 102.03 | 1119.8 | 1017.77
10197 | 2.4737 | 133.98 | 61.482 | 0.007029 | 102.04 | 1119.8 |  | 10197 | 133.98 | 2.4737 | 61.482 | 0.007029 | 102.04 | 1119.8 | 1017.76
10198 | 2.4743 | 133.99 | 61.482 | 0.0070308 | 102.05 | 1119.8 |  | 10198 | 133.99 | 2.4743 | 61.482 | 0.0070308 | 102.05 | 1119.8 | 1017.75
10199 | 2.475 | 134 | 61.482 | 0.0070325 | 102.06 | 1119.8 |  | 10199 | 134 | 2.475 | 61.482 | 0.0070325 | 102.06 | 1119.8 | 1017.74
10200 | 2.4756 | 134.01 | 61.481 | 0.0070342 | 102.07 | 1119.8 |  | 10200 | 134.01 | 2.4756 | 61.481 | 0.0070342 | 102.07 | 1119.8 | 1017.73
10201 | 2.4763 | 134.02 | 61.481 | 0.007036 | 102.08 | 1119.9 |  | 10201 | 134.02 | 2.4763 | 61.481 | 0.007036 | 102.08 | 1119.9 | 1017.82
10202 | 2.4769 | 134.03 | 61.481 | 0.0070377 | 102.09 | 1119.9 |  | 10202 | 134.03 | 2.4769 | 61.481 | 0.0070377 | 102.09 | 1119.9 | 1017.81
10203 | 2.4776 | 134.04 | 61.481 | 0.0070395 | 102.1 | 1119.9 |  | 10203 | 134.04 | 2.4776 | 61.481 | 0.0070395 | 102.1 | 1119.9 | 1017.8
10204 | 2.4782 | 134.05 | 61.481 | 0.0070412 | 102.11 | 1119.9 |  | 10204 | 134.05 | 2.4782 | 61.481 | 0.0070412 | 102.11 | 1119.9 | 1017.79
10205 | 2.4789 | 134.06 | 61.481 | 0.0070429 | 102.12 | 1119.9 |  | 10205 | 134.06 | 2.4789 | 61.481 | 0.0070429 | 102.12 | 1119.9 | 1017.78
10206 | 2.4796 | 134.07 | 61.48 | 0.0070447 | 102.13 | 1119.9 |  | 10206 | 134.07 | 2.4796 | 61.48 | 0.0070447 | 102.13 | 1119.9 | 1017.77
10207 | 2.4802 | 134.08 | 61.48 | 0.0070464 | 102.14 | 1119.9 |  | 10207 | 134.08 | 2.4802 | 61.48 | 0.0070464 | 102.14 | 1119.9 | 1017.76
10208 | 2.4809 | 134.09 | 61.48 | 0.0070482 | 102.15 | 1119.9 |  | 10208 | 134.09 | 2.4809 | 61.48 | 0.0070482 | 102.15 | 1119.9 | 1017.75
10209 | 2.4815 | 134.1 | 61.48 | 0.0070499 | 102.16 | 1119.9 |  | 10209 | 134.1 | 2.4815 | 61.48 | 0.0070499 | 102.16 | 1119.9 | 1017.74
10210 | 2.4822 | 134.11 | 61.48 | 0.0070516 | 102.17 | 1119.9 |  | 10210 | 134.11 | 2.4822 | 61.48 | 0.0070516 | 102.17 | 1119.9 | 1017.73
10211 | 2.4828 | 134.12 | 61.48 | 0.0070534 | 102.18 | 1119.9 |  | 10211 | 134.12 | 2.4828 | 61.48 | 0.0070534 | 102.18 | 1119.9 | 1017.72
10212 | 2.4835 | 134.13 | 61.479 | 0.0070551 | 102.19 | 1119.9 |  | 10212 | 134.13 | 2.4835 | 61.479 | 0.0070551 | 102.19 | 1119.9 | 1017.71
10213 | 2.4841 | 134.14 | 61.479 | 0.0070569 | 102.2 | 1119.9 |  | 10213 | 134.14 | 2.4841 | 61.479 | 0.0070569 | 102.2 | 1119.9 | 1017.7
10214 | 2.4848 | 134.15 | 61.479 | 0.0070586 | 102.21 | 1119.9 |  | 10214 | 134.15 | 2.4848 | 61.479 | 0.0070586 | 102.21 | 1119.9 | 1017.69
10215 | 2.4854 | 134.16 | 61.479 | 0.0070604 | 102.22 | 1119.9 |  | 10215 | 134.16 | 2.4854 | 61.479 | 0.0070604 | 102.22 | 1119.9 | 1017.68
10216 | 2.4861 | 134.17 | 61.479 | 0.0070621 | 102.23 | 1119.9 |  | 10216 | 134.17 | 2.4861 | 61.479 | 0.0070621 | 102.23 | 1119.9 | 1017.67
10217 | 2.4867 | 134.18 | 61.479 | 0.0070638 | 102.24 | 1119.9 |  | 10217 | 134.18 | 2.4867 | 61.479 | 0.0070638 | 102.24 | 1119.9 | 1017.66
10218 | 2.4874 | 134.19 | 61.478 | 0.0070656 | 102.25 | 1119.9 |  | 10218 | 134.19 | 2.4874 | 61.478 | 0.0070656 | 102.25 | 1119.9 | 1017.65
10219 | 2.488 | 134.2 | 61.478 | 0.0070673 | 102.26 | 1119.9 |  | 10219 | 134.2 | 2.488 | 61.478 | 0.0070673 | 102.26 | 1119.9 | 1017.64
10220 | 2.4887 | 134.21 | 61.478 | 0.0070691 | 102.27 | 1119.9 |  | 10220 | 134.21 | 2.4887 | 61.478 | 0.0070691 | 102.27 | 1119.9 | 1017.63
10221 | 2.4893 | 134.22 | 61.478 | 0.0070708 | 102.28 | 1119.9 |  | 10221 | 134.22 | 2.4893 | 61.478 | 0.0070708 | 102.28 | 1119.9 | 1017.62
10222 | 2.49 | 134.23 | 61.478 | 0.0070726 | 102.29 | 1119.9 |  | 10222 | 134.23 | 2.49 | 61.478 | 0.0070726 | 102.29 | 1119.9 | 1017.61
10223 | 2.4907 | 134.24 | 61.477 | 0.0070743 | 102.3 | 1119.9 |  | 10223 | 134.24 | 2.4907 | 61.477 | 0.0070743 | 102.3 | 1119.9 | 1017.6
10224 | 2.4913 | 134.25 | 61.477 | 0.0070761 | 102.31 | 1119.9 |  | 10224 | 134.25 | 2.4913 | 61.477 | 0.0070761 | 102.31 | 1119.9 | 1017.59
10225 | 2.492 | 134.26 | 61.477 | 0.0070778 | 102.32 | 1120 |  | 10225 | 134.26 | 2.492 | 61.477 | 0.0070778 | 102.32 | 1120 | 1017.68
10226 | 2.4926 | 134.27 | 61.477 | 0.0070796 | 102.33 | 1120 |  | 10226 | 134.27 | 2.4926 | 61.477 | 0.0070796 | 102.33 | 1120 | 1017.67
10227 | 2.4933 | 134.28 | 61.477 | 0.0070813 | 102.34 | 1120 |  | 10227 | 134.28 | 2.4933 | 61.477 | 0.0070813 | 102.34 | 1120 | 1017.66
10228 | 2.4939 | 134.29 | 61.477 | 0.0070831 | 102.35 | 1120 |  | 10228 | 134.29 | 2.4939 | 61.477 | 0.0070831 | 102.35 | 1120 | 1017.65
10229 | 2.4946 | 134.3 | 61.476 | 0.0070848 | 102.36 | 1120 |  | 10229 | 134.3 | 2.4946 | 61.476 | 0.0070848 | 102.36 | 1120 | 1017.64
10230 | 2.4952 | 134.31 | 61.476 | 0.0070865 | 102.37 | 1120 |  | 10230 | 134.31 | 2.4952 | 61.476 | 0.0070865 | 102.37 | 1120 | 1017.63
10231 | 2.4959 | 134.32 | 61.476 | 0.0070883 | 102.38 | 1120 |  | 10231 | 134.32 | 2.4959 | 61.476 | 0.0070883 | 102.38 | 1120 | 1017.62
10232 | 2.4966 | 134.33 | 61.476 | 0.00709 | 102.39 | 1120 |  | 10232 | 134.33 | 2.4966 | 61.476 | 0.00709 | 102.39 | 1120 | 1017.61
10233 | 2.4972 | 134.34 | 61.476 | 0.0070918 | 102.4 | 1120 |  | 10233 | 134.34 | 2.4972 | 61.476 | 0.0070918 | 102.4 | 1120 | 1017.6
10234 | 2.4979 | 134.35 | 61.476 | 0.0070935 | 102.41 | 1120 |  | 10234 | 134.35 | 2.4979 | 61.476 | 0.0070935 | 102.41 | 1120 | 1017.59
10235 | 2.4985 | 134.36 | 61.475 | 0.0070953 | 102.42 | 1120 |  | 10235 | 134.36 | 2.4985 | 61.475 | 0.0070953 | 102.42 | 1120 | 1017.58
10236 | 2.4992 | 134.37 | 61.475 | 0.007097 | 102.43 | 1120 |  | 10236 | 134.37 | 2.4992 | 61.475 | 0.007097 | 102.43 | 1120 | 1017.57
10237 | 2.4998 | 134.38 | 61.475 | 0.0070988 | 102.44 | 1120 |  | 10237 | 134.38 | 2.4998 | 61.475 | 0.0070988 | 102.44 | 1120 | 1017.56
10238 | 2.5005 | 134.39 | 61.475 | 0.0071006 | 102.45 | 1120 |  | 10238 | 134.39 | 2.5005 | 61.475 | 0.0071006 | 102.45 | 1120 | 1017.55
10239 | 2.5012 | 134.4 | 61.475 | 0.0071023 | 102.46 | 1120 |  | 10239 | 134.4 | 2.5012 | 61.475 | 0.0071023 | 102.46 | 1120 | 1017.54
10240 | 2.5018 | 134.41 | 61.475 | 0.0071041 | 102.47 | 1120 |  | 10240 | 134.41 | 2.5018 | 61.475 | 0.0071041 | 102.47 | 1120 | 1017.53
10241 | 2.5025 | 134.42 | 61.474 | 0.0071058 | 102.48 | 1120 |  | 10241 | 134.42 | 2.5025 | 61.474 | 0.0071058 | 102.48 | 1120 | 1017.52
10242 | 2.5031 | 134.43 | 61.474 | 0.0071076 | 102.49 | 1120 |  | 10242 | 134.43 | 2.5031 | 61.474 | 0.0071076 | 102.49 | 1120 | 1017.51
10243 | 2.5038 | 134.44 | 61.474 | 0.0071093 | 102.5 | 1120 |  | 10243 | 134.44 | 2.5038 | 61.474 | 0.0071093 | 102.5 | 1120 | 1017.5
10244 | 2.5044 | 134.45 | 61.474 | 0.0071111 | 102.51 | 1120 |  | 10244 | 134.45 | 2.5044 | 61.474 | 0.0071111 | 102.51 | 1120 | 1017.49
10245 | 2.5051 | 134.46 | 61.474 | 0.0071128 | 102.52 | 1120 |  | 10245 | 134.46 | 2.5051 | 61.474 | 0.0071128 | 102.52 | 1120 | 1017.48
10246 | 2.5058 | 134.47 | 61.474 | 0.0071146 | 102.53 | 1120 |  | 10246 | 134.47 | 2.5058 | 61.474 | 0.0071146 | 102.53 | 1120 | 1017.47
10247 | 2.5064 | 134.48 | 61.473 | 0.0071163 | 102.54 | 1120 |  | 10247 | 134.48 | 2.5064 | 61.473 | 0.0071163 | 102.54 | 1120 | 1017.46
10248 | 2.5071 | 134.49 | 61.473 | 0.0071181 | 102.55 | 1120 |  | 10248 | 134.49 | 2.5071 | 61.473 | 0.0071181 | 102.55 | 1120 | 1017.45
10249 | 2.5077 | 134.5 | 61.473 | 0.0071198 | 102.56 | 1120.1 |  | 10249 | 134.5 | 2.5077 | 61.473 | 0.0071198 | 102.56 | 1120.1 | 1017.54
10250 | 2.5084 | 134.51 | 61.473 | 0.0071216 | 102.57 | 1120.1 |  | 10250 | 134.51 | 2.5084 | 61.473 | 0.0071216 | 102.57 | 1120.1 | 1017.53
10251 | 2.509 | 134.52 | 61.473 | 0.0071234 | 102.58 | 1120.1 |  | 10251 | 134.52 | 2.509 | 61.473 | 0.0071234 | 102.58 | 1120.1 | 1017.52
10252 | 2.5097 | 134.53 | 61.472 | 0.0071251 | 102.59 | 1120.1 |  | 10252 | 134.53 | 2.5097 | 61.472 | 0.0071251 | 102.59 | 1120.1 | 1017.51
10253 | 2.5104 | 134.54 | 61.472 | 0.0071269 | 102.6 | 1120.1 |  | 10253 | 134.54 | 2.5104 | 61.472 | 0.0071269 | 102.6 | 1120.1 | 1017.5
10254 | 2.511 | 134.55 | 61.472 | 0.0071286 | 102.61 | 1120.1 |  | 10254 | 134.55 | 2.511 | 61.472 | 0.0071286 | 102.61 | 1120.1 | 1017.49
10255 | 2.5117 | 134.56 | 61.472 | 0.0071304 | 102.62 | 1120.1 |  | 10255 | 134.56 | 2.5117 | 61.472 | 0.0071304 | 102.62 | 1120.1 | 1017.48
10256 | 2.5123 | 134.57 | 61.472 | 0.0071321 | 102.63 | 1120.1 |  | 10256 | 134.57 | 2.5123 | 61.472 | 0.0071321 | 102.63 | 1120.1 | 1017.47
10257 | 2.513 | 134.58 | 61.472 | 0.0071339 | 102.64 | 1120.1 |  | 10257 | 134.58 | 2.513 | 61.472 | 0.0071339 | 102.64 | 1120.1 | 1017.46
10258 | 2.5137 | 134.59 | 61.471 | 0.0071357 | 102.65 | 1120.1 |  | 10258 | 134.59 | 2.5137 | 61.471 | 0.0071357 | 102.65 | 1120.1 | 1017.45
10259 | 2.5143 | 134.6 | 61.471 | 0.0071374 | 102.66 | 1120.1 |  | 10259 | 134.6 | 2.5143 | 61.471 | 0.0071374 | 102.66 | 1120.1 | 1017.44
10260 | 2.515 | 134.61 | 61.471 | 0.0071392 | 102.67 | 1120.1 |  | 10260 | 134.61 | 2.515 | 61.471 | 0.0071392 | 102.67 | 1120.1 | 1017.43
10261 | 2.5156 | 134.62 | 61.471 | 0.0071409 | 102.68 | 1120.1 |  | 10261 | 134.62 | 2.5156 | 61.471 | 0.0071409 | 102.68 | 1120.1 | 1017.42
10262 | 2.5163 | 134.63 | 61.471 | 0.0071427 | 102.69 | 1120.1 |  | 10262 | 134.63 | 2.5163 | 61.471 | 0.0071427 | 102.69 | 1120.1 | 1017.41
10263 | 2.517 | 134.64 | 61.471 | 0.0071445 | 102.7 | 1120.1 |  | 10263 | 134.64 | 2.517 | 61.471 | 0.0071445 | 102.7 | 1120.1 | 1017.4
10264 | 2.5176 | 134.65 | 61.47 | 0.0071462 | 102.71 | 1120.1 |  | 10264 | 134.65 | 2.5176 | 61.47 | 0.0071462 | 102.71 | 1120.1 | 1017.39
10265 | 2.5183 | 134.66 | 61.47 | 0.007148 | 102.72 | 1120.1 |  | 10265 | 134.66 | 2.5183 | 61.47 | 0.007148 | 102.72 | 1120.1 | 1017.38
10266 | 2.5189 | 134.67 | 61.47 | 0.0071497 | 102.73 | 1120.1 |  | 10266 | 134.67 | 2.5189 | 61.47 | 0.0071497 | 102.73 | 1120.1 | 1017.37
10267 | 2.5196 | 134.68 | 61.47 | 0.0071515 | 102.74 | 1120.1 |  | 10267 | 134.68 | 2.5196 | 61.47 | 0.0071515 | 102.74 | 1120.1 | 1017.36
10268 | 2.5203 | 134.69 | 61.47 | 0.0071533 | 102.75 | 1120.1 |  | 10268 | 134.69 | 2.5203 | 61.47 | 0.0071533 | 102.75 | 1120.1 | 1017.35
10269 | 2.5209 | 134.7 | 61.47 | 0.007155 | 102.76 | 1120.1 |  | 10269 | 134.7 | 2.5209 | 61.47 | 0.007155 | 102.76 | 1120.1 | 1017.34
10270 | 2.5216 | 134.71 | 61.469 | 0.0071568 | 102.77 | 1120.1 |  | 10270 | 134.71 | 2.5216 | 61.469 | 0.0071568 | 102.77 | 1120.1 | 1017.33
10271 | 2.5223 | 134.72 | 61.469 | 0.0071586 | 102.78 | 1120.1 |  | 10271 | 134.72 | 2.5223 | 61.469 | 0.0071586 | 102.78 | 1120.1 | 1017.32
10272 | 2.5229 | 134.73 | 61.469 | 0.0071603 | 102.79 | 1120.1 |  | 10272 | 134.73 | 2.5229 | 61.469 | 0.0071603 | 102.79 | 1120.1 | 1017.31
10273 | 2.5236 | 134.74 | 61.469 | 0.0071621 | 102.8 | 1120.2 |  | 10273 | 134.74 | 2.5236 | 61.469 | 0.0071621 | 102.8 | 1120.2 | 1017.4
10274 | 2.5242 | 134.75 | 61.469 | 0.0071638 | 102.81 | 1120.2 |  | 10274 | 134.75 | 2.5242 | 61.469 | 0.0071638 | 102.81 | 1120.2 | 1017.39
10275 | 2.5249 | 134.76 | 61.469 | 0.0071656 | 102.82 | 1120.2 |  | 10275 | 134.76 | 2.5249 | 61.469 | 0.0071656 | 102.82 | 1120.2 | 1017.38
10276 | 2.5256 | 134.77 | 61.468 | 0.0071674 | 102.83 | 1120.2 |  | 10276 | 134.77 | 2.5256 | 61.468 | 0.0071674 | 102.83 | 1120.2 | 1017.37
10277 | 2.5262 | 134.78 | 61.468 | 0.0071691 | 102.84 | 1120.2 |  | 10277 | 134.78 | 2.5262 | 61.468 | 0.0071691 | 102.84 | 1120.2 | 1017.36
10278 | 2.5269 | 134.79 | 61.468 | 0.0071709 | 102.85 | 1120.2 |  | 10278 | 134.79 | 2.5269 | 61.468 | 0.0071709 | 102.85 | 1120.2 | 1017.35
10279 | 2.5276 | 134.8 | 61.468 | 0.0071727 | 102.86 | 1120.2 |  | 10279 | 134.8 | 2.5276 | 61.468 | 0.0071727 | 102.86 | 1120.2 | 1017.34
10280 | 2.5282 | 134.81 | 61.468 | 0.0071744 | 102.87 | 1120.2 |  | 10280 | 134.81 | 2.5282 | 61.468 | 0.0071744 | 102.87 | 1120.2 | 1017.33
10281 | 2.5289 | 134.82 | 61.468 | 0.0071762 | 102.88 | 1120.2 |  | 10281 | 134.82 | 2.5289 | 61.468 | 0.0071762 | 102.88 | 1120.2 | 1017.32
10282 | 2.5295 | 134.83 | 61.467 | 0.007178 | 102.89 | 1120.2 |  | 10282 | 134.83 | 2.5295 | 61.467 | 0.007178 | 102.89 | 1120.2 | 1017.31
10283 | 2.5302 | 134.84 | 61.467 | 0.0071797 | 102.9 | 1120.2 |  | 10283 | 134.84 | 2.5302 | 61.467 | 0.0071797 | 102.9 | 1120.2 | 1017.3
10284 | 2.5309 | 134.85 | 61.467 | 0.0071815 | 102.91 | 1120.2 |  | 10284 | 134.85 | 2.5309 | 61.467 | 0.0071815 | 102.91 | 1120.2 | 1017.29
10285 | 2.5315 | 134.86 | 61.467 | 0.0071833 | 102.92 | 1120.2 |  | 10285 | 134.86 | 2.5315 | 61.467 | 0.0071833 | 102.92 | 1120.2 | 1017.28
10286 | 2.5322 | 134.87 | 61.467 | 0.0071851 | 102.93 | 1120.2 |  | 10286 | 134.87 | 2.5322 | 61.467 | 0.0071851 | 102.93 | 1120.2 | 1017.27
10287 | 2.5329 | 134.88 | 61.466 | 0.0071868 | 102.94 | 1120.2 |  | 10287 | 134.88 | 2.5329 | 61.466 | 0.0071868 | 102.94 | 1120.2 | 1017.26
10288 | 2.5335 | 134.89 | 61.466 | 0.0071886 | 102.95 | 1120.2 |  | 10288 | 134.89 | 2.5335 | 61.466 | 0.0071886 | 102.95 | 1120.2 | 1017.25
10289 | 2.5342 | 134.9 | 61.466 | 0.0071904 | 102.96 | 1120.2 |  | 10289 | 134.9 | 2.5342 | 61.466 | 0.0071904 | 102.96 | 1120.2 | 1017.24
10290 | 2.5349 | 134.91 | 61.466 | 0.0071921 | 102.97 | 1120.2 |  | 10290 | 134.91 | 2.5349 | 61.466 | 0.0071921 | 102.97 | 1120.2 | 1017.23
10291 | 2.5355 | 134.92 | 61.466 | 0.0071939 | 102.98 | 1120.2 |  | 10291 | 134.92 | 2.5355 | 61.466 | 0.0071939 | 102.98 | 1120.2 | 1017.22
10292 | 2.5362 | 134.93 | 61.466 | 0.0071957 | 102.99 | 1120.2 |  | 10292 | 134.93 | 2.5362 | 61.466 | 0.0071957 | 102.99 | 1120.2 | 1017.21
10293 | 2.5368 | 134.94 | 61.465 | 0.0071974 | 103 | 1120.2 |  | 10293 | 134.94 | 2.5368 | 61.465 | 0.0071974 | 103 | 1120.2 | 1017.2
10294 | 2.5375 | 134.95 | 61.465 | 0.0071992 | 103.01 | 1120.2 |  | 10294 | 134.95 | 2.5375 | 61.465 | 0.0071992 | 103.01 | 1120.2 | 1017.19
10295 | 2.5382 | 134.96 | 61.465 | 0.007201 | 103.02 | 1120.2 |  | 10295 | 134.96 | 2.5382 | 61.465 | 0.007201 | 103.02 | 1120.2 | 1017.18
10296 | 2.5388 | 134.97 | 61.465 | 0.0072028 | 103.03 | 1120.2 |  | 10296 | 134.97 | 2.5388 | 61.465 | 0.0072028 | 103.03 | 1120.2 | 1017.17
10297 | 2.5395 | 134.98 | 61.465 | 0.0072045 | 103.04 | 1120.3 |  | 10297 | 134.98 | 2.5395 | 61.465 | 0.0072045 | 103.04 | 1120.3 | 1017.26
10298 | 2.5402 | 134.99 | 61.465 | 0.0072063 | 103.05 | 1120.3 |  | 10298 | 134.99 | 2.5402 | 61.465 | 0.0072063 | 103.05 | 1120.3 | 1017.25
10299 | 2.5408 | 135 | 61.464 | 0.0072081 | 103.06 | 1120.3 |  | 10299 | 135 | 2.5408 | 61.464 | 0.0072081 | 103.06 | 1120.3 | 1017.24
10300 | 2.5415 | 135.01 | 61.464 | 0.0072099 | 103.07 | 1120.3 |  | 10300 | 135.01 | 2.5415 | 61.464 | 0.0072099 | 103.07 | 1120.3 | 1017.23
10301 | 2.5422 | 135.02 | 61.464 | 0.0072116 | 103.08 | 1120.3 |  | 10301 | 135.02 | 2.5422 | 61.464 | 0.0072116 | 103.08 | 1120.3 | 1017.22
10302 | 2.5428 | 135.03 | 61.464 | 0.0072134 | 103.09 | 1120.3 |  | 10302 | 135.03 | 2.5428 | 61.464 | 0.0072134 | 103.09 | 1120.3 | 1017.21
10303 | 2.5435 | 135.04 | 61.464 | 0.0072152 | 103.1 | 1120.3 |  | 10303 | 135.04 | 2.5435 | 61.464 | 0.0072152 | 103.1 | 1120.3 | 1017.2
10304 | 2.5442 | 135.05 | 61.464 | 0.007217 | 103.11 | 1120.3 |  | 10304 | 135.05 | 2.5442 | 61.464 | 0.007217 | 103.11 | 1120.3 | 1017.19
10305 | 2.5448 | 135.06 | 61.463 | 0.0072187 | 103.12 | 1120.3 |  | 10305 | 135.06 | 2.5448 | 61.463 | 0.0072187 | 103.12 | 1120.3 | 1017.18
10306 | 2.5455 | 135.07 | 61.463 | 0.0072205 | 103.13 | 1120.3 |  | 10306 | 135.07 | 2.5455 | 61.463 | 0.0072205 | 103.13 | 1120.3 | 1017.17
10307 | 2.5462 | 135.08 | 61.463 | 0.0072223 | 103.14 | 1120.3 |  | 10307 | 135.08 | 2.5462 | 61.463 | 0.0072223 | 103.14 | 1120.3 | 1017.16
10308 | 2.5468 | 135.09 | 61.463 | 0.0072241 | 103.15 | 1120.3 |  | 10308 | 135.09 | 2.5468 | 61.463 | 0.0072241 | 103.15 | 1120.3 | 1017.15
10309 | 2.5475 | 135.1 | 61.463 | 0.0072258 | 103.16 | 1120.3 |  | 10309 | 135.1 | 2.5475 | 61.463 | 0.0072258 | 103.16 | 1120.3 | 1017.14
10310 | 2.5482 | 135.11 | 61.463 | 0.0072276 | 103.17 | 1120.3 |  | 10310 | 135.11 | 2.5482 | 61.463 | 0.0072276 | 103.17 | 1120.3 | 1017.13
10311 | 2.5488 | 135.12 | 61.462 | 0.0072294 | 103.18 | 1120.3 |  | 10311 | 135.12 | 2.5488 | 61.462 | 0.0072294 | 103.18 | 1120.3 | 1017.12
10312 | 2.5495 | 135.13 | 61.462 | 0.0072312 | 103.19 | 1120.3 |  | 10312 | 135.13 | 2.5495 | 61.462 | 0.0072312 | 103.19 | 1120.3 | 1017.11
10313 | 2.5502 | 135.14 | 61.462 | 0.007233 | 103.2 | 1120.3 |  | 10313 | 135.14 | 2.5502 | 61.462 | 0.007233 | 103.2 | 1120.3 | 1017.1
10314 | 2.5508 | 135.15 | 61.462 | 0.0072347 | 103.21 | 1120.3 |  | 10314 | 135.15 | 2.5508 | 61.462 | 0.0072347 | 103.21 | 1120.3 | 1017.09
10315 | 2.5515 | 135.16 | 61.462 | 0.0072365 | 103.22 | 1120.3 |  | 10315 | 135.16 | 2.5515 | 61.462 | 0.0072365 | 103.22 | 1120.3 | 1017.08
10316 | 2.5522 | 135.17 | 61.461 | 0.0072383 | 103.23 | 1120.3 |  | 10316 | 135.17 | 2.5522 | 61.461 | 0.0072383 | 103.23 | 1120.3 | 1017.07
10317 | 2.5529 | 135.18 | 61.461 | 0.0072401 | 103.24 | 1120.3 |  | 10317 | 135.18 | 2.5529 | 61.461 | 0.0072401 | 103.24 | 1120.3 | 1017.06
10318 | 2.5535 | 135.19 | 61.461 | 0.0072419 | 103.25 | 1120.3 |  | 10318 | 135.19 | 2.5535 | 61.461 | 0.0072419 | 103.25 | 1120.3 | 1017.05
10319 | 2.5542 | 135.2 | 61.461 | 0.0072436 | 103.26 | 1120.3 |  | 10319 | 135.2 | 2.5542 | 61.461 | 0.0072436 | 103.26 | 1120.3 | 1017.04
10320 | 2.5549 | 135.21 | 61.461 | 0.0072454 | 103.27 | 1120.3 |  | 10320 | 135.21 | 2.5549 | 61.461 | 0.0072454 | 103.27 | 1120.3 | 1017.03
10321 | 2.5555 | 135.22 | 61.461 | 0.0072472 | 103.28 | 1120.4 |  | 10321 | 135.22 | 2.5555 | 61.461 | 0.0072472 | 103.28 | 1120.4 | 1017.12
10322 | 2.5562 | 135.23 | 61.46 | 0.007249 | 103.29 | 1120.4 |  | 10322 | 135.23 | 2.5562 | 61.46 | 0.007249 | 103.29 | 1120.4 | 1017.11
10323 | 2.5569 | 135.24 | 61.46 | 0.0072508 | 103.3 | 1120.4 |  | 10323 | 135.24 | 2.5569 | 61.46 | 0.0072508 | 103.3 | 1120.4 | 1017.1
10324 | 2.5575 | 135.25 | 61.46 | 0.0072525 | 103.31 | 1120.4 |  | 10324 | 135.25 | 2.5575 | 61.46 | 0.0072525 | 103.31 | 1120.4 | 1017.09
10325 | 2.5582 | 135.26 | 61.46 | 0.0072543 | 103.32 | 1120.4 |  | 10325 | 135.26 | 2.5582 | 61.46 | 0.0072543 | 103.32 | 1120.4 | 1017.08
10326 | 2.5589 | 135.27 | 61.46 | 0.0072561 | 103.33 | 1120.4 |  | 10326 | 135.27 | 2.5589 | 61.46 | 0.0072561 | 103.33 | 1120.4 | 1017.07
10327 | 2.5595 | 135.28 | 61.46 | 0.0072579 | 103.34 | 1120.4 |  | 10327 | 135.28 | 2.5595 | 61.46 | 0.0072579 | 103.34 | 1120.4 | 1017.06
10328 | 2.5602 | 135.29 | 61.459 | 0.0072597 | 103.35 | 1120.4 |  | 10328 | 135.29 | 2.5602 | 61.459 | 0.0072597 | 103.35 | 1120.4 | 1017.05
10329 | 2.5609 | 135.3 | 61.459 | 0.0072615 | 103.36 | 1120.4 |  | 10329 | 135.3 | 2.5609 | 61.459 | 0.0072615 | 103.36 | 1120.4 | 1017.04
10330 | 2.5616 | 135.31 | 61.459 | 0.0072633 | 103.37 | 1120.4 |  | 10330 | 135.31 | 2.5616 | 61.459 | 0.0072633 | 103.37 | 1120.4 | 1017.03
10331 | 2.5622 | 135.32 | 61.459 | 0.007265 | 103.38 | 1120.4 |  | 10331 | 135.32 | 2.5622 | 61.459 | 0.007265 | 103.38 | 1120.4 | 1017.02
10332 | 2.5629 | 135.33 | 61.459 | 0.0072668 | 103.39 | 1120.4 |  | 10332 | 135.33 | 2.5629 | 61.459 | 0.0072668 | 103.39 | 1120.4 | 1017.01
10333 | 2.5636 | 135.34 | 61.459 | 0.0072686 | 103.4 | 1120.4 |  | 10333 | 135.34 | 2.5636 | 61.459 | 0.0072686 | 103.4 | 1120.4 | 1017
10334 | 2.5642 | 135.35 | 61.458 | 0.0072704 | 103.41 | 1120.4 |  | 10334 | 135.35 | 2.5642 | 61.458 | 0.0072704 | 103.41 | 1120.4 | 1016.99
10335 | 2.5649 | 135.36 | 61.458 | 0.0072722 | 103.42 | 1120.4 |  | 10335 | 135.36 | 2.5649 | 61.458 | 0.0072722 | 103.42 | 1120.4 | 1016.98
10336 | 2.5656 | 135.37 | 61.458 | 0.007274 | 103.43 | 1120.4 |  | 10336 | 135.37 | 2.5656 | 61.458 | 0.007274 | 103.43 | 1120.4 | 1016.97
10337 | 2.5663 | 135.38 | 61.458 | 0.0072758 | 103.44 | 1120.4 |  | 10337 | 135.38 | 2.5663 | 61.458 | 0.0072758 | 103.44 | 1120.4 | 1016.96
10338 | 2.5669 | 135.39 | 61.458 | 0.0072775 | 103.45 | 1120.4 |  | 10338 | 135.39 | 2.5669 | 61.458 | 0.0072775 | 103.45 | 1120.4 | 1016.95
10339 | 2.5676 | 135.4 | 61.457 | 0.0072793 | 103.46 | 1120.4 |  | 10339 | 135.4 | 2.5676 | 61.457 | 0.0072793 | 103.46 | 1120.4 | 1016.94
10340 | 2.5683 | 135.41 | 61.457 | 0.0072811 | 103.47 | 1120.4 |  | 10340 | 135.41 | 2.5683 | 61.457 | 0.0072811 | 103.47 | 1120.4 | 1016.93
10341 | 2.5689 | 135.42 | 61.457 | 0.0072829 | 103.48 | 1120.4 |  | 10341 | 135.42 | 2.5689 | 61.457 | 0.0072829 | 103.48 | 1120.4 | 1016.92
10342 | 2.5696 | 135.43 | 61.457 | 0.0072847 | 103.49 | 1120.4 |  | 10342 | 135.43 | 2.5696 | 61.457 | 0.0072847 | 103.49 | 1120.4 | 1016.91
10343 | 2.5703 | 135.44 | 61.457 | 0.0072865 | 103.5 | 1120.4 |  | 10343 | 135.44 | 2.5703 | 61.457 | 0.0072865 | 103.5 | 1120.4 | 1016.9
10344 | 2.571 | 135.45 | 61.457 | 0.0072883 | 103.51 | 1120.5 |  | 10344 | 135.45 | 2.571 | 61.457 | 0.0072883 | 103.51 | 1120.5 | 1016.99
10345 | 2.5716 | 135.46 | 61.456 | 0.0072901 | 103.52 | 1120.5 |  | 10345 | 135.46 | 2.5716 | 61.456 | 0.0072901 | 103.52 | 1120.5 | 1016.98
10346 | 2.5723 | 135.47 | 61.456 | 0.0072919 | 103.53 | 1120.5 |  | 10346 | 135.47 | 2.5723 | 61.456 | 0.0072919 | 103.53 | 1120.5 | 1016.97
10347 | 2.573 | 135.48 | 61.456 | 0.0072937 | 103.54 | 1120.5 |  | 10347 | 135.48 | 2.573 | 61.456 | 0.0072937 | 103.54 | 1120.5 | 1016.96
10348 | 2.5736 | 135.49 | 61.456 | 0.0072955 | 103.55 | 1120.5 |  | 10348 | 135.49 | 2.5736 | 61.456 | 0.0072955 | 103.55 | 1120.5 | 1016.95
10349 | 2.5743 | 135.5 | 61.456 | 0.0072972 | 103.56 | 1120.5 |  | 10349 | 135.5 | 2.5743 | 61.456 | 0.0072972 | 103.56 | 1120.5 | 1016.94
10350 | 2.575 | 135.51 | 61.456 | 0.007299 | 103.57 | 1120.5 |  | 10350 | 135.51 | 2.575 | 61.456 | 0.007299 | 103.57 | 1120.5 | 1016.93
10351 | 2.5757 | 135.52 | 61.455 | 0.0073008 | 103.58 | 1120.5 |  | 10351 | 135.52 | 2.5757 | 61.455 | 0.0073008 | 103.58 | 1120.5 | 1016.92
10352 | 2.5763 | 135.53 | 61.455 | 0.0073026 | 103.59 | 1120.5 |  | 10352 | 135.53 | 2.5763 | 61.455 | 0.0073026 | 103.59 | 1120.5 | 1016.91
10353 | 2.577 | 135.54 | 61.455 | 0.0073044 | 103.6 | 1120.5 |  | 10353 | 135.54 | 2.577 | 61.455 | 0.0073044 | 103.6 | 1120.5 | 1016.9
10354 | 2.5777 | 135.55 | 61.455 | 0.0073062 | 103.61 | 1120.5 |  | 10354 | 135.55 | 2.5777 | 61.455 | 0.0073062 | 103.61 | 1120.5 | 1016.89
10355 | 2.5784 | 135.56 | 61.455 | 0.007308 | 103.62 | 1120.5 |  | 10355 | 135.56 | 2.5784 | 61.455 | 0.007308 | 103.62 | 1120.5 | 1016.88
10356 | 2.579 | 135.57 | 61.455 | 0.0073098 | 103.63 | 1120.5 |  | 10356 | 135.57 | 2.579 | 61.455 | 0.0073098 | 103.63 | 1120.5 | 1016.87
10357 | 2.5797 | 135.58 | 61.454 | 0.0073116 | 103.64 | 1120.5 |  | 10357 | 135.58 | 2.5797 | 61.454 | 0.0073116 | 103.64 | 1120.5 | 1016.86
10358 | 2.5804 | 135.59 | 61.454 | 0.0073134 | 103.65 | 1120.5 |  | 10358 | 135.59 | 2.5804 | 61.454 | 0.0073134 | 103.65 | 1120.5 | 1016.85
10359 | 2.5811 | 135.6 | 61.454 | 0.0073152 | 103.66 | 1120.5 |  | 10359 | 135.6 | 2.5811 | 61.454 | 0.0073152 | 103.66 | 1120.5 | 1016.84
10360 | 2.5817 | 135.61 | 61.454 | 0.007317 | 103.67 | 1120.5 |  | 10360 | 135.61 | 2.5817 | 61.454 | 0.007317 | 103.67 | 1120.5 | 1016.83
10361 | 2.5824 | 135.62 | 61.454 | 0.0073188 | 103.68 | 1120.5 |  | 10361 | 135.62 | 2.5824 | 61.454 | 0.0073188 | 103.68 | 1120.5 | 1016.82
10362 | 2.5831 | 135.63 | 61.454 | 0.0073206 | 103.69 | 1120.5 |  | 10362 | 135.63 | 2.5831 | 61.454 | 0.0073206 | 103.69 | 1120.5 | 1016.81
10363 | 2.5838 | 135.64 | 61.453 | 0.0073224 | 103.7 | 1120.5 |  | 10363 | 135.64 | 2.5838 | 61.453 | 0.0073224 | 103.7 | 1120.5 | 1016.8
10364 | 2.5844 | 135.65 | 61.453 | 0.0073242 | 103.71 | 1120.5 |  | 10364 | 135.65 | 2.5844 | 61.453 | 0.0073242 | 103.71 | 1120.5 | 1016.79
10365 | 2.5851 | 135.66 | 61.453 | 0.007326 | 103.72 | 1120.5 |  | 10365 | 135.66 | 2.5851 | 61.453 | 0.007326 | 103.72 | 1120.5 | 1016.78
10366 | 2.5858 | 135.67 | 61.453 | 0.0073278 | 103.73 | 1120.5 |  | 10366 | 135.67 | 2.5858 | 61.453 | 0.0073278 | 103.73 | 1120.5 | 1016.77
10367 | 2.5865 | 135.68 | 61.453 | 0.0073296 | 103.74 | 1120.5 |  | 10367 | 135.68 | 2.5865 | 61.453 | 0.0073296 | 103.74 | 1120.5 | 1016.76
10368 | 2.5871 | 135.69 | 61.452 | 0.0073314 | 103.75 | 1120.6 |  | 10368 | 135.69 | 2.5871 | 61.452 | 0.0073314 | 103.75 | 1120.6 | 1016.85
10369 | 2.5878 | 135.7 | 61.452 | 0.0073332 | 103.76 | 1120.6 |  | 10369 | 135.7 | 2.5878 | 61.452 | 0.0073332 | 103.76 | 1120.6 | 1016.84
10370 | 2.5885 | 135.71 | 61.452 | 0.007335 | 103.77 | 1120.6 |  | 10370 | 135.71 | 2.5885 | 61.452 | 0.007335 | 103.77 | 1120.6 | 1016.83
10371 | 2.5892 | 135.72 | 61.452 | 0.0073368 | 103.78 | 1120.6 |  | 10371 | 135.72 | 2.5892 | 61.452 | 0.0073368 | 103.78 | 1120.6 | 1016.82
10372 | 2.5899 | 135.73 | 61.452 | 0.0073386 | 103.79 | 1120.6 |  | 10372 | 135.73 | 2.5899 | 61.452 | 0.0073386 | 103.79 | 1120.6 | 1016.81
10373 | 2.5905 | 135.74 | 61.452 | 0.0073404 | 103.8 | 1120.6 |  | 10373 | 135.74 | 2.5905 | 61.452 | 0.0073404 | 103.8 | 1120.6 | 1016.8
10374 | 2.5912 | 135.75 | 61.451 | 0.0073422 | 103.81 | 1120.6 |  | 10374 | 135.75 | 2.5912 | 61.451 | 0.0073422 | 103.81 | 1120.6 | 1016.79
10375 | 2.5919 | 135.76 | 61.451 | 0.007344 | 103.82 | 1120.6 |  | 10375 | 135.76 | 2.5919 | 61.451 | 0.007344 | 103.82 | 1120.6 | 1016.78
10376 | 2.5926 | 135.77 | 61.451 | 0.0073458 | 103.83 | 1120.6 |  | 10376 | 135.77 | 2.5926 | 61.451 | 0.0073458 | 103.83 | 1120.6 | 1016.77
10377 | 2.5932 | 135.78 | 61.451 | 0.0073476 | 103.84 | 1120.6 |  | 10377 | 135.78 | 2.5932 | 61.451 | 0.0073476 | 103.84 | 1120.6 | 1016.76
10378 | 2.5939 | 135.79 | 61.451 | 0.0073494 | 103.85 | 1120.6 |  | 10378 | 135.79 | 2.5939 | 61.451 | 0.0073494 | 103.85 | 1120.6 | 1016.75
10379 | 2.5946 | 135.8 | 61.451 | 0.0073512 | 103.86 | 1120.6 |  | 10379 | 135.8 | 2.5946 | 61.451 | 0.0073512 | 103.86 | 1120.6 | 1016.74
10380 | 2.5953 | 135.81 | 61.45 | 0.007353 | 103.87 | 1120.6 |  | 10380 | 135.81 | 2.5953 | 61.45 | 0.007353 | 103.87 | 1120.6 | 1016.73
10381 | 2.5959 | 135.82 | 61.45 | 0.0073548 | 103.88 | 1120.6 |  | 10381 | 135.82 | 2.5959 | 61.45 | 0.0073548 | 103.88 | 1120.6 | 1016.72
10382 | 2.5966 | 135.83 | 61.45 | 0.0073566 | 103.89 | 1120.6 |  | 10382 | 135.83 | 2.5966 | 61.45 | 0.0073566 | 103.89 | 1120.6 | 1016.71
10383 | 2.5973 | 135.84 | 61.45 | 0.0073584 | 103.9 | 1120.6 |  | 10383 | 135.84 | 2.5973 | 61.45 | 0.0073584 | 103.9 | 1120.6 | 1016.7
10384 | 2.598 | 135.85 | 61.45 | 0.0073602 | 103.91 | 1120.6 |  | 10384 | 135.85 | 2.598 | 61.45 | 0.0073602 | 103.91 | 1120.6 | 1016.69
10385 | 2.5987 | 135.86 | 61.45 | 0.007362 | 103.92 | 1120.6 |  | 10385 | 135.86 | 2.5987 | 61.45 | 0.007362 | 103.92 | 1120.6 | 1016.68
10386 | 2.5993 | 135.87 | 61.449 | 0.0073638 | 103.93 | 1120.6 |  | 10386 | 135.87 | 2.5993 | 61.449 | 0.0073638 | 103.93 | 1120.6 | 1016.67
10387 | 2.6 | 135.88 | 61.449 | 0.0073656 | 103.94 | 1120.6 |  | 10387 | 135.88 | 2.6 | 61.449 | 0.0073656 | 103.94 | 1120.6 | 1016.66
10388 | 2.6007 | 135.89 | 61.449 | 0.0073674 | 103.95 | 1120.6 |  | 10388 | 135.89 | 2.6007 | 61.449 | 0.0073674 | 103.95 | 1120.6 | 1016.65
10389 | 2.6014 | 135.9 | 61.449 | 0.0073692 | 103.96 | 1120.6 |  | 10389 | 135.9 | 2.6014 | 61.449 | 0.0073692 | 103.96 | 1120.6 | 1016.64
10390 | 2.6021 | 135.91 | 61.449 | 0.007371 | 103.97 | 1120.6 |  | 10390 | 135.91 | 2.6021 | 61.449 | 0.007371 | 103.97 | 1120.6 | 1016.63
10391 | 2.6027 | 135.92 | 61.448 | 0.0073728 | 103.98 | 1120.6 |  | 10391 | 135.92 | 2.6027 | 61.448 | 0.0073728 | 103.98 | 1120.6 | 1016.62
10392 | 2.6034 | 135.93 | 61.448 | 0.0073747 | 103.99 | 1120.7 |  | 10392 | 135.93 | 2.6034 | 61.448 | 0.0073747 | 103.99 | 1120.7 | 1016.71
10393 | 2.6041 | 135.94 | 61.448 | 0.0073765 | 104 | 1120.7 |  | 10393 | 135.94 | 2.6041 | 61.448 | 0.0073765 | 104 | 1120.7 | 1016.7
10394 | 2.6048 | 135.95 | 61.448 | 0.0073783 | 104.01 | 1120.7 |  | 10394 | 135.95 | 2.6048 | 61.448 | 0.0073783 | 104.01 | 1120.7 | 1016.69
10395 | 2.6055 | 135.96 | 61.448 | 0.0073801 | 104.02 | 1120.7 |  | 10395 | 135.96 | 2.6055 | 61.448 | 0.0073801 | 104.02 | 1120.7 | 1016.68
10396 | 2.6061 | 135.97 | 61.448 | 0.0073819 | 104.03 | 1120.7 |  | 10396 | 135.97 | 2.6061 | 61.448 | 0.0073819 | 104.03 | 1120.7 | 1016.67
10397 | 2.6068 | 135.98 | 61.447 | 0.0073837 | 104.04 | 1120.7 |  | 10397 | 135.98 | 2.6068 | 61.447 | 0.0073837 | 104.04 | 1120.7 | 1016.66
10398 | 2.6075 | 135.99 | 61.447 | 0.0073855 | 104.05 | 1120.7 |  | 10398 | 135.99 | 2.6075 | 61.447 | 0.0073855 | 104.05 | 1120.7 | 1016.65
10399 | 2.6082 | 136 | 61.447 | 0.0073873 | 104.06 | 1120.7 |  | 10399 | 136 | 2.6082 | 61.447 | 0.0073873 | 104.06 | 1120.7 | 1016.64
10400 | 2.6089 | 136.01 | 61.447 | 0.0073891 | 104.07 | 1120.7 |  | 10400 | 136.01 | 2.6089 | 61.447 | 0.0073891 | 104.07 | 1120.7 | 1016.63
10401 | 2.6095 | 136.02 | 61.447 | 0.0073909 | 104.08 | 1120.7 |  | 10401 | 136.02 | 2.6095 | 61.447 | 0.0073909 | 104.08 | 1120.7 | 1016.62
10402 | 2.6102 | 136.03 | 61.447 | 0.0073928 | 104.09 | 1120.7 |  | 10402 | 136.03 | 2.6102 | 61.447 | 0.0073928 | 104.09 | 1120.7 | 1016.61
10403 | 2.6109 | 136.04 | 61.446 | 0.0073946 | 104.1 | 1120.7 |  | 10403 | 136.04 | 2.6109 | 61.446 | 0.0073946 | 104.1 | 1120.7 | 1016.6
10404 | 2.6116 | 136.05 | 61.446 | 0.0073964 | 104.11 | 1120.7 |  | 10404 | 136.05 | 2.6116 | 61.446 | 0.0073964 | 104.11 | 1120.7 | 1016.59
10405 | 2.6123 | 136.06 | 61.446 | 0.0073982 | 104.12 | 1120.7 |  | 10405 | 136.06 | 2.6123 | 61.446 | 0.0073982 | 104.12 | 1120.7 | 1016.58
10406 | 2.613 | 136.07 | 61.446 | 0.0074 | 104.13 | 1120.7 |  | 10406 | 136.07 | 2.613 | 61.446 | 0.0074 | 104.13 | 1120.7 | 1016.57
10407 | 2.6136 | 136.08 | 61.446 | 0.0074018 | 104.14 | 1120.7 |  | 10407 | 136.08 | 2.6136 | 61.446 | 0.0074018 | 104.14 | 1120.7 | 1016.56
10408 | 2.6143 | 136.09 | 61.446 | 0.0074036 | 104.15 | 1120.7 |  | 10408 | 136.09 | 2.6143 | 61.446 | 0.0074036 | 104.15 | 1120.7 | 1016.55
10409 | 2.615 | 136.1 | 61.445 | 0.0074055 | 104.16 | 1120.7 |  | 10409 | 136.1 | 2.615 | 61.445 | 0.0074055 | 104.16 | 1120.7 | 1016.54
10410 | 2.6157 | 136.11 | 61.445 | 0.0074073 | 104.17 | 1120.7 |  | 10410 | 136.11 | 2.6157 | 61.445 | 0.0074073 | 104.17 | 1120.7 | 1016.53
10411 | 2.6164 | 136.12 | 61.445 | 0.0074091 | 104.18 | 1120.7 |  | 10411 | 136.12 | 2.6164 | 61.445 | 0.0074091 | 104.18 | 1120.7 | 1016.52
10412 | 2.617 | 136.13 | 61.445 | 0.0074109 | 104.19 | 1120.7 |  | 10412 | 136.13 | 2.617 | 61.445 | 0.0074109 | 104.19 | 1120.7 | 1016.51
10413 | 2.6177 | 136.14 | 61.445 | 0.0074127 | 104.2 | 1120.7 |  | 10413 | 136.14 | 2.6177 | 61.445 | 0.0074127 | 104.2 | 1120.7 | 1016.5
10414 | 2.6184 | 136.15 | 61.444 | 0.0074145 | 104.21 | 1120.7 |  | 10414 | 136.15 | 2.6184 | 61.444 | 0.0074145 | 104.21 | 1120.7 | 1016.49
10415 | 2.6191 | 136.16 | 61.444 | 0.0074163 | 104.22 | 1120.7 |  | 10415 | 136.16 | 2.6191 | 61.444 | 0.0074163 | 104.22 | 1120.7 | 1016.48
10416 | 2.6198 | 136.17 | 61.444 | 0.0074182 | 104.23 | 1120.8 |  | 10416 | 136.17 | 2.6198 | 61.444 | 0.0074182 | 104.23 | 1120.8 | 1016.57
10417 | 2.6205 | 136.18 | 61.444 | 0.00742 | 104.24 | 1120.8 |  | 10417 | 136.18 | 2.6205 | 61.444 | 0.00742 | 104.24 | 1120.8 | 1016.56
10418 | 2.6211 | 136.19 | 61.444 | 0.0074218 | 104.25 | 1120.8 |  | 10418 | 136.19 | 2.6211 | 61.444 | 0.0074218 | 104.25 | 1120.8 | 1016.55
10419 | 2.6218 | 136.2 | 61.444 | 0.0074236 | 104.26 | 1120.8 |  | 10419 | 136.2 | 2.6218 | 61.444 | 0.0074236 | 104.26 | 1120.8 | 1016.54
10420 | 2.6225 | 136.21 | 61.443 | 0.0074254 | 104.27 | 1120.8 |  | 10420 | 136.21 | 2.6225 | 61.443 | 0.0074254 | 104.27 | 1120.8 | 1016.53
10421 | 2.6232 | 136.22 | 61.443 | 0.0074273 | 104.28 | 1120.8 |  | 10421 | 136.22 | 2.6232 | 61.443 | 0.0074273 | 104.28 | 1120.8 | 1016.52
10422 | 2.6239 | 136.23 | 61.443 | 0.0074291 | 104.29 | 1120.8 |  | 10422 | 136.23 | 2.6239 | 61.443 | 0.0074291 | 104.29 | 1120.8 | 1016.51
10423 | 2.6246 | 136.24 | 61.443 | 0.0074309 | 104.3 | 1120.8 |  | 10423 | 136.24 | 2.6246 | 61.443 | 0.0074309 | 104.3 | 1120.8 | 1016.5
10424 | 2.6253 | 136.25 | 61.443 | 0.0074327 | 104.31 | 1120.8 |  | 10424 | 136.25 | 2.6253 | 61.443 | 0.0074327 | 104.31 | 1120.8 | 1016.49
10425 | 2.6259 | 136.26 | 61.443 | 0.0074345 | 104.32 | 1120.8 |  | 10425 | 136.26 | 2.6259 | 61.443 | 0.0074345 | 104.32 | 1120.8 | 1016.48
10426 | 2.6266 | 136.27 | 61.442 | 0.0074364 | 104.33 | 1120.8 |  | 10426 | 136.27 | 2.6266 | 61.442 | 0.0074364 | 104.33 | 1120.8 | 1016.47
10427 | 2.6273 | 136.28 | 61.442 | 0.0074382 | 104.34 | 1120.8 |  | 10427 | 136.28 | 2.6273 | 61.442 | 0.0074382 | 104.34 | 1120.8 | 1016.46
10428 | 2.628 | 136.29 | 61.442 | 0.00744 | 104.35 | 1120.8 |  | 10428 | 136.29 | 2.628 | 61.442 | 0.00744 | 104.35 | 1120.8 | 1016.45
10429 | 2.6287 | 136.3 | 61.442 | 0.0074418 | 104.36 | 1120.8 |  | 10429 | 136.3 | 2.6287 | 61.442 | 0.0074418 | 104.36 | 1120.8 | 1016.44
10430 | 2.6294 | 136.31 | 61.442 | 0.0074436 | 104.37 | 1120.8 |  | 10430 | 136.31 | 2.6294 | 61.442 | 0.0074436 | 104.37 | 1120.8 | 1016.43
10431 | 2.63 | 136.32 | 61.442 | 0.0074455 | 104.38 | 1120.8 |  | 10431 | 136.32 | 2.63 | 61.442 | 0.0074455 | 104.38 | 1120.8 | 1016.42
10432 | 2.6307 | 136.33 | 61.441 | 0.0074473 | 104.39 | 1120.8 |  | 10432 | 136.33 | 2.6307 | 61.441 | 0.0074473 | 104.39 | 1120.8 | 1016.41
10433 | 2.6314 | 136.34 | 61.441 | 0.0074491 | 104.4 | 1120.8 |  | 10433 | 136.34 | 2.6314 | 61.441 | 0.0074491 | 104.4 | 1120.8 | 1016.4
10434 | 2.6321 | 136.35 | 61.441 | 0.0074509 | 104.41 | 1120.8 |  | 10434 | 136.35 | 2.6321 | 61.441 | 0.0074509 | 104.41 | 1120.8 | 1016.39
10435 | 2.6328 | 136.36 | 61.441 | 0.0074528 | 104.42 | 1120.8 |  | 10435 | 136.36 | 2.6328 | 61.441 | 0.0074528 | 104.42 | 1120.8 | 1016.38
10436 | 2.6335 | 136.37 | 61.441 | 0.0074546 | 104.43 | 1120.8 |  | 10436 | 136.37 | 2.6335 | 61.441 | 0.0074546 | 104.43 | 1120.8 | 1016.37
10437 | 2.6342 | 136.38 | 61.44 | 0.0074564 | 104.44 | 1120.8 |  | 10437 | 136.38 | 2.6342 | 61.44 | 0.0074564 | 104.44 | 1120.8 | 1016.36
10438 | 2.6349 | 136.39 | 61.44 | 0.0074582 | 104.45 | 1120.8 |  | 10438 | 136.39 | 2.6349 | 61.44 | 0.0074582 | 104.45 | 1120.8 | 1016.35
10439 | 2.6355 | 136.4 | 61.44 | 0.0074601 | 104.46 | 1120.8 |  | 10439 | 136.4 | 2.6355 | 61.44 | 0.0074601 | 104.46 | 1120.8 | 1016.34
10440 | 2.6362 | 136.41 | 61.44 | 0.0074619 | 104.47 | 1120.9 |  | 10440 | 136.41 | 2.6362 | 61.44 | 0.0074619 | 104.47 | 1120.9 | 1016.43
10441 | 2.6369 | 136.42 | 61.44 | 0.0074637 | 104.48 | 1120.9 |  | 10441 | 136.42 | 2.6369 | 61.44 | 0.0074637 | 104.48 | 1120.9 | 1016.42
10442 | 2.6376 | 136.43 | 61.44 | 0.0074655 | 104.49 | 1120.9 |  | 10442 | 136.43 | 2.6376 | 61.44 | 0.0074655 | 104.49 | 1120.9 | 1016.41
10443 | 2.6383 | 136.44 | 61.439 | 0.0074674 | 104.5 | 1120.9 |  | 10443 | 136.44 | 2.6383 | 61.439 | 0.0074674 | 104.5 | 1120.9 | 1016.4
10444 | 2.639 | 136.45 | 61.439 | 0.0074692 | 104.51 | 1120.9 |  | 10444 | 136.45 | 2.639 | 61.439 | 0.0074692 | 104.51 | 1120.9 | 1016.39
10445 | 2.6397 | 136.46 | 61.439 | 0.007471 | 104.52 | 1120.9 |  | 10445 | 136.46 | 2.6397 | 61.439 | 0.007471 | 104.52 | 1120.9 | 1016.38
10446 | 2.6404 | 136.47 | 61.439 | 0.0074729 | 104.53 | 1120.9 |  | 10446 | 136.47 | 2.6404 | 61.439 | 0.0074729 | 104.53 | 1120.9 | 1016.37
10447 | 2.641 | 136.48 | 61.439 | 0.0074747 | 104.54 | 1120.9 |  | 10447 | 136.48 | 2.641 | 61.439 | 0.0074747 | 104.54 | 1120.9 | 1016.36
10448 | 2.6417 | 136.49 | 61.439 | 0.0074765 | 104.55 | 1120.9 |  | 10448 | 136.49 | 2.6417 | 61.439 | 0.0074765 | 104.55 | 1120.9 | 1016.35
10449 | 2.6424 | 136.5 | 61.438 | 0.0074783 | 104.56 | 1120.9 |  | 10449 | 136.5 | 2.6424 | 61.438 | 0.0074783 | 104.56 | 1120.9 | 1016.34
10450 | 2.6431 | 136.51 | 61.438 | 0.0074802 | 104.57 | 1120.9 |  | 10450 | 136.51 | 2.6431 | 61.438 | 0.0074802 | 104.57 | 1120.9 | 1016.33
10451 | 2.6438 | 136.52 | 61.438 | 0.007482 | 104.58 | 1120.9 |  | 10451 | 136.52 | 2.6438 | 61.438 | 0.007482 | 104.58 | 1120.9 | 1016.32
10452 | 2.6445 | 136.53 | 61.438 | 0.0074838 | 104.59 | 1120.9 |  | 10452 | 136.53 | 2.6445 | 61.438 | 0.0074838 | 104.59 | 1120.9 | 1016.31
10453 | 2.6452 | 136.54 | 61.438 | 0.0074857 | 104.6 | 1120.9 |  | 10453 | 136.54 | 2.6452 | 61.438 | 0.0074857 | 104.6 | 1120.9 | 1016.3
10454 | 2.6459 | 136.55 | 61.438 | 0.0074875 | 104.61 | 1120.9 |  | 10454 | 136.55 | 2.6459 | 61.438 | 0.0074875 | 104.61 | 1120.9 | 1016.29
10455 | 2.6466 | 136.56 | 61.437 | 0.0074893 | 104.62 | 1120.9 |  | 10455 | 136.56 | 2.6466 | 61.437 | 0.0074893 | 104.62 | 1120.9 | 1016.28
10456 | 2.6472 | 136.57 | 61.437 | 0.0074912 | 104.63 | 1120.9 |  | 10456 | 136.57 | 2.6472 | 61.437 | 0.0074912 | 104.63 | 1120.9 | 1016.27
10457 | 2.6479 | 136.58 | 61.437 | 0.007493 | 104.64 | 1120.9 |  | 10457 | 136.58 | 2.6479 | 61.437 | 0.007493 | 104.64 | 1120.9 | 1016.26
10458 | 2.6486 | 136.59 | 61.437 | 0.0074948 | 104.65 | 1120.9 |  | 10458 | 136.59 | 2.6486 | 61.437 | 0.0074948 | 104.65 | 1120.9 | 1016.25
10459 | 2.6493 | 136.6 | 61.437 | 0.0074967 | 104.66 | 1120.9 |  | 10459 | 136.6 | 2.6493 | 61.437 | 0.0074967 | 104.66 | 1120.9 | 1016.24
10460 | 2.65 | 136.61 | 61.436 | 0.0074985 | 104.67 | 1120.9 |  | 10460 | 136.61 | 2.65 | 61.436 | 0.0074985 | 104.67 | 1120.9 | 1016.23
10461 | 2.6507 | 136.62 | 61.436 | 0.0075003 | 104.68 | 1120.9 |  | 10461 | 136.62 | 2.6507 | 61.436 | 0.0075003 | 104.68 | 1120.9 | 1016.22
10462 | 2.6514 | 136.63 | 61.436 | 0.0075022 | 104.69 | 1120.9 |  | 10462 | 136.63 | 2.6514 | 61.436 | 0.0075022 | 104.69 | 1120.9 | 1016.21
10463 | 2.6521 | 136.64 | 61.436 | 0.007504 | 104.7 | 1120.9 |  | 10463 | 136.64 | 2.6521 | 61.436 | 0.007504 | 104.7 | 1120.9 | 1016.2
10464 | 2.6528 | 136.65 | 61.436 | 0.0075058 | 104.71 | 1121 |  | 10464 | 136.65 | 2.6528 | 61.436 | 0.0075058 | 104.71 | 1121 | 1016.29
10465 | 2.6535 | 136.66 | 61.436 | 0.0075077 | 104.72 | 1121 |  | 10465 | 136.66 | 2.6535 | 61.436 | 0.0075077 | 104.72 | 1121 | 1016.28
10466 | 2.6541 | 136.67 | 61.435 | 0.0075095 | 104.73 | 1121 |  | 10466 | 136.67 | 2.6541 | 61.435 | 0.0075095 | 104.73 | 1121 | 1016.27
10467 | 2.6548 | 136.68 | 61.435 | 0.0075113 | 104.74 | 1121 |  | 10467 | 136.68 | 2.6548 | 61.435 | 0.0075113 | 104.74 | 1121 | 1016.26
10468 | 2.6555 | 136.69 | 61.435 | 0.0075132 | 104.75 | 1121 |  | 10468 | 136.69 | 2.6555 | 61.435 | 0.0075132 | 104.75 | 1121 | 1016.25
10469 | 2.6562 | 136.7 | 61.435 | 0.007515 | 104.76 | 1121 |  | 10469 | 136.7 | 2.6562 | 61.435 | 0.007515 | 104.76 | 1121 | 1016.24
10470 | 2.6569 | 136.71 | 61.435 | 0.0075168 | 104.77 | 1121 |  | 10470 | 136.71 | 2.6569 | 61.435 | 0.0075168 | 104.77 | 1121 | 1016.23
10471 | 2.6576 | 136.72 | 61.435 | 0.0075187 | 104.78 | 1121 |  | 10471 | 136.72 | 2.6576 | 61.435 | 0.0075187 | 104.78 | 1121 | 1016.22
10472 | 2.6583 | 136.73 | 61.434 | 0.0075205 | 104.79 | 1121 |  | 10472 | 136.73 | 2.6583 | 61.434 | 0.0075205 | 104.79 | 1121 | 1016.21
10473 | 2.659 | 136.74 | 61.434 | 0.0075224 | 104.8 | 1121 |  | 10473 | 136.74 | 2.659 | 61.434 | 0.0075224 | 104.8 | 1121 | 1016.2
10474 | 2.6597 | 136.75 | 61.434 | 0.0075242 | 104.81 | 1121 |  | 10474 | 136.75 | 2.6597 | 61.434 | 0.0075242 | 104.81 | 1121 | 1016.19
10475 | 2.6604 | 136.76 | 61.434 | 0.007526 | 104.82 | 1121 |  | 10475 | 136.76 | 2.6604 | 61.434 | 0.007526 | 104.82 | 1121 | 1016.18
10476 | 2.6611 | 136.77 | 61.434 | 0.0075279 | 104.83 | 1121 |  | 10476 | 136.77 | 2.6611 | 61.434 | 0.0075279 | 104.83 | 1121 | 1016.17
10477 | 2.6618 | 136.78 | 61.434 | 0.0075297 | 104.84 | 1121 |  | 10477 | 136.78 | 2.6618 | 61.434 | 0.0075297 | 104.84 | 1121 | 1016.16
10478 | 2.6625 | 136.79 | 61.433 | 0.0075316 | 104.85 | 1121 |  | 10478 | 136.79 | 2.6625 | 61.433 | 0.0075316 | 104.85 | 1121 | 1016.15
10479 | 2.6631 | 136.8 | 61.433 | 0.0075334 | 104.86 | 1121 |  | 10479 | 136.8 | 2.6631 | 61.433 | 0.0075334 | 104.86 | 1121 | 1016.14
10480 | 2.6638 | 136.81 | 61.433 | 0.0075352 | 104.87 | 1121 |  | 10480 | 136.81 | 2.6638 | 61.433 | 0.0075352 | 104.87 | 1121 | 1016.13
10481 | 2.6645 | 136.82 | 61.433 | 0.0075371 | 104.88 | 1121 |  | 10481 | 136.82 | 2.6645 | 61.433 | 0.0075371 | 104.88 | 1121 | 1016.12
10482 | 2.6652 | 136.83 | 61.433 | 0.0075389 | 104.89 | 1121 |  | 10482 | 136.83 | 2.6652 | 61.433 | 0.0075389 | 104.89 | 1121 | 1016.11
10483 | 2.6659 | 136.84 | 61.432 | 0.0075408 | 104.9 | 1121 |  | 10483 | 136.84 | 2.6659 | 61.432 | 0.0075408 | 104.9 | 1121 | 1016.1
10484 | 2.6666 | 136.85 | 61.432 | 0.0075426 | 104.91 | 1121 |  | 10484 | 136.85 | 2.6666 | 61.432 | 0.0075426 | 104.91 | 1121 | 1016.09
10485 | 2.6673 | 136.86 | 61.432 | 0.0075445 | 104.92 | 1121 |  | 10485 | 136.86 | 2.6673 | 61.432 | 0.0075445 | 104.92 | 1121 | 1016.08
10486 | 2.668 | 136.87 | 61.432 | 0.0075463 | 104.93 | 1121 |  | 10486 | 136.87 | 2.668 | 61.432 | 0.0075463 | 104.93 | 1121 | 1016.07
10487 | 2.6687 | 136.88 | 61.432 | 0.0075481 | 104.94 | 1121 |  | 10487 | 136.88 | 2.6687 | 61.432 | 0.0075481 | 104.94 | 1121 | 1016.06
10488 | 2.6694 | 136.89 | 61.432 | 0.00755 | 104.95 | 1121.1 |  | 10488 | 136.89 | 2.6694 | 61.432 | 0.00755 | 104.95 | 1121.1 | 1016.15
10489 | 2.6701 | 136.9 | 61.431 | 0.0075518 | 104.96 | 1121.1 |  | 10489 | 136.9 | 2.6701 | 61.431 | 0.0075518 | 104.96 | 1121.1 | 1016.14
10490 | 2.6708 | 136.91 | 61.431 | 0.0075537 | 104.97 | 1121.1 |  | 10490 | 136.91 | 2.6708 | 61.431 | 0.0075537 | 104.97 | 1121.1 | 1016.13
10491 | 2.6715 | 136.92 | 61.431 | 0.0075555 | 104.98 | 1121.1 |  | 10491 | 136.92 | 2.6715 | 61.431 | 0.0075555 | 104.98 | 1121.1 | 1016.12
10492 | 2.6722 | 136.93 | 61.431 | 0.0075574 | 104.99 | 1121.1 |  | 10492 | 136.93 | 2.6722 | 61.431 | 0.0075574 | 104.99 | 1121.1 | 1016.11
10493 | 2.6729 | 136.94 | 61.431 | 0.0075592 | 105 | 1121.1 |  | 10493 | 136.94 | 2.6729 | 61.431 | 0.0075592 | 105 | 1121.1 | 1016.1
10494 | 2.6736 | 136.95 | 61.431 | 0.0075611 | 105.01 | 1121.1 |  | 10494 | 136.95 | 2.6736 | 61.431 | 0.0075611 | 105.01 | 1121.1 | 1016.09
10495 | 2.6743 | 136.96 | 61.43 | 0.0075629 | 105.02 | 1121.1 |  | 10495 | 136.96 | 2.6743 | 61.43 | 0.0075629 | 105.02 | 1121.1 | 1016.08
10496 | 2.675 | 136.97 | 61.43 | 0.0075648 | 105.03 | 1121.1 |  | 10496 | 136.97 | 2.675 | 61.43 | 0.0075648 | 105.03 | 1121.1 | 1016.07
10497 | 2.6756 | 136.98 | 61.43 | 0.0075666 | 105.04 | 1121.1 |  | 10497 | 136.98 | 2.6756 | 61.43 | 0.0075666 | 105.04 | 1121.1 | 1016.06
10498 | 2.6763 | 136.99 | 61.43 | 0.0075684 | 105.05 | 1121.1 |  | 10498 | 136.99 | 2.6763 | 61.43 | 0.0075684 | 105.05 | 1121.1 | 1016.05
10499 | 2.677 | 137 | 61.43 | 0.0075703 | 105.06 | 1121.1 |  | 10499 | 137 | 2.677 | 61.43 | 0.0075703 | 105.06 | 1121.1 | 1016.04
10500 | 2.6777 | 137.01 | 61.429 | 0.0075721 | 105.07 | 1121.1 |  | 10500 | 137.01 | 2.6777 | 61.429 | 0.0075721 | 105.07 | 1121.1 | 1016.03
10501 | 2.6784 | 137.02 | 61.429 | 0.007574 | 105.08 | 1121.1 |  | 10501 | 137.02 | 2.6784 | 61.429 | 0.007574 | 105.08 | 1121.1 | 1016.02
10502 | 2.6791 | 137.03 | 61.429 | 0.0075758 | 105.09 | 1121.1 |  | 10502 | 137.03 | 2.6791 | 61.429 | 0.0075758 | 105.09 | 1121.1 | 1016.01
10503 | 2.6798 | 137.04 | 61.429 | 0.0075777 | 105.1 | 1121.1 |  | 10503 | 137.04 | 2.6798 | 61.429 | 0.0075777 | 105.1 | 1121.1 | 1016
10504 | 2.6805 | 137.05 | 61.429 | 0.0075795 | 105.11 | 1121.1 |  | 10504 | 137.05 | 2.6805 | 61.429 | 0.0075795 | 105.11 | 1121.1 | 1015.99
10505 | 2.6812 | 137.06 | 61.429 | 0.0075814 | 105.12 | 1121.1 |  | 10505 | 137.06 | 2.6812 | 61.429 | 0.0075814 | 105.12 | 1121.1 | 1015.98
10506 | 2.6819 | 137.07 | 61.428 | 0.0075832 | 105.13 | 1121.1 |  | 10506 | 137.07 | 2.6819 | 61.428 | 0.0075832 | 105.13 | 1121.1 | 1015.97
10507 | 2.6826 | 137.08 | 61.428 | 0.0075851 | 105.14 | 1121.1 |  | 10507 | 137.08 | 2.6826 | 61.428 | 0.0075851 | 105.14 | 1121.1 | 1015.96
10508 | 2.6833 | 137.09 | 61.428 | 0.0075869 | 105.15 | 1121.1 |  | 10508 | 137.09 | 2.6833 | 61.428 | 0.0075869 | 105.15 | 1121.1 | 1015.95
10509 | 2.684 | 137.1 | 61.428 | 0.0075888 | 105.16 | 1121.1 |  | 10509 | 137.1 | 2.684 | 61.428 | 0.0075888 | 105.16 | 1121.1 | 1015.94
10510 | 2.6847 | 137.11 | 61.428 | 0.0075907 | 105.17 | 1121.1 |  | 10510 | 137.11 | 2.6847 | 61.428 | 0.0075907 | 105.17 | 1121.1 | 1015.93
10511 | 2.6854 | 137.12 | 61.428 | 0.0075925 | 105.18 | 1121.1 |  | 10511 | 137.12 | 2.6854 | 61.428 | 0.0075925 | 105.18 | 1121.1 | 1015.92
10512 | 2.6861 | 137.13 | 61.427 | 0.0075944 | 105.19 | 1121.2 |  | 10512 | 137.13 | 2.6861 | 61.427 | 0.0075944 | 105.19 | 1121.2 | 1016.01
10513 | 2.6868 | 137.14 | 61.427 | 0.0075962 | 105.2 | 1121.2 |  | 10513 | 137.14 | 2.6868 | 61.427 | 0.0075962 | 105.2 | 1121.2 | 1016
10514 | 2.6875 | 137.15 | 61.427 | 0.0075981 | 105.21 | 1121.2 |  | 10514 | 137.15 | 2.6875 | 61.427 | 0.0075981 | 105.21 | 1121.2 | 1015.99
10515 | 2.6882 | 137.16 | 61.427 | 0.0075999 | 105.22 | 1121.2 |  | 10515 | 137.16 | 2.6882 | 61.427 | 0.0075999 | 105.22 | 1121.2 | 1015.98
10516 | 2.6889 | 137.17 | 61.427 | 0.0076018 | 105.23 | 1121.2 |  | 10516 | 137.17 | 2.6889 | 61.427 | 0.0076018 | 105.23 | 1121.2 | 1015.97
10517 | 2.6896 | 137.18 | 61.427 | 0.0076036 | 105.24 | 1121.2 |  | 10517 | 137.18 | 2.6896 | 61.427 | 0.0076036 | 105.24 | 1121.2 | 1015.96
10518 | 2.6903 | 137.19 | 61.426 | 0.0076055 | 105.25 | 1121.2 |  | 10518 | 137.19 | 2.6903 | 61.426 | 0.0076055 | 105.25 | 1121.2 | 1015.95
10519 | 2.691 | 137.2 | 61.426 | 0.0076073 | 105.26 | 1121.2 |  | 10519 | 137.2 | 2.691 | 61.426 | 0.0076073 | 105.26 | 1121.2 | 1015.94
10520 | 2.6917 | 137.21 | 61.426 | 0.0076092 | 105.27 | 1121.2 |  | 10520 | 137.21 | 2.6917 | 61.426 | 0.0076092 | 105.27 | 1121.2 | 1015.93
10521 | 2.6924 | 137.22 | 61.426 | 0.0076111 | 105.28 | 1121.2 |  | 10521 | 137.22 | 2.6924 | 61.426 | 0.0076111 | 105.28 | 1121.2 | 1015.92
10522 | 2.6931 | 137.23 | 61.426 | 0.0076129 | 105.29 | 1121.2 |  | 10522 | 137.23 | 2.6931 | 61.426 | 0.0076129 | 105.29 | 1121.2 | 1015.91
10523 | 2.6938 | 137.24 | 61.425 | 0.0076148 | 105.3 | 1121.2 |  | 10523 | 137.24 | 2.6938 | 61.425 | 0.0076148 | 105.3 | 1121.2 | 1015.9
10524 | 2.6945 | 137.25 | 61.425 | 0.0076166 | 105.31 | 1121.2 |  | 10524 | 137.25 | 2.6945 | 61.425 | 0.0076166 | 105.31 | 1121.2 | 1015.89
10525 | 2.6952 | 137.26 | 61.425 | 0.0076185 | 105.32 | 1121.2 |  | 10525 | 137.26 | 2.6952 | 61.425 | 0.0076185 | 105.32 | 1121.2 | 1015.88
10526 | 2.6959 | 137.27 | 61.425 | 0.0076203 | 105.33 | 1121.2 |  | 10526 | 137.27 | 2.6959 | 61.425 | 0.0076203 | 105.33 | 1121.2 | 1015.87
10527 | 2.6966 | 137.28 | 61.425 | 0.0076222 | 105.34 | 1121.2 |  | 10527 | 137.28 | 2.6966 | 61.425 | 0.0076222 | 105.34 | 1121.2 | 1015.86
10528 | 2.6973 | 137.29 | 61.425 | 0.0076241 | 105.35 | 1121.2 |  | 10528 | 137.29 | 2.6973 | 61.425 | 0.0076241 | 105.35 | 1121.2 | 1015.85
10529 | 2.698 | 137.3 | 61.424 | 0.0076259 | 105.36 | 1121.2 |  | 10529 | 137.3 | 2.698 | 61.424 | 0.0076259 | 105.36 | 1121.2 | 1015.84
10530 | 2.6987 | 137.31 | 61.424 | 0.0076278 | 105.37 | 1121.2 |  | 10530 | 137.31 | 2.6987 | 61.424 | 0.0076278 | 105.37 | 1121.2 | 1015.83
10531 | 2.6994 | 137.32 | 61.424 | 0.0076296 | 105.38 | 1121.2 |  | 10531 | 137.32 | 2.6994 | 61.424 | 0.0076296 | 105.38 | 1121.2 | 1015.82
10532 | 2.7001 | 137.33 | 61.424 | 0.0076315 | 105.39 | 1121.2 |  | 10532 | 137.33 | 2.7001 | 61.424 | 0.0076315 | 105.39 | 1121.2 | 1015.81
10533 | 2.7008 | 137.34 | 61.424 | 0.0076334 | 105.4 | 1121.2 |  | 10533 | 137.34 | 2.7008 | 61.424 | 0.0076334 | 105.4 | 1121.2 | 1015.8
10534 | 2.7015 | 137.35 | 61.424 | 0.0076352 | 105.41 | 1121.2 |  | 10534 | 137.35 | 2.7015 | 61.424 | 0.0076352 | 105.41 | 1121.2 | 1015.79
10535 | 2.7022 | 137.36 | 61.423 | 0.0076371 | 105.42 | 1121.2 |  | 10535 | 137.36 | 2.7022 | 61.423 | 0.0076371 | 105.42 | 1121.2 | 1015.78
10536 | 2.7029 | 137.37 | 61.423 | 0.007639 | 105.43 | 1121.3 |  | 10536 | 137.37 | 2.7029 | 61.423 | 0.007639 | 105.43 | 1121.3 | 1015.87
10537 | 2.7036 | 137.38 | 61.423 | 0.0076408 | 105.44 | 1121.3 |  | 10537 | 137.38 | 2.7036 | 61.423 | 0.0076408 | 105.44 | 1121.3 | 1015.86
10538 | 2.7043 | 137.39 | 61.423 | 0.0076427 | 105.45 | 1121.3 |  | 10538 | 137.39 | 2.7043 | 61.423 | 0.0076427 | 105.45 | 1121.3 | 1015.85
10539 | 2.705 | 137.4 | 61.423 | 0.0076445 | 105.46 | 1121.3 |  | 10539 | 137.4 | 2.705 | 61.423 | 0.0076445 | 105.46 | 1121.3 | 1015.84
10540 | 2.7057 | 137.41 | 61.422 | 0.0076464 | 105.47 | 1121.3 |  | 10540 | 137.41 | 2.7057 | 61.422 | 0.0076464 | 105.47 | 1121.3 | 1015.83
10541 | 2.7064 | 137.42 | 61.422 | 0.0076483 | 105.48 | 1121.3 |  | 10541 | 137.42 | 2.7064 | 61.422 | 0.0076483 | 105.48 | 1121.3 | 1015.82
10542 | 2.7071 | 137.43 | 61.422 | 0.0076501 | 105.49 | 1121.3 |  | 10542 | 137.43 | 2.7071 | 61.422 | 0.0076501 | 105.49 | 1121.3 | 1015.81
10543 | 2.7078 | 137.44 | 61.422 | 0.007652 | 105.5 | 1121.3 |  | 10543 | 137.44 | 2.7078 | 61.422 | 0.007652 | 105.5 | 1121.3 | 1015.8
10544 | 2.7085 | 137.45 | 61.422 | 0.0076539 | 105.51 | 1121.3 |  | 10544 | 137.45 | 2.7085 | 61.422 | 0.0076539 | 105.51 | 1121.3 | 1015.79
10545 | 2.7092 | 137.46 | 61.422 | 0.0076557 | 105.52 | 1121.3 |  | 10545 | 137.46 | 2.7092 | 61.422 | 0.0076557 | 105.52 | 1121.3 | 1015.78
10546 | 2.7099 | 137.47 | 61.421 | 0.0076576 | 105.53 | 1121.3 |  | 10546 | 137.47 | 2.7099 | 61.421 | 0.0076576 | 105.53 | 1121.3 | 1015.77
10547 | 2.7106 | 137.48 | 61.421 | 0.0076595 | 105.54 | 1121.3 |  | 10547 | 137.48 | 2.7106 | 61.421 | 0.0076595 | 105.54 | 1121.3 | 1015.76
10548 | 2.7113 | 137.49 | 61.421 | 0.0076613 | 105.55 | 1121.3 |  | 10548 | 137.49 | 2.7113 | 61.421 | 0.0076613 | 105.55 | 1121.3 | 1015.75
10549 | 2.712 | 137.5 | 61.421 | 0.0076632 | 105.56 | 1121.3 |  | 10549 | 137.5 | 2.712 | 61.421 | 0.0076632 | 105.56 | 1121.3 | 1015.74
10550 | 2.7127 | 137.51 | 61.421 | 0.0076651 | 105.57 | 1121.3 |  | 10550 | 137.51 | 2.7127 | 61.421 | 0.0076651 | 105.57 | 1121.3 | 1015.73
10551 | 2.7135 | 137.52 | 61.421 | 0.0076669 | 105.58 | 1121.3 |  | 10551 | 137.52 | 2.7135 | 61.421 | 0.0076669 | 105.58 | 1121.3 | 1015.72
10552 | 2.7142 | 137.53 | 61.42 | 0.0076688 | 105.59 | 1121.3 |  | 10552 | 137.53 | 2.7142 | 61.42 | 0.0076688 | 105.59 | 1121.3 | 1015.71
10553 | 2.7149 | 137.54 | 61.42 | 0.0076707 | 105.6 | 1121.3 |  | 10553 | 137.54 | 2.7149 | 61.42 | 0.0076707 | 105.6 | 1121.3 | 1015.7
10554 | 2.7156 | 137.55 | 61.42 | 0.0076725 | 105.61 | 1121.3 |  | 10554 | 137.55 | 2.7156 | 61.42 | 0.0076725 | 105.61 | 1121.3 | 1015.69
10555 | 2.7163 | 137.56 | 61.42 | 0.0076744 | 105.62 | 1121.3 |  | 10555 | 137.56 | 2.7163 | 61.42 | 0.0076744 | 105.62 | 1121.3 | 1015.68
10556 | 2.717 | 137.57 | 61.42 | 0.0076763 | 105.63 | 1121.3 |  | 10556 | 137.57 | 2.717 | 61.42 | 0.0076763 | 105.63 | 1121.3 | 1015.67
10557 | 2.7177 | 137.58 | 61.42 | 0.0076781 | 105.64 | 1121.3 |  | 10557 | 137.58 | 2.7177 | 61.42 | 0.0076781 | 105.64 | 1121.3 | 1015.66
10558 | 2.7184 | 137.59 | 61.419 | 0.00768 | 105.65 | 1121.3 |  | 10558 | 137.59 | 2.7184 | 61.419 | 0.00768 | 105.65 | 1121.3 | 1015.65
10559 | 2.7191 | 137.6 | 61.419 | 0.0076819 | 105.66 | 1121.3 |  | 10559 | 137.6 | 2.7191 | 61.419 | 0.0076819 | 105.66 | 1121.3 | 1015.64
10560 | 2.7198 | 137.61 | 61.419 | 0.0076838 | 105.67 | 1121.4 |  | 10560 | 137.61 | 2.7198 | 61.419 | 0.0076838 | 105.67 | 1121.4 | 1015.73
10561 | 2.7205 | 137.62 | 61.419 | 0.0076856 | 105.68 | 1121.4 |  | 10561 | 137.62 | 2.7205 | 61.419 | 0.0076856 | 105.68 | 1121.4 | 1015.72
10562 | 2.7212 | 137.63 | 61.419 | 0.0076875 | 105.69 | 1121.4 |  | 10562 | 137.63 | 2.7212 | 61.419 | 0.0076875 | 105.69 | 1121.4 | 1015.71
10563 | 2.7219 | 137.64 | 61.418 | 0.0076894 | 105.7 | 1121.4 |  | 10563 | 137.64 | 2.7219 | 61.418 | 0.0076894 | 105.7 | 1121.4 | 1015.7
10564 | 2.7226 | 137.65 | 61.418 | 0.0076913 | 105.71 | 1121.4 |  | 10564 | 137.65 | 2.7226 | 61.418 | 0.0076913 | 105.71 | 1121.4 | 1015.69
10565 | 2.7233 | 137.66 | 61.418 | 0.0076931 | 105.72 | 1121.4 |  | 10565 | 137.66 | 2.7233 | 61.418 | 0.0076931 | 105.72 | 1121.4 | 1015.68
10566 | 2.724 | 137.67 | 61.418 | 0.007695 | 105.73 | 1121.4 |  | 10566 | 137.67 | 2.724 | 61.418 | 0.007695 | 105.73 | 1121.4 | 1015.67
10567 | 2.7247 | 137.68 | 61.418 | 0.0076969 | 105.74 | 1121.4 |  | 10567 | 137.68 | 2.7247 | 61.418 | 0.0076969 | 105.74 | 1121.4 | 1015.66
10568 | 2.7254 | 137.69 | 61.418 | 0.0076987 | 105.75 | 1121.4 |  | 10568 | 137.69 | 2.7254 | 61.418 | 0.0076987 | 105.75 | 1121.4 | 1015.65
10569 | 2.7262 | 137.7 | 61.417 | 0.0077006 | 105.76 | 1121.4 |  | 10569 | 137.7 | 2.7262 | 61.417 | 0.0077006 | 105.76 | 1121.4 | 1015.64
10570 | 2.7269 | 137.71 | 61.417 | 0.0077025 | 105.77 | 1121.4 |  | 10570 | 137.71 | 2.7269 | 61.417 | 0.0077025 | 105.77 | 1121.4 | 1015.63
10571 | 2.7276 | 137.72 | 61.417 | 0.0077044 | 105.78 | 1121.4 |  | 10571 | 137.72 | 2.7276 | 61.417 | 0.0077044 | 105.78 | 1121.4 | 1015.62
10572 | 2.7283 | 137.73 | 61.417 | 0.0077063 | 105.79 | 1121.4 |  | 10572 | 137.73 | 2.7283 | 61.417 | 0.0077063 | 105.79 | 1121.4 | 1015.61
10573 | 2.729 | 137.74 | 61.417 | 0.0077081 | 105.8 | 1121.4 |  | 10573 | 137.74 | 2.729 | 61.417 | 0.0077081 | 105.8 | 1121.4 | 1015.6
10574 | 2.7297 | 137.75 | 61.417 | 0.00771 | 105.81 | 1121.4 |  | 10574 | 137.75 | 2.7297 | 61.417 | 0.00771 | 105.81 | 1121.4 | 1015.59
10575 | 2.7304 | 137.76 | 61.416 | 0.0077119 | 105.82 | 1121.4 |  | 10575 | 137.76 | 2.7304 | 61.416 | 0.0077119 | 105.82 | 1121.4 | 1015.58
10576 | 2.7311 | 137.77 | 61.416 | 0.0077138 | 105.83 | 1121.4 |  | 10576 | 137.77 | 2.7311 | 61.416 | 0.0077138 | 105.83 | 1121.4 | 1015.57
10577 | 2.7318 | 137.78 | 61.416 | 0.0077156 | 105.84 | 1121.4 |  | 10577 | 137.78 | 2.7318 | 61.416 | 0.0077156 | 105.84 | 1121.4 | 1015.56
10578 | 2.7325 | 137.79 | 61.416 | 0.0077175 | 105.85 | 1121.4 |  | 10578 | 137.79 | 2.7325 | 61.416 | 0.0077175 | 105.85 | 1121.4 | 1015.55
10579 | 2.7332 | 137.8 | 61.416 | 0.0077194 | 105.86 | 1121.4 |  | 10579 | 137.8 | 2.7332 | 61.416 | 0.0077194 | 105.86 | 1121.4 | 1015.54
10580 | 2.7339 | 137.81 | 61.415 | 0.0077213 | 105.87 | 1121.4 |  | 10580 | 137.81 | 2.7339 | 61.415 | 0.0077213 | 105.87 | 1121.4 | 1015.53
10581 | 2.7347 | 137.82 | 61.415 | 0.0077232 | 105.88 | 1121.4 |  | 10581 | 137.82 | 2.7347 | 61.415 | 0.0077232 | 105.88 | 1121.4 | 1015.52
10582 | 2.7354 | 137.83 | 61.415 | 0.007725 | 105.89 | 1121.4 |  | 10582 | 137.83 | 2.7354 | 61.415 | 0.007725 | 105.89 | 1121.4 | 1015.51
10583 | 2.7361 | 137.84 | 61.415 | 0.0077269 | 105.9 | 1121.4 |  | 10583 | 137.84 | 2.7361 | 61.415 | 0.0077269 | 105.9 | 1121.4 | 1015.5
10584 | 2.7368 | 137.85 | 61.415 | 0.0077288 | 105.91 | 1121.5 |  | 10584 | 137.85 | 2.7368 | 61.415 | 0.0077288 | 105.91 | 1121.5 | 1015.59
10585 | 2.7375 | 137.86 | 61.415 | 0.0077307 | 105.92 | 1121.5 |  | 10585 | 137.86 | 2.7375 | 61.415 | 0.0077307 | 105.92 | 1121.5 | 1015.58
10586 | 2.7382 | 137.87 | 61.414 | 0.0077326 | 105.93 | 1121.5 |  | 10586 | 137.87 | 2.7382 | 61.414 | 0.0077326 | 105.93 | 1121.5 | 1015.57
10587 | 2.7389 | 137.88 | 61.414 | 0.0077344 | 105.94 | 1121.5 |  | 10587 | 137.88 | 2.7389 | 61.414 | 0.0077344 | 105.94 | 1121.5 | 1015.56
10588 | 2.7396 | 137.89 | 61.414 | 0.0077363 | 105.95 | 1121.5 |  | 10588 | 137.89 | 2.7396 | 61.414 | 0.0077363 | 105.95 | 1121.5 | 1015.55
10589 | 2.7403 | 137.9 | 61.414 | 0.0077382 | 105.96 | 1121.5 |  | 10589 | 137.9 | 2.7403 | 61.414 | 0.0077382 | 105.96 | 1121.5 | 1015.54
10590 | 2.741 | 137.91 | 61.414 | 0.0077401 | 105.97 | 1121.5 |  | 10590 | 137.91 | 2.741 | 61.414 | 0.0077401 | 105.97 | 1121.5 | 1015.53
10591 | 2.7418 | 137.92 | 61.414 | 0.007742 | 105.98 | 1121.5 |  | 10591 | 137.92 | 2.7418 | 61.414 | 0.007742 | 105.98 | 1121.5 | 1015.52
10592 | 2.7425 | 137.93 | 61.413 | 0.0077439 | 105.99 | 1121.5 |  | 10592 | 137.93 | 2.7425 | 61.413 | 0.0077439 | 105.99 | 1121.5 | 1015.51
10593 | 2.7432 | 137.94 | 61.413 | 0.0077457 | 106 | 1121.5 |  | 10593 | 137.94 | 2.7432 | 61.413 | 0.0077457 | 106 | 1121.5 | 1015.5
10594 | 2.7439 | 137.95 | 61.413 | 0.0077476 | 106.01 | 1121.5 |  | 10594 | 137.95 | 2.7439 | 61.413 | 0.0077476 | 106.01 | 1121.5 | 1015.49
10595 | 2.7446 | 137.96 | 61.413 | 0.0077495 | 106.02 | 1121.5 |  | 10595 | 137.96 | 2.7446 | 61.413 | 0.0077495 | 106.02 | 1121.5 | 1015.48
10596 | 2.7453 | 137.97 | 61.413 | 0.0077514 | 106.03 | 1121.5 |  | 10596 | 137.97 | 2.7453 | 61.413 | 0.0077514 | 106.03 | 1121.5 | 1015.47
10597 | 2.746 | 137.98 | 61.412 | 0.0077533 | 106.04 | 1121.5 |  | 10597 | 137.98 | 2.746 | 61.412 | 0.0077533 | 106.04 | 1121.5 | 1015.46
10598 | 2.7467 | 137.99 | 61.412 | 0.0077552 | 106.05 | 1121.5 |  | 10598 | 137.99 | 2.7467 | 61.412 | 0.0077552 | 106.05 | 1121.5 | 1015.45
10599 | 2.7474 | 138 | 61.412 | 0.0077571 | 106.06 | 1121.5 |  | 10599 | 138 | 2.7474 | 61.412 | 0.0077571 | 106.06 | 1121.5 | 1015.44
10600 | 2.7482 | 138.01 | 61.412 | 0.0077589 | 106.07 | 1121.5 |  | 10600 | 138.01 | 2.7482 | 61.412 | 0.0077589 | 106.07 | 1121.5 | 1015.43
10601 | 2.7489 | 138.02 | 61.412 | 0.0077608 | 106.08 | 1121.5 |  | 10601 | 138.02 | 2.7489 | 61.412 | 0.0077608 | 106.08 | 1121.5 | 1015.42
10602 | 2.7496 | 138.03 | 61.412 | 0.0077627 | 106.09 | 1121.5 |  | 10602 | 138.03 | 2.7496 | 61.412 | 0.0077627 | 106.09 | 1121.5 | 1015.41
10603 | 2.7503 | 138.04 | 61.411 | 0.0077646 | 106.1 | 1121.5 |  | 10603 | 138.04 | 2.7503 | 61.411 | 0.0077646 | 106.1 | 1121.5 | 1015.4
10604 | 2.751 | 138.05 | 61.411 | 0.0077665 | 106.11 | 1121.5 |  | 10604 | 138.05 | 2.751 | 61.411 | 0.0077665 | 106.11 | 1121.5 | 1015.39
10605 | 2.7517 | 138.06 | 61.411 | 0.0077684 | 106.12 | 1121.5 |  | 10605 | 138.06 | 2.7517 | 61.411 | 0.0077684 | 106.12 | 1121.5 | 1015.38
10606 | 2.7524 | 138.07 | 61.411 | 0.0077703 | 106.13 | 1121.5 |  | 10606 | 138.07 | 2.7524 | 61.411 | 0.0077703 | 106.13 | 1121.5 | 1015.37
10607 | 2.7531 | 138.08 | 61.411 | 0.0077722 | 106.14 | 1121.5 |  | 10607 | 138.08 | 2.7531 | 61.411 | 0.0077722 | 106.14 | 1121.5 | 1015.36
10608 | 2.7539 | 138.09 | 61.411 | 0.007774 | 106.15 | 1121.6 |  | 10608 | 138.09 | 2.7539 | 61.411 | 0.007774 | 106.15 | 1121.6 | 1015.45
10609 | 2.7546 | 138.1 | 61.41 | 0.0077759 | 106.16 | 1121.6 |  | 10609 | 138.1 | 2.7546 | 61.41 | 0.0077759 | 106.16 | 1121.6 | 1015.44
10610 | 2.7553 | 138.11 | 61.41 | 0.0077778 | 106.17 | 1121.6 |  | 10610 | 138.11 | 2.7553 | 61.41 | 0.0077778 | 106.17 | 1121.6 | 1015.43
10611 | 2.756 | 138.12 | 61.41 | 0.0077797 | 106.18 | 1121.6 |  | 10611 | 138.12 | 2.756 | 61.41 | 0.0077797 | 106.18 | 1121.6 | 1015.42
10612 | 2.7567 | 138.13 | 61.41 | 0.0077816 | 106.19 | 1121.6 |  | 10612 | 138.13 | 2.7567 | 61.41 | 0.0077816 | 106.19 | 1121.6 | 1015.41
10613 | 2.7574 | 138.14 | 61.41 | 0.0077835 | 106.2 | 1121.6 |  | 10613 | 138.14 | 2.7574 | 61.41 | 0.0077835 | 106.2 | 1121.6 | 1015.4
10614 | 2.7581 | 138.15 | 61.409 | 0.0077854 | 106.21 | 1121.6 |  | 10614 | 138.15 | 2.7581 | 61.409 | 0.0077854 | 106.21 | 1121.6 | 1015.39
10615 | 2.7588 | 138.16 | 61.409 | 0.0077873 | 106.22 | 1121.6 |  | 10615 | 138.16 | 2.7588 | 61.409 | 0.0077873 | 106.22 | 1121.6 | 1015.38
10616 | 2.7596 | 138.17 | 61.409 | 0.0077892 | 106.23 | 1121.6 |  | 10616 | 138.17 | 2.7596 | 61.409 | 0.0077892 | 106.23 | 1121.6 | 1015.37
10617 | 2.7603 | 138.18 | 61.409 | 0.0077911 | 106.24 | 1121.6 |  | 10617 | 138.18 | 2.7603 | 61.409 | 0.0077911 | 106.24 | 1121.6 | 1015.36
10618 | 2.761 | 138.19 | 61.409 | 0.007793 | 106.25 | 1121.6 |  | 10618 | 138.19 | 2.761 | 61.409 | 0.007793 | 106.25 | 1121.6 | 1015.35
10619 | 2.7617 | 138.2 | 61.409 | 0.0077949 | 106.26 | 1121.6 |  | 10619 | 138.2 | 2.7617 | 61.409 | 0.0077949 | 106.26 | 1121.6 | 1015.34
10620 | 2.7624 | 138.21 | 61.408 | 0.0077968 | 106.27 | 1121.6 |  | 10620 | 138.21 | 2.7624 | 61.408 | 0.0077968 | 106.27 | 1121.6 | 1015.33
10621 | 2.7631 | 138.22 | 61.408 | 0.0077987 | 106.28 | 1121.6 |  | 10621 | 138.22 | 2.7631 | 61.408 | 0.0077987 | 106.28 | 1121.6 | 1015.32
10622 | 2.7639 | 138.23 | 61.408 | 0.0078005 | 106.29 | 1121.6 |  | 10622 | 138.23 | 2.7639 | 61.408 | 0.0078005 | 106.29 | 1121.6 | 1015.31
10623 | 2.7646 | 138.24 | 61.408 | 0.0078024 | 106.3 | 1121.6 |  | 10623 | 138.24 | 2.7646 | 61.408 | 0.0078024 | 106.3 | 1121.6 | 1015.3
10624 | 2.7653 | 138.25 | 61.408 | 0.0078043 | 106.31 | 1121.6 |  | 10624 | 138.25 | 2.7653 | 61.408 | 0.0078043 | 106.31 | 1121.6 | 1015.29
10625 | 2.766 | 138.26 | 61.408 | 0.0078062 | 106.32 | 1121.6 |  | 10625 | 138.26 | 2.766 | 61.408 | 0.0078062 | 106.32 | 1121.6 | 1015.28
10626 | 2.7667 | 138.27 | 61.407 | 0.0078081 | 106.33 | 1121.6 |  | 10626 | 138.27 | 2.7667 | 61.407 | 0.0078081 | 106.33 | 1121.6 | 1015.27
10627 | 2.7674 | 138.28 | 61.407 | 0.00781 | 106.34 | 1121.6 |  | 10627 | 138.28 | 2.7674 | 61.407 | 0.00781 | 106.34 | 1121.6 | 1015.26
10628 | 2.7681 | 138.29 | 61.407 | 0.0078119 | 106.35 | 1121.6 |  | 10628 | 138.29 | 2.7681 | 61.407 | 0.0078119 | 106.35 | 1121.6 | 1015.25
10629 | 2.7689 | 138.3 | 61.407 | 0.0078138 | 106.36 | 1121.6 |  | 10629 | 138.3 | 2.7689 | 61.407 | 0.0078138 | 106.36 | 1121.6 | 1015.24
10630 | 2.7696 | 138.31 | 61.407 | 0.0078157 | 106.37 | 1121.6 |  | 10630 | 138.31 | 2.7696 | 61.407 | 0.0078157 | 106.37 | 1121.6 | 1015.23
10631 | 2.7703 | 138.32 | 61.406 | 0.0078176 | 106.38 | 1121.6 |  | 10631 | 138.32 | 2.7703 | 61.406 | 0.0078176 | 106.38 | 1121.6 | 1015.22
10632 | 2.771 | 138.33 | 61.406 | 0.0078195 | 106.39 | 1121.7 |  | 10632 | 138.33 | 2.771 | 61.406 | 0.0078195 | 106.39 | 1121.7 | 1015.31
10633 | 2.7717 | 138.34 | 61.406 | 0.0078214 | 106.4 | 1121.7 |  | 10633 | 138.34 | 2.7717 | 61.406 | 0.0078214 | 106.4 | 1121.7 | 1015.3
10634 | 2.7725 | 138.35 | 61.406 | 0.0078233 | 106.41 | 1121.7 |  | 10634 | 138.35 | 2.7725 | 61.406 | 0.0078233 | 106.41 | 1121.7 | 1015.29
10635 | 2.7732 | 138.36 | 61.406 | 0.0078252 | 106.42 | 1121.7 |  | 10635 | 138.36 | 2.7732 | 61.406 | 0.0078252 | 106.42 | 1121.7 | 1015.28
10636 | 2.7739 | 138.37 | 61.406 | 0.0078271 | 106.43 | 1121.7 |  | 10636 | 138.37 | 2.7739 | 61.406 | 0.0078271 | 106.43 | 1121.7 | 1015.27
10637 | 2.7746 | 138.38 | 61.405 | 0.007829 | 106.44 | 1121.7 |  | 10637 | 138.38 | 2.7746 | 61.405 | 0.007829 | 106.44 | 1121.7 | 1015.26
10638 | 2.7753 | 138.39 | 61.405 | 0.0078309 | 106.45 | 1121.7 |  | 10638 | 138.39 | 2.7753 | 61.405 | 0.0078309 | 106.45 | 1121.7 | 1015.25
10639 | 2.776 | 138.4 | 61.405 | 0.0078328 | 106.46 | 1121.7 |  | 10639 | 138.4 | 2.776 | 61.405 | 0.0078328 | 106.46 | 1121.7 | 1015.24
10640 | 2.7768 | 138.41 | 61.405 | 0.0078347 | 106.47 | 1121.7 |  | 10640 | 138.41 | 2.7768 | 61.405 | 0.0078347 | 106.47 | 1121.7 | 1015.23
10641 | 2.7775 | 138.42 | 61.405 | 0.0078366 | 106.48 | 1121.7 |  | 10641 | 138.42 | 2.7775 | 61.405 | 0.0078366 | 106.48 | 1121.7 | 1015.22
10642 | 2.7782 | 138.43 | 61.405 | 0.0078385 | 106.49 | 1121.7 |  | 10642 | 138.43 | 2.7782 | 61.405 | 0.0078385 | 106.49 | 1121.7 | 1015.21
10643 | 2.7789 | 138.44 | 61.404 | 0.0078404 | 106.5 | 1121.7 |  | 10643 | 138.44 | 2.7789 | 61.404 | 0.0078404 | 106.5 | 1121.7 | 1015.2
10644 | 2.7796 | 138.45 | 61.404 | 0.0078423 | 106.51 | 1121.7 |  | 10644 | 138.45 | 2.7796 | 61.404 | 0.0078423 | 106.51 | 1121.7 | 1015.19
10645 | 2.7804 | 138.46 | 61.404 | 0.0078443 | 106.52 | 1121.7 |  | 10645 | 138.46 | 2.7804 | 61.404 | 0.0078443 | 106.52 | 1121.7 | 1015.18
10646 | 2.7811 | 138.47 | 61.404 | 0.0078462 | 106.53 | 1121.7 |  | 10646 | 138.47 | 2.7811 | 61.404 | 0.0078462 | 106.53 | 1121.7 | 1015.17
10647 | 2.7818 | 138.48 | 61.404 | 0.0078481 | 106.54 | 1121.7 |  | 10647 | 138.48 | 2.7818 | 61.404 | 0.0078481 | 106.54 | 1121.7 | 1015.16
10648 | 2.7825 | 138.49 | 61.403 | 0.00785 | 106.55 | 1121.7 |  | 10648 | 138.49 | 2.7825 | 61.403 | 0.00785 | 106.55 | 1121.7 | 1015.15
10649 | 2.7832 | 138.5 | 61.403 | 0.0078519 | 106.56 | 1121.7 |  | 10649 | 138.5 | 2.7832 | 61.403 | 0.0078519 | 106.56 | 1121.7 | 1015.14
10650 | 2.7839 | 138.51 | 61.403 | 0.0078538 | 106.57 | 1121.7 |  | 10650 | 138.51 | 2.7839 | 61.403 | 0.0078538 | 106.57 | 1121.7 | 1015.13
10651 | 2.7847 | 138.52 | 61.403 | 0.0078557 | 106.58 | 1121.7 |  | 10651 | 138.52 | 2.7847 | 61.403 | 0.0078557 | 106.58 | 1121.7 | 1015.12
10652 | 2.7854 | 138.53 | 61.403 | 0.0078576 | 106.59 | 1121.7 |  | 10652 | 138.53 | 2.7854 | 61.403 | 0.0078576 | 106.59 | 1121.7 | 1015.11
10653 | 2.7861 | 138.54 | 61.403 | 0.0078595 | 106.6 | 1121.7 |  | 10653 | 138.54 | 2.7861 | 61.403 | 0.0078595 | 106.6 | 1121.7 | 1015.1
10654 | 2.7868 | 138.55 | 61.402 | 0.0078614 | 106.61 | 1121.7 |  | 10654 | 138.55 | 2.7868 | 61.402 | 0.0078614 | 106.61 | 1121.7 | 1015.09
10655 | 2.7875 | 138.56 | 61.402 | 0.0078633 | 106.62 | 1121.7 |  | 10655 | 138.56 | 2.7875 | 61.402 | 0.0078633 | 106.62 | 1121.7 | 1015.08
10656 | 2.7883 | 138.57 | 61.402 | 0.0078652 | 106.63 | 1121.8 |  | 10656 | 138.57 | 2.7883 | 61.402 | 0.0078652 | 106.63 | 1121.8 | 1015.17
10657 | 2.789 | 138.58 | 61.402 | 0.0078671 | 106.64 | 1121.8 |  | 10657 | 138.58 | 2.789 | 61.402 | 0.0078671 | 106.64 | 1121.8 | 1015.16
10658 | 2.7897 | 138.59 | 61.402 | 0.007869 | 106.65 | 1121.8 |  | 10658 | 138.59 | 2.7897 | 61.402 | 0.007869 | 106.65 | 1121.8 | 1015.15
10659 | 2.7904 | 138.6 | 61.402 | 0.007871 | 106.66 | 1121.8 |  | 10659 | 138.6 | 2.7904 | 61.402 | 0.007871 | 106.66 | 1121.8 | 1015.14
10660 | 2.7912 | 138.61 | 61.401 | 0.0078729 | 106.67 | 1121.8 |  | 10660 | 138.61 | 2.7912 | 61.401 | 0.0078729 | 106.67 | 1121.8 | 1015.13
10661 | 2.7919 | 138.62 | 61.401 | 0.0078748 | 106.68 | 1121.8 |  | 10661 | 138.62 | 2.7919 | 61.401 | 0.0078748 | 106.68 | 1121.8 | 1015.12
10662 | 2.7926 | 138.63 | 61.401 | 0.0078767 | 106.69 | 1121.8 |  | 10662 | 138.63 | 2.7926 | 61.401 | 0.0078767 | 106.69 | 1121.8 | 1015.11
10663 | 2.7933 | 138.64 | 61.401 | 0.0078786 | 106.7 | 1121.8 |  | 10663 | 138.64 | 2.7933 | 61.401 | 0.0078786 | 106.7 | 1121.8 | 1015.1
10664 | 2.794 | 138.65 | 61.401 | 0.0078805 | 106.71 | 1121.8 |  | 10664 | 138.65 | 2.794 | 61.401 | 0.0078805 | 106.71 | 1121.8 | 1015.09
10665 | 2.7948 | 138.66 | 61.4 | 0.0078824 | 106.72 | 1121.8 |  | 10665 | 138.66 | 2.7948 | 61.4 | 0.0078824 | 106.72 | 1121.8 | 1015.08
10666 | 2.7955 | 138.67 | 61.4 | 0.0078843 | 106.73 | 1121.8 |  | 10666 | 138.67 | 2.7955 | 61.4 | 0.0078843 | 106.73 | 1121.8 | 1015.07
10667 | 2.7962 | 138.68 | 61.4 | 0.0078862 | 106.74 | 1121.8 |  | 10667 | 138.68 | 2.7962 | 61.4 | 0.0078862 | 106.74 | 1121.8 | 1015.06
10668 | 2.7969 | 138.69 | 61.4 | 0.0078882 | 106.75 | 1121.8 |  | 10668 | 138.69 | 2.7969 | 61.4 | 0.0078882 | 106.75 | 1121.8 | 1015.05
10669 | 2.7977 | 138.7 | 61.4 | 0.0078901 | 106.76 | 1121.8 |  | 10669 | 138.7 | 2.7977 | 61.4 | 0.0078901 | 106.76 | 1121.8 | 1015.04
10670 | 2.7984 | 138.71 | 61.4 | 0.007892 | 106.77 | 1121.8 |  | 10670 | 138.71 | 2.7984 | 61.4 | 0.007892 | 106.77 | 1121.8 | 1015.03
10671 | 2.7991 | 138.72 | 61.399 | 0.0078939 | 106.78 | 1121.8 |  | 10671 | 138.72 | 2.7991 | 61.399 | 0.0078939 | 106.78 | 1121.8 | 1015.02
10672 | 2.7998 | 138.73 | 61.399 | 0.0078958 | 106.79 | 1121.8 |  | 10672 | 138.73 | 2.7998 | 61.399 | 0.0078958 | 106.79 | 1121.8 | 1015.01
10673 | 2.8005 | 138.74 | 61.399 | 0.0078977 | 106.8 | 1121.8 |  | 10673 | 138.74 | 2.8005 | 61.399 | 0.0078977 | 106.8 | 1121.8 | 1015
10674 | 2.8013 | 138.75 | 61.399 | 0.0078996 | 106.81 | 1121.8 |  | 10674 | 138.75 | 2.8013 | 61.399 | 0.0078996 | 106.81 | 1121.8 | 1014.99
10675 | 2.802 | 138.76 | 61.399 | 0.0079016 | 106.82 | 1121.8 |  | 10675 | 138.76 | 2.802 | 61.399 | 0.0079016 | 106.82 | 1121.8 | 1014.98
10676 | 2.8027 | 138.77 | 61.399 | 0.0079035 | 106.83 | 1121.8 |  | 10676 | 138.77 | 2.8027 | 61.399 | 0.0079035 | 106.83 | 1121.8 | 1014.97
10677 | 2.8034 | 138.78 | 61.398 | 0.0079054 | 106.84 | 1121.8 |  | 10677 | 138.78 | 2.8034 | 61.398 | 0.0079054 | 106.84 | 1121.8 | 1014.96
10678 | 2.8042 | 138.79 | 61.398 | 0.0079073 | 106.85 | 1121.8 |  | 10678 | 138.79 | 2.8042 | 61.398 | 0.0079073 | 106.85 | 1121.8 | 1014.95
10679 | 2.8049 | 138.8 | 61.398 | 0.0079092 | 106.86 | 1121.8 |  | 10679 | 138.8 | 2.8049 | 61.398 | 0.0079092 | 106.86 | 1121.8 | 1014.94
10680 | 2.8056 | 138.81 | 61.398 | 0.0079111 | 106.87 | 1121.9 |  | 10680 | 138.81 | 2.8056 | 61.398 | 0.0079111 | 106.87 | 1121.9 | 1015.03
10681 | 2.8063 | 138.82 | 61.398 | 0.0079131 | 106.88 | 1121.9 |  | 10681 | 138.82 | 2.8063 | 61.398 | 0.0079131 | 106.88 | 1121.9 | 1015.02
10682 | 2.8071 | 138.83 | 61.397 | 0.007915 | 106.89 | 1121.9 |  | 10682 | 138.83 | 2.8071 | 61.397 | 0.007915 | 106.89 | 1121.9 | 1015.01
10683 | 2.8078 | 138.84 | 61.397 | 0.0079169 | 106.9 | 1121.9 |  | 10683 | 138.84 | 2.8078 | 61.397 | 0.0079169 | 106.9 | 1121.9 | 1015
10684 | 2.8085 | 138.85 | 61.397 | 0.0079188 | 106.91 | 1121.9 |  | 10684 | 138.85 | 2.8085 | 61.397 | 0.0079188 | 106.91 | 1121.9 | 1014.99
10685 | 2.8092 | 138.86 | 61.397 | 0.0079207 | 106.92 | 1121.9 |  | 10685 | 138.86 | 2.8092 | 61.397 | 0.0079207 | 106.92 | 1121.9 | 1014.98
10686 | 2.81 | 138.87 | 61.397 | 0.0079227 | 106.93 | 1121.9 |  | 10686 | 138.87 | 2.81 | 61.397 | 0.0079227 | 106.93 | 1121.9 | 1014.97
10687 | 2.8107 | 138.88 | 61.397 | 0.0079246 | 106.94 | 1121.9 |  | 10687 | 138.88 | 2.8107 | 61.397 | 0.0079246 | 106.94 | 1121.9 | 1014.96
10688 | 2.8114 | 138.89 | 61.396 | 0.0079265 | 106.95 | 1121.9 |  | 10688 | 138.89 | 2.8114 | 61.396 | 0.0079265 | 106.95 | 1121.9 | 1014.95
10689 | 2.8121 | 138.9 | 61.396 | 0.0079284 | 106.96 | 1121.9 |  | 10689 | 138.9 | 2.8121 | 61.396 | 0.0079284 | 106.96 | 1121.9 | 1014.94
10690 | 2.8129 | 138.91 | 61.396 | 0.0079303 | 106.97 | 1121.9 |  | 10690 | 138.91 | 2.8129 | 61.396 | 0.0079303 | 106.97 | 1121.9 | 1014.93
10691 | 2.8136 | 138.92 | 61.396 | 0.0079323 | 106.98 | 1121.9 |  | 10691 | 138.92 | 2.8136 | 61.396 | 0.0079323 | 106.98 | 1121.9 | 1014.92
10692 | 2.8143 | 138.93 | 61.396 | 0.0079342 | 106.99 | 1121.9 |  | 10692 | 138.93 | 2.8143 | 61.396 | 0.0079342 | 106.99 | 1121.9 | 1014.91
10693 | 2.815 | 138.94 | 61.396 | 0.0079361 | 107 | 1121.9 |  | 10693 | 138.94 | 2.815 | 61.396 | 0.0079361 | 107 | 1121.9 | 1014.9
10694 | 2.8158 | 138.95 | 61.395 | 0.007938 | 107.01 | 1121.9 |  | 10694 | 138.95 | 2.8158 | 61.395 | 0.007938 | 107.01 | 1121.9 | 1014.89
10695 | 2.8165 | 138.96 | 61.395 | 0.00794 | 107.02 | 1121.9 |  | 10695 | 138.96 | 2.8165 | 61.395 | 0.00794 | 107.02 | 1121.9 | 1014.88
10696 | 2.8172 | 138.97 | 61.395 | 0.0079419 | 107.03 | 1121.9 |  | 10696 | 138.97 | 2.8172 | 61.395 | 0.0079419 | 107.03 | 1121.9 | 1014.87
10697 | 2.818 | 138.98 | 61.395 | 0.0079438 | 107.04 | 1121.9 |  | 10697 | 138.98 | 2.818 | 61.395 | 0.0079438 | 107.04 | 1121.9 | 1014.86
10698 | 2.8187 | 138.99 | 61.395 | 0.0079457 | 107.05 | 1121.9 |  | 10698 | 138.99 | 2.8187 | 61.395 | 0.0079457 | 107.05 | 1121.9 | 1014.85
10699 | 2.8194 | 139 | 61.394 | 0.0079477 | 107.06 | 1121.9 |  | 10699 | 139 | 2.8194 | 61.394 | 0.0079477 | 107.06 | 1121.9 | 1014.84
10700 | 2.8201 | 139.01 | 61.394 | 0.0079496 | 107.07 | 1121.9 |  | 10700 | 139.01 | 2.8201 | 61.394 | 0.0079496 | 107.07 | 1121.9 | 1014.83
10701 | 2.8209 | 139.02 | 61.394 | 0.0079515 | 107.08 | 1121.9 |  | 10701 | 139.02 | 2.8209 | 61.394 | 0.0079515 | 107.08 | 1121.9 | 1014.82
10702 | 2.8216 | 139.03 | 61.394 | 0.0079534 | 107.09 | 1121.9 |  | 10702 | 139.03 | 2.8216 | 61.394 | 0.0079534 | 107.09 | 1121.9 | 1014.81
10703 | 2.8223 | 139.04 | 61.394 | 0.0079554 | 107.1 | 1121.9 |  | 10703 | 139.04 | 2.8223 | 61.394 | 0.0079554 | 107.1 | 1121.9 | 1014.8
10704 | 2.8231 | 139.05 | 61.394 | 0.0079573 | 107.11 | 1122 |  | 10704 | 139.05 | 2.8231 | 61.394 | 0.0079573 | 107.11 | 1122 | 1014.89
10705 | 2.8238 | 139.06 | 61.393 | 0.0079592 | 107.12 | 1122 |  | 10705 | 139.06 | 2.8238 | 61.393 | 0.0079592 | 107.12 | 1122 | 1014.88
10706 | 2.8245 | 139.07 | 61.393 | 0.0079611 | 107.13 | 1122 |  | 10706 | 139.07 | 2.8245 | 61.393 | 0.0079611 | 107.13 | 1122 | 1014.87
10707 | 2.8252 | 139.08 | 61.393 | 0.0079631 | 107.14 | 1122 |  | 10707 | 139.08 | 2.8252 | 61.393 | 0.0079631 | 107.14 | 1122 | 1014.86
10708 | 2.826 | 139.09 | 61.393 | 0.007965 | 107.15 | 1122 |  | 10708 | 139.09 | 2.826 | 61.393 | 0.007965 | 107.15 | 1122 | 1014.85
10709 | 2.8267 | 139.1 | 61.393 | 0.0079669 | 107.16 | 1122 |  | 10709 | 139.1 | 2.8267 | 61.393 | 0.0079669 | 107.16 | 1122 | 1014.84
10710 | 2.8274 | 139.11 | 61.393 | 0.0079689 | 107.17 | 1122 |  | 10710 | 139.11 | 2.8274 | 61.393 | 0.0079689 | 107.17 | 1122 | 1014.83
10711 | 2.8282 | 139.12 | 61.392 | 0.0079708 | 107.18 | 1122 |  | 10711 | 139.12 | 2.8282 | 61.392 | 0.0079708 | 107.18 | 1122 | 1014.82
10712 | 2.8289 | 139.13 | 61.392 | 0.0079727 | 107.19 | 1122 |  | 10712 | 139.13 | 2.8289 | 61.392 | 0.0079727 | 107.19 | 1122 | 1014.81
10713 | 2.8296 | 139.14 | 61.392 | 0.0079747 | 107.2 | 1122 |  | 10713 | 139.14 | 2.8296 | 61.392 | 0.0079747 | 107.2 | 1122 | 1014.8
10714 | 2.8303 | 139.15 | 61.392 | 0.0079766 | 107.21 | 1122 |  | 10714 | 139.15 | 2.8303 | 61.392 | 0.0079766 | 107.21 | 1122 | 1014.79
10715 | 2.8311 | 139.16 | 61.392 | 0.0079785 | 107.22 | 1122 |  | 10715 | 139.16 | 2.8311 | 61.392 | 0.0079785 | 107.22 | 1122 | 1014.78
10716 | 2.8318 | 139.17 | 61.391 | 0.0079805 | 107.23 | 1122 |  | 10716 | 139.17 | 2.8318 | 61.391 | 0.0079805 | 107.23 | 1122 | 1014.77
10717 | 2.8325 | 139.18 | 61.391 | 0.0079824 | 107.24 | 1122 |  | 10717 | 139.18 | 2.8325 | 61.391 | 0.0079824 | 107.24 | 1122 | 1014.76
10718 | 2.8333 | 139.19 | 61.391 | 0.0079843 | 107.25 | 1122 |  | 10718 | 139.19 | 2.8333 | 61.391 | 0.0079843 | 107.25 | 1122 | 1014.75
10719 | 2.834 | 139.2 | 61.391 | 0.0079862 | 107.26 | 1122 |  | 10719 | 139.2 | 2.834 | 61.391 | 0.0079862 | 107.26 | 1122 | 1014.74
10720 | 2.8347 | 139.21 | 61.391 | 0.0079882 | 107.27 | 1122 |  | 10720 | 139.21 | 2.8347 | 61.391 | 0.0079882 | 107.27 | 1122 | 1014.73
10721 | 2.8355 | 139.22 | 61.391 | 0.0079901 | 107.28 | 1122 |  | 10721 | 139.22 | 2.8355 | 61.391 | 0.0079901 | 107.28 | 1122 | 1014.72
10722 | 2.8362 | 139.23 | 61.39 | 0.0079921 | 107.29 | 1122 |  | 10722 | 139.23 | 2.8362 | 61.39 | 0.0079921 | 107.29 | 1122 | 1014.71
10723 | 2.8369 | 139.24 | 61.39 | 0.007994 | 107.3 | 1122 |  | 10723 | 139.24 | 2.8369 | 61.39 | 0.007994 | 107.3 | 1122 | 1014.7
10724 | 2.8377 | 139.25 | 61.39 | 0.0079959 | 107.31 | 1122 |  | 10724 | 139.25 | 2.8377 | 61.39 | 0.0079959 | 107.31 | 1122 | 1014.69
10725 | 2.8384 | 139.26 | 61.39 | 0.0079979 | 107.32 | 1122 |  | 10725 | 139.26 | 2.8384 | 61.39 | 0.0079979 | 107.32 | 1122 | 1014.68
10726 | 2.8391 | 139.27 | 61.39 | 0.0079998 | 107.33 | 1122 |  | 10726 | 139.27 | 2.8391 | 61.39 | 0.0079998 | 107.33 | 1122 | 1014.67
10727 | 2.8399 | 139.28 | 61.389 | 0.0080017 | 107.34 | 1122 |  | 10727 | 139.28 | 2.8399 | 61.389 | 0.0080017 | 107.34 | 1122 | 1014.66
10728 | 2.8406 | 139.29 | 61.389 | 0.0080037 | 107.35 | 1122.1 |  | 10728 | 139.29 | 2.8406 | 61.389 | 0.0080037 | 107.35 | 1122.1 | 1014.75
10729 | 2.8413 | 139.3 | 61.389 | 0.0080056 | 107.36 | 1122.1 |  | 10729 | 139.3 | 2.8413 | 61.389 | 0.0080056 | 107.36 | 1122.1 | 1014.74
10730 | 2.842 | 139.31 | 61.389 | 0.0080075 | 107.37 | 1122.1 |  | 10730 | 139.31 | 2.842 | 61.389 | 0.0080075 | 107.37 | 1122.1 | 1014.73
10731 | 2.8428 | 139.32 | 61.389 | 0.0080095 | 107.38 | 1122.1 |  | 10731 | 139.32 | 2.8428 | 61.389 | 0.0080095 | 107.38 | 1122.1 | 1014.72
10732 | 2.8435 | 139.33 | 61.389 | 0.0080114 | 107.39 | 1122.1 |  | 10732 | 139.33 | 2.8435 | 61.389 | 0.0080114 | 107.39 | 1122.1 | 1014.71
10733 | 2.8442 | 139.34 | 61.388 | 0.0080134 | 107.4 | 1122.1 |  | 10733 | 139.34 | 2.8442 | 61.388 | 0.0080134 | 107.4 | 1122.1 | 1014.7
10734 | 2.845 | 139.35 | 61.388 | 0.0080153 | 107.41 | 1122.1 |  | 10734 | 139.35 | 2.845 | 61.388 | 0.0080153 | 107.41 | 1122.1 | 1014.69
10735 | 2.8457 | 139.36 | 61.388 | 0.0080172 | 107.42 | 1122.1 |  | 10735 | 139.36 | 2.8457 | 61.388 | 0.0080172 | 107.42 | 1122.1 | 1014.68
10736 | 2.8464 | 139.37 | 61.388 | 0.0080192 | 107.43 | 1122.1 |  | 10736 | 139.37 | 2.8464 | 61.388 | 0.0080192 | 107.43 | 1122.1 | 1014.67
10737 | 2.8472 | 139.38 | 61.388 | 0.0080211 | 107.44 | 1122.1 |  | 10737 | 139.38 | 2.8472 | 61.388 | 0.0080211 | 107.44 | 1122.1 | 1014.66
10738 | 2.8479 | 139.39 | 61.388 | 0.0080231 | 107.45 | 1122.1 |  | 10738 | 139.39 | 2.8479 | 61.388 | 0.0080231 | 107.45 | 1122.1 | 1014.65
10739 | 2.8486 | 139.4 | 61.387 | 0.008025 | 107.46 | 1122.1 |  | 10739 | 139.4 | 2.8486 | 61.387 | 0.008025 | 107.46 | 1122.1 | 1014.64
10740 | 2.8494 | 139.41 | 61.387 | 0.0080269 | 107.47 | 1122.1 |  | 10740 | 139.41 | 2.8494 | 61.387 | 0.0080269 | 107.47 | 1122.1 | 1014.63
10741 | 2.8501 | 139.42 | 61.387 | 0.0080289 | 107.48 | 1122.1 |  | 10741 | 139.42 | 2.8501 | 61.387 | 0.0080289 | 107.48 | 1122.1 | 1014.62
10742 | 2.8509 | 139.43 | 61.387 | 0.0080308 | 107.49 | 1122.1 |  | 10742 | 139.43 | 2.8509 | 61.387 | 0.0080308 | 107.49 | 1122.1 | 1014.61
10743 | 2.8516 | 139.44 | 61.387 | 0.0080328 | 107.5 | 1122.1 |  | 10743 | 139.44 | 2.8516 | 61.387 | 0.0080328 | 107.5 | 1122.1 | 1014.6
10744 | 2.8523 | 139.45 | 61.386 | 0.0080347 | 107.51 | 1122.1 |  | 10744 | 139.45 | 2.8523 | 61.386 | 0.0080347 | 107.51 | 1122.1 | 1014.59
10745 | 2.8531 | 139.46 | 61.386 | 0.0080367 | 107.52 | 1122.1 |  | 10745 | 139.46 | 2.8531 | 61.386 | 0.0080367 | 107.52 | 1122.1 | 1014.58
10746 | 2.8538 | 139.47 | 61.386 | 0.0080386 | 107.53 | 1122.1 |  | 10746 | 139.47 | 2.8538 | 61.386 | 0.0080386 | 107.53 | 1122.1 | 1014.57
10747 | 2.8545 | 139.48 | 61.386 | 0.0080405 | 107.54 | 1122.1 |  | 10747 | 139.48 | 2.8545 | 61.386 | 0.0080405 | 107.54 | 1122.1 | 1014.56
10748 | 2.8553 | 139.49 | 61.386 | 0.0080425 | 107.55 | 1122.1 |  | 10748 | 139.49 | 2.8553 | 61.386 | 0.0080425 | 107.55 | 1122.1 | 1014.55
10749 | 2.856 | 139.5 | 61.386 | 0.0080444 | 107.56 | 1122.1 |  | 10749 | 139.5 | 2.856 | 61.386 | 0.0080444 | 107.56 | 1122.1 | 1014.54
10750 | 2.8567 | 139.51 | 61.385 | 0.0080464 | 107.57 | 1122.1 |  | 10750 | 139.51 | 2.8567 | 61.385 | 0.0080464 | 107.57 | 1122.1 | 1014.53
10751 | 2.8575 | 139.52 | 61.385 | 0.0080483 | 107.58 | 1122.1 |  | 10751 | 139.52 | 2.8575 | 61.385 | 0.0080483 | 107.58 | 1122.1 | 1014.52
10752 | 2.8582 | 139.53 | 61.385 | 0.0080503 | 107.59 | 1122.2 |  | 10752 | 139.53 | 2.8582 | 61.385 | 0.0080503 | 107.59 | 1122.2 | 1014.61
10753 | 2.8589 | 139.54 | 61.385 | 0.0080522 | 107.6 | 1122.2 |  | 10753 | 139.54 | 2.8589 | 61.385 | 0.0080522 | 107.6 | 1122.2 | 1014.6
10754 | 2.8597 | 139.55 | 61.385 | 0.0080542 | 107.61 | 1122.2 |  | 10754 | 139.55 | 2.8597 | 61.385 | 0.0080542 | 107.61 | 1122.2 | 1014.59
10755 | 2.8604 | 139.56 | 61.385 | 0.0080561 | 107.62 | 1122.2 |  | 10755 | 139.56 | 2.8604 | 61.385 | 0.0080561 | 107.62 | 1122.2 | 1014.58
10756 | 2.8612 | 139.57 | 61.384 | 0.0080581 | 107.63 | 1122.2 |  | 10756 | 139.57 | 2.8612 | 61.384 | 0.0080581 | 107.63 | 1122.2 | 1014.57
10757 | 2.8619 | 139.58 | 61.384 | 0.00806 | 107.64 | 1122.2 |  | 10757 | 139.58 | 2.8619 | 61.384 | 0.00806 | 107.64 | 1122.2 | 1014.56
10758 | 2.8626 | 139.59 | 61.384 | 0.008062 | 107.65 | 1122.2 |  | 10758 | 139.59 | 2.8626 | 61.384 | 0.008062 | 107.65 | 1122.2 | 1014.55
10759 | 2.8634 | 139.6 | 61.384 | 0.0080639 | 107.66 | 1122.2 |  | 10759 | 139.6 | 2.8634 | 61.384 | 0.0080639 | 107.66 | 1122.2 | 1014.54
10760 | 2.8641 | 139.61 | 61.384 | 0.0080658 | 107.67 | 1122.2 |  | 10760 | 139.61 | 2.8641 | 61.384 | 0.0080658 | 107.67 | 1122.2 | 1014.53
10761 | 2.8648 | 139.62 | 61.383 | 0.0080678 | 107.68 | 1122.2 |  | 10761 | 139.62 | 2.8648 | 61.383 | 0.0080678 | 107.68 | 1122.2 | 1014.52
10762 | 2.8656 | 139.63 | 61.383 | 0.0080697 | 107.69 | 1122.2 |  | 10762 | 139.63 | 2.8656 | 61.383 | 0.0080697 | 107.69 | 1122.2 | 1014.51
10763 | 2.8663 | 139.64 | 61.383 | 0.0080717 | 107.7 | 1122.2 |  | 10763 | 139.64 | 2.8663 | 61.383 | 0.0080717 | 107.7 | 1122.2 | 1014.5
10764 | 2.8671 | 139.65 | 61.383 | 0.0080736 | 107.71 | 1122.2 |  | 10764 | 139.65 | 2.8671 | 61.383 | 0.0080736 | 107.71 | 1122.2 | 1014.49
10765 | 2.8678 | 139.66 | 61.383 | 0.0080756 | 107.72 | 1122.2 |  | 10765 | 139.66 | 2.8678 | 61.383 | 0.0080756 | 107.72 | 1122.2 | 1014.48
10766 | 2.8685 | 139.67 | 61.383 | 0.0080776 | 107.73 | 1122.2 |  | 10766 | 139.67 | 2.8685 | 61.383 | 0.0080776 | 107.73 | 1122.2 | 1014.47
10767 | 2.8693 | 139.68 | 61.382 | 0.0080795 | 107.74 | 1122.2 |  | 10767 | 139.68 | 2.8693 | 61.382 | 0.0080795 | 107.74 | 1122.2 | 1014.46
10768 | 2.87 | 139.69 | 61.382 | 0.0080815 | 107.75 | 1122.2 |  | 10768 | 139.69 | 2.87 | 61.382 | 0.0080815 | 107.75 | 1122.2 | 1014.45
10769 | 2.8707 | 139.7 | 61.382 | 0.0080834 | 107.76 | 1122.2 |  | 10769 | 139.7 | 2.8707 | 61.382 | 0.0080834 | 107.76 | 1122.2 | 1014.44
10770 | 2.8715 | 139.71 | 61.382 | 0.0080854 | 107.77 | 1122.2 |  | 10770 | 139.71 | 2.8715 | 61.382 | 0.0080854 | 107.77 | 1122.2 | 1014.43
10771 | 2.8722 | 139.72 | 61.382 | 0.0080873 | 107.78 | 1122.2 |  | 10771 | 139.72 | 2.8722 | 61.382 | 0.0080873 | 107.78 | 1122.2 | 1014.42
10772 | 2.873 | 139.73 | 61.381 | 0.0080893 | 107.79 | 1122.2 |  | 10772 | 139.73 | 2.873 | 61.381 | 0.0080893 | 107.79 | 1122.2 | 1014.41
10773 | 2.8737 | 139.74 | 61.381 | 0.0080912 | 107.8 | 1122.2 |  | 10773 | 139.74 | 2.8737 | 61.381 | 0.0080912 | 107.8 | 1122.2 | 1014.4
10774 | 2.8744 | 139.75 | 61.381 | 0.0080932 | 107.81 | 1122.2 |  | 10774 | 139.75 | 2.8744 | 61.381 | 0.0080932 | 107.81 | 1122.2 | 1014.39
10775 | 2.8752 | 139.76 | 61.381 | 0.0080951 | 107.82 | 1122.2 |  | 10775 | 139.76 | 2.8752 | 61.381 | 0.0080951 | 107.82 | 1122.2 | 1014.38
10776 | 2.8759 | 139.77 | 61.381 | 0.0080971 | 107.83 | 1122.3 |  | 10776 | 139.77 | 2.8759 | 61.381 | 0.0080971 | 107.83 | 1122.3 | 1014.47
10777 | 2.8767 | 139.78 | 61.381 | 0.008099 | 107.84 | 1122.3 |  | 10777 | 139.78 | 2.8767 | 61.381 | 0.008099 | 107.84 | 1122.3 | 1014.46
10778 | 2.8774 | 139.79 | 61.38 | 0.008101 | 107.85 | 1122.3 |  | 10778 | 139.79 | 2.8774 | 61.38 | 0.008101 | 107.85 | 1122.3 | 1014.45
10779 | 2.8781 | 139.8 | 61.38 | 0.008103 | 107.86 | 1122.3 |  | 10779 | 139.8 | 2.8781 | 61.38 | 0.008103 | 107.86 | 1122.3 | 1014.44
10780 | 2.8789 | 139.81 | 61.38 | 0.0081049 | 107.87 | 1122.3 |  | 10780 | 139.81 | 2.8789 | 61.38 | 0.0081049 | 107.87 | 1122.3 | 1014.43
10781 | 2.8796 | 139.82 | 61.38 | 0.0081069 | 107.88 | 1122.3 |  | 10781 | 139.82 | 2.8796 | 61.38 | 0.0081069 | 107.88 | 1122.3 | 1014.42
10782 | 2.8804 | 139.83 | 61.38 | 0.0081088 | 107.89 | 1122.3 |  | 10782 | 139.83 | 2.8804 | 61.38 | 0.0081088 | 107.89 | 1122.3 | 1014.41
10783 | 2.8811 | 139.84 | 61.38 | 0.0081108 | 107.9 | 1122.3 |  | 10783 | 139.84 | 2.8811 | 61.38 | 0.0081108 | 107.9 | 1122.3 | 1014.4
10784 | 2.8818 | 139.85 | 61.379 | 0.0081128 | 107.91 | 1122.3 |  | 10784 | 139.85 | 2.8818 | 61.379 | 0.0081128 | 107.91 | 1122.3 | 1014.39
10785 | 2.8826 | 139.86 | 61.379 | 0.0081147 | 107.92 | 1122.3 |  | 10785 | 139.86 | 2.8826 | 61.379 | 0.0081147 | 107.92 | 1122.3 | 1014.38
10786 | 2.8833 | 139.87 | 61.379 | 0.0081167 | 107.93 | 1122.3 |  | 10786 | 139.87 | 2.8833 | 61.379 | 0.0081167 | 107.93 | 1122.3 | 1014.37
10787 | 2.8841 | 139.88 | 61.379 | 0.0081186 | 107.94 | 1122.3 |  | 10787 | 139.88 | 2.8841 | 61.379 | 0.0081186 | 107.94 | 1122.3 | 1014.36
10788 | 2.8848 | 139.89 | 61.379 | 0.0081206 | 107.95 | 1122.3 |  | 10788 | 139.89 | 2.8848 | 61.379 | 0.0081206 | 107.95 | 1122.3 | 1014.35
10789 | 2.8856 | 139.9 | 61.378 | 0.0081226 | 107.96 | 1122.3 |  | 10789 | 139.9 | 2.8856 | 61.378 | 0.0081226 | 107.96 | 1122.3 | 1014.34
10790 | 2.8863 | 139.91 | 61.378 | 0.0081245 | 107.97 | 1122.3 |  | 10790 | 139.91 | 2.8863 | 61.378 | 0.0081245 | 107.97 | 1122.3 | 1014.33
10791 | 2.887 | 139.92 | 61.378 | 0.0081265 | 107.98 | 1122.3 |  | 10791 | 139.92 | 2.887 | 61.378 | 0.0081265 | 107.98 | 1122.3 | 1014.32
10792 | 2.8878 | 139.93 | 61.378 | 0.0081284 | 107.99 | 1122.3 |  | 10792 | 139.93 | 2.8878 | 61.378 | 0.0081284 | 107.99 | 1122.3 | 1014.31
10793 | 2.8885 | 139.94 | 61.378 | 0.0081304 | 108 | 1122.3 |  | 10793 | 139.94 | 2.8885 | 61.378 | 0.0081304 | 108 | 1122.3 | 1014.3
10794 | 2.8893 | 139.95 | 61.378 | 0.0081324 | 108.01 | 1122.3 |  | 10794 | 139.95 | 2.8893 | 61.378 | 0.0081324 | 108.01 | 1122.3 | 1014.29
10795 | 2.89 | 139.96 | 61.377 | 0.0081343 | 108.02 | 1122.3 |  | 10795 | 139.96 | 2.89 | 61.377 | 0.0081343 | 108.02 | 1122.3 | 1014.28
10796 | 2.8908 | 139.97 | 61.377 | 0.0081363 | 108.03 | 1122.3 |  | 10796 | 139.97 | 2.8908 | 61.377 | 0.0081363 | 108.03 | 1122.3 | 1014.27
10797 | 2.8915 | 139.98 | 61.377 | 0.0081383 | 108.04 | 1122.3 |  | 10797 | 139.98 | 2.8915 | 61.377 | 0.0081383 | 108.04 | 1122.3 | 1014.26
10798 | 2.8922 | 139.99 | 61.377 | 0.0081402 | 108.05 | 1122.3 |  | 10798 | 139.99 | 2.8922 | 61.377 | 0.0081402 | 108.05 | 1122.3 | 1014.25
10799 | 2.893 | 140 | 61.377 | 0.0081422 | 108.06 | 1122.3 |  | 10799 | 140 | 2.893 | 61.377 | 0.0081422 | 108.06 | 1122.3 | 1014.24
10800 | 2.8937 | 140.01 | 61.377 | 0.0081441 | 108.07 | 1122.4 |  | 10800 | 140.01 | 2.8937 | 61.377 | 0.0081441 | 108.07 | 1122.4 | 1014.33
10801 | 2.8945 | 140.02 | 61.376 | 0.0081461 | 108.08 | 1122.4 |  | 10801 | 140.02 | 2.8945 | 61.376 | 0.0081461 | 108.08 | 1122.4 | 1014.32
10802 | 2.8952 | 140.03 | 61.376 | 0.0081481 | 108.09 | 1122.4 |  | 10802 | 140.03 | 2.8952 | 61.376 | 0.0081481 | 108.09 | 1122.4 | 1014.31
10803 | 2.896 | 140.04 | 61.376 | 0.00815 | 108.1 | 1122.4 |  | 10803 | 140.04 | 2.896 | 61.376 | 0.00815 | 108.1 | 1122.4 | 1014.3
10804 | 2.8967 | 140.05 | 61.376 | 0.008152 | 108.11 | 1122.4 |  | 10804 | 140.05 | 2.8967 | 61.376 | 0.008152 | 108.11 | 1122.4 | 1014.29
10805 | 2.8975 | 140.06 | 61.376 | 0.008154 | 108.12 | 1122.4 |  | 10805 | 140.06 | 2.8975 | 61.376 | 0.008154 | 108.12 | 1122.4 | 1014.28
10806 | 2.8982 | 140.07 | 61.375 | 0.0081559 | 108.13 | 1122.4 |  | 10806 | 140.07 | 2.8982 | 61.375 | 0.0081559 | 108.13 | 1122.4 | 1014.27
10807 | 2.8989 | 140.08 | 61.375 | 0.0081579 | 108.14 | 1122.4 |  | 10807 | 140.08 | 2.8989 | 61.375 | 0.0081579 | 108.14 | 1122.4 | 1014.26
10808 | 2.8997 | 140.09 | 61.375 | 0.0081599 | 108.15 | 1122.4 |  | 10808 | 140.09 | 2.8997 | 61.375 | 0.0081599 | 108.15 | 1122.4 | 1014.25
10809 | 2.9004 | 140.1 | 61.375 | 0.0081619 | 108.16 | 1122.4 |  | 10809 | 140.1 | 2.9004 | 61.375 | 0.0081619 | 108.16 | 1122.4 | 1014.24
10810 | 2.9012 | 140.11 | 61.375 | 0.0081638 | 108.17 | 1122.4 |  | 10810 | 140.11 | 2.9012 | 61.375 | 0.0081638 | 108.17 | 1122.4 | 1014.23
10811 | 2.9019 | 140.12 | 61.375 | 0.0081658 | 108.18 | 1122.4 |  | 10811 | 140.12 | 2.9019 | 61.375 | 0.0081658 | 108.18 | 1122.4 | 1014.22
10812 | 2.9027 | 140.13 | 61.374 | 0.0081678 | 108.19 | 1122.4 |  | 10812 | 140.13 | 2.9027 | 61.374 | 0.0081678 | 108.19 | 1122.4 | 1014.21
10813 | 2.9034 | 140.14 | 61.374 | 0.0081697 | 108.2 | 1122.4 |  | 10813 | 140.14 | 2.9034 | 61.374 | 0.0081697 | 108.2 | 1122.4 | 1014.2
10814 | 2.9042 | 140.15 | 61.374 | 0.0081717 | 108.21 | 1122.4 |  | 10814 | 140.15 | 2.9042 | 61.374 | 0.0081717 | 108.21 | 1122.4 | 1014.19
10815 | 2.9049 | 140.16 | 61.374 | 0.0081737 | 108.22 | 1122.4 |  | 10815 | 140.16 | 2.9049 | 61.374 | 0.0081737 | 108.22 | 1122.4 | 1014.18
10816 | 2.9057 | 140.17 | 61.374 | 0.0081756 | 108.23 | 1122.4 |  | 10816 | 140.17 | 2.9057 | 61.374 | 0.0081756 | 108.23 | 1122.4 | 1014.17
10817 | 2.9064 | 140.18 | 61.373 | 0.0081776 | 108.24 | 1122.4 |  | 10817 | 140.18 | 2.9064 | 61.373 | 0.0081776 | 108.24 | 1122.4 | 1014.16
10818 | 2.9071 | 140.19 | 61.373 | 0.0081796 | 108.25 | 1122.4 |  | 10818 | 140.19 | 2.9071 | 61.373 | 0.0081796 | 108.25 | 1122.4 | 1014.15
10819 | 2.9079 | 140.2 | 61.373 | 0.0081816 | 108.26 | 1122.4 |  | 10819 | 140.2 | 2.9079 | 61.373 | 0.0081816 | 108.26 | 1122.4 | 1014.14
10820 | 2.9086 | 140.21 | 61.373 | 0.0081835 | 108.27 | 1122.4 |  | 10820 | 140.21 | 2.9086 | 61.373 | 0.0081835 | 108.27 | 1122.4 | 1014.13
10821 | 2.9094 | 140.22 | 61.373 | 0.0081855 | 108.28 | 1122.4 |  | 10821 | 140.22 | 2.9094 | 61.373 | 0.0081855 | 108.28 | 1122.4 | 1014.12
10822 | 2.9101 | 140.23 | 61.373 | 0.0081875 | 108.29 | 1122.4 |  | 10822 | 140.23 | 2.9101 | 61.373 | 0.0081875 | 108.29 | 1122.4 | 1014.11
10823 | 2.9109 | 140.24 | 61.372 | 0.0081895 | 108.3 | 1122.4 |  | 10823 | 140.24 | 2.9109 | 61.372 | 0.0081895 | 108.3 | 1122.4 | 1014.1
10824 | 2.9116 | 140.25 | 61.372 | 0.0081914 | 108.31 | 1122.5 |  | 10824 | 140.25 | 2.9116 | 61.372 | 0.0081914 | 108.31 | 1122.5 | 1014.19
10825 | 2.9124 | 140.26 | 61.372 | 0.0081934 | 108.32 | 1122.5 |  | 10825 | 140.26 | 2.9124 | 61.372 | 0.0081934 | 108.32 | 1122.5 | 1014.18
10826 | 2.9131 | 140.27 | 61.372 | 0.0081954 | 108.33 | 1122.5 |  | 10826 | 140.27 | 2.9131 | 61.372 | 0.0081954 | 108.33 | 1122.5 | 1014.17
10827 | 2.9139 | 140.28 | 61.372 | 0.0081974 | 108.34 | 1122.5 |  | 10827 | 140.28 | 2.9139 | 61.372 | 0.0081974 | 108.34 | 1122.5 | 1014.16
10828 | 2.9146 | 140.29 | 61.372 | 0.0081993 | 108.35 | 1122.5 |  | 10828 | 140.29 | 2.9146 | 61.372 | 0.0081993 | 108.35 | 1122.5 | 1014.15
10829 | 2.9154 | 140.3 | 61.371 | 0.0082013 | 108.36 | 1122.5 |  | 10829 | 140.3 | 2.9154 | 61.371 | 0.0082013 | 108.36 | 1122.5 | 1014.14
10830 | 2.9161 | 140.31 | 61.371 | 0.0082033 | 108.37 | 1122.5 |  | 10830 | 140.31 | 2.9161 | 61.371 | 0.0082033 | 108.37 | 1122.5 | 1014.13
10831 | 2.9169 | 140.32 | 61.371 | 0.0082053 | 108.38 | 1122.5 |  | 10831 | 140.32 | 2.9169 | 61.371 | 0.0082053 | 108.38 | 1122.5 | 1014.12
10832 | 2.9176 | 140.33 | 61.371 | 0.0082072 | 108.39 | 1122.5 |  | 10832 | 140.33 | 2.9176 | 61.371 | 0.0082072 | 108.39 | 1122.5 | 1014.11
10833 | 2.9184 | 140.34 | 61.371 | 0.0082092 | 108.4 | 1122.5 |  | 10833 | 140.34 | 2.9184 | 61.371 | 0.0082092 | 108.4 | 1122.5 | 1014.1
10834 | 2.9191 | 140.35 | 61.37 | 0.0082112 | 108.41 | 1122.5 |  | 10834 | 140.35 | 2.9191 | 61.37 | 0.0082112 | 108.41 | 1122.5 | 1014.09
10835 | 2.9199 | 140.36 | 61.37 | 0.0082132 | 108.42 | 1122.5 |  | 10835 | 140.36 | 2.9199 | 61.37 | 0.0082132 | 108.42 | 1122.5 | 1014.08
10836 | 2.9206 | 140.37 | 61.37 | 0.0082152 | 108.43 | 1122.5 |  | 10836 | 140.37 | 2.9206 | 61.37 | 0.0082152 | 108.43 | 1122.5 | 1014.07
10837 | 2.9214 | 140.38 | 61.37 | 0.0082171 | 108.44 | 1122.5 |  | 10837 | 140.38 | 2.9214 | 61.37 | 0.0082171 | 108.44 | 1122.5 | 1014.06
10838 | 2.9221 | 140.39 | 61.37 | 0.0082191 | 108.45 | 1122.5 |  | 10838 | 140.39 | 2.9221 | 61.37 | 0.0082191 | 108.45 | 1122.5 | 1014.05
10839 | 2.9229 | 140.4 | 61.37 | 0.0082211 | 108.46 | 1122.5 |  | 10839 | 140.4 | 2.9229 | 61.37 | 0.0082211 | 108.46 | 1122.5 | 1014.04
10840 | 2.9236 | 140.41 | 61.369 | 0.0082231 | 108.47 | 1122.5 |  | 10840 | 140.41 | 2.9236 | 61.369 | 0.0082231 | 108.47 | 1122.5 | 1014.03
10841 | 2.9244 | 140.42 | 61.369 | 0.0082251 | 108.48 | 1122.5 |  | 10841 | 140.42 | 2.9244 | 61.369 | 0.0082251 | 108.48 | 1122.5 | 1014.02
10842 | 2.9251 | 140.43 | 61.369 | 0.008227 | 108.49 | 1122.5 |  | 10842 | 140.43 | 2.9251 | 61.369 | 0.008227 | 108.49 | 1122.5 | 1014.01
10843 | 2.9259 | 140.44 | 61.369 | 0.008229 | 108.5 | 1122.5 |  | 10843 | 140.44 | 2.9259 | 61.369 | 0.008229 | 108.5 | 1122.5 | 1014
10844 | 2.9266 | 140.45 | 61.369 | 0.008231 | 108.51 | 1122.5 |  | 10844 | 140.45 | 2.9266 | 61.369 | 0.008231 | 108.51 | 1122.5 | 1013.99
10845 | 2.9274 | 140.46 | 61.368 | 0.008233 | 108.52 | 1122.5 |  | 10845 | 140.46 | 2.9274 | 61.368 | 0.008233 | 108.52 | 1122.5 | 1013.98
10846 | 2.9281 | 140.47 | 61.368 | 0.008235 | 108.53 | 1122.5 |  | 10846 | 140.47 | 2.9281 | 61.368 | 0.008235 | 108.53 | 1122.5 | 1013.97
10847 | 2.9289 | 140.48 | 61.368 | 0.008237 | 108.54 | 1122.5 |  | 10847 | 140.48 | 2.9289 | 61.368 | 0.008237 | 108.54 | 1122.5 | 1013.96
10848 | 2.9296 | 140.49 | 61.368 | 0.0082389 | 108.55 | 1122.6 |  | 10848 | 140.49 | 2.9296 | 61.368 | 0.0082389 | 108.55 | 1122.6 | 1014.05
10849 | 2.9304 | 140.5 | 61.368 | 0.0082409 | 108.56 | 1122.6 |  | 10849 | 140.5 | 2.9304 | 61.368 | 0.0082409 | 108.56 | 1122.6 | 1014.04
10850 | 2.9311 | 140.51 | 61.368 | 0.0082429 | 108.57 | 1122.6 |  | 10850 | 140.51 | 2.9311 | 61.368 | 0.0082429 | 108.57 | 1122.6 | 1014.03
10851 | 2.9319 | 140.52 | 61.367 | 0.0082449 | 108.58 | 1122.6 |  | 10851 | 140.52 | 2.9319 | 61.367 | 0.0082449 | 108.58 | 1122.6 | 1014.02
10852 | 2.9326 | 140.53 | 61.367 | 0.0082469 | 108.59 | 1122.6 |  | 10852 | 140.53 | 2.9326 | 61.367 | 0.0082469 | 108.59 | 1122.6 | 1014.01
10853 | 2.9334 | 140.54 | 61.367 | 0.0082489 | 108.6 | 1122.6 |  | 10853 | 140.54 | 2.9334 | 61.367 | 0.0082489 | 108.6 | 1122.6 | 1014
10854 | 2.9341 | 140.55 | 61.367 | 0.0082509 | 108.61 | 1122.6 |  | 10854 | 140.55 | 2.9341 | 61.367 | 0.0082509 | 108.61 | 1122.6 | 1013.99
10855 | 2.9349 | 140.56 | 61.367 | 0.0082528 | 108.62 | 1122.6 |  | 10855 | 140.56 | 2.9349 | 61.367 | 0.0082528 | 108.62 | 1122.6 | 1013.98
10856 | 2.9356 | 140.57 | 61.367 | 0.0082548 | 108.63 | 1122.6 |  | 10856 | 140.57 | 2.9356 | 61.367 | 0.0082548 | 108.63 | 1122.6 | 1013.97
10857 | 2.9364 | 140.58 | 61.366 | 0.0082568 | 108.64 | 1122.6 |  | 10857 | 140.58 | 2.9364 | 61.366 | 0.0082568 | 108.64 | 1122.6 | 1013.96
10858 | 2.9372 | 140.59 | 61.366 | 0.0082588 | 108.65 | 1122.6 |  | 10858 | 140.59 | 2.9372 | 61.366 | 0.0082588 | 108.65 | 1122.6 | 1013.95
10859 | 2.9379 | 140.6 | 61.366 | 0.0082608 | 108.66 | 1122.6 |  | 10859 | 140.6 | 2.9379 | 61.366 | 0.0082608 | 108.66 | 1122.6 | 1013.94
10860 | 2.9387 | 140.61 | 61.366 | 0.0082628 | 108.67 | 1122.6 |  | 10860 | 140.61 | 2.9387 | 61.366 | 0.0082628 | 108.67 | 1122.6 | 1013.93
10861 | 2.9394 | 140.62 | 61.366 | 0.0082648 | 108.68 | 1122.6 |  | 10861 | 140.62 | 2.9394 | 61.366 | 0.0082648 | 108.68 | 1122.6 | 1013.92
10862 | 2.9402 | 140.63 | 61.365 | 0.0082668 | 108.69 | 1122.6 |  | 10862 | 140.63 | 2.9402 | 61.365 | 0.0082668 | 108.69 | 1122.6 | 1013.91
10863 | 2.9409 | 140.64 | 61.365 | 0.0082688 | 108.7 | 1122.6 |  | 10863 | 140.64 | 2.9409 | 61.365 | 0.0082688 | 108.7 | 1122.6 | 1013.9
10864 | 2.9417 | 140.65 | 61.365 | 0.0082707 | 108.71 | 1122.6 |  | 10864 | 140.65 | 2.9417 | 61.365 | 0.0082707 | 108.71 | 1122.6 | 1013.89
10865 | 2.9424 | 140.66 | 61.365 | 0.0082727 | 108.72 | 1122.6 |  | 10865 | 140.66 | 2.9424 | 61.365 | 0.0082727 | 108.72 | 1122.6 | 1013.88
10866 | 2.9432 | 140.67 | 61.365 | 0.0082747 | 108.73 | 1122.6 |  | 10866 | 140.67 | 2.9432 | 61.365 | 0.0082747 | 108.73 | 1122.6 | 1013.87
10867 | 2.9439 | 140.68 | 61.365 | 0.0082767 | 108.74 | 1122.6 |  | 10867 | 140.68 | 2.9439 | 61.365 | 0.0082767 | 108.74 | 1122.6 | 1013.86
10868 | 2.9447 | 140.69 | 61.364 | 0.0082787 | 108.75 | 1122.6 |  | 10868 | 140.69 | 2.9447 | 61.364 | 0.0082787 | 108.75 | 1122.6 | 1013.85
10869 | 2.9455 | 140.7 | 61.364 | 0.0082807 | 108.76 | 1122.6 |  | 10869 | 140.7 | 2.9455 | 61.364 | 0.0082807 | 108.76 | 1122.6 | 1013.84
10870 | 2.9462 | 140.71 | 61.364 | 0.0082827 | 108.77 | 1122.6 |  | 10870 | 140.71 | 2.9462 | 61.364 | 0.0082827 | 108.77 | 1122.6 | 1013.83
10871 | 2.947 | 140.72 | 61.364 | 0.0082847 | 108.78 | 1122.6 |  | 10871 | 140.72 | 2.947 | 61.364 | 0.0082847 | 108.78 | 1122.6 | 1013.82
10872 | 2.9477 | 140.73 | 61.364 | 0.0082867 | 108.79 | 1122.7 |  | 10872 | 140.73 | 2.9477 | 61.364 | 0.0082867 | 108.79 | 1122.7 | 1013.91
10873 | 2.9485 | 140.74 | 61.363 | 0.0082887 | 108.8 | 1122.7 |  | 10873 | 140.74 | 2.9485 | 61.363 | 0.0082887 | 108.8 | 1122.7 | 1013.9
10874 | 2.9492 | 140.75 | 61.363 | 0.0082907 | 108.81 | 1122.7 |  | 10874 | 140.75 | 2.9492 | 61.363 | 0.0082907 | 108.81 | 1122.7 | 1013.89
10875 | 2.95 | 140.76 | 61.363 | 0.0082927 | 108.82 | 1122.7 |  | 10875 | 140.76 | 2.95 | 61.363 | 0.0082927 | 108.82 | 1122.7 | 1013.88
10876 | 2.9507 | 140.77 | 61.363 | 0.0082947 | 108.83 | 1122.7 |  | 10876 | 140.77 | 2.9507 | 61.363 | 0.0082947 | 108.83 | 1122.7 | 1013.87
10877 | 2.9515 | 140.78 | 61.363 | 0.0082967 | 108.84 | 1122.7 |  | 10877 | 140.78 | 2.9515 | 61.363 | 0.0082967 | 108.84 | 1122.7 | 1013.86
10878 | 2.9523 | 140.79 | 61.363 | 0.0082987 | 108.85 | 1122.7 |  | 10878 | 140.79 | 2.9523 | 61.363 | 0.0082987 | 108.85 | 1122.7 | 1013.85
10879 | 2.953 | 140.8 | 61.362 | 0.0083007 | 108.86 | 1122.7 |  | 10879 | 140.8 | 2.953 | 61.362 | 0.0083007 | 108.86 | 1122.7 | 1013.84
10880 | 2.9538 | 140.81 | 61.362 | 0.0083027 | 108.87 | 1122.7 |  | 10880 | 140.81 | 2.9538 | 61.362 | 0.0083027 | 108.87 | 1122.7 | 1013.83
10881 | 2.9545 | 140.82 | 61.362 | 0.0083047 | 108.88 | 1122.7 |  | 10881 | 140.82 | 2.9545 | 61.362 | 0.0083047 | 108.88 | 1122.7 | 1013.82
10882 | 2.9553 | 140.83 | 61.362 | 0.0083066 | 108.89 | 1122.7 |  | 10882 | 140.83 | 2.9553 | 61.362 | 0.0083066 | 108.89 | 1122.7 | 1013.81
10883 | 2.956 | 140.84 | 61.362 | 0.0083086 | 108.9 | 1122.7 |  | 10883 | 140.84 | 2.956 | 61.362 | 0.0083086 | 108.9 | 1122.7 | 1013.8
10884 | 2.9568 | 140.85 | 61.361 | 0.0083106 | 108.91 | 1122.7 |  | 10884 | 140.85 | 2.9568 | 61.361 | 0.0083106 | 108.91 | 1122.7 | 1013.79
10885 | 2.9576 | 140.86 | 61.361 | 0.0083126 | 108.92 | 1122.7 |  | 10885 | 140.86 | 2.9576 | 61.361 | 0.0083126 | 108.92 | 1122.7 | 1013.78
10886 | 2.9583 | 140.87 | 61.361 | 0.0083146 | 108.93 | 1122.7 |  | 10886 | 140.87 | 2.9583 | 61.361 | 0.0083146 | 108.93 | 1122.7 | 1013.77
10887 | 2.9591 | 140.88 | 61.361 | 0.0083166 | 108.94 | 1122.7 |  | 10887 | 140.88 | 2.9591 | 61.361 | 0.0083166 | 108.94 | 1122.7 | 1013.76
10888 | 2.9598 | 140.89 | 61.361 | 0.0083186 | 108.95 | 1122.7 |  | 10888 | 140.89 | 2.9598 | 61.361 | 0.0083186 | 108.95 | 1122.7 | 1013.75
10889 | 2.9606 | 140.9 | 61.361 | 0.0083206 | 108.96 | 1122.7 |  | 10889 | 140.9 | 2.9606 | 61.361 | 0.0083206 | 108.96 | 1122.7 | 1013.74
10890 | 2.9614 | 140.91 | 61.36 | 0.0083226 | 108.97 | 1122.7 |  | 10890 | 140.91 | 2.9614 | 61.36 | 0.0083226 | 108.97 | 1122.7 | 1013.73
10891 | 2.9621 | 140.92 | 61.36 | 0.0083246 | 108.98 | 1122.7 |  | 10891 | 140.92 | 2.9621 | 61.36 | 0.0083246 | 108.98 | 1122.7 | 1013.72
10892 | 2.9629 | 140.93 | 61.36 | 0.0083267 | 108.99 | 1122.7 |  | 10892 | 140.93 | 2.9629 | 61.36 | 0.0083267 | 108.99 | 1122.7 | 1013.71
10893 | 2.9636 | 140.94 | 61.36 | 0.0083287 | 109 | 1122.7 |  | 10893 | 140.94 | 2.9636 | 61.36 | 0.0083287 | 109 | 1122.7 | 1013.7
10894 | 2.9644 | 140.95 | 61.36 | 0.0083307 | 109.01 | 1122.7 |  | 10894 | 140.95 | 2.9644 | 61.36 | 0.0083307 | 109.01 | 1122.7 | 1013.69
10895 | 2.9651 | 140.96 | 61.36 | 0.0083327 | 109.02 | 1122.7 |  | 10895 | 140.96 | 2.9651 | 61.36 | 0.0083327 | 109.02 | 1122.7 | 1013.68
10896 | 2.9659 | 140.97 | 61.359 | 0.0083347 | 109.03 | 1122.8 |  | 10896 | 140.97 | 2.9659 | 61.359 | 0.0083347 | 109.03 | 1122.8 | 1013.77
10897 | 2.9667 | 140.98 | 61.359 | 0.0083367 | 109.04 | 1122.8 |  | 10897 | 140.98 | 2.9667 | 61.359 | 0.0083367 | 109.04 | 1122.8 | 1013.76
10898 | 2.9674 | 140.99 | 61.359 | 0.0083387 | 109.05 | 1122.8 |  | 10898 | 140.99 | 2.9674 | 61.359 | 0.0083387 | 109.05 | 1122.8 | 1013.75
10899 | 2.9682 | 141 | 61.359 | 0.0083407 | 109.06 | 1122.8 |  | 10899 | 141 | 2.9682 | 61.359 | 0.0083407 | 109.06 | 1122.8 | 1013.74
10900 | 2.9689 | 141.01 | 61.359 | 0.0083427 | 109.07 | 1122.8 |  | 10900 | 141.01 | 2.9689 | 61.359 | 0.0083427 | 109.07 | 1122.8 | 1013.73
10901 | 2.9697 | 141.02 | 61.358 | 0.0083447 | 109.08 | 1122.8 |  | 10901 | 141.02 | 2.9697 | 61.358 | 0.0083447 | 109.08 | 1122.8 | 1013.72
10902 | 2.9705 | 141.03 | 61.358 | 0.0083467 | 109.09 | 1122.8 |  | 10902 | 141.03 | 2.9705 | 61.358 | 0.0083467 | 109.09 | 1122.8 | 1013.71
10903 | 2.9712 | 141.04 | 61.358 | 0.0083487 | 109.1 | 1122.8 |  | 10903 | 141.04 | 2.9712 | 61.358 | 0.0083487 | 109.1 | 1122.8 | 1013.7
10904 | 2.972 | 141.05 | 61.358 | 0.0083507 | 109.11 | 1122.8 |  | 10904 | 141.05 | 2.972 | 61.358 | 0.0083507 | 109.11 | 1122.8 | 1013.69
10905 | 2.9728 | 141.06 | 61.358 | 0.0083527 | 109.12 | 1122.8 |  | 10905 | 141.06 | 2.9728 | 61.358 | 0.0083527 | 109.12 | 1122.8 | 1013.68
10906 | 2.9735 | 141.07 | 61.358 | 0.0083547 | 109.13 | 1122.8 |  | 10906 | 141.07 | 2.9735 | 61.358 | 0.0083547 | 109.13 | 1122.8 | 1013.67
10907 | 2.9743 | 141.08 | 61.357 | 0.0083567 | 109.14 | 1122.8 |  | 10907 | 141.08 | 2.9743 | 61.357 | 0.0083567 | 109.14 | 1122.8 | 1013.66
10908 | 2.975 | 141.09 | 61.357 | 0.0083587 | 109.15 | 1122.8 |  | 10908 | 141.09 | 2.975 | 61.357 | 0.0083587 | 109.15 | 1122.8 | 1013.65
10909 | 2.9758 | 141.1 | 61.357 | 0.0083607 | 109.16 | 1122.8 |  | 10909 | 141.1 | 2.9758 | 61.357 | 0.0083607 | 109.16 | 1122.8 | 1013.64
10910 | 2.9766 | 141.11 | 61.357 | 0.0083628 | 109.17 | 1122.8 |  | 10910 | 141.11 | 2.9766 | 61.357 | 0.0083628 | 109.17 | 1122.8 | 1013.63
10911 | 2.9773 | 141.12 | 61.357 | 0.0083648 | 109.18 | 1122.8 |  | 10911 | 141.12 | 2.9773 | 61.357 | 0.0083648 | 109.18 | 1122.8 | 1013.62
10912 | 2.9781 | 141.13 | 61.356 | 0.0083668 | 109.19 | 1122.8 |  | 10912 | 141.13 | 2.9781 | 61.356 | 0.0083668 | 109.19 | 1122.8 | 1013.61
10913 | 2.9788 | 141.14 | 61.356 | 0.0083688 | 109.2 | 1122.8 |  | 10913 | 141.14 | 2.9788 | 61.356 | 0.0083688 | 109.2 | 1122.8 | 1013.6
10914 | 2.9796 | 141.15 | 61.356 | 0.0083708 | 109.21 | 1122.8 |  | 10914 | 141.15 | 2.9796 | 61.356 | 0.0083708 | 109.21 | 1122.8 | 1013.59
10915 | 2.9804 | 141.16 | 61.356 | 0.0083728 | 109.22 | 1122.8 |  | 10915 | 141.16 | 2.9804 | 61.356 | 0.0083728 | 109.22 | 1122.8 | 1013.58
10916 | 2.9811 | 141.17 | 61.356 | 0.0083748 | 109.23 | 1122.8 |  | 10916 | 141.17 | 2.9811 | 61.356 | 0.0083748 | 109.23 | 1122.8 | 1013.57
10917 | 2.9819 | 141.18 | 61.356 | 0.0083768 | 109.24 | 1122.8 |  | 10917 | 141.18 | 2.9819 | 61.356 | 0.0083768 | 109.24 | 1122.8 | 1013.56
10918 | 2.9827 | 141.19 | 61.355 | 0.0083788 | 109.25 | 1122.8 |  | 10918 | 141.19 | 2.9827 | 61.355 | 0.0083788 | 109.25 | 1122.8 | 1013.55
10919 | 2.9834 | 141.2 | 61.355 | 0.0083809 | 109.26 | 1122.8 |  | 10919 | 141.2 | 2.9834 | 61.355 | 0.0083809 | 109.26 | 1122.8 | 1013.54
10920 | 2.9842 | 141.21 | 61.355 | 0.0083829 | 109.27 | 1122.9 |  | 10920 | 141.21 | 2.9842 | 61.355 | 0.0083829 | 109.27 | 1122.9 | 1013.63
10921 | 2.985 | 141.22 | 61.355 | 0.0083849 | 109.28 | 1122.9 |  | 10921 | 141.22 | 2.985 | 61.355 | 0.0083849 | 109.28 | 1122.9 | 1013.62
10922 | 2.9857 | 141.23 | 61.355 | 0.0083869 | 109.29 | 1122.9 |  | 10922 | 141.23 | 2.9857 | 61.355 | 0.0083869 | 109.29 | 1122.9 | 1013.61
10923 | 2.9865 | 141.24 | 61.354 | 0.0083889 | 109.3 | 1122.9 |  | 10923 | 141.24 | 2.9865 | 61.354 | 0.0083889 | 109.3 | 1122.9 | 1013.6
10924 | 2.9872 | 141.25 | 61.354 | 0.0083909 | 109.31 | 1122.9 |  | 10924 | 141.25 | 2.9872 | 61.354 | 0.0083909 | 109.31 | 1122.9 | 1013.59
10925 | 2.988 | 141.26 | 61.354 | 0.0083929 | 109.32 | 1122.9 |  | 10925 | 141.26 | 2.988 | 61.354 | 0.0083929 | 109.32 | 1122.9 | 1013.58
10926 | 2.9888 | 141.27 | 61.354 | 0.008395 | 109.33 | 1122.9 |  | 10926 | 141.27 | 2.9888 | 61.354 | 0.008395 | 109.33 | 1122.9 | 1013.57
10927 | 2.9895 | 141.28 | 61.354 | 0.008397 | 109.34 | 1122.9 |  | 10927 | 141.28 | 2.9895 | 61.354 | 0.008397 | 109.34 | 1122.9 | 1013.56
10928 | 2.9903 | 141.29 | 61.354 | 0.008399 | 109.35 | 1122.9 |  | 10928 | 141.29 | 2.9903 | 61.354 | 0.008399 | 109.35 | 1122.9 | 1013.55
10929 | 2.9911 | 141.3 | 61.353 | 0.008401 | 109.36 | 1122.9 |  | 10929 | 141.3 | 2.9911 | 61.353 | 0.008401 | 109.36 | 1122.9 | 1013.54
10930 | 2.9918 | 141.31 | 61.353 | 0.008403 | 109.37 | 1122.9 |  | 10930 | 141.31 | 2.9918 | 61.353 | 0.008403 | 109.37 | 1122.9 | 1013.53
10931 | 2.9926 | 141.32 | 61.353 | 0.008405 | 109.38 | 1122.9 |  | 10931 | 141.32 | 2.9926 | 61.353 | 0.008405 | 109.38 | 1122.9 | 1013.52
10932 | 2.9934 | 141.33 | 61.353 | 0.0084071 | 109.39 | 1122.9 |  | 10932 | 141.33 | 2.9934 | 61.353 | 0.0084071 | 109.39 | 1122.9 | 1013.51
10933 | 2.9941 | 141.34 | 61.353 | 0.0084091 | 109.4 | 1122.9 |  | 10933 | 141.34 | 2.9941 | 61.353 | 0.0084091 | 109.4 | 1122.9 | 1013.5
10934 | 2.9949 | 141.35 | 61.353 | 0.0084111 | 109.41 | 1122.9 |  | 10934 | 141.35 | 2.9949 | 61.353 | 0.0084111 | 109.41 | 1122.9 | 1013.49
10935 | 2.9957 | 141.36 | 61.352 | 0.0084131 | 109.42 | 1122.9 |  | 10935 | 141.36 | 2.9957 | 61.352 | 0.0084131 | 109.42 | 1122.9 | 1013.48
10936 | 2.9964 | 141.37 | 61.352 | 0.0084151 | 109.43 | 1122.9 |  | 10936 | 141.37 | 2.9964 | 61.352 | 0.0084151 | 109.43 | 1122.9 | 1013.47
10937 | 2.9972 | 141.38 | 61.352 | 0.0084172 | 109.44 | 1122.9 |  | 10937 | 141.38 | 2.9972 | 61.352 | 0.0084172 | 109.44 | 1122.9 | 1013.46
10938 | 2.998 | 141.39 | 61.352 | 0.0084192 | 109.45 | 1122.9 |  | 10938 | 141.39 | 2.998 | 61.352 | 0.0084192 | 109.45 | 1122.9 | 1013.45
10939 | 2.9987 | 141.4 | 61.352 | 0.0084212 | 109.46 | 1122.9 |  | 10939 | 141.4 | 2.9987 | 61.352 | 0.0084212 | 109.46 | 1122.9 | 1013.44
10940 | 2.9995 | 141.41 | 61.351 | 0.0084232 | 109.47 | 1122.9 |  | 10940 | 141.41 | 2.9995 | 61.351 | 0.0084232 | 109.47 | 1122.9 | 1013.43
10941 | 3.0003 | 141.42 | 61.351 | 0.0084252 | 109.48 | 1122.9 |  | 10941 | 141.42 | 3.0003 | 61.351 | 0.0084252 | 109.48 | 1122.9 | 1013.42
10942 | 3.001 | 141.43 | 61.351 | 0.0084273 | 109.49 | 1122.9 |  | 10942 | 141.43 | 3.001 | 61.351 | 0.0084273 | 109.49 | 1122.9 | 1013.41
10943 | 3.0018 | 141.44 | 61.351 | 0.0084293 | 109.5 | 1122.9 |  | 10943 | 141.44 | 3.0018 | 61.351 | 0.0084293 | 109.5 | 1122.9 | 1013.4
10944 | 3.0026 | 141.45 | 61.351 | 0.0084313 | 109.51 | 1123 |  | 10944 | 141.45 | 3.0026 | 61.351 | 0.0084313 | 109.51 | 1123 | 1013.49
10945 | 3.0033 | 141.46 | 61.351 | 0.0084333 | 109.52 | 1123 |  | 10945 | 141.46 | 3.0033 | 61.351 | 0.0084333 | 109.52 | 1123 | 1013.48
10946 | 3.0041 | 141.47 | 61.35 | 0.0084354 | 109.53 | 1123 |  | 10946 | 141.47 | 3.0041 | 61.35 | 0.0084354 | 109.53 | 1123 | 1013.47
10947 | 3.0049 | 141.48 | 61.35 | 0.0084374 | 109.54 | 1123 |  | 10947 | 141.48 | 3.0049 | 61.35 | 0.0084374 | 109.54 | 1123 | 1013.46
10948 | 3.0056 | 141.49 | 61.35 | 0.0084394 | 109.55 | 1123 |  | 10948 | 141.49 | 3.0056 | 61.35 | 0.0084394 | 109.55 | 1123 | 1013.45
10949 | 3.0064 | 141.5 | 61.35 | 0.0084414 | 109.56 | 1123 |  | 10949 | 141.5 | 3.0064 | 61.35 | 0.0084414 | 109.56 | 1123 | 1013.44
10950 | 3.0072 | 141.51 | 61.35 | 0.0084435 | 109.57 | 1123 |  | 10950 | 141.51 | 3.0072 | 61.35 | 0.0084435 | 109.57 | 1123 | 1013.43
10951 | 3.0079 | 141.52 | 61.349 | 0.0084455 | 109.58 | 1123 |  | 10951 | 141.52 | 3.0079 | 61.349 | 0.0084455 | 109.58 | 1123 | 1013.42
10952 | 3.0087 | 141.53 | 61.349 | 0.0084475 | 109.59 | 1123 |  | 10952 | 141.53 | 3.0087 | 61.349 | 0.0084475 | 109.59 | 1123 | 1013.41
10953 | 3.0095 | 141.54 | 61.349 | 0.0084495 | 109.6 | 1123 |  | 10953 | 141.54 | 3.0095 | 61.349 | 0.0084495 | 109.6 | 1123 | 1013.4
10954 | 3.0103 | 141.55 | 61.349 | 0.0084516 | 109.61 | 1123 |  | 10954 | 141.55 | 3.0103 | 61.349 | 0.0084516 | 109.61 | 1123 | 1013.39
10955 | 3.011 | 141.56 | 61.349 | 0.0084536 | 109.62 | 1123 |  | 10955 | 141.56 | 3.011 | 61.349 | 0.0084536 | 109.62 | 1123 | 1013.38
10956 | 3.0118 | 141.57 | 61.349 | 0.0084556 | 109.63 | 1123 |  | 10956 | 141.57 | 3.0118 | 61.349 | 0.0084556 | 109.63 | 1123 | 1013.37
10957 | 3.0126 | 141.58 | 61.348 | 0.0084576 | 109.64 | 1123 |  | 10957 | 141.58 | 3.0126 | 61.348 | 0.0084576 | 109.64 | 1123 | 1013.36
10958 | 3.0133 | 141.59 | 61.348 | 0.0084597 | 109.65 | 1123 |  | 10958 | 141.59 | 3.0133 | 61.348 | 0.0084597 | 109.65 | 1123 | 1013.35
10959 | 3.0141 | 141.6 | 61.348 | 0.0084617 | 109.66 | 1123 |  | 10959 | 141.6 | 3.0141 | 61.348 | 0.0084617 | 109.66 | 1123 | 1013.34
10960 | 3.0149 | 141.61 | 61.348 | 0.0084637 | 109.67 | 1123 |  | 10960 | 141.61 | 3.0149 | 61.348 | 0.0084637 | 109.67 | 1123 | 1013.33
10961 | 3.0156 | 141.62 | 61.348 | 0.0084658 | 109.68 | 1123 |  | 10961 | 141.62 | 3.0156 | 61.348 | 0.0084658 | 109.68 | 1123 | 1013.32
10962 | 3.0164 | 141.63 | 61.347 | 0.0084678 | 109.69 | 1123 |  | 10962 | 141.63 | 3.0164 | 61.347 | 0.0084678 | 109.69 | 1123 | 1013.31
10963 | 3.0172 | 141.64 | 61.347 | 0.0084698 | 109.7 | 1123 |  | 10963 | 141.64 | 3.0172 | 61.347 | 0.0084698 | 109.7 | 1123 | 1013.3
10964 | 3.018 | 141.65 | 61.347 | 0.0084719 | 109.71 | 1123 |  | 10964 | 141.65 | 3.018 | 61.347 | 0.0084719 | 109.71 | 1123 | 1013.29
10965 | 3.0187 | 141.66 | 61.347 | 0.0084739 | 109.72 | 1123 |  | 10965 | 141.66 | 3.0187 | 61.347 | 0.0084739 | 109.72 | 1123 | 1013.28
10966 | 3.0195 | 141.67 | 61.347 | 0.0084759 | 109.73 | 1123 |  | 10966 | 141.67 | 3.0195 | 61.347 | 0.0084759 | 109.73 | 1123 | 1013.27
10967 | 3.0203 | 141.68 | 61.347 | 0.008478 | 109.74 | 1123 |  | 10967 | 141.68 | 3.0203 | 61.347 | 0.008478 | 109.74 | 1123 | 1013.26
10968 | 3.021 | 141.69 | 61.346 | 0.00848 | 109.75 | 1123.1 |  | 10968 | 141.69 | 3.021 | 61.346 | 0.00848 | 109.75 | 1123.1 | 1013.35
10969 | 3.0218 | 141.7 | 61.346 | 0.008482 | 109.76 | 1123.1 |  | 10969 | 141.7 | 3.0218 | 61.346 | 0.008482 | 109.76 | 1123.1 | 1013.34
10970 | 3.0226 | 141.71 | 61.346 | 0.0084841 | 109.77 | 1123.1 |  | 10970 | 141.71 | 3.0226 | 61.346 | 0.0084841 | 109.77 | 1123.1 | 1013.33
10971 | 3.0234 | 141.72 | 61.346 | 0.0084861 | 109.78 | 1123.1 |  | 10971 | 141.72 | 3.0234 | 61.346 | 0.0084861 | 109.78 | 1123.1 | 1013.32
10972 | 3.0241 | 141.73 | 61.346 | 0.0084881 | 109.79 | 1123.1 |  | 10972 | 141.73 | 3.0241 | 61.346 | 0.0084881 | 109.79 | 1123.1 | 1013.31
10973 | 3.0249 | 141.74 | 61.345 | 0.0084902 | 109.8 | 1123.1 |  | 10973 | 141.74 | 3.0249 | 61.345 | 0.0084902 | 109.8 | 1123.1 | 1013.3
10974 | 3.0257 | 141.75 | 61.345 | 0.0084922 | 109.81 | 1123.1 |  | 10974 | 141.75 | 3.0257 | 61.345 | 0.0084922 | 109.81 | 1123.1 | 1013.29
10975 | 3.0264 | 141.76 | 61.345 | 0.0084942 | 109.82 | 1123.1 |  | 10975 | 141.76 | 3.0264 | 61.345 | 0.0084942 | 109.82 | 1123.1 | 1013.28
10976 | 3.0272 | 141.77 | 61.345 | 0.0084963 | 109.83 | 1123.1 |  | 10976 | 141.77 | 3.0272 | 61.345 | 0.0084963 | 109.83 | 1123.1 | 1013.27
10977 | 3.028 | 141.78 | 61.345 | 0.0084983 | 109.84 | 1123.1 |  | 10977 | 141.78 | 3.028 | 61.345 | 0.0084983 | 109.84 | 1123.1 | 1013.26
10978 | 3.0288 | 141.79 | 61.345 | 0.0085003 | 109.85 | 1123.1 |  | 10978 | 141.79 | 3.0288 | 61.345 | 0.0085003 | 109.85 | 1123.1 | 1013.25
10979 | 3.0295 | 141.8 | 61.344 | 0.0085024 | 109.86 | 1123.1 |  | 10979 | 141.8 | 3.0295 | 61.344 | 0.0085024 | 109.86 | 1123.1 | 1013.24
10980 | 3.0303 | 141.81 | 61.344 | 0.0085044 | 109.87 | 1123.1 |  | 10980 | 141.81 | 3.0303 | 61.344 | 0.0085044 | 109.87 | 1123.1 | 1013.23
10981 | 3.0311 | 141.82 | 61.344 | 0.0085065 | 109.88 | 1123.1 |  | 10981 | 141.82 | 3.0311 | 61.344 | 0.0085065 | 109.88 | 1123.1 | 1013.22
10982 | 3.0319 | 141.83 | 61.344 | 0.0085085 | 109.89 | 1123.1 |  | 10982 | 141.83 | 3.0319 | 61.344 | 0.0085085 | 109.89 | 1123.1 | 1013.21
10983 | 3.0326 | 141.84 | 61.344 | 0.0085105 | 109.9 | 1123.1 |  | 10983 | 141.84 | 3.0326 | 61.344 | 0.0085105 | 109.9 | 1123.1 | 1013.2
10984 | 3.0334 | 141.85 | 61.344 | 0.0085126 | 109.91 | 1123.1 |  | 10984 | 141.85 | 3.0334 | 61.344 | 0.0085126 | 109.91 | 1123.1 | 1013.19
10985 | 3.0342 | 141.86 | 61.343 | 0.0085146 | 109.92 | 1123.1 |  | 10985 | 141.86 | 3.0342 | 61.343 | 0.0085146 | 109.92 | 1123.1 | 1013.18
10986 | 3.035 | 141.87 | 61.343 | 0.0085166 | 109.93 | 1123.1 |  | 10986 | 141.87 | 3.035 | 61.343 | 0.0085166 | 109.93 | 1123.1 | 1013.17
10987 | 3.0357 | 141.88 | 61.343 | 0.0085187 | 109.94 | 1123.1 |  | 10987 | 141.88 | 3.0357 | 61.343 | 0.0085187 | 109.94 | 1123.1 | 1013.16
10988 | 3.0365 | 141.89 | 61.343 | 0.0085207 | 109.95 | 1123.1 |  | 10988 | 141.89 | 3.0365 | 61.343 | 0.0085207 | 109.95 | 1123.1 | 1013.15
10989 | 3.0373 | 141.9 | 61.343 | 0.0085228 | 109.96 | 1123.1 |  | 10989 | 141.9 | 3.0373 | 61.343 | 0.0085228 | 109.96 | 1123.1 | 1013.14
10990 | 3.0381 | 141.91 | 61.342 | 0.0085248 | 109.97 | 1123.1 |  | 10990 | 141.91 | 3.0381 | 61.342 | 0.0085248 | 109.97 | 1123.1 | 1013.13
10991 | 3.0388 | 141.92 | 61.342 | 0.0085269 | 109.98 | 1123.1 |  | 10991 | 141.92 | 3.0388 | 61.342 | 0.0085269 | 109.98 | 1123.1 | 1013.12
10992 | 3.0396 | 141.93 | 61.342 | 0.0085289 | 109.99 | 1123.2 |  | 10992 | 141.93 | 3.0396 | 61.342 | 0.0085289 | 109.99 | 1123.2 | 1013.21
10993 | 3.0404 | 141.94 | 61.342 | 0.0085309 | 110 | 1123.2 |  | 10993 | 141.94 | 3.0404 | 61.342 | 0.0085309 | 110 | 1123.2 | 1013.2
10994 | 3.0412 | 141.95 | 61.342 | 0.008533 | 110.01 | 1123.2 |  | 10994 | 141.95 | 3.0412 | 61.342 | 0.008533 | 110.01 | 1123.2 | 1013.19
10995 | 3.0419 | 141.96 | 61.342 | 0.008535 | 110.02 | 1123.2 |  | 10995 | 141.96 | 3.0419 | 61.342 | 0.008535 | 110.02 | 1123.2 | 1013.18
10996 | 3.0427 | 141.97 | 61.341 | 0.0085371 | 110.03 | 1123.2 |  | 10996 | 141.97 | 3.0427 | 61.341 | 0.0085371 | 110.03 | 1123.2 | 1013.17
10997 | 3.0435 | 141.98 | 61.341 | 0.0085391 | 110.04 | 1123.2 |  | 10997 | 141.98 | 3.0435 | 61.341 | 0.0085391 | 110.04 | 1123.2 | 1013.16
10998 | 3.0443 | 141.99 | 61.341 | 0.0085412 | 110.05 | 1123.2 |  | 10998 | 141.99 | 3.0443 | 61.341 | 0.0085412 | 110.05 | 1123.2 | 1013.15
10999 | 3.045 | 142 | 61.341 | 0.0085432 | 110.06 | 1123.2 |  | 10999 | 142 | 3.045 | 61.341 | 0.0085432 | 110.06 | 1123.2 | 1013.14
11000 | 3.0458 | 142.01 | 61.341 | 0.0085453 | 110.07 | 1123.2 |  | 11000 | 142.01 | 3.0458 | 61.341 | 0.0085453 | 110.07 | 1123.2 | 1013.13
11001 | 3.0466 | 142.02 | 61.34 | 0.0085473 | 110.08 | 1123.2 |  | 11001 | 142.02 | 3.0466 | 61.34 | 0.0085473 | 110.08 | 1123.2 | 1013.12
11002 | 3.0474 | 142.03 | 61.34 | 0.0085493 | 110.09 | 1123.2 |  | 11002 | 142.03 | 3.0474 | 61.34 | 0.0085493 | 110.09 | 1123.2 | 1013.11
11003 | 3.0482 | 142.04 | 61.34 | 0.0085514 | 110.1 | 1123.2 |  | 11003 | 142.04 | 3.0482 | 61.34 | 0.0085514 | 110.1 | 1123.2 | 1013.1
11004 | 3.0489 | 142.05 | 61.34 | 0.0085534 | 110.11 | 1123.2 |  | 11004 | 142.05 | 3.0489 | 61.34 | 0.0085534 | 110.11 | 1123.2 | 1013.09
11005 | 3.0497 | 142.06 | 61.34 | 0.0085555 | 110.12 | 1123.2 |  | 11005 | 142.06 | 3.0497 | 61.34 | 0.0085555 | 110.12 | 1123.2 | 1013.08
11006 | 3.0505 | 142.07 | 61.34 | 0.0085575 | 110.13 | 1123.2 |  | 11006 | 142.07 | 3.0505 | 61.34 | 0.0085575 | 110.13 | 1123.2 | 1013.07
11007 | 3.0513 | 142.08 | 61.339 | 0.0085596 | 110.14 | 1123.2 |  | 11007 | 142.08 | 3.0513 | 61.339 | 0.0085596 | 110.14 | 1123.2 | 1013.06
11008 | 3.052 | 142.09 | 61.339 | 0.0085616 | 110.15 | 1123.2 |  | 11008 | 142.09 | 3.052 | 61.339 | 0.0085616 | 110.15 | 1123.2 | 1013.05
11009 | 3.0528 | 142.1 | 61.339 | 0.0085637 | 110.16 | 1123.2 |  | 11009 | 142.1 | 3.0528 | 61.339 | 0.0085637 | 110.16 | 1123.2 | 1013.04
11010 | 3.0536 | 142.11 | 61.339 | 0.0085657 | 110.17 | 1123.2 |  | 11010 | 142.11 | 3.0536 | 61.339 | 0.0085657 | 110.17 | 1123.2 | 1013.03
11011 | 3.0544 | 142.12 | 61.339 | 0.0085678 | 110.18 | 1123.2 |  | 11011 | 142.12 | 3.0544 | 61.339 | 0.0085678 | 110.18 | 1123.2 | 1013.02
11012 | 3.0552 | 142.13 | 61.338 | 0.0085698 | 110.19 | 1123.2 |  | 11012 | 142.13 | 3.0552 | 61.338 | 0.0085698 | 110.19 | 1123.2 | 1013.01
11013 | 3.0559 | 142.14 | 61.338 | 0.0085719 | 110.2 | 1123.2 |  | 11013 | 142.14 | 3.0559 | 61.338 | 0.0085719 | 110.2 | 1123.2 | 1013
11014 | 3.0567 | 142.15 | 61.338 | 0.0085739 | 110.21 | 1123.2 |  | 11014 | 142.15 | 3.0567 | 61.338 | 0.0085739 | 110.21 | 1123.2 | 1012.99
11015 | 3.0575 | 142.16 | 61.338 | 0.008576 | 110.22 | 1123.2 |  | 11015 | 142.16 | 3.0575 | 61.338 | 0.008576 | 110.22 | 1123.2 | 1012.98
11016 | 3.0583 | 142.17 | 61.338 | 0.008578 | 110.23 | 1123.2 |  | 11016 | 142.17 | 3.0583 | 61.338 | 0.008578 | 110.23 | 1123.2 | 1012.97
11017 | 3.0591 | 142.18 | 61.338 | 0.0085801 | 110.24 | 1123.3 |  | 11017 | 142.18 | 3.0591 | 61.338 | 0.0085801 | 110.24 | 1123.3 | 1013.06
11018 | 3.0598 | 142.19 | 61.337 | 0.0085822 | 110.25 | 1123.3 |  | 11018 | 142.19 | 3.0598 | 61.337 | 0.0085822 | 110.25 | 1123.3 | 1013.05
11019 | 3.0606 | 142.2 | 61.337 | 0.0085842 | 110.26 | 1123.3 |  | 11019 | 142.2 | 3.0606 | 61.337 | 0.0085842 | 110.26 | 1123.3 | 1013.04
11020 | 3.0614 | 142.21 | 61.337 | 0.0085863 | 110.27 | 1123.3 |  | 11020 | 142.21 | 3.0614 | 61.337 | 0.0085863 | 110.27 | 1123.3 | 1013.03
11021 | 3.0622 | 142.22 | 61.337 | 0.0085883 | 110.28 | 1123.3 |  | 11021 | 142.22 | 3.0622 | 61.337 | 0.0085883 | 110.28 | 1123.3 | 1013.02
11022 | 3.063 | 142.23 | 61.337 | 0.0085904 | 110.29 | 1123.3 |  | 11022 | 142.23 | 3.063 | 61.337 | 0.0085904 | 110.29 | 1123.3 | 1013.01
11023 | 3.0637 | 142.24 | 61.336 | 0.0085924 | 110.3 | 1123.3 |  | 11023 | 142.24 | 3.0637 | 61.336 | 0.0085924 | 110.3 | 1123.3 | 1013
11024 | 3.0645 | 142.25 | 61.336 | 0.0085945 | 110.31 | 1123.3 |  | 11024 | 142.25 | 3.0645 | 61.336 | 0.0085945 | 110.31 | 1123.3 | 1012.99
11025 | 3.0653 | 142.26 | 61.336 | 0.0085965 | 110.32 | 1123.3 |  | 11025 | 142.26 | 3.0653 | 61.336 | 0.0085965 | 110.32 | 1123.3 | 1012.98
11026 | 3.0661 | 142.27 | 61.336 | 0.0085986 | 110.33 | 1123.3 |  | 11026 | 142.27 | 3.0661 | 61.336 | 0.0085986 | 110.33 | 1123.3 | 1012.97
11027 | 3.0669 | 142.28 | 61.336 | 0.0086007 | 110.34 | 1123.3 |  | 11027 | 142.28 | 3.0669 | 61.336 | 0.0086007 | 110.34 | 1123.3 | 1012.96
11028 | 3.0676 | 142.29 | 61.336 | 0.0086027 | 110.35 | 1123.3 |  | 11028 | 142.29 | 3.0676 | 61.336 | 0.0086027 | 110.35 | 1123.3 | 1012.95
11029 | 3.0684 | 142.3 | 61.335 | 0.0086048 | 110.36 | 1123.3 |  | 11029 | 142.3 | 3.0684 | 61.335 | 0.0086048 | 110.36 | 1123.3 | 1012.94
11030 | 3.0692 | 142.31 | 61.335 | 0.0086068 | 110.37 | 1123.3 |  | 11030 | 142.31 | 3.0692 | 61.335 | 0.0086068 | 110.37 | 1123.3 | 1012.93
11031 | 3.07 | 142.32 | 61.335 | 0.0086089 | 110.38 | 1123.3 |  | 11031 | 142.32 | 3.07 | 61.335 | 0.0086089 | 110.38 | 1123.3 | 1012.92
11032 | 3.0708 | 142.33 | 61.335 | 0.0086109 | 110.39 | 1123.3 |  | 11032 | 142.33 | 3.0708 | 61.335 | 0.0086109 | 110.39 | 1123.3 | 1012.91
11033 | 3.0716 | 142.34 | 61.335 | 0.008613 | 110.4 | 1123.3 |  | 11033 | 142.34 | 3.0716 | 61.335 | 0.008613 | 110.4 | 1123.3 | 1012.9
11034 | 3.0723 | 142.35 | 61.334 | 0.0086151 | 110.41 | 1123.3 |  | 11034 | 142.35 | 3.0723 | 61.334 | 0.0086151 | 110.41 | 1123.3 | 1012.89
11035 | 3.0731 | 142.36 | 61.334 | 0.0086171 | 110.42 | 1123.3 |  | 11035 | 142.36 | 3.0731 | 61.334 | 0.0086171 | 110.42 | 1123.3 | 1012.88
11036 | 3.0739 | 142.37 | 61.334 | 0.0086192 | 110.43 | 1123.3 |  | 11036 | 142.37 | 3.0739 | 61.334 | 0.0086192 | 110.43 | 1123.3 | 1012.87
11037 | 3.0747 | 142.38 | 61.334 | 0.0086212 | 110.44 | 1123.3 |  | 11037 | 142.38 | 3.0747 | 61.334 | 0.0086212 | 110.44 | 1123.3 | 1012.86
11038 | 3.0755 | 142.39 | 61.334 | 0.0086233 | 110.45 | 1123.3 |  | 11038 | 142.39 | 3.0755 | 61.334 | 0.0086233 | 110.45 | 1123.3 | 1012.85
11039 | 3.0763 | 142.4 | 61.334 | 0.0086254 | 110.46 | 1123.3 |  | 11039 | 142.4 | 3.0763 | 61.334 | 0.0086254 | 110.46 | 1123.3 | 1012.84
11040 | 3.077 | 142.41 | 61.333 | 0.0086274 | 110.47 | 1123.3 |  | 11040 | 142.41 | 3.077 | 61.333 | 0.0086274 | 110.47 | 1123.3 | 1012.83
11041 | 3.0778 | 142.42 | 61.333 | 0.0086295 | 110.48 | 1123.4 |  | 11041 | 142.42 | 3.0778 | 61.333 | 0.0086295 | 110.48 | 1123.4 | 1012.92
11042 | 3.0786 | 142.43 | 61.333 | 0.0086316 | 110.49 | 1123.4 |  | 11042 | 142.43 | 3.0786 | 61.333 | 0.0086316 | 110.49 | 1123.4 | 1012.91
11043 | 3.0794 | 142.44 | 61.333 | 0.0086336 | 110.5 | 1123.4 |  | 11043 | 142.44 | 3.0794 | 61.333 | 0.0086336 | 110.5 | 1123.4 | 1012.9
11044 | 3.0802 | 142.45 | 61.333 | 0.0086357 | 110.51 | 1123.4 |  | 11044 | 142.45 | 3.0802 | 61.333 | 0.0086357 | 110.51 | 1123.4 | 1012.89
11045 | 3.081 | 142.46 | 61.332 | 0.0086377 | 110.52 | 1123.4 |  | 11045 | 142.46 | 3.081 | 61.332 | 0.0086377 | 110.52 | 1123.4 | 1012.88
11046 | 3.0817 | 142.47 | 61.332 | 0.0086398 | 110.53 | 1123.4 |  | 11046 | 142.47 | 3.0817 | 61.332 | 0.0086398 | 110.53 | 1123.4 | 1012.87
11047 | 3.0825 | 142.48 | 61.332 | 0.0086419 | 110.54 | 1123.4 |  | 11047 | 142.48 | 3.0825 | 61.332 | 0.0086419 | 110.54 | 1123.4 | 1012.86
11048 | 3.0833 | 142.49 | 61.332 | 0.0086439 | 110.55 | 1123.4 |  | 11048 | 142.49 | 3.0833 | 61.332 | 0.0086439 | 110.55 | 1123.4 | 1012.85
11049 | 3.0841 | 142.5 | 61.332 | 0.008646 | 110.56 | 1123.4 |  | 11049 | 142.5 | 3.0841 | 61.332 | 0.008646 | 110.56 | 1123.4 | 1012.84
11050 | 3.0849 | 142.51 | 61.332 | 0.0086481 | 110.57 | 1123.4 |  | 11050 | 142.51 | 3.0849 | 61.332 | 0.0086481 | 110.57 | 1123.4 | 1012.83
11051 | 3.0857 | 142.52 | 61.331 | 0.0086501 | 110.58 | 1123.4 |  | 11051 | 142.52 | 3.0857 | 61.331 | 0.0086501 | 110.58 | 1123.4 | 1012.82
11052 | 3.0865 | 142.53 | 61.331 | 0.0086522 | 110.59 | 1123.4 |  | 11052 | 142.53 | 3.0865 | 61.331 | 0.0086522 | 110.59 | 1123.4 | 1012.81
11053 | 3.0872 | 142.54 | 61.331 | 0.0086543 | 110.6 | 1123.4 |  | 11053 | 142.54 | 3.0872 | 61.331 | 0.0086543 | 110.6 | 1123.4 | 1012.8
11054 | 3.088 | 142.55 | 61.331 | 0.0086563 | 110.61 | 1123.4 |  | 11054 | 142.55 | 3.088 | 61.331 | 0.0086563 | 110.61 | 1123.4 | 1012.79
11055 | 3.0888 | 142.56 | 61.331 | 0.0086584 | 110.62 | 1123.4 |  | 11055 | 142.56 | 3.0888 | 61.331 | 0.0086584 | 110.62 | 1123.4 | 1012.78
11056 | 3.0896 | 142.57 | 61.33 | 0.0086605 | 110.63 | 1123.4 |  | 11056 | 142.57 | 3.0896 | 61.33 | 0.0086605 | 110.63 | 1123.4 | 1012.77
11057 | 3.0904 | 142.58 | 61.33 | 0.0086626 | 110.64 | 1123.4 |  | 11057 | 142.58 | 3.0904 | 61.33 | 0.0086626 | 110.64 | 1123.4 | 1012.76
11058 | 3.0912 | 142.59 | 61.33 | 0.0086646 | 110.65 | 1123.4 |  | 11058 | 142.59 | 3.0912 | 61.33 | 0.0086646 | 110.65 | 1123.4 | 1012.75
11059 | 3.092 | 142.6 | 61.33 | 0.0086667 | 110.66 | 1123.4 |  | 11059 | 142.6 | 3.092 | 61.33 | 0.0086667 | 110.66 | 1123.4 | 1012.74
11060 | 3.0928 | 142.61 | 61.33 | 0.0086688 | 110.67 | 1123.4 |  | 11060 | 142.61 | 3.0928 | 61.33 | 0.0086688 | 110.67 | 1123.4 | 1012.73
11061 | 3.0935 | 142.62 | 61.33 | 0.0086708 | 110.68 | 1123.4 |  | 11061 | 142.62 | 3.0935 | 61.33 | 0.0086708 | 110.68 | 1123.4 | 1012.72
11062 | 3.0943 | 142.63 | 61.329 | 0.0086729 | 110.69 | 1123.4 |  | 11062 | 142.63 | 3.0943 | 61.329 | 0.0086729 | 110.69 | 1123.4 | 1012.71
11063 | 3.0951 | 142.64 | 61.329 | 0.008675 | 110.7 | 1123.4 |  | 11063 | 142.64 | 3.0951 | 61.329 | 0.008675 | 110.7 | 1123.4 | 1012.7
11064 | 3.0959 | 142.65 | 61.329 | 0.0086771 | 110.71 | 1123.4 |  | 11064 | 142.65 | 3.0959 | 61.329 | 0.0086771 | 110.71 | 1123.4 | 1012.69
11065 | 3.0967 | 142.66 | 61.329 | 0.0086791 | 110.72 | 1123.5 |  | 11065 | 142.66 | 3.0967 | 61.329 | 0.0086791 | 110.72 | 1123.5 | 1012.78
11066 | 3.0975 | 142.67 | 61.329 | 0.0086812 | 110.73 | 1123.5 |  | 11066 | 142.67 | 3.0975 | 61.329 | 0.0086812 | 110.73 | 1123.5 | 1012.77
11067 | 3.0983 | 142.68 | 61.328 | 0.0086833 | 110.74 | 1123.5 |  | 11067 | 142.68 | 3.0983 | 61.328 | 0.0086833 | 110.74 | 1123.5 | 1012.76
11068 | 3.0991 | 142.69 | 61.328 | 0.0086853 | 110.75 | 1123.5 |  | 11068 | 142.69 | 3.0991 | 61.328 | 0.0086853 | 110.75 | 1123.5 | 1012.75
11069 | 3.0998 | 142.7 | 61.328 | 0.0086874 | 110.76 | 1123.5 |  | 11069 | 142.7 | 3.0998 | 61.328 | 0.0086874 | 110.76 | 1123.5 | 1012.74
11070 | 3.1006 | 142.71 | 61.328 | 0.0086895 | 110.77 | 1123.5 |  | 11070 | 142.71 | 3.1006 | 61.328 | 0.0086895 | 110.77 | 1123.5 | 1012.73
11071 | 3.1014 | 142.72 | 61.328 | 0.0086916 | 110.78 | 1123.5 |  | 11071 | 142.72 | 3.1014 | 61.328 | 0.0086916 | 110.78 | 1123.5 | 1012.72
11072 | 3.1022 | 142.73 | 61.328 | 0.0086936 | 110.79 | 1123.5 |  | 11072 | 142.73 | 3.1022 | 61.328 | 0.0086936 | 110.79 | 1123.5 | 1012.71
11073 | 3.103 | 142.74 | 61.327 | 0.0086957 | 110.8 | 1123.5 |  | 11073 | 142.74 | 3.103 | 61.327 | 0.0086957 | 110.8 | 1123.5 | 1012.7
11074 | 3.1038 | 142.75 | 61.327 | 0.0086978 | 110.81 | 1123.5 |  | 11074 | 142.75 | 3.1038 | 61.327 | 0.0086978 | 110.81 | 1123.5 | 1012.69
11075 | 3.1046 | 142.76 | 61.327 | 0.0086999 | 110.82 | 1123.5 |  | 11075 | 142.76 | 3.1046 | 61.327 | 0.0086999 | 110.82 | 1123.5 | 1012.68
11076 | 3.1054 | 142.77 | 61.327 | 0.008702 | 110.83 | 1123.5 |  | 11076 | 142.77 | 3.1054 | 61.327 | 0.008702 | 110.83 | 1123.5 | 1012.67
11077 | 3.1062 | 142.78 | 61.327 | 0.008704 | 110.84 | 1123.5 |  | 11077 | 142.78 | 3.1062 | 61.327 | 0.008704 | 110.84 | 1123.5 | 1012.66
11078 | 3.107 | 142.79 | 61.327 | 0.0087061 | 110.85 | 1123.5 |  | 11078 | 142.79 | 3.107 | 61.327 | 0.0087061 | 110.85 | 1123.5 | 1012.65
11079 | 3.1077 | 142.8 | 61.326 | 0.0087082 | 110.86 | 1123.5 |  | 11079 | 142.8 | 3.1077 | 61.326 | 0.0087082 | 110.86 | 1123.5 | 1012.64
11080 | 3.1085 | 142.81 | 61.326 | 0.0087103 | 110.87 | 1123.5 |  | 11080 | 142.81 | 3.1085 | 61.326 | 0.0087103 | 110.87 | 1123.5 | 1012.63
11081 | 3.1093 | 142.82 | 61.326 | 0.0087123 | 110.88 | 1123.5 |  | 11081 | 142.82 | 3.1093 | 61.326 | 0.0087123 | 110.88 | 1123.5 | 1012.62
11082 | 3.1101 | 142.83 | 61.326 | 0.0087144 | 110.89 | 1123.5 |  | 11082 | 142.83 | 3.1101 | 61.326 | 0.0087144 | 110.89 | 1123.5 | 1012.61
11083 | 3.1109 | 142.84 | 61.326 | 0.0087165 | 110.9 | 1123.5 |  | 11083 | 142.84 | 3.1109 | 61.326 | 0.0087165 | 110.9 | 1123.5 | 1012.6
11084 | 3.1117 | 142.85 | 61.325 | 0.0087186 | 110.91 | 1123.5 |  | 11084 | 142.85 | 3.1117 | 61.325 | 0.0087186 | 110.91 | 1123.5 | 1012.59
11085 | 3.1125 | 142.86 | 61.325 | 0.0087207 | 110.92 | 1123.5 |  | 11085 | 142.86 | 3.1125 | 61.325 | 0.0087207 | 110.92 | 1123.5 | 1012.58
11086 | 3.1133 | 142.87 | 61.325 | 0.0087227 | 110.93 | 1123.5 |  | 11086 | 142.87 | 3.1133 | 61.325 | 0.0087227 | 110.93 | 1123.5 | 1012.57
11087 | 3.1141 | 142.88 | 61.325 | 0.0087248 | 110.94 | 1123.5 |  | 11087 | 142.88 | 3.1141 | 61.325 | 0.0087248 | 110.94 | 1123.5 | 1012.56
11088 | 3.1149 | 142.89 | 61.325 | 0.0087269 | 110.95 | 1123.5 |  | 11088 | 142.89 | 3.1149 | 61.325 | 0.0087269 | 110.95 | 1123.5 | 1012.55
11089 | 3.1157 | 142.9 | 61.325 | 0.008729 | 110.96 | 1123.6 |  | 11089 | 142.9 | 3.1157 | 61.325 | 0.008729 | 110.96 | 1123.6 | 1012.64
11090 | 3.1165 | 142.91 | 61.324 | 0.0087311 | 110.97 | 1123.6 |  | 11090 | 142.91 | 3.1165 | 61.324 | 0.0087311 | 110.97 | 1123.6 | 1012.63
11091 | 3.1172 | 142.92 | 61.324 | 0.0087332 | 110.98 | 1123.6 |  | 11091 | 142.92 | 3.1172 | 61.324 | 0.0087332 | 110.98 | 1123.6 | 1012.62
11092 | 3.118 | 142.93 | 61.324 | 0.0087352 | 110.99 | 1123.6 |  | 11092 | 142.93 | 3.118 | 61.324 | 0.0087352 | 110.99 | 1123.6 | 1012.61
11093 | 3.1188 | 142.94 | 61.324 | 0.0087373 | 111 | 1123.6 |  | 11093 | 142.94 | 3.1188 | 61.324 | 0.0087373 | 111 | 1123.6 | 1012.6
11094 | 3.1196 | 142.95 | 61.324 | 0.0087394 | 111.01 | 1123.6 |  | 11094 | 142.95 | 3.1196 | 61.324 | 0.0087394 | 111.01 | 1123.6 | 1012.59
11095 | 3.1204 | 142.96 | 61.323 | 0.0087415 | 111.02 | 1123.6 |  | 11095 | 142.96 | 3.1204 | 61.323 | 0.0087415 | 111.02 | 1123.6 | 1012.58
11096 | 3.1212 | 142.97 | 61.323 | 0.0087436 | 111.03 | 1123.6 |  | 11096 | 142.97 | 3.1212 | 61.323 | 0.0087436 | 111.03 | 1123.6 | 1012.57
11097 | 3.122 | 142.98 | 61.323 | 0.0087457 | 111.04 | 1123.6 |  | 11097 | 142.98 | 3.122 | 61.323 | 0.0087457 | 111.04 | 1123.6 | 1012.56
11098 | 3.1228 | 142.99 | 61.323 | 0.0087478 | 111.05 | 1123.6 |  | 11098 | 142.99 | 3.1228 | 61.323 | 0.0087478 | 111.05 | 1123.6 | 1012.55
11099 | 3.1236 | 143 | 61.323 | 0.0087498 | 111.06 | 1123.6 |  | 11099 | 143 | 3.1236 | 61.323 | 0.0087498 | 111.06 | 1123.6 | 1012.54
11100 | 3.1244 | 143.01 | 61.323 | 0.0087519 | 111.07 | 1123.6 |  | 11100 | 143.01 | 3.1244 | 61.323 | 0.0087519 | 111.07 | 1123.6 | 1012.53
11101 | 3.1252 | 143.02 | 61.322 | 0.008754 | 111.08 | 1123.6 |  | 11101 | 143.02 | 3.1252 | 61.322 | 0.008754 | 111.08 | 1123.6 | 1012.52
11102 | 3.126 | 143.03 | 61.322 | 0.0087561 | 111.09 | 1123.6 |  | 11102 | 143.03 | 3.126 | 61.322 | 0.0087561 | 111.09 | 1123.6 | 1012.51
11103 | 3.1268 | 143.04 | 61.322 | 0.0087582 | 111.1 | 1123.6 |  | 11103 | 143.04 | 3.1268 | 61.322 | 0.0087582 | 111.1 | 1123.6 | 1012.5
11104 | 3.1276 | 143.05 | 61.322 | 0.0087603 | 111.11 | 1123.6 |  | 11104 | 143.05 | 3.1276 | 61.322 | 0.0087603 | 111.11 | 1123.6 | 1012.49
11105 | 3.1284 | 143.06 | 61.322 | 0.0087624 | 111.12 | 1123.6 |  | 11105 | 143.06 | 3.1284 | 61.322 | 0.0087624 | 111.12 | 1123.6 | 1012.48
11106 | 3.1292 | 143.07 | 61.321 | 0.0087645 | 111.13 | 1123.6 |  | 11106 | 143.07 | 3.1292 | 61.321 | 0.0087645 | 111.13 | 1123.6 | 1012.47
11107 | 3.1299 | 143.08 | 61.321 | 0.0087666 | 111.14 | 1123.6 |  | 11107 | 143.08 | 3.1299 | 61.321 | 0.0087666 | 111.14 | 1123.6 | 1012.46
11108 | 3.1307 | 143.09 | 61.321 | 0.0087686 | 111.15 | 1123.6 |  | 11108 | 143.09 | 3.1307 | 61.321 | 0.0087686 | 111.15 | 1123.6 | 1012.45
11109 | 3.1315 | 143.1 | 61.321 | 0.0087707 | 111.16 | 1123.6 |  | 11109 | 143.1 | 3.1315 | 61.321 | 0.0087707 | 111.16 | 1123.6 | 1012.44
11110 | 3.1323 | 143.11 | 61.321 | 0.0087728 | 111.17 | 1123.6 |  | 11110 | 143.11 | 3.1323 | 61.321 | 0.0087728 | 111.17 | 1123.6 | 1012.43
11111 | 3.1331 | 143.12 | 61.321 | 0.0087749 | 111.18 | 1123.6 |  | 11111 | 143.12 | 3.1331 | 61.321 | 0.0087749 | 111.18 | 1123.6 | 1012.42
11112 | 3.1339 | 143.13 | 61.32 | 0.008777 | 111.19 | 1123.6 |  | 11112 | 143.13 | 3.1339 | 61.32 | 0.008777 | 111.19 | 1123.6 | 1012.41
11113 | 3.1347 | 143.14 | 61.32 | 0.0087791 | 111.2 | 1123.7 |  | 11113 | 143.14 | 3.1347 | 61.32 | 0.0087791 | 111.2 | 1123.7 | 1012.5
11114 | 3.1355 | 143.15 | 61.32 | 0.0087812 | 111.21 | 1123.7 |  | 11114 | 143.15 | 3.1355 | 61.32 | 0.0087812 | 111.21 | 1123.7 | 1012.49
11115 | 3.1363 | 143.16 | 61.32 | 0.0087833 | 111.22 | 1123.7 |  | 11115 | 143.16 | 3.1363 | 61.32 | 0.0087833 | 111.22 | 1123.7 | 1012.48
11116 | 3.1371 | 143.17 | 61.32 | 0.0087854 | 111.23 | 1123.7 |  | 11116 | 143.17 | 3.1371 | 61.32 | 0.0087854 | 111.23 | 1123.7 | 1012.47
11117 | 3.1379 | 143.18 | 61.319 | 0.0087875 | 111.24 | 1123.7 |  | 11117 | 143.18 | 3.1379 | 61.319 | 0.0087875 | 111.24 | 1123.7 | 1012.46
11118 | 3.1387 | 143.19 | 61.319 | 0.0087896 | 111.25 | 1123.7 |  | 11118 | 143.19 | 3.1387 | 61.319 | 0.0087896 | 111.25 | 1123.7 | 1012.45
11119 | 3.1395 | 143.2 | 61.319 | 0.0087917 | 111.26 | 1123.7 |  | 11119 | 143.2 | 3.1395 | 61.319 | 0.0087917 | 111.26 | 1123.7 | 1012.44
11120 | 3.1403 | 143.21 | 61.319 | 0.0087938 | 111.27 | 1123.7 |  | 11120 | 143.21 | 3.1403 | 61.319 | 0.0087938 | 111.27 | 1123.7 | 1012.43
11121 | 3.1411 | 143.22 | 61.319 | 0.0087959 | 111.28 | 1123.7 |  | 11121 | 143.22 | 3.1411 | 61.319 | 0.0087959 | 111.28 | 1123.7 | 1012.42
11122 | 3.1419 | 143.23 | 61.319 | 0.008798 | 111.29 | 1123.7 |  | 11122 | 143.23 | 3.1419 | 61.319 | 0.008798 | 111.29 | 1123.7 | 1012.41
11123 | 3.1427 | 143.24 | 61.318 | 0.0088001 | 111.3 | 1123.7 |  | 11123 | 143.24 | 3.1427 | 61.318 | 0.0088001 | 111.3 | 1123.7 | 1012.4
11124 | 3.1435 | 143.25 | 61.318 | 0.0088022 | 111.31 | 1123.7 |  | 11124 | 143.25 | 3.1435 | 61.318 | 0.0088022 | 111.31 | 1123.7 | 1012.39
11125 | 3.1443 | 143.26 | 61.318 | 0.0088043 | 111.32 | 1123.7 |  | 11125 | 143.26 | 3.1443 | 61.318 | 0.0088043 | 111.32 | 1123.7 | 1012.38
11126 | 3.1451 | 143.27 | 61.318 | 0.0088064 | 111.33 | 1123.7 |  | 11126 | 143.27 | 3.1451 | 61.318 | 0.0088064 | 111.33 | 1123.7 | 1012.37
11127 | 3.1459 | 143.28 | 61.318 | 0.0088084 | 111.34 | 1123.7 |  | 11127 | 143.28 | 3.1459 | 61.318 | 0.0088084 | 111.34 | 1123.7 | 1012.36
11128 | 3.1467 | 143.29 | 61.317 | 0.0088105 | 111.35 | 1123.7 |  | 11128 | 143.29 | 3.1467 | 61.317 | 0.0088105 | 111.35 | 1123.7 | 1012.35
11129 | 3.1475 | 143.3 | 61.317 | 0.0088126 | 111.36 | 1123.7 |  | 11129 | 143.3 | 3.1475 | 61.317 | 0.0088126 | 111.36 | 1123.7 | 1012.34
11130 | 3.1483 | 143.31 | 61.317 | 0.0088147 | 111.37 | 1123.7 |  | 11130 | 143.31 | 3.1483 | 61.317 | 0.0088147 | 111.37 | 1123.7 | 1012.33
11131 | 3.1491 | 143.32 | 61.317 | 0.0088168 | 111.38 | 1123.7 |  | 11131 | 143.32 | 3.1491 | 61.317 | 0.0088168 | 111.38 | 1123.7 | 1012.32
11132 | 3.1499 | 143.33 | 61.317 | 0.0088189 | 111.39 | 1123.7 |  | 11132 | 143.33 | 3.1499 | 61.317 | 0.0088189 | 111.39 | 1123.7 | 1012.31
11133 | 3.1507 | 143.34 | 61.317 | 0.008821 | 111.4 | 1123.7 |  | 11133 | 143.34 | 3.1507 | 61.317 | 0.008821 | 111.4 | 1123.7 | 1012.3
11134 | 3.1515 | 143.35 | 61.316 | 0.0088232 | 111.41 | 1123.7 |  | 11134 | 143.35 | 3.1515 | 61.316 | 0.0088232 | 111.41 | 1123.7 | 1012.29
11135 | 3.1523 | 143.36 | 61.316 | 0.0088253 | 111.42 | 1123.7 |  | 11135 | 143.36 | 3.1523 | 61.316 | 0.0088253 | 111.42 | 1123.7 | 1012.28
11136 | 3.1531 | 143.37 | 61.316 | 0.0088274 | 111.43 | 1123.7 |  | 11136 | 143.37 | 3.1531 | 61.316 | 0.0088274 | 111.43 | 1123.7 | 1012.27
11137 | 3.1539 | 143.38 | 61.316 | 0.0088295 | 111.44 | 1123.8 |  | 11137 | 143.38 | 3.1539 | 61.316 | 0.0088295 | 111.44 | 1123.8 | 1012.36
11138 | 3.1547 | 143.39 | 61.316 | 0.0088316 | 111.45 | 1123.8 |  | 11138 | 143.39 | 3.1547 | 61.316 | 0.0088316 | 111.45 | 1123.8 | 1012.35
11139 | 3.1555 | 143.4 | 61.315 | 0.0088337 | 111.46 | 1123.8 |  | 11139 | 143.4 | 3.1555 | 61.315 | 0.0088337 | 111.46 | 1123.8 | 1012.34
11140 | 3.1563 | 143.41 | 61.315 | 0.0088358 | 111.47 | 1123.8 |  | 11140 | 143.41 | 3.1563 | 61.315 | 0.0088358 | 111.47 | 1123.8 | 1012.33
11141 | 3.1571 | 143.42 | 61.315 | 0.0088379 | 111.48 | 1123.8 |  | 11141 | 143.42 | 3.1571 | 61.315 | 0.0088379 | 111.48 | 1123.8 | 1012.32
11142 | 3.1579 | 143.43 | 61.315 | 0.00884 | 111.49 | 1123.8 |  | 11142 | 143.43 | 3.1579 | 61.315 | 0.00884 | 111.49 | 1123.8 | 1012.31
11143 | 3.1587 | 143.44 | 61.315 | 0.0088421 | 111.5 | 1123.8 |  | 11143 | 143.44 | 3.1587 | 61.315 | 0.0088421 | 111.5 | 1123.8 | 1012.3
11144 | 3.1595 | 143.45 | 61.315 | 0.0088442 | 111.51 | 1123.8 |  | 11144 | 143.45 | 3.1595 | 61.315 | 0.0088442 | 111.51 | 1123.8 | 1012.29
11145 | 3.1603 | 143.46 | 61.314 | 0.0088463 | 111.52 | 1123.8 |  | 11145 | 143.46 | 3.1603 | 61.314 | 0.0088463 | 111.52 | 1123.8 | 1012.28
11146 | 3.1611 | 143.47 | 61.314 | 0.0088484 | 111.53 | 1123.8 |  | 11146 | 143.47 | 3.1611 | 61.314 | 0.0088484 | 111.53 | 1123.8 | 1012.27
11147 | 3.1619 | 143.48 | 61.314 | 0.0088505 | 111.54 | 1123.8 |  | 11147 | 143.48 | 3.1619 | 61.314 | 0.0088505 | 111.54 | 1123.8 | 1012.26
11148 | 3.1627 | 143.49 | 61.314 | 0.0088526 | 111.55 | 1123.8 |  | 11148 | 143.49 | 3.1627 | 61.314 | 0.0088526 | 111.55 | 1123.8 | 1012.25
11149 | 3.1635 | 143.5 | 61.314 | 0.0088547 | 111.56 | 1123.8 |  | 11149 | 143.5 | 3.1635 | 61.314 | 0.0088547 | 111.56 | 1123.8 | 1012.24
11150 | 3.1643 | 143.51 | 61.313 | 0.0088568 | 111.57 | 1123.8 |  | 11150 | 143.51 | 3.1643 | 61.313 | 0.0088568 | 111.57 | 1123.8 | 1012.23
11151 | 3.1651 | 143.52 | 61.313 | 0.0088589 | 111.58 | 1123.8 |  | 11151 | 143.52 | 3.1651 | 61.313 | 0.0088589 | 111.58 | 1123.8 | 1012.22
11152 | 3.1659 | 143.53 | 61.313 | 0.0088611 | 111.59 | 1123.8 |  | 11152 | 143.53 | 3.1659 | 61.313 | 0.0088611 | 111.59 | 1123.8 | 1012.21
11153 | 3.1667 | 143.54 | 61.313 | 0.0088632 | 111.6 | 1123.8 |  | 11153 | 143.54 | 3.1667 | 61.313 | 0.0088632 | 111.6 | 1123.8 | 1012.2
11154 | 3.1675 | 143.55 | 61.313 | 0.0088653 | 111.61 | 1123.8 |  | 11154 | 143.55 | 3.1675 | 61.313 | 0.0088653 | 111.61 | 1123.8 | 1012.19
11155 | 3.1683 | 143.56 | 61.312 | 0.0088674 | 111.62 | 1123.8 |  | 11155 | 143.56 | 3.1683 | 61.312 | 0.0088674 | 111.62 | 1123.8 | 1012.18
11156 | 3.1691 | 143.57 | 61.312 | 0.0088695 | 111.63 | 1123.8 |  | 11156 | 143.57 | 3.1691 | 61.312 | 0.0088695 | 111.63 | 1123.8 | 1012.17
11157 | 3.1699 | 143.58 | 61.312 | 0.0088716 | 111.64 | 1123.8 |  | 11157 | 143.58 | 3.1699 | 61.312 | 0.0088716 | 111.64 | 1123.8 | 1012.16
11158 | 3.1707 | 143.59 | 61.312 | 0.0088737 | 111.65 | 1123.8 |  | 11158 | 143.59 | 3.1707 | 61.312 | 0.0088737 | 111.65 | 1123.8 | 1012.15
11159 | 3.1715 | 143.6 | 61.312 | 0.0088758 | 111.66 | 1123.8 |  | 11159 | 143.6 | 3.1715 | 61.312 | 0.0088758 | 111.66 | 1123.8 | 1012.14
11160 | 3.1723 | 143.61 | 61.312 | 0.0088779 | 111.67 | 1123.8 |  | 11160 | 143.61 | 3.1723 | 61.312 | 0.0088779 | 111.67 | 1123.8 | 1012.13
11161 | 3.1731 | 143.62 | 61.311 | 0.0088801 | 111.68 | 1123.9 |  | 11161 | 143.62 | 3.1731 | 61.311 | 0.0088801 | 111.68 | 1123.9 | 1012.22
11162 | 3.174 | 143.63 | 61.311 | 0.0088822 | 111.69 | 1123.9 |  | 11162 | 143.63 | 3.174 | 61.311 | 0.0088822 | 111.69 | 1123.9 | 1012.21
11163 | 3.1748 | 143.64 | 61.311 | 0.0088843 | 111.7 | 1123.9 |  | 11163 | 143.64 | 3.1748 | 61.311 | 0.0088843 | 111.7 | 1123.9 | 1012.2
11164 | 3.1756 | 143.65 | 61.311 | 0.0088864 | 111.71 | 1123.9 |  | 11164 | 143.65 | 3.1756 | 61.311 | 0.0088864 | 111.71 | 1123.9 | 1012.19
11165 | 3.1764 | 143.66 | 61.311 | 0.0088885 | 111.72 | 1123.9 |  | 11165 | 143.66 | 3.1764 | 61.311 | 0.0088885 | 111.72 | 1123.9 | 1012.18
11166 | 3.1772 | 143.67 | 61.31 | 0.0088906 | 111.73 | 1123.9 |  | 11166 | 143.67 | 3.1772 | 61.31 | 0.0088906 | 111.73 | 1123.9 | 1012.17
11167 | 3.178 | 143.68 | 61.31 | 0.0088927 | 111.74 | 1123.9 |  | 11167 | 143.68 | 3.178 | 61.31 | 0.0088927 | 111.74 | 1123.9 | 1012.16
11168 | 3.1788 | 143.69 | 61.31 | 0.0088949 | 111.75 | 1123.9 |  | 11168 | 143.69 | 3.1788 | 61.31 | 0.0088949 | 111.75 | 1123.9 | 1012.15
11169 | 3.1796 | 143.7 | 61.31 | 0.008897 | 111.76 | 1123.9 |  | 11169 | 143.7 | 3.1796 | 61.31 | 0.008897 | 111.76 | 1123.9 | 1012.14
11170 | 3.1804 | 143.71 | 61.31 | 0.0088991 | 111.77 | 1123.9 |  | 11170 | 143.71 | 3.1804 | 61.31 | 0.0088991 | 111.77 | 1123.9 | 1012.13
11171 | 3.1812 | 143.72 | 61.31 | 0.0089012 | 111.78 | 1123.9 |  | 11171 | 143.72 | 3.1812 | 61.31 | 0.0089012 | 111.78 | 1123.9 | 1012.12
11172 | 3.182 | 143.73 | 61.309 | 0.0089033 | 111.79 | 1123.9 |  | 11172 | 143.73 | 3.182 | 61.309 | 0.0089033 | 111.79 | 1123.9 | 1012.11
11173 | 3.1828 | 143.74 | 61.309 | 0.0089054 | 111.8 | 1123.9 |  | 11173 | 143.74 | 3.1828 | 61.309 | 0.0089054 | 111.8 | 1123.9 | 1012.1
11174 | 3.1836 | 143.75 | 61.309 | 0.0089076 | 111.81 | 1123.9 |  | 11174 | 143.75 | 3.1836 | 61.309 | 0.0089076 | 111.81 | 1123.9 | 1012.09
11175 | 3.1844 | 143.76 | 61.309 | 0.0089097 | 111.82 | 1123.9 |  | 11175 | 143.76 | 3.1844 | 61.309 | 0.0089097 | 111.82 | 1123.9 | 1012.08
11176 | 3.1852 | 143.77 | 61.309 | 0.0089118 | 111.83 | 1123.9 |  | 11176 | 143.77 | 3.1852 | 61.309 | 0.0089118 | 111.83 | 1123.9 | 1012.07
11177 | 3.186 | 143.78 | 61.308 | 0.0089139 | 111.84 | 1123.9 |  | 11177 | 143.78 | 3.186 | 61.308 | 0.0089139 | 111.84 | 1123.9 | 1012.06
11178 | 3.1869 | 143.79 | 61.308 | 0.008916 | 111.85 | 1123.9 |  | 11178 | 143.79 | 3.1869 | 61.308 | 0.008916 | 111.85 | 1123.9 | 1012.05
11179 | 3.1877 | 143.8 | 61.308 | 0.0089182 | 111.86 | 1123.9 |  | 11179 | 143.8 | 3.1877 | 61.308 | 0.0089182 | 111.86 | 1123.9 | 1012.04
11180 | 3.1885 | 143.81 | 61.308 | 0.0089203 | 111.87 | 1123.9 |  | 11180 | 143.81 | 3.1885 | 61.308 | 0.0089203 | 111.87 | 1123.9 | 1012.03
11181 | 3.1893 | 143.82 | 61.308 | 0.0089224 | 111.88 | 1123.9 |  | 11181 | 143.82 | 3.1893 | 61.308 | 0.0089224 | 111.88 | 1123.9 | 1012.02
11182 | 3.1901 | 143.83 | 61.308 | 0.0089245 | 111.89 | 1123.9 |  | 11182 | 143.83 | 3.1901 | 61.308 | 0.0089245 | 111.89 | 1123.9 | 1012.01
11183 | 3.1909 | 143.84 | 61.307 | 0.0089266 | 111.9 | 1123.9 |  | 11183 | 143.84 | 3.1909 | 61.307 | 0.0089266 | 111.9 | 1123.9 | 1012
11184 | 3.1917 | 143.85 | 61.307 | 0.0089288 | 111.91 | 1123.9 |  | 11184 | 143.85 | 3.1917 | 61.307 | 0.0089288 | 111.91 | 1123.9 | 1011.99
11185 | 3.1925 | 143.86 | 61.307 | 0.0089309 | 111.92 | 1124 |  | 11185 | 143.86 | 3.1925 | 61.307 | 0.0089309 | 111.92 | 1124 | 1012.08
11186 | 3.1933 | 143.87 | 61.307 | 0.008933 | 111.93 | 1124 |  | 11186 | 143.87 | 3.1933 | 61.307 | 0.008933 | 111.93 | 1124 | 1012.07
11187 | 3.1941 | 143.88 | 61.307 | 0.0089351 | 111.94 | 1124 |  | 11187 | 143.88 | 3.1941 | 61.307 | 0.0089351 | 111.94 | 1124 | 1012.06
11188 | 3.1949 | 143.89 | 61.306 | 0.0089373 | 111.95 | 1124 |  | 11188 | 143.89 | 3.1949 | 61.306 | 0.0089373 | 111.95 | 1124 | 1012.05
11189 | 3.1957 | 143.9 | 61.306 | 0.0089394 | 111.96 | 1124 |  | 11189 | 143.9 | 3.1957 | 61.306 | 0.0089394 | 111.96 | 1124 | 1012.04
11190 | 3.1966 | 143.91 | 61.306 | 0.0089415 | 111.97 | 1124 |  | 11190 | 143.91 | 3.1966 | 61.306 | 0.0089415 | 111.97 | 1124 | 1012.03
11191 | 3.1974 | 143.92 | 61.306 | 0.0089436 | 111.98 | 1124 |  | 11191 | 143.92 | 3.1974 | 61.306 | 0.0089436 | 111.98 | 1124 | 1012.02
11192 | 3.1982 | 143.93 | 61.306 | 0.0089458 | 111.99 | 1124 |  | 11192 | 143.93 | 3.1982 | 61.306 | 0.0089458 | 111.99 | 1124 | 1012.01
11193 | 3.199 | 143.94 | 61.306 | 0.0089479 | 112 | 1124 |  | 11193 | 143.94 | 3.199 | 61.306 | 0.0089479 | 112 | 1124 | 1012
11194 | 3.1998 | 143.95 | 61.305 | 0.00895 | 112.01 | 1124 |  | 11194 | 143.95 | 3.1998 | 61.305 | 0.00895 | 112.01 | 1124 | 1011.99
11195 | 3.2006 | 143.96 | 61.305 | 0.0089521 | 112.02 | 1124 |  | 11195 | 143.96 | 3.2006 | 61.305 | 0.0089521 | 112.02 | 1124 | 1011.98
11196 | 3.2014 | 143.97 | 61.305 | 0.0089543 | 112.03 | 1124 |  | 11196 | 143.97 | 3.2014 | 61.305 | 0.0089543 | 112.03 | 1124 | 1011.97
11197 | 3.2022 | 143.98 | 61.305 | 0.0089564 | 112.04 | 1124 |  | 11197 | 143.98 | 3.2022 | 61.305 | 0.0089564 | 112.04 | 1124 | 1011.96
11198 | 3.203 | 143.99 | 61.305 | 0.0089585 | 112.05 | 1124 |  | 11198 | 143.99 | 3.203 | 61.305 | 0.0089585 | 112.05 | 1124 | 1011.95
11199 | 3.2039 | 144 | 61.304 | 0.0089607 | 112.06 | 1124 |  | 11199 | 144 | 3.2039 | 61.304 | 0.0089607 | 112.06 | 1124 | 1011.94
11200 | 3.2047 | 144.01 | 61.304 | 0.0089628 | 112.07 | 1124 |  | 11200 | 144.01 | 3.2047 | 61.304 | 0.0089628 | 112.07 | 1124 | 1011.93
11201 | 3.2055 | 144.02 | 61.304 | 0.0089649 | 112.08 | 1124 |  | 11201 | 144.02 | 3.2055 | 61.304 | 0.0089649 | 112.08 | 1124 | 1011.92
11202 | 3.2063 | 144.03 | 61.304 | 0.008967 | 112.09 | 1124 |  | 11202 | 144.03 | 3.2063 | 61.304 | 0.008967 | 112.09 | 1124 | 1011.91
11203 | 3.2071 | 144.04 | 61.304 | 0.0089692 | 112.1 | 1124 |  | 11203 | 144.04 | 3.2071 | 61.304 | 0.0089692 | 112.1 | 1124 | 1011.9
11204 | 3.2079 | 144.05 | 61.304 | 0.0089713 | 112.11 | 1124 |  | 11204 | 144.05 | 3.2079 | 61.304 | 0.0089713 | 112.11 | 1124 | 1011.89
11205 | 3.2087 | 144.06 | 61.303 | 0.0089734 | 112.12 | 1124 |  | 11205 | 144.06 | 3.2087 | 61.303 | 0.0089734 | 112.12 | 1124 | 1011.88
11206 | 3.2095 | 144.07 | 61.303 | 0.0089756 | 112.13 | 1124 |  | 11206 | 144.07 | 3.2095 | 61.303 | 0.0089756 | 112.13 | 1124 | 1011.87
11207 | 3.2103 | 144.08 | 61.303 | 0.0089777 | 112.14 | 1124 |  | 11207 | 144.08 | 3.2103 | 61.303 | 0.0089777 | 112.14 | 1124 | 1011.86
11208 | 3.2112 | 144.09 | 61.303 | 0.0089798 | 112.15 | 1124 |  | 11208 | 144.09 | 3.2112 | 61.303 | 0.0089798 | 112.15 | 1124 | 1011.85
11209 | 3.212 | 144.1 | 61.303 | 0.008982 | 112.16 | 1124.1 |  | 11209 | 144.1 | 3.212 | 61.303 | 0.008982 | 112.16 | 1124.1 | 1011.94
11210 | 3.2128 | 144.11 | 61.302 | 0.0089841 | 112.17 | 1124.1 |  | 11210 | 144.11 | 3.2128 | 61.302 | 0.0089841 | 112.17 | 1124.1 | 1011.93
11211 | 3.2136 | 144.12 | 61.302 | 0.0089862 | 112.18 | 1124.1 |  | 11211 | 144.12 | 3.2136 | 61.302 | 0.0089862 | 112.18 | 1124.1 | 1011.92
11212 | 3.2144 | 144.13 | 61.302 | 0.0089884 | 112.19 | 1124.1 |  | 11212 | 144.13 | 3.2144 | 61.302 | 0.0089884 | 112.19 | 1124.1 | 1011.91
11213 | 3.2152 | 144.14 | 61.302 | 0.0089905 | 112.2 | 1124.1 |  | 11213 | 144.14 | 3.2152 | 61.302 | 0.0089905 | 112.2 | 1124.1 | 1011.9
11214 | 3.216 | 144.15 | 61.302 | 0.0089926 | 112.21 | 1124.1 |  | 11214 | 144.15 | 3.216 | 61.302 | 0.0089926 | 112.21 | 1124.1 | 1011.89
11215 | 3.2169 | 144.16 | 61.302 | 0.0089948 | 112.22 | 1124.1 |  | 11215 | 144.16 | 3.2169 | 61.302 | 0.0089948 | 112.22 | 1124.1 | 1011.88
11216 | 3.2177 | 144.17 | 61.301 | 0.0089969 | 112.23 | 1124.1 |  | 11216 | 144.17 | 3.2177 | 61.301 | 0.0089969 | 112.23 | 1124.1 | 1011.87
11217 | 3.2185 | 144.18 | 61.301 | 0.008999 | 112.24 | 1124.1 |  | 11217 | 144.18 | 3.2185 | 61.301 | 0.008999 | 112.24 | 1124.1 | 1011.86
11218 | 3.2193 | 144.19 | 61.301 | 0.0090012 | 112.25 | 1124.1 |  | 11218 | 144.19 | 3.2193 | 61.301 | 0.0090012 | 112.25 | 1124.1 | 1011.85
11219 | 3.2201 | 144.2 | 61.301 | 0.0090033 | 112.26 | 1124.1 |  | 11219 | 144.2 | 3.2201 | 61.301 | 0.0090033 | 112.26 | 1124.1 | 1011.84
11220 | 3.2209 | 144.21 | 61.301 | 0.0090055 | 112.27 | 1124.1 |  | 11220 | 144.21 | 3.2209 | 61.301 | 0.0090055 | 112.27 | 1124.1 | 1011.83
11221 | 3.2217 | 144.22 | 61.3 | 0.0090076 | 112.28 | 1124.1 |  | 11221 | 144.22 | 3.2217 | 61.3 | 0.0090076 | 112.28 | 1124.1 | 1011.82
11222 | 3.2226 | 144.23 | 61.3 | 0.0090097 | 112.29 | 1124.1 |  | 11222 | 144.23 | 3.2226 | 61.3 | 0.0090097 | 112.29 | 1124.1 | 1011.81
11223 | 3.2234 | 144.24 | 61.3 | 0.0090119 | 112.3 | 1124.1 |  | 11223 | 144.24 | 3.2234 | 61.3 | 0.0090119 | 112.3 | 1124.1 | 1011.8
11224 | 3.2242 | 144.25 | 61.3 | 0.009014 | 112.31 | 1124.1 |  | 11224 | 144.25 | 3.2242 | 61.3 | 0.009014 | 112.31 | 1124.1 | 1011.79
11225 | 3.225 | 144.26 | 61.3 | 0.0090162 | 112.32 | 1124.1 |  | 11225 | 144.26 | 3.225 | 61.3 | 0.0090162 | 112.32 | 1124.1 | 1011.78
11226 | 3.2258 | 144.27 | 61.3 | 0.0090183 | 112.33 | 1124.1 |  | 11226 | 144.27 | 3.2258 | 61.3 | 0.0090183 | 112.33 | 1124.1 | 1011.77
11227 | 3.2266 | 144.28 | 61.299 | 0.0090204 | 112.34 | 1124.1 |  | 11227 | 144.28 | 3.2266 | 61.299 | 0.0090204 | 112.34 | 1124.1 | 1011.76
11228 | 3.2275 | 144.29 | 61.299 | 0.0090226 | 112.35 | 1124.1 |  | 11228 | 144.29 | 3.2275 | 61.299 | 0.0090226 | 112.35 | 1124.1 | 1011.75
11229 | 3.2283 | 144.3 | 61.299 | 0.0090247 | 112.36 | 1124.1 |  | 11229 | 144.3 | 3.2283 | 61.299 | 0.0090247 | 112.36 | 1124.1 | 1011.74
11230 | 3.2291 | 144.31 | 61.299 | 0.0090269 | 112.37 | 1124.1 |  | 11230 | 144.31 | 3.2291 | 61.299 | 0.0090269 | 112.37 | 1124.1 | 1011.73
11231 | 3.2299 | 144.32 | 61.299 | 0.009029 | 112.38 | 1124.1 |  | 11231 | 144.32 | 3.2299 | 61.299 | 0.009029 | 112.38 | 1124.1 | 1011.72
11232 | 3.2307 | 144.33 | 61.298 | 0.0090311 | 112.39 | 1124.1 |  | 11232 | 144.33 | 3.2307 | 61.298 | 0.0090311 | 112.39 | 1124.1 | 1011.71
11233 | 3.2315 | 144.34 | 61.298 | 0.0090333 | 112.4 | 1124.2 |  | 11233 | 144.34 | 3.2315 | 61.298 | 0.0090333 | 112.4 | 1124.2 | 1011.8
11234 | 3.2324 | 144.35 | 61.298 | 0.0090354 | 112.41 | 1124.2 |  | 11234 | 144.35 | 3.2324 | 61.298 | 0.0090354 | 112.41 | 1124.2 | 1011.79
11235 | 3.2332 | 144.36 | 61.298 | 0.0090376 | 112.42 | 1124.2 |  | 11235 | 144.36 | 3.2332 | 61.298 | 0.0090376 | 112.42 | 1124.2 | 1011.78
11236 | 3.234 | 144.37 | 61.298 | 0.0090397 | 112.43 | 1124.2 |  | 11236 | 144.37 | 3.234 | 61.298 | 0.0090397 | 112.43 | 1124.2 | 1011.77
11237 | 3.2348 | 144.38 | 61.298 | 0.0090419 | 112.44 | 1124.2 |  | 11237 | 144.38 | 3.2348 | 61.298 | 0.0090419 | 112.44 | 1124.2 | 1011.76
11238 | 3.2356 | 144.39 | 61.297 | 0.009044 | 112.45 | 1124.2 |  | 11238 | 144.39 | 3.2356 | 61.297 | 0.009044 | 112.45 | 1124.2 | 1011.75
11239 | 3.2364 | 144.4 | 61.297 | 0.0090462 | 112.46 | 1124.2 |  | 11239 | 144.4 | 3.2364 | 61.297 | 0.0090462 | 112.46 | 1124.2 | 1011.74
11240 | 3.2373 | 144.41 | 61.297 | 0.0090483 | 112.47 | 1124.2 |  | 11240 | 144.41 | 3.2373 | 61.297 | 0.0090483 | 112.47 | 1124.2 | 1011.73
11241 | 3.2381 | 144.42 | 61.297 | 0.0090504 | 112.48 | 1124.2 |  | 11241 | 144.42 | 3.2381 | 61.297 | 0.0090504 | 112.48 | 1124.2 | 1011.72
11242 | 3.2389 | 144.43 | 61.297 | 0.0090526 | 112.49 | 1124.2 |  | 11242 | 144.43 | 3.2389 | 61.297 | 0.0090526 | 112.49 | 1124.2 | 1011.71
11243 | 3.2397 | 144.44 | 61.296 | 0.0090547 | 112.5 | 1124.2 |  | 11243 | 144.44 | 3.2397 | 61.296 | 0.0090547 | 112.5 | 1124.2 | 1011.7
11244 | 3.2405 | 144.45 | 61.296 | 0.0090569 | 112.51 | 1124.2 |  | 11244 | 144.45 | 3.2405 | 61.296 | 0.0090569 | 112.51 | 1124.2 | 1011.69
11245 | 3.2414 | 144.46 | 61.296 | 0.009059 | 112.52 | 1124.2 |  | 11245 | 144.46 | 3.2414 | 61.296 | 0.009059 | 112.52 | 1124.2 | 1011.68
11246 | 3.2422 | 144.47 | 61.296 | 0.0090612 | 112.53 | 1124.2 |  | 11246 | 144.47 | 3.2422 | 61.296 | 0.0090612 | 112.53 | 1124.2 | 1011.67
11247 | 3.243 | 144.48 | 61.296 | 0.0090633 | 112.54 | 1124.2 |  | 11247 | 144.48 | 3.243 | 61.296 | 0.0090633 | 112.54 | 1124.2 | 1011.66
11248 | 3.2438 | 144.49 | 61.295 | 0.0090655 | 112.55 | 1124.2 |  | 11248 | 144.49 | 3.2438 | 61.295 | 0.0090655 | 112.55 | 1124.2 | 1011.65
11249 | 3.2446 | 144.5 | 61.295 | 0.0090676 | 112.56 | 1124.2 |  | 11249 | 144.5 | 3.2446 | 61.295 | 0.0090676 | 112.56 | 1124.2 | 1011.64
11250 | 3.2455 | 144.51 | 61.295 | 0.0090698 | 112.57 | 1124.2 |  | 11250 | 144.51 | 3.2455 | 61.295 | 0.0090698 | 112.57 | 1124.2 | 1011.63
11251 | 3.2463 | 144.52 | 61.295 | 0.0090719 | 112.58 | 1124.2 |  | 11251 | 144.52 | 3.2463 | 61.295 | 0.0090719 | 112.58 | 1124.2 | 1011.62
11252 | 3.2471 | 144.53 | 61.295 | 0.0090741 | 112.59 | 1124.2 |  | 11252 | 144.53 | 3.2471 | 61.295 | 0.0090741 | 112.59 | 1124.2 | 1011.61
11253 | 3.2479 | 144.54 | 61.295 | 0.0090762 | 112.6 | 1124.2 |  | 11253 | 144.54 | 3.2479 | 61.295 | 0.0090762 | 112.6 | 1124.2 | 1011.6
11254 | 3.2487 | 144.55 | 61.294 | 0.0090784 | 112.61 | 1124.2 |  | 11254 | 144.55 | 3.2487 | 61.294 | 0.0090784 | 112.61 | 1124.2 | 1011.59
11255 | 3.2496 | 144.56 | 61.294 | 0.0090805 | 112.62 | 1124.2 |  | 11255 | 144.56 | 3.2496 | 61.294 | 0.0090805 | 112.62 | 1124.2 | 1011.58
11256 | 3.2504 | 144.57 | 61.294 | 0.0090827 | 112.63 | 1124.2 |  | 11256 | 144.57 | 3.2504 | 61.294 | 0.0090827 | 112.63 | 1124.2 | 1011.57
11257 | 3.2512 | 144.58 | 61.294 | 0.0090849 | 112.64 | 1124.2 |  | 11257 | 144.58 | 3.2512 | 61.294 | 0.0090849 | 112.64 | 1124.2 | 1011.56
11258 | 3.252 | 144.59 | 61.294 | 0.009087 | 112.65 | 1124.3 |  | 11258 | 144.59 | 3.252 | 61.294 | 0.009087 | 112.65 | 1124.3 | 1011.65
11259 | 3.2528 | 144.6 | 61.293 | 0.0090892 | 112.66 | 1124.3 |  | 11259 | 144.6 | 3.2528 | 61.293 | 0.0090892 | 112.66 | 1124.3 | 1011.64
11260 | 3.2537 | 144.61 | 61.293 | 0.0090913 | 112.67 | 1124.3 |  | 11260 | 144.61 | 3.2537 | 61.293 | 0.0090913 | 112.67 | 1124.3 | 1011.63
11261 | 3.2545 | 144.62 | 61.293 | 0.0090935 | 112.68 | 1124.3 |  | 11261 | 144.62 | 3.2545 | 61.293 | 0.0090935 | 112.68 | 1124.3 | 1011.62
11262 | 3.2553 | 144.63 | 61.293 | 0.0090956 | 112.69 | 1124.3 |  | 11262 | 144.63 | 3.2553 | 61.293 | 0.0090956 | 112.69 | 1124.3 | 1011.61
11263 | 3.2561 | 144.64 | 61.293 | 0.0090978 | 112.7 | 1124.3 |  | 11263 | 144.64 | 3.2561 | 61.293 | 0.0090978 | 112.7 | 1124.3 | 1011.6
11264 | 3.257 | 144.65 | 61.293 | 0.0090999 | 112.71 | 1124.3 |  | 11264 | 144.65 | 3.257 | 61.293 | 0.0090999 | 112.71 | 1124.3 | 1011.59
11265 | 3.2578 | 144.66 | 61.292 | 0.0091021 | 112.72 | 1124.3 |  | 11265 | 144.66 | 3.2578 | 61.292 | 0.0091021 | 112.72 | 1124.3 | 1011.58
11266 | 3.2586 | 144.67 | 61.292 | 0.0091043 | 112.73 | 1124.3 |  | 11266 | 144.67 | 3.2586 | 61.292 | 0.0091043 | 112.73 | 1124.3 | 1011.57
11267 | 3.2594 | 144.68 | 61.292 | 0.0091064 | 112.74 | 1124.3 |  | 11267 | 144.68 | 3.2594 | 61.292 | 0.0091064 | 112.74 | 1124.3 | 1011.56
11268 | 3.2602 | 144.69 | 61.292 | 0.0091086 | 112.75 | 1124.3 |  | 11268 | 144.69 | 3.2602 | 61.292 | 0.0091086 | 112.75 | 1124.3 | 1011.55
11269 | 3.2611 | 144.7 | 61.292 | 0.0091107 | 112.76 | 1124.3 |  | 11269 | 144.7 | 3.2611 | 61.292 | 0.0091107 | 112.76 | 1124.3 | 1011.54
11270 | 3.2619 | 144.71 | 61.291 | 0.0091129 | 112.77 | 1124.3 |  | 11270 | 144.71 | 3.2619 | 61.291 | 0.0091129 | 112.77 | 1124.3 | 1011.53
11271 | 3.2627 | 144.72 | 61.291 | 0.009115 | 112.78 | 1124.3 |  | 11271 | 144.72 | 3.2627 | 61.291 | 0.009115 | 112.78 | 1124.3 | 1011.52
11272 | 3.2635 | 144.73 | 61.291 | 0.0091172 | 112.79 | 1124.3 |  | 11272 | 144.73 | 3.2635 | 61.291 | 0.0091172 | 112.79 | 1124.3 | 1011.51
11273 | 3.2644 | 144.74 | 61.291 | 0.0091194 | 112.8 | 1124.3 |  | 11273 | 144.74 | 3.2644 | 61.291 | 0.0091194 | 112.8 | 1124.3 | 1011.5
11274 | 3.2652 | 144.75 | 61.291 | 0.0091215 | 112.81 | 1124.3 |  | 11274 | 144.75 | 3.2652 | 61.291 | 0.0091215 | 112.81 | 1124.3 | 1011.49
11275 | 3.266 | 144.76 | 61.291 | 0.0091237 | 112.82 | 1124.3 |  | 11275 | 144.76 | 3.266 | 61.291 | 0.0091237 | 112.82 | 1124.3 | 1011.48
11276 | 3.2668 | 144.77 | 61.29 | 0.0091259 | 112.83 | 1124.3 |  | 11276 | 144.77 | 3.2668 | 61.29 | 0.0091259 | 112.83 | 1124.3 | 1011.47
11277 | 3.2677 | 144.78 | 61.29 | 0.009128 | 112.84 | 1124.3 |  | 11277 | 144.78 | 3.2677 | 61.29 | 0.009128 | 112.84 | 1124.3 | 1011.46
11278 | 3.2685 | 144.79 | 61.29 | 0.0091302 | 112.85 | 1124.3 |  | 11278 | 144.79 | 3.2685 | 61.29 | 0.0091302 | 112.85 | 1124.3 | 1011.45
11279 | 3.2693 | 144.8 | 61.29 | 0.0091323 | 112.86 | 1124.3 |  | 11279 | 144.8 | 3.2693 | 61.29 | 0.0091323 | 112.86 | 1124.3 | 1011.44
11280 | 3.2701 | 144.81 | 61.29 | 0.0091345 | 112.87 | 1124.3 |  | 11280 | 144.81 | 3.2701 | 61.29 | 0.0091345 | 112.87 | 1124.3 | 1011.43
11281 | 3.271 | 144.82 | 61.289 | 0.0091367 | 112.88 | 1124.3 |  | 11281 | 144.82 | 3.271 | 61.289 | 0.0091367 | 112.88 | 1124.3 | 1011.42
11282 | 3.2718 | 144.83 | 61.289 | 0.0091388 | 112.89 | 1124.4 |  | 11282 | 144.83 | 3.2718 | 61.289 | 0.0091388 | 112.89 | 1124.4 | 1011.51
11283 | 3.2726 | 144.84 | 61.289 | 0.009141 | 112.9 | 1124.4 |  | 11283 | 144.84 | 3.2726 | 61.289 | 0.009141 | 112.9 | 1124.4 | 1011.5
11284 | 3.2734 | 144.85 | 61.289 | 0.0091432 | 112.91 | 1124.4 |  | 11284 | 144.85 | 3.2734 | 61.289 | 0.0091432 | 112.91 | 1124.4 | 1011.49
11285 | 3.2743 | 144.86 | 61.289 | 0.0091453 | 112.92 | 1124.4 |  | 11285 | 144.86 | 3.2743 | 61.289 | 0.0091453 | 112.92 | 1124.4 | 1011.48
11286 | 3.2751 | 144.87 | 61.289 | 0.0091475 | 112.93 | 1124.4 |  | 11286 | 144.87 | 3.2751 | 61.289 | 0.0091475 | 112.93 | 1124.4 | 1011.47
11287 | 3.2759 | 144.88 | 61.288 | 0.0091497 | 112.94 | 1124.4 |  | 11287 | 144.88 | 3.2759 | 61.288 | 0.0091497 | 112.94 | 1124.4 | 1011.46
11288 | 3.2768 | 144.89 | 61.288 | 0.0091518 | 112.95 | 1124.4 |  | 11288 | 144.89 | 3.2768 | 61.288 | 0.0091518 | 112.95 | 1124.4 | 1011.45
11289 | 3.2776 | 144.9 | 61.288 | 0.009154 | 112.96 | 1124.4 |  | 11289 | 144.9 | 3.2776 | 61.288 | 0.009154 | 112.96 | 1124.4 | 1011.44
11290 | 3.2784 | 144.91 | 61.288 | 0.0091562 | 112.97 | 1124.4 |  | 11290 | 144.91 | 3.2784 | 61.288 | 0.0091562 | 112.97 | 1124.4 | 1011.43
11291 | 3.2792 | 144.92 | 61.288 | 0.0091583 | 112.98 | 1124.4 |  | 11291 | 144.92 | 3.2792 | 61.288 | 0.0091583 | 112.98 | 1124.4 | 1011.42
11292 | 3.2801 | 144.93 | 61.287 | 0.0091605 | 112.99 | 1124.4 |  | 11292 | 144.93 | 3.2801 | 61.287 | 0.0091605 | 112.99 | 1124.4 | 1011.41
11293 | 3.2809 | 144.94 | 61.287 | 0.0091627 | 113 | 1124.4 |  | 11293 | 144.94 | 3.2809 | 61.287 | 0.0091627 | 113 | 1124.4 | 1011.4
11294 | 3.2817 | 144.95 | 61.287 | 0.0091648 | 113.01 | 1124.4 |  | 11294 | 144.95 | 3.2817 | 61.287 | 0.0091648 | 113.01 | 1124.4 | 1011.39
11295 | 3.2825 | 144.96 | 61.287 | 0.009167 | 113.02 | 1124.4 |  | 11295 | 144.96 | 3.2825 | 61.287 | 0.009167 | 113.02 | 1124.4 | 1011.38
11296 | 3.2834 | 144.97 | 61.287 | 0.0091692 | 113.03 | 1124.4 |  | 11296 | 144.97 | 3.2834 | 61.287 | 0.0091692 | 113.03 | 1124.4 | 1011.37
11297 | 3.2842 | 144.98 | 61.287 | 0.0091713 | 113.04 | 1124.4 |  | 11297 | 144.98 | 3.2842 | 61.287 | 0.0091713 | 113.04 | 1124.4 | 1011.36
11298 | 3.285 | 144.99 | 61.286 | 0.0091735 | 113.05 | 1124.4 |  | 11298 | 144.99 | 3.285 | 61.286 | 0.0091735 | 113.05 | 1124.4 | 1011.35
11299 | 3.2859 | 145 | 61.286 | 0.0091757 | 113.06 | 1124.4 |  | 11299 | 145 | 3.2859 | 61.286 | 0.0091757 | 113.06 | 1124.4 | 1011.34
11300 | 3.2867 | 145.01 | 61.286 | 0.0091779 | 113.07 | 1124.4 |  | 11300 | 145.01 | 3.2867 | 61.286 | 0.0091779 | 113.07 | 1124.4 | 1011.33
11301 | 3.2875 | 145.02 | 61.286 | 0.00918 | 113.08 | 1124.4 |  | 11301 | 145.02 | 3.2875 | 61.286 | 0.00918 | 113.08 | 1124.4 | 1011.32
11302 | 3.2883 | 145.03 | 61.286 | 0.0091822 | 113.09 | 1124.4 |  | 11302 | 145.03 | 3.2883 | 61.286 | 0.0091822 | 113.09 | 1124.4 | 1011.31
11303 | 3.2892 | 145.04 | 61.285 | 0.0091844 | 113.1 | 1124.4 |  | 11303 | 145.04 | 3.2892 | 61.285 | 0.0091844 | 113.1 | 1124.4 | 1011.3
11304 | 3.29 | 145.05 | 61.285 | 0.0091866 | 113.11 | 1124.4 |  | 11304 | 145.05 | 3.29 | 61.285 | 0.0091866 | 113.11 | 1124.4 | 1011.29
11305 | 3.2908 | 145.06 | 61.285 | 0.0091887 | 113.12 | 1124.4 |  | 11305 | 145.06 | 3.2908 | 61.285 | 0.0091887 | 113.12 | 1124.4 | 1011.28
11306 | 3.2917 | 145.07 | 61.285 | 0.0091909 | 113.13 | 1124.5 |  | 11306 | 145.07 | 3.2917 | 61.285 | 0.0091909 | 113.13 | 1124.5 | 1011.37
11307 | 3.2925 | 145.08 | 61.285 | 0.0091931 | 113.14 | 1124.5 |  | 11307 | 145.08 | 3.2925 | 61.285 | 0.0091931 | 113.14 | 1124.5 | 1011.36
11308 | 3.2933 | 145.09 | 61.284 | 0.0091953 | 113.15 | 1124.5 |  | 11308 | 145.09 | 3.2933 | 61.284 | 0.0091953 | 113.15 | 1124.5 | 1011.35
11309 | 3.2942 | 145.1 | 61.284 | 0.0091974 | 113.16 | 1124.5 |  | 11309 | 145.1 | 3.2942 | 61.284 | 0.0091974 | 113.16 | 1124.5 | 1011.34
11310 | 3.295 | 145.11 | 61.284 | 0.0091996 | 113.17 | 1124.5 |  | 11310 | 145.11 | 3.295 | 61.284 | 0.0091996 | 113.17 | 1124.5 | 1011.33
11311 | 3.2958 | 145.12 | 61.284 | 0.0092018 | 113.18 | 1124.5 |  | 11311 | 145.12 | 3.2958 | 61.284 | 0.0092018 | 113.18 | 1124.5 | 1011.32
11312 | 3.2967 | 145.13 | 61.284 | 0.009204 | 113.19 | 1124.5 |  | 11312 | 145.13 | 3.2967 | 61.284 | 0.009204 | 113.19 | 1124.5 | 1011.31
11313 | 3.2975 | 145.14 | 61.284 | 0.0092061 | 113.2 | 1124.5 |  | 11313 | 145.14 | 3.2975 | 61.284 | 0.0092061 | 113.2 | 1124.5 | 1011.3
11314 | 3.2983 | 145.15 | 61.283 | 0.0092083 | 113.21 | 1124.5 |  | 11314 | 145.15 | 3.2983 | 61.283 | 0.0092083 | 113.21 | 1124.5 | 1011.29
11315 | 3.2991 | 145.16 | 61.283 | 0.0092105 | 113.22 | 1124.5 |  | 11315 | 145.16 | 3.2991 | 61.283 | 0.0092105 | 113.22 | 1124.5 | 1011.28
11316 | 3.3 | 145.17 | 61.283 | 0.0092127 | 113.23 | 1124.5 |  | 11316 | 145.17 | 3.3 | 61.283 | 0.0092127 | 113.23 | 1124.5 | 1011.27
11317 | 3.3008 | 145.18 | 61.283 | 0.0092149 | 113.24 | 1124.5 |  | 11317 | 145.18 | 3.3008 | 61.283 | 0.0092149 | 113.24 | 1124.5 | 1011.26
11318 | 3.3016 | 145.19 | 61.283 | 0.009217 | 113.25 | 1124.5 |  | 11318 | 145.19 | 3.3016 | 61.283 | 0.009217 | 113.25 | 1124.5 | 1011.25
11319 | 3.3025 | 145.2 | 61.282 | 0.0092192 | 113.26 | 1124.5 |  | 11319 | 145.2 | 3.3025 | 61.282 | 0.0092192 | 113.26 | 1124.5 | 1011.24
11320 | 3.3033 | 145.21 | 61.282 | 0.0092214 | 113.27 | 1124.5 |  | 11320 | 145.21 | 3.3033 | 61.282 | 0.0092214 | 113.27 | 1124.5 | 1011.23
11321 | 3.3041 | 145.22 | 61.282 | 0.0092236 | 113.28 | 1124.5 |  | 11321 | 145.22 | 3.3041 | 61.282 | 0.0092236 | 113.28 | 1124.5 | 1011.22
11322 | 3.305 | 145.23 | 61.282 | 0.0092258 | 113.29 | 1124.5 |  | 11322 | 145.23 | 3.305 | 61.282 | 0.0092258 | 113.29 | 1124.5 | 1011.21
11323 | 3.3058 | 145.24 | 61.282 | 0.0092279 | 113.3 | 1124.5 |  | 11323 | 145.24 | 3.3058 | 61.282 | 0.0092279 | 113.3 | 1124.5 | 1011.2
11324 | 3.3066 | 145.25 | 61.282 | 0.0092301 | 113.31 | 1124.5 |  | 11324 | 145.25 | 3.3066 | 61.282 | 0.0092301 | 113.31 | 1124.5 | 1011.19
11325 | 3.3075 | 145.26 | 61.281 | 0.0092323 | 113.32 | 1124.5 |  | 11325 | 145.26 | 3.3075 | 61.281 | 0.0092323 | 113.32 | 1124.5 | 1011.18
11326 | 3.3083 | 145.27 | 61.281 | 0.0092345 | 113.33 | 1124.5 |  | 11326 | 145.27 | 3.3083 | 61.281 | 0.0092345 | 113.33 | 1124.5 | 1011.17
11327 | 3.3091 | 145.28 | 61.281 | 0.0092367 | 113.34 | 1124.5 |  | 11327 | 145.28 | 3.3091 | 61.281 | 0.0092367 | 113.34 | 1124.5 | 1011.16
11328 | 3.31 | 145.29 | 61.281 | 0.0092389 | 113.35 | 1124.5 |  | 11328 | 145.29 | 3.31 | 61.281 | 0.0092389 | 113.35 | 1124.5 | 1011.15
11329 | 3.3108 | 145.3 | 61.281 | 0.009241 | 113.36 | 1124.5 |  | 11329 | 145.3 | 3.3108 | 61.281 | 0.009241 | 113.36 | 1124.5 | 1011.14
11330 | 3.3116 | 145.31 | 61.28 | 0.0092432 | 113.37 | 1124.6 |  | 11330 | 145.31 | 3.3116 | 61.28 | 0.0092432 | 113.37 | 1124.6 | 1011.23
11331 | 3.3125 | 145.32 | 61.28 | 0.0092454 | 113.38 | 1124.6 |  | 11331 | 145.32 | 3.3125 | 61.28 | 0.0092454 | 113.38 | 1124.6 | 1011.22
11332 | 3.3133 | 145.33 | 61.28 | 0.0092476 | 113.39 | 1124.6 |  | 11332 | 145.33 | 3.3133 | 61.28 | 0.0092476 | 113.39 | 1124.6 | 1011.21
11333 | 3.3141 | 145.34 | 61.28 | 0.0092498 | 113.4 | 1124.6 |  | 11333 | 145.34 | 3.3141 | 61.28 | 0.0092498 | 113.4 | 1124.6 | 1011.2
11334 | 3.315 | 145.35 | 61.28 | 0.009252 | 113.41 | 1124.6 |  | 11334 | 145.35 | 3.315 | 61.28 | 0.009252 | 113.41 | 1124.6 | 1011.19
11335 | 3.3158 | 145.36 | 61.28 | 0.0092542 | 113.42 | 1124.6 |  | 11335 | 145.36 | 3.3158 | 61.28 | 0.0092542 | 113.42 | 1124.6 | 1011.18
11336 | 3.3167 | 145.37 | 61.279 | 0.0092563 | 113.43 | 1124.6 |  | 11336 | 145.37 | 3.3167 | 61.279 | 0.0092563 | 113.43 | 1124.6 | 1011.17
11337 | 3.3175 | 145.38 | 61.279 | 0.0092585 | 113.44 | 1124.6 |  | 11337 | 145.38 | 3.3175 | 61.279 | 0.0092585 | 113.44 | 1124.6 | 1011.16
11338 | 3.3183 | 145.39 | 61.279 | 0.0092607 | 113.45 | 1124.6 |  | 11338 | 145.39 | 3.3183 | 61.279 | 0.0092607 | 113.45 | 1124.6 | 1011.15
11339 | 3.3192 | 145.4 | 61.279 | 0.0092629 | 113.46 | 1124.6 |  | 11339 | 145.4 | 3.3192 | 61.279 | 0.0092629 | 113.46 | 1124.6 | 1011.14
11340 | 3.32 | 145.41 | 61.279 | 0.0092651 | 113.47 | 1124.6 |  | 11340 | 145.41 | 3.32 | 61.279 | 0.0092651 | 113.47 | 1124.6 | 1011.13
11341 | 3.3208 | 145.42 | 61.278 | 0.0092673 | 113.48 | 1124.6 |  | 11341 | 145.42 | 3.3208 | 61.278 | 0.0092673 | 113.48 | 1124.6 | 1011.12
11342 | 3.3217 | 145.43 | 61.278 | 0.0092695 | 113.49 | 1124.6 |  | 11342 | 145.43 | 3.3217 | 61.278 | 0.0092695 | 113.49 | 1124.6 | 1011.11
11343 | 3.3225 | 145.44 | 61.278 | 0.0092717 | 113.5 | 1124.6 |  | 11343 | 145.44 | 3.3225 | 61.278 | 0.0092717 | 113.5 | 1124.6 | 1011.1
11344 | 3.3233 | 145.45 | 61.278 | 0.0092739 | 113.51 | 1124.6 |  | 11344 | 145.45 | 3.3233 | 61.278 | 0.0092739 | 113.51 | 1124.6 | 1011.09
11345 | 3.3242 | 145.46 | 61.278 | 0.009276 | 113.52 | 1124.6 |  | 11345 | 145.46 | 3.3242 | 61.278 | 0.009276 | 113.52 | 1124.6 | 1011.08
11346 | 3.325 | 145.47 | 61.277 | 0.0092782 | 113.53 | 1124.6 |  | 11346 | 145.47 | 3.325 | 61.277 | 0.0092782 | 113.53 | 1124.6 | 1011.07
11347 | 3.3259 | 145.48 | 61.277 | 0.0092804 | 113.54 | 1124.6 |  | 11347 | 145.48 | 3.3259 | 61.277 | 0.0092804 | 113.54 | 1124.6 | 1011.06
11348 | 3.3267 | 145.49 | 61.277 | 0.0092826 | 113.55 | 1124.6 |  | 11348 | 145.49 | 3.3267 | 61.277 | 0.0092826 | 113.55 | 1124.6 | 1011.05
11349 | 3.3275 | 145.5 | 61.277 | 0.0092848 | 113.56 | 1124.6 |  | 11349 | 145.5 | 3.3275 | 61.277 | 0.0092848 | 113.56 | 1124.6 | 1011.04
11350 | 3.3284 | 145.51 | 61.277 | 0.009287 | 113.57 | 1124.6 |  | 11350 | 145.51 | 3.3284 | 61.277 | 0.009287 | 113.57 | 1124.6 | 1011.03
11351 | 3.3292 | 145.52 | 61.277 | 0.0092892 | 113.58 | 1124.6 |  | 11351 | 145.52 | 3.3292 | 61.277 | 0.0092892 | 113.58 | 1124.6 | 1011.02
11352 | 3.33 | 145.53 | 61.276 | 0.0092914 | 113.59 | 1124.6 |  | 11352 | 145.53 | 3.33 | 61.276 | 0.0092914 | 113.59 | 1124.6 | 1011.01
11353 | 3.3309 | 145.54 | 61.276 | 0.0092936 | 113.6 | 1124.6 |  | 11353 | 145.54 | 3.3309 | 61.276 | 0.0092936 | 113.6 | 1124.6 | 1011
11354 | 3.3317 | 145.55 | 61.276 | 0.0092958 | 113.61 | 1124.7 |  | 11354 | 145.55 | 3.3317 | 61.276 | 0.0092958 | 113.61 | 1124.7 | 1011.09
11355 | 3.3326 | 145.56 | 61.276 | 0.009298 | 113.62 | 1124.7 |  | 11355 | 145.56 | 3.3326 | 61.276 | 0.009298 | 113.62 | 1124.7 | 1011.08
11356 | 3.3334 | 145.57 | 61.276 | 0.0093002 | 113.63 | 1124.7 |  | 11356 | 145.57 | 3.3334 | 61.276 | 0.0093002 | 113.63 | 1124.7 | 1011.07
11357 | 3.3342 | 145.58 | 61.275 | 0.0093024 | 113.64 | 1124.7 |  | 11357 | 145.58 | 3.3342 | 61.275 | 0.0093024 | 113.64 | 1124.7 | 1011.06
11358 | 3.3351 | 145.59 | 61.275 | 0.0093046 | 113.65 | 1124.7 |  | 11358 | 145.59 | 3.3351 | 61.275 | 0.0093046 | 113.65 | 1124.7 | 1011.05
11359 | 3.3359 | 145.6 | 61.275 | 0.0093068 | 113.66 | 1124.7 |  | 11359 | 145.6 | 3.3359 | 61.275 | 0.0093068 | 113.66 | 1124.7 | 1011.04
11360 | 3.3368 | 145.61 | 61.275 | 0.009309 | 113.67 | 1124.7 |  | 11360 | 145.61 | 3.3368 | 61.275 | 0.009309 | 113.67 | 1124.7 | 1011.03
11361 | 3.3376 | 145.62 | 61.275 | 0.0093112 | 113.68 | 1124.7 |  | 11361 | 145.62 | 3.3376 | 61.275 | 0.0093112 | 113.68 | 1124.7 | 1011.02
11362 | 3.3384 | 145.63 | 61.275 | 0.0093134 | 113.69 | 1124.7 |  | 11362 | 145.63 | 3.3384 | 61.275 | 0.0093134 | 113.69 | 1124.7 | 1011.01
11363 | 3.3393 | 145.64 | 61.274 | 0.0093156 | 113.7 | 1124.7 |  | 11363 | 145.64 | 3.3393 | 61.274 | 0.0093156 | 113.7 | 1124.7 | 1011
11364 | 3.3401 | 145.65 | 61.274 | 0.0093178 | 113.71 | 1124.7 |  | 11364 | 145.65 | 3.3401 | 61.274 | 0.0093178 | 113.71 | 1124.7 | 1010.99
11365 | 3.341 | 145.66 | 61.274 | 0.00932 | 113.72 | 1124.7 |  | 11365 | 145.66 | 3.341 | 61.274 | 0.00932 | 113.72 | 1124.7 | 1010.98
11366 | 3.3418 | 145.67 | 61.274 | 0.0093222 | 113.73 | 1124.7 |  | 11366 | 145.67 | 3.3418 | 61.274 | 0.0093222 | 113.73 | 1124.7 | 1010.97
11367 | 3.3426 | 145.68 | 61.274 | 0.0093244 | 113.74 | 1124.7 |  | 11367 | 145.68 | 3.3426 | 61.274 | 0.0093244 | 113.74 | 1124.7 | 1010.96
11368 | 3.3435 | 145.69 | 61.273 | 0.0093266 | 113.75 | 1124.7 |  | 11368 | 145.69 | 3.3435 | 61.273 | 0.0093266 | 113.75 | 1124.7 | 1010.95
11369 | 3.3443 | 145.7 | 61.273 | 0.0093288 | 113.76 | 1124.7 |  | 11369 | 145.7 | 3.3443 | 61.273 | 0.0093288 | 113.76 | 1124.7 | 1010.94
11370 | 3.3452 | 145.71 | 61.273 | 0.009331 | 113.77 | 1124.7 |  | 11370 | 145.71 | 3.3452 | 61.273 | 0.009331 | 113.77 | 1124.7 | 1010.93
11371 | 3.346 | 145.72 | 61.273 | 0.0093332 | 113.78 | 1124.7 |  | 11371 | 145.72 | 3.346 | 61.273 | 0.0093332 | 113.78 | 1124.7 | 1010.92
11372 | 3.3468 | 145.73 | 61.273 | 0.0093354 | 113.79 | 1124.7 |  | 11372 | 145.73 | 3.3468 | 61.273 | 0.0093354 | 113.79 | 1124.7 | 1010.91
11373 | 3.3477 | 145.74 | 61.272 | 0.0093376 | 113.8 | 1124.7 |  | 11373 | 145.74 | 3.3477 | 61.272 | 0.0093376 | 113.8 | 1124.7 | 1010.9
11374 | 3.3485 | 145.75 | 61.272 | 0.0093398 | 113.81 | 1124.7 |  | 11374 | 145.75 | 3.3485 | 61.272 | 0.0093398 | 113.81 | 1124.7 | 1010.89
11375 | 3.3494 | 145.76 | 61.272 | 0.009342 | 113.82 | 1124.7 |  | 11375 | 145.76 | 3.3494 | 61.272 | 0.009342 | 113.82 | 1124.7 | 1010.88
11376 | 3.3502 | 145.77 | 61.272 | 0.0093442 | 113.83 | 1124.7 |  | 11376 | 145.77 | 3.3502 | 61.272 | 0.0093442 | 113.83 | 1124.7 | 1010.87
11377 | 3.3511 | 145.78 | 61.272 | 0.0093464 | 113.84 | 1124.7 |  | 11377 | 145.78 | 3.3511 | 61.272 | 0.0093464 | 113.84 | 1124.7 | 1010.86
11378 | 3.3519 | 145.79 | 61.272 | 0.0093486 | 113.85 | 1124.8 |  | 11378 | 145.79 | 3.3519 | 61.272 | 0.0093486 | 113.85 | 1124.8 | 1010.95
11379 | 3.3527 | 145.8 | 61.271 | 0.0093508 | 113.86 | 1124.8 |  | 11379 | 145.8 | 3.3527 | 61.271 | 0.0093508 | 113.86 | 1124.8 | 1010.94
11380 | 3.3536 | 145.81 | 61.271 | 0.009353 | 113.87 | 1124.8 |  | 11380 | 145.81 | 3.3536 | 61.271 | 0.009353 | 113.87 | 1124.8 | 1010.93
11381 | 3.3544 | 145.82 | 61.271 | 0.0093552 | 113.88 | 1124.8 |  | 11381 | 145.82 | 3.3544 | 61.271 | 0.0093552 | 113.88 | 1124.8 | 1010.92
11382 | 3.3553 | 145.83 | 61.271 | 0.0093574 | 113.89 | 1124.8 |  | 11382 | 145.83 | 3.3553 | 61.271 | 0.0093574 | 113.89 | 1124.8 | 1010.91
11383 | 3.3561 | 145.84 | 61.271 | 0.0093596 | 113.9 | 1124.8 |  | 11383 | 145.84 | 3.3561 | 61.271 | 0.0093596 | 113.9 | 1124.8 | 1010.9
11384 | 3.357 | 145.85 | 61.27 | 0.0093619 | 113.91 | 1124.8 |  | 11384 | 145.85 | 3.357 | 61.27 | 0.0093619 | 113.91 | 1124.8 | 1010.89
11385 | 3.3578 | 145.86 | 61.27 | 0.0093641 | 113.92 | 1124.8 |  | 11385 | 145.86 | 3.3578 | 61.27 | 0.0093641 | 113.92 | 1124.8 | 1010.88
11386 | 3.3587 | 145.87 | 61.27 | 0.0093663 | 113.93 | 1124.8 |  | 11386 | 145.87 | 3.3587 | 61.27 | 0.0093663 | 113.93 | 1124.8 | 1010.87
11387 | 3.3595 | 145.88 | 61.27 | 0.0093685 | 113.94 | 1124.8 |  | 11387 | 145.88 | 3.3595 | 61.27 | 0.0093685 | 113.94 | 1124.8 | 1010.86
11388 | 3.3603 | 145.89 | 61.27 | 0.0093707 | 113.95 | 1124.8 |  | 11388 | 145.89 | 3.3603 | 61.27 | 0.0093707 | 113.95 | 1124.8 | 1010.85
11389 | 3.3612 | 145.9 | 61.27 | 0.0093729 | 113.96 | 1124.8 |  | 11389 | 145.9 | 3.3612 | 61.27 | 0.0093729 | 113.96 | 1124.8 | 1010.84
11390 | 3.362 | 145.91 | 61.269 | 0.0093751 | 113.97 | 1124.8 |  | 11390 | 145.91 | 3.362 | 61.269 | 0.0093751 | 113.97 | 1124.8 | 1010.83
11391 | 3.3629 | 145.92 | 61.269 | 0.0093773 | 113.98 | 1124.8 |  | 11391 | 145.92 | 3.3629 | 61.269 | 0.0093773 | 113.98 | 1124.8 | 1010.82
11392 | 3.3637 | 145.93 | 61.269 | 0.0093795 | 113.99 | 1124.8 |  | 11392 | 145.93 | 3.3637 | 61.269 | 0.0093795 | 113.99 | 1124.8 | 1010.81
11393 | 3.3646 | 145.94 | 61.269 | 0.0093817 | 114 | 1124.8 |  | 11393 | 145.94 | 3.3646 | 61.269 | 0.0093817 | 114 | 1124.8 | 1010.8
11394 | 3.3654 | 145.95 | 61.269 | 0.009384 | 114.01 | 1124.8 |  | 11394 | 145.95 | 3.3654 | 61.269 | 0.009384 | 114.01 | 1124.8 | 1010.79
11395 | 3.3663 | 145.96 | 61.268 | 0.0093862 | 114.02 | 1124.8 |  | 11395 | 145.96 | 3.3663 | 61.268 | 0.0093862 | 114.02 | 1124.8 | 1010.78
11396 | 3.3671 | 145.97 | 61.268 | 0.0093884 | 114.03 | 1124.8 |  | 11396 | 145.97 | 3.3671 | 61.268 | 0.0093884 | 114.03 | 1124.8 | 1010.77
11397 | 3.368 | 145.98 | 61.268 | 0.0093906 | 114.04 | 1124.8 |  | 11397 | 145.98 | 3.368 | 61.268 | 0.0093906 | 114.04 | 1124.8 | 1010.76
11398 | 3.3688 | 145.99 | 61.268 | 0.0093928 | 114.05 | 1124.8 |  | 11398 | 145.99 | 3.3688 | 61.268 | 0.0093928 | 114.05 | 1124.8 | 1010.75
11399 | 3.3696 | 146 | 61.268 | 0.009395 | 114.06 | 1124.8 |  | 11399 | 146 | 3.3696 | 61.268 | 0.009395 | 114.06 | 1124.8 | 1010.74
11400 | 3.3705 | 146.01 | 61.268 | 0.0093972 | 114.07 | 1124.8 |  | 11400 | 146.01 | 3.3705 | 61.268 | 0.0093972 | 114.07 | 1124.8 | 1010.73
11401 | 3.3713 | 146.02 | 61.267 | 0.0093995 | 114.08 | 1124.8 |  | 11401 | 146.02 | 3.3713 | 61.267 | 0.0093995 | 114.08 | 1124.8 | 1010.72
11402 | 3.3722 | 146.03 | 61.267 | 0.0094017 | 114.09 | 1124.9 |  | 11402 | 146.03 | 3.3722 | 61.267 | 0.0094017 | 114.09 | 1124.9 | 1010.81
11403 | 3.373 | 146.04 | 61.267 | 0.0094039 | 114.1 | 1124.9 |  | 11403 | 146.04 | 3.373 | 61.267 | 0.0094039 | 114.1 | 1124.9 | 1010.8
11404 | 3.3739 | 146.05 | 61.267 | 0.0094061 | 114.11 | 1124.9 |  | 11404 | 146.05 | 3.3739 | 61.267 | 0.0094061 | 114.11 | 1124.9 | 1010.79
11405 | 3.3747 | 146.06 | 61.267 | 0.0094083 | 114.12 | 1124.9 |  | 11405 | 146.06 | 3.3747 | 61.267 | 0.0094083 | 114.12 | 1124.9 | 1010.78
11406 | 3.3756 | 146.07 | 61.266 | 0.0094105 | 114.13 | 1124.9 |  | 11406 | 146.07 | 3.3756 | 61.266 | 0.0094105 | 114.13 | 1124.9 | 1010.77
11407 | 3.3764 | 146.08 | 61.266 | 0.0094128 | 114.14 | 1124.9 |  | 11407 | 146.08 | 3.3764 | 61.266 | 0.0094128 | 114.14 | 1124.9 | 1010.76
11408 | 3.3773 | 146.09 | 61.266 | 0.009415 | 114.15 | 1124.9 |  | 11408 | 146.09 | 3.3773 | 61.266 | 0.009415 | 114.15 | 1124.9 | 1010.75
11409 | 3.3781 | 146.1 | 61.266 | 0.0094172 | 114.16 | 1124.9 |  | 11409 | 146.1 | 3.3781 | 61.266 | 0.0094172 | 114.16 | 1124.9 | 1010.74
11410 | 3.379 | 146.11 | 61.266 | 0.0094194 | 114.17 | 1124.9 |  | 11410 | 146.11 | 3.379 | 61.266 | 0.0094194 | 114.17 | 1124.9 | 1010.73
11411 | 3.3798 | 146.12 | 61.265 | 0.0094216 | 114.18 | 1124.9 |  | 11411 | 146.12 | 3.3798 | 61.265 | 0.0094216 | 114.18 | 1124.9 | 1010.72
11412 | 3.3807 | 146.13 | 61.265 | 0.0094239 | 114.19 | 1124.9 |  | 11412 | 146.13 | 3.3807 | 61.265 | 0.0094239 | 114.19 | 1124.9 | 1010.71
11413 | 3.3815 | 146.14 | 61.265 | 0.0094261 | 114.2 | 1124.9 |  | 11413 | 146.14 | 3.3815 | 61.265 | 0.0094261 | 114.2 | 1124.9 | 1010.7
11414 | 3.3824 | 146.15 | 61.265 | 0.0094283 | 114.21 | 1124.9 |  | 11414 | 146.15 | 3.3824 | 61.265 | 0.0094283 | 114.21 | 1124.9 | 1010.69
11415 | 3.3832 | 146.16 | 61.265 | 0.0094305 | 114.22 | 1124.9 |  | 11415 | 146.16 | 3.3832 | 61.265 | 0.0094305 | 114.22 | 1124.9 | 1010.68
11416 | 3.3841 | 146.17 | 61.265 | 0.0094327 | 114.23 | 1124.9 |  | 11416 | 146.17 | 3.3841 | 61.265 | 0.0094327 | 114.23 | 1124.9 | 1010.67
11417 | 3.3849 | 146.18 | 61.264 | 0.009435 | 114.24 | 1124.9 |  | 11417 | 146.18 | 3.3849 | 61.264 | 0.009435 | 114.24 | 1124.9 | 1010.66
11418 | 3.3858 | 146.19 | 61.264 | 0.0094372 | 114.25 | 1124.9 |  | 11418 | 146.19 | 3.3858 | 61.264 | 0.0094372 | 114.25 | 1124.9 | 1010.65
11419 | 3.3866 | 146.2 | 61.264 | 0.0094394 | 114.26 | 1124.9 |  | 11419 | 146.2 | 3.3866 | 61.264 | 0.0094394 | 114.26 | 1124.9 | 1010.64
11420 | 3.3875 | 146.21 | 61.264 | 0.0094416 | 114.27 | 1124.9 |  | 11420 | 146.21 | 3.3875 | 61.264 | 0.0094416 | 114.27 | 1124.9 | 1010.63
11421 | 3.3883 | 146.22 | 61.264 | 0.0094439 | 114.28 | 1124.9 |  | 11421 | 146.22 | 3.3883 | 61.264 | 0.0094439 | 114.28 | 1124.9 | 1010.62
11422 | 3.3892 | 146.23 | 61.263 | 0.0094461 | 114.29 | 1124.9 |  | 11422 | 146.23 | 3.3892 | 61.263 | 0.0094461 | 114.29 | 1124.9 | 1010.61
11423 | 3.39 | 146.24 | 61.263 | 0.0094483 | 114.3 | 1124.9 |  | 11423 | 146.24 | 3.39 | 61.263 | 0.0094483 | 114.3 | 1124.9 | 1010.6
11424 | 3.3909 | 146.25 | 61.263 | 0.0094505 | 114.31 | 1124.9 |  | 11424 | 146.25 | 3.3909 | 61.263 | 0.0094505 | 114.31 | 1124.9 | 1010.59
11425 | 3.3917 | 146.26 | 61.263 | 0.0094528 | 114.32 | 1124.9 |  | 11425 | 146.26 | 3.3917 | 61.263 | 0.0094528 | 114.32 | 1124.9 | 1010.58
11426 | 3.3926 | 146.27 | 61.263 | 0.009455 | 114.33 | 1124.9 |  | 11426 | 146.27 | 3.3926 | 61.263 | 0.009455 | 114.33 | 1124.9 | 1010.57
11427 | 3.3934 | 146.28 | 61.263 | 0.0094572 | 114.34 | 1125 |  | 11427 | 146.28 | 3.3934 | 61.263 | 0.0094572 | 114.34 | 1125 | 1010.66
11428 | 3.3943 | 146.29 | 61.262 | 0.0094595 | 114.35 | 1125 |  | 11428 | 146.29 | 3.3943 | 61.262 | 0.0094595 | 114.35 | 1125 | 1010.65
11429 | 3.3951 | 146.3 | 61.262 | 0.0094617 | 114.36 | 1125 |  | 11429 | 146.3 | 3.3951 | 61.262 | 0.0094617 | 114.36 | 1125 | 1010.64
11430 | 3.396 | 146.31 | 61.262 | 0.0094639 | 114.37 | 1125 |  | 11430 | 146.31 | 3.396 | 61.262 | 0.0094639 | 114.37 | 1125 | 1010.63
11431 | 3.3968 | 146.32 | 61.262 | 0.0094661 | 114.38 | 1125 |  | 11431 | 146.32 | 3.3968 | 61.262 | 0.0094661 | 114.38 | 1125 | 1010.62
11432 | 3.3977 | 146.33 | 61.262 | 0.0094684 | 114.39 | 1125 |  | 11432 | 146.33 | 3.3977 | 61.262 | 0.0094684 | 114.39 | 1125 | 1010.61
11433 | 3.3985 | 146.34 | 61.261 | 0.0094706 | 114.4 | 1125 |  | 11433 | 146.34 | 3.3985 | 61.261 | 0.0094706 | 114.4 | 1125 | 1010.6
11434 | 3.3994 | 146.35 | 61.261 | 0.0094728 | 114.41 | 1125 |  | 11434 | 146.35 | 3.3994 | 61.261 | 0.0094728 | 114.41 | 1125 | 1010.59
11435 | 3.4003 | 146.36 | 61.261 | 0.0094751 | 114.42 | 1125 |  | 11435 | 146.36 | 3.4003 | 61.261 | 0.0094751 | 114.42 | 1125 | 1010.58
11436 | 3.4011 | 146.37 | 61.261 | 0.0094773 | 114.43 | 1125 |  | 11436 | 146.37 | 3.4011 | 61.261 | 0.0094773 | 114.43 | 1125 | 1010.57
11437 | 3.402 | 146.38 | 61.261 | 0.0094795 | 114.44 | 1125 |  | 11437 | 146.38 | 3.402 | 61.261 | 0.0094795 | 114.44 | 1125 | 1010.56
11438 | 3.4028 | 146.39 | 61.26 | 0.0094818 | 114.45 | 1125 |  | 11438 | 146.39 | 3.4028 | 61.26 | 0.0094818 | 114.45 | 1125 | 1010.55
11439 | 3.4037 | 146.4 | 61.26 | 0.009484 | 114.46 | 1125 |  | 11439 | 146.4 | 3.4037 | 61.26 | 0.009484 | 114.46 | 1125 | 1010.54
11440 | 3.4045 | 146.41 | 61.26 | 0.0094862 | 114.47 | 1125 |  | 11440 | 146.41 | 3.4045 | 61.26 | 0.0094862 | 114.47 | 1125 | 1010.53
11441 | 3.4054 | 146.42 | 61.26 | 0.0094884 | 114.48 | 1125 |  | 11441 | 146.42 | 3.4054 | 61.26 | 0.0094884 | 114.48 | 1125 | 1010.52
11442 | 3.4062 | 146.43 | 61.26 | 0.0094907 | 114.49 | 1125 |  | 11442 | 146.43 | 3.4062 | 61.26 | 0.0094907 | 114.49 | 1125 | 1010.51
11443 | 3.4071 | 146.44 | 61.26 | 0.0094929 | 114.5 | 1125 |  | 11443 | 146.44 | 3.4071 | 61.26 | 0.0094929 | 114.5 | 1125 | 1010.5
11444 | 3.4079 | 146.45 | 61.259 | 0.0094952 | 114.51 | 1125 |  | 11444 | 146.45 | 3.4079 | 61.259 | 0.0094952 | 114.51 | 1125 | 1010.49
11445 | 3.4088 | 146.46 | 61.259 | 0.0094974 | 114.52 | 1125 |  | 11445 | 146.46 | 3.4088 | 61.259 | 0.0094974 | 114.52 | 1125 | 1010.48
11446 | 3.4096 | 146.47 | 61.259 | 0.0094996 | 114.53 | 1125 |  | 11446 | 146.47 | 3.4096 | 61.259 | 0.0094996 | 114.53 | 1125 | 1010.47
11447 | 3.4105 | 146.48 | 61.259 | 0.0095019 | 114.54 | 1125 |  | 11447 | 146.48 | 3.4105 | 61.259 | 0.0095019 | 114.54 | 1125 | 1010.46
11448 | 3.4114 | 146.49 | 61.259 | 0.0095041 | 114.55 | 1125 |  | 11448 | 146.49 | 3.4114 | 61.259 | 0.0095041 | 114.55 | 1125 | 1010.45
11449 | 3.4122 | 146.5 | 61.258 | 0.0095063 | 114.56 | 1125 |  | 11449 | 146.5 | 3.4122 | 61.258 | 0.0095063 | 114.56 | 1125 | 1010.44
11450 | 3.4131 | 146.51 | 61.258 | 0.0095086 | 114.57 | 1125 |  | 11450 | 146.51 | 3.4131 | 61.258 | 0.0095086 | 114.57 | 1125 | 1010.43
11451 | 3.4139 | 146.52 | 61.258 | 0.0095108 | 114.58 | 1125.1 |  | 11451 | 146.52 | 3.4139 | 61.258 | 0.0095108 | 114.58 | 1125.1 | 1010.52
11452 | 3.4148 | 146.53 | 61.258 | 0.009513 | 114.59 | 1125.1 |  | 11452 | 146.53 | 3.4148 | 61.258 | 0.009513 | 114.59 | 1125.1 | 1010.51
11453 | 3.4156 | 146.54 | 61.258 | 0.0095153 | 114.6 | 1125.1 |  | 11453 | 146.54 | 3.4156 | 61.258 | 0.0095153 | 114.6 | 1125.1 | 1010.5
11454 | 3.4165 | 146.55 | 61.257 | 0.0095175 | 114.61 | 1125.1 |  | 11454 | 146.55 | 3.4165 | 61.257 | 0.0095175 | 114.61 | 1125.1 | 1010.49
11455 | 3.4174 | 146.56 | 61.257 | 0.0095198 | 114.62 | 1125.1 |  | 11455 | 146.56 | 3.4174 | 61.257 | 0.0095198 | 114.62 | 1125.1 | 1010.48
11456 | 3.4182 | 146.57 | 61.257 | 0.009522 | 114.63 | 1125.1 |  | 11456 | 146.57 | 3.4182 | 61.257 | 0.009522 | 114.63 | 1125.1 | 1010.47
11457 | 3.4191 | 146.58 | 61.257 | 0.0095242 | 114.64 | 1125.1 |  | 11457 | 146.58 | 3.4191 | 61.257 | 0.0095242 | 114.64 | 1125.1 | 1010.46
11458 | 3.4199 | 146.59 | 61.257 | 0.0095265 | 114.65 | 1125.1 |  | 11458 | 146.59 | 3.4199 | 61.257 | 0.0095265 | 114.65 | 1125.1 | 1010.45
11459 | 3.4208 | 146.6 | 61.257 | 0.0095287 | 114.66 | 1125.1 |  | 11459 | 146.6 | 3.4208 | 61.257 | 0.0095287 | 114.66 | 1125.1 | 1010.44
11460 | 3.4216 | 146.61 | 61.256 | 0.009531 | 114.67 | 1125.1 |  | 11460 | 146.61 | 3.4216 | 61.256 | 0.009531 | 114.67 | 1125.1 | 1010.43
11461 | 3.4225 | 146.62 | 61.256 | 0.0095332 | 114.68 | 1125.1 |  | 11461 | 146.62 | 3.4225 | 61.256 | 0.0095332 | 114.68 | 1125.1 | 1010.42
11462 | 3.4234 | 146.63 | 61.256 | 0.0095355 | 114.69 | 1125.1 |  | 11462 | 146.63 | 3.4234 | 61.256 | 0.0095355 | 114.69 | 1125.1 | 1010.41
11463 | 3.4242 | 146.64 | 61.256 | 0.0095377 | 114.7 | 1125.1 |  | 11463 | 146.64 | 3.4242 | 61.256 | 0.0095377 | 114.7 | 1125.1 | 1010.4
11464 | 3.4251 | 146.65 | 61.256 | 0.0095399 | 114.71 | 1125.1 |  | 11464 | 146.65 | 3.4251 | 61.256 | 0.0095399 | 114.71 | 1125.1 | 1010.39
11465 | 3.4259 | 146.66 | 61.255 | 0.0095422 | 114.72 | 1125.1 |  | 11465 | 146.66 | 3.4259 | 61.255 | 0.0095422 | 114.72 | 1125.1 | 1010.38
11466 | 3.4268 | 146.67 | 61.255 | 0.0095444 | 114.73 | 1125.1 |  | 11466 | 146.67 | 3.4268 | 61.255 | 0.0095444 | 114.73 | 1125.1 | 1010.37
11467 | 3.4277 | 146.68 | 61.255 | 0.0095467 | 114.74 | 1125.1 |  | 11467 | 146.68 | 3.4277 | 61.255 | 0.0095467 | 114.74 | 1125.1 | 1010.36
11468 | 3.4285 | 146.69 | 61.255 | 0.0095489 | 114.75 | 1125.1 |  | 11468 | 146.69 | 3.4285 | 61.255 | 0.0095489 | 114.75 | 1125.1 | 1010.35
11469 | 3.4294 | 146.7 | 61.255 | 0.0095512 | 114.76 | 1125.1 |  | 11469 | 146.7 | 3.4294 | 61.255 | 0.0095512 | 114.76 | 1125.1 | 1010.34
11470 | 3.4302 | 146.71 | 61.255 | 0.0095534 | 114.77 | 1125.1 |  | 11470 | 146.71 | 3.4302 | 61.255 | 0.0095534 | 114.77 | 1125.1 | 1010.33
11471 | 3.4311 | 146.72 | 61.254 | 0.0095557 | 114.78 | 1125.1 |  | 11471 | 146.72 | 3.4311 | 61.254 | 0.0095557 | 114.78 | 1125.1 | 1010.32
11472 | 3.4319 | 146.73 | 61.254 | 0.0095579 | 114.79 | 1125.1 |  | 11472 | 146.73 | 3.4319 | 61.254 | 0.0095579 | 114.79 | 1125.1 | 1010.31
11473 | 3.4328 | 146.74 | 61.254 | 0.0095601 | 114.8 | 1125.1 |  | 11473 | 146.74 | 3.4328 | 61.254 | 0.0095601 | 114.8 | 1125.1 | 1010.3
11474 | 3.4337 | 146.75 | 61.254 | 0.0095624 | 114.81 | 1125.1 |  | 11474 | 146.75 | 3.4337 | 61.254 | 0.0095624 | 114.81 | 1125.1 | 1010.29
11475 | 3.4345 | 146.76 | 61.254 | 0.0095646 | 114.82 | 1125.2 |  | 11475 | 146.76 | 3.4345 | 61.254 | 0.0095646 | 114.82 | 1125.2 | 1010.38
11476 | 3.4354 | 146.77 | 61.253 | 0.0095669 | 114.83 | 1125.2 |  | 11476 | 146.77 | 3.4354 | 61.253 | 0.0095669 | 114.83 | 1125.2 | 1010.37
11477 | 3.4363 | 146.78 | 61.253 | 0.0095691 | 114.84 | 1125.2 |  | 11477 | 146.78 | 3.4363 | 61.253 | 0.0095691 | 114.84 | 1125.2 | 1010.36
11478 | 3.4371 | 146.79 | 61.253 | 0.0095714 | 114.85 | 1125.2 |  | 11478 | 146.79 | 3.4371 | 61.253 | 0.0095714 | 114.85 | 1125.2 | 1010.35
11479 | 3.438 | 146.8 | 61.253 | 0.0095736 | 114.86 | 1125.2 |  | 11479 | 146.8 | 3.438 | 61.253 | 0.0095736 | 114.86 | 1125.2 | 1010.34
11480 | 3.4388 | 146.81 | 61.253 | 0.0095759 | 114.87 | 1125.2 |  | 11480 | 146.81 | 3.4388 | 61.253 | 0.0095759 | 114.87 | 1125.2 | 1010.33
11481 | 3.4397 | 146.82 | 61.252 | 0.0095781 | 114.88 | 1125.2 |  | 11481 | 146.82 | 3.4397 | 61.252 | 0.0095781 | 114.88 | 1125.2 | 1010.32
11482 | 3.4406 | 146.83 | 61.252 | 0.0095804 | 114.89 | 1125.2 |  | 11482 | 146.83 | 3.4406 | 61.252 | 0.0095804 | 114.89 | 1125.2 | 1010.31
11483 | 3.4414 | 146.84 | 61.252 | 0.0095826 | 114.91 | 1125.2 |  | 11483 | 146.84 | 3.4414 | 61.252 | 0.0095826 | 114.91 | 1125.2 | 1010.29
11484 | 3.4423 | 146.85 | 61.252 | 0.0095849 | 114.92 | 1125.2 |  | 11484 | 146.85 | 3.4423 | 61.252 | 0.0095849 | 114.92 | 1125.2 | 1010.28
11485 | 3.4431 | 146.86 | 61.252 | 0.0095872 | 114.93 | 1125.2 |  | 11485 | 146.86 | 3.4431 | 61.252 | 0.0095872 | 114.93 | 1125.2 | 1010.27
11486 | 3.444 | 146.87 | 61.252 | 0.0095894 | 114.94 | 1125.2 |  | 11486 | 146.87 | 3.444 | 61.252 | 0.0095894 | 114.94 | 1125.2 | 1010.26
11487 | 3.4449 | 146.88 | 61.251 | 0.0095917 | 114.95 | 1125.2 |  | 11487 | 146.88 | 3.4449 | 61.251 | 0.0095917 | 114.95 | 1125.2 | 1010.25
11488 | 3.4457 | 146.89 | 61.251 | 0.0095939 | 114.96 | 1125.2 |  | 11488 | 146.89 | 3.4457 | 61.251 | 0.0095939 | 114.96 | 1125.2 | 1010.24
11489 | 3.4466 | 146.9 | 61.251 | 0.0095962 | 114.97 | 1125.2 |  | 11489 | 146.9 | 3.4466 | 61.251 | 0.0095962 | 114.97 | 1125.2 | 1010.23
11490 | 3.4475 | 146.91 | 61.251 | 0.0095984 | 114.98 | 1125.2 |  | 11490 | 146.91 | 3.4475 | 61.251 | 0.0095984 | 114.98 | 1125.2 | 1010.22
11491 | 3.4483 | 146.92 | 61.251 | 0.0096007 | 114.99 | 1125.2 |  | 11491 | 146.92 | 3.4483 | 61.251 | 0.0096007 | 114.99 | 1125.2 | 1010.21
11492 | 3.4492 | 146.93 | 61.25 | 0.0096029 | 115 | 1125.2 |  | 11492 | 146.93 | 3.4492 | 61.25 | 0.0096029 | 115 | 1125.2 | 1010.2
11493 | 3.4501 | 146.94 | 61.25 | 0.0096052 | 115.01 | 1125.2 |  | 11493 | 146.94 | 3.4501 | 61.25 | 0.0096052 | 115.01 | 1125.2 | 1010.19
11494 | 3.4509 | 146.95 | 61.25 | 0.0096074 | 115.02 | 1125.2 |  | 11494 | 146.95 | 3.4509 | 61.25 | 0.0096074 | 115.02 | 1125.2 | 1010.18
11495 | 3.4518 | 146.96 | 61.25 | 0.0096097 | 115.03 | 1125.2 |  | 11495 | 146.96 | 3.4518 | 61.25 | 0.0096097 | 115.03 | 1125.2 | 1010.17
11496 | 3.4526 | 146.97 | 61.25 | 0.009612 | 115.04 | 1125.2 |  | 11496 | 146.97 | 3.4526 | 61.25 | 0.009612 | 115.04 | 1125.2 | 1010.16
11497 | 3.4535 | 146.98 | 61.25 | 0.0096142 | 115.05 | 1125.2 |  | 11497 | 146.98 | 3.4535 | 61.25 | 0.0096142 | 115.05 | 1125.2 | 1010.15
11498 | 3.4544 | 146.99 | 61.249 | 0.0096165 | 115.06 | 1125.2 |  | 11498 | 146.99 | 3.4544 | 61.249 | 0.0096165 | 115.06 | 1125.2 | 1010.14
11499 | 3.4552 | 147 | 61.249 | 0.0096187 | 115.07 | 1125.3 |  | 11499 | 147 | 3.4552 | 61.249 | 0.0096187 | 115.07 | 1125.3 | 1010.23
11500 | 3.4561 | 147.01 | 61.249 | 0.009621 | 115.08 | 1125.3 |  | 11500 | 147.01 | 3.4561 | 61.249 | 0.009621 | 115.08 | 1125.3 | 1010.22
11501 | 3.457 | 147.02 | 61.249 | 0.0096233 | 115.09 | 1125.3 |  | 11501 | 147.02 | 3.457 | 61.249 | 0.0096233 | 115.09 | 1125.3 | 1010.21
11502 | 3.4578 | 147.03 | 61.249 | 0.0096255 | 115.1 | 1125.3 |  | 11502 | 147.03 | 3.4578 | 61.249 | 0.0096255 | 115.1 | 1125.3 | 1010.2
11503 | 3.4587 | 147.04 | 61.248 | 0.0096278 | 115.11 | 1125.3 |  | 11503 | 147.04 | 3.4587 | 61.248 | 0.0096278 | 115.11 | 1125.3 | 1010.19
11504 | 3.4596 | 147.05 | 61.248 | 0.00963 | 115.12 | 1125.3 |  | 11504 | 147.05 | 3.4596 | 61.248 | 0.00963 | 115.12 | 1125.3 | 1010.18
11505 | 3.4604 | 147.06 | 61.248 | 0.0096323 | 115.13 | 1125.3 |  | 11505 | 147.06 | 3.4604 | 61.248 | 0.0096323 | 115.13 | 1125.3 | 1010.17
11506 | 3.4613 | 147.07 | 61.248 | 0.0096346 | 115.14 | 1125.3 |  | 11506 | 147.07 | 3.4613 | 61.248 | 0.0096346 | 115.14 | 1125.3 | 1010.16
11507 | 3.4622 | 147.08 | 61.248 | 0.0096368 | 115.15 | 1125.3 |  | 11507 | 147.08 | 3.4622 | 61.248 | 0.0096368 | 115.15 | 1125.3 | 1010.15
11508 | 3.463 | 147.09 | 61.247 | 0.0096391 | 115.16 | 1125.3 |  | 11508 | 147.09 | 3.463 | 61.247 | 0.0096391 | 115.16 | 1125.3 | 1010.14
11509 | 3.4639 | 147.1 | 61.247 | 0.0096413 | 115.17 | 1125.3 |  | 11509 | 147.1 | 3.4639 | 61.247 | 0.0096413 | 115.17 | 1125.3 | 1010.13
11510 | 3.4648 | 147.11 | 61.247 | 0.0096436 | 115.18 | 1125.3 |  | 11510 | 147.11 | 3.4648 | 61.247 | 0.0096436 | 115.18 | 1125.3 | 1010.12
11511 | 3.4656 | 147.12 | 61.247 | 0.0096459 | 115.19 | 1125.3 |  | 11511 | 147.12 | 3.4656 | 61.247 | 0.0096459 | 115.19 | 1125.3 | 1010.11
11512 | 3.4665 | 147.13 | 61.247 | 0.0096481 | 115.2 | 1125.3 |  | 11512 | 147.13 | 3.4665 | 61.247 | 0.0096481 | 115.2 | 1125.3 | 1010.1
11513 | 3.4674 | 147.14 | 61.247 | 0.0096504 | 115.21 | 1125.3 |  | 11513 | 147.14 | 3.4674 | 61.247 | 0.0096504 | 115.21 | 1125.3 | 1010.09
11514 | 3.4682 | 147.15 | 61.246 | 0.0096527 | 115.22 | 1125.3 |  | 11514 | 147.15 | 3.4682 | 61.246 | 0.0096527 | 115.22 | 1125.3 | 1010.08
11515 | 3.4691 | 147.16 | 61.246 | 0.0096549 | 115.23 | 1125.3 |  | 11515 | 147.16 | 3.4691 | 61.246 | 0.0096549 | 115.23 | 1125.3 | 1010.07
11516 | 3.47 | 147.17 | 61.246 | 0.0096572 | 115.24 | 1125.3 |  | 11516 | 147.17 | 3.47 | 61.246 | 0.0096572 | 115.24 | 1125.3 | 1010.06
11517 | 3.4708 | 147.18 | 61.246 | 0.0096595 | 115.25 | 1125.3 |  | 11517 | 147.18 | 3.4708 | 61.246 | 0.0096595 | 115.25 | 1125.3 | 1010.05
11518 | 3.4717 | 147.19 | 61.246 | 0.0096617 | 115.26 | 1125.3 |  | 11518 | 147.19 | 3.4717 | 61.246 | 0.0096617 | 115.26 | 1125.3 | 1010.04
11519 | 3.4726 | 147.2 | 61.245 | 0.009664 | 115.27 | 1125.3 |  | 11519 | 147.2 | 3.4726 | 61.245 | 0.009664 | 115.27 | 1125.3 | 1010.03
11520 | 3.4734 | 147.21 | 61.245 | 0.0096663 | 115.28 | 1125.3 |  | 11520 | 147.21 | 3.4734 | 61.245 | 0.0096663 | 115.28 | 1125.3 | 1010.02
11521 | 3.4743 | 147.22 | 61.245 | 0.0096685 | 115.29 | 1125.3 |  | 11521 | 147.22 | 3.4743 | 61.245 | 0.0096685 | 115.29 | 1125.3 | 1010.01
11522 | 3.4752 | 147.23 | 61.245 | 0.0096708 | 115.3 | 1125.3 |  | 11522 | 147.23 | 3.4752 | 61.245 | 0.0096708 | 115.3 | 1125.3 | 1010
11523 | 3.4761 | 147.24 | 61.245 | 0.0096731 | 115.31 | 1125.4 |  | 11523 | 147.24 | 3.4761 | 61.245 | 0.0096731 | 115.31 | 1125.4 | 1010.09
11524 | 3.4769 | 147.25 | 61.244 | 0.0096754 | 115.32 | 1125.4 |  | 11524 | 147.25 | 3.4769 | 61.244 | 0.0096754 | 115.32 | 1125.4 | 1010.08
11525 | 3.4778 | 147.26 | 61.244 | 0.0096776 | 115.33 | 1125.4 |  | 11525 | 147.26 | 3.4778 | 61.244 | 0.0096776 | 115.33 | 1125.4 | 1010.07
11526 | 3.4787 | 147.27 | 61.244 | 0.0096799 | 115.34 | 1125.4 |  | 11526 | 147.27 | 3.4787 | 61.244 | 0.0096799 | 115.34 | 1125.4 | 1010.06
11527 | 3.4795 | 147.28 | 61.244 | 0.0096822 | 115.35 | 1125.4 |  | 11527 | 147.28 | 3.4795 | 61.244 | 0.0096822 | 115.35 | 1125.4 | 1010.05
11528 | 3.4804 | 147.29 | 61.244 | 0.0096844 | 115.36 | 1125.4 |  | 11528 | 147.29 | 3.4804 | 61.244 | 0.0096844 | 115.36 | 1125.4 | 1010.04
11529 | 3.4813 | 147.3 | 61.244 | 0.0096867 | 115.37 | 1125.4 |  | 11529 | 147.3 | 3.4813 | 61.244 | 0.0096867 | 115.37 | 1125.4 | 1010.03
11530 | 3.4821 | 147.31 | 61.243 | 0.009689 | 115.38 | 1125.4 |  | 11530 | 147.31 | 3.4821 | 61.243 | 0.009689 | 115.38 | 1125.4 | 1010.02
11531 | 3.483 | 147.32 | 61.243 | 0.0096913 | 115.39 | 1125.4 |  | 11531 | 147.32 | 3.483 | 61.243 | 0.0096913 | 115.39 | 1125.4 | 1010.01
11532 | 3.4839 | 147.33 | 61.243 | 0.0096935 | 115.4 | 1125.4 |  | 11532 | 147.33 | 3.4839 | 61.243 | 0.0096935 | 115.4 | 1125.4 | 1010
11533 | 3.4848 | 147.34 | 61.243 | 0.0096958 | 115.41 | 1125.4 |  | 11533 | 147.34 | 3.4848 | 61.243 | 0.0096958 | 115.41 | 1125.4 | 1009.99
11534 | 3.4856 | 147.35 | 61.243 | 0.0096981 | 115.42 | 1125.4 |  | 11534 | 147.35 | 3.4856 | 61.243 | 0.0096981 | 115.42 | 1125.4 | 1009.98
11535 | 3.4865 | 147.36 | 61.242 | 0.0097004 | 115.43 | 1125.4 |  | 11535 | 147.36 | 3.4865 | 61.242 | 0.0097004 | 115.43 | 1125.4 | 1009.97
11536 | 3.4874 | 147.37 | 61.242 | 0.0097026 | 115.44 | 1125.4 |  | 11536 | 147.37 | 3.4874 | 61.242 | 0.0097026 | 115.44 | 1125.4 | 1009.96
11537 | 3.4882 | 147.38 | 61.242 | 0.0097049 | 115.45 | 1125.4 |  | 11537 | 147.38 | 3.4882 | 61.242 | 0.0097049 | 115.45 | 1125.4 | 1009.95
11538 | 3.4891 | 147.39 | 61.242 | 0.0097072 | 115.46 | 1125.4 |  | 11538 | 147.39 | 3.4891 | 61.242 | 0.0097072 | 115.46 | 1125.4 | 1009.94
11539 | 3.49 | 147.4 | 61.242 | 0.0097095 | 115.47 | 1125.4 |  | 11539 | 147.4 | 3.49 | 61.242 | 0.0097095 | 115.47 | 1125.4 | 1009.93
11540 | 3.4909 | 147.41 | 61.241 | 0.0097117 | 115.48 | 1125.4 |  | 11540 | 147.41 | 3.4909 | 61.241 | 0.0097117 | 115.48 | 1125.4 | 1009.92
11541 | 3.4917 | 147.42 | 61.241 | 0.009714 | 115.49 | 1125.4 |  | 11541 | 147.42 | 3.4917 | 61.241 | 0.009714 | 115.49 | 1125.4 | 1009.91
11542 | 3.4926 | 147.43 | 61.241 | 0.0097163 | 115.5 | 1125.4 |  | 11542 | 147.43 | 3.4926 | 61.241 | 0.0097163 | 115.5 | 1125.4 | 1009.9
11543 | 3.4935 | 147.44 | 61.241 | 0.0097186 | 115.51 | 1125.4 |  | 11543 | 147.44 | 3.4935 | 61.241 | 0.0097186 | 115.51 | 1125.4 | 1009.89
11544 | 3.4944 | 147.45 | 61.241 | 0.0097208 | 115.52 | 1125.4 |  | 11544 | 147.45 | 3.4944 | 61.241 | 0.0097208 | 115.52 | 1125.4 | 1009.88
11545 | 3.4952 | 147.46 | 61.241 | 0.0097231 | 115.53 | 1125.4 |  | 11545 | 147.46 | 3.4952 | 61.241 | 0.0097231 | 115.53 | 1125.4 | 1009.87
11546 | 3.4961 | 147.47 | 61.24 | 0.0097254 | 115.54 | 1125.4 |  | 11546 | 147.47 | 3.4961 | 61.24 | 0.0097254 | 115.54 | 1125.4 | 1009.86
11547 | 3.497 | 147.48 | 61.24 | 0.0097277 | 115.55 | 1125.4 |  | 11547 | 147.48 | 3.497 | 61.24 | 0.0097277 | 115.55 | 1125.4 | 1009.85
11548 | 3.4979 | 147.49 | 61.24 | 0.00973 | 115.56 | 1125.5 |  | 11548 | 147.49 | 3.4979 | 61.24 | 0.00973 | 115.56 | 1125.5 | 1009.94
11549 | 3.4987 | 147.5 | 61.24 | 0.0097322 | 115.57 | 1125.5 |  | 11549 | 147.5 | 3.4987 | 61.24 | 0.0097322 | 115.57 | 1125.5 | 1009.93
11550 | 3.4996 | 147.51 | 61.24 | 0.0097345 | 115.58 | 1125.5 |  | 11550 | 147.51 | 3.4996 | 61.24 | 0.0097345 | 115.58 | 1125.5 | 1009.92
11551 | 3.5005 | 147.52 | 61.239 | 0.0097368 | 115.59 | 1125.5 |  | 11551 | 147.52 | 3.5005 | 61.239 | 0.0097368 | 115.59 | 1125.5 | 1009.91
11552 | 3.5013 | 147.53 | 61.239 | 0.0097391 | 115.6 | 1125.5 |  | 11552 | 147.53 | 3.5013 | 61.239 | 0.0097391 | 115.6 | 1125.5 | 1009.9
11553 | 3.5022 | 147.54 | 61.239 | 0.0097414 | 115.61 | 1125.5 |  | 11553 | 147.54 | 3.5022 | 61.239 | 0.0097414 | 115.61 | 1125.5 | 1009.89
11554 | 3.5031 | 147.55 | 61.239 | 0.0097437 | 115.62 | 1125.5 |  | 11554 | 147.55 | 3.5031 | 61.239 | 0.0097437 | 115.62 | 1125.5 | 1009.88
11555 | 3.504 | 147.56 | 61.239 | 0.0097459 | 115.63 | 1125.5 |  | 11555 | 147.56 | 3.504 | 61.239 | 0.0097459 | 115.63 | 1125.5 | 1009.87
11556 | 3.5048 | 147.57 | 61.239 | 0.0097482 | 115.64 | 1125.5 |  | 11556 | 147.57 | 3.5048 | 61.239 | 0.0097482 | 115.64 | 1125.5 | 1009.86
11557 | 3.5057 | 147.58 | 61.238 | 0.0097505 | 115.65 | 1125.5 |  | 11557 | 147.58 | 3.5057 | 61.238 | 0.0097505 | 115.65 | 1125.5 | 1009.85
11558 | 3.5066 | 147.59 | 61.238 | 0.0097528 | 115.66 | 1125.5 |  | 11558 | 147.59 | 3.5066 | 61.238 | 0.0097528 | 115.66 | 1125.5 | 1009.84
11559 | 3.5075 | 147.6 | 61.238 | 0.0097551 | 115.67 | 1125.5 |  | 11559 | 147.6 | 3.5075 | 61.238 | 0.0097551 | 115.67 | 1125.5 | 1009.83
11560 | 3.5084 | 147.61 | 61.238 | 0.0097574 | 115.68 | 1125.5 |  | 11560 | 147.61 | 3.5084 | 61.238 | 0.0097574 | 115.68 | 1125.5 | 1009.82
11561 | 3.5092 | 147.62 | 61.238 | 0.0097597 | 115.69 | 1125.5 |  | 11561 | 147.62 | 3.5092 | 61.238 | 0.0097597 | 115.69 | 1125.5 | 1009.81
11562 | 3.5101 | 147.63 | 61.237 | 0.0097619 | 115.7 | 1125.5 |  | 11562 | 147.63 | 3.5101 | 61.237 | 0.0097619 | 115.7 | 1125.5 | 1009.8
11563 | 3.511 | 147.64 | 61.237 | 0.0097642 | 115.71 | 1125.5 |  | 11563 | 147.64 | 3.511 | 61.237 | 0.0097642 | 115.71 | 1125.5 | 1009.79
11564 | 3.5119 | 147.65 | 61.237 | 0.0097665 | 115.72 | 1125.5 |  | 11564 | 147.65 | 3.5119 | 61.237 | 0.0097665 | 115.72 | 1125.5 | 1009.78
11565 | 3.5127 | 147.66 | 61.237 | 0.0097688 | 115.73 | 1125.5 |  | 11565 | 147.66 | 3.5127 | 61.237 | 0.0097688 | 115.73 | 1125.5 | 1009.77
11566 | 3.5136 | 147.67 | 61.237 | 0.0097711 | 115.74 | 1125.5 |  | 11566 | 147.67 | 3.5136 | 61.237 | 0.0097711 | 115.74 | 1125.5 | 1009.76
11567 | 3.5145 | 147.68 | 61.236 | 0.0097734 | 115.75 | 1125.5 |  | 11567 | 147.68 | 3.5145 | 61.236 | 0.0097734 | 115.75 | 1125.5 | 1009.75
11568 | 3.5154 | 147.69 | 61.236 | 0.0097757 | 115.76 | 1125.5 |  | 11568 | 147.69 | 3.5154 | 61.236 | 0.0097757 | 115.76 | 1125.5 | 1009.74
11569 | 3.5162 | 147.7 | 61.236 | 0.009778 | 115.77 | 1125.5 |  | 11569 | 147.7 | 3.5162 | 61.236 | 0.009778 | 115.77 | 1125.5 | 1009.73
11570 | 3.5171 | 147.71 | 61.236 | 0.0097803 | 115.78 | 1125.5 |  | 11570 | 147.71 | 3.5171 | 61.236 | 0.0097803 | 115.78 | 1125.5 | 1009.72
11571 | 3.518 | 147.72 | 61.236 | 0.0097825 | 115.79 | 1125.5 |  | 11571 | 147.72 | 3.518 | 61.236 | 0.0097825 | 115.79 | 1125.5 | 1009.71
11572 | 3.5189 | 147.73 | 61.236 | 0.0097848 | 115.8 | 1125.6 |  | 11572 | 147.73 | 3.5189 | 61.236 | 0.0097848 | 115.8 | 1125.6 | 1009.8
11573 | 3.5198 | 147.74 | 61.235 | 0.0097871 | 115.81 | 1125.6 |  | 11573 | 147.74 | 3.5198 | 61.235 | 0.0097871 | 115.81 | 1125.6 | 1009.79
11574 | 3.5206 | 147.75 | 61.235 | 0.0097894 | 115.82 | 1125.6 |  | 11574 | 147.75 | 3.5206 | 61.235 | 0.0097894 | 115.82 | 1125.6 | 1009.78
11575 | 3.5215 | 147.76 | 61.235 | 0.0097917 | 115.83 | 1125.6 |  | 11575 | 147.76 | 3.5215 | 61.235 | 0.0097917 | 115.83 | 1125.6 | 1009.77
11576 | 3.5224 | 147.77 | 61.235 | 0.009794 | 115.84 | 1125.6 |  | 11576 | 147.77 | 3.5224 | 61.235 | 0.009794 | 115.84 | 1125.6 | 1009.76
11577 | 3.5233 | 147.78 | 61.235 | 0.0097963 | 115.85 | 1125.6 |  | 11577 | 147.78 | 3.5233 | 61.235 | 0.0097963 | 115.85 | 1125.6 | 1009.75
11578 | 3.5242 | 147.79 | 61.234 | 0.0097986 | 115.86 | 1125.6 |  | 11578 | 147.79 | 3.5242 | 61.234 | 0.0097986 | 115.86 | 1125.6 | 1009.74
11579 | 3.525 | 147.8 | 61.234 | 0.0098009 | 115.87 | 1125.6 |  | 11579 | 147.8 | 3.525 | 61.234 | 0.0098009 | 115.87 | 1125.6 | 1009.73
11580 | 3.5259 | 147.81 | 61.234 | 0.0098032 | 115.88 | 1125.6 |  | 11580 | 147.81 | 3.5259 | 61.234 | 0.0098032 | 115.88 | 1125.6 | 1009.72
11581 | 3.5268 | 147.82 | 61.234 | 0.0098055 | 115.89 | 1125.6 |  | 11581 | 147.82 | 3.5268 | 61.234 | 0.0098055 | 115.89 | 1125.6 | 1009.71
11582 | 3.5277 | 147.83 | 61.234 | 0.0098078 | 115.9 | 1125.6 |  | 11582 | 147.83 | 3.5277 | 61.234 | 0.0098078 | 115.9 | 1125.6 | 1009.7
11583 | 3.5286 | 147.84 | 61.233 | 0.0098101 | 115.91 | 1125.6 |  | 11583 | 147.84 | 3.5286 | 61.233 | 0.0098101 | 115.91 | 1125.6 | 1009.69
11584 | 3.5294 | 147.85 | 61.233 | 0.0098124 | 115.92 | 1125.6 |  | 11584 | 147.85 | 3.5294 | 61.233 | 0.0098124 | 115.92 | 1125.6 | 1009.68
11585 | 3.5303 | 147.86 | 61.233 | 0.0098147 | 115.93 | 1125.6 |  | 11585 | 147.86 | 3.5303 | 61.233 | 0.0098147 | 115.93 | 1125.6 | 1009.67
11586 | 3.5312 | 147.87 | 61.233 | 0.009817 | 115.94 | 1125.6 |  | 11586 | 147.87 | 3.5312 | 61.233 | 0.009817 | 115.94 | 1125.6 | 1009.66
11587 | 3.5321 | 147.88 | 61.233 | 0.0098193 | 115.95 | 1125.6 |  | 11587 | 147.88 | 3.5321 | 61.233 | 0.0098193 | 115.95 | 1125.6 | 1009.65
11588 | 3.533 | 147.89 | 61.233 | 0.0098216 | 115.96 | 1125.6 |  | 11588 | 147.89 | 3.533 | 61.233 | 0.0098216 | 115.96 | 1125.6 | 1009.64
11589 | 3.5338 | 147.9 | 61.232 | 0.0098239 | 115.97 | 1125.6 |  | 11589 | 147.9 | 3.5338 | 61.232 | 0.0098239 | 115.97 | 1125.6 | 1009.63
11590 | 3.5347 | 147.91 | 61.232 | 0.0098262 | 115.98 | 1125.6 |  | 11590 | 147.91 | 3.5347 | 61.232 | 0.0098262 | 115.98 | 1125.6 | 1009.62
11591 | 3.5356 | 147.92 | 61.232 | 0.0098285 | 115.99 | 1125.6 |  | 11591 | 147.92 | 3.5356 | 61.232 | 0.0098285 | 115.99 | 1125.6 | 1009.61
11592 | 3.5365 | 147.93 | 61.232 | 0.0098308 | 116 | 1125.6 |  | 11592 | 147.93 | 3.5365 | 61.232 | 0.0098308 | 116 | 1125.6 | 1009.6
11593 | 3.5374 | 147.94 | 61.232 | 0.0098331 | 116.01 | 1125.6 |  | 11593 | 147.94 | 3.5374 | 61.232 | 0.0098331 | 116.01 | 1125.6 | 1009.59
11594 | 3.5383 | 147.95 | 61.231 | 0.0098354 | 116.02 | 1125.6 |  | 11594 | 147.95 | 3.5383 | 61.231 | 0.0098354 | 116.02 | 1125.6 | 1009.58
11595 | 3.5391 | 147.96 | 61.231 | 0.0098377 | 116.03 | 1125.6 |  | 11595 | 147.96 | 3.5391 | 61.231 | 0.0098377 | 116.03 | 1125.6 | 1009.57
11596 | 3.54 | 147.97 | 61.231 | 0.00984 | 116.04 | 1125.7 |  | 11596 | 147.97 | 3.54 | 61.231 | 0.00984 | 116.04 | 1125.7 | 1009.66
11597 | 3.5409 | 147.98 | 61.231 | 0.0098423 | 116.05 | 1125.7 |  | 11597 | 147.98 | 3.5409 | 61.231 | 0.0098423 | 116.05 | 1125.7 | 1009.65
11598 | 3.5418 | 147.99 | 61.231 | 0.0098446 | 116.06 | 1125.7 |  | 11598 | 147.99 | 3.5418 | 61.231 | 0.0098446 | 116.06 | 1125.7 | 1009.64
11599 | 3.5427 | 148 | 61.23 | 0.0098469 | 116.07 | 1125.7 |  | 11599 | 148 | 3.5427 | 61.23 | 0.0098469 | 116.07 | 1125.7 | 1009.63
11600 | 3.5436 | 148.01 | 61.23 | 0.0098492 | 116.08 | 1125.7 |  | 11600 | 148.01 | 3.5436 | 61.23 | 0.0098492 | 116.08 | 1125.7 | 1009.62
11601 | 3.5444 | 148.02 | 61.23 | 0.0098515 | 116.09 | 1125.7 |  | 11601 | 148.02 | 3.5444 | 61.23 | 0.0098515 | 116.09 | 1125.7 | 1009.61
11602 | 3.5453 | 148.03 | 61.23 | 0.0098538 | 116.1 | 1125.7 |  | 11602 | 148.03 | 3.5453 | 61.23 | 0.0098538 | 116.1 | 1125.7 | 1009.6
11603 | 3.5462 | 148.04 | 61.23 | 0.0098561 | 116.11 | 1125.7 |  | 11603 | 148.04 | 3.5462 | 61.23 | 0.0098561 | 116.11 | 1125.7 | 1009.59
11604 | 3.5471 | 148.05 | 61.23 | 0.0098584 | 116.12 | 1125.7 |  | 11604 | 148.05 | 3.5471 | 61.23 | 0.0098584 | 116.12 | 1125.7 | 1009.58
11605 | 3.548 | 148.06 | 61.229 | 0.0098607 | 116.13 | 1125.7 |  | 11605 | 148.06 | 3.548 | 61.229 | 0.0098607 | 116.13 | 1125.7 | 1009.57
11606 | 3.5489 | 148.07 | 61.229 | 0.009863 | 116.14 | 1125.7 |  | 11606 | 148.07 | 3.5489 | 61.229 | 0.009863 | 116.14 | 1125.7 | 1009.56
11607 | 3.5497 | 148.08 | 61.229 | 0.0098653 | 116.15 | 1125.7 |  | 11607 | 148.08 | 3.5497 | 61.229 | 0.0098653 | 116.15 | 1125.7 | 1009.55
11608 | 3.5506 | 148.09 | 61.229 | 0.0098676 | 116.16 | 1125.7 |  | 11608 | 148.09 | 3.5506 | 61.229 | 0.0098676 | 116.16 | 1125.7 | 1009.54
11609 | 3.5515 | 148.1 | 61.229 | 0.0098699 | 116.17 | 1125.7 |  | 11609 | 148.1 | 3.5515 | 61.229 | 0.0098699 | 116.17 | 1125.7 | 1009.53
11610 | 3.5524 | 148.11 | 61.228 | 0.0098722 | 116.18 | 1125.7 |  | 11610 | 148.11 | 3.5524 | 61.228 | 0.0098722 | 116.18 | 1125.7 | 1009.52
11611 | 3.5533 | 148.12 | 61.228 | 0.0098746 | 116.19 | 1125.7 |  | 11611 | 148.12 | 3.5533 | 61.228 | 0.0098746 | 116.19 | 1125.7 | 1009.51
11612 | 3.5542 | 148.13 | 61.228 | 0.0098769 | 116.2 | 1125.7 |  | 11612 | 148.13 | 3.5542 | 61.228 | 0.0098769 | 116.2 | 1125.7 | 1009.5
11613 | 3.5551 | 148.14 | 61.228 | 0.0098792 | 116.21 | 1125.7 |  | 11613 | 148.14 | 3.5551 | 61.228 | 0.0098792 | 116.21 | 1125.7 | 1009.49
11614 | 3.5559 | 148.15 | 61.228 | 0.0098815 | 116.22 | 1125.7 |  | 11614 | 148.15 | 3.5559 | 61.228 | 0.0098815 | 116.22 | 1125.7 | 1009.48
11615 | 3.5568 | 148.16 | 61.227 | 0.0098838 | 116.23 | 1125.7 |  | 11615 | 148.16 | 3.5568 | 61.227 | 0.0098838 | 116.23 | 1125.7 | 1009.47
11616 | 3.5577 | 148.17 | 61.227 | 0.0098861 | 116.24 | 1125.7 |  | 11616 | 148.17 | 3.5577 | 61.227 | 0.0098861 | 116.24 | 1125.7 | 1009.46
11617 | 3.5586 | 148.18 | 61.227 | 0.0098884 | 116.25 | 1125.7 |  | 11617 | 148.18 | 3.5586 | 61.227 | 0.0098884 | 116.25 | 1125.7 | 1009.45
11618 | 3.5595 | 148.19 | 61.227 | 0.0098907 | 116.26 | 1125.7 |  | 11618 | 148.19 | 3.5595 | 61.227 | 0.0098907 | 116.26 | 1125.7 | 1009.44
11619 | 3.5604 | 148.2 | 61.227 | 0.009893 | 116.27 | 1125.7 |  | 11619 | 148.2 | 3.5604 | 61.227 | 0.009893 | 116.27 | 1125.7 | 1009.43
11620 | 3.5613 | 148.21 | 61.227 | 0.0098954 | 116.28 | 1125.8 |  | 11620 | 148.21 | 3.5613 | 61.227 | 0.0098954 | 116.28 | 1125.8 | 1009.52
11621 | 3.5622 | 148.22 | 61.226 | 0.0098977 | 116.29 | 1125.8 |  | 11621 | 148.22 | 3.5622 | 61.226 | 0.0098977 | 116.29 | 1125.8 | 1009.51
11622 | 3.563 | 148.23 | 61.226 | 0.0099 | 116.3 | 1125.8 |  | 11622 | 148.23 | 3.563 | 61.226 | 0.0099 | 116.3 | 1125.8 | 1009.5
11623 | 3.5639 | 148.24 | 61.226 | 0.0099023 | 116.31 | 1125.8 |  | 11623 | 148.24 | 3.5639 | 61.226 | 0.0099023 | 116.31 | 1125.8 | 1009.49
11624 | 3.5648 | 148.25 | 61.226 | 0.0099046 | 116.32 | 1125.8 |  | 11624 | 148.25 | 3.5648 | 61.226 | 0.0099046 | 116.32 | 1125.8 | 1009.48
11625 | 3.5657 | 148.26 | 61.226 | 0.0099069 | 116.33 | 1125.8 |  | 11625 | 148.26 | 3.5657 | 61.226 | 0.0099069 | 116.33 | 1125.8 | 1009.47
11626 | 3.5666 | 148.27 | 61.225 | 0.0099092 | 116.34 | 1125.8 |  | 11626 | 148.27 | 3.5666 | 61.225 | 0.0099092 | 116.34 | 1125.8 | 1009.46
11627 | 3.5675 | 148.28 | 61.225 | 0.0099116 | 116.35 | 1125.8 |  | 11627 | 148.28 | 3.5675 | 61.225 | 0.0099116 | 116.35 | 1125.8 | 1009.45
11628 | 3.5684 | 148.29 | 61.225 | 0.0099139 | 116.36 | 1125.8 |  | 11628 | 148.29 | 3.5684 | 61.225 | 0.0099139 | 116.36 | 1125.8 | 1009.44
11629 | 3.5693 | 148.3 | 61.225 | 0.0099162 | 116.37 | 1125.8 |  | 11629 | 148.3 | 3.5693 | 61.225 | 0.0099162 | 116.37 | 1125.8 | 1009.43
11630 | 3.5702 | 148.31 | 61.225 | 0.0099185 | 116.38 | 1125.8 |  | 11630 | 148.31 | 3.5702 | 61.225 | 0.0099185 | 116.38 | 1125.8 | 1009.42
11631 | 3.571 | 148.32 | 61.224 | 0.0099208 | 116.39 | 1125.8 |  | 11631 | 148.32 | 3.571 | 61.224 | 0.0099208 | 116.39 | 1125.8 | 1009.41
11632 | 3.5719 | 148.33 | 61.224 | 0.0099231 | 116.4 | 1125.8 |  | 11632 | 148.33 | 3.5719 | 61.224 | 0.0099231 | 116.4 | 1125.8 | 1009.4
11633 | 3.5728 | 148.34 | 61.224 | 0.0099255 | 116.41 | 1125.8 |  | 11633 | 148.34 | 3.5728 | 61.224 | 0.0099255 | 116.41 | 1125.8 | 1009.39
11634 | 3.5737 | 148.35 | 61.224 | 0.0099278 | 116.42 | 1125.8 |  | 11634 | 148.35 | 3.5737 | 61.224 | 0.0099278 | 116.42 | 1125.8 | 1009.38
11635 | 3.5746 | 148.36 | 61.224 | 0.0099301 | 116.43 | 1125.8 |  | 11635 | 148.36 | 3.5746 | 61.224 | 0.0099301 | 116.43 | 1125.8 | 1009.37
11636 | 3.5755 | 148.37 | 61.224 | 0.0099324 | 116.44 | 1125.8 |  | 11636 | 148.37 | 3.5755 | 61.224 | 0.0099324 | 116.44 | 1125.8 | 1009.36
11637 | 3.5764 | 148.38 | 61.223 | 0.0099347 | 116.45 | 1125.8 |  | 11637 | 148.38 | 3.5764 | 61.223 | 0.0099347 | 116.45 | 1125.8 | 1009.35
11638 | 3.5773 | 148.39 | 61.223 | 0.0099371 | 116.46 | 1125.8 |  | 11638 | 148.39 | 3.5773 | 61.223 | 0.0099371 | 116.46 | 1125.8 | 1009.34
11639 | 3.5782 | 148.4 | 61.223 | 0.0099394 | 116.47 | 1125.8 |  | 11639 | 148.4 | 3.5782 | 61.223 | 0.0099394 | 116.47 | 1125.8 | 1009.33
11640 | 3.5791 | 148.41 | 61.223 | 0.0099417 | 116.48 | 1125.8 |  | 11640 | 148.41 | 3.5791 | 61.223 | 0.0099417 | 116.48 | 1125.8 | 1009.32
11641 | 3.58 | 148.42 | 61.223 | 0.009944 | 116.49 | 1125.8 |  | 11641 | 148.42 | 3.58 | 61.223 | 0.009944 | 116.49 | 1125.8 | 1009.31
11642 | 3.5808 | 148.43 | 61.222 | 0.0099464 | 116.5 | 1125.8 |  | 11642 | 148.43 | 3.5808 | 61.222 | 0.0099464 | 116.5 | 1125.8 | 1009.3
11643 | 3.5817 | 148.44 | 61.222 | 0.0099487 | 116.51 | 1125.8 |  | 11643 | 148.44 | 3.5817 | 61.222 | 0.0099487 | 116.51 | 1125.8 | 1009.29
11644 | 3.5826 | 148.45 | 61.222 | 0.009951 | 116.52 | 1125.9 |  | 11644 | 148.45 | 3.5826 | 61.222 | 0.009951 | 116.52 | 1125.9 | 1009.38
11645 | 3.5835 | 148.46 | 61.222 | 0.0099533 | 116.53 | 1125.9 |  | 11645 | 148.46 | 3.5835 | 61.222 | 0.0099533 | 116.53 | 1125.9 | 1009.37
11646 | 3.5844 | 148.47 | 61.222 | 0.0099557 | 116.54 | 1125.9 |  | 11646 | 148.47 | 3.5844 | 61.222 | 0.0099557 | 116.54 | 1125.9 | 1009.36
11647 | 3.5853 | 148.48 | 61.221 | 0.009958 | 116.55 | 1125.9 |  | 11647 | 148.48 | 3.5853 | 61.221 | 0.009958 | 116.55 | 1125.9 | 1009.35
11648 | 3.5862 | 148.49 | 61.221 | 0.0099603 | 116.56 | 1125.9 |  | 11648 | 148.49 | 3.5862 | 61.221 | 0.0099603 | 116.56 | 1125.9 | 1009.34
11649 | 3.5871 | 148.5 | 61.221 | 0.0099626 | 116.57 | 1125.9 |  | 11649 | 148.5 | 3.5871 | 61.221 | 0.0099626 | 116.57 | 1125.9 | 1009.33
11650 | 3.588 | 148.51 | 61.221 | 0.009965 | 116.58 | 1125.9 |  | 11650 | 148.51 | 3.588 | 61.221 | 0.009965 | 116.58 | 1125.9 | 1009.32
11651 | 3.5889 | 148.52 | 61.221 | 0.0099673 | 116.59 | 1125.9 |  | 11651 | 148.52 | 3.5889 | 61.221 | 0.0099673 | 116.59 | 1125.9 | 1009.31
11652 | 3.5898 | 148.53 | 61.221 | 0.0099696 | 116.6 | 1125.9 |  | 11652 | 148.53 | 3.5898 | 61.221 | 0.0099696 | 116.6 | 1125.9 | 1009.3
11653 | 3.5907 | 148.54 | 61.22 | 0.0099719 | 116.61 | 1125.9 |  | 11653 | 148.54 | 3.5907 | 61.22 | 0.0099719 | 116.61 | 1125.9 | 1009.29
11654 | 3.5916 | 148.55 | 61.22 | 0.0099743 | 116.62 | 1125.9 |  | 11654 | 148.55 | 3.5916 | 61.22 | 0.0099743 | 116.62 | 1125.9 | 1009.28
11655 | 3.5925 | 148.56 | 61.22 | 0.0099766 | 116.63 | 1125.9 |  | 11655 | 148.56 | 3.5925 | 61.22 | 0.0099766 | 116.63 | 1125.9 | 1009.27
11656 | 3.5933 | 148.57 | 61.22 | 0.0099789 | 116.64 | 1125.9 |  | 11656 | 148.57 | 3.5933 | 61.22 | 0.0099789 | 116.64 | 1125.9 | 1009.26
11657 | 3.5942 | 148.58 | 61.22 | 0.0099813 | 116.65 | 1125.9 |  | 11657 | 148.58 | 3.5942 | 61.22 | 0.0099813 | 116.65 | 1125.9 | 1009.25
11658 | 3.5951 | 148.59 | 61.219 | 0.0099836 | 116.66 | 1125.9 |  | 11658 | 148.59 | 3.5951 | 61.219 | 0.0099836 | 116.66 | 1125.9 | 1009.24
11659 | 3.596 | 148.6 | 61.219 | 0.0099859 | 116.67 | 1125.9 |  | 11659 | 148.6 | 3.596 | 61.219 | 0.0099859 | 116.67 | 1125.9 | 1009.23
11660 | 3.5969 | 148.61 | 61.219 | 0.0099882 | 116.68 | 1125.9 |  | 11660 | 148.61 | 3.5969 | 61.219 | 0.0099882 | 116.68 | 1125.9 | 1009.22
11661 | 3.5978 | 148.62 | 61.219 | 0.0099906 | 116.69 | 1125.9 |  | 11661 | 148.62 | 3.5978 | 61.219 | 0.0099906 | 116.69 | 1125.9 | 1009.21
11662 | 3.5987 | 148.63 | 61.219 | 0.0099929 | 116.7 | 1125.9 |  | 11662 | 148.63 | 3.5987 | 61.219 | 0.0099929 | 116.7 | 1125.9 | 1009.2
11663 | 3.5996 | 148.64 | 61.218 | 0.0099952 | 116.71 | 1125.9 |  | 11663 | 148.64 | 3.5996 | 61.218 | 0.0099952 | 116.71 | 1125.9 | 1009.19
11664 | 3.6005 | 148.65 | 61.218 | 0.0099976 | 116.72 | 1125.9 |  | 11664 | 148.65 | 3.6005 | 61.218 | 0.0099976 | 116.72 | 1125.9 | 1009.18
11665 | 3.6014 | 148.66 | 61.218 | 0.0099999 | 116.73 | 1125.9 |  | 11665 | 148.66 | 3.6014 | 61.218 | 0.0099999 | 116.73 | 1125.9 | 1009.17
11666 | 3.6023 | 148.67 | 61.218 | 0.010002 | 116.74 | 1125.9 |  | 11666 | 148.67 | 3.6023 | 61.218 | 0.010002 | 116.74 | 1125.9 | 1009.16
11667 | 3.6032 | 148.68 | 61.218 | 0.010005 | 116.75 | 1125.9 |  | 11667 | 148.68 | 3.6032 | 61.218 | 0.010005 | 116.75 | 1125.9 | 1009.15
11668 | 3.6041 | 148.69 | 61.218 | 0.010007 | 116.76 | 1125.9 |  | 11668 | 148.69 | 3.6041 | 61.218 | 0.010007 | 116.76 | 1125.9 | 1009.14
11669 | 3.605 | 148.7 | 61.217 | 0.010009 | 116.77 | 1126 |  | 11669 | 148.7 | 3.605 | 61.217 | 0.010009 | 116.77 | 1126 | 1009.23
11670 | 3.6059 | 148.71 | 61.217 | 0.010012 | 116.78 | 1126 |  | 11670 | 148.71 | 3.6059 | 61.217 | 0.010012 | 116.78 | 1126 | 1009.22
11671 | 3.6068 | 148.72 | 61.217 | 0.010014 | 116.79 | 1126 |  | 11671 | 148.72 | 3.6068 | 61.217 | 0.010014 | 116.79 | 1126 | 1009.21
11672 | 3.6077 | 148.73 | 61.217 | 0.010016 | 116.8 | 1126 |  | 11672 | 148.73 | 3.6077 | 61.217 | 0.010016 | 116.8 | 1126 | 1009.2
11673 | 3.6086 | 148.74 | 61.217 | 0.010019 | 116.81 | 1126 |  | 11673 | 148.74 | 3.6086 | 61.217 | 0.010019 | 116.81 | 1126 | 1009.19
11674 | 3.6095 | 148.75 | 61.216 | 0.010021 | 116.82 | 1126 |  | 11674 | 148.75 | 3.6095 | 61.216 | 0.010021 | 116.82 | 1126 | 1009.18
11675 | 3.6104 | 148.76 | 61.216 | 0.010023 | 116.83 | 1126 |  | 11675 | 148.76 | 3.6104 | 61.216 | 0.010023 | 116.83 | 1126 | 1009.17
11676 | 3.6113 | 148.77 | 61.216 | 0.010026 | 116.84 | 1126 |  | 11676 | 148.77 | 3.6113 | 61.216 | 0.010026 | 116.84 | 1126 | 1009.16
11677 | 3.6122 | 148.78 | 61.216 | 0.010028 | 116.85 | 1126 |  | 11677 | 148.78 | 3.6122 | 61.216 | 0.010028 | 116.85 | 1126 | 1009.15
11678 | 3.6131 | 148.79 | 61.216 | 0.01003 | 116.86 | 1126 |  | 11678 | 148.79 | 3.6131 | 61.216 | 0.01003 | 116.86 | 1126 | 1009.14
11679 | 3.614 | 148.8 | 61.215 | 0.010033 | 116.87 | 1126 |  | 11679 | 148.8 | 3.614 | 61.215 | 0.010033 | 116.87 | 1126 | 1009.13
11680 | 3.6149 | 148.81 | 61.215 | 0.010035 | 116.88 | 1126 |  | 11680 | 148.81 | 3.6149 | 61.215 | 0.010035 | 116.88 | 1126 | 1009.12
11681 | 3.6158 | 148.82 | 61.215 | 0.010037 | 116.89 | 1126 |  | 11681 | 148.82 | 3.6158 | 61.215 | 0.010037 | 116.89 | 1126 | 1009.11
11682 | 3.6167 | 148.83 | 61.215 | 0.01004 | 116.9 | 1126 |  | 11682 | 148.83 | 3.6167 | 61.215 | 0.01004 | 116.9 | 1126 | 1009.1
11683 | 3.6176 | 148.84 | 61.215 | 0.010042 | 116.91 | 1126 |  | 11683 | 148.84 | 3.6176 | 61.215 | 0.010042 | 116.91 | 1126 | 1009.09
11684 | 3.6185 | 148.85 | 61.215 | 0.010044 | 116.92 | 1126 |  | 11684 | 148.85 | 3.6185 | 61.215 | 0.010044 | 116.92 | 1126 | 1009.08
11685 | 3.6194 | 148.86 | 61.214 | 0.010047 | 116.93 | 1126 |  | 11685 | 148.86 | 3.6194 | 61.214 | 0.010047 | 116.93 | 1126 | 1009.07
11686 | 3.6203 | 148.87 | 61.214 | 0.010049 | 116.94 | 1126 |  | 11686 | 148.87 | 3.6203 | 61.214 | 0.010049 | 116.94 | 1126 | 1009.06
11687 | 3.6212 | 148.88 | 61.214 | 0.010051 | 116.95 | 1126 |  | 11687 | 148.88 | 3.6212 | 61.214 | 0.010051 | 116.95 | 1126 | 1009.05
11688 | 3.6221 | 148.89 | 61.214 | 0.010054 | 116.96 | 1126 |  | 11688 | 148.89 | 3.6221 | 61.214 | 0.010054 | 116.96 | 1126 | 1009.04
11689 | 3.623 | 148.9 | 61.214 | 0.010056 | 116.97 | 1126 |  | 11689 | 148.9 | 3.623 | 61.214 | 0.010056 | 116.97 | 1126 | 1009.03
11690 | 3.6239 | 148.91 | 61.213 | 0.010058 | 116.98 | 1126 |  | 11690 | 148.91 | 3.6239 | 61.213 | 0.010058 | 116.98 | 1126 | 1009.02
11691 | 3.6248 | 148.92 | 61.213 | 0.010061 | 116.99 | 1126 |  | 11691 | 148.92 | 3.6248 | 61.213 | 0.010061 | 116.99 | 1126 | 1009.01
11692 | 3.6257 | 148.93 | 61.213 | 0.010063 | 117 | 1126 |  | 11692 | 148.93 | 3.6257 | 61.213 | 0.010063 | 117 | 1126 | 1009
11693 | 3.6266 | 148.94 | 61.213 | 0.010065 | 117.01 | 1126.1 |  | 11693 | 148.94 | 3.6266 | 61.213 | 0.010065 | 117.01 | 1126.1 | 1009.09
11694 | 3.6275 | 148.95 | 61.213 | 0.010068 | 117.02 | 1126.1 |  | 11694 | 148.95 | 3.6275 | 61.213 | 0.010068 | 117.02 | 1126.1 | 1009.08
11695 | 3.6284 | 148.96 | 61.212 | 0.01007 | 117.03 | 1126.1 |  | 11695 | 148.96 | 3.6284 | 61.212 | 0.01007 | 117.03 | 1126.1 | 1009.07
11696 | 3.6293 | 148.97 | 61.212 | 0.010072 | 117.04 | 1126.1 |  | 11696 | 148.97 | 3.6293 | 61.212 | 0.010072 | 117.04 | 1126.1 | 1009.06
11697 | 3.6302 | 148.98 | 61.212 | 0.010075 | 117.05 | 1126.1 |  | 11697 | 148.98 | 3.6302 | 61.212 | 0.010075 | 117.05 | 1126.1 | 1009.05
11698 | 3.6311 | 148.99 | 61.212 | 0.010077 | 117.06 | 1126.1 |  | 11698 | 148.99 | 3.6311 | 61.212 | 0.010077 | 117.06 | 1126.1 | 1009.04
11699 | 3.632 | 149 | 61.212 | 0.01008 | 117.07 | 1126.1 |  | 11699 | 149 | 3.632 | 61.212 | 0.01008 | 117.07 | 1126.1 | 1009.03
11700 | 3.6329 | 149.01 | 61.212 | 0.010082 | 117.08 | 1126.1 |  | 11700 | 149.01 | 3.6329 | 61.212 | 0.010082 | 117.08 | 1126.1 | 1009.02
11701 | 3.6338 | 149.02 | 61.211 | 0.010084 | 117.09 | 1126.1 |  | 11701 | 149.02 | 3.6338 | 61.211 | 0.010084 | 117.09 | 1126.1 | 1009.01
11702 | 3.6347 | 149.03 | 61.211 | 0.010087 | 117.1 | 1126.1 |  | 11702 | 149.03 | 3.6347 | 61.211 | 0.010087 | 117.1 | 1126.1 | 1009
11703 | 3.6356 | 149.04 | 61.211 | 0.010089 | 117.11 | 1126.1 |  | 11703 | 149.04 | 3.6356 | 61.211 | 0.010089 | 117.11 | 1126.1 | 1008.99
11704 | 3.6365 | 149.05 | 61.211 | 0.010091 | 117.12 | 1126.1 |  | 11704 | 149.05 | 3.6365 | 61.211 | 0.010091 | 117.12 | 1126.1 | 1008.98
11705 | 3.6374 | 149.06 | 61.211 | 0.010094 | 117.13 | 1126.1 |  | 11705 | 149.06 | 3.6374 | 61.211 | 0.010094 | 117.13 | 1126.1 | 1008.97
11706 | 3.6383 | 149.07 | 61.21 | 0.010096 | 117.14 | 1126.1 |  | 11706 | 149.07 | 3.6383 | 61.21 | 0.010096 | 117.14 | 1126.1 | 1008.96
11707 | 3.6392 | 149.08 | 61.21 | 0.010098 | 117.15 | 1126.1 |  | 11707 | 149.08 | 3.6392 | 61.21 | 0.010098 | 117.15 | 1126.1 | 1008.95
11708 | 3.6401 | 149.09 | 61.21 | 0.010101 | 117.16 | 1126.1 |  | 11708 | 149.09 | 3.6401 | 61.21 | 0.010101 | 117.16 | 1126.1 | 1008.94
11709 | 3.641 | 149.1 | 61.21 | 0.010103 | 117.17 | 1126.1 |  | 11709 | 149.1 | 3.641 | 61.21 | 0.010103 | 117.17 | 1126.1 | 1008.93
11710 | 3.6419 | 149.11 | 61.21 | 0.010105 | 117.18 | 1126.1 |  | 11710 | 149.11 | 3.6419 | 61.21 | 0.010105 | 117.18 | 1126.1 | 1008.92
11711 | 3.6428 | 149.12 | 61.209 | 0.010108 | 117.19 | 1126.1 |  | 11711 | 149.12 | 3.6428 | 61.209 | 0.010108 | 117.19 | 1126.1 | 1008.91
11712 | 3.6437 | 149.13 | 61.209 | 0.01011 | 117.2 | 1126.1 |  | 11712 | 149.13 | 3.6437 | 61.209 | 0.01011 | 117.2 | 1126.1 | 1008.9
11713 | 3.6446 | 149.14 | 61.209 | 0.010112 | 117.21 | 1126.1 |  | 11713 | 149.14 | 3.6446 | 61.209 | 0.010112 | 117.21 | 1126.1 | 1008.89
11714 | 3.6455 | 149.15 | 61.209 | 0.010115 | 117.22 | 1126.1 |  | 11714 | 149.15 | 3.6455 | 61.209 | 0.010115 | 117.22 | 1126.1 | 1008.88
11715 | 3.6464 | 149.16 | 61.209 | 0.010117 | 117.23 | 1126.1 |  | 11715 | 149.16 | 3.6464 | 61.209 | 0.010117 | 117.23 | 1126.1 | 1008.87
11716 | 3.6473 | 149.17 | 61.208 | 0.01012 | 117.24 | 1126.1 |  | 11716 | 149.17 | 3.6473 | 61.208 | 0.01012 | 117.24 | 1126.1 | 1008.86
11717 | 3.6483 | 149.18 | 61.208 | 0.010122 | 117.25 | 1126.2 |  | 11717 | 149.18 | 3.6483 | 61.208 | 0.010122 | 117.25 | 1126.2 | 1008.95
11718 | 3.6492 | 149.19 | 61.208 | 0.010124 | 117.26 | 1126.2 |  | 11718 | 149.19 | 3.6492 | 61.208 | 0.010124 | 117.26 | 1126.2 | 1008.94
11719 | 3.6501 | 149.2 | 61.208 | 0.010127 | 117.27 | 1126.2 |  | 11719 | 149.2 | 3.6501 | 61.208 | 0.010127 | 117.27 | 1126.2 | 1008.93
11720 | 3.651 | 149.21 | 61.208 | 0.010129 | 117.28 | 1126.2 |  | 11720 | 149.21 | 3.651 | 61.208 | 0.010129 | 117.28 | 1126.2 | 1008.92
11721 | 3.6519 | 149.22 | 61.208 | 0.010131 | 117.29 | 1126.2 |  | 11721 | 149.22 | 3.6519 | 61.208 | 0.010131 | 117.29 | 1126.2 | 1008.91
11722 | 3.6528 | 149.23 | 61.207 | 0.010134 | 117.3 | 1126.2 |  | 11722 | 149.23 | 3.6528 | 61.207 | 0.010134 | 117.3 | 1126.2 | 1008.9
11723 | 3.6537 | 149.24 | 61.207 | 0.010136 | 117.31 | 1126.2 |  | 11723 | 149.24 | 3.6537 | 61.207 | 0.010136 | 117.31 | 1126.2 | 1008.89
11724 | 3.6546 | 149.25 | 61.207 | 0.010138 | 117.32 | 1126.2 |  | 11724 | 149.25 | 3.6546 | 61.207 | 0.010138 | 117.32 | 1126.2 | 1008.88
11725 | 3.6555 | 149.26 | 61.207 | 0.010141 | 117.33 | 1126.2 |  | 11725 | 149.26 | 3.6555 | 61.207 | 0.010141 | 117.33 | 1126.2 | 1008.87
11726 | 3.6564 | 149.27 | 61.207 | 0.010143 | 117.34 | 1126.2 |  | 11726 | 149.27 | 3.6564 | 61.207 | 0.010143 | 117.34 | 1126.2 | 1008.86
11727 | 3.6573 | 149.28 | 61.206 | 0.010145 | 117.35 | 1126.2 |  | 11727 | 149.28 | 3.6573 | 61.206 | 0.010145 | 117.35 | 1126.2 | 1008.85
11728 | 3.6582 | 149.29 | 61.206 | 0.010148 | 117.36 | 1126.2 |  | 11728 | 149.29 | 3.6582 | 61.206 | 0.010148 | 117.36 | 1126.2 | 1008.84
11729 | 3.6591 | 149.3 | 61.206 | 0.01015 | 117.37 | 1126.2 |  | 11729 | 149.3 | 3.6591 | 61.206 | 0.01015 | 117.37 | 1126.2 | 1008.83
11730 | 3.66 | 149.31 | 61.206 | 0.010153 | 117.38 | 1126.2 |  | 11730 | 149.31 | 3.66 | 61.206 | 0.010153 | 117.38 | 1126.2 | 1008.82
11731 | 3.661 | 149.32 | 61.206 | 0.010155 | 117.39 | 1126.2 |  | 11731 | 149.32 | 3.661 | 61.206 | 0.010155 | 117.39 | 1126.2 | 1008.81
11732 | 3.6619 | 149.33 | 61.205 | 0.010157 | 117.4 | 1126.2 |  | 11732 | 149.33 | 3.6619 | 61.205 | 0.010157 | 117.4 | 1126.2 | 1008.8
11733 | 3.6628 | 149.34 | 61.205 | 0.01016 | 117.41 | 1126.2 |  | 11733 | 149.34 | 3.6628 | 61.205 | 0.01016 | 117.41 | 1126.2 | 1008.79
11734 | 3.6637 | 149.35 | 61.205 | 0.010162 | 117.42 | 1126.2 |  | 11734 | 149.35 | 3.6637 | 61.205 | 0.010162 | 117.42 | 1126.2 | 1008.78
11735 | 3.6646 | 149.36 | 61.205 | 0.010164 | 117.43 | 1126.2 |  | 11735 | 149.36 | 3.6646 | 61.205 | 0.010164 | 117.43 | 1126.2 | 1008.77
11736 | 3.6655 | 149.37 | 61.205 | 0.010167 | 117.44 | 1126.2 |  | 11736 | 149.37 | 3.6655 | 61.205 | 0.010167 | 117.44 | 1126.2 | 1008.76
11737 | 3.6664 | 149.38 | 61.205 | 0.010169 | 117.45 | 1126.2 |  | 11737 | 149.38 | 3.6664 | 61.205 | 0.010169 | 117.45 | 1126.2 | 1008.75
11738 | 3.6673 | 149.39 | 61.204 | 0.010171 | 117.46 | 1126.2 |  | 11738 | 149.39 | 3.6673 | 61.204 | 0.010171 | 117.46 | 1126.2 | 1008.74
11739 | 3.6682 | 149.4 | 61.204 | 0.010174 | 117.47 | 1126.2 |  | 11739 | 149.4 | 3.6682 | 61.204 | 0.010174 | 117.47 | 1126.2 | 1008.73
11740 | 3.6691 | 149.41 | 61.204 | 0.010176 | 117.48 | 1126.2 |  | 11740 | 149.41 | 3.6691 | 61.204 | 0.010176 | 117.48 | 1126.2 | 1008.72
11741 | 3.67 | 149.42 | 61.204 | 0.010179 | 117.49 | 1126.3 |  | 11741 | 149.42 | 3.67 | 61.204 | 0.010179 | 117.49 | 1126.3 | 1008.81
11742 | 3.671 | 149.43 | 61.204 | 0.010181 | 117.5 | 1126.3 |  | 11742 | 149.43 | 3.671 | 61.204 | 0.010181 | 117.5 | 1126.3 | 1008.8
11743 | 3.6719 | 149.44 | 61.203 | 0.010183 | 117.51 | 1126.3 |  | 11743 | 149.44 | 3.6719 | 61.203 | 0.010183 | 117.51 | 1126.3 | 1008.79
11744 | 3.6728 | 149.45 | 61.203 | 0.010186 | 117.52 | 1126.3 |  | 11744 | 149.45 | 3.6728 | 61.203 | 0.010186 | 117.52 | 1126.3 | 1008.78
11745 | 3.6737 | 149.46 | 61.203 | 0.010188 | 117.53 | 1126.3 |  | 11745 | 149.46 | 3.6737 | 61.203 | 0.010188 | 117.53 | 1126.3 | 1008.77
11746 | 3.6746 | 149.47 | 61.203 | 0.01019 | 117.54 | 1126.3 |  | 11746 | 149.47 | 3.6746 | 61.203 | 0.01019 | 117.54 | 1126.3 | 1008.76
11747 | 3.6755 | 149.48 | 61.203 | 0.010193 | 117.55 | 1126.3 |  | 11747 | 149.48 | 3.6755 | 61.203 | 0.010193 | 117.55 | 1126.3 | 1008.75
11748 | 3.6764 | 149.49 | 61.202 | 0.010195 | 117.56 | 1126.3 |  | 11748 | 149.49 | 3.6764 | 61.202 | 0.010195 | 117.56 | 1126.3 | 1008.74
11749 | 3.6773 | 149.5 | 61.202 | 0.010198 | 117.57 | 1126.3 |  | 11749 | 149.5 | 3.6773 | 61.202 | 0.010198 | 117.57 | 1126.3 | 1008.73
11750 | 3.6783 | 149.51 | 61.202 | 0.0102 | 117.58 | 1126.3 |  | 11750 | 149.51 | 3.6783 | 61.202 | 0.0102 | 117.58 | 1126.3 | 1008.72
11751 | 3.6792 | 149.52 | 61.202 | 0.010202 | 117.59 | 1126.3 |  | 11751 | 149.52 | 3.6792 | 61.202 | 0.010202 | 117.59 | 1126.3 | 1008.71
11752 | 3.6801 | 149.53 | 61.202 | 0.010205 | 117.6 | 1126.3 |  | 11752 | 149.53 | 3.6801 | 61.202 | 0.010205 | 117.6 | 1126.3 | 1008.7
11753 | 3.681 | 149.54 | 61.202 | 0.010207 | 117.61 | 1126.3 |  | 11753 | 149.54 | 3.681 | 61.202 | 0.010207 | 117.61 | 1126.3 | 1008.69
11754 | 3.6819 | 149.55 | 61.201 | 0.010209 | 117.62 | 1126.3 |  | 11754 | 149.55 | 3.6819 | 61.201 | 0.010209 | 117.62 | 1126.3 | 1008.68
11755 | 3.6828 | 149.56 | 61.201 | 0.010212 | 117.63 | 1126.3 |  | 11755 | 149.56 | 3.6828 | 61.201 | 0.010212 | 117.63 | 1126.3 | 1008.67
11756 | 3.6837 | 149.57 | 61.201 | 0.010214 | 117.64 | 1126.3 |  | 11756 | 149.57 | 3.6837 | 61.201 | 0.010214 | 117.64 | 1126.3 | 1008.66
11757 | 3.6846 | 149.58 | 61.201 | 0.010217 | 117.65 | 1126.3 |  | 11757 | 149.58 | 3.6846 | 61.201 | 0.010217 | 117.65 | 1126.3 | 1008.65
11758 | 3.6856 | 149.59 | 61.201 | 0.010219 | 117.66 | 1126.3 |  | 11758 | 149.59 | 3.6856 | 61.201 | 0.010219 | 117.66 | 1126.3 | 1008.64
11759 | 3.6865 | 149.6 | 61.2 | 0.010221 | 117.67 | 1126.3 |  | 11759 | 149.6 | 3.6865 | 61.2 | 0.010221 | 117.67 | 1126.3 | 1008.63
11760 | 3.6874 | 149.61 | 61.2 | 0.010224 | 117.68 | 1126.3 |  | 11760 | 149.61 | 3.6874 | 61.2 | 0.010224 | 117.68 | 1126.3 | 1008.62
11761 | 3.6883 | 149.62 | 61.2 | 0.010226 | 117.69 | 1126.3 |  | 11761 | 149.62 | 3.6883 | 61.2 | 0.010226 | 117.69 | 1126.3 | 1008.61
11762 | 3.6892 | 149.63 | 61.2 | 0.010228 | 117.7 | 1126.3 |  | 11762 | 149.63 | 3.6892 | 61.2 | 0.010228 | 117.7 | 1126.3 | 1008.6
11763 | 3.6901 | 149.64 | 61.2 | 0.010231 | 117.71 | 1126.3 |  | 11763 | 149.64 | 3.6901 | 61.2 | 0.010231 | 117.71 | 1126.3 | 1008.59
11764 | 3.691 | 149.65 | 61.199 | 0.010233 | 117.72 | 1126.3 |  | 11764 | 149.65 | 3.691 | 61.199 | 0.010233 | 117.72 | 1126.3 | 1008.58
11765 | 3.692 | 149.66 | 61.199 | 0.010236 | 117.73 | 1126.3 |  | 11765 | 149.66 | 3.692 | 61.199 | 0.010236 | 117.73 | 1126.3 | 1008.57
11766 | 3.6929 | 149.67 | 61.199 | 0.010238 | 117.74 | 1126.4 |  | 11766 | 149.67 | 3.6929 | 61.199 | 0.010238 | 117.74 | 1126.4 | 1008.66
11767 | 3.6938 | 149.68 | 61.199 | 0.01024 | 117.75 | 1126.4 |  | 11767 | 149.68 | 3.6938 | 61.199 | 0.01024 | 117.75 | 1126.4 | 1008.65
11768 | 3.6947 | 149.69 | 61.199 | 0.010243 | 117.76 | 1126.4 |  | 11768 | 149.69 | 3.6947 | 61.199 | 0.010243 | 117.76 | 1126.4 | 1008.64
11769 | 3.6956 | 149.7 | 61.198 | 0.010245 | 117.77 | 1126.4 |  | 11769 | 149.7 | 3.6956 | 61.198 | 0.010245 | 117.77 | 1126.4 | 1008.63
11770 | 3.6965 | 149.71 | 61.198 | 0.010247 | 117.78 | 1126.4 |  | 11770 | 149.71 | 3.6965 | 61.198 | 0.010247 | 117.78 | 1126.4 | 1008.62
11771 | 3.6975 | 149.72 | 61.198 | 0.01025 | 117.79 | 1126.4 |  | 11771 | 149.72 | 3.6975 | 61.198 | 0.01025 | 117.79 | 1126.4 | 1008.61
11772 | 3.6984 | 149.73 | 61.198 | 0.010252 | 117.8 | 1126.4 |  | 11772 | 149.73 | 3.6984 | 61.198 | 0.010252 | 117.8 | 1126.4 | 1008.6
11773 | 3.6993 | 149.74 | 61.198 | 0.010255 | 117.81 | 1126.4 |  | 11773 | 149.74 | 3.6993 | 61.198 | 0.010255 | 117.81 | 1126.4 | 1008.59
11774 | 3.7002 | 149.75 | 61.198 | 0.010257 | 117.82 | 1126.4 |  | 11774 | 149.75 | 3.7002 | 61.198 | 0.010257 | 117.82 | 1126.4 | 1008.58
11775 | 3.7011 | 149.76 | 61.197 | 0.010259 | 117.83 | 1126.4 |  | 11775 | 149.76 | 3.7011 | 61.197 | 0.010259 | 117.83 | 1126.4 | 1008.57
11776 | 3.702 | 149.77 | 61.197 | 0.010262 | 117.84 | 1126.4 |  | 11776 | 149.77 | 3.702 | 61.197 | 0.010262 | 117.84 | 1126.4 | 1008.56
11777 | 3.703 | 149.78 | 61.197 | 0.010264 | 117.85 | 1126.4 |  | 11777 | 149.78 | 3.703 | 61.197 | 0.010264 | 117.85 | 1126.4 | 1008.55
11778 | 3.7039 | 149.79 | 61.197 | 0.010267 | 117.86 | 1126.4 |  | 11778 | 149.79 | 3.7039 | 61.197 | 0.010267 | 117.86 | 1126.4 | 1008.54
11779 | 3.7048 | 149.8 | 61.197 | 0.010269 | 117.87 | 1126.4 |  | 11779 | 149.8 | 3.7048 | 61.197 | 0.010269 | 117.87 | 1126.4 | 1008.53
11780 | 3.7057 | 149.81 | 61.196 | 0.010271 | 117.88 | 1126.4 |  | 11780 | 149.81 | 3.7057 | 61.196 | 0.010271 | 117.88 | 1126.4 | 1008.52
11781 | 3.7066 | 149.82 | 61.196 | 0.010274 | 117.89 | 1126.4 |  | 11781 | 149.82 | 3.7066 | 61.196 | 0.010274 | 117.89 | 1126.4 | 1008.51
11782 | 3.7075 | 149.83 | 61.196 | 0.010276 | 117.9 | 1126.4 |  | 11782 | 149.83 | 3.7075 | 61.196 | 0.010276 | 117.9 | 1126.4 | 1008.5
11783 | 3.7085 | 149.84 | 61.196 | 0.010278 | 117.91 | 1126.4 |  | 11783 | 149.84 | 3.7085 | 61.196 | 0.010278 | 117.91 | 1126.4 | 1008.49
11784 | 3.7094 | 149.85 | 61.196 | 0.010281 | 117.92 | 1126.4 |  | 11784 | 149.85 | 3.7094 | 61.196 | 0.010281 | 117.92 | 1126.4 | 1008.48
11785 | 3.7103 | 149.86 | 61.195 | 0.010283 | 117.93 | 1126.4 |  | 11785 | 149.86 | 3.7103 | 61.195 | 0.010283 | 117.93 | 1126.4 | 1008.47
11786 | 3.7112 | 149.87 | 61.195 | 0.010286 | 117.94 | 1126.4 |  | 11786 | 149.87 | 3.7112 | 61.195 | 0.010286 | 117.94 | 1126.4 | 1008.46
11787 | 3.7121 | 149.88 | 61.195 | 0.010288 | 117.95 | 1126.4 |  | 11787 | 149.88 | 3.7121 | 61.195 | 0.010288 | 117.95 | 1126.4 | 1008.45
11788 | 3.7131 | 149.89 | 61.195 | 0.01029 | 117.96 | 1126.4 |  | 11788 | 149.89 | 3.7131 | 61.195 | 0.01029 | 117.96 | 1126.4 | 1008.44
11789 | 3.714 | 149.9 | 61.195 | 0.010293 | 117.97 | 1126.4 |  | 11789 | 149.9 | 3.714 | 61.195 | 0.010293 | 117.97 | 1126.4 | 1008.43
11790 | 3.7149 | 149.91 | 61.195 | 0.010295 | 117.98 | 1126.5 |  | 11790 | 149.91 | 3.7149 | 61.195 | 0.010295 | 117.98 | 1126.5 | 1008.52
11791 | 3.7158 | 149.92 | 61.194 | 0.010298 | 117.99 | 1126.5 |  | 11791 | 149.92 | 3.7158 | 61.194 | 0.010298 | 117.99 | 1126.5 | 1008.51
11792 | 3.7167 | 149.93 | 61.194 | 0.0103 | 118 | 1126.5 |  | 11792 | 149.93 | 3.7167 | 61.194 | 0.0103 | 118 | 1126.5 | 1008.5
11793 | 3.7177 | 149.94 | 61.194 | 0.010302 | 118.01 | 1126.5 |  | 11793 | 149.94 | 3.7177 | 61.194 | 0.010302 | 118.01 | 1126.5 | 1008.49
11794 | 3.7186 | 149.95 | 61.194 | 0.010305 | 118.02 | 1126.5 |  | 11794 | 149.95 | 3.7186 | 61.194 | 0.010305 | 118.02 | 1126.5 | 1008.48
11795 | 3.7195 | 149.96 | 61.194 | 0.010307 | 118.03 | 1126.5 |  | 11795 | 149.96 | 3.7195 | 61.194 | 0.010307 | 118.03 | 1126.5 | 1008.47
11796 | 3.7204 | 149.97 | 61.193 | 0.01031 | 118.04 | 1126.5 |  | 11796 | 149.97 | 3.7204 | 61.193 | 0.01031 | 118.04 | 1126.5 | 1008.46
11797 | 3.7213 | 149.98 | 61.193 | 0.010312 | 118.05 | 1126.5 |  | 11797 | 149.98 | 3.7213 | 61.193 | 0.010312 | 118.05 | 1126.5 | 1008.45
11798 | 3.7223 | 149.99 | 61.193 | 0.010314 | 118.06 | 1126.5 |  | 11798 | 149.99 | 3.7223 | 61.193 | 0.010314 | 118.06 | 1126.5 | 1008.44
11799 | 3.7232 | 150 | 61.193 | 0.010317 | 118.07 | 1126.5 |  | 11799 | 150 | 3.7232 | 61.193 | 0.010317 | 118.07 | 1126.5 | 1008.43
11800 | 3.7241 | 150.01 | 61.193 | 0.010319 | 118.08 | 1126.5 |  | 11800 | 150.01 | 3.7241 | 61.193 | 0.010319 | 118.08 | 1126.5 | 1008.42
11801 | 3.725 | 150.02 | 61.192 | 0.010322 | 118.09 | 1126.5 |  | 11801 | 150.02 | 3.725 | 61.192 | 0.010322 | 118.09 | 1126.5 | 1008.41
11802 | 3.7259 | 150.03 | 61.192 | 0.010324 | 118.1 | 1126.5 |  | 11802 | 150.03 | 3.7259 | 61.192 | 0.010324 | 118.1 | 1126.5 | 1008.4
11803 | 3.7269 | 150.04 | 61.192 | 0.010326 | 118.11 | 1126.5 |  | 11803 | 150.04 | 3.7269 | 61.192 | 0.010326 | 118.11 | 1126.5 | 1008.39
11804 | 3.7278 | 150.05 | 61.192 | 0.010329 | 118.12 | 1126.5 |  | 11804 | 150.05 | 3.7278 | 61.192 | 0.010329 | 118.12 | 1126.5 | 1008.38
11805 | 3.7287 | 150.06 | 61.192 | 0.010331 | 118.13 | 1126.5 |  | 11805 | 150.06 | 3.7287 | 61.192 | 0.010331 | 118.13 | 1126.5 | 1008.37
11806 | 3.7296 | 150.07 | 61.191 | 0.010334 | 118.14 | 1126.5 |  | 11806 | 150.07 | 3.7296 | 61.191 | 0.010334 | 118.14 | 1126.5 | 1008.36
11807 | 3.7306 | 150.08 | 61.191 | 0.010336 | 118.15 | 1126.5 |  | 11807 | 150.08 | 3.7306 | 61.191 | 0.010336 | 118.15 | 1126.5 | 1008.35
11808 | 3.7315 | 150.09 | 61.191 | 0.010338 | 118.16 | 1126.5 |  | 11808 | 150.09 | 3.7315 | 61.191 | 0.010338 | 118.16 | 1126.5 | 1008.34
11809 | 3.7324 | 150.1 | 61.191 | 0.010341 | 118.17 | 1126.5 |  | 11809 | 150.1 | 3.7324 | 61.191 | 0.010341 | 118.17 | 1126.5 | 1008.33
11810 | 3.7333 | 150.11 | 61.191 | 0.010343 | 118.18 | 1126.5 |  | 11810 | 150.11 | 3.7333 | 61.191 | 0.010343 | 118.18 | 1126.5 | 1008.32
11811 | 3.7343 | 150.12 | 61.191 | 0.010346 | 118.19 | 1126.5 |  | 11811 | 150.12 | 3.7343 | 61.191 | 0.010346 | 118.19 | 1126.5 | 1008.31
11812 | 3.7352 | 150.13 | 61.19 | 0.010348 | 118.2 | 1126.5 |  | 11812 | 150.13 | 3.7352 | 61.19 | 0.010348 | 118.2 | 1126.5 | 1008.3
11813 | 3.7361 | 150.14 | 61.19 | 0.01035 | 118.21 | 1126.5 |  | 11813 | 150.14 | 3.7361 | 61.19 | 0.01035 | 118.21 | 1126.5 | 1008.29
11814 | 3.737 | 150.15 | 61.19 | 0.010353 | 118.22 | 1126.6 |  | 11814 | 150.15 | 3.737 | 61.19 | 0.010353 | 118.22 | 1126.6 | 1008.38
11815 | 3.738 | 150.16 | 61.19 | 0.010355 | 118.23 | 1126.6 |  | 11815 | 150.16 | 3.738 | 61.19 | 0.010355 | 118.23 | 1126.6 | 1008.37
11816 | 3.7389 | 150.17 | 61.19 | 0.010358 | 118.24 | 1126.6 |  | 11816 | 150.17 | 3.7389 | 61.19 | 0.010358 | 118.24 | 1126.6 | 1008.36
11817 | 3.7398 | 150.18 | 61.189 | 0.01036 | 118.25 | 1126.6 |  | 11817 | 150.18 | 3.7398 | 61.189 | 0.01036 | 118.25 | 1126.6 | 1008.35
11818 | 3.7407 | 150.19 | 61.189 | 0.010362 | 118.26 | 1126.6 |  | 11818 | 150.19 | 3.7407 | 61.189 | 0.010362 | 118.26 | 1126.6 | 1008.34
11819 | 3.7417 | 150.2 | 61.189 | 0.010365 | 118.27 | 1126.6 |  | 11819 | 150.2 | 3.7417 | 61.189 | 0.010365 | 118.27 | 1126.6 | 1008.33
11820 | 3.7426 | 150.21 | 61.189 | 0.010367 | 118.28 | 1126.6 |  | 11820 | 150.21 | 3.7426 | 61.189 | 0.010367 | 118.28 | 1126.6 | 1008.32
11821 | 3.7435 | 150.22 | 61.189 | 0.01037 | 118.29 | 1126.6 |  | 11821 | 150.22 | 3.7435 | 61.189 | 0.01037 | 118.29 | 1126.6 | 1008.31
11822 | 3.7444 | 150.23 | 61.188 | 0.010372 | 118.3 | 1126.6 |  | 11822 | 150.23 | 3.7444 | 61.188 | 0.010372 | 118.3 | 1126.6 | 1008.3
11823 | 3.7454 | 150.24 | 61.188 | 0.010374 | 118.31 | 1126.6 |  | 11823 | 150.24 | 3.7454 | 61.188 | 0.010374 | 118.31 | 1126.6 | 1008.29
11824 | 3.7463 | 150.25 | 61.188 | 0.010377 | 118.32 | 1126.6 |  | 11824 | 150.25 | 3.7463 | 61.188 | 0.010377 | 118.32 | 1126.6 | 1008.28
11825 | 3.7472 | 150.26 | 61.188 | 0.010379 | 118.33 | 1126.6 |  | 11825 | 150.26 | 3.7472 | 61.188 | 0.010379 | 118.33 | 1126.6 | 1008.27
11826 | 3.7481 | 150.27 | 61.188 | 0.010382 | 118.34 | 1126.6 |  | 11826 | 150.27 | 3.7481 | 61.188 | 0.010382 | 118.34 | 1126.6 | 1008.26
11827 | 3.7491 | 150.28 | 61.188 | 0.010384 | 118.35 | 1126.6 |  | 11827 | 150.28 | 3.7491 | 61.188 | 0.010384 | 118.35 | 1126.6 | 1008.25
11828 | 3.75 | 150.29 | 61.187 | 0.010386 | 118.36 | 1126.6 |  | 11828 | 150.29 | 3.75 | 61.187 | 0.010386 | 118.36 | 1126.6 | 1008.24
11829 | 3.7509 | 150.3 | 61.187 | 0.010389 | 118.37 | 1126.6 |  | 11829 | 150.3 | 3.7509 | 61.187 | 0.010389 | 118.37 | 1126.6 | 1008.23
11830 | 3.7518 | 150.31 | 61.187 | 0.010391 | 118.38 | 1126.6 |  | 11830 | 150.31 | 3.7518 | 61.187 | 0.010391 | 118.38 | 1126.6 | 1008.22
11831 | 3.7528 | 150.32 | 61.187 | 0.010394 | 118.39 | 1126.6 |  | 11831 | 150.32 | 3.7528 | 61.187 | 0.010394 | 118.39 | 1126.6 | 1008.21
11832 | 3.7537 | 150.33 | 61.187 | 0.010396 | 118.4 | 1126.6 |  | 11832 | 150.33 | 3.7537 | 61.187 | 0.010396 | 118.4 | 1126.6 | 1008.2
11833 | 3.7546 | 150.34 | 61.186 | 0.010398 | 118.41 | 1126.6 |  | 11833 | 150.34 | 3.7546 | 61.186 | 0.010398 | 118.41 | 1126.6 | 1008.19
11834 | 3.7556 | 150.35 | 61.186 | 0.010401 | 118.42 | 1126.6 |  | 11834 | 150.35 | 3.7556 | 61.186 | 0.010401 | 118.42 | 1126.6 | 1008.18
11835 | 3.7565 | 150.36 | 61.186 | 0.010403 | 118.43 | 1126.6 |  | 11835 | 150.36 | 3.7565 | 61.186 | 0.010403 | 118.43 | 1126.6 | 1008.17
11836 | 3.7574 | 150.37 | 61.186 | 0.010406 | 118.44 | 1126.6 |  | 11836 | 150.37 | 3.7574 | 61.186 | 0.010406 | 118.44 | 1126.6 | 1008.16
11837 | 3.7583 | 150.38 | 61.186 | 0.010408 | 118.45 | 1126.6 |  | 11837 | 150.38 | 3.7583 | 61.186 | 0.010408 | 118.45 | 1126.6 | 1008.15
11838 | 3.7593 | 150.39 | 61.185 | 0.010411 | 118.46 | 1126.7 |  | 11838 | 150.39 | 3.7593 | 61.185 | 0.010411 | 118.46 | 1126.7 | 1008.24
11839 | 3.7602 | 150.4 | 61.185 | 0.010413 | 118.47 | 1126.7 |  | 11839 | 150.4 | 3.7602 | 61.185 | 0.010413 | 118.47 | 1126.7 | 1008.23
11840 | 3.7611 | 150.41 | 61.185 | 0.010415 | 118.48 | 1126.7 |  | 11840 | 150.41 | 3.7611 | 61.185 | 0.010415 | 118.48 | 1126.7 | 1008.22
11841 | 3.7621 | 150.42 | 61.185 | 0.010418 | 118.49 | 1126.7 |  | 11841 | 150.42 | 3.7621 | 61.185 | 0.010418 | 118.49 | 1126.7 | 1008.21
11842 | 3.763 | 150.43 | 61.185 | 0.01042 | 118.5 | 1126.7 |  | 11842 | 150.43 | 3.763 | 61.185 | 0.01042 | 118.5 | 1126.7 | 1008.2
11843 | 3.7639 | 150.44 | 61.184 | 0.010423 | 118.51 | 1126.7 |  | 11843 | 150.44 | 3.7639 | 61.184 | 0.010423 | 118.51 | 1126.7 | 1008.19
11844 | 3.7649 | 150.45 | 61.184 | 0.010425 | 118.52 | 1126.7 |  | 11844 | 150.45 | 3.7649 | 61.184 | 0.010425 | 118.52 | 1126.7 | 1008.18
11845 | 3.7658 | 150.46 | 61.184 | 0.010427 | 118.53 | 1126.7 |  | 11845 | 150.46 | 3.7658 | 61.184 | 0.010427 | 118.53 | 1126.7 | 1008.17
11846 | 3.7667 | 150.47 | 61.184 | 0.01043 | 118.54 | 1126.7 |  | 11846 | 150.47 | 3.7667 | 61.184 | 0.01043 | 118.54 | 1126.7 | 1008.16
11847 | 3.7676 | 150.48 | 61.184 | 0.010432 | 118.55 | 1126.7 |  | 11847 | 150.48 | 3.7676 | 61.184 | 0.010432 | 118.55 | 1126.7 | 1008.15
11848 | 3.7686 | 150.49 | 61.184 | 0.010435 | 118.56 | 1126.7 |  | 11848 | 150.49 | 3.7686 | 61.184 | 0.010435 | 118.56 | 1126.7 | 1008.14
11849 | 3.7695 | 150.5 | 61.183 | 0.010437 | 118.57 | 1126.7 |  | 11849 | 150.5 | 3.7695 | 61.183 | 0.010437 | 118.57 | 1126.7 | 1008.13
11850 | 3.7704 | 150.51 | 61.183 | 0.01044 | 118.58 | 1126.7 |  | 11850 | 150.51 | 3.7704 | 61.183 | 0.01044 | 118.58 | 1126.7 | 1008.12
11851 | 3.7714 | 150.52 | 61.183 | 0.010442 | 118.59 | 1126.7 |  | 11851 | 150.52 | 3.7714 | 61.183 | 0.010442 | 118.59 | 1126.7 | 1008.11
11852 | 3.7723 | 150.53 | 61.183 | 0.010444 | 118.6 | 1126.7 |  | 11852 | 150.53 | 3.7723 | 61.183 | 0.010444 | 118.6 | 1126.7 | 1008.1
11853 | 3.7732 | 150.54 | 61.183 | 0.010447 | 118.61 | 1126.7 |  | 11853 | 150.54 | 3.7732 | 61.183 | 0.010447 | 118.61 | 1126.7 | 1008.09
11854 | 3.7742 | 150.55 | 61.182 | 0.010449 | 118.62 | 1126.7 |  | 11854 | 150.55 | 3.7742 | 61.182 | 0.010449 | 118.62 | 1126.7 | 1008.08
11855 | 3.7751 | 150.56 | 61.182 | 0.010452 | 118.63 | 1126.7 |  | 11855 | 150.56 | 3.7751 | 61.182 | 0.010452 | 118.63 | 1126.7 | 1008.07
11856 | 3.776 | 150.57 | 61.182 | 0.010454 | 118.64 | 1126.7 |  | 11856 | 150.57 | 3.776 | 61.182 | 0.010454 | 118.64 | 1126.7 | 1008.06
11857 | 3.777 | 150.58 | 61.182 | 0.010456 | 118.65 | 1126.7 |  | 11857 | 150.58 | 3.777 | 61.182 | 0.010456 | 118.65 | 1126.7 | 1008.05
11858 | 3.7779 | 150.59 | 61.182 | 0.010459 | 118.66 | 1126.7 |  | 11858 | 150.59 | 3.7779 | 61.182 | 0.010459 | 118.66 | 1126.7 | 1008.04
11859 | 3.7788 | 150.6 | 61.181 | 0.010461 | 118.67 | 1126.7 |  | 11859 | 150.6 | 3.7788 | 61.181 | 0.010461 | 118.67 | 1126.7 | 1008.03
11860 | 3.7798 | 150.61 | 61.181 | 0.010464 | 118.68 | 1126.7 |  | 11860 | 150.61 | 3.7798 | 61.181 | 0.010464 | 118.68 | 1126.7 | 1008.02
11861 | 3.7807 | 150.62 | 61.181 | 0.010466 | 118.69 | 1126.7 |  | 11861 | 150.62 | 3.7807 | 61.181 | 0.010466 | 118.69 | 1126.7 | 1008.01
11862 | 3.7816 | 150.63 | 61.181 | 0.010469 | 118.7 | 1126.7 |  | 11862 | 150.63 | 3.7816 | 61.181 | 0.010469 | 118.7 | 1126.7 | 1008
11863 | 3.7826 | 150.64 | 61.181 | 0.010471 | 118.71 | 1126.8 |  | 11863 | 150.64 | 3.7826 | 61.181 | 0.010471 | 118.71 | 1126.8 | 1008.09
11864 | 3.7835 | 150.65 | 61.18 | 0.010473 | 118.72 | 1126.8 |  | 11864 | 150.65 | 3.7835 | 61.18 | 0.010473 | 118.72 | 1126.8 | 1008.08
11865 | 3.7844 | 150.66 | 61.18 | 0.010476 | 118.73 | 1126.8 |  | 11865 | 150.66 | 3.7844 | 61.18 | 0.010476 | 118.73 | 1126.8 | 1008.07
11866 | 3.7854 | 150.67 | 61.18 | 0.010478 | 118.74 | 1126.8 |  | 11866 | 150.67 | 3.7854 | 61.18 | 0.010478 | 118.74 | 1126.8 | 1008.06
11867 | 3.7863 | 150.68 | 61.18 | 0.010481 | 118.75 | 1126.8 |  | 11867 | 150.68 | 3.7863 | 61.18 | 0.010481 | 118.75 | 1126.8 | 1008.05
11868 | 3.7872 | 150.69 | 61.18 | 0.010483 | 118.76 | 1126.8 |  | 11868 | 150.69 | 3.7872 | 61.18 | 0.010483 | 118.76 | 1126.8 | 1008.04
11869 | 3.7882 | 150.7 | 61.18 | 0.010486 | 118.77 | 1126.8 |  | 11869 | 150.7 | 3.7882 | 61.18 | 0.010486 | 118.77 | 1126.8 | 1008.03
11870 | 3.7891 | 150.71 | 61.179 | 0.010488 | 118.78 | 1126.8 |  | 11870 | 150.71 | 3.7891 | 61.179 | 0.010488 | 118.78 | 1126.8 | 1008.02
11871 | 3.79 | 150.72 | 61.179 | 0.01049 | 118.79 | 1126.8 |  | 11871 | 150.72 | 3.79 | 61.179 | 0.01049 | 118.79 | 1126.8 | 1008.01
11872 | 3.791 | 150.73 | 61.179 | 0.010493 | 118.8 | 1126.8 |  | 11872 | 150.73 | 3.791 | 61.179 | 0.010493 | 118.8 | 1126.8 | 1008
11873 | 3.7919 | 150.74 | 61.179 | 0.010495 | 118.81 | 1126.8 |  | 11873 | 150.74 | 3.7919 | 61.179 | 0.010495 | 118.81 | 1126.8 | 1007.99
11874 | 3.7929 | 150.75 | 61.179 | 0.010498 | 118.82 | 1126.8 |  | 11874 | 150.75 | 3.7929 | 61.179 | 0.010498 | 118.82 | 1126.8 | 1007.98
11875 | 3.7938 | 150.76 | 61.178 | 0.0105 | 118.83 | 1126.8 |  | 11875 | 150.76 | 3.7938 | 61.178 | 0.0105 | 118.83 | 1126.8 | 1007.97
11876 | 3.7947 | 150.77 | 61.178 | 0.010503 | 118.84 | 1126.8 |  | 11876 | 150.77 | 3.7947 | 61.178 | 0.010503 | 118.84 | 1126.8 | 1007.96
11877 | 3.7957 | 150.78 | 61.178 | 0.010505 | 118.85 | 1126.8 |  | 11877 | 150.78 | 3.7957 | 61.178 | 0.010505 | 118.85 | 1126.8 | 1007.95
11878 | 3.7966 | 150.79 | 61.178 | 0.010507 | 118.86 | 1126.8 |  | 11878 | 150.79 | 3.7966 | 61.178 | 0.010507 | 118.86 | 1126.8 | 1007.94
11879 | 3.7975 | 150.8 | 61.178 | 0.01051 | 118.87 | 1126.8 |  | 11879 | 150.8 | 3.7975 | 61.178 | 0.01051 | 118.87 | 1126.8 | 1007.93
11880 | 3.7985 | 150.81 | 61.177 | 0.010512 | 118.88 | 1126.8 |  | 11880 | 150.81 | 3.7985 | 61.177 | 0.010512 | 118.88 | 1126.8 | 1007.92
11881 | 3.7994 | 150.82 | 61.177 | 0.010515 | 118.89 | 1126.8 |  | 11881 | 150.82 | 3.7994 | 61.177 | 0.010515 | 118.89 | 1126.8 | 1007.91
11882 | 3.8004 | 150.83 | 61.177 | 0.010517 | 118.9 | 1126.8 |  | 11882 | 150.83 | 3.8004 | 61.177 | 0.010517 | 118.9 | 1126.8 | 1007.9
11883 | 3.8013 | 150.84 | 61.177 | 0.01052 | 118.91 | 1126.8 |  | 11883 | 150.84 | 3.8013 | 61.177 | 0.01052 | 118.91 | 1126.8 | 1007.89
11884 | 3.8022 | 150.85 | 61.177 | 0.010522 | 118.92 | 1126.8 |  | 11884 | 150.85 | 3.8022 | 61.177 | 0.010522 | 118.92 | 1126.8 | 1007.88
11885 | 3.8032 | 150.86 | 61.176 | 0.010524 | 118.93 | 1126.8 |  | 11885 | 150.86 | 3.8032 | 61.176 | 0.010524 | 118.93 | 1126.8 | 1007.87
11886 | 3.8041 | 150.87 | 61.176 | 0.010527 | 118.94 | 1126.8 |  | 11886 | 150.87 | 3.8041 | 61.176 | 0.010527 | 118.94 | 1126.8 | 1007.86
11887 | 3.805 | 150.88 | 61.176 | 0.010529 | 118.95 | 1126.9 |  | 11887 | 150.88 | 3.805 | 61.176 | 0.010529 | 118.95 | 1126.9 | 1007.95
11888 | 3.806 | 150.89 | 61.176 | 0.010532 | 118.96 | 1126.9 |  | 11888 | 150.89 | 3.806 | 61.176 | 0.010532 | 118.96 | 1126.9 | 1007.94
11889 | 3.8069 | 150.9 | 61.176 | 0.010534 | 118.97 | 1126.9 |  | 11889 | 150.9 | 3.8069 | 61.176 | 0.010534 | 118.97 | 1126.9 | 1007.93
11890 | 3.8079 | 150.91 | 61.176 | 0.010537 | 118.98 | 1126.9 |  | 11890 | 150.91 | 3.8079 | 61.176 | 0.010537 | 118.98 | 1126.9 | 1007.92
11891 | 3.8088 | 150.92 | 61.175 | 0.010539 | 118.99 | 1126.9 |  | 11891 | 150.92 | 3.8088 | 61.175 | 0.010539 | 118.99 | 1126.9 | 1007.91
11892 | 3.8097 | 150.93 | 61.175 | 0.010542 | 119 | 1126.9 |  | 11892 | 150.93 | 3.8097 | 61.175 | 0.010542 | 119 | 1126.9 | 1007.9
11893 | 3.8107 | 150.94 | 61.175 | 0.010544 | 119.01 | 1126.9 |  | 11893 | 150.94 | 3.8107 | 61.175 | 0.010544 | 119.01 | 1126.9 | 1007.89
11894 | 3.8116 | 150.95 | 61.175 | 0.010546 | 119.02 | 1126.9 |  | 11894 | 150.95 | 3.8116 | 61.175 | 0.010546 | 119.02 | 1126.9 | 1007.88
11895 | 3.8126 | 150.96 | 61.175 | 0.010549 | 119.03 | 1126.9 |  | 11895 | 150.96 | 3.8126 | 61.175 | 0.010549 | 119.03 | 1126.9 | 1007.87
11896 | 3.8135 | 150.97 | 61.174 | 0.010551 | 119.04 | 1126.9 |  | 11896 | 150.97 | 3.8135 | 61.174 | 0.010551 | 119.04 | 1126.9 | 1007.86
11897 | 3.8144 | 150.98 | 61.174 | 0.010554 | 119.05 | 1126.9 |  | 11897 | 150.98 | 3.8144 | 61.174 | 0.010554 | 119.05 | 1126.9 | 1007.85
11898 | 3.8154 | 150.99 | 61.174 | 0.010556 | 119.06 | 1126.9 |  | 11898 | 150.99 | 3.8154 | 61.174 | 0.010556 | 119.06 | 1126.9 | 1007.84
11899 | 3.8163 | 151 | 61.174 | 0.010559 | 119.07 | 1126.9 |  | 11899 | 151 | 3.8163 | 61.174 | 0.010559 | 119.07 | 1126.9 | 1007.83
11900 | 3.8173 | 151.01 | 61.174 | 0.010561 | 119.08 | 1126.9 |  | 11900 | 151.01 | 3.8173 | 61.174 | 0.010561 | 119.08 | 1126.9 | 1007.82
11901 | 3.8182 | 151.02 | 61.173 | 0.010563 | 119.09 | 1126.9 |  | 11901 | 151.02 | 3.8182 | 61.173 | 0.010563 | 119.09 | 1126.9 | 1007.81
11902 | 3.8191 | 151.03 | 61.173 | 0.010566 | 119.1 | 1126.9 |  | 11902 | 151.03 | 3.8191 | 61.173 | 0.010566 | 119.1 | 1126.9 | 1007.8
11903 | 3.8201 | 151.04 | 61.173 | 0.010568 | 119.11 | 1126.9 |  | 11903 | 151.04 | 3.8201 | 61.173 | 0.010568 | 119.11 | 1126.9 | 1007.79
11904 | 3.821 | 151.05 | 61.173 | 0.010571 | 119.12 | 1126.9 |  | 11904 | 151.05 | 3.821 | 61.173 | 0.010571 | 119.12 | 1126.9 | 1007.78
11905 | 3.822 | 151.06 | 61.173 | 0.010573 | 119.13 | 1126.9 |  | 11905 | 151.06 | 3.822 | 61.173 | 0.010573 | 119.13 | 1126.9 | 1007.77
11906 | 3.8229 | 151.07 | 61.172 | 0.010576 | 119.14 | 1126.9 |  | 11906 | 151.07 | 3.8229 | 61.172 | 0.010576 | 119.14 | 1126.9 | 1007.76
11907 | 3.8239 | 151.08 | 61.172 | 0.010578 | 119.15 | 1126.9 |  | 11907 | 151.08 | 3.8239 | 61.172 | 0.010578 | 119.15 | 1126.9 | 1007.75
11908 | 3.8248 | 151.09 | 61.172 | 0.010581 | 119.16 | 1126.9 |  | 11908 | 151.09 | 3.8248 | 61.172 | 0.010581 | 119.16 | 1126.9 | 1007.74
11909 | 3.8257 | 151.1 | 61.172 | 0.010583 | 119.17 | 1126.9 |  | 11909 | 151.1 | 3.8257 | 61.172 | 0.010583 | 119.17 | 1126.9 | 1007.73
11910 | 3.8267 | 151.11 | 61.172 | 0.010585 | 119.18 | 1126.9 |  | 11910 | 151.11 | 3.8267 | 61.172 | 0.010585 | 119.18 | 1126.9 | 1007.72
11911 | 3.8276 | 151.12 | 61.172 | 0.010588 | 119.19 | 1127 |  | 11911 | 151.12 | 3.8276 | 61.172 | 0.010588 | 119.19 | 1127 | 1007.81
11912 | 3.8286 | 151.13 | 61.171 | 0.01059 | 119.2 | 1127 |  | 11912 | 151.13 | 3.8286 | 61.171 | 0.01059 | 119.2 | 1127 | 1007.8
11913 | 3.8295 | 151.14 | 61.171 | 0.010593 | 119.21 | 1127 |  | 11913 | 151.14 | 3.8295 | 61.171 | 0.010593 | 119.21 | 1127 | 1007.79
11914 | 3.8305 | 151.15 | 61.171 | 0.010595 | 119.22 | 1127 |  | 11914 | 151.15 | 3.8305 | 61.171 | 0.010595 | 119.22 | 1127 | 1007.78
11915 | 3.8314 | 151.16 | 61.171 | 0.010598 | 119.23 | 1127 |  | 11915 | 151.16 | 3.8314 | 61.171 | 0.010598 | 119.23 | 1127 | 1007.77
11916 | 3.8324 | 151.17 | 61.171 | 0.0106 | 119.24 | 1127 |  | 11916 | 151.17 | 3.8324 | 61.171 | 0.0106 | 119.24 | 1127 | 1007.76
11917 | 3.8333 | 151.18 | 61.17 | 0.010603 | 119.25 | 1127 |  | 11917 | 151.18 | 3.8333 | 61.17 | 0.010603 | 119.25 | 1127 | 1007.75
11918 | 3.8342 | 151.19 | 61.17 | 0.010605 | 119.26 | 1127 |  | 11918 | 151.19 | 3.8342 | 61.17 | 0.010605 | 119.26 | 1127 | 1007.74
11919 | 3.8352 | 151.2 | 61.17 | 0.010608 | 119.27 | 1127 |  | 11919 | 151.2 | 3.8352 | 61.17 | 0.010608 | 119.27 | 1127 | 1007.73
11920 | 3.8361 | 151.21 | 61.17 | 0.01061 | 119.28 | 1127 |  | 11920 | 151.21 | 3.8361 | 61.17 | 0.01061 | 119.28 | 1127 | 1007.72
11921 | 3.8371 | 151.22 | 61.17 | 0.010612 | 119.29 | 1127 |  | 11921 | 151.22 | 3.8371 | 61.17 | 0.010612 | 119.29 | 1127 | 1007.71
11922 | 3.838 | 151.23 | 61.169 | 0.010615 | 119.3 | 1127 |  | 11922 | 151.23 | 3.838 | 61.169 | 0.010615 | 119.3 | 1127 | 1007.7
11923 | 3.839 | 151.24 | 61.169 | 0.010617 | 119.31 | 1127 |  | 11923 | 151.24 | 3.839 | 61.169 | 0.010617 | 119.31 | 1127 | 1007.69
11924 | 3.8399 | 151.25 | 61.169 | 0.01062 | 119.32 | 1127 |  | 11924 | 151.25 | 3.8399 | 61.169 | 0.01062 | 119.32 | 1127 | 1007.68
11925 | 3.8409 | 151.26 | 61.169 | 0.010622 | 119.33 | 1127 |  | 11925 | 151.26 | 3.8409 | 61.169 | 0.010622 | 119.33 | 1127 | 1007.67
11926 | 3.8418 | 151.27 | 61.169 | 0.010625 | 119.34 | 1127 |  | 11926 | 151.27 | 3.8418 | 61.169 | 0.010625 | 119.34 | 1127 | 1007.66
11927 | 3.8428 | 151.28 | 61.168 | 0.010627 | 119.35 | 1127 |  | 11927 | 151.28 | 3.8428 | 61.168 | 0.010627 | 119.35 | 1127 | 1007.65
11928 | 3.8437 | 151.29 | 61.168 | 0.01063 | 119.36 | 1127 |  | 11928 | 151.29 | 3.8437 | 61.168 | 0.01063 | 119.36 | 1127 | 1007.64
11929 | 3.8447 | 151.3 | 61.168 | 0.010632 | 119.37 | 1127 |  | 11929 | 151.3 | 3.8447 | 61.168 | 0.010632 | 119.37 | 1127 | 1007.63
11930 | 3.8456 | 151.31 | 61.168 | 0.010635 | 119.38 | 1127 |  | 11930 | 151.31 | 3.8456 | 61.168 | 0.010635 | 119.38 | 1127 | 1007.62
11931 | 3.8465 | 151.32 | 61.168 | 0.010637 | 119.39 | 1127 |  | 11931 | 151.32 | 3.8465 | 61.168 | 0.010637 | 119.39 | 1127 | 1007.61
11932 | 3.8475 | 151.33 | 61.168 | 0.010639 | 119.4 | 1127 |  | 11932 | 151.33 | 3.8475 | 61.168 | 0.010639 | 119.4 | 1127 | 1007.6
11933 | 3.8484 | 151.34 | 61.167 | 0.010642 | 119.41 | 1127 |  | 11933 | 151.34 | 3.8484 | 61.167 | 0.010642 | 119.41 | 1127 | 1007.59
11934 | 3.8494 | 151.35 | 61.167 | 0.010644 | 119.42 | 1127 |  | 11934 | 151.35 | 3.8494 | 61.167 | 0.010644 | 119.42 | 1127 | 1007.58
11935 | 3.8503 | 151.36 | 61.167 | 0.010647 | 119.43 | 1127.1 |  | 11935 | 151.36 | 3.8503 | 61.167 | 0.010647 | 119.43 | 1127.1 | 1007.67
11936 | 3.8513 | 151.37 | 61.167 | 0.010649 | 119.44 | 1127.1 |  | 11936 | 151.37 | 3.8513 | 61.167 | 0.010649 | 119.44 | 1127.1 | 1007.66
11937 | 3.8522 | 151.38 | 61.167 | 0.010652 | 119.45 | 1127.1 |  | 11937 | 151.38 | 3.8522 | 61.167 | 0.010652 | 119.45 | 1127.1 | 1007.65
11938 | 3.8532 | 151.39 | 61.166 | 0.010654 | 119.46 | 1127.1 |  | 11938 | 151.39 | 3.8532 | 61.166 | 0.010654 | 119.46 | 1127.1 | 1007.64
11939 | 3.8541 | 151.4 | 61.166 | 0.010657 | 119.47 | 1127.1 |  | 11939 | 151.4 | 3.8541 | 61.166 | 0.010657 | 119.47 | 1127.1 | 1007.63
11940 | 3.8551 | 151.41 | 61.166 | 0.010659 | 119.48 | 1127.1 |  | 11940 | 151.41 | 3.8551 | 61.166 | 0.010659 | 119.48 | 1127.1 | 1007.62
11941 | 3.856 | 151.42 | 61.166 | 0.010662 | 119.49 | 1127.1 |  | 11941 | 151.42 | 3.856 | 61.166 | 0.010662 | 119.49 | 1127.1 | 1007.61
11942 | 3.857 | 151.43 | 61.166 | 0.010664 | 119.5 | 1127.1 |  | 11942 | 151.43 | 3.857 | 61.166 | 0.010664 | 119.5 | 1127.1 | 1007.6
11943 | 3.8579 | 151.44 | 61.165 | 0.010667 | 119.51 | 1127.1 |  | 11943 | 151.44 | 3.8579 | 61.165 | 0.010667 | 119.51 | 1127.1 | 1007.59
11944 | 3.8589 | 151.45 | 61.165 | 0.010669 | 119.52 | 1127.1 |  | 11944 | 151.45 | 3.8589 | 61.165 | 0.010669 | 119.52 | 1127.1 | 1007.58
11945 | 3.8598 | 151.46 | 61.165 | 0.010671 | 119.53 | 1127.1 |  | 11945 | 151.46 | 3.8598 | 61.165 | 0.010671 | 119.53 | 1127.1 | 1007.57
11946 | 3.8608 | 151.47 | 61.165 | 0.010674 | 119.54 | 1127.1 |  | 11946 | 151.47 | 3.8608 | 61.165 | 0.010674 | 119.54 | 1127.1 | 1007.56
11947 | 3.8617 | 151.48 | 61.165 | 0.010676 | 119.55 | 1127.1 |  | 11947 | 151.48 | 3.8617 | 61.165 | 0.010676 | 119.55 | 1127.1 | 1007.55
11948 | 3.8627 | 151.49 | 61.164 | 0.010679 | 119.56 | 1127.1 |  | 11948 | 151.49 | 3.8627 | 61.164 | 0.010679 | 119.56 | 1127.1 | 1007.54
11949 | 3.8636 | 151.5 | 61.164 | 0.010681 | 119.57 | 1127.1 |  | 11949 | 151.5 | 3.8636 | 61.164 | 0.010681 | 119.57 | 1127.1 | 1007.53
11950 | 3.8646 | 151.51 | 61.164 | 0.010684 | 119.58 | 1127.1 |  | 11950 | 151.51 | 3.8646 | 61.164 | 0.010684 | 119.58 | 1127.1 | 1007.52
11951 | 3.8655 | 151.52 | 61.164 | 0.010686 | 119.59 | 1127.1 |  | 11951 | 151.52 | 3.8655 | 61.164 | 0.010686 | 119.59 | 1127.1 | 1007.51
11952 | 3.8665 | 151.53 | 61.164 | 0.010689 | 119.6 | 1127.1 |  | 11952 | 151.53 | 3.8665 | 61.164 | 0.010689 | 119.6 | 1127.1 | 1007.5
11953 | 3.8674 | 151.54 | 61.164 | 0.010691 | 119.61 | 1127.1 |  | 11953 | 151.54 | 3.8674 | 61.164 | 0.010691 | 119.61 | 1127.1 | 1007.49
11954 | 3.8684 | 151.55 | 61.163 | 0.010694 | 119.62 | 1127.1 |  | 11954 | 151.55 | 3.8684 | 61.163 | 0.010694 | 119.62 | 1127.1 | 1007.48
11955 | 3.8693 | 151.56 | 61.163 | 0.010696 | 119.63 | 1127.1 |  | 11955 | 151.56 | 3.8693 | 61.163 | 0.010696 | 119.63 | 1127.1 | 1007.47
11956 | 3.8703 | 151.57 | 61.163 | 0.010699 | 119.64 | 1127.1 |  | 11956 | 151.57 | 3.8703 | 61.163 | 0.010699 | 119.64 | 1127.1 | 1007.46
11957 | 3.8712 | 151.58 | 61.163 | 0.010701 | 119.65 | 1127.1 |  | 11957 | 151.58 | 3.8712 | 61.163 | 0.010701 | 119.65 | 1127.1 | 1007.45
11958 | 3.8722 | 151.59 | 61.163 | 0.010703 | 119.66 | 1127.1 |  | 11958 | 151.59 | 3.8722 | 61.163 | 0.010703 | 119.66 | 1127.1 | 1007.44
11959 | 3.8732 | 151.6 | 61.162 | 0.010706 | 119.67 | 1127.1 |  | 11959 | 151.6 | 3.8732 | 61.162 | 0.010706 | 119.67 | 1127.1 | 1007.43
11960 | 3.8741 | 151.61 | 61.162 | 0.010708 | 119.68 | 1127.2 |  | 11960 | 151.61 | 3.8741 | 61.162 | 0.010708 | 119.68 | 1127.2 | 1007.52
11961 | 3.8751 | 151.62 | 61.162 | 0.010711 | 119.69 | 1127.2 |  | 11961 | 151.62 | 3.8751 | 61.162 | 0.010711 | 119.69 | 1127.2 | 1007.51
11962 | 3.876 | 151.63 | 61.162 | 0.010713 | 119.7 | 1127.2 |  | 11962 | 151.63 | 3.876 | 61.162 | 0.010713 | 119.7 | 1127.2 | 1007.5
11963 | 3.877 | 151.64 | 61.162 | 0.010716 | 119.71 | 1127.2 |  | 11963 | 151.64 | 3.877 | 61.162 | 0.010716 | 119.71 | 1127.2 | 1007.49
11964 | 3.8779 | 151.65 | 61.161 | 0.010718 | 119.72 | 1127.2 |  | 11964 | 151.65 | 3.8779 | 61.161 | 0.010718 | 119.72 | 1127.2 | 1007.48
11965 | 3.8789 | 151.66 | 61.161 | 0.010721 | 119.73 | 1127.2 |  | 11965 | 151.66 | 3.8789 | 61.161 | 0.010721 | 119.73 | 1127.2 | 1007.47
11966 | 3.8798 | 151.67 | 61.161 | 0.010723 | 119.74 | 1127.2 |  | 11966 | 151.67 | 3.8798 | 61.161 | 0.010723 | 119.74 | 1127.2 | 1007.46
11967 | 3.8808 | 151.68 | 61.161 | 0.010726 | 119.75 | 1127.2 |  | 11967 | 151.68 | 3.8808 | 61.161 | 0.010726 | 119.75 | 1127.2 | 1007.45
11968 | 3.8817 | 151.69 | 61.161 | 0.010728 | 119.76 | 1127.2 |  | 11968 | 151.69 | 3.8817 | 61.161 | 0.010728 | 119.76 | 1127.2 | 1007.44
11969 | 3.8827 | 151.7 | 61.16 | 0.010731 | 119.77 | 1127.2 |  | 11969 | 151.7 | 3.8827 | 61.16 | 0.010731 | 119.77 | 1127.2 | 1007.43
11970 | 3.8836 | 151.71 | 61.16 | 0.010733 | 119.78 | 1127.2 |  | 11970 | 151.71 | 3.8836 | 61.16 | 0.010733 | 119.78 | 1127.2 | 1007.42
11971 | 3.8846 | 151.72 | 61.16 | 0.010736 | 119.79 | 1127.2 |  | 11971 | 151.72 | 3.8846 | 61.16 | 0.010736 | 119.79 | 1127.2 | 1007.41
11972 | 3.8856 | 151.73 | 61.16 | 0.010738 | 119.8 | 1127.2 |  | 11972 | 151.73 | 3.8856 | 61.16 | 0.010738 | 119.8 | 1127.2 | 1007.4
11973 | 3.8865 | 151.74 | 61.16 | 0.010741 | 119.81 | 1127.2 |  | 11973 | 151.74 | 3.8865 | 61.16 | 0.010741 | 119.81 | 1127.2 | 1007.39
11974 | 3.8875 | 151.75 | 61.16 | 0.010743 | 119.82 | 1127.2 |  | 11974 | 151.75 | 3.8875 | 61.16 | 0.010743 | 119.82 | 1127.2 | 1007.38
11975 | 3.8884 | 151.76 | 61.159 | 0.010746 | 119.83 | 1127.2 |  | 11975 | 151.76 | 3.8884 | 61.159 | 0.010746 | 119.83 | 1127.2 | 1007.37
11976 | 3.8894 | 151.77 | 61.159 | 0.010748 | 119.84 | 1127.2 |  | 11976 | 151.77 | 3.8894 | 61.159 | 0.010748 | 119.84 | 1127.2 | 1007.36
11977 | 3.8903 | 151.78 | 61.159 | 0.010751 | 119.85 | 1127.2 |  | 11977 | 151.78 | 3.8903 | 61.159 | 0.010751 | 119.85 | 1127.2 | 1007.35
11978 | 3.8913 | 151.79 | 61.159 | 0.010753 | 119.86 | 1127.2 |  | 11978 | 151.79 | 3.8913 | 61.159 | 0.010753 | 119.86 | 1127.2 | 1007.34
11979 | 3.8923 | 151.8 | 61.159 | 0.010755 | 119.87 | 1127.2 |  | 11979 | 151.8 | 3.8923 | 61.159 | 0.010755 | 119.87 | 1127.2 | 1007.33
11980 | 3.8932 | 151.81 | 61.158 | 0.010758 | 119.88 | 1127.2 |  | 11980 | 151.81 | 3.8932 | 61.158 | 0.010758 | 119.88 | 1127.2 | 1007.32
11981 | 3.8942 | 151.82 | 61.158 | 0.01076 | 119.89 | 1127.2 |  | 11981 | 151.82 | 3.8942 | 61.158 | 0.01076 | 119.89 | 1127.2 | 1007.31
11982 | 3.8951 | 151.83 | 61.158 | 0.010763 | 119.9 | 1127.2 |  | 11982 | 151.83 | 3.8951 | 61.158 | 0.010763 | 119.9 | 1127.2 | 1007.3
11983 | 3.8961 | 151.84 | 61.158 | 0.010765 | 119.91 | 1127.2 |  | 11983 | 151.84 | 3.8961 | 61.158 | 0.010765 | 119.91 | 1127.2 | 1007.29
11984 | 3.897 | 151.85 | 61.158 | 0.010768 | 119.92 | 1127.3 |  | 11984 | 151.85 | 3.897 | 61.158 | 0.010768 | 119.92 | 1127.3 | 1007.38
11985 | 3.898 | 151.86 | 61.157 | 0.01077 | 119.93 | 1127.3 |  | 11985 | 151.86 | 3.898 | 61.157 | 0.01077 | 119.93 | 1127.3 | 1007.37
11986 | 3.899 | 151.87 | 61.157 | 0.010773 | 119.94 | 1127.3 |  | 11986 | 151.87 | 3.899 | 61.157 | 0.010773 | 119.94 | 1127.3 | 1007.36
11987 | 3.8999 | 151.88 | 61.157 | 0.010775 | 119.95 | 1127.3 |  | 11987 | 151.88 | 3.8999 | 61.157 | 0.010775 | 119.95 | 1127.3 | 1007.35
11988 | 3.9009 | 151.89 | 61.157 | 0.010778 | 119.96 | 1127.3 |  | 11988 | 151.89 | 3.9009 | 61.157 | 0.010778 | 119.96 | 1127.3 | 1007.34
11989 | 3.9018 | 151.9 | 61.157 | 0.01078 | 119.97 | 1127.3 |  | 11989 | 151.9 | 3.9018 | 61.157 | 0.01078 | 119.97 | 1127.3 | 1007.33
11990 | 3.9028 | 151.91 | 61.156 | 0.010783 | 119.98 | 1127.3 |  | 11990 | 151.91 | 3.9028 | 61.156 | 0.010783 | 119.98 | 1127.3 | 1007.32
11991 | 3.9038 | 151.92 | 61.156 | 0.010785 | 119.99 | 1127.3 |  | 11991 | 151.92 | 3.9038 | 61.156 | 0.010785 | 119.99 | 1127.3 | 1007.31
11992 | 3.9047 | 151.93 | 61.156 | 0.010788 | 120 | 1127.3 |  | 11992 | 151.93 | 3.9047 | 61.156 | 0.010788 | 120 | 1127.3 | 1007.3
11993 | 3.9057 | 151.94 | 61.156 | 0.01079 | 120.01 | 1127.3 |  | 11993 | 151.94 | 3.9057 | 61.156 | 0.01079 | 120.01 | 1127.3 | 1007.29
11994 | 3.9066 | 151.95 | 61.156 | 0.010793 | 120.02 | 1127.3 |  | 11994 | 151.95 | 3.9066 | 61.156 | 0.010793 | 120.02 | 1127.3 | 1007.28
11995 | 3.9076 | 151.96 | 61.155 | 0.010795 | 120.03 | 1127.3 |  | 11995 | 151.96 | 3.9076 | 61.155 | 0.010795 | 120.03 | 1127.3 | 1007.27
11996 | 3.9086 | 151.97 | 61.155 | 0.010798 | 120.04 | 1127.3 |  | 11996 | 151.97 | 3.9086 | 61.155 | 0.010798 | 120.04 | 1127.3 | 1007.26
11997 | 3.9095 | 151.98 | 61.155 | 0.0108 | 120.05 | 1127.3 |  | 11997 | 151.98 | 3.9095 | 61.155 | 0.0108 | 120.05 | 1127.3 | 1007.25
11998 | 3.9105 | 151.99 | 61.155 | 0.010803 | 120.06 | 1127.3 |  | 11998 | 151.99 | 3.9105 | 61.155 | 0.010803 | 120.06 | 1127.3 | 1007.24
11999 | 3.9114 | 152 | 61.155 | 0.010805 | 120.07 | 1127.3 |  | 11999 | 152 | 3.9114 | 61.155 | 0.010805 | 120.07 | 1127.3 | 1007.23
12000 | 3.9124 | 152.01 | 61.155 | 0.010808 | 120.08 | 1127.3 |  | 12000 | 152.01 | 3.9124 | 61.155 | 0.010808 | 120.08 | 1127.3 | 1007.22
12001 | 3.9134 | 152.02 | 61.154 | 0.01081 | 120.09 | 1127.3 |  | 12001 | 152.02 | 3.9134 | 61.154 | 0.01081 | 120.09 | 1127.3 | 1007.21
12002 | 3.9143 | 152.03 | 61.154 | 0.010813 | 120.1 | 1127.3 |  | 12002 | 152.03 | 3.9143 | 61.154 | 0.010813 | 120.1 | 1127.3 | 1007.2
12003 | 3.9153 | 152.04 | 61.154 | 0.010815 | 120.11 | 1127.3 |  | 12003 | 152.04 | 3.9153 | 61.154 | 0.010815 | 120.11 | 1127.3 | 1007.19
12004 | 3.9162 | 152.05 | 61.154 | 0.010818 | 120.12 | 1127.3 |  | 12004 | 152.05 | 3.9162 | 61.154 | 0.010818 | 120.12 | 1127.3 | 1007.18
12005 | 3.9172 | 152.06 | 61.154 | 0.01082 | 120.13 | 1127.3 |  | 12005 | 152.06 | 3.9172 | 61.154 | 0.01082 | 120.13 | 1127.3 | 1007.17
12006 | 3.9182 | 152.07 | 61.153 | 0.010823 | 120.14 | 1127.3 |  | 12006 | 152.07 | 3.9182 | 61.153 | 0.010823 | 120.14 | 1127.3 | 1007.16
12007 | 3.9191 | 152.08 | 61.153 | 0.010825 | 120.15 | 1127.3 |  | 12007 | 152.08 | 3.9191 | 61.153 | 0.010825 | 120.15 | 1127.3 | 1007.15
12008 | 3.9201 | 152.09 | 61.153 | 0.010828 | 120.16 | 1127.4 |  | 12008 | 152.09 | 3.9201 | 61.153 | 0.010828 | 120.16 | 1127.4 | 1007.24
12009 | 3.9211 | 152.1 | 61.153 | 0.01083 | 120.17 | 1127.4 |  | 12009 | 152.1 | 3.9211 | 61.153 | 0.01083 | 120.17 | 1127.4 | 1007.23
12010 | 3.922 | 152.11 | 61.153 | 0.010833 | 120.18 | 1127.4 |  | 12010 | 152.11 | 3.922 | 61.153 | 0.010833 | 120.18 | 1127.4 | 1007.22
12011 | 3.923 | 152.12 | 61.152 | 0.010835 | 120.19 | 1127.4 |  | 12011 | 152.12 | 3.923 | 61.152 | 0.010835 | 120.19 | 1127.4 | 1007.21
12012 | 3.9239 | 152.13 | 61.152 | 0.010838 | 120.2 | 1127.4 |  | 12012 | 152.13 | 3.9239 | 61.152 | 0.010838 | 120.2 | 1127.4 | 1007.2
12013 | 3.9249 | 152.14 | 61.152 | 0.01084 | 120.21 | 1127.4 |  | 12013 | 152.14 | 3.9249 | 61.152 | 0.01084 | 120.21 | 1127.4 | 1007.19
12014 | 3.9259 | 152.15 | 61.152 | 0.010843 | 120.22 | 1127.4 |  | 12014 | 152.15 | 3.9259 | 61.152 | 0.010843 | 120.22 | 1127.4 | 1007.18
12015 | 3.9268 | 152.16 | 61.152 | 0.010845 | 120.23 | 1127.4 |  | 12015 | 152.16 | 3.9268 | 61.152 | 0.010845 | 120.23 | 1127.4 | 1007.17
12016 | 3.9278 | 152.17 | 61.151 | 0.010848 | 120.24 | 1127.4 |  | 12016 | 152.17 | 3.9278 | 61.151 | 0.010848 | 120.24 | 1127.4 | 1007.16
12017 | 3.9288 | 152.18 | 61.151 | 0.01085 | 120.25 | 1127.4 |  | 12017 | 152.18 | 3.9288 | 61.151 | 0.01085 | 120.25 | 1127.4 | 1007.15
12018 | 3.9297 | 152.19 | 61.151 | 0.010853 | 120.26 | 1127.4 |  | 12018 | 152.19 | 3.9297 | 61.151 | 0.010853 | 120.26 | 1127.4 | 1007.14
12019 | 3.9307 | 152.2 | 61.151 | 0.010855 | 120.27 | 1127.4 |  | 12019 | 152.2 | 3.9307 | 61.151 | 0.010855 | 120.27 | 1127.4 | 1007.13
12020 | 3.9317 | 152.21 | 61.151 | 0.010858 | 120.28 | 1127.4 |  | 12020 | 152.21 | 3.9317 | 61.151 | 0.010858 | 120.28 | 1127.4 | 1007.12
12021 | 3.9326 | 152.22 | 61.151 | 0.01086 | 120.29 | 1127.4 |  | 12021 | 152.22 | 3.9326 | 61.151 | 0.01086 | 120.29 | 1127.4 | 1007.11
12022 | 3.9336 | 152.23 | 61.15 | 0.010863 | 120.3 | 1127.4 |  | 12022 | 152.23 | 3.9336 | 61.15 | 0.010863 | 120.3 | 1127.4 | 1007.1
12023 | 3.9346 | 152.24 | 61.15 | 0.010865 | 120.31 | 1127.4 |  | 12023 | 152.24 | 3.9346 | 61.15 | 0.010865 | 120.31 | 1127.4 | 1007.09
12024 | 3.9355 | 152.25 | 61.15 | 0.010868 | 120.32 | 1127.4 |  | 12024 | 152.25 | 3.9355 | 61.15 | 0.010868 | 120.32 | 1127.4 | 1007.08
12025 | 3.9365 | 152.26 | 61.15 | 0.01087 | 120.33 | 1127.4 |  | 12025 | 152.26 | 3.9365 | 61.15 | 0.01087 | 120.33 | 1127.4 | 1007.07
12026 | 3.9375 | 152.27 | 61.15 | 0.010873 | 120.34 | 1127.4 |  | 12026 | 152.27 | 3.9375 | 61.15 | 0.010873 | 120.34 | 1127.4 | 1007.06
12027 | 3.9384 | 152.28 | 61.149 | 0.010875 | 120.35 | 1127.4 |  | 12027 | 152.28 | 3.9384 | 61.149 | 0.010875 | 120.35 | 1127.4 | 1007.05
12028 | 3.9394 | 152.29 | 61.149 | 0.010878 | 120.36 | 1127.4 |  | 12028 | 152.29 | 3.9394 | 61.149 | 0.010878 | 120.36 | 1127.4 | 1007.04
12029 | 3.9404 | 152.3 | 61.149 | 0.01088 | 120.37 | 1127.4 |  | 12029 | 152.3 | 3.9404 | 61.149 | 0.01088 | 120.37 | 1127.4 | 1007.03
12030 | 3.9413 | 152.31 | 61.149 | 0.010883 | 120.38 | 1127.4 |  | 12030 | 152.31 | 3.9413 | 61.149 | 0.010883 | 120.38 | 1127.4 | 1007.02
12031 | 3.9423 | 152.32 | 61.149 | 0.010885 | 120.39 | 1127.4 |  | 12031 | 152.32 | 3.9423 | 61.149 | 0.010885 | 120.39 | 1127.4 | 1007.01
12032 | 3.9433 | 152.33 | 61.148 | 0.010888 | 120.4 | 1127.4 |  | 12032 | 152.33 | 3.9433 | 61.148 | 0.010888 | 120.4 | 1127.4 | 1007
12033 | 3.9442 | 152.34 | 61.148 | 0.01089 | 120.41 | 1127.5 |  | 12033 | 152.34 | 3.9442 | 61.148 | 0.01089 | 120.41 | 1127.5 | 1007.09
12034 | 3.9452 | 152.35 | 61.148 | 0.010893 | 120.42 | 1127.5 |  | 12034 | 152.35 | 3.9452 | 61.148 | 0.010893 | 120.42 | 1127.5 | 1007.08
12035 | 3.9462 | 152.36 | 61.148 | 0.010895 | 120.43 | 1127.5 |  | 12035 | 152.36 | 3.9462 | 61.148 | 0.010895 | 120.43 | 1127.5 | 1007.07
12036 | 3.9471 | 152.37 | 61.148 | 0.010898 | 120.44 | 1127.5 |  | 12036 | 152.37 | 3.9471 | 61.148 | 0.010898 | 120.44 | 1127.5 | 1007.06
12037 | 3.9481 | 152.38 | 61.147 | 0.0109 | 120.45 | 1127.5 |  | 12037 | 152.38 | 3.9481 | 61.147 | 0.0109 | 120.45 | 1127.5 | 1007.05
12038 | 3.9491 | 152.39 | 61.147 | 0.010903 | 120.46 | 1127.5 |  | 12038 | 152.39 | 3.9491 | 61.147 | 0.010903 | 120.46 | 1127.5 | 1007.04
12039 | 3.95 | 152.4 | 61.147 | 0.010905 | 120.47 | 1127.5 |  | 12039 | 152.4 | 3.95 | 61.147 | 0.010905 | 120.47 | 1127.5 | 1007.03
12040 | 3.951 | 152.41 | 61.147 | 0.010908 | 120.48 | 1127.5 |  | 12040 | 152.41 | 3.951 | 61.147 | 0.010908 | 120.48 | 1127.5 | 1007.02
12041 | 3.952 | 152.42 | 61.147 | 0.01091 | 120.49 | 1127.5 |  | 12041 | 152.42 | 3.952 | 61.147 | 0.01091 | 120.49 | 1127.5 | 1007.01
12042 | 3.9529 | 152.43 | 61.146 | 0.010913 | 120.5 | 1127.5 |  | 12042 | 152.43 | 3.9529 | 61.146 | 0.010913 | 120.5 | 1127.5 | 1007
12043 | 3.9539 | 152.44 | 61.146 | 0.010915 | 120.51 | 1127.5 |  | 12043 | 152.44 | 3.9539 | 61.146 | 0.010915 | 120.51 | 1127.5 | 1006.99
12044 | 3.9549 | 152.45 | 61.146 | 0.010918 | 120.52 | 1127.5 |  | 12044 | 152.45 | 3.9549 | 61.146 | 0.010918 | 120.52 | 1127.5 | 1006.98
12045 | 3.9559 | 152.46 | 61.146 | 0.01092 | 120.53 | 1127.5 |  | 12045 | 152.46 | 3.9559 | 61.146 | 0.01092 | 120.53 | 1127.5 | 1006.97
12046 | 3.9568 | 152.47 | 61.146 | 0.010923 | 120.54 | 1127.5 |  | 12046 | 152.47 | 3.9568 | 61.146 | 0.010923 | 120.54 | 1127.5 | 1006.96
12047 | 3.9578 | 152.48 | 61.146 | 0.010925 | 120.55 | 1127.5 |  | 12047 | 152.48 | 3.9578 | 61.146 | 0.010925 | 120.55 | 1127.5 | 1006.95
12048 | 3.9588 | 152.49 | 61.145 | 0.010928 | 120.56 | 1127.5 |  | 12048 | 152.49 | 3.9588 | 61.145 | 0.010928 | 120.56 | 1127.5 | 1006.94
12049 | 3.9597 | 152.5 | 61.145 | 0.01093 | 120.57 | 1127.5 |  | 12049 | 152.5 | 3.9597 | 61.145 | 0.01093 | 120.57 | 1127.5 | 1006.93
12050 | 3.9607 | 152.51 | 61.145 | 0.010933 | 120.58 | 1127.5 |  | 12050 | 152.51 | 3.9607 | 61.145 | 0.010933 | 120.58 | 1127.5 | 1006.92
12051 | 3.9617 | 152.52 | 61.145 | 0.010935 | 120.59 | 1127.5 |  | 12051 | 152.52 | 3.9617 | 61.145 | 0.010935 | 120.59 | 1127.5 | 1006.91
12052 | 3.9627 | 152.53 | 61.145 | 0.010938 | 120.6 | 1127.5 |  | 12052 | 152.53 | 3.9627 | 61.145 | 0.010938 | 120.6 | 1127.5 | 1006.9
12053 | 3.9636 | 152.54 | 61.144 | 0.01094 | 120.61 | 1127.5 |  | 12053 | 152.54 | 3.9636 | 61.144 | 0.01094 | 120.61 | 1127.5 | 1006.89
12054 | 3.9646 | 152.55 | 61.144 | 0.010943 | 120.62 | 1127.5 |  | 12054 | 152.55 | 3.9646 | 61.144 | 0.010943 | 120.62 | 1127.5 | 1006.88
12055 | 3.9656 | 152.56 | 61.144 | 0.010945 | 120.63 | 1127.5 |  | 12055 | 152.56 | 3.9656 | 61.144 | 0.010945 | 120.63 | 1127.5 | 1006.87
12056 | 3.9665 | 152.57 | 61.144 | 0.010948 | 120.64 | 1127.5 |  | 12056 | 152.57 | 3.9665 | 61.144 | 0.010948 | 120.64 | 1127.5 | 1006.86
12057 | 3.9675 | 152.58 | 61.144 | 0.01095 | 120.65 | 1127.6 |  | 12057 | 152.58 | 3.9675 | 61.144 | 0.01095 | 120.65 | 1127.6 | 1006.95
12058 | 3.9685 | 152.59 | 61.143 | 0.010953 | 120.66 | 1127.6 |  | 12058 | 152.59 | 3.9685 | 61.143 | 0.010953 | 120.66 | 1127.6 | 1006.94
12059 | 3.9695 | 152.6 | 61.143 | 0.010955 | 120.67 | 1127.6 |  | 12059 | 152.6 | 3.9695 | 61.143 | 0.010955 | 120.67 | 1127.6 | 1006.93
12060 | 3.9704 | 152.61 | 61.143 | 0.010958 | 120.68 | 1127.6 |  | 12060 | 152.61 | 3.9704 | 61.143 | 0.010958 | 120.68 | 1127.6 | 1006.92
12061 | 3.9714 | 152.62 | 61.143 | 0.01096 | 120.69 | 1127.6 |  | 12061 | 152.62 | 3.9714 | 61.143 | 0.01096 | 120.69 | 1127.6 | 1006.91
12062 | 3.9724 | 152.63 | 61.143 | 0.010963 | 120.7 | 1127.6 |  | 12062 | 152.63 | 3.9724 | 61.143 | 0.010963 | 120.7 | 1127.6 | 1006.9
12063 | 3.9734 | 152.64 | 61.142 | 0.010965 | 120.71 | 1127.6 |  | 12063 | 152.64 | 3.9734 | 61.142 | 0.010965 | 120.71 | 1127.6 | 1006.89
12064 | 3.9743 | 152.65 | 61.142 | 0.010968 | 120.72 | 1127.6 |  | 12064 | 152.65 | 3.9743 | 61.142 | 0.010968 | 120.72 | 1127.6 | 1006.88
12065 | 3.9753 | 152.66 | 61.142 | 0.010971 | 120.73 | 1127.6 |  | 12065 | 152.66 | 3.9753 | 61.142 | 0.010971 | 120.73 | 1127.6 | 1006.87
12066 | 3.9763 | 152.67 | 61.142 | 0.010973 | 120.74 | 1127.6 |  | 12066 | 152.67 | 3.9763 | 61.142 | 0.010973 | 120.74 | 1127.6 | 1006.86
12067 | 3.9773 | 152.68 | 61.142 | 0.010976 | 120.75 | 1127.6 |  | 12067 | 152.68 | 3.9773 | 61.142 | 0.010976 | 120.75 | 1127.6 | 1006.85
12068 | 3.9782 | 152.69 | 61.141 | 0.010978 | 120.76 | 1127.6 |  | 12068 | 152.69 | 3.9782 | 61.141 | 0.010978 | 120.76 | 1127.6 | 1006.84
12069 | 3.9792 | 152.7 | 61.141 | 0.010981 | 120.77 | 1127.6 |  | 12069 | 152.7 | 3.9792 | 61.141 | 0.010981 | 120.77 | 1127.6 | 1006.83
12070 | 3.9802 | 152.71 | 61.141 | 0.010983 | 120.78 | 1127.6 |  | 12070 | 152.71 | 3.9802 | 61.141 | 0.010983 | 120.78 | 1127.6 | 1006.82
12071 | 3.9812 | 152.72 | 61.141 | 0.010986 | 120.79 | 1127.6 |  | 12071 | 152.72 | 3.9812 | 61.141 | 0.010986 | 120.79 | 1127.6 | 1006.81
12072 | 3.9821 | 152.73 | 61.141 | 0.010988 | 120.8 | 1127.6 |  | 12072 | 152.73 | 3.9821 | 61.141 | 0.010988 | 120.8 | 1127.6 | 1006.8
12073 | 3.9831 | 152.74 | 61.141 | 0.010991 | 120.81 | 1127.6 |  | 12073 | 152.74 | 3.9831 | 61.141 | 0.010991 | 120.81 | 1127.6 | 1006.79
12074 | 3.9841 | 152.75 | 61.14 | 0.010993 | 120.82 | 1127.6 |  | 12074 | 152.75 | 3.9841 | 61.14 | 0.010993 | 120.82 | 1127.6 | 1006.78
12075 | 3.9851 | 152.76 | 61.14 | 0.010996 | 120.83 | 1127.6 |  | 12075 | 152.76 | 3.9851 | 61.14 | 0.010996 | 120.83 | 1127.6 | 1006.77
12076 | 3.986 | 152.77 | 61.14 | 0.010998 | 120.84 | 1127.6 |  | 12076 | 152.77 | 3.986 | 61.14 | 0.010998 | 120.84 | 1127.6 | 1006.76
12077 | 3.987 | 152.78 | 61.14 | 0.011001 | 120.85 | 1127.6 |  | 12077 | 152.78 | 3.987 | 61.14 | 0.011001 | 120.85 | 1127.6 | 1006.75
12078 | 3.988 | 152.79 | 61.14 | 0.011003 | 120.86 | 1127.6 |  | 12078 | 152.79 | 3.988 | 61.14 | 0.011003 | 120.86 | 1127.6 | 1006.74
12079 | 3.989 | 152.8 | 61.139 | 0.011006 | 120.87 | 1127.6 |  | 12079 | 152.8 | 3.989 | 61.139 | 0.011006 | 120.87 | 1127.6 | 1006.73
12080 | 3.9899 | 152.81 | 61.139 | 0.011008 | 120.88 | 1127.6 |  | 12080 | 152.81 | 3.9899 | 61.139 | 0.011008 | 120.88 | 1127.6 | 1006.72
12081 | 3.9909 | 152.82 | 61.139 | 0.011011 | 120.89 | 1127.7 |  | 12081 | 152.82 | 3.9909 | 61.139 | 0.011011 | 120.89 | 1127.7 | 1006.81
12082 | 3.9919 | 152.83 | 61.139 | 0.011013 | 120.9 | 1127.7 |  | 12082 | 152.83 | 3.9919 | 61.139 | 0.011013 | 120.9 | 1127.7 | 1006.8
12083 | 3.9929 | 152.84 | 61.139 | 0.011016 | 120.91 | 1127.7 |  | 12083 | 152.84 | 3.9929 | 61.139 | 0.011016 | 120.91 | 1127.7 | 1006.79
12084 | 3.9939 | 152.85 | 61.138 | 0.011019 | 120.92 | 1127.7 |  | 12084 | 152.85 | 3.9939 | 61.138 | 0.011019 | 120.92 | 1127.7 | 1006.78
12085 | 3.9948 | 152.86 | 61.138 | 0.011021 | 120.93 | 1127.7 |  | 12085 | 152.86 | 3.9948 | 61.138 | 0.011021 | 120.93 | 1127.7 | 1006.77
12086 | 3.9958 | 152.87 | 61.138 | 0.011024 | 120.94 | 1127.7 |  | 12086 | 152.87 | 3.9958 | 61.138 | 0.011024 | 120.94 | 1127.7 | 1006.76
12087 | 3.9968 | 152.88 | 61.138 | 0.011026 | 120.95 | 1127.7 |  | 12087 | 152.88 | 3.9968 | 61.138 | 0.011026 | 120.95 | 1127.7 | 1006.75
12088 | 3.9978 | 152.89 | 61.138 | 0.011029 | 120.96 | 1127.7 |  | 12088 | 152.89 | 3.9978 | 61.138 | 0.011029 | 120.96 | 1127.7 | 1006.74
12089 | 3.9987 | 152.9 | 61.137 | 0.011031 | 120.97 | 1127.7 |  | 12089 | 152.9 | 3.9987 | 61.137 | 0.011031 | 120.97 | 1127.7 | 1006.73
12090 | 3.9997 | 152.91 | 61.137 | 0.011034 | 120.98 | 1127.7 |  | 12090 | 152.91 | 3.9997 | 61.137 | 0.011034 | 120.98 | 1127.7 | 1006.72
12091 | 4.0007 | 152.92 | 61.137 | 0.011036 | 120.99 | 1127.7 |  | 12091 | 152.92 | 4.0007 | 61.137 | 0.011036 | 120.99 | 1127.7 | 1006.71
12092 | 4.0017 | 152.93 | 61.137 | 0.011039 | 121 | 1127.7 |  | 12092 | 152.93 | 4.0017 | 61.137 | 0.011039 | 121 | 1127.7 | 1006.7
12093 | 4.0027 | 152.94 | 61.137 | 0.011041 | 121.01 | 1127.7 |  | 12093 | 152.94 | 4.0027 | 61.137 | 0.011041 | 121.01 | 1127.7 | 1006.69
12094 | 4.0036 | 152.95 | 61.136 | 0.011044 | 121.02 | 1127.7 |  | 12094 | 152.95 | 4.0036 | 61.136 | 0.011044 | 121.02 | 1127.7 | 1006.68
12095 | 4.0046 | 152.96 | 61.136 | 0.011046 | 121.03 | 1127.7 |  | 12095 | 152.96 | 4.0046 | 61.136 | 0.011046 | 121.03 | 1127.7 | 1006.67
12096 | 4.0056 | 152.97 | 61.136 | 0.011049 | 121.04 | 1127.7 |  | 12096 | 152.97 | 4.0056 | 61.136 | 0.011049 | 121.04 | 1127.7 | 1006.66
12097 | 4.0066 | 152.98 | 61.136 | 0.011051 | 121.05 | 1127.7 |  | 12097 | 152.98 | 4.0066 | 61.136 | 0.011051 | 121.05 | 1127.7 | 1006.65
12098 | 4.0076 | 152.99 | 61.136 | 0.011054 | 121.06 | 1127.7 |  | 12098 | 152.99 | 4.0076 | 61.136 | 0.011054 | 121.06 | 1127.7 | 1006.64
12099 | 4.0085 | 153 | 61.136 | 0.011057 | 121.07 | 1127.7 |  | 12099 | 153 | 4.0085 | 61.136 | 0.011057 | 121.07 | 1127.7 | 1006.63
12100 | 4.0095 | 153.01 | 61.135 | 0.011059 | 121.08 | 1127.7 |  | 12100 | 153.01 | 4.0095 | 61.135 | 0.011059 | 121.08 | 1127.7 | 1006.62
12101 | 4.0105 | 153.02 | 61.135 | 0.011062 | 121.09 | 1127.7 |  | 12101 | 153.02 | 4.0105 | 61.135 | 0.011062 | 121.09 | 1127.7 | 1006.61
12102 | 4.0115 | 153.03 | 61.135 | 0.011064 | 121.1 | 1127.7 |  | 12102 | 153.03 | 4.0115 | 61.135 | 0.011064 | 121.1 | 1127.7 | 1006.6
12103 | 4.0125 | 153.04 | 61.135 | 0.011067 | 121.11 | 1127.7 |  | 12103 | 153.04 | 4.0125 | 61.135 | 0.011067 | 121.11 | 1127.7 | 1006.59
12104 | 4.0135 | 153.05 | 61.135 | 0.011069 | 121.12 | 1127.7 |  | 12104 | 153.05 | 4.0135 | 61.135 | 0.011069 | 121.12 | 1127.7 | 1006.58
12105 | 4.0144 | 153.06 | 61.134 | 0.011072 | 121.13 | 1127.7 |  | 12105 | 153.06 | 4.0144 | 61.134 | 0.011072 | 121.13 | 1127.7 | 1006.57
12106 | 4.0154 | 153.07 | 61.134 | 0.011074 | 121.14 | 1127.8 |  | 12106 | 153.07 | 4.0154 | 61.134 | 0.011074 | 121.14 | 1127.8 | 1006.66
12107 | 4.0164 | 153.08 | 61.134 | 0.011077 | 121.15 | 1127.8 |  | 12107 | 153.08 | 4.0164 | 61.134 | 0.011077 | 121.15 | 1127.8 | 1006.65
12108 | 4.0174 | 153.09 | 61.134 | 0.011079 | 121.16 | 1127.8 |  | 12108 | 153.09 | 4.0174 | 61.134 | 0.011079 | 121.16 | 1127.8 | 1006.64
12109 | 4.0184 | 153.1 | 61.134 | 0.011082 | 121.17 | 1127.8 |  | 12109 | 153.1 | 4.0184 | 61.134 | 0.011082 | 121.17 | 1127.8 | 1006.63
12110 | 4.0194 | 153.11 | 61.133 | 0.011084 | 121.18 | 1127.8 |  | 12110 | 153.11 | 4.0194 | 61.133 | 0.011084 | 121.18 | 1127.8 | 1006.62
12111 | 4.0203 | 153.12 | 61.133 | 0.011087 | 121.19 | 1127.8 |  | 12111 | 153.12 | 4.0203 | 61.133 | 0.011087 | 121.19 | 1127.8 | 1006.61
12112 | 4.0213 | 153.13 | 61.133 | 0.01109 | 121.2 | 1127.8 |  | 12112 | 153.13 | 4.0213 | 61.133 | 0.01109 | 121.2 | 1127.8 | 1006.6
12113 | 4.0223 | 153.14 | 61.133 | 0.011092 | 121.21 | 1127.8 |  | 12113 | 153.14 | 4.0223 | 61.133 | 0.011092 | 121.21 | 1127.8 | 1006.59
12114 | 4.0233 | 153.15 | 61.133 | 0.011095 | 121.22 | 1127.8 |  | 12114 | 153.15 | 4.0233 | 61.133 | 0.011095 | 121.22 | 1127.8 | 1006.58
12115 | 4.0243 | 153.16 | 61.132 | 0.011097 | 121.23 | 1127.8 |  | 12115 | 153.16 | 4.0243 | 61.132 | 0.011097 | 121.23 | 1127.8 | 1006.57
12116 | 4.0253 | 153.17 | 61.132 | 0.0111 | 121.24 | 1127.8 |  | 12116 | 153.17 | 4.0253 | 61.132 | 0.0111 | 121.24 | 1127.8 | 1006.56
12117 | 4.0262 | 153.18 | 61.132 | 0.011102 | 121.25 | 1127.8 |  | 12117 | 153.18 | 4.0262 | 61.132 | 0.011102 | 121.25 | 1127.8 | 1006.55
12118 | 4.0272 | 153.19 | 61.132 | 0.011105 | 121.26 | 1127.8 |  | 12118 | 153.19 | 4.0272 | 61.132 | 0.011105 | 121.26 | 1127.8 | 1006.54
12119 | 4.0282 | 153.2 | 61.132 | 0.011107 | 121.27 | 1127.8 |  | 12119 | 153.2 | 4.0282 | 61.132 | 0.011107 | 121.27 | 1127.8 | 1006.53
12120 | 4.0292 | 153.21 | 61.131 | 0.01111 | 121.28 | 1127.8 |  | 12120 | 153.21 | 4.0292 | 61.131 | 0.01111 | 121.28 | 1127.8 | 1006.52
12121 | 4.0302 | 153.22 | 61.131 | 0.011112 | 121.29 | 1127.8 |  | 12121 | 153.22 | 4.0302 | 61.131 | 0.011112 | 121.29 | 1127.8 | 1006.51
12122 | 4.0312 | 153.23 | 61.131 | 0.011115 | 121.3 | 1127.8 |  | 12122 | 153.23 | 4.0312 | 61.131 | 0.011115 | 121.3 | 1127.8 | 1006.5
12123 | 4.0322 | 153.24 | 61.131 | 0.011118 | 121.31 | 1127.8 |  | 12123 | 153.24 | 4.0322 | 61.131 | 0.011118 | 121.31 | 1127.8 | 1006.49
12124 | 4.0331 | 153.25 | 61.131 | 0.01112 | 121.32 | 1127.8 |  | 12124 | 153.25 | 4.0331 | 61.131 | 0.01112 | 121.32 | 1127.8 | 1006.48
12125 | 4.0341 | 153.26 | 61.131 | 0.011123 | 121.33 | 1127.8 |  | 12125 | 153.26 | 4.0341 | 61.131 | 0.011123 | 121.33 | 1127.8 | 1006.47
12126 | 4.0351 | 153.27 | 61.13 | 0.011125 | 121.34 | 1127.8 |  | 12126 | 153.27 | 4.0351 | 61.13 | 0.011125 | 121.34 | 1127.8 | 1006.46
12127 | 4.0361 | 153.28 | 61.13 | 0.011128 | 121.35 | 1127.8 |  | 12127 | 153.28 | 4.0361 | 61.13 | 0.011128 | 121.35 | 1127.8 | 1006.45
12128 | 4.0371 | 153.29 | 61.13 | 0.01113 | 121.36 | 1127.8 |  | 12128 | 153.29 | 4.0371 | 61.13 | 0.01113 | 121.36 | 1127.8 | 1006.44
12129 | 4.0381 | 153.3 | 61.13 | 0.011133 | 121.37 | 1127.8 |  | 12129 | 153.3 | 4.0381 | 61.13 | 0.011133 | 121.37 | 1127.8 | 1006.43
12130 | 4.0391 | 153.31 | 61.13 | 0.011135 | 121.38 | 1127.9 |  | 12130 | 153.31 | 4.0391 | 61.13 | 0.011135 | 121.38 | 1127.9 | 1006.52
12131 | 4.0401 | 153.32 | 61.129 | 0.011138 | 121.39 | 1127.9 |  | 12131 | 153.32 | 4.0401 | 61.129 | 0.011138 | 121.39 | 1127.9 | 1006.51
12132 | 4.041 | 153.33 | 61.129 | 0.011141 | 121.4 | 1127.9 |  | 12132 | 153.33 | 4.041 | 61.129 | 0.011141 | 121.4 | 1127.9 | 1006.5
12133 | 4.042 | 153.34 | 61.129 | 0.011143 | 121.41 | 1127.9 |  | 12133 | 153.34 | 4.042 | 61.129 | 0.011143 | 121.41 | 1127.9 | 1006.49
12134 | 4.043 | 153.35 | 61.129 | 0.011146 | 121.42 | 1127.9 |  | 12134 | 153.35 | 4.043 | 61.129 | 0.011146 | 121.42 | 1127.9 | 1006.48
12135 | 4.044 | 153.36 | 61.129 | 0.011148 | 121.43 | 1127.9 |  | 12135 | 153.36 | 4.044 | 61.129 | 0.011148 | 121.43 | 1127.9 | 1006.47
12136 | 4.045 | 153.37 | 61.128 | 0.011151 | 121.44 | 1127.9 |  | 12136 | 153.37 | 4.045 | 61.128 | 0.011151 | 121.44 | 1127.9 | 1006.46
12137 | 4.046 | 153.38 | 61.128 | 0.011153 | 121.45 | 1127.9 |  | 12137 | 153.38 | 4.046 | 61.128 | 0.011153 | 121.45 | 1127.9 | 1006.45
12138 | 4.047 | 153.39 | 61.128 | 0.011156 | 121.46 | 1127.9 |  | 12138 | 153.39 | 4.047 | 61.128 | 0.011156 | 121.46 | 1127.9 | 1006.44
12139 | 4.048 | 153.4 | 61.128 | 0.011158 | 121.47 | 1127.9 |  | 12139 | 153.4 | 4.048 | 61.128 | 0.011158 | 121.47 | 1127.9 | 1006.43
12140 | 4.0489 | 153.41 | 61.128 | 0.011161 | 121.48 | 1127.9 |  | 12140 | 153.41 | 4.0489 | 61.128 | 0.011161 | 121.48 | 1127.9 | 1006.42
12141 | 4.0499 | 153.42 | 61.127 | 0.011164 | 121.49 | 1127.9 |  | 12141 | 153.42 | 4.0499 | 61.127 | 0.011164 | 121.49 | 1127.9 | 1006.41
12142 | 4.0509 | 153.43 | 61.127 | 0.011166 | 121.5 | 1127.9 |  | 12142 | 153.43 | 4.0509 | 61.127 | 0.011166 | 121.5 | 1127.9 | 1006.4
12143 | 4.0519 | 153.44 | 61.127 | 0.011169 | 121.51 | 1127.9 |  | 12143 | 153.44 | 4.0519 | 61.127 | 0.011169 | 121.51 | 1127.9 | 1006.39
12144 | 4.0529 | 153.45 | 61.127 | 0.011171 | 121.52 | 1127.9 |  | 12144 | 153.45 | 4.0529 | 61.127 | 0.011171 | 121.52 | 1127.9 | 1006.38
12145 | 4.0539 | 153.46 | 61.127 | 0.011174 | 121.53 | 1127.9 |  | 12145 | 153.46 | 4.0539 | 61.127 | 0.011174 | 121.53 | 1127.9 | 1006.37
12146 | 4.0549 | 153.47 | 61.126 | 0.011176 | 121.54 | 1127.9 |  | 12146 | 153.47 | 4.0549 | 61.126 | 0.011176 | 121.54 | 1127.9 | 1006.36
12147 | 4.0559 | 153.48 | 61.126 | 0.011179 | 121.55 | 1127.9 |  | 12147 | 153.48 | 4.0559 | 61.126 | 0.011179 | 121.55 | 1127.9 | 1006.35
12148 | 4.0569 | 153.49 | 61.126 | 0.011181 | 121.56 | 1127.9 |  | 12148 | 153.49 | 4.0569 | 61.126 | 0.011181 | 121.56 | 1127.9 | 1006.34
12149 | 4.0579 | 153.5 | 61.126 | 0.011184 | 121.57 | 1127.9 |  | 12149 | 153.5 | 4.0579 | 61.126 | 0.011184 | 121.57 | 1127.9 | 1006.33
12150 | 4.0589 | 153.51 | 61.126 | 0.011187 | 121.58 | 1127.9 |  | 12150 | 153.51 | 4.0589 | 61.126 | 0.011187 | 121.58 | 1127.9 | 1006.32
12151 | 4.0598 | 153.52 | 61.125 | 0.011189 | 121.59 | 1127.9 |  | 12151 | 153.52 | 4.0598 | 61.125 | 0.011189 | 121.59 | 1127.9 | 1006.31
12152 | 4.0608 | 153.53 | 61.125 | 0.011192 | 121.6 | 1127.9 |  | 12152 | 153.53 | 4.0608 | 61.125 | 0.011192 | 121.6 | 1127.9 | 1006.3
12153 | 4.0618 | 153.54 | 61.125 | 0.011194 | 121.61 | 1127.9 |  | 12153 | 153.54 | 4.0618 | 61.125 | 0.011194 | 121.61 | 1127.9 | 1006.29
12154 | 4.0628 | 153.55 | 61.125 | 0.011197 | 121.62 | 1128 |  | 12154 | 153.55 | 4.0628 | 61.125 | 0.011197 | 121.62 | 1128 | 1006.38
12155 | 4.0638 | 153.56 | 61.125 | 0.011199 | 121.63 | 1128 |  | 12155 | 153.56 | 4.0638 | 61.125 | 0.011199 | 121.63 | 1128 | 1006.37
12156 | 4.0648 | 153.57 | 61.125 | 0.011202 | 121.64 | 1128 |  | 12156 | 153.57 | 4.0648 | 61.125 | 0.011202 | 121.64 | 1128 | 1006.36
12157 | 4.0658 | 153.58 | 61.124 | 0.011205 | 121.65 | 1128 |  | 12157 | 153.58 | 4.0658 | 61.124 | 0.011205 | 121.65 | 1128 | 1006.35
12158 | 4.0668 | 153.59 | 61.124 | 0.011207 | 121.66 | 1128 |  | 12158 | 153.59 | 4.0668 | 61.124 | 0.011207 | 121.66 | 1128 | 1006.34
12159 | 4.0678 | 153.6 | 61.124 | 0.01121 | 121.67 | 1128 |  | 12159 | 153.6 | 4.0678 | 61.124 | 0.01121 | 121.67 | 1128 | 1006.33
12160 | 4.0688 | 153.61 | 61.124 | 0.011212 | 121.68 | 1128 |  | 12160 | 153.61 | 4.0688 | 61.124 | 0.011212 | 121.68 | 1128 | 1006.32
12161 | 4.0698 | 153.62 | 61.124 | 0.011215 | 121.69 | 1128 |  | 12161 | 153.62 | 4.0698 | 61.124 | 0.011215 | 121.69 | 1128 | 1006.31
12162 | 4.0708 | 153.63 | 61.123 | 0.011217 | 121.7 | 1128 |  | 12162 | 153.63 | 4.0708 | 61.123 | 0.011217 | 121.7 | 1128 | 1006.3
12163 | 4.0718 | 153.64 | 61.123 | 0.01122 | 121.71 | 1128 |  | 12163 | 153.64 | 4.0718 | 61.123 | 0.01122 | 121.71 | 1128 | 1006.29
12164 | 4.0728 | 153.65 | 61.123 | 0.011223 | 121.72 | 1128 |  | 12164 | 153.65 | 4.0728 | 61.123 | 0.011223 | 121.72 | 1128 | 1006.28
12165 | 4.0738 | 153.66 | 61.123 | 0.011225 | 121.73 | 1128 |  | 12165 | 153.66 | 4.0738 | 61.123 | 0.011225 | 121.73 | 1128 | 1006.27
12166 | 4.0747 | 153.67 | 61.123 | 0.011228 | 121.74 | 1128 |  | 12166 | 153.67 | 4.0747 | 61.123 | 0.011228 | 121.74 | 1128 | 1006.26
12167 | 4.0757 | 153.68 | 61.122 | 0.01123 | 121.75 | 1128 |  | 12167 | 153.68 | 4.0757 | 61.122 | 0.01123 | 121.75 | 1128 | 1006.25
12168 | 4.0767 | 153.69 | 61.122 | 0.011233 | 121.76 | 1128 |  | 12168 | 153.69 | 4.0767 | 61.122 | 0.011233 | 121.76 | 1128 | 1006.24
12169 | 4.0777 | 153.7 | 61.122 | 0.011235 | 121.77 | 1128 |  | 12169 | 153.7 | 4.0777 | 61.122 | 0.011235 | 121.77 | 1128 | 1006.23
12170 | 4.0787 | 153.71 | 61.122 | 0.011238 | 121.78 | 1128 |  | 12170 | 153.71 | 4.0787 | 61.122 | 0.011238 | 121.78 | 1128 | 1006.22
12171 | 4.0797 | 153.72 | 61.122 | 0.011241 | 121.79 | 1128 |  | 12171 | 153.72 | 4.0797 | 61.122 | 0.011241 | 121.79 | 1128 | 1006.21
12172 | 4.0807 | 153.73 | 61.121 | 0.011243 | 121.8 | 1128 |  | 12172 | 153.73 | 4.0807 | 61.121 | 0.011243 | 121.8 | 1128 | 1006.2
12173 | 4.0817 | 153.74 | 61.121 | 0.011246 | 121.81 | 1128 |  | 12173 | 153.74 | 4.0817 | 61.121 | 0.011246 | 121.81 | 1128 | 1006.19
12174 | 4.0827 | 153.75 | 61.121 | 0.011248 | 121.82 | 1128 |  | 12174 | 153.75 | 4.0827 | 61.121 | 0.011248 | 121.82 | 1128 | 1006.18
12175 | 4.0837 | 153.76 | 61.121 | 0.011251 | 121.83 | 1128 |  | 12175 | 153.76 | 4.0837 | 61.121 | 0.011251 | 121.83 | 1128 | 1006.17
12176 | 4.0847 | 153.77 | 61.121 | 0.011253 | 121.84 | 1128 |  | 12176 | 153.77 | 4.0847 | 61.121 | 0.011253 | 121.84 | 1128 | 1006.16
12177 | 4.0857 | 153.78 | 61.12 | 0.011256 | 121.85 | 1128 |  | 12177 | 153.78 | 4.0857 | 61.12 | 0.011256 | 121.85 | 1128 | 1006.15
12178 | 4.0867 | 153.79 | 61.12 | 0.011259 | 121.86 | 1128 |  | 12178 | 153.79 | 4.0867 | 61.12 | 0.011259 | 121.86 | 1128 | 1006.14
12179 | 4.0877 | 153.8 | 61.12 | 0.011261 | 121.87 | 1128.1 |  | 12179 | 153.8 | 4.0877 | 61.12 | 0.011261 | 121.87 | 1128.1 | 1006.23
12180 | 4.0887 | 153.81 | 61.12 | 0.011264 | 121.88 | 1128.1 |  | 12180 | 153.81 | 4.0887 | 61.12 | 0.011264 | 121.88 | 1128.1 | 1006.22
12181 | 4.0897 | 153.82 | 61.12 | 0.011266 | 121.89 | 1128.1 |  | 12181 | 153.82 | 4.0897 | 61.12 | 0.011266 | 121.89 | 1128.1 | 1006.21
12182 | 4.0907 | 153.83 | 61.12 | 0.011269 | 121.9 | 1128.1 |  | 12182 | 153.83 | 4.0907 | 61.12 | 0.011269 | 121.9 | 1128.1 | 1006.2
12183 | 4.0917 | 153.84 | 61.119 | 0.011271 | 121.91 | 1128.1 |  | 12183 | 153.84 | 4.0917 | 61.119 | 0.011271 | 121.91 | 1128.1 | 1006.19
12184 | 4.0927 | 153.85 | 61.119 | 0.011274 | 121.92 | 1128.1 |  | 12184 | 153.85 | 4.0927 | 61.119 | 0.011274 | 121.92 | 1128.1 | 1006.18
12185 | 4.0937 | 153.86 | 61.119 | 0.011277 | 121.93 | 1128.1 |  | 12185 | 153.86 | 4.0937 | 61.119 | 0.011277 | 121.93 | 1128.1 | 1006.17
12186 | 4.0947 | 153.87 | 61.119 | 0.011279 | 121.94 | 1128.1 |  | 12186 | 153.87 | 4.0947 | 61.119 | 0.011279 | 121.94 | 1128.1 | 1006.16
12187 | 4.0957 | 153.88 | 61.119 | 0.011282 | 121.95 | 1128.1 |  | 12187 | 153.88 | 4.0957 | 61.119 | 0.011282 | 121.95 | 1128.1 | 1006.15
12188 | 4.0967 | 153.89 | 61.118 | 0.011284 | 121.96 | 1128.1 |  | 12188 | 153.89 | 4.0967 | 61.118 | 0.011284 | 121.96 | 1128.1 | 1006.14
12189 | 4.0977 | 153.9 | 61.118 | 0.011287 | 121.97 | 1128.1 |  | 12189 | 153.9 | 4.0977 | 61.118 | 0.011287 | 121.97 | 1128.1 | 1006.13
12190 | 4.0987 | 153.91 | 61.118 | 0.011289 | 121.98 | 1128.1 |  | 12190 | 153.91 | 4.0987 | 61.118 | 0.011289 | 121.98 | 1128.1 | 1006.12
12191 | 4.0997 | 153.92 | 61.118 | 0.011292 | 121.99 | 1128.1 |  | 12191 | 153.92 | 4.0997 | 61.118 | 0.011292 | 121.99 | 1128.1 | 1006.11
12192 | 4.1007 | 153.93 | 61.118 | 0.011295 | 122 | 1128.1 |  | 12192 | 153.93 | 4.1007 | 61.118 | 0.011295 | 122 | 1128.1 | 1006.1
12193 | 4.1017 | 153.94 | 61.117 | 0.011297 | 122.01 | 1128.1 |  | 12193 | 153.94 | 4.1017 | 61.117 | 0.011297 | 122.01 | 1128.1 | 1006.09
12194 | 4.1027 | 153.95 | 61.117 | 0.0113 | 122.02 | 1128.1 |  | 12194 | 153.95 | 4.1027 | 61.117 | 0.0113 | 122.02 | 1128.1 | 1006.08
12195 | 4.1037 | 153.96 | 61.117 | 0.011302 | 122.03 | 1128.1 |  | 12195 | 153.96 | 4.1037 | 61.117 | 0.011302 | 122.03 | 1128.1 | 1006.07
12196 | 4.1047 | 153.97 | 61.117 | 0.011305 | 122.04 | 1128.1 |  | 12196 | 153.97 | 4.1047 | 61.117 | 0.011305 | 122.04 | 1128.1 | 1006.06
12197 | 4.1057 | 153.98 | 61.117 | 0.011308 | 122.05 | 1128.1 |  | 12197 | 153.98 | 4.1057 | 61.117 | 0.011308 | 122.05 | 1128.1 | 1006.05
12198 | 4.1067 | 153.99 | 61.116 | 0.01131 | 122.06 | 1128.1 |  | 12198 | 153.99 | 4.1067 | 61.116 | 0.01131 | 122.06 | 1128.1 | 1006.04
12199 | 4.1077 | 154 | 61.116 | 0.011313 | 122.07 | 1128.1 |  | 12199 | 154 | 4.1077 | 61.116 | 0.011313 | 122.07 | 1128.1 | 1006.03
12200 | 4.1087 | 154.01 | 61.116 | 0.011315 | 122.08 | 1128.1 |  | 12200 | 154.01 | 4.1087 | 61.116 | 0.011315 | 122.08 | 1128.1 | 1006.02
12201 | 4.1097 | 154.02 | 61.116 | 0.011318 | 122.09 | 1128.1 |  | 12201 | 154.02 | 4.1097 | 61.116 | 0.011318 | 122.09 | 1128.1 | 1006.01
12202 | 4.1107 | 154.03 | 61.116 | 0.011321 | 122.1 | 1128.1 |  | 12202 | 154.03 | 4.1107 | 61.116 | 0.011321 | 122.1 | 1128.1 | 1006
12203 | 4.1117 | 154.04 | 61.115 | 0.011323 | 122.11 | 1128.2 |  | 12203 | 154.04 | 4.1117 | 61.115 | 0.011323 | 122.11 | 1128.2 | 1006.09
12204 | 4.1127 | 154.05 | 61.115 | 0.011326 | 122.12 | 1128.2 |  | 12204 | 154.05 | 4.1127 | 61.115 | 0.011326 | 122.12 | 1128.2 | 1006.08
12205 | 4.1137 | 154.06 | 61.115 | 0.011328 | 122.13 | 1128.2 |  | 12205 | 154.06 | 4.1137 | 61.115 | 0.011328 | 122.13 | 1128.2 | 1006.07
12206 | 4.1147 | 154.07 | 61.115 | 0.011331 | 122.14 | 1128.2 |  | 12206 | 154.07 | 4.1147 | 61.115 | 0.011331 | 122.14 | 1128.2 | 1006.06
12207 | 4.1157 | 154.08 | 61.115 | 0.011333 | 122.15 | 1128.2 |  | 12207 | 154.08 | 4.1157 | 61.115 | 0.011333 | 122.15 | 1128.2 | 1006.05
12208 | 4.1167 | 154.09 | 61.114 | 0.011336 | 122.16 | 1128.2 |  | 12208 | 154.09 | 4.1167 | 61.114 | 0.011336 | 122.16 | 1128.2 | 1006.04
12209 | 4.1177 | 154.1 | 61.114 | 0.011339 | 122.17 | 1128.2 |  | 12209 | 154.1 | 4.1177 | 61.114 | 0.011339 | 122.17 | 1128.2 | 1006.03
12210 | 4.1187 | 154.11 | 61.114 | 0.011341 | 122.18 | 1128.2 |  | 12210 | 154.11 | 4.1187 | 61.114 | 0.011341 | 122.18 | 1128.2 | 1006.02
12211 | 4.1197 | 154.12 | 61.114 | 0.011344 | 122.19 | 1128.2 |  | 12211 | 154.12 | 4.1197 | 61.114 | 0.011344 | 122.19 | 1128.2 | 1006.01
12212 | 4.1207 | 154.13 | 61.114 | 0.011346 | 122.2 | 1128.2 |  | 12212 | 154.13 | 4.1207 | 61.114 | 0.011346 | 122.2 | 1128.2 | 1006
12213 | 4.1217 | 154.14 | 61.114 | 0.011349 | 122.21 | 1128.2 |  | 12213 | 154.14 | 4.1217 | 61.114 | 0.011349 | 122.21 | 1128.2 | 1005.99
12214 | 4.1227 | 154.15 | 61.113 | 0.011352 | 122.22 | 1128.2 |  | 12214 | 154.15 | 4.1227 | 61.113 | 0.011352 | 122.22 | 1128.2 | 1005.98
12215 | 4.1237 | 154.16 | 61.113 | 0.011354 | 122.23 | 1128.2 |  | 12215 | 154.16 | 4.1237 | 61.113 | 0.011354 | 122.23 | 1128.2 | 1005.97
12216 | 4.1248 | 154.17 | 61.113 | 0.011357 | 122.24 | 1128.2 |  | 12216 | 154.17 | 4.1248 | 61.113 | 0.011357 | 122.24 | 1128.2 | 1005.96
12217 | 4.1258 | 154.18 | 61.113 | 0.011359 | 122.25 | 1128.2 |  | 12217 | 154.18 | 4.1258 | 61.113 | 0.011359 | 122.25 | 1128.2 | 1005.95
12218 | 4.1268 | 154.19 | 61.113 | 0.011362 | 122.26 | 1128.2 |  | 12218 | 154.19 | 4.1268 | 61.113 | 0.011362 | 122.26 | 1128.2 | 1005.94
12219 | 4.1278 | 154.2 | 61.112 | 0.011365 | 122.27 | 1128.2 |  | 12219 | 154.2 | 4.1278 | 61.112 | 0.011365 | 122.27 | 1128.2 | 1005.93
12220 | 4.1288 | 154.21 | 61.112 | 0.011367 | 122.28 | 1128.2 |  | 12220 | 154.21 | 4.1288 | 61.112 | 0.011367 | 122.28 | 1128.2 | 1005.92
12221 | 4.1298 | 154.22 | 61.112 | 0.01137 | 122.29 | 1128.2 |  | 12221 | 154.22 | 4.1298 | 61.112 | 0.01137 | 122.29 | 1128.2 | 1005.91
12222 | 4.1308 | 154.23 | 61.112 | 0.011372 | 122.3 | 1128.2 |  | 12222 | 154.23 | 4.1308 | 61.112 | 0.011372 | 122.3 | 1128.2 | 1005.9
12223 | 4.1318 | 154.24 | 61.112 | 0.011375 | 122.31 | 1128.2 |  | 12223 | 154.24 | 4.1318 | 61.112 | 0.011375 | 122.31 | 1128.2 | 1005.89
12224 | 4.1328 | 154.25 | 61.111 | 0.011378 | 122.32 | 1128.2 |  | 12224 | 154.25 | 4.1328 | 61.111 | 0.011378 | 122.32 | 1128.2 | 1005.88
12225 | 4.1338 | 154.26 | 61.111 | 0.01138 | 122.33 | 1128.2 |  | 12225 | 154.26 | 4.1338 | 61.111 | 0.01138 | 122.33 | 1128.2 | 1005.87
12226 | 4.1348 | 154.27 | 61.111 | 0.011383 | 122.34 | 1128.2 |  | 12226 | 154.27 | 4.1348 | 61.111 | 0.011383 | 122.34 | 1128.2 | 1005.86
12227 | 4.1358 | 154.28 | 61.111 | 0.011385 | 122.35 | 1128.3 |  | 12227 | 154.28 | 4.1358 | 61.111 | 0.011385 | 122.35 | 1128.3 | 1005.95
12228 | 4.1368 | 154.29 | 61.111 | 0.011388 | 122.36 | 1128.3 |  | 12228 | 154.29 | 4.1368 | 61.111 | 0.011388 | 122.36 | 1128.3 | 1005.94
12229 | 4.1378 | 154.3 | 61.11 | 0.011391 | 122.37 | 1128.3 |  | 12229 | 154.3 | 4.1378 | 61.11 | 0.011391 | 122.37 | 1128.3 | 1005.93
12230 | 4.1388 | 154.31 | 61.11 | 0.011393 | 122.38 | 1128.3 |  | 12230 | 154.31 | 4.1388 | 61.11 | 0.011393 | 122.38 | 1128.3 | 1005.92
12231 | 4.1399 | 154.32 | 61.11 | 0.011396 | 122.39 | 1128.3 |  | 12231 | 154.32 | 4.1399 | 61.11 | 0.011396 | 122.39 | 1128.3 | 1005.91
12232 | 4.1409 | 154.33 | 61.11 | 0.011398 | 122.4 | 1128.3 |  | 12232 | 154.33 | 4.1409 | 61.11 | 0.011398 | 122.4 | 1128.3 | 1005.9
12233 | 4.1419 | 154.34 | 61.11 | 0.011401 | 122.41 | 1128.3 |  | 12233 | 154.34 | 4.1419 | 61.11 | 0.011401 | 122.41 | 1128.3 | 1005.89
12234 | 4.1429 | 154.35 | 61.109 | 0.011404 | 122.42 | 1128.3 |  | 12234 | 154.35 | 4.1429 | 61.109 | 0.011404 | 122.42 | 1128.3 | 1005.88
12235 | 4.1439 | 154.36 | 61.109 | 0.011406 | 122.43 | 1128.3 |  | 12235 | 154.36 | 4.1439 | 61.109 | 0.011406 | 122.43 | 1128.3 | 1005.87
12236 | 4.1449 | 154.37 | 61.109 | 0.011409 | 122.44 | 1128.3 |  | 12236 | 154.37 | 4.1449 | 61.109 | 0.011409 | 122.44 | 1128.3 | 1005.86
12237 | 4.1459 | 154.38 | 61.109 | 0.011411 | 122.45 | 1128.3 |  | 12237 | 154.38 | 4.1459 | 61.109 | 0.011411 | 122.45 | 1128.3 | 1005.85
12238 | 4.1469 | 154.39 | 61.109 | 0.011414 | 122.46 | 1128.3 |  | 12238 | 154.39 | 4.1469 | 61.109 | 0.011414 | 122.46 | 1128.3 | 1005.84
12239 | 4.1479 | 154.4 | 61.108 | 0.011417 | 122.47 | 1128.3 |  | 12239 | 154.4 | 4.1479 | 61.108 | 0.011417 | 122.47 | 1128.3 | 1005.83
12240 | 4.1489 | 154.41 | 61.108 | 0.011419 | 122.48 | 1128.3 |  | 12240 | 154.41 | 4.1489 | 61.108 | 0.011419 | 122.48 | 1128.3 | 1005.82
12241 | 4.1499 | 154.42 | 61.108 | 0.011422 | 122.49 | 1128.3 |  | 12241 | 154.42 | 4.1499 | 61.108 | 0.011422 | 122.49 | 1128.3 | 1005.81
12242 | 4.151 | 154.43 | 61.108 | 0.011424 | 122.5 | 1128.3 |  | 12242 | 154.43 | 4.151 | 61.108 | 0.011424 | 122.5 | 1128.3 | 1005.8
12243 | 4.152 | 154.44 | 61.108 | 0.011427 | 122.51 | 1128.3 |  | 12243 | 154.44 | 4.152 | 61.108 | 0.011427 | 122.51 | 1128.3 | 1005.79
12244 | 4.153 | 154.45 | 61.107 | 0.01143 | 122.52 | 1128.3 |  | 12244 | 154.45 | 4.153 | 61.107 | 0.01143 | 122.52 | 1128.3 | 1005.78
12245 | 4.154 | 154.46 | 61.107 | 0.011432 | 122.53 | 1128.3 |  | 12245 | 154.46 | 4.154 | 61.107 | 0.011432 | 122.53 | 1128.3 | 1005.77
12246 | 4.155 | 154.47 | 61.107 | 0.011435 | 122.54 | 1128.3 |  | 12246 | 154.47 | 4.155 | 61.107 | 0.011435 | 122.54 | 1128.3 | 1005.76
12247 | 4.156 | 154.48 | 61.107 | 0.011437 | 122.55 | 1128.3 |  | 12247 | 154.48 | 4.156 | 61.107 | 0.011437 | 122.55 | 1128.3 | 1005.75
12248 | 4.157 | 154.49 | 61.107 | 0.01144 | 122.56 | 1128.3 |  | 12248 | 154.49 | 4.157 | 61.107 | 0.01144 | 122.56 | 1128.3 | 1005.74
12249 | 4.158 | 154.5 | 61.107 | 0.011443 | 122.57 | 1128.3 |  | 12249 | 154.5 | 4.158 | 61.107 | 0.011443 | 122.57 | 1128.3 | 1005.73
12250 | 4.1591 | 154.51 | 61.106 | 0.011445 | 122.58 | 1128.3 |  | 12250 | 154.51 | 4.1591 | 61.106 | 0.011445 | 122.58 | 1128.3 | 1005.72
12251 | 4.1601 | 154.52 | 61.106 | 0.011448 | 122.59 | 1128.3 |  | 12251 | 154.52 | 4.1601 | 61.106 | 0.011448 | 122.59 | 1128.3 | 1005.71
12252 | 4.1611 | 154.53 | 61.106 | 0.011451 | 122.6 | 1128.4 |  | 12252 | 154.53 | 4.1611 | 61.106 | 0.011451 | 122.6 | 1128.4 | 1005.8
12253 | 4.1621 | 154.54 | 61.106 | 0.011453 | 122.61 | 1128.4 |  | 12253 | 154.54 | 4.1621 | 61.106 | 0.011453 | 122.61 | 1128.4 | 1005.79
12254 | 4.1631 | 154.55 | 61.106 | 0.011456 | 122.62 | 1128.4 |  | 12254 | 154.55 | 4.1631 | 61.106 | 0.011456 | 122.62 | 1128.4 | 1005.78
12255 | 4.1641 | 154.56 | 61.105 | 0.011458 | 122.63 | 1128.4 |  | 12255 | 154.56 | 4.1641 | 61.105 | 0.011458 | 122.63 | 1128.4 | 1005.77
12256 | 4.1651 | 154.57 | 61.105 | 0.011461 | 122.64 | 1128.4 |  | 12256 | 154.57 | 4.1651 | 61.105 | 0.011461 | 122.64 | 1128.4 | 1005.76
12257 | 4.1661 | 154.58 | 61.105 | 0.011464 | 122.65 | 1128.4 |  | 12257 | 154.58 | 4.1661 | 61.105 | 0.011464 | 122.65 | 1128.4 | 1005.75
12258 | 4.1672 | 154.59 | 61.105 | 0.011466 | 122.66 | 1128.4 |  | 12258 | 154.59 | 4.1672 | 61.105 | 0.011466 | 122.66 | 1128.4 | 1005.74
12259 | 4.1682 | 154.6 | 61.105 | 0.011469 | 122.67 | 1128.4 |  | 12259 | 154.6 | 4.1682 | 61.105 | 0.011469 | 122.67 | 1128.4 | 1005.73
12260 | 4.1692 | 154.61 | 61.104 | 0.011471 | 122.68 | 1128.4 |  | 12260 | 154.61 | 4.1692 | 61.104 | 0.011471 | 122.68 | 1128.4 | 1005.72
12261 | 4.1702 | 154.62 | 61.104 | 0.011474 | 122.69 | 1128.4 |  | 12261 | 154.62 | 4.1702 | 61.104 | 0.011474 | 122.69 | 1128.4 | 1005.71
12262 | 4.1712 | 154.63 | 61.104 | 0.011477 | 122.7 | 1128.4 |  | 12262 | 154.63 | 4.1712 | 61.104 | 0.011477 | 122.7 | 1128.4 | 1005.7
12263 | 4.1722 | 154.64 | 61.104 | 0.011479 | 122.71 | 1128.4 |  | 12263 | 154.64 | 4.1722 | 61.104 | 0.011479 | 122.71 | 1128.4 | 1005.69
12264 | 4.1732 | 154.65 | 61.104 | 0.011482 | 122.72 | 1128.4 |  | 12264 | 154.65 | 4.1732 | 61.104 | 0.011482 | 122.72 | 1128.4 | 1005.68
12265 | 4.1743 | 154.66 | 61.103 | 0.011485 | 122.73 | 1128.4 |  | 12265 | 154.66 | 4.1743 | 61.103 | 0.011485 | 122.73 | 1128.4 | 1005.67
12266 | 4.1753 | 154.67 | 61.103 | 0.011487 | 122.74 | 1128.4 |  | 12266 | 154.67 | 4.1753 | 61.103 | 0.011487 | 122.74 | 1128.4 | 1005.66
12267 | 4.1763 | 154.68 | 61.103 | 0.01149 | 122.75 | 1128.4 |  | 12267 | 154.68 | 4.1763 | 61.103 | 0.01149 | 122.75 | 1128.4 | 1005.65
12268 | 4.1773 | 154.69 | 61.103 | 0.011492 | 122.76 | 1128.4 |  | 12268 | 154.69 | 4.1773 | 61.103 | 0.011492 | 122.76 | 1128.4 | 1005.64
12269 | 4.1783 | 154.7 | 61.103 | 0.011495 | 122.77 | 1128.4 |  | 12269 | 154.7 | 4.1783 | 61.103 | 0.011495 | 122.77 | 1128.4 | 1005.63
12270 | 4.1793 | 154.71 | 61.102 | 0.011498 | 122.78 | 1128.4 |  | 12270 | 154.71 | 4.1793 | 61.102 | 0.011498 | 122.78 | 1128.4 | 1005.62
12271 | 4.1804 | 154.72 | 61.102 | 0.0115 | 122.79 | 1128.4 |  | 12271 | 154.72 | 4.1804 | 61.102 | 0.0115 | 122.79 | 1128.4 | 1005.61
12272 | 4.1814 | 154.73 | 61.102 | 0.011503 | 122.8 | 1128.4 |  | 12272 | 154.73 | 4.1814 | 61.102 | 0.011503 | 122.8 | 1128.4 | 1005.6
12273 | 4.1824 | 154.74 | 61.102 | 0.011506 | 122.81 | 1128.4 |  | 12273 | 154.74 | 4.1824 | 61.102 | 0.011506 | 122.81 | 1128.4 | 1005.59
12274 | 4.1834 | 154.75 | 61.102 | 0.011508 | 122.82 | 1128.4 |  | 12274 | 154.75 | 4.1834 | 61.102 | 0.011508 | 122.82 | 1128.4 | 1005.58
12275 | 4.1844 | 154.76 | 61.101 | 0.011511 | 122.83 | 1128.4 |  | 12275 | 154.76 | 4.1844 | 61.101 | 0.011511 | 122.83 | 1128.4 | 1005.57
12276 | 4.1854 | 154.77 | 61.101 | 0.011513 | 122.84 | 1128.5 |  | 12276 | 154.77 | 4.1854 | 61.101 | 0.011513 | 122.84 | 1128.5 | 1005.66
12277 | 4.1865 | 154.78 | 61.101 | 0.011516 | 122.85 | 1128.5 |  | 12277 | 154.78 | 4.1865 | 61.101 | 0.011516 | 122.85 | 1128.5 | 1005.65
12278 | 4.1875 | 154.79 | 61.101 | 0.011519 | 122.86 | 1128.5 |  | 12278 | 154.79 | 4.1875 | 61.101 | 0.011519 | 122.86 | 1128.5 | 1005.64
12279 | 4.1885 | 154.8 | 61.101 | 0.011521 | 122.87 | 1128.5 |  | 12279 | 154.8 | 4.1885 | 61.101 | 0.011521 | 122.87 | 1128.5 | 1005.63
12280 | 4.1895 | 154.81 | 61.1 | 0.011524 | 122.88 | 1128.5 |  | 12280 | 154.81 | 4.1895 | 61.1 | 0.011524 | 122.88 | 1128.5 | 1005.62
12281 | 4.1905 | 154.82 | 61.1 | 0.011527 | 122.89 | 1128.5 |  | 12281 | 154.82 | 4.1905 | 61.1 | 0.011527 | 122.89 | 1128.5 | 1005.61
12282 | 4.1916 | 154.83 | 61.1 | 0.011529 | 122.9 | 1128.5 |  | 12282 | 154.83 | 4.1916 | 61.1 | 0.011529 | 122.9 | 1128.5 | 1005.6
12283 | 4.1926 | 154.84 | 61.1 | 0.011532 | 122.91 | 1128.5 |  | 12283 | 154.84 | 4.1926 | 61.1 | 0.011532 | 122.91 | 1128.5 | 1005.59
12284 | 4.1936 | 154.85 | 61.1 | 0.011534 | 122.92 | 1128.5 |  | 12284 | 154.85 | 4.1936 | 61.1 | 0.011534 | 122.92 | 1128.5 | 1005.58
12285 | 4.1946 | 154.86 | 61.1 | 0.011537 | 122.93 | 1128.5 |  | 12285 | 154.86 | 4.1946 | 61.1 | 0.011537 | 122.93 | 1128.5 | 1005.57
12286 | 4.1956 | 154.87 | 61.099 | 0.01154 | 122.94 | 1128.5 |  | 12286 | 154.87 | 4.1956 | 61.099 | 0.01154 | 122.94 | 1128.5 | 1005.56
12287 | 4.1967 | 154.88 | 61.099 | 0.011542 | 122.95 | 1128.5 |  | 12287 | 154.88 | 4.1967 | 61.099 | 0.011542 | 122.95 | 1128.5 | 1005.55
12288 | 4.1977 | 154.89 | 61.099 | 0.011545 | 122.96 | 1128.5 |  | 12288 | 154.89 | 4.1977 | 61.099 | 0.011545 | 122.96 | 1128.5 | 1005.54
12289 | 4.1987 | 154.9 | 61.099 | 0.011548 | 122.97 | 1128.5 |  | 12289 | 154.9 | 4.1987 | 61.099 | 0.011548 | 122.97 | 1128.5 | 1005.53
12290 | 4.1997 | 154.91 | 61.099 | 0.01155 | 122.98 | 1128.5 |  | 12290 | 154.91 | 4.1997 | 61.099 | 0.01155 | 122.98 | 1128.5 | 1005.52
12291 | 4.2007 | 154.92 | 61.098 | 0.011553 | 122.99 | 1128.5 |  | 12291 | 154.92 | 4.2007 | 61.098 | 0.011553 | 122.99 | 1128.5 | 1005.51
12292 | 4.2018 | 154.93 | 61.098 | 0.011555 | 123 | 1128.5 |  | 12292 | 154.93 | 4.2018 | 61.098 | 0.011555 | 123 | 1128.5 | 1005.5
12293 | 4.2028 | 154.94 | 61.098 | 0.011558 | 123.01 | 1128.5 |  | 12293 | 154.94 | 4.2028 | 61.098 | 0.011558 | 123.01 | 1128.5 | 1005.49
12294 | 4.2038 | 154.95 | 61.098 | 0.011561 | 123.02 | 1128.5 |  | 12294 | 154.95 | 4.2038 | 61.098 | 0.011561 | 123.02 | 1128.5 | 1005.48
12295 | 4.2048 | 154.96 | 61.098 | 0.011563 | 123.03 | 1128.5 |  | 12295 | 154.96 | 4.2048 | 61.098 | 0.011563 | 123.03 | 1128.5 | 1005.47
12296 | 4.2058 | 154.97 | 61.097 | 0.011566 | 123.04 | 1128.5 |  | 12296 | 154.97 | 4.2058 | 61.097 | 0.011566 | 123.04 | 1128.5 | 1005.46
12297 | 4.2069 | 154.98 | 61.097 | 0.011569 | 123.05 | 1128.5 |  | 12297 | 154.98 | 4.2069 | 61.097 | 0.011569 | 123.05 | 1128.5 | 1005.45
12298 | 4.2079 | 154.99 | 61.097 | 0.011571 | 123.06 | 1128.5 |  | 12298 | 154.99 | 4.2079 | 61.097 | 0.011571 | 123.06 | 1128.5 | 1005.44
12299 | 4.2089 | 155 | 61.097 | 0.011574 | 123.07 | 1128.5 |  | 12299 | 155 | 4.2089 | 61.097 | 0.011574 | 123.07 | 1128.5 | 1005.43
12300 | 4.2099 | 155.01 | 61.097 | 0.011577 | 123.08 | 1128.5 |  | 12300 | 155.01 | 4.2099 | 61.097 | 0.011577 | 123.08 | 1128.5 | 1005.42
12301 | 4.211 | 155.02 | 61.096 | 0.011579 | 123.09 | 1128.6 |  | 12301 | 155.02 | 4.211 | 61.096 | 0.011579 | 123.09 | 1128.6 | 1005.51
12302 | 4.212 | 155.03 | 61.096 | 0.011582 | 123.1 | 1128.6 |  | 12302 | 155.03 | 4.212 | 61.096 | 0.011582 | 123.1 | 1128.6 | 1005.5
12303 | 4.213 | 155.04 | 61.096 | 0.011584 | 123.11 | 1128.6 |  | 12303 | 155.04 | 4.213 | 61.096 | 0.011584 | 123.11 | 1128.6 | 1005.49
12304 | 4.214 | 155.05 | 61.096 | 0.011587 | 123.12 | 1128.6 |  | 12304 | 155.05 | 4.214 | 61.096 | 0.011587 | 123.12 | 1128.6 | 1005.48
12305 | 4.215 | 155.06 | 61.096 | 0.01159 | 123.13 | 1128.6 |  | 12305 | 155.06 | 4.215 | 61.096 | 0.01159 | 123.13 | 1128.6 | 1005.47
12306 | 4.2161 | 155.07 | 61.095 | 0.011592 | 123.14 | 1128.6 |  | 12306 | 155.07 | 4.2161 | 61.095 | 0.011592 | 123.14 | 1128.6 | 1005.46
12307 | 4.2171 | 155.08 | 61.095 | 0.011595 | 123.15 | 1128.6 |  | 12307 | 155.08 | 4.2171 | 61.095 | 0.011595 | 123.15 | 1128.6 | 1005.45
12308 | 4.2181 | 155.09 | 61.095 | 0.011598 | 123.16 | 1128.6 |  | 12308 | 155.09 | 4.2181 | 61.095 | 0.011598 | 123.16 | 1128.6 | 1005.44
12309 | 4.2191 | 155.1 | 61.095 | 0.0116 | 123.17 | 1128.6 |  | 12309 | 155.1 | 4.2191 | 61.095 | 0.0116 | 123.17 | 1128.6 | 1005.43
12310 | 4.2202 | 155.11 | 61.095 | 0.011603 | 123.18 | 1128.6 |  | 12310 | 155.11 | 4.2202 | 61.095 | 0.011603 | 123.18 | 1128.6 | 1005.42
12311 | 4.2212 | 155.12 | 61.094 | 0.011606 | 123.19 | 1128.6 |  | 12311 | 155.12 | 4.2212 | 61.094 | 0.011606 | 123.19 | 1128.6 | 1005.41
12312 | 4.2222 | 155.13 | 61.094 | 0.011608 | 123.2 | 1128.6 |  | 12312 | 155.13 | 4.2222 | 61.094 | 0.011608 | 123.2 | 1128.6 | 1005.4
12313 | 4.2232 | 155.14 | 61.094 | 0.011611 | 123.21 | 1128.6 |  | 12313 | 155.14 | 4.2232 | 61.094 | 0.011611 | 123.21 | 1128.6 | 1005.39
12314 | 4.2243 | 155.15 | 61.094 | 0.011613 | 123.23 | 1128.6 |  | 12314 | 155.15 | 4.2243 | 61.094 | 0.011613 | 123.23 | 1128.6 | 1005.37
12315 | 4.2253 | 155.16 | 61.094 | 0.011616 | 123.24 | 1128.6 |  | 12315 | 155.16 | 4.2253 | 61.094 | 0.011616 | 123.24 | 1128.6 | 1005.36
12316 | 4.2263 | 155.17 | 61.093 | 0.011619 | 123.25 | 1128.6 |  | 12316 | 155.17 | 4.2263 | 61.093 | 0.011619 | 123.25 | 1128.6 | 1005.35
12317 | 4.2273 | 155.18 | 61.093 | 0.011621 | 123.26 | 1128.6 |  | 12317 | 155.18 | 4.2273 | 61.093 | 0.011621 | 123.26 | 1128.6 | 1005.34
12318 | 4.2284 | 155.19 | 61.093 | 0.011624 | 123.27 | 1128.6 |  | 12318 | 155.19 | 4.2284 | 61.093 | 0.011624 | 123.27 | 1128.6 | 1005.33
12319 | 4.2294 | 155.2 | 61.093 | 0.011627 | 123.28 | 1128.6 |  | 12319 | 155.2 | 4.2294 | 61.093 | 0.011627 | 123.28 | 1128.6 | 1005.32
12320 | 4.2304 | 155.21 | 61.093 | 0.011629 | 123.29 | 1128.6 |  | 12320 | 155.21 | 4.2304 | 61.093 | 0.011629 | 123.29 | 1128.6 | 1005.31
12321 | 4.2315 | 155.22 | 61.093 | 0.011632 | 123.3 | 1128.6 |  | 12321 | 155.22 | 4.2315 | 61.093 | 0.011632 | 123.3 | 1128.6 | 1005.3
12322 | 4.2325 | 155.23 | 61.092 | 0.011635 | 123.31 | 1128.6 |  | 12322 | 155.23 | 4.2325 | 61.092 | 0.011635 | 123.31 | 1128.6 | 1005.29
12323 | 4.2335 | 155.24 | 61.092 | 0.011637 | 123.32 | 1128.6 |  | 12323 | 155.24 | 4.2335 | 61.092 | 0.011637 | 123.32 | 1128.6 | 1005.28
12324 | 4.2345 | 155.25 | 61.092 | 0.01164 | 123.33 | 1128.6 |  | 12324 | 155.25 | 4.2345 | 61.092 | 0.01164 | 123.33 | 1128.6 | 1005.27
12325 | 4.2356 | 155.26 | 61.092 | 0.011643 | 123.34 | 1128.7 |  | 12325 | 155.26 | 4.2356 | 61.092 | 0.011643 | 123.34 | 1128.7 | 1005.36
12326 | 4.2366 | 155.27 | 61.092 | 0.011645 | 123.35 | 1128.7 |  | 12326 | 155.27 | 4.2366 | 61.092 | 0.011645 | 123.35 | 1128.7 | 1005.35
12327 | 4.2376 | 155.28 | 61.091 | 0.011648 | 123.36 | 1128.7 |  | 12327 | 155.28 | 4.2376 | 61.091 | 0.011648 | 123.36 | 1128.7 | 1005.34
12328 | 4.2387 | 155.29 | 61.091 | 0.011651 | 123.37 | 1128.7 |  | 12328 | 155.29 | 4.2387 | 61.091 | 0.011651 | 123.37 | 1128.7 | 1005.33
12329 | 4.2397 | 155.3 | 61.091 | 0.011653 | 123.38 | 1128.7 |  | 12329 | 155.3 | 4.2397 | 61.091 | 0.011653 | 123.38 | 1128.7 | 1005.32
12330 | 4.2407 | 155.31 | 61.091 | 0.011656 | 123.39 | 1128.7 |  | 12330 | 155.31 | 4.2407 | 61.091 | 0.011656 | 123.39 | 1128.7 | 1005.31
12331 | 4.2417 | 155.32 | 61.091 | 0.011659 | 123.4 | 1128.7 |  | 12331 | 155.32 | 4.2417 | 61.091 | 0.011659 | 123.4 | 1128.7 | 1005.3
12332 | 4.2428 | 155.33 | 61.09 | 0.011661 | 123.41 | 1128.7 |  | 12332 | 155.33 | 4.2428 | 61.09 | 0.011661 | 123.41 | 1128.7 | 1005.29
12333 | 4.2438 | 155.34 | 61.09 | 0.011664 | 123.42 | 1128.7 |  | 12333 | 155.34 | 4.2438 | 61.09 | 0.011664 | 123.42 | 1128.7 | 1005.28
12334 | 4.2448 | 155.35 | 61.09 | 0.011666 | 123.43 | 1128.7 |  | 12334 | 155.35 | 4.2448 | 61.09 | 0.011666 | 123.43 | 1128.7 | 1005.27
12335 | 4.2459 | 155.36 | 61.09 | 0.011669 | 123.44 | 1128.7 |  | 12335 | 155.36 | 4.2459 | 61.09 | 0.011669 | 123.44 | 1128.7 | 1005.26
12336 | 4.2469 | 155.37 | 61.09 | 0.011672 | 123.45 | 1128.7 |  | 12336 | 155.37 | 4.2469 | 61.09 | 0.011672 | 123.45 | 1128.7 | 1005.25
12337 | 4.2479 | 155.38 | 61.089 | 0.011674 | 123.46 | 1128.7 |  | 12337 | 155.38 | 4.2479 | 61.089 | 0.011674 | 123.46 | 1128.7 | 1005.24
12338 | 4.2489 | 155.39 | 61.089 | 0.011677 | 123.47 | 1128.7 |  | 12338 | 155.39 | 4.2489 | 61.089 | 0.011677 | 123.47 | 1128.7 | 1005.23
12339 | 4.25 | 155.4 | 61.089 | 0.01168 | 123.48 | 1128.7 |  | 12339 | 155.4 | 4.25 | 61.089 | 0.01168 | 123.48 | 1128.7 | 1005.22
12340 | 4.251 | 155.41 | 61.089 | 0.011682 | 123.49 | 1128.7 |  | 12340 | 155.41 | 4.251 | 61.089 | 0.011682 | 123.49 | 1128.7 | 1005.21
12341 | 4.252 | 155.42 | 61.089 | 0.011685 | 123.5 | 1128.7 |  | 12341 | 155.42 | 4.252 | 61.089 | 0.011685 | 123.5 | 1128.7 | 1005.2
12342 | 4.2531 | 155.43 | 61.088 | 0.011688 | 123.51 | 1128.7 |  | 12342 | 155.43 | 4.2531 | 61.088 | 0.011688 | 123.51 | 1128.7 | 1005.19
12343 | 4.2541 | 155.44 | 61.088 | 0.01169 | 123.52 | 1128.7 |  | 12343 | 155.44 | 4.2541 | 61.088 | 0.01169 | 123.52 | 1128.7 | 1005.18
12344 | 4.2551 | 155.45 | 61.088 | 0.011693 | 123.53 | 1128.7 |  | 12344 | 155.45 | 4.2551 | 61.088 | 0.011693 | 123.53 | 1128.7 | 1005.17
12345 | 4.2562 | 155.46 | 61.088 | 0.011696 | 123.54 | 1128.7 |  | 12345 | 155.46 | 4.2562 | 61.088 | 0.011696 | 123.54 | 1128.7 | 1005.16
12346 | 4.2572 | 155.47 | 61.088 | 0.011698 | 123.55 | 1128.7 |  | 12346 | 155.47 | 4.2572 | 61.088 | 0.011698 | 123.55 | 1128.7 | 1005.15
12347 | 4.2582 | 155.48 | 61.087 | 0.011701 | 123.56 | 1128.7 |  | 12347 | 155.48 | 4.2582 | 61.087 | 0.011701 | 123.56 | 1128.7 | 1005.14
12348 | 4.2593 | 155.49 | 61.087 | 0.011704 | 123.57 | 1128.7 |  | 12348 | 155.49 | 4.2593 | 61.087 | 0.011704 | 123.57 | 1128.7 | 1005.13
12349 | 4.2603 | 155.5 | 61.087 | 0.011706 | 123.58 | 1128.8 |  | 12349 | 155.5 | 4.2603 | 61.087 | 0.011706 | 123.58 | 1128.8 | 1005.22
12350 | 4.2613 | 155.51 | 61.087 | 0.011709 | 123.59 | 1128.8 |  | 12350 | 155.51 | 4.2613 | 61.087 | 0.011709 | 123.59 | 1128.8 | 1005.21
12351 | 4.2624 | 155.52 | 61.087 | 0.011712 | 123.6 | 1128.8 |  | 12351 | 155.52 | 4.2624 | 61.087 | 0.011712 | 123.6 | 1128.8 | 1005.2
12352 | 4.2634 | 155.53 | 61.086 | 0.011714 | 123.61 | 1128.8 |  | 12352 | 155.53 | 4.2634 | 61.086 | 0.011714 | 123.61 | 1128.8 | 1005.19
12353 | 4.2644 | 155.54 | 61.086 | 0.011717 | 123.62 | 1128.8 |  | 12353 | 155.54 | 4.2644 | 61.086 | 0.011717 | 123.62 | 1128.8 | 1005.18
12354 | 4.2655 | 155.55 | 61.086 | 0.01172 | 123.63 | 1128.8 |  | 12354 | 155.55 | 4.2655 | 61.086 | 0.01172 | 123.63 | 1128.8 | 1005.17
12355 | 4.2665 | 155.56 | 61.086 | 0.011722 | 123.64 | 1128.8 |  | 12355 | 155.56 | 4.2665 | 61.086 | 0.011722 | 123.64 | 1128.8 | 1005.16
12356 | 4.2675 | 155.57 | 61.086 | 0.011725 | 123.65 | 1128.8 |  | 12356 | 155.57 | 4.2675 | 61.086 | 0.011725 | 123.65 | 1128.8 | 1005.15
12357 | 4.2686 | 155.58 | 61.085 | 0.011728 | 123.66 | 1128.8 |  | 12357 | 155.58 | 4.2686 | 61.085 | 0.011728 | 123.66 | 1128.8 | 1005.14
12358 | 4.2696 | 155.59 | 61.085 | 0.01173 | 123.67 | 1128.8 |  | 12358 | 155.59 | 4.2696 | 61.085 | 0.01173 | 123.67 | 1128.8 | 1005.13
12359 | 4.2706 | 155.6 | 61.085 | 0.011733 | 123.68 | 1128.8 |  | 12359 | 155.6 | 4.2706 | 61.085 | 0.011733 | 123.68 | 1128.8 | 1005.12
12360 | 4.2717 | 155.61 | 61.085 | 0.011736 | 123.69 | 1128.8 |  | 12360 | 155.61 | 4.2717 | 61.085 | 0.011736 | 123.69 | 1128.8 | 1005.11
12361 | 4.2727 | 155.62 | 61.085 | 0.011738 | 123.7 | 1128.8 |  | 12361 | 155.62 | 4.2727 | 61.085 | 0.011738 | 123.7 | 1128.8 | 1005.1
12362 | 4.2738 | 155.63 | 61.085 | 0.011741 | 123.71 | 1128.8 |  | 12362 | 155.63 | 4.2738 | 61.085 | 0.011741 | 123.71 | 1128.8 | 1005.09
12363 | 4.2748 | 155.64 | 61.084 | 0.011744 | 123.72 | 1128.8 |  | 12363 | 155.64 | 4.2748 | 61.084 | 0.011744 | 123.72 | 1128.8 | 1005.08
12364 | 4.2758 | 155.65 | 61.084 | 0.011746 | 123.73 | 1128.8 |  | 12364 | 155.65 | 4.2758 | 61.084 | 0.011746 | 123.73 | 1128.8 | 1005.07
12365 | 4.2769 | 155.66 | 61.084 | 0.011749 | 123.74 | 1128.8 |  | 12365 | 155.66 | 4.2769 | 61.084 | 0.011749 | 123.74 | 1128.8 | 1005.06
12366 | 4.2779 | 155.67 | 61.084 | 0.011752 | 123.75 | 1128.8 |  | 12366 | 155.67 | 4.2779 | 61.084 | 0.011752 | 123.75 | 1128.8 | 1005.05
12367 | 4.2789 | 155.68 | 61.084 | 0.011754 | 123.76 | 1128.8 |  | 12367 | 155.68 | 4.2789 | 61.084 | 0.011754 | 123.76 | 1128.8 | 1005.04
12368 | 4.28 | 155.69 | 61.083 | 0.011757 | 123.77 | 1128.8 |  | 12368 | 155.69 | 4.28 | 61.083 | 0.011757 | 123.77 | 1128.8 | 1005.03
12369 | 4.281 | 155.7 | 61.083 | 0.01176 | 123.78 | 1128.8 |  | 12369 | 155.7 | 4.281 | 61.083 | 0.01176 | 123.78 | 1128.8 | 1005.02
12370 | 4.282 | 155.71 | 61.083 | 0.011762 | 123.79 | 1128.8 |  | 12370 | 155.71 | 4.282 | 61.083 | 0.011762 | 123.79 | 1128.8 | 1005.01
12371 | 4.2831 | 155.72 | 61.083 | 0.011765 | 123.8 | 1128.8 |  | 12371 | 155.72 | 4.2831 | 61.083 | 0.011765 | 123.8 | 1128.8 | 1005
12372 | 4.2841 | 155.73 | 61.083 | 0.011768 | 123.81 | 1128.8 |  | 12372 | 155.73 | 4.2841 | 61.083 | 0.011768 | 123.81 | 1128.8 | 1004.99
12373 | 4.2852 | 155.74 | 61.082 | 0.01177 | 123.82 | 1128.8 |  | 12373 | 155.74 | 4.2852 | 61.082 | 0.01177 | 123.82 | 1128.8 | 1004.98
12374 | 4.2862 | 155.75 | 61.082 | 0.011773 | 123.83 | 1128.9 |  | 12374 | 155.75 | 4.2862 | 61.082 | 0.011773 | 123.83 | 1128.9 | 1005.07
12375 | 4.2872 | 155.76 | 61.082 | 0.011776 | 123.84 | 1128.9 |  | 12375 | 155.76 | 4.2872 | 61.082 | 0.011776 | 123.84 | 1128.9 | 1005.06
12376 | 4.2883 | 155.77 | 61.082 | 0.011778 | 123.85 | 1128.9 |  | 12376 | 155.77 | 4.2883 | 61.082 | 0.011778 | 123.85 | 1128.9 | 1005.05
12377 | 4.2893 | 155.78 | 61.082 | 0.011781 | 123.86 | 1128.9 |  | 12377 | 155.78 | 4.2893 | 61.082 | 0.011781 | 123.86 | 1128.9 | 1005.04
12378 | 4.2904 | 155.79 | 61.081 | 0.011784 | 123.87 | 1128.9 |  | 12378 | 155.79 | 4.2904 | 61.081 | 0.011784 | 123.87 | 1128.9 | 1005.03
12379 | 4.2914 | 155.8 | 61.081 | 0.011786 | 123.88 | 1128.9 |  | 12379 | 155.8 | 4.2914 | 61.081 | 0.011786 | 123.88 | 1128.9 | 1005.02
12380 | 4.2924 | 155.81 | 61.081 | 0.011789 | 123.89 | 1128.9 |  | 12380 | 155.81 | 4.2924 | 61.081 | 0.011789 | 123.89 | 1128.9 | 1005.01
12381 | 4.2935 | 155.82 | 61.081 | 0.011792 | 123.9 | 1128.9 |  | 12381 | 155.82 | 4.2935 | 61.081 | 0.011792 | 123.9 | 1128.9 | 1005
12382 | 4.2945 | 155.83 | 61.081 | 0.011794 | 123.91 | 1128.9 |  | 12382 | 155.83 | 4.2945 | 61.081 | 0.011794 | 123.91 | 1128.9 | 1004.99
12383 | 4.2956 | 155.84 | 61.08 | 0.011797 | 123.92 | 1128.9 |  | 12383 | 155.84 | 4.2956 | 61.08 | 0.011797 | 123.92 | 1128.9 | 1004.98
12384 | 4.2966 | 155.85 | 61.08 | 0.0118 | 123.93 | 1128.9 |  | 12384 | 155.85 | 4.2966 | 61.08 | 0.0118 | 123.93 | 1128.9 | 1004.97
12385 | 4.2976 | 155.86 | 61.08 | 0.011802 | 123.94 | 1128.9 |  | 12385 | 155.86 | 4.2976 | 61.08 | 0.011802 | 123.94 | 1128.9 | 1004.96
12386 | 4.2987 | 155.87 | 61.08 | 0.011805 | 123.95 | 1128.9 |  | 12386 | 155.87 | 4.2987 | 61.08 | 0.011805 | 123.95 | 1128.9 | 1004.95
12387 | 4.2997 | 155.88 | 61.08 | 0.011808 | 123.96 | 1128.9 |  | 12387 | 155.88 | 4.2997 | 61.08 | 0.011808 | 123.96 | 1128.9 | 1004.94
12388 | 4.3008 | 155.89 | 61.079 | 0.011811 | 123.97 | 1128.9 |  | 12388 | 155.89 | 4.3008 | 61.079 | 0.011811 | 123.97 | 1128.9 | 1004.93
12389 | 4.3018 | 155.9 | 61.079 | 0.011813 | 123.98 | 1128.9 |  | 12389 | 155.9 | 4.3018 | 61.079 | 0.011813 | 123.98 | 1128.9 | 1004.92
12390 | 4.3028 | 155.91 | 61.079 | 0.011816 | 123.99 | 1128.9 |  | 12390 | 155.91 | 4.3028 | 61.079 | 0.011816 | 123.99 | 1128.9 | 1004.91
12391 | 4.3039 | 155.92 | 61.079 | 0.011819 | 124 | 1128.9 |  | 12391 | 155.92 | 4.3039 | 61.079 | 0.011819 | 124 | 1128.9 | 1004.9
12392 | 4.3049 | 155.93 | 61.079 | 0.011821 | 124.01 | 1128.9 |  | 12392 | 155.93 | 4.3049 | 61.079 | 0.011821 | 124.01 | 1128.9 | 1004.89
12393 | 4.306 | 155.94 | 61.078 | 0.011824 | 124.02 | 1128.9 |  | 12393 | 155.94 | 4.306 | 61.078 | 0.011824 | 124.02 | 1128.9 | 1004.88
12394 | 4.307 | 155.95 | 61.078 | 0.011827 | 124.03 | 1128.9 |  | 12394 | 155.95 | 4.307 | 61.078 | 0.011827 | 124.03 | 1128.9 | 1004.87
12395 | 4.3081 | 155.96 | 61.078 | 0.011829 | 124.04 | 1128.9 |  | 12395 | 155.96 | 4.3081 | 61.078 | 0.011829 | 124.04 | 1128.9 | 1004.86
12396 | 4.3091 | 155.97 | 61.078 | 0.011832 | 124.05 | 1128.9 |  | 12396 | 155.97 | 4.3091 | 61.078 | 0.011832 | 124.05 | 1128.9 | 1004.85
12397 | 4.3101 | 155.98 | 61.078 | 0.011835 | 124.06 | 1128.9 |  | 12397 | 155.98 | 4.3101 | 61.078 | 0.011835 | 124.06 | 1128.9 | 1004.84
12398 | 4.3112 | 155.99 | 61.077 | 0.011837 | 124.07 | 1129 |  | 12398 | 155.99 | 4.3112 | 61.077 | 0.011837 | 124.07 | 1129 | 1004.93
12399 | 4.3122 | 156 | 61.077 | 0.01184 | 124.08 | 1129 |  | 12399 | 156 | 4.3122 | 61.077 | 0.01184 | 124.08 | 1129 | 1004.92
12400 | 4.3133 | 156.01 | 61.077 | 0.011843 | 124.09 | 1129 |  | 12400 | 156.01 | 4.3133 | 61.077 | 0.011843 | 124.09 | 1129 | 1004.91
12401 | 4.3143 | 156.02 | 61.077 | 0.011845 | 124.1 | 1129 |  | 12401 | 156.02 | 4.3143 | 61.077 | 0.011845 | 124.1 | 1129 | 1004.9
12402 | 4.3154 | 156.03 | 61.077 | 0.011848 | 124.11 | 1129 |  | 12402 | 156.03 | 4.3154 | 61.077 | 0.011848 | 124.11 | 1129 | 1004.89
12403 | 4.3164 | 156.04 | 61.076 | 0.011851 | 124.12 | 1129 |  | 12403 | 156.04 | 4.3164 | 61.076 | 0.011851 | 124.12 | 1129 | 1004.88
12404 | 4.3174 | 156.05 | 61.076 | 0.011853 | 124.13 | 1129 |  | 12404 | 156.05 | 4.3174 | 61.076 | 0.011853 | 124.13 | 1129 | 1004.87
12405 | 4.3185 | 156.06 | 61.076 | 0.011856 | 124.14 | 1129 |  | 12405 | 156.06 | 4.3185 | 61.076 | 0.011856 | 124.14 | 1129 | 1004.86
12406 | 4.3195 | 156.07 | 61.076 | 0.011859 | 124.15 | 1129 |  | 12406 | 156.07 | 4.3195 | 61.076 | 0.011859 | 124.15 | 1129 | 1004.85
12407 | 4.3206 | 156.08 | 61.076 | 0.011862 | 124.16 | 1129 |  | 12407 | 156.08 | 4.3206 | 61.076 | 0.011862 | 124.16 | 1129 | 1004.84
12408 | 4.3216 | 156.09 | 61.076 | 0.011864 | 124.17 | 1129 |  | 12408 | 156.09 | 4.3216 | 61.076 | 0.011864 | 124.17 | 1129 | 1004.83
12409 | 4.3227 | 156.1 | 61.075 | 0.011867 | 124.18 | 1129 |  | 12409 | 156.1 | 4.3227 | 61.075 | 0.011867 | 124.18 | 1129 | 1004.82
12410 | 4.3237 | 156.11 | 61.075 | 0.01187 | 124.19 | 1129 |  | 12410 | 156.11 | 4.3237 | 61.075 | 0.01187 | 124.19 | 1129 | 1004.81
12411 | 4.3248 | 156.12 | 61.075 | 0.011872 | 124.2 | 1129 |  | 12411 | 156.12 | 4.3248 | 61.075 | 0.011872 | 124.2 | 1129 | 1004.8
12412 | 4.3258 | 156.13 | 61.075 | 0.011875 | 124.21 | 1129 |  | 12412 | 156.13 | 4.3258 | 61.075 | 0.011875 | 124.21 | 1129 | 1004.79
12413 | 4.3269 | 156.14 | 61.075 | 0.011878 | 124.22 | 1129 |  | 12413 | 156.14 | 4.3269 | 61.075 | 0.011878 | 124.22 | 1129 | 1004.78
12414 | 4.3279 | 156.15 | 61.074 | 0.01188 | 124.23 | 1129 |  | 12414 | 156.15 | 4.3279 | 61.074 | 0.01188 | 124.23 | 1129 | 1004.77
12415 | 4.329 | 156.16 | 61.074 | 0.011883 | 124.24 | 1129 |  | 12415 | 156.16 | 4.329 | 61.074 | 0.011883 | 124.24 | 1129 | 1004.76
12416 | 4.33 | 156.17 | 61.074 | 0.011886 | 124.25 | 1129 |  | 12416 | 156.17 | 4.33 | 61.074 | 0.011886 | 124.25 | 1129 | 1004.75
12417 | 4.331 | 156.18 | 61.074 | 0.011888 | 124.26 | 1129 |  | 12417 | 156.18 | 4.331 | 61.074 | 0.011888 | 124.26 | 1129 | 1004.74
12418 | 4.3321 | 156.19 | 61.074 | 0.011891 | 124.27 | 1129 |  | 12418 | 156.19 | 4.3321 | 61.074 | 0.011891 | 124.27 | 1129 | 1004.73
12419 | 4.3331 | 156.2 | 61.073 | 0.011894 | 124.28 | 1129 |  | 12419 | 156.2 | 4.3331 | 61.073 | 0.011894 | 124.28 | 1129 | 1004.72
12420 | 4.3342 | 156.21 | 61.073 | 0.011897 | 124.29 | 1129 |  | 12420 | 156.21 | 4.3342 | 61.073 | 0.011897 | 124.29 | 1129 | 1004.71
12421 | 4.3352 | 156.22 | 61.073 | 0.011899 | 124.3 | 1129 |  | 12421 | 156.22 | 4.3352 | 61.073 | 0.011899 | 124.3 | 1129 | 1004.7
12422 | 4.3363 | 156.23 | 61.073 | 0.011902 | 124.31 | 1129 |  | 12422 | 156.23 | 4.3363 | 61.073 | 0.011902 | 124.31 | 1129 | 1004.69
12423 | 4.3373 | 156.24 | 61.073 | 0.011905 | 124.32 | 1129.1 |  | 12423 | 156.24 | 4.3373 | 61.073 | 0.011905 | 124.32 | 1129.1 | 1004.78
12424 | 4.3384 | 156.25 | 61.072 | 0.011907 | 124.33 | 1129.1 |  | 12424 | 156.25 | 4.3384 | 61.072 | 0.011907 | 124.33 | 1129.1 | 1004.77
12425 | 4.3394 | 156.26 | 61.072 | 0.01191 | 124.34 | 1129.1 |  | 12425 | 156.26 | 4.3394 | 61.072 | 0.01191 | 124.34 | 1129.1 | 1004.76
12426 | 4.3405 | 156.27 | 61.072 | 0.011913 | 124.35 | 1129.1 |  | 12426 | 156.27 | 4.3405 | 61.072 | 0.011913 | 124.35 | 1129.1 | 1004.75
12427 | 4.3415 | 156.28 | 61.072 | 0.011915 | 124.36 | 1129.1 |  | 12427 | 156.28 | 4.3415 | 61.072 | 0.011915 | 124.36 | 1129.1 | 1004.74
12428 | 4.3426 | 156.29 | 61.072 | 0.011918 | 124.37 | 1129.1 |  | 12428 | 156.29 | 4.3426 | 61.072 | 0.011918 | 124.37 | 1129.1 | 1004.73
12429 | 4.3436 | 156.3 | 61.071 | 0.011921 | 124.38 | 1129.1 |  | 12429 | 156.3 | 4.3436 | 61.071 | 0.011921 | 124.38 | 1129.1 | 1004.72
12430 | 4.3447 | 156.31 | 61.071 | 0.011924 | 124.39 | 1129.1 |  | 12430 | 156.31 | 4.3447 | 61.071 | 0.011924 | 124.39 | 1129.1 | 1004.71
12431 | 4.3457 | 156.32 | 61.071 | 0.011926 | 124.4 | 1129.1 |  | 12431 | 156.32 | 4.3457 | 61.071 | 0.011926 | 124.4 | 1129.1 | 1004.7
12432 | 4.3468 | 156.33 | 61.071 | 0.011929 | 124.41 | 1129.1 |  | 12432 | 156.33 | 4.3468 | 61.071 | 0.011929 | 124.41 | 1129.1 | 1004.69
12433 | 4.3478 | 156.34 | 61.071 | 0.011932 | 124.42 | 1129.1 |  | 12433 | 156.34 | 4.3478 | 61.071 | 0.011932 | 124.42 | 1129.1 | 1004.68
12434 | 4.3489 | 156.35 | 61.07 | 0.011934 | 124.43 | 1129.1 |  | 12434 | 156.35 | 4.3489 | 61.07 | 0.011934 | 124.43 | 1129.1 | 1004.67
12435 | 4.3499 | 156.36 | 61.07 | 0.011937 | 124.44 | 1129.1 |  | 12435 | 156.36 | 4.3499 | 61.07 | 0.011937 | 124.44 | 1129.1 | 1004.66
12436 | 4.351 | 156.37 | 61.07 | 0.01194 | 124.45 | 1129.1 |  | 12436 | 156.37 | 4.351 | 61.07 | 0.01194 | 124.45 | 1129.1 | 1004.65
12437 | 4.352 | 156.38 | 61.07 | 0.011942 | 124.46 | 1129.1 |  | 12437 | 156.38 | 4.352 | 61.07 | 0.011942 | 124.46 | 1129.1 | 1004.64
12438 | 4.3531 | 156.39 | 61.07 | 0.011945 | 124.47 | 1129.1 |  | 12438 | 156.39 | 4.3531 | 61.07 | 0.011945 | 124.47 | 1129.1 | 1004.63
12439 | 4.3542 | 156.4 | 61.069 | 0.011948 | 124.48 | 1129.1 |  | 12439 | 156.4 | 4.3542 | 61.069 | 0.011948 | 124.48 | 1129.1 | 1004.62
12440 | 4.3552 | 156.41 | 61.069 | 0.011951 | 124.49 | 1129.1 |  | 12440 | 156.41 | 4.3552 | 61.069 | 0.011951 | 124.49 | 1129.1 | 1004.61
12441 | 4.3563 | 156.42 | 61.069 | 0.011953 | 124.5 | 1129.1 |  | 12441 | 156.42 | 4.3563 | 61.069 | 0.011953 | 124.5 | 1129.1 | 1004.6
12442 | 4.3573 | 156.43 | 61.069 | 0.011956 | 124.51 | 1129.1 |  | 12442 | 156.43 | 4.3573 | 61.069 | 0.011956 | 124.51 | 1129.1 | 1004.59
12443 | 4.3584 | 156.44 | 61.069 | 0.011959 | 124.52 | 1129.1 |  | 12443 | 156.44 | 4.3584 | 61.069 | 0.011959 | 124.52 | 1129.1 | 1004.58
12444 | 4.3594 | 156.45 | 61.068 | 0.011961 | 124.53 | 1129.1 |  | 12444 | 156.45 | 4.3594 | 61.068 | 0.011961 | 124.53 | 1129.1 | 1004.57
12445 | 4.3605 | 156.46 | 61.068 | 0.011964 | 124.54 | 1129.1 |  | 12445 | 156.46 | 4.3605 | 61.068 | 0.011964 | 124.54 | 1129.1 | 1004.56
12446 | 4.3615 | 156.47 | 61.068 | 0.011967 | 124.55 | 1129.1 |  | 12446 | 156.47 | 4.3615 | 61.068 | 0.011967 | 124.55 | 1129.1 | 1004.55
12447 | 4.3626 | 156.48 | 61.068 | 0.01197 | 124.56 | 1129.2 |  | 12447 | 156.48 | 4.3626 | 61.068 | 0.01197 | 124.56 | 1129.2 | 1004.64
12448 | 4.3636 | 156.49 | 61.068 | 0.011972 | 124.57 | 1129.2 |  | 12448 | 156.49 | 4.3636 | 61.068 | 0.011972 | 124.57 | 1129.2 | 1004.63
12449 | 4.3647 | 156.5 | 61.067 | 0.011975 | 124.58 | 1129.2 |  | 12449 | 156.5 | 4.3647 | 61.067 | 0.011975 | 124.58 | 1129.2 | 1004.62
12450 | 4.3657 | 156.51 | 61.067 | 0.011978 | 124.59 | 1129.2 |  | 12450 | 156.51 | 4.3657 | 61.067 | 0.011978 | 124.59 | 1129.2 | 1004.61
12451 | 4.3668 | 156.52 | 61.067 | 0.01198 | 124.6 | 1129.2 |  | 12451 | 156.52 | 4.3668 | 61.067 | 0.01198 | 124.6 | 1129.2 | 1004.6
12452 | 4.3678 | 156.53 | 61.067 | 0.011983 | 124.61 | 1129.2 |  | 12452 | 156.53 | 4.3678 | 61.067 | 0.011983 | 124.61 | 1129.2 | 1004.59
12453 | 4.3689 | 156.54 | 61.067 | 0.011986 | 124.62 | 1129.2 |  | 12453 | 156.54 | 4.3689 | 61.067 | 0.011986 | 124.62 | 1129.2 | 1004.58
12454 | 4.37 | 156.55 | 61.066 | 0.011989 | 124.63 | 1129.2 |  | 12454 | 156.55 | 4.37 | 61.066 | 0.011989 | 124.63 | 1129.2 | 1004.57
12455 | 4.371 | 156.56 | 61.066 | 0.011991 | 124.64 | 1129.2 |  | 12455 | 156.56 | 4.371 | 61.066 | 0.011991 | 124.64 | 1129.2 | 1004.56
12456 | 4.3721 | 156.57 | 61.066 | 0.011994 | 124.65 | 1129.2 |  | 12456 | 156.57 | 4.3721 | 61.066 | 0.011994 | 124.65 | 1129.2 | 1004.55
12457 | 4.3731 | 156.58 | 61.066 | 0.011997 | 124.66 | 1129.2 |  | 12457 | 156.58 | 4.3731 | 61.066 | 0.011997 | 124.66 | 1129.2 | 1004.54
12458 | 4.3742 | 156.59 | 61.066 | 0.011999 | 124.67 | 1129.2 |  | 12458 | 156.59 | 4.3742 | 61.066 | 0.011999 | 124.67 | 1129.2 | 1004.53
12459 | 4.3752 | 156.6 | 61.066 | 0.012002 | 124.68 | 1129.2 |  | 12459 | 156.6 | 4.3752 | 61.066 | 0.012002 | 124.68 | 1129.2 | 1004.52
12460 | 4.3763 | 156.61 | 61.065 | 0.012005 | 124.69 | 1129.2 |  | 12460 | 156.61 | 4.3763 | 61.065 | 0.012005 | 124.69 | 1129.2 | 1004.51
12461 | 4.3774 | 156.62 | 61.065 | 0.012008 | 124.7 | 1129.2 |  | 12461 | 156.62 | 4.3774 | 61.065 | 0.012008 | 124.7 | 1129.2 | 1004.5
12462 | 4.3784 | 156.63 | 61.065 | 0.01201 | 124.71 | 1129.2 |  | 12462 | 156.63 | 4.3784 | 61.065 | 0.01201 | 124.71 | 1129.2 | 1004.49
12463 | 4.3795 | 156.64 | 61.065 | 0.012013 | 124.72 | 1129.2 |  | 12463 | 156.64 | 4.3795 | 61.065 | 0.012013 | 124.72 | 1129.2 | 1004.48
12464 | 4.3805 | 156.65 | 61.065 | 0.012016 | 124.73 | 1129.2 |  | 12464 | 156.65 | 4.3805 | 61.065 | 0.012016 | 124.73 | 1129.2 | 1004.47
12465 | 4.3816 | 156.66 | 61.064 | 0.012018 | 124.74 | 1129.2 |  | 12465 | 156.66 | 4.3816 | 61.064 | 0.012018 | 124.74 | 1129.2 | 1004.46
12466 | 4.3826 | 156.67 | 61.064 | 0.012021 | 124.75 | 1129.2 |  | 12466 | 156.67 | 4.3826 | 61.064 | 0.012021 | 124.75 | 1129.2 | 1004.45
12467 | 4.3837 | 156.68 | 61.064 | 0.012024 | 124.76 | 1129.2 |  | 12467 | 156.68 | 4.3837 | 61.064 | 0.012024 | 124.76 | 1129.2 | 1004.44
12468 | 4.3848 | 156.69 | 61.064 | 0.012027 | 124.77 | 1129.2 |  | 12468 | 156.69 | 4.3848 | 61.064 | 0.012027 | 124.77 | 1129.2 | 1004.43
12469 | 4.3858 | 156.7 | 61.064 | 0.012029 | 124.78 | 1129.2 |  | 12469 | 156.7 | 4.3858 | 61.064 | 0.012029 | 124.78 | 1129.2 | 1004.42
12470 | 4.3869 | 156.71 | 61.063 | 0.012032 | 124.79 | 1129.2 |  | 12470 | 156.71 | 4.3869 | 61.063 | 0.012032 | 124.79 | 1129.2 | 1004.41
12471 | 4.3879 | 156.72 | 61.063 | 0.012035 | 124.8 | 1129.3 |  | 12471 | 156.72 | 4.3879 | 61.063 | 0.012035 | 124.8 | 1129.3 | 1004.5
12472 | 4.389 | 156.73 | 61.063 | 0.012038 | 124.81 | 1129.3 |  | 12472 | 156.73 | 4.389 | 61.063 | 0.012038 | 124.81 | 1129.3 | 1004.49
12473 | 4.3901 | 156.74 | 61.063 | 0.01204 | 124.82 | 1129.3 |  | 12473 | 156.74 | 4.3901 | 61.063 | 0.01204 | 124.82 | 1129.3 | 1004.48
12474 | 4.3911 | 156.75 | 61.063 | 0.012043 | 124.83 | 1129.3 |  | 12474 | 156.75 | 4.3911 | 61.063 | 0.012043 | 124.83 | 1129.3 | 1004.47
12475 | 4.3922 | 156.76 | 61.062 | 0.012046 | 124.84 | 1129.3 |  | 12475 | 156.76 | 4.3922 | 61.062 | 0.012046 | 124.84 | 1129.3 | 1004.46
12476 | 4.3932 | 156.77 | 61.062 | 0.012048 | 124.85 | 1129.3 |  | 12476 | 156.77 | 4.3932 | 61.062 | 0.012048 | 124.85 | 1129.3 | 1004.45
12477 | 4.3943 | 156.78 | 61.062 | 0.012051 | 124.86 | 1129.3 |  | 12477 | 156.78 | 4.3943 | 61.062 | 0.012051 | 124.86 | 1129.3 | 1004.44
12478 | 4.3954 | 156.79 | 61.062 | 0.012054 | 124.87 | 1129.3 |  | 12478 | 156.79 | 4.3954 | 61.062 | 0.012054 | 124.87 | 1129.3 | 1004.43
12479 | 4.3964 | 156.8 | 61.062 | 0.012057 | 124.88 | 1129.3 |  | 12479 | 156.8 | 4.3964 | 61.062 | 0.012057 | 124.88 | 1129.3 | 1004.42
12480 | 4.3975 | 156.81 | 61.061 | 0.012059 | 124.89 | 1129.3 |  | 12480 | 156.81 | 4.3975 | 61.061 | 0.012059 | 124.89 | 1129.3 | 1004.41
12481 | 4.3985 | 156.82 | 61.061 | 0.012062 | 124.9 | 1129.3 |  | 12481 | 156.82 | 4.3985 | 61.061 | 0.012062 | 124.9 | 1129.3 | 1004.4
12482 | 4.3996 | 156.83 | 61.061 | 0.012065 | 124.91 | 1129.3 |  | 12482 | 156.83 | 4.3996 | 61.061 | 0.012065 | 124.91 | 1129.3 | 1004.39
12483 | 4.4007 | 156.84 | 61.061 | 0.012068 | 124.92 | 1129.3 |  | 12483 | 156.84 | 4.4007 | 61.061 | 0.012068 | 124.92 | 1129.3 | 1004.38
12484 | 4.4017 | 156.85 | 61.061 | 0.01207 | 124.93 | 1129.3 |  | 12484 | 156.85 | 4.4017 | 61.061 | 0.01207 | 124.93 | 1129.3 | 1004.37
12485 | 4.4028 | 156.86 | 61.06 | 0.012073 | 124.94 | 1129.3 |  | 12485 | 156.86 | 4.4028 | 61.06 | 0.012073 | 124.94 | 1129.3 | 1004.36
12486 | 4.4039 | 156.87 | 61.06 | 0.012076 | 124.95 | 1129.3 |  | 12486 | 156.87 | 4.4039 | 61.06 | 0.012076 | 124.95 | 1129.3 | 1004.35
12487 | 4.4049 | 156.88 | 61.06 | 0.012078 | 124.96 | 1129.3 |  | 12487 | 156.88 | 4.4049 | 61.06 | 0.012078 | 124.96 | 1129.3 | 1004.34
12488 | 4.406 | 156.89 | 61.06 | 0.012081 | 124.97 | 1129.3 |  | 12488 | 156.89 | 4.406 | 61.06 | 0.012081 | 124.97 | 1129.3 | 1004.33
12489 | 4.407 | 156.9 | 61.06 | 0.012084 | 124.98 | 1129.3 |  | 12489 | 156.9 | 4.407 | 61.06 | 0.012084 | 124.98 | 1129.3 | 1004.32
12490 | 4.4081 | 156.91 | 61.059 | 0.012087 | 124.99 | 1129.3 |  | 12490 | 156.91 | 4.4081 | 61.059 | 0.012087 | 124.99 | 1129.3 | 1004.31
12491 | 4.4092 | 156.92 | 61.059 | 0.012089 | 125 | 1129.3 |  | 12491 | 156.92 | 4.4092 | 61.059 | 0.012089 | 125 | 1129.3 | 1004.3
12492 | 4.4102 | 156.93 | 61.059 | 0.012092 | 125.01 | 1129.3 |  | 12492 | 156.93 | 4.4102 | 61.059 | 0.012092 | 125.01 | 1129.3 | 1004.29
12493 | 4.4113 | 156.94 | 61.059 | 0.012095 | 125.02 | 1129.3 |  | 12493 | 156.94 | 4.4113 | 61.059 | 0.012095 | 125.02 | 1129.3 | 1004.28
12494 | 4.4124 | 156.95 | 61.059 | 0.012098 | 125.03 | 1129.3 |  | 12494 | 156.95 | 4.4124 | 61.059 | 0.012098 | 125.03 | 1129.3 | 1004.27
12495 | 4.4134 | 156.96 | 61.058 | 0.0121 | 125.04 | 1129.3 |  | 12495 | 156.96 | 4.4134 | 61.058 | 0.0121 | 125.04 | 1129.3 | 1004.26
12496 | 4.4145 | 156.97 | 61.058 | 0.012103 | 125.05 | 1129.4 |  | 12496 | 156.97 | 4.4145 | 61.058 | 0.012103 | 125.05 | 1129.4 | 1004.35
12497 | 4.4156 | 156.98 | 61.058 | 0.012106 | 125.06 | 1129.4 |  | 12497 | 156.98 | 4.4156 | 61.058 | 0.012106 | 125.06 | 1129.4 | 1004.34
12498 | 4.4166 | 156.99 | 61.058 | 0.012109 | 125.07 | 1129.4 |  | 12498 | 156.99 | 4.4166 | 61.058 | 0.012109 | 125.07 | 1129.4 | 1004.33
12499 | 4.4177 | 157 | 61.058 | 0.012111 | 125.08 | 1129.4 |  | 12499 | 157 | 4.4177 | 61.058 | 0.012111 | 125.08 | 1129.4 | 1004.32
12500 | 4.4187 | 157.01 | 61.057 | 0.012114 | 125.09 | 1129.4 |  | 12500 | 157.01 | 4.4187 | 61.057 | 0.012114 | 125.09 | 1129.4 | 1004.31
12501 | 4.4198 | 157.02 | 61.057 | 0.012117 | 125.1 | 1129.4 |  | 12501 | 157.02 | 4.4198 | 61.057 | 0.012117 | 125.1 | 1129.4 | 1004.3
12502 | 4.4209 | 157.03 | 61.057 | 0.012119 | 125.11 | 1129.4 |  | 12502 | 157.03 | 4.4209 | 61.057 | 0.012119 | 125.11 | 1129.4 | 1004.29
12503 | 4.4219 | 157.04 | 61.057 | 0.012122 | 125.12 | 1129.4 |  | 12503 | 157.04 | 4.4219 | 61.057 | 0.012122 | 125.12 | 1129.4 | 1004.28
12504 | 4.423 | 157.05 | 61.057 | 0.012125 | 125.13 | 1129.4 |  | 12504 | 157.05 | 4.423 | 61.057 | 0.012125 | 125.13 | 1129.4 | 1004.27
12505 | 4.4241 | 157.06 | 61.056 | 0.012128 | 125.14 | 1129.4 |  | 12505 | 157.06 | 4.4241 | 61.056 | 0.012128 | 125.14 | 1129.4 | 1004.26
12506 | 4.4251 | 157.07 | 61.056 | 0.01213 | 125.15 | 1129.4 |  | 12506 | 157.07 | 4.4251 | 61.056 | 0.01213 | 125.15 | 1129.4 | 1004.25
12507 | 4.4262 | 157.08 | 61.056 | 0.012133 | 125.16 | 1129.4 |  | 12507 | 157.08 | 4.4262 | 61.056 | 0.012133 | 125.16 | 1129.4 | 1004.24
12508 | 4.4273 | 157.09 | 61.056 | 0.012136 | 125.17 | 1129.4 |  | 12508 | 157.09 | 4.4273 | 61.056 | 0.012136 | 125.17 | 1129.4 | 1004.23
12509 | 4.4283 | 157.1 | 61.056 | 0.012139 | 125.18 | 1129.4 |  | 12509 | 157.1 | 4.4283 | 61.056 | 0.012139 | 125.18 | 1129.4 | 1004.22
12510 | 4.4294 | 157.11 | 61.055 | 0.012141 | 125.19 | 1129.4 |  | 12510 | 157.11 | 4.4294 | 61.055 | 0.012141 | 125.19 | 1129.4 | 1004.21
12511 | 4.4305 | 157.12 | 61.055 | 0.012144 | 125.2 | 1129.4 |  | 12511 | 157.12 | 4.4305 | 61.055 | 0.012144 | 125.2 | 1129.4 | 1004.2
12512 | 4.4316 | 157.13 | 61.055 | 0.012147 | 125.21 | 1129.4 |  | 12512 | 157.13 | 4.4316 | 61.055 | 0.012147 | 125.21 | 1129.4 | 1004.19
12513 | 4.4326 | 157.14 | 61.055 | 0.01215 | 125.22 | 1129.4 |  | 12513 | 157.14 | 4.4326 | 61.055 | 0.01215 | 125.22 | 1129.4 | 1004.18
12514 | 4.4337 | 157.15 | 61.055 | 0.012152 | 125.23 | 1129.4 |  | 12514 | 157.15 | 4.4337 | 61.055 | 0.012152 | 125.23 | 1129.4 | 1004.17
12515 | 4.4348 | 157.16 | 61.054 | 0.012155 | 125.24 | 1129.4 |  | 12515 | 157.16 | 4.4348 | 61.054 | 0.012155 | 125.24 | 1129.4 | 1004.16
12516 | 4.4358 | 157.17 | 61.054 | 0.012158 | 125.25 | 1129.4 |  | 12516 | 157.17 | 4.4358 | 61.054 | 0.012158 | 125.25 | 1129.4 | 1004.15
12517 | 4.4369 | 157.18 | 61.054 | 0.012161 | 125.26 | 1129.4 |  | 12517 | 157.18 | 4.4369 | 61.054 | 0.012161 | 125.26 | 1129.4 | 1004.14
12518 | 4.438 | 157.19 | 61.054 | 0.012163 | 125.27 | 1129.4 |  | 12518 | 157.19 | 4.438 | 61.054 | 0.012163 | 125.27 | 1129.4 | 1004.13
12519 | 4.439 | 157.2 | 61.054 | 0.012166 | 125.28 | 1129.4 |  | 12519 | 157.2 | 4.439 | 61.054 | 0.012166 | 125.28 | 1129.4 | 1004.12
12520 | 4.4401 | 157.21 | 61.054 | 0.012169 | 125.29 | 1129.5 |  | 12520 | 157.21 | 4.4401 | 61.054 | 0.012169 | 125.29 | 1129.5 | 1004.21
12521 | 4.4412 | 157.22 | 61.053 | 0.012172 | 125.3 | 1129.5 |  | 12521 | 157.22 | 4.4412 | 61.053 | 0.012172 | 125.3 | 1129.5 | 1004.2
12522 | 4.4422 | 157.23 | 61.053 | 0.012174 | 125.31 | 1129.5 |  | 12522 | 157.23 | 4.4422 | 61.053 | 0.012174 | 125.31 | 1129.5 | 1004.19
12523 | 4.4433 | 157.24 | 61.053 | 0.012177 | 125.32 | 1129.5 |  | 12523 | 157.24 | 4.4433 | 61.053 | 0.012177 | 125.32 | 1129.5 | 1004.18
12524 | 4.4444 | 157.25 | 61.053 | 0.01218 | 125.33 | 1129.5 |  | 12524 | 157.25 | 4.4444 | 61.053 | 0.01218 | 125.33 | 1129.5 | 1004.17
12525 | 4.4455 | 157.26 | 61.053 | 0.012183 | 125.34 | 1129.5 |  | 12525 | 157.26 | 4.4455 | 61.053 | 0.012183 | 125.34 | 1129.5 | 1004.16
12526 | 4.4465 | 157.27 | 61.052 | 0.012185 | 125.35 | 1129.5 |  | 12526 | 157.27 | 4.4465 | 61.052 | 0.012185 | 125.35 | 1129.5 | 1004.15
12527 | 4.4476 | 157.28 | 61.052 | 0.012188 | 125.36 | 1129.5 |  | 12527 | 157.28 | 4.4476 | 61.052 | 0.012188 | 125.36 | 1129.5 | 1004.14
12528 | 4.4487 | 157.29 | 61.052 | 0.012191 | 125.37 | 1129.5 |  | 12528 | 157.29 | 4.4487 | 61.052 | 0.012191 | 125.37 | 1129.5 | 1004.13
12529 | 4.4497 | 157.3 | 61.052 | 0.012194 | 125.38 | 1129.5 |  | 12529 | 157.3 | 4.4497 | 61.052 | 0.012194 | 125.38 | 1129.5 | 1004.12
12530 | 4.4508 | 157.31 | 61.052 | 0.012196 | 125.39 | 1129.5 |  | 12530 | 157.31 | 4.4508 | 61.052 | 0.012196 | 125.39 | 1129.5 | 1004.11
12531 | 4.4519 | 157.32 | 61.051 | 0.012199 | 125.4 | 1129.5 |  | 12531 | 157.32 | 4.4519 | 61.051 | 0.012199 | 125.4 | 1129.5 | 1004.1
12532 | 4.453 | 157.33 | 61.051 | 0.012202 | 125.41 | 1129.5 |  | 12532 | 157.33 | 4.453 | 61.051 | 0.012202 | 125.41 | 1129.5 | 1004.09
12533 | 4.454 | 157.34 | 61.051 | 0.012205 | 125.42 | 1129.5 |  | 12533 | 157.34 | 4.454 | 61.051 | 0.012205 | 125.42 | 1129.5 | 1004.08
12534 | 4.4551 | 157.35 | 61.051 | 0.012207 | 125.43 | 1129.5 |  | 12534 | 157.35 | 4.4551 | 61.051 | 0.012207 | 125.43 | 1129.5 | 1004.07
12535 | 4.4562 | 157.36 | 61.051 | 0.01221 | 125.44 | 1129.5 |  | 12535 | 157.36 | 4.4562 | 61.051 | 0.01221 | 125.44 | 1129.5 | 1004.06
12536 | 4.4573 | 157.37 | 61.05 | 0.012213 | 125.45 | 1129.5 |  | 12536 | 157.37 | 4.4573 | 61.05 | 0.012213 | 125.45 | 1129.5 | 1004.05
12537 | 4.4583 | 157.38 | 61.05 | 0.012216 | 125.46 | 1129.5 |  | 12537 | 157.38 | 4.4583 | 61.05 | 0.012216 | 125.46 | 1129.5 | 1004.04
12538 | 4.4594 | 157.39 | 61.05 | 0.012218 | 125.47 | 1129.5 |  | 12538 | 157.39 | 4.4594 | 61.05 | 0.012218 | 125.47 | 1129.5 | 1004.03
12539 | 4.4605 | 157.4 | 61.05 | 0.012221 | 125.48 | 1129.5 |  | 12539 | 157.4 | 4.4605 | 61.05 | 0.012221 | 125.48 | 1129.5 | 1004.02
12540 | 4.4615 | 157.41 | 61.05 | 0.012224 | 125.49 | 1129.5 |  | 12540 | 157.41 | 4.4615 | 61.05 | 0.012224 | 125.49 | 1129.5 | 1004.01
12541 | 4.4626 | 157.42 | 61.049 | 0.012227 | 125.5 | 1129.5 |  | 12541 | 157.42 | 4.4626 | 61.049 | 0.012227 | 125.5 | 1129.5 | 1004
12542 | 4.4637 | 157.43 | 61.049 | 0.012229 | 125.51 | 1129.5 |  | 12542 | 157.43 | 4.4637 | 61.049 | 0.012229 | 125.51 | 1129.5 | 1003.99
12543 | 4.4648 | 157.44 | 61.049 | 0.012232 | 125.52 | 1129.5 |  | 12543 | 157.44 | 4.4648 | 61.049 | 0.012232 | 125.52 | 1129.5 | 1003.98
12544 | 4.4658 | 157.45 | 61.049 | 0.012235 | 125.53 | 1129.5 |  | 12544 | 157.45 | 4.4658 | 61.049 | 0.012235 | 125.53 | 1129.5 | 1003.97
12545 | 4.4669 | 157.46 | 61.049 | 0.012238 | 125.54 | 1129.6 |  | 12545 | 157.46 | 4.4669 | 61.049 | 0.012238 | 125.54 | 1129.6 | 1004.06
12546 | 4.468 | 157.47 | 61.048 | 0.012241 | 125.55 | 1129.6 |  | 12546 | 157.47 | 4.468 | 61.048 | 0.012241 | 125.55 | 1129.6 | 1004.05
12547 | 4.4691 | 157.48 | 61.048 | 0.012243 | 125.56 | 1129.6 |  | 12547 | 157.48 | 4.4691 | 61.048 | 0.012243 | 125.56 | 1129.6 | 1004.04
12548 | 4.4701 | 157.49 | 61.048 | 0.012246 | 125.57 | 1129.6 |  | 12548 | 157.49 | 4.4701 | 61.048 | 0.012246 | 125.57 | 1129.6 | 1004.03
12549 | 4.4712 | 157.5 | 61.048 | 0.012249 | 125.58 | 1129.6 |  | 12549 | 157.5 | 4.4712 | 61.048 | 0.012249 | 125.58 | 1129.6 | 1004.02
12550 | 4.4723 | 157.51 | 61.048 | 0.012252 | 125.59 | 1129.6 |  | 12550 | 157.51 | 4.4723 | 61.048 | 0.012252 | 125.59 | 1129.6 | 1004.01
12551 | 4.4734 | 157.52 | 61.047 | 0.012254 | 125.6 | 1129.6 |  | 12551 | 157.52 | 4.4734 | 61.047 | 0.012254 | 125.6 | 1129.6 | 1004
12552 | 4.4745 | 157.53 | 61.047 | 0.012257 | 125.61 | 1129.6 |  | 12552 | 157.53 | 4.4745 | 61.047 | 0.012257 | 125.61 | 1129.6 | 1003.99
12553 | 4.4755 | 157.54 | 61.047 | 0.01226 | 125.62 | 1129.6 |  | 12553 | 157.54 | 4.4755 | 61.047 | 0.01226 | 125.62 | 1129.6 | 1003.98
12554 | 4.4766 | 157.55 | 61.047 | 0.012263 | 125.63 | 1129.6 |  | 12554 | 157.55 | 4.4766 | 61.047 | 0.012263 | 125.63 | 1129.6 | 1003.97
12555 | 4.4777 | 157.56 | 61.047 | 0.012265 | 125.64 | 1129.6 |  | 12555 | 157.56 | 4.4777 | 61.047 | 0.012265 | 125.64 | 1129.6 | 1003.96
12556 | 4.4788 | 157.57 | 61.046 | 0.012268 | 125.65 | 1129.6 |  | 12556 | 157.57 | 4.4788 | 61.046 | 0.012268 | 125.65 | 1129.6 | 1003.95
12557 | 4.4798 | 157.58 | 61.046 | 0.012271 | 125.66 | 1129.6 |  | 12557 | 157.58 | 4.4798 | 61.046 | 0.012271 | 125.66 | 1129.6 | 1003.94
12558 | 4.4809 | 157.59 | 61.046 | 0.012274 | 125.67 | 1129.6 |  | 12558 | 157.59 | 4.4809 | 61.046 | 0.012274 | 125.67 | 1129.6 | 1003.93
12559 | 4.482 | 157.6 | 61.046 | 0.012276 | 125.68 | 1129.6 |  | 12559 | 157.6 | 4.482 | 61.046 | 0.012276 | 125.68 | 1129.6 | 1003.92
12560 | 4.4831 | 157.61 | 61.046 | 0.012279 | 125.69 | 1129.6 |  | 12560 | 157.61 | 4.4831 | 61.046 | 0.012279 | 125.69 | 1129.6 | 1003.91
12561 | 4.4842 | 157.62 | 61.045 | 0.012282 | 125.7 | 1129.6 |  | 12561 | 157.62 | 4.4842 | 61.045 | 0.012282 | 125.7 | 1129.6 | 1003.9
12562 | 4.4852 | 157.63 | 61.045 | 0.012285 | 125.71 | 1129.6 |  | 12562 | 157.63 | 4.4852 | 61.045 | 0.012285 | 125.71 | 1129.6 | 1003.89
12563 | 4.4863 | 157.64 | 61.045 | 0.012288 | 125.72 | 1129.6 |  | 12563 | 157.64 | 4.4863 | 61.045 | 0.012288 | 125.72 | 1129.6 | 1003.88
12564 | 4.4874 | 157.65 | 61.045 | 0.01229 | 125.73 | 1129.6 |  | 12564 | 157.65 | 4.4874 | 61.045 | 0.01229 | 125.73 | 1129.6 | 1003.87
12565 | 4.4885 | 157.66 | 61.045 | 0.012293 | 125.74 | 1129.6 |  | 12565 | 157.66 | 4.4885 | 61.045 | 0.012293 | 125.74 | 1129.6 | 1003.86
12566 | 4.4896 | 157.67 | 61.044 | 0.012296 | 125.75 | 1129.6 |  | 12566 | 157.67 | 4.4896 | 61.044 | 0.012296 | 125.75 | 1129.6 | 1003.85
12567 | 4.4906 | 157.68 | 61.044 | 0.012299 | 125.76 | 1129.6 |  | 12567 | 157.68 | 4.4906 | 61.044 | 0.012299 | 125.76 | 1129.6 | 1003.84
12568 | 4.4917 | 157.69 | 61.044 | 0.012301 | 125.77 | 1129.6 |  | 12568 | 157.69 | 4.4917 | 61.044 | 0.012301 | 125.77 | 1129.6 | 1003.83
12569 | 4.4928 | 157.7 | 61.044 | 0.012304 | 125.78 | 1129.7 |  | 12569 | 157.7 | 4.4928 | 61.044 | 0.012304 | 125.78 | 1129.7 | 1003.92
12570 | 4.4939 | 157.71 | 61.044 | 0.012307 | 125.79 | 1129.7 |  | 12570 | 157.71 | 4.4939 | 61.044 | 0.012307 | 125.79 | 1129.7 | 1003.91
12571 | 4.495 | 157.72 | 61.043 | 0.01231 | 125.8 | 1129.7 |  | 12571 | 157.72 | 4.495 | 61.043 | 0.01231 | 125.8 | 1129.7 | 1003.9
12572 | 4.496 | 157.73 | 61.043 | 0.012312 | 125.81 | 1129.7 |  | 12572 | 157.73 | 4.496 | 61.043 | 0.012312 | 125.81 | 1129.7 | 1003.89
12573 | 4.4971 | 157.74 | 61.043 | 0.012315 | 125.82 | 1129.7 |  | 12573 | 157.74 | 4.4971 | 61.043 | 0.012315 | 125.82 | 1129.7 | 1003.88
12574 | 4.4982 | 157.75 | 61.043 | 0.012318 | 125.83 | 1129.7 |  | 12574 | 157.75 | 4.4982 | 61.043 | 0.012318 | 125.83 | 1129.7 | 1003.87
12575 | 4.4993 | 157.76 | 61.043 | 0.012321 | 125.84 | 1129.7 |  | 12575 | 157.76 | 4.4993 | 61.043 | 0.012321 | 125.84 | 1129.7 | 1003.86
12576 | 4.5004 | 157.77 | 61.042 | 0.012324 | 125.85 | 1129.7 |  | 12576 | 157.77 | 4.5004 | 61.042 | 0.012324 | 125.85 | 1129.7 | 1003.85
12577 | 4.5014 | 157.78 | 61.042 | 0.012326 | 125.86 | 1129.7 |  | 12577 | 157.78 | 4.5014 | 61.042 | 0.012326 | 125.86 | 1129.7 | 1003.84
12578 | 4.5025 | 157.79 | 61.042 | 0.012329 | 125.87 | 1129.7 |  | 12578 | 157.79 | 4.5025 | 61.042 | 0.012329 | 125.87 | 1129.7 | 1003.83
12579 | 4.5036 | 157.8 | 61.042 | 0.012332 | 125.88 | 1129.7 |  | 12579 | 157.8 | 4.5036 | 61.042 | 0.012332 | 125.88 | 1129.7 | 1003.82
12580 | 4.5047 | 157.81 | 61.042 | 0.012335 | 125.89 | 1129.7 |  | 12580 | 157.81 | 4.5047 | 61.042 | 0.012335 | 125.89 | 1129.7 | 1003.81
12581 | 4.5058 | 157.82 | 61.041 | 0.012337 | 125.9 | 1129.7 |  | 12581 | 157.82 | 4.5058 | 61.041 | 0.012337 | 125.9 | 1129.7 | 1003.8
12582 | 4.5069 | 157.83 | 61.041 | 0.01234 | 125.91 | 1129.7 |  | 12582 | 157.83 | 4.5069 | 61.041 | 0.01234 | 125.91 | 1129.7 | 1003.79
12583 | 4.5079 | 157.84 | 61.041 | 0.012343 | 125.92 | 1129.7 |  | 12583 | 157.84 | 4.5079 | 61.041 | 0.012343 | 125.92 | 1129.7 | 1003.78
12584 | 4.509 | 157.85 | 61.041 | 0.012346 | 125.93 | 1129.7 |  | 12584 | 157.85 | 4.509 | 61.041 | 0.012346 | 125.93 | 1129.7 | 1003.77
12585 | 4.5101 | 157.86 | 61.041 | 0.012349 | 125.94 | 1129.7 |  | 12585 | 157.86 | 4.5101 | 61.041 | 0.012349 | 125.94 | 1129.7 | 1003.76
12586 | 4.5112 | 157.87 | 61.04 | 0.012351 | 125.95 | 1129.7 |  | 12586 | 157.87 | 4.5112 | 61.04 | 0.012351 | 125.95 | 1129.7 | 1003.75
12587 | 4.5123 | 157.88 | 61.04 | 0.012354 | 125.96 | 1129.7 |  | 12587 | 157.88 | 4.5123 | 61.04 | 0.012354 | 125.96 | 1129.7 | 1003.74
12588 | 4.5134 | 157.89 | 61.04 | 0.012357 | 125.97 | 1129.7 |  | 12588 | 157.89 | 4.5134 | 61.04 | 0.012357 | 125.97 | 1129.7 | 1003.73
12589 | 4.5145 | 157.9 | 61.04 | 0.01236 | 125.98 | 1129.7 |  | 12589 | 157.9 | 4.5145 | 61.04 | 0.01236 | 125.98 | 1129.7 | 1003.72
12590 | 4.5155 | 157.91 | 61.04 | 0.012363 | 125.99 | 1129.7 |  | 12590 | 157.91 | 4.5155 | 61.04 | 0.012363 | 125.99 | 1129.7 | 1003.71
12591 | 4.5166 | 157.92 | 61.04 | 0.012365 | 126 | 1129.7 |  | 12591 | 157.92 | 4.5166 | 61.04 | 0.012365 | 126 | 1129.7 | 1003.7
12592 | 4.5177 | 157.93 | 61.039 | 0.012368 | 126.01 | 1129.7 |  | 12592 | 157.93 | 4.5177 | 61.039 | 0.012368 | 126.01 | 1129.7 | 1003.69
12593 | 4.5188 | 157.94 | 61.039 | 0.012371 | 126.02 | 1129.7 |  | 12593 | 157.94 | 4.5188 | 61.039 | 0.012371 | 126.02 | 1129.7 | 1003.68
12594 | 4.5199 | 157.95 | 61.039 | 0.012374 | 126.03 | 1129.8 |  | 12594 | 157.95 | 4.5199 | 61.039 | 0.012374 | 126.03 | 1129.8 | 1003.77
12595 | 4.521 | 157.96 | 61.039 | 0.012376 | 126.04 | 1129.8 |  | 12595 | 157.96 | 4.521 | 61.039 | 0.012376 | 126.04 | 1129.8 | 1003.76
12596 | 4.5221 | 157.97 | 61.039 | 0.012379 | 126.05 | 1129.8 |  | 12596 | 157.97 | 4.5221 | 61.039 | 0.012379 | 126.05 | 1129.8 | 1003.75
12597 | 4.5231 | 157.98 | 61.038 | 0.012382 | 126.06 | 1129.8 |  | 12597 | 157.98 | 4.5231 | 61.038 | 0.012382 | 126.06 | 1129.8 | 1003.74
12598 | 4.5242 | 157.99 | 61.038 | 0.012385 | 126.07 | 1129.8 |  | 12598 | 157.99 | 4.5242 | 61.038 | 0.012385 | 126.07 | 1129.8 | 1003.73
12599 | 4.5253 | 158 | 61.038 | 0.012388 | 126.08 | 1129.8 |  | 12599 | 158 | 4.5253 | 61.038 | 0.012388 | 126.08 | 1129.8 | 1003.72
12600 | 4.5264 | 158.01 | 61.038 | 0.01239 | 126.09 | 1129.8 |  | 12600 | 158.01 | 4.5264 | 61.038 | 0.01239 | 126.09 | 1129.8 | 1003.71
12601 | 4.5275 | 158.02 | 61.038 | 0.012393 | 126.1 | 1129.8 |  | 12601 | 158.02 | 4.5275 | 61.038 | 0.012393 | 126.1 | 1129.8 | 1003.7
12602 | 4.5286 | 158.03 | 61.037 | 0.012396 | 126.11 | 1129.8 |  | 12602 | 158.03 | 4.5286 | 61.037 | 0.012396 | 126.11 | 1129.8 | 1003.69
12603 | 4.5297 | 158.04 | 61.037 | 0.012399 | 126.12 | 1129.8 |  | 12603 | 158.04 | 4.5297 | 61.037 | 0.012399 | 126.12 | 1129.8 | 1003.68
12604 | 4.5308 | 158.05 | 61.037 | 0.012402 | 126.13 | 1129.8 |  | 12604 | 158.05 | 4.5308 | 61.037 | 0.012402 | 126.13 | 1129.8 | 1003.67
12605 | 4.5318 | 158.06 | 61.037 | 0.012404 | 126.14 | 1129.8 |  | 12605 | 158.06 | 4.5318 | 61.037 | 0.012404 | 126.14 | 1129.8 | 1003.66
12606 | 4.5329 | 158.07 | 61.037 | 0.012407 | 126.15 | 1129.8 |  | 12606 | 158.07 | 4.5329 | 61.037 | 0.012407 | 126.15 | 1129.8 | 1003.65
12607 | 4.534 | 158.08 | 61.036 | 0.01241 | 126.16 | 1129.8 |  | 12607 | 158.08 | 4.534 | 61.036 | 0.01241 | 126.16 | 1129.8 | 1003.64
12608 | 4.5351 | 158.09 | 61.036 | 0.012413 | 126.17 | 1129.8 |  | 12608 | 158.09 | 4.5351 | 61.036 | 0.012413 | 126.17 | 1129.8 | 1003.63
12609 | 4.5362 | 158.1 | 61.036 | 0.012416 | 126.18 | 1129.8 |  | 12609 | 158.1 | 4.5362 | 61.036 | 0.012416 | 126.18 | 1129.8 | 1003.62
12610 | 4.5373 | 158.11 | 61.036 | 0.012418 | 126.19 | 1129.8 |  | 12610 | 158.11 | 4.5373 | 61.036 | 0.012418 | 126.19 | 1129.8 | 1003.61
12611 | 4.5384 | 158.12 | 61.036 | 0.012421 | 126.2 | 1129.8 |  | 12611 | 158.12 | 4.5384 | 61.036 | 0.012421 | 126.2 | 1129.8 | 1003.6
12612 | 4.5395 | 158.13 | 61.035 | 0.012424 | 126.21 | 1129.8 |  | 12612 | 158.13 | 4.5395 | 61.035 | 0.012424 | 126.21 | 1129.8 | 1003.59
12613 | 4.5406 | 158.14 | 61.035 | 0.012427 | 126.22 | 1129.8 |  | 12613 | 158.14 | 4.5406 | 61.035 | 0.012427 | 126.22 | 1129.8 | 1003.58
12614 | 4.5416 | 158.15 | 61.035 | 0.01243 | 126.23 | 1129.8 |  | 12614 | 158.15 | 4.5416 | 61.035 | 0.01243 | 126.23 | 1129.8 | 1003.57
12615 | 4.5427 | 158.16 | 61.035 | 0.012432 | 126.24 | 1129.8 |  | 12615 | 158.16 | 4.5427 | 61.035 | 0.012432 | 126.24 | 1129.8 | 1003.56
12616 | 4.5438 | 158.17 | 61.035 | 0.012435 | 126.25 | 1129.8 |  | 12616 | 158.17 | 4.5438 | 61.035 | 0.012435 | 126.25 | 1129.8 | 1003.55
12617 | 4.5449 | 158.18 | 61.034 | 0.012438 | 126.26 | 1129.8 |  | 12617 | 158.18 | 4.5449 | 61.034 | 0.012438 | 126.26 | 1129.8 | 1003.54
12618 | 4.546 | 158.19 | 61.034 | 0.012441 | 126.27 | 1129.9 |  | 12618 | 158.19 | 4.546 | 61.034 | 0.012441 | 126.27 | 1129.9 | 1003.63
12619 | 4.5471 | 158.2 | 61.034 | 0.012444 | 126.28 | 1129.9 |  | 12619 | 158.2 | 4.5471 | 61.034 | 0.012444 | 126.28 | 1129.9 | 1003.62
12620 | 4.5482 | 158.21 | 61.034 | 0.012446 | 126.29 | 1129.9 |  | 12620 | 158.21 | 4.5482 | 61.034 | 0.012446 | 126.29 | 1129.9 | 1003.61
12621 | 4.5493 | 158.22 | 61.034 | 0.012449 | 126.3 | 1129.9 |  | 12621 | 158.22 | 4.5493 | 61.034 | 0.012449 | 126.3 | 1129.9 | 1003.6
12622 | 4.5504 | 158.23 | 61.033 | 0.012452 | 126.31 | 1129.9 |  | 12622 | 158.23 | 4.5504 | 61.033 | 0.012452 | 126.31 | 1129.9 | 1003.59
12623 | 4.5515 | 158.24 | 61.033 | 0.012455 | 126.32 | 1129.9 |  | 12623 | 158.24 | 4.5515 | 61.033 | 0.012455 | 126.32 | 1129.9 | 1003.58
12624 | 4.5526 | 158.25 | 61.033 | 0.012458 | 126.33 | 1129.9 |  | 12624 | 158.25 | 4.5526 | 61.033 | 0.012458 | 126.33 | 1129.9 | 1003.57
12625 | 4.5537 | 158.26 | 61.033 | 0.01246 | 126.34 | 1129.9 |  | 12625 | 158.26 | 4.5537 | 61.033 | 0.01246 | 126.34 | 1129.9 | 1003.56
12626 | 4.5547 | 158.27 | 61.033 | 0.012463 | 126.35 | 1129.9 |  | 12626 | 158.27 | 4.5547 | 61.033 | 0.012463 | 126.35 | 1129.9 | 1003.55
12627 | 4.5558 | 158.28 | 61.032 | 0.012466 | 126.36 | 1129.9 |  | 12627 | 158.28 | 4.5558 | 61.032 | 0.012466 | 126.36 | 1129.9 | 1003.54
12628 | 4.5569 | 158.29 | 61.032 | 0.012469 | 126.37 | 1129.9 |  | 12628 | 158.29 | 4.5569 | 61.032 | 0.012469 | 126.37 | 1129.9 | 1003.53
12629 | 4.558 | 158.3 | 61.032 | 0.012472 | 126.38 | 1129.9 |  | 12629 | 158.3 | 4.558 | 61.032 | 0.012472 | 126.38 | 1129.9 | 1003.52
12630 | 4.5591 | 158.31 | 61.032 | 0.012474 | 126.39 | 1129.9 |  | 12630 | 158.31 | 4.5591 | 61.032 | 0.012474 | 126.39 | 1129.9 | 1003.51
12631 | 4.5602 | 158.32 | 61.032 | 0.012477 | 126.4 | 1129.9 |  | 12631 | 158.32 | 4.5602 | 61.032 | 0.012477 | 126.4 | 1129.9 | 1003.5
12632 | 4.5613 | 158.33 | 61.031 | 0.01248 | 126.41 | 1129.9 |  | 12632 | 158.33 | 4.5613 | 61.031 | 0.01248 | 126.41 | 1129.9 | 1003.49
12633 | 4.5624 | 158.34 | 61.031 | 0.012483 | 126.42 | 1129.9 |  | 12633 | 158.34 | 4.5624 | 61.031 | 0.012483 | 126.42 | 1129.9 | 1003.48
12634 | 4.5635 | 158.35 | 61.031 | 0.012486 | 126.43 | 1129.9 |  | 12634 | 158.35 | 4.5635 | 61.031 | 0.012486 | 126.43 | 1129.9 | 1003.47
12635 | 4.5646 | 158.36 | 61.031 | 0.012488 | 126.44 | 1129.9 |  | 12635 | 158.36 | 4.5646 | 61.031 | 0.012488 | 126.44 | 1129.9 | 1003.46
12636 | 4.5657 | 158.37 | 61.031 | 0.012491 | 126.45 | 1129.9 |  | 12636 | 158.37 | 4.5657 | 61.031 | 0.012491 | 126.45 | 1129.9 | 1003.45
12637 | 4.5668 | 158.38 | 61.03 | 0.012494 | 126.46 | 1129.9 |  | 12637 | 158.38 | 4.5668 | 61.03 | 0.012494 | 126.46 | 1129.9 | 1003.44
12638 | 4.5679 | 158.39 | 61.03 | 0.012497 | 126.47 | 1129.9 |  | 12638 | 158.39 | 4.5679 | 61.03 | 0.012497 | 126.47 | 1129.9 | 1003.43
12639 | 4.569 | 158.4 | 61.03 | 0.0125 | 126.48 | 1129.9 |  | 12639 | 158.4 | 4.569 | 61.03 | 0.0125 | 126.48 | 1129.9 | 1003.42
12640 | 4.5701 | 158.41 | 61.03 | 0.012502 | 126.49 | 1129.9 |  | 12640 | 158.41 | 4.5701 | 61.03 | 0.012502 | 126.49 | 1129.9 | 1003.41
12641 | 4.5712 | 158.42 | 61.03 | 0.012505 | 126.5 | 1129.9 |  | 12641 | 158.42 | 4.5712 | 61.03 | 0.012505 | 126.5 | 1129.9 | 1003.4
12642 | 4.5723 | 158.43 | 61.029 | 0.012508 | 126.51 | 1129.9 |  | 12642 | 158.43 | 4.5723 | 61.029 | 0.012508 | 126.51 | 1129.9 | 1003.39
12643 | 4.5734 | 158.44 | 61.029 | 0.012511 | 126.52 | 1130 |  | 12643 | 158.44 | 4.5734 | 61.029 | 0.012511 | 126.52 | 1130 | 1003.48
12644 | 4.5745 | 158.45 | 61.029 | 0.012514 | 126.53 | 1130 |  | 12644 | 158.45 | 4.5745 | 61.029 | 0.012514 | 126.53 | 1130 | 1003.47
12645 | 4.5756 | 158.46 | 61.029 | 0.012517 | 126.54 | 1130 |  | 12645 | 158.46 | 4.5756 | 61.029 | 0.012517 | 126.54 | 1130 | 1003.46
12646 | 4.5767 | 158.47 | 61.029 | 0.012519 | 126.55 | 1130 |  | 12646 | 158.47 | 4.5767 | 61.029 | 0.012519 | 126.55 | 1130 | 1003.45
12647 | 4.5778 | 158.48 | 61.028 | 0.012522 | 126.56 | 1130 |  | 12647 | 158.48 | 4.5778 | 61.028 | 0.012522 | 126.56 | 1130 | 1003.44
12648 | 4.5789 | 158.49 | 61.028 | 0.012525 | 126.57 | 1130 |  | 12648 | 158.49 | 4.5789 | 61.028 | 0.012525 | 126.57 | 1130 | 1003.43
12649 | 4.58 | 158.5 | 61.028 | 0.012528 | 126.58 | 1130 |  | 12649 | 158.5 | 4.58 | 61.028 | 0.012528 | 126.58 | 1130 | 1003.42
12650 | 4.5811 | 158.51 | 61.028 | 0.012531 | 126.59 | 1130 |  | 12650 | 158.51 | 4.5811 | 61.028 | 0.012531 | 126.59 | 1130 | 1003.41
12651 | 4.5822 | 158.52 | 61.028 | 0.012533 | 126.6 | 1130 |  | 12651 | 158.52 | 4.5822 | 61.028 | 0.012533 | 126.6 | 1130 | 1003.4
12652 | 4.5832 | 158.53 | 61.027 | 0.012536 | 126.61 | 1130 |  | 12652 | 158.53 | 4.5832 | 61.027 | 0.012536 | 126.61 | 1130 | 1003.39
12653 | 4.5843 | 158.54 | 61.027 | 0.012539 | 126.62 | 1130 |  | 12653 | 158.54 | 4.5843 | 61.027 | 0.012539 | 126.62 | 1130 | 1003.38
12654 | 4.5854 | 158.55 | 61.027 | 0.012542 | 126.63 | 1130 |  | 12654 | 158.55 | 4.5854 | 61.027 | 0.012542 | 126.63 | 1130 | 1003.37
12655 | 4.5865 | 158.56 | 61.027 | 0.012545 | 126.64 | 1130 |  | 12655 | 158.56 | 4.5865 | 61.027 | 0.012545 | 126.64 | 1130 | 1003.36
12656 | 4.5876 | 158.57 | 61.027 | 0.012547 | 126.65 | 1130 |  | 12656 | 158.57 | 4.5876 | 61.027 | 0.012547 | 126.65 | 1130 | 1003.35
12657 | 4.5887 | 158.58 | 61.026 | 0.01255 | 126.66 | 1130 |  | 12657 | 158.58 | 4.5887 | 61.026 | 0.01255 | 126.66 | 1130 | 1003.34
12658 | 4.5898 | 158.59 | 61.026 | 0.012553 | 126.67 | 1130 |  | 12658 | 158.59 | 4.5898 | 61.026 | 0.012553 | 126.67 | 1130 | 1003.33
12659 | 4.5909 | 158.6 | 61.026 | 0.012556 | 126.68 | 1130 |  | 12659 | 158.6 | 4.5909 | 61.026 | 0.012556 | 126.68 | 1130 | 1003.32
12660 | 4.592 | 158.61 | 61.026 | 0.012559 | 126.69 | 1130 |  | 12660 | 158.61 | 4.592 | 61.026 | 0.012559 | 126.69 | 1130 | 1003.31
12661 | 4.5931 | 158.62 | 61.026 | 0.012562 | 126.7 | 1130 |  | 12661 | 158.62 | 4.5931 | 61.026 | 0.012562 | 126.7 | 1130 | 1003.3
12662 | 4.5943 | 158.63 | 61.025 | 0.012564 | 126.71 | 1130 |  | 12662 | 158.63 | 4.5943 | 61.025 | 0.012564 | 126.71 | 1130 | 1003.29
12663 | 4.5954 | 158.64 | 61.025 | 0.012567 | 126.72 | 1130 |  | 12663 | 158.64 | 4.5954 | 61.025 | 0.012567 | 126.72 | 1130 | 1003.28
12664 | 4.5965 | 158.65 | 61.025 | 0.01257 | 126.73 | 1130 |  | 12664 | 158.65 | 4.5965 | 61.025 | 0.01257 | 126.73 | 1130 | 1003.27
12665 | 4.5976 | 158.66 | 61.025 | 0.012573 | 126.74 | 1130 |  | 12665 | 158.66 | 4.5976 | 61.025 | 0.012573 | 126.74 | 1130 | 1003.26
12666 | 4.5987 | 158.67 | 61.025 | 0.012576 | 126.75 | 1130 |  | 12666 | 158.67 | 4.5987 | 61.025 | 0.012576 | 126.75 | 1130 | 1003.25
12667 | 4.5998 | 158.68 | 61.024 | 0.012579 | 126.76 | 1130.1 |  | 12667 | 158.68 | 4.5998 | 61.024 | 0.012579 | 126.76 | 1130.1 | 1003.34
12668 | 4.6009 | 158.69 | 61.024 | 0.012581 | 126.77 | 1130.1 |  | 12668 | 158.69 | 4.6009 | 61.024 | 0.012581 | 126.77 | 1130.1 | 1003.33
12669 | 4.602 | 158.7 | 61.024 | 0.012584 | 126.78 | 1130.1 |  | 12669 | 158.7 | 4.602 | 61.024 | 0.012584 | 126.78 | 1130.1 | 1003.32
12670 | 4.6031 | 158.71 | 61.024 | 0.012587 | 126.79 | 1130.1 |  | 12670 | 158.71 | 4.6031 | 61.024 | 0.012587 | 126.79 | 1130.1 | 1003.31
12671 | 4.6042 | 158.72 | 61.024 | 0.01259 | 126.8 | 1130.1 |  | 12671 | 158.72 | 4.6042 | 61.024 | 0.01259 | 126.8 | 1130.1 | 1003.3
12672 | 4.6053 | 158.73 | 61.023 | 0.012593 | 126.81 | 1130.1 |  | 12672 | 158.73 | 4.6053 | 61.023 | 0.012593 | 126.81 | 1130.1 | 1003.29
12673 | 4.6064 | 158.74 | 61.023 | 0.012596 | 126.82 | 1130.1 |  | 12673 | 158.74 | 4.6064 | 61.023 | 0.012596 | 126.82 | 1130.1 | 1003.28
12674 | 4.6075 | 158.75 | 61.023 | 0.012598 | 126.83 | 1130.1 |  | 12674 | 158.75 | 4.6075 | 61.023 | 0.012598 | 126.83 | 1130.1 | 1003.27
12675 | 4.6086 | 158.76 | 61.023 | 0.012601 | 126.84 | 1130.1 |  | 12675 | 158.76 | 4.6086 | 61.023 | 0.012601 | 126.84 | 1130.1 | 1003.26
12676 | 4.6097 | 158.77 | 61.023 | 0.012604 | 126.85 | 1130.1 |  | 12676 | 158.77 | 4.6097 | 61.023 | 0.012604 | 126.85 | 1130.1 | 1003.25
12677 | 4.6108 | 158.78 | 61.022 | 0.012607 | 126.86 | 1130.1 |  | 12677 | 158.78 | 4.6108 | 61.022 | 0.012607 | 126.86 | 1130.1 | 1003.24
12678 | 4.6119 | 158.79 | 61.022 | 0.01261 | 126.87 | 1130.1 |  | 12678 | 158.79 | 4.6119 | 61.022 | 0.01261 | 126.87 | 1130.1 | 1003.23
12679 | 4.613 | 158.8 | 61.022 | 0.012612 | 126.88 | 1130.1 |  | 12679 | 158.8 | 4.613 | 61.022 | 0.012612 | 126.88 | 1130.1 | 1003.22
12680 | 4.6141 | 158.81 | 61.022 | 0.012615 | 126.89 | 1130.1 |  | 12680 | 158.81 | 4.6141 | 61.022 | 0.012615 | 126.89 | 1130.1 | 1003.21
12681 | 4.6152 | 158.82 | 61.022 | 0.012618 | 126.9 | 1130.1 |  | 12681 | 158.82 | 4.6152 | 61.022 | 0.012618 | 126.9 | 1130.1 | 1003.2
12682 | 4.6163 | 158.83 | 61.021 | 0.012621 | 126.91 | 1130.1 |  | 12682 | 158.83 | 4.6163 | 61.021 | 0.012621 | 126.91 | 1130.1 | 1003.19
12683 | 4.6174 | 158.84 | 61.021 | 0.012624 | 126.92 | 1130.1 |  | 12683 | 158.84 | 4.6174 | 61.021 | 0.012624 | 126.92 | 1130.1 | 1003.18
12684 | 4.6185 | 158.85 | 61.021 | 0.012627 | 126.93 | 1130.1 |  | 12684 | 158.85 | 4.6185 | 61.021 | 0.012627 | 126.93 | 1130.1 | 1003.17
12685 | 4.6196 | 158.86 | 61.021 | 0.012629 | 126.94 | 1130.1 |  | 12685 | 158.86 | 4.6196 | 61.021 | 0.012629 | 126.94 | 1130.1 | 1003.16
12686 | 4.6207 | 158.87 | 61.021 | 0.012632 | 126.95 | 1130.1 |  | 12686 | 158.87 | 4.6207 | 61.021 | 0.012632 | 126.95 | 1130.1 | 1003.15
12687 | 4.6219 | 158.88 | 61.02 | 0.012635 | 126.96 | 1130.1 |  | 12687 | 158.88 | 4.6219 | 61.02 | 0.012635 | 126.96 | 1130.1 | 1003.14
12688 | 4.623 | 158.89 | 61.02 | 0.012638 | 126.97 | 1130.1 |  | 12688 | 158.89 | 4.623 | 61.02 | 0.012638 | 126.97 | 1130.1 | 1003.13
12689 | 4.6241 | 158.9 | 61.02 | 0.012641 | 126.98 | 1130.1 |  | 12689 | 158.9 | 4.6241 | 61.02 | 0.012641 | 126.98 | 1130.1 | 1003.12
12690 | 4.6252 | 158.91 | 61.02 | 0.012644 | 126.99 | 1130.1 |  | 12690 | 158.91 | 4.6252 | 61.02 | 0.012644 | 126.99 | 1130.1 | 1003.11
12691 | 4.6263 | 158.92 | 61.02 | 0.012647 | 127 | 1130.1 |  | 12691 | 158.92 | 4.6263 | 61.02 | 0.012647 | 127 | 1130.1 | 1003.1
12692 | 4.6274 | 158.93 | 61.019 | 0.012649 | 127.01 | 1130.2 |  | 12692 | 158.93 | 4.6274 | 61.019 | 0.012649 | 127.01 | 1130.2 | 1003.19
12693 | 4.6285 | 158.94 | 61.019 | 0.012652 | 127.02 | 1130.2 |  | 12693 | 158.94 | 4.6285 | 61.019 | 0.012652 | 127.02 | 1130.2 | 1003.18
12694 | 4.6296 | 158.95 | 61.019 | 0.012655 | 127.03 | 1130.2 |  | 12694 | 158.95 | 4.6296 | 61.019 | 0.012655 | 127.03 | 1130.2 | 1003.17
12695 | 4.6307 | 158.96 | 61.019 | 0.012658 | 127.04 | 1130.2 |  | 12695 | 158.96 | 4.6307 | 61.019 | 0.012658 | 127.04 | 1130.2 | 1003.16
12696 | 4.6318 | 158.97 | 61.019 | 0.012661 | 127.05 | 1130.2 |  | 12696 | 158.97 | 4.6318 | 61.019 | 0.012661 | 127.05 | 1130.2 | 1003.15
12697 | 4.6329 | 158.98 | 61.018 | 0.012664 | 127.06 | 1130.2 |  | 12697 | 158.98 | 4.6329 | 61.018 | 0.012664 | 127.06 | 1130.2 | 1003.14
12698 | 4.634 | 158.99 | 61.018 | 0.012666 | 127.07 | 1130.2 |  | 12698 | 158.99 | 4.634 | 61.018 | 0.012666 | 127.07 | 1130.2 | 1003.13
12699 | 4.6352 | 159 | 61.018 | 0.012669 | 127.08 | 1130.2 |  | 12699 | 159 | 4.6352 | 61.018 | 0.012669 | 127.08 | 1130.2 | 1003.12
12700 | 4.6363 | 159.01 | 61.018 | 0.012672 | 127.09 | 1130.2 |  | 12700 | 159.01 | 4.6363 | 61.018 | 0.012672 | 127.09 | 1130.2 | 1003.11
12701 | 4.6374 | 159.02 | 61.018 | 0.012675 | 127.1 | 1130.2 |  | 12701 | 159.02 | 4.6374 | 61.018 | 0.012675 | 127.1 | 1130.2 | 1003.1
12702 | 4.6385 | 159.03 | 61.017 | 0.012678 | 127.11 | 1130.2 |  | 12702 | 159.03 | 4.6385 | 61.017 | 0.012678 | 127.11 | 1130.2 | 1003.09
12703 | 4.6396 | 159.04 | 61.017 | 0.012681 | 127.12 | 1130.2 |  | 12703 | 159.04 | 4.6396 | 61.017 | 0.012681 | 127.12 | 1130.2 | 1003.08
12704 | 4.6407 | 159.05 | 61.017 | 0.012683 | 127.13 | 1130.2 |  | 12704 | 159.05 | 4.6407 | 61.017 | 0.012683 | 127.13 | 1130.2 | 1003.07
12705 | 4.6418 | 159.06 | 61.017 | 0.012686 | 127.14 | 1130.2 |  | 12705 | 159.06 | 4.6418 | 61.017 | 0.012686 | 127.14 | 1130.2 | 1003.06
12706 | 4.6429 | 159.07 | 61.017 | 0.012689 | 127.15 | 1130.2 |  | 12706 | 159.07 | 4.6429 | 61.017 | 0.012689 | 127.15 | 1130.2 | 1003.05
12707 | 4.644 | 159.08 | 61.016 | 0.012692 | 127.16 | 1130.2 |  | 12707 | 159.08 | 4.644 | 61.016 | 0.012692 | 127.16 | 1130.2 | 1003.04
12708 | 4.6451 | 159.09 | 61.016 | 0.012695 | 127.17 | 1130.2 |  | 12708 | 159.09 | 4.6451 | 61.016 | 0.012695 | 127.17 | 1130.2 | 1003.03
12709 | 4.6463 | 159.1 | 61.016 | 0.012698 | 127.18 | 1130.2 |  | 12709 | 159.1 | 4.6463 | 61.016 | 0.012698 | 127.18 | 1130.2 | 1003.02
12710 | 4.6474 | 159.11 | 61.016 | 0.012701 | 127.19 | 1130.2 |  | 12710 | 159.11 | 4.6474 | 61.016 | 0.012701 | 127.19 | 1130.2 | 1003.01
12711 | 4.6485 | 159.12 | 61.016 | 0.012703 | 127.2 | 1130.2 |  | 12711 | 159.12 | 4.6485 | 61.016 | 0.012703 | 127.2 | 1130.2 | 1003
12712 | 4.6496 | 159.13 | 61.015 | 0.012706 | 127.21 | 1130.2 |  | 12712 | 159.13 | 4.6496 | 61.015 | 0.012706 | 127.21 | 1130.2 | 1002.99
12713 | 4.6507 | 159.14 | 61.015 | 0.012709 | 127.22 | 1130.2 |  | 12713 | 159.14 | 4.6507 | 61.015 | 0.012709 | 127.22 | 1130.2 | 1002.98
12714 | 4.6518 | 159.15 | 61.015 | 0.012712 | 127.23 | 1130.2 |  | 12714 | 159.15 | 4.6518 | 61.015 | 0.012712 | 127.23 | 1130.2 | 1002.97
12715 | 4.6529 | 159.16 | 61.015 | 0.012715 | 127.24 | 1130.2 |  | 12715 | 159.16 | 4.6529 | 61.015 | 0.012715 | 127.24 | 1130.2 | 1002.96
12716 | 4.654 | 159.17 | 61.015 | 0.012718 | 127.25 | 1130.3 |  | 12716 | 159.17 | 4.654 | 61.015 | 0.012718 | 127.25 | 1130.3 | 1003.05
12717 | 4.6552 | 159.18 | 61.015 | 0.01272 | 127.26 | 1130.3 |  | 12717 | 159.18 | 4.6552 | 61.015 | 0.01272 | 127.26 | 1130.3 | 1003.04
12718 | 4.6563 | 159.19 | 61.014 | 0.012723 | 127.27 | 1130.3 |  | 12718 | 159.19 | 4.6563 | 61.014 | 0.012723 | 127.27 | 1130.3 | 1003.03
12719 | 4.6574 | 159.2 | 61.014 | 0.012726 | 127.28 | 1130.3 |  | 12719 | 159.2 | 4.6574 | 61.014 | 0.012726 | 127.28 | 1130.3 | 1003.02
12720 | 4.6585 | 159.21 | 61.014 | 0.012729 | 127.29 | 1130.3 |  | 12720 | 159.21 | 4.6585 | 61.014 | 0.012729 | 127.29 | 1130.3 | 1003.01
12721 | 4.6596 | 159.22 | 61.014 | 0.012732 | 127.3 | 1130.3 |  | 12721 | 159.22 | 4.6596 | 61.014 | 0.012732 | 127.3 | 1130.3 | 1003
12722 | 4.6607 | 159.23 | 61.014 | 0.012735 | 127.31 | 1130.3 |  | 12722 | 159.23 | 4.6607 | 61.014 | 0.012735 | 127.31 | 1130.3 | 1002.99
12723 | 4.6618 | 159.24 | 61.013 | 0.012738 | 127.32 | 1130.3 |  | 12723 | 159.24 | 4.6618 | 61.013 | 0.012738 | 127.32 | 1130.3 | 1002.98
12724 | 4.663 | 159.25 | 61.013 | 0.01274 | 127.33 | 1130.3 |  | 12724 | 159.25 | 4.663 | 61.013 | 0.01274 | 127.33 | 1130.3 | 1002.97
12725 | 4.6641 | 159.26 | 61.013 | 0.012743 | 127.34 | 1130.3 |  | 12725 | 159.26 | 4.6641 | 61.013 | 0.012743 | 127.34 | 1130.3 | 1002.96
12726 | 4.6652 | 159.27 | 61.013 | 0.012746 | 127.35 | 1130.3 |  | 12726 | 159.27 | 4.6652 | 61.013 | 0.012746 | 127.35 | 1130.3 | 1002.95
12727 | 4.6663 | 159.28 | 61.013 | 0.012749 | 127.36 | 1130.3 |  | 12727 | 159.28 | 4.6663 | 61.013 | 0.012749 | 127.36 | 1130.3 | 1002.94
12728 | 4.6674 | 159.29 | 61.012 | 0.012752 | 127.37 | 1130.3 |  | 12728 | 159.29 | 4.6674 | 61.012 | 0.012752 | 127.37 | 1130.3 | 1002.93
12729 | 4.6685 | 159.3 | 61.012 | 0.012755 | 127.38 | 1130.3 |  | 12729 | 159.3 | 4.6685 | 61.012 | 0.012755 | 127.38 | 1130.3 | 1002.92
12730 | 4.6697 | 159.31 | 61.012 | 0.012758 | 127.39 | 1130.3 |  | 12730 | 159.31 | 4.6697 | 61.012 | 0.012758 | 127.39 | 1130.3 | 1002.91
12731 | 4.6708 | 159.32 | 61.012 | 0.01276 | 127.4 | 1130.3 |  | 12731 | 159.32 | 4.6708 | 61.012 | 0.01276 | 127.4 | 1130.3 | 1002.9
12732 | 4.6719 | 159.33 | 61.012 | 0.012763 | 127.41 | 1130.3 |  | 12732 | 159.33 | 4.6719 | 61.012 | 0.012763 | 127.41 | 1130.3 | 1002.89
12733 | 4.673 | 159.34 | 61.011 | 0.012766 | 127.42 | 1130.3 |  | 12733 | 159.34 | 4.673 | 61.011 | 0.012766 | 127.42 | 1130.3 | 1002.88
12734 | 4.6741 | 159.35 | 61.011 | 0.012769 | 127.43 | 1130.3 |  | 12734 | 159.35 | 4.6741 | 61.011 | 0.012769 | 127.43 | 1130.3 | 1002.87
12735 | 4.6752 | 159.36 | 61.011 | 0.012772 | 127.44 | 1130.3 |  | 12735 | 159.36 | 4.6752 | 61.011 | 0.012772 | 127.44 | 1130.3 | 1002.86
12736 | 4.6764 | 159.37 | 61.011 | 0.012775 | 127.45 | 1130.3 |  | 12736 | 159.37 | 4.6764 | 61.011 | 0.012775 | 127.45 | 1130.3 | 1002.85
12737 | 4.6775 | 159.38 | 61.011 | 0.012778 | 127.46 | 1130.3 |  | 12737 | 159.38 | 4.6775 | 61.011 | 0.012778 | 127.46 | 1130.3 | 1002.84
12738 | 4.6786 | 159.39 | 61.01 | 0.01278 | 127.47 | 1130.3 |  | 12738 | 159.39 | 4.6786 | 61.01 | 0.01278 | 127.47 | 1130.3 | 1002.83
12739 | 4.6797 | 159.4 | 61.01 | 0.012783 | 127.48 | 1130.3 |  | 12739 | 159.4 | 4.6797 | 61.01 | 0.012783 | 127.48 | 1130.3 | 1002.82
12740 | 4.6808 | 159.41 | 61.01 | 0.012786 | 127.49 | 1130.3 |  | 12740 | 159.41 | 4.6808 | 61.01 | 0.012786 | 127.49 | 1130.3 | 1002.81
12741 | 4.682 | 159.42 | 61.01 | 0.012789 | 127.5 | 1130.4 |  | 12741 | 159.42 | 4.682 | 61.01 | 0.012789 | 127.5 | 1130.4 | 1002.9
12742 | 4.6831 | 159.43 | 61.01 | 0.012792 | 127.51 | 1130.4 |  | 12742 | 159.43 | 4.6831 | 61.01 | 0.012792 | 127.51 | 1130.4 | 1002.89
12743 | 4.6842 | 159.44 | 61.009 | 0.012795 | 127.52 | 1130.4 |  | 12743 | 159.44 | 4.6842 | 61.009 | 0.012795 | 127.52 | 1130.4 | 1002.88
12744 | 4.6853 | 159.45 | 61.009 | 0.012798 | 127.53 | 1130.4 |  | 12744 | 159.45 | 4.6853 | 61.009 | 0.012798 | 127.53 | 1130.4 | 1002.87
12745 | 4.6864 | 159.46 | 61.009 | 0.012801 | 127.54 | 1130.4 |  | 12745 | 159.46 | 4.6864 | 61.009 | 0.012801 | 127.54 | 1130.4 | 1002.86
12746 | 4.6875 | 159.47 | 61.009 | 0.012803 | 127.55 | 1130.4 |  | 12746 | 159.47 | 4.6875 | 61.009 | 0.012803 | 127.55 | 1130.4 | 1002.85
12747 | 4.6887 | 159.48 | 61.009 | 0.012806 | 127.56 | 1130.4 |  | 12747 | 159.48 | 4.6887 | 61.009 | 0.012806 | 127.56 | 1130.4 | 1002.84
12748 | 4.6898 | 159.49 | 61.008 | 0.012809 | 127.57 | 1130.4 |  | 12748 | 159.49 | 4.6898 | 61.008 | 0.012809 | 127.57 | 1130.4 | 1002.83
12749 | 4.6909 | 159.5 | 61.008 | 0.012812 | 127.58 | 1130.4 |  | 12749 | 159.5 | 4.6909 | 61.008 | 0.012812 | 127.58 | 1130.4 | 1002.82
12750 | 4.692 | 159.51 | 61.008 | 0.012815 | 127.59 | 1130.4 |  | 12750 | 159.51 | 4.692 | 61.008 | 0.012815 | 127.59 | 1130.4 | 1002.81
12751 | 4.6932 | 159.52 | 61.008 | 0.012818 | 127.6 | 1130.4 |  | 12751 | 159.52 | 4.6932 | 61.008 | 0.012818 | 127.6 | 1130.4 | 1002.8
12752 | 4.6943 | 159.53 | 61.008 | 0.012821 | 127.61 | 1130.4 |  | 12752 | 159.53 | 4.6943 | 61.008 | 0.012821 | 127.61 | 1130.4 | 1002.79
12753 | 4.6954 | 159.54 | 61.007 | 0.012823 | 127.62 | 1130.4 |  | 12753 | 159.54 | 4.6954 | 61.007 | 0.012823 | 127.62 | 1130.4 | 1002.78
12754 | 4.6965 | 159.55 | 61.007 | 0.012826 | 127.63 | 1130.4 |  | 12754 | 159.55 | 4.6965 | 61.007 | 0.012826 | 127.63 | 1130.4 | 1002.77
12755 | 4.6976 | 159.56 | 61.007 | 0.012829 | 127.64 | 1130.4 |  | 12755 | 159.56 | 4.6976 | 61.007 | 0.012829 | 127.64 | 1130.4 | 1002.76
12756 | 4.6988 | 159.57 | 61.007 | 0.012832 | 127.65 | 1130.4 |  | 12756 | 159.57 | 4.6988 | 61.007 | 0.012832 | 127.65 | 1130.4 | 1002.75
12757 | 4.6999 | 159.58 | 61.007 | 0.012835 | 127.66 | 1130.4 |  | 12757 | 159.58 | 4.6999 | 61.007 | 0.012835 | 127.66 | 1130.4 | 1002.74
12758 | 4.701 | 159.59 | 61.006 | 0.012838 | 127.67 | 1130.4 |  | 12758 | 159.59 | 4.701 | 61.006 | 0.012838 | 127.67 | 1130.4 | 1002.73
12759 | 4.7021 | 159.6 | 61.006 | 0.012841 | 127.68 | 1130.4 |  | 12759 | 159.6 | 4.7021 | 61.006 | 0.012841 | 127.68 | 1130.4 | 1002.72
12760 | 4.7033 | 159.61 | 61.006 | 0.012844 | 127.69 | 1130.4 |  | 12760 | 159.61 | 4.7033 | 61.006 | 0.012844 | 127.69 | 1130.4 | 1002.71
12761 | 4.7044 | 159.62 | 61.006 | 0.012846 | 127.7 | 1130.4 |  | 12761 | 159.62 | 4.7044 | 61.006 | 0.012846 | 127.7 | 1130.4 | 1002.7
12762 | 4.7055 | 159.63 | 61.006 | 0.012849 | 127.71 | 1130.4 |  | 12762 | 159.63 | 4.7055 | 61.006 | 0.012849 | 127.71 | 1130.4 | 1002.69
12763 | 4.7066 | 159.64 | 61.005 | 0.012852 | 127.72 | 1130.4 |  | 12763 | 159.64 | 4.7066 | 61.005 | 0.012852 | 127.72 | 1130.4 | 1002.68
12764 | 4.7077 | 159.65 | 61.005 | 0.012855 | 127.73 | 1130.4 |  | 12764 | 159.65 | 4.7077 | 61.005 | 0.012855 | 127.73 | 1130.4 | 1002.67
12765 | 4.7089 | 159.66 | 61.005 | 0.012858 | 127.74 | 1130.5 |  | 12765 | 159.66 | 4.7089 | 61.005 | 0.012858 | 127.74 | 1130.5 | 1002.76
12766 | 4.71 | 159.67 | 61.005 | 0.012861 | 127.75 | 1130.5 |  | 12766 | 159.67 | 4.71 | 61.005 | 0.012861 | 127.75 | 1130.5 | 1002.75
12767 | 4.7111 | 159.68 | 61.005 | 0.012864 | 127.76 | 1130.5 |  | 12767 | 159.68 | 4.7111 | 61.005 | 0.012864 | 127.76 | 1130.5 | 1002.74
12768 | 4.7122 | 159.69 | 61.004 | 0.012867 | 127.77 | 1130.5 |  | 12768 | 159.69 | 4.7122 | 61.004 | 0.012867 | 127.77 | 1130.5 | 1002.73
12769 | 4.7134 | 159.7 | 61.004 | 0.01287 | 127.78 | 1130.5 |  | 12769 | 159.7 | 4.7134 | 61.004 | 0.01287 | 127.78 | 1130.5 | 1002.72
12770 | 4.7145 | 159.71 | 61.004 | 0.012872 | 127.79 | 1130.5 |  | 12770 | 159.71 | 4.7145 | 61.004 | 0.012872 | 127.79 | 1130.5 | 1002.71
12771 | 4.7156 | 159.72 | 61.004 | 0.012875 | 127.8 | 1130.5 |  | 12771 | 159.72 | 4.7156 | 61.004 | 0.012875 | 127.8 | 1130.5 | 1002.7
12772 | 4.7167 | 159.73 | 61.004 | 0.012878 | 127.81 | 1130.5 |  | 12772 | 159.73 | 4.7167 | 61.004 | 0.012878 | 127.81 | 1130.5 | 1002.69
12773 | 4.7179 | 159.74 | 61.003 | 0.012881 | 127.82 | 1130.5 |  | 12773 | 159.74 | 4.7179 | 61.003 | 0.012881 | 127.82 | 1130.5 | 1002.68
12774 | 4.719 | 159.75 | 61.003 | 0.012884 | 127.83 | 1130.5 |  | 12774 | 159.75 | 4.719 | 61.003 | 0.012884 | 127.83 | 1130.5 | 1002.67
12775 | 4.7201 | 159.76 | 61.003 | 0.012887 | 127.84 | 1130.5 |  | 12775 | 159.76 | 4.7201 | 61.003 | 0.012887 | 127.84 | 1130.5 | 1002.66
12776 | 4.7213 | 159.77 | 61.003 | 0.01289 | 127.85 | 1130.5 |  | 12776 | 159.77 | 4.7213 | 61.003 | 0.01289 | 127.85 | 1130.5 | 1002.65
12777 | 4.7224 | 159.78 | 61.003 | 0.012893 | 127.86 | 1130.5 |  | 12777 | 159.78 | 4.7224 | 61.003 | 0.012893 | 127.86 | 1130.5 | 1002.64
12778 | 4.7235 | 159.79 | 61.002 | 0.012895 | 127.87 | 1130.5 |  | 12778 | 159.79 | 4.7235 | 61.002 | 0.012895 | 127.87 | 1130.5 | 1002.63
12779 | 4.7246 | 159.8 | 61.002 | 0.012898 | 127.88 | 1130.5 |  | 12779 | 159.8 | 4.7246 | 61.002 | 0.012898 | 127.88 | 1130.5 | 1002.62
12780 | 4.7258 | 159.81 | 61.002 | 0.012901 | 127.89 | 1130.5 |  | 12780 | 159.81 | 4.7258 | 61.002 | 0.012901 | 127.89 | 1130.5 | 1002.61
12781 | 4.7269 | 159.82 | 61.002 | 0.012904 | 127.9 | 1130.5 |  | 12781 | 159.82 | 4.7269 | 61.002 | 0.012904 | 127.9 | 1130.5 | 1002.6
12782 | 4.728 | 159.83 | 61.002 | 0.012907 | 127.91 | 1130.5 |  | 12782 | 159.83 | 4.728 | 61.002 | 0.012907 | 127.91 | 1130.5 | 1002.59
12783 | 4.7291 | 159.84 | 61.001 | 0.01291 | 127.92 | 1130.5 |  | 12783 | 159.84 | 4.7291 | 61.001 | 0.01291 | 127.92 | 1130.5 | 1002.58
12784 | 4.7303 | 159.85 | 61.001 | 0.012913 | 127.93 | 1130.5 |  | 12784 | 159.85 | 4.7303 | 61.001 | 0.012913 | 127.93 | 1130.5 | 1002.57
12785 | 4.7314 | 159.86 | 61.001 | 0.012916 | 127.94 | 1130.5 |  | 12785 | 159.86 | 4.7314 | 61.001 | 0.012916 | 127.94 | 1130.5 | 1002.56
12786 | 4.7325 | 159.87 | 61.001 | 0.012919 | 127.95 | 1130.5 |  | 12786 | 159.87 | 4.7325 | 61.001 | 0.012919 | 127.95 | 1130.5 | 1002.55
12787 | 4.7337 | 159.88 | 61.001 | 0.012921 | 127.96 | 1130.5 |  | 12787 | 159.88 | 4.7337 | 61.001 | 0.012921 | 127.96 | 1130.5 | 1002.54
12788 | 4.7348 | 159.89 | 61 | 0.012924 | 127.97 | 1130.5 |  | 12788 | 159.89 | 4.7348 | 61 | 0.012924 | 127.97 | 1130.5 | 1002.53
12789 | 4.7359 | 159.9 | 61 | 0.012927 | 127.98 | 1130.5 |  | 12789 | 159.9 | 4.7359 | 61 | 0.012927 | 127.98 | 1130.5 | 1002.52
12790 | 4.7371 | 159.91 | 61 | 0.01293 | 127.99 | 1130.6 |  | 12790 | 159.91 | 4.7371 | 61 | 0.01293 | 127.99 | 1130.6 | 1002.61
12791 | 4.7382 | 159.92 | 61 | 0.012933 | 128 | 1130.6 |  | 12791 | 159.92 | 4.7382 | 61 | 0.012933 | 128 | 1130.6 | 1002.6
12792 | 4.7393 | 159.93 | 61 | 0.012936 | 128.01 | 1130.6 |  | 12792 | 159.93 | 4.7393 | 61 | 0.012936 | 128.01 | 1130.6 | 1002.59
12793 | 4.7404 | 159.94 | 60.999 | 0.012939 | 128.02 | 1130.6 |  | 12793 | 159.94 | 4.7404 | 60.999 | 0.012939 | 128.02 | 1130.6 | 1002.58
12794 | 4.7416 | 159.95 | 60.999 | 0.012942 | 128.03 | 1130.6 |  | 12794 | 159.95 | 4.7416 | 60.999 | 0.012942 | 128.03 | 1130.6 | 1002.57
12795 | 4.7427 | 159.96 | 60.999 | 0.012945 | 128.04 | 1130.6 |  | 12795 | 159.96 | 4.7427 | 60.999 | 0.012945 | 128.04 | 1130.6 | 1002.56
12796 | 4.7438 | 159.97 | 60.999 | 0.012947 | 128.05 | 1130.6 |  | 12796 | 159.97 | 4.7438 | 60.999 | 0.012947 | 128.05 | 1130.6 | 1002.55
12797 | 4.745 | 159.98 | 60.999 | 0.01295 | 128.06 | 1130.6 |  | 12797 | 159.98 | 4.745 | 60.999 | 0.01295 | 128.06 | 1130.6 | 1002.54
12798 | 4.7461 | 159.99 | 60.998 | 0.012953 | 128.07 | 1130.6 |  | 12798 | 159.99 | 4.7461 | 60.998 | 0.012953 | 128.07 | 1130.6 | 1002.53
12799 | 4.7472 | 160 | 60.998 | 0.012956 | 128.08 | 1130.6 |  | 12799 | 160 | 4.7472 | 60.998 | 0.012956 | 128.08 | 1130.6 | 1002.52
12800 | 4.7484 | 160.01 | 60.998 | 0.012959 | 128.09 | 1130.6 |  | 12800 | 160.01 | 4.7484 | 60.998 | 0.012959 | 128.09 | 1130.6 | 1002.51
12801 | 4.7495 | 160.02 | 60.998 | 0.012962 | 128.1 | 1130.6 |  | 12801 | 160.02 | 4.7495 | 60.998 | 0.012962 | 128.1 | 1130.6 | 1002.5
12802 | 4.7506 | 160.03 | 60.998 | 0.012965 | 128.11 | 1130.6 |  | 12802 | 160.03 | 4.7506 | 60.998 | 0.012965 | 128.11 | 1130.6 | 1002.49
12803 | 4.7518 | 160.04 | 60.997 | 0.012968 | 128.12 | 1130.6 |  | 12803 | 160.04 | 4.7518 | 60.997 | 0.012968 | 128.12 | 1130.6 | 1002.48
12804 | 4.7529 | 160.05 | 60.997 | 0.012971 | 128.13 | 1130.6 |  | 12804 | 160.05 | 4.7529 | 60.997 | 0.012971 | 128.13 | 1130.6 | 1002.47
12805 | 4.754 | 160.06 | 60.997 | 0.012974 | 128.14 | 1130.6 |  | 12805 | 160.06 | 4.754 | 60.997 | 0.012974 | 128.14 | 1130.6 | 1002.46
12806 | 4.7552 | 160.07 | 60.997 | 0.012976 | 128.15 | 1130.6 |  | 12806 | 160.07 | 4.7552 | 60.997 | 0.012976 | 128.15 | 1130.6 | 1002.45
12807 | 4.7563 | 160.08 | 60.997 | 0.012979 | 128.16 | 1130.6 |  | 12807 | 160.08 | 4.7563 | 60.997 | 0.012979 | 128.16 | 1130.6 | 1002.44
12808 | 4.7574 | 160.09 | 60.996 | 0.012982 | 128.17 | 1130.6 |  | 12808 | 160.09 | 4.7574 | 60.996 | 0.012982 | 128.17 | 1130.6 | 1002.43
12809 | 4.7586 | 160.1 | 60.996 | 0.012985 | 128.18 | 1130.6 |  | 12809 | 160.1 | 4.7586 | 60.996 | 0.012985 | 128.18 | 1130.6 | 1002.42
12810 | 4.7597 | 160.11 | 60.996 | 0.012988 | 128.19 | 1130.6 |  | 12810 | 160.11 | 4.7597 | 60.996 | 0.012988 | 128.19 | 1130.6 | 1002.41
12811 | 4.7608 | 160.12 | 60.996 | 0.012991 | 128.2 | 1130.6 |  | 12811 | 160.12 | 4.7608 | 60.996 | 0.012991 | 128.2 | 1130.6 | 1002.4
12812 | 4.762 | 160.13 | 60.996 | 0.012994 | 128.21 | 1130.6 |  | 12812 | 160.13 | 4.762 | 60.996 | 0.012994 | 128.21 | 1130.6 | 1002.39
12813 | 4.7631 | 160.14 | 60.995 | 0.012997 | 128.22 | 1130.6 |  | 12813 | 160.14 | 4.7631 | 60.995 | 0.012997 | 128.22 | 1130.6 | 1002.38
12814 | 4.7642 | 160.15 | 60.995 | 0.013 | 128.23 | 1130.7 |  | 12814 | 160.15 | 4.7642 | 60.995 | 0.013 | 128.23 | 1130.7 | 1002.47
12815 | 4.7654 | 160.16 | 60.995 | 0.013003 | 128.24 | 1130.7 |  | 12815 | 160.16 | 4.7654 | 60.995 | 0.013003 | 128.24 | 1130.7 | 1002.46
12816 | 4.7665 | 160.17 | 60.995 | 0.013005 | 128.25 | 1130.7 |  | 12816 | 160.17 | 4.7665 | 60.995 | 0.013005 | 128.25 | 1130.7 | 1002.45
12817 | 4.7677 | 160.18 | 60.995 | 0.013008 | 128.26 | 1130.7 |  | 12817 | 160.18 | 4.7677 | 60.995 | 0.013008 | 128.26 | 1130.7 | 1002.44
12818 | 4.7688 | 160.19 | 60.994 | 0.013011 | 128.27 | 1130.7 |  | 12818 | 160.19 | 4.7688 | 60.994 | 0.013011 | 128.27 | 1130.7 | 1002.43
12819 | 4.7699 | 160.2 | 60.994 | 0.013014 | 128.28 | 1130.7 |  | 12819 | 160.2 | 4.7699 | 60.994 | 0.013014 | 128.28 | 1130.7 | 1002.42
12820 | 4.7711 | 160.21 | 60.994 | 0.013017 | 128.29 | 1130.7 |  | 12820 | 160.21 | 4.7711 | 60.994 | 0.013017 | 128.29 | 1130.7 | 1002.41
12821 | 4.7722 | 160.22 | 60.994 | 0.01302 | 128.3 | 1130.7 |  | 12821 | 160.22 | 4.7722 | 60.994 | 0.01302 | 128.3 | 1130.7 | 1002.4
12822 | 4.7733 | 160.23 | 60.994 | 0.013023 | 128.31 | 1130.7 |  | 12822 | 160.23 | 4.7733 | 60.994 | 0.013023 | 128.31 | 1130.7 | 1002.39
12823 | 4.7745 | 160.24 | 60.993 | 0.013026 | 128.32 | 1130.7 |  | 12823 | 160.24 | 4.7745 | 60.993 | 0.013026 | 128.32 | 1130.7 | 1002.38
12824 | 4.7756 | 160.25 | 60.993 | 0.013029 | 128.33 | 1130.7 |  | 12824 | 160.25 | 4.7756 | 60.993 | 0.013029 | 128.33 | 1130.7 | 1002.37
12825 | 4.7767 | 160.26 | 60.993 | 0.013032 | 128.34 | 1130.7 |  | 12825 | 160.26 | 4.7767 | 60.993 | 0.013032 | 128.34 | 1130.7 | 1002.36
12826 | 4.7779 | 160.27 | 60.993 | 0.013035 | 128.35 | 1130.7 |  | 12826 | 160.27 | 4.7779 | 60.993 | 0.013035 | 128.35 | 1130.7 | 1002.35
12827 | 4.779 | 160.28 | 60.993 | 0.013037 | 128.36 | 1130.7 |  | 12827 | 160.28 | 4.779 | 60.993 | 0.013037 | 128.36 | 1130.7 | 1002.34
12828 | 4.7802 | 160.29 | 60.992 | 0.01304 | 128.37 | 1130.7 |  | 12828 | 160.29 | 4.7802 | 60.992 | 0.01304 | 128.37 | 1130.7 | 1002.33
12829 | 4.7813 | 160.3 | 60.992 | 0.013043 | 128.38 | 1130.7 |  | 12829 | 160.3 | 4.7813 | 60.992 | 0.013043 | 128.38 | 1130.7 | 1002.32
12830 | 4.7824 | 160.31 | 60.992 | 0.013046 | 128.39 | 1130.7 |  | 12830 | 160.31 | 4.7824 | 60.992 | 0.013046 | 128.39 | 1130.7 | 1002.31
12831 | 4.7836 | 160.32 | 60.992 | 0.013049 | 128.4 | 1130.7 |  | 12831 | 160.32 | 4.7836 | 60.992 | 0.013049 | 128.4 | 1130.7 | 1002.3
12832 | 4.7847 | 160.33 | 60.992 | 0.013052 | 128.41 | 1130.7 |  | 12832 | 160.33 | 4.7847 | 60.992 | 0.013052 | 128.41 | 1130.7 | 1002.29
12833 | 4.7859 | 160.34 | 60.991 | 0.013055 | 128.42 | 1130.7 |  | 12833 | 160.34 | 4.7859 | 60.991 | 0.013055 | 128.42 | 1130.7 | 1002.28
12834 | 4.787 | 160.35 | 60.991 | 0.013058 | 128.43 | 1130.7 |  | 12834 | 160.35 | 4.787 | 60.991 | 0.013058 | 128.43 | 1130.7 | 1002.27
12835 | 4.7881 | 160.36 | 60.991 | 0.013061 | 128.44 | 1130.7 |  | 12835 | 160.36 | 4.7881 | 60.991 | 0.013061 | 128.44 | 1130.7 | 1002.26
12836 | 4.7893 | 160.37 | 60.991 | 0.013064 | 128.45 | 1130.7 |  | 12836 | 160.37 | 4.7893 | 60.991 | 0.013064 | 128.45 | 1130.7 | 1002.25
12837 | 4.7904 | 160.38 | 60.991 | 0.013067 | 128.46 | 1130.7 |  | 12837 | 160.38 | 4.7904 | 60.991 | 0.013067 | 128.46 | 1130.7 | 1002.24
12838 | 4.7916 | 160.39 | 60.99 | 0.013069 | 128.47 | 1130.7 |  | 12838 | 160.39 | 4.7916 | 60.99 | 0.013069 | 128.47 | 1130.7 | 1002.23
12839 | 4.7927 | 160.4 | 60.99 | 0.013072 | 128.48 | 1130.8 |  | 12839 | 160.4 | 4.7927 | 60.99 | 0.013072 | 128.48 | 1130.8 | 1002.32
12840 | 4.7938 | 160.41 | 60.99 | 0.013075 | 128.49 | 1130.8 |  | 12840 | 160.41 | 4.7938 | 60.99 | 0.013075 | 128.49 | 1130.8 | 1002.31
12841 | 4.795 | 160.42 | 60.99 | 0.013078 | 128.5 | 1130.8 |  | 12841 | 160.42 | 4.795 | 60.99 | 0.013078 | 128.5 | 1130.8 | 1002.3
12842 | 4.7961 | 160.43 | 60.99 | 0.013081 | 128.51 | 1130.8 |  | 12842 | 160.43 | 4.7961 | 60.99 | 0.013081 | 128.51 | 1130.8 | 1002.29
12843 | 4.7973 | 160.44 | 60.989 | 0.013084 | 128.52 | 1130.8 |  | 12843 | 160.44 | 4.7973 | 60.989 | 0.013084 | 128.52 | 1130.8 | 1002.28
12844 | 4.7984 | 160.45 | 60.989 | 0.013087 | 128.53 | 1130.8 |  | 12844 | 160.45 | 4.7984 | 60.989 | 0.013087 | 128.53 | 1130.8 | 1002.27
12845 | 4.7996 | 160.46 | 60.989 | 0.01309 | 128.54 | 1130.8 |  | 12845 | 160.46 | 4.7996 | 60.989 | 0.01309 | 128.54 | 1130.8 | 1002.26
12846 | 4.8007 | 160.47 | 60.989 | 0.013093 | 128.55 | 1130.8 |  | 12846 | 160.47 | 4.8007 | 60.989 | 0.013093 | 128.55 | 1130.8 | 1002.25
12847 | 4.8018 | 160.48 | 60.989 | 0.013096 | 128.56 | 1130.8 |  | 12847 | 160.48 | 4.8018 | 60.989 | 0.013096 | 128.56 | 1130.8 | 1002.24
12848 | 4.803 | 160.49 | 60.988 | 0.013099 | 128.57 | 1130.8 |  | 12848 | 160.49 | 4.803 | 60.988 | 0.013099 | 128.57 | 1130.8 | 1002.23
12849 | 4.8041 | 160.5 | 60.988 | 0.013102 | 128.58 | 1130.8 |  | 12849 | 160.5 | 4.8041 | 60.988 | 0.013102 | 128.58 | 1130.8 | 1002.22
12850 | 4.8053 | 160.51 | 60.988 | 0.013105 | 128.59 | 1130.8 |  | 12850 | 160.51 | 4.8053 | 60.988 | 0.013105 | 128.59 | 1130.8 | 1002.21
12851 | 4.8064 | 160.52 | 60.988 | 0.013107 | 128.6 | 1130.8 |  | 12851 | 160.52 | 4.8064 | 60.988 | 0.013107 | 128.6 | 1130.8 | 1002.2
12852 | 4.8076 | 160.53 | 60.988 | 0.01311 | 128.61 | 1130.8 |  | 12852 | 160.53 | 4.8076 | 60.988 | 0.01311 | 128.61 | 1130.8 | 1002.19
12853 | 4.8087 | 160.54 | 60.987 | 0.013113 | 128.62 | 1130.8 |  | 12853 | 160.54 | 4.8087 | 60.987 | 0.013113 | 128.62 | 1130.8 | 1002.18
12854 | 4.8099 | 160.55 | 60.987 | 0.013116 | 128.63 | 1130.8 |  | 12854 | 160.55 | 4.8099 | 60.987 | 0.013116 | 128.63 | 1130.8 | 1002.17
12855 | 4.811 | 160.56 | 60.987 | 0.013119 | 128.64 | 1130.8 |  | 12855 | 160.56 | 4.811 | 60.987 | 0.013119 | 128.64 | 1130.8 | 1002.16
12856 | 4.8121 | 160.57 | 60.987 | 0.013122 | 128.65 | 1130.8 |  | 12856 | 160.57 | 4.8121 | 60.987 | 0.013122 | 128.65 | 1130.8 | 1002.15
12857 | 4.8133 | 160.58 | 60.987 | 0.013125 | 128.66 | 1130.8 |  | 12857 | 160.58 | 4.8133 | 60.987 | 0.013125 | 128.66 | 1130.8 | 1002.14
12858 | 4.8144 | 160.59 | 60.986 | 0.013128 | 128.67 | 1130.8 |  | 12858 | 160.59 | 4.8144 | 60.986 | 0.013128 | 128.67 | 1130.8 | 1002.13
12859 | 4.8156 | 160.6 | 60.986 | 0.013131 | 128.68 | 1130.8 |  | 12859 | 160.6 | 4.8156 | 60.986 | 0.013131 | 128.68 | 1130.8 | 1002.12
12860 | 4.8167 | 160.61 | 60.986 | 0.013134 | 128.69 | 1130.8 |  | 12860 | 160.61 | 4.8167 | 60.986 | 0.013134 | 128.69 | 1130.8 | 1002.11
12861 | 4.8179 | 160.62 | 60.986 | 0.013137 | 128.7 | 1130.8 |  | 12861 | 160.62 | 4.8179 | 60.986 | 0.013137 | 128.7 | 1130.8 | 1002.1
12862 | 4.819 | 160.63 | 60.986 | 0.01314 | 128.71 | 1130.8 |  | 12862 | 160.63 | 4.819 | 60.986 | 0.01314 | 128.71 | 1130.8 | 1002.09
12863 | 4.8202 | 160.64 | 60.985 | 0.013143 | 128.72 | 1130.9 |  | 12863 | 160.64 | 4.8202 | 60.985 | 0.013143 | 128.72 | 1130.9 | 1002.18
12864 | 4.8213 | 160.65 | 60.985 | 0.013146 | 128.73 | 1130.9 |  | 12864 | 160.65 | 4.8213 | 60.985 | 0.013146 | 128.73 | 1130.9 | 1002.17
12865 | 4.8225 | 160.66 | 60.985 | 0.013148 | 128.74 | 1130.9 |  | 12865 | 160.66 | 4.8225 | 60.985 | 0.013148 | 128.74 | 1130.9 | 1002.16
12866 | 4.8236 | 160.67 | 60.985 | 0.013151 | 128.75 | 1130.9 |  | 12866 | 160.67 | 4.8236 | 60.985 | 0.013151 | 128.75 | 1130.9 | 1002.15
12867 | 4.8248 | 160.68 | 60.985 | 0.013154 | 128.76 | 1130.9 |  | 12867 | 160.68 | 4.8248 | 60.985 | 0.013154 | 128.76 | 1130.9 | 1002.14
12868 | 4.8259 | 160.69 | 60.984 | 0.013157 | 128.77 | 1130.9 |  | 12868 | 160.69 | 4.8259 | 60.984 | 0.013157 | 128.77 | 1130.9 | 1002.13
12869 | 4.827 | 160.7 | 60.984 | 0.01316 | 128.78 | 1130.9 |  | 12869 | 160.7 | 4.827 | 60.984 | 0.01316 | 128.78 | 1130.9 | 1002.12
12870 | 4.8282 | 160.71 | 60.984 | 0.013163 | 128.79 | 1130.9 |  | 12870 | 160.71 | 4.8282 | 60.984 | 0.013163 | 128.79 | 1130.9 | 1002.11
12871 | 4.8293 | 160.72 | 60.984 | 0.013166 | 128.8 | 1130.9 |  | 12871 | 160.72 | 4.8293 | 60.984 | 0.013166 | 128.8 | 1130.9 | 1002.1
12872 | 4.8305 | 160.73 | 60.984 | 0.013169 | 128.81 | 1130.9 |  | 12872 | 160.73 | 4.8305 | 60.984 | 0.013169 | 128.81 | 1130.9 | 1002.09
12873 | 4.8316 | 160.74 | 60.983 | 0.013172 | 128.82 | 1130.9 |  | 12873 | 160.74 | 4.8316 | 60.983 | 0.013172 | 128.82 | 1130.9 | 1002.08
12874 | 4.8328 | 160.75 | 60.983 | 0.013175 | 128.83 | 1130.9 |  | 12874 | 160.75 | 4.8328 | 60.983 | 0.013175 | 128.83 | 1130.9 | 1002.07
12875 | 4.8339 | 160.76 | 60.983 | 0.013178 | 128.84 | 1130.9 |  | 12875 | 160.76 | 4.8339 | 60.983 | 0.013178 | 128.84 | 1130.9 | 1002.06
12876 | 4.8351 | 160.77 | 60.983 | 0.013181 | 128.85 | 1130.9 |  | 12876 | 160.77 | 4.8351 | 60.983 | 0.013181 | 128.85 | 1130.9 | 1002.05
12877 | 4.8362 | 160.78 | 60.983 | 0.013184 | 128.86 | 1130.9 |  | 12877 | 160.78 | 4.8362 | 60.983 | 0.013184 | 128.86 | 1130.9 | 1002.04
12878 | 4.8374 | 160.79 | 60.982 | 0.013187 | 128.87 | 1130.9 |  | 12878 | 160.79 | 4.8374 | 60.982 | 0.013187 | 128.87 | 1130.9 | 1002.03
12879 | 4.8385 | 160.8 | 60.982 | 0.01319 | 128.88 | 1130.9 |  | 12879 | 160.8 | 4.8385 | 60.982 | 0.01319 | 128.88 | 1130.9 | 1002.02
12880 | 4.8397 | 160.81 | 60.982 | 0.013192 | 128.89 | 1130.9 |  | 12880 | 160.81 | 4.8397 | 60.982 | 0.013192 | 128.89 | 1130.9 | 1002.01
12881 | 4.8408 | 160.82 | 60.982 | 0.013195 | 128.9 | 1130.9 |  | 12881 | 160.82 | 4.8408 | 60.982 | 0.013195 | 128.9 | 1130.9 | 1002
12882 | 4.842 | 160.83 | 60.982 | 0.013198 | 128.91 | 1130.9 |  | 12882 | 160.83 | 4.842 | 60.982 | 0.013198 | 128.91 | 1130.9 | 1001.99
12883 | 4.8431 | 160.84 | 60.981 | 0.013201 | 128.92 | 1130.9 |  | 12883 | 160.84 | 4.8431 | 60.981 | 0.013201 | 128.92 | 1130.9 | 1001.98
12884 | 4.8443 | 160.85 | 60.981 | 0.013204 | 128.94 | 1130.9 |  | 12884 | 160.85 | 4.8443 | 60.981 | 0.013204 | 128.94 | 1130.9 | 1001.96
12885 | 4.8454 | 160.86 | 60.981 | 0.013207 | 128.95 | 1130.9 |  | 12885 | 160.86 | 4.8454 | 60.981 | 0.013207 | 128.95 | 1130.9 | 1001.95
12886 | 4.8466 | 160.87 | 60.981 | 0.01321 | 128.96 | 1130.9 |  | 12886 | 160.87 | 4.8466 | 60.981 | 0.01321 | 128.96 | 1130.9 | 1001.94
12887 | 4.8478 | 160.88 | 60.981 | 0.013213 | 128.97 | 1130.9 |  | 12887 | 160.88 | 4.8478 | 60.981 | 0.013213 | 128.97 | 1130.9 | 1001.93
12888 | 4.8489 | 160.89 | 60.98 | 0.013216 | 128.98 | 1131 |  | 12888 | 160.89 | 4.8489 | 60.98 | 0.013216 | 128.98 | 1131 | 1002.02
12889 | 4.8501 | 160.9 | 60.98 | 0.013219 | 128.99 | 1131 |  | 12889 | 160.9 | 4.8501 | 60.98 | 0.013219 | 128.99 | 1131 | 1002.01
12890 | 4.8512 | 160.91 | 60.98 | 0.013222 | 129 | 1131 |  | 12890 | 160.91 | 4.8512 | 60.98 | 0.013222 | 129 | 1131 | 1002
12891 | 4.8524 | 160.92 | 60.98 | 0.013225 | 129.01 | 1131 |  | 12891 | 160.92 | 4.8524 | 60.98 | 0.013225 | 129.01 | 1131 | 1001.99
12892 | 4.8535 | 160.93 | 60.98 | 0.013228 | 129.02 | 1131 |  | 12892 | 160.93 | 4.8535 | 60.98 | 0.013228 | 129.02 | 1131 | 1001.98
12893 | 4.8547 | 160.94 | 60.979 | 0.013231 | 129.03 | 1131 |  | 12893 | 160.94 | 4.8547 | 60.979 | 0.013231 | 129.03 | 1131 | 1001.97
12894 | 4.8558 | 160.95 | 60.979 | 0.013234 | 129.04 | 1131 |  | 12894 | 160.95 | 4.8558 | 60.979 | 0.013234 | 129.04 | 1131 | 1001.96
12895 | 4.857 | 160.96 | 60.979 | 0.013237 | 129.05 | 1131 |  | 12895 | 160.96 | 4.857 | 60.979 | 0.013237 | 129.05 | 1131 | 1001.95
12896 | 4.8581 | 160.97 | 60.979 | 0.01324 | 129.06 | 1131 |  | 12896 | 160.97 | 4.8581 | 60.979 | 0.01324 | 129.06 | 1131 | 1001.94
12897 | 4.8593 | 160.98 | 60.979 | 0.013243 | 129.07 | 1131 |  | 12897 | 160.98 | 4.8593 | 60.979 | 0.013243 | 129.07 | 1131 | 1001.93
12898 | 4.8604 | 160.99 | 60.978 | 0.013245 | 129.08 | 1131 |  | 12898 | 160.99 | 4.8604 | 60.978 | 0.013245 | 129.08 | 1131 | 1001.92
12899 | 4.8616 | 161 | 60.978 | 0.013248 | 129.09 | 1131 |  | 12899 | 161 | 4.8616 | 60.978 | 0.013248 | 129.09 | 1131 | 1001.91
12900 | 4.8628 | 161.01 | 60.978 | 0.013251 | 129.1 | 1131 |  | 12900 | 161.01 | 4.8628 | 60.978 | 0.013251 | 129.1 | 1131 | 1001.9
12901 | 4.8639 | 161.02 | 60.978 | 0.013254 | 129.11 | 1131 |  | 12901 | 161.02 | 4.8639 | 60.978 | 0.013254 | 129.11 | 1131 | 1001.89
12902 | 4.8651 | 161.03 | 60.977 | 0.013257 | 129.12 | 1131 |  | 12902 | 161.03 | 4.8651 | 60.977 | 0.013257 | 129.12 | 1131 | 1001.88
12903 | 4.8662 | 161.04 | 60.977 | 0.01326 | 129.13 | 1131 |  | 12903 | 161.04 | 4.8662 | 60.977 | 0.01326 | 129.13 | 1131 | 1001.87
12904 | 4.8674 | 161.05 | 60.977 | 0.013263 | 129.14 | 1131 |  | 12904 | 161.05 | 4.8674 | 60.977 | 0.013263 | 129.14 | 1131 | 1001.86
12905 | 4.8685 | 161.06 | 60.977 | 0.013266 | 129.15 | 1131 |  | 12905 | 161.06 | 4.8685 | 60.977 | 0.013266 | 129.15 | 1131 | 1001.85
12906 | 4.8697 | 161.07 | 60.977 | 0.013269 | 129.16 | 1131 |  | 12906 | 161.07 | 4.8697 | 60.977 | 0.013269 | 129.16 | 1131 | 1001.84
12907 | 4.8708 | 161.08 | 60.976 | 0.013272 | 129.17 | 1131 |  | 12907 | 161.08 | 4.8708 | 60.976 | 0.013272 | 129.17 | 1131 | 1001.83
12908 | 4.872 | 161.09 | 60.976 | 0.013275 | 129.18 | 1131 |  | 12908 | 161.09 | 4.872 | 60.976 | 0.013275 | 129.18 | 1131 | 1001.82
12909 | 4.8732 | 161.1 | 60.976 | 0.013278 | 129.19 | 1131 |  | 12909 | 161.1 | 4.8732 | 60.976 | 0.013278 | 129.19 | 1131 | 1001.81
12910 | 4.8743 | 161.11 | 60.976 | 0.013281 | 129.2 | 1131 |  | 12910 | 161.11 | 4.8743 | 60.976 | 0.013281 | 129.2 | 1131 | 1001.8
12911 | 4.8755 | 161.12 | 60.976 | 0.013284 | 129.21 | 1131 |  | 12911 | 161.12 | 4.8755 | 60.976 | 0.013284 | 129.21 | 1131 | 1001.79
12912 | 4.8766 | 161.13 | 60.975 | 0.013287 | 129.22 | 1131.1 |  | 12912 | 161.13 | 4.8766 | 60.975 | 0.013287 | 129.22 | 1131.1 | 1001.88
12913 | 4.8778 | 161.14 | 60.975 | 0.01329 | 129.23 | 1131.1 |  | 12913 | 161.14 | 4.8778 | 60.975 | 0.01329 | 129.23 | 1131.1 | 1001.87
12914 | 4.879 | 161.15 | 60.975 | 0.013293 | 129.24 | 1131.1 |  | 12914 | 161.15 | 4.879 | 60.975 | 0.013293 | 129.24 | 1131.1 | 1001.86
12915 | 4.8801 | 161.16 | 60.975 | 0.013296 | 129.25 | 1131.1 |  | 12915 | 161.16 | 4.8801 | 60.975 | 0.013296 | 129.25 | 1131.1 | 1001.85
12916 | 4.8813 | 161.17 | 60.975 | 0.013299 | 129.26 | 1131.1 |  | 12916 | 161.17 | 4.8813 | 60.975 | 0.013299 | 129.26 | 1131.1 | 1001.84
12917 | 4.8824 | 161.18 | 60.974 | 0.013302 | 129.27 | 1131.1 |  | 12917 | 161.18 | 4.8824 | 60.974 | 0.013302 | 129.27 | 1131.1 | 1001.83
12918 | 4.8836 | 161.19 | 60.974 | 0.013305 | 129.28 | 1131.1 |  | 12918 | 161.19 | 4.8836 | 60.974 | 0.013305 | 129.28 | 1131.1 | 1001.82
12919 | 4.8847 | 161.2 | 60.974 | 0.013308 | 129.29 | 1131.1 |  | 12919 | 161.2 | 4.8847 | 60.974 | 0.013308 | 129.29 | 1131.1 | 1001.81
12920 | 4.8859 | 161.21 | 60.974 | 0.01331 | 129.3 | 1131.1 |  | 12920 | 161.21 | 4.8859 | 60.974 | 0.01331 | 129.3 | 1131.1 | 1001.8
12921 | 4.8871 | 161.22 | 60.974 | 0.013313 | 129.31 | 1131.1 |  | 12921 | 161.22 | 4.8871 | 60.974 | 0.013313 | 129.31 | 1131.1 | 1001.79
12922 | 4.8882 | 161.23 | 60.973 | 0.013316 | 129.32 | 1131.1 |  | 12922 | 161.23 | 4.8882 | 60.973 | 0.013316 | 129.32 | 1131.1 | 1001.78
12923 | 4.8894 | 161.24 | 60.973 | 0.013319 | 129.33 | 1131.1 |  | 12923 | 161.24 | 4.8894 | 60.973 | 0.013319 | 129.33 | 1131.1 | 1001.77
12924 | 4.8906 | 161.25 | 60.973 | 0.013322 | 129.34 | 1131.1 |  | 12924 | 161.25 | 4.8906 | 60.973 | 0.013322 | 129.34 | 1131.1 | 1001.76
12925 | 4.8917 | 161.26 | 60.973 | 0.013325 | 129.35 | 1131.1 |  | 12925 | 161.26 | 4.8917 | 60.973 | 0.013325 | 129.35 | 1131.1 | 1001.75
12926 | 4.8929 | 161.27 | 60.973 | 0.013328 | 129.36 | 1131.1 |  | 12926 | 161.27 | 4.8929 | 60.973 | 0.013328 | 129.36 | 1131.1 | 1001.74
12927 | 4.894 | 161.28 | 60.972 | 0.013331 | 129.37 | 1131.1 |  | 12927 | 161.28 | 4.894 | 60.972 | 0.013331 | 129.37 | 1131.1 | 1001.73
12928 | 4.8952 | 161.29 | 60.972 | 0.013334 | 129.38 | 1131.1 |  | 12928 | 161.29 | 4.8952 | 60.972 | 0.013334 | 129.38 | 1131.1 | 1001.72
12929 | 4.8964 | 161.3 | 60.972 | 0.013337 | 129.39 | 1131.1 |  | 12929 | 161.3 | 4.8964 | 60.972 | 0.013337 | 129.39 | 1131.1 | 1001.71
12930 | 4.8975 | 161.31 | 60.972 | 0.01334 | 129.4 | 1131.1 |  | 12930 | 161.31 | 4.8975 | 60.972 | 0.01334 | 129.4 | 1131.1 | 1001.7
12931 | 4.8987 | 161.32 | 60.972 | 0.013343 | 129.41 | 1131.1 |  | 12931 | 161.32 | 4.8987 | 60.972 | 0.013343 | 129.41 | 1131.1 | 1001.69
12932 | 4.8998 | 161.33 | 60.971 | 0.013346 | 129.42 | 1131.1 |  | 12932 | 161.33 | 4.8998 | 60.971 | 0.013346 | 129.42 | 1131.1 | 1001.68
12933 | 4.901 | 161.34 | 60.971 | 0.013349 | 129.43 | 1131.1 |  | 12933 | 161.34 | 4.901 | 60.971 | 0.013349 | 129.43 | 1131.1 | 1001.67
12934 | 4.9022 | 161.35 | 60.971 | 0.013352 | 129.44 | 1131.1 |  | 12934 | 161.35 | 4.9022 | 60.971 | 0.013352 | 129.44 | 1131.1 | 1001.66
12935 | 4.9033 | 161.36 | 60.971 | 0.013355 | 129.45 | 1131.1 |  | 12935 | 161.36 | 4.9033 | 60.971 | 0.013355 | 129.45 | 1131.1 | 1001.65
12936 | 4.9045 | 161.37 | 60.971 | 0.013358 | 129.46 | 1131.1 |  | 12936 | 161.37 | 4.9045 | 60.971 | 0.013358 | 129.46 | 1131.1 | 1001.64
12937 | 4.9057 | 161.38 | 60.97 | 0.013361 | 129.47 | 1131.2 |  | 12937 | 161.38 | 4.9057 | 60.97 | 0.013361 | 129.47 | 1131.2 | 1001.73
12938 | 4.9068 | 161.39 | 60.97 | 0.013364 | 129.48 | 1131.2 |  | 12938 | 161.39 | 4.9068 | 60.97 | 0.013364 | 129.48 | 1131.2 | 1001.72
12939 | 4.908 | 161.4 | 60.97 | 0.013367 | 129.49 | 1131.2 |  | 12939 | 161.4 | 4.908 | 60.97 | 0.013367 | 129.49 | 1131.2 | 1001.71
12940 | 4.9092 | 161.41 | 60.97 | 0.01337 | 129.5 | 1131.2 |  | 12940 | 161.41 | 4.9092 | 60.97 | 0.01337 | 129.5 | 1131.2 | 1001.7
12941 | 4.9103 | 161.42 | 60.97 | 0.013373 | 129.51 | 1131.2 |  | 12941 | 161.42 | 4.9103 | 60.97 | 0.013373 | 129.51 | 1131.2 | 1001.69
12942 | 4.9115 | 161.43 | 60.969 | 0.013376 | 129.52 | 1131.2 |  | 12942 | 161.43 | 4.9115 | 60.969 | 0.013376 | 129.52 | 1131.2 | 1001.68
12943 | 4.9127 | 161.44 | 60.969 | 0.013379 | 129.53 | 1131.2 |  | 12943 | 161.44 | 4.9127 | 60.969 | 0.013379 | 129.53 | 1131.2 | 1001.67
12944 | 4.9138 | 161.45 | 60.969 | 0.013382 | 129.54 | 1131.2 |  | 12944 | 161.45 | 4.9138 | 60.969 | 0.013382 | 129.54 | 1131.2 | 1001.66
12945 | 4.915 | 161.46 | 60.969 | 0.013385 | 129.55 | 1131.2 |  | 12945 | 161.46 | 4.915 | 60.969 | 0.013385 | 129.55 | 1131.2 | 1001.65
12946 | 4.9161 | 161.47 | 60.969 | 0.013388 | 129.56 | 1131.2 |  | 12946 | 161.47 | 4.9161 | 60.969 | 0.013388 | 129.56 | 1131.2 | 1001.64
12947 | 4.9173 | 161.48 | 60.968 | 0.013391 | 129.57 | 1131.2 |  | 12947 | 161.48 | 4.9173 | 60.968 | 0.013391 | 129.57 | 1131.2 | 1001.63
12948 | 4.9185 | 161.49 | 60.968 | 0.013394 | 129.58 | 1131.2 |  | 12948 | 161.49 | 4.9185 | 60.968 | 0.013394 | 129.58 | 1131.2 | 1001.62
12949 | 4.9196 | 161.5 | 60.968 | 0.013397 | 129.59 | 1131.2 |  | 12949 | 161.5 | 4.9196 | 60.968 | 0.013397 | 129.59 | 1131.2 | 1001.61
12950 | 4.9208 | 161.51 | 60.968 | 0.0134 | 129.6 | 1131.2 |  | 12950 | 161.51 | 4.9208 | 60.968 | 0.0134 | 129.6 | 1131.2 | 1001.6
12951 | 4.922 | 161.52 | 60.968 | 0.013403 | 129.61 | 1131.2 |  | 12951 | 161.52 | 4.922 | 60.968 | 0.013403 | 129.61 | 1131.2 | 1001.59
12952 | 4.9232 | 161.53 | 60.967 | 0.013406 | 129.62 | 1131.2 |  | 12952 | 161.53 | 4.9232 | 60.967 | 0.013406 | 129.62 | 1131.2 | 1001.58
12953 | 4.9243 | 161.54 | 60.967 | 0.013409 | 129.63 | 1131.2 |  | 12953 | 161.54 | 4.9243 | 60.967 | 0.013409 | 129.63 | 1131.2 | 1001.57
12954 | 4.9255 | 161.55 | 60.967 | 0.013412 | 129.64 | 1131.2 |  | 12954 | 161.55 | 4.9255 | 60.967 | 0.013412 | 129.64 | 1131.2 | 1001.56
12955 | 4.9267 | 161.56 | 60.967 | 0.013414 | 129.65 | 1131.2 |  | 12955 | 161.56 | 4.9267 | 60.967 | 0.013414 | 129.65 | 1131.2 | 1001.55
12956 | 4.9278 | 161.57 | 60.967 | 0.013417 | 129.66 | 1131.2 |  | 12956 | 161.57 | 4.9278 | 60.967 | 0.013417 | 129.66 | 1131.2 | 1001.54
12957 | 4.929 | 161.58 | 60.966 | 0.01342 | 129.67 | 1131.2 |  | 12957 | 161.58 | 4.929 | 60.966 | 0.01342 | 129.67 | 1131.2 | 1001.53
12958 | 4.9302 | 161.59 | 60.966 | 0.013423 | 129.68 | 1131.2 |  | 12958 | 161.59 | 4.9302 | 60.966 | 0.013423 | 129.68 | 1131.2 | 1001.52
12959 | 4.9313 | 161.6 | 60.966 | 0.013426 | 129.69 | 1131.2 |  | 12959 | 161.6 | 4.9313 | 60.966 | 0.013426 | 129.69 | 1131.2 | 1001.51
12960 | 4.9325 | 161.61 | 60.966 | 0.013429 | 129.7 | 1131.2 |  | 12960 | 161.61 | 4.9325 | 60.966 | 0.013429 | 129.7 | 1131.2 | 1001.5
12961 | 4.9337 | 161.62 | 60.966 | 0.013432 | 129.71 | 1131.3 |  | 12961 | 161.62 | 4.9337 | 60.966 | 0.013432 | 129.71 | 1131.3 | 1001.59
12962 | 4.9348 | 161.63 | 60.965 | 0.013435 | 129.72 | 1131.3 |  | 12962 | 161.63 | 4.9348 | 60.965 | 0.013435 | 129.72 | 1131.3 | 1001.58
12963 | 4.936 | 161.64 | 60.965 | 0.013438 | 129.73 | 1131.3 |  | 12963 | 161.64 | 4.936 | 60.965 | 0.013438 | 129.73 | 1131.3 | 1001.57
12964 | 4.9372 | 161.65 | 60.965 | 0.013441 | 129.74 | 1131.3 |  | 12964 | 161.65 | 4.9372 | 60.965 | 0.013441 | 129.74 | 1131.3 | 1001.56
12965 | 4.9383 | 161.66 | 60.965 | 0.013444 | 129.75 | 1131.3 |  | 12965 | 161.66 | 4.9383 | 60.965 | 0.013444 | 129.75 | 1131.3 | 1001.55
12966 | 4.9395 | 161.67 | 60.965 | 0.013447 | 129.76 | 1131.3 |  | 12966 | 161.67 | 4.9395 | 60.965 | 0.013447 | 129.76 | 1131.3 | 1001.54
12967 | 4.9407 | 161.68 | 60.964 | 0.01345 | 129.77 | 1131.3 |  | 12967 | 161.68 | 4.9407 | 60.964 | 0.01345 | 129.77 | 1131.3 | 1001.53
12968 | 4.9419 | 161.69 | 60.964 | 0.013453 | 129.78 | 1131.3 |  | 12968 | 161.69 | 4.9419 | 60.964 | 0.013453 | 129.78 | 1131.3 | 1001.52
12969 | 4.943 | 161.7 | 60.964 | 0.013456 | 129.79 | 1131.3 |  | 12969 | 161.7 | 4.943 | 60.964 | 0.013456 | 129.79 | 1131.3 | 1001.51
12970 | 4.9442 | 161.71 | 60.964 | 0.013459 | 129.8 | 1131.3 |  | 12970 | 161.71 | 4.9442 | 60.964 | 0.013459 | 129.8 | 1131.3 | 1001.5
12971 | 4.9454 | 161.72 | 60.964 | 0.013462 | 129.81 | 1131.3 |  | 12971 | 161.72 | 4.9454 | 60.964 | 0.013462 | 129.81 | 1131.3 | 1001.49
12972 | 4.9465 | 161.73 | 60.963 | 0.013465 | 129.82 | 1131.3 |  | 12972 | 161.73 | 4.9465 | 60.963 | 0.013465 | 129.82 | 1131.3 | 1001.48
12973 | 4.9477 | 161.74 | 60.963 | 0.013468 | 129.83 | 1131.3 |  | 12973 | 161.74 | 4.9477 | 60.963 | 0.013468 | 129.83 | 1131.3 | 1001.47
12974 | 4.9489 | 161.75 | 60.963 | 0.013471 | 129.84 | 1131.3 |  | 12974 | 161.75 | 4.9489 | 60.963 | 0.013471 | 129.84 | 1131.3 | 1001.46
12975 | 4.9501 | 161.76 | 60.963 | 0.013474 | 129.85 | 1131.3 |  | 12975 | 161.76 | 4.9501 | 60.963 | 0.013474 | 129.85 | 1131.3 | 1001.45
12976 | 4.9512 | 161.77 | 60.963 | 0.013477 | 129.86 | 1131.3 |  | 12976 | 161.77 | 4.9512 | 60.963 | 0.013477 | 129.86 | 1131.3 | 1001.44
12977 | 4.9524 | 161.78 | 60.962 | 0.01348 | 129.87 | 1131.3 |  | 12977 | 161.78 | 4.9524 | 60.962 | 0.01348 | 129.87 | 1131.3 | 1001.43
12978 | 4.9536 | 161.79 | 60.962 | 0.013483 | 129.88 | 1131.3 |  | 12978 | 161.79 | 4.9536 | 60.962 | 0.013483 | 129.88 | 1131.3 | 1001.42
12979 | 4.9548 | 161.8 | 60.962 | 0.013486 | 129.89 | 1131.3 |  | 12979 | 161.8 | 4.9548 | 60.962 | 0.013486 | 129.89 | 1131.3 | 1001.41
12980 | 4.9559 | 161.81 | 60.962 | 0.013489 | 129.9 | 1131.3 |  | 12980 | 161.81 | 4.9559 | 60.962 | 0.013489 | 129.9 | 1131.3 | 1001.4
12981 | 4.9571 | 161.82 | 60.962 | 0.013492 | 129.91 | 1131.3 |  | 12981 | 161.82 | 4.9571 | 60.962 | 0.013492 | 129.91 | 1131.3 | 1001.39
12982 | 4.9583 | 161.83 | 60.961 | 0.013495 | 129.92 | 1131.3 |  | 12982 | 161.83 | 4.9583 | 60.961 | 0.013495 | 129.92 | 1131.3 | 1001.38
12983 | 4.9595 | 161.84 | 60.961 | 0.013498 | 129.93 | 1131.3 |  | 12983 | 161.84 | 4.9595 | 60.961 | 0.013498 | 129.93 | 1131.3 | 1001.37
12984 | 4.9606 | 161.85 | 60.961 | 0.013501 | 129.94 | 1131.3 |  | 12984 | 161.85 | 4.9606 | 60.961 | 0.013501 | 129.94 | 1131.3 | 1001.36
12985 | 4.9618 | 161.86 | 60.961 | 0.013504 | 129.95 | 1131.3 |  | 12985 | 161.86 | 4.9618 | 60.961 | 0.013504 | 129.95 | 1131.3 | 1001.35
12986 | 4.963 | 161.87 | 60.961 | 0.013507 | 129.96 | 1131.4 |  | 12986 | 161.87 | 4.963 | 60.961 | 0.013507 | 129.96 | 1131.4 | 1001.44
12987 | 4.9642 | 161.88 | 60.96 | 0.01351 | 129.97 | 1131.4 |  | 12987 | 161.88 | 4.9642 | 60.96 | 0.01351 | 129.97 | 1131.4 | 1001.43
12988 | 4.9653 | 161.89 | 60.96 | 0.013513 | 129.98 | 1131.4 |  | 12988 | 161.89 | 4.9653 | 60.96 | 0.013513 | 129.98 | 1131.4 | 1001.42
12989 | 4.9665 | 161.9 | 60.96 | 0.013516 | 129.99 | 1131.4 |  | 12989 | 161.9 | 4.9665 | 60.96 | 0.013516 | 129.99 | 1131.4 | 1001.41
12990 | 4.9677 | 161.91 | 60.96 | 0.013519 | 130 | 1131.4 |  | 12990 | 161.91 | 4.9677 | 60.96 | 0.013519 | 130 | 1131.4 | 1001.4
12991 | 4.9689 | 161.92 | 60.96 | 0.013522 | 130.01 | 1131.4 |  | 12991 | 161.92 | 4.9689 | 60.96 | 0.013522 | 130.01 | 1131.4 | 1001.39
12992 | 4.97 | 161.93 | 60.959 | 0.013525 | 130.02 | 1131.4 |  | 12992 | 161.93 | 4.97 | 60.959 | 0.013525 | 130.02 | 1131.4 | 1001.38
12993 | 4.9712 | 161.94 | 60.959 | 0.013528 | 130.03 | 1131.4 |  | 12993 | 161.94 | 4.9712 | 60.959 | 0.013528 | 130.03 | 1131.4 | 1001.37
12994 | 4.9724 | 161.95 | 60.959 | 0.013531 | 130.04 | 1131.4 |  | 12994 | 161.95 | 4.9724 | 60.959 | 0.013531 | 130.04 | 1131.4 | 1001.36
12995 | 4.9736 | 161.96 | 60.959 | 0.013534 | 130.05 | 1131.4 |  | 12995 | 161.96 | 4.9736 | 60.959 | 0.013534 | 130.05 | 1131.4 | 1001.35
12996 | 4.9747 | 161.97 | 60.959 | 0.013537 | 130.06 | 1131.4 |  | 12996 | 161.97 | 4.9747 | 60.959 | 0.013537 | 130.06 | 1131.4 | 1001.34
12997 | 4.9759 | 161.98 | 60.958 | 0.01354 | 130.07 | 1131.4 |  | 12997 | 161.98 | 4.9759 | 60.958 | 0.01354 | 130.07 | 1131.4 | 1001.33
12998 | 4.9771 | 161.99 | 60.958 | 0.013543 | 130.08 | 1131.4 |  | 12998 | 161.99 | 4.9771 | 60.958 | 0.013543 | 130.08 | 1131.4 | 1001.32
12999 | 4.9783 | 162 | 60.958 | 0.013546 | 130.09 | 1131.4 |  | 12999 | 162 | 4.9783 | 60.958 | 0.013546 | 130.09 | 1131.4 | 1001.31
13000 | 4.9795 | 162.01 | 60.958 | 0.013549 | 130.1 | 1131.4 |  | 13000 | 162.01 | 4.9795 | 60.958 | 0.013549 | 130.1 | 1131.4 | 1001.3
13001 | 4.9806 | 162.02 | 60.958 | 0.013552 | 130.11 | 1131.4 |  | 13001 | 162.02 | 4.9806 | 60.958 | 0.013552 | 130.11 | 1131.4 | 1001.29
13002 | 4.9818 | 162.03 | 60.957 | 0.013555 | 130.12 | 1131.4 |  | 13002 | 162.03 | 4.9818 | 60.957 | 0.013555 | 130.12 | 1131.4 | 1001.28
13003 | 4.983 | 162.04 | 60.957 | 0.013558 | 130.13 | 1131.4 |  | 13003 | 162.04 | 4.983 | 60.957 | 0.013558 | 130.13 | 1131.4 | 1001.27
13004 | 4.9842 | 162.05 | 60.957 | 0.013561 | 130.14 | 1131.4 |  | 13004 | 162.05 | 4.9842 | 60.957 | 0.013561 | 130.14 | 1131.4 | 1001.26
13005 | 4.9854 | 162.06 | 60.957 | 0.013564 | 130.15 | 1131.4 |  | 13005 | 162.06 | 4.9854 | 60.957 | 0.013564 | 130.15 | 1131.4 | 1001.25
13006 | 4.9865 | 162.07 | 60.957 | 0.013567 | 130.16 | 1131.4 |  | 13006 | 162.07 | 4.9865 | 60.957 | 0.013567 | 130.16 | 1131.4 | 1001.24
13007 | 4.9877 | 162.08 | 60.956 | 0.01357 | 130.17 | 1131.4 |  | 13007 | 162.08 | 4.9877 | 60.956 | 0.01357 | 130.17 | 1131.4 | 1001.23
13008 | 4.9889 | 162.09 | 60.956 | 0.013573 | 130.18 | 1131.4 |  | 13008 | 162.09 | 4.9889 | 60.956 | 0.013573 | 130.18 | 1131.4 | 1001.22
13009 | 4.9901 | 162.1 | 60.956 | 0.013576 | 130.19 | 1131.4 |  | 13009 | 162.1 | 4.9901 | 60.956 | 0.013576 | 130.19 | 1131.4 | 1001.21
13010 | 4.9913 | 162.11 | 60.956 | 0.013579 | 130.2 | 1131.4 |  | 13010 | 162.11 | 4.9913 | 60.956 | 0.013579 | 130.2 | 1131.4 | 1001.2
13011 | 4.9924 | 162.12 | 60.956 | 0.013582 | 130.21 | 1131.5 |  | 13011 | 162.12 | 4.9924 | 60.956 | 0.013582 | 130.21 | 1131.5 | 1001.29
13012 | 4.9936 | 162.13 | 60.955 | 0.013585 | 130.22 | 1131.5 |  | 13012 | 162.13 | 4.9936 | 60.955 | 0.013585 | 130.22 | 1131.5 | 1001.28
13013 | 4.9948 | 162.14 | 60.955 | 0.013588 | 130.23 | 1131.5 |  | 13013 | 162.14 | 4.9948 | 60.955 | 0.013588 | 130.23 | 1131.5 | 1001.27
13014 | 4.996 | 162.15 | 60.955 | 0.013591 | 130.24 | 1131.5 |  | 13014 | 162.15 | 4.996 | 60.955 | 0.013591 | 130.24 | 1131.5 | 1001.26
13015 | 4.9972 | 162.16 | 60.955 | 0.013594 | 130.25 | 1131.5 |  | 13015 | 162.16 | 4.9972 | 60.955 | 0.013594 | 130.25 | 1131.5 | 1001.25
13016 | 4.9984 | 162.17 | 60.955 | 0.013597 | 130.26 | 1131.5 |  | 13016 | 162.17 | 4.9984 | 60.955 | 0.013597 | 130.26 | 1131.5 | 1001.24
13017 | 4.9995 | 162.18 | 60.954 | 0.0136 | 130.27 | 1131.5 |  | 13017 | 162.18 | 4.9995 | 60.954 | 0.0136 | 130.27 | 1131.5 | 1001.23
13018 | 5.0007 | 162.19 | 60.954 | 0.013603 | 130.28 | 1131.5 |  | 13018 | 162.19 | 5.0007 | 60.954 | 0.013603 | 130.28 | 1131.5 | 1001.22
13019 | 5.0019 | 162.2 | 60.954 | 0.013606 | 130.29 | 1131.5 |  | 13019 | 162.2 | 5.0019 | 60.954 | 0.013606 | 130.29 | 1131.5 | 1001.21
13020 | 5.0031 | 162.21 | 60.954 | 0.013609 | 130.3 | 1131.5 |  | 13020 | 162.21 | 5.0031 | 60.954 | 0.013609 | 130.3 | 1131.5 | 1001.2
13021 | 5.0043 | 162.22 | 60.954 | 0.013612 | 130.31 | 1131.5 |  | 13021 | 162.22 | 5.0043 | 60.954 | 0.013612 | 130.31 | 1131.5 | 1001.19
13022 | 5.0055 | 162.23 | 60.953 | 0.013615 | 130.32 | 1131.5 |  | 13022 | 162.23 | 5.0055 | 60.953 | 0.013615 | 130.32 | 1131.5 | 1001.18
13023 | 5.0066 | 162.24 | 60.953 | 0.013618 | 130.33 | 1131.5 |  | 13023 | 162.24 | 5.0066 | 60.953 | 0.013618 | 130.33 | 1131.5 | 1001.17
13024 | 5.0078 | 162.25 | 60.953 | 0.013621 | 130.34 | 1131.5 |  | 13024 | 162.25 | 5.0078 | 60.953 | 0.013621 | 130.34 | 1131.5 | 1001.16
13025 | 5.009 | 162.26 | 60.953 | 0.013624 | 130.35 | 1131.5 |  | 13025 | 162.26 | 5.009 | 60.953 | 0.013624 | 130.35 | 1131.5 | 1001.15
13026 | 5.0102 | 162.27 | 60.953 | 0.013628 | 130.36 | 1131.5 |  | 13026 | 162.27 | 5.0102 | 60.953 | 0.013628 | 130.36 | 1131.5 | 1001.14
13027 | 5.0114 | 162.28 | 60.952 | 0.013631 | 130.37 | 1131.5 |  | 13027 | 162.28 | 5.0114 | 60.952 | 0.013631 | 130.37 | 1131.5 | 1001.13
13028 | 5.0126 | 162.29 | 60.952 | 0.013634 | 130.38 | 1131.5 |  | 13028 | 162.29 | 5.0126 | 60.952 | 0.013634 | 130.38 | 1131.5 | 1001.12
13029 | 5.0137 | 162.3 | 60.952 | 0.013637 | 130.39 | 1131.5 |  | 13029 | 162.3 | 5.0137 | 60.952 | 0.013637 | 130.39 | 1131.5 | 1001.11
13030 | 5.0149 | 162.31 | 60.952 | 0.01364 | 130.4 | 1131.5 |  | 13030 | 162.31 | 5.0149 | 60.952 | 0.01364 | 130.4 | 1131.5 | 1001.1
13031 | 5.0161 | 162.32 | 60.951 | 0.013643 | 130.41 | 1131.5 |  | 13031 | 162.32 | 5.0161 | 60.951 | 0.013643 | 130.41 | 1131.5 | 1001.09
13032 | 5.0173 | 162.33 | 60.951 | 0.013646 | 130.42 | 1131.5 |  | 13032 | 162.33 | 5.0173 | 60.951 | 0.013646 | 130.42 | 1131.5 | 1001.08
13033 | 5.0185 | 162.34 | 60.951 | 0.013649 | 130.43 | 1131.5 |  | 13033 | 162.34 | 5.0185 | 60.951 | 0.013649 | 130.43 | 1131.5 | 1001.07
13034 | 5.0197 | 162.35 | 60.951 | 0.013652 | 130.44 | 1131.5 |  | 13034 | 162.35 | 5.0197 | 60.951 | 0.013652 | 130.44 | 1131.5 | 1001.06
13035 | 5.0209 | 162.36 | 60.951 | 0.013655 | 130.45 | 1131.6 |  | 13035 | 162.36 | 5.0209 | 60.951 | 0.013655 | 130.45 | 1131.6 | 1001.15
13036 | 5.022 | 162.37 | 60.95 | 0.013658 | 130.46 | 1131.6 |  | 13036 | 162.37 | 5.022 | 60.95 | 0.013658 | 130.46 | 1131.6 | 1001.14
13037 | 5.0232 | 162.38 | 60.95 | 0.013661 | 130.47 | 1131.6 |  | 13037 | 162.38 | 5.0232 | 60.95 | 0.013661 | 130.47 | 1131.6 | 1001.13
13038 | 5.0244 | 162.39 | 60.95 | 0.013664 | 130.48 | 1131.6 |  | 13038 | 162.39 | 5.0244 | 60.95 | 0.013664 | 130.48 | 1131.6 | 1001.12
13039 | 5.0256 | 162.4 | 60.95 | 0.013667 | 130.49 | 1131.6 |  | 13039 | 162.4 | 5.0256 | 60.95 | 0.013667 | 130.49 | 1131.6 | 1001.11
13040 | 5.0268 | 162.41 | 60.95 | 0.01367 | 130.5 | 1131.6 |  | 13040 | 162.41 | 5.0268 | 60.95 | 0.01367 | 130.5 | 1131.6 | 1001.1
13041 | 5.028 | 162.42 | 60.949 | 0.013673 | 130.51 | 1131.6 |  | 13041 | 162.42 | 5.028 | 60.949 | 0.013673 | 130.51 | 1131.6 | 1001.09
13042 | 5.0292 | 162.43 | 60.949 | 0.013676 | 130.52 | 1131.6 |  | 13042 | 162.43 | 5.0292 | 60.949 | 0.013676 | 130.52 | 1131.6 | 1001.08
13043 | 5.0304 | 162.44 | 60.949 | 0.013679 | 130.53 | 1131.6 |  | 13043 | 162.44 | 5.0304 | 60.949 | 0.013679 | 130.53 | 1131.6 | 1001.07
13044 | 5.0316 | 162.45 | 60.949 | 0.013682 | 130.54 | 1131.6 |  | 13044 | 162.45 | 5.0316 | 60.949 | 0.013682 | 130.54 | 1131.6 | 1001.06
13045 | 5.0327 | 162.46 | 60.949 | 0.013685 | 130.55 | 1131.6 |  | 13045 | 162.46 | 5.0327 | 60.949 | 0.013685 | 130.55 | 1131.6 | 1001.05
13046 | 5.0339 | 162.47 | 60.948 | 0.013688 | 130.56 | 1131.6 |  | 13046 | 162.47 | 5.0339 | 60.948 | 0.013688 | 130.56 | 1131.6 | 1001.04
13047 | 5.0351 | 162.48 | 60.948 | 0.013691 | 130.57 | 1131.6 |  | 13047 | 162.48 | 5.0351 | 60.948 | 0.013691 | 130.57 | 1131.6 | 1001.03
13048 | 5.0363 | 162.49 | 60.948 | 0.013694 | 130.58 | 1131.6 |  | 13048 | 162.49 | 5.0363 | 60.948 | 0.013694 | 130.58 | 1131.6 | 1001.02
13049 | 5.0375 | 162.5 | 60.948 | 0.013697 | 130.59 | 1131.6 |  | 13049 | 162.5 | 5.0375 | 60.948 | 0.013697 | 130.59 | 1131.6 | 1001.01
13050 | 5.0387 | 162.51 | 60.948 | 0.0137 | 130.6 | 1131.6 |  | 13050 | 162.51 | 5.0387 | 60.948 | 0.0137 | 130.6 | 1131.6 | 1001
13051 | 5.0399 | 162.52 | 60.947 | 0.013703 | 130.61 | 1131.6 |  | 13051 | 162.52 | 5.0399 | 60.947 | 0.013703 | 130.61 | 1131.6 | 1000.99
13052 | 5.0411 | 162.53 | 60.947 | 0.013706 | 130.62 | 1131.6 |  | 13052 | 162.53 | 5.0411 | 60.947 | 0.013706 | 130.62 | 1131.6 | 1000.98
13053 | 5.0423 | 162.54 | 60.947 | 0.013709 | 130.63 | 1131.6 |  | 13053 | 162.54 | 5.0423 | 60.947 | 0.013709 | 130.63 | 1131.6 | 1000.97
13054 | 5.0435 | 162.55 | 60.947 | 0.013712 | 130.64 | 1131.6 |  | 13054 | 162.55 | 5.0435 | 60.947 | 0.013712 | 130.64 | 1131.6 | 1000.96
13055 | 5.0447 | 162.56 | 60.947 | 0.013715 | 130.65 | 1131.6 |  | 13055 | 162.56 | 5.0447 | 60.947 | 0.013715 | 130.65 | 1131.6 | 1000.95
13056 | 5.0458 | 162.57 | 60.946 | 0.013718 | 130.66 | 1131.6 |  | 13056 | 162.57 | 5.0458 | 60.946 | 0.013718 | 130.66 | 1131.6 | 1000.94
13057 | 5.047 | 162.58 | 60.946 | 0.013721 | 130.67 | 1131.6 |  | 13057 | 162.58 | 5.047 | 60.946 | 0.013721 | 130.67 | 1131.6 | 1000.93
13058 | 5.0482 | 162.59 | 60.946 | 0.013724 | 130.68 | 1131.6 |  | 13058 | 162.59 | 5.0482 | 60.946 | 0.013724 | 130.68 | 1131.6 | 1000.92
13059 | 5.0494 | 162.6 | 60.946 | 0.013727 | 130.69 | 1131.6 |  | 13059 | 162.6 | 5.0494 | 60.946 | 0.013727 | 130.69 | 1131.6 | 1000.91
13060 | 5.0506 | 162.61 | 60.946 | 0.013731 | 130.7 | 1131.7 |  | 13060 | 162.61 | 5.0506 | 60.946 | 0.013731 | 130.7 | 1131.7 | 1001
13061 | 5.0518 | 162.62 | 60.945 | 0.013734 | 130.71 | 1131.7 |  | 13061 | 162.62 | 5.0518 | 60.945 | 0.013734 | 130.71 | 1131.7 | 1000.99
13062 | 5.053 | 162.63 | 60.945 | 0.013737 | 130.72 | 1131.7 |  | 13062 | 162.63 | 5.053 | 60.945 | 0.013737 | 130.72 | 1131.7 | 1000.98
13063 | 5.0542 | 162.64 | 60.945 | 0.01374 | 130.73 | 1131.7 |  | 13063 | 162.64 | 5.0542 | 60.945 | 0.01374 | 130.73 | 1131.7 | 1000.97
13064 | 5.0554 | 162.65 | 60.945 | 0.013743 | 130.74 | 1131.7 |  | 13064 | 162.65 | 5.0554 | 60.945 | 0.013743 | 130.74 | 1131.7 | 1000.96
13065 | 5.0566 | 162.66 | 60.945 | 0.013746 | 130.75 | 1131.7 |  | 13065 | 162.66 | 5.0566 | 60.945 | 0.013746 | 130.75 | 1131.7 | 1000.95
13066 | 5.0578 | 162.67 | 60.944 | 0.013749 | 130.76 | 1131.7 |  | 13066 | 162.67 | 5.0578 | 60.944 | 0.013749 | 130.76 | 1131.7 | 1000.94
13067 | 5.059 | 162.68 | 60.944 | 0.013752 | 130.77 | 1131.7 |  | 13067 | 162.68 | 5.059 | 60.944 | 0.013752 | 130.77 | 1131.7 | 1000.93
13068 | 5.0602 | 162.69 | 60.944 | 0.013755 | 130.78 | 1131.7 |  | 13068 | 162.69 | 5.0602 | 60.944 | 0.013755 | 130.78 | 1131.7 | 1000.92
13069 | 5.0614 | 162.7 | 60.944 | 0.013758 | 130.79 | 1131.7 |  | 13069 | 162.7 | 5.0614 | 60.944 | 0.013758 | 130.79 | 1131.7 | 1000.91
13070 | 5.0626 | 162.71 | 60.944 | 0.013761 | 130.8 | 1131.7 |  | 13070 | 162.71 | 5.0626 | 60.944 | 0.013761 | 130.8 | 1131.7 | 1000.9
13071 | 5.0638 | 162.72 | 60.943 | 0.013764 | 130.81 | 1131.7 |  | 13071 | 162.72 | 5.0638 | 60.943 | 0.013764 | 130.81 | 1131.7 | 1000.89
13072 | 5.0649 | 162.73 | 60.943 | 0.013767 | 130.82 | 1131.7 |  | 13072 | 162.73 | 5.0649 | 60.943 | 0.013767 | 130.82 | 1131.7 | 1000.88
13073 | 5.0661 | 162.74 | 60.943 | 0.01377 | 130.83 | 1131.7 |  | 13073 | 162.74 | 5.0661 | 60.943 | 0.01377 | 130.83 | 1131.7 | 1000.87
13074 | 5.0673 | 162.75 | 60.943 | 0.013773 | 130.84 | 1131.7 |  | 13074 | 162.75 | 5.0673 | 60.943 | 0.013773 | 130.84 | 1131.7 | 1000.86
13075 | 5.0685 | 162.76 | 60.943 | 0.013776 | 130.85 | 1131.7 |  | 13075 | 162.76 | 5.0685 | 60.943 | 0.013776 | 130.85 | 1131.7 | 1000.85
13076 | 5.0697 | 162.77 | 60.942 | 0.013779 | 130.86 | 1131.7 |  | 13076 | 162.77 | 5.0697 | 60.942 | 0.013779 | 130.86 | 1131.7 | 1000.84
13077 | 5.0709 | 162.78 | 60.942 | 0.013782 | 130.87 | 1131.7 |  | 13077 | 162.78 | 5.0709 | 60.942 | 0.013782 | 130.87 | 1131.7 | 1000.83
13078 | 5.0721 | 162.79 | 60.942 | 0.013785 | 130.88 | 1131.7 |  | 13078 | 162.79 | 5.0721 | 60.942 | 0.013785 | 130.88 | 1131.7 | 1000.82
13079 | 5.0733 | 162.8 | 60.942 | 0.013788 | 130.89 | 1131.7 |  | 13079 | 162.8 | 5.0733 | 60.942 | 0.013788 | 130.89 | 1131.7 | 1000.81
13080 | 5.0745 | 162.81 | 60.942 | 0.013791 | 130.9 | 1131.7 |  | 13080 | 162.81 | 5.0745 | 60.942 | 0.013791 | 130.9 | 1131.7 | 1000.8
13081 | 5.0757 | 162.82 | 60.941 | 0.013794 | 130.91 | 1131.7 |  | 13081 | 162.82 | 5.0757 | 60.941 | 0.013794 | 130.91 | 1131.7 | 1000.79
13082 | 5.0769 | 162.83 | 60.941 | 0.013798 | 130.92 | 1131.7 |  | 13082 | 162.83 | 5.0769 | 60.941 | 0.013798 | 130.92 | 1131.7 | 1000.78
13083 | 5.0781 | 162.84 | 60.941 | 0.013801 | 130.93 | 1131.7 |  | 13083 | 162.84 | 5.0781 | 60.941 | 0.013801 | 130.93 | 1131.7 | 1000.77
13084 | 5.0793 | 162.85 | 60.941 | 0.013804 | 130.94 | 1131.8 |  | 13084 | 162.85 | 5.0793 | 60.941 | 0.013804 | 130.94 | 1131.8 | 1000.86
13085 | 5.0805 | 162.86 | 60.941 | 0.013807 | 130.95 | 1131.8 |  | 13085 | 162.86 | 5.0805 | 60.941 | 0.013807 | 130.95 | 1131.8 | 1000.85
13086 | 5.0817 | 162.87 | 60.94 | 0.01381 | 130.96 | 1131.8 |  | 13086 | 162.87 | 5.0817 | 60.94 | 0.01381 | 130.96 | 1131.8 | 1000.84
13087 | 5.0829 | 162.88 | 60.94 | 0.013813 | 130.97 | 1131.8 |  | 13087 | 162.88 | 5.0829 | 60.94 | 0.013813 | 130.97 | 1131.8 | 1000.83
13088 | 5.0841 | 162.89 | 60.94 | 0.013816 | 130.98 | 1131.8 |  | 13088 | 162.89 | 5.0841 | 60.94 | 0.013816 | 130.98 | 1131.8 | 1000.82
13089 | 5.0853 | 162.9 | 60.94 | 0.013819 | 130.99 | 1131.8 |  | 13089 | 162.9 | 5.0853 | 60.94 | 0.013819 | 130.99 | 1131.8 | 1000.81
13090 | 5.0865 | 162.91 | 60.94 | 0.013822 | 131 | 1131.8 |  | 13090 | 162.91 | 5.0865 | 60.94 | 0.013822 | 131 | 1131.8 | 1000.8
13091 | 5.0877 | 162.92 | 60.939 | 0.013825 | 131.01 | 1131.8 |  | 13091 | 162.92 | 5.0877 | 60.939 | 0.013825 | 131.01 | 1131.8 | 1000.79
13092 | 5.0889 | 162.93 | 60.939 | 0.013828 | 131.02 | 1131.8 |  | 13092 | 162.93 | 5.0889 | 60.939 | 0.013828 | 131.02 | 1131.8 | 1000.78
13093 | 5.0901 | 162.94 | 60.939 | 0.013831 | 131.03 | 1131.8 |  | 13093 | 162.94 | 5.0901 | 60.939 | 0.013831 | 131.03 | 1131.8 | 1000.77
13094 | 5.0913 | 162.95 | 60.939 | 0.013834 | 131.04 | 1131.8 |  | 13094 | 162.95 | 5.0913 | 60.939 | 0.013834 | 131.04 | 1131.8 | 1000.76
13095 | 5.0925 | 162.96 | 60.939 | 0.013837 | 131.05 | 1131.8 |  | 13095 | 162.96 | 5.0925 | 60.939 | 0.013837 | 131.05 | 1131.8 | 1000.75
13096 | 5.0937 | 162.97 | 60.938 | 0.01384 | 131.06 | 1131.8 |  | 13096 | 162.97 | 5.0937 | 60.938 | 0.01384 | 131.06 | 1131.8 | 1000.74
13097 | 5.0949 | 162.98 | 60.938 | 0.013843 | 131.07 | 1131.8 |  | 13097 | 162.98 | 5.0949 | 60.938 | 0.013843 | 131.07 | 1131.8 | 1000.73
13098 | 5.0961 | 162.99 | 60.938 | 0.013846 | 131.08 | 1131.8 |  | 13098 | 162.99 | 5.0961 | 60.938 | 0.013846 | 131.08 | 1131.8 | 1000.72
13099 | 5.0973 | 163 | 60.938 | 0.013849 | 131.09 | 1131.8 |  | 13099 | 163 | 5.0973 | 60.938 | 0.013849 | 131.09 | 1131.8 | 1000.71
13100 | 5.0985 | 163.01 | 60.938 | 0.013853 | 131.1 | 1131.8 |  | 13100 | 163.01 | 5.0985 | 60.938 | 0.013853 | 131.1 | 1131.8 | 1000.7
13101 | 5.0997 | 163.02 | 60.937 | 0.013856 | 131.11 | 1131.8 |  | 13101 | 163.02 | 5.0997 | 60.937 | 0.013856 | 131.11 | 1131.8 | 1000.69
13102 | 5.1009 | 163.03 | 60.937 | 0.013859 | 131.12 | 1131.8 |  | 13102 | 163.03 | 5.1009 | 60.937 | 0.013859 | 131.12 | 1131.8 | 1000.68
13103 | 5.1021 | 163.04 | 60.937 | 0.013862 | 131.13 | 1131.8 |  | 13103 | 163.04 | 5.1021 | 60.937 | 0.013862 | 131.13 | 1131.8 | 1000.67
13104 | 5.1033 | 163.05 | 60.937 | 0.013865 | 131.14 | 1131.8 |  | 13104 | 163.05 | 5.1033 | 60.937 | 0.013865 | 131.14 | 1131.8 | 1000.66
13105 | 5.1045 | 163.06 | 60.936 | 0.013868 | 131.15 | 1131.8 |  | 13105 | 163.06 | 5.1045 | 60.936 | 0.013868 | 131.15 | 1131.8 | 1000.65
13106 | 5.1057 | 163.07 | 60.936 | 0.013871 | 131.16 | 1131.8 |  | 13106 | 163.07 | 5.1057 | 60.936 | 0.013871 | 131.16 | 1131.8 | 1000.64
13107 | 5.1069 | 163.08 | 60.936 | 0.013874 | 131.17 | 1131.8 |  | 13107 | 163.08 | 5.1069 | 60.936 | 0.013874 | 131.17 | 1131.8 | 1000.63
13108 | 5.1082 | 163.09 | 60.936 | 0.013877 | 131.18 | 1131.8 |  | 13108 | 163.09 | 5.1082 | 60.936 | 0.013877 | 131.18 | 1131.8 | 1000.62
13109 | 5.1094 | 163.1 | 60.936 | 0.01388 | 131.19 | 1131.9 |  | 13109 | 163.1 | 5.1094 | 60.936 | 0.01388 | 131.19 | 1131.9 | 1000.71
13110 | 5.1106 | 163.11 | 60.935 | 0.013883 | 131.2 | 1131.9 |  | 13110 | 163.11 | 5.1106 | 60.935 | 0.013883 | 131.2 | 1131.9 | 1000.7
13111 | 5.1118 | 163.12 | 60.935 | 0.013886 | 131.21 | 1131.9 |  | 13111 | 163.12 | 5.1118 | 60.935 | 0.013886 | 131.21 | 1131.9 | 1000.69
13112 | 5.113 | 163.13 | 60.935 | 0.013889 | 131.22 | 1131.9 |  | 13112 | 163.13 | 5.113 | 60.935 | 0.013889 | 131.22 | 1131.9 | 1000.68
13113 | 5.1142 | 163.14 | 60.935 | 0.013892 | 131.23 | 1131.9 |  | 13113 | 163.14 | 5.1142 | 60.935 | 0.013892 | 131.23 | 1131.9 | 1000.67
13114 | 5.1154 | 163.15 | 60.935 | 0.013895 | 131.24 | 1131.9 |  | 13114 | 163.15 | 5.1154 | 60.935 | 0.013895 | 131.24 | 1131.9 | 1000.66
13115 | 5.1166 | 163.16 | 60.934 | 0.013899 | 131.25 | 1131.9 |  | 13115 | 163.16 | 5.1166 | 60.934 | 0.013899 | 131.25 | 1131.9 | 1000.65
13116 | 5.1178 | 163.17 | 60.934 | 0.013902 | 131.26 | 1131.9 |  | 13116 | 163.17 | 5.1178 | 60.934 | 0.013902 | 131.26 | 1131.9 | 1000.64
13117 | 5.119 | 163.18 | 60.934 | 0.013905 | 131.27 | 1131.9 |  | 13117 | 163.18 | 5.119 | 60.934 | 0.013905 | 131.27 | 1131.9 | 1000.63
13118 | 5.1202 | 163.19 | 60.934 | 0.013908 | 131.28 | 1131.9 |  | 13118 | 163.19 | 5.1202 | 60.934 | 0.013908 | 131.28 | 1131.9 | 1000.62
13119 | 5.1214 | 163.2 | 60.934 | 0.013911 | 131.29 | 1131.9 |  | 13119 | 163.2 | 5.1214 | 60.934 | 0.013911 | 131.29 | 1131.9 | 1000.61
13120 | 5.1226 | 163.21 | 60.933 | 0.013914 | 131.3 | 1131.9 |  | 13120 | 163.21 | 5.1226 | 60.933 | 0.013914 | 131.3 | 1131.9 | 1000.6
13121 | 5.1238 | 163.22 | 60.933 | 0.013917 | 131.31 | 1131.9 |  | 13121 | 163.22 | 5.1238 | 60.933 | 0.013917 | 131.31 | 1131.9 | 1000.59
13122 | 5.125 | 163.23 | 60.933 | 0.01392 | 131.32 | 1131.9 |  | 13122 | 163.23 | 5.125 | 60.933 | 0.01392 | 131.32 | 1131.9 | 1000.58
13123 | 5.1262 | 163.24 | 60.933 | 0.013923 | 131.33 | 1131.9 |  | 13123 | 163.24 | 5.1262 | 60.933 | 0.013923 | 131.33 | 1131.9 | 1000.57
13124 | 5.1275 | 163.25 | 60.933 | 0.013926 | 131.34 | 1131.9 |  | 13124 | 163.25 | 5.1275 | 60.933 | 0.013926 | 131.34 | 1131.9 | 1000.56
13125 | 5.1287 | 163.26 | 60.932 | 0.013929 | 131.35 | 1131.9 |  | 13125 | 163.26 | 5.1287 | 60.932 | 0.013929 | 131.35 | 1131.9 | 1000.55
13126 | 5.1299 | 163.27 | 60.932 | 0.013932 | 131.36 | 1131.9 |  | 13126 | 163.27 | 5.1299 | 60.932 | 0.013932 | 131.36 | 1131.9 | 1000.54
13127 | 5.1311 | 163.28 | 60.932 | 0.013935 | 131.37 | 1131.9 |  | 13127 | 163.28 | 5.1311 | 60.932 | 0.013935 | 131.37 | 1131.9 | 1000.53
13128 | 5.1323 | 163.29 | 60.932 | 0.013938 | 131.38 | 1131.9 |  | 13128 | 163.29 | 5.1323 | 60.932 | 0.013938 | 131.38 | 1131.9 | 1000.52
13129 | 5.1335 | 163.3 | 60.932 | 0.013942 | 131.39 | 1131.9 |  | 13129 | 163.3 | 5.1335 | 60.932 | 0.013942 | 131.39 | 1131.9 | 1000.51
13130 | 5.1347 | 163.31 | 60.931 | 0.013945 | 131.4 | 1131.9 |  | 13130 | 163.31 | 5.1347 | 60.931 | 0.013945 | 131.4 | 1131.9 | 1000.5
13131 | 5.1359 | 163.32 | 60.931 | 0.013948 | 131.41 | 1131.9 |  | 13131 | 163.32 | 5.1359 | 60.931 | 0.013948 | 131.41 | 1131.9 | 1000.49
13132 | 5.1371 | 163.33 | 60.931 | 0.013951 | 131.42 | 1131.9 |  | 13132 | 163.33 | 5.1371 | 60.931 | 0.013951 | 131.42 | 1131.9 | 1000.48
13133 | 5.1383 | 163.34 | 60.931 | 0.013954 | 131.43 | 1131.9 |  | 13133 | 163.34 | 5.1383 | 60.931 | 0.013954 | 131.43 | 1131.9 | 1000.47
13134 | 5.1395 | 163.35 | 60.931 | 0.013957 | 131.44 | 1132 |  | 13134 | 163.35 | 5.1395 | 60.931 | 0.013957 | 131.44 | 1132 | 1000.56
13135 | 5.1408 | 163.36 | 60.93 | 0.01396 | 131.45 | 1132 |  | 13135 | 163.36 | 5.1408 | 60.93 | 0.01396 | 131.45 | 1132 | 1000.55
13136 | 5.142 | 163.37 | 60.93 | 0.013963 | 131.46 | 1132 |  | 13136 | 163.37 | 5.142 | 60.93 | 0.013963 | 131.46 | 1132 | 1000.54
13137 | 5.1432 | 163.38 | 60.93 | 0.013966 | 131.47 | 1132 |  | 13137 | 163.38 | 5.1432 | 60.93 | 0.013966 | 131.47 | 1132 | 1000.53
13138 | 5.1444 | 163.39 | 60.93 | 0.013969 | 131.48 | 1132 |  | 13138 | 163.39 | 5.1444 | 60.93 | 0.013969 | 131.48 | 1132 | 1000.52
13139 | 5.1456 | 163.4 | 60.93 | 0.013972 | 131.49 | 1132 |  | 13139 | 163.4 | 5.1456 | 60.93 | 0.013972 | 131.49 | 1132 | 1000.51
13140 | 5.1468 | 163.41 | 60.929 | 0.013975 | 131.5 | 1132 |  | 13140 | 163.41 | 5.1468 | 60.929 | 0.013975 | 131.5 | 1132 | 1000.5
13141 | 5.148 | 163.42 | 60.929 | 0.013979 | 131.51 | 1132 |  | 13141 | 163.42 | 5.148 | 60.929 | 0.013979 | 131.51 | 1132 | 1000.49
13142 | 5.1492 | 163.43 | 60.929 | 0.013982 | 131.52 | 1132 |  | 13142 | 163.43 | 5.1492 | 60.929 | 0.013982 | 131.52 | 1132 | 1000.48
13143 | 5.1505 | 163.44 | 60.929 | 0.013985 | 131.53 | 1132 |  | 13143 | 163.44 | 5.1505 | 60.929 | 0.013985 | 131.53 | 1132 | 1000.47
13144 | 5.1517 | 163.45 | 60.929 | 0.013988 | 131.54 | 1132 |  | 13144 | 163.45 | 5.1517 | 60.929 | 0.013988 | 131.54 | 1132 | 1000.46
13145 | 5.1529 | 163.46 | 60.928 | 0.013991 | 131.55 | 1132 |  | 13145 | 163.46 | 5.1529 | 60.928 | 0.013991 | 131.55 | 1132 | 1000.45
13146 | 5.1541 | 163.47 | 60.928 | 0.013994 | 131.56 | 1132 |  | 13146 | 163.47 | 5.1541 | 60.928 | 0.013994 | 131.56 | 1132 | 1000.44
13147 | 5.1553 | 163.48 | 60.928 | 0.013997 | 131.57 | 1132 |  | 13147 | 163.48 | 5.1553 | 60.928 | 0.013997 | 131.57 | 1132 | 1000.43
13148 | 5.1565 | 163.49 | 60.928 | 0.014 | 131.58 | 1132 |  | 13148 | 163.49 | 5.1565 | 60.928 | 0.014 | 131.58 | 1132 | 1000.42
13149 | 5.1577 | 163.5 | 60.928 | 0.014003 | 131.59 | 1132 |  | 13149 | 163.5 | 5.1577 | 60.928 | 0.014003 | 131.59 | 1132 | 1000.41
13150 | 5.1589 | 163.51 | 60.927 | 0.014006 | 131.6 | 1132 |  | 13150 | 163.51 | 5.1589 | 60.927 | 0.014006 | 131.6 | 1132 | 1000.4
13151 | 5.1602 | 163.52 | 60.927 | 0.014009 | 131.61 | 1132 |  | 13151 | 163.52 | 5.1602 | 60.927 | 0.014009 | 131.61 | 1132 | 1000.39
13152 | 5.1614 | 163.53 | 60.927 | 0.014012 | 131.62 | 1132 |  | 13152 | 163.53 | 5.1614 | 60.927 | 0.014012 | 131.62 | 1132 | 1000.38
13153 | 5.1626 | 163.54 | 60.927 | 0.014016 | 131.63 | 1132 |  | 13153 | 163.54 | 5.1626 | 60.927 | 0.014016 | 131.63 | 1132 | 1000.37
13154 | 5.1638 | 163.55 | 60.927 | 0.014019 | 131.64 | 1132 |  | 13154 | 163.55 | 5.1638 | 60.927 | 0.014019 | 131.64 | 1132 | 1000.36
13155 | 5.165 | 163.56 | 60.926 | 0.014022 | 131.65 | 1132 |  | 13155 | 163.56 | 5.165 | 60.926 | 0.014022 | 131.65 | 1132 | 1000.35
13156 | 5.1662 | 163.57 | 60.926 | 0.014025 | 131.66 | 1132 |  | 13156 | 163.57 | 5.1662 | 60.926 | 0.014025 | 131.66 | 1132 | 1000.34
13157 | 5.1675 | 163.58 | 60.926 | 0.014028 | 131.67 | 1132 |  | 13157 | 163.58 | 5.1675 | 60.926 | 0.014028 | 131.67 | 1132 | 1000.33
13158 | 5.1687 | 163.59 | 60.926 | 0.014031 | 131.68 | 1132.1 |  | 13158 | 163.59 | 5.1687 | 60.926 | 0.014031 | 131.68 | 1132.1 | 1000.42
13159 | 5.1699 | 163.6 | 60.926 | 0.014034 | 131.69 | 1132.1 |  | 13159 | 163.6 | 5.1699 | 60.926 | 0.014034 | 131.69 | 1132.1 | 1000.41
13160 | 5.1711 | 163.61 | 60.925 | 0.014037 | 131.7 | 1132.1 |  | 13160 | 163.61 | 5.1711 | 60.925 | 0.014037 | 131.7 | 1132.1 | 1000.4
13161 | 5.1723 | 163.62 | 60.925 | 0.01404 | 131.71 | 1132.1 |  | 13161 | 163.62 | 5.1723 | 60.925 | 0.01404 | 131.71 | 1132.1 | 1000.39
13162 | 5.1735 | 163.63 | 60.925 | 0.014043 | 131.72 | 1132.1 |  | 13162 | 163.63 | 5.1735 | 60.925 | 0.014043 | 131.72 | 1132.1 | 1000.38
13163 | 5.1748 | 163.64 | 60.925 | 0.014047 | 131.73 | 1132.1 |  | 13163 | 163.64 | 5.1748 | 60.925 | 0.014047 | 131.73 | 1132.1 | 1000.37
13164 | 5.176 | 163.65 | 60.924 | 0.01405 | 131.74 | 1132.1 |  | 13164 | 163.65 | 5.176 | 60.924 | 0.01405 | 131.74 | 1132.1 | 1000.36
13165 | 5.1772 | 163.66 | 60.924 | 0.014053 | 131.75 | 1132.1 |  | 13165 | 163.66 | 5.1772 | 60.924 | 0.014053 | 131.75 | 1132.1 | 1000.35
13166 | 5.1784 | 163.67 | 60.924 | 0.014056 | 131.76 | 1132.1 |  | 13166 | 163.67 | 5.1784 | 60.924 | 0.014056 | 131.76 | 1132.1 | 1000.34
13167 | 5.1796 | 163.68 | 60.924 | 0.014059 | 131.77 | 1132.1 |  | 13167 | 163.68 | 5.1796 | 60.924 | 0.014059 | 131.77 | 1132.1 | 1000.33
13168 | 5.1809 | 163.69 | 60.924 | 0.014062 | 131.78 | 1132.1 |  | 13168 | 163.69 | 5.1809 | 60.924 | 0.014062 | 131.78 | 1132.1 | 1000.32
13169 | 5.1821 | 163.7 | 60.923 | 0.014065 | 131.79 | 1132.1 |  | 13169 | 163.7 | 5.1821 | 60.923 | 0.014065 | 131.79 | 1132.1 | 1000.31
13170 | 5.1833 | 163.71 | 60.923 | 0.014068 | 131.8 | 1132.1 |  | 13170 | 163.71 | 5.1833 | 60.923 | 0.014068 | 131.8 | 1132.1 | 1000.3
13171 | 5.1845 | 163.72 | 60.923 | 0.014071 | 131.81 | 1132.1 |  | 13171 | 163.72 | 5.1845 | 60.923 | 0.014071 | 131.81 | 1132.1 | 1000.29
13172 | 5.1857 | 163.73 | 60.923 | 0.014074 | 131.82 | 1132.1 |  | 13172 | 163.73 | 5.1857 | 60.923 | 0.014074 | 131.82 | 1132.1 | 1000.28
13173 | 5.1869 | 163.74 | 60.923 | 0.014078 | 131.83 | 1132.1 |  | 13173 | 163.74 | 5.1869 | 60.923 | 0.014078 | 131.83 | 1132.1 | 1000.27
13174 | 5.1882 | 163.75 | 60.922 | 0.014081 | 131.84 | 1132.1 |  | 13174 | 163.75 | 5.1882 | 60.922 | 0.014081 | 131.84 | 1132.1 | 1000.26
13175 | 5.1894 | 163.76 | 60.922 | 0.014084 | 131.85 | 1132.1 |  | 13175 | 163.76 | 5.1894 | 60.922 | 0.014084 | 131.85 | 1132.1 | 1000.25
13176 | 5.1906 | 163.77 | 60.922 | 0.014087 | 131.86 | 1132.1 |  | 13176 | 163.77 | 5.1906 | 60.922 | 0.014087 | 131.86 | 1132.1 | 1000.24
13177 | 5.1918 | 163.78 | 60.922 | 0.01409 | 131.87 | 1132.1 |  | 13177 | 163.78 | 5.1918 | 60.922 | 0.01409 | 131.87 | 1132.1 | 1000.23
13178 | 5.1931 | 163.79 | 60.922 | 0.014093 | 131.88 | 1132.1 |  | 13178 | 163.79 | 5.1931 | 60.922 | 0.014093 | 131.88 | 1132.1 | 1000.22
13179 | 5.1943 | 163.8 | 60.921 | 0.014096 | 131.89 | 1132.1 |  | 13179 | 163.8 | 5.1943 | 60.921 | 0.014096 | 131.89 | 1132.1 | 1000.21
13180 | 5.1955 | 163.81 | 60.921 | 0.014099 | 131.9 | 1132.1 |  | 13180 | 163.81 | 5.1955 | 60.921 | 0.014099 | 131.9 | 1132.1 | 1000.2
13181 | 5.1967 | 163.82 | 60.921 | 0.014102 | 131.91 | 1132.1 |  | 13181 | 163.82 | 5.1967 | 60.921 | 0.014102 | 131.91 | 1132.1 | 1000.19
13182 | 5.1979 | 163.83 | 60.921 | 0.014105 | 131.92 | 1132.1 |  | 13182 | 163.83 | 5.1979 | 60.921 | 0.014105 | 131.92 | 1132.1 | 1000.18
13183 | 5.1992 | 163.84 | 60.921 | 0.014109 | 131.93 | 1132.2 |  | 13183 | 163.84 | 5.1992 | 60.921 | 0.014109 | 131.93 | 1132.2 | 1000.27
13184 | 5.2004 | 163.85 | 60.92 | 0.014112 | 131.94 | 1132.2 |  | 13184 | 163.85 | 5.2004 | 60.92 | 0.014112 | 131.94 | 1132.2 | 1000.26
13185 | 5.2016 | 163.86 | 60.92 | 0.014115 | 131.95 | 1132.2 |  | 13185 | 163.86 | 5.2016 | 60.92 | 0.014115 | 131.95 | 1132.2 | 1000.25
13186 | 5.2028 | 163.87 | 60.92 | 0.014118 | 131.96 | 1132.2 |  | 13186 | 163.87 | 5.2028 | 60.92 | 0.014118 | 131.96 | 1132.2 | 1000.24
13187 | 5.2041 | 163.88 | 60.92 | 0.014121 | 131.97 | 1132.2 |  | 13187 | 163.88 | 5.2041 | 60.92 | 0.014121 | 131.97 | 1132.2 | 1000.23
13188 | 5.2053 | 163.89 | 60.92 | 0.014124 | 131.98 | 1132.2 |  | 13188 | 163.89 | 5.2053 | 60.92 | 0.014124 | 131.98 | 1132.2 | 1000.22
13189 | 5.2065 | 163.9 | 60.919 | 0.014127 | 131.99 | 1132.2 |  | 13189 | 163.9 | 5.2065 | 60.919 | 0.014127 | 131.99 | 1132.2 | 1000.21
13190 | 5.2077 | 163.91 | 60.919 | 0.01413 | 132 | 1132.2 |  | 13190 | 163.91 | 5.2077 | 60.919 | 0.01413 | 132 | 1132.2 | 1000.2
13191 | 5.2089 | 163.92 | 60.919 | 0.014133 | 132.01 | 1132.2 |  | 13191 | 163.92 | 5.2089 | 60.919 | 0.014133 | 132.01 | 1132.2 | 1000.19
13192 | 5.2102 | 163.93 | 60.919 | 0.014137 | 132.02 | 1132.2 |  | 13192 | 163.93 | 5.2102 | 60.919 | 0.014137 | 132.02 | 1132.2 | 1000.18
13193 | 5.2114 | 163.94 | 60.919 | 0.01414 | 132.03 | 1132.2 |  | 13193 | 163.94 | 5.2114 | 60.919 | 0.01414 | 132.03 | 1132.2 | 1000.17
13194 | 5.2126 | 163.95 | 60.918 | 0.014143 | 132.04 | 1132.2 |  | 13194 | 163.95 | 5.2126 | 60.918 | 0.014143 | 132.04 | 1132.2 | 1000.16
13195 | 5.2138 | 163.96 | 60.918 | 0.014146 | 132.05 | 1132.2 |  | 13195 | 163.96 | 5.2138 | 60.918 | 0.014146 | 132.05 | 1132.2 | 1000.15
13196 | 5.2151 | 163.97 | 60.918 | 0.014149 | 132.06 | 1132.2 |  | 13196 | 163.97 | 5.2151 | 60.918 | 0.014149 | 132.06 | 1132.2 | 1000.14
13197 | 5.2163 | 163.98 | 60.918 | 0.014152 | 132.07 | 1132.2 |  | 13197 | 163.98 | 5.2163 | 60.918 | 0.014152 | 132.07 | 1132.2 | 1000.13
13198 | 5.2175 | 163.99 | 60.918 | 0.014155 | 132.08 | 1132.2 |  | 13198 | 163.99 | 5.2175 | 60.918 | 0.014155 | 132.08 | 1132.2 | 1000.12
13199 | 5.2188 | 164 | 60.917 | 0.014158 | 132.09 | 1132.2 |  | 13199 | 164 | 5.2188 | 60.917 | 0.014158 | 132.09 | 1132.2 | 1000.11
13200 | 5.22 | 164.01 | 60.917 | 0.014161 | 132.1 | 1132.2 |  | 13200 | 164.01 | 5.22 | 60.917 | 0.014161 | 132.1 | 1132.2 | 1000.1
13201 | 5.2212 | 164.02 | 60.917 | 0.014165 | 132.11 | 1132.2 |  | 13201 | 164.02 | 5.2212 | 60.917 | 0.014165 | 132.11 | 1132.2 | 1000.09
13202 | 5.2224 | 164.03 | 60.917 | 0.014168 | 132.12 | 1132.2 |  | 13202 | 164.03 | 5.2224 | 60.917 | 0.014168 | 132.12 | 1132.2 | 1000.08
13203 | 5.2237 | 164.04 | 60.917 | 0.014171 | 132.13 | 1132.2 |  | 13203 | 164.04 | 5.2237 | 60.917 | 0.014171 | 132.13 | 1132.2 | 1000.07
13204 | 5.2249 | 164.05 | 60.916 | 0.014174 | 132.14 | 1132.2 |  | 13204 | 164.05 | 5.2249 | 60.916 | 0.014174 | 132.14 | 1132.2 | 1000.06
13205 | 5.2261 | 164.06 | 60.916 | 0.014177 | 132.15 | 1132.2 |  | 13205 | 164.06 | 5.2261 | 60.916 | 0.014177 | 132.15 | 1132.2 | 1000.05
13206 | 5.2273 | 164.07 | 60.916 | 0.01418 | 132.16 | 1132.2 |  | 13206 | 164.07 | 5.2273 | 60.916 | 0.01418 | 132.16 | 1132.2 | 1000.04
13207 | 5.2286 | 164.08 | 60.916 | 0.014183 | 132.17 | 1132.3 |  | 13207 | 164.08 | 5.2286 | 60.916 | 0.014183 | 132.17 | 1132.3 | 1000.13
13208 | 5.2298 | 164.09 | 60.916 | 0.014186 | 132.18 | 1132.3 |  | 13208 | 164.09 | 5.2298 | 60.916 | 0.014186 | 132.18 | 1132.3 | 1000.12
13209 | 5.231 | 164.1 | 60.915 | 0.01419 | 132.19 | 1132.3 |  | 13209 | 164.1 | 5.231 | 60.915 | 0.01419 | 132.19 | 1132.3 | 1000.11
13210 | 5.2323 | 164.11 | 60.915 | 0.014193 | 132.2 | 1132.3 |  | 13210 | 164.11 | 5.2323 | 60.915 | 0.014193 | 132.2 | 1132.3 | 1000.1
13211 | 5.2335 | 164.12 | 60.915 | 0.014196 | 132.21 | 1132.3 |  | 13211 | 164.12 | 5.2335 | 60.915 | 0.014196 | 132.21 | 1132.3 | 1000.09
13212 | 5.2347 | 164.13 | 60.915 | 0.014199 | 132.22 | 1132.3 |  | 13212 | 164.13 | 5.2347 | 60.915 | 0.014199 | 132.22 | 1132.3 | 1000.08
13213 | 5.2359 | 164.14 | 60.915 | 0.014202 | 132.23 | 1132.3 |  | 13213 | 164.14 | 5.2359 | 60.915 | 0.014202 | 132.23 | 1132.3 | 1000.07
13214 | 5.2372 | 164.15 | 60.914 | 0.014205 | 132.24 | 1132.3 |  | 13214 | 164.15 | 5.2372 | 60.914 | 0.014205 | 132.24 | 1132.3 | 1000.06
13215 | 5.2384 | 164.16 | 60.914 | 0.014208 | 132.25 | 1132.3 |  | 13215 | 164.16 | 5.2384 | 60.914 | 0.014208 | 132.25 | 1132.3 | 1000.05
13216 | 5.2396 | 164.17 | 60.914 | 0.014211 | 132.26 | 1132.3 |  | 13216 | 164.17 | 5.2396 | 60.914 | 0.014211 | 132.26 | 1132.3 | 1000.04
13217 | 5.2409 | 164.18 | 60.914 | 0.014215 | 132.27 | 1132.3 |  | 13217 | 164.18 | 5.2409 | 60.914 | 0.014215 | 132.27 | 1132.3 | 1000.03
13218 | 5.2421 | 164.19 | 60.913 | 0.014218 | 132.28 | 1132.3 |  | 13218 | 164.19 | 5.2421 | 60.913 | 0.014218 | 132.28 | 1132.3 | 1000.02
13219 | 5.2433 | 164.2 | 60.913 | 0.014221 | 132.29 | 1132.3 |  | 13219 | 164.2 | 5.2433 | 60.913 | 0.014221 | 132.29 | 1132.3 | 1000.01
13220 | 5.2446 | 164.21 | 60.913 | 0.014224 | 132.3 | 1132.3 |  | 13220 | 164.21 | 5.2446 | 60.913 | 0.014224 | 132.3 | 1132.3 | 1000
13221 | 5.2458 | 164.22 | 60.913 | 0.014227 | 132.31 | 1132.3 |  | 13221 | 164.22 | 5.2458 | 60.913 | 0.014227 | 132.31 | 1132.3 | 999.99
13222 | 5.247 | 164.23 | 60.913 | 0.01423 | 132.32 | 1132.3 |  | 13222 | 164.23 | 5.247 | 60.913 | 0.01423 | 132.32 | 1132.3 | 999.98
13223 | 5.2483 | 164.24 | 60.912 | 0.014233 | 132.33 | 1132.3 |  | 13223 | 164.24 | 5.2483 | 60.912 | 0.014233 | 132.33 | 1132.3 | 999.97
13224 | 5.2495 | 164.25 | 60.912 | 0.014236 | 132.34 | 1132.3 |  | 13224 | 164.25 | 5.2495 | 60.912 | 0.014236 | 132.34 | 1132.3 | 999.96
13225 | 5.2507 | 164.26 | 60.912 | 0.01424 | 132.35 | 1132.3 |  | 13225 | 164.26 | 5.2507 | 60.912 | 0.01424 | 132.35 | 1132.3 | 999.95
13226 | 5.252 | 164.27 | 60.912 | 0.014243 | 132.36 | 1132.3 |  | 13226 | 164.27 | 5.252 | 60.912 | 0.014243 | 132.36 | 1132.3 | 999.94
13227 | 5.2532 | 164.28 | 60.912 | 0.014246 | 132.37 | 1132.3 |  | 13227 | 164.28 | 5.2532 | 60.912 | 0.014246 | 132.37 | 1132.3 | 999.93
13228 | 5.2544 | 164.29 | 60.911 | 0.014249 | 132.38 | 1132.3 |  | 13228 | 164.29 | 5.2544 | 60.911 | 0.014249 | 132.38 | 1132.3 | 999.92
13229 | 5.2557 | 164.3 | 60.911 | 0.014252 | 132.39 | 1132.3 |  | 13229 | 164.3 | 5.2557 | 60.911 | 0.014252 | 132.39 | 1132.3 | 999.91
13230 | 5.2569 | 164.31 | 60.911 | 0.014255 | 132.4 | 1132.3 |  | 13230 | 164.31 | 5.2569 | 60.911 | 0.014255 | 132.4 | 1132.3 | 999.9
13231 | 5.2581 | 164.32 | 60.911 | 0.014258 | 132.41 | 1132.3 |  | 13231 | 164.32 | 5.2581 | 60.911 | 0.014258 | 132.41 | 1132.3 | 999.89
13232 | 5.2594 | 164.33 | 60.911 | 0.014262 | 132.42 | 1132.4 |  | 13232 | 164.33 | 5.2594 | 60.911 | 0.014262 | 132.42 | 1132.4 | 999.98
13233 | 5.2606 | 164.34 | 60.91 | 0.014265 | 132.43 | 1132.4 |  | 13233 | 164.34 | 5.2606 | 60.91 | 0.014265 | 132.43 | 1132.4 | 999.97
13234 | 5.2618 | 164.35 | 60.91 | 0.014268 | 132.44 | 1132.4 |  | 13234 | 164.35 | 5.2618 | 60.91 | 0.014268 | 132.44 | 1132.4 | 999.96
13235 | 5.2631 | 164.36 | 60.91 | 0.014271 | 132.45 | 1132.4 |  | 13235 | 164.36 | 5.2631 | 60.91 | 0.014271 | 132.45 | 1132.4 | 999.95
13236 | 5.2643 | 164.37 | 60.91 | 0.014274 | 132.46 | 1132.4 |  | 13236 | 164.37 | 5.2643 | 60.91 | 0.014274 | 132.46 | 1132.4 | 999.94
13237 | 5.2655 | 164.38 | 60.91 | 0.014277 | 132.47 | 1132.4 |  | 13237 | 164.38 | 5.2655 | 60.91 | 0.014277 | 132.47 | 1132.4 | 999.93
13238 | 5.2668 | 164.39 | 60.909 | 0.01428 | 132.48 | 1132.4 |  | 13238 | 164.39 | 5.2668 | 60.909 | 0.01428 | 132.48 | 1132.4 | 999.92
13239 | 5.268 | 164.4 | 60.909 | 0.014284 | 132.49 | 1132.4 |  | 13239 | 164.4 | 5.268 | 60.909 | 0.014284 | 132.49 | 1132.4 | 999.91
13240 | 5.2692 | 164.41 | 60.909 | 0.014287 | 132.5 | 1132.4 |  | 13240 | 164.41 | 5.2692 | 60.909 | 0.014287 | 132.5 | 1132.4 | 999.9
13241 | 5.2705 | 164.42 | 60.909 | 0.01429 | 132.51 | 1132.4 |  | 13241 | 164.42 | 5.2705 | 60.909 | 0.01429 | 132.51 | 1132.4 | 999.89
13242 | 5.2717 | 164.43 | 60.909 | 0.014293 | 132.52 | 1132.4 |  | 13242 | 164.43 | 5.2717 | 60.909 | 0.014293 | 132.52 | 1132.4 | 999.88
13243 | 5.273 | 164.44 | 60.908 | 0.014296 | 132.53 | 1132.4 |  | 13243 | 164.44 | 5.273 | 60.908 | 0.014296 | 132.53 | 1132.4 | 999.87
13244 | 5.2742 | 164.45 | 60.908 | 0.014299 | 132.54 | 1132.4 |  | 13244 | 164.45 | 5.2742 | 60.908 | 0.014299 | 132.54 | 1132.4 | 999.86
13245 | 5.2754 | 164.46 | 60.908 | 0.014302 | 132.55 | 1132.4 |  | 13245 | 164.46 | 5.2754 | 60.908 | 0.014302 | 132.55 | 1132.4 | 999.85
13246 | 5.2767 | 164.47 | 60.908 | 0.014306 | 132.56 | 1132.4 |  | 13246 | 164.47 | 5.2767 | 60.908 | 0.014306 | 132.56 | 1132.4 | 999.84
13247 | 5.2779 | 164.48 | 60.908 | 0.014309 | 132.57 | 1132.4 |  | 13247 | 164.48 | 5.2779 | 60.908 | 0.014309 | 132.57 | 1132.4 | 999.83
13248 | 5.2791 | 164.49 | 60.907 | 0.014312 | 132.58 | 1132.4 |  | 13248 | 164.49 | 5.2791 | 60.907 | 0.014312 | 132.58 | 1132.4 | 999.82
13249 | 5.2804 | 164.5 | 60.907 | 0.014315 | 132.59 | 1132.4 |  | 13249 | 164.5 | 5.2804 | 60.907 | 0.014315 | 132.59 | 1132.4 | 999.81
13250 | 5.2816 | 164.51 | 60.907 | 0.014318 | 132.6 | 1132.4 |  | 13250 | 164.51 | 5.2816 | 60.907 | 0.014318 | 132.6 | 1132.4 | 999.8
13251 | 5.2829 | 164.52 | 60.907 | 0.014321 | 132.61 | 1132.4 |  | 13251 | 164.52 | 5.2829 | 60.907 | 0.014321 | 132.61 | 1132.4 | 999.79
13252 | 5.2841 | 164.53 | 60.907 | 0.014324 | 132.62 | 1132.4 |  | 13252 | 164.53 | 5.2841 | 60.907 | 0.014324 | 132.62 | 1132.4 | 999.78
13253 | 5.2853 | 164.54 | 60.906 | 0.014328 | 132.63 | 1132.4 |  | 13253 | 164.54 | 5.2853 | 60.906 | 0.014328 | 132.63 | 1132.4 | 999.77
13254 | 5.2866 | 164.55 | 60.906 | 0.014331 | 132.64 | 1132.4 |  | 13254 | 164.55 | 5.2866 | 60.906 | 0.014331 | 132.64 | 1132.4 | 999.76
13255 | 5.2878 | 164.56 | 60.906 | 0.014334 | 132.65 | 1132.4 |  | 13255 | 164.56 | 5.2878 | 60.906 | 0.014334 | 132.65 | 1132.4 | 999.75
13256 | 5.2891 | 164.57 | 60.906 | 0.014337 | 132.66 | 1132.4 |  | 13256 | 164.57 | 5.2891 | 60.906 | 0.014337 | 132.66 | 1132.4 | 999.74
13257 | 5.2903 | 164.58 | 60.906 | 0.01434 | 132.67 | 1132.5 |  | 13257 | 164.58 | 5.2903 | 60.906 | 0.01434 | 132.67 | 1132.5 | 999.83
13258 | 5.2915 | 164.59 | 60.905 | 0.014343 | 132.68 | 1132.5 |  | 13258 | 164.59 | 5.2915 | 60.905 | 0.014343 | 132.68 | 1132.5 | 999.82
13259 | 5.2928 | 164.6 | 60.905 | 0.014346 | 132.69 | 1132.5 |  | 13259 | 164.6 | 5.2928 | 60.905 | 0.014346 | 132.69 | 1132.5 | 999.81
13260 | 5.294 | 164.61 | 60.905 | 0.01435 | 132.7 | 1132.5 |  | 13260 | 164.61 | 5.294 | 60.905 | 0.01435 | 132.7 | 1132.5 | 999.8
13261 | 5.2953 | 164.62 | 60.905 | 0.014353 | 132.71 | 1132.5 |  | 13261 | 164.62 | 5.2953 | 60.905 | 0.014353 | 132.71 | 1132.5 | 999.79
13262 | 5.2965 | 164.63 | 60.904 | 0.014356 | 132.72 | 1132.5 |  | 13262 | 164.63 | 5.2965 | 60.904 | 0.014356 | 132.72 | 1132.5 | 999.78
13263 | 5.2977 | 164.64 | 60.904 | 0.014359 | 132.73 | 1132.5 |  | 13263 | 164.64 | 5.2977 | 60.904 | 0.014359 | 132.73 | 1132.5 | 999.77
13264 | 5.299 | 164.65 | 60.904 | 0.014362 | 132.74 | 1132.5 |  | 13264 | 164.65 | 5.299 | 60.904 | 0.014362 | 132.74 | 1132.5 | 999.76
13265 | 5.3002 | 164.66 | 60.904 | 0.014365 | 132.75 | 1132.5 |  | 13265 | 164.66 | 5.3002 | 60.904 | 0.014365 | 132.75 | 1132.5 | 999.75
13266 | 5.3015 | 164.67 | 60.904 | 0.014369 | 132.76 | 1132.5 |  | 13266 | 164.67 | 5.3015 | 60.904 | 0.014369 | 132.76 | 1132.5 | 999.74
13267 | 5.3027 | 164.68 | 60.903 | 0.014372 | 132.77 | 1132.5 |  | 13267 | 164.68 | 5.3027 | 60.903 | 0.014372 | 132.77 | 1132.5 | 999.73
13268 | 5.304 | 164.69 | 60.903 | 0.014375 | 132.78 | 1132.5 |  | 13268 | 164.69 | 5.304 | 60.903 | 0.014375 | 132.78 | 1132.5 | 999.72
13269 | 5.3052 | 164.7 | 60.903 | 0.014378 | 132.79 | 1132.5 |  | 13269 | 164.7 | 5.3052 | 60.903 | 0.014378 | 132.79 | 1132.5 | 999.71
13270 | 5.3064 | 164.71 | 60.903 | 0.014381 | 132.8 | 1132.5 |  | 13270 | 164.71 | 5.3064 | 60.903 | 0.014381 | 132.8 | 1132.5 | 999.7
13271 | 5.3077 | 164.72 | 60.903 | 0.014384 | 132.81 | 1132.5 |  | 13271 | 164.72 | 5.3077 | 60.903 | 0.014384 | 132.81 | 1132.5 | 999.69
13272 | 5.3089 | 164.73 | 60.902 | 0.014387 | 132.82 | 1132.5 |  | 13272 | 164.73 | 5.3089 | 60.902 | 0.014387 | 132.82 | 1132.5 | 999.68
13273 | 5.3102 | 164.74 | 60.902 | 0.014391 | 132.83 | 1132.5 |  | 13273 | 164.74 | 5.3102 | 60.902 | 0.014391 | 132.83 | 1132.5 | 999.67
13274 | 5.3114 | 164.75 | 60.902 | 0.014394 | 132.84 | 1132.5 |  | 13274 | 164.75 | 5.3114 | 60.902 | 0.014394 | 132.84 | 1132.5 | 999.66
13275 | 5.3127 | 164.76 | 60.902 | 0.014397 | 132.85 | 1132.5 |  | 13275 | 164.76 | 5.3127 | 60.902 | 0.014397 | 132.85 | 1132.5 | 999.65
13276 | 5.3139 | 164.77 | 60.902 | 0.0144 | 132.86 | 1132.5 |  | 13276 | 164.77 | 5.3139 | 60.902 | 0.0144 | 132.86 | 1132.5 | 999.64
13277 | 5.3152 | 164.78 | 60.901 | 0.014403 | 132.87 | 1132.5 |  | 13277 | 164.78 | 5.3152 | 60.901 | 0.014403 | 132.87 | 1132.5 | 999.63
13278 | 5.3164 | 164.79 | 60.901 | 0.014406 | 132.88 | 1132.5 |  | 13278 | 164.79 | 5.3164 | 60.901 | 0.014406 | 132.88 | 1132.5 | 999.62
13279 | 5.3176 | 164.8 | 60.901 | 0.01441 | 132.89 | 1132.5 |  | 13279 | 164.8 | 5.3176 | 60.901 | 0.01441 | 132.89 | 1132.5 | 999.61
13280 | 5.3189 | 164.81 | 60.901 | 0.014413 | 132.9 | 1132.5 |  | 13280 | 164.81 | 5.3189 | 60.901 | 0.014413 | 132.9 | 1132.5 | 999.6
13281 | 5.3201 | 164.82 | 60.901 | 0.014416 | 132.91 | 1132.6 |  | 13281 | 164.82 | 5.3201 | 60.901 | 0.014416 | 132.91 | 1132.6 | 999.69
13282 | 5.3214 | 164.83 | 60.9 | 0.014419 | 132.92 | 1132.6 |  | 13282 | 164.83 | 5.3214 | 60.9 | 0.014419 | 132.92 | 1132.6 | 999.68
13283 | 5.3226 | 164.84 | 60.9 | 0.014422 | 132.93 | 1132.6 |  | 13283 | 164.84 | 5.3226 | 60.9 | 0.014422 | 132.93 | 1132.6 | 999.67
13284 | 5.3239 | 164.85 | 60.9 | 0.014425 | 132.94 | 1132.6 |  | 13284 | 164.85 | 5.3239 | 60.9 | 0.014425 | 132.94 | 1132.6 | 999.66
13285 | 5.3251 | 164.86 | 60.9 | 0.014429 | 132.95 | 1132.6 |  | 13285 | 164.86 | 5.3251 | 60.9 | 0.014429 | 132.95 | 1132.6 | 999.65
13286 | 5.3264 | 164.87 | 60.9 | 0.014432 | 132.96 | 1132.6 |  | 13286 | 164.87 | 5.3264 | 60.9 | 0.014432 | 132.96 | 1132.6 | 999.64
13287 | 5.3276 | 164.88 | 60.899 | 0.014435 | 132.97 | 1132.6 |  | 13287 | 164.88 | 5.3276 | 60.899 | 0.014435 | 132.97 | 1132.6 | 999.63
13288 | 5.3289 | 164.89 | 60.899 | 0.014438 | 132.98 | 1132.6 |  | 13288 | 164.89 | 5.3289 | 60.899 | 0.014438 | 132.98 | 1132.6 | 999.62
13289 | 5.3301 | 164.9 | 60.899 | 0.014441 | 132.99 | 1132.6 |  | 13289 | 164.9 | 5.3301 | 60.899 | 0.014441 | 132.99 | 1132.6 | 999.61
13290 | 5.3314 | 164.91 | 60.899 | 0.014444 | 133 | 1132.6 |  | 13290 | 164.91 | 5.3314 | 60.899 | 0.014444 | 133 | 1132.6 | 999.6
13291 | 5.3326 | 164.92 | 60.899 | 0.014448 | 133.01 | 1132.6 |  | 13291 | 164.92 | 5.3326 | 60.899 | 0.014448 | 133.01 | 1132.6 | 999.59
13292 | 5.3339 | 164.93 | 60.898 | 0.014451 | 133.02 | 1132.6 |  | 13292 | 164.93 | 5.3339 | 60.898 | 0.014451 | 133.02 | 1132.6 | 999.58
13293 | 5.3351 | 164.94 | 60.898 | 0.014454 | 133.03 | 1132.6 |  | 13293 | 164.94 | 5.3351 | 60.898 | 0.014454 | 133.03 | 1132.6 | 999.57
13294 | 5.3364 | 164.95 | 60.898 | 0.014457 | 133.04 | 1132.6 |  | 13294 | 164.95 | 5.3364 | 60.898 | 0.014457 | 133.04 | 1132.6 | 999.56
13295 | 5.3376 | 164.96 | 60.898 | 0.01446 | 133.05 | 1132.6 |  | 13295 | 164.96 | 5.3376 | 60.898 | 0.01446 | 133.05 | 1132.6 | 999.55
13296 | 5.3389 | 164.97 | 60.898 | 0.014463 | 133.06 | 1132.6 |  | 13296 | 164.97 | 5.3389 | 60.898 | 0.014463 | 133.06 | 1132.6 | 999.54
13297 | 5.3401 | 164.98 | 60.897 | 0.014467 | 133.07 | 1132.6 |  | 13297 | 164.98 | 5.3401 | 60.897 | 0.014467 | 133.07 | 1132.6 | 999.53
13298 | 5.3414 | 164.99 | 60.897 | 0.01447 | 133.08 | 1132.6 |  | 13298 | 164.99 | 5.3414 | 60.897 | 0.01447 | 133.08 | 1132.6 | 999.52
13299 | 5.3426 | 165 | 60.897 | 0.014473 | 133.09 | 1132.6 |  | 13299 | 165 | 5.3426 | 60.897 | 0.014473 | 133.09 | 1132.6 | 999.51
13300 | 5.3439 | 165.01 | 60.897 | 0.014476 | 133.1 | 1132.6 |  | 13300 | 165.01 | 5.3439 | 60.897 | 0.014476 | 133.1 | 1132.6 | 999.5
13301 | 5.3451 | 165.02 | 60.897 | 0.014479 | 133.11 | 1132.6 |  | 13301 | 165.02 | 5.3451 | 60.897 | 0.014479 | 133.11 | 1132.6 | 999.49
13302 | 5.3464 | 165.03 | 60.896 | 0.014482 | 133.12 | 1132.6 |  | 13302 | 165.03 | 5.3464 | 60.896 | 0.014482 | 133.12 | 1132.6 | 999.48
13303 | 5.3476 | 165.04 | 60.896 | 0.014486 | 133.13 | 1132.6 |  | 13303 | 165.04 | 5.3476 | 60.896 | 0.014486 | 133.13 | 1132.6 | 999.47
13304 | 5.3489 | 165.05 | 60.896 | 0.014489 | 133.14 | 1132.6 |  | 13304 | 165.05 | 5.3489 | 60.896 | 0.014489 | 133.14 | 1132.6 | 999.46
13305 | 5.3501 | 165.06 | 60.896 | 0.014492 | 133.15 | 1132.6 |  | 13305 | 165.06 | 5.3501 | 60.896 | 0.014492 | 133.15 | 1132.6 | 999.45
13306 | 5.3514 | 165.07 | 60.895 | 0.014495 | 133.16 | 1132.7 |  | 13306 | 165.07 | 5.3514 | 60.895 | 0.014495 | 133.16 | 1132.7 | 999.54
13307 | 5.3526 | 165.08 | 60.895 | 0.014498 | 133.17 | 1132.7 |  | 13307 | 165.08 | 5.3526 | 60.895 | 0.014498 | 133.17 | 1132.7 | 999.53
13308 | 5.3539 | 165.09 | 60.895 | 0.014502 | 133.18 | 1132.7 |  | 13308 | 165.09 | 5.3539 | 60.895 | 0.014502 | 133.18 | 1132.7 | 999.52
13309 | 5.3551 | 165.1 | 60.895 | 0.014505 | 133.19 | 1132.7 |  | 13309 | 165.1 | 5.3551 | 60.895 | 0.014505 | 133.19 | 1132.7 | 999.51
13310 | 5.3564 | 165.11 | 60.895 | 0.014508 | 133.2 | 1132.7 |  | 13310 | 165.11 | 5.3564 | 60.895 | 0.014508 | 133.2 | 1132.7 | 999.5
13311 | 5.3576 | 165.12 | 60.894 | 0.014511 | 133.21 | 1132.7 |  | 13311 | 165.12 | 5.3576 | 60.894 | 0.014511 | 133.21 | 1132.7 | 999.49
13312 | 5.3589 | 165.13 | 60.894 | 0.014514 | 133.22 | 1132.7 |  | 13312 | 165.13 | 5.3589 | 60.894 | 0.014514 | 133.22 | 1132.7 | 999.48
13313 | 5.3602 | 165.14 | 60.894 | 0.014517 | 133.23 | 1132.7 |  | 13313 | 165.14 | 5.3602 | 60.894 | 0.014517 | 133.23 | 1132.7 | 999.47
13314 | 5.3614 | 165.15 | 60.894 | 0.014521 | 133.24 | 1132.7 |  | 13314 | 165.15 | 5.3614 | 60.894 | 0.014521 | 133.24 | 1132.7 | 999.46
13315 | 5.3627 | 165.16 | 60.894 | 0.014524 | 133.25 | 1132.7 |  | 13315 | 165.16 | 5.3627 | 60.894 | 0.014524 | 133.25 | 1132.7 | 999.45
13316 | 5.3639 | 165.17 | 60.893 | 0.014527 | 133.26 | 1132.7 |  | 13316 | 165.17 | 5.3639 | 60.893 | 0.014527 | 133.26 | 1132.7 | 999.44
13317 | 5.3652 | 165.18 | 60.893 | 0.01453 | 133.27 | 1132.7 |  | 13317 | 165.18 | 5.3652 | 60.893 | 0.01453 | 133.27 | 1132.7 | 999.43
13318 | 5.3664 | 165.19 | 60.893 | 0.014533 | 133.28 | 1132.7 |  | 13318 | 165.19 | 5.3664 | 60.893 | 0.014533 | 133.28 | 1132.7 | 999.42
13319 | 5.3677 | 165.2 | 60.893 | 0.014537 | 133.29 | 1132.7 |  | 13319 | 165.2 | 5.3677 | 60.893 | 0.014537 | 133.29 | 1132.7 | 999.41
13320 | 5.3689 | 165.21 | 60.893 | 0.01454 | 133.3 | 1132.7 |  | 13320 | 165.21 | 5.3689 | 60.893 | 0.01454 | 133.3 | 1132.7 | 999.4
13321 | 5.3702 | 165.22 | 60.892 | 0.014543 | 133.31 | 1132.7 |  | 13321 | 165.22 | 5.3702 | 60.892 | 0.014543 | 133.31 | 1132.7 | 999.39
13322 | 5.3715 | 165.23 | 60.892 | 0.014546 | 133.32 | 1132.7 |  | 13322 | 165.23 | 5.3715 | 60.892 | 0.014546 | 133.32 | 1132.7 | 999.38
13323 | 5.3727 | 165.24 | 60.892 | 0.014549 | 133.33 | 1132.7 |  | 13323 | 165.24 | 5.3727 | 60.892 | 0.014549 | 133.33 | 1132.7 | 999.37
13324 | 5.374 | 165.25 | 60.892 | 0.014553 | 133.34 | 1132.7 |  | 13324 | 165.25 | 5.374 | 60.892 | 0.014553 | 133.34 | 1132.7 | 999.36
13325 | 5.3752 | 165.26 | 60.892 | 0.014556 | 133.35 | 1132.7 |  | 13325 | 165.26 | 5.3752 | 60.892 | 0.014556 | 133.35 | 1132.7 | 999.35
13326 | 5.3765 | 165.27 | 60.891 | 0.014559 | 133.36 | 1132.7 |  | 13326 | 165.27 | 5.3765 | 60.891 | 0.014559 | 133.36 | 1132.7 | 999.34
13327 | 5.3777 | 165.28 | 60.891 | 0.014562 | 133.37 | 1132.7 |  | 13327 | 165.28 | 5.3777 | 60.891 | 0.014562 | 133.37 | 1132.7 | 999.33
13328 | 5.379 | 165.29 | 60.891 | 0.014565 | 133.38 | 1132.7 |  | 13328 | 165.29 | 5.379 | 60.891 | 0.014565 | 133.38 | 1132.7 | 999.32
13329 | 5.3803 | 165.3 | 60.891 | 0.014568 | 133.39 | 1132.7 |  | 13329 | 165.3 | 5.3803 | 60.891 | 0.014568 | 133.39 | 1132.7 | 999.31
13330 | 5.3815 | 165.31 | 60.891 | 0.014572 | 133.4 | 1132.7 |  | 13330 | 165.31 | 5.3815 | 60.891 | 0.014572 | 133.4 | 1132.7 | 999.3
13331 | 5.3828 | 165.32 | 60.89 | 0.014575 | 133.41 | 1132.8 |  | 13331 | 165.32 | 5.3828 | 60.89 | 0.014575 | 133.41 | 1132.8 | 999.39
13332 | 5.384 | 165.33 | 60.89 | 0.014578 | 133.42 | 1132.8 |  | 13332 | 165.33 | 5.384 | 60.89 | 0.014578 | 133.42 | 1132.8 | 999.38
13333 | 5.3853 | 165.34 | 60.89 | 0.014581 | 133.43 | 1132.8 |  | 13333 | 165.34 | 5.3853 | 60.89 | 0.014581 | 133.43 | 1132.8 | 999.37
13334 | 5.3865 | 165.35 | 60.89 | 0.014584 | 133.44 | 1132.8 |  | 13334 | 165.35 | 5.3865 | 60.89 | 0.014584 | 133.44 | 1132.8 | 999.36
13335 | 5.3878 | 165.36 | 60.89 | 0.014588 | 133.45 | 1132.8 |  | 13335 | 165.36 | 5.3878 | 60.89 | 0.014588 | 133.45 | 1132.8 | 999.35
13336 | 5.3891 | 165.37 | 60.889 | 0.014591 | 133.46 | 1132.8 |  | 13336 | 165.37 | 5.3891 | 60.889 | 0.014591 | 133.46 | 1132.8 | 999.34
13337 | 5.3903 | 165.38 | 60.889 | 0.014594 | 133.47 | 1132.8 |  | 13337 | 165.38 | 5.3903 | 60.889 | 0.014594 | 133.47 | 1132.8 | 999.33
13338 | 5.3916 | 165.39 | 60.889 | 0.014597 | 133.48 | 1132.8 |  | 13338 | 165.39 | 5.3916 | 60.889 | 0.014597 | 133.48 | 1132.8 | 999.32
13339 | 5.3928 | 165.4 | 60.889 | 0.0146 | 133.49 | 1132.8 |  | 13339 | 165.4 | 5.3928 | 60.889 | 0.0146 | 133.49 | 1132.8 | 999.31
13340 | 5.3941 | 165.41 | 60.888 | 0.014604 | 133.5 | 1132.8 |  | 13340 | 165.41 | 5.3941 | 60.888 | 0.014604 | 133.5 | 1132.8 | 999.3
13341 | 5.3954 | 165.42 | 60.888 | 0.014607 | 133.52 | 1132.8 |  | 13341 | 165.42 | 5.3954 | 60.888 | 0.014607 | 133.52 | 1132.8 | 999.28
13342 | 5.3966 | 165.43 | 60.888 | 0.01461 | 133.53 | 1132.8 |  | 13342 | 165.43 | 5.3966 | 60.888 | 0.01461 | 133.53 | 1132.8 | 999.27
13343 | 5.3979 | 165.44 | 60.888 | 0.014613 | 133.54 | 1132.8 |  | 13343 | 165.44 | 5.3979 | 60.888 | 0.014613 | 133.54 | 1132.8 | 999.26
13344 | 5.3992 | 165.45 | 60.888 | 0.014616 | 133.55 | 1132.8 |  | 13344 | 165.45 | 5.3992 | 60.888 | 0.014616 | 133.55 | 1132.8 | 999.25
13345 | 5.4004 | 165.46 | 60.887 | 0.01462 | 133.56 | 1132.8 |  | 13345 | 165.46 | 5.4004 | 60.887 | 0.01462 | 133.56 | 1132.8 | 999.24
13346 | 5.4017 | 165.47 | 60.887 | 0.014623 | 133.57 | 1132.8 |  | 13346 | 165.47 | 5.4017 | 60.887 | 0.014623 | 133.57 | 1132.8 | 999.23
13347 | 5.4029 | 165.48 | 60.887 | 0.014626 | 133.58 | 1132.8 |  | 13347 | 165.48 | 5.4029 | 60.887 | 0.014626 | 133.58 | 1132.8 | 999.22
13348 | 5.4042 | 165.49 | 60.887 | 0.014629 | 133.59 | 1132.8 |  | 13348 | 165.49 | 5.4042 | 60.887 | 0.014629 | 133.59 | 1132.8 | 999.21
13349 | 5.4055 | 165.5 | 60.887 | 0.014632 | 133.6 | 1132.8 |  | 13349 | 165.5 | 5.4055 | 60.887 | 0.014632 | 133.6 | 1132.8 | 999.2
13350 | 5.4067 | 165.51 | 60.886 | 0.014636 | 133.61 | 1132.8 |  | 13350 | 165.51 | 5.4067 | 60.886 | 0.014636 | 133.61 | 1132.8 | 999.19
13351 | 5.408 | 165.52 | 60.886 | 0.014639 | 133.62 | 1132.8 |  | 13351 | 165.52 | 5.408 | 60.886 | 0.014639 | 133.62 | 1132.8 | 999.18
13352 | 5.4093 | 165.53 | 60.886 | 0.014642 | 133.63 | 1132.8 |  | 13352 | 165.53 | 5.4093 | 60.886 | 0.014642 | 133.63 | 1132.8 | 999.17
13353 | 5.4105 | 165.54 | 60.886 | 0.014645 | 133.64 | 1132.8 |  | 13353 | 165.54 | 5.4105 | 60.886 | 0.014645 | 133.64 | 1132.8 | 999.16
13354 | 5.4118 | 165.55 | 60.886 | 0.014648 | 133.65 | 1132.8 |  | 13354 | 165.55 | 5.4118 | 60.886 | 0.014648 | 133.65 | 1132.8 | 999.15
13355 | 5.4131 | 165.56 | 60.885 | 0.014652 | 133.66 | 1132.9 |  | 13355 | 165.56 | 5.4131 | 60.885 | 0.014652 | 133.66 | 1132.9 | 999.24
13356 | 5.4143 | 165.57 | 60.885 | 0.014655 | 133.67 | 1132.9 |  | 13356 | 165.57 | 5.4143 | 60.885 | 0.014655 | 133.67 | 1132.9 | 999.23
13357 | 5.4156 | 165.58 | 60.885 | 0.014658 | 133.68 | 1132.9 |  | 13357 | 165.58 | 5.4156 | 60.885 | 0.014658 | 133.68 | 1132.9 | 999.22
13358 | 5.4169 | 165.59 | 60.885 | 0.014661 | 133.69 | 1132.9 |  | 13358 | 165.59 | 5.4169 | 60.885 | 0.014661 | 133.69 | 1132.9 | 999.21
13359 | 5.4181 | 165.6 | 60.885 | 0.014664 | 133.7 | 1132.9 |  | 13359 | 165.6 | 5.4181 | 60.885 | 0.014664 | 133.7 | 1132.9 | 999.2
13360 | 5.4194 | 165.61 | 60.884 | 0.014668 | 133.71 | 1132.9 |  | 13360 | 165.61 | 5.4194 | 60.884 | 0.014668 | 133.71 | 1132.9 | 999.19
13361 | 5.4206 | 165.62 | 60.884 | 0.014671 | 133.72 | 1132.9 |  | 13361 | 165.62 | 5.4206 | 60.884 | 0.014671 | 133.72 | 1132.9 | 999.18
13362 | 5.4219 | 165.63 | 60.884 | 0.014674 | 133.73 | 1132.9 |  | 13362 | 165.63 | 5.4219 | 60.884 | 0.014674 | 133.73 | 1132.9 | 999.17
13363 | 5.4232 | 165.64 | 60.884 | 0.014677 | 133.74 | 1132.9 |  | 13363 | 165.64 | 5.4232 | 60.884 | 0.014677 | 133.74 | 1132.9 | 999.16
13364 | 5.4244 | 165.65 | 60.884 | 0.014681 | 133.75 | 1132.9 |  | 13364 | 165.65 | 5.4244 | 60.884 | 0.014681 | 133.75 | 1132.9 | 999.15
13365 | 5.4257 | 165.66 | 60.883 | 0.014684 | 133.76 | 1132.9 |  | 13365 | 165.66 | 5.4257 | 60.883 | 0.014684 | 133.76 | 1132.9 | 999.14
13366 | 5.427 | 165.67 | 60.883 | 0.014687 | 133.77 | 1132.9 |  | 13366 | 165.67 | 5.427 | 60.883 | 0.014687 | 133.77 | 1132.9 | 999.13
13367 | 5.4283 | 165.68 | 60.883 | 0.01469 | 133.78 | 1132.9 |  | 13367 | 165.68 | 5.4283 | 60.883 | 0.01469 | 133.78 | 1132.9 | 999.12
13368 | 5.4295 | 165.69 | 60.883 | 0.014693 | 133.79 | 1132.9 |  | 13368 | 165.69 | 5.4295 | 60.883 | 0.014693 | 133.79 | 1132.9 | 999.11
13369 | 5.4308 | 165.7 | 60.883 | 0.014697 | 133.8 | 1132.9 |  | 13369 | 165.7 | 5.4308 | 60.883 | 0.014697 | 133.8 | 1132.9 | 999.1
13370 | 5.4321 | 165.71 | 60.882 | 0.0147 | 133.81 | 1132.9 |  | 13370 | 165.71 | 5.4321 | 60.882 | 0.0147 | 133.81 | 1132.9 | 999.09
13371 | 5.4333 | 165.72 | 60.882 | 0.014703 | 133.82 | 1132.9 |  | 13371 | 165.72 | 5.4333 | 60.882 | 0.014703 | 133.82 | 1132.9 | 999.08
13372 | 5.4346 | 165.73 | 60.882 | 0.014706 | 133.83 | 1132.9 |  | 13372 | 165.73 | 5.4346 | 60.882 | 0.014706 | 133.83 | 1132.9 | 999.07
13373 | 5.4359 | 165.74 | 60.882 | 0.014709 | 133.84 | 1132.9 |  | 13373 | 165.74 | 5.4359 | 60.882 | 0.014709 | 133.84 | 1132.9 | 999.06
13374 | 5.4371 | 165.75 | 60.882 | 0.014713 | 133.85 | 1132.9 |  | 13374 | 165.75 | 5.4371 | 60.882 | 0.014713 | 133.85 | 1132.9 | 999.05
13375 | 5.4384 | 165.76 | 60.881 | 0.014716 | 133.86 | 1132.9 |  | 13375 | 165.76 | 5.4384 | 60.881 | 0.014716 | 133.86 | 1132.9 | 999.04
13376 | 5.4397 | 165.77 | 60.881 | 0.014719 | 133.87 | 1132.9 |  | 13376 | 165.77 | 5.4397 | 60.881 | 0.014719 | 133.87 | 1132.9 | 999.03
13377 | 5.4409 | 165.78 | 60.881 | 0.014722 | 133.88 | 1132.9 |  | 13377 | 165.78 | 5.4409 | 60.881 | 0.014722 | 133.88 | 1132.9 | 999.02
13378 | 5.4422 | 165.79 | 60.881 | 0.014726 | 133.89 | 1132.9 |  | 13378 | 165.79 | 5.4422 | 60.881 | 0.014726 | 133.89 | 1132.9 | 999.01
13379 | 5.4435 | 165.8 | 60.88 | 0.014729 | 133.9 | 1132.9 |  | 13379 | 165.8 | 5.4435 | 60.88 | 0.014729 | 133.9 | 1132.9 | 999
13380 | 5.4448 | 165.81 | 60.88 | 0.014732 | 133.91 | 1133 |  | 13380 | 165.81 | 5.4448 | 60.88 | 0.014732 | 133.91 | 1133 | 999.09
13381 | 5.446 | 165.82 | 60.88 | 0.014735 | 133.92 | 1133 |  | 13381 | 165.82 | 5.446 | 60.88 | 0.014735 | 133.92 | 1133 | 999.08
13382 | 5.4473 | 165.83 | 60.88 | 0.014738 | 133.93 | 1133 |  | 13382 | 165.83 | 5.4473 | 60.88 | 0.014738 | 133.93 | 1133 | 999.07
13383 | 5.4486 | 165.84 | 60.88 | 0.014742 | 133.94 | 1133 |  | 13383 | 165.84 | 5.4486 | 60.88 | 0.014742 | 133.94 | 1133 | 999.06
13384 | 5.4498 | 165.85 | 60.879 | 0.014745 | 133.95 | 1133 |  | 13384 | 165.85 | 5.4498 | 60.879 | 0.014745 | 133.95 | 1133 | 999.05
13385 | 5.4511 | 165.86 | 60.879 | 0.014748 | 133.96 | 1133 |  | 13385 | 165.86 | 5.4511 | 60.879 | 0.014748 | 133.96 | 1133 | 999.04
13386 | 5.4524 | 165.87 | 60.879 | 0.014751 | 133.97 | 1133 |  | 13386 | 165.87 | 5.4524 | 60.879 | 0.014751 | 133.97 | 1133 | 999.03
13387 | 5.4537 | 165.88 | 60.879 | 0.014755 | 133.98 | 1133 |  | 13387 | 165.88 | 5.4537 | 60.879 | 0.014755 | 133.98 | 1133 | 999.02
13388 | 5.4549 | 165.89 | 60.879 | 0.014758 | 133.99 | 1133 |  | 13388 | 165.89 | 5.4549 | 60.879 | 0.014758 | 133.99 | 1133 | 999.01
13389 | 5.4562 | 165.9 | 60.878 | 0.014761 | 134 | 1133 |  | 13389 | 165.9 | 5.4562 | 60.878 | 0.014761 | 134 | 1133 | 999
13390 | 5.4575 | 165.91 | 60.878 | 0.014764 | 134.01 | 1133 |  | 13390 | 165.91 | 5.4575 | 60.878 | 0.014764 | 134.01 | 1133 | 998.99
13391 | 5.4587 | 165.92 | 60.878 | 0.014768 | 134.02 | 1133 |  | 13391 | 165.92 | 5.4587 | 60.878 | 0.014768 | 134.02 | 1133 | 998.98
13392 | 5.46 | 165.93 | 60.878 | 0.014771 | 134.03 | 1133 |  | 13392 | 165.93 | 5.46 | 60.878 | 0.014771 | 134.03 | 1133 | 998.97
13393 | 5.4613 | 165.94 | 60.878 | 0.014774 | 134.04 | 1133 |  | 13393 | 165.94 | 5.4613 | 60.878 | 0.014774 | 134.04 | 1133 | 998.96
13394 | 5.4626 | 165.95 | 60.877 | 0.014777 | 134.05 | 1133 |  | 13394 | 165.95 | 5.4626 | 60.877 | 0.014777 | 134.05 | 1133 | 998.95
13395 | 5.4638 | 165.96 | 60.877 | 0.01478 | 134.06 | 1133 |  | 13395 | 165.96 | 5.4638 | 60.877 | 0.01478 | 134.06 | 1133 | 998.94
13396 | 5.4651 | 165.97 | 60.877 | 0.014784 | 134.07 | 1133 |  | 13396 | 165.97 | 5.4651 | 60.877 | 0.014784 | 134.07 | 1133 | 998.93
13397 | 5.4664 | 165.98 | 60.877 | 0.014787 | 134.08 | 1133 |  | 13397 | 165.98 | 5.4664 | 60.877 | 0.014787 | 134.08 | 1133 | 998.92
13398 | 5.4677 | 165.99 | 60.877 | 0.01479 | 134.09 | 1133 |  | 13398 | 165.99 | 5.4677 | 60.877 | 0.01479 | 134.09 | 1133 | 998.91
13399 | 5.4689 | 166 | 60.876 | 0.014793 | 134.1 | 1133 |  | 13399 | 166 | 5.4689 | 60.876 | 0.014793 | 134.1 | 1133 | 998.9
13400 | 5.4702 | 166.01 | 60.876 | 0.014797 | 134.11 | 1133 |  | 13400 | 166.01 | 5.4702 | 60.876 | 0.014797 | 134.11 | 1133 | 998.89
13401 | 5.4715 | 166.02 | 60.876 | 0.0148 | 134.12 | 1133 |  | 13401 | 166.02 | 5.4715 | 60.876 | 0.0148 | 134.12 | 1133 | 998.88
13402 | 5.4728 | 166.03 | 60.876 | 0.014803 | 134.13 | 1133 |  | 13402 | 166.03 | 5.4728 | 60.876 | 0.014803 | 134.13 | 1133 | 998.87
13403 | 5.4741 | 166.04 | 60.876 | 0.014806 | 134.14 | 1133 |  | 13403 | 166.04 | 5.4741 | 60.876 | 0.014806 | 134.14 | 1133 | 998.86
13404 | 5.4753 | 166.05 | 60.875 | 0.01481 | 134.15 | 1133 |  | 13404 | 166.05 | 5.4753 | 60.875 | 0.01481 | 134.15 | 1133 | 998.85
13405 | 5.4766 | 166.06 | 60.875 | 0.014813 | 134.16 | 1133.1 |  | 13405 | 166.06 | 5.4766 | 60.875 | 0.014813 | 134.16 | 1133.1 | 998.94
13406 | 5.4779 | 166.07 | 60.875 | 0.014816 | 134.17 | 1133.1 |  | 13406 | 166.07 | 5.4779 | 60.875 | 0.014816 | 134.17 | 1133.1 | 998.93
13407 | 5.4792 | 166.08 | 60.875 | 0.014819 | 134.18 | 1133.1 |  | 13407 | 166.08 | 5.4792 | 60.875 | 0.014819 | 134.18 | 1133.1 | 998.92
13408 | 5.4804 | 166.09 | 60.875 | 0.014822 | 134.19 | 1133.1 |  | 13408 | 166.09 | 5.4804 | 60.875 | 0.014822 | 134.19 | 1133.1 | 998.91
13409 | 5.4817 | 166.1 | 60.874 | 0.014826 | 134.2 | 1133.1 |  | 13409 | 166.1 | 5.4817 | 60.874 | 0.014826 | 134.2 | 1133.1 | 998.9
13410 | 5.483 | 166.11 | 60.874 | 0.014829 | 134.21 | 1133.1 |  | 13410 | 166.11 | 5.483 | 60.874 | 0.014829 | 134.21 | 1133.1 | 998.89
13411 | 5.4843 | 166.12 | 60.874 | 0.014832 | 134.22 | 1133.1 |  | 13411 | 166.12 | 5.4843 | 60.874 | 0.014832 | 134.22 | 1133.1 | 998.88
13412 | 5.4856 | 166.13 | 60.874 | 0.014835 | 134.23 | 1133.1 |  | 13412 | 166.13 | 5.4856 | 60.874 | 0.014835 | 134.23 | 1133.1 | 998.87
13413 | 5.4868 | 166.14 | 60.873 | 0.014839 | 134.24 | 1133.1 |  | 13413 | 166.14 | 5.4868 | 60.873 | 0.014839 | 134.24 | 1133.1 | 998.86
13414 | 5.4881 | 166.15 | 60.873 | 0.014842 | 134.25 | 1133.1 |  | 13414 | 166.15 | 5.4881 | 60.873 | 0.014842 | 134.25 | 1133.1 | 998.85
13415 | 5.4894 | 166.16 | 60.873 | 0.014845 | 134.26 | 1133.1 |  | 13415 | 166.16 | 5.4894 | 60.873 | 0.014845 | 134.26 | 1133.1 | 998.84
13416 | 5.4907 | 166.17 | 60.873 | 0.014848 | 134.27 | 1133.1 |  | 13416 | 166.17 | 5.4907 | 60.873 | 0.014848 | 134.27 | 1133.1 | 998.83
13417 | 5.492 | 166.18 | 60.873 | 0.014852 | 134.28 | 1133.1 |  | 13417 | 166.18 | 5.492 | 60.873 | 0.014852 | 134.28 | 1133.1 | 998.82
13418 | 5.4932 | 166.19 | 60.872 | 0.014855 | 134.29 | 1133.1 |  | 13418 | 166.19 | 5.4932 | 60.872 | 0.014855 | 134.29 | 1133.1 | 998.81
13419 | 5.4945 | 166.2 | 60.872 | 0.014858 | 134.3 | 1133.1 |  | 13419 | 166.2 | 5.4945 | 60.872 | 0.014858 | 134.3 | 1133.1 | 998.8
13420 | 5.4958 | 166.21 | 60.872 | 0.014861 | 134.31 | 1133.1 |  | 13420 | 166.21 | 5.4958 | 60.872 | 0.014861 | 134.31 | 1133.1 | 998.79
13421 | 5.4971 | 166.22 | 60.872 | 0.014865 | 134.32 | 1133.1 |  | 13421 | 166.22 | 5.4971 | 60.872 | 0.014865 | 134.32 | 1133.1 | 998.78
13422 | 5.4984 | 166.23 | 60.872 | 0.014868 | 134.33 | 1133.1 |  | 13422 | 166.23 | 5.4984 | 60.872 | 0.014868 | 134.33 | 1133.1 | 998.77
13423 | 5.4996 | 166.24 | 60.871 | 0.014871 | 134.34 | 1133.1 |  | 13423 | 166.24 | 5.4996 | 60.871 | 0.014871 | 134.34 | 1133.1 | 998.76
13424 | 5.5009 | 166.25 | 60.871 | 0.014874 | 134.35 | 1133.1 |  | 13424 | 166.25 | 5.5009 | 60.871 | 0.014874 | 134.35 | 1133.1 | 998.75
13425 | 5.5022 | 166.26 | 60.871 | 0.014878 | 134.36 | 1133.1 |  | 13425 | 166.26 | 5.5022 | 60.871 | 0.014878 | 134.36 | 1133.1 | 998.74
13426 | 5.5035 | 166.27 | 60.871 | 0.014881 | 134.37 | 1133.1 |  | 13426 | 166.27 | 5.5035 | 60.871 | 0.014881 | 134.37 | 1133.1 | 998.73
13427 | 5.5048 | 166.28 | 60.871 | 0.014884 | 134.38 | 1133.1 |  | 13427 | 166.28 | 5.5048 | 60.871 | 0.014884 | 134.38 | 1133.1 | 998.72
13428 | 5.5061 | 166.29 | 60.87 | 0.014887 | 134.39 | 1133.1 |  | 13428 | 166.29 | 5.5061 | 60.87 | 0.014887 | 134.39 | 1133.1 | 998.71
13429 | 5.5073 | 166.3 | 60.87 | 0.014891 | 134.4 | 1133.2 |  | 13429 | 166.3 | 5.5073 | 60.87 | 0.014891 | 134.4 | 1133.2 | 998.8
13430 | 5.5086 | 166.31 | 60.87 | 0.014894 | 134.41 | 1133.2 |  | 13430 | 166.31 | 5.5086 | 60.87 | 0.014894 | 134.41 | 1133.2 | 998.79
13431 | 5.5099 | 166.32 | 60.87 | 0.014897 | 134.42 | 1133.2 |  | 13431 | 166.32 | 5.5099 | 60.87 | 0.014897 | 134.42 | 1133.2 | 998.78
13432 | 5.5112 | 166.33 | 60.87 | 0.0149 | 134.43 | 1133.2 |  | 13432 | 166.33 | 5.5112 | 60.87 | 0.0149 | 134.43 | 1133.2 | 998.77
13433 | 5.5125 | 166.34 | 60.869 | 0.014904 | 134.44 | 1133.2 |  | 13433 | 166.34 | 5.5125 | 60.869 | 0.014904 | 134.44 | 1133.2 | 998.76
13434 | 5.5138 | 166.35 | 60.869 | 0.014907 | 134.45 | 1133.2 |  | 13434 | 166.35 | 5.5138 | 60.869 | 0.014907 | 134.45 | 1133.2 | 998.75
13435 | 5.515 | 166.36 | 60.869 | 0.01491 | 134.46 | 1133.2 |  | 13435 | 166.36 | 5.515 | 60.869 | 0.01491 | 134.46 | 1133.2 | 998.74
13436 | 5.5163 | 166.37 | 60.869 | 0.014913 | 134.47 | 1133.2 |  | 13436 | 166.37 | 5.5163 | 60.869 | 0.014913 | 134.47 | 1133.2 | 998.73
13437 | 5.5176 | 166.38 | 60.869 | 0.014917 | 134.48 | 1133.2 |  | 13437 | 166.38 | 5.5176 | 60.869 | 0.014917 | 134.48 | 1133.2 | 998.72
13438 | 5.5189 | 166.39 | 60.868 | 0.01492 | 134.49 | 1133.2 |  | 13438 | 166.39 | 5.5189 | 60.868 | 0.01492 | 134.49 | 1133.2 | 998.71
13439 | 5.5202 | 166.4 | 60.868 | 0.014923 | 134.5 | 1133.2 |  | 13439 | 166.4 | 5.5202 | 60.868 | 0.014923 | 134.5 | 1133.2 | 998.7
13440 | 5.5215 | 166.41 | 60.868 | 0.014926 | 134.51 | 1133.2 |  | 13440 | 166.41 | 5.5215 | 60.868 | 0.014926 | 134.51 | 1133.2 | 998.69
13441 | 5.5228 | 166.42 | 60.868 | 0.01493 | 134.52 | 1133.2 |  | 13441 | 166.42 | 5.5228 | 60.868 | 0.01493 | 134.52 | 1133.2 | 998.68
13442 | 5.524 | 166.43 | 60.867 | 0.014933 | 134.53 | 1133.2 |  | 13442 | 166.43 | 5.524 | 60.867 | 0.014933 | 134.53 | 1133.2 | 998.67
13443 | 5.5253 | 166.44 | 60.867 | 0.014936 | 134.54 | 1133.2 |  | 13443 | 166.44 | 5.5253 | 60.867 | 0.014936 | 134.54 | 1133.2 | 998.66
13444 | 5.5266 | 166.45 | 60.867 | 0.014939 | 134.55 | 1133.2 |  | 13444 | 166.45 | 5.5266 | 60.867 | 0.014939 | 134.55 | 1133.2 | 998.65
13445 | 5.5279 | 166.46 | 60.867 | 0.014943 | 134.56 | 1133.2 |  | 13445 | 166.46 | 5.5279 | 60.867 | 0.014943 | 134.56 | 1133.2 | 998.64
13446 | 5.5292 | 166.47 | 60.867 | 0.014946 | 134.57 | 1133.2 |  | 13446 | 166.47 | 5.5292 | 60.867 | 0.014946 | 134.57 | 1133.2 | 998.63
13447 | 5.5305 | 166.48 | 60.866 | 0.014949 | 134.58 | 1133.2 |  | 13447 | 166.48 | 5.5305 | 60.866 | 0.014949 | 134.58 | 1133.2 | 998.62
13448 | 5.5318 | 166.49 | 60.866 | 0.014952 | 134.59 | 1133.2 |  | 13448 | 166.49 | 5.5318 | 60.866 | 0.014952 | 134.59 | 1133.2 | 998.61
13449 | 5.5331 | 166.5 | 60.866 | 0.014956 | 134.6 | 1133.2 |  | 13449 | 166.5 | 5.5331 | 60.866 | 0.014956 | 134.6 | 1133.2 | 998.6
13450 | 5.5343 | 166.51 | 60.866 | 0.014959 | 134.61 | 1133.2 |  | 13450 | 166.51 | 5.5343 | 60.866 | 0.014959 | 134.61 | 1133.2 | 998.59
13451 | 5.5356 | 166.52 | 60.866 | 0.014962 | 134.62 | 1133.2 |  | 13451 | 166.52 | 5.5356 | 60.866 | 0.014962 | 134.62 | 1133.2 | 998.58
13452 | 5.5369 | 166.53 | 60.865 | 0.014966 | 134.63 | 1133.2 |  | 13452 | 166.53 | 5.5369 | 60.865 | 0.014966 | 134.63 | 1133.2 | 998.57
13453 | 5.5382 | 166.54 | 60.865 | 0.014969 | 134.64 | 1133.2 |  | 13453 | 166.54 | 5.5382 | 60.865 | 0.014969 | 134.64 | 1133.2 | 998.56
13454 | 5.5395 | 166.55 | 60.865 | 0.014972 | 134.65 | 1133.3 |  | 13454 | 166.55 | 5.5395 | 60.865 | 0.014972 | 134.65 | 1133.3 | 998.65
13455 | 5.5408 | 166.56 | 60.865 | 0.014975 | 134.66 | 1133.3 |  | 13455 | 166.56 | 5.5408 | 60.865 | 0.014975 | 134.66 | 1133.3 | 998.64
13456 | 5.5421 | 166.57 | 60.865 | 0.014979 | 134.67 | 1133.3 |  | 13456 | 166.57 | 5.5421 | 60.865 | 0.014979 | 134.67 | 1133.3 | 998.63
13457 | 5.5434 | 166.58 | 60.864 | 0.014982 | 134.68 | 1133.3 |  | 13457 | 166.58 | 5.5434 | 60.864 | 0.014982 | 134.68 | 1133.3 | 998.62
13458 | 5.5447 | 166.59 | 60.864 | 0.014985 | 134.69 | 1133.3 |  | 13458 | 166.59 | 5.5447 | 60.864 | 0.014985 | 134.69 | 1133.3 | 998.61
13459 | 5.5459 | 166.6 | 60.864 | 0.014988 | 134.7 | 1133.3 |  | 13459 | 166.6 | 5.5459 | 60.864 | 0.014988 | 134.7 | 1133.3 | 998.6
13460 | 5.5472 | 166.61 | 60.864 | 0.014992 | 134.71 | 1133.3 |  | 13460 | 166.61 | 5.5472 | 60.864 | 0.014992 | 134.71 | 1133.3 | 998.59
13461 | 5.5485 | 166.62 | 60.864 | 0.014995 | 134.72 | 1133.3 |  | 13461 | 166.62 | 5.5485 | 60.864 | 0.014995 | 134.72 | 1133.3 | 998.58
13462 | 5.5498 | 166.63 | 60.863 | 0.014998 | 134.73 | 1133.3 |  | 13462 | 166.63 | 5.5498 | 60.863 | 0.014998 | 134.73 | 1133.3 | 998.57
13463 | 5.5511 | 166.64 | 60.863 | 0.015001 | 134.74 | 1133.3 |  | 13463 | 166.64 | 5.5511 | 60.863 | 0.015001 | 134.74 | 1133.3 | 998.56
13464 | 5.5524 | 166.65 | 60.863 | 0.015005 | 134.75 | 1133.3 |  | 13464 | 166.65 | 5.5524 | 60.863 | 0.015005 | 134.75 | 1133.3 | 998.55
13465 | 5.5537 | 166.66 | 60.863 | 0.015008 | 134.76 | 1133.3 |  | 13465 | 166.66 | 5.5537 | 60.863 | 0.015008 | 134.76 | 1133.3 | 998.54
13466 | 5.555 | 166.67 | 60.863 | 0.015011 | 134.77 | 1133.3 |  | 13466 | 166.67 | 5.555 | 60.863 | 0.015011 | 134.77 | 1133.3 | 998.53
13467 | 5.5563 | 166.68 | 60.862 | 0.015015 | 134.78 | 1133.3 |  | 13467 | 166.68 | 5.5563 | 60.862 | 0.015015 | 134.78 | 1133.3 | 998.52
13468 | 5.5576 | 166.69 | 60.862 | 0.015018 | 134.79 | 1133.3 |  | 13468 | 166.69 | 5.5576 | 60.862 | 0.015018 | 134.79 | 1133.3 | 998.51
13469 | 5.5589 | 166.7 | 60.862 | 0.015021 | 134.8 | 1133.3 |  | 13469 | 166.7 | 5.5589 | 60.862 | 0.015021 | 134.8 | 1133.3 | 998.5
13470 | 5.5602 | 166.71 | 60.862 | 0.015024 | 134.81 | 1133.3 |  | 13470 | 166.71 | 5.5602 | 60.862 | 0.015024 | 134.81 | 1133.3 | 998.49
13471 | 5.5615 | 166.72 | 60.862 | 0.015028 | 134.82 | 1133.3 |  | 13471 | 166.72 | 5.5615 | 60.862 | 0.015028 | 134.82 | 1133.3 | 998.48
13472 | 5.5628 | 166.73 | 60.861 | 0.015031 | 134.83 | 1133.3 |  | 13472 | 166.73 | 5.5628 | 60.861 | 0.015031 | 134.83 | 1133.3 | 998.47
13473 | 5.564 | 166.74 | 60.861 | 0.015034 | 134.84 | 1133.3 |  | 13473 | 166.74 | 5.564 | 60.861 | 0.015034 | 134.84 | 1133.3 | 998.46
13474 | 5.5653 | 166.75 | 60.861 | 0.015037 | 134.85 | 1133.3 |  | 13474 | 166.75 | 5.5653 | 60.861 | 0.015037 | 134.85 | 1133.3 | 998.45
13475 | 5.5666 | 166.76 | 60.861 | 0.015041 | 134.86 | 1133.3 |  | 13475 | 166.76 | 5.5666 | 60.861 | 0.015041 | 134.86 | 1133.3 | 998.44
13476 | 5.5679 | 166.77 | 60.86 | 0.015044 | 134.87 | 1133.3 |  | 13476 | 166.77 | 5.5679 | 60.86 | 0.015044 | 134.87 | 1133.3 | 998.43
13477 | 5.5692 | 166.78 | 60.86 | 0.015047 | 134.88 | 1133.3 |  | 13477 | 166.78 | 5.5692 | 60.86 | 0.015047 | 134.88 | 1133.3 | 998.42
13478 | 5.5705 | 166.79 | 60.86 | 0.015051 | 134.89 | 1133.3 |  | 13478 | 166.79 | 5.5705 | 60.86 | 0.015051 | 134.89 | 1133.3 | 998.41
13479 | 5.5718 | 166.8 | 60.86 | 0.015054 | 134.9 | 1133.4 |  | 13479 | 166.8 | 5.5718 | 60.86 | 0.015054 | 134.9 | 1133.4 | 998.5
13480 | 5.5731 | 166.81 | 60.86 | 0.015057 | 134.91 | 1133.4 |  | 13480 | 166.81 | 5.5731 | 60.86 | 0.015057 | 134.91 | 1133.4 | 998.49
13481 | 5.5744 | 166.82 | 60.859 | 0.01506 | 134.92 | 1133.4 |  | 13481 | 166.82 | 5.5744 | 60.859 | 0.01506 | 134.92 | 1133.4 | 998.48
13482 | 5.5757 | 166.83 | 60.859 | 0.015064 | 134.93 | 1133.4 |  | 13482 | 166.83 | 5.5757 | 60.859 | 0.015064 | 134.93 | 1133.4 | 998.47
13483 | 5.577 | 166.84 | 60.859 | 0.015067 | 134.94 | 1133.4 |  | 13483 | 166.84 | 5.577 | 60.859 | 0.015067 | 134.94 | 1133.4 | 998.46
13484 | 5.5783 | 166.85 | 60.859 | 0.01507 | 134.95 | 1133.4 |  | 13484 | 166.85 | 5.5783 | 60.859 | 0.01507 | 134.95 | 1133.4 | 998.45
13485 | 5.5796 | 166.86 | 60.859 | 0.015074 | 134.96 | 1133.4 |  | 13485 | 166.86 | 5.5796 | 60.859 | 0.015074 | 134.96 | 1133.4 | 998.44
13486 | 5.5809 | 166.87 | 60.858 | 0.015077 | 134.97 | 1133.4 |  | 13486 | 166.87 | 5.5809 | 60.858 | 0.015077 | 134.97 | 1133.4 | 998.43
13487 | 5.5822 | 166.88 | 60.858 | 0.01508 | 134.98 | 1133.4 |  | 13487 | 166.88 | 5.5822 | 60.858 | 0.01508 | 134.98 | 1133.4 | 998.42
13488 | 5.5835 | 166.89 | 60.858 | 0.015083 | 134.99 | 1133.4 |  | 13488 | 166.89 | 5.5835 | 60.858 | 0.015083 | 134.99 | 1133.4 | 998.41
13489 | 5.5848 | 166.9 | 60.858 | 0.015087 | 135 | 1133.4 |  | 13489 | 166.9 | 5.5848 | 60.858 | 0.015087 | 135 | 1133.4 | 998.4
13490 | 5.5861 | 166.91 | 60.858 | 0.01509 | 135.01 | 1133.4 |  | 13490 | 166.91 | 5.5861 | 60.858 | 0.01509 | 135.01 | 1133.4 | 998.39
13491 | 5.5874 | 166.92 | 60.857 | 0.015093 | 135.02 | 1133.4 |  | 13491 | 166.92 | 5.5874 | 60.857 | 0.015093 | 135.02 | 1133.4 | 998.38
13492 | 5.5887 | 166.93 | 60.857 | 0.015097 | 135.03 | 1133.4 |  | 13492 | 166.93 | 5.5887 | 60.857 | 0.015097 | 135.03 | 1133.4 | 998.37
13493 | 5.59 | 166.94 | 60.857 | 0.0151 | 135.04 | 1133.4 |  | 13493 | 166.94 | 5.59 | 60.857 | 0.0151 | 135.04 | 1133.4 | 998.36
13494 | 5.5913 | 166.95 | 60.857 | 0.015103 | 135.05 | 1133.4 |  | 13494 | 166.95 | 5.5913 | 60.857 | 0.015103 | 135.05 | 1133.4 | 998.35
13495 | 5.5926 | 166.96 | 60.857 | 0.015106 | 135.06 | 1133.4 |  | 13495 | 166.96 | 5.5926 | 60.857 | 0.015106 | 135.06 | 1133.4 | 998.34
13496 | 5.5939 | 166.97 | 60.856 | 0.01511 | 135.07 | 1133.4 |  | 13496 | 166.97 | 5.5939 | 60.856 | 0.01511 | 135.07 | 1133.4 | 998.33
13497 | 5.5952 | 166.98 | 60.856 | 0.015113 | 135.08 | 1133.4 |  | 13497 | 166.98 | 5.5952 | 60.856 | 0.015113 | 135.08 | 1133.4 | 998.32
13498 | 5.5965 | 166.99 | 60.856 | 0.015116 | 135.09 | 1133.4 |  | 13498 | 166.99 | 5.5965 | 60.856 | 0.015116 | 135.09 | 1133.4 | 998.31
13499 | 5.5978 | 167 | 60.856 | 0.01512 | 135.1 | 1133.4 |  | 13499 | 167 | 5.5978 | 60.856 | 0.01512 | 135.1 | 1133.4 | 998.3
13500 | 5.5991 | 167.01 | 60.856 | 0.015123 | 135.11 | 1133.4 |  | 13500 | 167.01 | 5.5991 | 60.856 | 0.015123 | 135.11 | 1133.4 | 998.29
13501 | 5.6004 | 167.02 | 60.855 | 0.015126 | 135.12 | 1133.4 |  | 13501 | 167.02 | 5.6004 | 60.855 | 0.015126 | 135.12 | 1133.4 | 998.28
13502 | 5.6017 | 167.03 | 60.855 | 0.015129 | 135.13 | 1133.4 |  | 13502 | 167.03 | 5.6017 | 60.855 | 0.015129 | 135.13 | 1133.4 | 998.27
13503 | 5.603 | 167.04 | 60.855 | 0.015133 | 135.14 | 1133.4 |  | 13503 | 167.04 | 5.603 | 60.855 | 0.015133 | 135.14 | 1133.4 | 998.26
13504 | 5.6043 | 167.05 | 60.855 | 0.015136 | 135.15 | 1133.5 |  | 13504 | 167.05 | 5.6043 | 60.855 | 0.015136 | 135.15 | 1133.5 | 998.35
13505 | 5.6056 | 167.06 | 60.854 | 0.015139 | 135.16 | 1133.5 |  | 13505 | 167.06 | 5.6056 | 60.854 | 0.015139 | 135.16 | 1133.5 | 998.34
13506 | 5.6069 | 167.07 | 60.854 | 0.015143 | 135.17 | 1133.5 |  | 13506 | 167.07 | 5.6069 | 60.854 | 0.015143 | 135.17 | 1133.5 | 998.33
13507 | 5.6082 | 167.08 | 60.854 | 0.015146 | 135.18 | 1133.5 |  | 13507 | 167.08 | 5.6082 | 60.854 | 0.015146 | 135.18 | 1133.5 | 998.32
13508 | 5.6095 | 167.09 | 60.854 | 0.015149 | 135.19 | 1133.5 |  | 13508 | 167.09 | 5.6095 | 60.854 | 0.015149 | 135.19 | 1133.5 | 998.31
13509 | 5.6108 | 167.1 | 60.854 | 0.015153 | 135.2 | 1133.5 |  | 13509 | 167.1 | 5.6108 | 60.854 | 0.015153 | 135.2 | 1133.5 | 998.3
13510 | 5.6121 | 167.11 | 60.853 | 0.015156 | 135.21 | 1133.5 |  | 13510 | 167.11 | 5.6121 | 60.853 | 0.015156 | 135.21 | 1133.5 | 998.29
13511 | 5.6134 | 167.12 | 60.853 | 0.015159 | 135.22 | 1133.5 |  | 13511 | 167.12 | 5.6134 | 60.853 | 0.015159 | 135.22 | 1133.5 | 998.28
13512 | 5.6147 | 167.13 | 60.853 | 0.015162 | 135.23 | 1133.5 |  | 13512 | 167.13 | 5.6147 | 60.853 | 0.015162 | 135.23 | 1133.5 | 998.27
13513 | 5.616 | 167.14 | 60.853 | 0.015166 | 135.24 | 1133.5 |  | 13513 | 167.14 | 5.616 | 60.853 | 0.015166 | 135.24 | 1133.5 | 998.26
13514 | 5.6173 | 167.15 | 60.853 | 0.015169 | 135.25 | 1133.5 |  | 13514 | 167.15 | 5.6173 | 60.853 | 0.015169 | 135.25 | 1133.5 | 998.25
13515 | 5.6186 | 167.16 | 60.852 | 0.015172 | 135.26 | 1133.5 |  | 13515 | 167.16 | 5.6186 | 60.852 | 0.015172 | 135.26 | 1133.5 | 998.24
13516 | 5.6199 | 167.17 | 60.852 | 0.015176 | 135.27 | 1133.5 |  | 13516 | 167.17 | 5.6199 | 60.852 | 0.015176 | 135.27 | 1133.5 | 998.23
13517 | 5.6212 | 167.18 | 60.852 | 0.015179 | 135.28 | 1133.5 |  | 13517 | 167.18 | 5.6212 | 60.852 | 0.015179 | 135.28 | 1133.5 | 998.22
13518 | 5.6226 | 167.19 | 60.852 | 0.015182 | 135.29 | 1133.5 |  | 13518 | 167.19 | 5.6226 | 60.852 | 0.015182 | 135.29 | 1133.5 | 998.21
13519 | 5.6239 | 167.2 | 60.852 | 0.015186 | 135.3 | 1133.5 |  | 13519 | 167.2 | 5.6239 | 60.852 | 0.015186 | 135.3 | 1133.5 | 998.2
13520 | 5.6252 | 167.21 | 60.851 | 0.015189 | 135.31 | 1133.5 |  | 13520 | 167.21 | 5.6252 | 60.851 | 0.015189 | 135.31 | 1133.5 | 998.19
13521 | 5.6265 | 167.22 | 60.851 | 0.015192 | 135.32 | 1133.5 |  | 13521 | 167.22 | 5.6265 | 60.851 | 0.015192 | 135.32 | 1133.5 | 998.18
13522 | 5.6278 | 167.23 | 60.851 | 0.015195 | 135.33 | 1133.5 |  | 13522 | 167.23 | 5.6278 | 60.851 | 0.015195 | 135.33 | 1133.5 | 998.17
13523 | 5.6291 | 167.24 | 60.851 | 0.015199 | 135.34 | 1133.5 |  | 13523 | 167.24 | 5.6291 | 60.851 | 0.015199 | 135.34 | 1133.5 | 998.16
13524 | 5.6304 | 167.25 | 60.851 | 0.015202 | 135.35 | 1133.5 |  | 13524 | 167.25 | 5.6304 | 60.851 | 0.015202 | 135.35 | 1133.5 | 998.15
13525 | 5.6317 | 167.26 | 60.85 | 0.015205 | 135.36 | 1133.5 |  | 13525 | 167.26 | 5.6317 | 60.85 | 0.015205 | 135.36 | 1133.5 | 998.14
13526 | 5.633 | 167.27 | 60.85 | 0.015209 | 135.37 | 1133.5 |  | 13526 | 167.27 | 5.633 | 60.85 | 0.015209 | 135.37 | 1133.5 | 998.13
13527 | 5.6343 | 167.28 | 60.85 | 0.015212 | 135.38 | 1133.5 |  | 13527 | 167.28 | 5.6343 | 60.85 | 0.015212 | 135.38 | 1133.5 | 998.12
13528 | 5.6356 | 167.29 | 60.85 | 0.015215 | 135.39 | 1133.6 |  | 13528 | 167.29 | 5.6356 | 60.85 | 0.015215 | 135.39 | 1133.6 | 998.21
13529 | 5.6369 | 167.3 | 60.849 | 0.015219 | 135.4 | 1133.6 |  | 13529 | 167.3 | 5.6369 | 60.849 | 0.015219 | 135.4 | 1133.6 | 998.2
13530 | 5.6382 | 167.31 | 60.849 | 0.015222 | 135.41 | 1133.6 |  | 13530 | 167.31 | 5.6382 | 60.849 | 0.015222 | 135.41 | 1133.6 | 998.19
13531 | 5.6396 | 167.32 | 60.849 | 0.015225 | 135.42 | 1133.6 |  | 13531 | 167.32 | 5.6396 | 60.849 | 0.015225 | 135.42 | 1133.6 | 998.18
13532 | 5.6409 | 167.33 | 60.849 | 0.015229 | 135.43 | 1133.6 |  | 13532 | 167.33 | 5.6409 | 60.849 | 0.015229 | 135.43 | 1133.6 | 998.17
13533 | 5.6422 | 167.34 | 60.849 | 0.015232 | 135.44 | 1133.6 |  | 13533 | 167.34 | 5.6422 | 60.849 | 0.015232 | 135.44 | 1133.6 | 998.16
13534 | 5.6435 | 167.35 | 60.848 | 0.015235 | 135.45 | 1133.6 |  | 13534 | 167.35 | 5.6435 | 60.848 | 0.015235 | 135.45 | 1133.6 | 998.15
13535 | 5.6448 | 167.36 | 60.848 | 0.015238 | 135.46 | 1133.6 |  | 13535 | 167.36 | 5.6448 | 60.848 | 0.015238 | 135.46 | 1133.6 | 998.14
13536 | 5.6461 | 167.37 | 60.848 | 0.015242 | 135.47 | 1133.6 |  | 13536 | 167.37 | 5.6461 | 60.848 | 0.015242 | 135.47 | 1133.6 | 998.13
13537 | 5.6474 | 167.38 | 60.848 | 0.015245 | 135.48 | 1133.6 |  | 13537 | 167.38 | 5.6474 | 60.848 | 0.015245 | 135.48 | 1133.6 | 998.12
13538 | 5.6487 | 167.39 | 60.848 | 0.015248 | 135.49 | 1133.6 |  | 13538 | 167.39 | 5.6487 | 60.848 | 0.015248 | 135.49 | 1133.6 | 998.11
13539 | 5.65 | 167.4 | 60.847 | 0.015252 | 135.5 | 1133.6 |  | 13539 | 167.4 | 5.65 | 60.847 | 0.015252 | 135.5 | 1133.6 | 998.1
13540 | 5.6513 | 167.41 | 60.847 | 0.015255 | 135.51 | 1133.6 |  | 13540 | 167.41 | 5.6513 | 60.847 | 0.015255 | 135.51 | 1133.6 | 998.09
13541 | 5.6527 | 167.42 | 60.847 | 0.015258 | 135.52 | 1133.6 |  | 13541 | 167.42 | 5.6527 | 60.847 | 0.015258 | 135.52 | 1133.6 | 998.08
13542 | 5.654 | 167.43 | 60.847 | 0.015262 | 135.53 | 1133.6 |  | 13542 | 167.43 | 5.654 | 60.847 | 0.015262 | 135.53 | 1133.6 | 998.07
13543 | 5.6553 | 167.44 | 60.847 | 0.015265 | 135.54 | 1133.6 |  | 13543 | 167.44 | 5.6553 | 60.847 | 0.015265 | 135.54 | 1133.6 | 998.06
13544 | 5.6566 | 167.45 | 60.846 | 0.015268 | 135.55 | 1133.6 |  | 13544 | 167.45 | 5.6566 | 60.846 | 0.015268 | 135.55 | 1133.6 | 998.05
13545 | 5.6579 | 167.46 | 60.846 | 0.015272 | 135.56 | 1133.6 |  | 13545 | 167.46 | 5.6579 | 60.846 | 0.015272 | 135.56 | 1133.6 | 998.04
13546 | 5.6592 | 167.47 | 60.846 | 0.015275 | 135.57 | 1133.6 |  | 13546 | 167.47 | 5.6592 | 60.846 | 0.015275 | 135.57 | 1133.6 | 998.03
13547 | 5.6605 | 167.48 | 60.846 | 0.015278 | 135.58 | 1133.6 |  | 13547 | 167.48 | 5.6605 | 60.846 | 0.015278 | 135.58 | 1133.6 | 998.02
13548 | 5.6618 | 167.49 | 60.846 | 0.015282 | 135.59 | 1133.6 |  | 13548 | 167.49 | 5.6618 | 60.846 | 0.015282 | 135.59 | 1133.6 | 998.01
13549 | 5.6632 | 167.5 | 60.845 | 0.015285 | 135.6 | 1133.6 |  | 13549 | 167.5 | 5.6632 | 60.845 | 0.015285 | 135.6 | 1133.6 | 998
13550 | 5.6645 | 167.51 | 60.845 | 0.015288 | 135.61 | 1133.6 |  | 13550 | 167.51 | 5.6645 | 60.845 | 0.015288 | 135.61 | 1133.6 | 997.99
13551 | 5.6658 | 167.52 | 60.845 | 0.015292 | 135.62 | 1133.6 |  | 13551 | 167.52 | 5.6658 | 60.845 | 0.015292 | 135.62 | 1133.6 | 997.98
13552 | 5.6671 | 167.53 | 60.845 | 0.015295 | 135.63 | 1133.6 |  | 13552 | 167.53 | 5.6671 | 60.845 | 0.015295 | 135.63 | 1133.6 | 997.97
13553 | 5.6684 | 167.54 | 60.845 | 0.015298 | 135.64 | 1133.7 |  | 13553 | 167.54 | 5.6684 | 60.845 | 0.015298 | 135.64 | 1133.7 | 998.06
13554 | 5.6697 | 167.55 | 60.844 | 0.015302 | 135.65 | 1133.7 |  | 13554 | 167.55 | 5.6697 | 60.844 | 0.015302 | 135.65 | 1133.7 | 998.05
13555 | 5.6711 | 167.56 | 60.844 | 0.015305 | 135.66 | 1133.7 |  | 13555 | 167.56 | 5.6711 | 60.844 | 0.015305 | 135.66 | 1133.7 | 998.04
13556 | 5.6724 | 167.57 | 60.844 | 0.015308 | 135.67 | 1133.7 |  | 13556 | 167.57 | 5.6724 | 60.844 | 0.015308 | 135.67 | 1133.7 | 998.03
13557 | 5.6737 | 167.58 | 60.844 | 0.015312 | 135.68 | 1133.7 |  | 13557 | 167.58 | 5.6737 | 60.844 | 0.015312 | 135.68 | 1133.7 | 998.02
13558 | 5.675 | 167.59 | 60.843 | 0.015315 | 135.69 | 1133.7 |  | 13558 | 167.59 | 5.675 | 60.843 | 0.015315 | 135.69 | 1133.7 | 998.01
13559 | 5.6763 | 167.6 | 60.843 | 0.015318 | 135.7 | 1133.7 |  | 13559 | 167.6 | 5.6763 | 60.843 | 0.015318 | 135.7 | 1133.7 | 998
13560 | 5.6776 | 167.61 | 60.843 | 0.015322 | 135.71 | 1133.7 |  | 13560 | 167.61 | 5.6776 | 60.843 | 0.015322 | 135.71 | 1133.7 | 997.99
13561 | 5.6789 | 167.62 | 60.843 | 0.015325 | 135.72 | 1133.7 |  | 13561 | 167.62 | 5.6789 | 60.843 | 0.015325 | 135.72 | 1133.7 | 997.98
13562 | 5.6803 | 167.63 | 60.843 | 0.015328 | 135.73 | 1133.7 |  | 13562 | 167.63 | 5.6803 | 60.843 | 0.015328 | 135.73 | 1133.7 | 997.97
13563 | 5.6816 | 167.64 | 60.842 | 0.015332 | 135.74 | 1133.7 |  | 13563 | 167.64 | 5.6816 | 60.842 | 0.015332 | 135.74 | 1133.7 | 997.96
13564 | 5.6829 | 167.65 | 60.842 | 0.015335 | 135.75 | 1133.7 |  | 13564 | 167.65 | 5.6829 | 60.842 | 0.015335 | 135.75 | 1133.7 | 997.95
13565 | 5.6842 | 167.66 | 60.842 | 0.015338 | 135.76 | 1133.7 |  | 13565 | 167.66 | 5.6842 | 60.842 | 0.015338 | 135.76 | 1133.7 | 997.94
13566 | 5.6855 | 167.67 | 60.842 | 0.015341 | 135.77 | 1133.7 |  | 13566 | 167.67 | 5.6855 | 60.842 | 0.015341 | 135.77 | 1133.7 | 997.93
13567 | 5.6869 | 167.68 | 60.842 | 0.015345 | 135.78 | 1133.7 |  | 13567 | 167.68 | 5.6869 | 60.842 | 0.015345 | 135.78 | 1133.7 | 997.92
13568 | 5.6882 | 167.69 | 60.841 | 0.015348 | 135.79 | 1133.7 |  | 13568 | 167.69 | 5.6882 | 60.841 | 0.015348 | 135.79 | 1133.7 | 997.91
13569 | 5.6895 | 167.7 | 60.841 | 0.015351 | 135.8 | 1133.7 |  | 13569 | 167.7 | 5.6895 | 60.841 | 0.015351 | 135.8 | 1133.7 | 997.9
13570 | 5.6908 | 167.71 | 60.841 | 0.015355 | 135.81 | 1133.7 |  | 13570 | 167.71 | 5.6908 | 60.841 | 0.015355 | 135.81 | 1133.7 | 997.89
13571 | 5.6921 | 167.72 | 60.841 | 0.015358 | 135.82 | 1133.7 |  | 13571 | 167.72 | 5.6921 | 60.841 | 0.015358 | 135.82 | 1133.7 | 997.88
13572 | 5.6934 | 167.73 | 60.841 | 0.015361 | 135.83 | 1133.7 |  | 13572 | 167.73 | 5.6934 | 60.841 | 0.015361 | 135.83 | 1133.7 | 997.87
13573 | 5.6948 | 167.74 | 60.84 | 0.015365 | 135.84 | 1133.7 |  | 13573 | 167.74 | 5.6948 | 60.84 | 0.015365 | 135.84 | 1133.7 | 997.86
13574 | 5.6961 | 167.75 | 60.84 | 0.015368 | 135.85 | 1133.7 |  | 13574 | 167.75 | 5.6961 | 60.84 | 0.015368 | 135.85 | 1133.7 | 997.85
13575 | 5.6974 | 167.76 | 60.84 | 0.015372 | 135.86 | 1133.7 |  | 13575 | 167.76 | 5.6974 | 60.84 | 0.015372 | 135.86 | 1133.7 | 997.84
13576 | 5.6987 | 167.77 | 60.84 | 0.015375 | 135.87 | 1133.7 |  | 13576 | 167.77 | 5.6987 | 60.84 | 0.015375 | 135.87 | 1133.7 | 997.83
13577 | 5.7001 | 167.78 | 60.84 | 0.015378 | 135.88 | 1133.7 |  | 13577 | 167.78 | 5.7001 | 60.84 | 0.015378 | 135.88 | 1133.7 | 997.82
13578 | 5.7014 | 167.79 | 60.839 | 0.015382 | 135.89 | 1133.8 |  | 13578 | 167.79 | 5.7014 | 60.839 | 0.015382 | 135.89 | 1133.8 | 997.91
13579 | 5.7027 | 167.8 | 60.839 | 0.015385 | 135.9 | 1133.8 |  | 13579 | 167.8 | 5.7027 | 60.839 | 0.015385 | 135.9 | 1133.8 | 997.9
13580 | 5.704 | 167.81 | 60.839 | 0.015388 | 135.91 | 1133.8 |  | 13580 | 167.81 | 5.704 | 60.839 | 0.015388 | 135.91 | 1133.8 | 997.89
13581 | 5.7053 | 167.82 | 60.839 | 0.015392 | 135.92 | 1133.8 |  | 13581 | 167.82 | 5.7053 | 60.839 | 0.015392 | 135.92 | 1133.8 | 997.88
13582 | 5.7067 | 167.83 | 60.838 | 0.015395 | 135.93 | 1133.8 |  | 13582 | 167.83 | 5.7067 | 60.838 | 0.015395 | 135.93 | 1133.8 | 997.87
13583 | 5.708 | 167.84 | 60.838 | 0.015398 | 135.94 | 1133.8 |  | 13583 | 167.84 | 5.708 | 60.838 | 0.015398 | 135.94 | 1133.8 | 997.86
13584 | 5.7093 | 167.85 | 60.838 | 0.015402 | 135.95 | 1133.8 |  | 13584 | 167.85 | 5.7093 | 60.838 | 0.015402 | 135.95 | 1133.8 | 997.85
13585 | 5.7106 | 167.86 | 60.838 | 0.015405 | 135.96 | 1133.8 |  | 13585 | 167.86 | 5.7106 | 60.838 | 0.015405 | 135.96 | 1133.8 | 997.84
13586 | 5.712 | 167.87 | 60.838 | 0.015408 | 135.97 | 1133.8 |  | 13586 | 167.87 | 5.712 | 60.838 | 0.015408 | 135.97 | 1133.8 | 997.83
13587 | 5.7133 | 167.88 | 60.837 | 0.015412 | 135.98 | 1133.8 |  | 13587 | 167.88 | 5.7133 | 60.837 | 0.015412 | 135.98 | 1133.8 | 997.82
13588 | 5.7146 | 167.89 | 60.837 | 0.015415 | 135.99 | 1133.8 |  | 13588 | 167.89 | 5.7146 | 60.837 | 0.015415 | 135.99 | 1133.8 | 997.81
13589 | 5.7159 | 167.9 | 60.837 | 0.015418 | 136 | 1133.8 |  | 13589 | 167.9 | 5.7159 | 60.837 | 0.015418 | 136 | 1133.8 | 997.8
13590 | 5.7172 | 167.91 | 60.837 | 0.015422 | 136.01 | 1133.8 |  | 13590 | 167.91 | 5.7172 | 60.837 | 0.015422 | 136.01 | 1133.8 | 997.79
13591 | 5.7186 | 167.92 | 60.837 | 0.015425 | 136.02 | 1133.8 |  | 13591 | 167.92 | 5.7186 | 60.837 | 0.015425 | 136.02 | 1133.8 | 997.78
13592 | 5.7199 | 167.93 | 60.836 | 0.015428 | 136.03 | 1133.8 |  | 13592 | 167.93 | 5.7199 | 60.836 | 0.015428 | 136.03 | 1133.8 | 997.77
13593 | 5.7212 | 167.94 | 60.836 | 0.015432 | 136.04 | 1133.8 |  | 13593 | 167.94 | 5.7212 | 60.836 | 0.015432 | 136.04 | 1133.8 | 997.76
13594 | 5.7225 | 167.95 | 60.836 | 0.015435 | 136.05 | 1133.8 |  | 13594 | 167.95 | 5.7225 | 60.836 | 0.015435 | 136.05 | 1133.8 | 997.75
13595 | 5.7239 | 167.96 | 60.836 | 0.015438 | 136.06 | 1133.8 |  | 13595 | 167.96 | 5.7239 | 60.836 | 0.015438 | 136.06 | 1133.8 | 997.74
13596 | 5.7252 | 167.97 | 60.836 | 0.015442 | 136.07 | 1133.8 |  | 13596 | 167.97 | 5.7252 | 60.836 | 0.015442 | 136.07 | 1133.8 | 997.73
13597 | 5.7265 | 167.98 | 60.835 | 0.015445 | 136.08 | 1133.8 |  | 13597 | 167.98 | 5.7265 | 60.835 | 0.015445 | 136.08 | 1133.8 | 997.72
13598 | 5.7279 | 167.99 | 60.835 | 0.015448 | 136.09 | 1133.8 |  | 13598 | 167.99 | 5.7279 | 60.835 | 0.015448 | 136.09 | 1133.8 | 997.71
13599 | 5.7292 | 168 | 60.835 | 0.015452 | 136.1 | 1133.8 |  | 13599 | 168 | 5.7292 | 60.835 | 0.015452 | 136.1 | 1133.8 | 997.7
13600 | 5.7305 | 168.01 | 60.835 | 0.015455 | 136.11 | 1133.8 |  | 13600 | 168.01 | 5.7305 | 60.835 | 0.015455 | 136.11 | 1133.8 | 997.69
13601 | 5.7318 | 168.02 | 60.835 | 0.015458 | 136.12 | 1133.8 |  | 13601 | 168.02 | 5.7318 | 60.835 | 0.015458 | 136.12 | 1133.8 | 997.68
13602 | 5.7332 | 168.03 | 60.834 | 0.015462 | 136.13 | 1133.8 |  | 13602 | 168.03 | 5.7332 | 60.834 | 0.015462 | 136.13 | 1133.8 | 997.67
13603 | 5.7345 | 168.04 | 60.834 | 0.015465 | 136.14 | 1133.9 |  | 13603 | 168.04 | 5.7345 | 60.834 | 0.015465 | 136.14 | 1133.9 | 997.76
13604 | 5.7358 | 168.05 | 60.834 | 0.015469 | 136.15 | 1133.9 |  | 13604 | 168.05 | 5.7358 | 60.834 | 0.015469 | 136.15 | 1133.9 | 997.75
13605 | 5.7371 | 168.06 | 60.834 | 0.015472 | 136.16 | 1133.9 |  | 13605 | 168.06 | 5.7371 | 60.834 | 0.015472 | 136.16 | 1133.9 | 997.74
13606 | 5.7385 | 168.07 | 60.834 | 0.015475 | 136.17 | 1133.9 |  | 13606 | 168.07 | 5.7385 | 60.834 | 0.015475 | 136.17 | 1133.9 | 997.73
13607 | 5.7398 | 168.08 | 60.833 | 0.015479 | 136.18 | 1133.9 |  | 13607 | 168.08 | 5.7398 | 60.833 | 0.015479 | 136.18 | 1133.9 | 997.72
13608 | 5.7411 | 168.09 | 60.833 | 0.015482 | 136.19 | 1133.9 |  | 13608 | 168.09 | 5.7411 | 60.833 | 0.015482 | 136.19 | 1133.9 | 997.71
13609 | 5.7425 | 168.1 | 60.833 | 0.015485 | 136.2 | 1133.9 |  | 13609 | 168.1 | 5.7425 | 60.833 | 0.015485 | 136.2 | 1133.9 | 997.7
13610 | 5.7438 | 168.11 | 60.833 | 0.015489 | 136.21 | 1133.9 |  | 13610 | 168.11 | 5.7438 | 60.833 | 0.015489 | 136.21 | 1133.9 | 997.69
13611 | 5.7451 | 168.12 | 60.832 | 0.015492 | 136.22 | 1133.9 |  | 13611 | 168.12 | 5.7451 | 60.832 | 0.015492 | 136.22 | 1133.9 | 997.68
13612 | 5.7464 | 168.13 | 60.832 | 0.015495 | 136.23 | 1133.9 |  | 13612 | 168.13 | 5.7464 | 60.832 | 0.015495 | 136.23 | 1133.9 | 997.67
13613 | 5.7478 | 168.14 | 60.832 | 0.015499 | 136.24 | 1133.9 |  | 13613 | 168.14 | 5.7478 | 60.832 | 0.015499 | 136.24 | 1133.9 | 997.66
13614 | 5.7491 | 168.15 | 60.832 | 0.015502 | 136.25 | 1133.9 |  | 13614 | 168.15 | 5.7491 | 60.832 | 0.015502 | 136.25 | 1133.9 | 997.65
13615 | 5.7504 | 168.16 | 60.832 | 0.015505 | 136.26 | 1133.9 |  | 13615 | 168.16 | 5.7504 | 60.832 | 0.015505 | 136.26 | 1133.9 | 997.64
13616 | 5.7518 | 168.17 | 60.831 | 0.015509 | 136.27 | 1133.9 |  | 13616 | 168.17 | 5.7518 | 60.831 | 0.015509 | 136.27 | 1133.9 | 997.63
13617 | 5.7531 | 168.18 | 60.831 | 0.015512 | 136.28 | 1133.9 |  | 13617 | 168.18 | 5.7531 | 60.831 | 0.015512 | 136.28 | 1133.9 | 997.62
13618 | 5.7544 | 168.19 | 60.831 | 0.015516 | 136.29 | 1133.9 |  | 13618 | 168.19 | 5.7544 | 60.831 | 0.015516 | 136.29 | 1133.9 | 997.61
13619 | 5.7558 | 168.2 | 60.831 | 0.015519 | 136.3 | 1133.9 |  | 13619 | 168.2 | 5.7558 | 60.831 | 0.015519 | 136.3 | 1133.9 | 997.6
13620 | 5.7571 | 168.21 | 60.831 | 0.015522 | 136.31 | 1133.9 |  | 13620 | 168.21 | 5.7571 | 60.831 | 0.015522 | 136.31 | 1133.9 | 997.59
13621 | 5.7584 | 168.22 | 60.83 | 0.015526 | 136.32 | 1133.9 |  | 13621 | 168.22 | 5.7584 | 60.83 | 0.015526 | 136.32 | 1133.9 | 997.58
13622 | 5.7598 | 168.23 | 60.83 | 0.015529 | 136.33 | 1133.9 |  | 13622 | 168.23 | 5.7598 | 60.83 | 0.015529 | 136.33 | 1133.9 | 997.57
13623 | 5.7611 | 168.24 | 60.83 | 0.015532 | 136.34 | 1133.9 |  | 13623 | 168.24 | 5.7611 | 60.83 | 0.015532 | 136.34 | 1133.9 | 997.56
13624 | 5.7624 | 168.25 | 60.83 | 0.015536 | 136.35 | 1133.9 |  | 13624 | 168.25 | 5.7624 | 60.83 | 0.015536 | 136.35 | 1133.9 | 997.55
13625 | 5.7638 | 168.26 | 60.83 | 0.015539 | 136.36 | 1133.9 |  | 13625 | 168.26 | 5.7638 | 60.83 | 0.015539 | 136.36 | 1133.9 | 997.54
13626 | 5.7651 | 168.27 | 60.829 | 0.015542 | 136.37 | 1133.9 |  | 13626 | 168.27 | 5.7651 | 60.829 | 0.015542 | 136.37 | 1133.9 | 997.53
13627 | 5.7664 | 168.28 | 60.829 | 0.015546 | 136.38 | 1134 |  | 13627 | 168.28 | 5.7664 | 60.829 | 0.015546 | 136.38 | 1134 | 997.62
13628 | 5.7678 | 168.29 | 60.829 | 0.015549 | 136.39 | 1134 |  | 13628 | 168.29 | 5.7678 | 60.829 | 0.015549 | 136.39 | 1134 | 997.61
13629 | 5.7691 | 168.3 | 60.829 | 0.015553 | 136.4 | 1134 |  | 13629 | 168.3 | 5.7691 | 60.829 | 0.015553 | 136.4 | 1134 | 997.6
13630 | 5.7704 | 168.31 | 60.829 | 0.015556 | 136.41 | 1134 |  | 13630 | 168.31 | 5.7704 | 60.829 | 0.015556 | 136.41 | 1134 | 997.59
13631 | 5.7718 | 168.32 | 60.828 | 0.015559 | 136.42 | 1134 |  | 13631 | 168.32 | 5.7718 | 60.828 | 0.015559 | 136.42 | 1134 | 997.58
13632 | 5.7731 | 168.33 | 60.828 | 0.015563 | 136.43 | 1134 |  | 13632 | 168.33 | 5.7731 | 60.828 | 0.015563 | 136.43 | 1134 | 997.57
13633 | 5.7744 | 168.34 | 60.828 | 0.015566 | 136.44 | 1134 |  | 13633 | 168.34 | 5.7744 | 60.828 | 0.015566 | 136.44 | 1134 | 997.56
13634 | 5.7758 | 168.35 | 60.828 | 0.015569 | 136.45 | 1134 |  | 13634 | 168.35 | 5.7758 | 60.828 | 0.015569 | 136.45 | 1134 | 997.55
13635 | 5.7771 | 168.36 | 60.827 | 0.015573 | 136.46 | 1134 |  | 13635 | 168.36 | 5.7771 | 60.827 | 0.015573 | 136.46 | 1134 | 997.54
13636 | 5.7784 | 168.37 | 60.827 | 0.015576 | 136.47 | 1134 |  | 13636 | 168.37 | 5.7784 | 60.827 | 0.015576 | 136.47 | 1134 | 997.53
13637 | 5.7798 | 168.38 | 60.827 | 0.01558 | 136.48 | 1134 |  | 13637 | 168.38 | 5.7798 | 60.827 | 0.01558 | 136.48 | 1134 | 997.52
13638 | 5.7811 | 168.39 | 60.827 | 0.015583 | 136.49 | 1134 |  | 13638 | 168.39 | 5.7811 | 60.827 | 0.015583 | 136.49 | 1134 | 997.51
13639 | 5.7825 | 168.4 | 60.827 | 0.015586 | 136.5 | 1134 |  | 13639 | 168.4 | 5.7825 | 60.827 | 0.015586 | 136.5 | 1134 | 997.5
13640 | 5.7838 | 168.41 | 60.826 | 0.01559 | 136.51 | 1134 |  | 13640 | 168.41 | 5.7838 | 60.826 | 0.01559 | 136.51 | 1134 | 997.49
13641 | 5.7851 | 168.42 | 60.826 | 0.015593 | 136.52 | 1134 |  | 13641 | 168.42 | 5.7851 | 60.826 | 0.015593 | 136.52 | 1134 | 997.48
13642 | 5.7865 | 168.43 | 60.826 | 0.015596 | 136.53 | 1134 |  | 13642 | 168.43 | 5.7865 | 60.826 | 0.015596 | 136.53 | 1134 | 997.47
13643 | 5.7878 | 168.44 | 60.826 | 0.0156 | 136.54 | 1134 |  | 13643 | 168.44 | 5.7878 | 60.826 | 0.0156 | 136.54 | 1134 | 997.46
13644 | 5.7891 | 168.45 | 60.826 | 0.015603 | 136.55 | 1134 |  | 13644 | 168.45 | 5.7891 | 60.826 | 0.015603 | 136.55 | 1134 | 997.45
13645 | 5.7905 | 168.46 | 60.825 | 0.015607 | 136.56 | 1134 |  | 13645 | 168.46 | 5.7905 | 60.825 | 0.015607 | 136.56 | 1134 | 997.44
13646 | 5.7918 | 168.47 | 60.825 | 0.01561 | 136.57 | 1134 |  | 13646 | 168.47 | 5.7918 | 60.825 | 0.01561 | 136.57 | 1134 | 997.43
13647 | 5.7932 | 168.48 | 60.825 | 0.015613 | 136.58 | 1134 |  | 13647 | 168.48 | 5.7932 | 60.825 | 0.015613 | 136.58 | 1134 | 997.42
13648 | 5.7945 | 168.49 | 60.825 | 0.015617 | 136.59 | 1134 |  | 13648 | 168.49 | 5.7945 | 60.825 | 0.015617 | 136.59 | 1134 | 997.41
13649 | 5.7958 | 168.5 | 60.825 | 0.01562 | 136.6 | 1134 |  | 13649 | 168.5 | 5.7958 | 60.825 | 0.01562 | 136.6 | 1134 | 997.4
13650 | 5.7972 | 168.51 | 60.824 | 0.015624 | 136.61 | 1134 |  | 13650 | 168.51 | 5.7972 | 60.824 | 0.015624 | 136.61 | 1134 | 997.39
13651 | 5.7985 | 168.52 | 60.824 | 0.015627 | 136.62 | 1134 |  | 13651 | 168.52 | 5.7985 | 60.824 | 0.015627 | 136.62 | 1134 | 997.38
13652 | 5.7999 | 168.53 | 60.824 | 0.01563 | 136.63 | 1134.1 |  | 13652 | 168.53 | 5.7999 | 60.824 | 0.01563 | 136.63 | 1134.1 | 997.47
13653 | 5.8012 | 168.54 | 60.824 | 0.015634 | 136.64 | 1134.1 |  | 13653 | 168.54 | 5.8012 | 60.824 | 0.015634 | 136.64 | 1134.1 | 997.46
13654 | 5.8025 | 168.55 | 60.824 | 0.015637 | 136.65 | 1134.1 |  | 13654 | 168.55 | 5.8025 | 60.824 | 0.015637 | 136.65 | 1134.1 | 997.45
13655 | 5.8039 | 168.56 | 60.823 | 0.01564 | 136.66 | 1134.1 |  | 13655 | 168.56 | 5.8039 | 60.823 | 0.01564 | 136.66 | 1134.1 | 997.44
13656 | 5.8052 | 168.57 | 60.823 | 0.015644 | 136.67 | 1134.1 |  | 13656 | 168.57 | 5.8052 | 60.823 | 0.015644 | 136.67 | 1134.1 | 997.43
13657 | 5.8066 | 168.58 | 60.823 | 0.015647 | 136.68 | 1134.1 |  | 13657 | 168.58 | 5.8066 | 60.823 | 0.015647 | 136.68 | 1134.1 | 997.42
13658 | 5.8079 | 168.59 | 60.823 | 0.015651 | 136.69 | 1134.1 |  | 13658 | 168.59 | 5.8079 | 60.823 | 0.015651 | 136.69 | 1134.1 | 997.41
13659 | 5.8093 | 168.6 | 60.822 | 0.015654 | 136.7 | 1134.1 |  | 13659 | 168.6 | 5.8093 | 60.822 | 0.015654 | 136.7 | 1134.1 | 997.4
13660 | 5.8106 | 168.61 | 60.822 | 0.015657 | 136.71 | 1134.1 |  | 13660 | 168.61 | 5.8106 | 60.822 | 0.015657 | 136.71 | 1134.1 | 997.39
13661 | 5.8119 | 168.62 | 60.822 | 0.015661 | 136.72 | 1134.1 |  | 13661 | 168.62 | 5.8119 | 60.822 | 0.015661 | 136.72 | 1134.1 | 997.38
13662 | 5.8133 | 168.63 | 60.822 | 0.015664 | 136.73 | 1134.1 |  | 13662 | 168.63 | 5.8133 | 60.822 | 0.015664 | 136.73 | 1134.1 | 997.37
13663 | 5.8146 | 168.64 | 60.822 | 0.015668 | 136.74 | 1134.1 |  | 13663 | 168.64 | 5.8146 | 60.822 | 0.015668 | 136.74 | 1134.1 | 997.36
13664 | 5.816 | 168.65 | 60.821 | 0.015671 | 136.75 | 1134.1 |  | 13664 | 168.65 | 5.816 | 60.821 | 0.015671 | 136.75 | 1134.1 | 997.35
13665 | 5.8173 | 168.66 | 60.821 | 0.015674 | 136.76 | 1134.1 |  | 13665 | 168.66 | 5.8173 | 60.821 | 0.015674 | 136.76 | 1134.1 | 997.34
13666 | 5.8187 | 168.67 | 60.821 | 0.015678 | 136.77 | 1134.1 |  | 13666 | 168.67 | 5.8187 | 60.821 | 0.015678 | 136.77 | 1134.1 | 997.33
13667 | 5.82 | 168.68 | 60.821 | 0.015681 | 136.78 | 1134.1 |  | 13667 | 168.68 | 5.82 | 60.821 | 0.015681 | 136.78 | 1134.1 | 997.32
13668 | 5.8213 | 168.69 | 60.821 | 0.015684 | 136.79 | 1134.1 |  | 13668 | 168.69 | 5.8213 | 60.821 | 0.015684 | 136.79 | 1134.1 | 997.31
13669 | 5.8227 | 168.7 | 60.82 | 0.015688 | 136.8 | 1134.1 |  | 13669 | 168.7 | 5.8227 | 60.82 | 0.015688 | 136.8 | 1134.1 | 997.3
13670 | 5.824 | 168.71 | 60.82 | 0.015691 | 136.81 | 1134.1 |  | 13670 | 168.71 | 5.824 | 60.82 | 0.015691 | 136.81 | 1134.1 | 997.29
13671 | 5.8254 | 168.72 | 60.82 | 0.015695 | 136.82 | 1134.1 |  | 13671 | 168.72 | 5.8254 | 60.82 | 0.015695 | 136.82 | 1134.1 | 997.28
13672 | 5.8267 | 168.73 | 60.82 | 0.015698 | 136.83 | 1134.1 |  | 13672 | 168.73 | 5.8267 | 60.82 | 0.015698 | 136.83 | 1134.1 | 997.27
13673 | 5.8281 | 168.74 | 60.82 | 0.015701 | 136.84 | 1134.1 |  | 13673 | 168.74 | 5.8281 | 60.82 | 0.015701 | 136.84 | 1134.1 | 997.26
13674 | 5.8294 | 168.75 | 60.819 | 0.015705 | 136.85 | 1134.1 |  | 13674 | 168.75 | 5.8294 | 60.819 | 0.015705 | 136.85 | 1134.1 | 997.25
13675 | 5.8308 | 168.76 | 60.819 | 0.015708 | 136.86 | 1134.1 |  | 13675 | 168.76 | 5.8308 | 60.819 | 0.015708 | 136.86 | 1134.1 | 997.24
13676 | 5.8321 | 168.77 | 60.819 | 0.015712 | 136.87 | 1134.1 |  | 13676 | 168.77 | 5.8321 | 60.819 | 0.015712 | 136.87 | 1134.1 | 997.23
13677 | 5.8335 | 168.78 | 60.819 | 0.015715 | 136.88 | 1134.2 |  | 13677 | 168.78 | 5.8335 | 60.819 | 0.015715 | 136.88 | 1134.2 | 997.32
13678 | 5.8348 | 168.79 | 60.818 | 0.015718 | 136.89 | 1134.2 |  | 13678 | 168.79 | 5.8348 | 60.818 | 0.015718 | 136.89 | 1134.2 | 997.31
13679 | 5.8362 | 168.8 | 60.818 | 0.015722 | 136.9 | 1134.2 |  | 13679 | 168.8 | 5.8362 | 60.818 | 0.015722 | 136.9 | 1134.2 | 997.3
13680 | 5.8375 | 168.81 | 60.818 | 0.015725 | 136.91 | 1134.2 |  | 13680 | 168.81 | 5.8375 | 60.818 | 0.015725 | 136.91 | 1134.2 | 997.29
13681 | 5.8388 | 168.82 | 60.818 | 0.015729 | 136.92 | 1134.2 |  | 13681 | 168.82 | 5.8388 | 60.818 | 0.015729 | 136.92 | 1134.2 | 997.28
13682 | 5.8402 | 168.83 | 60.818 | 0.015732 | 136.93 | 1134.2 |  | 13682 | 168.83 | 5.8402 | 60.818 | 0.015732 | 136.93 | 1134.2 | 997.27
13683 | 5.8415 | 168.84 | 60.817 | 0.015735 | 136.94 | 1134.2 |  | 13683 | 168.84 | 5.8415 | 60.817 | 0.015735 | 136.94 | 1134.2 | 997.26
13684 | 5.8429 | 168.85 | 60.817 | 0.015739 | 136.95 | 1134.2 |  | 13684 | 168.85 | 5.8429 | 60.817 | 0.015739 | 136.95 | 1134.2 | 997.25
13685 | 5.8442 | 168.86 | 60.817 | 0.015742 | 136.96 | 1134.2 |  | 13685 | 168.86 | 5.8442 | 60.817 | 0.015742 | 136.96 | 1134.2 | 997.24
13686 | 5.8456 | 168.87 | 60.817 | 0.015746 | 136.97 | 1134.2 |  | 13686 | 168.87 | 5.8456 | 60.817 | 0.015746 | 136.97 | 1134.2 | 997.23
13687 | 5.8469 | 168.88 | 60.817 | 0.015749 | 136.98 | 1134.2 |  | 13687 | 168.88 | 5.8469 | 60.817 | 0.015749 | 136.98 | 1134.2 | 997.22
13688 | 5.8483 | 168.89 | 60.816 | 0.015752 | 136.99 | 1134.2 |  | 13688 | 168.89 | 5.8483 | 60.816 | 0.015752 | 136.99 | 1134.2 | 997.21
13689 | 5.8496 | 168.9 | 60.816 | 0.015756 | 137 | 1134.2 |  | 13689 | 168.9 | 5.8496 | 60.816 | 0.015756 | 137 | 1134.2 | 997.2
13690 | 5.851 | 168.91 | 60.816 | 0.015759 | 137.01 | 1134.2 |  | 13690 | 168.91 | 5.851 | 60.816 | 0.015759 | 137.01 | 1134.2 | 997.19
13691 | 5.8523 | 168.92 | 60.816 | 0.015763 | 137.02 | 1134.2 |  | 13691 | 168.92 | 5.8523 | 60.816 | 0.015763 | 137.02 | 1134.2 | 997.18
13692 | 5.8537 | 168.93 | 60.816 | 0.015766 | 137.03 | 1134.2 |  | 13692 | 168.93 | 5.8537 | 60.816 | 0.015766 | 137.03 | 1134.2 | 997.17
13693 | 5.855 | 168.94 | 60.815 | 0.01577 | 137.04 | 1134.2 |  | 13693 | 168.94 | 5.855 | 60.815 | 0.01577 | 137.04 | 1134.2 | 997.16
13694 | 5.8564 | 168.95 | 60.815 | 0.015773 | 137.05 | 1134.2 |  | 13694 | 168.95 | 5.8564 | 60.815 | 0.015773 | 137.05 | 1134.2 | 997.15
13695 | 5.8577 | 168.96 | 60.815 | 0.015776 | 137.06 | 1134.2 |  | 13695 | 168.96 | 5.8577 | 60.815 | 0.015776 | 137.06 | 1134.2 | 997.14
13696 | 5.8591 | 168.97 | 60.815 | 0.01578 | 137.07 | 1134.2 |  | 13696 | 168.97 | 5.8591 | 60.815 | 0.01578 | 137.07 | 1134.2 | 997.13
13697 | 5.8605 | 168.98 | 60.815 | 0.015783 | 137.08 | 1134.2 |  | 13697 | 168.98 | 5.8605 | 60.815 | 0.015783 | 137.08 | 1134.2 | 997.12
13698 | 5.8618 | 168.99 | 60.814 | 0.015787 | 137.09 | 1134.2 |  | 13698 | 168.99 | 5.8618 | 60.814 | 0.015787 | 137.09 | 1134.2 | 997.11
13699 | 5.8632 | 169 | 60.814 | 0.01579 | 137.1 | 1134.2 |  | 13699 | 169 | 5.8632 | 60.814 | 0.01579 | 137.1 | 1134.2 | 997.1
13700 | 5.8645 | 169.01 | 60.814 | 0.015793 | 137.11 | 1134.2 |  | 13700 | 169.01 | 5.8645 | 60.814 | 0.015793 | 137.11 | 1134.2 | 997.09
13701 | 5.8659 | 169.02 | 60.814 | 0.015797 | 137.12 | 1134.2 |  | 13701 | 169.02 | 5.8659 | 60.814 | 0.015797 | 137.12 | 1134.2 | 997.08
13702 | 5.8672 | 169.03 | 60.813 | 0.0158 | 137.13 | 1134.3 |  | 13702 | 169.03 | 5.8672 | 60.813 | 0.0158 | 137.13 | 1134.3 | 997.17
13703 | 5.8686 | 169.04 | 60.813 | 0.015804 | 137.14 | 1134.3 |  | 13703 | 169.04 | 5.8686 | 60.813 | 0.015804 | 137.14 | 1134.3 | 997.16
13704 | 5.8699 | 169.05 | 60.813 | 0.015807 | 137.15 | 1134.3 |  | 13704 | 169.05 | 5.8699 | 60.813 | 0.015807 | 137.15 | 1134.3 | 997.15
13705 | 5.8713 | 169.06 | 60.813 | 0.01581 | 137.16 | 1134.3 |  | 13705 | 169.06 | 5.8713 | 60.813 | 0.01581 | 137.16 | 1134.3 | 997.14
13706 | 5.8726 | 169.07 | 60.813 | 0.015814 | 137.17 | 1134.3 |  | 13706 | 169.07 | 5.8726 | 60.813 | 0.015814 | 137.17 | 1134.3 | 997.13
13707 | 5.874 | 169.08 | 60.812 | 0.015817 | 137.18 | 1134.3 |  | 13707 | 169.08 | 5.874 | 60.812 | 0.015817 | 137.18 | 1134.3 | 997.12
13708 | 5.8753 | 169.09 | 60.812 | 0.015821 | 137.19 | 1134.3 |  | 13708 | 169.09 | 5.8753 | 60.812 | 0.015821 | 137.19 | 1134.3 | 997.11
13709 | 5.8767 | 169.1 | 60.812 | 0.015824 | 137.2 | 1134.3 |  | 13709 | 169.1 | 5.8767 | 60.812 | 0.015824 | 137.2 | 1134.3 | 997.1
13710 | 5.8781 | 169.11 | 60.812 | 0.015828 | 137.21 | 1134.3 |  | 13710 | 169.11 | 5.8781 | 60.812 | 0.015828 | 137.21 | 1134.3 | 997.09
13711 | 5.8794 | 169.12 | 60.812 | 0.015831 | 137.22 | 1134.3 |  | 13711 | 169.12 | 5.8794 | 60.812 | 0.015831 | 137.22 | 1134.3 | 997.08
13712 | 5.8808 | 169.13 | 60.811 | 0.015834 | 137.23 | 1134.3 |  | 13712 | 169.13 | 5.8808 | 60.811 | 0.015834 | 137.23 | 1134.3 | 997.07
13713 | 5.8821 | 169.14 | 60.811 | 0.015838 | 137.24 | 1134.3 |  | 13713 | 169.14 | 5.8821 | 60.811 | 0.015838 | 137.24 | 1134.3 | 997.06
13714 | 5.8835 | 169.15 | 60.811 | 0.015841 | 137.25 | 1134.3 |  | 13714 | 169.15 | 5.8835 | 60.811 | 0.015841 | 137.25 | 1134.3 | 997.05
13715 | 5.8848 | 169.16 | 60.811 | 0.015845 | 137.26 | 1134.3 |  | 13715 | 169.16 | 5.8848 | 60.811 | 0.015845 | 137.26 | 1134.3 | 997.04
13716 | 5.8862 | 169.17 | 60.811 | 0.015848 | 137.27 | 1134.3 |  | 13716 | 169.17 | 5.8862 | 60.811 | 0.015848 | 137.27 | 1134.3 | 997.03
13717 | 5.8875 | 169.18 | 60.81 | 0.015852 | 137.28 | 1134.3 |  | 13717 | 169.18 | 5.8875 | 60.81 | 0.015852 | 137.28 | 1134.3 | 997.02
13718 | 5.8889 | 169.19 | 60.81 | 0.015855 | 137.29 | 1134.3 |  | 13718 | 169.19 | 5.8889 | 60.81 | 0.015855 | 137.29 | 1134.3 | 997.01
13719 | 5.8903 | 169.2 | 60.81 | 0.015858 | 137.3 | 1134.3 |  | 13719 | 169.2 | 5.8903 | 60.81 | 0.015858 | 137.3 | 1134.3 | 997
13720 | 5.8916 | 169.21 | 60.81 | 0.015862 | 137.31 | 1134.3 |  | 13720 | 169.21 | 5.8916 | 60.81 | 0.015862 | 137.31 | 1134.3 | 996.99
13721 | 5.893 | 169.22 | 60.81 | 0.015865 | 137.32 | 1134.3 |  | 13721 | 169.22 | 5.893 | 60.81 | 0.015865 | 137.32 | 1134.3 | 996.98
13722 | 5.8943 | 169.23 | 60.809 | 0.015869 | 137.33 | 1134.3 |  | 13722 | 169.23 | 5.8943 | 60.809 | 0.015869 | 137.33 | 1134.3 | 996.97
13723 | 5.8957 | 169.24 | 60.809 | 0.015872 | 137.34 | 1134.3 |  | 13723 | 169.24 | 5.8957 | 60.809 | 0.015872 | 137.34 | 1134.3 | 996.96
13724 | 5.8971 | 169.25 | 60.809 | 0.015875 | 137.35 | 1134.3 |  | 13724 | 169.25 | 5.8971 | 60.809 | 0.015875 | 137.35 | 1134.3 | 996.95
13725 | 5.8984 | 169.26 | 60.809 | 0.015879 | 137.36 | 1134.3 |  | 13725 | 169.26 | 5.8984 | 60.809 | 0.015879 | 137.36 | 1134.3 | 996.94
13726 | 5.8998 | 169.27 | 60.808 | 0.015882 | 137.37 | 1134.4 |  | 13726 | 169.27 | 5.8998 | 60.808 | 0.015882 | 137.37 | 1134.4 | 997.03
13727 | 5.9011 | 169.28 | 60.808 | 0.015886 | 137.38 | 1134.4 |  | 13727 | 169.28 | 5.9011 | 60.808 | 0.015886 | 137.38 | 1134.4 | 997.02
13728 | 5.9025 | 169.29 | 60.808 | 0.015889 | 137.39 | 1134.4 |  | 13728 | 169.29 | 5.9025 | 60.808 | 0.015889 | 137.39 | 1134.4 | 997.01
13729 | 5.9039 | 169.3 | 60.808 | 0.015893 | 137.41 | 1134.4 |  | 13729 | 169.3 | 5.9039 | 60.808 | 0.015893 | 137.41 | 1134.4 | 996.99
13730 | 5.9052 | 169.31 | 60.808 | 0.015896 | 137.42 | 1134.4 |  | 13730 | 169.31 | 5.9052 | 60.808 | 0.015896 | 137.42 | 1134.4 | 996.98
13731 | 5.9066 | 169.32 | 60.807 | 0.0159 | 137.43 | 1134.4 |  | 13731 | 169.32 | 5.9066 | 60.807 | 0.0159 | 137.43 | 1134.4 | 996.97
13732 | 5.9079 | 169.33 | 60.807 | 0.015903 | 137.44 | 1134.4 |  | 13732 | 169.33 | 5.9079 | 60.807 | 0.015903 | 137.44 | 1134.4 | 996.96
13733 | 5.9093 | 169.34 | 60.807 | 0.015906 | 137.45 | 1134.4 |  | 13733 | 169.34 | 5.9093 | 60.807 | 0.015906 | 137.45 | 1134.4 | 996.95
13734 | 5.9107 | 169.35 | 60.807 | 0.01591 | 137.46 | 1134.4 |  | 13734 | 169.35 | 5.9107 | 60.807 | 0.01591 | 137.46 | 1134.4 | 996.94
13735 | 5.912 | 169.36 | 60.807 | 0.015913 | 137.47 | 1134.4 |  | 13735 | 169.36 | 5.912 | 60.807 | 0.015913 | 137.47 | 1134.4 | 996.93
13736 | 5.9134 | 169.37 | 60.806 | 0.015917 | 137.48 | 1134.4 |  | 13736 | 169.37 | 5.9134 | 60.806 | 0.015917 | 137.48 | 1134.4 | 996.92
13737 | 5.9148 | 169.38 | 60.806 | 0.01592 | 137.49 | 1134.4 |  | 13737 | 169.38 | 5.9148 | 60.806 | 0.01592 | 137.49 | 1134.4 | 996.91
13738 | 5.9161 | 169.39 | 60.806 | 0.015924 | 137.5 | 1134.4 |  | 13738 | 169.39 | 5.9161 | 60.806 | 0.015924 | 137.5 | 1134.4 | 996.9
13739 | 5.9175 | 169.4 | 60.806 | 0.015927 | 137.51 | 1134.4 |  | 13739 | 169.4 | 5.9175 | 60.806 | 0.015927 | 137.51 | 1134.4 | 996.89
13740 | 5.9188 | 169.41 | 60.806 | 0.01593 | 137.52 | 1134.4 |  | 13740 | 169.41 | 5.9188 | 60.806 | 0.01593 | 137.52 | 1134.4 | 996.88
13741 | 5.9202 | 169.42 | 60.805 | 0.015934 | 137.53 | 1134.4 |  | 13741 | 169.42 | 5.9202 | 60.805 | 0.015934 | 137.53 | 1134.4 | 996.87
13742 | 5.9216 | 169.43 | 60.805 | 0.015937 | 137.54 | 1134.4 |  | 13742 | 169.43 | 5.9216 | 60.805 | 0.015937 | 137.54 | 1134.4 | 996.86
13743 | 5.9229 | 169.44 | 60.805 | 0.015941 | 137.55 | 1134.4 |  | 13743 | 169.44 | 5.9229 | 60.805 | 0.015941 | 137.55 | 1134.4 | 996.85
13744 | 5.9243 | 169.45 | 60.805 | 0.015944 | 137.56 | 1134.4 |  | 13744 | 169.45 | 5.9243 | 60.805 | 0.015944 | 137.56 | 1134.4 | 996.84
13745 | 5.9257 | 169.46 | 60.804 | 0.015948 | 137.57 | 1134.4 |  | 13745 | 169.46 | 5.9257 | 60.804 | 0.015948 | 137.57 | 1134.4 | 996.83
13746 | 5.927 | 169.47 | 60.804 | 0.015951 | 137.58 | 1134.4 |  | 13746 | 169.47 | 5.927 | 60.804 | 0.015951 | 137.58 | 1134.4 | 996.82
13747 | 5.9284 | 169.48 | 60.804 | 0.015954 | 137.59 | 1134.4 |  | 13747 | 169.48 | 5.9284 | 60.804 | 0.015954 | 137.59 | 1134.4 | 996.81
13748 | 5.9298 | 169.49 | 60.804 | 0.015958 | 137.6 | 1134.4 |  | 13748 | 169.49 | 5.9298 | 60.804 | 0.015958 | 137.6 | 1134.4 | 996.8
13749 | 5.9311 | 169.5 | 60.804 | 0.015961 | 137.61 | 1134.4 |  | 13749 | 169.5 | 5.9311 | 60.804 | 0.015961 | 137.61 | 1134.4 | 996.79
13750 | 5.9325 | 169.51 | 60.803 | 0.015965 | 137.62 | 1134.4 |  | 13750 | 169.51 | 5.9325 | 60.803 | 0.015965 | 137.62 | 1134.4 | 996.78
13751 | 5.9339 | 169.52 | 60.803 | 0.015968 | 137.63 | 1134.5 |  | 13751 | 169.52 | 5.9339 | 60.803 | 0.015968 | 137.63 | 1134.5 | 996.87
13752 | 5.9352 | 169.53 | 60.803 | 0.015972 | 137.64 | 1134.5 |  | 13752 | 169.53 | 5.9352 | 60.803 | 0.015972 | 137.64 | 1134.5 | 996.86
13753 | 5.9366 | 169.54 | 60.803 | 0.015975 | 137.65 | 1134.5 |  | 13753 | 169.54 | 5.9366 | 60.803 | 0.015975 | 137.65 | 1134.5 | 996.85
13754 | 5.938 | 169.55 | 60.803 | 0.015979 | 137.66 | 1134.5 |  | 13754 | 169.55 | 5.938 | 60.803 | 0.015979 | 137.66 | 1134.5 | 996.84
13755 | 5.9393 | 169.56 | 60.802 | 0.015982 | 137.67 | 1134.5 |  | 13755 | 169.56 | 5.9393 | 60.802 | 0.015982 | 137.67 | 1134.5 | 996.83
13756 | 5.9407 | 169.57 | 60.802 | 0.015985 | 137.68 | 1134.5 |  | 13756 | 169.57 | 5.9407 | 60.802 | 0.015985 | 137.68 | 1134.5 | 996.82
13757 | 5.9421 | 169.58 | 60.802 | 0.015989 | 137.69 | 1134.5 |  | 13757 | 169.58 | 5.9421 | 60.802 | 0.015989 | 137.69 | 1134.5 | 996.81
13758 | 5.9434 | 169.59 | 60.802 | 0.015992 | 137.7 | 1134.5 |  | 13758 | 169.59 | 5.9434 | 60.802 | 0.015992 | 137.7 | 1134.5 | 996.8
13759 | 5.9448 | 169.6 | 60.802 | 0.015996 | 137.71 | 1134.5 |  | 13759 | 169.6 | 5.9448 | 60.802 | 0.015996 | 137.71 | 1134.5 | 996.79
13760 | 5.9462 | 169.61 | 60.801 | 0.015999 | 137.72 | 1134.5 |  | 13760 | 169.61 | 5.9462 | 60.801 | 0.015999 | 137.72 | 1134.5 | 996.78
13761 | 5.9475 | 169.62 | 60.801 | 0.016003 | 137.73 | 1134.5 |  | 13761 | 169.62 | 5.9475 | 60.801 | 0.016003 | 137.73 | 1134.5 | 996.77
13762 | 5.9489 | 169.63 | 60.801 | 0.016006 | 137.74 | 1134.5 |  | 13762 | 169.63 | 5.9489 | 60.801 | 0.016006 | 137.74 | 1134.5 | 996.76
13763 | 5.9503 | 169.64 | 60.801 | 0.01601 | 137.75 | 1134.5 |  | 13763 | 169.64 | 5.9503 | 60.801 | 0.01601 | 137.75 | 1134.5 | 996.75
13764 | 5.9516 | 169.65 | 60.8 | 0.016013 | 137.76 | 1134.5 |  | 13764 | 169.65 | 5.9516 | 60.8 | 0.016013 | 137.76 | 1134.5 | 996.74
13765 | 5.953 | 169.66 | 60.8 | 0.016017 | 137.77 | 1134.5 |  | 13765 | 169.66 | 5.953 | 60.8 | 0.016017 | 137.77 | 1134.5 | 996.73
13766 | 5.9544 | 169.67 | 60.8 | 0.01602 | 137.78 | 1134.5 |  | 13766 | 169.67 | 5.9544 | 60.8 | 0.01602 | 137.78 | 1134.5 | 996.72
13767 | 5.9558 | 169.68 | 60.8 | 0.016023 | 137.79 | 1134.5 |  | 13767 | 169.68 | 5.9558 | 60.8 | 0.016023 | 137.79 | 1134.5 | 996.71
13768 | 5.9571 | 169.69 | 60.8 | 0.016027 | 137.8 | 1134.5 |  | 13768 | 169.69 | 5.9571 | 60.8 | 0.016027 | 137.8 | 1134.5 | 996.7
13769 | 5.9585 | 169.7 | 60.799 | 0.01603 | 137.81 | 1134.5 |  | 13769 | 169.7 | 5.9585 | 60.799 | 0.01603 | 137.81 | 1134.5 | 996.69
13770 | 5.9599 | 169.71 | 60.799 | 0.016034 | 137.82 | 1134.5 |  | 13770 | 169.71 | 5.9599 | 60.799 | 0.016034 | 137.82 | 1134.5 | 996.68
13771 | 5.9612 | 169.72 | 60.799 | 0.016037 | 137.83 | 1134.5 |  | 13771 | 169.72 | 5.9612 | 60.799 | 0.016037 | 137.83 | 1134.5 | 996.67
13772 | 5.9626 | 169.73 | 60.799 | 0.016041 | 137.84 | 1134.5 |  | 13772 | 169.73 | 5.9626 | 60.799 | 0.016041 | 137.84 | 1134.5 | 996.66
13773 | 5.964 | 169.74 | 60.799 | 0.016044 | 137.85 | 1134.5 |  | 13773 | 169.74 | 5.964 | 60.799 | 0.016044 | 137.85 | 1134.5 | 996.65
13774 | 5.9654 | 169.75 | 60.798 | 0.016048 | 137.86 | 1134.5 |  | 13774 | 169.75 | 5.9654 | 60.798 | 0.016048 | 137.86 | 1134.5 | 996.64
13775 | 5.9667 | 169.76 | 60.798 | 0.016051 | 137.87 | 1134.5 |  | 13775 | 169.76 | 5.9667 | 60.798 | 0.016051 | 137.87 | 1134.5 | 996.63
13776 | 5.9681 | 169.77 | 60.798 | 0.016055 | 137.88 | 1134.6 |  | 13776 | 169.77 | 5.9681 | 60.798 | 0.016055 | 137.88 | 1134.6 | 996.72
13777 | 5.9695 | 169.78 | 60.798 | 0.016058 | 137.89 | 1134.6 |  | 13777 | 169.78 | 5.9695 | 60.798 | 0.016058 | 137.89 | 1134.6 | 996.71
13778 | 5.9709 | 169.79 | 60.798 | 0.016061 | 137.9 | 1134.6 |  | 13778 | 169.79 | 5.9709 | 60.798 | 0.016061 | 137.9 | 1134.6 | 996.7
13779 | 5.9722 | 169.8 | 60.797 | 0.016065 | 137.91 | 1134.6 |  | 13779 | 169.8 | 5.9722 | 60.797 | 0.016065 | 137.91 | 1134.6 | 996.69
13780 | 5.9736 | 169.81 | 60.797 | 0.016068 | 137.92 | 1134.6 |  | 13780 | 169.81 | 5.9736 | 60.797 | 0.016068 | 137.92 | 1134.6 | 996.68
13781 | 5.975 | 169.82 | 60.797 | 0.016072 | 137.93 | 1134.6 |  | 13781 | 169.82 | 5.975 | 60.797 | 0.016072 | 137.93 | 1134.6 | 996.67
13782 | 5.9764 | 169.83 | 60.797 | 0.016075 | 137.94 | 1134.6 |  | 13782 | 169.83 | 5.9764 | 60.797 | 0.016075 | 137.94 | 1134.6 | 996.66
13783 | 5.9777 | 169.84 | 60.797 | 0.016079 | 137.95 | 1134.6 |  | 13783 | 169.84 | 5.9777 | 60.797 | 0.016079 | 137.95 | 1134.6 | 996.65
13784 | 5.9791 | 169.85 | 60.796 | 0.016082 | 137.96 | 1134.6 |  | 13784 | 169.85 | 5.9791 | 60.796 | 0.016082 | 137.96 | 1134.6 | 996.64
13785 | 5.9805 | 169.86 | 60.796 | 0.016086 | 137.97 | 1134.6 |  | 13785 | 169.86 | 5.9805 | 60.796 | 0.016086 | 137.97 | 1134.6 | 996.63
13786 | 5.9819 | 169.87 | 60.796 | 0.016089 | 137.98 | 1134.6 |  | 13786 | 169.87 | 5.9819 | 60.796 | 0.016089 | 137.98 | 1134.6 | 996.62
13787 | 5.9832 | 169.88 | 60.796 | 0.016093 | 137.99 | 1134.6 |  | 13787 | 169.88 | 5.9832 | 60.796 | 0.016093 | 137.99 | 1134.6 | 996.61
13788 | 5.9846 | 169.89 | 60.795 | 0.016096 | 138 | 1134.6 |  | 13788 | 169.89 | 5.9846 | 60.795 | 0.016096 | 138 | 1134.6 | 996.6
13789 | 5.986 | 169.9 | 60.795 | 0.0161 | 138.01 | 1134.6 |  | 13789 | 169.9 | 5.986 | 60.795 | 0.0161 | 138.01 | 1134.6 | 996.59
13790 | 5.9874 | 169.91 | 60.795 | 0.016103 | 138.02 | 1134.6 |  | 13790 | 169.91 | 5.9874 | 60.795 | 0.016103 | 138.02 | 1134.6 | 996.58
13791 | 5.9887 | 169.92 | 60.795 | 0.016107 | 138.03 | 1134.6 |  | 13791 | 169.92 | 5.9887 | 60.795 | 0.016107 | 138.03 | 1134.6 | 996.57
13792 | 5.9901 | 169.93 | 60.795 | 0.01611 | 138.04 | 1134.6 |  | 13792 | 169.93 | 5.9901 | 60.795 | 0.01611 | 138.04 | 1134.6 | 996.56
13793 | 5.9915 | 169.94 | 60.794 | 0.016113 | 138.05 | 1134.6 |  | 13793 | 169.94 | 5.9915 | 60.794 | 0.016113 | 138.05 | 1134.6 | 996.55
13794 | 5.9929 | 169.95 | 60.794 | 0.016117 | 138.06 | 1134.6 |  | 13794 | 169.95 | 5.9929 | 60.794 | 0.016117 | 138.06 | 1134.6 | 996.54
13795 | 5.9942 | 169.96 | 60.794 | 0.01612 | 138.07 | 1134.6 |  | 13795 | 169.96 | 5.9942 | 60.794 | 0.01612 | 138.07 | 1134.6 | 996.53
13796 | 5.9956 | 169.97 | 60.794 | 0.016124 | 138.08 | 1134.6 |  | 13796 | 169.97 | 5.9956 | 60.794 | 0.016124 | 138.08 | 1134.6 | 996.52
13797 | 5.997 | 169.98 | 60.794 | 0.016127 | 138.09 | 1134.6 |  | 13797 | 169.98 | 5.997 | 60.794 | 0.016127 | 138.09 | 1134.6 | 996.51
13798 | 5.9984 | 169.99 | 60.793 | 0.016131 | 138.1 | 1134.6 |  | 13798 | 169.99 | 5.9984 | 60.793 | 0.016131 | 138.1 | 1134.6 | 996.5
13799 | 5.9998 | 170 | 60.793 | 0.016134 | 138.11 | 1134.6 |  | 13799 | 170 | 5.9998 | 60.793 | 0.016134 | 138.11 | 1134.6 | 996.49
13800 | 6.0011 | 170.01 | 60.793 | 0.016138 | 138.12 | 1134.6 |  | 13800 | 170.01 | 6.0011 | 60.793 | 0.016138 | 138.12 | 1134.6 | 996.48
13801 | 6.0025 | 170.02 | 60.793 | 0.016141 | 138.13 | 1134.7 |  | 13801 | 170.02 | 6.0025 | 60.793 | 0.016141 | 138.13 | 1134.7 | 996.57
13802 | 6.0039 | 170.03 | 60.793 | 0.016145 | 138.14 | 1134.7 |  | 13802 | 170.03 | 6.0039 | 60.793 | 0.016145 | 138.14 | 1134.7 | 996.56
13803 | 6.0053 | 170.04 | 60.792 | 0.016148 | 138.15 | 1134.7 |  | 13803 | 170.04 | 6.0053 | 60.792 | 0.016148 | 138.15 | 1134.7 | 996.55
13804 | 6.0067 | 170.05 | 60.792 | 0.016152 | 138.16 | 1134.7 |  | 13804 | 170.05 | 6.0067 | 60.792 | 0.016152 | 138.16 | 1134.7 | 996.54
13805 | 6.008 | 170.06 | 60.792 | 0.016155 | 138.17 | 1134.7 |  | 13805 | 170.06 | 6.008 | 60.792 | 0.016155 | 138.17 | 1134.7 | 996.53
13806 | 6.0094 | 170.07 | 60.792 | 0.016159 | 138.18 | 1134.7 |  | 13806 | 170.07 | 6.0094 | 60.792 | 0.016159 | 138.18 | 1134.7 | 996.52
13807 | 6.0108 | 170.08 | 60.791 | 0.016162 | 138.19 | 1134.7 |  | 13807 | 170.08 | 6.0108 | 60.791 | 0.016162 | 138.19 | 1134.7 | 996.51
13808 | 6.0122 | 170.09 | 60.791 | 0.016166 | 138.2 | 1134.7 |  | 13808 | 170.09 | 6.0122 | 60.791 | 0.016166 | 138.2 | 1134.7 | 996.5
13809 | 6.0136 | 170.1 | 60.791 | 0.016169 | 138.21 | 1134.7 |  | 13809 | 170.1 | 6.0136 | 60.791 | 0.016169 | 138.21 | 1134.7 | 996.49
13810 | 6.0149 | 170.11 | 60.791 | 0.016173 | 138.22 | 1134.7 |  | 13810 | 170.11 | 6.0149 | 60.791 | 0.016173 | 138.22 | 1134.7 | 996.48
13811 | 6.0163 | 170.12 | 60.791 | 0.016176 | 138.23 | 1134.7 |  | 13811 | 170.12 | 6.0163 | 60.791 | 0.016176 | 138.23 | 1134.7 | 996.47
13812 | 6.0177 | 170.13 | 60.79 | 0.01618 | 138.24 | 1134.7 |  | 13812 | 170.13 | 6.0177 | 60.79 | 0.01618 | 138.24 | 1134.7 | 996.46
13813 | 6.0191 | 170.14 | 60.79 | 0.016183 | 138.25 | 1134.7 |  | 13813 | 170.14 | 6.0191 | 60.79 | 0.016183 | 138.25 | 1134.7 | 996.45
13814 | 6.0205 | 170.15 | 60.79 | 0.016186 | 138.26 | 1134.7 |  | 13814 | 170.15 | 6.0205 | 60.79 | 0.016186 | 138.26 | 1134.7 | 996.44
13815 | 6.0219 | 170.16 | 60.79 | 0.01619 | 138.27 | 1134.7 |  | 13815 | 170.16 | 6.0219 | 60.79 | 0.01619 | 138.27 | 1134.7 | 996.43
13816 | 6.0232 | 170.17 | 60.79 | 0.016193 | 138.28 | 1134.7 |  | 13816 | 170.17 | 6.0232 | 60.79 | 0.016193 | 138.28 | 1134.7 | 996.42
13817 | 6.0246 | 170.18 | 60.789 | 0.016197 | 138.29 | 1134.7 |  | 13817 | 170.18 | 6.0246 | 60.789 | 0.016197 | 138.29 | 1134.7 | 996.41
13818 | 6.026 | 170.19 | 60.789 | 0.0162 | 138.3 | 1134.7 |  | 13818 | 170.19 | 6.026 | 60.789 | 0.0162 | 138.3 | 1134.7 | 996.4
13819 | 6.0274 | 170.2 | 60.789 | 0.016204 | 138.31 | 1134.7 |  | 13819 | 170.2 | 6.0274 | 60.789 | 0.016204 | 138.31 | 1134.7 | 996.39
13820 | 6.0288 | 170.21 | 60.789 | 0.016207 | 138.32 | 1134.7 |  | 13820 | 170.21 | 6.0288 | 60.789 | 0.016207 | 138.32 | 1134.7 | 996.38
13821 | 6.0302 | 170.22 | 60.789 | 0.016211 | 138.33 | 1134.7 |  | 13821 | 170.22 | 6.0302 | 60.789 | 0.016211 | 138.33 | 1134.7 | 996.37
13822 | 6.0316 | 170.23 | 60.788 | 0.016214 | 138.34 | 1134.7 |  | 13822 | 170.23 | 6.0316 | 60.788 | 0.016214 | 138.34 | 1134.7 | 996.36
13823 | 6.0329 | 170.24 | 60.788 | 0.016218 | 138.35 | 1134.7 |  | 13823 | 170.24 | 6.0329 | 60.788 | 0.016218 | 138.35 | 1134.7 | 996.35
13824 | 6.0343 | 170.25 | 60.788 | 0.016221 | 138.36 | 1134.7 |  | 13824 | 170.25 | 6.0343 | 60.788 | 0.016221 | 138.36 | 1134.7 | 996.34
13825 | 6.0357 | 170.26 | 60.788 | 0.016225 | 138.37 | 1134.7 |  | 13825 | 170.26 | 6.0357 | 60.788 | 0.016225 | 138.37 | 1134.7 | 996.33
13826 | 6.0371 | 170.27 | 60.787 | 0.016228 | 138.38 | 1134.8 |  | 13826 | 170.27 | 6.0371 | 60.787 | 0.016228 | 138.38 | 1134.8 | 996.42
13827 | 6.0385 | 170.28 | 60.787 | 0.016232 | 138.39 | 1134.8 |  | 13827 | 170.28 | 6.0385 | 60.787 | 0.016232 | 138.39 | 1134.8 | 996.41
13828 | 6.0399 | 170.29 | 60.787 | 0.016235 | 138.4 | 1134.8 |  | 13828 | 170.29 | 6.0399 | 60.787 | 0.016235 | 138.4 | 1134.8 | 996.4
13829 | 6.0413 | 170.3 | 60.787 | 0.016239 | 138.41 | 1134.8 |  | 13829 | 170.3 | 6.0413 | 60.787 | 0.016239 | 138.41 | 1134.8 | 996.39
13830 | 6.0426 | 170.31 | 60.787 | 0.016242 | 138.42 | 1134.8 |  | 13830 | 170.31 | 6.0426 | 60.787 | 0.016242 | 138.42 | 1134.8 | 996.38
13831 | 6.044 | 170.32 | 60.786 | 0.016246 | 138.43 | 1134.8 |  | 13831 | 170.32 | 6.044 | 60.786 | 0.016246 | 138.43 | 1134.8 | 996.37
13832 | 6.0454 | 170.33 | 60.786 | 0.016249 | 138.44 | 1134.8 |  | 13832 | 170.33 | 6.0454 | 60.786 | 0.016249 | 138.44 | 1134.8 | 996.36
13833 | 6.0468 | 170.34 | 60.786 | 0.016253 | 138.45 | 1134.8 |  | 13833 | 170.34 | 6.0468 | 60.786 | 0.016253 | 138.45 | 1134.8 | 996.35
13834 | 6.0482 | 170.35 | 60.786 | 0.016256 | 138.46 | 1134.8 |  | 13834 | 170.35 | 6.0482 | 60.786 | 0.016256 | 138.46 | 1134.8 | 996.34
13835 | 6.0496 | 170.36 | 60.786 | 0.01626 | 138.47 | 1134.8 |  | 13835 | 170.36 | 6.0496 | 60.786 | 0.01626 | 138.47 | 1134.8 | 996.33
13836 | 6.051 | 170.37 | 60.785 | 0.016263 | 138.48 | 1134.8 |  | 13836 | 170.37 | 6.051 | 60.785 | 0.016263 | 138.48 | 1134.8 | 996.32
13837 | 6.0524 | 170.38 | 60.785 | 0.016267 | 138.49 | 1134.8 |  | 13837 | 170.38 | 6.0524 | 60.785 | 0.016267 | 138.49 | 1134.8 | 996.31
13838 | 6.0538 | 170.39 | 60.785 | 0.01627 | 138.5 | 1134.8 |  | 13838 | 170.39 | 6.0538 | 60.785 | 0.01627 | 138.5 | 1134.8 | 996.3
13839 | 6.0551 | 170.4 | 60.785 | 0.016274 | 138.51 | 1134.8 |  | 13839 | 170.4 | 6.0551 | 60.785 | 0.016274 | 138.51 | 1134.8 | 996.29
13840 | 6.0565 | 170.41 | 60.785 | 0.016277 | 138.52 | 1134.8 |  | 13840 | 170.41 | 6.0565 | 60.785 | 0.016277 | 138.52 | 1134.8 | 996.28
13841 | 6.0579 | 170.42 | 60.784 | 0.016281 | 138.53 | 1134.8 |  | 13841 | 170.42 | 6.0579 | 60.784 | 0.016281 | 138.53 | 1134.8 | 996.27
13842 | 6.0593 | 170.43 | 60.784 | 0.016284 | 138.54 | 1134.8 |  | 13842 | 170.43 | 6.0593 | 60.784 | 0.016284 | 138.54 | 1134.8 | 996.26
13843 | 6.0607 | 170.44 | 60.784 | 0.016288 | 138.55 | 1134.8 |  | 13843 | 170.44 | 6.0607 | 60.784 | 0.016288 | 138.55 | 1134.8 | 996.25
13844 | 6.0621 | 170.45 | 60.784 | 0.016291 | 138.56 | 1134.8 |  | 13844 | 170.45 | 6.0621 | 60.784 | 0.016291 | 138.56 | 1134.8 | 996.24
13845 | 6.0635 | 170.46 | 60.783 | 0.016295 | 138.57 | 1134.8 |  | 13845 | 170.46 | 6.0635 | 60.783 | 0.016295 | 138.57 | 1134.8 | 996.23
13846 | 6.0649 | 170.47 | 60.783 | 0.016298 | 138.58 | 1134.8 |  | 13846 | 170.47 | 6.0649 | 60.783 | 0.016298 | 138.58 | 1134.8 | 996.22
13847 | 6.0663 | 170.48 | 60.783 | 0.016302 | 138.59 | 1134.8 |  | 13847 | 170.48 | 6.0663 | 60.783 | 0.016302 | 138.59 | 1134.8 | 996.21
13848 | 6.0677 | 170.49 | 60.783 | 0.016305 | 138.6 | 1134.8 |  | 13848 | 170.49 | 6.0677 | 60.783 | 0.016305 | 138.6 | 1134.8 | 996.2
13849 | 6.0691 | 170.5 | 60.783 | 0.016309 | 138.61 | 1134.8 |  | 13849 | 170.5 | 6.0691 | 60.783 | 0.016309 | 138.61 | 1134.8 | 996.19
13850 | 6.0705 | 170.51 | 60.782 | 0.016312 | 138.62 | 1134.8 |  | 13850 | 170.51 | 6.0705 | 60.782 | 0.016312 | 138.62 | 1134.8 | 996.18
13851 | 6.0718 | 170.52 | 60.782 | 0.016316 | 138.63 | 1134.9 |  | 13851 | 170.52 | 6.0718 | 60.782 | 0.016316 | 138.63 | 1134.9 | 996.27
13852 | 6.0732 | 170.53 | 60.782 | 0.016319 | 138.64 | 1134.9 |  | 13852 | 170.53 | 6.0732 | 60.782 | 0.016319 | 138.64 | 1134.9 | 996.26
13853 | 6.0746 | 170.54 | 60.782 | 0.016323 | 138.65 | 1134.9 |  | 13853 | 170.54 | 6.0746 | 60.782 | 0.016323 | 138.65 | 1134.9 | 996.25
13854 | 6.076 | 170.55 | 60.782 | 0.016326 | 138.66 | 1134.9 |  | 13854 | 170.55 | 6.076 | 60.782 | 0.016326 | 138.66 | 1134.9 | 996.24
13855 | 6.0774 | 170.56 | 60.781 | 0.01633 | 138.67 | 1134.9 |  | 13855 | 170.56 | 6.0774 | 60.781 | 0.01633 | 138.67 | 1134.9 | 996.23
13856 | 6.0788 | 170.57 | 60.781 | 0.016333 | 138.68 | 1134.9 |  | 13856 | 170.57 | 6.0788 | 60.781 | 0.016333 | 138.68 | 1134.9 | 996.22
13857 | 6.0802 | 170.58 | 60.781 | 0.016337 | 138.69 | 1134.9 |  | 13857 | 170.58 | 6.0802 | 60.781 | 0.016337 | 138.69 | 1134.9 | 996.21
13858 | 6.0816 | 170.59 | 60.781 | 0.01634 | 138.7 | 1134.9 |  | 13858 | 170.59 | 6.0816 | 60.781 | 0.01634 | 138.7 | 1134.9 | 996.2
13859 | 6.083 | 170.6 | 60.781 | 0.016344 | 138.71 | 1134.9 |  | 13859 | 170.6 | 6.083 | 60.781 | 0.016344 | 138.71 | 1134.9 | 996.19
13860 | 6.0844 | 170.61 | 60.78 | 0.016347 | 138.72 | 1134.9 |  | 13860 | 170.61 | 6.0844 | 60.78 | 0.016347 | 138.72 | 1134.9 | 996.18
13861 | 6.0858 | 170.62 | 60.78 | 0.016351 | 138.73 | 1134.9 |  | 13861 | 170.62 | 6.0858 | 60.78 | 0.016351 | 138.73 | 1134.9 | 996.17
13862 | 6.0872 | 170.63 | 60.78 | 0.016354 | 138.74 | 1134.9 |  | 13862 | 170.63 | 6.0872 | 60.78 | 0.016354 | 138.74 | 1134.9 | 996.16
13863 | 6.0886 | 170.64 | 60.78 | 0.016358 | 138.75 | 1134.9 |  | 13863 | 170.64 | 6.0886 | 60.78 | 0.016358 | 138.75 | 1134.9 | 996.15
13864 | 6.09 | 170.65 | 60.779 | 0.016361 | 138.76 | 1134.9 |  | 13864 | 170.65 | 6.09 | 60.779 | 0.016361 | 138.76 | 1134.9 | 996.14
13865 | 6.0914 | 170.66 | 60.779 | 0.016365 | 138.77 | 1134.9 |  | 13865 | 170.66 | 6.0914 | 60.779 | 0.016365 | 138.77 | 1134.9 | 996.13
13866 | 6.0928 | 170.67 | 60.779 | 0.016368 | 138.78 | 1134.9 |  | 13866 | 170.67 | 6.0928 | 60.779 | 0.016368 | 138.78 | 1134.9 | 996.12
13867 | 6.0942 | 170.68 | 60.779 | 0.016372 | 138.79 | 1134.9 |  | 13867 | 170.68 | 6.0942 | 60.779 | 0.016372 | 138.79 | 1134.9 | 996.11
13868 | 6.0956 | 170.69 | 60.779 | 0.016375 | 138.8 | 1134.9 |  | 13868 | 170.69 | 6.0956 | 60.779 | 0.016375 | 138.8 | 1134.9 | 996.1
13869 | 6.097 | 170.7 | 60.778 | 0.016379 | 138.81 | 1134.9 |  | 13869 | 170.7 | 6.097 | 60.778 | 0.016379 | 138.81 | 1134.9 | 996.09
13870 | 6.0984 | 170.71 | 60.778 | 0.016383 | 138.82 | 1134.9 |  | 13870 | 170.71 | 6.0984 | 60.778 | 0.016383 | 138.82 | 1134.9 | 996.08
13871 | 6.0998 | 170.72 | 60.778 | 0.016386 | 138.83 | 1134.9 |  | 13871 | 170.72 | 6.0998 | 60.778 | 0.016386 | 138.83 | 1134.9 | 996.07
13872 | 6.1012 | 170.73 | 60.778 | 0.01639 | 138.84 | 1134.9 |  | 13872 | 170.73 | 6.1012 | 60.778 | 0.01639 | 138.84 | 1134.9 | 996.06
13873 | 6.1026 | 170.74 | 60.778 | 0.016393 | 138.85 | 1134.9 |  | 13873 | 170.74 | 6.1026 | 60.778 | 0.016393 | 138.85 | 1134.9 | 996.05
13874 | 6.104 | 170.75 | 60.777 | 0.016397 | 138.86 | 1134.9 |  | 13874 | 170.75 | 6.104 | 60.777 | 0.016397 | 138.86 | 1134.9 | 996.04
13875 | 6.1054 | 170.76 | 60.777 | 0.0164 | 138.87 | 1135 |  | 13875 | 170.76 | 6.1054 | 60.777 | 0.0164 | 138.87 | 1135 | 996.13
13876 | 6.1068 | 170.77 | 60.777 | 0.016404 | 138.88 | 1135 |  | 13876 | 170.77 | 6.1068 | 60.777 | 0.016404 | 138.88 | 1135 | 996.12
13877 | 6.1082 | 170.78 | 60.777 | 0.016407 | 138.89 | 1135 |  | 13877 | 170.78 | 6.1082 | 60.777 | 0.016407 | 138.89 | 1135 | 996.11
13878 | 6.1096 | 170.79 | 60.777 | 0.016411 | 138.9 | 1135 |  | 13878 | 170.79 | 6.1096 | 60.777 | 0.016411 | 138.9 | 1135 | 996.1
13879 | 6.111 | 170.8 | 60.776 | 0.016414 | 138.91 | 1135 |  | 13879 | 170.8 | 6.111 | 60.776 | 0.016414 | 138.91 | 1135 | 996.09
13880 | 6.1124 | 170.81 | 60.776 | 0.016418 | 138.92 | 1135 |  | 13880 | 170.81 | 6.1124 | 60.776 | 0.016418 | 138.92 | 1135 | 996.08
13881 | 6.1138 | 170.82 | 60.776 | 0.016421 | 138.93 | 1135 |  | 13881 | 170.82 | 6.1138 | 60.776 | 0.016421 | 138.93 | 1135 | 996.07
13882 | 6.1152 | 170.83 | 60.776 | 0.016425 | 138.94 | 1135 |  | 13882 | 170.83 | 6.1152 | 60.776 | 0.016425 | 138.94 | 1135 | 996.06
13883 | 6.1166 | 170.84 | 60.775 | 0.016428 | 138.95 | 1135 |  | 13883 | 170.84 | 6.1166 | 60.775 | 0.016428 | 138.95 | 1135 | 996.05
13884 | 6.118 | 170.85 | 60.775 | 0.016432 | 138.96 | 1135 |  | 13884 | 170.85 | 6.118 | 60.775 | 0.016432 | 138.96 | 1135 | 996.04
13885 | 6.1194 | 170.86 | 60.775 | 0.016435 | 138.97 | 1135 |  | 13885 | 170.86 | 6.1194 | 60.775 | 0.016435 | 138.97 | 1135 | 996.03
13886 | 6.1208 | 170.87 | 60.775 | 0.016439 | 138.98 | 1135 |  | 13886 | 170.87 | 6.1208 | 60.775 | 0.016439 | 138.98 | 1135 | 996.02
13887 | 6.1222 | 170.88 | 60.775 | 0.016442 | 138.99 | 1135 |  | 13887 | 170.88 | 6.1222 | 60.775 | 0.016442 | 138.99 | 1135 | 996.01
13888 | 6.1236 | 170.89 | 60.774 | 0.016446 | 139 | 1135 |  | 13888 | 170.89 | 6.1236 | 60.774 | 0.016446 | 139 | 1135 | 996
13889 | 6.125 | 170.9 | 60.774 | 0.016449 | 139.01 | 1135 |  | 13889 | 170.9 | 6.125 | 60.774 | 0.016449 | 139.01 | 1135 | 995.99
13890 | 6.1264 | 170.91 | 60.774 | 0.016453 | 139.02 | 1135 |  | 13890 | 170.91 | 6.1264 | 60.774 | 0.016453 | 139.02 | 1135 | 995.98
13891 | 6.1278 | 170.92 | 60.774 | 0.016457 | 139.03 | 1135 |  | 13891 | 170.92 | 6.1278 | 60.774 | 0.016457 | 139.03 | 1135 | 995.97
13892 | 6.1292 | 170.93 | 60.774 | 0.01646 | 139.04 | 1135 |  | 13892 | 170.93 | 6.1292 | 60.774 | 0.01646 | 139.04 | 1135 | 995.96
13893 | 6.1306 | 170.94 | 60.773 | 0.016464 | 139.05 | 1135 |  | 13893 | 170.94 | 6.1306 | 60.773 | 0.016464 | 139.05 | 1135 | 995.95
13894 | 6.132 | 170.95 | 60.773 | 0.016467 | 139.06 | 1135 |  | 13894 | 170.95 | 6.132 | 60.773 | 0.016467 | 139.06 | 1135 | 995.94
13895 | 6.1334 | 170.96 | 60.773 | 0.016471 | 139.07 | 1135 |  | 13895 | 170.96 | 6.1334 | 60.773 | 0.016471 | 139.07 | 1135 | 995.93
13896 | 6.1348 | 170.97 | 60.773 | 0.016474 | 139.08 | 1135 |  | 13896 | 170.97 | 6.1348 | 60.773 | 0.016474 | 139.08 | 1135 | 995.92
13897 | 6.1362 | 170.98 | 60.773 | 0.016478 | 139.09 | 1135 |  | 13897 | 170.98 | 6.1362 | 60.773 | 0.016478 | 139.09 | 1135 | 995.91
13898 | 6.1376 | 170.99 | 60.772 | 0.016481 | 139.1 | 1135 |  | 13898 | 170.99 | 6.1376 | 60.772 | 0.016481 | 139.1 | 1135 | 995.9
13899 | 6.139 | 171 | 60.772 | 0.016485 | 139.11 | 1135 |  | 13899 | 171 | 6.139 | 60.772 | 0.016485 | 139.11 | 1135 | 995.89
13900 | 6.1404 | 171.01 | 60.772 | 0.016488 | 139.12 | 1135.1 |  | 13900 | 171.01 | 6.1404 | 60.772 | 0.016488 | 139.12 | 1135.1 | 995.98
13901 | 6.1418 | 171.02 | 60.772 | 0.016492 | 139.13 | 1135.1 |  | 13901 | 171.02 | 6.1418 | 60.772 | 0.016492 | 139.13 | 1135.1 | 995.97
13902 | 6.1433 | 171.03 | 60.771 | 0.016495 | 139.14 | 1135.1 |  | 13902 | 171.03 | 6.1433 | 60.771 | 0.016495 | 139.14 | 1135.1 | 995.96
13903 | 6.1447 | 171.04 | 60.771 | 0.016499 | 139.15 | 1135.1 |  | 13903 | 171.04 | 6.1447 | 60.771 | 0.016499 | 139.15 | 1135.1 | 995.95
13904 | 6.1461 | 171.05 | 60.771 | 0.016503 | 139.16 | 1135.1 |  | 13904 | 171.05 | 6.1461 | 60.771 | 0.016503 | 139.16 | 1135.1 | 995.94
13905 | 6.1475 | 171.06 | 60.771 | 0.016506 | 139.17 | 1135.1 |  | 13905 | 171.06 | 6.1475 | 60.771 | 0.016506 | 139.17 | 1135.1 | 995.93
13906 | 6.1489 | 171.07 | 60.771 | 0.01651 | 139.18 | 1135.1 |  | 13906 | 171.07 | 6.1489 | 60.771 | 0.01651 | 139.18 | 1135.1 | 995.92
13907 | 6.1503 | 171.08 | 60.77 | 0.016513 | 139.19 | 1135.1 |  | 13907 | 171.08 | 6.1503 | 60.77 | 0.016513 | 139.19 | 1135.1 | 995.91
13908 | 6.1517 | 171.09 | 60.77 | 0.016517 | 139.2 | 1135.1 |  | 13908 | 171.09 | 6.1517 | 60.77 | 0.016517 | 139.2 | 1135.1 | 995.9
13909 | 6.1531 | 171.1 | 60.77 | 0.01652 | 139.21 | 1135.1 |  | 13909 | 171.1 | 6.1531 | 60.77 | 0.01652 | 139.21 | 1135.1 | 995.89
13910 | 6.1545 | 171.11 | 60.77 | 0.016524 | 139.22 | 1135.1 |  | 13910 | 171.11 | 6.1545 | 60.77 | 0.016524 | 139.22 | 1135.1 | 995.88
13911 | 6.1559 | 171.12 | 60.77 | 0.016527 | 139.23 | 1135.1 |  | 13911 | 171.12 | 6.1559 | 60.77 | 0.016527 | 139.23 | 1135.1 | 995.87
13912 | 6.1573 | 171.13 | 60.769 | 0.016531 | 139.24 | 1135.1 |  | 13912 | 171.13 | 6.1573 | 60.769 | 0.016531 | 139.24 | 1135.1 | 995.86
13913 | 6.1587 | 171.14 | 60.769 | 0.016534 | 139.25 | 1135.1 |  | 13913 | 171.14 | 6.1587 | 60.769 | 0.016534 | 139.25 | 1135.1 | 995.85
13914 | 6.1602 | 171.15 | 60.769 | 0.016538 | 139.26 | 1135.1 |  | 13914 | 171.15 | 6.1602 | 60.769 | 0.016538 | 139.26 | 1135.1 | 995.84
13915 | 6.1616 | 171.16 | 60.769 | 0.016541 | 139.27 | 1135.1 |  | 13915 | 171.16 | 6.1616 | 60.769 | 0.016541 | 139.27 | 1135.1 | 995.83
13916 | 6.163 | 171.17 | 60.769 | 0.016545 | 139.28 | 1135.1 |  | 13916 | 171.17 | 6.163 | 60.769 | 0.016545 | 139.28 | 1135.1 | 995.82
13917 | 6.1644 | 171.18 | 60.768 | 0.016549 | 139.29 | 1135.1 |  | 13917 | 171.18 | 6.1644 | 60.768 | 0.016549 | 139.29 | 1135.1 | 995.81
13918 | 6.1658 | 171.19 | 60.768 | 0.016552 | 139.3 | 1135.1 |  | 13918 | 171.19 | 6.1658 | 60.768 | 0.016552 | 139.3 | 1135.1 | 995.8
13919 | 6.1672 | 171.2 | 60.768 | 0.016556 | 139.31 | 1135.1 |  | 13919 | 171.2 | 6.1672 | 60.768 | 0.016556 | 139.31 | 1135.1 | 995.79
13920 | 6.1686 | 171.21 | 60.768 | 0.016559 | 139.32 | 1135.1 |  | 13920 | 171.21 | 6.1686 | 60.768 | 0.016559 | 139.32 | 1135.1 | 995.78
13921 | 6.17 | 171.22 | 60.767 | 0.016563 | 139.33 | 1135.1 |  | 13921 | 171.22 | 6.17 | 60.767 | 0.016563 | 139.33 | 1135.1 | 995.77
13922 | 6.1714 | 171.23 | 60.767 | 0.016566 | 139.34 | 1135.1 |  | 13922 | 171.23 | 6.1714 | 60.767 | 0.016566 | 139.34 | 1135.1 | 995.76
13923 | 6.1729 | 171.24 | 60.767 | 0.01657 | 139.35 | 1135.1 |  | 13923 | 171.24 | 6.1729 | 60.767 | 0.01657 | 139.35 | 1135.1 | 995.75
13924 | 6.1743 | 171.25 | 60.767 | 0.016573 | 139.36 | 1135.1 |  | 13924 | 171.25 | 6.1743 | 60.767 | 0.016573 | 139.36 | 1135.1 | 995.74
13925 | 6.1757 | 171.26 | 60.767 | 0.016577 | 139.37 | 1135.2 |  | 13925 | 171.26 | 6.1757 | 60.767 | 0.016577 | 139.37 | 1135.2 | 995.83
13926 | 6.1771 | 171.27 | 60.766 | 0.016581 | 139.38 | 1135.2 |  | 13926 | 171.27 | 6.1771 | 60.766 | 0.016581 | 139.38 | 1135.2 | 995.82
13927 | 6.1785 | 171.28 | 60.766 | 0.016584 | 139.39 | 1135.2 |  | 13927 | 171.28 | 6.1785 | 60.766 | 0.016584 | 139.39 | 1135.2 | 995.81
13928 | 6.1799 | 171.29 | 60.766 | 0.016588 | 139.4 | 1135.2 |  | 13928 | 171.29 | 6.1799 | 60.766 | 0.016588 | 139.4 | 1135.2 | 995.8
13929 | 6.1813 | 171.3 | 60.766 | 0.016591 | 139.41 | 1135.2 |  | 13929 | 171.3 | 6.1813 | 60.766 | 0.016591 | 139.41 | 1135.2 | 995.79
13930 | 6.1828 | 171.31 | 60.766 | 0.016595 | 139.42 | 1135.2 |  | 13930 | 171.31 | 6.1828 | 60.766 | 0.016595 | 139.42 | 1135.2 | 995.78
13931 | 6.1842 | 171.32 | 60.765 | 0.016598 | 139.43 | 1135.2 |  | 13931 | 171.32 | 6.1842 | 60.765 | 0.016598 | 139.43 | 1135.2 | 995.77
13932 | 6.1856 | 171.33 | 60.765 | 0.016602 | 139.44 | 1135.2 |  | 13932 | 171.33 | 6.1856 | 60.765 | 0.016602 | 139.44 | 1135.2 | 995.76
13933 | 6.187 | 171.34 | 60.765 | 0.016605 | 139.45 | 1135.2 |  | 13933 | 171.34 | 6.187 | 60.765 | 0.016605 | 139.45 | 1135.2 | 995.75
13934 | 6.1884 | 171.35 | 60.765 | 0.016609 | 139.46 | 1135.2 |  | 13934 | 171.35 | 6.1884 | 60.765 | 0.016609 | 139.46 | 1135.2 | 995.74
13935 | 6.1898 | 171.36 | 60.765 | 0.016613 | 139.47 | 1135.2 |  | 13935 | 171.36 | 6.1898 | 60.765 | 0.016613 | 139.47 | 1135.2 | 995.73
13936 | 6.1913 | 171.37 | 60.764 | 0.016616 | 139.48 | 1135.2 |  | 13936 | 171.37 | 6.1913 | 60.764 | 0.016616 | 139.48 | 1135.2 | 995.72
13937 | 6.1927 | 171.38 | 60.764 | 0.01662 | 139.49 | 1135.2 |  | 13937 | 171.38 | 6.1927 | 60.764 | 0.01662 | 139.49 | 1135.2 | 995.71
13938 | 6.1941 | 171.39 | 60.764 | 0.016623 | 139.5 | 1135.2 |  | 13938 | 171.39 | 6.1941 | 60.764 | 0.016623 | 139.5 | 1135.2 | 995.7
13939 | 6.1955 | 171.4 | 60.764 | 0.016627 | 139.51 | 1135.2 |  | 13939 | 171.4 | 6.1955 | 60.764 | 0.016627 | 139.51 | 1135.2 | 995.69
13940 | 6.1969 | 171.41 | 60.763 | 0.01663 | 139.52 | 1135.2 |  | 13940 | 171.41 | 6.1969 | 60.763 | 0.01663 | 139.52 | 1135.2 | 995.68
13941 | 6.1983 | 171.42 | 60.763 | 0.016634 | 139.53 | 1135.2 |  | 13941 | 171.42 | 6.1983 | 60.763 | 0.016634 | 139.53 | 1135.2 | 995.67
13942 | 6.1998 | 171.43 | 60.763 | 0.016637 | 139.54 | 1135.2 |  | 13942 | 171.43 | 6.1998 | 60.763 | 0.016637 | 139.54 | 1135.2 | 995.66
13943 | 6.2012 | 171.44 | 60.763 | 0.016641 | 139.55 | 1135.2 |  | 13943 | 171.44 | 6.2012 | 60.763 | 0.016641 | 139.55 | 1135.2 | 995.65
13944 | 6.2026 | 171.45 | 60.763 | 0.016645 | 139.56 | 1135.2 |  | 13944 | 171.45 | 6.2026 | 60.763 | 0.016645 | 139.56 | 1135.2 | 995.64
13945 | 6.204 | 171.46 | 60.762 | 0.016648 | 139.57 | 1135.2 |  | 13945 | 171.46 | 6.204 | 60.762 | 0.016648 | 139.57 | 1135.2 | 995.63
13946 | 6.2054 | 171.47 | 60.762 | 0.016652 | 139.58 | 1135.2 |  | 13946 | 171.47 | 6.2054 | 60.762 | 0.016652 | 139.58 | 1135.2 | 995.62
13947 | 6.2068 | 171.48 | 60.762 | 0.016655 | 139.59 | 1135.2 |  | 13947 | 171.48 | 6.2068 | 60.762 | 0.016655 | 139.59 | 1135.2 | 995.61
13948 | 6.2083 | 171.49 | 60.762 | 0.016659 | 139.6 | 1135.2 |  | 13948 | 171.49 | 6.2083 | 60.762 | 0.016659 | 139.6 | 1135.2 | 995.6
13949 | 6.2097 | 171.5 | 60.762 | 0.016662 | 139.61 | 1135.2 |  | 13949 | 171.5 | 6.2097 | 60.762 | 0.016662 | 139.61 | 1135.2 | 995.59
13950 | 6.2111 | 171.51 | 60.761 | 0.016666 | 139.62 | 1135.3 |  | 13950 | 171.51 | 6.2111 | 60.761 | 0.016666 | 139.62 | 1135.3 | 995.68
13951 | 6.2125 | 171.52 | 60.761 | 0.01667 | 139.63 | 1135.3 |  | 13951 | 171.52 | 6.2125 | 60.761 | 0.01667 | 139.63 | 1135.3 | 995.67
13952 | 6.2139 | 171.53 | 60.761 | 0.016673 | 139.64 | 1135.3 |  | 13952 | 171.53 | 6.2139 | 60.761 | 0.016673 | 139.64 | 1135.3 | 995.66
13953 | 6.2154 | 171.54 | 60.761 | 0.016677 | 139.65 | 1135.3 |  | 13953 | 171.54 | 6.2154 | 60.761 | 0.016677 | 139.65 | 1135.3 | 995.65
13954 | 6.2168 | 171.55 | 60.76 | 0.01668 | 139.66 | 1135.3 |  | 13954 | 171.55 | 6.2168 | 60.76 | 0.01668 | 139.66 | 1135.3 | 995.64
13955 | 6.2182 | 171.56 | 60.76 | 0.016684 | 139.67 | 1135.3 |  | 13955 | 171.56 | 6.2182 | 60.76 | 0.016684 | 139.67 | 1135.3 | 995.63
13956 | 6.2196 | 171.57 | 60.76 | 0.016687 | 139.68 | 1135.3 |  | 13956 | 171.57 | 6.2196 | 60.76 | 0.016687 | 139.68 | 1135.3 | 995.62
13957 | 6.2211 | 171.58 | 60.76 | 0.016691 | 139.69 | 1135.3 |  | 13957 | 171.58 | 6.2211 | 60.76 | 0.016691 | 139.69 | 1135.3 | 995.61
13958 | 6.2225 | 171.59 | 60.76 | 0.016695 | 139.7 | 1135.3 |  | 13958 | 171.59 | 6.2225 | 60.76 | 0.016695 | 139.7 | 1135.3 | 995.6
13959 | 6.2239 | 171.6 | 60.759 | 0.016698 | 139.71 | 1135.3 |  | 13959 | 171.6 | 6.2239 | 60.759 | 0.016698 | 139.71 | 1135.3 | 995.59
13960 | 6.2253 | 171.61 | 60.759 | 0.016702 | 139.72 | 1135.3 |  | 13960 | 171.61 | 6.2253 | 60.759 | 0.016702 | 139.72 | 1135.3 | 995.58
13961 | 6.2267 | 171.62 | 60.759 | 0.016705 | 139.73 | 1135.3 |  | 13961 | 171.62 | 6.2267 | 60.759 | 0.016705 | 139.73 | 1135.3 | 995.57
13962 | 6.2282 | 171.63 | 60.759 | 0.016709 | 139.74 | 1135.3 |  | 13962 | 171.63 | 6.2282 | 60.759 | 0.016709 | 139.74 | 1135.3 | 995.56
13963 | 6.2296 | 171.64 | 60.759 | 0.016712 | 139.75 | 1135.3 |  | 13963 | 171.64 | 6.2296 | 60.759 | 0.016712 | 139.75 | 1135.3 | 995.55
13964 | 6.231 | 171.65 | 60.758 | 0.016716 | 139.76 | 1135.3 |  | 13964 | 171.65 | 6.231 | 60.758 | 0.016716 | 139.76 | 1135.3 | 995.54
13965 | 6.2324 | 171.66 | 60.758 | 0.01672 | 139.77 | 1135.3 |  | 13965 | 171.66 | 6.2324 | 60.758 | 0.01672 | 139.77 | 1135.3 | 995.53
13966 | 6.2339 | 171.67 | 60.758 | 0.016723 | 139.78 | 1135.3 |  | 13966 | 171.67 | 6.2339 | 60.758 | 0.016723 | 139.78 | 1135.3 | 995.52
13967 | 6.2353 | 171.68 | 60.758 | 0.016727 | 139.79 | 1135.3 |  | 13967 | 171.68 | 6.2353 | 60.758 | 0.016727 | 139.79 | 1135.3 | 995.51
13968 | 6.2367 | 171.69 | 60.758 | 0.01673 | 139.8 | 1135.3 |  | 13968 | 171.69 | 6.2367 | 60.758 | 0.01673 | 139.8 | 1135.3 | 995.5
13969 | 6.2381 | 171.7 | 60.757 | 0.016734 | 139.81 | 1135.3 |  | 13969 | 171.7 | 6.2381 | 60.757 | 0.016734 | 139.81 | 1135.3 | 995.49
13970 | 6.2396 | 171.71 | 60.757 | 0.016737 | 139.82 | 1135.3 |  | 13970 | 171.71 | 6.2396 | 60.757 | 0.016737 | 139.82 | 1135.3 | 995.48
13971 | 6.241 | 171.72 | 60.757 | 0.016741 | 139.83 | 1135.3 |  | 13971 | 171.72 | 6.241 | 60.757 | 0.016741 | 139.83 | 1135.3 | 995.47
13972 | 6.2424 | 171.73 | 60.757 | 0.016745 | 139.84 | 1135.3 |  | 13972 | 171.73 | 6.2424 | 60.757 | 0.016745 | 139.84 | 1135.3 | 995.46
13973 | 6.2438 | 171.74 | 60.756 | 0.016748 | 139.85 | 1135.3 |  | 13973 | 171.74 | 6.2438 | 60.756 | 0.016748 | 139.85 | 1135.3 | 995.45
13974 | 6.2453 | 171.75 | 60.756 | 0.016752 | 139.86 | 1135.3 |  | 13974 | 171.75 | 6.2453 | 60.756 | 0.016752 | 139.86 | 1135.3 | 995.44
13975 | 6.2467 | 171.76 | 60.756 | 0.016755 | 139.87 | 1135.4 |  | 13975 | 171.76 | 6.2467 | 60.756 | 0.016755 | 139.87 | 1135.4 | 995.53
13976 | 6.2481 | 171.77 | 60.756 | 0.016759 | 139.88 | 1135.4 |  | 13976 | 171.77 | 6.2481 | 60.756 | 0.016759 | 139.88 | 1135.4 | 995.52
13977 | 6.2495 | 171.78 | 60.756 | 0.016763 | 139.89 | 1135.4 |  | 13977 | 171.78 | 6.2495 | 60.756 | 0.016763 | 139.89 | 1135.4 | 995.51
13978 | 6.251 | 171.79 | 60.755 | 0.016766 | 139.9 | 1135.4 |  | 13978 | 171.79 | 6.251 | 60.755 | 0.016766 | 139.9 | 1135.4 | 995.5
13979 | 6.2524 | 171.8 | 60.755 | 0.01677 | 139.91 | 1135.4 |  | 13979 | 171.8 | 6.2524 | 60.755 | 0.01677 | 139.91 | 1135.4 | 995.49
13980 | 6.2538 | 171.81 | 60.755 | 0.016773 | 139.92 | 1135.4 |  | 13980 | 171.81 | 6.2538 | 60.755 | 0.016773 | 139.92 | 1135.4 | 995.48
13981 | 6.2553 | 171.82 | 60.755 | 0.016777 | 139.93 | 1135.4 |  | 13981 | 171.82 | 6.2553 | 60.755 | 0.016777 | 139.93 | 1135.4 | 995.47
13982 | 6.2567 | 171.83 | 60.755 | 0.016781 | 139.94 | 1135.4 |  | 13982 | 171.83 | 6.2567 | 60.755 | 0.016781 | 139.94 | 1135.4 | 995.46
13983 | 6.2581 | 171.84 | 60.754 | 0.016784 | 139.95 | 1135.4 |  | 13983 | 171.84 | 6.2581 | 60.754 | 0.016784 | 139.95 | 1135.4 | 995.45
13984 | 6.2595 | 171.85 | 60.754 | 0.016788 | 139.96 | 1135.4 |  | 13984 | 171.85 | 6.2595 | 60.754 | 0.016788 | 139.96 | 1135.4 | 995.44
13985 | 6.261 | 171.86 | 60.754 | 0.016791 | 139.97 | 1135.4 |  | 13985 | 171.86 | 6.261 | 60.754 | 0.016791 | 139.97 | 1135.4 | 995.43
13986 | 6.2624 | 171.87 | 60.754 | 0.016795 | 139.98 | 1135.4 |  | 13986 | 171.87 | 6.2624 | 60.754 | 0.016795 | 139.98 | 1135.4 | 995.42
13987 | 6.2638 | 171.88 | 60.753 | 0.016798 | 139.99 | 1135.4 |  | 13987 | 171.88 | 6.2638 | 60.753 | 0.016798 | 139.99 | 1135.4 | 995.41
13988 | 6.2653 | 171.89 | 60.753 | 0.016802 | 140 | 1135.4 |  | 13988 | 171.89 | 6.2653 | 60.753 | 0.016802 | 140 | 1135.4 | 995.4
13989 | 6.2667 | 171.9 | 60.753 | 0.016806 | 140.01 | 1135.4 |  | 13989 | 171.9 | 6.2667 | 60.753 | 0.016806 | 140.01 | 1135.4 | 995.39
13990 | 6.2681 | 171.91 | 60.753 | 0.016809 | 140.02 | 1135.4 |  | 13990 | 171.91 | 6.2681 | 60.753 | 0.016809 | 140.02 | 1135.4 | 995.38
13991 | 6.2696 | 171.92 | 60.753 | 0.016813 | 140.03 | 1135.4 |  | 13991 | 171.92 | 6.2696 | 60.753 | 0.016813 | 140.03 | 1135.4 | 995.37
13992 | 6.271 | 171.93 | 60.752 | 0.016816 | 140.04 | 1135.4 |  | 13992 | 171.93 | 6.271 | 60.752 | 0.016816 | 140.04 | 1135.4 | 995.36
13993 | 6.2724 | 171.94 | 60.752 | 0.01682 | 140.05 | 1135.4 |  | 13993 | 171.94 | 6.2724 | 60.752 | 0.01682 | 140.05 | 1135.4 | 995.35
13994 | 6.2739 | 171.95 | 60.752 | 0.016824 | 140.06 | 1135.4 |  | 13994 | 171.95 | 6.2739 | 60.752 | 0.016824 | 140.06 | 1135.4 | 995.34
13995 | 6.2753 | 171.96 | 60.752 | 0.016827 | 140.07 | 1135.4 |  | 13995 | 171.96 | 6.2753 | 60.752 | 0.016827 | 140.07 | 1135.4 | 995.33
13996 | 6.2767 | 171.97 | 60.752 | 0.016831 | 140.08 | 1135.4 |  | 13996 | 171.97 | 6.2767 | 60.752 | 0.016831 | 140.08 | 1135.4 | 995.32
13997 | 6.2782 | 171.98 | 60.751 | 0.016834 | 140.09 | 1135.4 |  | 13997 | 171.98 | 6.2782 | 60.751 | 0.016834 | 140.09 | 1135.4 | 995.31
13998 | 6.2796 | 171.99 | 60.751 | 0.016838 | 140.1 | 1135.4 |  | 13998 | 171.99 | 6.2796 | 60.751 | 0.016838 | 140.1 | 1135.4 | 995.3
13999 | 6.281 | 172 | 60.751 | 0.016842 | 140.11 | 1135.4 |  | 13999 | 172 | 6.281 | 60.751 | 0.016842 | 140.11 | 1135.4 | 995.29
14000 | 6.2825 | 172.01 | 60.751 | 0.016845 | 140.12 | 1135.5 |  | 14000 | 172.01 | 6.2825 | 60.751 | 0.016845 | 140.12 | 1135.5 | 995.38
14001 | 6.2839 | 172.02 | 60.751 | 0.016849 | 140.13 | 1135.5 |  | 14001 | 172.02 | 6.2839 | 60.751 | 0.016849 | 140.13 | 1135.5 | 995.37
14002 | 6.2853 | 172.03 | 60.75 | 0.016852 | 140.14 | 1135.5 |  | 14002 | 172.03 | 6.2853 | 60.75 | 0.016852 | 140.14 | 1135.5 | 995.36
14003 | 6.2868 | 172.04 | 60.75 | 0.016856 | 140.15 | 1135.5 |  | 14003 | 172.04 | 6.2868 | 60.75 | 0.016856 | 140.15 | 1135.5 | 995.35
14004 | 6.2882 | 172.05 | 60.75 | 0.01686 | 140.16 | 1135.5 |  | 14004 | 172.05 | 6.2882 | 60.75 | 0.01686 | 140.16 | 1135.5 | 995.34
14005 | 6.2896 | 172.06 | 60.75 | 0.016863 | 140.17 | 1135.5 |  | 14005 | 172.06 | 6.2896 | 60.75 | 0.016863 | 140.17 | 1135.5 | 995.33
14006 | 6.2911 | 172.07 | 60.749 | 0.016867 | 140.18 | 1135.5 |  | 14006 | 172.07 | 6.2911 | 60.749 | 0.016867 | 140.18 | 1135.5 | 995.32
14007 | 6.2925 | 172.08 | 60.749 | 0.01687 | 140.19 | 1135.5 |  | 14007 | 172.08 | 6.2925 | 60.749 | 0.01687 | 140.19 | 1135.5 | 995.31
14008 | 6.2939 | 172.09 | 60.749 | 0.016874 | 140.2 | 1135.5 |  | 14008 | 172.09 | 6.2939 | 60.749 | 0.016874 | 140.2 | 1135.5 | 995.3
14009 | 6.2954 | 172.1 | 60.749 | 0.016878 | 140.21 | 1135.5 |  | 14009 | 172.1 | 6.2954 | 60.749 | 0.016878 | 140.21 | 1135.5 | 995.29
14010 | 6.2968 | 172.11 | 60.749 | 0.016881 | 140.22 | 1135.5 |  | 14010 | 172.11 | 6.2968 | 60.749 | 0.016881 | 140.22 | 1135.5 | 995.28
14011 | 6.2982 | 172.12 | 60.748 | 0.016885 | 140.23 | 1135.5 |  | 14011 | 172.12 | 6.2982 | 60.748 | 0.016885 | 140.23 | 1135.5 | 995.27
14012 | 6.2997 | 172.13 | 60.748 | 0.016888 | 140.24 | 1135.5 |  | 14012 | 172.13 | 6.2997 | 60.748 | 0.016888 | 140.24 | 1135.5 | 995.26
14013 | 6.3011 | 172.14 | 60.748 | 0.016892 | 140.25 | 1135.5 |  | 14013 | 172.14 | 6.3011 | 60.748 | 0.016892 | 140.25 | 1135.5 | 995.25
14014 | 6.3026 | 172.15 | 60.748 | 0.016896 | 140.26 | 1135.5 |  | 14014 | 172.15 | 6.3026 | 60.748 | 0.016896 | 140.26 | 1135.5 | 995.24
14015 | 6.304 | 172.16 | 60.748 | 0.016899 | 140.27 | 1135.5 |  | 14015 | 172.16 | 6.304 | 60.748 | 0.016899 | 140.27 | 1135.5 | 995.23
14016 | 6.3054 | 172.17 | 60.747 | 0.016903 | 140.28 | 1135.5 |  | 14016 | 172.17 | 6.3054 | 60.747 | 0.016903 | 140.28 | 1135.5 | 995.22
14017 | 6.3069 | 172.18 | 60.747 | 0.016907 | 140.29 | 1135.5 |  | 14017 | 172.18 | 6.3069 | 60.747 | 0.016907 | 140.29 | 1135.5 | 995.21
14018 | 6.3083 | 172.19 | 60.747 | 0.01691 | 140.3 | 1135.5 |  | 14018 | 172.19 | 6.3083 | 60.747 | 0.01691 | 140.3 | 1135.5 | 995.2
14019 | 6.3097 | 172.2 | 60.747 | 0.016914 | 140.31 | 1135.5 |  | 14019 | 172.2 | 6.3097 | 60.747 | 0.016914 | 140.31 | 1135.5 | 995.19
14020 | 6.3112 | 172.21 | 60.747 | 0.016917 | 140.32 | 1135.5 |  | 14020 | 172.21 | 6.3112 | 60.747 | 0.016917 | 140.32 | 1135.5 | 995.18
14021 | 6.3126 | 172.22 | 60.746 | 0.016921 | 140.33 | 1135.5 |  | 14021 | 172.22 | 6.3126 | 60.746 | 0.016921 | 140.33 | 1135.5 | 995.17
14022 | 6.3141 | 172.23 | 60.746 | 0.016925 | 140.34 | 1135.5 |  | 14022 | 172.23 | 6.3141 | 60.746 | 0.016925 | 140.34 | 1135.5 | 995.16
14023 | 6.3155 | 172.24 | 60.746 | 0.016928 | 140.35 | 1135.5 |  | 14023 | 172.24 | 6.3155 | 60.746 | 0.016928 | 140.35 | 1135.5 | 995.15
14024 | 6.3169 | 172.25 | 60.746 | 0.016932 | 140.36 | 1135.5 |  | 14024 | 172.25 | 6.3169 | 60.746 | 0.016932 | 140.36 | 1135.5 | 995.14
14025 | 6.3184 | 172.26 | 60.745 | 0.016935 | 140.37 | 1135.6 |  | 14025 | 172.26 | 6.3184 | 60.745 | 0.016935 | 140.37 | 1135.6 | 995.23
14026 | 6.3198 | 172.27 | 60.745 | 0.016939 | 140.38 | 1135.6 |  | 14026 | 172.27 | 6.3198 | 60.745 | 0.016939 | 140.38 | 1135.6 | 995.22
14027 | 6.3213 | 172.28 | 60.745 | 0.016943 | 140.39 | 1135.6 |  | 14027 | 172.28 | 6.3213 | 60.745 | 0.016943 | 140.39 | 1135.6 | 995.21
14028 | 6.3227 | 172.29 | 60.745 | 0.016946 | 140.4 | 1135.6 |  | 14028 | 172.29 | 6.3227 | 60.745 | 0.016946 | 140.4 | 1135.6 | 995.2
14029 | 6.3241 | 172.3 | 60.745 | 0.01695 | 140.41 | 1135.6 |  | 14029 | 172.3 | 6.3241 | 60.745 | 0.01695 | 140.41 | 1135.6 | 995.19
14030 | 6.3256 | 172.31 | 60.744 | 0.016954 | 140.42 | 1135.6 |  | 14030 | 172.31 | 6.3256 | 60.744 | 0.016954 | 140.42 | 1135.6 | 995.18
14031 | 6.327 | 172.32 | 60.744 | 0.016957 | 140.43 | 1135.6 |  | 14031 | 172.32 | 6.327 | 60.744 | 0.016957 | 140.43 | 1135.6 | 995.17
14032 | 6.3285 | 172.33 | 60.744 | 0.016961 | 140.44 | 1135.6 |  | 14032 | 172.33 | 6.3285 | 60.744 | 0.016961 | 140.44 | 1135.6 | 995.16
14033 | 6.3299 | 172.34 | 60.744 | 0.016964 | 140.45 | 1135.6 |  | 14033 | 172.34 | 6.3299 | 60.744 | 0.016964 | 140.45 | 1135.6 | 995.15
14034 | 6.3314 | 172.35 | 60.744 | 0.016968 | 140.46 | 1135.6 |  | 14034 | 172.35 | 6.3314 | 60.744 | 0.016968 | 140.46 | 1135.6 | 995.14
14035 | 6.3328 | 172.36 | 60.743 | 0.016972 | 140.47 | 1135.6 |  | 14035 | 172.36 | 6.3328 | 60.743 | 0.016972 | 140.47 | 1135.6 | 995.13
14036 | 6.3342 | 172.37 | 60.743 | 0.016975 | 140.48 | 1135.6 |  | 14036 | 172.37 | 6.3342 | 60.743 | 0.016975 | 140.48 | 1135.6 | 995.12
14037 | 6.3357 | 172.38 | 60.743 | 0.016979 | 140.49 | 1135.6 |  | 14037 | 172.38 | 6.3357 | 60.743 | 0.016979 | 140.49 | 1135.6 | 995.11
14038 | 6.3371 | 172.39 | 60.743 | 0.016982 | 140.5 | 1135.6 |  | 14038 | 172.39 | 6.3371 | 60.743 | 0.016982 | 140.5 | 1135.6 | 995.1
14039 | 6.3386 | 172.4 | 60.742 | 0.016986 | 140.51 | 1135.6 |  | 14039 | 172.4 | 6.3386 | 60.742 | 0.016986 | 140.51 | 1135.6 | 995.09
14040 | 6.34 | 172.41 | 60.742 | 0.01699 | 140.52 | 1135.6 |  | 14040 | 172.41 | 6.34 | 60.742 | 0.01699 | 140.52 | 1135.6 | 995.08
14041 | 6.3415 | 172.42 | 60.742 | 0.016993 | 140.53 | 1135.6 |  | 14041 | 172.42 | 6.3415 | 60.742 | 0.016993 | 140.53 | 1135.6 | 995.07
14042 | 6.3429 | 172.43 | 60.742 | 0.016997 | 140.54 | 1135.6 |  | 14042 | 172.43 | 6.3429 | 60.742 | 0.016997 | 140.54 | 1135.6 | 995.06
14043 | 6.3444 | 172.44 | 60.742 | 0.017001 | 140.55 | 1135.6 |  | 14043 | 172.44 | 6.3444 | 60.742 | 0.017001 | 140.55 | 1135.6 | 995.05
14044 | 6.3458 | 172.45 | 60.741 | 0.017004 | 140.56 | 1135.6 |  | 14044 | 172.45 | 6.3458 | 60.741 | 0.017004 | 140.56 | 1135.6 | 995.04
14045 | 6.3473 | 172.46 | 60.741 | 0.017008 | 140.57 | 1135.6 |  | 14045 | 172.46 | 6.3473 | 60.741 | 0.017008 | 140.57 | 1135.6 | 995.03
14046 | 6.3487 | 172.47 | 60.741 | 0.017012 | 140.58 | 1135.6 |  | 14046 | 172.47 | 6.3487 | 60.741 | 0.017012 | 140.58 | 1135.6 | 995.02
14047 | 6.3501 | 172.48 | 60.741 | 0.017015 | 140.59 | 1135.6 |  | 14047 | 172.48 | 6.3501 | 60.741 | 0.017015 | 140.59 | 1135.6 | 995.01
14048 | 6.3516 | 172.49 | 60.741 | 0.017019 | 140.6 | 1135.6 |  | 14048 | 172.49 | 6.3516 | 60.741 | 0.017019 | 140.6 | 1135.6 | 995
14049 | 6.353 | 172.5 | 60.74 | 0.017022 | 140.61 | 1135.7 |  | 14049 | 172.5 | 6.353 | 60.74 | 0.017022 | 140.61 | 1135.7 | 995.09
14050 | 6.3545 | 172.51 | 60.74 | 0.017026 | 140.62 | 1135.7 |  | 14050 | 172.51 | 6.3545 | 60.74 | 0.017026 | 140.62 | 1135.7 | 995.08
14051 | 6.3559 | 172.52 | 60.74 | 0.01703 | 140.63 | 1135.7 |  | 14051 | 172.52 | 6.3559 | 60.74 | 0.01703 | 140.63 | 1135.7 | 995.07
14052 | 6.3574 | 172.53 | 60.74 | 0.017033 | 140.64 | 1135.7 |  | 14052 | 172.53 | 6.3574 | 60.74 | 0.017033 | 140.64 | 1135.7 | 995.06
14053 | 6.3588 | 172.54 | 60.739 | 0.017037 | 140.65 | 1135.7 |  | 14053 | 172.54 | 6.3588 | 60.739 | 0.017037 | 140.65 | 1135.7 | 995.05
14054 | 6.3603 | 172.55 | 60.739 | 0.017041 | 140.66 | 1135.7 |  | 14054 | 172.55 | 6.3603 | 60.739 | 0.017041 | 140.66 | 1135.7 | 995.04
14055 | 6.3617 | 172.56 | 60.739 | 0.017044 | 140.67 | 1135.7 |  | 14055 | 172.56 | 6.3617 | 60.739 | 0.017044 | 140.67 | 1135.7 | 995.03
14056 | 6.3632 | 172.57 | 60.739 | 0.017048 | 140.68 | 1135.7 |  | 14056 | 172.57 | 6.3632 | 60.739 | 0.017048 | 140.68 | 1135.7 | 995.02
14057 | 6.3646 | 172.58 | 60.739 | 0.017051 | 140.69 | 1135.7 |  | 14057 | 172.58 | 6.3646 | 60.739 | 0.017051 | 140.69 | 1135.7 | 995.01
14058 | 6.3661 | 172.59 | 60.738 | 0.017055 | 140.7 | 1135.7 |  | 14058 | 172.59 | 6.3661 | 60.738 | 0.017055 | 140.7 | 1135.7 | 995
14059 | 6.3675 | 172.6 | 60.738 | 0.017059 | 140.71 | 1135.7 |  | 14059 | 172.6 | 6.3675 | 60.738 | 0.017059 | 140.71 | 1135.7 | 994.99
14060 | 6.369 | 172.61 | 60.738 | 0.017062 | 140.72 | 1135.7 |  | 14060 | 172.61 | 6.369 | 60.738 | 0.017062 | 140.72 | 1135.7 | 994.98
14061 | 6.3704 | 172.62 | 60.738 | 0.017066 | 140.73 | 1135.7 |  | 14061 | 172.62 | 6.3704 | 60.738 | 0.017066 | 140.73 | 1135.7 | 994.97
14062 | 6.3719 | 172.63 | 60.738 | 0.01707 | 140.74 | 1135.7 |  | 14062 | 172.63 | 6.3719 | 60.738 | 0.01707 | 140.74 | 1135.7 | 994.96
14063 | 6.3733 | 172.64 | 60.737 | 0.017073 | 140.75 | 1135.7 |  | 14063 | 172.64 | 6.3733 | 60.737 | 0.017073 | 140.75 | 1135.7 | 994.95
14064 | 6.3748 | 172.65 | 60.737 | 0.017077 | 140.76 | 1135.7 |  | 14064 | 172.65 | 6.3748 | 60.737 | 0.017077 | 140.76 | 1135.7 | 994.94
14065 | 6.3762 | 172.66 | 60.737 | 0.017081 | 140.77 | 1135.7 |  | 14065 | 172.66 | 6.3762 | 60.737 | 0.017081 | 140.77 | 1135.7 | 994.93
14066 | 6.3777 | 172.67 | 60.737 | 0.017084 | 140.78 | 1135.7 |  | 14066 | 172.67 | 6.3777 | 60.737 | 0.017084 | 140.78 | 1135.7 | 994.92
14067 | 6.3791 | 172.68 | 60.737 | 0.017088 | 140.79 | 1135.7 |  | 14067 | 172.68 | 6.3791 | 60.737 | 0.017088 | 140.79 | 1135.7 | 994.91
14068 | 6.3806 | 172.69 | 60.736 | 0.017092 | 140.8 | 1135.7 |  | 14068 | 172.69 | 6.3806 | 60.736 | 0.017092 | 140.8 | 1135.7 | 994.9
14069 | 6.382 | 172.7 | 60.736 | 0.017095 | 140.81 | 1135.7 |  | 14069 | 172.7 | 6.382 | 60.736 | 0.017095 | 140.81 | 1135.7 | 994.89
14070 | 6.3835 | 172.71 | 60.736 | 0.017099 | 140.83 | 1135.7 |  | 14070 | 172.71 | 6.3835 | 60.736 | 0.017099 | 140.83 | 1135.7 | 994.87
14071 | 6.3849 | 172.72 | 60.736 | 0.017102 | 140.84 | 1135.7 |  | 14071 | 172.72 | 6.3849 | 60.736 | 0.017102 | 140.84 | 1135.7 | 994.86
14072 | 6.3864 | 172.73 | 60.735 | 0.017106 | 140.85 | 1135.7 |  | 14072 | 172.73 | 6.3864 | 60.735 | 0.017106 | 140.85 | 1135.7 | 994.85
14073 | 6.3879 | 172.74 | 60.735 | 0.01711 | 140.86 | 1135.7 |  | 14073 | 172.74 | 6.3879 | 60.735 | 0.01711 | 140.86 | 1135.7 | 994.84
14074 | 6.3893 | 172.75 | 60.735 | 0.017113 | 140.87 | 1135.8 |  | 14074 | 172.75 | 6.3893 | 60.735 | 0.017113 | 140.87 | 1135.8 | 994.93
14075 | 6.3908 | 172.76 | 60.735 | 0.017117 | 140.88 | 1135.8 |  | 14075 | 172.76 | 6.3908 | 60.735 | 0.017117 | 140.88 | 1135.8 | 994.92
14076 | 6.3922 | 172.77 | 60.735 | 0.017121 | 140.89 | 1135.8 |  | 14076 | 172.77 | 6.3922 | 60.735 | 0.017121 | 140.89 | 1135.8 | 994.91
14077 | 6.3937 | 172.78 | 60.734 | 0.017124 | 140.9 | 1135.8 |  | 14077 | 172.78 | 6.3937 | 60.734 | 0.017124 | 140.9 | 1135.8 | 994.9
14078 | 6.3951 | 172.79 | 60.734 | 0.017128 | 140.91 | 1135.8 |  | 14078 | 172.79 | 6.3951 | 60.734 | 0.017128 | 140.91 | 1135.8 | 994.89
14079 | 6.3966 | 172.8 | 60.734 | 0.017132 | 140.92 | 1135.8 |  | 14079 | 172.8 | 6.3966 | 60.734 | 0.017132 | 140.92 | 1135.8 | 994.88
14080 | 6.398 | 172.81 | 60.734 | 0.017135 | 140.93 | 1135.8 |  | 14080 | 172.81 | 6.398 | 60.734 | 0.017135 | 140.93 | 1135.8 | 994.87
14081 | 6.3995 | 172.82 | 60.734 | 0.017139 | 140.94 | 1135.8 |  | 14081 | 172.82 | 6.3995 | 60.734 | 0.017139 | 140.94 | 1135.8 | 994.86
14082 | 6.401 | 172.83 | 60.733 | 0.017143 | 140.95 | 1135.8 |  | 14082 | 172.83 | 6.401 | 60.733 | 0.017143 | 140.95 | 1135.8 | 994.85
14083 | 6.4024 | 172.84 | 60.733 | 0.017146 | 140.96 | 1135.8 |  | 14083 | 172.84 | 6.4024 | 60.733 | 0.017146 | 140.96 | 1135.8 | 994.84
14084 | 6.4039 | 172.85 | 60.733 | 0.01715 | 140.97 | 1135.8 |  | 14084 | 172.85 | 6.4039 | 60.733 | 0.01715 | 140.97 | 1135.8 | 994.83
14085 | 6.4053 | 172.86 | 60.733 | 0.017154 | 140.98 | 1135.8 |  | 14085 | 172.86 | 6.4053 | 60.733 | 0.017154 | 140.98 | 1135.8 | 994.82
14086 | 6.4068 | 172.87 | 60.732 | 0.017157 | 140.99 | 1135.8 |  | 14086 | 172.87 | 6.4068 | 60.732 | 0.017157 | 140.99 | 1135.8 | 994.81
14087 | 6.4082 | 172.88 | 60.732 | 0.017161 | 141 | 1135.8 |  | 14087 | 172.88 | 6.4082 | 60.732 | 0.017161 | 141 | 1135.8 | 994.8
14088 | 6.4097 | 172.89 | 60.732 | 0.017165 | 141.01 | 1135.8 |  | 14088 | 172.89 | 6.4097 | 60.732 | 0.017165 | 141.01 | 1135.8 | 994.79
14089 | 6.4112 | 172.9 | 60.732 | 0.017168 | 141.02 | 1135.8 |  | 14089 | 172.9 | 6.4112 | 60.732 | 0.017168 | 141.02 | 1135.8 | 994.78
14090 | 6.4126 | 172.91 | 60.732 | 0.017172 | 141.03 | 1135.8 |  | 14090 | 172.91 | 6.4126 | 60.732 | 0.017172 | 141.03 | 1135.8 | 994.77
14091 | 6.4141 | 172.92 | 60.731 | 0.017175 | 141.04 | 1135.8 |  | 14091 | 172.92 | 6.4141 | 60.731 | 0.017175 | 141.04 | 1135.8 | 994.76
14092 | 6.4155 | 172.93 | 60.731 | 0.017179 | 141.05 | 1135.8 |  | 14092 | 172.93 | 6.4155 | 60.731 | 0.017179 | 141.05 | 1135.8 | 994.75
14093 | 6.417 | 172.94 | 60.731 | 0.017183 | 141.06 | 1135.8 |  | 14093 | 172.94 | 6.417 | 60.731 | 0.017183 | 141.06 | 1135.8 | 994.74
14094 | 6.4185 | 172.95 | 60.731 | 0.017186 | 141.07 | 1135.8 |  | 14094 | 172.95 | 6.4185 | 60.731 | 0.017186 | 141.07 | 1135.8 | 994.73
14095 | 6.4199 | 172.96 | 60.731 | 0.01719 | 141.08 | 1135.8 |  | 14095 | 172.96 | 6.4199 | 60.731 | 0.01719 | 141.08 | 1135.8 | 994.72
14096 | 6.4214 | 172.97 | 60.73 | 0.017194 | 141.09 | 1135.8 |  | 14096 | 172.97 | 6.4214 | 60.73 | 0.017194 | 141.09 | 1135.8 | 994.71
14097 | 6.4228 | 172.98 | 60.73 | 0.017197 | 141.1 | 1135.8 |  | 14097 | 172.98 | 6.4228 | 60.73 | 0.017197 | 141.1 | 1135.8 | 994.7
14098 | 6.4243 | 172.99 | 60.73 | 0.017201 | 141.11 | 1135.8 |  | 14098 | 172.99 | 6.4243 | 60.73 | 0.017201 | 141.11 | 1135.8 | 994.69
14099 | 6.4258 | 173 | 60.73 | 0.017205 | 141.12 | 1135.9 |  | 14099 | 173 | 6.4258 | 60.73 | 0.017205 | 141.12 | 1135.9 | 994.78
14100 | 6.4272 | 173.01 | 60.729 | 0.017208 | 141.13 | 1135.9 |  | 14100 | 173.01 | 6.4272 | 60.729 | 0.017208 | 141.13 | 1135.9 | 994.77
14101 | 6.4287 | 173.02 | 60.729 | 0.017212 | 141.14 | 1135.9 |  | 14101 | 173.02 | 6.4287 | 60.729 | 0.017212 | 141.14 | 1135.9 | 994.76
14102 | 6.4301 | 173.03 | 60.729 | 0.017216 | 141.15 | 1135.9 |  | 14102 | 173.03 | 6.4301 | 60.729 | 0.017216 | 141.15 | 1135.9 | 994.75
14103 | 6.4316 | 173.04 | 60.729 | 0.017219 | 141.16 | 1135.9 |  | 14103 | 173.04 | 6.4316 | 60.729 | 0.017219 | 141.16 | 1135.9 | 994.74
14104 | 6.4331 | 173.05 | 60.729 | 0.017223 | 141.17 | 1135.9 |  | 14104 | 173.05 | 6.4331 | 60.729 | 0.017223 | 141.17 | 1135.9 | 994.73
14105 | 6.4345 | 173.06 | 60.728 | 0.017227 | 141.18 | 1135.9 |  | 14105 | 173.06 | 6.4345 | 60.728 | 0.017227 | 141.18 | 1135.9 | 994.72
14106 | 6.436 | 173.07 | 60.728 | 0.01723 | 141.19 | 1135.9 |  | 14106 | 173.07 | 6.436 | 60.728 | 0.01723 | 141.19 | 1135.9 | 994.71
14107 | 6.4375 | 173.08 | 60.728 | 0.017234 | 141.2 | 1135.9 |  | 14107 | 173.08 | 6.4375 | 60.728 | 0.017234 | 141.2 | 1135.9 | 994.7
14108 | 6.4389 | 173.09 | 60.728 | 0.017238 | 141.21 | 1135.9 |  | 14108 | 173.09 | 6.4389 | 60.728 | 0.017238 | 141.21 | 1135.9 | 994.69
14109 | 6.4404 | 173.1 | 60.728 | 0.017241 | 141.22 | 1135.9 |  | 14109 | 173.1 | 6.4404 | 60.728 | 0.017241 | 141.22 | 1135.9 | 994.68
14110 | 6.4418 | 173.11 | 60.727 | 0.017245 | 141.23 | 1135.9 |  | 14110 | 173.11 | 6.4418 | 60.727 | 0.017245 | 141.23 | 1135.9 | 994.67
14111 | 6.4433 | 173.12 | 60.727 | 0.017249 | 141.24 | 1135.9 |  | 14111 | 173.12 | 6.4433 | 60.727 | 0.017249 | 141.24 | 1135.9 | 994.66
14112 | 6.4448 | 173.13 | 60.727 | 0.017252 | 141.25 | 1135.9 |  | 14112 | 173.13 | 6.4448 | 60.727 | 0.017252 | 141.25 | 1135.9 | 994.65
14113 | 6.4462 | 173.14 | 60.727 | 0.017256 | 141.26 | 1135.9 |  | 14113 | 173.14 | 6.4462 | 60.727 | 0.017256 | 141.26 | 1135.9 | 994.64
14114 | 6.4477 | 173.15 | 60.727 | 0.01726 | 141.27 | 1135.9 |  | 14114 | 173.15 | 6.4477 | 60.727 | 0.01726 | 141.27 | 1135.9 | 994.63
14115 | 6.4492 | 173.16 | 60.726 | 0.017263 | 141.28 | 1135.9 |  | 14115 | 173.16 | 6.4492 | 60.726 | 0.017263 | 141.28 | 1135.9 | 994.62
14116 | 6.4506 | 173.17 | 60.726 | 0.017267 | 141.29 | 1135.9 |  | 14116 | 173.17 | 6.4506 | 60.726 | 0.017267 | 141.29 | 1135.9 | 994.61
14117 | 6.4521 | 173.18 | 60.726 | 0.017271 | 141.3 | 1135.9 |  | 14117 | 173.18 | 6.4521 | 60.726 | 0.017271 | 141.3 | 1135.9 | 994.6
14118 | 6.4536 | 173.19 | 60.726 | 0.017275 | 141.31 | 1135.9 |  | 14118 | 173.19 | 6.4536 | 60.726 | 0.017275 | 141.31 | 1135.9 | 994.59
14119 | 6.455 | 173.2 | 60.725 | 0.017278 | 141.32 | 1135.9 |  | 14119 | 173.2 | 6.455 | 60.725 | 0.017278 | 141.32 | 1135.9 | 994.58
14120 | 6.4565 | 173.21 | 60.725 | 0.017282 | 141.33 | 1135.9 |  | 14120 | 173.21 | 6.4565 | 60.725 | 0.017282 | 141.33 | 1135.9 | 994.57
14121 | 6.458 | 173.22 | 60.725 | 0.017286 | 141.34 | 1135.9 |  | 14121 | 173.22 | 6.458 | 60.725 | 0.017286 | 141.34 | 1135.9 | 994.56
14122 | 6.4594 | 173.23 | 60.725 | 0.017289 | 141.35 | 1135.9 |  | 14122 | 173.23 | 6.4594 | 60.725 | 0.017289 | 141.35 | 1135.9 | 994.55
14123 | 6.4609 | 173.24 | 60.725 | 0.017293 | 141.36 | 1135.9 |  | 14123 | 173.24 | 6.4609 | 60.725 | 0.017293 | 141.36 | 1135.9 | 994.54
14124 | 6.4624 | 173.25 | 60.724 | 0.017297 | 141.37 | 1136 |  | 14124 | 173.25 | 6.4624 | 60.724 | 0.017297 | 141.37 | 1136 | 994.63
14125 | 6.4638 | 173.26 | 60.724 | 0.0173 | 141.38 | 1136 |  | 14125 | 173.26 | 6.4638 | 60.724 | 0.0173 | 141.38 | 1136 | 994.62
14126 | 6.4653 | 173.27 | 60.724 | 0.017304 | 141.39 | 1136 |  | 14126 | 173.27 | 6.4653 | 60.724 | 0.017304 | 141.39 | 1136 | 994.61
14127 | 6.4668 | 173.28 | 60.724 | 0.017308 | 141.4 | 1136 |  | 14127 | 173.28 | 6.4668 | 60.724 | 0.017308 | 141.4 | 1136 | 994.6
14128 | 6.4682 | 173.29 | 60.724 | 0.017311 | 141.41 | 1136 |  | 14128 | 173.29 | 6.4682 | 60.724 | 0.017311 | 141.41 | 1136 | 994.59
14129 | 6.4697 | 173.3 | 60.723 | 0.017315 | 141.42 | 1136 |  | 14129 | 173.3 | 6.4697 | 60.723 | 0.017315 | 141.42 | 1136 | 994.58
14130 | 6.4712 | 173.31 | 60.723 | 0.017319 | 141.43 | 1136 |  | 14130 | 173.31 | 6.4712 | 60.723 | 0.017319 | 141.43 | 1136 | 994.57
14131 | 6.4727 | 173.32 | 60.723 | 0.017322 | 141.44 | 1136 |  | 14131 | 173.32 | 6.4727 | 60.723 | 0.017322 | 141.44 | 1136 | 994.56
14132 | 6.4741 | 173.33 | 60.723 | 0.017326 | 141.45 | 1136 |  | 14132 | 173.33 | 6.4741 | 60.723 | 0.017326 | 141.45 | 1136 | 994.55
14133 | 6.4756 | 173.34 | 60.722 | 0.01733 | 141.46 | 1136 |  | 14133 | 173.34 | 6.4756 | 60.722 | 0.01733 | 141.46 | 1136 | 994.54
14134 | 6.4771 | 173.35 | 60.722 | 0.017333 | 141.47 | 1136 |  | 14134 | 173.35 | 6.4771 | 60.722 | 0.017333 | 141.47 | 1136 | 994.53
14135 | 6.4785 | 173.36 | 60.722 | 0.017337 | 141.48 | 1136 |  | 14135 | 173.36 | 6.4785 | 60.722 | 0.017337 | 141.48 | 1136 | 994.52
14136 | 6.48 | 173.37 | 60.722 | 0.017341 | 141.49 | 1136 |  | 14136 | 173.37 | 6.48 | 60.722 | 0.017341 | 141.49 | 1136 | 994.51
14137 | 6.4815 | 173.38 | 60.722 | 0.017344 | 141.5 | 1136 |  | 14137 | 173.38 | 6.4815 | 60.722 | 0.017344 | 141.5 | 1136 | 994.5
14138 | 6.483 | 173.39 | 60.721 | 0.017348 | 141.51 | 1136 |  | 14138 | 173.39 | 6.483 | 60.721 | 0.017348 | 141.51 | 1136 | 994.49
14139 | 6.4844 | 173.4 | 60.721 | 0.017352 | 141.52 | 1136 |  | 14139 | 173.4 | 6.4844 | 60.721 | 0.017352 | 141.52 | 1136 | 994.48
14140 | 6.4859 | 173.41 | 60.721 | 0.017356 | 141.53 | 1136 |  | 14140 | 173.41 | 6.4859 | 60.721 | 0.017356 | 141.53 | 1136 | 994.47
14141 | 6.4874 | 173.42 | 60.721 | 0.017359 | 141.54 | 1136 |  | 14141 | 173.42 | 6.4874 | 60.721 | 0.017359 | 141.54 | 1136 | 994.46
14142 | 6.4888 | 173.43 | 60.721 | 0.017363 | 141.55 | 1136 |  | 14142 | 173.43 | 6.4888 | 60.721 | 0.017363 | 141.55 | 1136 | 994.45
14143 | 6.4903 | 173.44 | 60.72 | 0.017367 | 141.56 | 1136 |  | 14143 | 173.44 | 6.4903 | 60.72 | 0.017367 | 141.56 | 1136 | 994.44
14144 | 6.4918 | 173.45 | 60.72 | 0.01737 | 141.57 | 1136 |  | 14144 | 173.45 | 6.4918 | 60.72 | 0.01737 | 141.57 | 1136 | 994.43
14145 | 6.4933 | 173.46 | 60.72 | 0.017374 | 141.58 | 1136 |  | 14145 | 173.46 | 6.4933 | 60.72 | 0.017374 | 141.58 | 1136 | 994.42
14146 | 6.4947 | 173.47 | 60.72 | 0.017378 | 141.59 | 1136 |  | 14146 | 173.47 | 6.4947 | 60.72 | 0.017378 | 141.59 | 1136 | 994.41
14147 | 6.4962 | 173.48 | 60.719 | 0.017381 | 141.6 | 1136 |  | 14147 | 173.48 | 6.4962 | 60.719 | 0.017381 | 141.6 | 1136 | 994.4
14148 | 6.4977 | 173.49 | 60.719 | 0.017385 | 141.61 | 1136 |  | 14148 | 173.49 | 6.4977 | 60.719 | 0.017385 | 141.61 | 1136 | 994.39
14149 | 6.4992 | 173.5 | 60.719 | 0.017389 | 141.62 | 1136.1 |  | 14149 | 173.5 | 6.4992 | 60.719 | 0.017389 | 141.62 | 1136.1 | 994.48
14150 | 6.5006 | 173.51 | 60.719 | 0.017392 | 141.63 | 1136.1 |  | 14150 | 173.51 | 6.5006 | 60.719 | 0.017392 | 141.63 | 1136.1 | 994.47
14151 | 6.5021 | 173.52 | 60.719 | 0.017396 | 141.64 | 1136.1 |  | 14151 | 173.52 | 6.5021 | 60.719 | 0.017396 | 141.64 | 1136.1 | 994.46
14152 | 6.5036 | 173.53 | 60.718 | 0.0174 | 141.65 | 1136.1 |  | 14152 | 173.53 | 6.5036 | 60.718 | 0.0174 | 141.65 | 1136.1 | 994.45
14153 | 6.5051 | 173.54 | 60.718 | 0.017404 | 141.66 | 1136.1 |  | 14153 | 173.54 | 6.5051 | 60.718 | 0.017404 | 141.66 | 1136.1 | 994.44
14154 | 6.5065 | 173.55 | 60.718 | 0.017407 | 141.67 | 1136.1 |  | 14154 | 173.55 | 6.5065 | 60.718 | 0.017407 | 141.67 | 1136.1 | 994.43
14155 | 6.508 | 173.56 | 60.718 | 0.017411 | 141.68 | 1136.1 |  | 14155 | 173.56 | 6.508 | 60.718 | 0.017411 | 141.68 | 1136.1 | 994.42
14156 | 6.5095 | 173.57 | 60.718 | 0.017415 | 141.69 | 1136.1 |  | 14156 | 173.57 | 6.5095 | 60.718 | 0.017415 | 141.69 | 1136.1 | 994.41
14157 | 6.511 | 173.58 | 60.717 | 0.017418 | 141.7 | 1136.1 |  | 14157 | 173.58 | 6.511 | 60.717 | 0.017418 | 141.7 | 1136.1 | 994.4
14158 | 6.5125 | 173.59 | 60.717 | 0.017422 | 141.71 | 1136.1 |  | 14158 | 173.59 | 6.5125 | 60.717 | 0.017422 | 141.71 | 1136.1 | 994.39
14159 | 6.5139 | 173.6 | 60.717 | 0.017426 | 141.72 | 1136.1 |  | 14159 | 173.6 | 6.5139 | 60.717 | 0.017426 | 141.72 | 1136.1 | 994.38
14160 | 6.5154 | 173.61 | 60.717 | 0.017429 | 141.73 | 1136.1 |  | 14160 | 173.61 | 6.5154 | 60.717 | 0.017429 | 141.73 | 1136.1 | 994.37
14161 | 6.5169 | 173.62 | 60.716 | 0.017433 | 141.74 | 1136.1 |  | 14161 | 173.62 | 6.5169 | 60.716 | 0.017433 | 141.74 | 1136.1 | 994.36
14162 | 6.5184 | 173.63 | 60.716 | 0.017437 | 141.75 | 1136.1 |  | 14162 | 173.63 | 6.5184 | 60.716 | 0.017437 | 141.75 | 1136.1 | 994.35
14163 | 6.5198 | 173.64 | 60.716 | 0.017441 | 141.76 | 1136.1 |  | 14163 | 173.64 | 6.5198 | 60.716 | 0.017441 | 141.76 | 1136.1 | 994.34
14164 | 6.5213 | 173.65 | 60.716 | 0.017444 | 141.77 | 1136.1 |  | 14164 | 173.65 | 6.5213 | 60.716 | 0.017444 | 141.77 | 1136.1 | 994.33
14165 | 6.5228 | 173.66 | 60.716 | 0.017448 | 141.78 | 1136.1 |  | 14165 | 173.66 | 6.5228 | 60.716 | 0.017448 | 141.78 | 1136.1 | 994.32
14166 | 6.5243 | 173.67 | 60.715 | 0.017452 | 141.79 | 1136.1 |  | 14166 | 173.67 | 6.5243 | 60.715 | 0.017452 | 141.79 | 1136.1 | 994.31
14167 | 6.5258 | 173.68 | 60.715 | 0.017455 | 141.8 | 1136.1 |  | 14167 | 173.68 | 6.5258 | 60.715 | 0.017455 | 141.8 | 1136.1 | 994.3
14168 | 6.5272 | 173.69 | 60.715 | 0.017459 | 141.81 | 1136.1 |  | 14168 | 173.69 | 6.5272 | 60.715 | 0.017459 | 141.81 | 1136.1 | 994.29
14169 | 6.5287 | 173.7 | 60.715 | 0.017463 | 141.82 | 1136.1 |  | 14169 | 173.7 | 6.5287 | 60.715 | 0.017463 | 141.82 | 1136.1 | 994.28
14170 | 6.5302 | 173.71 | 60.715 | 0.017467 | 141.83 | 1136.1 |  | 14170 | 173.71 | 6.5302 | 60.715 | 0.017467 | 141.83 | 1136.1 | 994.27
14171 | 6.5317 | 173.72 | 60.714 | 0.01747 | 141.84 | 1136.1 |  | 14171 | 173.72 | 6.5317 | 60.714 | 0.01747 | 141.84 | 1136.1 | 994.26
14172 | 6.5332 | 173.73 | 60.714 | 0.017474 | 141.85 | 1136.1 |  | 14172 | 173.73 | 6.5332 | 60.714 | 0.017474 | 141.85 | 1136.1 | 994.25
14173 | 6.5347 | 173.74 | 60.714 | 0.017478 | 141.86 | 1136.1 |  | 14173 | 173.74 | 6.5347 | 60.714 | 0.017478 | 141.86 | 1136.1 | 994.24
14174 | 6.5361 | 173.75 | 60.714 | 0.017481 | 141.87 | 1136.2 |  | 14174 | 173.75 | 6.5361 | 60.714 | 0.017481 | 141.87 | 1136.2 | 994.33
14175 | 6.5376 | 173.76 | 60.713 | 0.017485 | 141.88 | 1136.2 |  | 14175 | 173.76 | 6.5376 | 60.713 | 0.017485 | 141.88 | 1136.2 | 994.32
14176 | 6.5391 | 173.77 | 60.713 | 0.017489 | 141.89 | 1136.2 |  | 14176 | 173.77 | 6.5391 | 60.713 | 0.017489 | 141.89 | 1136.2 | 994.31
14177 | 6.5406 | 173.78 | 60.713 | 0.017493 | 141.9 | 1136.2 |  | 14177 | 173.78 | 6.5406 | 60.713 | 0.017493 | 141.9 | 1136.2 | 994.3
14178 | 6.5421 | 173.79 | 60.713 | 0.017496 | 141.91 | 1136.2 |  | 14178 | 173.79 | 6.5421 | 60.713 | 0.017496 | 141.91 | 1136.2 | 994.29
14179 | 6.5436 | 173.8 | 60.713 | 0.0175 | 141.92 | 1136.2 |  | 14179 | 173.8 | 6.5436 | 60.713 | 0.0175 | 141.92 | 1136.2 | 994.28
14180 | 6.545 | 173.81 | 60.712 | 0.017504 | 141.93 | 1136.2 |  | 14180 | 173.81 | 6.545 | 60.712 | 0.017504 | 141.93 | 1136.2 | 994.27
14181 | 6.5465 | 173.82 | 60.712 | 0.017507 | 141.94 | 1136.2 |  | 14181 | 173.82 | 6.5465 | 60.712 | 0.017507 | 141.94 | 1136.2 | 994.26
14182 | 6.548 | 173.83 | 60.712 | 0.017511 | 141.95 | 1136.2 |  | 14182 | 173.83 | 6.548 | 60.712 | 0.017511 | 141.95 | 1136.2 | 994.25
14183 | 6.5495 | 173.84 | 60.712 | 0.017515 | 141.96 | 1136.2 |  | 14183 | 173.84 | 6.5495 | 60.712 | 0.017515 | 141.96 | 1136.2 | 994.24
14184 | 6.551 | 173.85 | 60.712 | 0.017519 | 141.97 | 1136.2 |  | 14184 | 173.85 | 6.551 | 60.712 | 0.017519 | 141.97 | 1136.2 | 994.23
14185 | 6.5525 | 173.86 | 60.711 | 0.017522 | 141.98 | 1136.2 |  | 14185 | 173.86 | 6.5525 | 60.711 | 0.017522 | 141.98 | 1136.2 | 994.22
14186 | 6.5539 | 173.87 | 60.711 | 0.017526 | 141.99 | 1136.2 |  | 14186 | 173.87 | 6.5539 | 60.711 | 0.017526 | 141.99 | 1136.2 | 994.21
14187 | 6.5554 | 173.88 | 60.711 | 0.01753 | 142 | 1136.2 |  | 14187 | 173.88 | 6.5554 | 60.711 | 0.01753 | 142 | 1136.2 | 994.2
14188 | 6.5569 | 173.89 | 60.711 | 0.017533 | 142.01 | 1136.2 |  | 14188 | 173.89 | 6.5569 | 60.711 | 0.017533 | 142.01 | 1136.2 | 994.19
14189 | 6.5584 | 173.9 | 60.711 | 0.017537 | 142.02 | 1136.2 |  | 14189 | 173.9 | 6.5584 | 60.711 | 0.017537 | 142.02 | 1136.2 | 994.18
14190 | 6.5599 | 173.91 | 60.71 | 0.017541 | 142.03 | 1136.2 |  | 14190 | 173.91 | 6.5599 | 60.71 | 0.017541 | 142.03 | 1136.2 | 994.17
14191 | 6.5614 | 173.92 | 60.71 | 0.017545 | 142.04 | 1136.2 |  | 14191 | 173.92 | 6.5614 | 60.71 | 0.017545 | 142.04 | 1136.2 | 994.16
14192 | 6.5629 | 173.93 | 60.71 | 0.017548 | 142.05 | 1136.2 |  | 14192 | 173.93 | 6.5629 | 60.71 | 0.017548 | 142.05 | 1136.2 | 994.15
14193 | 6.5644 | 173.94 | 60.71 | 0.017552 | 142.06 | 1136.2 |  | 14193 | 173.94 | 6.5644 | 60.71 | 0.017552 | 142.06 | 1136.2 | 994.14
14194 | 6.5658 | 173.95 | 60.709 | 0.017556 | 142.07 | 1136.2 |  | 14194 | 173.95 | 6.5658 | 60.709 | 0.017556 | 142.07 | 1136.2 | 994.13
14195 | 6.5673 | 173.96 | 60.709 | 0.017559 | 142.08 | 1136.2 |  | 14195 | 173.96 | 6.5673 | 60.709 | 0.017559 | 142.08 | 1136.2 | 994.12
14196 | 6.5688 | 173.97 | 60.709 | 0.017563 | 142.09 | 1136.2 |  | 14196 | 173.97 | 6.5688 | 60.709 | 0.017563 | 142.09 | 1136.2 | 994.11
14197 | 6.5703 | 173.98 | 60.709 | 0.017567 | 142.1 | 1136.2 |  | 14197 | 173.98 | 6.5703 | 60.709 | 0.017567 | 142.1 | 1136.2 | 994.1
14198 | 6.5718 | 173.99 | 60.709 | 0.017571 | 142.11 | 1136.2 |  | 14198 | 173.99 | 6.5718 | 60.709 | 0.017571 | 142.11 | 1136.2 | 994.09
14199 | 6.5733 | 174 | 60.708 | 0.017574 | 142.12 | 1136.3 |  | 14199 | 174 | 6.5733 | 60.708 | 0.017574 | 142.12 | 1136.3 | 994.18
14200 | 6.5748 | 174.01 | 60.708 | 0.017578 | 142.13 | 1136.3 |  | 14200 | 174.01 | 6.5748 | 60.708 | 0.017578 | 142.13 | 1136.3 | 994.17
14201 | 6.5763 | 174.02 | 60.708 | 0.017582 | 142.14 | 1136.3 |  | 14201 | 174.02 | 6.5763 | 60.708 | 0.017582 | 142.14 | 1136.3 | 994.16
14202 | 6.5778 | 174.03 | 60.708 | 0.017586 | 142.15 | 1136.3 |  | 14202 | 174.03 | 6.5778 | 60.708 | 0.017586 | 142.15 | 1136.3 | 994.15
14203 | 6.5792 | 174.04 | 60.708 | 0.017589 | 142.16 | 1136.3 |  | 14203 | 174.04 | 6.5792 | 60.708 | 0.017589 | 142.16 | 1136.3 | 994.14
14204 | 6.5807 | 174.05 | 60.707 | 0.017593 | 142.17 | 1136.3 |  | 14204 | 174.05 | 6.5807 | 60.707 | 0.017593 | 142.17 | 1136.3 | 994.13
14205 | 6.5822 | 174.06 | 60.707 | 0.017597 | 142.18 | 1136.3 |  | 14205 | 174.06 | 6.5822 | 60.707 | 0.017597 | 142.18 | 1136.3 | 994.12
14206 | 6.5837 | 174.07 | 60.707 | 0.017601 | 142.19 | 1136.3 |  | 14206 | 174.07 | 6.5837 | 60.707 | 0.017601 | 142.19 | 1136.3 | 994.11
14207 | 6.5852 | 174.08 | 60.707 | 0.017604 | 142.2 | 1136.3 |  | 14207 | 174.08 | 6.5852 | 60.707 | 0.017604 | 142.2 | 1136.3 | 994.1
14208 | 6.5867 | 174.09 | 60.706 | 0.017608 | 142.21 | 1136.3 |  | 14208 | 174.09 | 6.5867 | 60.706 | 0.017608 | 142.21 | 1136.3 | 994.09
14209 | 6.5882 | 174.1 | 60.706 | 0.017612 | 142.22 | 1136.3 |  | 14209 | 174.1 | 6.5882 | 60.706 | 0.017612 | 142.22 | 1136.3 | 994.08
14210 | 6.5897 | 174.11 | 60.706 | 0.017615 | 142.23 | 1136.3 |  | 14210 | 174.11 | 6.5897 | 60.706 | 0.017615 | 142.23 | 1136.3 | 994.07
14211 | 6.5912 | 174.12 | 60.706 | 0.017619 | 142.24 | 1136.3 |  | 14211 | 174.12 | 6.5912 | 60.706 | 0.017619 | 142.24 | 1136.3 | 994.06
14212 | 6.5927 | 174.13 | 60.706 | 0.017623 | 142.25 | 1136.3 |  | 14212 | 174.13 | 6.5927 | 60.706 | 0.017623 | 142.25 | 1136.3 | 994.05
14213 | 6.5942 | 174.14 | 60.705 | 0.017627 | 142.26 | 1136.3 |  | 14213 | 174.14 | 6.5942 | 60.705 | 0.017627 | 142.26 | 1136.3 | 994.04
14214 | 6.5957 | 174.15 | 60.705 | 0.01763 | 142.27 | 1136.3 |  | 14214 | 174.15 | 6.5957 | 60.705 | 0.01763 | 142.27 | 1136.3 | 994.03
14215 | 6.5971 | 174.16 | 60.705 | 0.017634 | 142.28 | 1136.3 |  | 14215 | 174.16 | 6.5971 | 60.705 | 0.017634 | 142.28 | 1136.3 | 994.02
14216 | 6.5986 | 174.17 | 60.705 | 0.017638 | 142.29 | 1136.3 |  | 14216 | 174.17 | 6.5986 | 60.705 | 0.017638 | 142.29 | 1136.3 | 994.01
14217 | 6.6001 | 174.18 | 60.705 | 0.017642 | 142.3 | 1136.3 |  | 14217 | 174.18 | 6.6001 | 60.705 | 0.017642 | 142.3 | 1136.3 | 994
14218 | 6.6016 | 174.19 | 60.704 | 0.017645 | 142.31 | 1136.3 |  | 14218 | 174.19 | 6.6016 | 60.704 | 0.017645 | 142.31 | 1136.3 | 993.99
14219 | 6.6031 | 174.2 | 60.704 | 0.017649 | 142.32 | 1136.3 |  | 14219 | 174.2 | 6.6031 | 60.704 | 0.017649 | 142.32 | 1136.3 | 993.98
14220 | 6.6046 | 174.21 | 60.704 | 0.017653 | 142.33 | 1136.3 |  | 14220 | 174.21 | 6.6046 | 60.704 | 0.017653 | 142.33 | 1136.3 | 993.97
14221 | 6.6061 | 174.22 | 60.704 | 0.017657 | 142.34 | 1136.3 |  | 14221 | 174.22 | 6.6061 | 60.704 | 0.017657 | 142.34 | 1136.3 | 993.96
14222 | 6.6076 | 174.23 | 60.703 | 0.01766 | 142.35 | 1136.3 |  | 14222 | 174.23 | 6.6076 | 60.703 | 0.01766 | 142.35 | 1136.3 | 993.95
14223 | 6.6091 | 174.24 | 60.703 | 0.017664 | 142.36 | 1136.3 |  | 14223 | 174.24 | 6.6091 | 60.703 | 0.017664 | 142.36 | 1136.3 | 993.94
14224 | 6.6106 | 174.25 | 60.703 | 0.017668 | 142.37 | 1136.4 |  | 14224 | 174.25 | 6.6106 | 60.703 | 0.017668 | 142.37 | 1136.4 | 994.03
14225 | 6.6121 | 174.26 | 60.703 | 0.017672 | 142.38 | 1136.4 |  | 14225 | 174.26 | 6.6121 | 60.703 | 0.017672 | 142.38 | 1136.4 | 994.02
14226 | 6.6136 | 174.27 | 60.703 | 0.017675 | 142.39 | 1136.4 |  | 14226 | 174.27 | 6.6136 | 60.703 | 0.017675 | 142.39 | 1136.4 | 994.01
14227 | 6.6151 | 174.28 | 60.702 | 0.017679 | 142.4 | 1136.4 |  | 14227 | 174.28 | 6.6151 | 60.702 | 0.017679 | 142.4 | 1136.4 | 994
14228 | 6.6166 | 174.29 | 60.702 | 0.017683 | 142.41 | 1136.4 |  | 14228 | 174.29 | 6.6166 | 60.702 | 0.017683 | 142.41 | 1136.4 | 993.99
14229 | 6.6181 | 174.3 | 60.702 | 0.017687 | 142.42 | 1136.4 |  | 14229 | 174.3 | 6.6181 | 60.702 | 0.017687 | 142.42 | 1136.4 | 993.98
14230 | 6.6196 | 174.31 | 60.702 | 0.01769 | 142.43 | 1136.4 |  | 14230 | 174.31 | 6.6196 | 60.702 | 0.01769 | 142.43 | 1136.4 | 993.97
14231 | 6.6211 | 174.32 | 60.702 | 0.017694 | 142.44 | 1136.4 |  | 14231 | 174.32 | 6.6211 | 60.702 | 0.017694 | 142.44 | 1136.4 | 993.96
14232 | 6.6226 | 174.33 | 60.701 | 0.017698 | 142.45 | 1136.4 |  | 14232 | 174.33 | 6.6226 | 60.701 | 0.017698 | 142.45 | 1136.4 | 993.95
14233 | 6.6241 | 174.34 | 60.701 | 0.017702 | 142.46 | 1136.4 |  | 14233 | 174.34 | 6.6241 | 60.701 | 0.017702 | 142.46 | 1136.4 | 993.94
14234 | 6.6256 | 174.35 | 60.701 | 0.017705 | 142.47 | 1136.4 |  | 14234 | 174.35 | 6.6256 | 60.701 | 0.017705 | 142.47 | 1136.4 | 993.93
14235 | 6.6271 | 174.36 | 60.701 | 0.017709 | 142.48 | 1136.4 |  | 14235 | 174.36 | 6.6271 | 60.701 | 0.017709 | 142.48 | 1136.4 | 993.92
14236 | 6.6286 | 174.37 | 60.7 | 0.017713 | 142.49 | 1136.4 |  | 14236 | 174.37 | 6.6286 | 60.7 | 0.017713 | 142.49 | 1136.4 | 993.91
14237 | 6.6301 | 174.38 | 60.7 | 0.017717 | 142.5 | 1136.4 |  | 14237 | 174.38 | 6.6301 | 60.7 | 0.017717 | 142.5 | 1136.4 | 993.9
14238 | 6.6316 | 174.39 | 60.7 | 0.01772 | 142.51 | 1136.4 |  | 14238 | 174.39 | 6.6316 | 60.7 | 0.01772 | 142.51 | 1136.4 | 993.89
14239 | 6.6331 | 174.4 | 60.7 | 0.017724 | 142.52 | 1136.4 |  | 14239 | 174.4 | 6.6331 | 60.7 | 0.017724 | 142.52 | 1136.4 | 993.88
14240 | 6.6346 | 174.41 | 60.7 | 0.017728 | 142.53 | 1136.4 |  | 14240 | 174.41 | 6.6346 | 60.7 | 0.017728 | 142.53 | 1136.4 | 993.87
14241 | 6.6361 | 174.42 | 60.699 | 0.017732 | 142.54 | 1136.4 |  | 14241 | 174.42 | 6.6361 | 60.699 | 0.017732 | 142.54 | 1136.4 | 993.86
14242 | 6.6376 | 174.43 | 60.699 | 0.017735 | 142.55 | 1136.4 |  | 14242 | 174.43 | 6.6376 | 60.699 | 0.017735 | 142.55 | 1136.4 | 993.85
14243 | 6.6391 | 174.44 | 60.699 | 0.017739 | 142.56 | 1136.4 |  | 14243 | 174.44 | 6.6391 | 60.699 | 0.017739 | 142.56 | 1136.4 | 993.84
14244 | 6.6406 | 174.45 | 60.699 | 0.017743 | 142.57 | 1136.4 |  | 14244 | 174.45 | 6.6406 | 60.699 | 0.017743 | 142.57 | 1136.4 | 993.83
14245 | 6.6421 | 174.46 | 60.699 | 0.017747 | 142.58 | 1136.4 |  | 14245 | 174.46 | 6.6421 | 60.699 | 0.017747 | 142.58 | 1136.4 | 993.82
14246 | 6.6436 | 174.47 | 60.698 | 0.01775 | 142.59 | 1136.4 |  | 14246 | 174.47 | 6.6436 | 60.698 | 0.01775 | 142.59 | 1136.4 | 993.81
14247 | 6.6451 | 174.48 | 60.698 | 0.017754 | 142.6 | 1136.4 |  | 14247 | 174.48 | 6.6451 | 60.698 | 0.017754 | 142.6 | 1136.4 | 993.8
14248 | 6.6466 | 174.49 | 60.698 | 0.017758 | 142.61 | 1136.4 |  | 14248 | 174.49 | 6.6466 | 60.698 | 0.017758 | 142.61 | 1136.4 | 993.79
14249 | 6.6481 | 174.5 | 60.698 | 0.017762 | 142.62 | 1136.5 |  | 14249 | 174.5 | 6.6481 | 60.698 | 0.017762 | 142.62 | 1136.5 | 993.88
14250 | 6.6496 | 174.51 | 60.697 | 0.017765 | 142.63 | 1136.5 |  | 14250 | 174.51 | 6.6496 | 60.697 | 0.017765 | 142.63 | 1136.5 | 993.87
14251 | 6.6511 | 174.52 | 60.697 | 0.017769 | 142.64 | 1136.5 |  | 14251 | 174.52 | 6.6511 | 60.697 | 0.017769 | 142.64 | 1136.5 | 993.86
14252 | 6.6526 | 174.53 | 60.697 | 0.017773 | 142.65 | 1136.5 |  | 14252 | 174.53 | 6.6526 | 60.697 | 0.017773 | 142.65 | 1136.5 | 993.85
14253 | 6.6541 | 174.54 | 60.697 | 0.017777 | 142.66 | 1136.5 |  | 14253 | 174.54 | 6.6541 | 60.697 | 0.017777 | 142.66 | 1136.5 | 993.84
14254 | 6.6556 | 174.55 | 60.697 | 0.01778 | 142.67 | 1136.5 |  | 14254 | 174.55 | 6.6556 | 60.697 | 0.01778 | 142.67 | 1136.5 | 993.83
14255 | 6.6571 | 174.56 | 60.696 | 0.017784 | 142.68 | 1136.5 |  | 14255 | 174.56 | 6.6571 | 60.696 | 0.017784 | 142.68 | 1136.5 | 993.82
14256 | 6.6586 | 174.57 | 60.696 | 0.017788 | 142.69 | 1136.5 |  | 14256 | 174.57 | 6.6586 | 60.696 | 0.017788 | 142.69 | 1136.5 | 993.81
14257 | 6.6601 | 174.58 | 60.696 | 0.017792 | 142.7 | 1136.5 |  | 14257 | 174.58 | 6.6601 | 60.696 | 0.017792 | 142.7 | 1136.5 | 993.8
14258 | 6.6617 | 174.59 | 60.696 | 0.017796 | 142.71 | 1136.5 |  | 14258 | 174.59 | 6.6617 | 60.696 | 0.017796 | 142.71 | 1136.5 | 993.79
14259 | 6.6632 | 174.6 | 60.696 | 0.017799 | 142.72 | 1136.5 |  | 14259 | 174.6 | 6.6632 | 60.696 | 0.017799 | 142.72 | 1136.5 | 993.78
14260 | 6.6647 | 174.61 | 60.695 | 0.017803 | 142.73 | 1136.5 |  | 14260 | 174.61 | 6.6647 | 60.695 | 0.017803 | 142.73 | 1136.5 | 993.77
14261 | 6.6662 | 174.62 | 60.695 | 0.017807 | 142.74 | 1136.5 |  | 14261 | 174.62 | 6.6662 | 60.695 | 0.017807 | 142.74 | 1136.5 | 993.76
14262 | 6.6677 | 174.63 | 60.695 | 0.017811 | 142.75 | 1136.5 |  | 14262 | 174.63 | 6.6677 | 60.695 | 0.017811 | 142.75 | 1136.5 | 993.75
14263 | 6.6692 | 174.64 | 60.695 | 0.017814 | 142.76 | 1136.5 |  | 14263 | 174.64 | 6.6692 | 60.695 | 0.017814 | 142.76 | 1136.5 | 993.74
14264 | 6.6707 | 174.65 | 60.694 | 0.017818 | 142.77 | 1136.5 |  | 14264 | 174.65 | 6.6707 | 60.694 | 0.017818 | 142.77 | 1136.5 | 993.73
14265 | 6.6722 | 174.66 | 60.694 | 0.017822 | 142.78 | 1136.5 |  | 14265 | 174.66 | 6.6722 | 60.694 | 0.017822 | 142.78 | 1136.5 | 993.72
14266 | 6.6737 | 174.67 | 60.694 | 0.017826 | 142.79 | 1136.5 |  | 14266 | 174.67 | 6.6737 | 60.694 | 0.017826 | 142.79 | 1136.5 | 993.71
14267 | 6.6752 | 174.68 | 60.694 | 0.017829 | 142.8 | 1136.5 |  | 14267 | 174.68 | 6.6752 | 60.694 | 0.017829 | 142.8 | 1136.5 | 993.7
14268 | 6.6767 | 174.69 | 60.694 | 0.017833 | 142.81 | 1136.5 |  | 14268 | 174.69 | 6.6767 | 60.694 | 0.017833 | 142.81 | 1136.5 | 993.69
14269 | 6.6782 | 174.7 | 60.693 | 0.017837 | 142.82 | 1136.5 |  | 14269 | 174.7 | 6.6782 | 60.693 | 0.017837 | 142.82 | 1136.5 | 993.68
14270 | 6.6797 | 174.71 | 60.693 | 0.017841 | 142.83 | 1136.5 |  | 14270 | 174.71 | 6.6797 | 60.693 | 0.017841 | 142.83 | 1136.5 | 993.67
14271 | 6.6813 | 174.72 | 60.693 | 0.017845 | 142.84 | 1136.5 |  | 14271 | 174.72 | 6.6813 | 60.693 | 0.017845 | 142.84 | 1136.5 | 993.66
14272 | 6.6828 | 174.73 | 60.693 | 0.017848 | 142.85 | 1136.5 |  | 14272 | 174.73 | 6.6828 | 60.693 | 0.017848 | 142.85 | 1136.5 | 993.65
14273 | 6.6843 | 174.74 | 60.693 | 0.017852 | 142.86 | 1136.5 |  | 14273 | 174.74 | 6.6843 | 60.693 | 0.017852 | 142.86 | 1136.5 | 993.64
14274 | 6.6858 | 174.75 | 60.692 | 0.017856 | 142.87 | 1136.6 |  | 14274 | 174.75 | 6.6858 | 60.692 | 0.017856 | 142.87 | 1136.6 | 993.73
14275 | 6.6873 | 174.76 | 60.692 | 0.01786 | 142.88 | 1136.6 |  | 14275 | 174.76 | 6.6873 | 60.692 | 0.01786 | 142.88 | 1136.6 | 993.72
14276 | 6.6888 | 174.77 | 60.692 | 0.017863 | 142.89 | 1136.6 |  | 14276 | 174.77 | 6.6888 | 60.692 | 0.017863 | 142.89 | 1136.6 | 993.71
14277 | 6.6903 | 174.78 | 60.692 | 0.017867 | 142.9 | 1136.6 |  | 14277 | 174.78 | 6.6903 | 60.692 | 0.017867 | 142.9 | 1136.6 | 993.7
14278 | 6.6918 | 174.79 | 60.691 | 0.017871 | 142.91 | 1136.6 |  | 14278 | 174.79 | 6.6918 | 60.691 | 0.017871 | 142.91 | 1136.6 | 993.69
14279 | 6.6933 | 174.8 | 60.691 | 0.017875 | 142.92 | 1136.6 |  | 14279 | 174.8 | 6.6933 | 60.691 | 0.017875 | 142.92 | 1136.6 | 993.68
14280 | 6.6949 | 174.81 | 60.691 | 0.017879 | 142.93 | 1136.6 |  | 14280 | 174.81 | 6.6949 | 60.691 | 0.017879 | 142.93 | 1136.6 | 993.67
14281 | 6.6964 | 174.82 | 60.691 | 0.017882 | 142.94 | 1136.6 |  | 14281 | 174.82 | 6.6964 | 60.691 | 0.017882 | 142.94 | 1136.6 | 993.66
14282 | 6.6979 | 174.83 | 60.691 | 0.017886 | 142.95 | 1136.6 |  | 14282 | 174.83 | 6.6979 | 60.691 | 0.017886 | 142.95 | 1136.6 | 993.65
14283 | 6.6994 | 174.84 | 60.69 | 0.01789 | 142.96 | 1136.6 |  | 14283 | 174.84 | 6.6994 | 60.69 | 0.01789 | 142.96 | 1136.6 | 993.64
14284 | 6.7009 | 174.85 | 60.69 | 0.017894 | 142.97 | 1136.6 |  | 14284 | 174.85 | 6.7009 | 60.69 | 0.017894 | 142.97 | 1136.6 | 993.63
14285 | 6.7024 | 174.86 | 60.69 | 0.017898 | 142.98 | 1136.6 |  | 14285 | 174.86 | 6.7024 | 60.69 | 0.017898 | 142.98 | 1136.6 | 993.62
14286 | 6.7039 | 174.87 | 60.69 | 0.017901 | 142.99 | 1136.6 |  | 14286 | 174.87 | 6.7039 | 60.69 | 0.017901 | 142.99 | 1136.6 | 993.61
14287 | 6.7055 | 174.88 | 60.69 | 0.017905 | 143 | 1136.6 |  | 14287 | 174.88 | 6.7055 | 60.69 | 0.017905 | 143 | 1136.6 | 993.6
14288 | 6.707 | 174.89 | 60.689 | 0.017909 | 143.01 | 1136.6 |  | 14288 | 174.89 | 6.707 | 60.689 | 0.017909 | 143.01 | 1136.6 | 993.59
14289 | 6.7085 | 174.9 | 60.689 | 0.017913 | 143.02 | 1136.6 |  | 14289 | 174.9 | 6.7085 | 60.689 | 0.017913 | 143.02 | 1136.6 | 993.58
14290 | 6.71 | 174.91 | 60.689 | 0.017916 | 143.03 | 1136.6 |  | 14290 | 174.91 | 6.71 | 60.689 | 0.017916 | 143.03 | 1136.6 | 993.57
14291 | 6.7115 | 174.92 | 60.689 | 0.01792 | 143.04 | 1136.6 |  | 14291 | 174.92 | 6.7115 | 60.689 | 0.01792 | 143.04 | 1136.6 | 993.56
14292 | 6.713 | 174.93 | 60.688 | 0.017924 | 143.05 | 1136.6 |  | 14292 | 174.93 | 6.713 | 60.688 | 0.017924 | 143.05 | 1136.6 | 993.55
14293 | 6.7145 | 174.94 | 60.688 | 0.017928 | 143.06 | 1136.6 |  | 14293 | 174.94 | 6.7145 | 60.688 | 0.017928 | 143.06 | 1136.6 | 993.54
14294 | 6.7161 | 174.95 | 60.688 | 0.017932 | 143.07 | 1136.6 |  | 14294 | 174.95 | 6.7161 | 60.688 | 0.017932 | 143.07 | 1136.6 | 993.53
14295 | 6.7176 | 174.96 | 60.688 | 0.017935 | 143.08 | 1136.6 |  | 14295 | 174.96 | 6.7176 | 60.688 | 0.017935 | 143.08 | 1136.6 | 993.52
14296 | 6.7191 | 174.97 | 60.688 | 0.017939 | 143.09 | 1136.6 |  | 14296 | 174.97 | 6.7191 | 60.688 | 0.017939 | 143.09 | 1136.6 | 993.51
14297 | 6.7206 | 174.98 | 60.687 | 0.017943 | 143.1 | 1136.6 |  | 14297 | 174.98 | 6.7206 | 60.687 | 0.017943 | 143.1 | 1136.6 | 993.5
14298 | 6.7221 | 174.99 | 60.687 | 0.017947 | 143.11 | 1136.6 |  | 14298 | 174.99 | 6.7221 | 60.687 | 0.017947 | 143.11 | 1136.6 | 993.49
14299 | 6.7236 | 175 | 60.687 | 0.017951 | 143.12 | 1136.7 |  | 14299 | 175 | 6.7236 | 60.687 | 0.017951 | 143.12 | 1136.7 | 993.58
14300 | 6.7252 | 175.01 | 60.687 | 0.017954 | 143.13 | 1136.7 |  | 14300 | 175.01 | 6.7252 | 60.687 | 0.017954 | 143.13 | 1136.7 | 993.57
14301 | 6.7267 | 175.02 | 60.686 | 0.017958 | 143.14 | 1136.7 |  | 14301 | 175.02 | 6.7267 | 60.686 | 0.017958 | 143.14 | 1136.7 | 993.56
14302 | 6.7282 | 175.03 | 60.686 | 0.017962 | 143.15 | 1136.7 |  | 14302 | 175.03 | 6.7282 | 60.686 | 0.017962 | 143.15 | 1136.7 | 993.55
14303 | 6.7297 | 175.04 | 60.686 | 0.017966 | 143.16 | 1136.7 |  | 14303 | 175.04 | 6.7297 | 60.686 | 0.017966 | 143.16 | 1136.7 | 993.54
14304 | 6.7312 | 175.05 | 60.686 | 0.01797 | 143.17 | 1136.7 |  | 14304 | 175.05 | 6.7312 | 60.686 | 0.01797 | 143.17 | 1136.7 | 993.53
14305 | 6.7328 | 175.06 | 60.686 | 0.017973 | 143.18 | 1136.7 |  | 14305 | 175.06 | 6.7328 | 60.686 | 0.017973 | 143.18 | 1136.7 | 993.52
14306 | 6.7343 | 175.07 | 60.685 | 0.017977 | 143.19 | 1136.7 |  | 14306 | 175.07 | 6.7343 | 60.685 | 0.017977 | 143.19 | 1136.7 | 993.51
14307 | 6.7358 | 175.08 | 60.685 | 0.017981 | 143.2 | 1136.7 |  | 14307 | 175.08 | 6.7358 | 60.685 | 0.017981 | 143.2 | 1136.7 | 993.5
14308 | 6.7373 | 175.09 | 60.685 | 0.017985 | 143.21 | 1136.7 |  | 14308 | 175.09 | 6.7373 | 60.685 | 0.017985 | 143.21 | 1136.7 | 993.49
14309 | 6.7388 | 175.1 | 60.685 | 0.017989 | 143.22 | 1136.7 |  | 14309 | 175.1 | 6.7388 | 60.685 | 0.017989 | 143.22 | 1136.7 | 993.48
14310 | 6.7404 | 175.11 | 60.685 | 0.017992 | 143.23 | 1136.7 |  | 14310 | 175.11 | 6.7404 | 60.685 | 0.017992 | 143.23 | 1136.7 | 993.47
14311 | 6.7419 | 175.12 | 60.684 | 0.017996 | 143.24 | 1136.7 |  | 14311 | 175.12 | 6.7419 | 60.684 | 0.017996 | 143.24 | 1136.7 | 993.46
14312 | 6.7434 | 175.13 | 60.684 | 0.018 | 143.25 | 1136.7 |  | 14312 | 175.13 | 6.7434 | 60.684 | 0.018 | 143.25 | 1136.7 | 993.45
14313 | 6.7449 | 175.14 | 60.684 | 0.018004 | 143.26 | 1136.7 |  | 14313 | 175.14 | 6.7449 | 60.684 | 0.018004 | 143.26 | 1136.7 | 993.44
14314 | 6.7464 | 175.15 | 60.684 | 0.018008 | 143.27 | 1136.7 |  | 14314 | 175.15 | 6.7464 | 60.684 | 0.018008 | 143.27 | 1136.7 | 993.43
14315 | 6.748 | 175.16 | 60.683 | 0.018011 | 143.28 | 1136.7 |  | 14315 | 175.16 | 6.748 | 60.683 | 0.018011 | 143.28 | 1136.7 | 993.42
14316 | 6.7495 | 175.17 | 60.683 | 0.018015 | 143.29 | 1136.7 |  | 14316 | 175.17 | 6.7495 | 60.683 | 0.018015 | 143.29 | 1136.7 | 993.41
14317 | 6.751 | 175.18 | 60.683 | 0.018019 | 143.3 | 1136.7 |  | 14317 | 175.18 | 6.751 | 60.683 | 0.018019 | 143.3 | 1136.7 | 993.4
14318 | 6.7525 | 175.19 | 60.683 | 0.018023 | 143.31 | 1136.7 |  | 14318 | 175.19 | 6.7525 | 60.683 | 0.018023 | 143.31 | 1136.7 | 993.39
14319 | 6.7541 | 175.2 | 60.683 | 0.018027 | 143.32 | 1136.7 |  | 14319 | 175.2 | 6.7541 | 60.683 | 0.018027 | 143.32 | 1136.7 | 993.38
14320 | 6.7556 | 175.21 | 60.682 | 0.01803 | 143.33 | 1136.7 |  | 14320 | 175.21 | 6.7556 | 60.682 | 0.01803 | 143.33 | 1136.7 | 993.37
14321 | 6.7571 | 175.22 | 60.682 | 0.018034 | 143.34 | 1136.7 |  | 14321 | 175.22 | 6.7571 | 60.682 | 0.018034 | 143.34 | 1136.7 | 993.36
14322 | 6.7586 | 175.23 | 60.682 | 0.018038 | 143.35 | 1136.7 |  | 14322 | 175.23 | 6.7586 | 60.682 | 0.018038 | 143.35 | 1136.7 | 993.35
14323 | 6.7602 | 175.24 | 60.682 | 0.018042 | 143.36 | 1136.7 |  | 14323 | 175.24 | 6.7602 | 60.682 | 0.018042 | 143.36 | 1136.7 | 993.34
14324 | 6.7617 | 175.25 | 60.682 | 0.018046 | 143.37 | 1136.8 |  | 14324 | 175.25 | 6.7617 | 60.682 | 0.018046 | 143.37 | 1136.8 | 993.43
14325 | 6.7632 | 175.26 | 60.681 | 0.018049 | 143.38 | 1136.8 |  | 14325 | 175.26 | 6.7632 | 60.681 | 0.018049 | 143.38 | 1136.8 | 993.42
14326 | 6.7647 | 175.27 | 60.681 | 0.018053 | 143.39 | 1136.8 |  | 14326 | 175.27 | 6.7647 | 60.681 | 0.018053 | 143.39 | 1136.8 | 993.41
14327 | 6.7663 | 175.28 | 60.681 | 0.018057 | 143.4 | 1136.8 |  | 14327 | 175.28 | 6.7663 | 60.681 | 0.018057 | 143.4 | 1136.8 | 993.4
14328 | 6.7678 | 175.29 | 60.681 | 0.018061 | 143.41 | 1136.8 |  | 14328 | 175.29 | 6.7678 | 60.681 | 0.018061 | 143.41 | 1136.8 | 993.39
14329 | 6.7693 | 175.3 | 60.68 | 0.018065 | 143.42 | 1136.8 |  | 14329 | 175.3 | 6.7693 | 60.68 | 0.018065 | 143.42 | 1136.8 | 993.38
14330 | 6.7708 | 175.31 | 60.68 | 0.018069 | 143.43 | 1136.8 |  | 14330 | 175.31 | 6.7708 | 60.68 | 0.018069 | 143.43 | 1136.8 | 993.37
14331 | 6.7724 | 175.32 | 60.68 | 0.018072 | 143.44 | 1136.8 |  | 14331 | 175.32 | 6.7724 | 60.68 | 0.018072 | 143.44 | 1136.8 | 993.36
14332 | 6.7739 | 175.33 | 60.68 | 0.018076 | 143.45 | 1136.8 |  | 14332 | 175.33 | 6.7739 | 60.68 | 0.018076 | 143.45 | 1136.8 | 993.35
14333 | 6.7754 | 175.34 | 60.68 | 0.01808 | 143.46 | 1136.8 |  | 14333 | 175.34 | 6.7754 | 60.68 | 0.01808 | 143.46 | 1136.8 | 993.34
14334 | 6.777 | 175.35 | 60.679 | 0.018084 | 143.47 | 1136.8 |  | 14334 | 175.35 | 6.777 | 60.679 | 0.018084 | 143.47 | 1136.8 | 993.33
14335 | 6.7785 | 175.36 | 60.679 | 0.018088 | 143.48 | 1136.8 |  | 14335 | 175.36 | 6.7785 | 60.679 | 0.018088 | 143.48 | 1136.8 | 993.32
14336 | 6.78 | 175.37 | 60.679 | 0.018091 | 143.49 | 1136.8 |  | 14336 | 175.37 | 6.78 | 60.679 | 0.018091 | 143.49 | 1136.8 | 993.31
14337 | 6.7815 | 175.38 | 60.679 | 0.018095 | 143.5 | 1136.8 |  | 14337 | 175.38 | 6.7815 | 60.679 | 0.018095 | 143.5 | 1136.8 | 993.3
14338 | 6.7831 | 175.39 | 60.679 | 0.018099 | 143.51 | 1136.8 |  | 14338 | 175.39 | 6.7831 | 60.679 | 0.018099 | 143.51 | 1136.8 | 993.29
14339 | 6.7846 | 175.4 | 60.678 | 0.018103 | 143.52 | 1136.8 |  | 14339 | 175.4 | 6.7846 | 60.678 | 0.018103 | 143.52 | 1136.8 | 993.28
14340 | 6.7861 | 175.41 | 60.678 | 0.018107 | 143.53 | 1136.8 |  | 14340 | 175.41 | 6.7861 | 60.678 | 0.018107 | 143.53 | 1136.8 | 993.27
14341 | 6.7877 | 175.42 | 60.678 | 0.018111 | 143.54 | 1136.8 |  | 14341 | 175.42 | 6.7877 | 60.678 | 0.018111 | 143.54 | 1136.8 | 993.26
14342 | 6.7892 | 175.43 | 60.678 | 0.018114 | 143.55 | 1136.8 |  | 14342 | 175.43 | 6.7892 | 60.678 | 0.018114 | 143.55 | 1136.8 | 993.25
14343 | 6.7907 | 175.44 | 60.677 | 0.018118 | 143.56 | 1136.8 |  | 14343 | 175.44 | 6.7907 | 60.677 | 0.018118 | 143.56 | 1136.8 | 993.24
14344 | 6.7922 | 175.45 | 60.677 | 0.018122 | 143.57 | 1136.8 |  | 14344 | 175.45 | 6.7922 | 60.677 | 0.018122 | 143.57 | 1136.8 | 993.23
14345 | 6.7938 | 175.46 | 60.677 | 0.018126 | 143.58 | 1136.8 |  | 14345 | 175.46 | 6.7938 | 60.677 | 0.018126 | 143.58 | 1136.8 | 993.22
14346 | 6.7953 | 175.47 | 60.677 | 0.01813 | 143.59 | 1136.8 |  | 14346 | 175.47 | 6.7953 | 60.677 | 0.01813 | 143.59 | 1136.8 | 993.21
14347 | 6.7968 | 175.48 | 60.677 | 0.018133 | 143.6 | 1136.8 |  | 14347 | 175.48 | 6.7968 | 60.677 | 0.018133 | 143.6 | 1136.8 | 993.2
14348 | 6.7984 | 175.49 | 60.676 | 0.018137 | 143.61 | 1136.8 |  | 14348 | 175.49 | 6.7984 | 60.676 | 0.018137 | 143.61 | 1136.8 | 993.19
14349 | 6.7999 | 175.5 | 60.676 | 0.018141 | 143.62 | 1136.9 |  | 14349 | 175.5 | 6.7999 | 60.676 | 0.018141 | 143.62 | 1136.9 | 993.28
14350 | 6.8014 | 175.51 | 60.676 | 0.018145 | 143.63 | 1136.9 |  | 14350 | 175.51 | 6.8014 | 60.676 | 0.018145 | 143.63 | 1136.9 | 993.27
14351 | 6.803 | 175.52 | 60.676 | 0.018149 | 143.64 | 1136.9 |  | 14351 | 175.52 | 6.803 | 60.676 | 0.018149 | 143.64 | 1136.9 | 993.26
14352 | 6.8045 | 175.53 | 60.676 | 0.018153 | 143.65 | 1136.9 |  | 14352 | 175.53 | 6.8045 | 60.676 | 0.018153 | 143.65 | 1136.9 | 993.25
14353 | 6.806 | 175.54 | 60.675 | 0.018156 | 143.66 | 1136.9 |  | 14353 | 175.54 | 6.806 | 60.675 | 0.018156 | 143.66 | 1136.9 | 993.24
14354 | 6.8076 | 175.55 | 60.675 | 0.01816 | 143.67 | 1136.9 |  | 14354 | 175.55 | 6.8076 | 60.675 | 0.01816 | 143.67 | 1136.9 | 993.23
14355 | 6.8091 | 175.56 | 60.675 | 0.018164 | 143.68 | 1136.9 |  | 14355 | 175.56 | 6.8091 | 60.675 | 0.018164 | 143.68 | 1136.9 | 993.22
14356 | 6.8106 | 175.57 | 60.675 | 0.018168 | 143.69 | 1136.9 |  | 14356 | 175.57 | 6.8106 | 60.675 | 0.018168 | 143.69 | 1136.9 | 993.21
14357 | 6.8122 | 175.58 | 60.674 | 0.018172 | 143.7 | 1136.9 |  | 14357 | 175.58 | 6.8122 | 60.674 | 0.018172 | 143.7 | 1136.9 | 993.2
14358 | 6.8137 | 175.59 | 60.674 | 0.018176 | 143.71 | 1136.9 |  | 14358 | 175.59 | 6.8137 | 60.674 | 0.018176 | 143.71 | 1136.9 | 993.19
14359 | 6.8152 | 175.6 | 60.674 | 0.018179 | 143.72 | 1136.9 |  | 14359 | 175.6 | 6.8152 | 60.674 | 0.018179 | 143.72 | 1136.9 | 993.18
14360 | 6.8168 | 175.61 | 60.674 | 0.018183 | 143.73 | 1136.9 |  | 14360 | 175.61 | 6.8168 | 60.674 | 0.018183 | 143.73 | 1136.9 | 993.17
14361 | 6.8183 | 175.62 | 60.674 | 0.018187 | 143.74 | 1136.9 |  | 14361 | 175.62 | 6.8183 | 60.674 | 0.018187 | 143.74 | 1136.9 | 993.16
14362 | 6.8199 | 175.63 | 60.673 | 0.018191 | 143.75 | 1136.9 |  | 14362 | 175.63 | 6.8199 | 60.673 | 0.018191 | 143.75 | 1136.9 | 993.15
14363 | 6.8214 | 175.64 | 60.673 | 0.018195 | 143.76 | 1136.9 |  | 14363 | 175.64 | 6.8214 | 60.673 | 0.018195 | 143.76 | 1136.9 | 993.14
14364 | 6.8229 | 175.65 | 60.673 | 0.018199 | 143.77 | 1136.9 |  | 14364 | 175.65 | 6.8229 | 60.673 | 0.018199 | 143.77 | 1136.9 | 993.13
14365 | 6.8245 | 175.66 | 60.673 | 0.018202 | 143.78 | 1136.9 |  | 14365 | 175.66 | 6.8245 | 60.673 | 0.018202 | 143.78 | 1136.9 | 993.12
14366 | 6.826 | 175.67 | 60.673 | 0.018206 | 143.79 | 1136.9 |  | 14366 | 175.67 | 6.826 | 60.673 | 0.018206 | 143.79 | 1136.9 | 993.11
14367 | 6.8275 | 175.68 | 60.672 | 0.01821 | 143.8 | 1136.9 |  | 14367 | 175.68 | 6.8275 | 60.672 | 0.01821 | 143.8 | 1136.9 | 993.1
14368 | 6.8291 | 175.69 | 60.672 | 0.018214 | 143.81 | 1136.9 |  | 14368 | 175.69 | 6.8291 | 60.672 | 0.018214 | 143.81 | 1136.9 | 993.09
14369 | 6.8306 | 175.7 | 60.672 | 0.018218 | 143.82 | 1136.9 |  | 14369 | 175.7 | 6.8306 | 60.672 | 0.018218 | 143.82 | 1136.9 | 993.08
14370 | 6.8321 | 175.71 | 60.672 | 0.018222 | 143.83 | 1136.9 |  | 14370 | 175.71 | 6.8321 | 60.672 | 0.018222 | 143.83 | 1136.9 | 993.07
14371 | 6.8337 | 175.72 | 60.671 | 0.018225 | 143.84 | 1136.9 |  | 14371 | 175.72 | 6.8337 | 60.671 | 0.018225 | 143.84 | 1136.9 | 993.06
14372 | 6.8352 | 175.73 | 60.671 | 0.018229 | 143.85 | 1136.9 |  | 14372 | 175.73 | 6.8352 | 60.671 | 0.018229 | 143.85 | 1136.9 | 993.05
14373 | 6.8368 | 175.74 | 60.671 | 0.018233 | 143.86 | 1136.9 |  | 14373 | 175.74 | 6.8368 | 60.671 | 0.018233 | 143.86 | 1136.9 | 993.04
14374 | 6.8383 | 175.75 | 60.671 | 0.018237 | 143.87 | 1137 |  | 14374 | 175.75 | 6.8383 | 60.671 | 0.018237 | 143.87 | 1137 | 993.13
14375 | 6.8398 | 175.76 | 60.671 | 0.018241 | 143.88 | 1137 |  | 14375 | 175.76 | 6.8398 | 60.671 | 0.018241 | 143.88 | 1137 | 993.12
14376 | 6.8414 | 175.77 | 60.67 | 0.018245 | 143.89 | 1137 |  | 14376 | 175.77 | 6.8414 | 60.67 | 0.018245 | 143.89 | 1137 | 993.11
14377 | 6.8429 | 175.78 | 60.67 | 0.018249 | 143.91 | 1137 |  | 14377 | 175.78 | 6.8429 | 60.67 | 0.018249 | 143.91 | 1137 | 993.09
14378 | 6.8445 | 175.79 | 60.67 | 0.018252 | 143.92 | 1137 |  | 14378 | 175.79 | 6.8445 | 60.67 | 0.018252 | 143.92 | 1137 | 993.08
14379 | 6.846 | 175.8 | 60.67 | 0.018256 | 143.93 | 1137 |  | 14379 | 175.8 | 6.846 | 60.67 | 0.018256 | 143.93 | 1137 | 993.07
14380 | 6.8475 | 175.81 | 60.669 | 0.01826 | 143.94 | 1137 |  | 14380 | 175.81 | 6.8475 | 60.669 | 0.01826 | 143.94 | 1137 | 993.06
14381 | 6.8491 | 175.82 | 60.669 | 0.018264 | 143.95 | 1137 |  | 14381 | 175.82 | 6.8491 | 60.669 | 0.018264 | 143.95 | 1137 | 993.05
14382 | 6.8506 | 175.83 | 60.669 | 0.018268 | 143.96 | 1137 |  | 14382 | 175.83 | 6.8506 | 60.669 | 0.018268 | 143.96 | 1137 | 993.04
14383 | 6.8522 | 175.84 | 60.669 | 0.018272 | 143.97 | 1137 |  | 14383 | 175.84 | 6.8522 | 60.669 | 0.018272 | 143.97 | 1137 | 993.03
14384 | 6.8537 | 175.85 | 60.669 | 0.018276 | 143.98 | 1137 |  | 14384 | 175.85 | 6.8537 | 60.669 | 0.018276 | 143.98 | 1137 | 993.02
14385 | 6.8553 | 175.86 | 60.668 | 0.018279 | 143.99 | 1137 |  | 14385 | 175.86 | 6.8553 | 60.668 | 0.018279 | 143.99 | 1137 | 993.01
14386 | 6.8568 | 175.87 | 60.668 | 0.018283 | 144 | 1137 |  | 14386 | 175.87 | 6.8568 | 60.668 | 0.018283 | 144 | 1137 | 993
14387 | 6.8583 | 175.88 | 60.668 | 0.018287 | 144.01 | 1137 |  | 14387 | 175.88 | 6.8583 | 60.668 | 0.018287 | 144.01 | 1137 | 992.99
14388 | 6.8599 | 175.89 | 60.668 | 0.018291 | 144.02 | 1137 |  | 14388 | 175.89 | 6.8599 | 60.668 | 0.018291 | 144.02 | 1137 | 992.98
14389 | 6.8614 | 175.9 | 60.668 | 0.018295 | 144.03 | 1137 |  | 14389 | 175.9 | 6.8614 | 60.668 | 0.018295 | 144.03 | 1137 | 992.97
14390 | 6.863 | 175.91 | 60.667 | 0.018299 | 144.04 | 1137 |  | 14390 | 175.91 | 6.863 | 60.667 | 0.018299 | 144.04 | 1137 | 992.96
14391 | 6.8645 | 175.92 | 60.667 | 0.018302 | 144.05 | 1137 |  | 14391 | 175.92 | 6.8645 | 60.667 | 0.018302 | 144.05 | 1137 | 992.95
14392 | 6.8661 | 175.93 | 60.667 | 0.018306 | 144.06 | 1137 |  | 14392 | 175.93 | 6.8661 | 60.667 | 0.018306 | 144.06 | 1137 | 992.94
14393 | 6.8676 | 175.94 | 60.667 | 0.01831 | 144.07 | 1137 |  | 14393 | 175.94 | 6.8676 | 60.667 | 0.01831 | 144.07 | 1137 | 992.93
14394 | 6.8692 | 175.95 | 60.666 | 0.018314 | 144.08 | 1137 |  | 14394 | 175.95 | 6.8692 | 60.666 | 0.018314 | 144.08 | 1137 | 992.92
14395 | 6.8707 | 175.96 | 60.666 | 0.018318 | 144.09 | 1137 |  | 14395 | 175.96 | 6.8707 | 60.666 | 0.018318 | 144.09 | 1137 | 992.91
14396 | 6.8722 | 175.97 | 60.666 | 0.018322 | 144.1 | 1137 |  | 14396 | 175.97 | 6.8722 | 60.666 | 0.018322 | 144.1 | 1137 | 992.9
14397 | 6.8738 | 175.98 | 60.666 | 0.018326 | 144.11 | 1137 |  | 14397 | 175.98 | 6.8738 | 60.666 | 0.018326 | 144.11 | 1137 | 992.89
14398 | 6.8753 | 175.99 | 60.666 | 0.018329 | 144.12 | 1137 |  | 14398 | 175.99 | 6.8753 | 60.666 | 0.018329 | 144.12 | 1137 | 992.88
14399 | 6.8769 | 176 | 60.665 | 0.018333 | 144.13 | 1137.1 |  | 14399 | 176 | 6.8769 | 60.665 | 0.018333 | 144.13 | 1137.1 | 992.97
14400 | 6.8784 | 176.01 | 60.665 | 0.018337 | 144.14 | 1137.1 |  | 14400 | 176.01 | 6.8784 | 60.665 | 0.018337 | 144.14 | 1137.1 | 992.96
14401 | 6.88 | 176.02 | 60.665 | 0.018341 | 144.15 | 1137.1 |  | 14401 | 176.02 | 6.88 | 60.665 | 0.018341 | 144.15 | 1137.1 | 992.95
14402 | 6.8815 | 176.03 | 60.665 | 0.018345 | 144.16 | 1137.1 |  | 14402 | 176.03 | 6.8815 | 60.665 | 0.018345 | 144.16 | 1137.1 | 992.94
14403 | 6.8831 | 176.04 | 60.665 | 0.018349 | 144.17 | 1137.1 |  | 14403 | 176.04 | 6.8831 | 60.665 | 0.018349 | 144.17 | 1137.1 | 992.93
14404 | 6.8846 | 176.05 | 60.664 | 0.018353 | 144.18 | 1137.1 |  | 14404 | 176.05 | 6.8846 | 60.664 | 0.018353 | 144.18 | 1137.1 | 992.92
14405 | 6.8862 | 176.06 | 60.664 | 0.018357 | 144.19 | 1137.1 |  | 14405 | 176.06 | 6.8862 | 60.664 | 0.018357 | 144.19 | 1137.1 | 992.91
14406 | 6.8877 | 176.07 | 60.664 | 0.01836 | 144.2 | 1137.1 |  | 14406 | 176.07 | 6.8877 | 60.664 | 0.01836 | 144.2 | 1137.1 | 992.9
14407 | 6.8893 | 176.08 | 60.664 | 0.018364 | 144.21 | 1137.1 |  | 14407 | 176.08 | 6.8893 | 60.664 | 0.018364 | 144.21 | 1137.1 | 992.89
14408 | 6.8908 | 176.09 | 60.663 | 0.018368 | 144.22 | 1137.1 |  | 14408 | 176.09 | 6.8908 | 60.663 | 0.018368 | 144.22 | 1137.1 | 992.88
14409 | 6.8924 | 176.1 | 60.663 | 0.018372 | 144.23 | 1137.1 |  | 14409 | 176.1 | 6.8924 | 60.663 | 0.018372 | 144.23 | 1137.1 | 992.87
14410 | 6.8939 | 176.11 | 60.663 | 0.018376 | 144.24 | 1137.1 |  | 14410 | 176.11 | 6.8939 | 60.663 | 0.018376 | 144.24 | 1137.1 | 992.86
14411 | 6.8955 | 176.12 | 60.663 | 0.01838 | 144.25 | 1137.1 |  | 14411 | 176.12 | 6.8955 | 60.663 | 0.01838 | 144.25 | 1137.1 | 992.85
14412 | 6.897 | 176.13 | 60.663 | 0.018384 | 144.26 | 1137.1 |  | 14412 | 176.13 | 6.897 | 60.663 | 0.018384 | 144.26 | 1137.1 | 992.84
14413 | 6.8986 | 176.14 | 60.662 | 0.018387 | 144.27 | 1137.1 |  | 14413 | 176.14 | 6.8986 | 60.662 | 0.018387 | 144.27 | 1137.1 | 992.83
14414 | 6.9001 | 176.15 | 60.662 | 0.018391 | 144.28 | 1137.1 |  | 14414 | 176.15 | 6.9001 | 60.662 | 0.018391 | 144.28 | 1137.1 | 992.82
14415 | 6.9017 | 176.16 | 60.662 | 0.018395 | 144.29 | 1137.1 |  | 14415 | 176.16 | 6.9017 | 60.662 | 0.018395 | 144.29 | 1137.1 | 992.81
14416 | 6.9032 | 176.17 | 60.662 | 0.018399 | 144.3 | 1137.1 |  | 14416 | 176.17 | 6.9032 | 60.662 | 0.018399 | 144.3 | 1137.1 | 992.8
14417 | 6.9048 | 176.18 | 60.661 | 0.018403 | 144.31 | 1137.1 |  | 14417 | 176.18 | 6.9048 | 60.661 | 0.018403 | 144.31 | 1137.1 | 992.79
14418 | 6.9063 | 176.19 | 60.661 | 0.018407 | 144.32 | 1137.1 |  | 14418 | 176.19 | 6.9063 | 60.661 | 0.018407 | 144.32 | 1137.1 | 992.78
14419 | 6.9079 | 176.2 | 60.661 | 0.018411 | 144.33 | 1137.1 |  | 14419 | 176.2 | 6.9079 | 60.661 | 0.018411 | 144.33 | 1137.1 | 992.77
14420 | 6.9094 | 176.21 | 60.661 | 0.018415 | 144.34 | 1137.1 |  | 14420 | 176.21 | 6.9094 | 60.661 | 0.018415 | 144.34 | 1137.1 | 992.76
14421 | 6.911 | 176.22 | 60.661 | 0.018418 | 144.35 | 1137.1 |  | 14421 | 176.22 | 6.911 | 60.661 | 0.018418 | 144.35 | 1137.1 | 992.75
14422 | 6.9125 | 176.23 | 60.66 | 0.018422 | 144.36 | 1137.1 |  | 14422 | 176.23 | 6.9125 | 60.66 | 0.018422 | 144.36 | 1137.1 | 992.74
14423 | 6.9141 | 176.24 | 60.66 | 0.018426 | 144.37 | 1137.1 |  | 14423 | 176.24 | 6.9141 | 60.66 | 0.018426 | 144.37 | 1137.1 | 992.73
14424 | 6.9157 | 176.25 | 60.66 | 0.01843 | 144.38 | 1137.2 |  | 14424 | 176.25 | 6.9157 | 60.66 | 0.01843 | 144.38 | 1137.2 | 992.82
14425 | 6.9172 | 176.26 | 60.66 | 0.018434 | 144.39 | 1137.2 |  | 14425 | 176.26 | 6.9172 | 60.66 | 0.018434 | 144.39 | 1137.2 | 992.81
14426 | 6.9188 | 176.27 | 60.66 | 0.018438 | 144.4 | 1137.2 |  | 14426 | 176.27 | 6.9188 | 60.66 | 0.018438 | 144.4 | 1137.2 | 992.8
14427 | 6.9203 | 176.28 | 60.659 | 0.018442 | 144.41 | 1137.2 |  | 14427 | 176.28 | 6.9203 | 60.659 | 0.018442 | 144.41 | 1137.2 | 992.79
14428 | 6.9219 | 176.29 | 60.659 | 0.018446 | 144.42 | 1137.2 |  | 14428 | 176.29 | 6.9219 | 60.659 | 0.018446 | 144.42 | 1137.2 | 992.78
14429 | 6.9234 | 176.3 | 60.659 | 0.018449 | 144.43 | 1137.2 |  | 14429 | 176.3 | 6.9234 | 60.659 | 0.018449 | 144.43 | 1137.2 | 992.77
14430 | 6.925 | 176.31 | 60.659 | 0.018453 | 144.44 | 1137.2 |  | 14430 | 176.31 | 6.925 | 60.659 | 0.018453 | 144.44 | 1137.2 | 992.76
14431 | 6.9265 | 176.32 | 60.658 | 0.018457 | 144.45 | 1137.2 |  | 14431 | 176.32 | 6.9265 | 60.658 | 0.018457 | 144.45 | 1137.2 | 992.75
14432 | 6.9281 | 176.33 | 60.658 | 0.018461 | 144.46 | 1137.2 |  | 14432 | 176.33 | 6.9281 | 60.658 | 0.018461 | 144.46 | 1137.2 | 992.74
14433 | 6.9297 | 176.34 | 60.658 | 0.018465 | 144.47 | 1137.2 |  | 14433 | 176.34 | 6.9297 | 60.658 | 0.018465 | 144.47 | 1137.2 | 992.73
14434 | 6.9312 | 176.35 | 60.658 | 0.018469 | 144.48 | 1137.2 |  | 14434 | 176.35 | 6.9312 | 60.658 | 0.018469 | 144.48 | 1137.2 | 992.72
14435 | 6.9328 | 176.36 | 60.658 | 0.018473 | 144.49 | 1137.2 |  | 14435 | 176.36 | 6.9328 | 60.658 | 0.018473 | 144.49 | 1137.2 | 992.71
14436 | 6.9343 | 176.37 | 60.657 | 0.018477 | 144.5 | 1137.2 |  | 14436 | 176.37 | 6.9343 | 60.657 | 0.018477 | 144.5 | 1137.2 | 992.7
14437 | 6.9359 | 176.38 | 60.657 | 0.018481 | 144.51 | 1137.2 |  | 14437 | 176.38 | 6.9359 | 60.657 | 0.018481 | 144.51 | 1137.2 | 992.69
14438 | 6.9374 | 176.39 | 60.657 | 0.018484 | 144.52 | 1137.2 |  | 14438 | 176.39 | 6.9374 | 60.657 | 0.018484 | 144.52 | 1137.2 | 992.68
14439 | 6.939 | 176.4 | 60.657 | 0.018488 | 144.53 | 1137.2 |  | 14439 | 176.4 | 6.939 | 60.657 | 0.018488 | 144.53 | 1137.2 | 992.67
14440 | 6.9406 | 176.41 | 60.657 | 0.018492 | 144.54 | 1137.2 |  | 14440 | 176.41 | 6.9406 | 60.657 | 0.018492 | 144.54 | 1137.2 | 992.66
14441 | 6.9421 | 176.42 | 60.656 | 0.018496 | 144.55 | 1137.2 |  | 14441 | 176.42 | 6.9421 | 60.656 | 0.018496 | 144.55 | 1137.2 | 992.65
14442 | 6.9437 | 176.43 | 60.656 | 0.0185 | 144.56 | 1137.2 |  | 14442 | 176.43 | 6.9437 | 60.656 | 0.0185 | 144.56 | 1137.2 | 992.64
14443 | 6.9452 | 176.44 | 60.656 | 0.018504 | 144.57 | 1137.2 |  | 14443 | 176.44 | 6.9452 | 60.656 | 0.018504 | 144.57 | 1137.2 | 992.63
14444 | 6.9468 | 176.45 | 60.656 | 0.018508 | 144.58 | 1137.2 |  | 14444 | 176.45 | 6.9468 | 60.656 | 0.018508 | 144.58 | 1137.2 | 992.62
14445 | 6.9484 | 176.46 | 60.655 | 0.018512 | 144.59 | 1137.2 |  | 14445 | 176.46 | 6.9484 | 60.655 | 0.018512 | 144.59 | 1137.2 | 992.61
14446 | 6.9499 | 176.47 | 60.655 | 0.018516 | 144.6 | 1137.2 |  | 14446 | 176.47 | 6.9499 | 60.655 | 0.018516 | 144.6 | 1137.2 | 992.6
14447 | 6.9515 | 176.48 | 60.655 | 0.018519 | 144.61 | 1137.2 |  | 14447 | 176.48 | 6.9515 | 60.655 | 0.018519 | 144.61 | 1137.2 | 992.59
14448 | 6.953 | 176.49 | 60.655 | 0.018523 | 144.62 | 1137.2 |  | 14448 | 176.49 | 6.953 | 60.655 | 0.018523 | 144.62 | 1137.2 | 992.58
14449 | 6.9546 | 176.5 | 60.655 | 0.018527 | 144.63 | 1137.3 |  | 14449 | 176.5 | 6.9546 | 60.655 | 0.018527 | 144.63 | 1137.3 | 992.67
14450 | 6.9562 | 176.51 | 60.654 | 0.018531 | 144.64 | 1137.3 |  | 14450 | 176.51 | 6.9562 | 60.654 | 0.018531 | 144.64 | 1137.3 | 992.66
14451 | 6.9577 | 176.52 | 60.654 | 0.018535 | 144.65 | 1137.3 |  | 14451 | 176.52 | 6.9577 | 60.654 | 0.018535 | 144.65 | 1137.3 | 992.65
14452 | 6.9593 | 176.53 | 60.654 | 0.018539 | 144.66 | 1137.3 |  | 14452 | 176.53 | 6.9593 | 60.654 | 0.018539 | 144.66 | 1137.3 | 992.64
14453 | 6.9609 | 176.54 | 60.654 | 0.018543 | 144.67 | 1137.3 |  | 14453 | 176.54 | 6.9609 | 60.654 | 0.018543 | 144.67 | 1137.3 | 992.63
14454 | 6.9624 | 176.55 | 60.653 | 0.018547 | 144.68 | 1137.3 |  | 14454 | 176.55 | 6.9624 | 60.653 | 0.018547 | 144.68 | 1137.3 | 992.62
14455 | 6.964 | 176.56 | 60.653 | 0.018551 | 144.69 | 1137.3 |  | 14455 | 176.56 | 6.964 | 60.653 | 0.018551 | 144.69 | 1137.3 | 992.61
14456 | 6.9655 | 176.57 | 60.653 | 0.018555 | 144.7 | 1137.3 |  | 14456 | 176.57 | 6.9655 | 60.653 | 0.018555 | 144.7 | 1137.3 | 992.6
14457 | 6.9671 | 176.58 | 60.653 | 0.018558 | 144.71 | 1137.3 |  | 14457 | 176.58 | 6.9671 | 60.653 | 0.018558 | 144.71 | 1137.3 | 992.59
14458 | 6.9687 | 176.59 | 60.653 | 0.018562 | 144.72 | 1137.3 |  | 14458 | 176.59 | 6.9687 | 60.653 | 0.018562 | 144.72 | 1137.3 | 992.58
14459 | 6.9702 | 176.6 | 60.652 | 0.018566 | 144.73 | 1137.3 |  | 14459 | 176.6 | 6.9702 | 60.652 | 0.018566 | 144.73 | 1137.3 | 992.57
14460 | 6.9718 | 176.61 | 60.652 | 0.01857 | 144.74 | 1137.3 |  | 14460 | 176.61 | 6.9718 | 60.652 | 0.01857 | 144.74 | 1137.3 | 992.56
14461 | 6.9734 | 176.62 | 60.652 | 0.018574 | 144.75 | 1137.3 |  | 14461 | 176.62 | 6.9734 | 60.652 | 0.018574 | 144.75 | 1137.3 | 992.55
14462 | 6.9749 | 176.63 | 60.652 | 0.018578 | 144.76 | 1137.3 |  | 14462 | 176.63 | 6.9749 | 60.652 | 0.018578 | 144.76 | 1137.3 | 992.54
14463 | 6.9765 | 176.64 | 60.652 | 0.018582 | 144.77 | 1137.3 |  | 14463 | 176.64 | 6.9765 | 60.652 | 0.018582 | 144.77 | 1137.3 | 992.53
14464 | 6.9781 | 176.65 | 60.651 | 0.018586 | 144.78 | 1137.3 |  | 14464 | 176.65 | 6.9781 | 60.651 | 0.018586 | 144.78 | 1137.3 | 992.52
14465 | 6.9796 | 176.66 | 60.651 | 0.01859 | 144.79 | 1137.3 |  | 14465 | 176.66 | 6.9796 | 60.651 | 0.01859 | 144.79 | 1137.3 | 992.51
14466 | 6.9812 | 176.67 | 60.651 | 0.018594 | 144.8 | 1137.3 |  | 14466 | 176.67 | 6.9812 | 60.651 | 0.018594 | 144.8 | 1137.3 | 992.5
14467 | 6.9828 | 176.68 | 60.651 | 0.018597 | 144.81 | 1137.3 |  | 14467 | 176.68 | 6.9828 | 60.651 | 0.018597 | 144.81 | 1137.3 | 992.49
14468 | 6.9843 | 176.69 | 60.65 | 0.018601 | 144.82 | 1137.3 |  | 14468 | 176.69 | 6.9843 | 60.65 | 0.018601 | 144.82 | 1137.3 | 992.48
14469 | 6.9859 | 176.7 | 60.65 | 0.018605 | 144.83 | 1137.3 |  | 14469 | 176.7 | 6.9859 | 60.65 | 0.018605 | 144.83 | 1137.3 | 992.47
14470 | 6.9875 | 176.71 | 60.65 | 0.018609 | 144.84 | 1137.3 |  | 14470 | 176.71 | 6.9875 | 60.65 | 0.018609 | 144.84 | 1137.3 | 992.46
14471 | 6.989 | 176.72 | 60.65 | 0.018613 | 144.85 | 1137.3 |  | 14471 | 176.72 | 6.989 | 60.65 | 0.018613 | 144.85 | 1137.3 | 992.45
14472 | 6.9906 | 176.73 | 60.65 | 0.018617 | 144.86 | 1137.3 |  | 14472 | 176.73 | 6.9906 | 60.65 | 0.018617 | 144.86 | 1137.3 | 992.44
14473 | 6.9922 | 176.74 | 60.649 | 0.018621 | 144.87 | 1137.3 |  | 14473 | 176.74 | 6.9922 | 60.649 | 0.018621 | 144.87 | 1137.3 | 992.43
14474 | 6.9937 | 176.75 | 60.649 | 0.018625 | 144.88 | 1137.4 |  | 14474 | 176.75 | 6.9937 | 60.649 | 0.018625 | 144.88 | 1137.4 | 992.52
14475 | 6.9953 | 176.76 | 60.649 | 0.018629 | 144.89 | 1137.4 |  | 14475 | 176.76 | 6.9953 | 60.649 | 0.018629 | 144.89 | 1137.4 | 992.51
14476 | 6.9969 | 176.77 | 60.649 | 0.018633 | 144.9 | 1137.4 |  | 14476 | 176.77 | 6.9969 | 60.649 | 0.018633 | 144.9 | 1137.4 | 992.5
14477 | 6.9984 | 176.78 | 60.649 | 0.018637 | 144.91 | 1137.4 |  | 14477 | 176.78 | 6.9984 | 60.649 | 0.018637 | 144.91 | 1137.4 | 992.49
14478 | 7 | 176.79 | 60.648 | 0.018641 | 144.92 | 1137.4 |  | 14478 | 176.79 | 7 | 60.648 | 0.018641 | 144.92 | 1137.4 | 992.48
14479 | 7.0016 | 176.8 | 60.648 | 0.018644 | 144.93 | 1137.4 |  | 14479 | 176.8 | 7.0016 | 60.648 | 0.018644 | 144.93 | 1137.4 | 992.47
14480 | 7.0032 | 176.81 | 60.648 | 0.018648 | 144.94 | 1137.4 |  | 14480 | 176.81 | 7.0032 | 60.648 | 0.018648 | 144.94 | 1137.4 | 992.46
14481 | 7.0047 | 176.82 | 60.648 | 0.018652 | 144.95 | 1137.4 |  | 14481 | 176.82 | 7.0047 | 60.648 | 0.018652 | 144.95 | 1137.4 | 992.45
14482 | 7.0063 | 176.83 | 60.647 | 0.018656 | 144.96 | 1137.4 |  | 14482 | 176.83 | 7.0063 | 60.647 | 0.018656 | 144.96 | 1137.4 | 992.44
14483 | 7.0079 | 176.84 | 60.647 | 0.01866 | 144.97 | 1137.4 |  | 14483 | 176.84 | 7.0079 | 60.647 | 0.01866 | 144.97 | 1137.4 | 992.43
14484 | 7.0094 | 176.85 | 60.647 | 0.018664 | 144.98 | 1137.4 |  | 14484 | 176.85 | 7.0094 | 60.647 | 0.018664 | 144.98 | 1137.4 | 992.42
14485 | 7.011 | 176.86 | 60.647 | 0.018668 | 144.99 | 1137.4 |  | 14485 | 176.86 | 7.011 | 60.647 | 0.018668 | 144.99 | 1137.4 | 992.41
14486 | 7.0126 | 176.87 | 60.647 | 0.018672 | 145 | 1137.4 |  | 14486 | 176.87 | 7.0126 | 60.647 | 0.018672 | 145 | 1137.4 | 992.4
14487 | 7.0142 | 176.88 | 60.646 | 0.018676 | 145.01 | 1137.4 |  | 14487 | 176.88 | 7.0142 | 60.646 | 0.018676 | 145.01 | 1137.4 | 992.39
14488 | 7.0157 | 176.89 | 60.646 | 0.01868 | 145.02 | 1137.4 |  | 14488 | 176.89 | 7.0157 | 60.646 | 0.01868 | 145.02 | 1137.4 | 992.38
14489 | 7.0173 | 176.9 | 60.646 | 0.018684 | 145.03 | 1137.4 |  | 14489 | 176.9 | 7.0173 | 60.646 | 0.018684 | 145.03 | 1137.4 | 992.37
14490 | 7.0189 | 176.91 | 60.646 | 0.018688 | 145.04 | 1137.4 |  | 14490 | 176.91 | 7.0189 | 60.646 | 0.018688 | 145.04 | 1137.4 | 992.36
14491 | 7.0205 | 176.92 | 60.645 | 0.018691 | 145.05 | 1137.4 |  | 14491 | 176.92 | 7.0205 | 60.645 | 0.018691 | 145.05 | 1137.4 | 992.35
14492 | 7.022 | 176.93 | 60.645 | 0.018695 | 145.06 | 1137.4 |  | 14492 | 176.93 | 7.022 | 60.645 | 0.018695 | 145.06 | 1137.4 | 992.34
14493 | 7.0236 | 176.94 | 60.645 | 0.018699 | 145.07 | 1137.4 |  | 14493 | 176.94 | 7.0236 | 60.645 | 0.018699 | 145.07 | 1137.4 | 992.33
14494 | 7.0252 | 176.95 | 60.645 | 0.018703 | 145.08 | 1137.4 |  | 14494 | 176.95 | 7.0252 | 60.645 | 0.018703 | 145.08 | 1137.4 | 992.32
14495 | 7.0267 | 176.96 | 60.645 | 0.018707 | 145.09 | 1137.4 |  | 14495 | 176.96 | 7.0267 | 60.645 | 0.018707 | 145.09 | 1137.4 | 992.31
14496 | 7.0283 | 176.97 | 60.644 | 0.018711 | 145.1 | 1137.4 |  | 14496 | 176.97 | 7.0283 | 60.644 | 0.018711 | 145.1 | 1137.4 | 992.3
14497 | 7.0299 | 176.98 | 60.644 | 0.018715 | 145.11 | 1137.4 |  | 14497 | 176.98 | 7.0299 | 60.644 | 0.018715 | 145.11 | 1137.4 | 992.29
14498 | 7.0315 | 176.99 | 60.644 | 0.018719 | 145.12 | 1137.4 |  | 14498 | 176.99 | 7.0315 | 60.644 | 0.018719 | 145.12 | 1137.4 | 992.28
14499 | 7.0331 | 177 | 60.644 | 0.018723 | 145.13 | 1137.5 |  | 14499 | 177 | 7.0331 | 60.644 | 0.018723 | 145.13 | 1137.5 | 992.37
14500 | 7.0346 | 177.01 | 60.644 | 0.018727 | 145.14 | 1137.5 |  | 14500 | 177.01 | 7.0346 | 60.644 | 0.018727 | 145.14 | 1137.5 | 992.36
14501 | 7.0362 | 177.02 | 60.643 | 0.018731 | 145.15 | 1137.5 |  | 14501 | 177.02 | 7.0362 | 60.643 | 0.018731 | 145.15 | 1137.5 | 992.35
14502 | 7.0378 | 177.03 | 60.643 | 0.018735 | 145.16 | 1137.5 |  | 14502 | 177.03 | 7.0378 | 60.643 | 0.018735 | 145.16 | 1137.5 | 992.34
14503 | 7.0394 | 177.04 | 60.643 | 0.018739 | 145.17 | 1137.5 |  | 14503 | 177.04 | 7.0394 | 60.643 | 0.018739 | 145.17 | 1137.5 | 992.33
14504 | 7.0409 | 177.05 | 60.643 | 0.018743 | 145.18 | 1137.5 |  | 14504 | 177.05 | 7.0409 | 60.643 | 0.018743 | 145.18 | 1137.5 | 992.32
14505 | 7.0425 | 177.06 | 60.642 | 0.018746 | 145.19 | 1137.5 |  | 14505 | 177.06 | 7.0425 | 60.642 | 0.018746 | 145.19 | 1137.5 | 992.31
14506 | 7.0441 | 177.07 | 60.642 | 0.01875 | 145.2 | 1137.5 |  | 14506 | 177.07 | 7.0441 | 60.642 | 0.01875 | 145.2 | 1137.5 | 992.3
14507 | 7.0457 | 177.08 | 60.642 | 0.018754 | 145.21 | 1137.5 |  | 14507 | 177.08 | 7.0457 | 60.642 | 0.018754 | 145.21 | 1137.5 | 992.29
14508 | 7.0473 | 177.09 | 60.642 | 0.018758 | 145.22 | 1137.5 |  | 14508 | 177.09 | 7.0473 | 60.642 | 0.018758 | 145.22 | 1137.5 | 992.28
14509 | 7.0488 | 177.1 | 60.642 | 0.018762 | 145.23 | 1137.5 |  | 14509 | 177.1 | 7.0488 | 60.642 | 0.018762 | 145.23 | 1137.5 | 992.27
14510 | 7.0504 | 177.11 | 60.641 | 0.018766 | 145.24 | 1137.5 |  | 14510 | 177.11 | 7.0504 | 60.641 | 0.018766 | 145.24 | 1137.5 | 992.26
14511 | 7.052 | 177.12 | 60.641 | 0.01877 | 145.25 | 1137.5 |  | 14511 | 177.12 | 7.052 | 60.641 | 0.01877 | 145.25 | 1137.5 | 992.25
14512 | 7.0536 | 177.13 | 60.641 | 0.018774 | 145.26 | 1137.5 |  | 14512 | 177.13 | 7.0536 | 60.641 | 0.018774 | 145.26 | 1137.5 | 992.24
14513 | 7.0552 | 177.14 | 60.641 | 0.018778 | 145.27 | 1137.5 |  | 14513 | 177.14 | 7.0552 | 60.641 | 0.018778 | 145.27 | 1137.5 | 992.23
14514 | 7.0567 | 177.15 | 60.64 | 0.018782 | 145.28 | 1137.5 |  | 14514 | 177.15 | 7.0567 | 60.64 | 0.018782 | 145.28 | 1137.5 | 992.22
14515 | 7.0583 | 177.16 | 60.64 | 0.018786 | 145.29 | 1137.5 |  | 14515 | 177.16 | 7.0583 | 60.64 | 0.018786 | 145.29 | 1137.5 | 992.21
14516 | 7.0599 | 177.17 | 60.64 | 0.01879 | 145.3 | 1137.5 |  | 14516 | 177.17 | 7.0599 | 60.64 | 0.01879 | 145.3 | 1137.5 | 992.2
14517 | 7.0615 | 177.18 | 60.64 | 0.018794 | 145.31 | 1137.5 |  | 14517 | 177.18 | 7.0615 | 60.64 | 0.018794 | 145.31 | 1137.5 | 992.19
14518 | 7.0631 | 177.19 | 60.64 | 0.018798 | 145.32 | 1137.5 |  | 14518 | 177.19 | 7.0631 | 60.64 | 0.018798 | 145.32 | 1137.5 | 992.18
14519 | 7.0646 | 177.2 | 60.639 | 0.018802 | 145.33 | 1137.5 |  | 14519 | 177.2 | 7.0646 | 60.639 | 0.018802 | 145.33 | 1137.5 | 992.17
14520 | 7.0662 | 177.21 | 60.639 | 0.018806 | 145.34 | 1137.5 |  | 14520 | 177.21 | 7.0662 | 60.639 | 0.018806 | 145.34 | 1137.5 | 992.16
14521 | 7.0678 | 177.22 | 60.639 | 0.018809 | 145.35 | 1137.5 |  | 14521 | 177.22 | 7.0678 | 60.639 | 0.018809 | 145.35 | 1137.5 | 992.15
14522 | 7.0694 | 177.23 | 60.639 | 0.018813 | 145.36 | 1137.5 |  | 14522 | 177.23 | 7.0694 | 60.639 | 0.018813 | 145.36 | 1137.5 | 992.14
14523 | 7.071 | 177.24 | 60.639 | 0.018817 | 145.37 | 1137.5 |  | 14523 | 177.24 | 7.071 | 60.639 | 0.018817 | 145.37 | 1137.5 | 992.13
14524 | 7.0726 | 177.25 | 60.638 | 0.018821 | 145.38 | 1137.6 |  | 14524 | 177.25 | 7.0726 | 60.638 | 0.018821 | 145.38 | 1137.6 | 992.22
14525 | 7.0741 | 177.26 | 60.638 | 0.018825 | 145.39 | 1137.6 |  | 14525 | 177.26 | 7.0741 | 60.638 | 0.018825 | 145.39 | 1137.6 | 992.21
14526 | 7.0757 | 177.27 | 60.638 | 0.018829 | 145.4 | 1137.6 |  | 14526 | 177.27 | 7.0757 | 60.638 | 0.018829 | 145.4 | 1137.6 | 992.2
14527 | 7.0773 | 177.28 | 60.638 | 0.018833 | 145.41 | 1137.6 |  | 14527 | 177.28 | 7.0773 | 60.638 | 0.018833 | 145.41 | 1137.6 | 992.19
14528 | 7.0789 | 177.29 | 60.637 | 0.018837 | 145.42 | 1137.6 |  | 14528 | 177.29 | 7.0789 | 60.637 | 0.018837 | 145.42 | 1137.6 | 992.18
14529 | 7.0805 | 177.3 | 60.637 | 0.018841 | 145.43 | 1137.6 |  | 14529 | 177.3 | 7.0805 | 60.637 | 0.018841 | 145.43 | 1137.6 | 992.17
14530 | 7.0821 | 177.31 | 60.637 | 0.018845 | 145.44 | 1137.6 |  | 14530 | 177.31 | 7.0821 | 60.637 | 0.018845 | 145.44 | 1137.6 | 992.16
14531 | 7.0836 | 177.32 | 60.637 | 0.018849 | 145.45 | 1137.6 |  | 14531 | 177.32 | 7.0836 | 60.637 | 0.018849 | 145.45 | 1137.6 | 992.15
14532 | 7.0852 | 177.33 | 60.637 | 0.018853 | 145.46 | 1137.6 |  | 14532 | 177.33 | 7.0852 | 60.637 | 0.018853 | 145.46 | 1137.6 | 992.14
14533 | 7.0868 | 177.34 | 60.636 | 0.018857 | 145.47 | 1137.6 |  | 14533 | 177.34 | 7.0868 | 60.636 | 0.018857 | 145.47 | 1137.6 | 992.13
14534 | 7.0884 | 177.35 | 60.636 | 0.018861 | 145.48 | 1137.6 |  | 14534 | 177.35 | 7.0884 | 60.636 | 0.018861 | 145.48 | 1137.6 | 992.12
14535 | 7.09 | 177.36 | 60.636 | 0.018865 | 145.49 | 1137.6 |  | 14535 | 177.36 | 7.09 | 60.636 | 0.018865 | 145.49 | 1137.6 | 992.11
14536 | 7.0916 | 177.37 | 60.636 | 0.018869 | 145.5 | 1137.6 |  | 14536 | 177.37 | 7.0916 | 60.636 | 0.018869 | 145.5 | 1137.6 | 992.1
14537 | 7.0932 | 177.38 | 60.635 | 0.018873 | 145.51 | 1137.6 |  | 14537 | 177.38 | 7.0932 | 60.635 | 0.018873 | 145.51 | 1137.6 | 992.09
14538 | 7.0948 | 177.39 | 60.635 | 0.018877 | 145.52 | 1137.6 |  | 14538 | 177.39 | 7.0948 | 60.635 | 0.018877 | 145.52 | 1137.6 | 992.08
14539 | 7.0963 | 177.4 | 60.635 | 0.018881 | 145.53 | 1137.6 |  | 14539 | 177.4 | 7.0963 | 60.635 | 0.018881 | 145.53 | 1137.6 | 992.07
14540 | 7.0979 | 177.41 | 60.635 | 0.018885 | 145.54 | 1137.6 |  | 14540 | 177.41 | 7.0979 | 60.635 | 0.018885 | 145.54 | 1137.6 | 992.06
14541 | 7.0995 | 177.42 | 60.635 | 0.018888 | 145.55 | 1137.6 |  | 14541 | 177.42 | 7.0995 | 60.635 | 0.018888 | 145.55 | 1137.6 | 992.05
14542 | 7.1011 | 177.43 | 60.634 | 0.018892 | 145.56 | 1137.6 |  | 14542 | 177.43 | 7.1011 | 60.634 | 0.018892 | 145.56 | 1137.6 | 992.04
14543 | 7.1027 | 177.44 | 60.634 | 0.018896 | 145.57 | 1137.6 |  | 14543 | 177.44 | 7.1027 | 60.634 | 0.018896 | 145.57 | 1137.6 | 992.03
14544 | 7.1043 | 177.45 | 60.634 | 0.0189 | 145.58 | 1137.6 |  | 14544 | 177.45 | 7.1043 | 60.634 | 0.0189 | 145.58 | 1137.6 | 992.02
14545 | 7.1059 | 177.46 | 60.634 | 0.018904 | 145.59 | 1137.6 |  | 14545 | 177.46 | 7.1059 | 60.634 | 0.018904 | 145.59 | 1137.6 | 992.01
14546 | 7.1075 | 177.47 | 60.634 | 0.018908 | 145.6 | 1137.6 |  | 14546 | 177.47 | 7.1075 | 60.634 | 0.018908 | 145.6 | 1137.6 | 992
14547 | 7.1091 | 177.48 | 60.633 | 0.018912 | 145.61 | 1137.6 |  | 14547 | 177.48 | 7.1091 | 60.633 | 0.018912 | 145.61 | 1137.6 | 991.99
14548 | 7.1107 | 177.49 | 60.633 | 0.018916 | 145.62 | 1137.6 |  | 14548 | 177.49 | 7.1107 | 60.633 | 0.018916 | 145.62 | 1137.6 | 991.98
14549 | 7.1122 | 177.5 | 60.633 | 0.01892 | 145.63 | 1137.7 |  | 14549 | 177.5 | 7.1122 | 60.633 | 0.01892 | 145.63 | 1137.7 | 992.07
14550 | 7.1138 | 177.51 | 60.633 | 0.018924 | 145.64 | 1137.7 |  | 14550 | 177.51 | 7.1138 | 60.633 | 0.018924 | 145.64 | 1137.7 | 992.06
14551 | 7.1154 | 177.52 | 60.632 | 0.018928 | 145.65 | 1137.7 |  | 14551 | 177.52 | 7.1154 | 60.632 | 0.018928 | 145.65 | 1137.7 | 992.05
14552 | 7.117 | 177.53 | 60.632 | 0.018932 | 145.66 | 1137.7 |  | 14552 | 177.53 | 7.117 | 60.632 | 0.018932 | 145.66 | 1137.7 | 992.04
14553 | 7.1186 | 177.54 | 60.632 | 0.018936 | 145.67 | 1137.7 |  | 14553 | 177.54 | 7.1186 | 60.632 | 0.018936 | 145.67 | 1137.7 | 992.03
14554 | 7.1202 | 177.55 | 60.632 | 0.01894 | 145.68 | 1137.7 |  | 14554 | 177.55 | 7.1202 | 60.632 | 0.01894 | 145.68 | 1137.7 | 992.02
14555 | 7.1218 | 177.56 | 60.632 | 0.018944 | 145.69 | 1137.7 |  | 14555 | 177.56 | 7.1218 | 60.632 | 0.018944 | 145.69 | 1137.7 | 992.01
14556 | 7.1234 | 177.57 | 60.631 | 0.018948 | 145.7 | 1137.7 |  | 14556 | 177.57 | 7.1234 | 60.631 | 0.018948 | 145.7 | 1137.7 | 992
14557 | 7.125 | 177.58 | 60.631 | 0.018952 | 145.71 | 1137.7 |  | 14557 | 177.58 | 7.125 | 60.631 | 0.018952 | 145.71 | 1137.7 | 991.99
14558 | 7.1266 | 177.59 | 60.631 | 0.018956 | 145.72 | 1137.7 |  | 14558 | 177.59 | 7.1266 | 60.631 | 0.018956 | 145.72 | 1137.7 | 991.98
14559 | 7.1282 | 177.6 | 60.631 | 0.01896 | 145.73 | 1137.7 |  | 14559 | 177.6 | 7.1282 | 60.631 | 0.01896 | 145.73 | 1137.7 | 991.97
14560 | 7.1298 | 177.61 | 60.631 | 0.018964 | 145.74 | 1137.7 |  | 14560 | 177.61 | 7.1298 | 60.631 | 0.018964 | 145.74 | 1137.7 | 991.96
14561 | 7.1314 | 177.62 | 60.63 | 0.018968 | 145.75 | 1137.7 |  | 14561 | 177.62 | 7.1314 | 60.63 | 0.018968 | 145.75 | 1137.7 | 991.95
14562 | 7.133 | 177.63 | 60.63 | 0.018972 | 145.76 | 1137.7 |  | 14562 | 177.63 | 7.133 | 60.63 | 0.018972 | 145.76 | 1137.7 | 991.94
14563 | 7.1346 | 177.64 | 60.63 | 0.018976 | 145.77 | 1137.7 |  | 14563 | 177.64 | 7.1346 | 60.63 | 0.018976 | 145.77 | 1137.7 | 991.93
14564 | 7.1361 | 177.65 | 60.63 | 0.01898 | 145.78 | 1137.7 |  | 14564 | 177.65 | 7.1361 | 60.63 | 0.01898 | 145.78 | 1137.7 | 991.92
14565 | 7.1377 | 177.66 | 60.629 | 0.018984 | 145.79 | 1137.7 |  | 14565 | 177.66 | 7.1377 | 60.629 | 0.018984 | 145.79 | 1137.7 | 991.91
14566 | 7.1393 | 177.67 | 60.629 | 0.018988 | 145.8 | 1137.7 |  | 14566 | 177.67 | 7.1393 | 60.629 | 0.018988 | 145.8 | 1137.7 | 991.9
14567 | 7.1409 | 177.68 | 60.629 | 0.018992 | 145.81 | 1137.7 |  | 14567 | 177.68 | 7.1409 | 60.629 | 0.018992 | 145.81 | 1137.7 | 991.89
14568 | 7.1425 | 177.69 | 60.629 | 0.018996 | 145.82 | 1137.7 |  | 14568 | 177.69 | 7.1425 | 60.629 | 0.018996 | 145.82 | 1137.7 | 991.88
14569 | 7.1441 | 177.7 | 60.629 | 0.019 | 145.83 | 1137.7 |  | 14569 | 177.7 | 7.1441 | 60.629 | 0.019 | 145.83 | 1137.7 | 991.87
14570 | 7.1457 | 177.71 | 60.628 | 0.019004 | 145.84 | 1137.7 |  | 14570 | 177.71 | 7.1457 | 60.628 | 0.019004 | 145.84 | 1137.7 | 991.86
14571 | 7.1473 | 177.72 | 60.628 | 0.019008 | 145.85 | 1137.7 |  | 14571 | 177.72 | 7.1473 | 60.628 | 0.019008 | 145.85 | 1137.7 | 991.85
14572 | 7.1489 | 177.73 | 60.628 | 0.019011 | 145.86 | 1137.7 |  | 14572 | 177.73 | 7.1489 | 60.628 | 0.019011 | 145.86 | 1137.7 | 991.84
14573 | 7.1505 | 177.74 | 60.628 | 0.019015 | 145.87 | 1137.7 |  | 14573 | 177.74 | 7.1505 | 60.628 | 0.019015 | 145.87 | 1137.7 | 991.83
14574 | 7.1521 | 177.75 | 60.627 | 0.019019 | 145.88 | 1137.8 |  | 14574 | 177.75 | 7.1521 | 60.627 | 0.019019 | 145.88 | 1137.8 | 991.92
14575 | 7.1537 | 177.76 | 60.627 | 0.019023 | 145.89 | 1137.8 |  | 14575 | 177.76 | 7.1537 | 60.627 | 0.019023 | 145.89 | 1137.8 | 991.91
14576 | 7.1553 | 177.77 | 60.627 | 0.019027 | 145.9 | 1137.8 |  | 14576 | 177.77 | 7.1553 | 60.627 | 0.019027 | 145.9 | 1137.8 | 991.9
14577 | 7.1569 | 177.78 | 60.627 | 0.019031 | 145.91 | 1137.8 |  | 14577 | 177.78 | 7.1569 | 60.627 | 0.019031 | 145.91 | 1137.8 | 991.89
14578 | 7.1585 | 177.79 | 60.627 | 0.019035 | 145.92 | 1137.8 |  | 14578 | 177.79 | 7.1585 | 60.627 | 0.019035 | 145.92 | 1137.8 | 991.88
14579 | 7.1601 | 177.8 | 60.626 | 0.019039 | 145.93 | 1137.8 |  | 14579 | 177.8 | 7.1601 | 60.626 | 0.019039 | 145.93 | 1137.8 | 991.87
14580 | 7.1617 | 177.81 | 60.626 | 0.019043 | 145.94 | 1137.8 |  | 14580 | 177.81 | 7.1617 | 60.626 | 0.019043 | 145.94 | 1137.8 | 991.86
14581 | 7.1633 | 177.82 | 60.626 | 0.019047 | 145.95 | 1137.8 |  | 14581 | 177.82 | 7.1633 | 60.626 | 0.019047 | 145.95 | 1137.8 | 991.85
14582 | 7.1649 | 177.83 | 60.626 | 0.019051 | 145.96 | 1137.8 |  | 14582 | 177.83 | 7.1649 | 60.626 | 0.019051 | 145.96 | 1137.8 | 991.84
14583 | 7.1665 | 177.84 | 60.625 | 0.019055 | 145.97 | 1137.8 |  | 14583 | 177.84 | 7.1665 | 60.625 | 0.019055 | 145.97 | 1137.8 | 991.83
14584 | 7.1681 | 177.85 | 60.625 | 0.019059 | 145.98 | 1137.8 |  | 14584 | 177.85 | 7.1681 | 60.625 | 0.019059 | 145.98 | 1137.8 | 991.82
14585 | 7.1697 | 177.86 | 60.625 | 0.019063 | 145.99 | 1137.8 |  | 14585 | 177.86 | 7.1697 | 60.625 | 0.019063 | 145.99 | 1137.8 | 991.81
14586 | 7.1713 | 177.87 | 60.625 | 0.019067 | 146 | 1137.8 |  | 14586 | 177.87 | 7.1713 | 60.625 | 0.019067 | 146 | 1137.8 | 991.8
14587 | 7.1729 | 177.88 | 60.625 | 0.019071 | 146.01 | 1137.8 |  | 14587 | 177.88 | 7.1729 | 60.625 | 0.019071 | 146.01 | 1137.8 | 991.79
14588 | 7.1745 | 177.89 | 60.624 | 0.019075 | 146.02 | 1137.8 |  | 14588 | 177.89 | 7.1745 | 60.624 | 0.019075 | 146.02 | 1137.8 | 991.78
14589 | 7.1761 | 177.9 | 60.624 | 0.019079 | 146.03 | 1137.8 |  | 14589 | 177.9 | 7.1761 | 60.624 | 0.019079 | 146.03 | 1137.8 | 991.77
14590 | 7.1777 | 177.91 | 60.624 | 0.019083 | 146.04 | 1137.8 |  | 14590 | 177.91 | 7.1777 | 60.624 | 0.019083 | 146.04 | 1137.8 | 991.76
14591 | 7.1793 | 177.92 | 60.624 | 0.019087 | 146.05 | 1137.8 |  | 14591 | 177.92 | 7.1793 | 60.624 | 0.019087 | 146.05 | 1137.8 | 991.75
14592 | 7.1809 | 177.93 | 60.624 | 0.019091 | 146.06 | 1137.8 |  | 14592 | 177.93 | 7.1809 | 60.624 | 0.019091 | 146.06 | 1137.8 | 991.74
14593 | 7.1826 | 177.94 | 60.623 | 0.019095 | 146.07 | 1137.8 |  | 14593 | 177.94 | 7.1826 | 60.623 | 0.019095 | 146.07 | 1137.8 | 991.73
14594 | 7.1842 | 177.95 | 60.623 | 0.019099 | 146.08 | 1137.8 |  | 14594 | 177.95 | 7.1842 | 60.623 | 0.019099 | 146.08 | 1137.8 | 991.72
14595 | 7.1858 | 177.96 | 60.623 | 0.019103 | 146.09 | 1137.8 |  | 14595 | 177.96 | 7.1858 | 60.623 | 0.019103 | 146.09 | 1137.8 | 991.71
14596 | 7.1874 | 177.97 | 60.623 | 0.019107 | 146.1 | 1137.8 |  | 14596 | 177.97 | 7.1874 | 60.623 | 0.019107 | 146.1 | 1137.8 | 991.7
14597 | 7.189 | 177.98 | 60.622 | 0.019111 | 146.11 | 1137.8 |  | 14597 | 177.98 | 7.189 | 60.622 | 0.019111 | 146.11 | 1137.8 | 991.69
14598 | 7.1906 | 177.99 | 60.622 | 0.019115 | 146.12 | 1137.8 |  | 14598 | 177.99 | 7.1906 | 60.622 | 0.019115 | 146.12 | 1137.8 | 991.68
14599 | 7.1922 | 178 | 60.622 | 0.019119 | 146.13 | 1137.9 |  | 14599 | 178 | 7.1922 | 60.622 | 0.019119 | 146.13 | 1137.9 | 991.77
14600 | 7.1938 | 178.01 | 60.622 | 0.019123 | 146.14 | 1137.9 |  | 14600 | 178.01 | 7.1938 | 60.622 | 0.019123 | 146.14 | 1137.9 | 991.76
14601 | 7.1954 | 178.02 | 60.622 | 0.019127 | 146.15 | 1137.9 |  | 14601 | 178.02 | 7.1954 | 60.622 | 0.019127 | 146.15 | 1137.9 | 991.75
14602 | 7.197 | 178.03 | 60.621 | 0.019131 | 146.16 | 1137.9 |  | 14602 | 178.03 | 7.197 | 60.621 | 0.019131 | 146.16 | 1137.9 | 991.74
14603 | 7.1986 | 178.04 | 60.621 | 0.019135 | 146.17 | 1137.9 |  | 14603 | 178.04 | 7.1986 | 60.621 | 0.019135 | 146.17 | 1137.9 | 991.73
14604 | 7.2002 | 178.05 | 60.621 | 0.019139 | 146.18 | 1137.9 |  | 14604 | 178.05 | 7.2002 | 60.621 | 0.019139 | 146.18 | 1137.9 | 991.72
14605 | 7.2018 | 178.06 | 60.621 | 0.019143 | 146.19 | 1137.9 |  | 14605 | 178.06 | 7.2018 | 60.621 | 0.019143 | 146.19 | 1137.9 | 991.71
14606 | 7.2034 | 178.07 | 60.62 | 0.019147 | 146.2 | 1137.9 |  | 14606 | 178.07 | 7.2034 | 60.62 | 0.019147 | 146.2 | 1137.9 | 991.7
14607 | 7.205 | 178.08 | 60.62 | 0.019151 | 146.21 | 1137.9 |  | 14607 | 178.08 | 7.205 | 60.62 | 0.019151 | 146.21 | 1137.9 | 991.69
14608 | 7.2067 | 178.09 | 60.62 | 0.019155 | 146.22 | 1137.9 |  | 14608 | 178.09 | 7.2067 | 60.62 | 0.019155 | 146.22 | 1137.9 | 991.68
14609 | 7.2083 | 178.1 | 60.62 | 0.019159 | 146.23 | 1137.9 |  | 14609 | 178.1 | 7.2083 | 60.62 | 0.019159 | 146.23 | 1137.9 | 991.67
14610 | 7.2099 | 178.11 | 60.62 | 0.019163 | 146.24 | 1137.9 |  | 14610 | 178.11 | 7.2099 | 60.62 | 0.019163 | 146.24 | 1137.9 | 991.66
14611 | 7.2115 | 178.12 | 60.619 | 0.019167 | 146.25 | 1137.9 |  | 14611 | 178.12 | 7.2115 | 60.619 | 0.019167 | 146.25 | 1137.9 | 991.65
14612 | 7.2131 | 178.13 | 60.619 | 0.019171 | 146.26 | 1137.9 |  | 14612 | 178.13 | 7.2131 | 60.619 | 0.019171 | 146.26 | 1137.9 | 991.64
14613 | 7.2147 | 178.14 | 60.619 | 0.019175 | 146.27 | 1137.9 |  | 14613 | 178.14 | 7.2147 | 60.619 | 0.019175 | 146.27 | 1137.9 | 991.63
14614 | 7.2163 | 178.15 | 60.619 | 0.019179 | 146.28 | 1137.9 |  | 14614 | 178.15 | 7.2163 | 60.619 | 0.019179 | 146.28 | 1137.9 | 991.62
14615 | 7.2179 | 178.16 | 60.619 | 0.019183 | 146.29 | 1137.9 |  | 14615 | 178.16 | 7.2179 | 60.619 | 0.019183 | 146.29 | 1137.9 | 991.61
14616 | 7.2195 | 178.17 | 60.618 | 0.019187 | 146.3 | 1137.9 |  | 14616 | 178.17 | 7.2195 | 60.618 | 0.019187 | 146.3 | 1137.9 | 991.6
14617 | 7.2211 | 178.18 | 60.618 | 0.019191 | 146.31 | 1137.9 |  | 14617 | 178.18 | 7.2211 | 60.618 | 0.019191 | 146.31 | 1137.9 | 991.59
14618 | 7.2228 | 178.19 | 60.618 | 0.019195 | 146.32 | 1137.9 |  | 14618 | 178.19 | 7.2228 | 60.618 | 0.019195 | 146.32 | 1137.9 | 991.58
14619 | 7.2244 | 178.2 | 60.618 | 0.019199 | 146.33 | 1137.9 |  | 14619 | 178.2 | 7.2244 | 60.618 | 0.019199 | 146.33 | 1137.9 | 991.57
14620 | 7.226 | 178.21 | 60.617 | 0.019203 | 146.34 | 1137.9 |  | 14620 | 178.21 | 7.226 | 60.617 | 0.019203 | 146.34 | 1137.9 | 991.56
14621 | 7.2276 | 178.22 | 60.617 | 0.019207 | 146.35 | 1137.9 |  | 14621 | 178.22 | 7.2276 | 60.617 | 0.019207 | 146.35 | 1137.9 | 991.55
14622 | 7.2292 | 178.23 | 60.617 | 0.019211 | 146.36 | 1137.9 |  | 14622 | 178.23 | 7.2292 | 60.617 | 0.019211 | 146.36 | 1137.9 | 991.54
14623 | 7.2308 | 178.24 | 60.617 | 0.019215 | 146.37 | 1137.9 |  | 14623 | 178.24 | 7.2308 | 60.617 | 0.019215 | 146.37 | 1137.9 | 991.53
14624 | 7.2324 | 178.25 | 60.617 | 0.019219 | 146.38 | 1138 |  | 14624 | 178.25 | 7.2324 | 60.617 | 0.019219 | 146.38 | 1138 | 991.62
14625 | 7.234 | 178.26 | 60.616 | 0.019223 | 146.39 | 1138 |  | 14625 | 178.26 | 7.234 | 60.616 | 0.019223 | 146.39 | 1138 | 991.61
14626 | 7.2357 | 178.27 | 60.616 | 0.019227 | 146.4 | 1138 |  | 14626 | 178.27 | 7.2357 | 60.616 | 0.019227 | 146.4 | 1138 | 991.6
14627 | 7.2373 | 178.28 | 60.616 | 0.019231 | 146.41 | 1138 |  | 14627 | 178.28 | 7.2373 | 60.616 | 0.019231 | 146.41 | 1138 | 991.59
14628 | 7.2389 | 178.29 | 60.616 | 0.019235 | 146.42 | 1138 |  | 14628 | 178.29 | 7.2389 | 60.616 | 0.019235 | 146.42 | 1138 | 991.58
14629 | 7.2405 | 178.3 | 60.615 | 0.019239 | 146.43 | 1138 |  | 14629 | 178.3 | 7.2405 | 60.615 | 0.019239 | 146.43 | 1138 | 991.57
14630 | 7.2421 | 178.31 | 60.615 | 0.019243 | 146.44 | 1138 |  | 14630 | 178.31 | 7.2421 | 60.615 | 0.019243 | 146.44 | 1138 | 991.56
14631 | 7.2437 | 178.32 | 60.615 | 0.019247 | 146.45 | 1138 |  | 14631 | 178.32 | 7.2437 | 60.615 | 0.019247 | 146.45 | 1138 | 991.55
14632 | 7.2454 | 178.33 | 60.615 | 0.019251 | 146.46 | 1138 |  | 14632 | 178.33 | 7.2454 | 60.615 | 0.019251 | 146.46 | 1138 | 991.54
14633 | 7.247 | 178.34 | 60.615 | 0.019255 | 146.47 | 1138 |  | 14633 | 178.34 | 7.247 | 60.615 | 0.019255 | 146.47 | 1138 | 991.53
14634 | 7.2486 | 178.35 | 60.614 | 0.01926 | 146.48 | 1138 |  | 14634 | 178.35 | 7.2486 | 60.614 | 0.01926 | 146.48 | 1138 | 991.52
14635 | 7.2502 | 178.36 | 60.614 | 0.019264 | 146.49 | 1138 |  | 14635 | 178.36 | 7.2502 | 60.614 | 0.019264 | 146.49 | 1138 | 991.51
14636 | 7.2518 | 178.37 | 60.614 | 0.019268 | 146.5 | 1138 |  | 14636 | 178.37 | 7.2518 | 60.614 | 0.019268 | 146.5 | 1138 | 991.5
14637 | 7.2534 | 178.38 | 60.614 | 0.019272 | 146.51 | 1138 |  | 14637 | 178.38 | 7.2534 | 60.614 | 0.019272 | 146.51 | 1138 | 991.49
14638 | 7.2551 | 178.39 | 60.614 | 0.019276 | 146.52 | 1138 |  | 14638 | 178.39 | 7.2551 | 60.614 | 0.019276 | 146.52 | 1138 | 991.48
14639 | 7.2567 | 178.4 | 60.613 | 0.01928 | 146.53 | 1138 |  | 14639 | 178.4 | 7.2567 | 60.613 | 0.01928 | 146.53 | 1138 | 991.47
14640 | 7.2583 | 178.41 | 60.613 | 0.019284 | 146.54 | 1138 |  | 14640 | 178.41 | 7.2583 | 60.613 | 0.019284 | 146.54 | 1138 | 991.46
14641 | 7.2599 | 178.42 | 60.613 | 0.019288 | 146.55 | 1138 |  | 14641 | 178.42 | 7.2599 | 60.613 | 0.019288 | 146.55 | 1138 | 991.45
14642 | 7.2615 | 178.43 | 60.613 | 0.019292 | 146.56 | 1138 |  | 14642 | 178.43 | 7.2615 | 60.613 | 0.019292 | 146.56 | 1138 | 991.44
14643 | 7.2632 | 178.44 | 60.612 | 0.019296 | 146.57 | 1138 |  | 14643 | 178.44 | 7.2632 | 60.612 | 0.019296 | 146.57 | 1138 | 991.43
14644 | 7.2648 | 178.45 | 60.612 | 0.0193 | 146.58 | 1138 |  | 14644 | 178.45 | 7.2648 | 60.612 | 0.0193 | 146.58 | 1138 | 991.42
14645 | 7.2664 | 178.46 | 60.612 | 0.019304 | 146.59 | 1138 |  | 14645 | 178.46 | 7.2664 | 60.612 | 0.019304 | 146.59 | 1138 | 991.41
14646 | 7.268 | 178.47 | 60.612 | 0.019308 | 146.6 | 1138 |  | 14646 | 178.47 | 7.268 | 60.612 | 0.019308 | 146.6 | 1138 | 991.4
14647 | 7.2696 | 178.48 | 60.612 | 0.019312 | 146.61 | 1138 |  | 14647 | 178.48 | 7.2696 | 60.612 | 0.019312 | 146.61 | 1138 | 991.39
14648 | 7.2713 | 178.49 | 60.611 | 0.019316 | 146.62 | 1138 |  | 14648 | 178.49 | 7.2713 | 60.611 | 0.019316 | 146.62 | 1138 | 991.38
14649 | 7.2729 | 178.5 | 60.611 | 0.01932 | 146.63 | 1138.1 |  | 14649 | 178.5 | 7.2729 | 60.611 | 0.01932 | 146.63 | 1138.1 | 991.47
14650 | 7.2745 | 178.51 | 60.611 | 0.019324 | 146.64 | 1138.1 |  | 14650 | 178.51 | 7.2745 | 60.611 | 0.019324 | 146.64 | 1138.1 | 991.46
14651 | 7.2761 | 178.52 | 60.611 | 0.019328 | 146.65 | 1138.1 |  | 14651 | 178.52 | 7.2761 | 60.611 | 0.019328 | 146.65 | 1138.1 | 991.45
14652 | 7.2777 | 178.53 | 60.61 | 0.019332 | 146.66 | 1138.1 |  | 14652 | 178.53 | 7.2777 | 60.61 | 0.019332 | 146.66 | 1138.1 | 991.44
14653 | 7.2794 | 178.54 | 60.61 | 0.019336 | 146.67 | 1138.1 |  | 14653 | 178.54 | 7.2794 | 60.61 | 0.019336 | 146.67 | 1138.1 | 991.43
14654 | 7.281 | 178.55 | 60.61 | 0.01934 | 146.68 | 1138.1 |  | 14654 | 178.55 | 7.281 | 60.61 | 0.01934 | 146.68 | 1138.1 | 991.42
14655 | 7.2826 | 178.56 | 60.61 | 0.019344 | 146.69 | 1138.1 |  | 14655 | 178.56 | 7.2826 | 60.61 | 0.019344 | 146.69 | 1138.1 | 991.41
14656 | 7.2842 | 178.57 | 60.61 | 0.019348 | 146.7 | 1138.1 |  | 14656 | 178.57 | 7.2842 | 60.61 | 0.019348 | 146.7 | 1138.1 | 991.4
14657 | 7.2859 | 178.58 | 60.609 | 0.019352 | 146.72 | 1138.1 |  | 14657 | 178.58 | 7.2859 | 60.609 | 0.019352 | 146.72 | 1138.1 | 991.38
14658 | 7.2875 | 178.59 | 60.609 | 0.019356 | 146.73 | 1138.1 |  | 14658 | 178.59 | 7.2875 | 60.609 | 0.019356 | 146.73 | 1138.1 | 991.37
14659 | 7.2891 | 178.6 | 60.609 | 0.01936 | 146.74 | 1138.1 |  | 14659 | 178.6 | 7.2891 | 60.609 | 0.01936 | 146.74 | 1138.1 | 991.36
14660 | 7.2907 | 178.61 | 60.609 | 0.019364 | 146.75 | 1138.1 |  | 14660 | 178.61 | 7.2907 | 60.609 | 0.019364 | 146.75 | 1138.1 | 991.35
14661 | 7.2924 | 178.62 | 60.608 | 0.019368 | 146.76 | 1138.1 |  | 14661 | 178.62 | 7.2924 | 60.608 | 0.019368 | 146.76 | 1138.1 | 991.34
14662 | 7.294 | 178.63 | 60.608 | 0.019372 | 146.77 | 1138.1 |  | 14662 | 178.63 | 7.294 | 60.608 | 0.019372 | 146.77 | 1138.1 | 991.33
14663 | 7.2956 | 178.64 | 60.608 | 0.019376 | 146.78 | 1138.1 |  | 14663 | 178.64 | 7.2956 | 60.608 | 0.019376 | 146.78 | 1138.1 | 991.32
14664 | 7.2972 | 178.65 | 60.608 | 0.01938 | 146.79 | 1138.1 |  | 14664 | 178.65 | 7.2972 | 60.608 | 0.01938 | 146.79 | 1138.1 | 991.31
14665 | 7.2989 | 178.66 | 60.608 | 0.019385 | 146.8 | 1138.1 |  | 14665 | 178.66 | 7.2989 | 60.608 | 0.019385 | 146.8 | 1138.1 | 991.3
14666 | 7.3005 | 178.67 | 60.607 | 0.019389 | 146.81 | 1138.1 |  | 14666 | 178.67 | 7.3005 | 60.607 | 0.019389 | 146.81 | 1138.1 | 991.29
14667 | 7.3021 | 178.68 | 60.607 | 0.019393 | 146.82 | 1138.1 |  | 14667 | 178.68 | 7.3021 | 60.607 | 0.019393 | 146.82 | 1138.1 | 991.28
14668 | 7.3037 | 178.69 | 60.607 | 0.019397 | 146.83 | 1138.1 |  | 14668 | 178.69 | 7.3037 | 60.607 | 0.019397 | 146.83 | 1138.1 | 991.27
14669 | 7.3054 | 178.7 | 60.607 | 0.019401 | 146.84 | 1138.1 |  | 14669 | 178.7 | 7.3054 | 60.607 | 0.019401 | 146.84 | 1138.1 | 991.26
14670 | 7.307 | 178.71 | 60.607 | 0.019405 | 146.85 | 1138.1 |  | 14670 | 178.71 | 7.307 | 60.607 | 0.019405 | 146.85 | 1138.1 | 991.25
14671 | 7.3086 | 178.72 | 60.606 | 0.019409 | 146.86 | 1138.1 |  | 14671 | 178.72 | 7.3086 | 60.606 | 0.019409 | 146.86 | 1138.1 | 991.24
14672 | 7.3102 | 178.73 | 60.606 | 0.019413 | 146.87 | 1138.1 |  | 14672 | 178.73 | 7.3102 | 60.606 | 0.019413 | 146.87 | 1138.1 | 991.23
14673 | 7.3119 | 178.74 | 60.606 | 0.019417 | 146.88 | 1138.1 |  | 14673 | 178.74 | 7.3119 | 60.606 | 0.019417 | 146.88 | 1138.1 | 991.22
14674 | 7.3135 | 178.75 | 60.606 | 0.019421 | 146.89 | 1138.2 |  | 14674 | 178.75 | 7.3135 | 60.606 | 0.019421 | 146.89 | 1138.2 | 991.31
14675 | 7.3151 | 178.76 | 60.605 | 0.019425 | 146.9 | 1138.2 |  | 14675 | 178.76 | 7.3151 | 60.605 | 0.019425 | 146.9 | 1138.2 | 991.3
14676 | 7.3168 | 178.77 | 60.605 | 0.019429 | 146.91 | 1138.2 |  | 14676 | 178.77 | 7.3168 | 60.605 | 0.019429 | 146.91 | 1138.2 | 991.29
14677 | 7.3184 | 178.78 | 60.605 | 0.019433 | 146.92 | 1138.2 |  | 14677 | 178.78 | 7.3184 | 60.605 | 0.019433 | 146.92 | 1138.2 | 991.28
14678 | 7.32 | 178.79 | 60.605 | 0.019437 | 146.93 | 1138.2 |  | 14678 | 178.79 | 7.32 | 60.605 | 0.019437 | 146.93 | 1138.2 | 991.27
14679 | 7.3217 | 178.8 | 60.605 | 0.019441 | 146.94 | 1138.2 |  | 14679 | 178.8 | 7.3217 | 60.605 | 0.019441 | 146.94 | 1138.2 | 991.26
14680 | 7.3233 | 178.81 | 60.604 | 0.019445 | 146.95 | 1138.2 |  | 14680 | 178.81 | 7.3233 | 60.604 | 0.019445 | 146.95 | 1138.2 | 991.25
14681 | 7.3249 | 178.82 | 60.604 | 0.019449 | 146.96 | 1138.2 |  | 14681 | 178.82 | 7.3249 | 60.604 | 0.019449 | 146.96 | 1138.2 | 991.24
14682 | 7.3265 | 178.83 | 60.604 | 0.019453 | 146.97 | 1138.2 |  | 14682 | 178.83 | 7.3265 | 60.604 | 0.019453 | 146.97 | 1138.2 | 991.23
14683 | 7.3282 | 178.84 | 60.604 | 0.019457 | 146.98 | 1138.2 |  | 14683 | 178.84 | 7.3282 | 60.604 | 0.019457 | 146.98 | 1138.2 | 991.22
14684 | 7.3298 | 178.85 | 60.603 | 0.019461 | 146.99 | 1138.2 |  | 14684 | 178.85 | 7.3298 | 60.603 | 0.019461 | 146.99 | 1138.2 | 991.21
14685 | 7.3314 | 178.86 | 60.603 | 0.019466 | 147 | 1138.2 |  | 14685 | 178.86 | 7.3314 | 60.603 | 0.019466 | 147 | 1138.2 | 991.2
14686 | 7.3331 | 178.87 | 60.603 | 0.01947 | 147.01 | 1138.2 |  | 14686 | 178.87 | 7.3331 | 60.603 | 0.01947 | 147.01 | 1138.2 | 991.19
14687 | 7.3347 | 178.88 | 60.603 | 0.019474 | 147.02 | 1138.2 |  | 14687 | 178.88 | 7.3347 | 60.603 | 0.019474 | 147.02 | 1138.2 | 991.18
14688 | 7.3363 | 178.89 | 60.603 | 0.019478 | 147.03 | 1138.2 |  | 14688 | 178.89 | 7.3363 | 60.603 | 0.019478 | 147.03 | 1138.2 | 991.17
14689 | 7.338 | 178.9 | 60.602 | 0.019482 | 147.04 | 1138.2 |  | 14689 | 178.9 | 7.338 | 60.602 | 0.019482 | 147.04 | 1138.2 | 991.16
14690 | 7.3396 | 178.91 | 60.602 | 0.019486 | 147.05 | 1138.2 |  | 14690 | 178.91 | 7.3396 | 60.602 | 0.019486 | 147.05 | 1138.2 | 991.15
14691 | 7.3412 | 178.92 | 60.602 | 0.01949 | 147.06 | 1138.2 |  | 14691 | 178.92 | 7.3412 | 60.602 | 0.01949 | 147.06 | 1138.2 | 991.14
14692 | 7.3429 | 178.93 | 60.602 | 0.019494 | 147.07 | 1138.2 |  | 14692 | 178.93 | 7.3429 | 60.602 | 0.019494 | 147.07 | 1138.2 | 991.13
14693 | 7.3445 | 178.94 | 60.601 | 0.019498 | 147.08 | 1138.2 |  | 14693 | 178.94 | 7.3445 | 60.601 | 0.019498 | 147.08 | 1138.2 | 991.12
14694 | 7.3461 | 178.95 | 60.601 | 0.019502 | 147.09 | 1138.2 |  | 14694 | 178.95 | 7.3461 | 60.601 | 0.019502 | 147.09 | 1138.2 | 991.11
14695 | 7.3478 | 178.96 | 60.601 | 0.019506 | 147.1 | 1138.2 |  | 14695 | 178.96 | 7.3478 | 60.601 | 0.019506 | 147.1 | 1138.2 | 991.1
14696 | 7.3494 | 178.97 | 60.601 | 0.01951 | 147.11 | 1138.2 |  | 14696 | 178.97 | 7.3494 | 60.601 | 0.01951 | 147.11 | 1138.2 | 991.09
14697 | 7.351 | 178.98 | 60.601 | 0.019514 | 147.12 | 1138.2 |  | 14697 | 178.98 | 7.351 | 60.601 | 0.019514 | 147.12 | 1138.2 | 991.08
14698 | 7.3527 | 178.99 | 60.6 | 0.019518 | 147.13 | 1138.2 |  | 14698 | 178.99 | 7.3527 | 60.6 | 0.019518 | 147.13 | 1138.2 | 991.07
14699 | 7.3543 | 179 | 60.6 | 0.019522 | 147.14 | 1138.2 |  | 14699 | 179 | 7.3543 | 60.6 | 0.019522 | 147.14 | 1138.2 | 991.06
14700 | 7.356 | 179.01 | 60.6 | 0.019526 | 147.15 | 1138.3 |  | 14700 | 179.01 | 7.356 | 60.6 | 0.019526 | 147.15 | 1138.3 | 991.15
14701 | 7.3576 | 179.02 | 60.6 | 0.019531 | 147.16 | 1138.3 |  | 14701 | 179.02 | 7.3576 | 60.6 | 0.019531 | 147.16 | 1138.3 | 991.14
14702 | 7.3592 | 179.03 | 60.6 | 0.019535 | 147.17 | 1138.3 |  | 14702 | 179.03 | 7.3592 | 60.6 | 0.019535 | 147.17 | 1138.3 | 991.13
14703 | 7.3609 | 179.04 | 60.599 | 0.019539 | 147.18 | 1138.3 |  | 14703 | 179.04 | 7.3609 | 60.599 | 0.019539 | 147.18 | 1138.3 | 991.12
14704 | 7.3625 | 179.05 | 60.599 | 0.019543 | 147.19 | 1138.3 |  | 14704 | 179.05 | 7.3625 | 60.599 | 0.019543 | 147.19 | 1138.3 | 991.11
14705 | 7.3641 | 179.06 | 60.599 | 0.019547 | 147.2 | 1138.3 |  | 14705 | 179.06 | 7.3641 | 60.599 | 0.019547 | 147.2 | 1138.3 | 991.1
14706 | 7.3658 | 179.07 | 60.599 | 0.019551 | 147.21 | 1138.3 |  | 14706 | 179.07 | 7.3658 | 60.599 | 0.019551 | 147.21 | 1138.3 | 991.09
14707 | 7.3674 | 179.08 | 60.598 | 0.019555 | 147.22 | 1138.3 |  | 14707 | 179.08 | 7.3674 | 60.598 | 0.019555 | 147.22 | 1138.3 | 991.08
14708 | 7.3691 | 179.09 | 60.598 | 0.019559 | 147.23 | 1138.3 |  | 14708 | 179.09 | 7.3691 | 60.598 | 0.019559 | 147.23 | 1138.3 | 991.07
14709 | 7.3707 | 179.1 | 60.598 | 0.019563 | 147.24 | 1138.3 |  | 14709 | 179.1 | 7.3707 | 60.598 | 0.019563 | 147.24 | 1138.3 | 991.06
14710 | 7.3723 | 179.11 | 60.598 | 0.019567 | 147.25 | 1138.3 |  | 14710 | 179.11 | 7.3723 | 60.598 | 0.019567 | 147.25 | 1138.3 | 991.05
14711 | 7.374 | 179.12 | 60.598 | 0.019571 | 147.26 | 1138.3 |  | 14711 | 179.12 | 7.374 | 60.598 | 0.019571 | 147.26 | 1138.3 | 991.04
14712 | 7.3756 | 179.13 | 60.597 | 0.019575 | 147.27 | 1138.3 |  | 14712 | 179.13 | 7.3756 | 60.597 | 0.019575 | 147.27 | 1138.3 | 991.03
14713 | 7.3773 | 179.14 | 60.597 | 0.019579 | 147.28 | 1138.3 |  | 14713 | 179.14 | 7.3773 | 60.597 | 0.019579 | 147.28 | 1138.3 | 991.02
14714 | 7.3789 | 179.15 | 60.597 | 0.019583 | 147.29 | 1138.3 |  | 14714 | 179.15 | 7.3789 | 60.597 | 0.019583 | 147.29 | 1138.3 | 991.01
14715 | 7.3805 | 179.16 | 60.597 | 0.019588 | 147.3 | 1138.3 |  | 14715 | 179.16 | 7.3805 | 60.597 | 0.019588 | 147.3 | 1138.3 | 991
14716 | 7.3822 | 179.17 | 60.596 | 0.019592 | 147.31 | 1138.3 |  | 14716 | 179.17 | 7.3822 | 60.596 | 0.019592 | 147.31 | 1138.3 | 990.99
14717 | 7.3838 | 179.18 | 60.596 | 0.019596 | 147.32 | 1138.3 |  | 14717 | 179.18 | 7.3838 | 60.596 | 0.019596 | 147.32 | 1138.3 | 990.98
14718 | 7.3855 | 179.19 | 60.596 | 0.0196 | 147.33 | 1138.3 |  | 14718 | 179.19 | 7.3855 | 60.596 | 0.0196 | 147.33 | 1138.3 | 990.97
14719 | 7.3871 | 179.2 | 60.596 | 0.019604 | 147.34 | 1138.3 |  | 14719 | 179.2 | 7.3871 | 60.596 | 0.019604 | 147.34 | 1138.3 | 990.96
14720 | 7.3888 | 179.21 | 60.596 | 0.019608 | 147.35 | 1138.3 |  | 14720 | 179.21 | 7.3888 | 60.596 | 0.019608 | 147.35 | 1138.3 | 990.95
14721 | 7.3904 | 179.22 | 60.595 | 0.019612 | 147.36 | 1138.3 |  | 14721 | 179.22 | 7.3904 | 60.595 | 0.019612 | 147.36 | 1138.3 | 990.94
14722 | 7.392 | 179.23 | 60.595 | 0.019616 | 147.37 | 1138.3 |  | 14722 | 179.23 | 7.392 | 60.595 | 0.019616 | 147.37 | 1138.3 | 990.93
14723 | 7.3937 | 179.24 | 60.595 | 0.01962 | 147.38 | 1138.3 |  | 14723 | 179.24 | 7.3937 | 60.595 | 0.01962 | 147.38 | 1138.3 | 990.92
14724 | 7.3953 | 179.25 | 60.595 | 0.019624 | 147.39 | 1138.3 |  | 14724 | 179.25 | 7.3953 | 60.595 | 0.019624 | 147.39 | 1138.3 | 990.91
14725 | 7.397 | 179.26 | 60.594 | 0.019628 | 147.4 | 1138.4 |  | 14725 | 179.26 | 7.397 | 60.594 | 0.019628 | 147.4 | 1138.4 | 991
14726 | 7.3986 | 179.27 | 60.594 | 0.019632 | 147.41 | 1138.4 |  | 14726 | 179.27 | 7.3986 | 60.594 | 0.019632 | 147.41 | 1138.4 | 990.99
14727 | 7.4003 | 179.28 | 60.594 | 0.019637 | 147.42 | 1138.4 |  | 14727 | 179.28 | 7.4003 | 60.594 | 0.019637 | 147.42 | 1138.4 | 990.98
14728 | 7.4019 | 179.29 | 60.594 | 0.019641 | 147.43 | 1138.4 |  | 14728 | 179.29 | 7.4019 | 60.594 | 0.019641 | 147.43 | 1138.4 | 990.97
14729 | 7.4036 | 179.3 | 60.594 | 0.019645 | 147.44 | 1138.4 |  | 14729 | 179.3 | 7.4036 | 60.594 | 0.019645 | 147.44 | 1138.4 | 990.96
14730 | 7.4052 | 179.31 | 60.593 | 0.019649 | 147.45 | 1138.4 |  | 14730 | 179.31 | 7.4052 | 60.593 | 0.019649 | 147.45 | 1138.4 | 990.95
14731 | 7.4068 | 179.32 | 60.593 | 0.019653 | 147.46 | 1138.4 |  | 14731 | 179.32 | 7.4068 | 60.593 | 0.019653 | 147.46 | 1138.4 | 990.94
14732 | 7.4085 | 179.33 | 60.593 | 0.019657 | 147.47 | 1138.4 |  | 14732 | 179.33 | 7.4085 | 60.593 | 0.019657 | 147.47 | 1138.4 | 990.93
14733 | 7.4101 | 179.34 | 60.593 | 0.019661 | 147.48 | 1138.4 |  | 14733 | 179.34 | 7.4101 | 60.593 | 0.019661 | 147.48 | 1138.4 | 990.92
14734 | 7.4118 | 179.35 | 60.593 | 0.019665 | 147.49 | 1138.4 |  | 14734 | 179.35 | 7.4118 | 60.593 | 0.019665 | 147.49 | 1138.4 | 990.91
14735 | 7.4134 | 179.36 | 60.592 | 0.019669 | 147.5 | 1138.4 |  | 14735 | 179.36 | 7.4134 | 60.592 | 0.019669 | 147.5 | 1138.4 | 990.9
14736 | 7.4151 | 179.37 | 60.592 | 0.019673 | 147.51 | 1138.4 |  | 14736 | 179.37 | 7.4151 | 60.592 | 0.019673 | 147.51 | 1138.4 | 990.89
14737 | 7.4167 | 179.38 | 60.592 | 0.019677 | 147.52 | 1138.4 |  | 14737 | 179.38 | 7.4167 | 60.592 | 0.019677 | 147.52 | 1138.4 | 990.88
14738 | 7.4184 | 179.39 | 60.592 | 0.019682 | 147.53 | 1138.4 |  | 14738 | 179.39 | 7.4184 | 60.592 | 0.019682 | 147.53 | 1138.4 | 990.87
14739 | 7.42 | 179.4 | 60.591 | 0.019686 | 147.54 | 1138.4 |  | 14739 | 179.4 | 7.42 | 60.591 | 0.019686 | 147.54 | 1138.4 | 990.86
14740 | 7.4217 | 179.41 | 60.591 | 0.01969 | 147.55 | 1138.4 |  | 14740 | 179.41 | 7.4217 | 60.591 | 0.01969 | 147.55 | 1138.4 | 990.85
14741 | 7.4233 | 179.42 | 60.591 | 0.019694 | 147.56 | 1138.4 |  | 14741 | 179.42 | 7.4233 | 60.591 | 0.019694 | 147.56 | 1138.4 | 990.84
14742 | 7.425 | 179.43 | 60.591 | 0.019698 | 147.57 | 1138.4 |  | 14742 | 179.43 | 7.425 | 60.591 | 0.019698 | 147.57 | 1138.4 | 990.83
14743 | 7.4266 | 179.44 | 60.591 | 0.019702 | 147.58 | 1138.4 |  | 14743 | 179.44 | 7.4266 | 60.591 | 0.019702 | 147.58 | 1138.4 | 990.82
14744 | 7.4283 | 179.45 | 60.59 | 0.019706 | 147.59 | 1138.4 |  | 14744 | 179.45 | 7.4283 | 60.59 | 0.019706 | 147.59 | 1138.4 | 990.81
14745 | 7.4299 | 179.46 | 60.59 | 0.01971 | 147.6 | 1138.4 |  | 14745 | 179.46 | 7.4299 | 60.59 | 0.01971 | 147.6 | 1138.4 | 990.8
14746 | 7.4316 | 179.47 | 60.59 | 0.019714 | 147.61 | 1138.4 |  | 14746 | 179.47 | 7.4316 | 60.59 | 0.019714 | 147.61 | 1138.4 | 990.79
14747 | 7.4332 | 179.48 | 60.59 | 0.019718 | 147.62 | 1138.4 |  | 14747 | 179.48 | 7.4332 | 60.59 | 0.019718 | 147.62 | 1138.4 | 990.78
14748 | 7.4349 | 179.49 | 60.589 | 0.019723 | 147.63 | 1138.4 |  | 14748 | 179.49 | 7.4349 | 60.589 | 0.019723 | 147.63 | 1138.4 | 990.77
14749 | 7.4365 | 179.5 | 60.589 | 0.019727 | 147.64 | 1138.4 |  | 14749 | 179.5 | 7.4365 | 60.589 | 0.019727 | 147.64 | 1138.4 | 990.76
14750 | 7.4382 | 179.51 | 60.589 | 0.019731 | 147.65 | 1138.5 |  | 14750 | 179.51 | 7.4382 | 60.589 | 0.019731 | 147.65 | 1138.5 | 990.85
14751 | 7.4398 | 179.52 | 60.589 | 0.019735 | 147.66 | 1138.5 |  | 14751 | 179.52 | 7.4398 | 60.589 | 0.019735 | 147.66 | 1138.5 | 990.84
14752 | 7.4415 | 179.53 | 60.589 | 0.019739 | 147.67 | 1138.5 |  | 14752 | 179.53 | 7.4415 | 60.589 | 0.019739 | 147.67 | 1138.5 | 990.83
14753 | 7.4431 | 179.54 | 60.588 | 0.019743 | 147.68 | 1138.5 |  | 14753 | 179.54 | 7.4431 | 60.588 | 0.019743 | 147.68 | 1138.5 | 990.82
14754 | 7.4448 | 179.55 | 60.588 | 0.019747 | 147.69 | 1138.5 |  | 14754 | 179.55 | 7.4448 | 60.588 | 0.019747 | 147.69 | 1138.5 | 990.81
14755 | 7.4465 | 179.56 | 60.588 | 0.019751 | 147.7 | 1138.5 |  | 14755 | 179.56 | 7.4465 | 60.588 | 0.019751 | 147.7 | 1138.5 | 990.8
14756 | 7.4481 | 179.57 | 60.588 | 0.019755 | 147.71 | 1138.5 |  | 14756 | 179.57 | 7.4481 | 60.588 | 0.019755 | 147.71 | 1138.5 | 990.79
14757 | 7.4498 | 179.58 | 60.587 | 0.019759 | 147.72 | 1138.5 |  | 14757 | 179.58 | 7.4498 | 60.587 | 0.019759 | 147.72 | 1138.5 | 990.78
14758 | 7.4514 | 179.59 | 60.587 | 0.019764 | 147.73 | 1138.5 |  | 14758 | 179.59 | 7.4514 | 60.587 | 0.019764 | 147.73 | 1138.5 | 990.77
14759 | 7.4531 | 179.6 | 60.587 | 0.019768 | 147.74 | 1138.5 |  | 14759 | 179.6 | 7.4531 | 60.587 | 0.019768 | 147.74 | 1138.5 | 990.76
14760 | 7.4547 | 179.61 | 60.587 | 0.019772 | 147.75 | 1138.5 |  | 14760 | 179.61 | 7.4547 | 60.587 | 0.019772 | 147.75 | 1138.5 | 990.75
14761 | 7.4564 | 179.62 | 60.587 | 0.019776 | 147.76 | 1138.5 |  | 14761 | 179.62 | 7.4564 | 60.587 | 0.019776 | 147.76 | 1138.5 | 990.74
14762 | 7.458 | 179.63 | 60.586 | 0.01978 | 147.77 | 1138.5 |  | 14762 | 179.63 | 7.458 | 60.586 | 0.01978 | 147.77 | 1138.5 | 990.73
14763 | 7.4597 | 179.64 | 60.586 | 0.019784 | 147.78 | 1138.5 |  | 14763 | 179.64 | 7.4597 | 60.586 | 0.019784 | 147.78 | 1138.5 | 990.72
14764 | 7.4613 | 179.65 | 60.586 | 0.019788 | 147.79 | 1138.5 |  | 14764 | 179.65 | 7.4613 | 60.586 | 0.019788 | 147.79 | 1138.5 | 990.71
14765 | 7.463 | 179.66 | 60.586 | 0.019792 | 147.8 | 1138.5 |  | 14765 | 179.66 | 7.463 | 60.586 | 0.019792 | 147.8 | 1138.5 | 990.7
14766 | 7.4647 | 179.67 | 60.586 | 0.019796 | 147.81 | 1138.5 |  | 14766 | 179.67 | 7.4647 | 60.586 | 0.019796 | 147.81 | 1138.5 | 990.69
14767 | 7.4663 | 179.68 | 60.585 | 0.019801 | 147.82 | 1138.5 |  | 14767 | 179.68 | 7.4663 | 60.585 | 0.019801 | 147.82 | 1138.5 | 990.68
14768 | 7.468 | 179.69 | 60.585 | 0.019805 | 147.83 | 1138.5 |  | 14768 | 179.69 | 7.468 | 60.585 | 0.019805 | 147.83 | 1138.5 | 990.67
14769 | 7.4696 | 179.7 | 60.585 | 0.019809 | 147.84 | 1138.5 |  | 14769 | 179.7 | 7.4696 | 60.585 | 0.019809 | 147.84 | 1138.5 | 990.66
14770 | 7.4713 | 179.71 | 60.585 | 0.019813 | 147.85 | 1138.5 |  | 14770 | 179.71 | 7.4713 | 60.585 | 0.019813 | 147.85 | 1138.5 | 990.65
14771 | 7.473 | 179.72 | 60.584 | 0.019817 | 147.86 | 1138.5 |  | 14771 | 179.72 | 7.473 | 60.584 | 0.019817 | 147.86 | 1138.5 | 990.64
14772 | 7.4746 | 179.73 | 60.584 | 0.019821 | 147.87 | 1138.5 |  | 14772 | 179.73 | 7.4746 | 60.584 | 0.019821 | 147.87 | 1138.5 | 990.63
14773 | 7.4763 | 179.74 | 60.584 | 0.019825 | 147.88 | 1138.5 |  | 14773 | 179.74 | 7.4763 | 60.584 | 0.019825 | 147.88 | 1138.5 | 990.62
14774 | 7.4779 | 179.75 | 60.584 | 0.019829 | 147.89 | 1138.5 |  | 14774 | 179.75 | 7.4779 | 60.584 | 0.019829 | 147.89 | 1138.5 | 990.61
14775 | 7.4796 | 179.76 | 60.584 | 0.019834 | 147.9 | 1138.6 |  | 14775 | 179.76 | 7.4796 | 60.584 | 0.019834 | 147.9 | 1138.6 | 990.7
14776 | 7.4812 | 179.77 | 60.583 | 0.019838 | 147.91 | 1138.6 |  | 14776 | 179.77 | 7.4812 | 60.583 | 0.019838 | 147.91 | 1138.6 | 990.69
14777 | 7.4829 | 179.78 | 60.583 | 0.019842 | 147.92 | 1138.6 |  | 14777 | 179.78 | 7.4829 | 60.583 | 0.019842 | 147.92 | 1138.6 | 990.68
14778 | 7.4846 | 179.79 | 60.583 | 0.019846 | 147.93 | 1138.6 |  | 14778 | 179.79 | 7.4846 | 60.583 | 0.019846 | 147.93 | 1138.6 | 990.67
14779 | 7.4862 | 179.8 | 60.583 | 0.01985 | 147.94 | 1138.6 |  | 14779 | 179.8 | 7.4862 | 60.583 | 0.01985 | 147.94 | 1138.6 | 990.66
14780 | 7.4879 | 179.81 | 60.582 | 0.019854 | 147.95 | 1138.6 |  | 14780 | 179.81 | 7.4879 | 60.582 | 0.019854 | 147.95 | 1138.6 | 990.65
14781 | 7.4896 | 179.82 | 60.582 | 0.019858 | 147.96 | 1138.6 |  | 14781 | 179.82 | 7.4896 | 60.582 | 0.019858 | 147.96 | 1138.6 | 990.64
14782 | 7.4912 | 179.83 | 60.582 | 0.019862 | 147.97 | 1138.6 |  | 14782 | 179.83 | 7.4912 | 60.582 | 0.019862 | 147.97 | 1138.6 | 990.63
14783 | 7.4929 | 179.84 | 60.582 | 0.019867 | 147.98 | 1138.6 |  | 14783 | 179.84 | 7.4929 | 60.582 | 0.019867 | 147.98 | 1138.6 | 990.62
14784 | 7.4945 | 179.85 | 60.582 | 0.019871 | 147.99 | 1138.6 |  | 14784 | 179.85 | 7.4945 | 60.582 | 0.019871 | 147.99 | 1138.6 | 990.61
14785 | 7.4962 | 179.86 | 60.581 | 0.019875 | 148 | 1138.6 |  | 14785 | 179.86 | 7.4962 | 60.581 | 0.019875 | 148 | 1138.6 | 990.6
14786 | 7.4979 | 179.87 | 60.581 | 0.019879 | 148.01 | 1138.6 |  | 14786 | 179.87 | 7.4979 | 60.581 | 0.019879 | 148.01 | 1138.6 | 990.59
14787 | 7.4995 | 179.88 | 60.581 | 0.019883 | 148.02 | 1138.6 |  | 14787 | 179.88 | 7.4995 | 60.581 | 0.019883 | 148.02 | 1138.6 | 990.58
14788 | 7.5012 | 179.89 | 60.581 | 0.019887 | 148.03 | 1138.6 |  | 14788 | 179.89 | 7.5012 | 60.581 | 0.019887 | 148.03 | 1138.6 | 990.57
14789 | 7.5029 | 179.9 | 60.58 | 0.019891 | 148.04 | 1138.6 |  | 14789 | 179.9 | 7.5029 | 60.58 | 0.019891 | 148.04 | 1138.6 | 990.56
14790 | 7.5045 | 179.91 | 60.58 | 0.019895 | 148.05 | 1138.6 |  | 14790 | 179.91 | 7.5045 | 60.58 | 0.019895 | 148.05 | 1138.6 | 990.55
14791 | 7.5062 | 179.92 | 60.58 | 0.0199 | 148.06 | 1138.6 |  | 14791 | 179.92 | 7.5062 | 60.58 | 0.0199 | 148.06 | 1138.6 | 990.54
14792 | 7.5079 | 179.93 | 60.58 | 0.019904 | 148.07 | 1138.6 |  | 14792 | 179.93 | 7.5079 | 60.58 | 0.019904 | 148.07 | 1138.6 | 990.53
14793 | 7.5095 | 179.94 | 60.58 | 0.019908 | 148.08 | 1138.6 |  | 14793 | 179.94 | 7.5095 | 60.58 | 0.019908 | 148.08 | 1138.6 | 990.52
14794 | 7.5112 | 179.95 | 60.579 | 0.019912 | 148.09 | 1138.6 |  | 14794 | 179.95 | 7.5112 | 60.579 | 0.019912 | 148.09 | 1138.6 | 990.51
14795 | 7.5128 | 179.96 | 60.579 | 0.019916 | 148.1 | 1138.6 |  | 14795 | 179.96 | 7.5128 | 60.579 | 0.019916 | 148.1 | 1138.6 | 990.5
14796 | 7.5145 | 179.97 | 60.579 | 0.01992 | 148.11 | 1138.6 |  | 14796 | 179.97 | 7.5145 | 60.579 | 0.01992 | 148.11 | 1138.6 | 990.49
14797 | 7.5162 | 179.98 | 60.579 | 0.019924 | 148.12 | 1138.6 |  | 14797 | 179.98 | 7.5162 | 60.579 | 0.019924 | 148.12 | 1138.6 | 990.48
14798 | 7.5178 | 179.99 | 60.578 | 0.019928 | 148.13 | 1138.6 |  | 14798 | 179.99 | 7.5178 | 60.578 | 0.019928 | 148.13 | 1138.6 | 990.47
14799 | 7.5195 | 180 | 60.578 | 0.019933 | 148.14 | 1138.6 |  | 14799 | 180 | 7.5195 | 60.578 | 0.019933 | 148.14 | 1138.6 | 990.46
14800 | 7.5212 | 180.01 | 60.578 | 0.019937 | 148.15 | 1138.7 |  | 14800 | 180.01 | 7.5212 | 60.578 | 0.019937 | 148.15 | 1138.7 | 990.55
14801 | 7.5229 | 180.02 | 60.578 | 0.019941 | 148.16 | 1138.7 |  | 14801 | 180.02 | 7.5229 | 60.578 | 0.019941 | 148.16 | 1138.7 | 990.54
14802 | 7.5245 | 180.03 | 60.578 | 0.019945 | 148.17 | 1138.7 |  | 14802 | 180.03 | 7.5245 | 60.578 | 0.019945 | 148.17 | 1138.7 | 990.53
14803 | 7.5262 | 180.04 | 60.577 | 0.019949 | 148.18 | 1138.7 |  | 14803 | 180.04 | 7.5262 | 60.577 | 0.019949 | 148.18 | 1138.7 | 990.52
14804 | 7.5279 | 180.05 | 60.577 | 0.019953 | 148.19 | 1138.7 |  | 14804 | 180.05 | 7.5279 | 60.577 | 0.019953 | 148.19 | 1138.7 | 990.51
14805 | 7.5295 | 180.06 | 60.577 | 0.019957 | 148.2 | 1138.7 |  | 14805 | 180.06 | 7.5295 | 60.577 | 0.019957 | 148.2 | 1138.7 | 990.5
14806 | 7.5312 | 180.07 | 60.577 | 0.019962 | 148.21 | 1138.7 |  | 14806 | 180.07 | 7.5312 | 60.577 | 0.019962 | 148.21 | 1138.7 | 990.49
14807 | 7.5329 | 180.08 | 60.577 | 0.019966 | 148.22 | 1138.7 |  | 14807 | 180.08 | 7.5329 | 60.577 | 0.019966 | 148.22 | 1138.7 | 990.48
14808 | 7.5345 | 180.09 | 60.576 | 0.01997 | 148.23 | 1138.7 |  | 14808 | 180.09 | 7.5345 | 60.576 | 0.01997 | 148.23 | 1138.7 | 990.47
14809 | 7.5362 | 180.1 | 60.576 | 0.019974 | 148.24 | 1138.7 |  | 14809 | 180.1 | 7.5362 | 60.576 | 0.019974 | 148.24 | 1138.7 | 990.46
14810 | 7.5379 | 180.11 | 60.576 | 0.019978 | 148.25 | 1138.7 |  | 14810 | 180.11 | 7.5379 | 60.576 | 0.019978 | 148.25 | 1138.7 | 990.45
14811 | 7.5395 | 180.12 | 60.576 | 0.019982 | 148.26 | 1138.7 |  | 14811 | 180.12 | 7.5395 | 60.576 | 0.019982 | 148.26 | 1138.7 | 990.44
14812 | 7.5412 | 180.13 | 60.575 | 0.019986 | 148.27 | 1138.7 |  | 14812 | 180.13 | 7.5412 | 60.575 | 0.019986 | 148.27 | 1138.7 | 990.43
14813 | 7.5429 | 180.14 | 60.575 | 0.019991 | 148.28 | 1138.7 |  | 14813 | 180.14 | 7.5429 | 60.575 | 0.019991 | 148.28 | 1138.7 | 990.42
14814 | 7.5446 | 180.15 | 60.575 | 0.019995 | 148.29 | 1138.7 |  | 14814 | 180.15 | 7.5446 | 60.575 | 0.019995 | 148.29 | 1138.7 | 990.41
14815 | 7.5462 | 180.16 | 60.575 | 0.019999 | 148.3 | 1138.7 |  | 14815 | 180.16 | 7.5462 | 60.575 | 0.019999 | 148.3 | 1138.7 | 990.4
14816 | 7.5479 | 180.17 | 60.575 | 0.020003 | 148.31 | 1138.7 |  | 14816 | 180.17 | 7.5479 | 60.575 | 0.020003 | 148.31 | 1138.7 | 990.39
14817 | 7.5496 | 180.18 | 60.574 | 0.020007 | 148.32 | 1138.7 |  | 14817 | 180.18 | 7.5496 | 60.574 | 0.020007 | 148.32 | 1138.7 | 990.38
14818 | 7.5513 | 180.19 | 60.574 | 0.020011 | 148.33 | 1138.7 |  | 14818 | 180.19 | 7.5513 | 60.574 | 0.020011 | 148.33 | 1138.7 | 990.37
14819 | 7.5529 | 180.2 | 60.574 | 0.020016 | 148.34 | 1138.7 |  | 14819 | 180.2 | 7.5529 | 60.574 | 0.020016 | 148.34 | 1138.7 | 990.36
14820 | 7.5546 | 180.21 | 60.574 | 0.02002 | 148.35 | 1138.7 |  | 14820 | 180.21 | 7.5546 | 60.574 | 0.02002 | 148.35 | 1138.7 | 990.35
14821 | 7.5563 | 180.22 | 60.573 | 0.020024 | 148.36 | 1138.7 |  | 14821 | 180.22 | 7.5563 | 60.573 | 0.020024 | 148.36 | 1138.7 | 990.34
14822 | 7.5579 | 180.23 | 60.573 | 0.020028 | 148.37 | 1138.7 |  | 14822 | 180.23 | 7.5579 | 60.573 | 0.020028 | 148.37 | 1138.7 | 990.33
14823 | 7.5596 | 180.24 | 60.573 | 0.020032 | 148.38 | 1138.7 |  | 14823 | 180.24 | 7.5596 | 60.573 | 0.020032 | 148.38 | 1138.7 | 990.32
14824 | 7.5613 | 180.25 | 60.573 | 0.020036 | 148.39 | 1138.7 |  | 14824 | 180.25 | 7.5613 | 60.573 | 0.020036 | 148.39 | 1138.7 | 990.31
14825 | 7.563 | 180.26 | 60.573 | 0.02004 | 148.4 | 1138.8 |  | 14825 | 180.26 | 7.563 | 60.573 | 0.02004 | 148.4 | 1138.8 | 990.4
14826 | 7.5646 | 180.27 | 60.572 | 0.020045 | 148.41 | 1138.8 |  | 14826 | 180.27 | 7.5646 | 60.572 | 0.020045 | 148.41 | 1138.8 | 990.39
14827 | 7.5663 | 180.28 | 60.572 | 0.020049 | 148.42 | 1138.8 |  | 14827 | 180.28 | 7.5663 | 60.572 | 0.020049 | 148.42 | 1138.8 | 990.38
14828 | 7.568 | 180.29 | 60.572 | 0.020053 | 148.43 | 1138.8 |  | 14828 | 180.29 | 7.568 | 60.572 | 0.020053 | 148.43 | 1138.8 | 990.37
14829 | 7.5697 | 180.3 | 60.572 | 0.020057 | 148.44 | 1138.8 |  | 14829 | 180.3 | 7.5697 | 60.572 | 0.020057 | 148.44 | 1138.8 | 990.36
14830 | 7.5714 | 180.31 | 60.571 | 0.020061 | 148.45 | 1138.8 |  | 14830 | 180.31 | 7.5714 | 60.571 | 0.020061 | 148.45 | 1138.8 | 990.35
14831 | 7.573 | 180.32 | 60.571 | 0.020065 | 148.46 | 1138.8 |  | 14831 | 180.32 | 7.573 | 60.571 | 0.020065 | 148.46 | 1138.8 | 990.34
14832 | 7.5747 | 180.33 | 60.571 | 0.02007 | 148.47 | 1138.8 |  | 14832 | 180.33 | 7.5747 | 60.571 | 0.02007 | 148.47 | 1138.8 | 990.33
14833 | 7.5764 | 180.34 | 60.571 | 0.020074 | 148.48 | 1138.8 |  | 14833 | 180.34 | 7.5764 | 60.571 | 0.020074 | 148.48 | 1138.8 | 990.32
14834 | 7.5781 | 180.35 | 60.571 | 0.020078 | 148.49 | 1138.8 |  | 14834 | 180.35 | 7.5781 | 60.571 | 0.020078 | 148.49 | 1138.8 | 990.31
14835 | 7.5797 | 180.36 | 60.57 | 0.020082 | 148.5 | 1138.8 |  | 14835 | 180.36 | 7.5797 | 60.57 | 0.020082 | 148.5 | 1138.8 | 990.3
14836 | 7.5814 | 180.37 | 60.57 | 0.020086 | 148.51 | 1138.8 |  | 14836 | 180.37 | 7.5814 | 60.57 | 0.020086 | 148.51 | 1138.8 | 990.29
14837 | 7.5831 | 180.38 | 60.57 | 0.02009 | 148.52 | 1138.8 |  | 14837 | 180.38 | 7.5831 | 60.57 | 0.02009 | 148.52 | 1138.8 | 990.28
14838 | 7.5848 | 180.39 | 60.57 | 0.020095 | 148.53 | 1138.8 |  | 14838 | 180.39 | 7.5848 | 60.57 | 0.020095 | 148.53 | 1138.8 | 990.27
14839 | 7.5865 | 180.4 | 60.569 | 0.020099 | 148.54 | 1138.8 |  | 14839 | 180.4 | 7.5865 | 60.569 | 0.020099 | 148.54 | 1138.8 | 990.26
14840 | 7.5881 | 180.41 | 60.569 | 0.020103 | 148.55 | 1138.8 |  | 14840 | 180.41 | 7.5881 | 60.569 | 0.020103 | 148.55 | 1138.8 | 990.25
14841 | 7.5898 | 180.42 | 60.569 | 0.020107 | 148.56 | 1138.8 |  | 14841 | 180.42 | 7.5898 | 60.569 | 0.020107 | 148.56 | 1138.8 | 990.24
14842 | 7.5915 | 180.43 | 60.569 | 0.020111 | 148.57 | 1138.8 |  | 14842 | 180.43 | 7.5915 | 60.569 | 0.020111 | 148.57 | 1138.8 | 990.23
14843 | 7.5932 | 180.44 | 60.569 | 0.020115 | 148.58 | 1138.8 |  | 14843 | 180.44 | 7.5932 | 60.569 | 0.020115 | 148.58 | 1138.8 | 990.22
14844 | 7.5949 | 180.45 | 60.568 | 0.02012 | 148.59 | 1138.8 |  | 14844 | 180.45 | 7.5949 | 60.568 | 0.02012 | 148.59 | 1138.8 | 990.21
14845 | 7.5965 | 180.46 | 60.568 | 0.020124 | 148.6 | 1138.8 |  | 14845 | 180.46 | 7.5965 | 60.568 | 0.020124 | 148.6 | 1138.8 | 990.2
14846 | 7.5982 | 180.47 | 60.568 | 0.020128 | 148.61 | 1138.8 |  | 14846 | 180.47 | 7.5982 | 60.568 | 0.020128 | 148.61 | 1138.8 | 990.19
14847 | 7.5999 | 180.48 | 60.568 | 0.020132 | 148.62 | 1138.8 |  | 14847 | 180.48 | 7.5999 | 60.568 | 0.020132 | 148.62 | 1138.8 | 990.18
14848 | 7.6016 | 180.49 | 60.567 | 0.020136 | 148.63 | 1138.8 |  | 14848 | 180.49 | 7.6016 | 60.567 | 0.020136 | 148.63 | 1138.8 | 990.17
14849 | 7.6033 | 180.5 | 60.567 | 0.02014 | 148.64 | 1138.8 |  | 14849 | 180.5 | 7.6033 | 60.567 | 0.02014 | 148.64 | 1138.8 | 990.16
14850 | 7.605 | 180.51 | 60.567 | 0.020145 | 148.65 | 1138.9 |  | 14850 | 180.51 | 7.605 | 60.567 | 0.020145 | 148.65 | 1138.9 | 990.25
14851 | 7.6066 | 180.52 | 60.567 | 0.020149 | 148.66 | 1138.9 |  | 14851 | 180.52 | 7.6066 | 60.567 | 0.020149 | 148.66 | 1138.9 | 990.24
14852 | 7.6083 | 180.53 | 60.567 | 0.020153 | 148.67 | 1138.9 |  | 14852 | 180.53 | 7.6083 | 60.567 | 0.020153 | 148.67 | 1138.9 | 990.23
14853 | 7.61 | 180.54 | 60.566 | 0.020157 | 148.68 | 1138.9 |  | 14853 | 180.54 | 7.61 | 60.566 | 0.020157 | 148.68 | 1138.9 | 990.22
14854 | 7.6117 | 180.55 | 60.566 | 0.020161 | 148.69 | 1138.9 |  | 14854 | 180.55 | 7.6117 | 60.566 | 0.020161 | 148.69 | 1138.9 | 990.21
14855 | 7.6134 | 180.56 | 60.566 | 0.020165 | 148.7 | 1138.9 |  | 14855 | 180.56 | 7.6134 | 60.566 | 0.020165 | 148.7 | 1138.9 | 990.2
14856 | 7.6151 | 180.57 | 60.566 | 0.02017 | 148.71 | 1138.9 |  | 14856 | 180.57 | 7.6151 | 60.566 | 0.02017 | 148.71 | 1138.9 | 990.19
14857 | 7.6167 | 180.58 | 60.565 | 0.020174 | 148.72 | 1138.9 |  | 14857 | 180.58 | 7.6167 | 60.565 | 0.020174 | 148.72 | 1138.9 | 990.18
14858 | 7.6184 | 180.59 | 60.565 | 0.020178 | 148.73 | 1138.9 |  | 14858 | 180.59 | 7.6184 | 60.565 | 0.020178 | 148.73 | 1138.9 | 990.17
14859 | 7.6201 | 180.6 | 60.565 | 0.020182 | 148.74 | 1138.9 |  | 14859 | 180.6 | 7.6201 | 60.565 | 0.020182 | 148.74 | 1138.9 | 990.16
14860 | 7.6218 | 180.61 | 60.565 | 0.020186 | 148.75 | 1138.9 |  | 14860 | 180.61 | 7.6218 | 60.565 | 0.020186 | 148.75 | 1138.9 | 990.15
14861 | 7.6235 | 180.62 | 60.565 | 0.02019 | 148.76 | 1138.9 |  | 14861 | 180.62 | 7.6235 | 60.565 | 0.02019 | 148.76 | 1138.9 | 990.14
14862 | 7.6252 | 180.63 | 60.564 | 0.020195 | 148.77 | 1138.9 |  | 14862 | 180.63 | 7.6252 | 60.564 | 0.020195 | 148.77 | 1138.9 | 990.13
14863 | 7.6269 | 180.64 | 60.564 | 0.020199 | 148.78 | 1138.9 |  | 14863 | 180.64 | 7.6269 | 60.564 | 0.020199 | 148.78 | 1138.9 | 990.12
14864 | 7.6286 | 180.65 | 60.564 | 0.020203 | 148.79 | 1138.9 |  | 14864 | 180.65 | 7.6286 | 60.564 | 0.020203 | 148.79 | 1138.9 | 990.11
14865 | 7.6302 | 180.66 | 60.564 | 0.020207 | 148.8 | 1138.9 |  | 14865 | 180.66 | 7.6302 | 60.564 | 0.020207 | 148.8 | 1138.9 | 990.1
14866 | 7.6319 | 180.67 | 60.564 | 0.020211 | 148.81 | 1138.9 |  | 14866 | 180.67 | 7.6319 | 60.564 | 0.020211 | 148.81 | 1138.9 | 990.09
14867 | 7.6336 | 180.68 | 60.563 | 0.020216 | 148.82 | 1138.9 |  | 14867 | 180.68 | 7.6336 | 60.563 | 0.020216 | 148.82 | 1138.9 | 990.08
14868 | 7.6353 | 180.69 | 60.563 | 0.02022 | 148.83 | 1138.9 |  | 14868 | 180.69 | 7.6353 | 60.563 | 0.02022 | 148.83 | 1138.9 | 990.07
14869 | 7.637 | 180.7 | 60.563 | 0.020224 | 148.84 | 1138.9 |  | 14869 | 180.7 | 7.637 | 60.563 | 0.020224 | 148.84 | 1138.9 | 990.06
14870 | 7.6387 | 180.71 | 60.563 | 0.020228 | 148.85 | 1138.9 |  | 14870 | 180.71 | 7.6387 | 60.563 | 0.020228 | 148.85 | 1138.9 | 990.05
14871 | 7.6404 | 180.72 | 60.562 | 0.020232 | 148.86 | 1138.9 |  | 14871 | 180.72 | 7.6404 | 60.562 | 0.020232 | 148.86 | 1138.9 | 990.04
14872 | 7.6421 | 180.73 | 60.562 | 0.020237 | 148.87 | 1138.9 |  | 14872 | 180.73 | 7.6421 | 60.562 | 0.020237 | 148.87 | 1138.9 | 990.03
14873 | 7.6438 | 180.74 | 60.562 | 0.020241 | 148.88 | 1138.9 |  | 14873 | 180.74 | 7.6438 | 60.562 | 0.020241 | 148.88 | 1138.9 | 990.02
14874 | 7.6454 | 180.75 | 60.562 | 0.020245 | 148.89 | 1138.9 |  | 14874 | 180.75 | 7.6454 | 60.562 | 0.020245 | 148.89 | 1138.9 | 990.01
14875 | 7.6471 | 180.76 | 60.562 | 0.020249 | 148.9 | 1138.9 |  | 14875 | 180.76 | 7.6471 | 60.562 | 0.020249 | 148.9 | 1138.9 | 990
14876 | 7.6488 | 180.77 | 60.561 | 0.020253 | 148.91 | 1139 |  | 14876 | 180.77 | 7.6488 | 60.561 | 0.020253 | 148.91 | 1139 | 990.09
14877 | 7.6505 | 180.78 | 60.561 | 0.020257 | 148.92 | 1139 |  | 14877 | 180.78 | 7.6505 | 60.561 | 0.020257 | 148.92 | 1139 | 990.08
14878 | 7.6522 | 180.79 | 60.561 | 0.020262 | 148.93 | 1139 |  | 14878 | 180.79 | 7.6522 | 60.561 | 0.020262 | 148.93 | 1139 | 990.07
14879 | 7.6539 | 180.8 | 60.561 | 0.020266 | 148.94 | 1139 |  | 14879 | 180.8 | 7.6539 | 60.561 | 0.020266 | 148.94 | 1139 | 990.06
14880 | 7.6556 | 180.81 | 60.56 | 0.02027 | 148.95 | 1139 |  | 14880 | 180.81 | 7.6556 | 60.56 | 0.02027 | 148.95 | 1139 | 990.05
14881 | 7.6573 | 180.82 | 60.56 | 0.020274 | 148.96 | 1139 |  | 14881 | 180.82 | 7.6573 | 60.56 | 0.020274 | 148.96 | 1139 | 990.04
14882 | 7.659 | 180.83 | 60.56 | 0.020278 | 148.97 | 1139 |  | 14882 | 180.83 | 7.659 | 60.56 | 0.020278 | 148.97 | 1139 | 990.03
14883 | 7.6607 | 180.84 | 60.56 | 0.020283 | 148.98 | 1139 |  | 14883 | 180.84 | 7.6607 | 60.56 | 0.020283 | 148.98 | 1139 | 990.02
14884 | 7.6624 | 180.85 | 60.56 | 0.020287 | 148.99 | 1139 |  | 14884 | 180.85 | 7.6624 | 60.56 | 0.020287 | 148.99 | 1139 | 990.01
14885 | 7.6641 | 180.86 | 60.559 | 0.020291 | 149 | 1139 |  | 14885 | 180.86 | 7.6641 | 60.559 | 0.020291 | 149 | 1139 | 990
14886 | 7.6658 | 180.87 | 60.559 | 0.020295 | 149.01 | 1139 |  | 14886 | 180.87 | 7.6658 | 60.559 | 0.020295 | 149.01 | 1139 | 989.99
14887 | 7.6674 | 180.88 | 60.559 | 0.020299 | 149.02 | 1139 |  | 14887 | 180.88 | 7.6674 | 60.559 | 0.020299 | 149.02 | 1139 | 989.98
14888 | 7.6691 | 180.89 | 60.559 | 0.020304 | 149.03 | 1139 |  | 14888 | 180.89 | 7.6691 | 60.559 | 0.020304 | 149.03 | 1139 | 989.97
14889 | 7.6708 | 180.9 | 60.558 | 0.020308 | 149.04 | 1139 |  | 14889 | 180.9 | 7.6708 | 60.558 | 0.020308 | 149.04 | 1139 | 989.96
14890 | 7.6725 | 180.91 | 60.558 | 0.020312 | 149.05 | 1139 |  | 14890 | 180.91 | 7.6725 | 60.558 | 0.020312 | 149.05 | 1139 | 989.95
14891 | 7.6742 | 180.92 | 60.558 | 0.020316 | 149.06 | 1139 |  | 14891 | 180.92 | 7.6742 | 60.558 | 0.020316 | 149.06 | 1139 | 989.94
14892 | 7.6759 | 180.93 | 60.558 | 0.02032 | 149.07 | 1139 |  | 14892 | 180.93 | 7.6759 | 60.558 | 0.02032 | 149.07 | 1139 | 989.93
14893 | 7.6776 | 180.94 | 60.558 | 0.020325 | 149.08 | 1139 |  | 14893 | 180.94 | 7.6776 | 60.558 | 0.020325 | 149.08 | 1139 | 989.92
14894 | 7.6793 | 180.95 | 60.557 | 0.020329 | 149.09 | 1139 |  | 14894 | 180.95 | 7.6793 | 60.557 | 0.020329 | 149.09 | 1139 | 989.91
14895 | 7.681 | 180.96 | 60.557 | 0.020333 | 149.1 | 1139 |  | 14895 | 180.96 | 7.681 | 60.557 | 0.020333 | 149.1 | 1139 | 989.9
14896 | 7.6827 | 180.97 | 60.557 | 0.020337 | 149.11 | 1139 |  | 14896 | 180.97 | 7.6827 | 60.557 | 0.020337 | 149.11 | 1139 | 989.89
14897 | 7.6844 | 180.98 | 60.557 | 0.020341 | 149.12 | 1139 |  | 14897 | 180.98 | 7.6844 | 60.557 | 0.020341 | 149.12 | 1139 | 989.88
14898 | 7.6861 | 180.99 | 60.556 | 0.020346 | 149.13 | 1139 |  | 14898 | 180.99 | 7.6861 | 60.556 | 0.020346 | 149.13 | 1139 | 989.87
14899 | 7.6878 | 181 | 60.556 | 0.02035 | 149.14 | 1139 |  | 14899 | 181 | 7.6878 | 60.556 | 0.02035 | 149.14 | 1139 | 989.86
14900 | 7.6895 | 181.01 | 60.556 | 0.020354 | 149.15 | 1139 |  | 14900 | 181.01 | 7.6895 | 60.556 | 0.020354 | 149.15 | 1139 | 989.85
14901 | 7.6912 | 181.02 | 60.556 | 0.020358 | 149.16 | 1139.1 |  | 14901 | 181.02 | 7.6912 | 60.556 | 0.020358 | 149.16 | 1139.1 | 989.94
14902 | 7.6929 | 181.03 | 60.556 | 0.020363 | 149.17 | 1139.1 |  | 14902 | 181.03 | 7.6929 | 60.556 | 0.020363 | 149.17 | 1139.1 | 989.93
14903 | 7.6946 | 181.04 | 60.555 | 0.020367 | 149.18 | 1139.1 |  | 14903 | 181.04 | 7.6946 | 60.555 | 0.020367 | 149.18 | 1139.1 | 989.92
14904 | 7.6963 | 181.05 | 60.555 | 0.020371 | 149.19 | 1139.1 |  | 14904 | 181.05 | 7.6963 | 60.555 | 0.020371 | 149.19 | 1139.1 | 989.91
14905 | 7.698 | 181.06 | 60.555 | 0.020375 | 149.2 | 1139.1 |  | 14905 | 181.06 | 7.698 | 60.555 | 0.020375 | 149.2 | 1139.1 | 989.9
14906 | 7.6997 | 181.07 | 60.555 | 0.020379 | 149.21 | 1139.1 |  | 14906 | 181.07 | 7.6997 | 60.555 | 0.020379 | 149.21 | 1139.1 | 989.89
14907 | 7.7014 | 181.08 | 60.554 | 0.020384 | 149.22 | 1139.1 |  | 14907 | 181.08 | 7.7014 | 60.554 | 0.020384 | 149.22 | 1139.1 | 989.88
14908 | 7.7031 | 181.09 | 60.554 | 0.020388 | 149.23 | 1139.1 |  | 14908 | 181.09 | 7.7031 | 60.554 | 0.020388 | 149.23 | 1139.1 | 989.87
14909 | 7.7048 | 181.1 | 60.554 | 0.020392 | 149.24 | 1139.1 |  | 14909 | 181.1 | 7.7048 | 60.554 | 0.020392 | 149.24 | 1139.1 | 989.86
14910 | 7.7065 | 181.11 | 60.554 | 0.020396 | 149.25 | 1139.1 |  | 14910 | 181.11 | 7.7065 | 60.554 | 0.020396 | 149.25 | 1139.1 | 989.85
14911 | 7.7082 | 181.12 | 60.554 | 0.0204 | 149.26 | 1139.1 |  | 14911 | 181.12 | 7.7082 | 60.554 | 0.0204 | 149.26 | 1139.1 | 989.84
14912 | 7.7099 | 181.13 | 60.553 | 0.020405 | 149.27 | 1139.1 |  | 14912 | 181.13 | 7.7099 | 60.553 | 0.020405 | 149.27 | 1139.1 | 989.83
14913 | 7.7116 | 181.14 | 60.553 | 0.020409 | 149.28 | 1139.1 |  | 14913 | 181.14 | 7.7116 | 60.553 | 0.020409 | 149.28 | 1139.1 | 989.82
14914 | 7.7133 | 181.15 | 60.553 | 0.020413 | 149.29 | 1139.1 |  | 14914 | 181.15 | 7.7133 | 60.553 | 0.020413 | 149.29 | 1139.1 | 989.81
14915 | 7.715 | 181.16 | 60.553 | 0.020417 | 149.3 | 1139.1 |  | 14915 | 181.16 | 7.715 | 60.553 | 0.020417 | 149.3 | 1139.1 | 989.8
14916 | 7.7167 | 181.17 | 60.552 | 0.020422 | 149.32 | 1139.1 |  | 14916 | 181.17 | 7.7167 | 60.552 | 0.020422 | 149.32 | 1139.1 | 989.78
14917 | 7.7184 | 181.18 | 60.552 | 0.020426 | 149.33 | 1139.1 |  | 14917 | 181.18 | 7.7184 | 60.552 | 0.020426 | 149.33 | 1139.1 | 989.77
14918 | 7.7201 | 181.19 | 60.552 | 0.02043 | 149.34 | 1139.1 |  | 14918 | 181.19 | 7.7201 | 60.552 | 0.02043 | 149.34 | 1139.1 | 989.76
14919 | 7.7218 | 181.2 | 60.552 | 0.020434 | 149.35 | 1139.1 |  | 14919 | 181.2 | 7.7218 | 60.552 | 0.020434 | 149.35 | 1139.1 | 989.75
14920 | 7.7235 | 181.21 | 60.552 | 0.020438 | 149.36 | 1139.1 |  | 14920 | 181.21 | 7.7235 | 60.552 | 0.020438 | 149.36 | 1139.1 | 989.74
14921 | 7.7253 | 181.22 | 60.551 | 0.020443 | 149.37 | 1139.1 |  | 14921 | 181.22 | 7.7253 | 60.551 | 0.020443 | 149.37 | 1139.1 | 989.73
14922 | 7.727 | 181.23 | 60.551 | 0.020447 | 149.38 | 1139.1 |  | 14922 | 181.23 | 7.727 | 60.551 | 0.020447 | 149.38 | 1139.1 | 989.72
14923 | 7.7287 | 181.24 | 60.551 | 0.020451 | 149.39 | 1139.1 |  | 14923 | 181.24 | 7.7287 | 60.551 | 0.020451 | 149.39 | 1139.1 | 989.71
14924 | 7.7304 | 181.25 | 60.551 | 0.020455 | 149.4 | 1139.1 |  | 14924 | 181.25 | 7.7304 | 60.551 | 0.020455 | 149.4 | 1139.1 | 989.7
14925 | 7.7321 | 181.26 | 60.55 | 0.02046 | 149.41 | 1139.1 |  | 14925 | 181.26 | 7.7321 | 60.55 | 0.02046 | 149.41 | 1139.1 | 989.69
14926 | 7.7338 | 181.27 | 60.55 | 0.020464 | 149.42 | 1139.2 |  | 14926 | 181.27 | 7.7338 | 60.55 | 0.020464 | 149.42 | 1139.2 | 989.78
14927 | 7.7355 | 181.28 | 60.55 | 0.020468 | 149.43 | 1139.2 |  | 14927 | 181.28 | 7.7355 | 60.55 | 0.020468 | 149.43 | 1139.2 | 989.77
14928 | 7.7372 | 181.29 | 60.55 | 0.020472 | 149.44 | 1139.2 |  | 14928 | 181.29 | 7.7372 | 60.55 | 0.020472 | 149.44 | 1139.2 | 989.76
14929 | 7.7389 | 181.3 | 60.55 | 0.020476 | 149.45 | 1139.2 |  | 14929 | 181.3 | 7.7389 | 60.55 | 0.020476 | 149.45 | 1139.2 | 989.75
14930 | 7.7406 | 181.31 | 60.549 | 0.020481 | 149.46 | 1139.2 |  | 14930 | 181.31 | 7.7406 | 60.549 | 0.020481 | 149.46 | 1139.2 | 989.74
14931 | 7.7423 | 181.32 | 60.549 | 0.020485 | 149.47 | 1139.2 |  | 14931 | 181.32 | 7.7423 | 60.549 | 0.020485 | 149.47 | 1139.2 | 989.73
14932 | 7.744 | 181.33 | 60.549 | 0.020489 | 149.48 | 1139.2 |  | 14932 | 181.33 | 7.744 | 60.549 | 0.020489 | 149.48 | 1139.2 | 989.72
14933 | 7.7457 | 181.34 | 60.549 | 0.020493 | 149.49 | 1139.2 |  | 14933 | 181.34 | 7.7457 | 60.549 | 0.020493 | 149.49 | 1139.2 | 989.71
14934 | 7.7475 | 181.35 | 60.549 | 0.020498 | 149.5 | 1139.2 |  | 14934 | 181.35 | 7.7475 | 60.549 | 0.020498 | 149.5 | 1139.2 | 989.7
14935 | 7.7492 | 181.36 | 60.548 | 0.020502 | 149.51 | 1139.2 |  | 14935 | 181.36 | 7.7492 | 60.548 | 0.020502 | 149.51 | 1139.2 | 989.69
14936 | 7.7509 | 181.37 | 60.548 | 0.020506 | 149.52 | 1139.2 |  | 14936 | 181.37 | 7.7509 | 60.548 | 0.020506 | 149.52 | 1139.2 | 989.68
14937 | 7.7526 | 181.38 | 60.548 | 0.02051 | 149.53 | 1139.2 |  | 14937 | 181.38 | 7.7526 | 60.548 | 0.02051 | 149.53 | 1139.2 | 989.67
14938 | 7.7543 | 181.39 | 60.548 | 0.020515 | 149.54 | 1139.2 |  | 14938 | 181.39 | 7.7543 | 60.548 | 0.020515 | 149.54 | 1139.2 | 989.66
14939 | 7.756 | 181.4 | 60.547 | 0.020519 | 149.55 | 1139.2 |  | 14939 | 181.4 | 7.756 | 60.547 | 0.020519 | 149.55 | 1139.2 | 989.65
14940 | 7.7577 | 181.41 | 60.547 | 0.020523 | 149.56 | 1139.2 |  | 14940 | 181.41 | 7.7577 | 60.547 | 0.020523 | 149.56 | 1139.2 | 989.64
14941 | 7.7594 | 181.42 | 60.547 | 0.020527 | 149.57 | 1139.2 |  | 14941 | 181.42 | 7.7594 | 60.547 | 0.020527 | 149.57 | 1139.2 | 989.63
14942 | 7.7611 | 181.43 | 60.547 | 0.020532 | 149.58 | 1139.2 |  | 14942 | 181.43 | 7.7611 | 60.547 | 0.020532 | 149.58 | 1139.2 | 989.62
14943 | 7.7629 | 181.44 | 60.547 | 0.020536 | 149.59 | 1139.2 |  | 14943 | 181.44 | 7.7629 | 60.547 | 0.020536 | 149.59 | 1139.2 | 989.61
14944 | 7.7646 | 181.45 | 60.546 | 0.02054 | 149.6 | 1139.2 |  | 14944 | 181.45 | 7.7646 | 60.546 | 0.02054 | 149.6 | 1139.2 | 989.6
14945 | 7.7663 | 181.46 | 60.546 | 0.020544 | 149.61 | 1139.2 |  | 14945 | 181.46 | 7.7663 | 60.546 | 0.020544 | 149.61 | 1139.2 | 989.59
14946 | 7.768 | 181.47 | 60.546 | 0.020549 | 149.62 | 1139.2 |  | 14946 | 181.47 | 7.768 | 60.546 | 0.020549 | 149.62 | 1139.2 | 989.58
14947 | 7.7697 | 181.48 | 60.546 | 0.020553 | 149.63 | 1139.2 |  | 14947 | 181.48 | 7.7697 | 60.546 | 0.020553 | 149.63 | 1139.2 | 989.57
14948 | 7.7714 | 181.49 | 60.545 | 0.020557 | 149.64 | 1139.2 |  | 14948 | 181.49 | 7.7714 | 60.545 | 0.020557 | 149.64 | 1139.2 | 989.56
14949 | 7.7731 | 181.5 | 60.545 | 0.020561 | 149.65 | 1139.2 |  | 14949 | 181.5 | 7.7731 | 60.545 | 0.020561 | 149.65 | 1139.2 | 989.55
14950 | 7.7748 | 181.51 | 60.545 | 0.020565 | 149.66 | 1139.2 |  | 14950 | 181.51 | 7.7748 | 60.545 | 0.020565 | 149.66 | 1139.2 | 989.54
14951 | 7.7766 | 181.52 | 60.545 | 0.02057 | 149.67 | 1139.3 |  | 14951 | 181.52 | 7.7766 | 60.545 | 0.02057 | 149.67 | 1139.3 | 989.63
14952 | 7.7783 | 181.53 | 60.545 | 0.020574 | 149.68 | 1139.3 |  | 14952 | 181.53 | 7.7783 | 60.545 | 0.020574 | 149.68 | 1139.3 | 989.62
14953 | 7.78 | 181.54 | 60.544 | 0.020578 | 149.69 | 1139.3 |  | 14953 | 181.54 | 7.78 | 60.544 | 0.020578 | 149.69 | 1139.3 | 989.61
14954 | 7.7817 | 181.55 | 60.544 | 0.020582 | 149.7 | 1139.3 |  | 14954 | 181.55 | 7.7817 | 60.544 | 0.020582 | 149.7 | 1139.3 | 989.6
14955 | 7.7834 | 181.56 | 60.544 | 0.020587 | 149.71 | 1139.3 |  | 14955 | 181.56 | 7.7834 | 60.544 | 0.020587 | 149.71 | 1139.3 | 989.59
14956 | 7.7851 | 181.57 | 60.544 | 0.020591 | 149.72 | 1139.3 |  | 14956 | 181.57 | 7.7851 | 60.544 | 0.020591 | 149.72 | 1139.3 | 989.58
14957 | 7.7869 | 181.58 | 60.543 | 0.020595 | 149.73 | 1139.3 |  | 14957 | 181.58 | 7.7869 | 60.543 | 0.020595 | 149.73 | 1139.3 | 989.57
14958 | 7.7886 | 181.59 | 60.543 | 0.020599 | 149.74 | 1139.3 |  | 14958 | 181.59 | 7.7886 | 60.543 | 0.020599 | 149.74 | 1139.3 | 989.56
14959 | 7.7903 | 181.6 | 60.543 | 0.020604 | 149.75 | 1139.3 |  | 14959 | 181.6 | 7.7903 | 60.543 | 0.020604 | 149.75 | 1139.3 | 989.55
14960 | 7.792 | 181.61 | 60.543 | 0.020608 | 149.76 | 1139.3 |  | 14960 | 181.61 | 7.792 | 60.543 | 0.020608 | 149.76 | 1139.3 | 989.54
14961 | 7.7937 | 181.62 | 60.543 | 0.020612 | 149.77 | 1139.3 |  | 14961 | 181.62 | 7.7937 | 60.543 | 0.020612 | 149.77 | 1139.3 | 989.53
14962 | 7.7954 | 181.63 | 60.542 | 0.020616 | 149.78 | 1139.3 |  | 14962 | 181.63 | 7.7954 | 60.542 | 0.020616 | 149.78 | 1139.3 | 989.52
14963 | 7.7972 | 181.64 | 60.542 | 0.020621 | 149.79 | 1139.3 |  | 14963 | 181.64 | 7.7972 | 60.542 | 0.020621 | 149.79 | 1139.3 | 989.51
14964 | 7.7989 | 181.65 | 60.542 | 0.020625 | 149.8 | 1139.3 |  | 14964 | 181.65 | 7.7989 | 60.542 | 0.020625 | 149.8 | 1139.3 | 989.5
14965 | 7.8006 | 181.66 | 60.542 | 0.020629 | 149.81 | 1139.3 |  | 14965 | 181.66 | 7.8006 | 60.542 | 0.020629 | 149.81 | 1139.3 | 989.49
14966 | 7.8023 | 181.67 | 60.541 | 0.020634 | 149.82 | 1139.3 |  | 14966 | 181.67 | 7.8023 | 60.541 | 0.020634 | 149.82 | 1139.3 | 989.48
14967 | 7.804 | 181.68 | 60.541 | 0.020638 | 149.83 | 1139.3 |  | 14967 | 181.68 | 7.804 | 60.541 | 0.020638 | 149.83 | 1139.3 | 989.47
14968 | 7.8058 | 181.69 | 60.541 | 0.020642 | 149.84 | 1139.3 |  | 14968 | 181.69 | 7.8058 | 60.541 | 0.020642 | 149.84 | 1139.3 | 989.46
14969 | 7.8075 | 181.7 | 60.541 | 0.020646 | 149.85 | 1139.3 |  | 14969 | 181.7 | 7.8075 | 60.541 | 0.020646 | 149.85 | 1139.3 | 989.45
14970 | 7.8092 | 181.71 | 60.541 | 0.020651 | 149.86 | 1139.3 |  | 14970 | 181.71 | 7.8092 | 60.541 | 0.020651 | 149.86 | 1139.3 | 989.44
14971 | 7.8109 | 181.72 | 60.54 | 0.020655 | 149.87 | 1139.3 |  | 14971 | 181.72 | 7.8109 | 60.54 | 0.020655 | 149.87 | 1139.3 | 989.43
14972 | 7.8126 | 181.73 | 60.54 | 0.020659 | 149.88 | 1139.3 |  | 14972 | 181.73 | 7.8126 | 60.54 | 0.020659 | 149.88 | 1139.3 | 989.42
14973 | 7.8144 | 181.74 | 60.54 | 0.020663 | 149.89 | 1139.3 |  | 14973 | 181.74 | 7.8144 | 60.54 | 0.020663 | 149.89 | 1139.3 | 989.41
14974 | 7.8161 | 181.75 | 60.54 | 0.020668 | 149.9 | 1139.3 |  | 14974 | 181.75 | 7.8161 | 60.54 | 0.020668 | 149.9 | 1139.3 | 989.4
14975 | 7.8178 | 181.76 | 60.539 | 0.020672 | 149.91 | 1139.3 |  | 14975 | 181.76 | 7.8178 | 60.539 | 0.020672 | 149.91 | 1139.3 | 989.39
14976 | 7.8195 | 181.77 | 60.539 | 0.020676 | 149.92 | 1139.4 |  | 14976 | 181.77 | 7.8195 | 60.539 | 0.020676 | 149.92 | 1139.4 | 989.48
14977 | 7.8213 | 181.78 | 60.539 | 0.02068 | 149.93 | 1139.4 |  | 14977 | 181.78 | 7.8213 | 60.539 | 0.02068 | 149.93 | 1139.4 | 989.47
14978 | 7.823 | 181.79 | 60.539 | 0.020685 | 149.94 | 1139.4 |  | 14978 | 181.79 | 7.823 | 60.539 | 0.020685 | 149.94 | 1139.4 | 989.46
14979 | 7.8247 | 181.8 | 60.539 | 0.020689 | 149.95 | 1139.4 |  | 14979 | 181.8 | 7.8247 | 60.539 | 0.020689 | 149.95 | 1139.4 | 989.45
14980 | 7.8264 | 181.81 | 60.538 | 0.020693 | 149.96 | 1139.4 |  | 14980 | 181.81 | 7.8264 | 60.538 | 0.020693 | 149.96 | 1139.4 | 989.44
14981 | 7.8282 | 181.82 | 60.538 | 0.020697 | 149.97 | 1139.4 |  | 14981 | 181.82 | 7.8282 | 60.538 | 0.020697 | 149.97 | 1139.4 | 989.43
14982 | 7.8299 | 181.83 | 60.538 | 0.020702 | 149.98 | 1139.4 |  | 14982 | 181.83 | 7.8299 | 60.538 | 0.020702 | 149.98 | 1139.4 | 989.42
14983 | 7.8316 | 181.84 | 60.538 | 0.020706 | 149.99 | 1139.4 |  | 14983 | 181.84 | 7.8316 | 60.538 | 0.020706 | 149.99 | 1139.4 | 989.41
14984 | 7.8333 | 181.85 | 60.537 | 0.02071 | 150 | 1139.4 |  | 14984 | 181.85 | 7.8333 | 60.537 | 0.02071 | 150 | 1139.4 | 989.4
14985 | 7.8351 | 181.86 | 60.537 | 0.020715 | 150.01 | 1139.4 |  | 14985 | 181.86 | 7.8351 | 60.537 | 0.020715 | 150.01 | 1139.4 | 989.39
14986 | 7.8368 | 181.87 | 60.537 | 0.020719 | 150.02 | 1139.4 |  | 14986 | 181.87 | 7.8368 | 60.537 | 0.020719 | 150.02 | 1139.4 | 989.38
14987 | 7.8385 | 181.88 | 60.537 | 0.020723 | 150.03 | 1139.4 |  | 14987 | 181.88 | 7.8385 | 60.537 | 0.020723 | 150.03 | 1139.4 | 989.37
14988 | 7.8402 | 181.89 | 60.537 | 0.020727 | 150.04 | 1139.4 |  | 14988 | 181.89 | 7.8402 | 60.537 | 0.020727 | 150.04 | 1139.4 | 989.36
14989 | 7.842 | 181.9 | 60.536 | 0.020732 | 150.05 | 1139.4 |  | 14989 | 181.9 | 7.842 | 60.536 | 0.020732 | 150.05 | 1139.4 | 989.35
14990 | 7.8437 | 181.91 | 60.536 | 0.020736 | 150.06 | 1139.4 |  | 14990 | 181.91 | 7.8437 | 60.536 | 0.020736 | 150.06 | 1139.4 | 989.34
14991 | 7.8454 | 181.92 | 60.536 | 0.02074 | 150.07 | 1139.4 |  | 14991 | 181.92 | 7.8454 | 60.536 | 0.02074 | 150.07 | 1139.4 | 989.33
14992 | 7.8471 | 181.93 | 60.536 | 0.020744 | 150.08 | 1139.4 |  | 14992 | 181.93 | 7.8471 | 60.536 | 0.020744 | 150.08 | 1139.4 | 989.32
14993 | 7.8489 | 181.94 | 60.535 | 0.020749 | 150.09 | 1139.4 |  | 14993 | 181.94 | 7.8489 | 60.535 | 0.020749 | 150.09 | 1139.4 | 989.31
14994 | 7.8506 | 181.95 | 60.535 | 0.020753 | 150.1 | 1139.4 |  | 14994 | 181.95 | 7.8506 | 60.535 | 0.020753 | 150.1 | 1139.4 | 989.3
14995 | 7.8523 | 181.96 | 60.535 | 0.020757 | 150.11 | 1139.4 |  | 14995 | 181.96 | 7.8523 | 60.535 | 0.020757 | 150.11 | 1139.4 | 989.29
14996 | 7.8541 | 181.97 | 60.535 | 0.020762 | 150.12 | 1139.4 |  | 14996 | 181.97 | 7.8541 | 60.535 | 0.020762 | 150.12 | 1139.4 | 989.28
14997 | 7.8558 | 181.98 | 60.535 | 0.020766 | 150.13 | 1139.4 |  | 14997 | 181.98 | 7.8558 | 60.535 | 0.020766 | 150.13 | 1139.4 | 989.27
14998 | 7.8575 | 181.99 | 60.534 | 0.02077 | 150.14 | 1139.4 |  | 14998 | 181.99 | 7.8575 | 60.534 | 0.02077 | 150.14 | 1139.4 | 989.26
14999 | 7.8592 | 182 | 60.534 | 0.020774 | 150.15 | 1139.4 |  | 14999 | 182 | 7.8592 | 60.534 | 0.020774 | 150.15 | 1139.4 | 989.25
15000 | 7.861 | 182.01 | 60.534 | 0.020779 | 150.16 | 1139.4 |  | 15000 | 182.01 | 7.861 | 60.534 | 0.020779 | 150.16 | 1139.4 | 989.24
15001 | 7.8627 | 182.02 | 60.534 | 0.020783 | 150.17 | 1139.4 |  | 15001 | 182.02 | 7.8627 | 60.534 | 0.020783 | 150.17 | 1139.4 | 989.23
15002 | 7.8644 | 182.03 | 60.533 | 0.020787 | 150.18 | 1139.5 |  | 15002 | 182.03 | 7.8644 | 60.533 | 0.020787 | 150.18 | 1139.5 | 989.32
15003 | 7.8662 | 182.04 | 60.533 | 0.020792 | 150.19 | 1139.5 |  | 15003 | 182.04 | 7.8662 | 60.533 | 0.020792 | 150.19 | 1139.5 | 989.31
15004 | 7.8679 | 182.05 | 60.533 | 0.020796 | 150.2 | 1139.5 |  | 15004 | 182.05 | 7.8679 | 60.533 | 0.020796 | 150.2 | 1139.5 | 989.3
15005 | 7.8696 | 182.06 | 60.533 | 0.0208 | 150.21 | 1139.5 |  | 15005 | 182.06 | 7.8696 | 60.533 | 0.0208 | 150.21 | 1139.5 | 989.29
15006 | 7.8714 | 182.07 | 60.533 | 0.020804 | 150.22 | 1139.5 |  | 15006 | 182.07 | 7.8714 | 60.533 | 0.020804 | 150.22 | 1139.5 | 989.28
15007 | 7.8731 | 182.08 | 60.532 | 0.020809 | 150.23 | 1139.5 |  | 15007 | 182.08 | 7.8731 | 60.532 | 0.020809 | 150.23 | 1139.5 | 989.27
15008 | 7.8748 | 182.09 | 60.532 | 0.020813 | 150.24 | 1139.5 |  | 15008 | 182.09 | 7.8748 | 60.532 | 0.020813 | 150.24 | 1139.5 | 989.26
15009 | 7.8766 | 182.1 | 60.532 | 0.020817 | 150.25 | 1139.5 |  | 15009 | 182.1 | 7.8766 | 60.532 | 0.020817 | 150.25 | 1139.5 | 989.25
15010 | 7.8783 | 182.11 | 60.532 | 0.020822 | 150.26 | 1139.5 |  | 15010 | 182.11 | 7.8783 | 60.532 | 0.020822 | 150.26 | 1139.5 | 989.24
15011 | 7.88 | 182.12 | 60.531 | 0.020826 | 150.27 | 1139.5 |  | 15011 | 182.12 | 7.88 | 60.531 | 0.020826 | 150.27 | 1139.5 | 989.23
15012 | 7.8818 | 182.13 | 60.531 | 0.02083 | 150.28 | 1139.5 |  | 15012 | 182.13 | 7.8818 | 60.531 | 0.02083 | 150.28 | 1139.5 | 989.22
15013 | 7.8835 | 182.14 | 60.531 | 0.020834 | 150.29 | 1139.5 |  | 15013 | 182.14 | 7.8835 | 60.531 | 0.020834 | 150.29 | 1139.5 | 989.21
15014 | 7.8852 | 182.15 | 60.531 | 0.020839 | 150.3 | 1139.5 |  | 15014 | 182.15 | 7.8852 | 60.531 | 0.020839 | 150.3 | 1139.5 | 989.2
15015 | 7.887 | 182.16 | 60.531 | 0.020843 | 150.31 | 1139.5 |  | 15015 | 182.16 | 7.887 | 60.531 | 0.020843 | 150.31 | 1139.5 | 989.19
15016 | 7.8887 | 182.17 | 60.53 | 0.020847 | 150.32 | 1139.5 |  | 15016 | 182.17 | 7.8887 | 60.53 | 0.020847 | 150.32 | 1139.5 | 989.18
15017 | 7.8904 | 182.18 | 60.53 | 0.020852 | 150.33 | 1139.5 |  | 15017 | 182.18 | 7.8904 | 60.53 | 0.020852 | 150.33 | 1139.5 | 989.17
15018 | 7.8922 | 182.19 | 60.53 | 0.020856 | 150.34 | 1139.5 |  | 15018 | 182.19 | 7.8922 | 60.53 | 0.020856 | 150.34 | 1139.5 | 989.16
15019 | 7.8939 | 182.2 | 60.53 | 0.02086 | 150.35 | 1139.5 |  | 15019 | 182.2 | 7.8939 | 60.53 | 0.02086 | 150.35 | 1139.5 | 989.15
15020 | 7.8957 | 182.21 | 60.529 | 0.020864 | 150.36 | 1139.5 |  | 15020 | 182.21 | 7.8957 | 60.529 | 0.020864 | 150.36 | 1139.5 | 989.14
15021 | 7.8974 | 182.22 | 60.529 | 0.020869 | 150.37 | 1139.5 |  | 15021 | 182.22 | 7.8974 | 60.529 | 0.020869 | 150.37 | 1139.5 | 989.13
15022 | 7.8991 | 182.23 | 60.529 | 0.020873 | 150.38 | 1139.5 |  | 15022 | 182.23 | 7.8991 | 60.529 | 0.020873 | 150.38 | 1139.5 | 989.12
15023 | 7.9009 | 182.24 | 60.529 | 0.020877 | 150.39 | 1139.5 |  | 15023 | 182.24 | 7.9009 | 60.529 | 0.020877 | 150.39 | 1139.5 | 989.11
15024 | 7.9026 | 182.25 | 60.529 | 0.020882 | 150.4 | 1139.5 |  | 15024 | 182.25 | 7.9026 | 60.529 | 0.020882 | 150.4 | 1139.5 | 989.1
15025 | 7.9043 | 182.26 | 60.528 | 0.020886 | 150.41 | 1139.5 |  | 15025 | 182.26 | 7.9043 | 60.528 | 0.020886 | 150.41 | 1139.5 | 989.09
15026 | 7.9061 | 182.27 | 60.528 | 0.02089 | 150.42 | 1139.5 |  | 15026 | 182.27 | 7.9061 | 60.528 | 0.02089 | 150.42 | 1139.5 | 989.08
15027 | 7.9078 | 182.28 | 60.528 | 0.020895 | 150.43 | 1139.6 |  | 15027 | 182.28 | 7.9078 | 60.528 | 0.020895 | 150.43 | 1139.6 | 989.17
15028 | 7.9096 | 182.29 | 60.528 | 0.020899 | 150.44 | 1139.6 |  | 15028 | 182.29 | 7.9096 | 60.528 | 0.020899 | 150.44 | 1139.6 | 989.16
15029 | 7.9113 | 182.3 | 60.527 | 0.020903 | 150.45 | 1139.6 |  | 15029 | 182.3 | 7.9113 | 60.527 | 0.020903 | 150.45 | 1139.6 | 989.15
15030 | 7.913 | 182.31 | 60.527 | 0.020907 | 150.46 | 1139.6 |  | 15030 | 182.31 | 7.913 | 60.527 | 0.020907 | 150.46 | 1139.6 | 989.14
15031 | 7.9148 | 182.32 | 60.527 | 0.020912 | 150.47 | 1139.6 |  | 15031 | 182.32 | 7.9148 | 60.527 | 0.020912 | 150.47 | 1139.6 | 989.13
15032 | 7.9165 | 182.33 | 60.527 | 0.020916 | 150.48 | 1139.6 |  | 15032 | 182.33 | 7.9165 | 60.527 | 0.020916 | 150.48 | 1139.6 | 989.12
15033 | 7.9183 | 182.34 | 60.527 | 0.02092 | 150.49 | 1139.6 |  | 15033 | 182.34 | 7.9183 | 60.527 | 0.02092 | 150.49 | 1139.6 | 989.11
15034 | 7.92 | 182.35 | 60.526 | 0.020925 | 150.5 | 1139.6 |  | 15034 | 182.35 | 7.92 | 60.526 | 0.020925 | 150.5 | 1139.6 | 989.1
15035 | 7.9217 | 182.36 | 60.526 | 0.020929 | 150.51 | 1139.6 |  | 15035 | 182.36 | 7.9217 | 60.526 | 0.020929 | 150.51 | 1139.6 | 989.09
15036 | 7.9235 | 182.37 | 60.526 | 0.020933 | 150.52 | 1139.6 |  | 15036 | 182.37 | 7.9235 | 60.526 | 0.020933 | 150.52 | 1139.6 | 989.08
15037 | 7.9252 | 182.38 | 60.526 | 0.020938 | 150.53 | 1139.6 |  | 15037 | 182.38 | 7.9252 | 60.526 | 0.020938 | 150.53 | 1139.6 | 989.07
15038 | 7.927 | 182.39 | 60.525 | 0.020942 | 150.54 | 1139.6 |  | 15038 | 182.39 | 7.927 | 60.525 | 0.020942 | 150.54 | 1139.6 | 989.06
15039 | 7.9287 | 182.4 | 60.525 | 0.020946 | 150.55 | 1139.6 |  | 15039 | 182.4 | 7.9287 | 60.525 | 0.020946 | 150.55 | 1139.6 | 989.05
15040 | 7.9305 | 182.41 | 60.525 | 0.020951 | 150.56 | 1139.6 |  | 15040 | 182.41 | 7.9305 | 60.525 | 0.020951 | 150.56 | 1139.6 | 989.04
15041 | 7.9322 | 182.42 | 60.525 | 0.020955 | 150.57 | 1139.6 |  | 15041 | 182.42 | 7.9322 | 60.525 | 0.020955 | 150.57 | 1139.6 | 989.03
15042 | 7.9339 | 182.43 | 60.525 | 0.020959 | 150.58 | 1139.6 |  | 15042 | 182.43 | 7.9339 | 60.525 | 0.020959 | 150.58 | 1139.6 | 989.02
15043 | 7.9357 | 182.44 | 60.524 | 0.020963 | 150.59 | 1139.6 |  | 15043 | 182.44 | 7.9357 | 60.524 | 0.020963 | 150.59 | 1139.6 | 989.01
15044 | 7.9374 | 182.45 | 60.524 | 0.020968 | 150.6 | 1139.6 |  | 15044 | 182.45 | 7.9374 | 60.524 | 0.020968 | 150.6 | 1139.6 | 989
15045 | 7.9392 | 182.46 | 60.524 | 0.020972 | 150.61 | 1139.6 |  | 15045 | 182.46 | 7.9392 | 60.524 | 0.020972 | 150.61 | 1139.6 | 988.99
15046 | 7.9409 | 182.47 | 60.524 | 0.020976 | 150.62 | 1139.6 |  | 15046 | 182.47 | 7.9409 | 60.524 | 0.020976 | 150.62 | 1139.6 | 988.98
15047 | 7.9427 | 182.48 | 60.523 | 0.020981 | 150.63 | 1139.6 |  | 15047 | 182.48 | 7.9427 | 60.523 | 0.020981 | 150.63 | 1139.6 | 988.97
15048 | 7.9444 | 182.49 | 60.523 | 0.020985 | 150.64 | 1139.6 |  | 15048 | 182.49 | 7.9444 | 60.523 | 0.020985 | 150.64 | 1139.6 | 988.96
15049 | 7.9462 | 182.5 | 60.523 | 0.020989 | 150.65 | 1139.6 |  | 15049 | 182.5 | 7.9462 | 60.523 | 0.020989 | 150.65 | 1139.6 | 988.95
15050 | 7.9479 | 182.51 | 60.523 | 0.020994 | 150.66 | 1139.6 |  | 15050 | 182.51 | 7.9479 | 60.523 | 0.020994 | 150.66 | 1139.6 | 988.94
15051 | 7.9497 | 182.52 | 60.523 | 0.020998 | 150.67 | 1139.6 |  | 15051 | 182.52 | 7.9497 | 60.523 | 0.020998 | 150.67 | 1139.6 | 988.93
15052 | 7.9514 | 182.53 | 60.522 | 0.021002 | 150.68 | 1139.7 |  | 15052 | 182.53 | 7.9514 | 60.522 | 0.021002 | 150.68 | 1139.7 | 989.02
15053 | 7.9531 | 182.54 | 60.522 | 0.021007 | 150.69 | 1139.7 |  | 15053 | 182.54 | 7.9531 | 60.522 | 0.021007 | 150.69 | 1139.7 | 989.01
15054 | 7.9549 | 182.55 | 60.522 | 0.021011 | 150.7 | 1139.7 |  | 15054 | 182.55 | 7.9549 | 60.522 | 0.021011 | 150.7 | 1139.7 | 989
15055 | 7.9566 | 182.56 | 60.522 | 0.021015 | 150.71 | 1139.7 |  | 15055 | 182.56 | 7.9566 | 60.522 | 0.021015 | 150.71 | 1139.7 | 988.99
15056 | 7.9584 | 182.57 | 60.521 | 0.02102 | 150.72 | 1139.7 |  | 15056 | 182.57 | 7.9584 | 60.521 | 0.02102 | 150.72 | 1139.7 | 988.98
15057 | 7.9601 | 182.58 | 60.521 | 0.021024 | 150.73 | 1139.7 |  | 15057 | 182.58 | 7.9601 | 60.521 | 0.021024 | 150.73 | 1139.7 | 988.97
15058 | 7.9619 | 182.59 | 60.521 | 0.021028 | 150.74 | 1139.7 |  | 15058 | 182.59 | 7.9619 | 60.521 | 0.021028 | 150.74 | 1139.7 | 988.96
15059 | 7.9636 | 182.6 | 60.521 | 0.021033 | 150.75 | 1139.7 |  | 15059 | 182.6 | 7.9636 | 60.521 | 0.021033 | 150.75 | 1139.7 | 988.95
15060 | 7.9654 | 182.61 | 60.521 | 0.021037 | 150.76 | 1139.7 |  | 15060 | 182.61 | 7.9654 | 60.521 | 0.021037 | 150.76 | 1139.7 | 988.94
15061 | 7.9671 | 182.62 | 60.52 | 0.021041 | 150.77 | 1139.7 |  | 15061 | 182.62 | 7.9671 | 60.52 | 0.021041 | 150.77 | 1139.7 | 988.93
15062 | 7.9689 | 182.63 | 60.52 | 0.021046 | 150.78 | 1139.7 |  | 15062 | 182.63 | 7.9689 | 60.52 | 0.021046 | 150.78 | 1139.7 | 988.92
15063 | 7.9706 | 182.64 | 60.52 | 0.02105 | 150.79 | 1139.7 |  | 15063 | 182.64 | 7.9706 | 60.52 | 0.02105 | 150.79 | 1139.7 | 988.91
15064 | 7.9724 | 182.65 | 60.52 | 0.021054 | 150.8 | 1139.7 |  | 15064 | 182.65 | 7.9724 | 60.52 | 0.021054 | 150.8 | 1139.7 | 988.9
15065 | 7.9741 | 182.66 | 60.519 | 0.021059 | 150.81 | 1139.7 |  | 15065 | 182.66 | 7.9741 | 60.519 | 0.021059 | 150.81 | 1139.7 | 988.89
15066 | 7.9759 | 182.67 | 60.519 | 0.021063 | 150.82 | 1139.7 |  | 15066 | 182.67 | 7.9759 | 60.519 | 0.021063 | 150.82 | 1139.7 | 988.88
15067 | 7.9776 | 182.68 | 60.519 | 0.021067 | 150.83 | 1139.7 |  | 15067 | 182.68 | 7.9776 | 60.519 | 0.021067 | 150.83 | 1139.7 | 988.87
15068 | 7.9794 | 182.69 | 60.519 | 0.021072 | 150.84 | 1139.7 |  | 15068 | 182.69 | 7.9794 | 60.519 | 0.021072 | 150.84 | 1139.7 | 988.86
15069 | 7.9812 | 182.7 | 60.519 | 0.021076 | 150.85 | 1139.7 |  | 15069 | 182.7 | 7.9812 | 60.519 | 0.021076 | 150.85 | 1139.7 | 988.85
15070 | 7.9829 | 182.71 | 60.518 | 0.02108 | 150.86 | 1139.7 |  | 15070 | 182.71 | 7.9829 | 60.518 | 0.02108 | 150.86 | 1139.7 | 988.84
15071 | 7.9847 | 182.72 | 60.518 | 0.021085 | 150.87 | 1139.7 |  | 15071 | 182.72 | 7.9847 | 60.518 | 0.021085 | 150.87 | 1139.7 | 988.83
15072 | 7.9864 | 182.73 | 60.518 | 0.021089 | 150.88 | 1139.7 |  | 15072 | 182.73 | 7.9864 | 60.518 | 0.021089 | 150.88 | 1139.7 | 988.82
15073 | 7.9882 | 182.74 | 60.518 | 0.021093 | 150.89 | 1139.7 |  | 15073 | 182.74 | 7.9882 | 60.518 | 0.021093 | 150.89 | 1139.7 | 988.81
15074 | 7.9899 | 182.75 | 60.517 | 0.021098 | 150.9 | 1139.7 |  | 15074 | 182.75 | 7.9899 | 60.517 | 0.021098 | 150.9 | 1139.7 | 988.8
15075 | 7.9917 | 182.76 | 60.517 | 0.021102 | 150.91 | 1139.7 |  | 15075 | 182.76 | 7.9917 | 60.517 | 0.021102 | 150.91 | 1139.7 | 988.79
15076 | 7.9934 | 182.77 | 60.517 | 0.021106 | 150.92 | 1139.7 |  | 15076 | 182.77 | 7.9934 | 60.517 | 0.021106 | 150.92 | 1139.7 | 988.78
15077 | 7.9952 | 182.78 | 60.517 | 0.021111 | 150.93 | 1139.8 |  | 15077 | 182.78 | 7.9952 | 60.517 | 0.021111 | 150.93 | 1139.8 | 988.87
15078 | 7.9969 | 182.79 | 60.517 | 0.021115 | 150.94 | 1139.8 |  | 15078 | 182.79 | 7.9969 | 60.517 | 0.021115 | 150.94 | 1139.8 | 988.86
15079 | 7.9987 | 182.8 | 60.516 | 0.021119 | 150.95 | 1139.8 |  | 15079 | 182.8 | 7.9987 | 60.516 | 0.021119 | 150.95 | 1139.8 | 988.85
15080 | 8.0004 | 182.81 | 60.516 | 0.021124 | 150.96 | 1139.8 |  | 15080 | 182.81 | 8.0004 | 60.516 | 0.021124 | 150.96 | 1139.8 | 988.84
15081 | 8.0022 | 182.82 | 60.516 | 0.021128 | 150.97 | 1139.8 |  | 15081 | 182.82 | 8.0022 | 60.516 | 0.021128 | 150.97 | 1139.8 | 988.83
15082 | 8.004 | 182.83 | 60.516 | 0.021132 | 150.98 | 1139.8 |  | 15082 | 182.83 | 8.004 | 60.516 | 0.021132 | 150.98 | 1139.8 | 988.82
15083 | 8.0057 | 182.84 | 60.515 | 0.021137 | 150.99 | 1139.8 |  | 15083 | 182.84 | 8.0057 | 60.515 | 0.021137 | 150.99 | 1139.8 | 988.81
15084 | 8.0075 | 182.85 | 60.515 | 0.021141 | 151 | 1139.8 |  | 15084 | 182.85 | 8.0075 | 60.515 | 0.021141 | 151 | 1139.8 | 988.8
15085 | 8.0092 | 182.86 | 60.515 | 0.021145 | 151.01 | 1139.8 |  | 15085 | 182.86 | 8.0092 | 60.515 | 0.021145 | 151.01 | 1139.8 | 988.79
15086 | 8.011 | 182.87 | 60.515 | 0.02115 | 151.02 | 1139.8 |  | 15086 | 182.87 | 8.011 | 60.515 | 0.02115 | 151.02 | 1139.8 | 988.78
15087 | 8.0128 | 182.88 | 60.515 | 0.021154 | 151.03 | 1139.8 |  | 15087 | 182.88 | 8.0128 | 60.515 | 0.021154 | 151.03 | 1139.8 | 988.77
15088 | 8.0145 | 182.89 | 60.514 | 0.021158 | 151.04 | 1139.8 |  | 15088 | 182.89 | 8.0145 | 60.514 | 0.021158 | 151.04 | 1139.8 | 988.76
15089 | 8.0163 | 182.9 | 60.514 | 0.021163 | 151.05 | 1139.8 |  | 15089 | 182.9 | 8.0163 | 60.514 | 0.021163 | 151.05 | 1139.8 | 988.75
15090 | 8.018 | 182.91 | 60.514 | 0.021167 | 151.06 | 1139.8 |  | 15090 | 182.91 | 8.018 | 60.514 | 0.021167 | 151.06 | 1139.8 | 988.74
15091 | 8.0198 | 182.92 | 60.514 | 0.021171 | 151.07 | 1139.8 |  | 15091 | 182.92 | 8.0198 | 60.514 | 0.021171 | 151.07 | 1139.8 | 988.73
15092 | 8.0215 | 182.93 | 60.513 | 0.021176 | 151.08 | 1139.8 |  | 15092 | 182.93 | 8.0215 | 60.513 | 0.021176 | 151.08 | 1139.8 | 988.72
15093 | 8.0233 | 182.94 | 60.513 | 0.02118 | 151.09 | 1139.8 |  | 15093 | 182.94 | 8.0233 | 60.513 | 0.02118 | 151.09 | 1139.8 | 988.71
15094 | 8.0251 | 182.95 | 60.513 | 0.021184 | 151.1 | 1139.8 |  | 15094 | 182.95 | 8.0251 | 60.513 | 0.021184 | 151.1 | 1139.8 | 988.7
15095 | 8.0268 | 182.96 | 60.513 | 0.021189 | 151.11 | 1139.8 |  | 15095 | 182.96 | 8.0268 | 60.513 | 0.021189 | 151.11 | 1139.8 | 988.69
15096 | 8.0286 | 182.97 | 60.513 | 0.021193 | 151.12 | 1139.8 |  | 15096 | 182.97 | 8.0286 | 60.513 | 0.021193 | 151.12 | 1139.8 | 988.68
15097 | 8.0304 | 182.98 | 60.512 | 0.021197 | 151.13 | 1139.8 |  | 15097 | 182.98 | 8.0304 | 60.512 | 0.021197 | 151.13 | 1139.8 | 988.67
15098 | 8.0321 | 182.99 | 60.512 | 0.021202 | 151.14 | 1139.8 |  | 15098 | 182.99 | 8.0321 | 60.512 | 0.021202 | 151.14 | 1139.8 | 988.66
15099 | 8.0339 | 183 | 60.512 | 0.021206 | 151.15 | 1139.8 |  | 15099 | 183 | 8.0339 | 60.512 | 0.021206 | 151.15 | 1139.8 | 988.65
15100 | 8.0356 | 183.01 | 60.512 | 0.02121 | 151.16 | 1139.8 |  | 15100 | 183.01 | 8.0356 | 60.512 | 0.02121 | 151.16 | 1139.8 | 988.64
15101 | 8.0374 | 183.02 | 60.511 | 0.021215 | 151.17 | 1139.8 |  | 15101 | 183.02 | 8.0374 | 60.511 | 0.021215 | 151.17 | 1139.8 | 988.63
15102 | 8.0392 | 183.03 | 60.511 | 0.021219 | 151.18 | 1139.8 |  | 15102 | 183.03 | 8.0392 | 60.511 | 0.021219 | 151.18 | 1139.8 | 988.62
15103 | 8.0409 | 183.04 | 60.511 | 0.021224 | 151.19 | 1139.9 |  | 15103 | 183.04 | 8.0409 | 60.511 | 0.021224 | 151.19 | 1139.9 | 988.71
15104 | 8.0427 | 183.05 | 60.511 | 0.021228 | 151.2 | 1139.9 |  | 15104 | 183.05 | 8.0427 | 60.511 | 0.021228 | 151.2 | 1139.9 | 988.7
15105 | 8.0445 | 183.06 | 60.511 | 0.021232 | 151.21 | 1139.9 |  | 15105 | 183.06 | 8.0445 | 60.511 | 0.021232 | 151.21 | 1139.9 | 988.69
15106 | 8.0462 | 183.07 | 60.51 | 0.021237 | 151.22 | 1139.9 |  | 15106 | 183.07 | 8.0462 | 60.51 | 0.021237 | 151.22 | 1139.9 | 988.68
15107 | 8.048 | 183.08 | 60.51 | 0.021241 | 151.23 | 1139.9 |  | 15107 | 183.08 | 8.048 | 60.51 | 0.021241 | 151.23 | 1139.9 | 988.67
15108 | 8.0498 | 183.09 | 60.51 | 0.021245 | 151.24 | 1139.9 |  | 15108 | 183.09 | 8.0498 | 60.51 | 0.021245 | 151.24 | 1139.9 | 988.66
15109 | 8.0515 | 183.1 | 60.51 | 0.02125 | 151.25 | 1139.9 |  | 15109 | 183.1 | 8.0515 | 60.51 | 0.02125 | 151.25 | 1139.9 | 988.65
15110 | 8.0533 | 183.11 | 60.509 | 0.021254 | 151.26 | 1139.9 |  | 15110 | 183.11 | 8.0533 | 60.509 | 0.021254 | 151.26 | 1139.9 | 988.64
15111 | 8.055 | 183.12 | 60.509 | 0.021258 | 151.27 | 1139.9 |  | 15111 | 183.12 | 8.055 | 60.509 | 0.021258 | 151.27 | 1139.9 | 988.63
15112 | 8.0568 | 183.13 | 60.509 | 0.021263 | 151.28 | 1139.9 |  | 15112 | 183.13 | 8.0568 | 60.509 | 0.021263 | 151.28 | 1139.9 | 988.62
15113 | 8.0586 | 183.14 | 60.509 | 0.021267 | 151.29 | 1139.9 |  | 15113 | 183.14 | 8.0586 | 60.509 | 0.021267 | 151.29 | 1139.9 | 988.61
15114 | 8.0603 | 183.15 | 60.509 | 0.021272 | 151.3 | 1139.9 |  | 15114 | 183.15 | 8.0603 | 60.509 | 0.021272 | 151.3 | 1139.9 | 988.6
15115 | 8.0621 | 183.16 | 60.508 | 0.021276 | 151.31 | 1139.9 |  | 15115 | 183.16 | 8.0621 | 60.508 | 0.021276 | 151.31 | 1139.9 | 988.59
15116 | 8.0639 | 183.17 | 60.508 | 0.02128 | 151.32 | 1139.9 |  | 15116 | 183.17 | 8.0639 | 60.508 | 0.02128 | 151.32 | 1139.9 | 988.58
15117 | 8.0657 | 183.18 | 60.508 | 0.021285 | 151.33 | 1139.9 |  | 15117 | 183.18 | 8.0657 | 60.508 | 0.021285 | 151.33 | 1139.9 | 988.57
15118 | 8.0674 | 183.19 | 60.508 | 0.021289 | 151.34 | 1139.9 |  | 15118 | 183.19 | 8.0674 | 60.508 | 0.021289 | 151.34 | 1139.9 | 988.56
15119 | 8.0692 | 183.2 | 60.507 | 0.021293 | 151.35 | 1139.9 |  | 15119 | 183.2 | 8.0692 | 60.507 | 0.021293 | 151.35 | 1139.9 | 988.55
15120 | 8.071 | 183.21 | 60.507 | 0.021298 | 151.36 | 1139.9 |  | 15120 | 183.21 | 8.071 | 60.507 | 0.021298 | 151.36 | 1139.9 | 988.54
15121 | 8.0727 | 183.22 | 60.507 | 0.021302 | 151.37 | 1139.9 |  | 15121 | 183.22 | 8.0727 | 60.507 | 0.021302 | 151.37 | 1139.9 | 988.53
15122 | 8.0745 | 183.23 | 60.507 | 0.021306 | 151.38 | 1139.9 |  | 15122 | 183.23 | 8.0745 | 60.507 | 0.021306 | 151.38 | 1139.9 | 988.52
15123 | 8.0763 | 183.24 | 60.507 | 0.021311 | 151.39 | 1139.9 |  | 15123 | 183.24 | 8.0763 | 60.507 | 0.021311 | 151.39 | 1139.9 | 988.51
15124 | 8.078 | 183.25 | 60.506 | 0.021315 | 151.4 | 1139.9 |  | 15124 | 183.25 | 8.078 | 60.506 | 0.021315 | 151.4 | 1139.9 | 988.5
15125 | 8.0798 | 183.26 | 60.506 | 0.02132 | 151.41 | 1139.9 |  | 15125 | 183.26 | 8.0798 | 60.506 | 0.02132 | 151.41 | 1139.9 | 988.49
15126 | 8.0816 | 183.27 | 60.506 | 0.021324 | 151.42 | 1139.9 |  | 15126 | 183.27 | 8.0816 | 60.506 | 0.021324 | 151.42 | 1139.9 | 988.48
15127 | 8.0834 | 183.28 | 60.506 | 0.021328 | 151.43 | 1139.9 |  | 15127 | 183.28 | 8.0834 | 60.506 | 0.021328 | 151.43 | 1139.9 | 988.47
15128 | 8.0851 | 183.29 | 60.505 | 0.021333 | 151.44 | 1140 |  | 15128 | 183.29 | 8.0851 | 60.505 | 0.021333 | 151.44 | 1140 | 988.56
15129 | 8.0869 | 183.3 | 60.505 | 0.021337 | 151.45 | 1140 |  | 15129 | 183.3 | 8.0869 | 60.505 | 0.021337 | 151.45 | 1140 | 988.55
15130 | 8.0887 | 183.31 | 60.505 | 0.021341 | 151.46 | 1140 |  | 15130 | 183.31 | 8.0887 | 60.505 | 0.021341 | 151.46 | 1140 | 988.54
15131 | 8.0904 | 183.32 | 60.505 | 0.021346 | 151.47 | 1140 |  | 15131 | 183.32 | 8.0904 | 60.505 | 0.021346 | 151.47 | 1140 | 988.53
15132 | 8.0922 | 183.33 | 60.505 | 0.02135 | 151.48 | 1140 |  | 15132 | 183.33 | 8.0922 | 60.505 | 0.02135 | 151.48 | 1140 | 988.52
15133 | 8.094 | 183.34 | 60.504 | 0.021355 | 151.49 | 1140 |  | 15133 | 183.34 | 8.094 | 60.504 | 0.021355 | 151.49 | 1140 | 988.51
15134 | 8.0958 | 183.35 | 60.504 | 0.021359 | 151.5 | 1140 |  | 15134 | 183.35 | 8.0958 | 60.504 | 0.021359 | 151.5 | 1140 | 988.5
15135 | 8.0975 | 183.36 | 60.504 | 0.021363 | 151.51 | 1140 |  | 15135 | 183.36 | 8.0975 | 60.504 | 0.021363 | 151.51 | 1140 | 988.49
15136 | 8.0993 | 183.37 | 60.504 | 0.021368 | 151.52 | 1140 |  | 15136 | 183.37 | 8.0993 | 60.504 | 0.021368 | 151.52 | 1140 | 988.48
15137 | 8.1011 | 183.38 | 60.503 | 0.021372 | 151.53 | 1140 |  | 15137 | 183.38 | 8.1011 | 60.503 | 0.021372 | 151.53 | 1140 | 988.47
15138 | 8.1029 | 183.39 | 60.503 | 0.021377 | 151.54 | 1140 |  | 15138 | 183.39 | 8.1029 | 60.503 | 0.021377 | 151.54 | 1140 | 988.46
15139 | 8.1046 | 183.4 | 60.503 | 0.021381 | 151.55 | 1140 |  | 15139 | 183.4 | 8.1046 | 60.503 | 0.021381 | 151.55 | 1140 | 988.45
15140 | 8.1064 | 183.41 | 60.503 | 0.021385 | 151.56 | 1140 |  | 15140 | 183.41 | 8.1064 | 60.503 | 0.021385 | 151.56 | 1140 | 988.44
15141 | 8.1082 | 183.42 | 60.503 | 0.02139 | 151.57 | 1140 |  | 15141 | 183.42 | 8.1082 | 60.503 | 0.02139 | 151.57 | 1140 | 988.43
15142 | 8.11 | 183.43 | 60.502 | 0.021394 | 151.58 | 1140 |  | 15142 | 183.43 | 8.11 | 60.502 | 0.021394 | 151.58 | 1140 | 988.42
15143 | 8.1117 | 183.44 | 60.502 | 0.021398 | 151.59 | 1140 |  | 15143 | 183.44 | 8.1117 | 60.502 | 0.021398 | 151.59 | 1140 | 988.41
15144 | 8.1135 | 183.45 | 60.502 | 0.021403 | 151.6 | 1140 |  | 15144 | 183.45 | 8.1135 | 60.502 | 0.021403 | 151.6 | 1140 | 988.4
15145 | 8.1153 | 183.46 | 60.502 | 0.021407 | 151.61 | 1140 |  | 15145 | 183.46 | 8.1153 | 60.502 | 0.021407 | 151.61 | 1140 | 988.39
15146 | 8.1171 | 183.47 | 60.501 | 0.021412 | 151.62 | 1140 |  | 15146 | 183.47 | 8.1171 | 60.501 | 0.021412 | 151.62 | 1140 | 988.38
15147 | 8.1188 | 183.48 | 60.501 | 0.021416 | 151.63 | 1140 |  | 15147 | 183.48 | 8.1188 | 60.501 | 0.021416 | 151.63 | 1140 | 988.37
15148 | 8.1206 | 183.49 | 60.501 | 0.02142 | 151.64 | 1140 |  | 15148 | 183.49 | 8.1206 | 60.501 | 0.02142 | 151.64 | 1140 | 988.36
15149 | 8.1224 | 183.5 | 60.501 | 0.021425 | 151.65 | 1140 |  | 15149 | 183.5 | 8.1224 | 60.501 | 0.021425 | 151.65 | 1140 | 988.35
15150 | 8.1242 | 183.51 | 60.501 | 0.021429 | 151.66 | 1140 |  | 15150 | 183.51 | 8.1242 | 60.501 | 0.021429 | 151.66 | 1140 | 988.34
15151 | 8.126 | 183.52 | 60.5 | 0.021434 | 151.67 | 1140 |  | 15151 | 183.52 | 8.126 | 60.5 | 0.021434 | 151.67 | 1140 | 988.33
15152 | 8.1277 | 183.53 | 60.5 | 0.021438 | 151.68 | 1140 |  | 15152 | 183.53 | 8.1277 | 60.5 | 0.021438 | 151.68 | 1140 | 988.32
15153 | 8.1295 | 183.54 | 60.5 | 0.021442 | 151.69 | 1140.1 |  | 15153 | 183.54 | 8.1295 | 60.5 | 0.021442 | 151.69 | 1140.1 | 988.41
15154 | 8.1313 | 183.55 | 60.5 | 0.021447 | 151.7 | 1140.1 |  | 15154 | 183.55 | 8.1313 | 60.5 | 0.021447 | 151.7 | 1140.1 | 988.4
15155 | 8.1331 | 183.56 | 60.499 | 0.021451 | 151.71 | 1140.1 |  | 15155 | 183.56 | 8.1331 | 60.499 | 0.021451 | 151.71 | 1140.1 | 988.39
15156 | 8.1349 | 183.57 | 60.499 | 0.021456 | 151.72 | 1140.1 |  | 15156 | 183.57 | 8.1349 | 60.499 | 0.021456 | 151.72 | 1140.1 | 988.38
15157 | 8.1366 | 183.58 | 60.499 | 0.02146 | 151.74 | 1140.1 |  | 15157 | 183.58 | 8.1366 | 60.499 | 0.02146 | 151.74 | 1140.1 | 988.36
15158 | 8.1384 | 183.59 | 60.499 | 0.021464 | 151.75 | 1140.1 |  | 15158 | 183.59 | 8.1384 | 60.499 | 0.021464 | 151.75 | 1140.1 | 988.35
15159 | 8.1402 | 183.6 | 60.499 | 0.021469 | 151.76 | 1140.1 |  | 15159 | 183.6 | 8.1402 | 60.499 | 0.021469 | 151.76 | 1140.1 | 988.34
15160 | 8.142 | 183.61 | 60.498 | 0.021473 | 151.77 | 1140.1 |  | 15160 | 183.61 | 8.142 | 60.498 | 0.021473 | 151.77 | 1140.1 | 988.33
15161 | 8.1438 | 183.62 | 60.498 | 0.021478 | 151.78 | 1140.1 |  | 15161 | 183.62 | 8.1438 | 60.498 | 0.021478 | 151.78 | 1140.1 | 988.32
15162 | 8.1456 | 183.63 | 60.498 | 0.021482 | 151.79 | 1140.1 |  | 15162 | 183.63 | 8.1456 | 60.498 | 0.021482 | 151.79 | 1140.1 | 988.31
15163 | 8.1473 | 183.64 | 60.498 | 0.021486 | 151.8 | 1140.1 |  | 15163 | 183.64 | 8.1473 | 60.498 | 0.021486 | 151.8 | 1140.1 | 988.3
15164 | 8.1491 | 183.65 | 60.497 | 0.021491 | 151.81 | 1140.1 |  | 15164 | 183.65 | 8.1491 | 60.497 | 0.021491 | 151.81 | 1140.1 | 988.29
15165 | 8.1509 | 183.66 | 60.497 | 0.021495 | 151.82 | 1140.1 |  | 15165 | 183.66 | 8.1509 | 60.497 | 0.021495 | 151.82 | 1140.1 | 988.28
15166 | 8.1527 | 183.67 | 60.497 | 0.0215 | 151.83 | 1140.1 |  | 15166 | 183.67 | 8.1527 | 60.497 | 0.0215 | 151.83 | 1140.1 | 988.27
15167 | 8.1545 | 183.68 | 60.497 | 0.021504 | 151.84 | 1140.1 |  | 15167 | 183.68 | 8.1545 | 60.497 | 0.021504 | 151.84 | 1140.1 | 988.26
15168 | 8.1563 | 183.69 | 60.497 | 0.021508 | 151.85 | 1140.1 |  | 15168 | 183.69 | 8.1563 | 60.497 | 0.021508 | 151.85 | 1140.1 | 988.25
15169 | 8.158 | 183.7 | 60.496 | 0.021513 | 151.86 | 1140.1 |  | 15169 | 183.7 | 8.158 | 60.496 | 0.021513 | 151.86 | 1140.1 | 988.24
15170 | 8.1598 | 183.71 | 60.496 | 0.021517 | 151.87 | 1140.1 |  | 15170 | 183.71 | 8.1598 | 60.496 | 0.021517 | 151.87 | 1140.1 | 988.23
15171 | 8.1616 | 183.72 | 60.496 | 0.021522 | 151.88 | 1140.1 |  | 15171 | 183.72 | 8.1616 | 60.496 | 0.021522 | 151.88 | 1140.1 | 988.22
15172 | 8.1634 | 183.73 | 60.496 | 0.021526 | 151.89 | 1140.1 |  | 15172 | 183.73 | 8.1634 | 60.496 | 0.021526 | 151.89 | 1140.1 | 988.21
15173 | 8.1652 | 183.74 | 60.495 | 0.02153 | 151.9 | 1140.1 |  | 15173 | 183.74 | 8.1652 | 60.495 | 0.02153 | 151.9 | 1140.1 | 988.2
15174 | 8.167 | 183.75 | 60.495 | 0.021535 | 151.91 | 1140.1 |  | 15174 | 183.75 | 8.167 | 60.495 | 0.021535 | 151.91 | 1140.1 | 988.19
15175 | 8.1688 | 183.76 | 60.495 | 0.021539 | 151.92 | 1140.1 |  | 15175 | 183.76 | 8.1688 | 60.495 | 0.021539 | 151.92 | 1140.1 | 988.18
15176 | 8.1705 | 183.77 | 60.495 | 0.021544 | 151.93 | 1140.1 |  | 15176 | 183.77 | 8.1705 | 60.495 | 0.021544 | 151.93 | 1140.1 | 988.17
15177 | 8.1723 | 183.78 | 60.495 | 0.021548 | 151.94 | 1140.1 |  | 15177 | 183.78 | 8.1723 | 60.495 | 0.021548 | 151.94 | 1140.1 | 988.16
15178 | 8.1741 | 183.79 | 60.494 | 0.021552 | 151.95 | 1140.2 |  | 15178 | 183.79 | 8.1741 | 60.494 | 0.021552 | 151.95 | 1140.2 | 988.25
15179 | 8.1759 | 183.8 | 60.494 | 0.021557 | 151.96 | 1140.2 |  | 15179 | 183.8 | 8.1759 | 60.494 | 0.021557 | 151.96 | 1140.2 | 988.24
15180 | 8.1777 | 183.81 | 60.494 | 0.021561 | 151.97 | 1140.2 |  | 15180 | 183.81 | 8.1777 | 60.494 | 0.021561 | 151.97 | 1140.2 | 988.23
15181 | 8.1795 | 183.82 | 60.494 | 0.021566 | 151.98 | 1140.2 |  | 15181 | 183.82 | 8.1795 | 60.494 | 0.021566 | 151.98 | 1140.2 | 988.22
15182 | 8.1813 | 183.83 | 60.493 | 0.02157 | 151.99 | 1140.2 |  | 15182 | 183.83 | 8.1813 | 60.493 | 0.02157 | 151.99 | 1140.2 | 988.21
15183 | 8.1831 | 183.84 | 60.493 | 0.021574 | 152 | 1140.2 |  | 15183 | 183.84 | 8.1831 | 60.493 | 0.021574 | 152 | 1140.2 | 988.2
15184 | 8.1849 | 183.85 | 60.493 | 0.021579 | 152.01 | 1140.2 |  | 15184 | 183.85 | 8.1849 | 60.493 | 0.021579 | 152.01 | 1140.2 | 988.19
15185 | 8.1866 | 183.86 | 60.493 | 0.021583 | 152.02 | 1140.2 |  | 15185 | 183.86 | 8.1866 | 60.493 | 0.021583 | 152.02 | 1140.2 | 988.18
15186 | 8.1884 | 183.87 | 60.493 | 0.021588 | 152.03 | 1140.2 |  | 15186 | 183.87 | 8.1884 | 60.493 | 0.021588 | 152.03 | 1140.2 | 988.17
15187 | 8.1902 | 183.88 | 60.492 | 0.021592 | 152.04 | 1140.2 |  | 15187 | 183.88 | 8.1902 | 60.492 | 0.021592 | 152.04 | 1140.2 | 988.16
15188 | 8.192 | 183.89 | 60.492 | 0.021597 | 152.05 | 1140.2 |  | 15188 | 183.89 | 8.192 | 60.492 | 0.021597 | 152.05 | 1140.2 | 988.15
15189 | 8.1938 | 183.9 | 60.492 | 0.021601 | 152.06 | 1140.2 |  | 15189 | 183.9 | 8.1938 | 60.492 | 0.021601 | 152.06 | 1140.2 | 988.14
15190 | 8.1956 | 183.91 | 60.492 | 0.021605 | 152.07 | 1140.2 |  | 15190 | 183.91 | 8.1956 | 60.492 | 0.021605 | 152.07 | 1140.2 | 988.13
15191 | 8.1974 | 183.92 | 60.491 | 0.02161 | 152.08 | 1140.2 |  | 15191 | 183.92 | 8.1974 | 60.491 | 0.02161 | 152.08 | 1140.2 | 988.12
15192 | 8.1992 | 183.93 | 60.491 | 0.021614 | 152.09 | 1140.2 |  | 15192 | 183.93 | 8.1992 | 60.491 | 0.021614 | 152.09 | 1140.2 | 988.11
15193 | 8.201 | 183.94 | 60.491 | 0.021619 | 152.1 | 1140.2 |  | 15193 | 183.94 | 8.201 | 60.491 | 0.021619 | 152.1 | 1140.2 | 988.1
15194 | 8.2028 | 183.95 | 60.491 | 0.021623 | 152.11 | 1140.2 |  | 15194 | 183.95 | 8.2028 | 60.491 | 0.021623 | 152.11 | 1140.2 | 988.09
15195 | 8.2046 | 183.96 | 60.491 | 0.021628 | 152.12 | 1140.2 |  | 15195 | 183.96 | 8.2046 | 60.491 | 0.021628 | 152.12 | 1140.2 | 988.08
15196 | 8.2064 | 183.97 | 60.49 | 0.021632 | 152.13 | 1140.2 |  | 15196 | 183.97 | 8.2064 | 60.49 | 0.021632 | 152.13 | 1140.2 | 988.07
15197 | 8.2082 | 183.98 | 60.49 | 0.021636 | 152.14 | 1140.2 |  | 15197 | 183.98 | 8.2082 | 60.49 | 0.021636 | 152.14 | 1140.2 | 988.06
15198 | 8.2099 | 183.99 | 60.49 | 0.021641 | 152.15 | 1140.2 |  | 15198 | 183.99 | 8.2099 | 60.49 | 0.021641 | 152.15 | 1140.2 | 988.05
15199 | 8.2117 | 184 | 60.49 | 0.021645 | 152.16 | 1140.2 |  | 15199 | 184 | 8.2117 | 60.49 | 0.021645 | 152.16 | 1140.2 | 988.04
15200 | 8.2135 | 184.01 | 60.489 | 0.02165 | 152.17 | 1140.2 |  | 15200 | 184.01 | 8.2135 | 60.489 | 0.02165 | 152.17 | 1140.2 | 988.03
15201 | 8.2153 | 184.02 | 60.489 | 0.021654 | 152.18 | 1140.2 |  | 15201 | 184.02 | 8.2153 | 60.489 | 0.021654 | 152.18 | 1140.2 | 988.02
15202 | 8.2171 | 184.03 | 60.489 | 0.021659 | 152.19 | 1140.2 |  | 15202 | 184.03 | 8.2171 | 60.489 | 0.021659 | 152.19 | 1140.2 | 988.01
15203 | 8.2189 | 184.04 | 60.489 | 0.021663 | 152.2 | 1140.2 |  | 15203 | 184.04 | 8.2189 | 60.489 | 0.021663 | 152.2 | 1140.2 | 988
15204 | 8.2207 | 184.05 | 60.488 | 0.021667 | 152.21 | 1140.3 |  | 15204 | 184.05 | 8.2207 | 60.488 | 0.021667 | 152.21 | 1140.3 | 988.09
15205 | 8.2225 | 184.06 | 60.488 | 0.021672 | 152.22 | 1140.3 |  | 15205 | 184.06 | 8.2225 | 60.488 | 0.021672 | 152.22 | 1140.3 | 988.08
15206 | 8.2243 | 184.07 | 60.488 | 0.021676 | 152.23 | 1140.3 |  | 15206 | 184.07 | 8.2243 | 60.488 | 0.021676 | 152.23 | 1140.3 | 988.07
15207 | 8.2261 | 184.08 | 60.488 | 0.021681 | 152.24 | 1140.3 |  | 15207 | 184.08 | 8.2261 | 60.488 | 0.021681 | 152.24 | 1140.3 | 988.06
15208 | 8.2279 | 184.09 | 60.488 | 0.021685 | 152.25 | 1140.3 |  | 15208 | 184.09 | 8.2279 | 60.488 | 0.021685 | 152.25 | 1140.3 | 988.05
15209 | 8.2297 | 184.1 | 60.487 | 0.02169 | 152.26 | 1140.3 |  | 15209 | 184.1 | 8.2297 | 60.487 | 0.02169 | 152.26 | 1140.3 | 988.04
15210 | 8.2315 | 184.11 | 60.487 | 0.021694 | 152.27 | 1140.3 |  | 15210 | 184.11 | 8.2315 | 60.487 | 0.021694 | 152.27 | 1140.3 | 988.03
15211 | 8.2333 | 184.12 | 60.487 | 0.021698 | 152.28 | 1140.3 |  | 15211 | 184.12 | 8.2333 | 60.487 | 0.021698 | 152.28 | 1140.3 | 988.02
15212 | 8.2351 | 184.13 | 60.487 | 0.021703 | 152.29 | 1140.3 |  | 15212 | 184.13 | 8.2351 | 60.487 | 0.021703 | 152.29 | 1140.3 | 988.01
15213 | 8.2369 | 184.14 | 60.486 | 0.021707 | 152.3 | 1140.3 |  | 15213 | 184.14 | 8.2369 | 60.486 | 0.021707 | 152.3 | 1140.3 | 988
15214 | 8.2387 | 184.15 | 60.486 | 0.021712 | 152.31 | 1140.3 |  | 15214 | 184.15 | 8.2387 | 60.486 | 0.021712 | 152.31 | 1140.3 | 987.99
15215 | 8.2405 | 184.16 | 60.486 | 0.021716 | 152.32 | 1140.3 |  | 15215 | 184.16 | 8.2405 | 60.486 | 0.021716 | 152.32 | 1140.3 | 987.98
15216 | 8.2423 | 184.17 | 60.486 | 0.021721 | 152.33 | 1140.3 |  | 15216 | 184.17 | 8.2423 | 60.486 | 0.021721 | 152.33 | 1140.3 | 987.97
15217 | 8.2441 | 184.18 | 60.486 | 0.021725 | 152.34 | 1140.3 |  | 15217 | 184.18 | 8.2441 | 60.486 | 0.021725 | 152.34 | 1140.3 | 987.96
15218 | 8.2459 | 184.19 | 60.485 | 0.02173 | 152.35 | 1140.3 |  | 15218 | 184.19 | 8.2459 | 60.485 | 0.02173 | 152.35 | 1140.3 | 987.95
15219 | 8.2477 | 184.2 | 60.485 | 0.021734 | 152.36 | 1140.3 |  | 15219 | 184.2 | 8.2477 | 60.485 | 0.021734 | 152.36 | 1140.3 | 987.94
15220 | 8.2495 | 184.21 | 60.485 | 0.021738 | 152.37 | 1140.3 |  | 15220 | 184.21 | 8.2495 | 60.485 | 0.021738 | 152.37 | 1140.3 | 987.93
15221 | 8.2513 | 184.22 | 60.485 | 0.021743 | 152.38 | 1140.3 |  | 15221 | 184.22 | 8.2513 | 60.485 | 0.021743 | 152.38 | 1140.3 | 987.92
15222 | 8.2531 | 184.23 | 60.484 | 0.021747 | 152.39 | 1140.3 |  | 15222 | 184.23 | 8.2531 | 60.484 | 0.021747 | 152.39 | 1140.3 | 987.91
15223 | 8.2549 | 184.24 | 60.484 | 0.021752 | 152.4 | 1140.3 |  | 15223 | 184.24 | 8.2549 | 60.484 | 0.021752 | 152.4 | 1140.3 | 987.9
15224 | 8.2567 | 184.25 | 60.484 | 0.021756 | 152.41 | 1140.3 |  | 15224 | 184.25 | 8.2567 | 60.484 | 0.021756 | 152.41 | 1140.3 | 987.89
15225 | 8.2585 | 184.26 | 60.484 | 0.021761 | 152.42 | 1140.3 |  | 15225 | 184.26 | 8.2585 | 60.484 | 0.021761 | 152.42 | 1140.3 | 987.88
15226 | 8.2603 | 184.27 | 60.484 | 0.021765 | 152.43 | 1140.3 |  | 15226 | 184.27 | 8.2603 | 60.484 | 0.021765 | 152.43 | 1140.3 | 987.87
15227 | 8.2621 | 184.28 | 60.483 | 0.02177 | 152.44 | 1140.3 |  | 15227 | 184.28 | 8.2621 | 60.483 | 0.02177 | 152.44 | 1140.3 | 987.86
15228 | 8.2639 | 184.29 | 60.483 | 0.021774 | 152.45 | 1140.3 |  | 15228 | 184.29 | 8.2639 | 60.483 | 0.021774 | 152.45 | 1140.3 | 987.85
15229 | 8.2657 | 184.3 | 60.483 | 0.021778 | 152.46 | 1140.4 |  | 15229 | 184.3 | 8.2657 | 60.483 | 0.021778 | 152.46 | 1140.4 | 987.94
15230 | 8.2675 | 184.31 | 60.483 | 0.021783 | 152.47 | 1140.4 |  | 15230 | 184.31 | 8.2675 | 60.483 | 0.021783 | 152.47 | 1140.4 | 987.93
15231 | 8.2694 | 184.32 | 60.482 | 0.021787 | 152.48 | 1140.4 |  | 15231 | 184.32 | 8.2694 | 60.482 | 0.021787 | 152.48 | 1140.4 | 987.92
15232 | 8.2712 | 184.33 | 60.482 | 0.021792 | 152.49 | 1140.4 |  | 15232 | 184.33 | 8.2712 | 60.482 | 0.021792 | 152.49 | 1140.4 | 987.91
15233 | 8.273 | 184.34 | 60.482 | 0.021796 | 152.5 | 1140.4 |  | 15233 | 184.34 | 8.273 | 60.482 | 0.021796 | 152.5 | 1140.4 | 987.9
15234 | 8.2748 | 184.35 | 60.482 | 0.021801 | 152.51 | 1140.4 |  | 15234 | 184.35 | 8.2748 | 60.482 | 0.021801 | 152.51 | 1140.4 | 987.89
15235 | 8.2766 | 184.36 | 60.482 | 0.021805 | 152.52 | 1140.4 |  | 15235 | 184.36 | 8.2766 | 60.482 | 0.021805 | 152.52 | 1140.4 | 987.88
15236 | 8.2784 | 184.37 | 60.481 | 0.02181 | 152.53 | 1140.4 |  | 15236 | 184.37 | 8.2784 | 60.481 | 0.02181 | 152.53 | 1140.4 | 987.87
15237 | 8.2802 | 184.38 | 60.481 | 0.021814 | 152.54 | 1140.4 |  | 15237 | 184.38 | 8.2802 | 60.481 | 0.021814 | 152.54 | 1140.4 | 987.86
15238 | 8.282 | 184.39 | 60.481 | 0.021819 | 152.55 | 1140.4 |  | 15238 | 184.39 | 8.282 | 60.481 | 0.021819 | 152.55 | 1140.4 | 987.85
15239 | 8.2838 | 184.4 | 60.481 | 0.021823 | 152.56 | 1140.4 |  | 15239 | 184.4 | 8.2838 | 60.481 | 0.021823 | 152.56 | 1140.4 | 987.84
15240 | 8.2856 | 184.41 | 60.48 | 0.021827 | 152.57 | 1140.4 |  | 15240 | 184.41 | 8.2856 | 60.48 | 0.021827 | 152.57 | 1140.4 | 987.83
15241 | 8.2874 | 184.42 | 60.48 | 0.021832 | 152.58 | 1140.4 |  | 15241 | 184.42 | 8.2874 | 60.48 | 0.021832 | 152.58 | 1140.4 | 987.82
15242 | 8.2892 | 184.43 | 60.48 | 0.021836 | 152.59 | 1140.4 |  | 15242 | 184.43 | 8.2892 | 60.48 | 0.021836 | 152.59 | 1140.4 | 987.81
15243 | 8.291 | 184.44 | 60.48 | 0.021841 | 152.6 | 1140.4 |  | 15243 | 184.44 | 8.291 | 60.48 | 0.021841 | 152.6 | 1140.4 | 987.8
15244 | 8.2929 | 184.45 | 60.48 | 0.021845 | 152.61 | 1140.4 |  | 15244 | 184.45 | 8.2929 | 60.48 | 0.021845 | 152.61 | 1140.4 | 987.79
15245 | 8.2947 | 184.46 | 60.479 | 0.02185 | 152.62 | 1140.4 |  | 15245 | 184.46 | 8.2947 | 60.479 | 0.02185 | 152.62 | 1140.4 | 987.78
15246 | 8.2965 | 184.47 | 60.479 | 0.021854 | 152.63 | 1140.4 |  | 15246 | 184.47 | 8.2965 | 60.479 | 0.021854 | 152.63 | 1140.4 | 987.77
15247 | 8.2983 | 184.48 | 60.479 | 0.021859 | 152.64 | 1140.4 |  | 15247 | 184.48 | 8.2983 | 60.479 | 0.021859 | 152.64 | 1140.4 | 987.76
15248 | 8.3001 | 184.49 | 60.479 | 0.021863 | 152.65 | 1140.4 |  | 15248 | 184.49 | 8.3001 | 60.479 | 0.021863 | 152.65 | 1140.4 | 987.75
15249 | 8.3019 | 184.5 | 60.478 | 0.021868 | 152.66 | 1140.4 |  | 15249 | 184.5 | 8.3019 | 60.478 | 0.021868 | 152.66 | 1140.4 | 987.74
15250 | 8.3037 | 184.51 | 60.478 | 0.021872 | 152.67 | 1140.4 |  | 15250 | 184.51 | 8.3037 | 60.478 | 0.021872 | 152.67 | 1140.4 | 987.73
15251 | 8.3055 | 184.52 | 60.478 | 0.021877 | 152.68 | 1140.4 |  | 15251 | 184.52 | 8.3055 | 60.478 | 0.021877 | 152.68 | 1140.4 | 987.72
15252 | 8.3073 | 184.53 | 60.478 | 0.021881 | 152.69 | 1140.4 |  | 15252 | 184.53 | 8.3073 | 60.478 | 0.021881 | 152.69 | 1140.4 | 987.71
15253 | 8.3092 | 184.54 | 60.478 | 0.021885 | 152.7 | 1140.4 |  | 15253 | 184.54 | 8.3092 | 60.478 | 0.021885 | 152.7 | 1140.4 | 987.7
15254 | 8.311 | 184.55 | 60.477 | 0.02189 | 152.71 | 1140.5 |  | 15254 | 184.55 | 8.311 | 60.477 | 0.02189 | 152.71 | 1140.5 | 987.79
15255 | 8.3128 | 184.56 | 60.477 | 0.021894 | 152.72 | 1140.5 |  | 15255 | 184.56 | 8.3128 | 60.477 | 0.021894 | 152.72 | 1140.5 | 987.78
15256 | 8.3146 | 184.57 | 60.477 | 0.021899 | 152.73 | 1140.5 |  | 15256 | 184.57 | 8.3146 | 60.477 | 0.021899 | 152.73 | 1140.5 | 987.77
15257 | 8.3164 | 184.58 | 60.477 | 0.021903 | 152.74 | 1140.5 |  | 15257 | 184.58 | 8.3164 | 60.477 | 0.021903 | 152.74 | 1140.5 | 987.76
15258 | 8.3182 | 184.59 | 60.476 | 0.021908 | 152.75 | 1140.5 |  | 15258 | 184.59 | 8.3182 | 60.476 | 0.021908 | 152.75 | 1140.5 | 987.75
15259 | 8.32 | 184.6 | 60.476 | 0.021912 | 152.76 | 1140.5 |  | 15259 | 184.6 | 8.32 | 60.476 | 0.021912 | 152.76 | 1140.5 | 987.74
15260 | 8.3219 | 184.61 | 60.476 | 0.021917 | 152.77 | 1140.5 |  | 15260 | 184.61 | 8.3219 | 60.476 | 0.021917 | 152.77 | 1140.5 | 987.73
15261 | 8.3237 | 184.62 | 60.476 | 0.021921 | 152.78 | 1140.5 |  | 15261 | 184.62 | 8.3237 | 60.476 | 0.021921 | 152.78 | 1140.5 | 987.72
15262 | 8.3255 | 184.63 | 60.476 | 0.021926 | 152.79 | 1140.5 |  | 15262 | 184.63 | 8.3255 | 60.476 | 0.021926 | 152.79 | 1140.5 | 987.71
15263 | 8.3273 | 184.64 | 60.475 | 0.02193 | 152.8 | 1140.5 |  | 15263 | 184.64 | 8.3273 | 60.475 | 0.02193 | 152.8 | 1140.5 | 987.7
15264 | 8.3291 | 184.65 | 60.475 | 0.021935 | 152.81 | 1140.5 |  | 15264 | 184.65 | 8.3291 | 60.475 | 0.021935 | 152.81 | 1140.5 | 987.69
15265 | 8.3309 | 184.66 | 60.475 | 0.021939 | 152.82 | 1140.5 |  | 15265 | 184.66 | 8.3309 | 60.475 | 0.021939 | 152.82 | 1140.5 | 987.68
15266 | 8.3327 | 184.67 | 60.475 | 0.021944 | 152.83 | 1140.5 |  | 15266 | 184.67 | 8.3327 | 60.475 | 0.021944 | 152.83 | 1140.5 | 987.67
15267 | 8.3346 | 184.68 | 60.474 | 0.021948 | 152.84 | 1140.5 |  | 15267 | 184.68 | 8.3346 | 60.474 | 0.021948 | 152.84 | 1140.5 | 987.66
15268 | 8.3364 | 184.69 | 60.474 | 0.021953 | 152.85 | 1140.5 |  | 15268 | 184.69 | 8.3364 | 60.474 | 0.021953 | 152.85 | 1140.5 | 987.65
15269 | 8.3382 | 184.7 | 60.474 | 0.021957 | 152.86 | 1140.5 |  | 15269 | 184.7 | 8.3382 | 60.474 | 0.021957 | 152.86 | 1140.5 | 987.64
15270 | 8.34 | 184.71 | 60.474 | 0.021962 | 152.87 | 1140.5 |  | 15270 | 184.71 | 8.34 | 60.474 | 0.021962 | 152.87 | 1140.5 | 987.63
15271 | 8.3418 | 184.72 | 60.473 | 0.021966 | 152.88 | 1140.5 |  | 15271 | 184.72 | 8.3418 | 60.473 | 0.021966 | 152.88 | 1140.5 | 987.62
15272 | 8.3437 | 184.73 | 60.473 | 0.021971 | 152.89 | 1140.5 |  | 15272 | 184.73 | 8.3437 | 60.473 | 0.021971 | 152.89 | 1140.5 | 987.61
15273 | 8.3455 | 184.74 | 60.473 | 0.021975 | 152.9 | 1140.5 |  | 15273 | 184.74 | 8.3455 | 60.473 | 0.021975 | 152.9 | 1140.5 | 987.6
15274 | 8.3473 | 184.75 | 60.473 | 0.021979 | 152.91 | 1140.5 |  | 15274 | 184.75 | 8.3473 | 60.473 | 0.021979 | 152.91 | 1140.5 | 987.59
15275 | 8.3491 | 184.76 | 60.473 | 0.021984 | 152.92 | 1140.5 |  | 15275 | 184.76 | 8.3491 | 60.473 | 0.021984 | 152.92 | 1140.5 | 987.58
15276 | 8.3509 | 184.77 | 60.472 | 0.021988 | 152.93 | 1140.5 |  | 15276 | 184.77 | 8.3509 | 60.472 | 0.021988 | 152.93 | 1140.5 | 987.57
15277 | 8.3528 | 184.78 | 60.472 | 0.021993 | 152.94 | 1140.5 |  | 15277 | 184.78 | 8.3528 | 60.472 | 0.021993 | 152.94 | 1140.5 | 987.56
15278 | 8.3546 | 184.79 | 60.472 | 0.021997 | 152.95 | 1140.5 |  | 15278 | 184.79 | 8.3546 | 60.472 | 0.021997 | 152.95 | 1140.5 | 987.55
15279 | 8.3564 | 184.8 | 60.472 | 0.022002 | 152.96 | 1140.5 |  | 15279 | 184.8 | 8.3564 | 60.472 | 0.022002 | 152.96 | 1140.5 | 987.54
15280 | 8.3582 | 184.81 | 60.471 | 0.022006 | 152.97 | 1140.6 |  | 15280 | 184.81 | 8.3582 | 60.471 | 0.022006 | 152.97 | 1140.6 | 987.63
15281 | 8.36 | 184.82 | 60.471 | 0.022011 | 152.98 | 1140.6 |  | 15281 | 184.82 | 8.36 | 60.471 | 0.022011 | 152.98 | 1140.6 | 987.62
15282 | 8.3619 | 184.83 | 60.471 | 0.022015 | 152.99 | 1140.6 |  | 15282 | 184.83 | 8.3619 | 60.471 | 0.022015 | 152.99 | 1140.6 | 987.61
15283 | 8.3637 | 184.84 | 60.471 | 0.02202 | 153 | 1140.6 |  | 15283 | 184.84 | 8.3637 | 60.471 | 0.02202 | 153 | 1140.6 | 987.6
15284 | 8.3655 | 184.85 | 60.471 | 0.022024 | 153.01 | 1140.6 |  | 15284 | 184.85 | 8.3655 | 60.471 | 0.022024 | 153.01 | 1140.6 | 987.59
15285 | 8.3673 | 184.86 | 60.47 | 0.022029 | 153.02 | 1140.6 |  | 15285 | 184.86 | 8.3673 | 60.47 | 0.022029 | 153.02 | 1140.6 | 987.58
15286 | 8.3692 | 184.87 | 60.47 | 0.022033 | 153.03 | 1140.6 |  | 15286 | 184.87 | 8.3692 | 60.47 | 0.022033 | 153.03 | 1140.6 | 987.57
15287 | 8.371 | 184.88 | 60.47 | 0.022038 | 153.04 | 1140.6 |  | 15287 | 184.88 | 8.371 | 60.47 | 0.022038 | 153.04 | 1140.6 | 987.56
15288 | 8.3728 | 184.89 | 60.47 | 0.022042 | 153.05 | 1140.6 |  | 15288 | 184.89 | 8.3728 | 60.47 | 0.022042 | 153.05 | 1140.6 | 987.55
15289 | 8.3746 | 184.9 | 60.469 | 0.022047 | 153.06 | 1140.6 |  | 15289 | 184.9 | 8.3746 | 60.469 | 0.022047 | 153.06 | 1140.6 | 987.54
15290 | 8.3765 | 184.91 | 60.469 | 0.022051 | 153.07 | 1140.6 |  | 15290 | 184.91 | 8.3765 | 60.469 | 0.022051 | 153.07 | 1140.6 | 987.53
15291 | 8.3783 | 184.92 | 60.469 | 0.022056 | 153.08 | 1140.6 |  | 15291 | 184.92 | 8.3783 | 60.469 | 0.022056 | 153.08 | 1140.6 | 987.52
15292 | 8.3801 | 184.93 | 60.469 | 0.02206 | 153.09 | 1140.6 |  | 15292 | 184.93 | 8.3801 | 60.469 | 0.02206 | 153.09 | 1140.6 | 987.51
15293 | 8.3819 | 184.94 | 60.469 | 0.022065 | 153.1 | 1140.6 |  | 15293 | 184.94 | 8.3819 | 60.469 | 0.022065 | 153.1 | 1140.6 | 987.5
15294 | 8.3838 | 184.95 | 60.468 | 0.022069 | 153.11 | 1140.6 |  | 15294 | 184.95 | 8.3838 | 60.468 | 0.022069 | 153.11 | 1140.6 | 987.49
15295 | 8.3856 | 184.96 | 60.468 | 0.022074 | 153.12 | 1140.6 |  | 15295 | 184.96 | 8.3856 | 60.468 | 0.022074 | 153.12 | 1140.6 | 987.48
15296 | 8.3874 | 184.97 | 60.468 | 0.022078 | 153.13 | 1140.6 |  | 15296 | 184.97 | 8.3874 | 60.468 | 0.022078 | 153.13 | 1140.6 | 987.47
15297 | 8.3892 | 184.98 | 60.468 | 0.022083 | 153.14 | 1140.6 |  | 15297 | 184.98 | 8.3892 | 60.468 | 0.022083 | 153.14 | 1140.6 | 987.46
15298 | 8.3911 | 184.99 | 60.467 | 0.022087 | 153.15 | 1140.6 |  | 15298 | 184.99 | 8.3911 | 60.467 | 0.022087 | 153.15 | 1140.6 | 987.45
15299 | 8.3929 | 185 | 60.467 | 0.022092 | 153.16 | 1140.6 |  | 15299 | 185 | 8.3929 | 60.467 | 0.022092 | 153.16 | 1140.6 | 987.44
15300 | 8.3947 | 185.01 | 60.467 | 0.022096 | 153.17 | 1140.6 |  | 15300 | 185.01 | 8.3947 | 60.467 | 0.022096 | 153.17 | 1140.6 | 987.43
15301 | 8.3966 | 185.02 | 60.467 | 0.022101 | 153.18 | 1140.6 |  | 15301 | 185.02 | 8.3966 | 60.467 | 0.022101 | 153.18 | 1140.6 | 987.42
15302 | 8.3984 | 185.03 | 60.467 | 0.022105 | 153.19 | 1140.6 |  | 15302 | 185.03 | 8.3984 | 60.467 | 0.022105 | 153.19 | 1140.6 | 987.41
15303 | 8.4002 | 185.04 | 60.466 | 0.02211 | 153.2 | 1140.6 |  | 15303 | 185.04 | 8.4002 | 60.466 | 0.02211 | 153.2 | 1140.6 | 987.4
15304 | 8.402 | 185.05 | 60.466 | 0.022114 | 153.21 | 1140.6 |  | 15304 | 185.05 | 8.402 | 60.466 | 0.022114 | 153.21 | 1140.6 | 987.39
15305 | 8.4039 | 185.06 | 60.466 | 0.022119 | 153.22 | 1140.7 |  | 15305 | 185.06 | 8.4039 | 60.466 | 0.022119 | 153.22 | 1140.7 | 987.48
15306 | 8.4057 | 185.07 | 60.466 | 0.022123 | 153.23 | 1140.7 |  | 15306 | 185.07 | 8.4057 | 60.466 | 0.022123 | 153.23 | 1140.7 | 987.47
15307 | 8.4075 | 185.08 | 60.465 | 0.022128 | 153.24 | 1140.7 |  | 15307 | 185.08 | 8.4075 | 60.465 | 0.022128 | 153.24 | 1140.7 | 987.46
15308 | 8.4094 | 185.09 | 60.465 | 0.022132 | 153.25 | 1140.7 |  | 15308 | 185.09 | 8.4094 | 60.465 | 0.022132 | 153.25 | 1140.7 | 987.45
15309 | 8.4112 | 185.1 | 60.465 | 0.022137 | 153.26 | 1140.7 |  | 15309 | 185.1 | 8.4112 | 60.465 | 0.022137 | 153.26 | 1140.7 | 987.44
15310 | 8.413 | 185.11 | 60.465 | 0.022141 | 153.27 | 1140.7 |  | 15310 | 185.11 | 8.413 | 60.465 | 0.022141 | 153.27 | 1140.7 | 987.43
15311 | 8.4149 | 185.12 | 60.465 | 0.022146 | 153.28 | 1140.7 |  | 15311 | 185.12 | 8.4149 | 60.465 | 0.022146 | 153.28 | 1140.7 | 987.42
15312 | 8.4167 | 185.13 | 60.464 | 0.02215 | 153.29 | 1140.7 |  | 15312 | 185.13 | 8.4167 | 60.464 | 0.02215 | 153.29 | 1140.7 | 987.41
15313 | 8.4185 | 185.14 | 60.464 | 0.022155 | 153.3 | 1140.7 |  | 15313 | 185.14 | 8.4185 | 60.464 | 0.022155 | 153.3 | 1140.7 | 987.4
15314 | 8.4204 | 185.15 | 60.464 | 0.022159 | 153.31 | 1140.7 |  | 15314 | 185.15 | 8.4204 | 60.464 | 0.022159 | 153.31 | 1140.7 | 987.39
15315 | 8.4222 | 185.16 | 60.464 | 0.022164 | 153.32 | 1140.7 |  | 15315 | 185.16 | 8.4222 | 60.464 | 0.022164 | 153.32 | 1140.7 | 987.38
15316 | 8.424 | 185.17 | 60.463 | 0.022169 | 153.33 | 1140.7 |  | 15316 | 185.17 | 8.424 | 60.463 | 0.022169 | 153.33 | 1140.7 | 987.37
15317 | 8.4259 | 185.18 | 60.463 | 0.022173 | 153.34 | 1140.7 |  | 15317 | 185.18 | 8.4259 | 60.463 | 0.022173 | 153.34 | 1140.7 | 987.36
15318 | 8.4277 | 185.19 | 60.463 | 0.022178 | 153.35 | 1140.7 |  | 15318 | 185.19 | 8.4277 | 60.463 | 0.022178 | 153.35 | 1140.7 | 987.35
15319 | 8.4295 | 185.2 | 60.463 | 0.022182 | 153.36 | 1140.7 |  | 15319 | 185.2 | 8.4295 | 60.463 | 0.022182 | 153.36 | 1140.7 | 987.34
15320 | 8.4314 | 185.21 | 60.462 | 0.022187 | 153.37 | 1140.7 |  | 15320 | 185.21 | 8.4314 | 60.462 | 0.022187 | 153.37 | 1140.7 | 987.33
15321 | 8.4332 | 185.22 | 60.462 | 0.022191 | 153.38 | 1140.7 |  | 15321 | 185.22 | 8.4332 | 60.462 | 0.022191 | 153.38 | 1140.7 | 987.32
15322 | 8.435 | 185.23 | 60.462 | 0.022196 | 153.39 | 1140.7 |  | 15322 | 185.23 | 8.435 | 60.462 | 0.022196 | 153.39 | 1140.7 | 987.31
15323 | 8.4369 | 185.24 | 60.462 | 0.0222 | 153.4 | 1140.7 |  | 15323 | 185.24 | 8.4369 | 60.462 | 0.0222 | 153.4 | 1140.7 | 987.3
15324 | 8.4387 | 185.25 | 60.462 | 0.022205 | 153.41 | 1140.7 |  | 15324 | 185.25 | 8.4387 | 60.462 | 0.022205 | 153.41 | 1140.7 | 987.29
15325 | 8.4405 | 185.26 | 60.461 | 0.022209 | 153.42 | 1140.7 |  | 15325 | 185.26 | 8.4405 | 60.461 | 0.022209 | 153.42 | 1140.7 | 987.28
15326 | 8.4424 | 185.27 | 60.461 | 0.022214 | 153.43 | 1140.7 |  | 15326 | 185.27 | 8.4424 | 60.461 | 0.022214 | 153.43 | 1140.7 | 987.27
15327 | 8.4442 | 185.28 | 60.461 | 0.022218 | 153.44 | 1140.7 |  | 15327 | 185.28 | 8.4442 | 60.461 | 0.022218 | 153.44 | 1140.7 | 987.26
15328 | 8.446 | 185.29 | 60.461 | 0.022223 | 153.45 | 1140.7 |  | 15328 | 185.29 | 8.446 | 60.461 | 0.022223 | 153.45 | 1140.7 | 987.25
15329 | 8.4479 | 185.3 | 60.46 | 0.022227 | 153.46 | 1140.7 |  | 15329 | 185.3 | 8.4479 | 60.46 | 0.022227 | 153.46 | 1140.7 | 987.24
15330 | 8.4497 | 185.31 | 60.46 | 0.022232 | 153.47 | 1140.8 |  | 15330 | 185.31 | 8.4497 | 60.46 | 0.022232 | 153.47 | 1140.8 | 987.33
15331 | 8.4516 | 185.32 | 60.46 | 0.022236 | 153.48 | 1140.8 |  | 15331 | 185.32 | 8.4516 | 60.46 | 0.022236 | 153.48 | 1140.8 | 987.32
15332 | 8.4534 | 185.33 | 60.46 | 0.022241 | 153.49 | 1140.8 |  | 15332 | 185.33 | 8.4534 | 60.46 | 0.022241 | 153.49 | 1140.8 | 987.31
15333 | 8.4552 | 185.34 | 60.46 | 0.022245 | 153.5 | 1140.8 |  | 15333 | 185.34 | 8.4552 | 60.46 | 0.022245 | 153.5 | 1140.8 | 987.3
15334 | 8.4571 | 185.35 | 60.459 | 0.02225 | 153.51 | 1140.8 |  | 15334 | 185.35 | 8.4571 | 60.459 | 0.02225 | 153.51 | 1140.8 | 987.29
15335 | 8.4589 | 185.36 | 60.459 | 0.022254 | 153.52 | 1140.8 |  | 15335 | 185.36 | 8.4589 | 60.459 | 0.022254 | 153.52 | 1140.8 | 987.28
15336 | 8.4608 | 185.37 | 60.459 | 0.022259 | 153.53 | 1140.8 |  | 15336 | 185.37 | 8.4608 | 60.459 | 0.022259 | 153.53 | 1140.8 | 987.27
15337 | 8.4626 | 185.38 | 60.459 | 0.022264 | 153.54 | 1140.8 |  | 15337 | 185.38 | 8.4626 | 60.459 | 0.022264 | 153.54 | 1140.8 | 987.26
15338 | 8.4644 | 185.39 | 60.458 | 0.022268 | 153.55 | 1140.8 |  | 15338 | 185.39 | 8.4644 | 60.458 | 0.022268 | 153.55 | 1140.8 | 987.25
15339 | 8.4663 | 185.4 | 60.458 | 0.022273 | 153.56 | 1140.8 |  | 15339 | 185.4 | 8.4663 | 60.458 | 0.022273 | 153.56 | 1140.8 | 987.24
15340 | 8.4681 | 185.41 | 60.458 | 0.022277 | 153.57 | 1140.8 |  | 15340 | 185.41 | 8.4681 | 60.458 | 0.022277 | 153.57 | 1140.8 | 987.23
15341 | 8.47 | 185.42 | 60.458 | 0.022282 | 153.58 | 1140.8 |  | 15341 | 185.42 | 8.47 | 60.458 | 0.022282 | 153.58 | 1140.8 | 987.22
15342 | 8.4718 | 185.43 | 60.458 | 0.022286 | 153.59 | 1140.8 |  | 15342 | 185.43 | 8.4718 | 60.458 | 0.022286 | 153.59 | 1140.8 | 987.21
15343 | 8.4737 | 185.44 | 60.457 | 0.022291 | 153.6 | 1140.8 |  | 15343 | 185.44 | 8.4737 | 60.457 | 0.022291 | 153.6 | 1140.8 | 987.2
15344 | 8.4755 | 185.45 | 60.457 | 0.022295 | 153.61 | 1140.8 |  | 15344 | 185.45 | 8.4755 | 60.457 | 0.022295 | 153.61 | 1140.8 | 987.19
15345 | 8.4773 | 185.46 | 60.457 | 0.0223 | 153.62 | 1140.8 |  | 15345 | 185.46 | 8.4773 | 60.457 | 0.0223 | 153.62 | 1140.8 | 987.18
15346 | 8.4792 | 185.47 | 60.457 | 0.022304 | 153.63 | 1140.8 |  | 15346 | 185.47 | 8.4792 | 60.457 | 0.022304 | 153.63 | 1140.8 | 987.17
15347 | 8.481 | 185.48 | 60.456 | 0.022309 | 153.64 | 1140.8 |  | 15347 | 185.48 | 8.481 | 60.456 | 0.022309 | 153.64 | 1140.8 | 987.16
15348 | 8.4829 | 185.49 | 60.456 | 0.022313 | 153.65 | 1140.8 |  | 15348 | 185.49 | 8.4829 | 60.456 | 0.022313 | 153.65 | 1140.8 | 987.15
15349 | 8.4847 | 185.5 | 60.456 | 0.022318 | 153.66 | 1140.8 |  | 15349 | 185.5 | 8.4847 | 60.456 | 0.022318 | 153.66 | 1140.8 | 987.14
15350 | 8.4866 | 185.51 | 60.456 | 0.022322 | 153.67 | 1140.8 |  | 15350 | 185.51 | 8.4866 | 60.456 | 0.022322 | 153.67 | 1140.8 | 987.13
15351 | 8.4884 | 185.52 | 60.456 | 0.022327 | 153.68 | 1140.8 |  | 15351 | 185.52 | 8.4884 | 60.456 | 0.022327 | 153.68 | 1140.8 | 987.12
15352 | 8.4903 | 185.53 | 60.455 | 0.022332 | 153.69 | 1140.8 |  | 15352 | 185.53 | 8.4903 | 60.455 | 0.022332 | 153.69 | 1140.8 | 987.11
15353 | 8.4921 | 185.54 | 60.455 | 0.022336 | 153.7 | 1140.8 |  | 15353 | 185.54 | 8.4921 | 60.455 | 0.022336 | 153.7 | 1140.8 | 987.1
15354 | 8.4939 | 185.55 | 60.455 | 0.022341 | 153.71 | 1140.8 |  | 15354 | 185.55 | 8.4939 | 60.455 | 0.022341 | 153.71 | 1140.8 | 987.09
15355 | 8.4958 | 185.56 | 60.455 | 0.022345 | 153.72 | 1140.8 |  | 15355 | 185.56 | 8.4958 | 60.455 | 0.022345 | 153.72 | 1140.8 | 987.08
15356 | 8.4976 | 185.57 | 60.454 | 0.02235 | 153.73 | 1140.9 |  | 15356 | 185.57 | 8.4976 | 60.454 | 0.02235 | 153.73 | 1140.9 | 987.17
15357 | 8.4995 | 185.58 | 60.454 | 0.022354 | 153.74 | 1140.9 |  | 15357 | 185.58 | 8.4995 | 60.454 | 0.022354 | 153.74 | 1140.9 | 987.16
15358 | 8.5013 | 185.59 | 60.454 | 0.022359 | 153.75 | 1140.9 |  | 15358 | 185.59 | 8.5013 | 60.454 | 0.022359 | 153.75 | 1140.9 | 987.15
15359 | 8.5032 | 185.6 | 60.454 | 0.022363 | 153.76 | 1140.9 |  | 15359 | 185.6 | 8.5032 | 60.454 | 0.022363 | 153.76 | 1140.9 | 987.14
15360 | 8.505 | 185.61 | 60.453 | 0.022368 | 153.77 | 1140.9 |  | 15360 | 185.61 | 8.505 | 60.453 | 0.022368 | 153.77 | 1140.9 | 987.13
15361 | 8.5069 | 185.62 | 60.453 | 0.022373 | 153.78 | 1140.9 |  | 15361 | 185.62 | 8.5069 | 60.453 | 0.022373 | 153.78 | 1140.9 | 987.12
15362 | 8.5087 | 185.63 | 60.453 | 0.022377 | 153.79 | 1140.9 |  | 15362 | 185.63 | 8.5087 | 60.453 | 0.022377 | 153.79 | 1140.9 | 987.11
15363 | 8.5106 | 185.64 | 60.453 | 0.022382 | 153.8 | 1140.9 |  | 15363 | 185.64 | 8.5106 | 60.453 | 0.022382 | 153.8 | 1140.9 | 987.1
15364 | 8.5124 | 185.65 | 60.453 | 0.022386 | 153.81 | 1140.9 |  | 15364 | 185.65 | 8.5124 | 60.453 | 0.022386 | 153.81 | 1140.9 | 987.09
15365 | 8.5143 | 185.66 | 60.452 | 0.022391 | 153.82 | 1140.9 |  | 15365 | 185.66 | 8.5143 | 60.452 | 0.022391 | 153.82 | 1140.9 | 987.08
15366 | 8.5161 | 185.67 | 60.452 | 0.022395 | 153.83 | 1140.9 |  | 15366 | 185.67 | 8.5161 | 60.452 | 0.022395 | 153.83 | 1140.9 | 987.07
15367 | 8.518 | 185.68 | 60.452 | 0.0224 | 153.84 | 1140.9 |  | 15367 | 185.68 | 8.518 | 60.452 | 0.0224 | 153.84 | 1140.9 | 987.06
15368 | 8.5198 | 185.69 | 60.452 | 0.022404 | 153.85 | 1140.9 |  | 15368 | 185.69 | 8.5198 | 60.452 | 0.022404 | 153.85 | 1140.9 | 987.05
15369 | 8.5217 | 185.7 | 60.451 | 0.022409 | 153.86 | 1140.9 |  | 15369 | 185.7 | 8.5217 | 60.451 | 0.022409 | 153.86 | 1140.9 | 987.04
15370 | 8.5235 | 185.71 | 60.451 | 0.022413 | 153.87 | 1140.9 |  | 15370 | 185.71 | 8.5235 | 60.451 | 0.022413 | 153.87 | 1140.9 | 987.03
15371 | 8.5254 | 185.72 | 60.451 | 0.022418 | 153.88 | 1140.9 |  | 15371 | 185.72 | 8.5254 | 60.451 | 0.022418 | 153.88 | 1140.9 | 987.02
15372 | 8.5272 | 185.73 | 60.451 | 0.022423 | 153.89 | 1140.9 |  | 15372 | 185.73 | 8.5272 | 60.451 | 0.022423 | 153.89 | 1140.9 | 987.01
15373 | 8.5291 | 185.74 | 60.451 | 0.022427 | 153.9 | 1140.9 |  | 15373 | 185.74 | 8.5291 | 60.451 | 0.022427 | 153.9 | 1140.9 | 987
15374 | 8.5309 | 185.75 | 60.45 | 0.022432 | 153.91 | 1140.9 |  | 15374 | 185.75 | 8.5309 | 60.45 | 0.022432 | 153.91 | 1140.9 | 986.99
15375 | 8.5328 | 185.76 | 60.45 | 0.022436 | 153.92 | 1140.9 |  | 15375 | 185.76 | 8.5328 | 60.45 | 0.022436 | 153.92 | 1140.9 | 986.98
15376 | 8.5346 | 185.77 | 60.45 | 0.022441 | 153.93 | 1140.9 |  | 15376 | 185.77 | 8.5346 | 60.45 | 0.022441 | 153.93 | 1140.9 | 986.97
15377 | 8.5365 | 185.78 | 60.45 | 0.022445 | 153.94 | 1140.9 |  | 15377 | 185.78 | 8.5365 | 60.45 | 0.022445 | 153.94 | 1140.9 | 986.96
15378 | 8.5384 | 185.79 | 60.449 | 0.02245 | 153.95 | 1140.9 |  | 15378 | 185.79 | 8.5384 | 60.449 | 0.02245 | 153.95 | 1140.9 | 986.95
15379 | 8.5402 | 185.8 | 60.449 | 0.022455 | 153.96 | 1140.9 |  | 15379 | 185.8 | 8.5402 | 60.449 | 0.022455 | 153.96 | 1140.9 | 986.94
15380 | 8.5421 | 185.81 | 60.449 | 0.022459 | 153.97 | 1140.9 |  | 15380 | 185.81 | 8.5421 | 60.449 | 0.022459 | 153.97 | 1140.9 | 986.93
15381 | 8.5439 | 185.82 | 60.449 | 0.022464 | 153.98 | 1141 |  | 15381 | 185.82 | 8.5439 | 60.449 | 0.022464 | 153.98 | 1141 | 987.02
15382 | 8.5458 | 185.83 | 60.449 | 0.022468 | 153.99 | 1141 |  | 15382 | 185.83 | 8.5458 | 60.449 | 0.022468 | 153.99 | 1141 | 987.01
15383 | 8.5476 | 185.84 | 60.448 | 0.022473 | 154 | 1141 |  | 15383 | 185.84 | 8.5476 | 60.448 | 0.022473 | 154 | 1141 | 987
15384 | 8.5495 | 185.85 | 60.448 | 0.022477 | 154.02 | 1141 |  | 15384 | 185.85 | 8.5495 | 60.448 | 0.022477 | 154.02 | 1141 | 986.98
15385 | 8.5513 | 185.86 | 60.448 | 0.022482 | 154.03 | 1141 |  | 15385 | 185.86 | 8.5513 | 60.448 | 0.022482 | 154.03 | 1141 | 986.97
15386 | 8.5532 | 185.87 | 60.448 | 0.022487 | 154.04 | 1141 |  | 15386 | 185.87 | 8.5532 | 60.448 | 0.022487 | 154.04 | 1141 | 986.96
15387 | 8.5551 | 185.88 | 60.447 | 0.022491 | 154.05 | 1141 |  | 15387 | 185.88 | 8.5551 | 60.447 | 0.022491 | 154.05 | 1141 | 986.95
15388 | 8.5569 | 185.89 | 60.447 | 0.022496 | 154.06 | 1141 |  | 15388 | 185.89 | 8.5569 | 60.447 | 0.022496 | 154.06 | 1141 | 986.94
15389 | 8.5588 | 185.9 | 60.447 | 0.0225 | 154.07 | 1141 |  | 15389 | 185.9 | 8.5588 | 60.447 | 0.0225 | 154.07 | 1141 | 986.93
15390 | 8.5606 | 185.91 | 60.447 | 0.022505 | 154.08 | 1141 |  | 15390 | 185.91 | 8.5606 | 60.447 | 0.022505 | 154.08 | 1141 | 986.92
15391 | 8.5625 | 185.92 | 60.447 | 0.022509 | 154.09 | 1141 |  | 15391 | 185.92 | 8.5625 | 60.447 | 0.022509 | 154.09 | 1141 | 986.91
15392 | 8.5644 | 185.93 | 60.446 | 0.022514 | 154.1 | 1141 |  | 15392 | 185.93 | 8.5644 | 60.446 | 0.022514 | 154.1 | 1141 | 986.9
15393 | 8.5662 | 185.94 | 60.446 | 0.022519 | 154.11 | 1141 |  | 15393 | 185.94 | 8.5662 | 60.446 | 0.022519 | 154.11 | 1141 | 986.89
15394 | 8.5681 | 185.95 | 60.446 | 0.022523 | 154.12 | 1141 |  | 15394 | 185.95 | 8.5681 | 60.446 | 0.022523 | 154.12 | 1141 | 986.88
15395 | 8.5699 | 185.96 | 60.446 | 0.022528 | 154.13 | 1141 |  | 15395 | 185.96 | 8.5699 | 60.446 | 0.022528 | 154.13 | 1141 | 986.87
15396 | 8.5718 | 185.97 | 60.445 | 0.022532 | 154.14 | 1141 |  | 15396 | 185.97 | 8.5718 | 60.445 | 0.022532 | 154.14 | 1141 | 986.86
15397 | 8.5737 | 185.98 | 60.445 | 0.022537 | 154.15 | 1141 |  | 15397 | 185.98 | 8.5737 | 60.445 | 0.022537 | 154.15 | 1141 | 986.85
15398 | 8.5755 | 185.99 | 60.445 | 0.022541 | 154.16 | 1141 |  | 15398 | 185.99 | 8.5755 | 60.445 | 0.022541 | 154.16 | 1141 | 986.84
15399 | 8.5774 | 186 | 60.445 | 0.022546 | 154.17 | 1141 |  | 15399 | 186 | 8.5774 | 60.445 | 0.022546 | 154.17 | 1141 | 986.83
15400 | 8.5792 | 186.01 | 60.444 | 0.022551 | 154.18 | 1141 |  | 15400 | 186.01 | 8.5792 | 60.444 | 0.022551 | 154.18 | 1141 | 986.82
15401 | 8.5811 | 186.02 | 60.444 | 0.022555 | 154.19 | 1141 |  | 15401 | 186.02 | 8.5811 | 60.444 | 0.022555 | 154.19 | 1141 | 986.81
15402 | 8.583 | 186.03 | 60.444 | 0.02256 | 154.2 | 1141 |  | 15402 | 186.03 | 8.583 | 60.444 | 0.02256 | 154.2 | 1141 | 986.8
15403 | 8.5848 | 186.04 | 60.444 | 0.022564 | 154.21 | 1141 |  | 15403 | 186.04 | 8.5848 | 60.444 | 0.022564 | 154.21 | 1141 | 986.79
15404 | 8.5867 | 186.05 | 60.444 | 0.022569 | 154.22 | 1141 |  | 15404 | 186.05 | 8.5867 | 60.444 | 0.022569 | 154.22 | 1141 | 986.78
15405 | 8.5886 | 186.06 | 60.443 | 0.022573 | 154.23 | 1141 |  | 15405 | 186.06 | 8.5886 | 60.443 | 0.022573 | 154.23 | 1141 | 986.77
15406 | 8.5904 | 186.07 | 60.443 | 0.022578 | 154.24 | 1141.1 |  | 15406 | 186.07 | 8.5904 | 60.443 | 0.022578 | 154.24 | 1141.1 | 986.86
15407 | 8.5923 | 186.08 | 60.443 | 0.022583 | 154.25 | 1141.1 |  | 15407 | 186.08 | 8.5923 | 60.443 | 0.022583 | 154.25 | 1141.1 | 986.85
15408 | 8.5941 | 186.09 | 60.443 | 0.022587 | 154.26 | 1141.1 |  | 15408 | 186.09 | 8.5941 | 60.443 | 0.022587 | 154.26 | 1141.1 | 986.84
15409 | 8.596 | 186.1 | 60.442 | 0.022592 | 154.27 | 1141.1 |  | 15409 | 186.1 | 8.596 | 60.442 | 0.022592 | 154.27 | 1141.1 | 986.83
15410 | 8.5979 | 186.11 | 60.442 | 0.022596 | 154.28 | 1141.1 |  | 15410 | 186.11 | 8.5979 | 60.442 | 0.022596 | 154.28 | 1141.1 | 986.82
15411 | 8.5997 | 186.12 | 60.442 | 0.022601 | 154.29 | 1141.1 |  | 15411 | 186.12 | 8.5997 | 60.442 | 0.022601 | 154.29 | 1141.1 | 986.81
15412 | 8.6016 | 186.13 | 60.442 | 0.022606 | 154.3 | 1141.1 |  | 15412 | 186.13 | 8.6016 | 60.442 | 0.022606 | 154.3 | 1141.1 | 986.8
15413 | 8.6035 | 186.14 | 60.442 | 0.02261 | 154.31 | 1141.1 |  | 15413 | 186.14 | 8.6035 | 60.442 | 0.02261 | 154.31 | 1141.1 | 986.79
15414 | 8.6053 | 186.15 | 60.441 | 0.022615 | 154.32 | 1141.1 |  | 15414 | 186.15 | 8.6053 | 60.441 | 0.022615 | 154.32 | 1141.1 | 986.78
15415 | 8.6072 | 186.16 | 60.441 | 0.022619 | 154.33 | 1141.1 |  | 15415 | 186.16 | 8.6072 | 60.441 | 0.022619 | 154.33 | 1141.1 | 986.77
15416 | 8.6091 | 186.17 | 60.441 | 0.022624 | 154.34 | 1141.1 |  | 15416 | 186.17 | 8.6091 | 60.441 | 0.022624 | 154.34 | 1141.1 | 986.76
15417 | 8.6109 | 186.18 | 60.441 | 0.022629 | 154.35 | 1141.1 |  | 15417 | 186.18 | 8.6109 | 60.441 | 0.022629 | 154.35 | 1141.1 | 986.75
15418 | 8.6128 | 186.19 | 60.44 | 0.022633 | 154.36 | 1141.1 |  | 15418 | 186.19 | 8.6128 | 60.44 | 0.022633 | 154.36 | 1141.1 | 986.74
15419 | 8.6147 | 186.2 | 60.44 | 0.022638 | 154.37 | 1141.1 |  | 15419 | 186.2 | 8.6147 | 60.44 | 0.022638 | 154.37 | 1141.1 | 986.73
15420 | 8.6165 | 186.21 | 60.44 | 0.022642 | 154.38 | 1141.1 |  | 15420 | 186.21 | 8.6165 | 60.44 | 0.022642 | 154.38 | 1141.1 | 986.72
15421 | 8.6184 | 186.22 | 60.44 | 0.022647 | 154.39 | 1141.1 |  | 15421 | 186.22 | 8.6184 | 60.44 | 0.022647 | 154.39 | 1141.1 | 986.71
15422 | 8.6203 | 186.23 | 60.44 | 0.022652 | 154.4 | 1141.1 |  | 15422 | 186.23 | 8.6203 | 60.44 | 0.022652 | 154.4 | 1141.1 | 986.7
15423 | 8.6222 | 186.24 | 60.439 | 0.022656 | 154.41 | 1141.1 |  | 15423 | 186.24 | 8.6222 | 60.439 | 0.022656 | 154.41 | 1141.1 | 986.69
15424 | 8.624 | 186.25 | 60.439 | 0.022661 | 154.42 | 1141.1 |  | 15424 | 186.25 | 8.624 | 60.439 | 0.022661 | 154.42 | 1141.1 | 986.68
15425 | 8.6259 | 186.26 | 60.439 | 0.022665 | 154.43 | 1141.1 |  | 15425 | 186.26 | 8.6259 | 60.439 | 0.022665 | 154.43 | 1141.1 | 986.67
15426 | 8.6278 | 186.27 | 60.439 | 0.02267 | 154.44 | 1141.1 |  | 15426 | 186.27 | 8.6278 | 60.439 | 0.02267 | 154.44 | 1141.1 | 986.66
15427 | 8.6296 | 186.28 | 60.438 | 0.022674 | 154.45 | 1141.1 |  | 15427 | 186.28 | 8.6296 | 60.438 | 0.022674 | 154.45 | 1141.1 | 986.65
15428 | 8.6315 | 186.29 | 60.438 | 0.022679 | 154.46 | 1141.1 |  | 15428 | 186.29 | 8.6315 | 60.438 | 0.022679 | 154.46 | 1141.1 | 986.64
15429 | 8.6334 | 186.3 | 60.438 | 0.022684 | 154.47 | 1141.1 |  | 15429 | 186.3 | 8.6334 | 60.438 | 0.022684 | 154.47 | 1141.1 | 986.63
15430 | 8.6353 | 186.31 | 60.438 | 0.022688 | 154.48 | 1141.1 |  | 15430 | 186.31 | 8.6353 | 60.438 | 0.022688 | 154.48 | 1141.1 | 986.62
15431 | 8.6371 | 186.32 | 60.437 | 0.022693 | 154.49 | 1141.1 |  | 15431 | 186.32 | 8.6371 | 60.437 | 0.022693 | 154.49 | 1141.1 | 986.61
15432 | 8.639 | 186.33 | 60.437 | 0.022698 | 154.5 | 1141.2 |  | 15432 | 186.33 | 8.639 | 60.437 | 0.022698 | 154.5 | 1141.2 | 986.7
15433 | 8.6409 | 186.34 | 60.437 | 0.022702 | 154.51 | 1141.2 |  | 15433 | 186.34 | 8.6409 | 60.437 | 0.022702 | 154.51 | 1141.2 | 986.69
15434 | 8.6427 | 186.35 | 60.437 | 0.022707 | 154.52 | 1141.2 |  | 15434 | 186.35 | 8.6427 | 60.437 | 0.022707 | 154.52 | 1141.2 | 986.68
15435 | 8.6446 | 186.36 | 60.437 | 0.022711 | 154.53 | 1141.2 |  | 15435 | 186.36 | 8.6446 | 60.437 | 0.022711 | 154.53 | 1141.2 | 986.67
15436 | 8.6465 | 186.37 | 60.436 | 0.022716 | 154.54 | 1141.2 |  | 15436 | 186.37 | 8.6465 | 60.436 | 0.022716 | 154.54 | 1141.2 | 986.66
15437 | 8.6484 | 186.38 | 60.436 | 0.022721 | 154.55 | 1141.2 |  | 15437 | 186.38 | 8.6484 | 60.436 | 0.022721 | 154.55 | 1141.2 | 986.65
15438 | 8.6502 | 186.39 | 60.436 | 0.022725 | 154.56 | 1141.2 |  | 15438 | 186.39 | 8.6502 | 60.436 | 0.022725 | 154.56 | 1141.2 | 986.64
15439 | 8.6521 | 186.4 | 60.436 | 0.02273 | 154.57 | 1141.2 |  | 15439 | 186.4 | 8.6521 | 60.436 | 0.02273 | 154.57 | 1141.2 | 986.63
15440 | 8.654 | 186.41 | 60.435 | 0.022734 | 154.58 | 1141.2 |  | 15440 | 186.41 | 8.654 | 60.435 | 0.022734 | 154.58 | 1141.2 | 986.62
15441 | 8.6559 | 186.42 | 60.435 | 0.022739 | 154.59 | 1141.2 |  | 15441 | 186.42 | 8.6559 | 60.435 | 0.022739 | 154.59 | 1141.2 | 986.61
15442 | 8.6577 | 186.43 | 60.435 | 0.022744 | 154.6 | 1141.2 |  | 15442 | 186.43 | 8.6577 | 60.435 | 0.022744 | 154.6 | 1141.2 | 986.6
15443 | 8.6596 | 186.44 | 60.435 | 0.022748 | 154.61 | 1141.2 |  | 15443 | 186.44 | 8.6596 | 60.435 | 0.022748 | 154.61 | 1141.2 | 986.59
15444 | 8.6615 | 186.45 | 60.435 | 0.022753 | 154.62 | 1141.2 |  | 15444 | 186.45 | 8.6615 | 60.435 | 0.022753 | 154.62 | 1141.2 | 986.58
15445 | 8.6634 | 186.46 | 60.434 | 0.022757 | 154.63 | 1141.2 |  | 15445 | 186.46 | 8.6634 | 60.434 | 0.022757 | 154.63 | 1141.2 | 986.57
15446 | 8.6652 | 186.47 | 60.434 | 0.022762 | 154.64 | 1141.2 |  | 15446 | 186.47 | 8.6652 | 60.434 | 0.022762 | 154.64 | 1141.2 | 986.56
15447 | 8.6671 | 186.48 | 60.434 | 0.022767 | 154.65 | 1141.2 |  | 15447 | 186.48 | 8.6671 | 60.434 | 0.022767 | 154.65 | 1141.2 | 986.55
15448 | 8.669 | 186.49 | 60.434 | 0.022771 | 154.66 | 1141.2 |  | 15448 | 186.49 | 8.669 | 60.434 | 0.022771 | 154.66 | 1141.2 | 986.54
15449 | 8.6709 | 186.5 | 60.433 | 0.022776 | 154.67 | 1141.2 |  | 15449 | 186.5 | 8.6709 | 60.433 | 0.022776 | 154.67 | 1141.2 | 986.53
15450 | 8.6728 | 186.51 | 60.433 | 0.022781 | 154.68 | 1141.2 |  | 15450 | 186.51 | 8.6728 | 60.433 | 0.022781 | 154.68 | 1141.2 | 986.52
15451 | 8.6746 | 186.52 | 60.433 | 0.022785 | 154.69 | 1141.2 |  | 15451 | 186.52 | 8.6746 | 60.433 | 0.022785 | 154.69 | 1141.2 | 986.51
15452 | 8.6765 | 186.53 | 60.433 | 0.02279 | 154.7 | 1141.2 |  | 15452 | 186.53 | 8.6765 | 60.433 | 0.02279 | 154.7 | 1141.2 | 986.5
15453 | 8.6784 | 186.54 | 60.433 | 0.022794 | 154.71 | 1141.2 |  | 15453 | 186.54 | 8.6784 | 60.433 | 0.022794 | 154.71 | 1141.2 | 986.49
15454 | 8.6803 | 186.55 | 60.432 | 0.022799 | 154.72 | 1141.2 |  | 15454 | 186.55 | 8.6803 | 60.432 | 0.022799 | 154.72 | 1141.2 | 986.48
15455 | 8.6822 | 186.56 | 60.432 | 0.022804 | 154.73 | 1141.2 |  | 15455 | 186.56 | 8.6822 | 60.432 | 0.022804 | 154.73 | 1141.2 | 986.47
15456 | 8.684 | 186.57 | 60.432 | 0.022808 | 154.74 | 1141.2 |  | 15456 | 186.57 | 8.684 | 60.432 | 0.022808 | 154.74 | 1141.2 | 986.46
15457 | 8.6859 | 186.58 | 60.432 | 0.022813 | 154.75 | 1141.3 |  | 15457 | 186.58 | 8.6859 | 60.432 | 0.022813 | 154.75 | 1141.3 | 986.55
15458 | 8.6878 | 186.59 | 60.431 | 0.022817 | 154.76 | 1141.3 |  | 15458 | 186.59 | 8.6878 | 60.431 | 0.022817 | 154.76 | 1141.3 | 986.54
15459 | 8.6897 | 186.6 | 60.431 | 0.022822 | 154.77 | 1141.3 |  | 15459 | 186.6 | 8.6897 | 60.431 | 0.022822 | 154.77 | 1141.3 | 986.53
15460 | 8.6916 | 186.61 | 60.431 | 0.022827 | 154.78 | 1141.3 |  | 15460 | 186.61 | 8.6916 | 60.431 | 0.022827 | 154.78 | 1141.3 | 986.52
15461 | 8.6935 | 186.62 | 60.431 | 0.022831 | 154.79 | 1141.3 |  | 15461 | 186.62 | 8.6935 | 60.431 | 0.022831 | 154.79 | 1141.3 | 986.51
15462 | 8.6953 | 186.63 | 60.43 | 0.022836 | 154.8 | 1141.3 |  | 15462 | 186.63 | 8.6953 | 60.43 | 0.022836 | 154.8 | 1141.3 | 986.5
15463 | 8.6972 | 186.64 | 60.43 | 0.022841 | 154.81 | 1141.3 |  | 15463 | 186.64 | 8.6972 | 60.43 | 0.022841 | 154.81 | 1141.3 | 986.49
15464 | 8.6991 | 186.65 | 60.43 | 0.022845 | 154.82 | 1141.3 |  | 15464 | 186.65 | 8.6991 | 60.43 | 0.022845 | 154.82 | 1141.3 | 986.48
15465 | 8.701 | 186.66 | 60.43 | 0.02285 | 154.83 | 1141.3 |  | 15465 | 186.66 | 8.701 | 60.43 | 0.02285 | 154.83 | 1141.3 | 986.47
15466 | 8.7029 | 186.67 | 60.43 | 0.022855 | 154.84 | 1141.3 |  | 15466 | 186.67 | 8.7029 | 60.43 | 0.022855 | 154.84 | 1141.3 | 986.46
15467 | 8.7048 | 186.68 | 60.429 | 0.022859 | 154.85 | 1141.3 |  | 15467 | 186.68 | 8.7048 | 60.429 | 0.022859 | 154.85 | 1141.3 | 986.45
15468 | 8.7066 | 186.69 | 60.429 | 0.022864 | 154.86 | 1141.3 |  | 15468 | 186.69 | 8.7066 | 60.429 | 0.022864 | 154.86 | 1141.3 | 986.44
15469 | 8.7085 | 186.7 | 60.429 | 0.022868 | 154.87 | 1141.3 |  | 15469 | 186.7 | 8.7085 | 60.429 | 0.022868 | 154.87 | 1141.3 | 986.43
15470 | 8.7104 | 186.71 | 60.429 | 0.022873 | 154.88 | 1141.3 |  | 15470 | 186.71 | 8.7104 | 60.429 | 0.022873 | 154.88 | 1141.3 | 986.42
15471 | 8.7123 | 186.72 | 60.428 | 0.022878 | 154.89 | 1141.3 |  | 15471 | 186.72 | 8.7123 | 60.428 | 0.022878 | 154.89 | 1141.3 | 986.41
15472 | 8.7142 | 186.73 | 60.428 | 0.022882 | 154.9 | 1141.3 |  | 15472 | 186.73 | 8.7142 | 60.428 | 0.022882 | 154.9 | 1141.3 | 986.4
15473 | 8.7161 | 186.74 | 60.428 | 0.022887 | 154.91 | 1141.3 |  | 15473 | 186.74 | 8.7161 | 60.428 | 0.022887 | 154.91 | 1141.3 | 986.39
15474 | 8.718 | 186.75 | 60.428 | 0.022892 | 154.92 | 1141.3 |  | 15474 | 186.75 | 8.718 | 60.428 | 0.022892 | 154.92 | 1141.3 | 986.38
15475 | 8.7198 | 186.76 | 60.428 | 0.022896 | 154.93 | 1141.3 |  | 15475 | 186.76 | 8.7198 | 60.428 | 0.022896 | 154.93 | 1141.3 | 986.37
15476 | 8.7217 | 186.77 | 60.427 | 0.022901 | 154.94 | 1141.3 |  | 15476 | 186.77 | 8.7217 | 60.427 | 0.022901 | 154.94 | 1141.3 | 986.36
15477 | 8.7236 | 186.78 | 60.427 | 0.022906 | 154.95 | 1141.3 |  | 15477 | 186.78 | 8.7236 | 60.427 | 0.022906 | 154.95 | 1141.3 | 986.35
15478 | 8.7255 | 186.79 | 60.427 | 0.02291 | 154.96 | 1141.3 |  | 15478 | 186.79 | 8.7255 | 60.427 | 0.02291 | 154.96 | 1141.3 | 986.34
15479 | 8.7274 | 186.8 | 60.427 | 0.022915 | 154.97 | 1141.3 |  | 15479 | 186.8 | 8.7274 | 60.427 | 0.022915 | 154.97 | 1141.3 | 986.33
15480 | 8.7293 | 186.81 | 60.426 | 0.022919 | 154.98 | 1141.3 |  | 15480 | 186.81 | 8.7293 | 60.426 | 0.022919 | 154.98 | 1141.3 | 986.32
15481 | 8.7312 | 186.82 | 60.426 | 0.022924 | 154.99 | 1141.3 |  | 15481 | 186.82 | 8.7312 | 60.426 | 0.022924 | 154.99 | 1141.3 | 986.31
15482 | 8.7331 | 186.83 | 60.426 | 0.022929 | 155 | 1141.4 |  | 15482 | 186.83 | 8.7331 | 60.426 | 0.022929 | 155 | 1141.4 | 986.4
15483 | 8.735 | 186.84 | 60.426 | 0.022933 | 155.01 | 1141.4 |  | 15483 | 186.84 | 8.735 | 60.426 | 0.022933 | 155.01 | 1141.4 | 986.39
15484 | 8.7368 | 186.85 | 60.426 | 0.022938 | 155.02 | 1141.4 |  | 15484 | 186.85 | 8.7368 | 60.426 | 0.022938 | 155.02 | 1141.4 | 986.38
15485 | 8.7387 | 186.86 | 60.425 | 0.022943 | 155.03 | 1141.4 |  | 15485 | 186.86 | 8.7387 | 60.425 | 0.022943 | 155.03 | 1141.4 | 986.37
15486 | 8.7406 | 186.87 | 60.425 | 0.022947 | 155.04 | 1141.4 |  | 15486 | 186.87 | 8.7406 | 60.425 | 0.022947 | 155.04 | 1141.4 | 986.36
15487 | 8.7425 | 186.88 | 60.425 | 0.022952 | 155.05 | 1141.4 |  | 15487 | 186.88 | 8.7425 | 60.425 | 0.022952 | 155.05 | 1141.4 | 986.35
15488 | 8.7444 | 186.89 | 60.425 | 0.022957 | 155.06 | 1141.4 |  | 15488 | 186.89 | 8.7444 | 60.425 | 0.022957 | 155.06 | 1141.4 | 986.34
15489 | 8.7463 | 186.9 | 60.424 | 0.022961 | 155.07 | 1141.4 |  | 15489 | 186.9 | 8.7463 | 60.424 | 0.022961 | 155.07 | 1141.4 | 986.33
15490 | 8.7482 | 186.91 | 60.424 | 0.022966 | 155.08 | 1141.4 |  | 15490 | 186.91 | 8.7482 | 60.424 | 0.022966 | 155.08 | 1141.4 | 986.32
15491 | 8.7501 | 186.92 | 60.424 | 0.022971 | 155.09 | 1141.4 |  | 15491 | 186.92 | 8.7501 | 60.424 | 0.022971 | 155.09 | 1141.4 | 986.31
15492 | 8.752 | 186.93 | 60.424 | 0.022975 | 155.1 | 1141.4 |  | 15492 | 186.93 | 8.752 | 60.424 | 0.022975 | 155.1 | 1141.4 | 986.3
15493 | 8.7539 | 186.94 | 60.423 | 0.02298 | 155.11 | 1141.4 |  | 15493 | 186.94 | 8.7539 | 60.423 | 0.02298 | 155.11 | 1141.4 | 986.29
15494 | 8.7558 | 186.95 | 60.423 | 0.022984 | 155.12 | 1141.4 |  | 15494 | 186.95 | 8.7558 | 60.423 | 0.022984 | 155.12 | 1141.4 | 986.28
15495 | 8.7577 | 186.96 | 60.423 | 0.022989 | 155.13 | 1141.4 |  | 15495 | 186.96 | 8.7577 | 60.423 | 0.022989 | 155.13 | 1141.4 | 986.27
15496 | 8.7596 | 186.97 | 60.423 | 0.022994 | 155.14 | 1141.4 |  | 15496 | 186.97 | 8.7596 | 60.423 | 0.022994 | 155.14 | 1141.4 | 986.26
15497 | 8.7614 | 186.98 | 60.423 | 0.022998 | 155.15 | 1141.4 |  | 15497 | 186.98 | 8.7614 | 60.423 | 0.022998 | 155.15 | 1141.4 | 986.25
15498 | 8.7633 | 186.99 | 60.422 | 0.023003 | 155.16 | 1141.4 |  | 15498 | 186.99 | 8.7633 | 60.422 | 0.023003 | 155.16 | 1141.4 | 986.24
15499 | 8.7652 | 187 | 60.422 | 0.023008 | 155.17 | 1141.4 |  | 15499 | 187 | 8.7652 | 60.422 | 0.023008 | 155.17 | 1141.4 | 986.23
15500 | 8.7671 | 187.01 | 60.422 | 0.023012 | 155.18 | 1141.4 |  | 15500 | 187.01 | 8.7671 | 60.422 | 0.023012 | 155.18 | 1141.4 | 986.22
15501 | 8.769 | 187.02 | 60.422 | 0.023017 | 155.19 | 1141.4 |  | 15501 | 187.02 | 8.769 | 60.422 | 0.023017 | 155.19 | 1141.4 | 986.21
15502 | 8.7709 | 187.03 | 60.421 | 0.023022 | 155.2 | 1141.4 |  | 15502 | 187.03 | 8.7709 | 60.421 | 0.023022 | 155.2 | 1141.4 | 986.2
15503 | 8.7728 | 187.04 | 60.421 | 0.023026 | 155.21 | 1141.4 |  | 15503 | 187.04 | 8.7728 | 60.421 | 0.023026 | 155.21 | 1141.4 | 986.19
15504 | 8.7747 | 187.05 | 60.421 | 0.023031 | 155.22 | 1141.4 |  | 15504 | 187.05 | 8.7747 | 60.421 | 0.023031 | 155.22 | 1141.4 | 986.18
15505 | 8.7766 | 187.06 | 60.421 | 0.023036 | 155.23 | 1141.4 |  | 15505 | 187.06 | 8.7766 | 60.421 | 0.023036 | 155.23 | 1141.4 | 986.17
15506 | 8.7785 | 187.07 | 60.421 | 0.02304 | 155.24 | 1141.4 |  | 15506 | 187.07 | 8.7785 | 60.421 | 0.02304 | 155.24 | 1141.4 | 986.16
15507 | 8.7804 | 187.08 | 60.42 | 0.023045 | 155.25 | 1141.4 |  | 15507 | 187.08 | 8.7804 | 60.42 | 0.023045 | 155.25 | 1141.4 | 986.15
15508 | 8.7823 | 187.09 | 60.42 | 0.02305 | 155.26 | 1141.5 |  | 15508 | 187.09 | 8.7823 | 60.42 | 0.02305 | 155.26 | 1141.5 | 986.24
15509 | 8.7842 | 187.1 | 60.42 | 0.023054 | 155.27 | 1141.5 |  | 15509 | 187.1 | 8.7842 | 60.42 | 0.023054 | 155.27 | 1141.5 | 986.23
15510 | 8.7861 | 187.11 | 60.42 | 0.023059 | 155.28 | 1141.5 |  | 15510 | 187.11 | 8.7861 | 60.42 | 0.023059 | 155.28 | 1141.5 | 986.22
15511 | 8.788 | 187.12 | 60.419 | 0.023064 | 155.29 | 1141.5 |  | 15511 | 187.12 | 8.788 | 60.419 | 0.023064 | 155.29 | 1141.5 | 986.21
15512 | 8.7899 | 187.13 | 60.419 | 0.023068 | 155.3 | 1141.5 |  | 15512 | 187.13 | 8.7899 | 60.419 | 0.023068 | 155.3 | 1141.5 | 986.2
15513 | 8.7918 | 187.14 | 60.419 | 0.023073 | 155.31 | 1141.5 |  | 15513 | 187.14 | 8.7918 | 60.419 | 0.023073 | 155.31 | 1141.5 | 986.19
15514 | 8.7937 | 187.15 | 60.419 | 0.023078 | 155.32 | 1141.5 |  | 15514 | 187.15 | 8.7937 | 60.419 | 0.023078 | 155.32 | 1141.5 | 986.18
15515 | 8.7956 | 187.16 | 60.419 | 0.023082 | 155.33 | 1141.5 |  | 15515 | 187.16 | 8.7956 | 60.419 | 0.023082 | 155.33 | 1141.5 | 986.17
15516 | 8.7975 | 187.17 | 60.418 | 0.023087 | 155.34 | 1141.5 |  | 15516 | 187.17 | 8.7975 | 60.418 | 0.023087 | 155.34 | 1141.5 | 986.16
15517 | 8.7994 | 187.18 | 60.418 | 0.023092 | 155.35 | 1141.5 |  | 15517 | 187.18 | 8.7994 | 60.418 | 0.023092 | 155.35 | 1141.5 | 986.15
15518 | 8.8013 | 187.19 | 60.418 | 0.023096 | 155.36 | 1141.5 |  | 15518 | 187.19 | 8.8013 | 60.418 | 0.023096 | 155.36 | 1141.5 | 986.14
15519 | 8.8032 | 187.2 | 60.418 | 0.023101 | 155.37 | 1141.5 |  | 15519 | 187.2 | 8.8032 | 60.418 | 0.023101 | 155.37 | 1141.5 | 986.13
15520 | 8.8051 | 187.21 | 60.417 | 0.023106 | 155.38 | 1141.5 |  | 15520 | 187.21 | 8.8051 | 60.417 | 0.023106 | 155.38 | 1141.5 | 986.12
15521 | 8.807 | 187.22 | 60.417 | 0.02311 | 155.39 | 1141.5 |  | 15521 | 187.22 | 8.807 | 60.417 | 0.02311 | 155.39 | 1141.5 | 986.11
15522 | 8.8089 | 187.23 | 60.417 | 0.023115 | 155.4 | 1141.5 |  | 15522 | 187.23 | 8.8089 | 60.417 | 0.023115 | 155.4 | 1141.5 | 986.1
15523 | 8.8108 | 187.24 | 60.417 | 0.02312 | 155.41 | 1141.5 |  | 15523 | 187.24 | 8.8108 | 60.417 | 0.02312 | 155.41 | 1141.5 | 986.09
15524 | 8.8127 | 187.25 | 60.416 | 0.023124 | 155.42 | 1141.5 |  | 15524 | 187.25 | 8.8127 | 60.416 | 0.023124 | 155.42 | 1141.5 | 986.08
15525 | 8.8146 | 187.26 | 60.416 | 0.023129 | 155.43 | 1141.5 |  | 15525 | 187.26 | 8.8146 | 60.416 | 0.023129 | 155.43 | 1141.5 | 986.07
15526 | 8.8165 | 187.27 | 60.416 | 0.023134 | 155.44 | 1141.5 |  | 15526 | 187.27 | 8.8165 | 60.416 | 0.023134 | 155.44 | 1141.5 | 986.06
15527 | 8.8185 | 187.28 | 60.416 | 0.023138 | 155.45 | 1141.5 |  | 15527 | 187.28 | 8.8185 | 60.416 | 0.023138 | 155.45 | 1141.5 | 986.05
15528 | 8.8204 | 187.29 | 60.416 | 0.023143 | 155.46 | 1141.5 |  | 15528 | 187.29 | 8.8204 | 60.416 | 0.023143 | 155.46 | 1141.5 | 986.04
15529 | 8.8223 | 187.3 | 60.415 | 0.023148 | 155.47 | 1141.5 |  | 15529 | 187.3 | 8.8223 | 60.415 | 0.023148 | 155.47 | 1141.5 | 986.03
15530 | 8.8242 | 187.31 | 60.415 | 0.023152 | 155.48 | 1141.5 |  | 15530 | 187.31 | 8.8242 | 60.415 | 0.023152 | 155.48 | 1141.5 | 986.02
15531 | 8.8261 | 187.32 | 60.415 | 0.023157 | 155.49 | 1141.5 |  | 15531 | 187.32 | 8.8261 | 60.415 | 0.023157 | 155.49 | 1141.5 | 986.01
15532 | 8.828 | 187.33 | 60.415 | 0.023162 | 155.5 | 1141.5 |  | 15532 | 187.33 | 8.828 | 60.415 | 0.023162 | 155.5 | 1141.5 | 986
15533 | 8.8299 | 187.34 | 60.414 | 0.023167 | 155.51 | 1141.6 |  | 15533 | 187.34 | 8.8299 | 60.414 | 0.023167 | 155.51 | 1141.6 | 986.09
15534 | 8.8318 | 187.35 | 60.414 | 0.023171 | 155.52 | 1141.6 |  | 15534 | 187.35 | 8.8318 | 60.414 | 0.023171 | 155.52 | 1141.6 | 986.08
15535 | 8.8337 | 187.36 | 60.414 | 0.023176 | 155.53 | 1141.6 |  | 15535 | 187.36 | 8.8337 | 60.414 | 0.023176 | 155.53 | 1141.6 | 986.07
15536 | 8.8356 | 187.37 | 60.414 | 0.023181 | 155.54 | 1141.6 |  | 15536 | 187.37 | 8.8356 | 60.414 | 0.023181 | 155.54 | 1141.6 | 986.06
15537 | 8.8375 | 187.38 | 60.414 | 0.023185 | 155.55 | 1141.6 |  | 15537 | 187.38 | 8.8375 | 60.414 | 0.023185 | 155.55 | 1141.6 | 986.05
15538 | 8.8394 | 187.39 | 60.413 | 0.02319 | 155.56 | 1141.6 |  | 15538 | 187.39 | 8.8394 | 60.413 | 0.02319 | 155.56 | 1141.6 | 986.04
15539 | 8.8413 | 187.4 | 60.413 | 0.023195 | 155.57 | 1141.6 |  | 15539 | 187.4 | 8.8413 | 60.413 | 0.023195 | 155.57 | 1141.6 | 986.03
15540 | 8.8433 | 187.41 | 60.413 | 0.023199 | 155.58 | 1141.6 |  | 15540 | 187.41 | 8.8433 | 60.413 | 0.023199 | 155.58 | 1141.6 | 986.02
15541 | 8.8452 | 187.42 | 60.413 | 0.023204 | 155.59 | 1141.6 |  | 15541 | 187.42 | 8.8452 | 60.413 | 0.023204 | 155.59 | 1141.6 | 986.01
15542 | 8.8471 | 187.43 | 60.412 | 0.023209 | 155.6 | 1141.6 |  | 15542 | 187.43 | 8.8471 | 60.412 | 0.023209 | 155.6 | 1141.6 | 986
15543 | 8.849 | 187.44 | 60.412 | 0.023213 | 155.61 | 1141.6 |  | 15543 | 187.44 | 8.849 | 60.412 | 0.023213 | 155.61 | 1141.6 | 985.99
15544 | 8.8509 | 187.45 | 60.412 | 0.023218 | 155.62 | 1141.6 |  | 15544 | 187.45 | 8.8509 | 60.412 | 0.023218 | 155.62 | 1141.6 | 985.98
15545 | 8.8528 | 187.46 | 60.412 | 0.023223 | 155.63 | 1141.6 |  | 15545 | 187.46 | 8.8528 | 60.412 | 0.023223 | 155.63 | 1141.6 | 985.97
15546 | 8.8547 | 187.47 | 60.411 | 0.023227 | 155.64 | 1141.6 |  | 15546 | 187.47 | 8.8547 | 60.411 | 0.023227 | 155.64 | 1141.6 | 985.96
15547 | 8.8566 | 187.48 | 60.411 | 0.023232 | 155.65 | 1141.6 |  | 15547 | 187.48 | 8.8566 | 60.411 | 0.023232 | 155.65 | 1141.6 | 985.95
15548 | 8.8585 | 187.49 | 60.411 | 0.023237 | 155.66 | 1141.6 |  | 15548 | 187.49 | 8.8585 | 60.411 | 0.023237 | 155.66 | 1141.6 | 985.94
15549 | 8.8605 | 187.5 | 60.411 | 0.023242 | 155.67 | 1141.6 |  | 15549 | 187.5 | 8.8605 | 60.411 | 0.023242 | 155.67 | 1141.6 | 985.93
15550 | 8.8624 | 187.51 | 60.411 | 0.023246 | 155.68 | 1141.6 |  | 15550 | 187.51 | 8.8624 | 60.411 | 0.023246 | 155.68 | 1141.6 | 985.92
15551 | 8.8643 | 187.52 | 60.41 | 0.023251 | 155.69 | 1141.6 |  | 15551 | 187.52 | 8.8643 | 60.41 | 0.023251 | 155.69 | 1141.6 | 985.91
15552 | 8.8662 | 187.53 | 60.41 | 0.023256 | 155.7 | 1141.6 |  | 15552 | 187.53 | 8.8662 | 60.41 | 0.023256 | 155.7 | 1141.6 | 985.9
15553 | 8.8681 | 187.54 | 60.41 | 0.02326 | 155.71 | 1141.6 |  | 15553 | 187.54 | 8.8681 | 60.41 | 0.02326 | 155.71 | 1141.6 | 985.89
15554 | 8.87 | 187.55 | 60.41 | 0.023265 | 155.72 | 1141.6 |  | 15554 | 187.55 | 8.87 | 60.41 | 0.023265 | 155.72 | 1141.6 | 985.88
15555 | 8.8719 | 187.56 | 60.409 | 0.02327 | 155.73 | 1141.6 |  | 15555 | 187.56 | 8.8719 | 60.409 | 0.02327 | 155.73 | 1141.6 | 985.87
15556 | 8.8739 | 187.57 | 60.409 | 0.023274 | 155.74 | 1141.6 |  | 15556 | 187.57 | 8.8739 | 60.409 | 0.023274 | 155.74 | 1141.6 | 985.86
15557 | 8.8758 | 187.58 | 60.409 | 0.023279 | 155.75 | 1141.6 |  | 15557 | 187.58 | 8.8758 | 60.409 | 0.023279 | 155.75 | 1141.6 | 985.85
15558 | 8.8777 | 187.59 | 60.409 | 0.023284 | 155.76 | 1141.6 |  | 15558 | 187.59 | 8.8777 | 60.409 | 0.023284 | 155.76 | 1141.6 | 985.84
15559 | 8.8796 | 187.6 | 60.409 | 0.023289 | 155.77 | 1141.7 |  | 15559 | 187.6 | 8.8796 | 60.409 | 0.023289 | 155.77 | 1141.7 | 985.93
15560 | 8.8815 | 187.61 | 60.408 | 0.023293 | 155.78 | 1141.7 |  | 15560 | 187.61 | 8.8815 | 60.408 | 0.023293 | 155.78 | 1141.7 | 985.92
15561 | 8.8834 | 187.62 | 60.408 | 0.023298 | 155.79 | 1141.7 |  | 15561 | 187.62 | 8.8834 | 60.408 | 0.023298 | 155.79 | 1141.7 | 985.91
15562 | 8.8853 | 187.63 | 60.408 | 0.023303 | 155.8 | 1141.7 |  | 15562 | 187.63 | 8.8853 | 60.408 | 0.023303 | 155.8 | 1141.7 | 985.9
15563 | 8.8873 | 187.64 | 60.408 | 0.023307 | 155.81 | 1141.7 |  | 15563 | 187.64 | 8.8873 | 60.408 | 0.023307 | 155.81 | 1141.7 | 985.89
15564 | 8.8892 | 187.65 | 60.407 | 0.023312 | 155.82 | 1141.7 |  | 15564 | 187.65 | 8.8892 | 60.407 | 0.023312 | 155.82 | 1141.7 | 985.88
15565 | 8.8911 | 187.66 | 60.407 | 0.023317 | 155.83 | 1141.7 |  | 15565 | 187.66 | 8.8911 | 60.407 | 0.023317 | 155.83 | 1141.7 | 985.87
15566 | 8.893 | 187.67 | 60.407 | 0.023322 | 155.84 | 1141.7 |  | 15566 | 187.67 | 8.893 | 60.407 | 0.023322 | 155.84 | 1141.7 | 985.86
15567 | 8.8949 | 187.68 | 60.407 | 0.023326 | 155.85 | 1141.7 |  | 15567 | 187.68 | 8.8949 | 60.407 | 0.023326 | 155.85 | 1141.7 | 985.85
15568 | 8.8969 | 187.69 | 60.406 | 0.023331 | 155.86 | 1141.7 |  | 15568 | 187.69 | 8.8969 | 60.406 | 0.023331 | 155.86 | 1141.7 | 985.84
15569 | 8.8988 | 187.7 | 60.406 | 0.023336 | 155.87 | 1141.7 |  | 15569 | 187.7 | 8.8988 | 60.406 | 0.023336 | 155.87 | 1141.7 | 985.83
15570 | 8.9007 | 187.71 | 60.406 | 0.02334 | 155.88 | 1141.7 |  | 15570 | 187.71 | 8.9007 | 60.406 | 0.02334 | 155.88 | 1141.7 | 985.82
15571 | 8.9026 | 187.72 | 60.406 | 0.023345 | 155.89 | 1141.7 |  | 15571 | 187.72 | 8.9026 | 60.406 | 0.023345 | 155.89 | 1141.7 | 985.81
15572 | 8.9045 | 187.73 | 60.406 | 0.02335 | 155.9 | 1141.7 |  | 15572 | 187.73 | 8.9045 | 60.406 | 0.02335 | 155.9 | 1141.7 | 985.8
15573 | 8.9065 | 187.74 | 60.405 | 0.023354 | 155.91 | 1141.7 |  | 15573 | 187.74 | 8.9065 | 60.405 | 0.023354 | 155.91 | 1141.7 | 985.79
15574 | 8.9084 | 187.75 | 60.405 | 0.023359 | 155.92 | 1141.7 |  | 15574 | 187.75 | 8.9084 | 60.405 | 0.023359 | 155.92 | 1141.7 | 985.78
15575 | 8.9103 | 187.76 | 60.405 | 0.023364 | 155.93 | 1141.7 |  | 15575 | 187.76 | 8.9103 | 60.405 | 0.023364 | 155.93 | 1141.7 | 985.77
15576 | 8.9122 | 187.77 | 60.405 | 0.023369 | 155.94 | 1141.7 |  | 15576 | 187.77 | 8.9122 | 60.405 | 0.023369 | 155.94 | 1141.7 | 985.76
15577 | 8.9141 | 187.78 | 60.404 | 0.023373 | 155.95 | 1141.7 |  | 15577 | 187.78 | 8.9141 | 60.404 | 0.023373 | 155.95 | 1141.7 | 985.75
15578 | 8.9161 | 187.79 | 60.404 | 0.023378 | 155.96 | 1141.7 |  | 15578 | 187.79 | 8.9161 | 60.404 | 0.023378 | 155.96 | 1141.7 | 985.74
15579 | 8.918 | 187.8 | 60.404 | 0.023383 | 155.97 | 1141.7 |  | 15579 | 187.8 | 8.918 | 60.404 | 0.023383 | 155.97 | 1141.7 | 985.73
15580 | 8.9199 | 187.81 | 60.404 | 0.023388 | 155.98 | 1141.7 |  | 15580 | 187.81 | 8.9199 | 60.404 | 0.023388 | 155.98 | 1141.7 | 985.72
15581 | 8.9218 | 187.82 | 60.404 | 0.023392 | 155.99 | 1141.7 |  | 15581 | 187.82 | 8.9218 | 60.404 | 0.023392 | 155.99 | 1141.7 | 985.71
15582 | 8.9238 | 187.83 | 60.403 | 0.023397 | 156 | 1141.7 |  | 15582 | 187.83 | 8.9238 | 60.403 | 0.023397 | 156 | 1141.7 | 985.7
15583 | 8.9257 | 187.84 | 60.403 | 0.023402 | 156.01 | 1141.7 |  | 15583 | 187.84 | 8.9257 | 60.403 | 0.023402 | 156.01 | 1141.7 | 985.69
15584 | 8.9276 | 187.85 | 60.403 | 0.023406 | 156.02 | 1141.8 |  | 15584 | 187.85 | 8.9276 | 60.403 | 0.023406 | 156.02 | 1141.8 | 985.78
15585 | 8.9295 | 187.86 | 60.403 | 0.023411 | 156.03 | 1141.8 |  | 15585 | 187.86 | 8.9295 | 60.403 | 0.023411 | 156.03 | 1141.8 | 985.77
15586 | 8.9315 | 187.87 | 60.402 | 0.023416 | 156.04 | 1141.8 |  | 15586 | 187.87 | 8.9315 | 60.402 | 0.023416 | 156.04 | 1141.8 | 985.76
15587 | 8.9334 | 187.88 | 60.402 | 0.023421 | 156.05 | 1141.8 |  | 15587 | 187.88 | 8.9334 | 60.402 | 0.023421 | 156.05 | 1141.8 | 985.75
15588 | 8.9353 | 187.89 | 60.402 | 0.023425 | 156.06 | 1141.8 |  | 15588 | 187.89 | 8.9353 | 60.402 | 0.023425 | 156.06 | 1141.8 | 985.74
15589 | 8.9372 | 187.9 | 60.402 | 0.02343 | 156.07 | 1141.8 |  | 15589 | 187.9 | 8.9372 | 60.402 | 0.02343 | 156.07 | 1141.8 | 985.73
15590 | 8.9392 | 187.91 | 60.401 | 0.023435 | 156.08 | 1141.8 |  | 15590 | 187.91 | 8.9392 | 60.401 | 0.023435 | 156.08 | 1141.8 | 985.72
15591 | 8.9411 | 187.92 | 60.401 | 0.023439 | 156.09 | 1141.8 |  | 15591 | 187.92 | 8.9411 | 60.401 | 0.023439 | 156.09 | 1141.8 | 985.71
15592 | 8.943 | 187.93 | 60.401 | 0.023444 | 156.1 | 1141.8 |  | 15592 | 187.93 | 8.943 | 60.401 | 0.023444 | 156.1 | 1141.8 | 985.7
15593 | 8.945 | 187.94 | 60.401 | 0.023449 | 156.11 | 1141.8 |  | 15593 | 187.94 | 8.945 | 60.401 | 0.023449 | 156.11 | 1141.8 | 985.69
15594 | 8.9469 | 187.95 | 60.401 | 0.023454 | 156.12 | 1141.8 |  | 15594 | 187.95 | 8.9469 | 60.401 | 0.023454 | 156.12 | 1141.8 | 985.68
15595 | 8.9488 | 187.96 | 60.4 | 0.023458 | 156.13 | 1141.8 |  | 15595 | 187.96 | 8.9488 | 60.4 | 0.023458 | 156.13 | 1141.8 | 985.67
15596 | 8.9507 | 187.97 | 60.4 | 0.023463 | 156.14 | 1141.8 |  | 15596 | 187.97 | 8.9507 | 60.4 | 0.023463 | 156.14 | 1141.8 | 985.66
15597 | 8.9527 | 187.98 | 60.4 | 0.023468 | 156.15 | 1141.8 |  | 15597 | 187.98 | 8.9527 | 60.4 | 0.023468 | 156.15 | 1141.8 | 985.65
15598 | 8.9546 | 187.99 | 60.4 | 0.023473 | 156.17 | 1141.8 |  | 15598 | 187.99 | 8.9546 | 60.4 | 0.023473 | 156.17 | 1141.8 | 985.63
15599 | 8.9565 | 188 | 60.399 | 0.023477 | 156.18 | 1141.8 |  | 15599 | 188 | 8.9565 | 60.399 | 0.023477 | 156.18 | 1141.8 | 985.62
15600 | 8.9585 | 188.01 | 60.399 | 0.023482 | 156.19 | 1141.8 |  | 15600 | 188.01 | 8.9585 | 60.399 | 0.023482 | 156.19 | 1141.8 | 985.61
15601 | 8.9604 | 188.02 | 60.399 | 0.023487 | 156.2 | 1141.8 |  | 15601 | 188.02 | 8.9604 | 60.399 | 0.023487 | 156.2 | 1141.8 | 985.6
15602 | 8.9623 | 188.03 | 60.399 | 0.023492 | 156.21 | 1141.8 |  | 15602 | 188.03 | 8.9623 | 60.399 | 0.023492 | 156.21 | 1141.8 | 985.59
15603 | 8.9643 | 188.04 | 60.399 | 0.023496 | 156.22 | 1141.8 |  | 15603 | 188.04 | 8.9643 | 60.399 | 0.023496 | 156.22 | 1141.8 | 985.58
15604 | 8.9662 | 188.05 | 60.398 | 0.023501 | 156.23 | 1141.8 |  | 15604 | 188.05 | 8.9662 | 60.398 | 0.023501 | 156.23 | 1141.8 | 985.57
15605 | 8.9681 | 188.06 | 60.398 | 0.023506 | 156.24 | 1141.8 |  | 15605 | 188.06 | 8.9681 | 60.398 | 0.023506 | 156.24 | 1141.8 | 985.56
15606 | 8.97 | 188.07 | 60.398 | 0.02351 | 156.25 | 1141.8 |  | 15606 | 188.07 | 8.97 | 60.398 | 0.02351 | 156.25 | 1141.8 | 985.55
15607 | 8.972 | 188.08 | 60.398 | 0.023515 | 156.26 | 1141.8 |  | 15607 | 188.08 | 8.972 | 60.398 | 0.023515 | 156.26 | 1141.8 | 985.54
15608 | 8.9739 | 188.09 | 60.397 | 0.02352 | 156.27 | 1141.8 |  | 15608 | 188.09 | 8.9739 | 60.397 | 0.02352 | 156.27 | 1141.8 | 985.53
15609 | 8.9758 | 188.1 | 60.397 | 0.023525 | 156.28 | 1141.8 |  | 15609 | 188.1 | 8.9758 | 60.397 | 0.023525 | 156.28 | 1141.8 | 985.52
15610 | 8.9778 | 188.11 | 60.397 | 0.023529 | 156.29 | 1141.9 |  | 15610 | 188.11 | 8.9778 | 60.397 | 0.023529 | 156.29 | 1141.9 | 985.61
15611 | 8.9797 | 188.12 | 60.397 | 0.023534 | 156.3 | 1141.9 |  | 15611 | 188.12 | 8.9797 | 60.397 | 0.023534 | 156.3 | 1141.9 | 985.6
15612 | 8.9816 | 188.13 | 60.396 | 0.023539 | 156.31 | 1141.9 |  | 15612 | 188.13 | 8.9816 | 60.396 | 0.023539 | 156.31 | 1141.9 | 985.59
15613 | 8.9836 | 188.14 | 60.396 | 0.023544 | 156.32 | 1141.9 |  | 15613 | 188.14 | 8.9836 | 60.396 | 0.023544 | 156.32 | 1141.9 | 985.58
15614 | 8.9855 | 188.15 | 60.396 | 0.023548 | 156.33 | 1141.9 |  | 15614 | 188.15 | 8.9855 | 60.396 | 0.023548 | 156.33 | 1141.9 | 985.57
15615 | 8.9875 | 188.16 | 60.396 | 0.023553 | 156.34 | 1141.9 |  | 15615 | 188.16 | 8.9875 | 60.396 | 0.023553 | 156.34 | 1141.9 | 985.56
15616 | 8.9894 | 188.17 | 60.396 | 0.023558 | 156.35 | 1141.9 |  | 15616 | 188.17 | 8.9894 | 60.396 | 0.023558 | 156.35 | 1141.9 | 985.55
15617 | 8.9913 | 188.18 | 60.395 | 0.023563 | 156.36 | 1141.9 |  | 15617 | 188.18 | 8.9913 | 60.395 | 0.023563 | 156.36 | 1141.9 | 985.54
15618 | 8.9933 | 188.19 | 60.395 | 0.023567 | 156.37 | 1141.9 |  | 15618 | 188.19 | 8.9933 | 60.395 | 0.023567 | 156.37 | 1141.9 | 985.53
15619 | 8.9952 | 188.2 | 60.395 | 0.023572 | 156.38 | 1141.9 |  | 15619 | 188.2 | 8.9952 | 60.395 | 0.023572 | 156.38 | 1141.9 | 985.52
15620 | 8.9971 | 188.21 | 60.395 | 0.023577 | 156.39 | 1141.9 |  | 15620 | 188.21 | 8.9971 | 60.395 | 0.023577 | 156.39 | 1141.9 | 985.51
15621 | 8.9991 | 188.22 | 60.394 | 0.023582 | 156.4 | 1141.9 |  | 15621 | 188.22 | 8.9991 | 60.394 | 0.023582 | 156.4 | 1141.9 | 985.5
15622 | 9.001 | 188.23 | 60.394 | 0.023586 | 156.41 | 1141.9 |  | 15622 | 188.23 | 9.001 | 60.394 | 0.023586 | 156.41 | 1141.9 | 985.49
15623 | 9.003 | 188.24 | 60.394 | 0.023591 | 156.42 | 1141.9 |  | 15623 | 188.24 | 9.003 | 60.394 | 0.023591 | 156.42 | 1141.9 | 985.48
15624 | 9.0049 | 188.25 | 60.394 | 0.023596 | 156.43 | 1141.9 |  | 15624 | 188.25 | 9.0049 | 60.394 | 0.023596 | 156.43 | 1141.9 | 985.47
15625 | 9.0068 | 188.26 | 60.394 | 0.023601 | 156.44 | 1141.9 |  | 15625 | 188.26 | 9.0068 | 60.394 | 0.023601 | 156.44 | 1141.9 | 985.46
15626 | 9.0088 | 188.27 | 60.393 | 0.023605 | 156.45 | 1141.9 |  | 15626 | 188.27 | 9.0088 | 60.393 | 0.023605 | 156.45 | 1141.9 | 985.45
15627 | 9.0107 | 188.28 | 60.393 | 0.02361 | 156.46 | 1141.9 |  | 15627 | 188.28 | 9.0107 | 60.393 | 0.02361 | 156.46 | 1141.9 | 985.44
15628 | 9.0127 | 188.29 | 60.393 | 0.023615 | 156.47 | 1141.9 |  | 15628 | 188.29 | 9.0127 | 60.393 | 0.023615 | 156.47 | 1141.9 | 985.43
15629 | 9.0146 | 188.3 | 60.393 | 0.02362 | 156.48 | 1141.9 |  | 15629 | 188.3 | 9.0146 | 60.393 | 0.02362 | 156.48 | 1141.9 | 985.42
15630 | 9.0165 | 188.31 | 60.392 | 0.023624 | 156.49 | 1141.9 |  | 15630 | 188.31 | 9.0165 | 60.392 | 0.023624 | 156.49 | 1141.9 | 985.41
15631 | 9.0185 | 188.32 | 60.392 | 0.023629 | 156.5 | 1141.9 |  | 15631 | 188.32 | 9.0185 | 60.392 | 0.023629 | 156.5 | 1141.9 | 985.4
15632 | 9.0204 | 188.33 | 60.392 | 0.023634 | 156.51 | 1141.9 |  | 15632 | 188.33 | 9.0204 | 60.392 | 0.023634 | 156.51 | 1141.9 | 985.39
15633 | 9.0224 | 188.34 | 60.392 | 0.023639 | 156.52 | 1141.9 |  | 15633 | 188.34 | 9.0224 | 60.392 | 0.023639 | 156.52 | 1141.9 | 985.38
15634 | 9.0243 | 188.35 | 60.391 | 0.023644 | 156.53 | 1141.9 |  | 15634 | 188.35 | 9.0243 | 60.391 | 0.023644 | 156.53 | 1141.9 | 985.37
15635 | 9.0262 | 188.36 | 60.391 | 0.023648 | 156.54 | 1142 |  | 15635 | 188.36 | 9.0262 | 60.391 | 0.023648 | 156.54 | 1142 | 985.46
15636 | 9.0282 | 188.37 | 60.391 | 0.023653 | 156.55 | 1142 |  | 15636 | 188.37 | 9.0282 | 60.391 | 0.023653 | 156.55 | 1142 | 985.45
15637 | 9.0301 | 188.38 | 60.391 | 0.023658 | 156.56 | 1142 |  | 15637 | 188.38 | 9.0301 | 60.391 | 0.023658 | 156.56 | 1142 | 985.44
15638 | 9.0321 | 188.39 | 60.391 | 0.023663 | 156.57 | 1142 |  | 15638 | 188.39 | 9.0321 | 60.391 | 0.023663 | 156.57 | 1142 | 985.43
15639 | 9.034 | 188.4 | 60.39 | 0.023667 | 156.58 | 1142 |  | 15639 | 188.4 | 9.034 | 60.39 | 0.023667 | 156.58 | 1142 | 985.42
15640 | 9.036 | 188.41 | 60.39 | 0.023672 | 156.59 | 1142 |  | 15640 | 188.41 | 9.036 | 60.39 | 0.023672 | 156.59 | 1142 | 985.41
15641 | 9.0379 | 188.42 | 60.39 | 0.023677 | 156.6 | 1142 |  | 15641 | 188.42 | 9.0379 | 60.39 | 0.023677 | 156.6 | 1142 | 985.4
15642 | 9.0398 | 188.43 | 60.39 | 0.023682 | 156.61 | 1142 |  | 15642 | 188.43 | 9.0398 | 60.39 | 0.023682 | 156.61 | 1142 | 985.39
15643 | 9.0418 | 188.44 | 60.389 | 0.023686 | 156.62 | 1142 |  | 15643 | 188.44 | 9.0418 | 60.389 | 0.023686 | 156.62 | 1142 | 985.38
15644 | 9.0437 | 188.45 | 60.389 | 0.023691 | 156.63 | 1142 |  | 15644 | 188.45 | 9.0437 | 60.389 | 0.023691 | 156.63 | 1142 | 985.37
15645 | 9.0457 | 188.46 | 60.389 | 0.023696 | 156.64 | 1142 |  | 15645 | 188.46 | 9.0457 | 60.389 | 0.023696 | 156.64 | 1142 | 985.36
15646 | 9.0476 | 188.47 | 60.389 | 0.023701 | 156.65 | 1142 |  | 15646 | 188.47 | 9.0476 | 60.389 | 0.023701 | 156.65 | 1142 | 985.35
15647 | 9.0496 | 188.48 | 60.389 | 0.023705 | 156.66 | 1142 |  | 15647 | 188.48 | 9.0496 | 60.389 | 0.023705 | 156.66 | 1142 | 985.34
15648 | 9.0515 | 188.49 | 60.388 | 0.02371 | 156.67 | 1142 |  | 15648 | 188.49 | 9.0515 | 60.388 | 0.02371 | 156.67 | 1142 | 985.33
15649 | 9.0535 | 188.5 | 60.388 | 0.023715 | 156.68 | 1142 |  | 15649 | 188.5 | 9.0535 | 60.388 | 0.023715 | 156.68 | 1142 | 985.32
15650 | 9.0554 | 188.51 | 60.388 | 0.02372 | 156.69 | 1142 |  | 15650 | 188.51 | 9.0554 | 60.388 | 0.02372 | 156.69 | 1142 | 985.31
15651 | 9.0574 | 188.52 | 60.388 | 0.023725 | 156.7 | 1142 |  | 15651 | 188.52 | 9.0574 | 60.388 | 0.023725 | 156.7 | 1142 | 985.3
15652 | 9.0593 | 188.53 | 60.387 | 0.023729 | 156.71 | 1142 |  | 15652 | 188.53 | 9.0593 | 60.387 | 0.023729 | 156.71 | 1142 | 985.29
15653 | 9.0613 | 188.54 | 60.387 | 0.023734 | 156.72 | 1142 |  | 15653 | 188.54 | 9.0613 | 60.387 | 0.023734 | 156.72 | 1142 | 985.28
15654 | 9.0632 | 188.55 | 60.387 | 0.023739 | 156.73 | 1142 |  | 15654 | 188.55 | 9.0632 | 60.387 | 0.023739 | 156.73 | 1142 | 985.27
15655 | 9.0652 | 188.56 | 60.387 | 0.023744 | 156.74 | 1142 |  | 15655 | 188.56 | 9.0652 | 60.387 | 0.023744 | 156.74 | 1142 | 985.26
15656 | 9.0671 | 188.57 | 60.386 | 0.023748 | 156.75 | 1142 |  | 15656 | 188.57 | 9.0671 | 60.386 | 0.023748 | 156.75 | 1142 | 985.25
15657 | 9.0691 | 188.58 | 60.386 | 0.023753 | 156.76 | 1142 |  | 15657 | 188.58 | 9.0691 | 60.386 | 0.023753 | 156.76 | 1142 | 985.24
15658 | 9.071 | 188.59 | 60.386 | 0.023758 | 156.77 | 1142 |  | 15658 | 188.59 | 9.071 | 60.386 | 0.023758 | 156.77 | 1142 | 985.23
15659 | 9.073 | 188.6 | 60.386 | 0.023763 | 156.78 | 1142 |  | 15659 | 188.6 | 9.073 | 60.386 | 0.023763 | 156.78 | 1142 | 985.22
15660 | 9.0749 | 188.61 | 60.386 | 0.023768 | 156.79 | 1142 |  | 15660 | 188.61 | 9.0749 | 60.386 | 0.023768 | 156.79 | 1142 | 985.21
15661 | 9.0769 | 188.62 | 60.385 | 0.023772 | 156.8 | 1142.1 |  | 15661 | 188.62 | 9.0769 | 60.385 | 0.023772 | 156.8 | 1142.1 | 985.3
15662 | 9.0788 | 188.63 | 60.385 | 0.023777 | 156.81 | 1142.1 |  | 15662 | 188.63 | 9.0788 | 60.385 | 0.023777 | 156.81 | 1142.1 | 985.29
15663 | 9.0808 | 188.64 | 60.385 | 0.023782 | 156.82 | 1142.1 |  | 15663 | 188.64 | 9.0808 | 60.385 | 0.023782 | 156.82 | 1142.1 | 985.28
15664 | 9.0827 | 188.65 | 60.385 | 0.023787 | 156.83 | 1142.1 |  | 15664 | 188.65 | 9.0827 | 60.385 | 0.023787 | 156.83 | 1142.1 | 985.27
15665 | 9.0847 | 188.66 | 60.384 | 0.023792 | 156.84 | 1142.1 |  | 15665 | 188.66 | 9.0847 | 60.384 | 0.023792 | 156.84 | 1142.1 | 985.26
15666 | 9.0866 | 188.67 | 60.384 | 0.023796 | 156.85 | 1142.1 |  | 15666 | 188.67 | 9.0866 | 60.384 | 0.023796 | 156.85 | 1142.1 | 985.25
15667 | 9.0886 | 188.68 | 60.384 | 0.023801 | 156.86 | 1142.1 |  | 15667 | 188.68 | 9.0886 | 60.384 | 0.023801 | 156.86 | 1142.1 | 985.24
15668 | 9.0905 | 188.69 | 60.384 | 0.023806 | 156.87 | 1142.1 |  | 15668 | 188.69 | 9.0905 | 60.384 | 0.023806 | 156.87 | 1142.1 | 985.23
15669 | 9.0925 | 188.7 | 60.384 | 0.023811 | 156.88 | 1142.1 |  | 15669 | 188.7 | 9.0925 | 60.384 | 0.023811 | 156.88 | 1142.1 | 985.22
15670 | 9.0945 | 188.71 | 60.383 | 0.023815 | 156.89 | 1142.1 |  | 15670 | 188.71 | 9.0945 | 60.383 | 0.023815 | 156.89 | 1142.1 | 985.21
15671 | 9.0964 | 188.72 | 60.383 | 0.02382 | 156.9 | 1142.1 |  | 15671 | 188.72 | 9.0964 | 60.383 | 0.02382 | 156.9 | 1142.1 | 985.2
15672 | 9.0984 | 188.73 | 60.383 | 0.023825 | 156.91 | 1142.1 |  | 15672 | 188.73 | 9.0984 | 60.383 | 0.023825 | 156.91 | 1142.1 | 985.19
15673 | 9.1003 | 188.74 | 60.383 | 0.02383 | 156.92 | 1142.1 |  | 15673 | 188.74 | 9.1003 | 60.383 | 0.02383 | 156.92 | 1142.1 | 985.18
15674 | 9.1023 | 188.75 | 60.382 | 0.023835 | 156.93 | 1142.1 |  | 15674 | 188.75 | 9.1023 | 60.382 | 0.023835 | 156.93 | 1142.1 | 985.17
15675 | 9.1042 | 188.76 | 60.382 | 0.023839 | 156.94 | 1142.1 |  | 15675 | 188.76 | 9.1042 | 60.382 | 0.023839 | 156.94 | 1142.1 | 985.16
15676 | 9.1062 | 188.77 | 60.382 | 0.023844 | 156.95 | 1142.1 |  | 15676 | 188.77 | 9.1062 | 60.382 | 0.023844 | 156.95 | 1142.1 | 985.15
15677 | 9.1081 | 188.78 | 60.382 | 0.023849 | 156.96 | 1142.1 |  | 15677 | 188.78 | 9.1081 | 60.382 | 0.023849 | 156.96 | 1142.1 | 985.14
15678 | 9.1101 | 188.79 | 60.381 | 0.023854 | 156.97 | 1142.1 |  | 15678 | 188.79 | 9.1101 | 60.381 | 0.023854 | 156.97 | 1142.1 | 985.13
15679 | 9.1121 | 188.8 | 60.381 | 0.023859 | 156.98 | 1142.1 |  | 15679 | 188.8 | 9.1121 | 60.381 | 0.023859 | 156.98 | 1142.1 | 985.12
15680 | 9.114 | 188.81 | 60.381 | 0.023863 | 156.99 | 1142.1 |  | 15680 | 188.81 | 9.114 | 60.381 | 0.023863 | 156.99 | 1142.1 | 985.11
15681 | 9.116 | 188.82 | 60.381 | 0.023868 | 157 | 1142.1 |  | 15681 | 188.82 | 9.116 | 60.381 | 0.023868 | 157 | 1142.1 | 985.1
15682 | 9.1179 | 188.83 | 60.381 | 0.023873 | 157.01 | 1142.1 |  | 15682 | 188.83 | 9.1179 | 60.381 | 0.023873 | 157.01 | 1142.1 | 985.09
15683 | 9.1199 | 188.84 | 60.38 | 0.023878 | 157.02 | 1142.1 |  | 15683 | 188.84 | 9.1199 | 60.38 | 0.023878 | 157.02 | 1142.1 | 985.08
15684 | 9.1219 | 188.85 | 60.38 | 0.023883 | 157.03 | 1142.1 |  | 15684 | 188.85 | 9.1219 | 60.38 | 0.023883 | 157.03 | 1142.1 | 985.07
15685 | 9.1238 | 188.86 | 60.38 | 0.023887 | 157.04 | 1142.1 |  | 15685 | 188.86 | 9.1238 | 60.38 | 0.023887 | 157.04 | 1142.1 | 985.06
15686 | 9.1258 | 188.87 | 60.38 | 0.023892 | 157.05 | 1142.2 |  | 15686 | 188.87 | 9.1258 | 60.38 | 0.023892 | 157.05 | 1142.2 | 985.15
15687 | 9.1277 | 188.88 | 60.379 | 0.023897 | 157.06 | 1142.2 |  | 15687 | 188.88 | 9.1277 | 60.379 | 0.023897 | 157.06 | 1142.2 | 985.14
15688 | 9.1297 | 188.89 | 60.379 | 0.023902 | 157.07 | 1142.2 |  | 15688 | 188.89 | 9.1297 | 60.379 | 0.023902 | 157.07 | 1142.2 | 985.13
15689 | 9.1317 | 188.9 | 60.379 | 0.023907 | 157.08 | 1142.2 |  | 15689 | 188.9 | 9.1317 | 60.379 | 0.023907 | 157.08 | 1142.2 | 985.12
15690 | 9.1336 | 188.91 | 60.379 | 0.023911 | 157.09 | 1142.2 |  | 15690 | 188.91 | 9.1336 | 60.379 | 0.023911 | 157.09 | 1142.2 | 985.11
15691 | 9.1356 | 188.92 | 60.378 | 0.023916 | 157.1 | 1142.2 |  | 15691 | 188.92 | 9.1356 | 60.378 | 0.023916 | 157.1 | 1142.2 | 985.1
15692 | 9.1375 | 188.93 | 60.378 | 0.023921 | 157.11 | 1142.2 |  | 15692 | 188.93 | 9.1375 | 60.378 | 0.023921 | 157.11 | 1142.2 | 985.09
15693 | 9.1395 | 188.94 | 60.378 | 0.023926 | 157.12 | 1142.2 |  | 15693 | 188.94 | 9.1395 | 60.378 | 0.023926 | 157.12 | 1142.2 | 985.08
15694 | 9.1415 | 188.95 | 60.378 | 0.023931 | 157.13 | 1142.2 |  | 15694 | 188.95 | 9.1415 | 60.378 | 0.023931 | 157.13 | 1142.2 | 985.07
15695 | 9.1434 | 188.96 | 60.378 | 0.023935 | 157.14 | 1142.2 |  | 15695 | 188.96 | 9.1434 | 60.378 | 0.023935 | 157.14 | 1142.2 | 985.06
15696 | 9.1454 | 188.97 | 60.377 | 0.02394 | 157.15 | 1142.2 |  | 15696 | 188.97 | 9.1454 | 60.377 | 0.02394 | 157.15 | 1142.2 | 985.05
15697 | 9.1474 | 188.98 | 60.377 | 0.023945 | 157.16 | 1142.2 |  | 15697 | 188.98 | 9.1474 | 60.377 | 0.023945 | 157.16 | 1142.2 | 985.04
15698 | 9.1493 | 188.99 | 60.377 | 0.02395 | 157.17 | 1142.2 |  | 15698 | 188.99 | 9.1493 | 60.377 | 0.02395 | 157.17 | 1142.2 | 985.03
15699 | 9.1513 | 189 | 60.377 | 0.023955 | 157.18 | 1142.2 |  | 15699 | 189 | 9.1513 | 60.377 | 0.023955 | 157.18 | 1142.2 | 985.02
15700 | 9.1533 | 189.01 | 60.376 | 0.02396 | 157.19 | 1142.2 |  | 15700 | 189.01 | 9.1533 | 60.376 | 0.02396 | 157.19 | 1142.2 | 985.01
15701 | 9.1552 | 189.02 | 60.376 | 0.023964 | 157.2 | 1142.2 |  | 15701 | 189.02 | 9.1552 | 60.376 | 0.023964 | 157.2 | 1142.2 | 985
15702 | 9.1572 | 189.03 | 60.376 | 0.023969 | 157.21 | 1142.2 |  | 15702 | 189.03 | 9.1572 | 60.376 | 0.023969 | 157.21 | 1142.2 | 984.99
15703 | 9.1592 | 189.04 | 60.376 | 0.023974 | 157.22 | 1142.2 |  | 15703 | 189.04 | 9.1592 | 60.376 | 0.023974 | 157.22 | 1142.2 | 984.98
15704 | 9.1611 | 189.05 | 60.376 | 0.023979 | 157.23 | 1142.2 |  | 15704 | 189.05 | 9.1611 | 60.376 | 0.023979 | 157.23 | 1142.2 | 984.97
15705 | 9.1631 | 189.06 | 60.375 | 0.023984 | 157.24 | 1142.2 |  | 15705 | 189.06 | 9.1631 | 60.375 | 0.023984 | 157.24 | 1142.2 | 984.96
15706 | 9.1651 | 189.07 | 60.375 | 0.023988 | 157.25 | 1142.2 |  | 15706 | 189.07 | 9.1651 | 60.375 | 0.023988 | 157.25 | 1142.2 | 984.95
15707 | 9.167 | 189.08 | 60.375 | 0.023993 | 157.26 | 1142.2 |  | 15707 | 189.08 | 9.167 | 60.375 | 0.023993 | 157.26 | 1142.2 | 984.94
15708 | 9.169 | 189.09 | 60.375 | 0.023998 | 157.27 | 1142.2 |  | 15708 | 189.09 | 9.169 | 60.375 | 0.023998 | 157.27 | 1142.2 | 984.93
15709 | 9.171 | 189.1 | 60.374 | 0.024003 | 157.28 | 1142.2 |  | 15709 | 189.1 | 9.171 | 60.374 | 0.024003 | 157.28 | 1142.2 | 984.92
15710 | 9.1729 | 189.11 | 60.374 | 0.024008 | 157.29 | 1142.2 |  | 15710 | 189.11 | 9.1729 | 60.374 | 0.024008 | 157.29 | 1142.2 | 984.91
15711 | 9.1749 | 189.12 | 60.374 | 0.024013 | 157.3 | 1142.3 |  | 15711 | 189.12 | 9.1749 | 60.374 | 0.024013 | 157.3 | 1142.3 | 985
15712 | 9.1769 | 189.13 | 60.374 | 0.024017 | 157.31 | 1142.3 |  | 15712 | 189.13 | 9.1769 | 60.374 | 0.024017 | 157.31 | 1142.3 | 984.99
15713 | 9.1788 | 189.14 | 60.373 | 0.024022 | 157.32 | 1142.3 |  | 15713 | 189.14 | 9.1788 | 60.373 | 0.024022 | 157.32 | 1142.3 | 984.98
15714 | 9.1808 | 189.15 | 60.373 | 0.024027 | 157.33 | 1142.3 |  | 15714 | 189.15 | 9.1808 | 60.373 | 0.024027 | 157.33 | 1142.3 | 984.97
15715 | 9.1828 | 189.16 | 60.373 | 0.024032 | 157.34 | 1142.3 |  | 15715 | 189.16 | 9.1828 | 60.373 | 0.024032 | 157.34 | 1142.3 | 984.96
15716 | 9.1848 | 189.17 | 60.373 | 0.024037 | 157.35 | 1142.3 |  | 15716 | 189.17 | 9.1848 | 60.373 | 0.024037 | 157.35 | 1142.3 | 984.95
15717 | 9.1867 | 189.18 | 60.373 | 0.024042 | 157.36 | 1142.3 |  | 15717 | 189.18 | 9.1867 | 60.373 | 0.024042 | 157.36 | 1142.3 | 984.94
15718 | 9.1887 | 189.19 | 60.372 | 0.024046 | 157.37 | 1142.3 |  | 15718 | 189.19 | 9.1887 | 60.372 | 0.024046 | 157.37 | 1142.3 | 984.93
15719 | 9.1907 | 189.2 | 60.372 | 0.024051 | 157.38 | 1142.3 |  | 15719 | 189.2 | 9.1907 | 60.372 | 0.024051 | 157.38 | 1142.3 | 984.92
15720 | 9.1926 | 189.21 | 60.372 | 0.024056 | 157.39 | 1142.3 |  | 15720 | 189.21 | 9.1926 | 60.372 | 0.024056 | 157.39 | 1142.3 | 984.91
15721 | 9.1946 | 189.22 | 60.372 | 0.024061 | 157.4 | 1142.3 |  | 15721 | 189.22 | 9.1946 | 60.372 | 0.024061 | 157.4 | 1142.3 | 984.9
15722 | 9.1966 | 189.23 | 60.371 | 0.024066 | 157.41 | 1142.3 |  | 15722 | 189.23 | 9.1966 | 60.371 | 0.024066 | 157.41 | 1142.3 | 984.89
15723 | 9.1986 | 189.24 | 60.371 | 0.02407 | 157.42 | 1142.3 |  | 15723 | 189.24 | 9.1986 | 60.371 | 0.02407 | 157.42 | 1142.3 | 984.88
15724 | 9.2005 | 189.25 | 60.371 | 0.024075 | 157.43 | 1142.3 |  | 15724 | 189.25 | 9.2005 | 60.371 | 0.024075 | 157.43 | 1142.3 | 984.87
15725 | 9.2025 | 189.26 | 60.371 | 0.02408 | 157.44 | 1142.3 |  | 15725 | 189.26 | 9.2025 | 60.371 | 0.02408 | 157.44 | 1142.3 | 984.86
15726 | 9.2045 | 189.27 | 60.371 | 0.024085 | 157.45 | 1142.3 |  | 15726 | 189.27 | 9.2045 | 60.371 | 0.024085 | 157.45 | 1142.3 | 984.85
15727 | 9.2065 | 189.28 | 60.37 | 0.02409 | 157.46 | 1142.3 |  | 15727 | 189.28 | 9.2065 | 60.37 | 0.02409 | 157.46 | 1142.3 | 984.84
15728 | 9.2084 | 189.29 | 60.37 | 0.024095 | 157.47 | 1142.3 |  | 15728 | 189.29 | 9.2084 | 60.37 | 0.024095 | 157.47 | 1142.3 | 984.83
15729 | 9.2104 | 189.3 | 60.37 | 0.024099 | 157.48 | 1142.3 |  | 15729 | 189.3 | 9.2104 | 60.37 | 0.024099 | 157.48 | 1142.3 | 984.82
15730 | 9.2124 | 189.31 | 60.37 | 0.024104 | 157.49 | 1142.3 |  | 15730 | 189.31 | 9.2124 | 60.37 | 0.024104 | 157.49 | 1142.3 | 984.81
15731 | 9.2144 | 189.32 | 60.369 | 0.024109 | 157.5 | 1142.3 |  | 15731 | 189.32 | 9.2144 | 60.369 | 0.024109 | 157.5 | 1142.3 | 984.8
15732 | 9.2163 | 189.33 | 60.369 | 0.024114 | 157.51 | 1142.3 |  | 15732 | 189.33 | 9.2163 | 60.369 | 0.024114 | 157.51 | 1142.3 | 984.79
15733 | 9.2183 | 189.34 | 60.369 | 0.024119 | 157.52 | 1142.3 |  | 15733 | 189.34 | 9.2183 | 60.369 | 0.024119 | 157.52 | 1142.3 | 984.78
15734 | 9.2203 | 189.35 | 60.369 | 0.024124 | 157.53 | 1142.3 |  | 15734 | 189.35 | 9.2203 | 60.369 | 0.024124 | 157.53 | 1142.3 | 984.77
15735 | 9.2223 | 189.36 | 60.368 | 0.024129 | 157.54 | 1142.3 |  | 15735 | 189.36 | 9.2223 | 60.368 | 0.024129 | 157.54 | 1142.3 | 984.76
15736 | 9.2242 | 189.37 | 60.368 | 0.024133 | 157.55 | 1142.3 |  | 15736 | 189.37 | 9.2242 | 60.368 | 0.024133 | 157.55 | 1142.3 | 984.75
15737 | 9.2262 | 189.38 | 60.368 | 0.024138 | 157.56 | 1142.4 |  | 15737 | 189.38 | 9.2262 | 60.368 | 0.024138 | 157.56 | 1142.4 | 984.84
15738 | 9.2282 | 189.39 | 60.368 | 0.024143 | 157.57 | 1142.4 |  | 15738 | 189.39 | 9.2282 | 60.368 | 0.024143 | 157.57 | 1142.4 | 984.83
15739 | 9.2302 | 189.4 | 60.368 | 0.024148 | 157.58 | 1142.4 |  | 15739 | 189.4 | 9.2302 | 60.368 | 0.024148 | 157.58 | 1142.4 | 984.82
15740 | 9.2322 | 189.41 | 60.367 | 0.024153 | 157.59 | 1142.4 |  | 15740 | 189.41 | 9.2322 | 60.367 | 0.024153 | 157.59 | 1142.4 | 984.81
15741 | 9.2341 | 189.42 | 60.367 | 0.024158 | 157.6 | 1142.4 |  | 15741 | 189.42 | 9.2341 | 60.367 | 0.024158 | 157.6 | 1142.4 | 984.8
15742 | 9.2361 | 189.43 | 60.367 | 0.024162 | 157.61 | 1142.4 |  | 15742 | 189.43 | 9.2361 | 60.367 | 0.024162 | 157.61 | 1142.4 | 984.79
15743 | 9.2381 | 189.44 | 60.367 | 0.024167 | 157.62 | 1142.4 |  | 15743 | 189.44 | 9.2381 | 60.367 | 0.024167 | 157.62 | 1142.4 | 984.78
15744 | 9.2401 | 189.45 | 60.366 | 0.024172 | 157.63 | 1142.4 |  | 15744 | 189.45 | 9.2401 | 60.366 | 0.024172 | 157.63 | 1142.4 | 984.77
15745 | 9.2421 | 189.46 | 60.366 | 0.024177 | 157.64 | 1142.4 |  | 15745 | 189.46 | 9.2421 | 60.366 | 0.024177 | 157.64 | 1142.4 | 984.76
15746 | 9.244 | 189.47 | 60.366 | 0.024182 | 157.65 | 1142.4 |  | 15746 | 189.47 | 9.244 | 60.366 | 0.024182 | 157.65 | 1142.4 | 984.75
15747 | 9.246 | 189.48 | 60.366 | 0.024187 | 157.66 | 1142.4 |  | 15747 | 189.48 | 9.246 | 60.366 | 0.024187 | 157.66 | 1142.4 | 984.74
15748 | 9.248 | 189.49 | 60.365 | 0.024192 | 157.67 | 1142.4 |  | 15748 | 189.49 | 9.248 | 60.365 | 0.024192 | 157.67 | 1142.4 | 984.73
15749 | 9.25 | 189.5 | 60.365 | 0.024196 | 157.68 | 1142.4 |  | 15749 | 189.5 | 9.25 | 60.365 | 0.024196 | 157.68 | 1142.4 | 984.72
15750 | 9.252 | 189.51 | 60.365 | 0.024201 | 157.69 | 1142.4 |  | 15750 | 189.51 | 9.252 | 60.365 | 0.024201 | 157.69 | 1142.4 | 984.71
15751 | 9.254 | 189.52 | 60.365 | 0.024206 | 157.7 | 1142.4 |  | 15751 | 189.52 | 9.254 | 60.365 | 0.024206 | 157.7 | 1142.4 | 984.7
15752 | 9.2559 | 189.53 | 60.365 | 0.024211 | 157.71 | 1142.4 |  | 15752 | 189.53 | 9.2559 | 60.365 | 0.024211 | 157.71 | 1142.4 | 984.69
15753 | 9.2579 | 189.54 | 60.364 | 0.024216 | 157.72 | 1142.4 |  | 15753 | 189.54 | 9.2579 | 60.364 | 0.024216 | 157.72 | 1142.4 | 984.68
15754 | 9.2599 | 189.55 | 60.364 | 0.024221 | 157.73 | 1142.4 |  | 15754 | 189.55 | 9.2599 | 60.364 | 0.024221 | 157.73 | 1142.4 | 984.67
15755 | 9.2619 | 189.56 | 60.364 | 0.024226 | 157.74 | 1142.4 |  | 15755 | 189.56 | 9.2619 | 60.364 | 0.024226 | 157.74 | 1142.4 | 984.66
15756 | 9.2639 | 189.57 | 60.364 | 0.02423 | 157.75 | 1142.4 |  | 15756 | 189.57 | 9.2639 | 60.364 | 0.02423 | 157.75 | 1142.4 | 984.65
15757 | 9.2659 | 189.58 | 60.363 | 0.024235 | 157.76 | 1142.4 |  | 15757 | 189.58 | 9.2659 | 60.363 | 0.024235 | 157.76 | 1142.4 | 984.64
15758 | 9.2679 | 189.59 | 60.363 | 0.02424 | 157.77 | 1142.4 |  | 15758 | 189.59 | 9.2679 | 60.363 | 0.02424 | 157.77 | 1142.4 | 984.63
15759 | 9.2698 | 189.6 | 60.363 | 0.024245 | 157.78 | 1142.4 |  | 15759 | 189.6 | 9.2698 | 60.363 | 0.024245 | 157.78 | 1142.4 | 984.62
15760 | 9.2718 | 189.61 | 60.363 | 0.02425 | 157.79 | 1142.4 |  | 15760 | 189.61 | 9.2718 | 60.363 | 0.02425 | 157.79 | 1142.4 | 984.61
15761 | 9.2738 | 189.62 | 60.363 | 0.024255 | 157.8 | 1142.4 |  | 15761 | 189.62 | 9.2738 | 60.363 | 0.024255 | 157.8 | 1142.4 | 984.6
15762 | 9.2758 | 189.63 | 60.362 | 0.02426 | 157.81 | 1142.5 |  | 15762 | 189.63 | 9.2758 | 60.362 | 0.02426 | 157.81 | 1142.5 | 984.69
15763 | 9.2778 | 189.64 | 60.362 | 0.024264 | 157.82 | 1142.5 |  | 15763 | 189.64 | 9.2778 | 60.362 | 0.024264 | 157.82 | 1142.5 | 984.68
15764 | 9.2798 | 189.65 | 60.362 | 0.024269 | 157.83 | 1142.5 |  | 15764 | 189.65 | 9.2798 | 60.362 | 0.024269 | 157.83 | 1142.5 | 984.67
15765 | 9.2818 | 189.66 | 60.362 | 0.024274 | 157.84 | 1142.5 |  | 15765 | 189.66 | 9.2818 | 60.362 | 0.024274 | 157.84 | 1142.5 | 984.66
15766 | 9.2838 | 189.67 | 60.361 | 0.024279 | 157.85 | 1142.5 |  | 15766 | 189.67 | 9.2838 | 60.361 | 0.024279 | 157.85 | 1142.5 | 984.65
15767 | 9.2857 | 189.68 | 60.361 | 0.024284 | 157.86 | 1142.5 |  | 15767 | 189.68 | 9.2857 | 60.361 | 0.024284 | 157.86 | 1142.5 | 984.64
15768 | 9.2877 | 189.69 | 60.361 | 0.024289 | 157.87 | 1142.5 |  | 15768 | 189.69 | 9.2877 | 60.361 | 0.024289 | 157.87 | 1142.5 | 984.63
15769 | 9.2897 | 189.7 | 60.361 | 0.024294 | 157.88 | 1142.5 |  | 15769 | 189.7 | 9.2897 | 60.361 | 0.024294 | 157.88 | 1142.5 | 984.62
15770 | 9.2917 | 189.71 | 60.36 | 0.024299 | 157.89 | 1142.5 |  | 15770 | 189.71 | 9.2917 | 60.36 | 0.024299 | 157.89 | 1142.5 | 984.61
15771 | 9.2937 | 189.72 | 60.36 | 0.024303 | 157.9 | 1142.5 |  | 15771 | 189.72 | 9.2937 | 60.36 | 0.024303 | 157.9 | 1142.5 | 984.6
15772 | 9.2957 | 189.73 | 60.36 | 0.024308 | 157.91 | 1142.5 |  | 15772 | 189.73 | 9.2957 | 60.36 | 0.024308 | 157.91 | 1142.5 | 984.59
15773 | 9.2977 | 189.74 | 60.36 | 0.024313 | 157.92 | 1142.5 |  | 15773 | 189.74 | 9.2977 | 60.36 | 0.024313 | 157.92 | 1142.5 | 984.58
15774 | 9.2997 | 189.75 | 60.36 | 0.024318 | 157.93 | 1142.5 |  | 15774 | 189.75 | 9.2997 | 60.36 | 0.024318 | 157.93 | 1142.5 | 984.57
15775 | 9.3017 | 189.76 | 60.359 | 0.024323 | 157.94 | 1142.5 |  | 15775 | 189.76 | 9.3017 | 60.359 | 0.024323 | 157.94 | 1142.5 | 984.56
15776 | 9.3037 | 189.77 | 60.359 | 0.024328 | 157.95 | 1142.5 |  | 15776 | 189.77 | 9.3037 | 60.359 | 0.024328 | 157.95 | 1142.5 | 984.55
15777 | 9.3057 | 189.78 | 60.359 | 0.024333 | 157.96 | 1142.5 |  | 15777 | 189.78 | 9.3057 | 60.359 | 0.024333 | 157.96 | 1142.5 | 984.54
15778 | 9.3076 | 189.79 | 60.359 | 0.024337 | 157.97 | 1142.5 |  | 15778 | 189.79 | 9.3076 | 60.359 | 0.024337 | 157.97 | 1142.5 | 984.53
15779 | 9.3096 | 189.8 | 60.358 | 0.024342 | 157.98 | 1142.5 |  | 15779 | 189.8 | 9.3096 | 60.358 | 0.024342 | 157.98 | 1142.5 | 984.52
15780 | 9.3116 | 189.81 | 60.358 | 0.024347 | 157.99 | 1142.5 |  | 15780 | 189.81 | 9.3116 | 60.358 | 0.024347 | 157.99 | 1142.5 | 984.51
15781 | 9.3136 | 189.82 | 60.358 | 0.024352 | 158 | 1142.5 |  | 15781 | 189.82 | 9.3136 | 60.358 | 0.024352 | 158 | 1142.5 | 984.5
15782 | 9.3156 | 189.83 | 60.358 | 0.024357 | 158.01 | 1142.5 |  | 15782 | 189.83 | 9.3156 | 60.358 | 0.024357 | 158.01 | 1142.5 | 984.49
15783 | 9.3176 | 189.84 | 60.357 | 0.024362 | 158.02 | 1142.5 |  | 15783 | 189.84 | 9.3176 | 60.357 | 0.024362 | 158.02 | 1142.5 | 984.48
15784 | 9.3196 | 189.85 | 60.357 | 0.024367 | 158.03 | 1142.5 |  | 15784 | 189.85 | 9.3196 | 60.357 | 0.024367 | 158.03 | 1142.5 | 984.47
15785 | 9.3216 | 189.86 | 60.357 | 0.024372 | 158.04 | 1142.5 |  | 15785 | 189.86 | 9.3216 | 60.357 | 0.024372 | 158.04 | 1142.5 | 984.46
15786 | 9.3236 | 189.87 | 60.357 | 0.024377 | 158.05 | 1142.5 |  | 15786 | 189.87 | 9.3236 | 60.357 | 0.024377 | 158.05 | 1142.5 | 984.45
15787 | 9.3256 | 189.88 | 60.357 | 0.024381 | 158.06 | 1142.5 |  | 15787 | 189.88 | 9.3256 | 60.357 | 0.024381 | 158.06 | 1142.5 | 984.44
15788 | 9.3276 | 189.89 | 60.356 | 0.024386 | 158.07 | 1142.6 |  | 15788 | 189.89 | 9.3276 | 60.356 | 0.024386 | 158.07 | 1142.6 | 984.53
15789 | 9.3296 | 189.9 | 60.356 | 0.024391 | 158.08 | 1142.6 |  | 15789 | 189.9 | 9.3296 | 60.356 | 0.024391 | 158.08 | 1142.6 | 984.52
15790 | 9.3316 | 189.91 | 60.356 | 0.024396 | 158.09 | 1142.6 |  | 15790 | 189.91 | 9.3316 | 60.356 | 0.024396 | 158.09 | 1142.6 | 984.51
15791 | 9.3336 | 189.92 | 60.356 | 0.024401 | 158.1 | 1142.6 |  | 15791 | 189.92 | 9.3336 | 60.356 | 0.024401 | 158.1 | 1142.6 | 984.5
15792 | 9.3356 | 189.93 | 60.355 | 0.024406 | 158.11 | 1142.6 |  | 15792 | 189.93 | 9.3356 | 60.355 | 0.024406 | 158.11 | 1142.6 | 984.49
15793 | 9.3376 | 189.94 | 60.355 | 0.024411 | 158.12 | 1142.6 |  | 15793 | 189.94 | 9.3376 | 60.355 | 0.024411 | 158.12 | 1142.6 | 984.48
15794 | 9.3396 | 189.95 | 60.355 | 0.024416 | 158.13 | 1142.6 |  | 15794 | 189.95 | 9.3396 | 60.355 | 0.024416 | 158.13 | 1142.6 | 984.47
15795 | 9.3416 | 189.96 | 60.355 | 0.024421 | 158.14 | 1142.6 |  | 15795 | 189.96 | 9.3416 | 60.355 | 0.024421 | 158.14 | 1142.6 | 984.46
15796 | 9.3436 | 189.97 | 60.354 | 0.024425 | 158.15 | 1142.6 |  | 15796 | 189.97 | 9.3436 | 60.354 | 0.024425 | 158.15 | 1142.6 | 984.45
15797 | 9.3456 | 189.98 | 60.354 | 0.02443 | 158.16 | 1142.6 |  | 15797 | 189.98 | 9.3456 | 60.354 | 0.02443 | 158.16 | 1142.6 | 984.44
15798 | 9.3476 | 189.99 | 60.354 | 0.024435 | 158.17 | 1142.6 |  | 15798 | 189.99 | 9.3476 | 60.354 | 0.024435 | 158.17 | 1142.6 | 984.43
15799 | 9.3496 | 190 | 60.354 | 0.02444 | 158.18 | 1142.6 |  | 15799 | 190 | 9.3496 | 60.354 | 0.02444 | 158.18 | 1142.6 | 984.42
15800 | 9.3516 | 190.01 | 60.354 | 0.024445 | 158.2 | 1142.6 |  | 15800 | 190.01 | 9.3516 | 60.354 | 0.024445 | 158.2 | 1142.6 | 984.4
15801 | 9.3536 | 190.02 | 60.353 | 0.02445 | 158.21 | 1142.6 |  | 15801 | 190.02 | 9.3536 | 60.353 | 0.02445 | 158.21 | 1142.6 | 984.39
15802 | 9.3556 | 190.03 | 60.353 | 0.024455 | 158.22 | 1142.6 |  | 15802 | 190.03 | 9.3556 | 60.353 | 0.024455 | 158.22 | 1142.6 | 984.38
15803 | 9.3576 | 190.04 | 60.353 | 0.02446 | 158.23 | 1142.6 |  | 15803 | 190.04 | 9.3576 | 60.353 | 0.02446 | 158.23 | 1142.6 | 984.37
15804 | 9.3596 | 190.05 | 60.353 | 0.024465 | 158.24 | 1142.6 |  | 15804 | 190.05 | 9.3596 | 60.353 | 0.024465 | 158.24 | 1142.6 | 984.36
15805 | 9.3616 | 190.06 | 60.352 | 0.024469 | 158.25 | 1142.6 |  | 15805 | 190.06 | 9.3616 | 60.352 | 0.024469 | 158.25 | 1142.6 | 984.35
15806 | 9.3636 | 190.07 | 60.352 | 0.024474 | 158.26 | 1142.6 |  | 15806 | 190.07 | 9.3636 | 60.352 | 0.024474 | 158.26 | 1142.6 | 984.34
15807 | 9.3656 | 190.08 | 60.352 | 0.024479 | 158.27 | 1142.6 |  | 15807 | 190.08 | 9.3656 | 60.352 | 0.024479 | 158.27 | 1142.6 | 984.33
15808 | 9.3676 | 190.09 | 60.352 | 0.024484 | 158.28 | 1142.6 |  | 15808 | 190.09 | 9.3676 | 60.352 | 0.024484 | 158.28 | 1142.6 | 984.32
15809 | 9.3696 | 190.1 | 60.352 | 0.024489 | 158.29 | 1142.6 |  | 15809 | 190.1 | 9.3696 | 60.352 | 0.024489 | 158.29 | 1142.6 | 984.31
15810 | 9.3716 | 190.11 | 60.351 | 0.024494 | 158.3 | 1142.6 |  | 15810 | 190.11 | 9.3716 | 60.351 | 0.024494 | 158.3 | 1142.6 | 984.3
15811 | 9.3736 | 190.12 | 60.351 | 0.024499 | 158.31 | 1142.6 |  | 15811 | 190.12 | 9.3736 | 60.351 | 0.024499 | 158.31 | 1142.6 | 984.29
15812 | 9.3756 | 190.13 | 60.351 | 0.024504 | 158.32 | 1142.6 |  | 15812 | 190.13 | 9.3756 | 60.351 | 0.024504 | 158.32 | 1142.6 | 984.28
15813 | 9.3776 | 190.14 | 60.351 | 0.024509 | 158.33 | 1142.6 |  | 15813 | 190.14 | 9.3776 | 60.351 | 0.024509 | 158.33 | 1142.6 | 984.27
15814 | 9.3796 | 190.15 | 60.35 | 0.024514 | 158.34 | 1142.7 |  | 15814 | 190.15 | 9.3796 | 60.35 | 0.024514 | 158.34 | 1142.7 | 984.36
15815 | 9.3816 | 190.16 | 60.35 | 0.024518 | 158.35 | 1142.7 |  | 15815 | 190.16 | 9.3816 | 60.35 | 0.024518 | 158.35 | 1142.7 | 984.35
15816 | 9.3836 | 190.17 | 60.35 | 0.024523 | 158.36 | 1142.7 |  | 15816 | 190.17 | 9.3836 | 60.35 | 0.024523 | 158.36 | 1142.7 | 984.34
15817 | 9.3857 | 190.18 | 60.35 | 0.024528 | 158.37 | 1142.7 |  | 15817 | 190.18 | 9.3857 | 60.35 | 0.024528 | 158.37 | 1142.7 | 984.33
15818 | 9.3877 | 190.19 | 60.349 | 0.024533 | 158.38 | 1142.7 |  | 15818 | 190.19 | 9.3877 | 60.349 | 0.024533 | 158.38 | 1142.7 | 984.32
15819 | 9.3897 | 190.2 | 60.349 | 0.024538 | 158.39 | 1142.7 |  | 15819 | 190.2 | 9.3897 | 60.349 | 0.024538 | 158.39 | 1142.7 | 984.31
15820 | 9.3917 | 190.21 | 60.349 | 0.024543 | 158.4 | 1142.7 |  | 15820 | 190.21 | 9.3917 | 60.349 | 0.024543 | 158.4 | 1142.7 | 984.3
15821 | 9.3937 | 190.22 | 60.349 | 0.024548 | 158.41 | 1142.7 |  | 15821 | 190.22 | 9.3937 | 60.349 | 0.024548 | 158.41 | 1142.7 | 984.29
15822 | 9.3957 | 190.23 | 60.349 | 0.024553 | 158.42 | 1142.7 |  | 15822 | 190.23 | 9.3957 | 60.349 | 0.024553 | 158.42 | 1142.7 | 984.28
15823 | 9.3977 | 190.24 | 60.348 | 0.024558 | 158.43 | 1142.7 |  | 15823 | 190.24 | 9.3977 | 60.348 | 0.024558 | 158.43 | 1142.7 | 984.27
15824 | 9.3997 | 190.25 | 60.348 | 0.024563 | 158.44 | 1142.7 |  | 15824 | 190.25 | 9.3997 | 60.348 | 0.024563 | 158.44 | 1142.7 | 984.26
15825 | 9.4017 | 190.26 | 60.348 | 0.024568 | 158.45 | 1142.7 |  | 15825 | 190.26 | 9.4017 | 60.348 | 0.024568 | 158.45 | 1142.7 | 984.25
15826 | 9.4037 | 190.27 | 60.348 | 0.024573 | 158.46 | 1142.7 |  | 15826 | 190.27 | 9.4037 | 60.348 | 0.024573 | 158.46 | 1142.7 | 984.24
15827 | 9.4057 | 190.28 | 60.347 | 0.024577 | 158.47 | 1142.7 |  | 15827 | 190.28 | 9.4057 | 60.347 | 0.024577 | 158.47 | 1142.7 | 984.23
15828 | 9.4078 | 190.29 | 60.347 | 0.024582 | 158.48 | 1142.7 |  | 15828 | 190.29 | 9.4078 | 60.347 | 0.024582 | 158.48 | 1142.7 | 984.22
15829 | 9.4098 | 190.3 | 60.347 | 0.024587 | 158.49 | 1142.7 |  | 15829 | 190.3 | 9.4098 | 60.347 | 0.024587 | 158.49 | 1142.7 | 984.21
15830 | 9.4118 | 190.31 | 60.347 | 0.024592 | 158.5 | 1142.7 |  | 15830 | 190.31 | 9.4118 | 60.347 | 0.024592 | 158.5 | 1142.7 | 984.2
15831 | 9.4138 | 190.32 | 60.346 | 0.024597 | 158.51 | 1142.7 |  | 15831 | 190.32 | 9.4138 | 60.346 | 0.024597 | 158.51 | 1142.7 | 984.19
15832 | 9.4158 | 190.33 | 60.346 | 0.024602 | 158.52 | 1142.7 |  | 15832 | 190.33 | 9.4158 | 60.346 | 0.024602 | 158.52 | 1142.7 | 984.18
15833 | 9.4178 | 190.34 | 60.346 | 0.024607 | 158.53 | 1142.7 |  | 15833 | 190.34 | 9.4178 | 60.346 | 0.024607 | 158.53 | 1142.7 | 984.17
15834 | 9.4198 | 190.35 | 60.346 | 0.024612 | 158.54 | 1142.7 |  | 15834 | 190.35 | 9.4198 | 60.346 | 0.024612 | 158.54 | 1142.7 | 984.16
15835 | 9.4218 | 190.36 | 60.346 | 0.024617 | 158.55 | 1142.7 |  | 15835 | 190.36 | 9.4218 | 60.346 | 0.024617 | 158.55 | 1142.7 | 984.15
15836 | 9.4239 | 190.37 | 60.345 | 0.024622 | 158.56 | 1142.7 |  | 15836 | 190.37 | 9.4239 | 60.345 | 0.024622 | 158.56 | 1142.7 | 984.14
15837 | 9.4259 | 190.38 | 60.345 | 0.024627 | 158.57 | 1142.7 |  | 15837 | 190.38 | 9.4259 | 60.345 | 0.024627 | 158.57 | 1142.7 | 984.13
15838 | 9.4279 | 190.39 | 60.345 | 0.024632 | 158.58 | 1142.7 |  | 15838 | 190.39 | 9.4279 | 60.345 | 0.024632 | 158.58 | 1142.7 | 984.12
15839 | 9.4299 | 190.4 | 60.345 | 0.024636 | 158.59 | 1142.8 |  | 15839 | 190.4 | 9.4299 | 60.345 | 0.024636 | 158.59 | 1142.8 | 984.21
15840 | 9.4319 | 190.41 | 60.344 | 0.024641 | 158.6 | 1142.8 |  | 15840 | 190.41 | 9.4319 | 60.344 | 0.024641 | 158.6 | 1142.8 | 984.2
15841 | 9.4339 | 190.42 | 60.344 | 0.024646 | 158.61 | 1142.8 |  | 15841 | 190.42 | 9.4339 | 60.344 | 0.024646 | 158.61 | 1142.8 | 984.19
15842 | 9.4359 | 190.43 | 60.344 | 0.024651 | 158.62 | 1142.8 |  | 15842 | 190.43 | 9.4359 | 60.344 | 0.024651 | 158.62 | 1142.8 | 984.18
15843 | 9.438 | 190.44 | 60.344 | 0.024656 | 158.63 | 1142.8 |  | 15843 | 190.44 | 9.438 | 60.344 | 0.024656 | 158.63 | 1142.8 | 984.17
15844 | 9.44 | 190.45 | 60.343 | 0.024661 | 158.64 | 1142.8 |  | 15844 | 190.45 | 9.44 | 60.343 | 0.024661 | 158.64 | 1142.8 | 984.16
15845 | 9.442 | 190.46 | 60.343 | 0.024666 | 158.65 | 1142.8 |  | 15845 | 190.46 | 9.442 | 60.343 | 0.024666 | 158.65 | 1142.8 | 984.15
15846 | 9.444 | 190.47 | 60.343 | 0.024671 | 158.66 | 1142.8 |  | 15846 | 190.47 | 9.444 | 60.343 | 0.024671 | 158.66 | 1142.8 | 984.14
15847 | 9.446 | 190.48 | 60.343 | 0.024676 | 158.67 | 1142.8 |  | 15847 | 190.48 | 9.446 | 60.343 | 0.024676 | 158.67 | 1142.8 | 984.13
15848 | 9.448 | 190.49 | 60.343 | 0.024681 | 158.68 | 1142.8 |  | 15848 | 190.49 | 9.448 | 60.343 | 0.024681 | 158.68 | 1142.8 | 984.12
15849 | 9.4501 | 190.5 | 60.342 | 0.024686 | 158.69 | 1142.8 |  | 15849 | 190.5 | 9.4501 | 60.342 | 0.024686 | 158.69 | 1142.8 | 984.11
15850 | 9.4521 | 190.51 | 60.342 | 0.024691 | 158.7 | 1142.8 |  | 15850 | 190.51 | 9.4521 | 60.342 | 0.024691 | 158.7 | 1142.8 | 984.1
15851 | 9.4541 | 190.52 | 60.342 | 0.024696 | 158.71 | 1142.8 |  | 15851 | 190.52 | 9.4541 | 60.342 | 0.024696 | 158.71 | 1142.8 | 984.09
15852 | 9.4561 | 190.53 | 60.342 | 0.024701 | 158.72 | 1142.8 |  | 15852 | 190.53 | 9.4561 | 60.342 | 0.024701 | 158.72 | 1142.8 | 984.08
15853 | 9.4581 | 190.54 | 60.341 | 0.024706 | 158.73 | 1142.8 |  | 15853 | 190.54 | 9.4581 | 60.341 | 0.024706 | 158.73 | 1142.8 | 984.07
15854 | 9.4602 | 190.55 | 60.341 | 0.02471 | 158.74 | 1142.8 |  | 15854 | 190.55 | 9.4602 | 60.341 | 0.02471 | 158.74 | 1142.8 | 984.06
15855 | 9.4622 | 190.56 | 60.341 | 0.024715 | 158.75 | 1142.8 |  | 15855 | 190.56 | 9.4622 | 60.341 | 0.024715 | 158.75 | 1142.8 | 984.05
15856 | 9.4642 | 190.57 | 60.341 | 0.02472 | 158.76 | 1142.8 |  | 15856 | 190.57 | 9.4642 | 60.341 | 0.02472 | 158.76 | 1142.8 | 984.04
15857 | 9.4662 | 190.58 | 60.341 | 0.024725 | 158.77 | 1142.8 |  | 15857 | 190.58 | 9.4662 | 60.341 | 0.024725 | 158.77 | 1142.8 | 984.03
15858 | 9.4683 | 190.59 | 60.34 | 0.02473 | 158.78 | 1142.8 |  | 15858 | 190.59 | 9.4683 | 60.34 | 0.02473 | 158.78 | 1142.8 | 984.02
15859 | 9.4703 | 190.6 | 60.34 | 0.024735 | 158.79 | 1142.8 |  | 15859 | 190.6 | 9.4703 | 60.34 | 0.024735 | 158.79 | 1142.8 | 984.01
15860 | 9.4723 | 190.61 | 60.34 | 0.02474 | 158.8 | 1142.8 |  | 15860 | 190.61 | 9.4723 | 60.34 | 0.02474 | 158.8 | 1142.8 | 984
15861 | 9.4743 | 190.62 | 60.34 | 0.024745 | 158.81 | 1142.8 |  | 15861 | 190.62 | 9.4743 | 60.34 | 0.024745 | 158.81 | 1142.8 | 983.99
15862 | 9.4763 | 190.63 | 60.339 | 0.02475 | 158.82 | 1142.8 |  | 15862 | 190.63 | 9.4763 | 60.339 | 0.02475 | 158.82 | 1142.8 | 983.98
15863 | 9.4784 | 190.64 | 60.339 | 0.024755 | 158.83 | 1142.8 |  | 15863 | 190.64 | 9.4784 | 60.339 | 0.024755 | 158.83 | 1142.8 | 983.97
15864 | 9.4804 | 190.65 | 60.339 | 0.02476 | 158.84 | 1142.8 |  | 15864 | 190.65 | 9.4804 | 60.339 | 0.02476 | 158.84 | 1142.8 | 983.96
15865 | 9.4824 | 190.66 | 60.339 | 0.024765 | 158.85 | 1142.9 |  | 15865 | 190.66 | 9.4824 | 60.339 | 0.024765 | 158.85 | 1142.9 | 984.05
15866 | 9.4844 | 190.67 | 60.338 | 0.02477 | 158.86 | 1142.9 |  | 15866 | 190.67 | 9.4844 | 60.338 | 0.02477 | 158.86 | 1142.9 | 984.04
15867 | 9.4865 | 190.68 | 60.338 | 0.024775 | 158.87 | 1142.9 |  | 15867 | 190.68 | 9.4865 | 60.338 | 0.024775 | 158.87 | 1142.9 | 984.03
15868 | 9.4885 | 190.69 | 60.338 | 0.02478 | 158.88 | 1142.9 |  | 15868 | 190.69 | 9.4885 | 60.338 | 0.02478 | 158.88 | 1142.9 | 984.02
15869 | 9.4905 | 190.7 | 60.338 | 0.024785 | 158.89 | 1142.9 |  | 15869 | 190.7 | 9.4905 | 60.338 | 0.024785 | 158.89 | 1142.9 | 984.01
15870 | 9.4925 | 190.71 | 60.338 | 0.02479 | 158.9 | 1142.9 |  | 15870 | 190.71 | 9.4925 | 60.338 | 0.02479 | 158.9 | 1142.9 | 984
15871 | 9.4946 | 190.72 | 60.337 | 0.024795 | 158.91 | 1142.9 |  | 15871 | 190.72 | 9.4946 | 60.337 | 0.024795 | 158.91 | 1142.9 | 983.99
15872 | 9.4966 | 190.73 | 60.337 | 0.024799 | 158.92 | 1142.9 |  | 15872 | 190.73 | 9.4966 | 60.337 | 0.024799 | 158.92 | 1142.9 | 983.98
15873 | 9.4986 | 190.74 | 60.337 | 0.024804 | 158.93 | 1142.9 |  | 15873 | 190.74 | 9.4986 | 60.337 | 0.024804 | 158.93 | 1142.9 | 983.97
15874 | 9.5006 | 190.75 | 60.337 | 0.024809 | 158.94 | 1142.9 |  | 15874 | 190.75 | 9.5006 | 60.337 | 0.024809 | 158.94 | 1142.9 | 983.96
15875 | 9.5027 | 190.76 | 60.336 | 0.024814 | 158.95 | 1142.9 |  | 15875 | 190.76 | 9.5027 | 60.336 | 0.024814 | 158.95 | 1142.9 | 983.95
15876 | 9.5047 | 190.77 | 60.336 | 0.024819 | 158.96 | 1142.9 |  | 15876 | 190.77 | 9.5047 | 60.336 | 0.024819 | 158.96 | 1142.9 | 983.94
15877 | 9.5067 | 190.78 | 60.336 | 0.024824 | 158.97 | 1142.9 |  | 15877 | 190.78 | 9.5067 | 60.336 | 0.024824 | 158.97 | 1142.9 | 983.93
15878 | 9.5088 | 190.79 | 60.336 | 0.024829 | 158.98 | 1142.9 |  | 15878 | 190.79 | 9.5088 | 60.336 | 0.024829 | 158.98 | 1142.9 | 983.92
15879 | 9.5108 | 190.8 | 60.335 | 0.024834 | 158.99 | 1142.9 |  | 15879 | 190.8 | 9.5108 | 60.335 | 0.024834 | 158.99 | 1142.9 | 983.91
15880 | 9.5128 | 190.81 | 60.335 | 0.024839 | 159 | 1142.9 |  | 15880 | 190.81 | 9.5128 | 60.335 | 0.024839 | 159 | 1142.9 | 983.9
15881 | 9.5148 | 190.82 | 60.335 | 0.024844 | 159.01 | 1142.9 |  | 15881 | 190.82 | 9.5148 | 60.335 | 0.024844 | 159.01 | 1142.9 | 983.89
15882 | 9.5169 | 190.83 | 60.335 | 0.024849 | 159.02 | 1142.9 |  | 15882 | 190.83 | 9.5169 | 60.335 | 0.024849 | 159.02 | 1142.9 | 983.88
15883 | 9.5189 | 190.84 | 60.335 | 0.024854 | 159.03 | 1142.9 |  | 15883 | 190.84 | 9.5189 | 60.335 | 0.024854 | 159.03 | 1142.9 | 983.87
15884 | 9.5209 | 190.85 | 60.334 | 0.024859 | 159.04 | 1142.9 |  | 15884 | 190.85 | 9.5209 | 60.334 | 0.024859 | 159.04 | 1142.9 | 983.86
15885 | 9.523 | 190.86 | 60.334 | 0.024864 | 159.05 | 1142.9 |  | 15885 | 190.86 | 9.523 | 60.334 | 0.024864 | 159.05 | 1142.9 | 983.85
15886 | 9.525 | 190.87 | 60.334 | 0.024869 | 159.06 | 1142.9 |  | 15886 | 190.87 | 9.525 | 60.334 | 0.024869 | 159.06 | 1142.9 | 983.84
15887 | 9.527 | 190.88 | 60.334 | 0.024874 | 159.07 | 1142.9 |  | 15887 | 190.88 | 9.527 | 60.334 | 0.024874 | 159.07 | 1142.9 | 983.83
15888 | 9.5291 | 190.89 | 60.333 | 0.024879 | 159.08 | 1142.9 |  | 15888 | 190.89 | 9.5291 | 60.333 | 0.024879 | 159.08 | 1142.9 | 983.82
15889 | 9.5311 | 190.9 | 60.333 | 0.024884 | 159.09 | 1142.9 |  | 15889 | 190.9 | 9.5311 | 60.333 | 0.024884 | 159.09 | 1142.9 | 983.81
15890 | 9.5331 | 190.91 | 60.333 | 0.024889 | 159.1 | 1143 |  | 15890 | 190.91 | 9.5331 | 60.333 | 0.024889 | 159.1 | 1143 | 983.9
15891 | 9.5352 | 190.92 | 60.333 | 0.024894 | 159.11 | 1143 |  | 15891 | 190.92 | 9.5352 | 60.333 | 0.024894 | 159.11 | 1143 | 983.89
15892 | 9.5372 | 190.93 | 60.332 | 0.024899 | 159.12 | 1143 |  | 15892 | 190.93 | 9.5372 | 60.332 | 0.024899 | 159.12 | 1143 | 983.88
15893 | 9.5392 | 190.94 | 60.332 | 0.024904 | 159.13 | 1143 |  | 15893 | 190.94 | 9.5392 | 60.332 | 0.024904 | 159.13 | 1143 | 983.87
15894 | 9.5413 | 190.95 | 60.332 | 0.024909 | 159.14 | 1143 |  | 15894 | 190.95 | 9.5413 | 60.332 | 0.024909 | 159.14 | 1143 | 983.86
15895 | 9.5433 | 190.96 | 60.332 | 0.024914 | 159.15 | 1143 |  | 15895 | 190.96 | 9.5433 | 60.332 | 0.024914 | 159.15 | 1143 | 983.85
15896 | 9.5453 | 190.97 | 60.332 | 0.024919 | 159.16 | 1143 |  | 15896 | 190.97 | 9.5453 | 60.332 | 0.024919 | 159.16 | 1143 | 983.84
15897 | 9.5474 | 190.98 | 60.331 | 0.024924 | 159.17 | 1143 |  | 15897 | 190.98 | 9.5474 | 60.331 | 0.024924 | 159.17 | 1143 | 983.83
15898 | 9.5494 | 190.99 | 60.331 | 0.024929 | 159.18 | 1143 |  | 15898 | 190.99 | 9.5494 | 60.331 | 0.024929 | 159.18 | 1143 | 983.82
15899 | 9.5515 | 191 | 60.331 | 0.024933 | 159.19 | 1143 |  | 15899 | 191 | 9.5515 | 60.331 | 0.024933 | 159.19 | 1143 | 983.81
15900 | 9.5535 | 191.01 | 60.331 | 0.024938 | 159.2 | 1143 |  | 15900 | 191.01 | 9.5535 | 60.331 | 0.024938 | 159.2 | 1143 | 983.8
15901 | 9.5555 | 191.02 | 60.33 | 0.024943 | 159.21 | 1143 |  | 15901 | 191.02 | 9.5555 | 60.33 | 0.024943 | 159.21 | 1143 | 983.79
15902 | 9.5576 | 191.03 | 60.33 | 0.024948 | 159.22 | 1143 |  | 15902 | 191.03 | 9.5576 | 60.33 | 0.024948 | 159.22 | 1143 | 983.78
15903 | 9.5596 | 191.04 | 60.33 | 0.024953 | 159.23 | 1143 |  | 15903 | 191.04 | 9.5596 | 60.33 | 0.024953 | 159.23 | 1143 | 983.77
15904 | 9.5616 | 191.05 | 60.33 | 0.024958 | 159.24 | 1143 |  | 15904 | 191.05 | 9.5616 | 60.33 | 0.024958 | 159.24 | 1143 | 983.76
15905 | 9.5637 | 191.06 | 60.329 | 0.024963 | 159.25 | 1143 |  | 15905 | 191.06 | 9.5637 | 60.329 | 0.024963 | 159.25 | 1143 | 983.75
15906 | 9.5657 | 191.07 | 60.329 | 0.024968 | 159.26 | 1143 |  | 15906 | 191.07 | 9.5657 | 60.329 | 0.024968 | 159.26 | 1143 | 983.74
15907 | 9.5678 | 191.08 | 60.329 | 0.024973 | 159.27 | 1143 |  | 15907 | 191.08 | 9.5678 | 60.329 | 0.024973 | 159.27 | 1143 | 983.73
15908 | 9.5698 | 191.09 | 60.329 | 0.024978 | 159.28 | 1143 |  | 15908 | 191.09 | 9.5698 | 60.329 | 0.024978 | 159.28 | 1143 | 983.72
15909 | 9.5718 | 191.1 | 60.329 | 0.024983 | 159.29 | 1143 |  | 15909 | 191.1 | 9.5718 | 60.329 | 0.024983 | 159.29 | 1143 | 983.71
15910 | 9.5739 | 191.11 | 60.328 | 0.024988 | 159.3 | 1143 |  | 15910 | 191.11 | 9.5739 | 60.328 | 0.024988 | 159.3 | 1143 | 983.7
15911 | 9.5759 | 191.12 | 60.328 | 0.024993 | 159.31 | 1143 |  | 15911 | 191.12 | 9.5759 | 60.328 | 0.024993 | 159.31 | 1143 | 983.69
15912 | 9.578 | 191.13 | 60.328 | 0.024998 | 159.32 | 1143 |  | 15912 | 191.13 | 9.578 | 60.328 | 0.024998 | 159.32 | 1143 | 983.68
15913 | 9.58 | 191.14 | 60.328 | 0.025003 | 159.33 | 1143 |  | 15913 | 191.14 | 9.58 | 60.328 | 0.025003 | 159.33 | 1143 | 983.67
15914 | 9.582 | 191.15 | 60.327 | 0.025008 | 159.34 | 1143 |  | 15914 | 191.15 | 9.582 | 60.327 | 0.025008 | 159.34 | 1143 | 983.66
15915 | 9.5841 | 191.16 | 60.327 | 0.025013 | 159.35 | 1143 |  | 15915 | 191.16 | 9.5841 | 60.327 | 0.025013 | 159.35 | 1143 | 983.65
15916 | 9.5861 | 191.17 | 60.327 | 0.025018 | 159.36 | 1143.1 |  | 15916 | 191.17 | 9.5861 | 60.327 | 0.025018 | 159.36 | 1143.1 | 983.74
15917 | 9.5882 | 191.18 | 60.327 | 0.025023 | 159.37 | 1143.1 |  | 15917 | 191.18 | 9.5882 | 60.327 | 0.025023 | 159.37 | 1143.1 | 983.73
15918 | 9.5902 | 191.19 | 60.326 | 0.025028 | 159.38 | 1143.1 |  | 15918 | 191.19 | 9.5902 | 60.326 | 0.025028 | 159.38 | 1143.1 | 983.72
15919 | 9.5923 | 191.2 | 60.326 | 0.025033 | 159.39 | 1143.1 |  | 15919 | 191.2 | 9.5923 | 60.326 | 0.025033 | 159.39 | 1143.1 | 983.71
15920 | 9.5943 | 191.21 | 60.326 | 0.025038 | 159.4 | 1143.1 |  | 15920 | 191.21 | 9.5943 | 60.326 | 0.025038 | 159.4 | 1143.1 | 983.7
15921 | 9.5963 | 191.22 | 60.326 | 0.025043 | 159.41 | 1143.1 |  | 15921 | 191.22 | 9.5963 | 60.326 | 0.025043 | 159.41 | 1143.1 | 983.69
15922 | 9.5984 | 191.23 | 60.326 | 0.025048 | 159.42 | 1143.1 |  | 15922 | 191.23 | 9.5984 | 60.326 | 0.025048 | 159.42 | 1143.1 | 983.68
15923 | 9.6004 | 191.24 | 60.325 | 0.025053 | 159.43 | 1143.1 |  | 15923 | 191.24 | 9.6004 | 60.325 | 0.025053 | 159.43 | 1143.1 | 983.67
15924 | 9.6025 | 191.25 | 60.325 | 0.025058 | 159.44 | 1143.1 |  | 15924 | 191.25 | 9.6025 | 60.325 | 0.025058 | 159.44 | 1143.1 | 983.66
15925 | 9.6045 | 191.26 | 60.325 | 0.025063 | 159.45 | 1143.1 |  | 15925 | 191.26 | 9.6045 | 60.325 | 0.025063 | 159.45 | 1143.1 | 983.65
15926 | 9.6066 | 191.27 | 60.325 | 0.025068 | 159.46 | 1143.1 |  | 15926 | 191.27 | 9.6066 | 60.325 | 0.025068 | 159.46 | 1143.1 | 983.64
15927 | 9.6086 | 191.28 | 60.324 | 0.025073 | 159.47 | 1143.1 |  | 15927 | 191.28 | 9.6086 | 60.324 | 0.025073 | 159.47 | 1143.1 | 983.63
15928 | 9.6107 | 191.29 | 60.324 | 0.025078 | 159.48 | 1143.1 |  | 15928 | 191.29 | 9.6107 | 60.324 | 0.025078 | 159.48 | 1143.1 | 983.62
15929 | 9.6127 | 191.3 | 60.324 | 0.025083 | 159.49 | 1143.1 |  | 15929 | 191.3 | 9.6127 | 60.324 | 0.025083 | 159.49 | 1143.1 | 983.61
15930 | 9.6148 | 191.31 | 60.324 | 0.025088 | 159.5 | 1143.1 |  | 15930 | 191.31 | 9.6148 | 60.324 | 0.025088 | 159.5 | 1143.1 | 983.6
15931 | 9.6168 | 191.32 | 60.323 | 0.025093 | 159.51 | 1143.1 |  | 15931 | 191.32 | 9.6168 | 60.323 | 0.025093 | 159.51 | 1143.1 | 983.59
15932 | 9.6189 | 191.33 | 60.323 | 0.025098 | 159.52 | 1143.1 |  | 15932 | 191.33 | 9.6189 | 60.323 | 0.025098 | 159.52 | 1143.1 | 983.58
15933 | 9.6209 | 191.34 | 60.323 | 0.025103 | 159.53 | 1143.1 |  | 15933 | 191.34 | 9.6209 | 60.323 | 0.025103 | 159.53 | 1143.1 | 983.57
15934 | 9.623 | 191.35 | 60.323 | 0.025108 | 159.54 | 1143.1 |  | 15934 | 191.35 | 9.623 | 60.323 | 0.025108 | 159.54 | 1143.1 | 983.56
15935 | 9.625 | 191.36 | 60.323 | 0.025113 | 159.55 | 1143.1 |  | 15935 | 191.36 | 9.625 | 60.323 | 0.025113 | 159.55 | 1143.1 | 983.55
15936 | 9.6271 | 191.37 | 60.322 | 0.025118 | 159.56 | 1143.1 |  | 15936 | 191.37 | 9.6271 | 60.322 | 0.025118 | 159.56 | 1143.1 | 983.54
15937 | 9.6291 | 191.38 | 60.322 | 0.025123 | 159.57 | 1143.1 |  | 15937 | 191.38 | 9.6291 | 60.322 | 0.025123 | 159.57 | 1143.1 | 983.53
15938 | 9.6312 | 191.39 | 60.322 | 0.025128 | 159.58 | 1143.1 |  | 15938 | 191.39 | 9.6312 | 60.322 | 0.025128 | 159.58 | 1143.1 | 983.52
15939 | 9.6332 | 191.4 | 60.322 | 0.025133 | 159.59 | 1143.1 |  | 15939 | 191.4 | 9.6332 | 60.322 | 0.025133 | 159.59 | 1143.1 | 983.51
15940 | 9.6353 | 191.41 | 60.321 | 0.025138 | 159.6 | 1143.1 |  | 15940 | 191.41 | 9.6353 | 60.321 | 0.025138 | 159.6 | 1143.1 | 983.5
15941 | 9.6373 | 191.42 | 60.321 | 0.025143 | 159.61 | 1143.2 |  | 15941 | 191.42 | 9.6373 | 60.321 | 0.025143 | 159.61 | 1143.2 | 983.59
15942 | 9.6394 | 191.43 | 60.321 | 0.025148 | 159.62 | 1143.2 |  | 15942 | 191.43 | 9.6394 | 60.321 | 0.025148 | 159.62 | 1143.2 | 983.58
15943 | 9.6414 | 191.44 | 60.321 | 0.025153 | 159.63 | 1143.2 |  | 15943 | 191.44 | 9.6414 | 60.321 | 0.025153 | 159.63 | 1143.2 | 983.57
15944 | 9.6435 | 191.45 | 60.32 | 0.025158 | 159.64 | 1143.2 |  | 15944 | 191.45 | 9.6435 | 60.32 | 0.025158 | 159.64 | 1143.2 | 983.56
15945 | 9.6455 | 191.46 | 60.32 | 0.025163 | 159.65 | 1143.2 |  | 15945 | 191.46 | 9.6455 | 60.32 | 0.025163 | 159.65 | 1143.2 | 983.55
15946 | 9.6476 | 191.47 | 60.32 | 0.025168 | 159.66 | 1143.2 |  | 15946 | 191.47 | 9.6476 | 60.32 | 0.025168 | 159.66 | 1143.2 | 983.54
15947 | 9.6496 | 191.48 | 60.32 | 0.025173 | 159.67 | 1143.2 |  | 15947 | 191.48 | 9.6496 | 60.32 | 0.025173 | 159.67 | 1143.2 | 983.53
15948 | 9.6517 | 191.49 | 60.32 | 0.025178 | 159.68 | 1143.2 |  | 15948 | 191.49 | 9.6517 | 60.32 | 0.025178 | 159.68 | 1143.2 | 983.52
15949 | 9.6537 | 191.5 | 60.319 | 0.025183 | 159.69 | 1143.2 |  | 15949 | 191.5 | 9.6537 | 60.319 | 0.025183 | 159.69 | 1143.2 | 983.51
15950 | 9.6558 | 191.51 | 60.319 | 0.025188 | 159.7 | 1143.2 |  | 15950 | 191.51 | 9.6558 | 60.319 | 0.025188 | 159.7 | 1143.2 | 983.5
15951 | 9.6579 | 191.52 | 60.319 | 0.025193 | 159.71 | 1143.2 |  | 15951 | 191.52 | 9.6579 | 60.319 | 0.025193 | 159.71 | 1143.2 | 983.49
15952 | 9.6599 | 191.53 | 60.319 | 0.025198 | 159.72 | 1143.2 |  | 15952 | 191.53 | 9.6599 | 60.319 | 0.025198 | 159.72 | 1143.2 | 983.48
15953 | 9.662 | 191.54 | 60.318 | 0.025203 | 159.73 | 1143.2 |  | 15953 | 191.54 | 9.662 | 60.318 | 0.025203 | 159.73 | 1143.2 | 983.47
15954 | 9.664 | 191.55 | 60.318 | 0.025208 | 159.74 | 1143.2 |  | 15954 | 191.55 | 9.664 | 60.318 | 0.025208 | 159.74 | 1143.2 | 983.46
15955 | 9.6661 | 191.56 | 60.318 | 0.025213 | 159.75 | 1143.2 |  | 15955 | 191.56 | 9.6661 | 60.318 | 0.025213 | 159.75 | 1143.2 | 983.45
15956 | 9.6681 | 191.57 | 60.318 | 0.025218 | 159.76 | 1143.2 |  | 15956 | 191.57 | 9.6681 | 60.318 | 0.025218 | 159.76 | 1143.2 | 983.44
15957 | 9.6702 | 191.58 | 60.317 | 0.025223 | 159.77 | 1143.2 |  | 15957 | 191.58 | 9.6702 | 60.317 | 0.025223 | 159.77 | 1143.2 | 983.43
15958 | 9.6722 | 191.59 | 60.317 | 0.025228 | 159.78 | 1143.2 |  | 15958 | 191.59 | 9.6722 | 60.317 | 0.025228 | 159.78 | 1143.2 | 983.42
15959 | 9.6743 | 191.6 | 60.317 | 0.025233 | 159.79 | 1143.2 |  | 15959 | 191.6 | 9.6743 | 60.317 | 0.025233 | 159.79 | 1143.2 | 983.41
15960 | 9.6764 | 191.61 | 60.317 | 0.025238 | 159.8 | 1143.2 |  | 15960 | 191.61 | 9.6764 | 60.317 | 0.025238 | 159.8 | 1143.2 | 983.4
15961 | 9.6784 | 191.62 | 60.317 | 0.025244 | 159.81 | 1143.2 |  | 15961 | 191.62 | 9.6784 | 60.317 | 0.025244 | 159.81 | 1143.2 | 983.39
15962 | 9.6805 | 191.63 | 60.316 | 0.025249 | 159.82 | 1143.2 |  | 15962 | 191.63 | 9.6805 | 60.316 | 0.025249 | 159.82 | 1143.2 | 983.38
15963 | 9.6825 | 191.64 | 60.316 | 0.025254 | 159.83 | 1143.2 |  | 15963 | 191.64 | 9.6825 | 60.316 | 0.025254 | 159.83 | 1143.2 | 983.37
15964 | 9.6846 | 191.65 | 60.316 | 0.025259 | 159.84 | 1143.2 |  | 15964 | 191.65 | 9.6846 | 60.316 | 0.025259 | 159.84 | 1143.2 | 983.36
15965 | 9.6867 | 191.66 | 60.316 | 0.025264 | 159.85 | 1143.2 |  | 15965 | 191.66 | 9.6867 | 60.316 | 0.025264 | 159.85 | 1143.2 | 983.35
15966 | 9.6887 | 191.67 | 60.315 | 0.025269 | 159.86 | 1143.2 |  | 15966 | 191.67 | 9.6887 | 60.315 | 0.025269 | 159.86 | 1143.2 | 983.34
15967 | 9.6908 | 191.68 | 60.315 | 0.025274 | 159.87 | 1143.3 |  | 15967 | 191.68 | 9.6908 | 60.315 | 0.025274 | 159.87 | 1143.3 | 983.43
15968 | 9.6928 | 191.69 | 60.315 | 0.025279 | 159.88 | 1143.3 |  | 15968 | 191.69 | 9.6928 | 60.315 | 0.025279 | 159.88 | 1143.3 | 983.42
15969 | 9.6949 | 191.7 | 60.315 | 0.025284 | 159.89 | 1143.3 |  | 15969 | 191.7 | 9.6949 | 60.315 | 0.025284 | 159.89 | 1143.3 | 983.41
15970 | 9.697 | 191.71 | 60.314 | 0.025289 | 159.9 | 1143.3 |  | 15970 | 191.71 | 9.697 | 60.314 | 0.025289 | 159.9 | 1143.3 | 983.4
15971 | 9.699 | 191.72 | 60.314 | 0.025294 | 159.91 | 1143.3 |  | 15971 | 191.72 | 9.699 | 60.314 | 0.025294 | 159.91 | 1143.3 | 983.39
15972 | 9.7011 | 191.73 | 60.314 | 0.025299 | 159.92 | 1143.3 |  | 15972 | 191.73 | 9.7011 | 60.314 | 0.025299 | 159.92 | 1143.3 | 983.38
15973 | 9.7032 | 191.74 | 60.314 | 0.025304 | 159.93 | 1143.3 |  | 15973 | 191.74 | 9.7032 | 60.314 | 0.025304 | 159.93 | 1143.3 | 983.37
15974 | 9.7052 | 191.75 | 60.314 | 0.025309 | 159.94 | 1143.3 |  | 15974 | 191.75 | 9.7052 | 60.314 | 0.025309 | 159.94 | 1143.3 | 983.36
15975 | 9.7073 | 191.76 | 60.313 | 0.025314 | 159.95 | 1143.3 |  | 15975 | 191.76 | 9.7073 | 60.313 | 0.025314 | 159.95 | 1143.3 | 983.35
15976 | 9.7094 | 191.77 | 60.313 | 0.025319 | 159.96 | 1143.3 |  | 15976 | 191.77 | 9.7094 | 60.313 | 0.025319 | 159.96 | 1143.3 | 983.34
15977 | 9.7114 | 191.78 | 60.313 | 0.025324 | 159.97 | 1143.3 |  | 15977 | 191.78 | 9.7114 | 60.313 | 0.025324 | 159.97 | 1143.3 | 983.33
15978 | 9.7135 | 191.79 | 60.313 | 0.025329 | 159.98 | 1143.3 |  | 15978 | 191.79 | 9.7135 | 60.313 | 0.025329 | 159.98 | 1143.3 | 983.32
15979 | 9.7156 | 191.8 | 60.312 | 0.025334 | 159.99 | 1143.3 |  | 15979 | 191.8 | 9.7156 | 60.312 | 0.025334 | 159.99 | 1143.3 | 983.31
15980 | 9.7176 | 191.81 | 60.312 | 0.025339 | 160 | 1143.3 |  | 15980 | 191.81 | 9.7176 | 60.312 | 0.025339 | 160 | 1143.3 | 983.3
15981 | 9.7197 | 191.82 | 60.312 | 0.025344 | 160.01 | 1143.3 |  | 15981 | 191.82 | 9.7197 | 60.312 | 0.025344 | 160.01 | 1143.3 | 983.29
15982 | 9.7218 | 191.83 | 60.312 | 0.025349 | 160.02 | 1143.3 |  | 15982 | 191.83 | 9.7218 | 60.312 | 0.025349 | 160.02 | 1143.3 | 983.28
15983 | 9.7238 | 191.84 | 60.311 | 0.025354 | 160.03 | 1143.3 |  | 15983 | 191.84 | 9.7238 | 60.311 | 0.025354 | 160.03 | 1143.3 | 983.27
15984 | 9.7259 | 191.85 | 60.311 | 0.025359 | 160.04 | 1143.3 |  | 15984 | 191.85 | 9.7259 | 60.311 | 0.025359 | 160.04 | 1143.3 | 983.26
15985 | 9.728 | 191.86 | 60.311 | 0.025364 | 160.05 | 1143.3 |  | 15985 | 191.86 | 9.728 | 60.311 | 0.025364 | 160.05 | 1143.3 | 983.25
15986 | 9.73 | 191.87 | 60.311 | 0.025369 | 160.06 | 1143.3 |  | 15986 | 191.87 | 9.73 | 60.311 | 0.025369 | 160.06 | 1143.3 | 983.24
15987 | 9.7321 | 191.88 | 60.311 | 0.025374 | 160.07 | 1143.3 |  | 15987 | 191.88 | 9.7321 | 60.311 | 0.025374 | 160.07 | 1143.3 | 983.23
15988 | 9.7342 | 191.89 | 60.31 | 0.025379 | 160.08 | 1143.3 |  | 15988 | 191.89 | 9.7342 | 60.31 | 0.025379 | 160.08 | 1143.3 | 983.22
15989 | 9.7362 | 191.9 | 60.31 | 0.025385 | 160.09 | 1143.3 |  | 15989 | 191.9 | 9.7362 | 60.31 | 0.025385 | 160.09 | 1143.3 | 983.21
15990 | 9.7383 | 191.91 | 60.31 | 0.02539 | 160.1 | 1143.3 |  | 15990 | 191.91 | 9.7383 | 60.31 | 0.02539 | 160.1 | 1143.3 | 983.2
15991 | 9.7404 | 191.92 | 60.31 | 0.025395 | 160.11 | 1143.3 |  | 15991 | 191.92 | 9.7404 | 60.31 | 0.025395 | 160.11 | 1143.3 | 983.19
15992 | 9.7424 | 191.93 | 60.309 | 0.0254 | 160.12 | 1143.4 |  | 15992 | 191.93 | 9.7424 | 60.309 | 0.0254 | 160.12 | 1143.4 | 983.28
15993 | 9.7445 | 191.94 | 60.309 | 0.025405 | 160.14 | 1143.4 |  | 15993 | 191.94 | 9.7445 | 60.309 | 0.025405 | 160.14 | 1143.4 | 983.26
15994 | 9.7466 | 191.95 | 60.309 | 0.02541 | 160.15 | 1143.4 |  | 15994 | 191.95 | 9.7466 | 60.309 | 0.02541 | 160.15 | 1143.4 | 983.25
15995 | 9.7487 | 191.96 | 60.309 | 0.025415 | 160.16 | 1143.4 |  | 15995 | 191.96 | 9.7487 | 60.309 | 0.025415 | 160.16 | 1143.4 | 983.24
15996 | 9.7507 | 191.97 | 60.308 | 0.02542 | 160.17 | 1143.4 |  | 15996 | 191.97 | 9.7507 | 60.308 | 0.02542 | 160.17 | 1143.4 | 983.23
15997 | 9.7528 | 191.98 | 60.308 | 0.025425 | 160.18 | 1143.4 |  | 15997 | 191.98 | 9.7528 | 60.308 | 0.025425 | 160.18 | 1143.4 | 983.22
15998 | 9.7549 | 191.99 | 60.308 | 0.02543 | 160.19 | 1143.4 |  | 15998 | 191.99 | 9.7549 | 60.308 | 0.02543 | 160.19 | 1143.4 | 983.21
15999 | 9.7569 | 192 | 60.308 | 0.025435 | 160.2 | 1143.4 |  | 15999 | 192 | 9.7569 | 60.308 | 0.025435 | 160.2 | 1143.4 | 983.2
16000 | 9.759 | 192.01 | 60.308 | 0.02544 | 160.21 | 1143.4 |  | 16000 | 192.01 | 9.759 | 60.308 | 0.02544 | 160.21 | 1143.4 | 983.19
16001 | 9.7611 | 192.02 | 60.307 | 0.025445 | 160.22 | 1143.4 |  | 16001 | 192.02 | 9.7611 | 60.307 | 0.025445 | 160.22 | 1143.4 | 983.18
16002 | 9.7632 | 192.03 | 60.307 | 0.02545 | 160.23 | 1143.4 |  | 16002 | 192.03 | 9.7632 | 60.307 | 0.02545 | 160.23 | 1143.4 | 983.17
16003 | 9.7652 | 192.04 | 60.307 | 0.025455 | 160.24 | 1143.4 |  | 16003 | 192.04 | 9.7652 | 60.307 | 0.025455 | 160.24 | 1143.4 | 983.16
16004 | 9.7673 | 192.05 | 60.307 | 0.02546 | 160.25 | 1143.4 |  | 16004 | 192.05 | 9.7673 | 60.307 | 0.02546 | 160.25 | 1143.4 | 983.15
16005 | 9.7694 | 192.06 | 60.306 | 0.025465 | 160.26 | 1143.4 |  | 16005 | 192.06 | 9.7694 | 60.306 | 0.025465 | 160.26 | 1143.4 | 983.14
16006 | 9.7715 | 192.07 | 60.306 | 0.02547 | 160.27 | 1143.4 |  | 16006 | 192.07 | 9.7715 | 60.306 | 0.02547 | 160.27 | 1143.4 | 983.13
16007 | 9.7735 | 192.08 | 60.306 | 0.025476 | 160.28 | 1143.4 |  | 16007 | 192.08 | 9.7735 | 60.306 | 0.025476 | 160.28 | 1143.4 | 983.12
16008 | 9.7756 | 192.09 | 60.306 | 0.025481 | 160.29 | 1143.4 |  | 16008 | 192.09 | 9.7756 | 60.306 | 0.025481 | 160.29 | 1143.4 | 983.11
16009 | 9.7777 | 192.1 | 60.305 | 0.025486 | 160.3 | 1143.4 |  | 16009 | 192.1 | 9.7777 | 60.305 | 0.025486 | 160.3 | 1143.4 | 983.1
16010 | 9.7798 | 192.11 | 60.305 | 0.025491 | 160.31 | 1143.4 |  | 16010 | 192.11 | 9.7798 | 60.305 | 0.025491 | 160.31 | 1143.4 | 983.09
16011 | 9.7818 | 192.12 | 60.305 | 0.025496 | 160.32 | 1143.4 |  | 16011 | 192.12 | 9.7818 | 60.305 | 0.025496 | 160.32 | 1143.4 | 983.08
16012 | 9.7839 | 192.13 | 60.305 | 0.025501 | 160.33 | 1143.4 |  | 16012 | 192.13 | 9.7839 | 60.305 | 0.025501 | 160.33 | 1143.4 | 983.07
16013 | 9.786 | 192.14 | 60.305 | 0.025506 | 160.34 | 1143.4 |  | 16013 | 192.14 | 9.786 | 60.305 | 0.025506 | 160.34 | 1143.4 | 983.06
16014 | 9.7881 | 192.15 | 60.304 | 0.025511 | 160.35 | 1143.4 |  | 16014 | 192.15 | 9.7881 | 60.304 | 0.025511 | 160.35 | 1143.4 | 983.05
16015 | 9.7902 | 192.16 | 60.304 | 0.025516 | 160.36 | 1143.4 |  | 16015 | 192.16 | 9.7902 | 60.304 | 0.025516 | 160.36 | 1143.4 | 983.04
16016 | 9.7922 | 192.17 | 60.304 | 0.025521 | 160.37 | 1143.4 |  | 16016 | 192.17 | 9.7922 | 60.304 | 0.025521 | 160.37 | 1143.4 | 983.03
16017 | 9.7943 | 192.18 | 60.304 | 0.025526 | 160.38 | 1143.4 |  | 16017 | 192.18 | 9.7943 | 60.304 | 0.025526 | 160.38 | 1143.4 | 983.02
16018 | 9.7964 | 192.19 | 60.303 | 0.025531 | 160.39 | 1143.5 |  | 16018 | 192.19 | 9.7964 | 60.303 | 0.025531 | 160.39 | 1143.5 | 983.11
16019 | 9.7985 | 192.2 | 60.303 | 0.025536 | 160.4 | 1143.5 |  | 16019 | 192.2 | 9.7985 | 60.303 | 0.025536 | 160.4 | 1143.5 | 983.1
16020 | 9.8006 | 192.21 | 60.303 | 0.025541 | 160.41 | 1143.5 |  | 16020 | 192.21 | 9.8006 | 60.303 | 0.025541 | 160.41 | 1143.5 | 983.09
16021 | 9.8026 | 192.22 | 60.303 | 0.025547 | 160.42 | 1143.5 |  | 16021 | 192.22 | 9.8026 | 60.303 | 0.025547 | 160.42 | 1143.5 | 983.08
16022 | 9.8047 | 192.23 | 60.302 | 0.025552 | 160.43 | 1143.5 |  | 16022 | 192.23 | 9.8047 | 60.302 | 0.025552 | 160.43 | 1143.5 | 983.07
16023 | 9.8068 | 192.24 | 60.302 | 0.025557 | 160.44 | 1143.5 |  | 16023 | 192.24 | 9.8068 | 60.302 | 0.025557 | 160.44 | 1143.5 | 983.06
16024 | 9.8089 | 192.25 | 60.302 | 0.025562 | 160.45 | 1143.5 |  | 16024 | 192.25 | 9.8089 | 60.302 | 0.025562 | 160.45 | 1143.5 | 983.05
16025 | 9.811 | 192.26 | 60.302 | 0.025567 | 160.46 | 1143.5 |  | 16025 | 192.26 | 9.811 | 60.302 | 0.025567 | 160.46 | 1143.5 | 983.04
16026 | 9.8131 | 192.27 | 60.302 | 0.025572 | 160.47 | 1143.5 |  | 16026 | 192.27 | 9.8131 | 60.302 | 0.025572 | 160.47 | 1143.5 | 983.03
16027 | 9.8151 | 192.28 | 60.301 | 0.025577 | 160.48 | 1143.5 |  | 16027 | 192.28 | 9.8151 | 60.301 | 0.025577 | 160.48 | 1143.5 | 983.02
16028 | 9.8172 | 192.29 | 60.301 | 0.025582 | 160.49 | 1143.5 |  | 16028 | 192.29 | 9.8172 | 60.301 | 0.025582 | 160.49 | 1143.5 | 983.01
16029 | 9.8193 | 192.3 | 60.301 | 0.025587 | 160.5 | 1143.5 |  | 16029 | 192.3 | 9.8193 | 60.301 | 0.025587 | 160.5 | 1143.5 | 983
16030 | 9.8214 | 192.31 | 60.301 | 0.025592 | 160.51 | 1143.5 |  | 16030 | 192.31 | 9.8214 | 60.301 | 0.025592 | 160.51 | 1143.5 | 982.99
16031 | 9.8235 | 192.32 | 60.3 | 0.025597 | 160.52 | 1143.5 |  | 16031 | 192.32 | 9.8235 | 60.3 | 0.025597 | 160.52 | 1143.5 | 982.98
16032 | 9.8256 | 192.33 | 60.3 | 0.025602 | 160.53 | 1143.5 |  | 16032 | 192.33 | 9.8256 | 60.3 | 0.025602 | 160.53 | 1143.5 | 982.97
16033 | 9.8276 | 192.34 | 60.3 | 0.025607 | 160.54 | 1143.5 |  | 16033 | 192.34 | 9.8276 | 60.3 | 0.025607 | 160.54 | 1143.5 | 982.96
16034 | 9.8297 | 192.35 | 60.3 | 0.025613 | 160.55 | 1143.5 |  | 16034 | 192.35 | 9.8297 | 60.3 | 0.025613 | 160.55 | 1143.5 | 982.95
16035 | 9.8318 | 192.36 | 60.299 | 0.025618 | 160.56 | 1143.5 |  | 16035 | 192.36 | 9.8318 | 60.299 | 0.025618 | 160.56 | 1143.5 | 982.94
16036 | 9.8339 | 192.37 | 60.299 | 0.025623 | 160.57 | 1143.5 |  | 16036 | 192.37 | 9.8339 | 60.299 | 0.025623 | 160.57 | 1143.5 | 982.93
16037 | 9.836 | 192.38 | 60.299 | 0.025628 | 160.58 | 1143.5 |  | 16037 | 192.38 | 9.836 | 60.299 | 0.025628 | 160.58 | 1143.5 | 982.92
16038 | 9.8381 | 192.39 | 60.299 | 0.025633 | 160.59 | 1143.5 |  | 16038 | 192.39 | 9.8381 | 60.299 | 0.025633 | 160.59 | 1143.5 | 982.91
16039 | 9.8402 | 192.4 | 60.299 | 0.025638 | 160.6 | 1143.5 |  | 16039 | 192.4 | 9.8402 | 60.299 | 0.025638 | 160.6 | 1143.5 | 982.9
16040 | 9.8423 | 192.41 | 60.298 | 0.025643 | 160.61 | 1143.5 |  | 16040 | 192.41 | 9.8423 | 60.298 | 0.025643 | 160.61 | 1143.5 | 982.89
16041 | 9.8443 | 192.42 | 60.298 | 0.025648 | 160.62 | 1143.5 |  | 16041 | 192.42 | 9.8443 | 60.298 | 0.025648 | 160.62 | 1143.5 | 982.88
16042 | 9.8464 | 192.43 | 60.298 | 0.025653 | 160.63 | 1143.5 |  | 16042 | 192.43 | 9.8464 | 60.298 | 0.025653 | 160.63 | 1143.5 | 982.87
16043 | 9.8485 | 192.44 | 60.298 | 0.025658 | 160.64 | 1143.5 |  | 16043 | 192.44 | 9.8485 | 60.298 | 0.025658 | 160.64 | 1143.5 | 982.86
16044 | 9.8506 | 192.45 | 60.297 | 0.025663 | 160.65 | 1143.6 |  | 16044 | 192.45 | 9.8506 | 60.297 | 0.025663 | 160.65 | 1143.6 | 982.95
16045 | 9.8527 | 192.46 | 60.297 | 0.025669 | 160.66 | 1143.6 |  | 16045 | 192.46 | 9.8527 | 60.297 | 0.025669 | 160.66 | 1143.6 | 982.94
16046 | 9.8548 | 192.47 | 60.297 | 0.025674 | 160.67 | 1143.6 |  | 16046 | 192.47 | 9.8548 | 60.297 | 0.025674 | 160.67 | 1143.6 | 982.93
16047 | 9.8569 | 192.48 | 60.297 | 0.025679 | 160.68 | 1143.6 |  | 16047 | 192.48 | 9.8569 | 60.297 | 0.025679 | 160.68 | 1143.6 | 982.92
16048 | 9.859 | 192.49 | 60.296 | 0.025684 | 160.69 | 1143.6 |  | 16048 | 192.49 | 9.859 | 60.296 | 0.025684 | 160.69 | 1143.6 | 982.91
16049 | 9.8611 | 192.5 | 60.296 | 0.025689 | 160.7 | 1143.6 |  | 16049 | 192.5 | 9.8611 | 60.296 | 0.025689 | 160.7 | 1143.6 | 982.9
16050 | 9.8632 | 192.51 | 60.296 | 0.025694 | 160.71 | 1143.6 |  | 16050 | 192.51 | 9.8632 | 60.296 | 0.025694 | 160.71 | 1143.6 | 982.89
16051 | 9.8652 | 192.52 | 60.296 | 0.025699 | 160.72 | 1143.6 |  | 16051 | 192.52 | 9.8652 | 60.296 | 0.025699 | 160.72 | 1143.6 | 982.88
16052 | 9.8673 | 192.53 | 60.296 | 0.025704 | 160.73 | 1143.6 |  | 16052 | 192.53 | 9.8673 | 60.296 | 0.025704 | 160.73 | 1143.6 | 982.87
16053 | 9.8694 | 192.54 | 60.295 | 0.025709 | 160.74 | 1143.6 |  | 16053 | 192.54 | 9.8694 | 60.295 | 0.025709 | 160.74 | 1143.6 | 982.86
16054 | 9.8715 | 192.55 | 60.295 | 0.025714 | 160.75 | 1143.6 |  | 16054 | 192.55 | 9.8715 | 60.295 | 0.025714 | 160.75 | 1143.6 | 982.85
16055 | 9.8736 | 192.56 | 60.295 | 0.02572 | 160.76 | 1143.6 |  | 16055 | 192.56 | 9.8736 | 60.295 | 0.02572 | 160.76 | 1143.6 | 982.84
16056 | 9.8757 | 192.57 | 60.295 | 0.025725 | 160.77 | 1143.6 |  | 16056 | 192.57 | 9.8757 | 60.295 | 0.025725 | 160.77 | 1143.6 | 982.83
16057 | 9.8778 | 192.58 | 60.294 | 0.02573 | 160.78 | 1143.6 |  | 16057 | 192.58 | 9.8778 | 60.294 | 0.02573 | 160.78 | 1143.6 | 982.82
16058 | 9.8799 | 192.59 | 60.294 | 0.025735 | 160.79 | 1143.6 |  | 16058 | 192.59 | 9.8799 | 60.294 | 0.025735 | 160.79 | 1143.6 | 982.81
16059 | 9.882 | 192.6 | 60.294 | 0.02574 | 160.8 | 1143.6 |  | 16059 | 192.6 | 9.882 | 60.294 | 0.02574 | 160.8 | 1143.6 | 982.8
16060 | 9.8841 | 192.61 | 60.294 | 0.025745 | 160.81 | 1143.6 |  | 16060 | 192.61 | 9.8841 | 60.294 | 0.025745 | 160.81 | 1143.6 | 982.79
16061 | 9.8862 | 192.62 | 60.293 | 0.02575 | 160.82 | 1143.6 |  | 16061 | 192.62 | 9.8862 | 60.293 | 0.02575 | 160.82 | 1143.6 | 982.78
16062 | 9.8883 | 192.63 | 60.293 | 0.025755 | 160.83 | 1143.6 |  | 16062 | 192.63 | 9.8883 | 60.293 | 0.025755 | 160.83 | 1143.6 | 982.77
16063 | 9.8904 | 192.64 | 60.293 | 0.02576 | 160.84 | 1143.6 |  | 16063 | 192.64 | 9.8904 | 60.293 | 0.02576 | 160.84 | 1143.6 | 982.76
16064 | 9.8925 | 192.65 | 60.293 | 0.025766 | 160.85 | 1143.6 |  | 16064 | 192.65 | 9.8925 | 60.293 | 0.025766 | 160.85 | 1143.6 | 982.75
16065 | 9.8946 | 192.66 | 60.293 | 0.025771 | 160.86 | 1143.6 |  | 16065 | 192.66 | 9.8946 | 60.293 | 0.025771 | 160.86 | 1143.6 | 982.74
16066 | 9.8967 | 192.67 | 60.292 | 0.025776 | 160.87 | 1143.6 |  | 16066 | 192.67 | 9.8967 | 60.292 | 0.025776 | 160.87 | 1143.6 | 982.73
16067 | 9.8988 | 192.68 | 60.292 | 0.025781 | 160.88 | 1143.6 |  | 16067 | 192.68 | 9.8988 | 60.292 | 0.025781 | 160.88 | 1143.6 | 982.72
16068 | 9.9009 | 192.69 | 60.292 | 0.025786 | 160.89 | 1143.6 |  | 16068 | 192.69 | 9.9009 | 60.292 | 0.025786 | 160.89 | 1143.6 | 982.71
16069 | 9.903 | 192.7 | 60.292 | 0.025791 | 160.9 | 1143.7 |  | 16069 | 192.7 | 9.903 | 60.292 | 0.025791 | 160.9 | 1143.7 | 982.8
16070 | 9.9051 | 192.71 | 60.291 | 0.025796 | 160.91 | 1143.7 |  | 16070 | 192.71 | 9.9051 | 60.291 | 0.025796 | 160.91 | 1143.7 | 982.79
16071 | 9.9072 | 192.72 | 60.291 | 0.025801 | 160.92 | 1143.7 |  | 16071 | 192.72 | 9.9072 | 60.291 | 0.025801 | 160.92 | 1143.7 | 982.78
16072 | 9.9093 | 192.73 | 60.291 | 0.025806 | 160.93 | 1143.7 |  | 16072 | 192.73 | 9.9093 | 60.291 | 0.025806 | 160.93 | 1143.7 | 982.77
16073 | 9.9114 | 192.74 | 60.291 | 0.025812 | 160.94 | 1143.7 |  | 16073 | 192.74 | 9.9114 | 60.291 | 0.025812 | 160.94 | 1143.7 | 982.76
16074 | 9.9135 | 192.75 | 60.29 | 0.025817 | 160.95 | 1143.7 |  | 16074 | 192.75 | 9.9135 | 60.29 | 0.025817 | 160.95 | 1143.7 | 982.75
16075 | 9.9156 | 192.76 | 60.29 | 0.025822 | 160.96 | 1143.7 |  | 16075 | 192.76 | 9.9156 | 60.29 | 0.025822 | 160.96 | 1143.7 | 982.74
16076 | 9.9177 | 192.77 | 60.29 | 0.025827 | 160.97 | 1143.7 |  | 16076 | 192.77 | 9.9177 | 60.29 | 0.025827 | 160.97 | 1143.7 | 982.73
16077 | 9.9198 | 192.78 | 60.29 | 0.025832 | 160.98 | 1143.7 |  | 16077 | 192.78 | 9.9198 | 60.29 | 0.025832 | 160.98 | 1143.7 | 982.72
16078 | 9.9219 | 192.79 | 60.29 | 0.025837 | 160.99 | 1143.7 |  | 16078 | 192.79 | 9.9219 | 60.29 | 0.025837 | 160.99 | 1143.7 | 982.71
16079 | 9.924 | 192.8 | 60.289 | 0.025842 | 161 | 1143.7 |  | 16079 | 192.8 | 9.924 | 60.289 | 0.025842 | 161 | 1143.7 | 982.7
16080 | 9.9261 | 192.81 | 60.289 | 0.025847 | 161.01 | 1143.7 |  | 16080 | 192.81 | 9.9261 | 60.289 | 0.025847 | 161.01 | 1143.7 | 982.69
16081 | 9.9282 | 192.82 | 60.289 | 0.025853 | 161.02 | 1143.7 |  | 16081 | 192.82 | 9.9282 | 60.289 | 0.025853 | 161.02 | 1143.7 | 982.68
16082 | 9.9303 | 192.83 | 60.289 | 0.025858 | 161.03 | 1143.7 |  | 16082 | 192.83 | 9.9303 | 60.289 | 0.025858 | 161.03 | 1143.7 | 982.67
16083 | 9.9324 | 192.84 | 60.288 | 0.025863 | 161.04 | 1143.7 |  | 16083 | 192.84 | 9.9324 | 60.288 | 0.025863 | 161.04 | 1143.7 | 982.66
16084 | 9.9345 | 192.85 | 60.288 | 0.025868 | 161.05 | 1143.7 |  | 16084 | 192.85 | 9.9345 | 60.288 | 0.025868 | 161.05 | 1143.7 | 982.65
16085 | 9.9366 | 192.86 | 60.288 | 0.025873 | 161.06 | 1143.7 |  | 16085 | 192.86 | 9.9366 | 60.288 | 0.025873 | 161.06 | 1143.7 | 982.64
16086 | 9.9387 | 192.87 | 60.288 | 0.025878 | 161.07 | 1143.7 |  | 16086 | 192.87 | 9.9387 | 60.288 | 0.025878 | 161.07 | 1143.7 | 982.63
16087 | 9.9408 | 192.88 | 60.287 | 0.025883 | 161.08 | 1143.7 |  | 16087 | 192.88 | 9.9408 | 60.287 | 0.025883 | 161.08 | 1143.7 | 982.62
16088 | 9.9429 | 192.89 | 60.287 | 0.025888 | 161.09 | 1143.7 |  | 16088 | 192.89 | 9.9429 | 60.287 | 0.025888 | 161.09 | 1143.7 | 982.61
16089 | 9.945 | 192.9 | 60.287 | 0.025894 | 161.1 | 1143.7 |  | 16089 | 192.9 | 9.945 | 60.287 | 0.025894 | 161.1 | 1143.7 | 982.6
16090 | 9.9471 | 192.91 | 60.287 | 0.025899 | 161.11 | 1143.7 |  | 16090 | 192.91 | 9.9471 | 60.287 | 0.025899 | 161.11 | 1143.7 | 982.59
16091 | 9.9492 | 192.92 | 60.287 | 0.025904 | 161.12 | 1143.7 |  | 16091 | 192.92 | 9.9492 | 60.287 | 0.025904 | 161.12 | 1143.7 | 982.58
16092 | 9.9513 | 192.93 | 60.286 | 0.025909 | 161.13 | 1143.7 |  | 16092 | 192.93 | 9.9513 | 60.286 | 0.025909 | 161.13 | 1143.7 | 982.57
16093 | 9.9535 | 192.94 | 60.286 | 0.025914 | 161.14 | 1143.7 |  | 16093 | 192.94 | 9.9535 | 60.286 | 0.025914 | 161.14 | 1143.7 | 982.56
16094 | 9.9556 | 192.95 | 60.286 | 0.025919 | 161.15 | 1143.7 |  | 16094 | 192.95 | 9.9556 | 60.286 | 0.025919 | 161.15 | 1143.7 | 982.55
16095 | 9.9577 | 192.96 | 60.286 | 0.025924 | 161.16 | 1143.8 |  | 16095 | 192.96 | 9.9577 | 60.286 | 0.025924 | 161.16 | 1143.8 | 982.64
16096 | 9.9598 | 192.97 | 60.285 | 0.025929 | 161.17 | 1143.8 |  | 16096 | 192.97 | 9.9598 | 60.285 | 0.025929 | 161.17 | 1143.8 | 982.63
16097 | 9.9619 | 192.98 | 60.285 | 0.025935 | 161.18 | 1143.8 |  | 16097 | 192.98 | 9.9619 | 60.285 | 0.025935 | 161.18 | 1143.8 | 982.62
16098 | 9.964 | 192.99 | 60.285 | 0.02594 | 161.19 | 1143.8 |  | 16098 | 192.99 | 9.964 | 60.285 | 0.02594 | 161.19 | 1143.8 | 982.61
16099 | 9.9661 | 193 | 60.285 | 0.025945 | 161.2 | 1143.8 |  | 16099 | 193 | 9.9661 | 60.285 | 0.025945 | 161.2 | 1143.8 | 982.6
16100 | 9.9682 | 193.01 | 60.284 | 0.02595 | 161.21 | 1143.8 |  | 16100 | 193.01 | 9.9682 | 60.284 | 0.02595 | 161.21 | 1143.8 | 982.59
16101 | 9.9703 | 193.02 | 60.284 | 0.025955 | 161.22 | 1143.8 |  | 16101 | 193.02 | 9.9703 | 60.284 | 0.025955 | 161.22 | 1143.8 | 982.58
16102 | 9.9724 | 193.03 | 60.284 | 0.02596 | 161.23 | 1143.8 |  | 16102 | 193.03 | 9.9724 | 60.284 | 0.02596 | 161.23 | 1143.8 | 982.57
16103 | 9.9746 | 193.04 | 60.284 | 0.025965 | 161.24 | 1143.8 |  | 16103 | 193.04 | 9.9746 | 60.284 | 0.025965 | 161.24 | 1143.8 | 982.56
16104 | 9.9767 | 193.05 | 60.283 | 0.025971 | 161.25 | 1143.8 |  | 16104 | 193.05 | 9.9767 | 60.283 | 0.025971 | 161.25 | 1143.8 | 982.55
16105 | 9.9788 | 193.06 | 60.283 | 0.025976 | 161.26 | 1143.8 |  | 16105 | 193.06 | 9.9788 | 60.283 | 0.025976 | 161.26 | 1143.8 | 982.54
16106 | 9.9809 | 193.07 | 60.283 | 0.025981 | 161.27 | 1143.8 |  | 16106 | 193.07 | 9.9809 | 60.283 | 0.025981 | 161.27 | 1143.8 | 982.53
16107 | 9.983 | 193.08 | 60.283 | 0.025986 | 161.28 | 1143.8 |  | 16107 | 193.08 | 9.983 | 60.283 | 0.025986 | 161.28 | 1143.8 | 982.52
16108 | 9.9851 | 193.09 | 60.283 | 0.025991 | 161.29 | 1143.8 |  | 16108 | 193.09 | 9.9851 | 60.283 | 0.025991 | 161.29 | 1143.8 | 982.51
16109 | 9.9872 | 193.1 | 60.282 | 0.025996 | 161.3 | 1143.8 |  | 16109 | 193.1 | 9.9872 | 60.282 | 0.025996 | 161.3 | 1143.8 | 982.5
16110 | 9.9893 | 193.11 | 60.282 | 0.026001 | 161.31 | 1143.8 |  | 16110 | 193.11 | 9.9893 | 60.282 | 0.026001 | 161.31 | 1143.8 | 982.49
16111 | 9.9915 | 193.12 | 60.282 | 0.026007 | 161.32 | 1143.8 |  | 16111 | 193.12 | 9.9915 | 60.282 | 0.026007 | 161.32 | 1143.8 | 982.48
16112 | 9.9936 | 193.13 | 60.282 | 0.026012 | 161.33 | 1143.8 |  | 16112 | 193.13 | 9.9936 | 60.282 | 0.026012 | 161.33 | 1143.8 | 982.47
16113 | 9.9957 | 193.14 | 60.281 | 0.026017 | 161.34 | 1143.8 |  | 16113 | 193.14 | 9.9957 | 60.281 | 0.026017 | 161.34 | 1143.8 | 982.46
16114 | 9.9978 | 193.15 | 60.281 | 0.026022 | 161.35 | 1143.8 |  | 16114 | 193.15 | 9.9978 | 60.281 | 0.026022 | 161.35 | 1143.8 | 982.45
16115 | 9.9999 | 193.16 | 60.281 | 0.026027 | 161.36 | 1143.8 |  | 16115 | 193.16 | 9.9999 | 60.281 | 0.026027 | 161.36 | 1143.8 | 982.44
16116 | 10.002 | 193.17 | 60.281 | 0.026032 | 161.37 | 1143.8 |  | 16116 | 193.17 | 10.002 | 60.281 | 0.026032 | 161.37 | 1143.8 | 982.43
16117 | 10.004 | 193.18 | 60.28 | 0.026038 | 161.38 | 1143.8 |  | 16117 | 193.18 | 10.004 | 60.28 | 0.026038 | 161.38 | 1143.8 | 982.42
16118 | 10.006 | 193.19 | 60.28 | 0.026043 | 161.39 | 1143.8 |  | 16118 | 193.19 | 10.006 | 60.28 | 0.026043 | 161.39 | 1143.8 | 982.41
16119 | 10.008 | 193.2 | 60.28 | 0.026048 | 161.4 | 1143.8 |  | 16119 | 193.2 | 10.008 | 60.28 | 0.026048 | 161.4 | 1143.8 | 982.4
16120 | 10.011 | 193.21 | 60.28 | 0.026053 | 161.41 | 1143.8 |  | 16120 | 193.21 | 10.011 | 60.28 | 0.026053 | 161.41 | 1143.8 | 982.39
16121 | 10.013 | 193.22 | 60.28 | 0.026058 | 161.42 | 1143.9 |  | 16121 | 193.22 | 10.013 | 60.28 | 0.026058 | 161.42 | 1143.9 | 982.48
16122 | 10.015 | 193.23 | 60.279 | 0.026063 | 161.43 | 1143.9 |  | 16122 | 193.23 | 10.015 | 60.279 | 0.026063 | 161.43 | 1143.9 | 982.47
16123 | 10.017 | 193.24 | 60.279 | 0.026068 | 161.44 | 1143.9 |  | 16123 | 193.24 | 10.017 | 60.279 | 0.026068 | 161.44 | 1143.9 | 982.46
16124 | 10.019 | 193.25 | 60.279 | 0.026074 | 161.45 | 1143.9 |  | 16124 | 193.25 | 10.019 | 60.279 | 0.026074 | 161.45 | 1143.9 | 982.45
16125 | 10.021 | 193.26 | 60.279 | 0.026079 | 161.46 | 1143.9 |  | 16125 | 193.26 | 10.021 | 60.279 | 0.026079 | 161.46 | 1143.9 | 982.44
16126 | 10.023 | 193.27 | 60.278 | 0.026084 | 161.47 | 1143.9 |  | 16126 | 193.27 | 10.023 | 60.278 | 0.026084 | 161.47 | 1143.9 | 982.43
16127 | 10.025 | 193.28 | 60.278 | 0.026089 | 161.48 | 1143.9 |  | 16127 | 193.28 | 10.025 | 60.278 | 0.026089 | 161.48 | 1143.9 | 982.42
16128 | 10.027 | 193.29 | 60.278 | 0.026094 | 161.49 | 1143.9 |  | 16128 | 193.29 | 10.027 | 60.278 | 0.026094 | 161.49 | 1143.9 | 982.41
16129 | 10.03 | 193.3 | 60.278 | 0.026099 | 161.5 | 1143.9 |  | 16129 | 193.3 | 10.03 | 60.278 | 0.026099 | 161.5 | 1143.9 | 982.4
16130 | 10.032 | 193.31 | 60.277 | 0.026105 | 161.51 | 1143.9 |  | 16130 | 193.31 | 10.032 | 60.277 | 0.026105 | 161.51 | 1143.9 | 982.39
16131 | 10.034 | 193.32 | 60.277 | 0.02611 | 161.52 | 1143.9 |  | 16131 | 193.32 | 10.034 | 60.277 | 0.02611 | 161.52 | 1143.9 | 982.38
16132 | 10.036 | 193.33 | 60.277 | 0.026115 | 161.53 | 1143.9 |  | 16132 | 193.33 | 10.036 | 60.277 | 0.026115 | 161.53 | 1143.9 | 982.37
16133 | 10.038 | 193.34 | 60.277 | 0.02612 | 161.54 | 1143.9 |  | 16133 | 193.34 | 10.038 | 60.277 | 0.02612 | 161.54 | 1143.9 | 982.36
16134 | 10.04 | 193.35 | 60.277 | 0.026125 | 161.55 | 1143.9 |  | 16134 | 193.35 | 10.04 | 60.277 | 0.026125 | 161.55 | 1143.9 | 982.35
16135 | 10.042 | 193.36 | 60.276 | 0.02613 | 161.56 | 1143.9 |  | 16135 | 193.36 | 10.042 | 60.276 | 0.02613 | 161.56 | 1143.9 | 982.34
16136 | 10.044 | 193.37 | 60.276 | 0.026136 | 161.57 | 1143.9 |  | 16136 | 193.37 | 10.044 | 60.276 | 0.026136 | 161.57 | 1143.9 | 982.33
16137 | 10.047 | 193.38 | 60.276 | 0.026141 | 161.58 | 1143.9 |  | 16137 | 193.38 | 10.047 | 60.276 | 0.026141 | 161.58 | 1143.9 | 982.32
16138 | 10.049 | 193.39 | 60.276 | 0.026146 | 161.59 | 1143.9 |  | 16138 | 193.39 | 10.049 | 60.276 | 0.026146 | 161.59 | 1143.9 | 982.31
16139 | 10.051 | 193.4 | 60.275 | 0.026151 | 161.6 | 1143.9 |  | 16139 | 193.4 | 10.051 | 60.275 | 0.026151 | 161.6 | 1143.9 | 982.3
16140 | 10.053 | 193.41 | 60.275 | 0.026156 | 161.61 | 1143.9 |  | 16140 | 193.41 | 10.053 | 60.275 | 0.026156 | 161.61 | 1143.9 | 982.29
16141 | 10.055 | 193.42 | 60.275 | 0.026162 | 161.62 | 1143.9 |  | 16141 | 193.42 | 10.055 | 60.275 | 0.026162 | 161.62 | 1143.9 | 982.28
16142 | 10.057 | 193.43 | 60.275 | 0.026167 | 161.63 | 1143.9 |  | 16142 | 193.43 | 10.057 | 60.275 | 0.026167 | 161.63 | 1143.9 | 982.27
16143 | 10.059 | 193.44 | 60.274 | 0.026172 | 161.64 | 1143.9 |  | 16143 | 193.44 | 10.059 | 60.274 | 0.026172 | 161.64 | 1143.9 | 982.26
16144 | 10.061 | 193.45 | 60.274 | 0.026177 | 161.65 | 1143.9 |  | 16144 | 193.45 | 10.061 | 60.274 | 0.026177 | 161.65 | 1143.9 | 982.25
16145 | 10.064 | 193.46 | 60.274 | 0.026182 | 161.66 | 1143.9 |  | 16145 | 193.46 | 10.064 | 60.274 | 0.026182 | 161.66 | 1143.9 | 982.24
16146 | 10.066 | 193.47 | 60.274 | 0.026187 | 161.67 | 1144 |  | 16146 | 193.47 | 10.066 | 60.274 | 0.026187 | 161.67 | 1144 | 982.33
16147 | 10.068 | 193.48 | 60.274 | 0.026193 | 161.68 | 1144 |  | 16147 | 193.48 | 10.068 | 60.274 | 0.026193 | 161.68 | 1144 | 982.32
16148 | 10.07 | 193.49 | 60.273 | 0.026198 | 161.69 | 1144 |  | 16148 | 193.49 | 10.07 | 60.273 | 0.026198 | 161.69 | 1144 | 982.31
16149 | 10.072 | 193.5 | 60.273 | 0.026203 | 161.7 | 1144 |  | 16149 | 193.5 | 10.072 | 60.273 | 0.026203 | 161.7 | 1144 | 982.3
16150 | 10.074 | 193.51 | 60.273 | 0.026208 | 161.71 | 1144 |  | 16150 | 193.51 | 10.074 | 60.273 | 0.026208 | 161.71 | 1144 | 982.29
16151 | 10.076 | 193.52 | 60.273 | 0.026213 | 161.72 | 1144 |  | 16151 | 193.52 | 10.076 | 60.273 | 0.026213 | 161.72 | 1144 | 982.28
16152 | 10.078 | 193.53 | 60.272 | 0.026218 | 161.73 | 1144 |  | 16152 | 193.53 | 10.078 | 60.272 | 0.026218 | 161.73 | 1144 | 982.27
16153 | 10.081 | 193.54 | 60.272 | 0.026224 | 161.74 | 1144 |  | 16153 | 193.54 | 10.081 | 60.272 | 0.026224 | 161.74 | 1144 | 982.26
16154 | 10.083 | 193.55 | 60.272 | 0.026229 | 161.75 | 1144 |  | 16154 | 193.55 | 10.083 | 60.272 | 0.026229 | 161.75 | 1144 | 982.25
16155 | 10.085 | 193.56 | 60.272 | 0.026234 | 161.76 | 1144 |  | 16155 | 193.56 | 10.085 | 60.272 | 0.026234 | 161.76 | 1144 | 982.24
16156 | 10.087 | 193.57 | 60.271 | 0.026239 | 161.77 | 1144 |  | 16156 | 193.57 | 10.087 | 60.271 | 0.026239 | 161.77 | 1144 | 982.23
16157 | 10.089 | 193.58 | 60.271 | 0.026244 | 161.78 | 1144 |  | 16157 | 193.58 | 10.089 | 60.271 | 0.026244 | 161.78 | 1144 | 982.22
16158 | 10.091 | 193.59 | 60.271 | 0.02625 | 161.79 | 1144 |  | 16158 | 193.59 | 10.091 | 60.271 | 0.02625 | 161.79 | 1144 | 982.21
16159 | 10.093 | 193.6 | 60.271 | 0.026255 | 161.8 | 1144 |  | 16159 | 193.6 | 10.093 | 60.271 | 0.026255 | 161.8 | 1144 | 982.2
16160 | 10.096 | 193.61 | 60.27 | 0.02626 | 161.81 | 1144 |  | 16160 | 193.61 | 10.096 | 60.27 | 0.02626 | 161.81 | 1144 | 982.19
16161 | 10.098 | 193.62 | 60.27 | 0.026265 | 161.82 | 1144 |  | 16161 | 193.62 | 10.098 | 60.27 | 0.026265 | 161.82 | 1144 | 982.18
16162 | 10.1 | 193.63 | 60.27 | 0.02627 | 161.83 | 1144 |  | 16162 | 193.63 | 10.1 | 60.27 | 0.02627 | 161.83 | 1144 | 982.17
16163 | 10.102 | 193.64 | 60.27 | 0.026276 | 161.84 | 1144 |  | 16163 | 193.64 | 10.102 | 60.27 | 0.026276 | 161.84 | 1144 | 982.16
16164 | 10.104 | 193.65 | 60.27 | 0.026281 | 161.85 | 1144 |  | 16164 | 193.65 | 10.104 | 60.27 | 0.026281 | 161.85 | 1144 | 982.15
16165 | 10.106 | 193.66 | 60.269 | 0.026286 | 161.86 | 1144 |  | 16165 | 193.66 | 10.106 | 60.269 | 0.026286 | 161.86 | 1144 | 982.14
16166 | 10.108 | 193.67 | 60.269 | 0.026291 | 161.87 | 1144 |  | 16166 | 193.67 | 10.108 | 60.269 | 0.026291 | 161.87 | 1144 | 982.13
16167 | 10.11 | 193.68 | 60.269 | 0.026296 | 161.88 | 1144 |  | 16167 | 193.68 | 10.11 | 60.269 | 0.026296 | 161.88 | 1144 | 982.12
16168 | 10.113 | 193.69 | 60.269 | 0.026302 | 161.89 | 1144 |  | 16168 | 193.69 | 10.113 | 60.269 | 0.026302 | 161.89 | 1144 | 982.11
16169 | 10.115 | 193.7 | 60.268 | 0.026307 | 161.9 | 1144 |  | 16169 | 193.7 | 10.115 | 60.268 | 0.026307 | 161.9 | 1144 | 982.1
16170 | 10.117 | 193.71 | 60.268 | 0.026312 | 161.91 | 1144 |  | 16170 | 193.71 | 10.117 | 60.268 | 0.026312 | 161.91 | 1144 | 982.09
16171 | 10.119 | 193.72 | 60.268 | 0.026317 | 161.92 | 1144 |  | 16171 | 193.72 | 10.119 | 60.268 | 0.026317 | 161.92 | 1144 | 982.08
16172 | 10.121 | 193.73 | 60.268 | 0.026322 | 161.93 | 1144.1 |  | 16172 | 193.73 | 10.121 | 60.268 | 0.026322 | 161.93 | 1144.1 | 982.17
16173 | 10.123 | 193.74 | 60.267 | 0.026328 | 161.94 | 1144.1 |  | 16173 | 193.74 | 10.123 | 60.267 | 0.026328 | 161.94 | 1144.1 | 982.16
16174 | 10.125 | 193.75 | 60.267 | 0.026333 | 161.95 | 1144.1 |  | 16174 | 193.75 | 10.125 | 60.267 | 0.026333 | 161.95 | 1144.1 | 982.15
16175 | 10.128 | 193.76 | 60.267 | 0.026338 | 161.96 | 1144.1 |  | 16175 | 193.76 | 10.128 | 60.267 | 0.026338 | 161.96 | 1144.1 | 982.14
16176 | 10.13 | 193.77 | 60.267 | 0.026343 | 161.97 | 1144.1 |  | 16176 | 193.77 | 10.13 | 60.267 | 0.026343 | 161.97 | 1144.1 | 982.13
16177 | 10.132 | 193.78 | 60.267 | 0.026348 | 161.99 | 1144.1 |  | 16177 | 193.78 | 10.132 | 60.267 | 0.026348 | 161.99 | 1144.1 | 982.11
16178 | 10.134 | 193.79 | 60.266 | 0.026354 | 162 | 1144.1 |  | 16178 | 193.79 | 10.134 | 60.266 | 0.026354 | 162 | 1144.1 | 982.1
16179 | 10.136 | 193.8 | 60.266 | 0.026359 | 162.01 | 1144.1 |  | 16179 | 193.8 | 10.136 | 60.266 | 0.026359 | 162.01 | 1144.1 | 982.09
16180 | 10.138 | 193.81 | 60.266 | 0.026364 | 162.02 | 1144.1 |  | 16180 | 193.81 | 10.138 | 60.266 | 0.026364 | 162.02 | 1144.1 | 982.08
16181 | 10.14 | 193.82 | 60.266 | 0.026369 | 162.03 | 1144.1 |  | 16181 | 193.82 | 10.14 | 60.266 | 0.026369 | 162.03 | 1144.1 | 982.07
16182 | 10.143 | 193.83 | 60.265 | 0.026374 | 162.04 | 1144.1 |  | 16182 | 193.83 | 10.143 | 60.265 | 0.026374 | 162.04 | 1144.1 | 982.06
16183 | 10.145 | 193.84 | 60.265 | 0.02638 | 162.05 | 1144.1 |  | 16183 | 193.84 | 10.145 | 60.265 | 0.02638 | 162.05 | 1144.1 | 982.05
16184 | 10.147 | 193.85 | 60.265 | 0.026385 | 162.06 | 1144.1 |  | 16184 | 193.85 | 10.147 | 60.265 | 0.026385 | 162.06 | 1144.1 | 982.04
16185 | 10.149 | 193.86 | 60.265 | 0.02639 | 162.07 | 1144.1 |  | 16185 | 193.86 | 10.149 | 60.265 | 0.02639 | 162.07 | 1144.1 | 982.03
16186 | 10.151 | 193.87 | 60.264 | 0.026395 | 162.08 | 1144.1 |  | 16186 | 193.87 | 10.151 | 60.264 | 0.026395 | 162.08 | 1144.1 | 982.02
16187 | 10.153 | 193.88 | 60.264 | 0.0264 | 162.09 | 1144.1 |  | 16187 | 193.88 | 10.153 | 60.264 | 0.0264 | 162.09 | 1144.1 | 982.01
16188 | 10.155 | 193.89 | 60.264 | 0.026406 | 162.1 | 1144.1 |  | 16188 | 193.89 | 10.155 | 60.264 | 0.026406 | 162.1 | 1144.1 | 982
16189 | 10.158 | 193.9 | 60.264 | 0.026411 | 162.11 | 1144.1 |  | 16189 | 193.9 | 10.158 | 60.264 | 0.026411 | 162.11 | 1144.1 | 981.99
16190 | 10.16 | 193.91 | 60.264 | 0.026416 | 162.12 | 1144.1 |  | 16190 | 193.91 | 10.16 | 60.264 | 0.026416 | 162.12 | 1144.1 | 981.98
16191 | 10.162 | 193.92 | 60.263 | 0.026421 | 162.13 | 1144.1 |  | 16191 | 193.92 | 10.162 | 60.263 | 0.026421 | 162.13 | 1144.1 | 981.97
16192 | 10.164 | 193.93 | 60.263 | 0.026427 | 162.14 | 1144.1 |  | 16192 | 193.93 | 10.164 | 60.263 | 0.026427 | 162.14 | 1144.1 | 981.96
16193 | 10.166 | 193.94 | 60.263 | 0.026432 | 162.15 | 1144.1 |  | 16193 | 193.94 | 10.166 | 60.263 | 0.026432 | 162.15 | 1144.1 | 981.95
16194 | 10.168 | 193.95 | 60.263 | 0.026437 | 162.16 | 1144.1 |  | 16194 | 193.95 | 10.168 | 60.263 | 0.026437 | 162.16 | 1144.1 | 981.94
16195 | 10.17 | 193.96 | 60.262 | 0.026442 | 162.17 | 1144.1 |  | 16195 | 193.96 | 10.17 | 60.262 | 0.026442 | 162.17 | 1144.1 | 981.93
16196 | 10.173 | 193.97 | 60.262 | 0.026447 | 162.18 | 1144.1 |  | 16196 | 193.97 | 10.173 | 60.262 | 0.026447 | 162.18 | 1144.1 | 981.92
16197 | 10.175 | 193.98 | 60.262 | 0.026453 | 162.19 | 1144.1 |  | 16197 | 193.98 | 10.175 | 60.262 | 0.026453 | 162.19 | 1144.1 | 981.91
16198 | 10.177 | 193.99 | 60.262 | 0.026458 | 162.2 | 1144.2 |  | 16198 | 193.99 | 10.177 | 60.262 | 0.026458 | 162.2 | 1144.2 | 982
16199 | 10.179 | 194 | 60.261 | 0.026463 | 162.21 | 1144.2 |  | 16199 | 194 | 10.179 | 60.261 | 0.026463 | 162.21 | 1144.2 | 981.99
16200 | 10.181 | 194.01 | 60.261 | 0.026468 | 162.22 | 1144.2 |  | 16200 | 194.01 | 10.181 | 60.261 | 0.026468 | 162.22 | 1144.2 | 981.98
16201 | 10.183 | 194.02 | 60.261 | 0.026474 | 162.23 | 1144.2 |  | 16201 | 194.02 | 10.183 | 60.261 | 0.026474 | 162.23 | 1144.2 | 981.97
16202 | 10.185 | 194.03 | 60.261 | 0.026479 | 162.24 | 1144.2 |  | 16202 | 194.03 | 10.185 | 60.261 | 0.026479 | 162.24 | 1144.2 | 981.96
16203 | 10.188 | 194.04 | 60.26 | 0.026484 | 162.25 | 1144.2 |  | 16203 | 194.04 | 10.188 | 60.26 | 0.026484 | 162.25 | 1144.2 | 981.95
16204 | 10.19 | 194.05 | 60.26 | 0.026489 | 162.26 | 1144.2 |  | 16204 | 194.05 | 10.19 | 60.26 | 0.026489 | 162.26 | 1144.2 | 981.94
16205 | 10.192 | 194.06 | 60.26 | 0.026494 | 162.27 | 1144.2 |  | 16205 | 194.06 | 10.192 | 60.26 | 0.026494 | 162.27 | 1144.2 | 981.93
16206 | 10.194 | 194.07 | 60.26 | 0.0265 | 162.28 | 1144.2 |  | 16206 | 194.07 | 10.194 | 60.26 | 0.0265 | 162.28 | 1144.2 | 981.92
16207 | 10.196 | 194.08 | 60.26 | 0.026505 | 162.29 | 1144.2 |  | 16207 | 194.08 | 10.196 | 60.26 | 0.026505 | 162.29 | 1144.2 | 981.91
16208 | 10.198 | 194.09 | 60.259 | 0.02651 | 162.3 | 1144.2 |  | 16208 | 194.09 | 10.198 | 60.259 | 0.02651 | 162.3 | 1144.2 | 981.9
16209 | 10.201 | 194.1 | 60.259 | 0.026515 | 162.31 | 1144.2 |  | 16209 | 194.1 | 10.201 | 60.259 | 0.026515 | 162.31 | 1144.2 | 981.89
16210 | 10.203 | 194.11 | 60.259 | 0.026521 | 162.32 | 1144.2 |  | 16210 | 194.11 | 10.203 | 60.259 | 0.026521 | 162.32 | 1144.2 | 981.88
16211 | 10.205 | 194.12 | 60.259 | 0.026526 | 162.33 | 1144.2 |  | 16211 | 194.12 | 10.205 | 60.259 | 0.026526 | 162.33 | 1144.2 | 981.87
16212 | 10.207 | 194.13 | 60.258 | 0.026531 | 162.34 | 1144.2 |  | 16212 | 194.13 | 10.207 | 60.258 | 0.026531 | 162.34 | 1144.2 | 981.86
16213 | 10.209 | 194.14 | 60.258 | 0.026536 | 162.35 | 1144.2 |  | 16213 | 194.14 | 10.209 | 60.258 | 0.026536 | 162.35 | 1144.2 | 981.85
16214 | 10.211 | 194.15 | 60.258 | 0.026542 | 162.36 | 1144.2 |  | 16214 | 194.15 | 10.211 | 60.258 | 0.026542 | 162.36 | 1144.2 | 981.84
16215 | 10.213 | 194.16 | 60.258 | 0.026547 | 162.37 | 1144.2 |  | 16215 | 194.16 | 10.213 | 60.258 | 0.026547 | 162.37 | 1144.2 | 981.83
16216 | 10.216 | 194.17 | 60.257 | 0.026552 | 162.38 | 1144.2 |  | 16216 | 194.17 | 10.216 | 60.257 | 0.026552 | 162.38 | 1144.2 | 981.82
16217 | 10.218 | 194.18 | 60.257 | 0.026557 | 162.39 | 1144.2 |  | 16217 | 194.18 | 10.218 | 60.257 | 0.026557 | 162.39 | 1144.2 | 981.81
16218 | 10.22 | 194.19 | 60.257 | 0.026562 | 162.4 | 1144.2 |  | 16218 | 194.19 | 10.22 | 60.257 | 0.026562 | 162.4 | 1144.2 | 981.8
16219 | 10.222 | 194.2 | 60.257 | 0.026568 | 162.41 | 1144.2 |  | 16219 | 194.2 | 10.222 | 60.257 | 0.026568 | 162.41 | 1144.2 | 981.79
16220 | 10.224 | 194.21 | 60.257 | 0.026573 | 162.42 | 1144.2 |  | 16220 | 194.21 | 10.224 | 60.257 | 0.026573 | 162.42 | 1144.2 | 981.78
16221 | 10.226 | 194.22 | 60.256 | 0.026578 | 162.43 | 1144.2 |  | 16221 | 194.22 | 10.226 | 60.256 | 0.026578 | 162.43 | 1144.2 | 981.77
16222 | 10.229 | 194.23 | 60.256 | 0.026583 | 162.44 | 1144.2 |  | 16222 | 194.23 | 10.229 | 60.256 | 0.026583 | 162.44 | 1144.2 | 981.76
16223 | 10.231 | 194.24 | 60.256 | 0.026589 | 162.45 | 1144.3 |  | 16223 | 194.24 | 10.231 | 60.256 | 0.026589 | 162.45 | 1144.3 | 981.85
16224 | 10.233 | 194.25 | 60.256 | 0.026594 | 162.46 | 1144.3 |  | 16224 | 194.25 | 10.233 | 60.256 | 0.026594 | 162.46 | 1144.3 | 981.84
16225 | 10.235 | 194.26 | 60.255 | 0.026599 | 162.47 | 1144.3 |  | 16225 | 194.26 | 10.235 | 60.255 | 0.026599 | 162.47 | 1144.3 | 981.83
16226 | 10.237 | 194.27 | 60.255 | 0.026604 | 162.48 | 1144.3 |  | 16226 | 194.27 | 10.237 | 60.255 | 0.026604 | 162.48 | 1144.3 | 981.82
16227 | 10.239 | 194.28 | 60.255 | 0.02661 | 162.49 | 1144.3 |  | 16227 | 194.28 | 10.239 | 60.255 | 0.02661 | 162.49 | 1144.3 | 981.81
16228 | 10.241 | 194.29 | 60.255 | 0.026615 | 162.5 | 1144.3 |  | 16228 | 194.29 | 10.241 | 60.255 | 0.026615 | 162.5 | 1144.3 | 981.8
16229 | 10.244 | 194.3 | 60.254 | 0.02662 | 162.51 | 1144.3 |  | 16229 | 194.3 | 10.244 | 60.254 | 0.02662 | 162.51 | 1144.3 | 981.79
16230 | 10.246 | 194.31 | 60.254 | 0.026625 | 162.52 | 1144.3 |  | 16230 | 194.31 | 10.246 | 60.254 | 0.026625 | 162.52 | 1144.3 | 981.78
16231 | 10.248 | 194.32 | 60.254 | 0.026631 | 162.53 | 1144.3 |  | 16231 | 194.32 | 10.248 | 60.254 | 0.026631 | 162.53 | 1144.3 | 981.77
16232 | 10.25 | 194.33 | 60.254 | 0.026636 | 162.54 | 1144.3 |  | 16232 | 194.33 | 10.25 | 60.254 | 0.026636 | 162.54 | 1144.3 | 981.76
16233 | 10.252 | 194.34 | 60.253 | 0.026641 | 162.55 | 1144.3 |  | 16233 | 194.34 | 10.252 | 60.253 | 0.026641 | 162.55 | 1144.3 | 981.75
16234 | 10.254 | 194.35 | 60.253 | 0.026646 | 162.56 | 1144.3 |  | 16234 | 194.35 | 10.254 | 60.253 | 0.026646 | 162.56 | 1144.3 | 981.74
16235 | 10.257 | 194.36 | 60.253 | 0.026652 | 162.57 | 1144.3 |  | 16235 | 194.36 | 10.257 | 60.253 | 0.026652 | 162.57 | 1144.3 | 981.73
16236 | 10.259 | 194.37 | 60.253 | 0.026657 | 162.58 | 1144.3 |  | 16236 | 194.37 | 10.259 | 60.253 | 0.026657 | 162.58 | 1144.3 | 981.72
16237 | 10.261 | 194.38 | 60.253 | 0.026662 | 162.59 | 1144.3 |  | 16237 | 194.38 | 10.261 | 60.253 | 0.026662 | 162.59 | 1144.3 | 981.71
16238 | 10.263 | 194.39 | 60.252 | 0.026667 | 162.6 | 1144.3 |  | 16238 | 194.39 | 10.263 | 60.252 | 0.026667 | 162.6 | 1144.3 | 981.7
16239 | 10.265 | 194.4 | 60.252 | 0.026673 | 162.61 | 1144.3 |  | 16239 | 194.4 | 10.265 | 60.252 | 0.026673 | 162.61 | 1144.3 | 981.69
16240 | 10.267 | 194.41 | 60.252 | 0.026678 | 162.62 | 1144.3 |  | 16240 | 194.41 | 10.267 | 60.252 | 0.026678 | 162.62 | 1144.3 | 981.68
16241 | 10.27 | 194.42 | 60.252 | 0.026683 | 162.63 | 1144.3 |  | 16241 | 194.42 | 10.27 | 60.252 | 0.026683 | 162.63 | 1144.3 | 981.67
16242 | 10.272 | 194.43 | 60.251 | 0.026689 | 162.64 | 1144.3 |  | 16242 | 194.43 | 10.272 | 60.251 | 0.026689 | 162.64 | 1144.3 | 981.66
16243 | 10.274 | 194.44 | 60.251 | 0.026694 | 162.65 | 1144.3 |  | 16243 | 194.44 | 10.274 | 60.251 | 0.026694 | 162.65 | 1144.3 | 981.65
16244 | 10.276 | 194.45 | 60.251 | 0.026699 | 162.66 | 1144.3 |  | 16244 | 194.45 | 10.276 | 60.251 | 0.026699 | 162.66 | 1144.3 | 981.64
16245 | 10.278 | 194.46 | 60.251 | 0.026704 | 162.67 | 1144.3 |  | 16245 | 194.46 | 10.278 | 60.251 | 0.026704 | 162.67 | 1144.3 | 981.63
16246 | 10.28 | 194.47 | 60.25 | 0.02671 | 162.68 | 1144.3 |  | 16246 | 194.47 | 10.28 | 60.25 | 0.02671 | 162.68 | 1144.3 | 981.62
16247 | 10.283 | 194.48 | 60.25 | 0.026715 | 162.69 | 1144.3 |  | 16247 | 194.48 | 10.283 | 60.25 | 0.026715 | 162.69 | 1144.3 | 981.61
16248 | 10.285 | 194.49 | 60.25 | 0.02672 | 162.7 | 1144.3 |  | 16248 | 194.49 | 10.285 | 60.25 | 0.02672 | 162.7 | 1144.3 | 981.6
16249 | 10.287 | 194.5 | 60.25 | 0.026725 | 162.71 | 1144.4 |  | 16249 | 194.5 | 10.287 | 60.25 | 0.026725 | 162.71 | 1144.4 | 981.69
16250 | 10.289 | 194.51 | 60.25 | 0.026731 | 162.72 | 1144.4 |  | 16250 | 194.51 | 10.289 | 60.25 | 0.026731 | 162.72 | 1144.4 | 981.68
16251 | 10.291 | 194.52 | 60.249 | 0.026736 | 162.73 | 1144.4 |  | 16251 | 194.52 | 10.291 | 60.249 | 0.026736 | 162.73 | 1144.4 | 981.67
16252 | 10.293 | 194.53 | 60.249 | 0.026741 | 162.74 | 1144.4 |  | 16252 | 194.53 | 10.293 | 60.249 | 0.026741 | 162.74 | 1144.4 | 981.66
16253 | 10.296 | 194.54 | 60.249 | 0.026746 | 162.75 | 1144.4 |  | 16253 | 194.54 | 10.296 | 60.249 | 0.026746 | 162.75 | 1144.4 | 981.65
16254 | 10.298 | 194.55 | 60.249 | 0.026752 | 162.76 | 1144.4 |  | 16254 | 194.55 | 10.298 | 60.249 | 0.026752 | 162.76 | 1144.4 | 981.64
16255 | 10.3 | 194.56 | 60.248 | 0.026757 | 162.77 | 1144.4 |  | 16255 | 194.56 | 10.3 | 60.248 | 0.026757 | 162.77 | 1144.4 | 981.63
16256 | 10.302 | 194.57 | 60.248 | 0.026762 | 162.78 | 1144.4 |  | 16256 | 194.57 | 10.302 | 60.248 | 0.026762 | 162.78 | 1144.4 | 981.62
16257 | 10.304 | 194.58 | 60.248 | 0.026768 | 162.79 | 1144.4 |  | 16257 | 194.58 | 10.304 | 60.248 | 0.026768 | 162.79 | 1144.4 | 981.61
16258 | 10.306 | 194.59 | 60.248 | 0.026773 | 162.8 | 1144.4 |  | 16258 | 194.59 | 10.306 | 60.248 | 0.026773 | 162.8 | 1144.4 | 981.6
16259 | 10.309 | 194.6 | 60.247 | 0.026778 | 162.81 | 1144.4 |  | 16259 | 194.6 | 10.309 | 60.247 | 0.026778 | 162.81 | 1144.4 | 981.59
16260 | 10.311 | 194.61 | 60.247 | 0.026783 | 162.82 | 1144.4 |  | 16260 | 194.61 | 10.311 | 60.247 | 0.026783 | 162.82 | 1144.4 | 981.58
16261 | 10.313 | 194.62 | 60.247 | 0.026789 | 162.83 | 1144.4 |  | 16261 | 194.62 | 10.313 | 60.247 | 0.026789 | 162.83 | 1144.4 | 981.57
16262 | 10.315 | 194.63 | 60.247 | 0.026794 | 162.84 | 1144.4 |  | 16262 | 194.63 | 10.315 | 60.247 | 0.026794 | 162.84 | 1144.4 | 981.56
16263 | 10.317 | 194.64 | 60.247 | 0.026799 | 162.85 | 1144.4 |  | 16263 | 194.64 | 10.317 | 60.247 | 0.026799 | 162.85 | 1144.4 | 981.55
16264 | 10.319 | 194.65 | 60.246 | 0.026804 | 162.86 | 1144.4 |  | 16264 | 194.65 | 10.319 | 60.246 | 0.026804 | 162.86 | 1144.4 | 981.54
16265 | 10.322 | 194.66 | 60.246 | 0.02681 | 162.87 | 1144.4 |  | 16265 | 194.66 | 10.322 | 60.246 | 0.02681 | 162.87 | 1144.4 | 981.53
16266 | 10.324 | 194.67 | 60.246 | 0.026815 | 162.88 | 1144.4 |  | 16266 | 194.67 | 10.324 | 60.246 | 0.026815 | 162.88 | 1144.4 | 981.52
16267 | 10.326 | 194.68 | 60.246 | 0.02682 | 162.89 | 1144.4 |  | 16267 | 194.68 | 10.326 | 60.246 | 0.02682 | 162.89 | 1144.4 | 981.51
16268 | 10.328 | 194.69 | 60.245 | 0.026826 | 162.9 | 1144.4 |  | 16268 | 194.69 | 10.328 | 60.245 | 0.026826 | 162.9 | 1144.4 | 981.5
16269 | 10.33 | 194.7 | 60.245 | 0.026831 | 162.91 | 1144.4 |  | 16269 | 194.7 | 10.33 | 60.245 | 0.026831 | 162.91 | 1144.4 | 981.49
16270 | 10.332 | 194.71 | 60.245 | 0.026836 | 162.92 | 1144.4 |  | 16270 | 194.71 | 10.332 | 60.245 | 0.026836 | 162.92 | 1144.4 | 981.48
16271 | 10.335 | 194.72 | 60.245 | 0.026841 | 162.93 | 1144.4 |  | 16271 | 194.72 | 10.335 | 60.245 | 0.026841 | 162.93 | 1144.4 | 981.47
16272 | 10.337 | 194.73 | 60.244 | 0.026847 | 162.94 | 1144.4 |  | 16272 | 194.73 | 10.337 | 60.244 | 0.026847 | 162.94 | 1144.4 | 981.46
16273 | 10.339 | 194.74 | 60.244 | 0.026852 | 162.95 | 1144.4 |  | 16273 | 194.74 | 10.339 | 60.244 | 0.026852 | 162.95 | 1144.4 | 981.45
16274 | 10.341 | 194.75 | 60.244 | 0.026857 | 162.96 | 1144.4 |  | 16274 | 194.75 | 10.341 | 60.244 | 0.026857 | 162.96 | 1144.4 | 981.44
16275 | 10.343 | 194.76 | 60.244 | 0.026863 | 162.97 | 1144.5 |  | 16275 | 194.76 | 10.343 | 60.244 | 0.026863 | 162.97 | 1144.5 | 981.53
16276 | 10.346 | 194.77 | 60.243 | 0.026868 | 162.98 | 1144.5 |  | 16276 | 194.77 | 10.346 | 60.243 | 0.026868 | 162.98 | 1144.5 | 981.52
16277 | 10.348 | 194.78 | 60.243 | 0.026873 | 162.99 | 1144.5 |  | 16277 | 194.78 | 10.348 | 60.243 | 0.026873 | 162.99 | 1144.5 | 981.51
16278 | 10.35 | 194.79 | 60.243 | 0.026878 | 163 | 1144.5 |  | 16278 | 194.79 | 10.35 | 60.243 | 0.026878 | 163 | 1144.5 | 981.5
16279 | 10.352 | 194.8 | 60.243 | 0.026884 | 163.01 | 1144.5 |  | 16279 | 194.8 | 10.352 | 60.243 | 0.026884 | 163.01 | 1144.5 | 981.49
16280 | 10.354 | 194.81 | 60.243 | 0.026889 | 163.02 | 1144.5 |  | 16280 | 194.81 | 10.354 | 60.243 | 0.026889 | 163.02 | 1144.5 | 981.48
16281 | 10.356 | 194.82 | 60.242 | 0.026894 | 163.03 | 1144.5 |  | 16281 | 194.82 | 10.356 | 60.242 | 0.026894 | 163.03 | 1144.5 | 981.47
16282 | 10.359 | 194.83 | 60.242 | 0.0269 | 163.04 | 1144.5 |  | 16282 | 194.83 | 10.359 | 60.242 | 0.0269 | 163.04 | 1144.5 | 981.46
16283 | 10.361 | 194.84 | 60.242 | 0.026905 | 163.05 | 1144.5 |  | 16283 | 194.84 | 10.361 | 60.242 | 0.026905 | 163.05 | 1144.5 | 981.45
16284 | 10.363 | 194.85 | 60.242 | 0.02691 | 163.06 | 1144.5 |  | 16284 | 194.85 | 10.363 | 60.242 | 0.02691 | 163.06 | 1144.5 | 981.44
16285 | 10.365 | 194.86 | 60.241 | 0.026915 | 163.07 | 1144.5 |  | 16285 | 194.86 | 10.365 | 60.241 | 0.026915 | 163.07 | 1144.5 | 981.43
16286 | 10.367 | 194.87 | 60.241 | 0.026921 | 163.08 | 1144.5 |  | 16286 | 194.87 | 10.367 | 60.241 | 0.026921 | 163.08 | 1144.5 | 981.42
16287 | 10.369 | 194.88 | 60.241 | 0.026926 | 163.09 | 1144.5 |  | 16287 | 194.88 | 10.369 | 60.241 | 0.026926 | 163.09 | 1144.5 | 981.41
16288 | 10.372 | 194.89 | 60.241 | 0.026931 | 163.1 | 1144.5 |  | 16288 | 194.89 | 10.372 | 60.241 | 0.026931 | 163.1 | 1144.5 | 981.4
16289 | 10.374 | 194.9 | 60.24 | 0.026937 | 163.11 | 1144.5 |  | 16289 | 194.9 | 10.374 | 60.24 | 0.026937 | 163.11 | 1144.5 | 981.39
16290 | 10.376 | 194.91 | 60.24 | 0.026942 | 163.12 | 1144.5 |  | 16290 | 194.91 | 10.376 | 60.24 | 0.026942 | 163.12 | 1144.5 | 981.38
16291 | 10.378 | 194.92 | 60.24 | 0.026947 | 163.13 | 1144.5 |  | 16291 | 194.92 | 10.378 | 60.24 | 0.026947 | 163.13 | 1144.5 | 981.37
16292 | 10.38 | 194.93 | 60.24 | 0.026953 | 163.14 | 1144.5 |  | 16292 | 194.93 | 10.38 | 60.24 | 0.026953 | 163.14 | 1144.5 | 981.36
16293 | 10.383 | 194.94 | 60.239 | 0.026958 | 163.15 | 1144.5 |  | 16293 | 194.94 | 10.383 | 60.239 | 0.026958 | 163.15 | 1144.5 | 981.35
16294 | 10.385 | 194.95 | 60.239 | 0.026963 | 163.16 | 1144.5 |  | 16294 | 194.95 | 10.385 | 60.239 | 0.026963 | 163.16 | 1144.5 | 981.34
16295 | 10.387 | 194.96 | 60.239 | 0.026969 | 163.17 | 1144.5 |  | 16295 | 194.96 | 10.387 | 60.239 | 0.026969 | 163.17 | 1144.5 | 981.33
16296 | 10.389 | 194.97 | 60.239 | 0.026974 | 163.18 | 1144.5 |  | 16296 | 194.97 | 10.389 | 60.239 | 0.026974 | 163.18 | 1144.5 | 981.32
16297 | 10.391 | 194.98 | 60.239 | 0.026979 | 163.19 | 1144.5 |  | 16297 | 194.98 | 10.391 | 60.239 | 0.026979 | 163.19 | 1144.5 | 981.31
16298 | 10.393 | 194.99 | 60.238 | 0.026984 | 163.2 | 1144.5 |  | 16298 | 194.99 | 10.393 | 60.238 | 0.026984 | 163.2 | 1144.5 | 981.3
16299 | 10.396 | 195 | 60.238 | 0.02699 | 163.21 | 1144.5 |  | 16299 | 195 | 10.396 | 60.238 | 0.02699 | 163.21 | 1144.5 | 981.29
16300 | 10.398 | 195.01 | 60.238 | 0.026995 | 163.22 | 1144.6 |  | 16300 | 195.01 | 10.398 | 60.238 | 0.026995 | 163.22 | 1144.6 | 981.38
16301 | 10.4 | 195.02 | 60.238 | 0.027 | 163.23 | 1144.6 |  | 16301 | 195.02 | 10.4 | 60.238 | 0.027 | 163.23 | 1144.6 | 981.37
16302 | 10.402 | 195.03 | 60.237 | 0.027006 | 163.24 | 1144.6 |  | 16302 | 195.03 | 10.402 | 60.237 | 0.027006 | 163.24 | 1144.6 | 981.36
16303 | 10.404 | 195.04 | 60.237 | 0.027011 | 163.25 | 1144.6 |  | 16303 | 195.04 | 10.404 | 60.237 | 0.027011 | 163.25 | 1144.6 | 981.35
16304 | 10.407 | 195.05 | 60.237 | 0.027016 | 163.26 | 1144.6 |  | 16304 | 195.05 | 10.407 | 60.237 | 0.027016 | 163.26 | 1144.6 | 981.34
16305 | 10.409 | 195.06 | 60.237 | 0.027022 | 163.27 | 1144.6 |  | 16305 | 195.06 | 10.409 | 60.237 | 0.027022 | 163.27 | 1144.6 | 981.33
16306 | 10.411 | 195.07 | 60.236 | 0.027027 | 163.28 | 1144.6 |  | 16306 | 195.07 | 10.411 | 60.236 | 0.027027 | 163.28 | 1144.6 | 981.32
16307 | 10.413 | 195.08 | 60.236 | 0.027032 | 163.29 | 1144.6 |  | 16307 | 195.08 | 10.413 | 60.236 | 0.027032 | 163.29 | 1144.6 | 981.31
16308 | 10.415 | 195.09 | 60.236 | 0.027038 | 163.3 | 1144.6 |  | 16308 | 195.09 | 10.415 | 60.236 | 0.027038 | 163.3 | 1144.6 | 981.3
16309 | 10.418 | 195.1 | 60.236 | 0.027043 | 163.31 | 1144.6 |  | 16309 | 195.1 | 10.418 | 60.236 | 0.027043 | 163.31 | 1144.6 | 981.29
16310 | 10.42 | 195.11 | 60.236 | 0.027048 | 163.32 | 1144.6 |  | 16310 | 195.11 | 10.42 | 60.236 | 0.027048 | 163.32 | 1144.6 | 981.28
16311 | 10.422 | 195.12 | 60.235 | 0.027054 | 163.33 | 1144.6 |  | 16311 | 195.12 | 10.422 | 60.235 | 0.027054 | 163.33 | 1144.6 | 981.27
16312 | 10.424 | 195.13 | 60.235 | 0.027059 | 163.34 | 1144.6 |  | 16312 | 195.13 | 10.424 | 60.235 | 0.027059 | 163.34 | 1144.6 | 981.26
16313 | 10.426 | 195.14 | 60.235 | 0.027064 | 163.35 | 1144.6 |  | 16313 | 195.14 | 10.426 | 60.235 | 0.027064 | 163.35 | 1144.6 | 981.25
16314 | 10.429 | 195.15 | 60.235 | 0.027069 | 163.36 | 1144.6 |  | 16314 | 195.15 | 10.429 | 60.235 | 0.027069 | 163.36 | 1144.6 | 981.24
16315 | 10.431 | 195.16 | 60.234 | 0.027075 | 163.37 | 1144.6 |  | 16315 | 195.16 | 10.431 | 60.234 | 0.027075 | 163.37 | 1144.6 | 981.23
16316 | 10.433 | 195.17 | 60.234 | 0.02708 | 163.38 | 1144.6 |  | 16316 | 195.17 | 10.433 | 60.234 | 0.02708 | 163.38 | 1144.6 | 981.22
16317 | 10.435 | 195.18 | 60.234 | 0.027085 | 163.39 | 1144.6 |  | 16317 | 195.18 | 10.435 | 60.234 | 0.027085 | 163.39 | 1144.6 | 981.21
16318 | 10.437 | 195.19 | 60.234 | 0.027091 | 163.4 | 1144.6 |  | 16318 | 195.19 | 10.437 | 60.234 | 0.027091 | 163.4 | 1144.6 | 981.2
16319 | 10.439 | 195.2 | 60.233 | 0.027096 | 163.41 | 1144.6 |  | 16319 | 195.2 | 10.439 | 60.233 | 0.027096 | 163.41 | 1144.6 | 981.19
16320 | 10.442 | 195.21 | 60.233 | 0.027101 | 163.42 | 1144.6 |  | 16320 | 195.21 | 10.442 | 60.233 | 0.027101 | 163.42 | 1144.6 | 981.18
16321 | 10.444 | 195.22 | 60.233 | 0.027107 | 163.43 | 1144.6 |  | 16321 | 195.22 | 10.444 | 60.233 | 0.027107 | 163.43 | 1144.6 | 981.17
16322 | 10.446 | 195.23 | 60.233 | 0.027112 | 163.44 | 1144.6 |  | 16322 | 195.23 | 10.446 | 60.233 | 0.027112 | 163.44 | 1144.6 | 981.16
16323 | 10.448 | 195.24 | 60.232 | 0.027117 | 163.45 | 1144.6 |  | 16323 | 195.24 | 10.448 | 60.232 | 0.027117 | 163.45 | 1144.6 | 981.15
16324 | 10.45 | 195.25 | 60.232 | 0.027123 | 163.46 | 1144.6 |  | 16324 | 195.25 | 10.45 | 60.232 | 0.027123 | 163.46 | 1144.6 | 981.14
16325 | 10.453 | 195.26 | 60.232 | 0.027128 | 163.47 | 1144.6 |  | 16325 | 195.26 | 10.453 | 60.232 | 0.027128 | 163.47 | 1144.6 | 981.13
16326 | 10.455 | 195.27 | 60.232 | 0.027133 | 163.48 | 1144.7 |  | 16326 | 195.27 | 10.455 | 60.232 | 0.027133 | 163.48 | 1144.7 | 981.22
16327 | 10.457 | 195.28 | 60.232 | 0.027139 | 163.49 | 1144.7 |  | 16327 | 195.28 | 10.457 | 60.232 | 0.027139 | 163.49 | 1144.7 | 981.21
16328 | 10.459 | 195.29 | 60.231 | 0.027144 | 163.5 | 1144.7 |  | 16328 | 195.29 | 10.459 | 60.231 | 0.027144 | 163.5 | 1144.7 | 981.2
16329 | 10.461 | 195.3 | 60.231 | 0.027149 | 163.51 | 1144.7 |  | 16329 | 195.3 | 10.461 | 60.231 | 0.027149 | 163.51 | 1144.7 | 981.19
16330 | 10.464 | 195.31 | 60.231 | 0.027155 | 163.52 | 1144.7 |  | 16330 | 195.31 | 10.464 | 60.231 | 0.027155 | 163.52 | 1144.7 | 981.18
16331 | 10.466 | 195.32 | 60.231 | 0.02716 | 163.53 | 1144.7 |  | 16331 | 195.32 | 10.466 | 60.231 | 0.02716 | 163.53 | 1144.7 | 981.17
16332 | 10.468 | 195.33 | 60.23 | 0.027165 | 163.54 | 1144.7 |  | 16332 | 195.33 | 10.468 | 60.23 | 0.027165 | 163.54 | 1144.7 | 981.16
16333 | 10.47 | 195.34 | 60.23 | 0.027171 | 163.55 | 1144.7 |  | 16333 | 195.34 | 10.47 | 60.23 | 0.027171 | 163.55 | 1144.7 | 981.15
16334 | 10.472 | 195.35 | 60.23 | 0.027176 | 163.56 | 1144.7 |  | 16334 | 195.35 | 10.472 | 60.23 | 0.027176 | 163.56 | 1144.7 | 981.14
16335 | 10.475 | 195.36 | 60.23 | 0.027181 | 163.57 | 1144.7 |  | 16335 | 195.36 | 10.475 | 60.23 | 0.027181 | 163.57 | 1144.7 | 981.13
16336 | 10.477 | 195.37 | 60.229 | 0.027187 | 163.58 | 1144.7 |  | 16336 | 195.37 | 10.477 | 60.229 | 0.027187 | 163.58 | 1144.7 | 981.12
16337 | 10.479 | 195.38 | 60.229 | 0.027192 | 163.59 | 1144.7 |  | 16337 | 195.38 | 10.479 | 60.229 | 0.027192 | 163.59 | 1144.7 | 981.11
16338 | 10.481 | 195.39 | 60.229 | 0.027197 | 163.6 | 1144.7 |  | 16338 | 195.39 | 10.481 | 60.229 | 0.027197 | 163.6 | 1144.7 | 981.1
16339 | 10.483 | 195.4 | 60.229 | 0.027203 | 163.61 | 1144.7 |  | 16339 | 195.4 | 10.483 | 60.229 | 0.027203 | 163.61 | 1144.7 | 981.09
16340 | 10.486 | 195.41 | 60.229 | 0.027208 | 163.62 | 1144.7 |  | 16340 | 195.41 | 10.486 | 60.229 | 0.027208 | 163.62 | 1144.7 | 981.08
16341 | 10.488 | 195.42 | 60.228 | 0.027213 | 163.63 | 1144.7 |  | 16341 | 195.42 | 10.488 | 60.228 | 0.027213 | 163.63 | 1144.7 | 981.07
16342 | 10.49 | 195.43 | 60.228 | 0.027219 | 163.64 | 1144.7 |  | 16342 | 195.43 | 10.49 | 60.228 | 0.027219 | 163.64 | 1144.7 | 981.06
16343 | 10.492 | 195.44 | 60.228 | 0.027224 | 163.65 | 1144.7 |  | 16343 | 195.44 | 10.492 | 60.228 | 0.027224 | 163.65 | 1144.7 | 981.05
16344 | 10.494 | 195.45 | 60.228 | 0.02723 | 163.66 | 1144.7 |  | 16344 | 195.45 | 10.494 | 60.228 | 0.02723 | 163.66 | 1144.7 | 981.04
16345 | 10.497 | 195.46 | 60.227 | 0.027235 | 163.67 | 1144.7 |  | 16345 | 195.46 | 10.497 | 60.227 | 0.027235 | 163.67 | 1144.7 | 981.03
16346 | 10.499 | 195.47 | 60.227 | 0.02724 | 163.68 | 1144.7 |  | 16346 | 195.47 | 10.499 | 60.227 | 0.02724 | 163.68 | 1144.7 | 981.02
16347 | 10.501 | 195.48 | 60.227 | 0.027246 | 163.69 | 1144.7 |  | 16347 | 195.48 | 10.501 | 60.227 | 0.027246 | 163.69 | 1144.7 | 981.01
16348 | 10.503 | 195.49 | 60.227 | 0.027251 | 163.7 | 1144.7 |  | 16348 | 195.49 | 10.503 | 60.227 | 0.027251 | 163.7 | 1144.7 | 981
16349 | 10.505 | 195.5 | 60.226 | 0.027256 | 163.71 | 1144.7 |  | 16349 | 195.5 | 10.505 | 60.226 | 0.027256 | 163.71 | 1144.7 | 980.99
16350 | 10.508 | 195.51 | 60.226 | 0.027262 | 163.72 | 1144.7 |  | 16350 | 195.51 | 10.508 | 60.226 | 0.027262 | 163.72 | 1144.7 | 980.98
16351 | 10.51 | 195.52 | 60.226 | 0.027267 | 163.73 | 1144.7 |  | 16351 | 195.52 | 10.51 | 60.226 | 0.027267 | 163.73 | 1144.7 | 980.97
16352 | 10.512 | 195.53 | 60.226 | 0.027272 | 163.74 | 1144.8 |  | 16352 | 195.53 | 10.512 | 60.226 | 0.027272 | 163.74 | 1144.8 | 981.06
16353 | 10.514 | 195.54 | 60.225 | 0.027278 | 163.75 | 1144.8 |  | 16353 | 195.54 | 10.514 | 60.225 | 0.027278 | 163.75 | 1144.8 | 981.05
16354 | 10.516 | 195.55 | 60.225 | 0.027283 | 163.77 | 1144.8 |  | 16354 | 195.55 | 10.516 | 60.225 | 0.027283 | 163.77 | 1144.8 | 981.03
16355 | 10.519 | 195.56 | 60.225 | 0.027288 | 163.78 | 1144.8 |  | 16355 | 195.56 | 10.519 | 60.225 | 0.027288 | 163.78 | 1144.8 | 981.02
16356 | 10.521 | 195.57 | 60.225 | 0.027294 | 163.79 | 1144.8 |  | 16356 | 195.57 | 10.521 | 60.225 | 0.027294 | 163.79 | 1144.8 | 981.01
16357 | 10.523 | 195.58 | 60.225 | 0.027299 | 163.8 | 1144.8 |  | 16357 | 195.58 | 10.523 | 60.225 | 0.027299 | 163.8 | 1144.8 | 981
16358 | 10.525 | 195.59 | 60.224 | 0.027304 | 163.81 | 1144.8 |  | 16358 | 195.59 | 10.525 | 60.224 | 0.027304 | 163.81 | 1144.8 | 980.99
16359 | 10.528 | 195.6 | 60.224 | 0.02731 | 163.82 | 1144.8 |  | 16359 | 195.6 | 10.528 | 60.224 | 0.02731 | 163.82 | 1144.8 | 980.98
16360 | 10.53 | 195.61 | 60.224 | 0.027315 | 163.83 | 1144.8 |  | 16360 | 195.61 | 10.53 | 60.224 | 0.027315 | 163.83 | 1144.8 | 980.97
16361 | 10.532 | 195.62 | 60.224 | 0.027321 | 163.84 | 1144.8 |  | 16361 | 195.62 | 10.532 | 60.224 | 0.027321 | 163.84 | 1144.8 | 980.96
16362 | 10.534 | 195.63 | 60.223 | 0.027326 | 163.85 | 1144.8 |  | 16362 | 195.63 | 10.534 | 60.223 | 0.027326 | 163.85 | 1144.8 | 980.95
16363 | 10.536 | 195.64 | 60.223 | 0.027331 | 163.86 | 1144.8 |  | 16363 | 195.64 | 10.536 | 60.223 | 0.027331 | 163.86 | 1144.8 | 980.94
16364 | 10.539 | 195.65 | 60.223 | 0.027337 | 163.87 | 1144.8 |  | 16364 | 195.65 | 10.539 | 60.223 | 0.027337 | 163.87 | 1144.8 | 980.93
16365 | 10.541 | 195.66 | 60.223 | 0.027342 | 163.88 | 1144.8 |  | 16365 | 195.66 | 10.541 | 60.223 | 0.027342 | 163.88 | 1144.8 | 980.92
16366 | 10.543 | 195.67 | 60.222 | 0.027347 | 163.89 | 1144.8 |  | 16366 | 195.67 | 10.543 | 60.222 | 0.027347 | 163.89 | 1144.8 | 980.91
16367 | 10.545 | 195.68 | 60.222 | 0.027353 | 163.9 | 1144.8 |  | 16367 | 195.68 | 10.545 | 60.222 | 0.027353 | 163.9 | 1144.8 | 980.9
16368 | 10.547 | 195.69 | 60.222 | 0.027358 | 163.91 | 1144.8 |  | 16368 | 195.69 | 10.547 | 60.222 | 0.027358 | 163.91 | 1144.8 | 980.89
16369 | 10.55 | 195.7 | 60.222 | 0.027363 | 163.92 | 1144.8 |  | 16369 | 195.7 | 10.55 | 60.222 | 0.027363 | 163.92 | 1144.8 | 980.88
16370 | 10.552 | 195.71 | 60.221 | 0.027369 | 163.93 | 1144.8 |  | 16370 | 195.71 | 10.552 | 60.221 | 0.027369 | 163.93 | 1144.8 | 980.87
16371 | 10.554 | 195.72 | 60.221 | 0.027374 | 163.94 | 1144.8 |  | 16371 | 195.72 | 10.554 | 60.221 | 0.027374 | 163.94 | 1144.8 | 980.86
16372 | 10.556 | 195.73 | 60.221 | 0.02738 | 163.95 | 1144.8 |  | 16372 | 195.73 | 10.556 | 60.221 | 0.02738 | 163.95 | 1144.8 | 980.85
16373 | 10.558 | 195.74 | 60.221 | 0.027385 | 163.96 | 1144.8 |  | 16373 | 195.74 | 10.558 | 60.221 | 0.027385 | 163.96 | 1144.8 | 980.84
16374 | 10.561 | 195.75 | 60.221 | 0.02739 | 163.97 | 1144.8 |  | 16374 | 195.75 | 10.561 | 60.221 | 0.02739 | 163.97 | 1144.8 | 980.83
16375 | 10.563 | 195.76 | 60.22 | 0.027396 | 163.98 | 1144.8 |  | 16375 | 195.76 | 10.563 | 60.22 | 0.027396 | 163.98 | 1144.8 | 980.82
16376 | 10.565 | 195.77 | 60.22 | 0.027401 | 163.99 | 1144.8 |  | 16376 | 195.77 | 10.565 | 60.22 | 0.027401 | 163.99 | 1144.8 | 980.81
16377 | 10.567 | 195.78 | 60.22 | 0.027406 | 164 | 1144.8 |  | 16377 | 195.78 | 10.567 | 60.22 | 0.027406 | 164 | 1144.8 | 980.8
16378 | 10.57 | 195.79 | 60.22 | 0.027412 | 164.01 | 1144.9 |  | 16378 | 195.79 | 10.57 | 60.22 | 0.027412 | 164.01 | 1144.9 | 980.89
16379 | 10.572 | 195.8 | 60.219 | 0.027417 | 164.02 | 1144.9 |  | 16379 | 195.8 | 10.572 | 60.219 | 0.027417 | 164.02 | 1144.9 | 980.88
16380 | 10.574 | 195.81 | 60.219 | 0.027423 | 164.03 | 1144.9 |  | 16380 | 195.81 | 10.574 | 60.219 | 0.027423 | 164.03 | 1144.9 | 980.87
16381 | 10.576 | 195.82 | 60.219 | 0.027428 | 164.04 | 1144.9 |  | 16381 | 195.82 | 10.576 | 60.219 | 0.027428 | 164.04 | 1144.9 | 980.86
16382 | 10.578 | 195.83 | 60.219 | 0.027433 | 164.05 | 1144.9 |  | 16382 | 195.83 | 10.578 | 60.219 | 0.027433 | 164.05 | 1144.9 | 980.85
16383 | 10.581 | 195.84 | 60.218 | 0.027439 | 164.06 | 1144.9 |  | 16383 | 195.84 | 10.581 | 60.218 | 0.027439 | 164.06 | 1144.9 | 980.84
16384 | 10.583 | 195.85 | 60.218 | 0.027444 | 164.07 | 1144.9 |  | 16384 | 195.85 | 10.583 | 60.218 | 0.027444 | 164.07 | 1144.9 | 980.83
16385 | 10.585 | 195.86 | 60.218 | 0.02745 | 164.08 | 1144.9 |  | 16385 | 195.86 | 10.585 | 60.218 | 0.02745 | 164.08 | 1144.9 | 980.82
16386 | 10.587 | 195.87 | 60.218 | 0.027455 | 164.09 | 1144.9 |  | 16386 | 195.87 | 10.587 | 60.218 | 0.027455 | 164.09 | 1144.9 | 980.81
16387 | 10.59 | 195.88 | 60.217 | 0.02746 | 164.1 | 1144.9 |  | 16387 | 195.88 | 10.59 | 60.217 | 0.02746 | 164.1 | 1144.9 | 980.8
16388 | 10.592 | 195.89 | 60.217 | 0.027466 | 164.11 | 1144.9 |  | 16388 | 195.89 | 10.592 | 60.217 | 0.027466 | 164.11 | 1144.9 | 980.79
16389 | 10.594 | 195.9 | 60.217 | 0.027471 | 164.12 | 1144.9 |  | 16389 | 195.9 | 10.594 | 60.217 | 0.027471 | 164.12 | 1144.9 | 980.78
16390 | 10.596 | 195.91 | 60.217 | 0.027476 | 164.13 | 1144.9 |  | 16390 | 195.91 | 10.596 | 60.217 | 0.027476 | 164.13 | 1144.9 | 980.77
16391 | 10.598 | 195.92 | 60.217 | 0.027482 | 164.14 | 1144.9 |  | 16391 | 195.92 | 10.598 | 60.217 | 0.027482 | 164.14 | 1144.9 | 980.76
16392 | 10.601 | 195.93 | 60.216 | 0.027487 | 164.15 | 1144.9 |  | 16392 | 195.93 | 10.601 | 60.216 | 0.027487 | 164.15 | 1144.9 | 980.75
16393 | 10.603 | 195.94 | 60.216 | 0.027493 | 164.16 | 1144.9 |  | 16393 | 195.94 | 10.603 | 60.216 | 0.027493 | 164.16 | 1144.9 | 980.74
16394 | 10.605 | 195.95 | 60.216 | 0.027498 | 164.17 | 1144.9 |  | 16394 | 195.95 | 10.605 | 60.216 | 0.027498 | 164.17 | 1144.9 | 980.73
16395 | 10.607 | 195.96 | 60.216 | 0.027503 | 164.18 | 1144.9 |  | 16395 | 195.96 | 10.607 | 60.216 | 0.027503 | 164.18 | 1144.9 | 980.72
16396 | 10.61 | 195.97 | 60.215 | 0.027509 | 164.19 | 1144.9 |  | 16396 | 195.97 | 10.61 | 60.215 | 0.027509 | 164.19 | 1144.9 | 980.71
16397 | 10.612 | 195.98 | 60.215 | 0.027514 | 164.2 | 1144.9 |  | 16397 | 195.98 | 10.612 | 60.215 | 0.027514 | 164.2 | 1144.9 | 980.7
16398 | 10.614 | 195.99 | 60.215 | 0.02752 | 164.21 | 1144.9 |  | 16398 | 195.99 | 10.614 | 60.215 | 0.02752 | 164.21 | 1144.9 | 980.69
16399 | 10.616 | 196 | 60.215 | 0.027525 | 164.22 | 1144.9 |  | 16399 | 196 | 10.616 | 60.215 | 0.027525 | 164.22 | 1144.9 | 980.68
16400 | 10.618 | 196.01 | 60.214 | 0.02753 | 164.23 | 1144.9 |  | 16400 | 196.01 | 10.618 | 60.214 | 0.02753 | 164.23 | 1144.9 | 980.67
16401 | 10.621 | 196.02 | 60.214 | 0.027536 | 164.24 | 1144.9 |  | 16401 | 196.02 | 10.621 | 60.214 | 0.027536 | 164.24 | 1144.9 | 980.66
16402 | 10.623 | 196.03 | 60.214 | 0.027541 | 164.25 | 1144.9 |  | 16402 | 196.03 | 10.623 | 60.214 | 0.027541 | 164.25 | 1144.9 | 980.65
16403 | 10.625 | 196.04 | 60.214 | 0.027547 | 164.26 | 1145 |  | 16403 | 196.04 | 10.625 | 60.214 | 0.027547 | 164.26 | 1145 | 980.74
16404 | 10.627 | 196.05 | 60.214 | 0.027552 | 164.27 | 1145 |  | 16404 | 196.05 | 10.627 | 60.214 | 0.027552 | 164.27 | 1145 | 980.73
16405 | 10.63 | 196.06 | 60.213 | 0.027557 | 164.28 | 1145 |  | 16405 | 196.06 | 10.63 | 60.213 | 0.027557 | 164.28 | 1145 | 980.72
16406 | 10.632 | 196.07 | 60.213 | 0.027563 | 164.29 | 1145 |  | 16406 | 196.07 | 10.632 | 60.213 | 0.027563 | 164.29 | 1145 | 980.71
16407 | 10.634 | 196.08 | 60.213 | 0.027568 | 164.3 | 1145 |  | 16407 | 196.08 | 10.634 | 60.213 | 0.027568 | 164.3 | 1145 | 980.7
16408 | 10.636 | 196.09 | 60.213 | 0.027574 | 164.31 | 1145 |  | 16408 | 196.09 | 10.636 | 60.213 | 0.027574 | 164.31 | 1145 | 980.69
16409 | 10.638 | 196.1 | 60.212 | 0.027579 | 164.32 | 1145 |  | 16409 | 196.1 | 10.638 | 60.212 | 0.027579 | 164.32 | 1145 | 980.68
16410 | 10.641 | 196.11 | 60.212 | 0.027584 | 164.33 | 1145 |  | 16410 | 196.11 | 10.641 | 60.212 | 0.027584 | 164.33 | 1145 | 980.67
16411 | 10.643 | 196.12 | 60.212 | 0.02759 | 164.34 | 1145 |  | 16411 | 196.12 | 10.643 | 60.212 | 0.02759 | 164.34 | 1145 | 980.66
16412 | 10.645 | 196.13 | 60.212 | 0.027595 | 164.35 | 1145 |  | 16412 | 196.13 | 10.645 | 60.212 | 0.027595 | 164.35 | 1145 | 980.65
16413 | 10.647 | 196.14 | 60.211 | 0.027601 | 164.36 | 1145 |  | 16413 | 196.14 | 10.647 | 60.211 | 0.027601 | 164.36 | 1145 | 980.64
16414 | 10.65 | 196.15 | 60.211 | 0.027606 | 164.37 | 1145 |  | 16414 | 196.15 | 10.65 | 60.211 | 0.027606 | 164.37 | 1145 | 980.63
16415 | 10.652 | 196.16 | 60.211 | 0.027611 | 164.38 | 1145 |  | 16415 | 196.16 | 10.652 | 60.211 | 0.027611 | 164.38 | 1145 | 980.62
16416 | 10.654 | 196.17 | 60.211 | 0.027617 | 164.39 | 1145 |  | 16416 | 196.17 | 10.654 | 60.211 | 0.027617 | 164.39 | 1145 | 980.61
16417 | 10.656 | 196.18 | 60.21 | 0.027622 | 164.4 | 1145 |  | 16417 | 196.18 | 10.656 | 60.21 | 0.027622 | 164.4 | 1145 | 980.6
16418 | 10.659 | 196.19 | 60.21 | 0.027628 | 164.41 | 1145 |  | 16418 | 196.19 | 10.659 | 60.21 | 0.027628 | 164.41 | 1145 | 980.59
16419 | 10.661 | 196.2 | 60.21 | 0.027633 | 164.42 | 1145 |  | 16419 | 196.2 | 10.661 | 60.21 | 0.027633 | 164.42 | 1145 | 980.58
16420 | 10.663 | 196.21 | 60.21 | 0.027638 | 164.43 | 1145 |  | 16420 | 196.21 | 10.663 | 60.21 | 0.027638 | 164.43 | 1145 | 980.57
16421 | 10.665 | 196.22 | 60.21 | 0.027644 | 164.44 | 1145 |  | 16421 | 196.22 | 10.665 | 60.21 | 0.027644 | 164.44 | 1145 | 980.56
16422 | 10.667 | 196.23 | 60.209 | 0.027649 | 164.45 | 1145 |  | 16422 | 196.23 | 10.667 | 60.209 | 0.027649 | 164.45 | 1145 | 980.55
16423 | 10.67 | 196.24 | 60.209 | 0.027655 | 164.46 | 1145 |  | 16423 | 196.24 | 10.67 | 60.209 | 0.027655 | 164.46 | 1145 | 980.54
16424 | 10.672 | 196.25 | 60.209 | 0.02766 | 164.47 | 1145 |  | 16424 | 196.25 | 10.672 | 60.209 | 0.02766 | 164.47 | 1145 | 980.53
16425 | 10.674 | 196.26 | 60.209 | 0.027666 | 164.48 | 1145 |  | 16425 | 196.26 | 10.674 | 60.209 | 0.027666 | 164.48 | 1145 | 980.52
16426 | 10.676 | 196.27 | 60.208 | 0.027671 | 164.49 | 1145 |  | 16426 | 196.27 | 10.676 | 60.208 | 0.027671 | 164.49 | 1145 | 980.51
16427 | 10.679 | 196.28 | 60.208 | 0.027676 | 164.5 | 1145 |  | 16427 | 196.28 | 10.679 | 60.208 | 0.027676 | 164.5 | 1145 | 980.5
16428 | 10.681 | 196.29 | 60.208 | 0.027682 | 164.51 | 1145 |  | 16428 | 196.29 | 10.681 | 60.208 | 0.027682 | 164.51 | 1145 | 980.49
16429 | 10.683 | 196.3 | 60.208 | 0.027687 | 164.52 | 1145.1 |  | 16429 | 196.3 | 10.683 | 60.208 | 0.027687 | 164.52 | 1145.1 | 980.58
16430 | 10.685 | 196.31 | 60.207 | 0.027693 | 164.53 | 1145.1 |  | 16430 | 196.31 | 10.685 | 60.207 | 0.027693 | 164.53 | 1145.1 | 980.57
16431 | 10.688 | 196.32 | 60.207 | 0.027698 | 164.54 | 1145.1 |  | 16431 | 196.32 | 10.688 | 60.207 | 0.027698 | 164.54 | 1145.1 | 980.56
16432 | 10.69 | 196.33 | 60.207 | 0.027703 | 164.55 | 1145.1 |  | 16432 | 196.33 | 10.69 | 60.207 | 0.027703 | 164.55 | 1145.1 | 980.55
16433 | 10.692 | 196.34 | 60.207 | 0.027709 | 164.56 | 1145.1 |  | 16433 | 196.34 | 10.692 | 60.207 | 0.027709 | 164.56 | 1145.1 | 980.54
16434 | 10.694 | 196.35 | 60.206 | 0.027714 | 164.57 | 1145.1 |  | 16434 | 196.35 | 10.694 | 60.206 | 0.027714 | 164.57 | 1145.1 | 980.53
16435 | 10.697 | 196.36 | 60.206 | 0.02772 | 164.58 | 1145.1 |  | 16435 | 196.36 | 10.697 | 60.206 | 0.02772 | 164.58 | 1145.1 | 980.52
16436 | 10.699 | 196.37 | 60.206 | 0.027725 | 164.59 | 1145.1 |  | 16436 | 196.37 | 10.699 | 60.206 | 0.027725 | 164.59 | 1145.1 | 980.51
16437 | 10.701 | 196.38 | 60.206 | 0.027731 | 164.6 | 1145.1 |  | 16437 | 196.38 | 10.701 | 60.206 | 0.027731 | 164.6 | 1145.1 | 980.5
16438 | 10.703 | 196.39 | 60.206 | 0.027736 | 164.61 | 1145.1 |  | 16438 | 196.39 | 10.703 | 60.206 | 0.027736 | 164.61 | 1145.1 | 980.49
16439 | 10.705 | 196.4 | 60.205 | 0.027741 | 164.62 | 1145.1 |  | 16439 | 196.4 | 10.705 | 60.205 | 0.027741 | 164.62 | 1145.1 | 980.48
16440 | 10.708 | 196.41 | 60.205 | 0.027747 | 164.63 | 1145.1 |  | 16440 | 196.41 | 10.708 | 60.205 | 0.027747 | 164.63 | 1145.1 | 980.47
16441 | 10.71 | 196.42 | 60.205 | 0.027752 | 164.64 | 1145.1 |  | 16441 | 196.42 | 10.71 | 60.205 | 0.027752 | 164.64 | 1145.1 | 980.46
16442 | 10.712 | 196.43 | 60.205 | 0.027758 | 164.65 | 1145.1 |  | 16442 | 196.43 | 10.712 | 60.205 | 0.027758 | 164.65 | 1145.1 | 980.45
16443 | 10.714 | 196.44 | 60.204 | 0.027763 | 164.66 | 1145.1 |  | 16443 | 196.44 | 10.714 | 60.204 | 0.027763 | 164.66 | 1145.1 | 980.44
16444 | 10.717 | 196.45 | 60.204 | 0.027769 | 164.67 | 1145.1 |  | 16444 | 196.45 | 10.717 | 60.204 | 0.027769 | 164.67 | 1145.1 | 980.43
16445 | 10.719 | 196.46 | 60.204 | 0.027774 | 164.68 | 1145.1 |  | 16445 | 196.46 | 10.719 | 60.204 | 0.027774 | 164.68 | 1145.1 | 980.42
16446 | 10.721 | 196.47 | 60.204 | 0.02778 | 164.69 | 1145.1 |  | 16446 | 196.47 | 10.721 | 60.204 | 0.02778 | 164.69 | 1145.1 | 980.41
16447 | 10.723 | 196.48 | 60.203 | 0.027785 | 164.7 | 1145.1 |  | 16447 | 196.48 | 10.723 | 60.203 | 0.027785 | 164.7 | 1145.1 | 980.4
16448 | 10.726 | 196.49 | 60.203 | 0.02779 | 164.71 | 1145.1 |  | 16448 | 196.49 | 10.726 | 60.203 | 0.02779 | 164.71 | 1145.1 | 980.39
16449 | 10.728 | 196.5 | 60.203 | 0.027796 | 164.72 | 1145.1 |  | 16449 | 196.5 | 10.728 | 60.203 | 0.027796 | 164.72 | 1145.1 | 980.38
16450 | 10.73 | 196.51 | 60.203 | 0.027801 | 164.73 | 1145.1 |  | 16450 | 196.51 | 10.73 | 60.203 | 0.027801 | 164.73 | 1145.1 | 980.37
16451 | 10.732 | 196.52 | 60.202 | 0.027807 | 164.74 | 1145.1 |  | 16451 | 196.52 | 10.732 | 60.202 | 0.027807 | 164.74 | 1145.1 | 980.36
16452 | 10.735 | 196.53 | 60.202 | 0.027812 | 164.75 | 1145.1 |  | 16452 | 196.53 | 10.735 | 60.202 | 0.027812 | 164.75 | 1145.1 | 980.35
16453 | 10.737 | 196.54 | 60.202 | 0.027818 | 164.76 | 1145.1 |  | 16453 | 196.54 | 10.737 | 60.202 | 0.027818 | 164.76 | 1145.1 | 980.34
16454 | 10.739 | 196.55 | 60.202 | 0.027823 | 164.77 | 1145.1 |  | 16454 | 196.55 | 10.739 | 60.202 | 0.027823 | 164.77 | 1145.1 | 980.33
16455 | 10.741 | 196.56 | 60.202 | 0.027828 | 164.78 | 1145.2 |  | 16455 | 196.56 | 10.741 | 60.202 | 0.027828 | 164.78 | 1145.2 | 980.42
16456 | 10.744 | 196.57 | 60.201 | 0.027834 | 164.79 | 1145.2 |  | 16456 | 196.57 | 10.744 | 60.201 | 0.027834 | 164.79 | 1145.2 | 980.41
16457 | 10.746 | 196.58 | 60.201 | 0.027839 | 164.8 | 1145.2 |  | 16457 | 196.58 | 10.746 | 60.201 | 0.027839 | 164.8 | 1145.2 | 980.4
16458 | 10.748 | 196.59 | 60.201 | 0.027845 | 164.81 | 1145.2 |  | 16458 | 196.59 | 10.748 | 60.201 | 0.027845 | 164.81 | 1145.2 | 980.39
16459 | 10.75 | 196.6 | 60.201 | 0.02785 | 164.82 | 1145.2 |  | 16459 | 196.6 | 10.75 | 60.201 | 0.02785 | 164.82 | 1145.2 | 980.38
16460 | 10.753 | 196.61 | 60.2 | 0.027856 | 164.83 | 1145.2 |  | 16460 | 196.61 | 10.753 | 60.2 | 0.027856 | 164.83 | 1145.2 | 980.37
16461 | 10.755 | 196.62 | 60.2 | 0.027861 | 164.84 | 1145.2 |  | 16461 | 196.62 | 10.755 | 60.2 | 0.027861 | 164.84 | 1145.2 | 980.36
16462 | 10.757 | 196.63 | 60.2 | 0.027867 | 164.85 | 1145.2 |  | 16462 | 196.63 | 10.757 | 60.2 | 0.027867 | 164.85 | 1145.2 | 980.35
16463 | 10.759 | 196.64 | 60.2 | 0.027872 | 164.86 | 1145.2 |  | 16463 | 196.64 | 10.759 | 60.2 | 0.027872 | 164.86 | 1145.2 | 980.34
16464 | 10.762 | 196.65 | 60.199 | 0.027877 | 164.87 | 1145.2 |  | 16464 | 196.65 | 10.762 | 60.199 | 0.027877 | 164.87 | 1145.2 | 980.33
16465 | 10.764 | 196.66 | 60.199 | 0.027883 | 164.88 | 1145.2 |  | 16465 | 196.66 | 10.764 | 60.199 | 0.027883 | 164.88 | 1145.2 | 980.32
16466 | 10.766 | 196.67 | 60.199 | 0.027888 | 164.89 | 1145.2 |  | 16466 | 196.67 | 10.766 | 60.199 | 0.027888 | 164.89 | 1145.2 | 980.31
16467 | 10.768 | 196.68 | 60.199 | 0.027894 | 164.9 | 1145.2 |  | 16467 | 196.68 | 10.768 | 60.199 | 0.027894 | 164.9 | 1145.2 | 980.3
16468 | 10.771 | 196.69 | 60.198 | 0.027899 | 164.91 | 1145.2 |  | 16468 | 196.69 | 10.771 | 60.198 | 0.027899 | 164.91 | 1145.2 | 980.29
16469 | 10.773 | 196.7 | 60.198 | 0.027905 | 164.92 | 1145.2 |  | 16469 | 196.7 | 10.773 | 60.198 | 0.027905 | 164.92 | 1145.2 | 980.28
16470 | 10.775 | 196.71 | 60.198 | 0.02791 | 164.93 | 1145.2 |  | 16470 | 196.71 | 10.775 | 60.198 | 0.02791 | 164.93 | 1145.2 | 980.27
16471 | 10.777 | 196.72 | 60.198 | 0.027916 | 164.94 | 1145.2 |  | 16471 | 196.72 | 10.777 | 60.198 | 0.027916 | 164.94 | 1145.2 | 980.26
16472 | 10.78 | 196.73 | 60.198 | 0.027921 | 164.95 | 1145.2 |  | 16472 | 196.73 | 10.78 | 60.198 | 0.027921 | 164.95 | 1145.2 | 980.25
16473 | 10.782 | 196.74 | 60.197 | 0.027927 | 164.96 | 1145.2 |  | 16473 | 196.74 | 10.782 | 60.197 | 0.027927 | 164.96 | 1145.2 | 980.24
16474 | 10.784 | 196.75 | 60.197 | 0.027932 | 164.97 | 1145.2 |  | 16474 | 196.75 | 10.784 | 60.197 | 0.027932 | 164.97 | 1145.2 | 980.23
16475 | 10.786 | 196.76 | 60.197 | 0.027938 | 164.98 | 1145.2 |  | 16475 | 196.76 | 10.786 | 60.197 | 0.027938 | 164.98 | 1145.2 | 980.22
16476 | 10.789 | 196.77 | 60.197 | 0.027943 | 164.99 | 1145.2 |  | 16476 | 196.77 | 10.789 | 60.197 | 0.027943 | 164.99 | 1145.2 | 980.21
16477 | 10.791 | 196.78 | 60.196 | 0.027948 | 165 | 1145.2 |  | 16477 | 196.78 | 10.791 | 60.196 | 0.027948 | 165 | 1145.2 | 980.2
16478 | 10.793 | 196.79 | 60.196 | 0.027954 | 165.01 | 1145.2 |  | 16478 | 196.79 | 10.793 | 60.196 | 0.027954 | 165.01 | 1145.2 | 980.19
16479 | 10.795 | 196.8 | 60.196 | 0.027959 | 165.02 | 1145.2 |  | 16479 | 196.8 | 10.795 | 60.196 | 0.027959 | 165.02 | 1145.2 | 980.18
16480 | 10.798 | 196.81 | 60.196 | 0.027965 | 165.03 | 1145.2 |  | 16480 | 196.81 | 10.798 | 60.196 | 0.027965 | 165.03 | 1145.2 | 980.17
16481 | 10.8 | 196.82 | 60.195 | 0.02797 | 165.04 | 1145.3 |  | 16481 | 196.82 | 10.8 | 60.195 | 0.02797 | 165.04 | 1145.3 | 980.26
16482 | 10.802 | 196.83 | 60.195 | 0.027976 | 165.05 | 1145.3 |  | 16482 | 196.83 | 10.802 | 60.195 | 0.027976 | 165.05 | 1145.3 | 980.25
16483 | 10.804 | 196.84 | 60.195 | 0.027981 | 165.06 | 1145.3 |  | 16483 | 196.84 | 10.804 | 60.195 | 0.027981 | 165.06 | 1145.3 | 980.24
16484 | 10.807 | 196.85 | 60.195 | 0.027987 | 165.07 | 1145.3 |  | 16484 | 196.85 | 10.807 | 60.195 | 0.027987 | 165.07 | 1145.3 | 980.23
16485 | 10.809 | 196.86 | 60.194 | 0.027992 | 165.08 | 1145.3 |  | 16485 | 196.86 | 10.809 | 60.194 | 0.027992 | 165.08 | 1145.3 | 980.22
16486 | 10.811 | 196.87 | 60.194 | 0.027998 | 165.09 | 1145.3 |  | 16486 | 196.87 | 10.811 | 60.194 | 0.027998 | 165.09 | 1145.3 | 980.21
16487 | 10.813 | 196.88 | 60.194 | 0.028003 | 165.1 | 1145.3 |  | 16487 | 196.88 | 10.813 | 60.194 | 0.028003 | 165.1 | 1145.3 | 980.2
16488 | 10.816 | 196.89 | 60.194 | 0.028009 | 165.11 | 1145.3 |  | 16488 | 196.89 | 10.816 | 60.194 | 0.028009 | 165.11 | 1145.3 | 980.19
16489 | 10.818 | 196.9 | 60.194 | 0.028014 | 165.12 | 1145.3 |  | 16489 | 196.9 | 10.818 | 60.194 | 0.028014 | 165.12 | 1145.3 | 980.18
16490 | 10.82 | 196.91 | 60.193 | 0.02802 | 165.13 | 1145.3 |  | 16490 | 196.91 | 10.82 | 60.193 | 0.02802 | 165.13 | 1145.3 | 980.17
16491 | 10.822 | 196.92 | 60.193 | 0.028025 | 165.14 | 1145.3 |  | 16491 | 196.92 | 10.822 | 60.193 | 0.028025 | 165.14 | 1145.3 | 980.16
16492 | 10.825 | 196.93 | 60.193 | 0.02803 | 165.15 | 1145.3 |  | 16492 | 196.93 | 10.825 | 60.193 | 0.02803 | 165.15 | 1145.3 | 980.15
16493 | 10.827 | 196.94 | 60.193 | 0.028036 | 165.16 | 1145.3 |  | 16493 | 196.94 | 10.827 | 60.193 | 0.028036 | 165.16 | 1145.3 | 980.14
16494 | 10.829 | 196.95 | 60.192 | 0.028041 | 165.17 | 1145.3 |  | 16494 | 196.95 | 10.829 | 60.192 | 0.028041 | 165.17 | 1145.3 | 980.13
16495 | 10.832 | 196.96 | 60.192 | 0.028047 | 165.18 | 1145.3 |  | 16495 | 196.96 | 10.832 | 60.192 | 0.028047 | 165.18 | 1145.3 | 980.12
16496 | 10.834 | 196.97 | 60.192 | 0.028052 | 165.19 | 1145.3 |  | 16496 | 196.97 | 10.834 | 60.192 | 0.028052 | 165.19 | 1145.3 | 980.11
16497 | 10.836 | 196.98 | 60.192 | 0.028058 | 165.2 | 1145.3 |  | 16497 | 196.98 | 10.836 | 60.192 | 0.028058 | 165.2 | 1145.3 | 980.1
16498 | 10.838 | 196.99 | 60.191 | 0.028063 | 165.21 | 1145.3 |  | 16498 | 196.99 | 10.838 | 60.191 | 0.028063 | 165.21 | 1145.3 | 980.09
16499 | 10.841 | 197 | 60.191 | 0.028069 | 165.22 | 1145.3 |  | 16499 | 197 | 10.841 | 60.191 | 0.028069 | 165.22 | 1145.3 | 980.08
16500 | 10.843 | 197.01 | 60.191 | 0.028074 | 165.23 | 1145.3 |  | 16500 | 197.01 | 10.843 | 60.191 | 0.028074 | 165.23 | 1145.3 | 980.07
16501 | 10.845 | 197.02 | 60.191 | 0.02808 | 165.24 | 1145.3 |  | 16501 | 197.02 | 10.845 | 60.191 | 0.02808 | 165.24 | 1145.3 | 980.06
16502 | 10.847 | 197.03 | 60.19 | 0.028085 | 165.25 | 1145.3 |  | 16502 | 197.03 | 10.847 | 60.19 | 0.028085 | 165.25 | 1145.3 | 980.05
16503 | 10.85 | 197.04 | 60.19 | 0.028091 | 165.26 | 1145.3 |  | 16503 | 197.04 | 10.85 | 60.19 | 0.028091 | 165.26 | 1145.3 | 980.04
16504 | 10.852 | 197.05 | 60.19 | 0.028096 | 165.27 | 1145.3 |  | 16504 | 197.05 | 10.852 | 60.19 | 0.028096 | 165.27 | 1145.3 | 980.03
16505 | 10.854 | 197.06 | 60.19 | 0.028102 | 165.28 | 1145.3 |  | 16505 | 197.06 | 10.854 | 60.19 | 0.028102 | 165.28 | 1145.3 | 980.02
16506 | 10.856 | 197.07 | 60.19 | 0.028107 | 165.29 | 1145.3 |  | 16506 | 197.07 | 10.856 | 60.19 | 0.028107 | 165.29 | 1145.3 | 980.01
16507 | 10.859 | 197.08 | 60.189 | 0.028113 | 165.3 | 1145.4 |  | 16507 | 197.08 | 10.859 | 60.189 | 0.028113 | 165.3 | 1145.4 | 980.1
16508 | 10.861 | 197.09 | 60.189 | 0.028118 | 165.31 | 1145.4 |  | 16508 | 197.09 | 10.861 | 60.189 | 0.028118 | 165.31 | 1145.4 | 980.09
16509 | 10.863 | 197.1 | 60.189 | 0.028124 | 165.32 | 1145.4 |  | 16509 | 197.1 | 10.863 | 60.189 | 0.028124 | 165.32 | 1145.4 | 980.08
16510 | 10.865 | 197.11 | 60.189 | 0.028129 | 165.33 | 1145.4 |  | 16510 | 197.11 | 10.865 | 60.189 | 0.028129 | 165.33 | 1145.4 | 980.07
16511 | 10.868 | 197.12 | 60.188 | 0.028135 | 165.34 | 1145.4 |  | 16511 | 197.12 | 10.868 | 60.188 | 0.028135 | 165.34 | 1145.4 | 980.06
16512 | 10.87 | 197.13 | 60.188 | 0.02814 | 165.35 | 1145.4 |  | 16512 | 197.13 | 10.87 | 60.188 | 0.02814 | 165.35 | 1145.4 | 980.05
16513 | 10.872 | 197.14 | 60.188 | 0.028146 | 165.36 | 1145.4 |  | 16513 | 197.14 | 10.872 | 60.188 | 0.028146 | 165.36 | 1145.4 | 980.04
16514 | 10.875 | 197.15 | 60.188 | 0.028151 | 165.37 | 1145.4 |  | 16514 | 197.15 | 10.875 | 60.188 | 0.028151 | 165.37 | 1145.4 | 980.03
16515 | 10.877 | 197.16 | 60.187 | 0.028157 | 165.38 | 1145.4 |  | 16515 | 197.16 | 10.877 | 60.187 | 0.028157 | 165.38 | 1145.4 | 980.02
16516 | 10.879 | 197.17 | 60.187 | 0.028162 | 165.39 | 1145.4 |  | 16516 | 197.17 | 10.879 | 60.187 | 0.028162 | 165.39 | 1145.4 | 980.01
16517 | 10.881 | 197.18 | 60.187 | 0.028168 | 165.4 | 1145.4 |  | 16517 | 197.18 | 10.881 | 60.187 | 0.028168 | 165.4 | 1145.4 | 980
16518 | 10.884 | 197.19 | 60.187 | 0.028173 | 165.41 | 1145.4 |  | 16518 | 197.19 | 10.884 | 60.187 | 0.028173 | 165.41 | 1145.4 | 979.99
16519 | 10.886 | 197.2 | 60.186 | 0.028179 | 165.42 | 1145.4 |  | 16519 | 197.2 | 10.886 | 60.186 | 0.028179 | 165.42 | 1145.4 | 979.98
16520 | 10.888 | 197.21 | 60.186 | 0.028184 | 165.43 | 1145.4 |  | 16520 | 197.21 | 10.888 | 60.186 | 0.028184 | 165.43 | 1145.4 | 979.97
16521 | 10.89 | 197.22 | 60.186 | 0.02819 | 165.44 | 1145.4 |  | 16521 | 197.22 | 10.89 | 60.186 | 0.02819 | 165.44 | 1145.4 | 979.96
16522 | 10.893 | 197.23 | 60.186 | 0.028195 | 165.45 | 1145.4 |  | 16522 | 197.23 | 10.893 | 60.186 | 0.028195 | 165.45 | 1145.4 | 979.95
16523 | 10.895 | 197.24 | 60.186 | 0.028201 | 165.47 | 1145.4 |  | 16523 | 197.24 | 10.895 | 60.186 | 0.028201 | 165.47 | 1145.4 | 979.93
16524 | 10.897 | 197.25 | 60.185 | 0.028206 | 165.48 | 1145.4 |  | 16524 | 197.25 | 10.897 | 60.185 | 0.028206 | 165.48 | 1145.4 | 979.92
16525 | 10.9 | 197.26 | 60.185 | 0.028212 | 165.49 | 1145.4 |  | 16525 | 197.26 | 10.9 | 60.185 | 0.028212 | 165.49 | 1145.4 | 979.91
16526 | 10.902 | 197.27 | 60.185 | 0.028217 | 165.5 | 1145.4 |  | 16526 | 197.27 | 10.902 | 60.185 | 0.028217 | 165.5 | 1145.4 | 979.9
16527 | 10.904 | 197.28 | 60.185 | 0.028223 | 165.51 | 1145.4 |  | 16527 | 197.28 | 10.904 | 60.185 | 0.028223 | 165.51 | 1145.4 | 979.89
16528 | 10.906 | 197.29 | 60.184 | 0.028228 | 165.52 | 1145.4 |  | 16528 | 197.29 | 10.906 | 60.184 | 0.028228 | 165.52 | 1145.4 | 979.88
16529 | 10.909 | 197.3 | 60.184 | 0.028234 | 165.53 | 1145.4 |  | 16529 | 197.3 | 10.909 | 60.184 | 0.028234 | 165.53 | 1145.4 | 979.87
16530 | 10.911 | 197.31 | 60.184 | 0.028239 | 165.54 | 1145.4 |  | 16530 | 197.31 | 10.911 | 60.184 | 0.028239 | 165.54 | 1145.4 | 979.86
16531 | 10.913 | 197.32 | 60.184 | 0.028245 | 165.55 | 1145.4 |  | 16531 | 197.32 | 10.913 | 60.184 | 0.028245 | 165.55 | 1145.4 | 979.85
16532 | 10.915 | 197.33 | 60.183 | 0.02825 | 165.56 | 1145.5 |  | 16532 | 197.33 | 10.915 | 60.183 | 0.02825 | 165.56 | 1145.5 | 979.94
16533 | 10.918 | 197.34 | 60.183 | 0.028256 | 165.57 | 1145.5 |  | 16533 | 197.34 | 10.918 | 60.183 | 0.028256 | 165.57 | 1145.5 | 979.93
16534 | 10.92 | 197.35 | 60.183 | 0.028261 | 165.58 | 1145.5 |  | 16534 | 197.35 | 10.92 | 60.183 | 0.028261 | 165.58 | 1145.5 | 979.92
16535 | 10.922 | 197.36 | 60.183 | 0.028267 | 165.59 | 1145.5 |  | 16535 | 197.36 | 10.922 | 60.183 | 0.028267 | 165.59 | 1145.5 | 979.91
16536 | 10.925 | 197.37 | 60.182 | 0.028272 | 165.6 | 1145.5 |  | 16536 | 197.37 | 10.925 | 60.182 | 0.028272 | 165.6 | 1145.5 | 979.9
16537 | 10.927 | 197.38 | 60.182 | 0.028278 | 165.61 | 1145.5 |  | 16537 | 197.38 | 10.927 | 60.182 | 0.028278 | 165.61 | 1145.5 | 979.89
16538 | 10.929 | 197.39 | 60.182 | 0.028283 | 165.62 | 1145.5 |  | 16538 | 197.39 | 10.929 | 60.182 | 0.028283 | 165.62 | 1145.5 | 979.88
16539 | 10.931 | 197.4 | 60.182 | 0.028289 | 165.63 | 1145.5 |  | 16539 | 197.4 | 10.931 | 60.182 | 0.028289 | 165.63 | 1145.5 | 979.87
16540 | 10.934 | 197.41 | 60.182 | 0.028294 | 165.64 | 1145.5 |  | 16540 | 197.41 | 10.934 | 60.182 | 0.028294 | 165.64 | 1145.5 | 979.86
16541 | 10.936 | 197.42 | 60.181 | 0.0283 | 165.65 | 1145.5 |  | 16541 | 197.42 | 10.936 | 60.181 | 0.0283 | 165.65 | 1145.5 | 979.85
16542 | 10.938 | 197.43 | 60.181 | 0.028305 | 165.66 | 1145.5 |  | 16542 | 197.43 | 10.938 | 60.181 | 0.028305 | 165.66 | 1145.5 | 979.84
16543 | 10.941 | 197.44 | 60.181 | 0.028311 | 165.67 | 1145.5 |  | 16543 | 197.44 | 10.941 | 60.181 | 0.028311 | 165.67 | 1145.5 | 979.83
16544 | 10.943 | 197.45 | 60.181 | 0.028316 | 165.68 | 1145.5 |  | 16544 | 197.45 | 10.943 | 60.181 | 0.028316 | 165.68 | 1145.5 | 979.82
16545 | 10.945 | 197.46 | 60.18 | 0.028322 | 165.69 | 1145.5 |  | 16545 | 197.46 | 10.945 | 60.18 | 0.028322 | 165.69 | 1145.5 | 979.81
16546 | 10.947 | 197.47 | 60.18 | 0.028328 | 165.7 | 1145.5 |  | 16546 | 197.47 | 10.947 | 60.18 | 0.028328 | 165.7 | 1145.5 | 979.8
16547 | 10.95 | 197.48 | 60.18 | 0.028333 | 165.71 | 1145.5 |  | 16547 | 197.48 | 10.95 | 60.18 | 0.028333 | 165.71 | 1145.5 | 979.79
16548 | 10.952 | 197.49 | 60.18 | 0.028339 | 165.72 | 1145.5 |  | 16548 | 197.49 | 10.952 | 60.18 | 0.028339 | 165.72 | 1145.5 | 979.78
16549 | 10.954 | 197.5 | 60.179 | 0.028344 | 165.73 | 1145.5 |  | 16549 | 197.5 | 10.954 | 60.179 | 0.028344 | 165.73 | 1145.5 | 979.77
16550 | 10.957 | 197.51 | 60.179 | 0.02835 | 165.74 | 1145.5 |  | 16550 | 197.51 | 10.957 | 60.179 | 0.02835 | 165.74 | 1145.5 | 979.76
16551 | 10.959 | 197.52 | 60.179 | 0.028355 | 165.75 | 1145.5 |  | 16551 | 197.52 | 10.959 | 60.179 | 0.028355 | 165.75 | 1145.5 | 979.75
16552 | 10.961 | 197.53 | 60.179 | 0.028361 | 165.76 | 1145.5 |  | 16552 | 197.53 | 10.961 | 60.179 | 0.028361 | 165.76 | 1145.5 | 979.74
16553 | 10.963 | 197.54 | 60.178 | 0.028366 | 165.77 | 1145.5 |  | 16553 | 197.54 | 10.963 | 60.178 | 0.028366 | 165.77 | 1145.5 | 979.73
16554 | 10.966 | 197.55 | 60.178 | 0.028372 | 165.78 | 1145.5 |  | 16554 | 197.55 | 10.966 | 60.178 | 0.028372 | 165.78 | 1145.5 | 979.72
16555 | 10.968 | 197.56 | 60.178 | 0.028377 | 165.79 | 1145.5 |  | 16555 | 197.56 | 10.968 | 60.178 | 0.028377 | 165.79 | 1145.5 | 979.71
16556 | 10.97 | 197.57 | 60.178 | 0.028383 | 165.8 | 1145.5 |  | 16556 | 197.57 | 10.97 | 60.178 | 0.028383 | 165.8 | 1145.5 | 979.7
16557 | 10.973 | 197.58 | 60.177 | 0.028388 | 165.81 | 1145.5 |  | 16557 | 197.58 | 10.973 | 60.177 | 0.028388 | 165.81 | 1145.5 | 979.69
16558 | 10.975 | 197.59 | 60.177 | 0.028394 | 165.82 | 1145.6 |  | 16558 | 197.59 | 10.975 | 60.177 | 0.028394 | 165.82 | 1145.6 | 979.78
16559 | 10.977 | 197.6 | 60.177 | 0.028399 | 165.83 | 1145.6 |  | 16559 | 197.6 | 10.977 | 60.177 | 0.028399 | 165.83 | 1145.6 | 979.77
16560 | 10.979 | 197.61 | 60.177 | 0.028405 | 165.84 | 1145.6 |  | 16560 | 197.61 | 10.979 | 60.177 | 0.028405 | 165.84 | 1145.6 | 979.76
16561 | 10.982 | 197.62 | 60.177 | 0.02841 | 165.85 | 1145.6 |  | 16561 | 197.62 | 10.982 | 60.177 | 0.02841 | 165.85 | 1145.6 | 979.75
16562 | 10.984 | 197.63 | 60.176 | 0.028416 | 165.86 | 1145.6 |  | 16562 | 197.63 | 10.984 | 60.176 | 0.028416 | 165.86 | 1145.6 | 979.74
16563 | 10.986 | 197.64 | 60.176 | 0.028422 | 165.87 | 1145.6 |  | 16563 | 197.64 | 10.986 | 60.176 | 0.028422 | 165.87 | 1145.6 | 979.73
16564 | 10.989 | 197.65 | 60.176 | 0.028427 | 165.88 | 1145.6 |  | 16564 | 197.65 | 10.989 | 60.176 | 0.028427 | 165.88 | 1145.6 | 979.72
16565 | 10.991 | 197.66 | 60.176 | 0.028433 | 165.89 | 1145.6 |  | 16565 | 197.66 | 10.991 | 60.176 | 0.028433 | 165.89 | 1145.6 | 979.71
16566 | 10.993 | 197.67 | 60.175 | 0.028438 | 165.9 | 1145.6 |  | 16566 | 197.67 | 10.993 | 60.175 | 0.028438 | 165.9 | 1145.6 | 979.7
16567 | 10.995 | 197.68 | 60.175 | 0.028444 | 165.91 | 1145.6 |  | 16567 | 197.68 | 10.995 | 60.175 | 0.028444 | 165.91 | 1145.6 | 979.69
16568 | 10.998 | 197.69 | 60.175 | 0.028449 | 165.92 | 1145.6 |  | 16568 | 197.69 | 10.998 | 60.175 | 0.028449 | 165.92 | 1145.6 | 979.68
16569 | 11 | 197.7 | 60.175 | 0.028455 | 165.93 | 1145.6 |  | 16569 | 197.7 | 11 | 60.175 | 0.028455 | 165.93 | 1145.6 | 979.67
16570 | 11.002 | 197.71 | 60.174 | 0.02846 | 165.94 | 1145.6 |  | 16570 | 197.71 | 11.002 | 60.174 | 0.02846 | 165.94 | 1145.6 | 979.66
16571 | 11.005 | 197.72 | 60.174 | 0.028466 | 165.95 | 1145.6 |  | 16571 | 197.72 | 11.005 | 60.174 | 0.028466 | 165.95 | 1145.6 | 979.65
16572 | 11.007 | 197.73 | 60.174 | 0.028471 | 165.96 | 1145.6 |  | 16572 | 197.73 | 11.007 | 60.174 | 0.028471 | 165.96 | 1145.6 | 979.64
16573 | 11.009 | 197.74 | 60.174 | 0.028477 | 165.97 | 1145.6 |  | 16573 | 197.74 | 11.009 | 60.174 | 0.028477 | 165.97 | 1145.6 | 979.63
16574 | 11.011 | 197.75 | 60.173 | 0.028483 | 165.98 | 1145.6 |  | 16574 | 197.75 | 11.011 | 60.173 | 0.028483 | 165.98 | 1145.6 | 979.62
16575 | 11.014 | 197.76 | 60.173 | 0.028488 | 165.99 | 1145.6 |  | 16575 | 197.76 | 11.014 | 60.173 | 0.028488 | 165.99 | 1145.6 | 979.61
16576 | 11.016 | 197.77 | 60.173 | 0.028494 | 166 | 1145.6 |  | 16576 | 197.77 | 11.016 | 60.173 | 0.028494 | 166 | 1145.6 | 979.6
16577 | 11.018 | 197.78 | 60.173 | 0.028499 | 166.01 | 1145.6 |  | 16577 | 197.78 | 11.018 | 60.173 | 0.028499 | 166.01 | 1145.6 | 979.59
16578 | 11.021 | 197.79 | 60.173 | 0.028505 | 166.02 | 1145.6 |  | 16578 | 197.79 | 11.021 | 60.173 | 0.028505 | 166.02 | 1145.6 | 979.58
16579 | 11.023 | 197.8 | 60.172 | 0.02851 | 166.03 | 1145.6 |  | 16579 | 197.8 | 11.023 | 60.172 | 0.02851 | 166.03 | 1145.6 | 979.57
16580 | 11.025 | 197.81 | 60.172 | 0.028516 | 166.04 | 1145.6 |  | 16580 | 197.81 | 11.025 | 60.172 | 0.028516 | 166.04 | 1145.6 | 979.56
16581 | 11.027 | 197.82 | 60.172 | 0.028521 | 166.05 | 1145.6 |  | 16581 | 197.82 | 11.027 | 60.172 | 0.028521 | 166.05 | 1145.6 | 979.55
16582 | 11.03 | 197.83 | 60.172 | 0.028527 | 166.06 | 1145.6 |  | 16582 | 197.83 | 11.03 | 60.172 | 0.028527 | 166.06 | 1145.6 | 979.54
16583 | 11.032 | 197.84 | 60.171 | 0.028533 | 166.07 | 1145.6 |  | 16583 | 197.84 | 11.032 | 60.171 | 0.028533 | 166.07 | 1145.6 | 979.53
16584 | 11.034 | 197.85 | 60.171 | 0.028538 | 166.08 | 1145.7 |  | 16584 | 197.85 | 11.034 | 60.171 | 0.028538 | 166.08 | 1145.7 | 979.62
16585 | 11.037 | 197.86 | 60.171 | 0.028544 | 166.09 | 1145.7 |  | 16585 | 197.86 | 11.037 | 60.171 | 0.028544 | 166.09 | 1145.7 | 979.61
16586 | 11.039 | 197.87 | 60.171 | 0.028549 | 166.1 | 1145.7 |  | 16586 | 197.87 | 11.039 | 60.171 | 0.028549 | 166.1 | 1145.7 | 979.6
16587 | 11.041 | 197.88 | 60.17 | 0.028555 | 166.11 | 1145.7 |  | 16587 | 197.88 | 11.041 | 60.17 | 0.028555 | 166.11 | 1145.7 | 979.59
16588 | 11.044 | 197.89 | 60.17 | 0.02856 | 166.12 | 1145.7 |  | 16588 | 197.89 | 11.044 | 60.17 | 0.02856 | 166.12 | 1145.7 | 979.58
16589 | 11.046 | 197.9 | 60.17 | 0.028566 | 166.13 | 1145.7 |  | 16589 | 197.9 | 11.046 | 60.17 | 0.028566 | 166.13 | 1145.7 | 979.57
16590 | 11.048 | 197.91 | 60.17 | 0.028571 | 166.14 | 1145.7 |  | 16590 | 197.91 | 11.048 | 60.17 | 0.028571 | 166.14 | 1145.7 | 979.56
16591 | 11.05 | 197.92 | 60.169 | 0.028577 | 166.15 | 1145.7 |  | 16591 | 197.92 | 11.05 | 60.169 | 0.028577 | 166.15 | 1145.7 | 979.55
16592 | 11.053 | 197.93 | 60.169 | 0.028583 | 166.16 | 1145.7 |  | 16592 | 197.93 | 11.053 | 60.169 | 0.028583 | 166.16 | 1145.7 | 979.54
16593 | 11.055 | 197.94 | 60.169 | 0.028588 | 166.17 | 1145.7 |  | 16593 | 197.94 | 11.055 | 60.169 | 0.028588 | 166.17 | 1145.7 | 979.53
16594 | 11.057 | 197.95 | 60.169 | 0.028594 | 166.18 | 1145.7 |  | 16594 | 197.95 | 11.057 | 60.169 | 0.028594 | 166.18 | 1145.7 | 979.52
16595 | 11.06 | 197.96 | 60.169 | 0.028599 | 166.19 | 1145.7 |  | 16595 | 197.96 | 11.06 | 60.169 | 0.028599 | 166.19 | 1145.7 | 979.51
16596 | 11.062 | 197.97 | 60.168 | 0.028605 | 166.2 | 1145.7 |  | 16596 | 197.97 | 11.062 | 60.168 | 0.028605 | 166.2 | 1145.7 | 979.5
16597 | 11.064 | 197.98 | 60.168 | 0.02861 | 166.21 | 1145.7 |  | 16597 | 197.98 | 11.064 | 60.168 | 0.02861 | 166.21 | 1145.7 | 979.49
16598 | 11.067 | 197.99 | 60.168 | 0.028616 | 166.22 | 1145.7 |  | 16598 | 197.99 | 11.067 | 60.168 | 0.028616 | 166.22 | 1145.7 | 979.48
16599 | 11.069 | 198 | 60.168 | 0.028622 | 166.23 | 1145.7 |  | 16599 | 198 | 11.069 | 60.168 | 0.028622 | 166.23 | 1145.7 | 979.47
16600 | 11.071 | 198.01 | 60.167 | 0.028627 | 166.24 | 1145.7 |  | 16600 | 198.01 | 11.071 | 60.167 | 0.028627 | 166.24 | 1145.7 | 979.46
16601 | 11.073 | 198.02 | 60.167 | 0.028633 | 166.25 | 1145.7 |  | 16601 | 198.02 | 11.073 | 60.167 | 0.028633 | 166.25 | 1145.7 | 979.45
16602 | 11.076 | 198.03 | 60.167 | 0.028638 | 166.26 | 1145.7 |  | 16602 | 198.03 | 11.076 | 60.167 | 0.028638 | 166.26 | 1145.7 | 979.44
16603 | 11.078 | 198.04 | 60.167 | 0.028644 | 166.27 | 1145.7 |  | 16603 | 198.04 | 11.078 | 60.167 | 0.028644 | 166.27 | 1145.7 | 979.43
16604 | 11.08 | 198.05 | 60.166 | 0.028649 | 166.28 | 1145.7 |  | 16604 | 198.05 | 11.08 | 60.166 | 0.028649 | 166.28 | 1145.7 | 979.42
16605 | 11.083 | 198.06 | 60.166 | 0.028655 | 166.29 | 1145.7 |  | 16605 | 198.06 | 11.083 | 60.166 | 0.028655 | 166.29 | 1145.7 | 979.41
16606 | 11.085 | 198.07 | 60.166 | 0.028661 | 166.3 | 1145.7 |  | 16606 | 198.07 | 11.085 | 60.166 | 0.028661 | 166.3 | 1145.7 | 979.4
16607 | 11.087 | 198.08 | 60.166 | 0.028666 | 166.31 | 1145.7 |  | 16607 | 198.08 | 11.087 | 60.166 | 0.028666 | 166.31 | 1145.7 | 979.39
16608 | 11.09 | 198.09 | 60.165 | 0.028672 | 166.32 | 1145.7 |  | 16608 | 198.09 | 11.09 | 60.165 | 0.028672 | 166.32 | 1145.7 | 979.38
16609 | 11.092 | 198.1 | 60.165 | 0.028677 | 166.33 | 1145.7 |  | 16609 | 198.1 | 11.092 | 60.165 | 0.028677 | 166.33 | 1145.7 | 979.37
16610 | 11.094 | 198.11 | 60.165 | 0.028683 | 166.34 | 1145.8 |  | 16610 | 198.11 | 11.094 | 60.165 | 0.028683 | 166.34 | 1145.8 | 979.46
16611 | 11.097 | 198.12 | 60.165 | 0.028688 | 166.35 | 1145.8 |  | 16611 | 198.12 | 11.097 | 60.165 | 0.028688 | 166.35 | 1145.8 | 979.45
16612 | 11.099 | 198.13 | 60.164 | 0.028694 | 166.36 | 1145.8 |  | 16612 | 198.13 | 11.099 | 60.164 | 0.028694 | 166.36 | 1145.8 | 979.44
16613 | 11.101 | 198.14 | 60.164 | 0.0287 | 166.37 | 1145.8 |  | 16613 | 198.14 | 11.101 | 60.164 | 0.0287 | 166.37 | 1145.8 | 979.43
16614 | 11.103 | 198.15 | 60.164 | 0.028705 | 166.38 | 1145.8 |  | 16614 | 198.15 | 11.103 | 60.164 | 0.028705 | 166.38 | 1145.8 | 979.42
16615 | 11.106 | 198.16 | 60.164 | 0.028711 | 166.39 | 1145.8 |  | 16615 | 198.16 | 11.106 | 60.164 | 0.028711 | 166.39 | 1145.8 | 979.41
16616 | 11.108 | 198.17 | 60.164 | 0.028716 | 166.4 | 1145.8 |  | 16616 | 198.17 | 11.108 | 60.164 | 0.028716 | 166.4 | 1145.8 | 979.4
16617 | 11.11 | 198.18 | 60.163 | 0.028722 | 166.41 | 1145.8 |  | 16617 | 198.18 | 11.11 | 60.163 | 0.028722 | 166.41 | 1145.8 | 979.39
16618 | 11.113 | 198.19 | 60.163 | 0.028728 | 166.42 | 1145.8 |  | 16618 | 198.19 | 11.113 | 60.163 | 0.028728 | 166.42 | 1145.8 | 979.38
16619 | 11.115 | 198.2 | 60.163 | 0.028733 | 166.43 | 1145.8 |  | 16619 | 198.2 | 11.115 | 60.163 | 0.028733 | 166.43 | 1145.8 | 979.37
16620 | 11.117 | 198.21 | 60.163 | 0.028739 | 166.44 | 1145.8 |  | 16620 | 198.21 | 11.117 | 60.163 | 0.028739 | 166.44 | 1145.8 | 979.36
16621 | 11.12 | 198.22 | 60.162 | 0.028744 | 166.45 | 1145.8 |  | 16621 | 198.22 | 11.12 | 60.162 | 0.028744 | 166.45 | 1145.8 | 979.35
16622 | 11.122 | 198.23 | 60.162 | 0.02875 | 166.46 | 1145.8 |  | 16622 | 198.23 | 11.122 | 60.162 | 0.02875 | 166.46 | 1145.8 | 979.34
16623 | 11.124 | 198.24 | 60.162 | 0.028755 | 166.47 | 1145.8 |  | 16623 | 198.24 | 11.124 | 60.162 | 0.028755 | 166.47 | 1145.8 | 979.33
16624 | 11.127 | 198.25 | 60.162 | 0.028761 | 166.48 | 1145.8 |  | 16624 | 198.25 | 11.127 | 60.162 | 0.028761 | 166.48 | 1145.8 | 979.32
16625 | 11.129 | 198.26 | 60.161 | 0.028767 | 166.49 | 1145.8 |  | 16625 | 198.26 | 11.129 | 60.161 | 0.028767 | 166.49 | 1145.8 | 979.31
16626 | 11.131 | 198.27 | 60.161 | 0.028772 | 166.5 | 1145.8 |  | 16626 | 198.27 | 11.131 | 60.161 | 0.028772 | 166.5 | 1145.8 | 979.3
16627 | 11.134 | 198.28 | 60.161 | 0.028778 | 166.51 | 1145.8 |  | 16627 | 198.28 | 11.134 | 60.161 | 0.028778 | 166.51 | 1145.8 | 979.29
16628 | 11.136 | 198.29 | 60.161 | 0.028783 | 166.52 | 1145.8 |  | 16628 | 198.29 | 11.136 | 60.161 | 0.028783 | 166.52 | 1145.8 | 979.28
16629 | 11.138 | 198.3 | 60.16 | 0.028789 | 166.53 | 1145.8 |  | 16629 | 198.3 | 11.138 | 60.16 | 0.028789 | 166.53 | 1145.8 | 979.27
16630 | 11.14 | 198.31 | 60.16 | 0.028795 | 166.54 | 1145.8 |  | 16630 | 198.31 | 11.14 | 60.16 | 0.028795 | 166.54 | 1145.8 | 979.26
16631 | 11.143 | 198.32 | 60.16 | 0.0288 | 166.55 | 1145.8 |  | 16631 | 198.32 | 11.143 | 60.16 | 0.0288 | 166.55 | 1145.8 | 979.25
16632 | 11.145 | 198.33 | 60.16 | 0.028806 | 166.56 | 1145.8 |  | 16632 | 198.33 | 11.145 | 60.16 | 0.028806 | 166.56 | 1145.8 | 979.24
16633 | 11.147 | 198.34 | 60.16 | 0.028811 | 166.57 | 1145.8 |  | 16633 | 198.34 | 11.147 | 60.16 | 0.028811 | 166.57 | 1145.8 | 979.23
16634 | 11.15 | 198.35 | 60.159 | 0.028817 | 166.58 | 1145.8 |  | 16634 | 198.35 | 11.15 | 60.159 | 0.028817 | 166.58 | 1145.8 | 979.22
16635 | 11.152 | 198.36 | 60.159 | 0.028823 | 166.59 | 1145.8 |  | 16635 | 198.36 | 11.152 | 60.159 | 0.028823 | 166.59 | 1145.8 | 979.21
16636 | 11.154 | 198.37 | 60.159 | 0.028828 | 166.6 | 1145.9 |  | 16636 | 198.37 | 11.154 | 60.159 | 0.028828 | 166.6 | 1145.9 | 979.3
16637 | 11.157 | 198.38 | 60.159 | 0.028834 | 166.61 | 1145.9 |  | 16637 | 198.38 | 11.157 | 60.159 | 0.028834 | 166.61 | 1145.9 | 979.29
16638 | 11.159 | 198.39 | 60.158 | 0.028839 | 166.62 | 1145.9 |  | 16638 | 198.39 | 11.159 | 60.158 | 0.028839 | 166.62 | 1145.9 | 979.28
16639 | 11.161 | 198.4 | 60.158 | 0.028845 | 166.63 | 1145.9 |  | 16639 | 198.4 | 11.161 | 60.158 | 0.028845 | 166.63 | 1145.9 | 979.27
16640 | 11.164 | 198.41 | 60.158 | 0.028851 | 166.64 | 1145.9 |  | 16640 | 198.41 | 11.164 | 60.158 | 0.028851 | 166.64 | 1145.9 | 979.26
16641 | 11.166 | 198.42 | 60.158 | 0.028856 | 166.65 | 1145.9 |  | 16641 | 198.42 | 11.166 | 60.158 | 0.028856 | 166.65 | 1145.9 | 979.25
16642 | 11.168 | 198.43 | 60.157 | 0.028862 | 166.66 | 1145.9 |  | 16642 | 198.43 | 11.168 | 60.157 | 0.028862 | 166.66 | 1145.9 | 979.24
16643 | 11.171 | 198.44 | 60.157 | 0.028868 | 166.67 | 1145.9 |  | 16643 | 198.44 | 11.171 | 60.157 | 0.028868 | 166.67 | 1145.9 | 979.23
16644 | 11.173 | 198.45 | 60.157 | 0.028873 | 166.68 | 1145.9 |  | 16644 | 198.45 | 11.173 | 60.157 | 0.028873 | 166.68 | 1145.9 | 979.22
16645 | 11.175 | 198.46 | 60.157 | 0.028879 | 166.69 | 1145.9 |  | 16645 | 198.46 | 11.175 | 60.157 | 0.028879 | 166.69 | 1145.9 | 979.21
16646 | 11.178 | 198.47 | 60.156 | 0.028884 | 166.7 | 1145.9 |  | 16646 | 198.47 | 11.178 | 60.156 | 0.028884 | 166.7 | 1145.9 | 979.2
16647 | 11.18 | 198.48 | 60.156 | 0.02889 | 166.71 | 1145.9 |  | 16647 | 198.48 | 11.18 | 60.156 | 0.02889 | 166.71 | 1145.9 | 979.19
16648 | 11.182 | 198.49 | 60.156 | 0.028896 | 166.72 | 1145.9 |  | 16648 | 198.49 | 11.182 | 60.156 | 0.028896 | 166.72 | 1145.9 | 979.18
16649 | 11.185 | 198.5 | 60.156 | 0.028901 | 166.73 | 1145.9 |  | 16649 | 198.5 | 11.185 | 60.156 | 0.028901 | 166.73 | 1145.9 | 979.17
16650 | 11.187 | 198.51 | 60.155 | 0.028907 | 166.74 | 1145.9 |  | 16650 | 198.51 | 11.187 | 60.155 | 0.028907 | 166.74 | 1145.9 | 979.16
16651 | 11.189 | 198.52 | 60.155 | 0.028912 | 166.75 | 1145.9 |  | 16651 | 198.52 | 11.189 | 60.155 | 0.028912 | 166.75 | 1145.9 | 979.15
16652 | 11.192 | 198.53 | 60.155 | 0.028918 | 166.76 | 1145.9 |  | 16652 | 198.53 | 11.192 | 60.155 | 0.028918 | 166.76 | 1145.9 | 979.14
16653 | 11.194 | 198.54 | 60.155 | 0.028924 | 166.77 | 1145.9 |  | 16653 | 198.54 | 11.194 | 60.155 | 0.028924 | 166.77 | 1145.9 | 979.13
16654 | 11.196 | 198.55 | 60.155 | 0.028929 | 166.78 | 1145.9 |  | 16654 | 198.55 | 11.196 | 60.155 | 0.028929 | 166.78 | 1145.9 | 979.12
16655 | 11.198 | 198.56 | 60.154 | 0.028935 | 166.79 | 1145.9 |  | 16655 | 198.56 | 11.198 | 60.154 | 0.028935 | 166.79 | 1145.9 | 979.11
16656 | 11.201 | 198.57 | 60.154 | 0.028941 | 166.8 | 1145.9 |  | 16656 | 198.57 | 11.201 | 60.154 | 0.028941 | 166.8 | 1145.9 | 979.1
16657 | 11.203 | 198.58 | 60.154 | 0.028946 | 166.81 | 1145.9 |  | 16657 | 198.58 | 11.203 | 60.154 | 0.028946 | 166.81 | 1145.9 | 979.09
16658 | 11.205 | 198.59 | 60.154 | 0.028952 | 166.82 | 1145.9 |  | 16658 | 198.59 | 11.205 | 60.154 | 0.028952 | 166.82 | 1145.9 | 979.08
16659 | 11.208 | 198.6 | 60.153 | 0.028957 | 166.83 | 1145.9 |  | 16659 | 198.6 | 11.208 | 60.153 | 0.028957 | 166.83 | 1145.9 | 979.07
16660 | 11.21 | 198.61 | 60.153 | 0.028963 | 166.84 | 1145.9 |  | 16660 | 198.61 | 11.21 | 60.153 | 0.028963 | 166.84 | 1145.9 | 979.06
16661 | 11.212 | 198.62 | 60.153 | 0.028969 | 166.85 | 1145.9 |  | 16661 | 198.62 | 11.212 | 60.153 | 0.028969 | 166.85 | 1145.9 | 979.05
16662 | 11.215 | 198.63 | 60.153 | 0.028974 | 166.86 | 1146 |  | 16662 | 198.63 | 11.215 | 60.153 | 0.028974 | 166.86 | 1146 | 979.14
16663 | 11.217 | 198.64 | 60.152 | 0.02898 | 166.87 | 1146 |  | 16663 | 198.64 | 11.217 | 60.152 | 0.02898 | 166.87 | 1146 | 979.13
16664 | 11.219 | 198.65 | 60.152 | 0.028986 | 166.88 | 1146 |  | 16664 | 198.65 | 11.219 | 60.152 | 0.028986 | 166.88 | 1146 | 979.12
16665 | 11.222 | 198.66 | 60.152 | 0.028991 | 166.89 | 1146 |  | 16665 | 198.66 | 11.222 | 60.152 | 0.028991 | 166.89 | 1146 | 979.11
16666 | 11.224 | 198.67 | 60.152 | 0.028997 | 166.9 | 1146 |  | 16666 | 198.67 | 11.224 | 60.152 | 0.028997 | 166.9 | 1146 | 979.1
16667 | 11.226 | 198.68 | 60.151 | 0.029002 | 166.91 | 1146 |  | 16667 | 198.68 | 11.226 | 60.151 | 0.029002 | 166.91 | 1146 | 979.09
16668 | 11.229 | 198.69 | 60.151 | 0.029008 | 166.92 | 1146 |  | 16668 | 198.69 | 11.229 | 60.151 | 0.029008 | 166.92 | 1146 | 979.08
16669 | 11.231 | 198.7 | 60.151 | 0.029014 | 166.93 | 1146 |  | 16669 | 198.7 | 11.231 | 60.151 | 0.029014 | 166.93 | 1146 | 979.07
16670 | 11.233 | 198.71 | 60.151 | 0.029019 | 166.94 | 1146 |  | 16670 | 198.71 | 11.233 | 60.151 | 0.029019 | 166.94 | 1146 | 979.06
16671 | 11.236 | 198.72 | 60.151 | 0.029025 | 166.95 | 1146 |  | 16671 | 198.72 | 11.236 | 60.151 | 0.029025 | 166.95 | 1146 | 979.05
16672 | 11.238 | 198.73 | 60.15 | 0.029031 | 166.96 | 1146 |  | 16672 | 198.73 | 11.238 | 60.15 | 0.029031 | 166.96 | 1146 | 979.04
16673 | 11.24 | 198.74 | 60.15 | 0.029036 | 166.97 | 1146 |  | 16673 | 198.74 | 11.24 | 60.15 | 0.029036 | 166.97 | 1146 | 979.03
16674 | 11.243 | 198.75 | 60.15 | 0.029042 | 166.98 | 1146 |  | 16674 | 198.75 | 11.243 | 60.15 | 0.029042 | 166.98 | 1146 | 979.02
16675 | 11.245 | 198.76 | 60.15 | 0.029048 | 166.99 | 1146 |  | 16675 | 198.76 | 11.245 | 60.15 | 0.029048 | 166.99 | 1146 | 979.01
16676 | 11.247 | 198.77 | 60.149 | 0.029053 | 167 | 1146 |  | 16676 | 198.77 | 11.247 | 60.149 | 0.029053 | 167 | 1146 | 979
16677 | 11.25 | 198.78 | 60.149 | 0.029059 | 167.01 | 1146 |  | 16677 | 198.78 | 11.25 | 60.149 | 0.029059 | 167.01 | 1146 | 978.99
16678 | 11.252 | 198.79 | 60.149 | 0.029064 | 167.02 | 1146 |  | 16678 | 198.79 | 11.252 | 60.149 | 0.029064 | 167.02 | 1146 | 978.98
16679 | 11.254 | 198.8 | 60.149 | 0.02907 | 167.03 | 1146 |  | 16679 | 198.8 | 11.254 | 60.149 | 0.02907 | 167.03 | 1146 | 978.97
16680 | 11.257 | 198.81 | 60.148 | 0.029076 | 167.04 | 1146 |  | 16680 | 198.81 | 11.257 | 60.148 | 0.029076 | 167.04 | 1146 | 978.96
16681 | 11.259 | 198.82 | 60.148 | 0.029081 | 167.05 | 1146 |  | 16681 | 198.82 | 11.259 | 60.148 | 0.029081 | 167.05 | 1146 | 978.95
16682 | 11.261 | 198.83 | 60.148 | 0.029087 | 167.06 | 1146 |  | 16682 | 198.83 | 11.261 | 60.148 | 0.029087 | 167.06 | 1146 | 978.94
16683 | 11.264 | 198.84 | 60.148 | 0.029093 | 167.07 | 1146 |  | 16683 | 198.84 | 11.264 | 60.148 | 0.029093 | 167.07 | 1146 | 978.93
16684 | 11.266 | 198.85 | 60.147 | 0.029098 | 167.08 | 1146 |  | 16684 | 198.85 | 11.266 | 60.147 | 0.029098 | 167.08 | 1146 | 978.92
16685 | 11.268 | 198.86 | 60.147 | 0.029104 | 167.09 | 1146 |  | 16685 | 198.86 | 11.268 | 60.147 | 0.029104 | 167.09 | 1146 | 978.91
16686 | 11.271 | 198.87 | 60.147 | 0.02911 | 167.1 | 1146 |  | 16686 | 198.87 | 11.271 | 60.147 | 0.02911 | 167.1 | 1146 | 978.9
16687 | 11.273 | 198.88 | 60.147 | 0.029115 | 167.12 | 1146 |  | 16687 | 198.88 | 11.273 | 60.147 | 0.029115 | 167.12 | 1146 | 978.88
16688 | 11.275 | 198.89 | 60.146 | 0.029121 | 167.13 | 1146.1 |  | 16688 | 198.89 | 11.275 | 60.146 | 0.029121 | 167.13 | 1146.1 | 978.97
16689 | 11.278 | 198.9 | 60.146 | 0.029127 | 167.14 | 1146.1 |  | 16689 | 198.9 | 11.278 | 60.146 | 0.029127 | 167.14 | 1146.1 | 978.96
16690 | 11.28 | 198.91 | 60.146 | 0.029132 | 167.15 | 1146.1 |  | 16690 | 198.91 | 11.28 | 60.146 | 0.029132 | 167.15 | 1146.1 | 978.95
16691 | 11.282 | 198.92 | 60.146 | 0.029138 | 167.16 | 1146.1 |  | 16691 | 198.92 | 11.282 | 60.146 | 0.029138 | 167.16 | 1146.1 | 978.94
16692 | 11.285 | 198.93 | 60.146 | 0.029143 | 167.17 | 1146.1 |  | 16692 | 198.93 | 11.285 | 60.146 | 0.029143 | 167.17 | 1146.1 | 978.93
16693 | 11.287 | 198.94 | 60.145 | 0.029149 | 167.18 | 1146.1 |  | 16693 | 198.94 | 11.287 | 60.145 | 0.029149 | 167.18 | 1146.1 | 978.92
16694 | 11.289 | 198.95 | 60.145 | 0.029155 | 167.19 | 1146.1 |  | 16694 | 198.95 | 11.289 | 60.145 | 0.029155 | 167.19 | 1146.1 | 978.91
16695 | 11.292 | 198.96 | 60.145 | 0.02916 | 167.2 | 1146.1 |  | 16695 | 198.96 | 11.292 | 60.145 | 0.02916 | 167.2 | 1146.1 | 978.9
16696 | 11.294 | 198.97 | 60.145 | 0.029166 | 167.21 | 1146.1 |  | 16696 | 198.97 | 11.294 | 60.145 | 0.029166 | 167.21 | 1146.1 | 978.89
16697 | 11.297 | 198.98 | 60.144 | 0.029172 | 167.22 | 1146.1 |  | 16697 | 198.98 | 11.297 | 60.144 | 0.029172 | 167.22 | 1146.1 | 978.88
16698 | 11.299 | 198.99 | 60.144 | 0.029177 | 167.23 | 1146.1 |  | 16698 | 198.99 | 11.299 | 60.144 | 0.029177 | 167.23 | 1146.1 | 978.87
16699 | 11.301 | 199 | 60.144 | 0.029183 | 167.24 | 1146.1 |  | 16699 | 199 | 11.301 | 60.144 | 0.029183 | 167.24 | 1146.1 | 978.86
16700 | 11.304 | 199.01 | 60.144 | 0.029189 | 167.25 | 1146.1 |  | 16700 | 199.01 | 11.304 | 60.144 | 0.029189 | 167.25 | 1146.1 | 978.85
16701 | 11.306 | 199.02 | 60.143 | 0.029194 | 167.26 | 1146.1 |  | 16701 | 199.02 | 11.306 | 60.143 | 0.029194 | 167.26 | 1146.1 | 978.84
16702 | 11.308 | 199.03 | 60.143 | 0.0292 | 167.27 | 1146.1 |  | 16702 | 199.03 | 11.308 | 60.143 | 0.0292 | 167.27 | 1146.1 | 978.83
16703 | 11.311 | 199.04 | 60.143 | 0.029206 | 167.28 | 1146.1 |  | 16703 | 199.04 | 11.311 | 60.143 | 0.029206 | 167.28 | 1146.1 | 978.82
16704 | 11.313 | 199.05 | 60.143 | 0.029211 | 167.29 | 1146.1 |  | 16704 | 199.05 | 11.313 | 60.143 | 0.029211 | 167.29 | 1146.1 | 978.81
16705 | 11.315 | 199.06 | 60.142 | 0.029217 | 167.3 | 1146.1 |  | 16705 | 199.06 | 11.315 | 60.142 | 0.029217 | 167.3 | 1146.1 | 978.8
16706 | 11.318 | 199.07 | 60.142 | 0.029223 | 167.31 | 1146.1 |  | 16706 | 199.07 | 11.318 | 60.142 | 0.029223 | 167.31 | 1146.1 | 978.79
16707 | 11.32 | 199.08 | 60.142 | 0.029228 | 167.32 | 1146.1 |  | 16707 | 199.08 | 11.32 | 60.142 | 0.029228 | 167.32 | 1146.1 | 978.78
16708 | 11.322 | 199.09 | 60.142 | 0.029234 | 167.33 | 1146.1 |  | 16708 | 199.09 | 11.322 | 60.142 | 0.029234 | 167.33 | 1146.1 | 978.77
16709 | 11.325 | 199.1 | 60.142 | 0.02924 | 167.34 | 1146.1 |  | 16709 | 199.1 | 11.325 | 60.142 | 0.02924 | 167.34 | 1146.1 | 978.76
16710 | 11.327 | 199.11 | 60.141 | 0.029245 | 167.35 | 1146.1 |  | 16710 | 199.11 | 11.327 | 60.141 | 0.029245 | 167.35 | 1146.1 | 978.75
16711 | 11.329 | 199.12 | 60.141 | 0.029251 | 167.36 | 1146.1 |  | 16711 | 199.12 | 11.329 | 60.141 | 0.029251 | 167.36 | 1146.1 | 978.74
16712 | 11.332 | 199.13 | 60.141 | 0.029257 | 167.37 | 1146.1 |  | 16712 | 199.13 | 11.332 | 60.141 | 0.029257 | 167.37 | 1146.1 | 978.73
16713 | 11.334 | 199.14 | 60.141 | 0.029262 | 167.38 | 1146.1 |  | 16713 | 199.14 | 11.334 | 60.141 | 0.029262 | 167.38 | 1146.1 | 978.72
16714 | 11.336 | 199.15 | 60.14 | 0.029268 | 167.39 | 1146.2 |  | 16714 | 199.15 | 11.336 | 60.14 | 0.029268 | 167.39 | 1146.2 | 978.81
16715 | 11.339 | 199.16 | 60.14 | 0.029274 | 167.4 | 1146.2 |  | 16715 | 199.16 | 11.339 | 60.14 | 0.029274 | 167.4 | 1146.2 | 978.8
16716 | 11.341 | 199.17 | 60.14 | 0.029279 | 167.41 | 1146.2 |  | 16716 | 199.17 | 11.341 | 60.14 | 0.029279 | 167.41 | 1146.2 | 978.79
16717 | 11.343 | 199.18 | 60.14 | 0.029285 | 167.42 | 1146.2 |  | 16717 | 199.18 | 11.343 | 60.14 | 0.029285 | 167.42 | 1146.2 | 978.78
16718 | 11.346 | 199.19 | 60.139 | 0.029291 | 167.43 | 1146.2 |  | 16718 | 199.19 | 11.346 | 60.139 | 0.029291 | 167.43 | 1146.2 | 978.77
16719 | 11.348 | 199.2 | 60.139 | 0.029296 | 167.44 | 1146.2 |  | 16719 | 199.2 | 11.348 | 60.139 | 0.029296 | 167.44 | 1146.2 | 978.76
16720 | 11.35 | 199.21 | 60.139 | 0.029302 | 167.45 | 1146.2 |  | 16720 | 199.21 | 11.35 | 60.139 | 0.029302 | 167.45 | 1146.2 | 978.75
16721 | 11.353 | 199.22 | 60.139 | 0.029308 | 167.46 | 1146.2 |  | 16721 | 199.22 | 11.353 | 60.139 | 0.029308 | 167.46 | 1146.2 | 978.74
16722 | 11.355 | 199.23 | 60.138 | 0.029314 | 167.47 | 1146.2 |  | 16722 | 199.23 | 11.355 | 60.138 | 0.029314 | 167.47 | 1146.2 | 978.73
16723 | 11.358 | 199.24 | 60.138 | 0.029319 | 167.48 | 1146.2 |  | 16723 | 199.24 | 11.358 | 60.138 | 0.029319 | 167.48 | 1146.2 | 978.72
16724 | 11.36 | 199.25 | 60.138 | 0.029325 | 167.49 | 1146.2 |  | 16724 | 199.25 | 11.36 | 60.138 | 0.029325 | 167.49 | 1146.2 | 978.71
16725 | 11.362 | 199.26 | 60.138 | 0.029331 | 167.5 | 1146.2 |  | 16725 | 199.26 | 11.362 | 60.138 | 0.029331 | 167.5 | 1146.2 | 978.7
16726 | 11.365 | 199.27 | 60.137 | 0.029336 | 167.51 | 1146.2 |  | 16726 | 199.27 | 11.365 | 60.137 | 0.029336 | 167.51 | 1146.2 | 978.69
16727 | 11.367 | 199.28 | 60.137 | 0.029342 | 167.52 | 1146.2 |  | 16727 | 199.28 | 11.367 | 60.137 | 0.029342 | 167.52 | 1146.2 | 978.68
16728 | 11.369 | 199.29 | 60.137 | 0.029348 | 167.53 | 1146.2 |  | 16728 | 199.29 | 11.369 | 60.137 | 0.029348 | 167.53 | 1146.2 | 978.67
16729 | 11.372 | 199.3 | 60.137 | 0.029353 | 167.54 | 1146.2 |  | 16729 | 199.3 | 11.372 | 60.137 | 0.029353 | 167.54 | 1146.2 | 978.66
16730 | 11.374 | 199.31 | 60.137 | 0.029359 | 167.55 | 1146.2 |  | 16730 | 199.31 | 11.374 | 60.137 | 0.029359 | 167.55 | 1146.2 | 978.65
16731 | 11.376 | 199.32 | 60.136 | 0.029365 | 167.56 | 1146.2 |  | 16731 | 199.32 | 11.376 | 60.136 | 0.029365 | 167.56 | 1146.2 | 978.64
16732 | 11.379 | 199.33 | 60.136 | 0.02937 | 167.57 | 1146.2 |  | 16732 | 199.33 | 11.379 | 60.136 | 0.02937 | 167.57 | 1146.2 | 978.63
16733 | 11.381 | 199.34 | 60.136 | 0.029376 | 167.58 | 1146.2 |  | 16733 | 199.34 | 11.381 | 60.136 | 0.029376 | 167.58 | 1146.2 | 978.62
16734 | 11.383 | 199.35 | 60.136 | 0.029382 | 167.59 | 1146.2 |  | 16734 | 199.35 | 11.383 | 60.136 | 0.029382 | 167.59 | 1146.2 | 978.61
16735 | 11.386 | 199.36 | 60.135 | 0.029387 | 167.6 | 1146.2 |  | 16735 | 199.36 | 11.386 | 60.135 | 0.029387 | 167.6 | 1146.2 | 978.6
16736 | 11.388 | 199.37 | 60.135 | 0.029393 | 167.61 | 1146.2 |  | 16736 | 199.37 | 11.388 | 60.135 | 0.029393 | 167.61 | 1146.2 | 978.59
16737 | 11.391 | 199.38 | 60.135 | 0.029399 | 167.62 | 1146.2 |  | 16737 | 199.38 | 11.391 | 60.135 | 0.029399 | 167.62 | 1146.2 | 978.58
16738 | 11.393 | 199.39 | 60.135 | 0.029405 | 167.63 | 1146.2 |  | 16738 | 199.39 | 11.393 | 60.135 | 0.029405 | 167.63 | 1146.2 | 978.57
16739 | 11.395 | 199.4 | 60.134 | 0.02941 | 167.64 | 1146.3 |  | 16739 | 199.4 | 11.395 | 60.134 | 0.02941 | 167.64 | 1146.3 | 978.66
16740 | 11.398 | 199.41 | 60.134 | 0.029416 | 167.65 | 1146.3 |  | 16740 | 199.41 | 11.398 | 60.134 | 0.029416 | 167.65 | 1146.3 | 978.65
16741 | 11.4 | 199.42 | 60.134 | 0.029422 | 167.66 | 1146.3 |  | 16741 | 199.42 | 11.4 | 60.134 | 0.029422 | 167.66 | 1146.3 | 978.64
16742 | 11.402 | 199.43 | 60.134 | 0.029427 | 167.67 | 1146.3 |  | 16742 | 199.43 | 11.402 | 60.134 | 0.029427 | 167.67 | 1146.3 | 978.63
16743 | 11.405 | 199.44 | 60.133 | 0.029433 | 167.68 | 1146.3 |  | 16743 | 199.44 | 11.405 | 60.133 | 0.029433 | 167.68 | 1146.3 | 978.62
16744 | 11.407 | 199.45 | 60.133 | 0.029439 | 167.69 | 1146.3 |  | 16744 | 199.45 | 11.407 | 60.133 | 0.029439 | 167.69 | 1146.3 | 978.61
16745 | 11.409 | 199.46 | 60.133 | 0.029444 | 167.7 | 1146.3 |  | 16745 | 199.46 | 11.409 | 60.133 | 0.029444 | 167.7 | 1146.3 | 978.6
16746 | 11.412 | 199.47 | 60.133 | 0.02945 | 167.71 | 1146.3 |  | 16746 | 199.47 | 11.412 | 60.133 | 0.02945 | 167.71 | 1146.3 | 978.59
16747 | 11.414 | 199.48 | 60.132 | 0.029456 | 167.72 | 1146.3 |  | 16747 | 199.48 | 11.414 | 60.132 | 0.029456 | 167.72 | 1146.3 | 978.58
16748 | 11.417 | 199.49 | 60.132 | 0.029462 | 167.73 | 1146.3 |  | 16748 | 199.49 | 11.417 | 60.132 | 0.029462 | 167.73 | 1146.3 | 978.57
16749 | 11.419 | 199.5 | 60.132 | 0.029467 | 167.74 | 1146.3 |  | 16749 | 199.5 | 11.419 | 60.132 | 0.029467 | 167.74 | 1146.3 | 978.56
16750 | 11.421 | 199.51 | 60.132 | 0.029473 | 167.75 | 1146.3 |  | 16750 | 199.51 | 11.421 | 60.132 | 0.029473 | 167.75 | 1146.3 | 978.55
16751 | 11.424 | 199.52 | 60.132 | 0.029479 | 167.76 | 1146.3 |  | 16751 | 199.52 | 11.424 | 60.132 | 0.029479 | 167.76 | 1146.3 | 978.54
16752 | 11.426 | 199.53 | 60.131 | 0.029484 | 167.77 | 1146.3 |  | 16752 | 199.53 | 11.426 | 60.131 | 0.029484 | 167.77 | 1146.3 | 978.53
16753 | 11.428 | 199.54 | 60.131 | 0.02949 | 167.78 | 1146.3 |  | 16753 | 199.54 | 11.428 | 60.131 | 0.02949 | 167.78 | 1146.3 | 978.52
16754 | 11.431 | 199.55 | 60.131 | 0.029496 | 167.79 | 1146.3 |  | 16754 | 199.55 | 11.431 | 60.131 | 0.029496 | 167.79 | 1146.3 | 978.51
16755 | 11.433 | 199.56 | 60.131 | 0.029501 | 167.8 | 1146.3 |  | 16755 | 199.56 | 11.433 | 60.131 | 0.029501 | 167.8 | 1146.3 | 978.5
16756 | 11.435 | 199.57 | 60.13 | 0.029507 | 167.81 | 1146.3 |  | 16756 | 199.57 | 11.435 | 60.13 | 0.029507 | 167.81 | 1146.3 | 978.49
16757 | 11.438 | 199.58 | 60.13 | 0.029513 | 167.82 | 1146.3 |  | 16757 | 199.58 | 11.438 | 60.13 | 0.029513 | 167.82 | 1146.3 | 978.48
16758 | 11.44 | 199.59 | 60.13 | 0.029519 | 167.83 | 1146.3 |  | 16758 | 199.59 | 11.44 | 60.13 | 0.029519 | 167.83 | 1146.3 | 978.47
16759 | 11.443 | 199.6 | 60.13 | 0.029524 | 167.84 | 1146.3 |  | 16759 | 199.6 | 11.443 | 60.13 | 0.029524 | 167.84 | 1146.3 | 978.46
16760 | 11.445 | 199.61 | 60.129 | 0.02953 | 167.85 | 1146.3 |  | 16760 | 199.61 | 11.445 | 60.129 | 0.02953 | 167.85 | 1146.3 | 978.45
16761 | 11.447 | 199.62 | 60.129 | 0.029536 | 167.86 | 1146.3 |  | 16761 | 199.62 | 11.447 | 60.129 | 0.029536 | 167.86 | 1146.3 | 978.44
16762 | 11.45 | 199.63 | 60.129 | 0.029541 | 167.87 | 1146.3 |  | 16762 | 199.63 | 11.45 | 60.129 | 0.029541 | 167.87 | 1146.3 | 978.43
16763 | 11.452 | 199.64 | 60.129 | 0.029547 | 167.88 | 1146.3 |  | 16763 | 199.64 | 11.452 | 60.129 | 0.029547 | 167.88 | 1146.3 | 978.42
16764 | 11.454 | 199.65 | 60.128 | 0.029553 | 167.89 | 1146.3 |  | 16764 | 199.65 | 11.454 | 60.128 | 0.029553 | 167.89 | 1146.3 | 978.41
16765 | 11.457 | 199.66 | 60.128 | 0.029559 | 167.9 | 1146.4 |  | 16765 | 199.66 | 11.457 | 60.128 | 0.029559 | 167.9 | 1146.4 | 978.5
16766 | 11.459 | 199.67 | 60.128 | 0.029564 | 167.91 | 1146.4 |  | 16766 | 199.67 | 11.459 | 60.128 | 0.029564 | 167.91 | 1146.4 | 978.49
16767 | 11.461 | 199.68 | 60.128 | 0.02957 | 167.92 | 1146.4 |  | 16767 | 199.68 | 11.461 | 60.128 | 0.02957 | 167.92 | 1146.4 | 978.48
16768 | 11.464 | 199.69 | 60.127 | 0.029576 | 167.93 | 1146.4 |  | 16768 | 199.69 | 11.464 | 60.127 | 0.029576 | 167.93 | 1146.4 | 978.47
16769 | 11.466 | 199.7 | 60.127 | 0.029582 | 167.94 | 1146.4 |  | 16769 | 199.7 | 11.466 | 60.127 | 0.029582 | 167.94 | 1146.4 | 978.46
16770 | 11.469 | 199.71 | 60.127 | 0.029587 | 167.95 | 1146.4 |  | 16770 | 199.71 | 11.469 | 60.127 | 0.029587 | 167.95 | 1146.4 | 978.45
16771 | 11.471 | 199.72 | 60.127 | 0.029593 | 167.96 | 1146.4 |  | 16771 | 199.72 | 11.471 | 60.127 | 0.029593 | 167.96 | 1146.4 | 978.44
16772 | 11.473 | 199.73 | 60.127 | 0.029599 | 167.97 | 1146.4 |  | 16772 | 199.73 | 11.473 | 60.127 | 0.029599 | 167.97 | 1146.4 | 978.43
16773 | 11.476 | 199.74 | 60.126 | 0.029604 | 167.98 | 1146.4 |  | 16773 | 199.74 | 11.476 | 60.126 | 0.029604 | 167.98 | 1146.4 | 978.42
16774 | 11.478 | 199.75 | 60.126 | 0.02961 | 167.99 | 1146.4 |  | 16774 | 199.75 | 11.478 | 60.126 | 0.02961 | 167.99 | 1146.4 | 978.41
16775 | 11.48 | 199.76 | 60.126 | 0.029616 | 168 | 1146.4 |  | 16775 | 199.76 | 11.48 | 60.126 | 0.029616 | 168 | 1146.4 | 978.4
16776 | 11.483 | 199.77 | 60.126 | 0.029622 | 168.01 | 1146.4 |  | 16776 | 199.77 | 11.483 | 60.126 | 0.029622 | 168.01 | 1146.4 | 978.39
16777 | 11.485 | 199.78 | 60.125 | 0.029627 | 168.02 | 1146.4 |  | 16777 | 199.78 | 11.485 | 60.125 | 0.029627 | 168.02 | 1146.4 | 978.38
16778 | 11.488 | 199.79 | 60.125 | 0.029633 | 168.03 | 1146.4 |  | 16778 | 199.79 | 11.488 | 60.125 | 0.029633 | 168.03 | 1146.4 | 978.37
16779 | 11.49 | 199.8 | 60.125 | 0.029639 | 168.04 | 1146.4 |  | 16779 | 199.8 | 11.49 | 60.125 | 0.029639 | 168.04 | 1146.4 | 978.36
16780 | 11.492 | 199.81 | 60.125 | 0.029645 | 168.05 | 1146.4 |  | 16780 | 199.81 | 11.492 | 60.125 | 0.029645 | 168.05 | 1146.4 | 978.35
16781 | 11.495 | 199.82 | 60.124 | 0.02965 | 168.06 | 1146.4 |  | 16781 | 199.82 | 11.495 | 60.124 | 0.02965 | 168.06 | 1146.4 | 978.34
16782 | 11.497 | 199.83 | 60.124 | 0.029656 | 168.07 | 1146.4 |  | 16782 | 199.83 | 11.497 | 60.124 | 0.029656 | 168.07 | 1146.4 | 978.33
16783 | 11.499 | 199.84 | 60.124 | 0.029662 | 168.08 | 1146.4 |  | 16783 | 199.84 | 11.499 | 60.124 | 0.029662 | 168.08 | 1146.4 | 978.32
16784 | 11.502 | 199.85 | 60.124 | 0.029667 | 168.09 | 1146.4 |  | 16784 | 199.85 | 11.502 | 60.124 | 0.029667 | 168.09 | 1146.4 | 978.31
16785 | 11.504 | 199.86 | 60.123 | 0.029673 | 168.1 | 1146.4 |  | 16785 | 199.86 | 11.504 | 60.123 | 0.029673 | 168.1 | 1146.4 | 978.3
16786 | 11.507 | 199.87 | 60.123 | 0.029679 | 168.11 | 1146.4 |  | 16786 | 199.87 | 11.507 | 60.123 | 0.029679 | 168.11 | 1146.4 | 978.29
16787 | 11.509 | 199.88 | 60.123 | 0.029685 | 168.12 | 1146.4 |  | 16787 | 199.88 | 11.509 | 60.123 | 0.029685 | 168.12 | 1146.4 | 978.28
16788 | 11.511 | 199.89 | 60.123 | 0.02969 | 168.13 | 1146.4 |  | 16788 | 199.89 | 11.511 | 60.123 | 0.02969 | 168.13 | 1146.4 | 978.27
16789 | 11.514 | 199.9 | 60.122 | 0.029696 | 168.14 | 1146.4 |  | 16789 | 199.9 | 11.514 | 60.122 | 0.029696 | 168.14 | 1146.4 | 978.26
16790 | 11.516 | 199.91 | 60.122 | 0.029702 | 168.15 | 1146.4 |  | 16790 | 199.91 | 11.516 | 60.122 | 0.029702 | 168.15 | 1146.4 | 978.25
16791 | 11.518 | 199.92 | 60.122 | 0.029708 | 168.16 | 1146.5 |  | 16791 | 199.92 | 11.518 | 60.122 | 0.029708 | 168.16 | 1146.5 | 978.34
16792 | 11.521 | 199.93 | 60.122 | 0.029713 | 168.17 | 1146.5 |  | 16792 | 199.93 | 11.521 | 60.122 | 0.029713 | 168.17 | 1146.5 | 978.33
16793 | 11.523 | 199.94 | 60.122 | 0.029719 | 168.18 | 1146.5 |  | 16793 | 199.94 | 11.523 | 60.122 | 0.029719 | 168.18 | 1146.5 | 978.32
16794 | 11.526 | 199.95 | 60.121 | 0.029725 | 168.19 | 1146.5 |  | 16794 | 199.95 | 11.526 | 60.121 | 0.029725 | 168.19 | 1146.5 | 978.31
16795 | 11.528 | 199.96 | 60.121 | 0.029731 | 168.2 | 1146.5 |  | 16795 | 199.96 | 11.528 | 60.121 | 0.029731 | 168.2 | 1146.5 | 978.3
16796 | 11.53 | 199.97 | 60.121 | 0.029736 | 168.21 | 1146.5 |  | 16796 | 199.97 | 11.53 | 60.121 | 0.029736 | 168.21 | 1146.5 | 978.29
16797 | 11.533 | 199.98 | 60.121 | 0.029742 | 168.22 | 1146.5 |  | 16797 | 199.98 | 11.533 | 60.121 | 0.029742 | 168.22 | 1146.5 | 978.28
16798 | 11.535 | 199.99 | 60.12 | 0.029748 | 168.23 | 1146.5 |  | 16798 | 199.99 | 11.535 | 60.12 | 0.029748 | 168.23 | 1146.5 | 978.27
16799 | 11.538 | 200 | 60.12 | 0.029754 | 168.24 | 1146.5 |  | 16799 | 200 | 11.538 | 60.12 | 0.029754 | 168.24 | 1146.5 | 978.26
16800 | 11.54 | 200.01 | 60.12 | 0.029759 | 168.25 | 1146.5 |  | 16800 | 200.01 | 11.54 | 60.12 | 0.029759 | 168.25 | 1146.5 | 978.25
16801 | 11.542 | 200.02 | 60.12 | 0.029765 | 168.26 | 1146.5 |  | 16801 | 200.02 | 11.542 | 60.12 | 0.029765 | 168.26 | 1146.5 | 978.24
16802 | 11.545 | 200.03 | 60.119 | 0.029771 | 168.27 | 1146.5 |  | 16802 | 200.03 | 11.545 | 60.119 | 0.029771 | 168.27 | 1146.5 | 978.23
16803 | 11.547 | 200.04 | 60.119 | 0.029777 | 168.28 | 1146.5 |  | 16803 | 200.04 | 11.547 | 60.119 | 0.029777 | 168.28 | 1146.5 | 978.22
16804 | 11.549 | 200.05 | 60.119 | 0.029782 | 168.29 | 1146.5 |  | 16804 | 200.05 | 11.549 | 60.119 | 0.029782 | 168.29 | 1146.5 | 978.21
16805 | 11.552 | 200.06 | 60.119 | 0.029788 | 168.3 | 1146.5 |  | 16805 | 200.06 | 11.552 | 60.119 | 0.029788 | 168.3 | 1146.5 | 978.2
16806 | 11.554 | 200.07 | 60.118 | 0.029794 | 168.31 | 1146.5 |  | 16806 | 200.07 | 11.554 | 60.118 | 0.029794 | 168.31 | 1146.5 | 978.19
16807 | 11.557 | 200.08 | 60.118 | 0.0298 | 168.32 | 1146.5 |  | 16807 | 200.08 | 11.557 | 60.118 | 0.0298 | 168.32 | 1146.5 | 978.18
16808 | 11.559 | 200.09 | 60.118 | 0.029805 | 168.33 | 1146.5 |  | 16808 | 200.09 | 11.559 | 60.118 | 0.029805 | 168.33 | 1146.5 | 978.17
16809 | 11.561 | 200.1 | 60.118 | 0.029811 | 168.34 | 1146.5 |  | 16809 | 200.1 | 11.561 | 60.118 | 0.029811 | 168.34 | 1146.5 | 978.16
16810 | 11.564 | 200.11 | 60.117 | 0.029817 | 168.35 | 1146.5 |  | 16810 | 200.11 | 11.564 | 60.117 | 0.029817 | 168.35 | 1146.5 | 978.15
16811 | 11.566 | 200.12 | 60.117 | 0.029823 | 168.36 | 1146.5 |  | 16811 | 200.12 | 11.566 | 60.117 | 0.029823 | 168.36 | 1146.5 | 978.14
16812 | 11.569 | 200.13 | 60.117 | 0.029829 | 168.37 | 1146.5 |  | 16812 | 200.13 | 11.569 | 60.117 | 0.029829 | 168.37 | 1146.5 | 978.13
16813 | 11.571 | 200.14 | 60.117 | 0.029834 | 168.38 | 1146.5 |  | 16813 | 200.14 | 11.571 | 60.117 | 0.029834 | 168.38 | 1146.5 | 978.12
16814 | 11.573 | 200.15 | 60.117 | 0.02984 | 168.39 | 1146.5 |  | 16814 | 200.15 | 11.573 | 60.117 | 0.02984 | 168.39 | 1146.5 | 978.11
16815 | 11.576 | 200.16 | 60.116 | 0.029846 | 168.4 | 1146.5 |  | 16815 | 200.16 | 11.576 | 60.116 | 0.029846 | 168.4 | 1146.5 | 978.1
16816 | 11.578 | 200.17 | 60.116 | 0.029852 | 168.41 | 1146.5 |  | 16816 | 200.17 | 11.578 | 60.116 | 0.029852 | 168.41 | 1146.5 | 978.09
16817 | 11.581 | 200.18 | 60.116 | 0.029857 | 168.42 | 1146.6 |  | 16817 | 200.18 | 11.581 | 60.116 | 0.029857 | 168.42 | 1146.6 | 978.18
16818 | 11.583 | 200.19 | 60.116 | 0.029863 | 168.43 | 1146.6 |  | 16818 | 200.19 | 11.583 | 60.116 | 0.029863 | 168.43 | 1146.6 | 978.17
16819 | 11.585 | 200.2 | 60.115 | 0.029869 | 168.44 | 1146.6 |  | 16819 | 200.2 | 11.585 | 60.115 | 0.029869 | 168.44 | 1146.6 | 978.16
16820 | 11.588 | 200.21 | 60.115 | 0.029875 | 168.45 | 1146.6 |  | 16820 | 200.21 | 11.588 | 60.115 | 0.029875 | 168.45 | 1146.6 | 978.15
16821 | 11.59 | 200.22 | 60.115 | 0.02988 | 168.46 | 1146.6 |  | 16821 | 200.22 | 11.59 | 60.115 | 0.02988 | 168.46 | 1146.6 | 978.14
16822 | 11.592 | 200.23 | 60.115 | 0.029886 | 168.47 | 1146.6 |  | 16822 | 200.23 | 11.592 | 60.115 | 0.029886 | 168.47 | 1146.6 | 978.13
16823 | 11.595 | 200.24 | 60.114 | 0.029892 | 168.48 | 1146.6 |  | 16823 | 200.24 | 11.595 | 60.114 | 0.029892 | 168.48 | 1146.6 | 978.12
16824 | 11.597 | 200.25 | 60.114 | 0.029898 | 168.49 | 1146.6 |  | 16824 | 200.25 | 11.597 | 60.114 | 0.029898 | 168.49 | 1146.6 | 978.11
16825 | 11.6 | 200.26 | 60.114 | 0.029903 | 168.5 | 1146.6 |  | 16825 | 200.26 | 11.6 | 60.114 | 0.029903 | 168.5 | 1146.6 | 978.1
16826 | 11.602 | 200.27 | 60.114 | 0.029909 | 168.51 | 1146.6 |  | 16826 | 200.27 | 11.602 | 60.114 | 0.029909 | 168.51 | 1146.6 | 978.09
16827 | 11.604 | 200.28 | 60.113 | 0.029915 | 168.52 | 1146.6 |  | 16827 | 200.28 | 11.604 | 60.113 | 0.029915 | 168.52 | 1146.6 | 978.08
16828 | 11.607 | 200.29 | 60.113 | 0.029921 | 168.53 | 1146.6 |  | 16828 | 200.29 | 11.607 | 60.113 | 0.029921 | 168.53 | 1146.6 | 978.07
16829 | 11.609 | 200.3 | 60.113 | 0.029927 | 168.54 | 1146.6 |  | 16829 | 200.3 | 11.609 | 60.113 | 0.029927 | 168.54 | 1146.6 | 978.06
16830 | 11.612 | 200.31 | 60.113 | 0.029932 | 168.55 | 1146.6 |  | 16830 | 200.31 | 11.612 | 60.113 | 0.029932 | 168.55 | 1146.6 | 978.05
16831 | 11.614 | 200.32 | 60.112 | 0.029938 | 168.56 | 1146.6 |  | 16831 | 200.32 | 11.614 | 60.112 | 0.029938 | 168.56 | 1146.6 | 978.04
16832 | 11.616 | 200.33 | 60.112 | 0.029944 | 168.57 | 1146.6 |  | 16832 | 200.33 | 11.616 | 60.112 | 0.029944 | 168.57 | 1146.6 | 978.03
16833 | 11.619 | 200.34 | 60.112 | 0.02995 | 168.58 | 1146.6 |  | 16833 | 200.34 | 11.619 | 60.112 | 0.02995 | 168.58 | 1146.6 | 978.02
16834 | 11.621 | 200.35 | 60.112 | 0.029956 | 168.59 | 1146.6 |  | 16834 | 200.35 | 11.621 | 60.112 | 0.029956 | 168.59 | 1146.6 | 978.01
16835 | 11.624 | 200.36 | 60.112 | 0.029961 | 168.6 | 1146.6 |  | 16835 | 200.36 | 11.624 | 60.112 | 0.029961 | 168.6 | 1146.6 | 978
16836 | 11.626 | 200.37 | 60.111 | 0.029967 | 168.61 | 1146.6 |  | 16836 | 200.37 | 11.626 | 60.111 | 0.029967 | 168.61 | 1146.6 | 977.99
16837 | 11.628 | 200.38 | 60.111 | 0.029973 | 168.62 | 1146.6 |  | 16837 | 200.38 | 11.628 | 60.111 | 0.029973 | 168.62 | 1146.6 | 977.98
16838 | 11.631 | 200.39 | 60.111 | 0.029979 | 168.63 | 1146.6 |  | 16838 | 200.39 | 11.631 | 60.111 | 0.029979 | 168.63 | 1146.6 | 977.97
16839 | 11.633 | 200.4 | 60.111 | 0.029984 | 168.64 | 1146.6 |  | 16839 | 200.4 | 11.633 | 60.111 | 0.029984 | 168.64 | 1146.6 | 977.96
16840 | 11.636 | 200.41 | 60.11 | 0.02999 | 168.65 | 1146.6 |  | 16840 | 200.41 | 11.636 | 60.11 | 0.02999 | 168.65 | 1146.6 | 977.95
16841 | 11.638 | 200.42 | 60.11 | 0.029996 | 168.66 | 1146.6 |  | 16841 | 200.42 | 11.638 | 60.11 | 0.029996 | 168.66 | 1146.6 | 977.94
16842 | 11.64 | 200.43 | 60.11 | 0.030002 | 168.67 | 1146.6 |  | 16842 | 200.43 | 11.64 | 60.11 | 0.030002 | 168.67 | 1146.6 | 977.93
16843 | 11.643 | 200.44 | 60.11 | 0.030008 | 168.68 | 1146.7 |  | 16843 | 200.44 | 11.643 | 60.11 | 0.030008 | 168.68 | 1146.7 | 978.02
16844 | 11.645 | 200.45 | 60.109 | 0.030013 | 168.7 | 1146.7 |  | 16844 | 200.45 | 11.645 | 60.109 | 0.030013 | 168.7 | 1146.7 | 978
16845 | 11.648 | 200.46 | 60.109 | 0.030019 | 168.71 | 1146.7 |  | 16845 | 200.46 | 11.648 | 60.109 | 0.030019 | 168.71 | 1146.7 | 977.99
16846 | 11.65 | 200.47 | 60.109 | 0.030025 | 168.72 | 1146.7 |  | 16846 | 200.47 | 11.65 | 60.109 | 0.030025 | 168.72 | 1146.7 | 977.98
16847 | 11.652 | 200.48 | 60.109 | 0.030031 | 168.73 | 1146.7 |  | 16847 | 200.48 | 11.652 | 60.109 | 0.030031 | 168.73 | 1146.7 | 977.97
16848 | 11.655 | 200.49 | 60.108 | 0.030037 | 168.74 | 1146.7 |  | 16848 | 200.49 | 11.655 | 60.108 | 0.030037 | 168.74 | 1146.7 | 977.96
16849 | 11.657 | 200.5 | 60.108 | 0.030042 | 168.75 | 1146.7 |  | 16849 | 200.5 | 11.657 | 60.108 | 0.030042 | 168.75 | 1146.7 | 977.95
16850 | 11.66 | 200.51 | 60.108 | 0.030048 | 168.76 | 1146.7 |  | 16850 | 200.51 | 11.66 | 60.108 | 0.030048 | 168.76 | 1146.7 | 977.94
16851 | 11.662 | 200.52 | 60.108 | 0.030054 | 168.77 | 1146.7 |  | 16851 | 200.52 | 11.662 | 60.108 | 0.030054 | 168.77 | 1146.7 | 977.93
16852 | 11.664 | 200.53 | 60.107 | 0.03006 | 168.78 | 1146.7 |  | 16852 | 200.53 | 11.664 | 60.107 | 0.03006 | 168.78 | 1146.7 | 977.92
16853 | 11.667 | 200.54 | 60.107 | 0.030066 | 168.79 | 1146.7 |  | 16853 | 200.54 | 11.667 | 60.107 | 0.030066 | 168.79 | 1146.7 | 977.91
16854 | 11.669 | 200.55 | 60.107 | 0.030071 | 168.8 | 1146.7 |  | 16854 | 200.55 | 11.669 | 60.107 | 0.030071 | 168.8 | 1146.7 | 977.9
16855 | 11.672 | 200.56 | 60.107 | 0.030077 | 168.81 | 1146.7 |  | 16855 | 200.56 | 11.672 | 60.107 | 0.030077 | 168.81 | 1146.7 | 977.89
16856 | 11.674 | 200.57 | 60.107 | 0.030083 | 168.82 | 1146.7 |  | 16856 | 200.57 | 11.674 | 60.107 | 0.030083 | 168.82 | 1146.7 | 977.88
16857 | 11.677 | 200.58 | 60.106 | 0.030089 | 168.83 | 1146.7 |  | 16857 | 200.58 | 11.677 | 60.106 | 0.030089 | 168.83 | 1146.7 | 977.87
16858 | 11.679 | 200.59 | 60.106 | 0.030095 | 168.84 | 1146.7 |  | 16858 | 200.59 | 11.679 | 60.106 | 0.030095 | 168.84 | 1146.7 | 977.86
16859 | 11.681 | 200.6 | 60.106 | 0.0301 | 168.85 | 1146.7 |  | 16859 | 200.6 | 11.681 | 60.106 | 0.0301 | 168.85 | 1146.7 | 977.85
16860 | 11.684 | 200.61 | 60.106 | 0.030106 | 168.86 | 1146.7 |  | 16860 | 200.61 | 11.684 | 60.106 | 0.030106 | 168.86 | 1146.7 | 977.84
16861 | 11.686 | 200.62 | 60.105 | 0.030112 | 168.87 | 1146.7 |  | 16861 | 200.62 | 11.686 | 60.105 | 0.030112 | 168.87 | 1146.7 | 977.83
16862 | 11.689 | 200.63 | 60.105 | 0.030118 | 168.88 | 1146.7 |  | 16862 | 200.63 | 11.689 | 60.105 | 0.030118 | 168.88 | 1146.7 | 977.82
16863 | 11.691 | 200.64 | 60.105 | 0.030124 | 168.89 | 1146.7 |  | 16863 | 200.64 | 11.691 | 60.105 | 0.030124 | 168.89 | 1146.7 | 977.81
16864 | 11.693 | 200.65 | 60.105 | 0.030129 | 168.9 | 1146.7 |  | 16864 | 200.65 | 11.693 | 60.105 | 0.030129 | 168.9 | 1146.7 | 977.8
16865 | 11.696 | 200.66 | 60.104 | 0.030135 | 168.91 | 1146.7 |  | 16865 | 200.66 | 11.696 | 60.104 | 0.030135 | 168.91 | 1146.7 | 977.79
16866 | 11.698 | 200.67 | 60.104 | 0.030141 | 168.92 | 1146.7 |  | 16866 | 200.67 | 11.698 | 60.104 | 0.030141 | 168.92 | 1146.7 | 977.78
16867 | 11.701 | 200.68 | 60.104 | 0.030147 | 168.93 | 1146.7 |  | 16867 | 200.68 | 11.701 | 60.104 | 0.030147 | 168.93 | 1146.7 | 977.77
16868 | 11.703 | 200.69 | 60.104 | 0.030153 | 168.94 | 1146.7 |  | 16868 | 200.69 | 11.703 | 60.104 | 0.030153 | 168.94 | 1146.7 | 977.76
16869 | 11.705 | 200.7 | 60.103 | 0.030158 | 168.95 | 1146.8 |  | 16869 | 200.7 | 11.705 | 60.103 | 0.030158 | 168.95 | 1146.8 | 977.85
16870 | 11.708 | 200.71 | 60.103 | 0.030164 | 168.96 | 1146.8 |  | 16870 | 200.71 | 11.708 | 60.103 | 0.030164 | 168.96 | 1146.8 | 977.84
16871 | 11.71 | 200.72 | 60.103 | 0.03017 | 168.97 | 1146.8 |  | 16871 | 200.72 | 11.71 | 60.103 | 0.03017 | 168.97 | 1146.8 | 977.83
16872 | 11.713 | 200.73 | 60.103 | 0.030176 | 168.98 | 1146.8 |  | 16872 | 200.73 | 11.713 | 60.103 | 0.030176 | 168.98 | 1146.8 | 977.82
16873 | 11.715 | 200.74 | 60.102 | 0.030182 | 168.99 | 1146.8 |  | 16873 | 200.74 | 11.715 | 60.102 | 0.030182 | 168.99 | 1146.8 | 977.81
16874 | 11.718 | 200.75 | 60.102 | 0.030188 | 169 | 1146.8 |  | 16874 | 200.75 | 11.718 | 60.102 | 0.030188 | 169 | 1146.8 | 977.8
16875 | 11.72 | 200.76 | 60.102 | 0.030193 | 169.01 | 1146.8 |  | 16875 | 200.76 | 11.72 | 60.102 | 0.030193 | 169.01 | 1146.8 | 977.79
16876 | 11.722 | 200.77 | 60.102 | 0.030199 | 169.02 | 1146.8 |  | 16876 | 200.77 | 11.722 | 60.102 | 0.030199 | 169.02 | 1146.8 | 977.78
16877 | 11.725 | 200.78 | 60.101 | 0.030205 | 169.03 | 1146.8 |  | 16877 | 200.78 | 11.725 | 60.101 | 0.030205 | 169.03 | 1146.8 | 977.77
16878 | 11.727 | 200.79 | 60.101 | 0.030211 | 169.04 | 1146.8 |  | 16878 | 200.79 | 11.727 | 60.101 | 0.030211 | 169.04 | 1146.8 | 977.76
16879 | 11.73 | 200.8 | 60.101 | 0.030217 | 169.05 | 1146.8 |  | 16879 | 200.8 | 11.73 | 60.101 | 0.030217 | 169.05 | 1146.8 | 977.75
16880 | 11.732 | 200.81 | 60.101 | 0.030222 | 169.06 | 1146.8 |  | 16880 | 200.81 | 11.732 | 60.101 | 0.030222 | 169.06 | 1146.8 | 977.74
16881 | 11.734 | 200.82 | 60.101 | 0.030228 | 169.07 | 1146.8 |  | 16881 | 200.82 | 11.734 | 60.101 | 0.030228 | 169.07 | 1146.8 | 977.73
16882 | 11.737 | 200.83 | 60.1 | 0.030234 | 169.08 | 1146.8 |  | 16882 | 200.83 | 11.737 | 60.1 | 0.030234 | 169.08 | 1146.8 | 977.72
16883 | 11.739 | 200.84 | 60.1 | 0.03024 | 169.09 | 1146.8 |  | 16883 | 200.84 | 11.739 | 60.1 | 0.03024 | 169.09 | 1146.8 | 977.71
16884 | 11.742 | 200.85 | 60.1 | 0.030246 | 169.1 | 1146.8 |  | 16884 | 200.85 | 11.742 | 60.1 | 0.030246 | 169.1 | 1146.8 | 977.7
16885 | 11.744 | 200.86 | 60.1 | 0.030252 | 169.11 | 1146.8 |  | 16885 | 200.86 | 11.744 | 60.1 | 0.030252 | 169.11 | 1146.8 | 977.69
16886 | 11.747 | 200.87 | 60.099 | 0.030257 | 169.12 | 1146.8 |  | 16886 | 200.87 | 11.747 | 60.099 | 0.030257 | 169.12 | 1146.8 | 977.68
16887 | 11.749 | 200.88 | 60.099 | 0.030263 | 169.13 | 1146.8 |  | 16887 | 200.88 | 11.749 | 60.099 | 0.030263 | 169.13 | 1146.8 | 977.67
16888 | 11.751 | 200.89 | 60.099 | 0.030269 | 169.14 | 1146.8 |  | 16888 | 200.89 | 11.751 | 60.099 | 0.030269 | 169.14 | 1146.8 | 977.66
16889 | 11.754 | 200.9 | 60.099 | 0.030275 | 169.15 | 1146.8 |  | 16889 | 200.9 | 11.754 | 60.099 | 0.030275 | 169.15 | 1146.8 | 977.65
16890 | 11.756 | 200.91 | 60.098 | 0.030281 | 169.16 | 1146.8 |  | 16890 | 200.91 | 11.756 | 60.098 | 0.030281 | 169.16 | 1146.8 | 977.64
16891 | 11.759 | 200.92 | 60.098 | 0.030287 | 169.17 | 1146.8 |  | 16891 | 200.92 | 11.759 | 60.098 | 0.030287 | 169.17 | 1146.8 | 977.63
16892 | 11.761 | 200.93 | 60.098 | 0.030292 | 169.18 | 1146.8 |  | 16892 | 200.93 | 11.761 | 60.098 | 0.030292 | 169.18 | 1146.8 | 977.62
16893 | 11.763 | 200.94 | 60.098 | 0.030298 | 169.19 | 1146.8 |  | 16893 | 200.94 | 11.763 | 60.098 | 0.030298 | 169.19 | 1146.8 | 977.61
16894 | 11.766 | 200.95 | 60.097 | 0.030304 | 169.2 | 1146.8 |  | 16894 | 200.95 | 11.766 | 60.097 | 0.030304 | 169.2 | 1146.8 | 977.6
16895 | 11.768 | 200.96 | 60.097 | 0.03031 | 169.21 | 1146.9 |  | 16895 | 200.96 | 11.768 | 60.097 | 0.03031 | 169.21 | 1146.9 | 977.69
16896 | 11.771 | 200.97 | 60.097 | 0.030316 | 169.22 | 1146.9 |  | 16896 | 200.97 | 11.771 | 60.097 | 0.030316 | 169.22 | 1146.9 | 977.68
16897 | 11.773 | 200.98 | 60.097 | 0.030322 | 169.23 | 1146.9 |  | 16897 | 200.98 | 11.773 | 60.097 | 0.030322 | 169.23 | 1146.9 | 977.67
16898 | 11.776 | 200.99 | 60.096 | 0.030327 | 169.24 | 1146.9 |  | 16898 | 200.99 | 11.776 | 60.096 | 0.030327 | 169.24 | 1146.9 | 977.66
16899 | 11.778 | 201 | 60.096 | 0.030333 | 169.25 | 1146.9 |  | 16899 | 201 | 11.778 | 60.096 | 0.030333 | 169.25 | 1146.9 | 977.65
16900 | 11.78 | 201.01 | 60.096 | 0.030339 | 169.26 | 1146.9 |  | 16900 | 201.01 | 11.78 | 60.096 | 0.030339 | 169.26 | 1146.9 | 977.64
16901 | 11.783 | 201.02 | 60.096 | 0.030345 | 169.27 | 1146.9 |  | 16901 | 201.02 | 11.783 | 60.096 | 0.030345 | 169.27 | 1146.9 | 977.63
16902 | 11.785 | 201.03 | 60.096 | 0.030351 | 169.28 | 1146.9 |  | 16902 | 201.03 | 11.785 | 60.096 | 0.030351 | 169.28 | 1146.9 | 977.62
16903 | 11.788 | 201.04 | 60.095 | 0.030357 | 169.29 | 1146.9 |  | 16903 | 201.04 | 11.788 | 60.095 | 0.030357 | 169.29 | 1146.9 | 977.61
16904 | 11.79 | 201.05 | 60.095 | 0.030363 | 169.3 | 1146.9 |  | 16904 | 201.05 | 11.79 | 60.095 | 0.030363 | 169.3 | 1146.9 | 977.6
16905 | 11.793 | 201.06 | 60.095 | 0.030368 | 169.31 | 1146.9 |  | 16905 | 201.06 | 11.793 | 60.095 | 0.030368 | 169.31 | 1146.9 | 977.59
16906 | 11.795 | 201.07 | 60.095 | 0.030374 | 169.32 | 1146.9 |  | 16906 | 201.07 | 11.795 | 60.095 | 0.030374 | 169.32 | 1146.9 | 977.58
16907 | 11.797 | 201.08 | 60.094 | 0.03038 | 169.33 | 1146.9 |  | 16907 | 201.08 | 11.797 | 60.094 | 0.03038 | 169.33 | 1146.9 | 977.57
16908 | 11.8 | 201.09 | 60.094 | 0.030386 | 169.34 | 1146.9 |  | 16908 | 201.09 | 11.8 | 60.094 | 0.030386 | 169.34 | 1146.9 | 977.56
16909 | 11.802 | 201.1 | 60.094 | 0.030392 | 169.35 | 1146.9 |  | 16909 | 201.1 | 11.802 | 60.094 | 0.030392 | 169.35 | 1146.9 | 977.55
16910 | 11.805 | 201.11 | 60.094 | 0.030398 | 169.36 | 1146.9 |  | 16910 | 201.11 | 11.805 | 60.094 | 0.030398 | 169.36 | 1146.9 | 977.54
16911 | 11.807 | 201.12 | 60.093 | 0.030404 | 169.37 | 1146.9 |  | 16911 | 201.12 | 11.807 | 60.093 | 0.030404 | 169.37 | 1146.9 | 977.53
16912 | 11.81 | 201.13 | 60.093 | 0.030409 | 169.38 | 1146.9 |  | 16912 | 201.13 | 11.81 | 60.093 | 0.030409 | 169.38 | 1146.9 | 977.52
16913 | 11.812 | 201.14 | 60.093 | 0.030415 | 169.39 | 1146.9 |  | 16913 | 201.14 | 11.812 | 60.093 | 0.030415 | 169.39 | 1146.9 | 977.51
16914 | 11.814 | 201.15 | 60.093 | 0.030421 | 169.4 | 1146.9 |  | 16914 | 201.15 | 11.814 | 60.093 | 0.030421 | 169.4 | 1146.9 | 977.5
16915 | 11.817 | 201.16 | 60.092 | 0.030427 | 169.41 | 1146.9 |  | 16915 | 201.16 | 11.817 | 60.092 | 0.030427 | 169.41 | 1146.9 | 977.49
16916 | 11.819 | 201.17 | 60.092 | 0.030433 | 169.42 | 1146.9 |  | 16916 | 201.17 | 11.819 | 60.092 | 0.030433 | 169.42 | 1146.9 | 977.48
16917 | 11.822 | 201.18 | 60.092 | 0.030439 | 169.43 | 1146.9 |  | 16917 | 201.18 | 11.822 | 60.092 | 0.030439 | 169.43 | 1146.9 | 977.47
16918 | 11.824 | 201.19 | 60.092 | 0.030445 | 169.44 | 1146.9 |  | 16918 | 201.19 | 11.824 | 60.092 | 0.030445 | 169.44 | 1146.9 | 977.46
16919 | 11.827 | 201.2 | 60.091 | 0.03045 | 169.45 | 1146.9 |  | 16919 | 201.2 | 11.827 | 60.091 | 0.03045 | 169.45 | 1146.9 | 977.45
16920 | 11.829 | 201.21 | 60.091 | 0.030456 | 169.46 | 1146.9 |  | 16920 | 201.21 | 11.829 | 60.091 | 0.030456 | 169.46 | 1146.9 | 977.44
16921 | 11.831 | 201.22 | 60.091 | 0.030462 | 169.47 | 1147 |  | 16921 | 201.22 | 11.831 | 60.091 | 0.030462 | 169.47 | 1147 | 977.53
16922 | 11.834 | 201.23 | 60.091 | 0.030468 | 169.48 | 1147 |  | 16922 | 201.23 | 11.834 | 60.091 | 0.030468 | 169.48 | 1147 | 977.52
16923 | 11.836 | 201.24 | 60.09 | 0.030474 | 169.49 | 1147 |  | 16923 | 201.24 | 11.836 | 60.09 | 0.030474 | 169.49 | 1147 | 977.51
16924 | 11.839 | 201.25 | 60.09 | 0.03048 | 169.5 | 1147 |  | 16924 | 201.25 | 11.839 | 60.09 | 0.03048 | 169.5 | 1147 | 977.5
16925 | 11.841 | 201.26 | 60.09 | 0.030486 | 169.51 | 1147 |  | 16925 | 201.26 | 11.841 | 60.09 | 0.030486 | 169.51 | 1147 | 977.49
16926 | 11.844 | 201.27 | 60.09 | 0.030491 | 169.52 | 1147 |  | 16926 | 201.27 | 11.844 | 60.09 | 0.030491 | 169.52 | 1147 | 977.48
16927 | 11.846 | 201.28 | 60.09 | 0.030497 | 169.53 | 1147 |  | 16927 | 201.28 | 11.846 | 60.09 | 0.030497 | 169.53 | 1147 | 977.47
16928 | 11.849 | 201.29 | 60.089 | 0.030503 | 169.54 | 1147 |  | 16928 | 201.29 | 11.849 | 60.089 | 0.030503 | 169.54 | 1147 | 977.46
16929 | 11.851 | 201.3 | 60.089 | 0.030509 | 169.55 | 1147 |  | 16929 | 201.3 | 11.851 | 60.089 | 0.030509 | 169.55 | 1147 | 977.45
16930 | 11.853 | 201.31 | 60.089 | 0.030515 | 169.56 | 1147 |  | 16930 | 201.31 | 11.853 | 60.089 | 0.030515 | 169.56 | 1147 | 977.44
16931 | 11.856 | 201.32 | 60.089 | 0.030521 | 169.57 | 1147 |  | 16931 | 201.32 | 11.856 | 60.089 | 0.030521 | 169.57 | 1147 | 977.43
16932 | 11.858 | 201.33 | 60.088 | 0.030527 | 169.58 | 1147 |  | 16932 | 201.33 | 11.858 | 60.088 | 0.030527 | 169.58 | 1147 | 977.42
16933 | 11.861 | 201.34 | 60.088 | 0.030533 | 169.59 | 1147 |  | 16933 | 201.34 | 11.861 | 60.088 | 0.030533 | 169.59 | 1147 | 977.41
16934 | 11.863 | 201.35 | 60.088 | 0.030538 | 169.6 | 1147 |  | 16934 | 201.35 | 11.863 | 60.088 | 0.030538 | 169.6 | 1147 | 977.4
16935 | 11.866 | 201.36 | 60.088 | 0.030544 | 169.61 | 1147 |  | 16935 | 201.36 | 11.866 | 60.088 | 0.030544 | 169.61 | 1147 | 977.39
16936 | 11.868 | 201.37 | 60.087 | 0.03055 | 169.62 | 1147 |  | 16936 | 201.37 | 11.868 | 60.087 | 0.03055 | 169.62 | 1147 | 977.38
16937 | 11.87 | 201.38 | 60.087 | 0.030556 | 169.63 | 1147 |  | 16937 | 201.38 | 11.87 | 60.087 | 0.030556 | 169.63 | 1147 | 977.37
16938 | 11.873 | 201.39 | 60.087 | 0.030562 | 169.64 | 1147 |  | 16938 | 201.39 | 11.873 | 60.087 | 0.030562 | 169.64 | 1147 | 977.36
16939 | 11.875 | 201.4 | 60.087 | 0.030568 | 169.65 | 1147 |  | 16939 | 201.4 | 11.875 | 60.087 | 0.030568 | 169.65 | 1147 | 977.35
16940 | 11.878 | 201.41 | 60.086 | 0.030574 | 169.66 | 1147 |  | 16940 | 201.41 | 11.878 | 60.086 | 0.030574 | 169.66 | 1147 | 977.34
16941 | 11.88 | 201.42 | 60.086 | 0.03058 | 169.67 | 1147 |  | 16941 | 201.42 | 11.88 | 60.086 | 0.03058 | 169.67 | 1147 | 977.33
16942 | 11.883 | 201.43 | 60.086 | 0.030585 | 169.68 | 1147 |  | 16942 | 201.43 | 11.883 | 60.086 | 0.030585 | 169.68 | 1147 | 977.32
16943 | 11.885 | 201.44 | 60.086 | 0.030591 | 169.69 | 1147 |  | 16943 | 201.44 | 11.885 | 60.086 | 0.030591 | 169.69 | 1147 | 977.31
16944 | 11.888 | 201.45 | 60.085 | 0.030597 | 169.7 | 1147 |  | 16944 | 201.45 | 11.888 | 60.085 | 0.030597 | 169.7 | 1147 | 977.3
16945 | 11.89 | 201.46 | 60.085 | 0.030603 | 169.71 | 1147 |  | 16945 | 201.46 | 11.89 | 60.085 | 0.030603 | 169.71 | 1147 | 977.29
16946 | 11.892 | 201.47 | 60.085 | 0.030609 | 169.72 | 1147 |  | 16946 | 201.47 | 11.892 | 60.085 | 0.030609 | 169.72 | 1147 | 977.28
16947 | 11.895 | 201.48 | 60.085 | 0.030615 | 169.73 | 1147.1 |  | 16947 | 201.48 | 11.895 | 60.085 | 0.030615 | 169.73 | 1147.1 | 977.37
16948 | 11.897 | 201.49 | 60.084 | 0.030621 | 169.74 | 1147.1 |  | 16948 | 201.49 | 11.897 | 60.084 | 0.030621 | 169.74 | 1147.1 | 977.36
16949 | 11.9 | 201.5 | 60.084 | 0.030627 | 169.75 | 1147.1 |  | 16949 | 201.5 | 11.9 | 60.084 | 0.030627 | 169.75 | 1147.1 | 977.35
16950 | 11.902 | 201.51 | 60.084 | 0.030632 | 169.76 | 1147.1 |  | 16950 | 201.51 | 11.902 | 60.084 | 0.030632 | 169.76 | 1147.1 | 977.34
16951 | 11.905 | 201.52 | 60.084 | 0.030638 | 169.77 | 1147.1 |  | 16951 | 201.52 | 11.905 | 60.084 | 0.030638 | 169.77 | 1147.1 | 977.33
16952 | 11.907 | 201.53 | 60.084 | 0.030644 | 169.78 | 1147.1 |  | 16952 | 201.53 | 11.907 | 60.084 | 0.030644 | 169.78 | 1147.1 | 977.32
16953 | 11.91 | 201.54 | 60.083 | 0.03065 | 169.79 | 1147.1 |  | 16953 | 201.54 | 11.91 | 60.083 | 0.03065 | 169.79 | 1147.1 | 977.31
16954 | 11.912 | 201.55 | 60.083 | 0.030656 | 169.8 | 1147.1 |  | 16954 | 201.55 | 11.912 | 60.083 | 0.030656 | 169.8 | 1147.1 | 977.3
16955 | 11.914 | 201.56 | 60.083 | 0.030662 | 169.81 | 1147.1 |  | 16955 | 201.56 | 11.914 | 60.083 | 0.030662 | 169.81 | 1147.1 | 977.29
16956 | 11.917 | 201.57 | 60.083 | 0.030668 | 169.82 | 1147.1 |  | 16956 | 201.57 | 11.917 | 60.083 | 0.030668 | 169.82 | 1147.1 | 977.28
16957 | 11.919 | 201.58 | 60.082 | 0.030674 | 169.83 | 1147.1 |  | 16957 | 201.58 | 11.919 | 60.082 | 0.030674 | 169.83 | 1147.1 | 977.27
16958 | 11.922 | 201.59 | 60.082 | 0.03068 | 169.84 | 1147.1 |  | 16958 | 201.59 | 11.922 | 60.082 | 0.03068 | 169.84 | 1147.1 | 977.26
16959 | 11.924 | 201.6 | 60.082 | 0.030686 | 169.85 | 1147.1 |  | 16959 | 201.6 | 11.924 | 60.082 | 0.030686 | 169.85 | 1147.1 | 977.25
16960 | 11.927 | 201.61 | 60.082 | 0.030691 | 169.86 | 1147.1 |  | 16960 | 201.61 | 11.927 | 60.082 | 0.030691 | 169.86 | 1147.1 | 977.24
16961 | 11.929 | 201.62 | 60.081 | 0.030697 | 169.87 | 1147.1 |  | 16961 | 201.62 | 11.929 | 60.081 | 0.030697 | 169.87 | 1147.1 | 977.23
16962 | 11.932 | 201.63 | 60.081 | 0.030703 | 169.88 | 1147.1 |  | 16962 | 201.63 | 11.932 | 60.081 | 0.030703 | 169.88 | 1147.1 | 977.22
16963 | 11.934 | 201.64 | 60.081 | 0.030709 | 169.89 | 1147.1 |  | 16963 | 201.64 | 11.934 | 60.081 | 0.030709 | 169.89 | 1147.1 | 977.21
16964 | 11.937 | 201.65 | 60.081 | 0.030715 | 169.9 | 1147.1 |  | 16964 | 201.65 | 11.937 | 60.081 | 0.030715 | 169.9 | 1147.1 | 977.2
16965 | 11.939 | 201.66 | 60.08 | 0.030721 | 169.91 | 1147.1 |  | 16965 | 201.66 | 11.939 | 60.08 | 0.030721 | 169.91 | 1147.1 | 977.19
16966 | 11.941 | 201.67 | 60.08 | 0.030727 | 169.92 | 1147.1 |  | 16966 | 201.67 | 11.941 | 60.08 | 0.030727 | 169.92 | 1147.1 | 977.18
16967 | 11.944 | 201.68 | 60.08 | 0.030733 | 169.93 | 1147.1 |  | 16967 | 201.68 | 11.944 | 60.08 | 0.030733 | 169.93 | 1147.1 | 977.17
16968 | 11.946 | 201.69 | 60.08 | 0.030739 | 169.94 | 1147.1 |  | 16968 | 201.69 | 11.946 | 60.08 | 0.030739 | 169.94 | 1147.1 | 977.16
16969 | 11.949 | 201.7 | 60.079 | 0.030745 | 169.95 | 1147.1 |  | 16969 | 201.7 | 11.949 | 60.079 | 0.030745 | 169.95 | 1147.1 | 977.15
16970 | 11.951 | 201.71 | 60.079 | 0.03075 | 169.96 | 1147.1 |  | 16970 | 201.71 | 11.951 | 60.079 | 0.03075 | 169.96 | 1147.1 | 977.14
16971 | 11.954 | 201.72 | 60.079 | 0.030756 | 169.97 | 1147.1 |  | 16971 | 201.72 | 11.954 | 60.079 | 0.030756 | 169.97 | 1147.1 | 977.13
16972 | 11.956 | 201.73 | 60.079 | 0.030762 | 169.98 | 1147.1 |  | 16972 | 201.73 | 11.956 | 60.079 | 0.030762 | 169.98 | 1147.1 | 977.12
16973 | 11.959 | 201.74 | 60.079 | 0.030768 | 169.99 | 1147.2 |  | 16973 | 201.74 | 11.959 | 60.079 | 0.030768 | 169.99 | 1147.2 | 977.21
16974 | 11.961 | 201.75 | 60.078 | 0.030774 | 170 | 1147.2 |  | 16974 | 201.75 | 11.961 | 60.078 | 0.030774 | 170 | 1147.2 | 977.2
16975 | 11.964 | 201.76 | 60.078 | 0.03078 | 170.01 | 1147.2 |  | 16975 | 201.76 | 11.964 | 60.078 | 0.03078 | 170.01 | 1147.2 | 977.19
16976 | 11.966 | 201.77 | 60.078 | 0.030786 | 170.02 | 1147.2 |  | 16976 | 201.77 | 11.966 | 60.078 | 0.030786 | 170.02 | 1147.2 | 977.18
16977 | 11.968 | 201.78 | 60.078 | 0.030792 | 170.03 | 1147.2 |  | 16977 | 201.78 | 11.968 | 60.078 | 0.030792 | 170.03 | 1147.2 | 977.17
16978 | 11.971 | 201.79 | 60.077 | 0.030798 | 170.04 | 1147.2 |  | 16978 | 201.79 | 11.971 | 60.077 | 0.030798 | 170.04 | 1147.2 | 977.16
16979 | 11.973 | 201.8 | 60.077 | 0.030804 | 170.05 | 1147.2 |  | 16979 | 201.8 | 11.973 | 60.077 | 0.030804 | 170.05 | 1147.2 | 977.15
16980 | 11.976 | 201.81 | 60.077 | 0.03081 | 170.06 | 1147.2 |  | 16980 | 201.81 | 11.976 | 60.077 | 0.03081 | 170.06 | 1147.2 | 977.14
16981 | 11.978 | 201.82 | 60.077 | 0.030816 | 170.07 | 1147.2 |  | 16981 | 201.82 | 11.978 | 60.077 | 0.030816 | 170.07 | 1147.2 | 977.13
16982 | 11.981 | 201.83 | 60.076 | 0.030821 | 170.08 | 1147.2 |  | 16982 | 201.83 | 11.981 | 60.076 | 0.030821 | 170.08 | 1147.2 | 977.12
16983 | 11.983 | 201.84 | 60.076 | 0.030827 | 170.09 | 1147.2 |  | 16983 | 201.84 | 11.983 | 60.076 | 0.030827 | 170.09 | 1147.2 | 977.11
16984 | 11.986 | 201.85 | 60.076 | 0.030833 | 170.1 | 1147.2 |  | 16984 | 201.85 | 11.986 | 60.076 | 0.030833 | 170.1 | 1147.2 | 977.1
16985 | 11.988 | 201.86 | 60.076 | 0.030839 | 170.11 | 1147.2 |  | 16985 | 201.86 | 11.988 | 60.076 | 0.030839 | 170.11 | 1147.2 | 977.09
16986 | 11.991 | 201.87 | 60.075 | 0.030845 | 170.12 | 1147.2 |  | 16986 | 201.87 | 11.991 | 60.075 | 0.030845 | 170.12 | 1147.2 | 977.08
16987 | 11.993 | 201.88 | 60.075 | 0.030851 | 170.13 | 1147.2 |  | 16987 | 201.88 | 11.993 | 60.075 | 0.030851 | 170.13 | 1147.2 | 977.07
16988 | 11.995 | 201.89 | 60.075 | 0.030857 | 170.14 | 1147.2 |  | 16988 | 201.89 | 11.995 | 60.075 | 0.030857 | 170.14 | 1147.2 | 977.06
16989 | 11.998 | 201.9 | 60.075 | 0.030863 | 170.15 | 1147.2 |  | 16989 | 201.9 | 11.998 | 60.075 | 0.030863 | 170.15 | 1147.2 | 977.05
16990 | 12 | 201.91 | 60.074 | 0.030869 | 170.16 | 1147.2 |  | 16990 | 201.91 | 12 | 60.074 | 0.030869 | 170.16 | 1147.2 | 977.04
16991 | 12.003 | 201.92 | 60.074 | 0.030875 | 170.17 | 1147.2 |  | 16991 | 201.92 | 12.003 | 60.074 | 0.030875 | 170.17 | 1147.2 | 977.03
16992 | 12.005 | 201.93 | 60.074 | 0.030881 | 170.18 | 1147.2 |  | 16992 | 201.93 | 12.005 | 60.074 | 0.030881 | 170.18 | 1147.2 | 977.02
16993 | 12.008 | 201.94 | 60.074 | 0.030887 | 170.19 | 1147.2 |  | 16993 | 201.94 | 12.008 | 60.074 | 0.030887 | 170.19 | 1147.2 | 977.01
16994 | 12.01 | 201.95 | 60.073 | 0.030893 | 170.2 | 1147.2 |  | 16994 | 201.95 | 12.01 | 60.073 | 0.030893 | 170.2 | 1147.2 | 977
16995 | 12.013 | 201.96 | 60.073 | 0.030898 | 170.21 | 1147.2 |  | 16995 | 201.96 | 12.013 | 60.073 | 0.030898 | 170.21 | 1147.2 | 976.99
16996 | 12.015 | 201.97 | 60.073 | 0.030904 | 170.23 | 1147.2 |  | 16996 | 201.97 | 12.015 | 60.073 | 0.030904 | 170.23 | 1147.2 | 976.97
16997 | 12.018 | 201.98 | 60.073 | 0.03091 | 170.24 | 1147.2 |  | 16997 | 201.98 | 12.018 | 60.073 | 0.03091 | 170.24 | 1147.2 | 976.96
16998 | 12.02 | 201.99 | 60.073 | 0.030916 | 170.25 | 1147.2 |  | 16998 | 201.99 | 12.02 | 60.073 | 0.030916 | 170.25 | 1147.2 | 976.95
16999 | 12.023 | 202 | 60.072 | 0.030922 | 170.26 | 1147.3 |  | 16999 | 202 | 12.023 | 60.072 | 0.030922 | 170.26 | 1147.3 | 977.04
17000 | 12.025 | 202.01 | 60.072 | 0.030928 | 170.27 | 1147.3 |  | 17000 | 202.01 | 12.025 | 60.072 | 0.030928 | 170.27 | 1147.3 | 977.03
17001 | 12.028 | 202.02 | 60.072 | 0.030934 | 170.28 | 1147.3 |  | 17001 | 202.02 | 12.028 | 60.072 | 0.030934 | 170.28 | 1147.3 | 977.02
17002 | 12.03 | 202.03 | 60.072 | 0.03094 | 170.29 | 1147.3 |  | 17002 | 202.03 | 12.03 | 60.072 | 0.03094 | 170.29 | 1147.3 | 977.01
17003 | 12.032 | 202.04 | 60.071 | 0.030946 | 170.3 | 1147.3 |  | 17003 | 202.04 | 12.032 | 60.071 | 0.030946 | 170.3 | 1147.3 | 977
17004 | 12.035 | 202.05 | 60.071 | 0.030952 | 170.31 | 1147.3 |  | 17004 | 202.05 | 12.035 | 60.071 | 0.030952 | 170.31 | 1147.3 | 976.99
17005 | 12.037 | 202.06 | 60.071 | 0.030958 | 170.32 | 1147.3 |  | 17005 | 202.06 | 12.037 | 60.071 | 0.030958 | 170.32 | 1147.3 | 976.98
17006 | 12.04 | 202.07 | 60.071 | 0.030964 | 170.33 | 1147.3 |  | 17006 | 202.07 | 12.04 | 60.071 | 0.030964 | 170.33 | 1147.3 | 976.97
17007 | 12.042 | 202.08 | 60.07 | 0.03097 | 170.34 | 1147.3 |  | 17007 | 202.08 | 12.042 | 60.07 | 0.03097 | 170.34 | 1147.3 | 976.96
17008 | 12.045 | 202.09 | 60.07 | 0.030976 | 170.35 | 1147.3 |  | 17008 | 202.09 | 12.045 | 60.07 | 0.030976 | 170.35 | 1147.3 | 976.95
17009 | 12.047 | 202.1 | 60.07 | 0.030982 | 170.36 | 1147.3 |  | 17009 | 202.1 | 12.047 | 60.07 | 0.030982 | 170.36 | 1147.3 | 976.94
17010 | 12.05 | 202.11 | 60.07 | 0.030988 | 170.37 | 1147.3 |  | 17010 | 202.11 | 12.05 | 60.07 | 0.030988 | 170.37 | 1147.3 | 976.93
17011 | 12.052 | 202.12 | 60.069 | 0.030993 | 170.38 | 1147.3 |  | 17011 | 202.12 | 12.052 | 60.069 | 0.030993 | 170.38 | 1147.3 | 976.92
17012 | 12.055 | 202.13 | 60.069 | 0.030999 | 170.39 | 1147.3 |  | 17012 | 202.13 | 12.055 | 60.069 | 0.030999 | 170.39 | 1147.3 | 976.91
17013 | 12.057 | 202.14 | 60.069 | 0.031005 | 170.4 | 1147.3 |  | 17013 | 202.14 | 12.057 | 60.069 | 0.031005 | 170.4 | 1147.3 | 976.9
17014 | 12.06 | 202.15 | 60.069 | 0.031011 | 170.41 | 1147.3 |  | 17014 | 202.15 | 12.06 | 60.069 | 0.031011 | 170.41 | 1147.3 | 976.89
17015 | 12.062 | 202.16 | 60.068 | 0.031017 | 170.42 | 1147.3 |  | 17015 | 202.16 | 12.062 | 60.068 | 0.031017 | 170.42 | 1147.3 | 976.88
17016 | 12.065 | 202.17 | 60.068 | 0.031023 | 170.43 | 1147.3 |  | 17016 | 202.17 | 12.065 | 60.068 | 0.031023 | 170.43 | 1147.3 | 976.87
17017 | 12.067 | 202.18 | 60.068 | 0.031029 | 170.44 | 1147.3 |  | 17017 | 202.18 | 12.067 | 60.068 | 0.031029 | 170.44 | 1147.3 | 976.86
17018 | 12.07 | 202.19 | 60.068 | 0.031035 | 170.45 | 1147.3 |  | 17018 | 202.19 | 12.07 | 60.068 | 0.031035 | 170.45 | 1147.3 | 976.85
17019 | 12.072 | 202.2 | 60.067 | 0.031041 | 170.46 | 1147.3 |  | 17019 | 202.2 | 12.072 | 60.067 | 0.031041 | 170.46 | 1147.3 | 976.84
17020 | 12.075 | 202.21 | 60.067 | 0.031047 | 170.47 | 1147.3 |  | 17020 | 202.21 | 12.075 | 60.067 | 0.031047 | 170.47 | 1147.3 | 976.83
17021 | 12.077 | 202.22 | 60.067 | 0.031053 | 170.48 | 1147.3 |  | 17021 | 202.22 | 12.077 | 60.067 | 0.031053 | 170.48 | 1147.3 | 976.82
17022 | 12.079 | 202.23 | 60.067 | 0.031059 | 170.49 | 1147.3 |  | 17022 | 202.23 | 12.079 | 60.067 | 0.031059 | 170.49 | 1147.3 | 976.81
17023 | 12.082 | 202.24 | 60.067 | 0.031065 | 170.5 | 1147.3 |  | 17023 | 202.24 | 12.082 | 60.067 | 0.031065 | 170.5 | 1147.3 | 976.8
17024 | 12.084 | 202.25 | 60.066 | 0.031071 | 170.51 | 1147.3 |  | 17024 | 202.25 | 12.084 | 60.066 | 0.031071 | 170.51 | 1147.3 | 976.79
17025 | 12.087 | 202.26 | 60.066 | 0.031077 | 170.52 | 1147.4 |  | 17025 | 202.26 | 12.087 | 60.066 | 0.031077 | 170.52 | 1147.4 | 976.88
17026 | 12.089 | 202.27 | 60.066 | 0.031083 | 170.53 | 1147.4 |  | 17026 | 202.27 | 12.089 | 60.066 | 0.031083 | 170.53 | 1147.4 | 976.87
17027 | 12.092 | 202.28 | 60.066 | 0.031089 | 170.54 | 1147.4 |  | 17027 | 202.28 | 12.092 | 60.066 | 0.031089 | 170.54 | 1147.4 | 976.86
17028 | 12.094 | 202.29 | 60.065 | 0.031095 | 170.55 | 1147.4 |  | 17028 | 202.29 | 12.094 | 60.065 | 0.031095 | 170.55 | 1147.4 | 976.85
17029 | 12.097 | 202.3 | 60.065 | 0.031101 | 170.56 | 1147.4 |  | 17029 | 202.3 | 12.097 | 60.065 | 0.031101 | 170.56 | 1147.4 | 976.84
17030 | 12.099 | 202.31 | 60.065 | 0.031107 | 170.57 | 1147.4 |  | 17030 | 202.31 | 12.099 | 60.065 | 0.031107 | 170.57 | 1147.4 | 976.83
17031 | 12.102 | 202.32 | 60.065 | 0.031113 | 170.58 | 1147.4 |  | 17031 | 202.32 | 12.102 | 60.065 | 0.031113 | 170.58 | 1147.4 | 976.82
17032 | 12.104 | 202.33 | 60.064 | 0.031119 | 170.59 | 1147.4 |  | 17032 | 202.33 | 12.104 | 60.064 | 0.031119 | 170.59 | 1147.4 | 976.81
17033 | 12.107 | 202.34 | 60.064 | 0.031125 | 170.6 | 1147.4 |  | 17033 | 202.34 | 12.107 | 60.064 | 0.031125 | 170.6 | 1147.4 | 976.8
17034 | 12.109 | 202.35 | 60.064 | 0.031131 | 170.61 | 1147.4 |  | 17034 | 202.35 | 12.109 | 60.064 | 0.031131 | 170.61 | 1147.4 | 976.79
17035 | 12.112 | 202.36 | 60.064 | 0.031136 | 170.62 | 1147.4 |  | 17035 | 202.36 | 12.112 | 60.064 | 0.031136 | 170.62 | 1147.4 | 976.78
17036 | 12.114 | 202.37 | 60.063 | 0.031142 | 170.63 | 1147.4 |  | 17036 | 202.37 | 12.114 | 60.063 | 0.031142 | 170.63 | 1147.4 | 976.77
17037 | 12.117 | 202.38 | 60.063 | 0.031148 | 170.64 | 1147.4 |  | 17037 | 202.38 | 12.117 | 60.063 | 0.031148 | 170.64 | 1147.4 | 976.76
17038 | 12.119 | 202.39 | 60.063 | 0.031154 | 170.65 | 1147.4 |  | 17038 | 202.39 | 12.119 | 60.063 | 0.031154 | 170.65 | 1147.4 | 976.75
17039 | 12.122 | 202.4 | 60.063 | 0.03116 | 170.66 | 1147.4 |  | 17039 | 202.4 | 12.122 | 60.063 | 0.03116 | 170.66 | 1147.4 | 976.74
17040 | 12.124 | 202.41 | 60.062 | 0.031166 | 170.67 | 1147.4 |  | 17040 | 202.41 | 12.124 | 60.062 | 0.031166 | 170.67 | 1147.4 | 976.73
17041 | 12.127 | 202.42 | 60.062 | 0.031172 | 170.68 | 1147.4 |  | 17041 | 202.42 | 12.127 | 60.062 | 0.031172 | 170.68 | 1147.4 | 976.72
17042 | 12.129 | 202.43 | 60.062 | 0.031178 | 170.69 | 1147.4 |  | 17042 | 202.43 | 12.129 | 60.062 | 0.031178 | 170.69 | 1147.4 | 976.71
17043 | 12.132 | 202.44 | 60.062 | 0.031184 | 170.7 | 1147.4 |  | 17043 | 202.44 | 12.132 | 60.062 | 0.031184 | 170.7 | 1147.4 | 976.7
17044 | 12.134 | 202.45 | 60.061 | 0.03119 | 170.71 | 1147.4 |  | 17044 | 202.45 | 12.134 | 60.061 | 0.03119 | 170.71 | 1147.4 | 976.69
17045 | 12.137 | 202.46 | 60.061 | 0.031196 | 170.72 | 1147.4 |  | 17045 | 202.46 | 12.137 | 60.061 | 0.031196 | 170.72 | 1147.4 | 976.68
17046 | 12.139 | 202.47 | 60.061 | 0.031202 | 170.73 | 1147.4 |  | 17046 | 202.47 | 12.139 | 60.061 | 0.031202 | 170.73 | 1147.4 | 976.67
17047 | 12.142 | 202.48 | 60.061 | 0.031208 | 170.74 | 1147.4 |  | 17047 | 202.48 | 12.142 | 60.061 | 0.031208 | 170.74 | 1147.4 | 976.66
17048 | 12.144 | 202.49 | 60.06 | 0.031214 | 170.75 | 1147.4 |  | 17048 | 202.49 | 12.144 | 60.06 | 0.031214 | 170.75 | 1147.4 | 976.65
17049 | 12.146 | 202.5 | 60.06 | 0.03122 | 170.76 | 1147.4 |  | 17049 | 202.5 | 12.146 | 60.06 | 0.03122 | 170.76 | 1147.4 | 976.64
17050 | 12.149 | 202.51 | 60.06 | 0.031226 | 170.77 | 1147.4 |  | 17050 | 202.51 | 12.149 | 60.06 | 0.031226 | 170.77 | 1147.4 | 976.63
17051 | 12.151 | 202.52 | 60.06 | 0.031232 | 170.78 | 1147.5 |  | 17051 | 202.52 | 12.151 | 60.06 | 0.031232 | 170.78 | 1147.5 | 976.72
17052 | 12.154 | 202.53 | 60.06 | 0.031238 | 170.79 | 1147.5 |  | 17052 | 202.53 | 12.154 | 60.06 | 0.031238 | 170.79 | 1147.5 | 976.71
17053 | 12.156 | 202.54 | 60.059 | 0.031244 | 170.8 | 1147.5 |  | 17053 | 202.54 | 12.156 | 60.059 | 0.031244 | 170.8 | 1147.5 | 976.7
17054 | 12.159 | 202.55 | 60.059 | 0.03125 | 170.81 | 1147.5 |  | 17054 | 202.55 | 12.159 | 60.059 | 0.03125 | 170.81 | 1147.5 | 976.69
17055 | 12.161 | 202.56 | 60.059 | 0.031256 | 170.82 | 1147.5 |  | 17055 | 202.56 | 12.161 | 60.059 | 0.031256 | 170.82 | 1147.5 | 976.68
17056 | 12.164 | 202.57 | 60.059 | 0.031262 | 170.83 | 1147.5 |  | 17056 | 202.57 | 12.164 | 60.059 | 0.031262 | 170.83 | 1147.5 | 976.67
17057 | 12.166 | 202.58 | 60.058 | 0.031268 | 170.84 | 1147.5 |  | 17057 | 202.58 | 12.166 | 60.058 | 0.031268 | 170.84 | 1147.5 | 976.66
17058 | 12.169 | 202.59 | 60.058 | 0.031274 | 170.85 | 1147.5 |  | 17058 | 202.59 | 12.169 | 60.058 | 0.031274 | 170.85 | 1147.5 | 976.65
17059 | 12.171 | 202.6 | 60.058 | 0.03128 | 170.86 | 1147.5 |  | 17059 | 202.6 | 12.171 | 60.058 | 0.03128 | 170.86 | 1147.5 | 976.64
17060 | 12.174 | 202.61 | 60.058 | 0.031286 | 170.87 | 1147.5 |  | 17060 | 202.61 | 12.174 | 60.058 | 0.031286 | 170.87 | 1147.5 | 976.63
17061 | 12.176 | 202.62 | 60.057 | 0.031292 | 170.88 | 1147.5 |  | 17061 | 202.62 | 12.176 | 60.057 | 0.031292 | 170.88 | 1147.5 | 976.62
17062 | 12.179 | 202.63 | 60.057 | 0.031298 | 170.89 | 1147.5 |  | 17062 | 202.63 | 12.179 | 60.057 | 0.031298 | 170.89 | 1147.5 | 976.61
17063 | 12.181 | 202.64 | 60.057 | 0.031304 | 170.9 | 1147.5 |  | 17063 | 202.64 | 12.181 | 60.057 | 0.031304 | 170.9 | 1147.5 | 976.6
17064 | 12.184 | 202.65 | 60.057 | 0.03131 | 170.91 | 1147.5 |  | 17064 | 202.65 | 12.184 | 60.057 | 0.03131 | 170.91 | 1147.5 | 976.59
17065 | 12.186 | 202.66 | 60.056 | 0.031316 | 170.92 | 1147.5 |  | 17065 | 202.66 | 12.186 | 60.056 | 0.031316 | 170.92 | 1147.5 | 976.58
17066 | 12.189 | 202.67 | 60.056 | 0.031322 | 170.93 | 1147.5 |  | 17066 | 202.67 | 12.189 | 60.056 | 0.031322 | 170.93 | 1147.5 | 976.57
17067 | 12.191 | 202.68 | 60.056 | 0.031328 | 170.94 | 1147.5 |  | 17067 | 202.68 | 12.191 | 60.056 | 0.031328 | 170.94 | 1147.5 | 976.56
17068 | 12.194 | 202.69 | 60.056 | 0.031334 | 170.95 | 1147.5 |  | 17068 | 202.69 | 12.194 | 60.056 | 0.031334 | 170.95 | 1147.5 | 976.55
17069 | 12.196 | 202.7 | 60.055 | 0.03134 | 170.96 | 1147.5 |  | 17069 | 202.7 | 12.196 | 60.055 | 0.03134 | 170.96 | 1147.5 | 976.54
17070 | 12.199 | 202.71 | 60.055 | 0.031346 | 170.97 | 1147.5 |  | 17070 | 202.71 | 12.199 | 60.055 | 0.031346 | 170.97 | 1147.5 | 976.53
17071 | 12.201 | 202.72 | 60.055 | 0.031352 | 170.98 | 1147.5 |  | 17071 | 202.72 | 12.201 | 60.055 | 0.031352 | 170.98 | 1147.5 | 976.52
17072 | 12.204 | 202.73 | 60.055 | 0.031358 | 170.99 | 1147.5 |  | 17072 | 202.73 | 12.204 | 60.055 | 0.031358 | 170.99 | 1147.5 | 976.51
17073 | 12.206 | 202.74 | 60.054 | 0.031364 | 171 | 1147.5 |  | 17073 | 202.74 | 12.206 | 60.054 | 0.031364 | 171 | 1147.5 | 976.5
17074 | 12.209 | 202.75 | 60.054 | 0.03137 | 171.01 | 1147.5 |  | 17074 | 202.75 | 12.209 | 60.054 | 0.03137 | 171.01 | 1147.5 | 976.49
17075 | 12.211 | 202.76 | 60.054 | 0.031376 | 171.02 | 1147.5 |  | 17075 | 202.76 | 12.211 | 60.054 | 0.031376 | 171.02 | 1147.5 | 976.48
17076 | 12.214 | 202.77 | 60.054 | 0.031382 | 171.03 | 1147.5 |  | 17076 | 202.77 | 12.214 | 60.054 | 0.031382 | 171.03 | 1147.5 | 976.47
17077 | 12.216 | 202.78 | 60.054 | 0.031388 | 171.04 | 1147.6 |  | 17077 | 202.78 | 12.216 | 60.054 | 0.031388 | 171.04 | 1147.6 | 976.56
17078 | 12.219 | 202.79 | 60.053 | 0.031394 | 171.05 | 1147.6 |  | 17078 | 202.79 | 12.219 | 60.053 | 0.031394 | 171.05 | 1147.6 | 976.55
17079 | 12.221 | 202.8 | 60.053 | 0.0314 | 171.06 | 1147.6 |  | 17079 | 202.8 | 12.221 | 60.053 | 0.0314 | 171.06 | 1147.6 | 976.54
17080 | 12.224 | 202.81 | 60.053 | 0.031406 | 171.07 | 1147.6 |  | 17080 | 202.81 | 12.224 | 60.053 | 0.031406 | 171.07 | 1147.6 | 976.53
17081 | 12.226 | 202.82 | 60.053 | 0.031412 | 171.08 | 1147.6 |  | 17081 | 202.82 | 12.226 | 60.053 | 0.031412 | 171.08 | 1147.6 | 976.52
17082 | 12.229 | 202.83 | 60.052 | 0.031418 | 171.09 | 1147.6 |  | 17082 | 202.83 | 12.229 | 60.052 | 0.031418 | 171.09 | 1147.6 | 976.51
17083 | 12.231 | 202.84 | 60.052 | 0.031424 | 171.1 | 1147.6 |  | 17083 | 202.84 | 12.231 | 60.052 | 0.031424 | 171.1 | 1147.6 | 976.5
17084 | 12.234 | 202.85 | 60.052 | 0.03143 | 171.11 | 1147.6 |  | 17084 | 202.85 | 12.234 | 60.052 | 0.03143 | 171.11 | 1147.6 | 976.49
17085 | 12.236 | 202.86 | 60.052 | 0.031436 | 171.12 | 1147.6 |  | 17085 | 202.86 | 12.236 | 60.052 | 0.031436 | 171.12 | 1147.6 | 976.48
17086 | 12.239 | 202.87 | 60.051 | 0.031442 | 171.13 | 1147.6 |  | 17086 | 202.87 | 12.239 | 60.051 | 0.031442 | 171.13 | 1147.6 | 976.47
17087 | 12.241 | 202.88 | 60.051 | 0.031448 | 171.14 | 1147.6 |  | 17087 | 202.88 | 12.241 | 60.051 | 0.031448 | 171.14 | 1147.6 | 976.46
17088 | 12.244 | 202.89 | 60.051 | 0.031454 | 171.15 | 1147.6 |  | 17088 | 202.89 | 12.244 | 60.051 | 0.031454 | 171.15 | 1147.6 | 976.45
17089 | 12.246 | 202.9 | 60.051 | 0.03146 | 171.16 | 1147.6 |  | 17089 | 202.9 | 12.246 | 60.051 | 0.03146 | 171.16 | 1147.6 | 976.44
17090 | 12.249 | 202.91 | 60.05 | 0.031466 | 171.17 | 1147.6 |  | 17090 | 202.91 | 12.249 | 60.05 | 0.031466 | 171.17 | 1147.6 | 976.43
17091 | 12.251 | 202.92 | 60.05 | 0.031472 | 171.18 | 1147.6 |  | 17091 | 202.92 | 12.251 | 60.05 | 0.031472 | 171.18 | 1147.6 | 976.42
17092 | 12.254 | 202.93 | 60.05 | 0.031478 | 171.19 | 1147.6 |  | 17092 | 202.93 | 12.254 | 60.05 | 0.031478 | 171.19 | 1147.6 | 976.41
17093 | 12.256 | 202.94 | 60.05 | 0.031484 | 171.2 | 1147.6 |  | 17093 | 202.94 | 12.256 | 60.05 | 0.031484 | 171.2 | 1147.6 | 976.4
17094 | 12.259 | 202.95 | 60.049 | 0.03149 | 171.21 | 1147.6 |  | 17094 | 202.95 | 12.259 | 60.049 | 0.03149 | 171.21 | 1147.6 | 976.39
17095 | 12.261 | 202.96 | 60.049 | 0.031496 | 171.22 | 1147.6 |  | 17095 | 202.96 | 12.261 | 60.049 | 0.031496 | 171.22 | 1147.6 | 976.38
17096 | 12.264 | 202.97 | 60.049 | 0.031502 | 171.23 | 1147.6 |  | 17096 | 202.97 | 12.264 | 60.049 | 0.031502 | 171.23 | 1147.6 | 976.37
17097 | 12.266 | 202.98 | 60.049 | 0.031508 | 171.24 | 1147.6 |  | 17097 | 202.98 | 12.266 | 60.049 | 0.031508 | 171.24 | 1147.6 | 976.36
17098 | 12.269 | 202.99 | 60.048 | 0.031514 | 171.25 | 1147.6 |  | 17098 | 202.99 | 12.269 | 60.048 | 0.031514 | 171.25 | 1147.6 | 976.35
17099 | 12.271 | 203 | 60.048 | 0.03152 | 171.26 | 1147.6 |  | 17099 | 203 | 12.271 | 60.048 | 0.03152 | 171.26 | 1147.6 | 976.34
17100 | 12.274 | 203.01 | 60.048 | 0.031526 | 171.27 | 1147.6 |  | 17100 | 203.01 | 12.274 | 60.048 | 0.031526 | 171.27 | 1147.6 | 976.33
17101 | 12.276 | 203.02 | 60.048 | 0.031532 | 171.28 | 1147.6 |  | 17101 | 203.02 | 12.276 | 60.048 | 0.031532 | 171.28 | 1147.6 | 976.32
17102 | 12.279 | 203.03 | 60.047 | 0.031539 | 171.29 | 1147.6 |  | 17102 | 203.03 | 12.279 | 60.047 | 0.031539 | 171.29 | 1147.6 | 976.31
17103 | 12.281 | 203.04 | 60.047 | 0.031545 | 171.3 | 1147.7 |  | 17103 | 203.04 | 12.281 | 60.047 | 0.031545 | 171.3 | 1147.7 | 976.4
17104 | 12.284 | 203.05 | 60.047 | 0.031551 | 171.31 | 1147.7 |  | 17104 | 203.05 | 12.284 | 60.047 | 0.031551 | 171.31 | 1147.7 | 976.39
17105 | 12.286 | 203.06 | 60.047 | 0.031557 | 171.32 | 1147.7 |  | 17105 | 203.06 | 12.286 | 60.047 | 0.031557 | 171.32 | 1147.7 | 976.38
17106 | 12.289 | 203.07 | 60.047 | 0.031563 | 171.33 | 1147.7 |  | 17106 | 203.07 | 12.289 | 60.047 | 0.031563 | 171.33 | 1147.7 | 976.37
17107 | 12.292 | 203.08 | 60.046 | 0.031569 | 171.34 | 1147.7 |  | 17107 | 203.08 | 12.292 | 60.046 | 0.031569 | 171.34 | 1147.7 | 976.36
17108 | 12.294 | 203.09 | 60.046 | 0.031575 | 171.35 | 1147.7 |  | 17108 | 203.09 | 12.294 | 60.046 | 0.031575 | 171.35 | 1147.7 | 976.35
17109 | 12.297 | 203.1 | 60.046 | 0.031581 | 171.36 | 1147.7 |  | 17109 | 203.1 | 12.297 | 60.046 | 0.031581 | 171.36 | 1147.7 | 976.34
17110 | 12.299 | 203.11 | 60.046 | 0.031587 | 171.37 | 1147.7 |  | 17110 | 203.11 | 12.299 | 60.046 | 0.031587 | 171.37 | 1147.7 | 976.33
17111 | 12.302 | 203.12 | 60.045 | 0.031593 | 171.38 | 1147.7 |  | 17111 | 203.12 | 12.302 | 60.045 | 0.031593 | 171.38 | 1147.7 | 976.32
17112 | 12.304 | 203.13 | 60.045 | 0.031599 | 171.39 | 1147.7 |  | 17112 | 203.13 | 12.304 | 60.045 | 0.031599 | 171.39 | 1147.7 | 976.31
17113 | 12.307 | 203.14 | 60.045 | 0.031605 | 171.4 | 1147.7 |  | 17113 | 203.14 | 12.307 | 60.045 | 0.031605 | 171.4 | 1147.7 | 976.3
17114 | 12.309 | 203.15 | 60.045 | 0.031611 | 171.41 | 1147.7 |  | 17114 | 203.15 | 12.309 | 60.045 | 0.031611 | 171.41 | 1147.7 | 976.29
17115 | 12.312 | 203.16 | 60.044 | 0.031617 | 171.42 | 1147.7 |  | 17115 | 203.16 | 12.312 | 60.044 | 0.031617 | 171.42 | 1147.7 | 976.28
17116 | 12.314 | 203.17 | 60.044 | 0.031623 | 171.43 | 1147.7 |  | 17116 | 203.17 | 12.314 | 60.044 | 0.031623 | 171.43 | 1147.7 | 976.27
17117 | 12.317 | 203.18 | 60.044 | 0.031629 | 171.44 | 1147.7 |  | 17117 | 203.18 | 12.317 | 60.044 | 0.031629 | 171.44 | 1147.7 | 976.26
17118 | 12.319 | 203.19 | 60.044 | 0.031635 | 171.45 | 1147.7 |  | 17118 | 203.19 | 12.319 | 60.044 | 0.031635 | 171.45 | 1147.7 | 976.25
17119 | 12.322 | 203.2 | 60.043 | 0.031641 | 171.46 | 1147.7 |  | 17119 | 203.2 | 12.322 | 60.043 | 0.031641 | 171.46 | 1147.7 | 976.24
17120 | 12.324 | 203.21 | 60.043 | 0.031647 | 171.47 | 1147.7 |  | 17120 | 203.21 | 12.324 | 60.043 | 0.031647 | 171.47 | 1147.7 | 976.23
17121 | 12.327 | 203.22 | 60.043 | 0.031653 | 171.48 | 1147.7 |  | 17121 | 203.22 | 12.327 | 60.043 | 0.031653 | 171.48 | 1147.7 | 976.22
17122 | 12.329 | 203.23 | 60.043 | 0.031659 | 171.49 | 1147.7 |  | 17122 | 203.23 | 12.329 | 60.043 | 0.031659 | 171.49 | 1147.7 | 976.21
17123 | 12.332 | 203.24 | 60.042 | 0.031665 | 171.5 | 1147.7 |  | 17123 | 203.24 | 12.332 | 60.042 | 0.031665 | 171.5 | 1147.7 | 976.2
17124 | 12.334 | 203.25 | 60.042 | 0.031671 | 171.51 | 1147.7 |  | 17124 | 203.25 | 12.334 | 60.042 | 0.031671 | 171.51 | 1147.7 | 976.19
17125 | 12.337 | 203.26 | 60.042 | 0.031677 | 171.52 | 1147.7 |  | 17125 | 203.26 | 12.337 | 60.042 | 0.031677 | 171.52 | 1147.7 | 976.18
17126 | 12.339 | 203.27 | 60.042 | 0.031684 | 171.53 | 1147.7 |  | 17126 | 203.27 | 12.339 | 60.042 | 0.031684 | 171.53 | 1147.7 | 976.17
17127 | 12.342 | 203.28 | 60.041 | 0.03169 | 171.54 | 1147.7 |  | 17127 | 203.28 | 12.342 | 60.041 | 0.03169 | 171.54 | 1147.7 | 976.16
17128 | 12.344 | 203.29 | 60.041 | 0.031696 | 171.55 | 1147.7 |  | 17128 | 203.29 | 12.344 | 60.041 | 0.031696 | 171.55 | 1147.7 | 976.15
17129 | 12.347 | 203.3 | 60.041 | 0.031702 | 171.56 | 1147.7 |  | 17129 | 203.3 | 12.347 | 60.041 | 0.031702 | 171.56 | 1147.7 | 976.14
17130 | 12.349 | 203.31 | 60.041 | 0.031708 | 171.57 | 1147.8 |  | 17130 | 203.31 | 12.349 | 60.041 | 0.031708 | 171.57 | 1147.8 | 976.23
17131 | 12.352 | 203.32 | 60.041 | 0.031714 | 171.58 | 1147.8 |  | 17131 | 203.32 | 12.352 | 60.041 | 0.031714 | 171.58 | 1147.8 | 976.22
17132 | 12.354 | 203.33 | 60.04 | 0.03172 | 171.59 | 1147.8 |  | 17132 | 203.33 | 12.354 | 60.04 | 0.03172 | 171.59 | 1147.8 | 976.21
17133 | 12.357 | 203.34 | 60.04 | 0.031726 | 171.6 | 1147.8 |  | 17133 | 203.34 | 12.357 | 60.04 | 0.031726 | 171.6 | 1147.8 | 976.2
17134 | 12.36 | 203.35 | 60.04 | 0.031732 | 171.61 | 1147.8 |  | 17134 | 203.35 | 12.36 | 60.04 | 0.031732 | 171.61 | 1147.8 | 976.19
17135 | 12.362 | 203.36 | 60.04 | 0.031738 | 171.62 | 1147.8 |  | 17135 | 203.36 | 12.362 | 60.04 | 0.031738 | 171.62 | 1147.8 | 976.18
17136 | 12.365 | 203.37 | 60.039 | 0.031744 | 171.63 | 1147.8 |  | 17136 | 203.37 | 12.365 | 60.039 | 0.031744 | 171.63 | 1147.8 | 976.17
17137 | 12.367 | 203.38 | 60.039 | 0.03175 | 171.64 | 1147.8 |  | 17137 | 203.38 | 12.367 | 60.039 | 0.03175 | 171.64 | 1147.8 | 976.16
17138 | 12.37 | 203.39 | 60.039 | 0.031756 | 171.65 | 1147.8 |  | 17138 | 203.39 | 12.37 | 60.039 | 0.031756 | 171.65 | 1147.8 | 976.15
17139 | 12.372 | 203.4 | 60.039 | 0.031762 | 171.66 | 1147.8 |  | 17139 | 203.4 | 12.372 | 60.039 | 0.031762 | 171.66 | 1147.8 | 976.14
17140 | 12.375 | 203.41 | 60.038 | 0.031768 | 171.67 | 1147.8 |  | 17140 | 203.41 | 12.375 | 60.038 | 0.031768 | 171.67 | 1147.8 | 976.13
17141 | 12.377 | 203.42 | 60.038 | 0.031774 | 171.68 | 1147.8 |  | 17141 | 203.42 | 12.377 | 60.038 | 0.031774 | 171.68 | 1147.8 | 976.12
17142 | 12.38 | 203.43 | 60.038 | 0.031781 | 171.69 | 1147.8 |  | 17142 | 203.43 | 12.38 | 60.038 | 0.031781 | 171.69 | 1147.8 | 976.11
17143 | 12.382 | 203.44 | 60.038 | 0.031787 | 171.71 | 1147.8 |  | 17143 | 203.44 | 12.382 | 60.038 | 0.031787 | 171.71 | 1147.8 | 976.09
17144 | 12.385 | 203.45 | 60.037 | 0.031793 | 171.72 | 1147.8 |  | 17144 | 203.45 | 12.385 | 60.037 | 0.031793 | 171.72 | 1147.8 | 976.08
17145 | 12.387 | 203.46 | 60.037 | 0.031799 | 171.73 | 1147.8 |  | 17145 | 203.46 | 12.387 | 60.037 | 0.031799 | 171.73 | 1147.8 | 976.07
17146 | 12.39 | 203.47 | 60.037 | 0.031805 | 171.74 | 1147.8 |  | 17146 | 203.47 | 12.39 | 60.037 | 0.031805 | 171.74 | 1147.8 | 976.06
17147 | 12.392 | 203.48 | 60.037 | 0.031811 | 171.75 | 1147.8 |  | 17147 | 203.48 | 12.392 | 60.037 | 0.031811 | 171.75 | 1147.8 | 976.05
17148 | 12.395 | 203.49 | 60.036 | 0.031817 | 171.76 | 1147.8 |  | 17148 | 203.49 | 12.395 | 60.036 | 0.031817 | 171.76 | 1147.8 | 976.04
17149 | 12.397 | 203.5 | 60.036 | 0.031823 | 171.77 | 1147.8 |  | 17149 | 203.5 | 12.397 | 60.036 | 0.031823 | 171.77 | 1147.8 | 976.03
17150 | 12.4 | 203.51 | 60.036 | 0.031829 | 171.78 | 1147.8 |  | 17150 | 203.51 | 12.4 | 60.036 | 0.031829 | 171.78 | 1147.8 | 976.02
17151 | 12.402 | 203.52 | 60.036 | 0.031835 | 171.79 | 1147.8 |  | 17151 | 203.52 | 12.402 | 60.036 | 0.031835 | 171.79 | 1147.8 | 976.01
17152 | 12.405 | 203.53 | 60.035 | 0.031841 | 171.8 | 1147.8 |  | 17152 | 203.53 | 12.405 | 60.035 | 0.031841 | 171.8 | 1147.8 | 976
17153 | 12.408 | 203.54 | 60.035 | 0.031847 | 171.81 | 1147.8 |  | 17153 | 203.54 | 12.408 | 60.035 | 0.031847 | 171.81 | 1147.8 | 975.99
17154 | 12.41 | 203.55 | 60.035 | 0.031853 | 171.82 | 1147.8 |  | 17154 | 203.55 | 12.41 | 60.035 | 0.031853 | 171.82 | 1147.8 | 975.98
17155 | 12.413 | 203.56 | 60.035 | 0.03186 | 171.83 | 1147.8 |  | 17155 | 203.56 | 12.413 | 60.035 | 0.03186 | 171.83 | 1147.8 | 975.97
17156 | 12.415 | 203.57 | 60.034 | 0.031866 | 171.84 | 1147.9 |  | 17156 | 203.57 | 12.415 | 60.034 | 0.031866 | 171.84 | 1147.9 | 976.06
17157 | 12.418 | 203.58 | 60.034 | 0.031872 | 171.85 | 1147.9 |  | 17157 | 203.58 | 12.418 | 60.034 | 0.031872 | 171.85 | 1147.9 | 976.05
17158 | 12.42 | 203.59 | 60.034 | 0.031878 | 171.86 | 1147.9 |  | 17158 | 203.59 | 12.42 | 60.034 | 0.031878 | 171.86 | 1147.9 | 976.04
17159 | 12.423 | 203.6 | 60.034 | 0.031884 | 171.87 | 1147.9 |  | 17159 | 203.6 | 12.423 | 60.034 | 0.031884 | 171.87 | 1147.9 | 976.03
17160 | 12.425 | 203.61 | 60.034 | 0.03189 | 171.88 | 1147.9 |  | 17160 | 203.61 | 12.425 | 60.034 | 0.03189 | 171.88 | 1147.9 | 976.02
17161 | 12.428 | 203.62 | 60.033 | 0.031896 | 171.89 | 1147.9 |  | 17161 | 203.62 | 12.428 | 60.033 | 0.031896 | 171.89 | 1147.9 | 976.01
17162 | 12.43 | 203.63 | 60.033 | 0.031902 | 171.9 | 1147.9 |  | 17162 | 203.63 | 12.43 | 60.033 | 0.031902 | 171.9 | 1147.9 | 976
17163 | 12.433 | 203.64 | 60.033 | 0.031908 | 171.91 | 1147.9 |  | 17163 | 203.64 | 12.433 | 60.033 | 0.031908 | 171.91 | 1147.9 | 975.99
17164 | 12.435 | 203.65 | 60.033 | 0.031914 | 171.92 | 1147.9 |  | 17164 | 203.65 | 12.435 | 60.033 | 0.031914 | 171.92 | 1147.9 | 975.98
17165 | 12.438 | 203.66 | 60.032 | 0.03192 | 171.93 | 1147.9 |  | 17165 | 203.66 | 12.438 | 60.032 | 0.03192 | 171.93 | 1147.9 | 975.97
17166 | 12.441 | 203.67 | 60.032 | 0.031926 | 171.94 | 1147.9 |  | 17166 | 203.67 | 12.441 | 60.032 | 0.031926 | 171.94 | 1147.9 | 975.96
17167 | 12.443 | 203.68 | 60.032 | 0.031933 | 171.95 | 1147.9 |  | 17167 | 203.68 | 12.443 | 60.032 | 0.031933 | 171.95 | 1147.9 | 975.95
17168 | 12.446 | 203.69 | 60.032 | 0.031939 | 171.96 | 1147.9 |  | 17168 | 203.69 | 12.446 | 60.032 | 0.031939 | 171.96 | 1147.9 | 975.94
17169 | 12.448 | 203.7 | 60.031 | 0.031945 | 171.97 | 1147.9 |  | 17169 | 203.7 | 12.448 | 60.031 | 0.031945 | 171.97 | 1147.9 | 975.93
17170 | 12.451 | 203.71 | 60.031 | 0.031951 | 171.98 | 1147.9 |  | 17170 | 203.71 | 12.451 | 60.031 | 0.031951 | 171.98 | 1147.9 | 975.92
17171 | 12.453 | 203.72 | 60.031 | 0.031957 | 171.99 | 1147.9 |  | 17171 | 203.72 | 12.453 | 60.031 | 0.031957 | 171.99 | 1147.9 | 975.91
17172 | 12.456 | 203.73 | 60.031 | 0.031963 | 172 | 1147.9 |  | 17172 | 203.73 | 12.456 | 60.031 | 0.031963 | 172 | 1147.9 | 975.9
17173 | 12.458 | 203.74 | 60.03 | 0.031969 | 172.01 | 1147.9 |  | 17173 | 203.74 | 12.458 | 60.03 | 0.031969 | 172.01 | 1147.9 | 975.89
17174 | 12.461 | 203.75 | 60.03 | 0.031975 | 172.02 | 1147.9 |  | 17174 | 203.75 | 12.461 | 60.03 | 0.031975 | 172.02 | 1147.9 | 975.88
17175 | 12.463 | 203.76 | 60.03 | 0.031981 | 172.03 | 1147.9 |  | 17175 | 203.76 | 12.463 | 60.03 | 0.031981 | 172.03 | 1147.9 | 975.87
17176 | 12.466 | 203.77 | 60.03 | 0.031987 | 172.04 | 1147.9 |  | 17176 | 203.77 | 12.466 | 60.03 | 0.031987 | 172.04 | 1147.9 | 975.86
17177 | 12.468 | 203.78 | 60.029 | 0.031994 | 172.05 | 1147.9 |  | 17177 | 203.78 | 12.468 | 60.029 | 0.031994 | 172.05 | 1147.9 | 975.85
17178 | 12.471 | 203.79 | 60.029 | 0.032 | 172.06 | 1147.9 |  | 17178 | 203.79 | 12.471 | 60.029 | 0.032 | 172.06 | 1147.9 | 975.84
17179 | 12.474 | 203.8 | 60.029 | 0.032006 | 172.07 | 1147.9 |  | 17179 | 203.8 | 12.474 | 60.029 | 0.032006 | 172.07 | 1147.9 | 975.83
17180 | 12.476 | 203.81 | 60.029 | 0.032012 | 172.08 | 1147.9 |  | 17180 | 203.81 | 12.476 | 60.029 | 0.032012 | 172.08 | 1147.9 | 975.82
17181 | 12.479 | 203.82 | 60.028 | 0.032018 | 172.09 | 1147.9 |  | 17181 | 203.82 | 12.479 | 60.028 | 0.032018 | 172.09 | 1147.9 | 975.81
17182 | 12.481 | 203.83 | 60.028 | 0.032024 | 172.1 | 1148 |  | 17182 | 203.83 | 12.481 | 60.028 | 0.032024 | 172.1 | 1148 | 975.9
17183 | 12.484 | 203.84 | 60.028 | 0.03203 | 172.11 | 1148 |  | 17183 | 203.84 | 12.484 | 60.028 | 0.03203 | 172.11 | 1148 | 975.89
17184 | 12.486 | 203.85 | 60.028 | 0.032036 | 172.12 | 1148 |  | 17184 | 203.85 | 12.486 | 60.028 | 0.032036 | 172.12 | 1148 | 975.88
17185 | 12.489 | 203.86 | 60.027 | 0.032042 | 172.13 | 1148 |  | 17185 | 203.86 | 12.489 | 60.027 | 0.032042 | 172.13 | 1148 | 975.87
17186 | 12.491 | 203.87 | 60.027 | 0.032049 | 172.14 | 1148 |  | 17186 | 203.87 | 12.491 | 60.027 | 0.032049 | 172.14 | 1148 | 975.86
17187 | 12.494 | 203.88 | 60.027 | 0.032055 | 172.15 | 1148 |  | 17187 | 203.88 | 12.494 | 60.027 | 0.032055 | 172.15 | 1148 | 975.85
17188 | 12.496 | 203.89 | 60.027 | 0.032061 | 172.16 | 1148 |  | 17188 | 203.89 | 12.496 | 60.027 | 0.032061 | 172.16 | 1148 | 975.84
17189 | 12.499 | 203.9 | 60.026 | 0.032067 | 172.17 | 1148 |  | 17189 | 203.9 | 12.499 | 60.026 | 0.032067 | 172.17 | 1148 | 975.83
17190 | 12.502 | 203.91 | 60.026 | 0.032073 | 172.18 | 1148 |  | 17190 | 203.91 | 12.502 | 60.026 | 0.032073 | 172.18 | 1148 | 975.82
17191 | 12.504 | 203.92 | 60.026 | 0.032079 | 172.19 | 1148 |  | 17191 | 203.92 | 12.504 | 60.026 | 0.032079 | 172.19 | 1148 | 975.81
17192 | 12.507 | 203.93 | 60.026 | 0.032085 | 172.2 | 1148 |  | 17192 | 203.93 | 12.507 | 60.026 | 0.032085 | 172.2 | 1148 | 975.8
17193 | 12.509 | 203.94 | 60.026 | 0.032091 | 172.21 | 1148 |  | 17193 | 203.94 | 12.509 | 60.026 | 0.032091 | 172.21 | 1148 | 975.79
17194 | 12.512 | 203.95 | 60.025 | 0.032097 | 172.22 | 1148 |  | 17194 | 203.95 | 12.512 | 60.025 | 0.032097 | 172.22 | 1148 | 975.78
17195 | 12.514 | 203.96 | 60.025 | 0.032104 | 172.23 | 1148 |  | 17195 | 203.96 | 12.514 | 60.025 | 0.032104 | 172.23 | 1148 | 975.77
17196 | 12.517 | 203.97 | 60.025 | 0.03211 | 172.24 | 1148 |  | 17196 | 203.97 | 12.517 | 60.025 | 0.03211 | 172.24 | 1148 | 975.76
17197 | 12.519 | 203.98 | 60.025 | 0.032116 | 172.25 | 1148 |  | 17197 | 203.98 | 12.519 | 60.025 | 0.032116 | 172.25 | 1148 | 975.75
17198 | 12.522 | 203.99 | 60.024 | 0.032122 | 172.26 | 1148 |  | 17198 | 203.99 | 12.522 | 60.024 | 0.032122 | 172.26 | 1148 | 975.74
17199 | 12.524 | 204 | 60.024 | 0.032128 | 172.27 | 1148 |  | 17199 | 204 | 12.524 | 60.024 | 0.032128 | 172.27 | 1148 | 975.73
17200 | 12.527 | 204.01 | 60.024 | 0.032134 | 172.28 | 1148 |  | 17200 | 204.01 | 12.527 | 60.024 | 0.032134 | 172.28 | 1148 | 975.72
17201 | 12.53 | 204.02 | 60.024 | 0.03214 | 172.29 | 1148 |  | 17201 | 204.02 | 12.53 | 60.024 | 0.03214 | 172.29 | 1148 | 975.71
17202 | 12.532 | 204.03 | 60.023 | 0.032146 | 172.3 | 1148 |  | 17202 | 204.03 | 12.532 | 60.023 | 0.032146 | 172.3 | 1148 | 975.7
17203 | 12.535 | 204.04 | 60.023 | 0.032153 | 172.31 | 1148 |  | 17203 | 204.04 | 12.535 | 60.023 | 0.032153 | 172.31 | 1148 | 975.69
17204 | 12.537 | 204.05 | 60.023 | 0.032159 | 172.32 | 1148 |  | 17204 | 204.05 | 12.537 | 60.023 | 0.032159 | 172.32 | 1148 | 975.68
17205 | 12.54 | 204.06 | 60.023 | 0.032165 | 172.33 | 1148 |  | 17205 | 204.06 | 12.54 | 60.023 | 0.032165 | 172.33 | 1148 | 975.67
17206 | 12.542 | 204.07 | 60.022 | 0.032171 | 172.34 | 1148 |  | 17206 | 204.07 | 12.542 | 60.022 | 0.032171 | 172.34 | 1148 | 975.66
17207 | 12.545 | 204.08 | 60.022 | 0.032177 | 172.35 | 1148 |  | 17207 | 204.08 | 12.545 | 60.022 | 0.032177 | 172.35 | 1148 | 975.65
17208 | 12.547 | 204.09 | 60.022 | 0.032183 | 172.36 | 1148.1 |  | 17208 | 204.09 | 12.547 | 60.022 | 0.032183 | 172.36 | 1148.1 | 975.74
17209 | 12.55 | 204.1 | 60.022 | 0.032189 | 172.37 | 1148.1 |  | 17209 | 204.1 | 12.55 | 60.022 | 0.032189 | 172.37 | 1148.1 | 975.73
17210 | 12.553 | 204.11 | 60.021 | 0.032195 | 172.38 | 1148.1 |  | 17210 | 204.11 | 12.553 | 60.021 | 0.032195 | 172.38 | 1148.1 | 975.72
17211 | 12.555 | 204.12 | 60.021 | 0.032202 | 172.39 | 1148.1 |  | 17211 | 204.12 | 12.555 | 60.021 | 0.032202 | 172.39 | 1148.1 | 975.71
17212 | 12.558 | 204.13 | 60.021 | 0.032208 | 172.4 | 1148.1 |  | 17212 | 204.13 | 12.558 | 60.021 | 0.032208 | 172.4 | 1148.1 | 975.7
17213 | 12.56 | 204.14 | 60.021 | 0.032214 | 172.41 | 1148.1 |  | 17213 | 204.14 | 12.56 | 60.021 | 0.032214 | 172.41 | 1148.1 | 975.69
17214 | 12.563 | 204.15 | 60.02 | 0.03222 | 172.42 | 1148.1 |  | 17214 | 204.15 | 12.563 | 60.02 | 0.03222 | 172.42 | 1148.1 | 975.68
17215 | 12.565 | 204.16 | 60.02 | 0.032226 | 172.43 | 1148.1 |  | 17215 | 204.16 | 12.565 | 60.02 | 0.032226 | 172.43 | 1148.1 | 975.67
17216 | 12.568 | 204.17 | 60.02 | 0.032232 | 172.44 | 1148.1 |  | 17216 | 204.17 | 12.568 | 60.02 | 0.032232 | 172.44 | 1148.1 | 975.66
17217 | 12.571 | 204.18 | 60.02 | 0.032238 | 172.45 | 1148.1 |  | 17217 | 204.18 | 12.571 | 60.02 | 0.032238 | 172.45 | 1148.1 | 975.65
17218 | 12.573 | 204.19 | 60.019 | 0.032245 | 172.46 | 1148.1 |  | 17218 | 204.19 | 12.573 | 60.019 | 0.032245 | 172.46 | 1148.1 | 975.64
17219 | 12.576 | 204.2 | 60.019 | 0.032251 | 172.47 | 1148.1 |  | 17219 | 204.2 | 12.576 | 60.019 | 0.032251 | 172.47 | 1148.1 | 975.63
17220 | 12.578 | 204.21 | 60.019 | 0.032257 | 172.48 | 1148.1 |  | 17220 | 204.21 | 12.578 | 60.019 | 0.032257 | 172.48 | 1148.1 | 975.62
17221 | 12.581 | 204.22 | 60.019 | 0.032263 | 172.49 | 1148.1 |  | 17221 | 204.22 | 12.581 | 60.019 | 0.032263 | 172.49 | 1148.1 | 975.61
17222 | 12.583 | 204.23 | 60.019 | 0.032269 | 172.5 | 1148.1 |  | 17222 | 204.23 | 12.583 | 60.019 | 0.032269 | 172.5 | 1148.1 | 975.6
17223 | 12.586 | 204.24 | 60.018 | 0.032275 | 172.51 | 1148.1 |  | 17223 | 204.24 | 12.586 | 60.018 | 0.032275 | 172.51 | 1148.1 | 975.59
17224 | 12.588 | 204.25 | 60.018 | 0.032281 | 172.52 | 1148.1 |  | 17224 | 204.25 | 12.588 | 60.018 | 0.032281 | 172.52 | 1148.1 | 975.58
17225 | 12.591 | 204.26 | 60.018 | 0.032288 | 172.53 | 1148.1 |  | 17225 | 204.26 | 12.591 | 60.018 | 0.032288 | 172.53 | 1148.1 | 975.57
17226 | 12.594 | 204.27 | 60.018 | 0.032294 | 172.54 | 1148.1 |  | 17226 | 204.27 | 12.594 | 60.018 | 0.032294 | 172.54 | 1148.1 | 975.56
17227 | 12.596 | 204.28 | 60.017 | 0.0323 | 172.55 | 1148.1 |  | 17227 | 204.28 | 12.596 | 60.017 | 0.0323 | 172.55 | 1148.1 | 975.55
17228 | 12.599 | 204.29 | 60.017 | 0.032306 | 172.56 | 1148.1 |  | 17228 | 204.29 | 12.599 | 60.017 | 0.032306 | 172.56 | 1148.1 | 975.54
17229 | 12.601 | 204.3 | 60.017 | 0.032312 | 172.57 | 1148.1 |  | 17229 | 204.3 | 12.601 | 60.017 | 0.032312 | 172.57 | 1148.1 | 975.53
17230 | 12.604 | 204.31 | 60.017 | 0.032318 | 172.58 | 1148.1 |  | 17230 | 204.31 | 12.604 | 60.017 | 0.032318 | 172.58 | 1148.1 | 975.52
17231 | 12.606 | 204.32 | 60.016 | 0.032325 | 172.59 | 1148.1 |  | 17231 | 204.32 | 12.606 | 60.016 | 0.032325 | 172.59 | 1148.1 | 975.51
17232 | 12.609 | 204.33 | 60.016 | 0.032331 | 172.6 | 1148.1 |  | 17232 | 204.33 | 12.609 | 60.016 | 0.032331 | 172.6 | 1148.1 | 975.5
17233 | 12.612 | 204.34 | 60.016 | 0.032337 | 172.61 | 1148.1 |  | 17233 | 204.34 | 12.612 | 60.016 | 0.032337 | 172.61 | 1148.1 | 975.49
17234 | 12.614 | 204.35 | 60.016 | 0.032343 | 172.62 | 1148.2 |  | 17234 | 204.35 | 12.614 | 60.016 | 0.032343 | 172.62 | 1148.2 | 975.58
17235 | 12.617 | 204.36 | 60.015 | 0.032349 | 172.63 | 1148.2 |  | 17235 | 204.36 | 12.617 | 60.015 | 0.032349 | 172.63 | 1148.2 | 975.57
17236 | 12.619 | 204.37 | 60.015 | 0.032355 | 172.64 | 1148.2 |  | 17236 | 204.37 | 12.619 | 60.015 | 0.032355 | 172.64 | 1148.2 | 975.56
17237 | 12.622 | 204.38 | 60.015 | 0.032361 | 172.65 | 1148.2 |  | 17237 | 204.38 | 12.622 | 60.015 | 0.032361 | 172.65 | 1148.2 | 975.55
17238 | 12.624 | 204.39 | 60.015 | 0.032368 | 172.66 | 1148.2 |  | 17238 | 204.39 | 12.624 | 60.015 | 0.032368 | 172.66 | 1148.2 | 975.54
17239 | 12.627 | 204.4 | 60.014 | 0.032374 | 172.67 | 1148.2 |  | 17239 | 204.4 | 12.627 | 60.014 | 0.032374 | 172.67 | 1148.2 | 975.53
17240 | 12.63 | 204.41 | 60.014 | 0.03238 | 172.68 | 1148.2 |  | 17240 | 204.41 | 12.63 | 60.014 | 0.03238 | 172.68 | 1148.2 | 975.52
17241 | 12.632 | 204.42 | 60.014 | 0.032386 | 172.69 | 1148.2 |  | 17241 | 204.42 | 12.632 | 60.014 | 0.032386 | 172.69 | 1148.2 | 975.51
17242 | 12.635 | 204.43 | 60.014 | 0.032392 | 172.7 | 1148.2 |  | 17242 | 204.43 | 12.635 | 60.014 | 0.032392 | 172.7 | 1148.2 | 975.5
17243 | 12.637 | 204.44 | 60.013 | 0.032398 | 172.71 | 1148.2 |  | 17243 | 204.44 | 12.637 | 60.013 | 0.032398 | 172.71 | 1148.2 | 975.49
17244 | 12.64 | 204.45 | 60.013 | 0.032405 | 172.72 | 1148.2 |  | 17244 | 204.45 | 12.64 | 60.013 | 0.032405 | 172.72 | 1148.2 | 975.48
17245 | 12.642 | 204.46 | 60.013 | 0.032411 | 172.73 | 1148.2 |  | 17245 | 204.46 | 12.642 | 60.013 | 0.032411 | 172.73 | 1148.2 | 975.47
17246 | 12.645 | 204.47 | 60.013 | 0.032417 | 172.74 | 1148.2 |  | 17246 | 204.47 | 12.645 | 60.013 | 0.032417 | 172.74 | 1148.2 | 975.46
17247 | 12.648 | 204.48 | 60.012 | 0.032423 | 172.75 | 1148.2 |  | 17247 | 204.48 | 12.648 | 60.012 | 0.032423 | 172.75 | 1148.2 | 975.45
17248 | 12.65 | 204.49 | 60.012 | 0.032429 | 172.76 | 1148.2 |  | 17248 | 204.49 | 12.65 | 60.012 | 0.032429 | 172.76 | 1148.2 | 975.44
17249 | 12.653 | 204.5 | 60.012 | 0.032435 | 172.77 | 1148.2 |  | 17249 | 204.5 | 12.653 | 60.012 | 0.032435 | 172.77 | 1148.2 | 975.43
17250 | 12.655 | 204.51 | 60.012 | 0.032442 | 172.78 | 1148.2 |  | 17250 | 204.51 | 12.655 | 60.012 | 0.032442 | 172.78 | 1148.2 | 975.42
17251 | 12.658 | 204.52 | 60.011 | 0.032448 | 172.79 | 1148.2 |  | 17251 | 204.52 | 12.658 | 60.011 | 0.032448 | 172.79 | 1148.2 | 975.41
17252 | 12.66 | 204.53 | 60.011 | 0.032454 | 172.8 | 1148.2 |  | 17252 | 204.53 | 12.66 | 60.011 | 0.032454 | 172.8 | 1148.2 | 975.4
17253 | 12.663 | 204.54 | 60.011 | 0.03246 | 172.81 | 1148.2 |  | 17253 | 204.54 | 12.663 | 60.011 | 0.03246 | 172.81 | 1148.2 | 975.39
17254 | 12.666 | 204.55 | 60.011 | 0.032466 | 172.82 | 1148.2 |  | 17254 | 204.55 | 12.666 | 60.011 | 0.032466 | 172.82 | 1148.2 | 975.38
17255 | 12.668 | 204.56 | 60.011 | 0.032472 | 172.83 | 1148.2 |  | 17255 | 204.56 | 12.668 | 60.011 | 0.032472 | 172.83 | 1148.2 | 975.37
17256 | 12.671 | 204.57 | 60.01 | 0.032479 | 172.84 | 1148.2 |  | 17256 | 204.57 | 12.671 | 60.01 | 0.032479 | 172.84 | 1148.2 | 975.36
17257 | 12.673 | 204.58 | 60.01 | 0.032485 | 172.85 | 1148.2 |  | 17257 | 204.58 | 12.673 | 60.01 | 0.032485 | 172.85 | 1148.2 | 975.35
17258 | 12.676 | 204.59 | 60.01 | 0.032491 | 172.86 | 1148.2 |  | 17258 | 204.59 | 12.676 | 60.01 | 0.032491 | 172.86 | 1148.2 | 975.34
17259 | 12.678 | 204.6 | 60.01 | 0.032497 | 172.87 | 1148.2 |  | 17259 | 204.6 | 12.678 | 60.01 | 0.032497 | 172.87 | 1148.2 | 975.33
17260 | 12.681 | 204.61 | 60.009 | 0.032503 | 172.88 | 1148.3 |  | 17260 | 204.61 | 12.681 | 60.009 | 0.032503 | 172.88 | 1148.3 | 975.42
17261 | 12.684 | 204.62 | 60.009 | 0.03251 | 172.89 | 1148.3 |  | 17261 | 204.62 | 12.684 | 60.009 | 0.03251 | 172.89 | 1148.3 | 975.41
17262 | 12.686 | 204.63 | 60.009 | 0.032516 | 172.9 | 1148.3 |  | 17262 | 204.63 | 12.686 | 60.009 | 0.032516 | 172.9 | 1148.3 | 975.4
17263 | 12.689 | 204.64 | 60.009 | 0.032522 | 172.91 | 1148.3 |  | 17263 | 204.64 | 12.689 | 60.009 | 0.032522 | 172.91 | 1148.3 | 975.39
17264 | 12.691 | 204.65 | 60.008 | 0.032528 | 172.92 | 1148.3 |  | 17264 | 204.65 | 12.691 | 60.008 | 0.032528 | 172.92 | 1148.3 | 975.38
17265 | 12.694 | 204.66 | 60.008 | 0.032534 | 172.93 | 1148.3 |  | 17265 | 204.66 | 12.694 | 60.008 | 0.032534 | 172.93 | 1148.3 | 975.37
17266 | 12.696 | 204.67 | 60.008 | 0.032541 | 172.94 | 1148.3 |  | 17266 | 204.67 | 12.696 | 60.008 | 0.032541 | 172.94 | 1148.3 | 975.36
17267 | 12.699 | 204.68 | 60.008 | 0.032547 | 172.95 | 1148.3 |  | 17267 | 204.68 | 12.699 | 60.008 | 0.032547 | 172.95 | 1148.3 | 975.35
17268 | 12.702 | 204.69 | 60.007 | 0.032553 | 172.96 | 1148.3 |  | 17268 | 204.69 | 12.702 | 60.007 | 0.032553 | 172.96 | 1148.3 | 975.34
17269 | 12.704 | 204.7 | 60.007 | 0.032559 | 172.97 | 1148.3 |  | 17269 | 204.7 | 12.704 | 60.007 | 0.032559 | 172.97 | 1148.3 | 975.33
17270 | 12.707 | 204.71 | 60.007 | 0.032565 | 172.98 | 1148.3 |  | 17270 | 204.71 | 12.707 | 60.007 | 0.032565 | 172.98 | 1148.3 | 975.32
17271 | 12.709 | 204.72 | 60.007 | 0.032571 | 172.99 | 1148.3 |  | 17271 | 204.72 | 12.709 | 60.007 | 0.032571 | 172.99 | 1148.3 | 975.31
17272 | 12.712 | 204.73 | 60.006 | 0.032578 | 173 | 1148.3 |  | 17272 | 204.73 | 12.712 | 60.006 | 0.032578 | 173 | 1148.3 | 975.3
17273 | 12.715 | 204.74 | 60.006 | 0.032584 | 173.01 | 1148.3 |  | 17273 | 204.74 | 12.715 | 60.006 | 0.032584 | 173.01 | 1148.3 | 975.29
17274 | 12.717 | 204.75 | 60.006 | 0.03259 | 173.02 | 1148.3 |  | 17274 | 204.75 | 12.717 | 60.006 | 0.03259 | 173.02 | 1148.3 | 975.28
17275 | 12.72 | 204.76 | 60.006 | 0.032596 | 173.03 | 1148.3 |  | 17275 | 204.76 | 12.72 | 60.006 | 0.032596 | 173.03 | 1148.3 | 975.27
17276 | 12.722 | 204.77 | 60.005 | 0.032602 | 173.04 | 1148.3 |  | 17276 | 204.77 | 12.722 | 60.005 | 0.032602 | 173.04 | 1148.3 | 975.26
17277 | 12.725 | 204.78 | 60.005 | 0.032609 | 173.05 | 1148.3 |  | 17277 | 204.78 | 12.725 | 60.005 | 0.032609 | 173.05 | 1148.3 | 975.25
17278 | 12.727 | 204.79 | 60.005 | 0.032615 | 173.06 | 1148.3 |  | 17278 | 204.79 | 12.727 | 60.005 | 0.032615 | 173.06 | 1148.3 | 975.24
17279 | 12.73 | 204.8 | 60.005 | 0.032621 | 173.07 | 1148.3 |  | 17279 | 204.8 | 12.73 | 60.005 | 0.032621 | 173.07 | 1148.3 | 975.23
17280 | 12.733 | 204.81 | 60.004 | 0.032627 | 173.08 | 1148.3 |  | 17280 | 204.81 | 12.733 | 60.004 | 0.032627 | 173.08 | 1148.3 | 975.22
17281 | 12.735 | 204.82 | 60.004 | 0.032633 | 173.09 | 1148.3 |  | 17281 | 204.82 | 12.735 | 60.004 | 0.032633 | 173.09 | 1148.3 | 975.21
17282 | 12.738 | 204.83 | 60.004 | 0.03264 | 173.1 | 1148.3 |  | 17282 | 204.83 | 12.738 | 60.004 | 0.03264 | 173.1 | 1148.3 | 975.2
17283 | 12.74 | 204.84 | 60.004 | 0.032646 | 173.11 | 1148.3 |  | 17283 | 204.84 | 12.74 | 60.004 | 0.032646 | 173.11 | 1148.3 | 975.19
17284 | 12.743 | 204.85 | 60.003 | 0.032652 | 173.12 | 1148.3 |  | 17284 | 204.85 | 12.743 | 60.003 | 0.032652 | 173.12 | 1148.3 | 975.18
17285 | 12.746 | 204.86 | 60.003 | 0.032658 | 173.13 | 1148.3 |  | 17285 | 204.86 | 12.746 | 60.003 | 0.032658 | 173.13 | 1148.3 | 975.17
17286 | 12.748 | 204.87 | 60.003 | 0.032664 | 173.15 | 1148.4 |  | 17286 | 204.87 | 12.748 | 60.003 | 0.032664 | 173.15 | 1148.4 | 975.25
17287 | 12.751 | 204.88 | 60.003 | 0.032671 | 173.16 | 1148.4 |  | 17287 | 204.88 | 12.751 | 60.003 | 0.032671 | 173.16 | 1148.4 | 975.24
17288 | 12.753 | 204.89 | 60.003 | 0.032677 | 173.17 | 1148.4 |  | 17288 | 204.89 | 12.753 | 60.003 | 0.032677 | 173.17 | 1148.4 | 975.23
17289 | 12.756 | 204.9 | 60.002 | 0.032683 | 173.18 | 1148.4 |  | 17289 | 204.9 | 12.756 | 60.002 | 0.032683 | 173.18 | 1148.4 | 975.22
17290 | 12.759 | 204.91 | 60.002 | 0.032689 | 173.19 | 1148.4 |  | 17290 | 204.91 | 12.759 | 60.002 | 0.032689 | 173.19 | 1148.4 | 975.21
17291 | 12.761 | 204.92 | 60.002 | 0.032696 | 173.2 | 1148.4 |  | 17291 | 204.92 | 12.761 | 60.002 | 0.032696 | 173.2 | 1148.4 | 975.2
17292 | 12.764 | 204.93 | 60.002 | 0.032702 | 173.21 | 1148.4 |  | 17292 | 204.93 | 12.764 | 60.002 | 0.032702 | 173.21 | 1148.4 | 975.19
17293 | 12.766 | 204.94 | 60.001 | 0.032708 | 173.22 | 1148.4 |  | 17293 | 204.94 | 12.766 | 60.001 | 0.032708 | 173.22 | 1148.4 | 975.18
17294 | 12.769 | 204.95 | 60.001 | 0.032714 | 173.23 | 1148.4 |  | 17294 | 204.95 | 12.769 | 60.001 | 0.032714 | 173.23 | 1148.4 | 975.17
17295 | 12.772 | 204.96 | 60.001 | 0.03272 | 173.24 | 1148.4 |  | 17295 | 204.96 | 12.772 | 60.001 | 0.03272 | 173.24 | 1148.4 | 975.16
17296 | 12.774 | 204.97 | 60.001 | 0.032727 | 173.25 | 1148.4 |  | 17296 | 204.97 | 12.774 | 60.001 | 0.032727 | 173.25 | 1148.4 | 975.15
17297 | 12.777 | 204.98 | 60 | 0.032733 | 173.26 | 1148.4 |  | 17297 | 204.98 | 12.777 | 60 | 0.032733 | 173.26 | 1148.4 | 975.14
17298 | 12.779 | 204.99 | 60 | 0.032739 | 173.27 | 1148.4 |  | 17298 | 204.99 | 12.779 | 60 | 0.032739 | 173.27 | 1148.4 | 975.13
17299 | 12.782 | 205 | 60 | 0.032745 | 173.28 | 1148.4 |  | 17299 | 205 | 12.782 | 60 | 0.032745 | 173.28 | 1148.4 | 975.12
17300 | 12.784 | 205.01 | 60 | 0.032751 | 173.29 | 1148.4 |  | 17300 | 205.01 | 12.784 | 60 | 0.032751 | 173.29 | 1148.4 | 975.11
17301 | 12.787 | 205.02 | 59.999 | 0.032758 | 173.3 | 1148.4 |  | 17301 | 205.02 | 12.787 | 59.999 | 0.032758 | 173.3 | 1148.4 | 975.1
17302 | 12.79 | 205.03 | 59.999 | 0.032764 | 173.31 | 1148.4 |  | 17302 | 205.03 | 12.79 | 59.999 | 0.032764 | 173.31 | 1148.4 | 975.09
17303 | 12.792 | 205.04 | 59.999 | 0.03277 | 173.32 | 1148.4 |  | 17303 | 205.04 | 12.792 | 59.999 | 0.03277 | 173.32 | 1148.4 | 975.08
17304 | 12.795 | 205.05 | 59.999 | 0.032776 | 173.33 | 1148.4 |  | 17304 | 205.05 | 12.795 | 59.999 | 0.032776 | 173.33 | 1148.4 | 975.07
17305 | 12.797 | 205.06 | 59.998 | 0.032783 | 173.34 | 1148.4 |  | 17305 | 205.06 | 12.797 | 59.998 | 0.032783 | 173.34 | 1148.4 | 975.06
17306 | 12.8 | 205.07 | 59.998 | 0.032789 | 173.35 | 1148.4 |  | 17306 | 205.07 | 12.8 | 59.998 | 0.032789 | 173.35 | 1148.4 | 975.05
17307 | 12.803 | 205.08 | 59.998 | 0.032795 | 173.36 | 1148.4 |  | 17307 | 205.08 | 12.803 | 59.998 | 0.032795 | 173.36 | 1148.4 | 975.04
17308 | 12.805 | 205.09 | 59.998 | 0.032801 | 173.37 | 1148.4 |  | 17308 | 205.09 | 12.805 | 59.998 | 0.032801 | 173.37 | 1148.4 | 975.03
17309 | 12.808 | 205.1 | 59.997 | 0.032807 | 173.38 | 1148.4 |  | 17309 | 205.1 | 12.808 | 59.997 | 0.032807 | 173.38 | 1148.4 | 975.02
17310 | 12.81 | 205.11 | 59.997 | 0.032814 | 173.39 | 1148.4 |  | 17310 | 205.11 | 12.81 | 59.997 | 0.032814 | 173.39 | 1148.4 | 975.01
17311 | 12.813 | 205.12 | 59.997 | 0.03282 | 173.4 | 1148.4 |  | 17311 | 205.12 | 12.813 | 59.997 | 0.03282 | 173.4 | 1148.4 | 975
17312 | 12.816 | 205.13 | 59.997 | 0.032826 | 173.41 | 1148.5 |  | 17312 | 205.13 | 12.816 | 59.997 | 0.032826 | 173.41 | 1148.5 | 975.09
17313 | 12.818 | 205.14 | 59.996 | 0.032832 | 173.42 | 1148.5 |  | 17313 | 205.14 | 12.818 | 59.996 | 0.032832 | 173.42 | 1148.5 | 975.08
17314 | 12.821 | 205.15 | 59.996 | 0.032839 | 173.43 | 1148.5 |  | 17314 | 205.15 | 12.821 | 59.996 | 0.032839 | 173.43 | 1148.5 | 975.07
17315 | 12.823 | 205.16 | 59.996 | 0.032845 | 173.44 | 1148.5 |  | 17315 | 205.16 | 12.823 | 59.996 | 0.032845 | 173.44 | 1148.5 | 975.06
17316 | 12.826 | 205.17 | 59.996 | 0.032851 | 173.45 | 1148.5 |  | 17316 | 205.17 | 12.826 | 59.996 | 0.032851 | 173.45 | 1148.5 | 975.05
17317 | 12.829 | 205.18 | 59.995 | 0.032857 | 173.46 | 1148.5 |  | 17317 | 205.18 | 12.829 | 59.995 | 0.032857 | 173.46 | 1148.5 | 975.04
17318 | 12.831 | 205.19 | 59.995 | 0.032864 | 173.47 | 1148.5 |  | 17318 | 205.19 | 12.831 | 59.995 | 0.032864 | 173.47 | 1148.5 | 975.03
17319 | 12.834 | 205.2 | 59.995 | 0.03287 | 173.48 | 1148.5 |  | 17319 | 205.2 | 12.834 | 59.995 | 0.03287 | 173.48 | 1148.5 | 975.02
17320 | 12.836 | 205.21 | 59.995 | 0.032876 | 173.49 | 1148.5 |  | 17320 | 205.21 | 12.836 | 59.995 | 0.032876 | 173.49 | 1148.5 | 975.01
17321 | 12.839 | 205.22 | 59.995 | 0.032882 | 173.5 | 1148.5 |  | 17321 | 205.22 | 12.839 | 59.995 | 0.032882 | 173.5 | 1148.5 | 975
17322 | 12.842 | 205.23 | 59.994 | 0.032889 | 173.51 | 1148.5 |  | 17322 | 205.23 | 12.842 | 59.994 | 0.032889 | 173.51 | 1148.5 | 974.99
17323 | 12.844 | 205.24 | 59.994 | 0.032895 | 173.52 | 1148.5 |  | 17323 | 205.24 | 12.844 | 59.994 | 0.032895 | 173.52 | 1148.5 | 974.98
17324 | 12.847 | 205.25 | 59.994 | 0.032901 | 173.53 | 1148.5 |  | 17324 | 205.25 | 12.847 | 59.994 | 0.032901 | 173.53 | 1148.5 | 974.97
17325 | 12.85 | 205.26 | 59.994 | 0.032907 | 173.54 | 1148.5 |  | 17325 | 205.26 | 12.85 | 59.994 | 0.032907 | 173.54 | 1148.5 | 974.96
17326 | 12.852 | 205.27 | 59.993 | 0.032914 | 173.55 | 1148.5 |  | 17326 | 205.27 | 12.852 | 59.993 | 0.032914 | 173.55 | 1148.5 | 974.95
17327 | 12.855 | 205.28 | 59.993 | 0.03292 | 173.56 | 1148.5 |  | 17327 | 205.28 | 12.855 | 59.993 | 0.03292 | 173.56 | 1148.5 | 974.94
17328 | 12.857 | 205.29 | 59.993 | 0.032926 | 173.57 | 1148.5 |  | 17328 | 205.29 | 12.857 | 59.993 | 0.032926 | 173.57 | 1148.5 | 974.93
17329 | 12.86 | 205.3 | 59.993 | 0.032932 | 173.58 | 1148.5 |  | 17329 | 205.3 | 12.86 | 59.993 | 0.032932 | 173.58 | 1148.5 | 974.92
17330 | 12.863 | 205.31 | 59.992 | 0.032939 | 173.59 | 1148.5 |  | 17330 | 205.31 | 12.863 | 59.992 | 0.032939 | 173.59 | 1148.5 | 974.91
17331 | 12.865 | 205.32 | 59.992 | 0.032945 | 173.6 | 1148.5 |  | 17331 | 205.32 | 12.865 | 59.992 | 0.032945 | 173.6 | 1148.5 | 974.9
17332 | 12.868 | 205.33 | 59.992 | 0.032951 | 173.61 | 1148.5 |  | 17332 | 205.33 | 12.868 | 59.992 | 0.032951 | 173.61 | 1148.5 | 974.89
17333 | 12.87 | 205.34 | 59.992 | 0.032957 | 173.62 | 1148.5 |  | 17333 | 205.34 | 12.87 | 59.992 | 0.032957 | 173.62 | 1148.5 | 974.88
17334 | 12.873 | 205.35 | 59.991 | 0.032964 | 173.63 | 1148.5 |  | 17334 | 205.35 | 12.873 | 59.991 | 0.032964 | 173.63 | 1148.5 | 974.87
17335 | 12.876 | 205.36 | 59.991 | 0.03297 | 173.64 | 1148.5 |  | 17335 | 205.36 | 12.876 | 59.991 | 0.03297 | 173.64 | 1148.5 | 974.86
17336 | 12.878 | 205.37 | 59.991 | 0.032976 | 173.65 | 1148.5 |  | 17336 | 205.37 | 12.878 | 59.991 | 0.032976 | 173.65 | 1148.5 | 974.85
17337 | 12.881 | 205.38 | 59.991 | 0.032982 | 173.66 | 1148.5 |  | 17337 | 205.38 | 12.881 | 59.991 | 0.032982 | 173.66 | 1148.5 | 974.84
17338 | 12.883 | 205.39 | 59.99 | 0.032989 | 173.67 | 1148.5 |  | 17338 | 205.39 | 12.883 | 59.99 | 0.032989 | 173.67 | 1148.5 | 974.83
17339 | 12.886 | 205.4 | 59.99 | 0.032995 | 173.68 | 1148.6 |  | 17339 | 205.4 | 12.886 | 59.99 | 0.032995 | 173.68 | 1148.6 | 974.92
17340 | 12.889 | 205.41 | 59.99 | 0.033001 | 173.69 | 1148.6 |  | 17340 | 205.41 | 12.889 | 59.99 | 0.033001 | 173.69 | 1148.6 | 974.91
17341 | 12.891 | 205.42 | 59.99 | 0.033007 | 173.7 | 1148.6 |  | 17341 | 205.42 | 12.891 | 59.99 | 0.033007 | 173.7 | 1148.6 | 974.9
17342 | 12.894 | 205.43 | 59.989 | 0.033014 | 173.71 | 1148.6 |  | 17342 | 205.43 | 12.894 | 59.989 | 0.033014 | 173.71 | 1148.6 | 974.89
17343 | 12.897 | 205.44 | 59.989 | 0.03302 | 173.72 | 1148.6 |  | 17343 | 205.44 | 12.897 | 59.989 | 0.03302 | 173.72 | 1148.6 | 974.88
17344 | 12.899 | 205.45 | 59.989 | 0.033026 | 173.73 | 1148.6 |  | 17344 | 205.45 | 12.899 | 59.989 | 0.033026 | 173.73 | 1148.6 | 974.87
17345 | 12.902 | 205.46 | 59.989 | 0.033032 | 173.74 | 1148.6 |  | 17345 | 205.46 | 12.902 | 59.989 | 0.033032 | 173.74 | 1148.6 | 974.86
17346 | 12.904 | 205.47 | 59.988 | 0.033039 | 173.75 | 1148.6 |  | 17346 | 205.47 | 12.904 | 59.988 | 0.033039 | 173.75 | 1148.6 | 974.85
17347 | 12.907 | 205.48 | 59.988 | 0.033045 | 173.76 | 1148.6 |  | 17347 | 205.48 | 12.907 | 59.988 | 0.033045 | 173.76 | 1148.6 | 974.84
17348 | 12.91 | 205.49 | 59.988 | 0.033051 | 173.77 | 1148.6 |  | 17348 | 205.49 | 12.91 | 59.988 | 0.033051 | 173.77 | 1148.6 | 974.83
17349 | 12.912 | 205.5 | 59.988 | 0.033057 | 173.78 | 1148.6 |  | 17349 | 205.5 | 12.912 | 59.988 | 0.033057 | 173.78 | 1148.6 | 974.82
17350 | 12.915 | 205.51 | 59.987 | 0.033064 | 173.79 | 1148.6 |  | 17350 | 205.51 | 12.915 | 59.987 | 0.033064 | 173.79 | 1148.6 | 974.81
17351 | 12.917 | 205.52 | 59.987 | 0.03307 | 173.8 | 1148.6 |  | 17351 | 205.52 | 12.917 | 59.987 | 0.03307 | 173.8 | 1148.6 | 974.8
17352 | 12.92 | 205.53 | 59.987 | 0.033076 | 173.81 | 1148.6 |  | 17352 | 205.53 | 12.92 | 59.987 | 0.033076 | 173.81 | 1148.6 | 974.79
17353 | 12.923 | 205.54 | 59.987 | 0.033083 | 173.82 | 1148.6 |  | 17353 | 205.54 | 12.923 | 59.987 | 0.033083 | 173.82 | 1148.6 | 974.78
17354 | 12.925 | 205.55 | 59.986 | 0.033089 | 173.83 | 1148.6 |  | 17354 | 205.55 | 12.925 | 59.986 | 0.033089 | 173.83 | 1148.6 | 974.77
17355 | 12.928 | 205.56 | 59.986 | 0.033095 | 173.84 | 1148.6 |  | 17355 | 205.56 | 12.928 | 59.986 | 0.033095 | 173.84 | 1148.6 | 974.76
17356 | 12.931 | 205.57 | 59.986 | 0.033101 | 173.85 | 1148.6 |  | 17356 | 205.57 | 12.931 | 59.986 | 0.033101 | 173.85 | 1148.6 | 974.75
17357 | 12.933 | 205.58 | 59.986 | 0.033108 | 173.86 | 1148.6 |  | 17357 | 205.58 | 12.933 | 59.986 | 0.033108 | 173.86 | 1148.6 | 974.74
17358 | 12.936 | 205.59 | 59.986 | 0.033114 | 173.87 | 1148.6 |  | 17358 | 205.59 | 12.936 | 59.986 | 0.033114 | 173.87 | 1148.6 | 974.73
17359 | 12.938 | 205.6 | 59.985 | 0.03312 | 173.88 | 1148.6 |  | 17359 | 205.6 | 12.938 | 59.985 | 0.03312 | 173.88 | 1148.6 | 974.72
17360 | 12.941 | 205.61 | 59.985 | 0.033126 | 173.89 | 1148.6 |  | 17360 | 205.61 | 12.941 | 59.985 | 0.033126 | 173.89 | 1148.6 | 974.71
17361 | 12.944 | 205.62 | 59.985 | 0.033133 | 173.9 | 1148.6 |  | 17361 | 205.62 | 12.944 | 59.985 | 0.033133 | 173.9 | 1148.6 | 974.7
17362 | 12.946 | 205.63 | 59.985 | 0.033139 | 173.91 | 1148.6 |  | 17362 | 205.63 | 12.946 | 59.985 | 0.033139 | 173.91 | 1148.6 | 974.69
17363 | 12.949 | 205.64 | 59.984 | 0.033145 | 173.92 | 1148.6 |  | 17363 | 205.64 | 12.949 | 59.984 | 0.033145 | 173.92 | 1148.6 | 974.68
17364 | 12.952 | 205.65 | 59.984 | 0.033152 | 173.93 | 1148.6 |  | 17364 | 205.65 | 12.952 | 59.984 | 0.033152 | 173.93 | 1148.6 | 974.67
17365 | 12.954 | 205.66 | 59.984 | 0.033158 | 173.94 | 1148.7 |  | 17365 | 205.66 | 12.954 | 59.984 | 0.033158 | 173.94 | 1148.7 | 974.76
17366 | 12.957 | 205.67 | 59.984 | 0.033164 | 173.95 | 1148.7 |  | 17366 | 205.67 | 12.957 | 59.984 | 0.033164 | 173.95 | 1148.7 | 974.75
17367 | 12.959 | 205.68 | 59.983 | 0.03317 | 173.96 | 1148.7 |  | 17367 | 205.68 | 12.959 | 59.983 | 0.03317 | 173.96 | 1148.7 | 974.74
17368 | 12.962 | 205.69 | 59.983 | 0.033177 | 173.97 | 1148.7 |  | 17368 | 205.69 | 12.962 | 59.983 | 0.033177 | 173.97 | 1148.7 | 974.73
17369 | 12.965 | 205.7 | 59.983 | 0.033183 | 173.98 | 1148.7 |  | 17369 | 205.7 | 12.965 | 59.983 | 0.033183 | 173.98 | 1148.7 | 974.72
17370 | 12.967 | 205.71 | 59.983 | 0.033189 | 173.99 | 1148.7 |  | 17370 | 205.71 | 12.967 | 59.983 | 0.033189 | 173.99 | 1148.7 | 974.71
17371 | 12.97 | 205.72 | 59.982 | 0.033196 | 174 | 1148.7 |  | 17371 | 205.72 | 12.97 | 59.982 | 0.033196 | 174 | 1148.7 | 974.7
17372 | 12.973 | 205.73 | 59.982 | 0.033202 | 174.01 | 1148.7 |  | 17372 | 205.73 | 12.973 | 59.982 | 0.033202 | 174.01 | 1148.7 | 974.69
17373 | 12.975 | 205.74 | 59.982 | 0.033208 | 174.02 | 1148.7 |  | 17373 | 205.74 | 12.975 | 59.982 | 0.033208 | 174.02 | 1148.7 | 974.68
17374 | 12.978 | 205.75 | 59.982 | 0.033214 | 174.03 | 1148.7 |  | 17374 | 205.75 | 12.978 | 59.982 | 0.033214 | 174.03 | 1148.7 | 974.67
17375 | 12.98 | 205.76 | 59.981 | 0.033221 | 174.04 | 1148.7 |  | 17375 | 205.76 | 12.98 | 59.981 | 0.033221 | 174.04 | 1148.7 | 974.66
17376 | 12.983 | 205.77 | 59.981 | 0.033227 | 174.05 | 1148.7 |  | 17376 | 205.77 | 12.983 | 59.981 | 0.033227 | 174.05 | 1148.7 | 974.65
17377 | 12.986 | 205.78 | 59.981 | 0.033233 | 174.06 | 1148.7 |  | 17377 | 205.78 | 12.986 | 59.981 | 0.033233 | 174.06 | 1148.7 | 974.64
17378 | 12.988 | 205.79 | 59.981 | 0.03324 | 174.07 | 1148.7 |  | 17378 | 205.79 | 12.988 | 59.981 | 0.03324 | 174.07 | 1148.7 | 974.63
17379 | 12.991 | 205.8 | 59.98 | 0.033246 | 174.08 | 1148.7 |  | 17379 | 205.8 | 12.991 | 59.98 | 0.033246 | 174.08 | 1148.7 | 974.62
17380 | 12.994 | 205.81 | 59.98 | 0.033252 | 174.09 | 1148.7 |  | 17380 | 205.81 | 12.994 | 59.98 | 0.033252 | 174.09 | 1148.7 | 974.61
17381 | 12.996 | 205.82 | 59.98 | 0.033259 | 174.1 | 1148.7 |  | 17381 | 205.82 | 12.996 | 59.98 | 0.033259 | 174.1 | 1148.7 | 974.6
17382 | 12.999 | 205.83 | 59.98 | 0.033265 | 174.11 | 1148.7 |  | 17382 | 205.83 | 12.999 | 59.98 | 0.033265 | 174.11 | 1148.7 | 974.59
17383 | 13.001 | 205.84 | 59.979 | 0.033271 | 174.12 | 1148.7 |  | 17383 | 205.84 | 13.001 | 59.979 | 0.033271 | 174.12 | 1148.7 | 974.58
17384 | 13.004 | 205.85 | 59.979 | 0.033277 | 174.13 | 1148.7 |  | 17384 | 205.85 | 13.004 | 59.979 | 0.033277 | 174.13 | 1148.7 | 974.57
17385 | 13.007 | 205.86 | 59.979 | 0.033284 | 174.14 | 1148.7 |  | 17385 | 205.86 | 13.007 | 59.979 | 0.033284 | 174.14 | 1148.7 | 974.56
17386 | 13.009 | 205.87 | 59.979 | 0.03329 | 174.15 | 1148.7 |  | 17386 | 205.87 | 13.009 | 59.979 | 0.03329 | 174.15 | 1148.7 | 974.55
17387 | 13.012 | 205.88 | 59.978 | 0.033296 | 174.16 | 1148.7 |  | 17387 | 205.88 | 13.012 | 59.978 | 0.033296 | 174.16 | 1148.7 | 974.54
17388 | 13.015 | 205.89 | 59.978 | 0.033303 | 174.17 | 1148.7 |  | 17388 | 205.89 | 13.015 | 59.978 | 0.033303 | 174.17 | 1148.7 | 974.53
17389 | 13.017 | 205.9 | 59.978 | 0.033309 | 174.18 | 1148.7 |  | 17389 | 205.9 | 13.017 | 59.978 | 0.033309 | 174.18 | 1148.7 | 974.52
17390 | 13.02 | 205.91 | 59.978 | 0.033315 | 174.19 | 1148.7 |  | 17390 | 205.91 | 13.02 | 59.978 | 0.033315 | 174.19 | 1148.7 | 974.51
17391 | 13.023 | 205.92 | 59.977 | 0.033322 | 174.2 | 1148.8 |  | 17391 | 205.92 | 13.023 | 59.977 | 0.033322 | 174.2 | 1148.8 | 974.6
17392 | 13.025 | 205.93 | 59.977 | 0.033328 | 174.21 | 1148.8 |  | 17392 | 205.93 | 13.025 | 59.977 | 0.033328 | 174.21 | 1148.8 | 974.59
17393 | 13.028 | 205.94 | 59.977 | 0.033334 | 174.22 | 1148.8 |  | 17393 | 205.94 | 13.028 | 59.977 | 0.033334 | 174.22 | 1148.8 | 974.58
17394 | 13.03 | 205.95 | 59.977 | 0.033341 | 174.23 | 1148.8 |  | 17394 | 205.95 | 13.03 | 59.977 | 0.033341 | 174.23 | 1148.8 | 974.57
17395 | 13.033 | 205.96 | 59.977 | 0.033347 | 174.24 | 1148.8 |  | 17395 | 205.96 | 13.033 | 59.977 | 0.033347 | 174.24 | 1148.8 | 974.56
17396 | 13.036 | 205.97 | 59.976 | 0.033353 | 174.25 | 1148.8 |  | 17396 | 205.97 | 13.036 | 59.976 | 0.033353 | 174.25 | 1148.8 | 974.55
17397 | 13.038 | 205.98 | 59.976 | 0.033359 | 174.26 | 1148.8 |  | 17397 | 205.98 | 13.038 | 59.976 | 0.033359 | 174.26 | 1148.8 | 974.54
17398 | 13.041 | 205.99 | 59.976 | 0.033366 | 174.27 | 1148.8 |  | 17398 | 205.99 | 13.041 | 59.976 | 0.033366 | 174.27 | 1148.8 | 974.53
17399 | 13.044 | 206 | 59.976 | 0.033372 | 174.28 | 1148.8 |  | 17399 | 206 | 13.044 | 59.976 | 0.033372 | 174.28 | 1148.8 | 974.52
17400 | 13.046 | 206.01 | 59.975 | 0.033378 | 174.29 | 1148.8 |  | 17400 | 206.01 | 13.046 | 59.975 | 0.033378 | 174.29 | 1148.8 | 974.51
17401 | 13.049 | 206.02 | 59.975 | 0.033385 | 174.3 | 1148.8 |  | 17401 | 206.02 | 13.049 | 59.975 | 0.033385 | 174.3 | 1148.8 | 974.5
17402 | 13.052 | 206.03 | 59.975 | 0.033391 | 174.31 | 1148.8 |  | 17402 | 206.03 | 13.052 | 59.975 | 0.033391 | 174.31 | 1148.8 | 974.49
17403 | 13.054 | 206.04 | 59.975 | 0.033397 | 174.32 | 1148.8 |  | 17403 | 206.04 | 13.054 | 59.975 | 0.033397 | 174.32 | 1148.8 | 974.48
17404 | 13.057 | 206.05 | 59.974 | 0.033404 | 174.33 | 1148.8 |  | 17404 | 206.05 | 13.057 | 59.974 | 0.033404 | 174.33 | 1148.8 | 974.47
17405 | 13.06 | 206.06 | 59.974 | 0.03341 | 174.34 | 1148.8 |  | 17405 | 206.06 | 13.06 | 59.974 | 0.03341 | 174.34 | 1148.8 | 974.46
17406 | 13.062 | 206.07 | 59.974 | 0.033416 | 174.35 | 1148.8 |  | 17406 | 206.07 | 13.062 | 59.974 | 0.033416 | 174.35 | 1148.8 | 974.45
17407 | 13.065 | 206.08 | 59.974 | 0.033423 | 174.36 | 1148.8 |  | 17407 | 206.08 | 13.065 | 59.974 | 0.033423 | 174.36 | 1148.8 | 974.44
17408 | 13.067 | 206.09 | 59.973 | 0.033429 | 174.37 | 1148.8 |  | 17408 | 206.09 | 13.067 | 59.973 | 0.033429 | 174.37 | 1148.8 | 974.43
17409 | 13.07 | 206.1 | 59.973 | 0.033435 | 174.38 | 1148.8 |  | 17409 | 206.1 | 13.07 | 59.973 | 0.033435 | 174.38 | 1148.8 | 974.42
17410 | 13.073 | 206.11 | 59.973 | 0.033442 | 174.39 | 1148.8 |  | 17410 | 206.11 | 13.073 | 59.973 | 0.033442 | 174.39 | 1148.8 | 974.41
17411 | 13.075 | 206.12 | 59.973 | 0.033448 | 174.4 | 1148.8 |  | 17411 | 206.12 | 13.075 | 59.973 | 0.033448 | 174.4 | 1148.8 | 974.4
17412 | 13.078 | 206.13 | 59.972 | 0.033454 | 174.41 | 1148.8 |  | 17412 | 206.13 | 13.078 | 59.972 | 0.033454 | 174.41 | 1148.8 | 974.39
17413 | 13.081 | 206.14 | 59.972 | 0.033461 | 174.42 | 1148.8 |  | 17413 | 206.14 | 13.081 | 59.972 | 0.033461 | 174.42 | 1148.8 | 974.38
17414 | 13.083 | 206.15 | 59.972 | 0.033467 | 174.43 | 1148.8 |  | 17414 | 206.15 | 13.083 | 59.972 | 0.033467 | 174.43 | 1148.8 | 974.37
17415 | 13.086 | 206.16 | 59.972 | 0.033473 | 174.44 | 1148.8 |  | 17415 | 206.16 | 13.086 | 59.972 | 0.033473 | 174.44 | 1148.8 | 974.36
17416 | 13.089 | 206.17 | 59.971 | 0.03348 | 174.45 | 1148.8 |  | 17416 | 206.17 | 13.089 | 59.971 | 0.03348 | 174.45 | 1148.8 | 974.35
17417 | 13.091 | 206.18 | 59.971 | 0.033486 | 174.46 | 1148.9 |  | 17417 | 206.18 | 13.091 | 59.971 | 0.033486 | 174.46 | 1148.9 | 974.44
17418 | 13.094 | 206.19 | 59.971 | 0.033492 | 174.47 | 1148.9 |  | 17418 | 206.19 | 13.094 | 59.971 | 0.033492 | 174.47 | 1148.9 | 974.43
17419 | 13.097 | 206.2 | 59.971 | 0.033499 | 174.48 | 1148.9 |  | 17419 | 206.2 | 13.097 | 59.971 | 0.033499 | 174.48 | 1148.9 | 974.42
17420 | 13.099 | 206.21 | 59.97 | 0.033505 | 174.49 | 1148.9 |  | 17420 | 206.21 | 13.099 | 59.97 | 0.033505 | 174.49 | 1148.9 | 974.41
17421 | 13.102 | 206.22 | 59.97 | 0.033511 | 174.5 | 1148.9 |  | 17421 | 206.22 | 13.102 | 59.97 | 0.033511 | 174.5 | 1148.9 | 974.4
17422 | 13.104 | 206.23 | 59.97 | 0.033518 | 174.51 | 1148.9 |  | 17422 | 206.23 | 13.104 | 59.97 | 0.033518 | 174.51 | 1148.9 | 974.39
17423 | 13.107 | 206.24 | 59.97 | 0.033524 | 174.52 | 1148.9 |  | 17423 | 206.24 | 13.107 | 59.97 | 0.033524 | 174.52 | 1148.9 | 974.38
17424 | 13.11 | 206.25 | 59.969 | 0.03353 | 174.53 | 1148.9 |  | 17424 | 206.25 | 13.11 | 59.969 | 0.03353 | 174.53 | 1148.9 | 974.37
17425 | 13.112 | 206.26 | 59.969 | 0.033537 | 174.55 | 1148.9 |  | 17425 | 206.26 | 13.112 | 59.969 | 0.033537 | 174.55 | 1148.9 | 974.35
17426 | 13.115 | 206.27 | 59.969 | 0.033543 | 174.56 | 1148.9 |  | 17426 | 206.27 | 13.115 | 59.969 | 0.033543 | 174.56 | 1148.9 | 974.34
17427 | 13.118 | 206.28 | 59.969 | 0.033549 | 174.57 | 1148.9 |  | 17427 | 206.28 | 13.118 | 59.969 | 0.033549 | 174.57 | 1148.9 | 974.33
17428 | 13.12 | 206.29 | 59.968 | 0.033556 | 174.58 | 1148.9 |  | 17428 | 206.29 | 13.12 | 59.968 | 0.033556 | 174.58 | 1148.9 | 974.32
17429 | 13.123 | 206.3 | 59.968 | 0.033562 | 174.59 | 1148.9 |  | 17429 | 206.3 | 13.123 | 59.968 | 0.033562 | 174.59 | 1148.9 | 974.31
17430 | 13.126 | 206.31 | 59.968 | 0.033568 | 174.6 | 1148.9 |  | 17430 | 206.31 | 13.126 | 59.968 | 0.033568 | 174.6 | 1148.9 | 974.3
17431 | 13.128 | 206.32 | 59.968 | 0.033575 | 174.61 | 1148.9 |  | 17431 | 206.32 | 13.128 | 59.968 | 0.033575 | 174.61 | 1148.9 | 974.29
17432 | 13.131 | 206.33 | 59.967 | 0.033581 | 174.62 | 1148.9 |  | 17432 | 206.33 | 13.131 | 59.967 | 0.033581 | 174.62 | 1148.9 | 974.28
17433 | 13.134 | 206.34 | 59.967 | 0.033587 | 174.63 | 1148.9 |  | 17433 | 206.34 | 13.134 | 59.967 | 0.033587 | 174.63 | 1148.9 | 974.27
17434 | 13.136 | 206.35 | 59.967 | 0.033594 | 174.64 | 1148.9 |  | 17434 | 206.35 | 13.136 | 59.967 | 0.033594 | 174.64 | 1148.9 | 974.26
17435 | 13.139 | 206.36 | 59.967 | 0.0336 | 174.65 | 1148.9 |  | 17435 | 206.36 | 13.139 | 59.967 | 0.0336 | 174.65 | 1148.9 | 974.25
17436 | 13.142 | 206.37 | 59.967 | 0.033607 | 174.66 | 1148.9 |  | 17436 | 206.37 | 13.142 | 59.967 | 0.033607 | 174.66 | 1148.9 | 974.24
17437 | 13.144 | 206.38 | 59.966 | 0.033613 | 174.67 | 1148.9 |  | 17437 | 206.38 | 13.144 | 59.966 | 0.033613 | 174.67 | 1148.9 | 974.23
17438 | 13.147 | 206.39 | 59.966 | 0.033619 | 174.68 | 1148.9 |  | 17438 | 206.39 | 13.147 | 59.966 | 0.033619 | 174.68 | 1148.9 | 974.22
17439 | 13.15 | 206.4 | 59.966 | 0.033626 | 174.69 | 1148.9 |  | 17439 | 206.4 | 13.15 | 59.966 | 0.033626 | 174.69 | 1148.9 | 974.21
17440 | 13.152 | 206.41 | 59.966 | 0.033632 | 174.7 | 1148.9 |  | 17440 | 206.41 | 13.152 | 59.966 | 0.033632 | 174.7 | 1148.9 | 974.2
17441 | 13.155 | 206.42 | 59.965 | 0.033638 | 174.71 | 1148.9 |  | 17441 | 206.42 | 13.155 | 59.965 | 0.033638 | 174.71 | 1148.9 | 974.19
17442 | 13.158 | 206.43 | 59.965 | 0.033645 | 174.72 | 1148.9 |  | 17442 | 206.43 | 13.158 | 59.965 | 0.033645 | 174.72 | 1148.9 | 974.18
17443 | 13.16 | 206.44 | 59.965 | 0.033651 | 174.73 | 1148.9 |  | 17443 | 206.44 | 13.16 | 59.965 | 0.033651 | 174.73 | 1148.9 | 974.17
17444 | 13.163 | 206.45 | 59.965 | 0.033657 | 174.74 | 1149 |  | 17444 | 206.45 | 13.163 | 59.965 | 0.033657 | 174.74 | 1149 | 974.26
17445 | 13.166 | 206.46 | 59.964 | 0.033664 | 174.75 | 1149 |  | 17445 | 206.46 | 13.166 | 59.964 | 0.033664 | 174.75 | 1149 | 974.25
17446 | 13.168 | 206.47 | 59.964 | 0.03367 | 174.76 | 1149 |  | 17446 | 206.47 | 13.168 | 59.964 | 0.03367 | 174.76 | 1149 | 974.24
17447 | 13.171 | 206.48 | 59.964 | 0.033676 | 174.77 | 1149 |  | 17447 | 206.48 | 13.171 | 59.964 | 0.033676 | 174.77 | 1149 | 974.23
17448 | 13.174 | 206.49 | 59.964 | 0.033683 | 174.78 | 1149 |  | 17448 | 206.49 | 13.174 | 59.964 | 0.033683 | 174.78 | 1149 | 974.22
17449 | 13.176 | 206.5 | 59.963 | 0.033689 | 174.79 | 1149 |  | 17449 | 206.5 | 13.176 | 59.963 | 0.033689 | 174.79 | 1149 | 974.21
17450 | 13.179 | 206.51 | 59.963 | 0.033696 | 174.8 | 1149 |  | 17450 | 206.51 | 13.179 | 59.963 | 0.033696 | 174.8 | 1149 | 974.2
17451 | 13.182 | 206.52 | 59.963 | 0.033702 | 174.81 | 1149 |  | 17451 | 206.52 | 13.182 | 59.963 | 0.033702 | 174.81 | 1149 | 974.19
17452 | 13.184 | 206.53 | 59.963 | 0.033708 | 174.82 | 1149 |  | 17452 | 206.53 | 13.184 | 59.963 | 0.033708 | 174.82 | 1149 | 974.18
17453 | 13.187 | 206.54 | 59.962 | 0.033715 | 174.83 | 1149 |  | 17453 | 206.54 | 13.187 | 59.962 | 0.033715 | 174.83 | 1149 | 974.17
17454 | 13.19 | 206.55 | 59.962 | 0.033721 | 174.84 | 1149 |  | 17454 | 206.55 | 13.19 | 59.962 | 0.033721 | 174.84 | 1149 | 974.16
17455 | 13.192 | 206.56 | 59.962 | 0.033727 | 174.85 | 1149 |  | 17455 | 206.56 | 13.192 | 59.962 | 0.033727 | 174.85 | 1149 | 974.15
17456 | 13.195 | 206.57 | 59.962 | 0.033734 | 174.86 | 1149 |  | 17456 | 206.57 | 13.195 | 59.962 | 0.033734 | 174.86 | 1149 | 974.14
17457 | 13.198 | 206.58 | 59.961 | 0.03374 | 174.87 | 1149 |  | 17457 | 206.58 | 13.198 | 59.961 | 0.03374 | 174.87 | 1149 | 974.13
17458 | 13.2 | 206.59 | 59.961 | 0.033747 | 174.88 | 1149 |  | 17458 | 206.59 | 13.2 | 59.961 | 0.033747 | 174.88 | 1149 | 974.12
17459 | 13.203 | 206.6 | 59.961 | 0.033753 | 174.89 | 1149 |  | 17459 | 206.6 | 13.203 | 59.961 | 0.033753 | 174.89 | 1149 | 974.11
17460 | 13.206 | 206.61 | 59.961 | 0.033759 | 174.9 | 1149 |  | 17460 | 206.61 | 13.206 | 59.961 | 0.033759 | 174.9 | 1149 | 974.1
17461 | 13.208 | 206.62 | 59.96 | 0.033766 | 174.91 | 1149 |  | 17461 | 206.62 | 13.208 | 59.96 | 0.033766 | 174.91 | 1149 | 974.09
17462 | 13.211 | 206.63 | 59.96 | 0.033772 | 174.92 | 1149 |  | 17462 | 206.63 | 13.211 | 59.96 | 0.033772 | 174.92 | 1149 | 974.08
17463 | 13.214 | 206.64 | 59.96 | 0.033778 | 174.93 | 1149 |  | 17463 | 206.64 | 13.214 | 59.96 | 0.033778 | 174.93 | 1149 | 974.07
17464 | 13.216 | 206.65 | 59.96 | 0.033785 | 174.94 | 1149 |  | 17464 | 206.65 | 13.216 | 59.96 | 0.033785 | 174.94 | 1149 | 974.06
17465 | 13.219 | 206.66 | 59.959 | 0.033791 | 174.95 | 1149 |  | 17465 | 206.66 | 13.219 | 59.959 | 0.033791 | 174.95 | 1149 | 974.05
17466 | 13.222 | 206.67 | 59.959 | 0.033798 | 174.96 | 1149 |  | 17466 | 206.67 | 13.222 | 59.959 | 0.033798 | 174.96 | 1149 | 974.04
17467 | 13.224 | 206.68 | 59.959 | 0.033804 | 174.97 | 1149 |  | 17467 | 206.68 | 13.224 | 59.959 | 0.033804 | 174.97 | 1149 | 974.03
17468 | 13.227 | 206.69 | 59.959 | 0.03381 | 174.98 | 1149 |  | 17468 | 206.69 | 13.227 | 59.959 | 0.03381 | 174.98 | 1149 | 974.02
17469 | 13.23 | 206.7 | 59.958 | 0.033817 | 174.99 | 1149 |  | 17469 | 206.7 | 13.23 | 59.958 | 0.033817 | 174.99 | 1149 | 974.01
17470 | 13.232 | 206.71 | 59.958 | 0.033823 | 175 | 1149.1 |  | 17470 | 206.71 | 13.232 | 59.958 | 0.033823 | 175 | 1149.1 | 974.1
17471 | 13.235 | 206.72 | 59.958 | 0.033829 | 175.01 | 1149.1 |  | 17471 | 206.72 | 13.235 | 59.958 | 0.033829 | 175.01 | 1149.1 | 974.09
17472 | 13.238 | 206.73 | 59.958 | 0.033836 | 175.02 | 1149.1 |  | 17472 | 206.73 | 13.238 | 59.958 | 0.033836 | 175.02 | 1149.1 | 974.08
17473 | 13.24 | 206.74 | 59.957 | 0.033842 | 175.03 | 1149.1 |  | 17473 | 206.74 | 13.24 | 59.957 | 0.033842 | 175.03 | 1149.1 | 974.07
17474 | 13.243 | 206.75 | 59.957 | 0.033849 | 175.04 | 1149.1 |  | 17474 | 206.75 | 13.243 | 59.957 | 0.033849 | 175.04 | 1149.1 | 974.06
17475 | 13.246 | 206.76 | 59.957 | 0.033855 | 175.05 | 1149.1 |  | 17475 | 206.76 | 13.246 | 59.957 | 0.033855 | 175.05 | 1149.1 | 974.05
17476 | 13.248 | 206.77 | 59.957 | 0.033861 | 175.06 | 1149.1 |  | 17476 | 206.77 | 13.248 | 59.957 | 0.033861 | 175.06 | 1149.1 | 974.04
17477 | 13.251 | 206.78 | 59.957 | 0.033868 | 175.07 | 1149.1 |  | 17477 | 206.78 | 13.251 | 59.957 | 0.033868 | 175.07 | 1149.1 | 974.03
17478 | 13.254 | 206.79 | 59.956 | 0.033874 | 175.08 | 1149.1 |  | 17478 | 206.79 | 13.254 | 59.956 | 0.033874 | 175.08 | 1149.1 | 974.02
17479 | 13.256 | 206.8 | 59.956 | 0.033881 | 175.09 | 1149.1 |  | 17479 | 206.8 | 13.256 | 59.956 | 0.033881 | 175.09 | 1149.1 | 974.01
17480 | 13.259 | 206.81 | 59.956 | 0.033887 | 175.1 | 1149.1 |  | 17480 | 206.81 | 13.259 | 59.956 | 0.033887 | 175.1 | 1149.1 | 974
17481 | 13.262 | 206.82 | 59.956 | 0.033893 | 175.11 | 1149.1 |  | 17481 | 206.82 | 13.262 | 59.956 | 0.033893 | 175.11 | 1149.1 | 973.99
17482 | 13.264 | 206.83 | 59.955 | 0.0339 | 175.12 | 1149.1 |  | 17482 | 206.83 | 13.264 | 59.955 | 0.0339 | 175.12 | 1149.1 | 973.98
17483 | 13.267 | 206.84 | 59.955 | 0.033906 | 175.13 | 1149.1 |  | 17483 | 206.84 | 13.267 | 59.955 | 0.033906 | 175.13 | 1149.1 | 973.97
17484 | 13.27 | 206.85 | 59.955 | 0.033913 | 175.14 | 1149.1 |  | 17484 | 206.85 | 13.27 | 59.955 | 0.033913 | 175.14 | 1149.1 | 973.96
17485 | 13.272 | 206.86 | 59.955 | 0.033919 | 175.15 | 1149.1 |  | 17485 | 206.86 | 13.272 | 59.955 | 0.033919 | 175.15 | 1149.1 | 973.95
17486 | 13.275 | 206.87 | 59.954 | 0.033925 | 175.16 | 1149.1 |  | 17486 | 206.87 | 13.275 | 59.954 | 0.033925 | 175.16 | 1149.1 | 973.94
17487 | 13.278 | 206.88 | 59.954 | 0.033932 | 175.17 | 1149.1 |  | 17487 | 206.88 | 13.278 | 59.954 | 0.033932 | 175.17 | 1149.1 | 973.93
17488 | 13.28 | 206.89 | 59.954 | 0.033938 | 175.18 | 1149.1 |  | 17488 | 206.89 | 13.28 | 59.954 | 0.033938 | 175.18 | 1149.1 | 973.92
17489 | 13.283 | 206.9 | 59.954 | 0.033945 | 175.19 | 1149.1 |  | 17489 | 206.9 | 13.283 | 59.954 | 0.033945 | 175.19 | 1149.1 | 973.91
17490 | 13.286 | 206.91 | 59.953 | 0.033951 | 175.2 | 1149.1 |  | 17490 | 206.91 | 13.286 | 59.953 | 0.033951 | 175.2 | 1149.1 | 973.9
17491 | 13.288 | 206.92 | 59.953 | 0.033957 | 175.21 | 1149.1 |  | 17491 | 206.92 | 13.288 | 59.953 | 0.033957 | 175.21 | 1149.1 | 973.89
17492 | 13.291 | 206.93 | 59.953 | 0.033964 | 175.22 | 1149.1 |  | 17492 | 206.93 | 13.291 | 59.953 | 0.033964 | 175.22 | 1149.1 | 973.88
17493 | 13.294 | 206.94 | 59.953 | 0.03397 | 175.23 | 1149.1 |  | 17493 | 206.94 | 13.294 | 59.953 | 0.03397 | 175.23 | 1149.1 | 973.87
17494 | 13.296 | 206.95 | 59.952 | 0.033977 | 175.24 | 1149.1 |  | 17494 | 206.95 | 13.296 | 59.952 | 0.033977 | 175.24 | 1149.1 | 973.86
17495 | 13.299 | 206.96 | 59.952 | 0.033983 | 175.25 | 1149.1 |  | 17495 | 206.96 | 13.299 | 59.952 | 0.033983 | 175.25 | 1149.1 | 973.85
17496 | 13.302 | 206.97 | 59.952 | 0.033989 | 175.26 | 1149.2 |  | 17496 | 206.97 | 13.302 | 59.952 | 0.033989 | 175.26 | 1149.2 | 973.94
17497 | 13.304 | 206.98 | 59.952 | 0.033996 | 175.27 | 1149.2 |  | 17497 | 206.98 | 13.304 | 59.952 | 0.033996 | 175.27 | 1149.2 | 973.93
17498 | 13.307 | 206.99 | 59.951 | 0.034002 | 175.28 | 1149.2 |  | 17498 | 206.99 | 13.307 | 59.951 | 0.034002 | 175.28 | 1149.2 | 973.92
17499 | 13.31 | 207 | 59.951 | 0.034009 | 175.29 | 1149.2 |  | 17499 | 207 | 13.31 | 59.951 | 0.034009 | 175.29 | 1149.2 | 973.91
17500 | 13.313 | 207.01 | 59.951 | 0.034015 | 175.3 | 1149.2 |  | 17500 | 207.01 | 13.313 | 59.951 | 0.034015 | 175.3 | 1149.2 | 973.9
17501 | 13.315 | 207.02 | 59.951 | 0.034022 | 175.31 | 1149.2 |  | 17501 | 207.02 | 13.315 | 59.951 | 0.034022 | 175.31 | 1149.2 | 973.89
17502 | 13.318 | 207.03 | 59.95 | 0.034028 | 175.32 | 1149.2 |  | 17502 | 207.03 | 13.318 | 59.95 | 0.034028 | 175.32 | 1149.2 | 973.88
17503 | 13.321 | 207.04 | 59.95 | 0.034034 | 175.33 | 1149.2 |  | 17503 | 207.04 | 13.321 | 59.95 | 0.034034 | 175.33 | 1149.2 | 973.87
17504 | 13.323 | 207.05 | 59.95 | 0.034041 | 175.34 | 1149.2 |  | 17504 | 207.05 | 13.323 | 59.95 | 0.034041 | 175.34 | 1149.2 | 973.86
17505 | 13.326 | 207.06 | 59.95 | 0.034047 | 175.35 | 1149.2 |  | 17505 | 207.06 | 13.326 | 59.95 | 0.034047 | 175.35 | 1149.2 | 973.85
17506 | 13.329 | 207.07 | 59.949 | 0.034054 | 175.36 | 1149.2 |  | 17506 | 207.07 | 13.329 | 59.949 | 0.034054 | 175.36 | 1149.2 | 973.84
17507 | 13.331 | 207.08 | 59.949 | 0.03406 | 175.37 | 1149.2 |  | 17507 | 207.08 | 13.331 | 59.949 | 0.03406 | 175.37 | 1149.2 | 973.83
17508 | 13.334 | 207.09 | 59.949 | 0.034067 | 175.38 | 1149.2 |  | 17508 | 207.09 | 13.334 | 59.949 | 0.034067 | 175.38 | 1149.2 | 973.82
17509 | 13.337 | 207.1 | 59.949 | 0.034073 | 175.39 | 1149.2 |  | 17509 | 207.1 | 13.337 | 59.949 | 0.034073 | 175.39 | 1149.2 | 973.81
17510 | 13.339 | 207.11 | 59.948 | 0.034079 | 175.4 | 1149.2 |  | 17510 | 207.11 | 13.339 | 59.948 | 0.034079 | 175.4 | 1149.2 | 973.8
17511 | 13.342 | 207.12 | 59.948 | 0.034086 | 175.41 | 1149.2 |  | 17511 | 207.12 | 13.342 | 59.948 | 0.034086 | 175.41 | 1149.2 | 973.79
17512 | 13.345 | 207.13 | 59.948 | 0.034092 | 175.42 | 1149.2 |  | 17512 | 207.13 | 13.345 | 59.948 | 0.034092 | 175.42 | 1149.2 | 973.78
17513 | 13.347 | 207.14 | 59.948 | 0.034099 | 175.43 | 1149.2 |  | 17513 | 207.14 | 13.347 | 59.948 | 0.034099 | 175.43 | 1149.2 | 973.77
17514 | 13.35 | 207.15 | 59.947 | 0.034105 | 175.44 | 1149.2 |  | 17514 | 207.15 | 13.35 | 59.947 | 0.034105 | 175.44 | 1149.2 | 973.76
17515 | 13.353 | 207.16 | 59.947 | 0.034111 | 175.45 | 1149.2 |  | 17515 | 207.16 | 13.353 | 59.947 | 0.034111 | 175.45 | 1149.2 | 973.75
17516 | 13.356 | 207.17 | 59.947 | 0.034118 | 175.46 | 1149.2 |  | 17516 | 207.17 | 13.356 | 59.947 | 0.034118 | 175.46 | 1149.2 | 973.74
17517 | 13.358 | 207.18 | 59.947 | 0.034124 | 175.47 | 1149.2 |  | 17517 | 207.18 | 13.358 | 59.947 | 0.034124 | 175.47 | 1149.2 | 973.73
17518 | 13.361 | 207.19 | 59.946 | 0.034131 | 175.48 | 1149.2 |  | 17518 | 207.19 | 13.361 | 59.946 | 0.034131 | 175.48 | 1149.2 | 973.72
17519 | 13.364 | 207.2 | 59.946 | 0.034137 | 175.49 | 1149.2 |  | 17519 | 207.2 | 13.364 | 59.946 | 0.034137 | 175.49 | 1149.2 | 973.71
17520 | 13.366 | 207.21 | 59.946 | 0.034144 | 175.5 | 1149.2 |  | 17520 | 207.21 | 13.366 | 59.946 | 0.034144 | 175.5 | 1149.2 | 973.7
17521 | 13.369 | 207.22 | 59.946 | 0.03415 | 175.51 | 1149.2 |  | 17521 | 207.22 | 13.369 | 59.946 | 0.03415 | 175.51 | 1149.2 | 973.69
17522 | 13.372 | 207.23 | 59.946 | 0.034157 | 175.52 | 1149.3 |  | 17522 | 207.23 | 13.372 | 59.946 | 0.034157 | 175.52 | 1149.3 | 973.78
17523 | 13.374 | 207.24 | 59.945 | 0.034163 | 175.53 | 1149.3 |  | 17523 | 207.24 | 13.374 | 59.945 | 0.034163 | 175.53 | 1149.3 | 973.77
17524 | 13.377 | 207.25 | 59.945 | 0.034169 | 175.54 | 1149.3 |  | 17524 | 207.25 | 13.377 | 59.945 | 0.034169 | 175.54 | 1149.3 | 973.76
17525 | 13.38 | 207.26 | 59.945 | 0.034176 | 175.55 | 1149.3 |  | 17525 | 207.26 | 13.38 | 59.945 | 0.034176 | 175.55 | 1149.3 | 973.75
17526 | 13.383 | 207.27 | 59.945 | 0.034182 | 175.56 | 1149.3 |  | 17526 | 207.27 | 13.383 | 59.945 | 0.034182 | 175.56 | 1149.3 | 973.74
17527 | 13.385 | 207.28 | 59.944 | 0.034189 | 175.57 | 1149.3 |  | 17527 | 207.28 | 13.385 | 59.944 | 0.034189 | 175.57 | 1149.3 | 973.73
17528 | 13.388 | 207.29 | 59.944 | 0.034195 | 175.58 | 1149.3 |  | 17528 | 207.29 | 13.388 | 59.944 | 0.034195 | 175.58 | 1149.3 | 973.72
17529 | 13.391 | 207.3 | 59.944 | 0.034202 | 175.59 | 1149.3 |  | 17529 | 207.3 | 13.391 | 59.944 | 0.034202 | 175.59 | 1149.3 | 973.71
17530 | 13.393 | 207.31 | 59.944 | 0.034208 | 175.6 | 1149.3 |  | 17530 | 207.31 | 13.393 | 59.944 | 0.034208 | 175.6 | 1149.3 | 973.7
17531 | 13.396 | 207.32 | 59.943 | 0.034215 | 175.61 | 1149.3 |  | 17531 | 207.32 | 13.396 | 59.943 | 0.034215 | 175.61 | 1149.3 | 973.69
17532 | 13.399 | 207.33 | 59.943 | 0.034221 | 175.62 | 1149.3 |  | 17532 | 207.33 | 13.399 | 59.943 | 0.034221 | 175.62 | 1149.3 | 973.68
17533 | 13.401 | 207.34 | 59.943 | 0.034227 | 175.63 | 1149.3 |  | 17533 | 207.34 | 13.401 | 59.943 | 0.034227 | 175.63 | 1149.3 | 973.67
17534 | 13.404 | 207.35 | 59.943 | 0.034234 | 175.64 | 1149.3 |  | 17534 | 207.35 | 13.404 | 59.943 | 0.034234 | 175.64 | 1149.3 | 973.66
17535 | 13.407 | 207.36 | 59.942 | 0.03424 | 175.65 | 1149.3 |  | 17535 | 207.36 | 13.407 | 59.942 | 0.03424 | 175.65 | 1149.3 | 973.65
17536 | 13.409 | 207.37 | 59.942 | 0.034247 | 175.66 | 1149.3 |  | 17536 | 207.37 | 13.409 | 59.942 | 0.034247 | 175.66 | 1149.3 | 973.64
17537 | 13.412 | 207.38 | 59.942 | 0.034253 | 175.67 | 1149.3 |  | 17537 | 207.38 | 13.412 | 59.942 | 0.034253 | 175.67 | 1149.3 | 973.63
17538 | 13.415 | 207.39 | 59.942 | 0.03426 | 175.68 | 1149.3 |  | 17538 | 207.39 | 13.415 | 59.942 | 0.03426 | 175.68 | 1149.3 | 973.62
17539 | 13.418 | 207.4 | 59.941 | 0.034266 | 175.69 | 1149.3 |  | 17539 | 207.4 | 13.418 | 59.941 | 0.034266 | 175.69 | 1149.3 | 973.61
17540 | 13.42 | 207.41 | 59.941 | 0.034273 | 175.7 | 1149.3 |  | 17540 | 207.41 | 13.42 | 59.941 | 0.034273 | 175.7 | 1149.3 | 973.6
17541 | 13.423 | 207.42 | 59.941 | 0.034279 | 175.71 | 1149.3 |  | 17541 | 207.42 | 13.423 | 59.941 | 0.034279 | 175.71 | 1149.3 | 973.59
17542 | 13.426 | 207.43 | 59.941 | 0.034286 | 175.72 | 1149.3 |  | 17542 | 207.43 | 13.426 | 59.941 | 0.034286 | 175.72 | 1149.3 | 973.58
17543 | 13.428 | 207.44 | 59.94 | 0.034292 | 175.73 | 1149.3 |  | 17543 | 207.44 | 13.428 | 59.94 | 0.034292 | 175.73 | 1149.3 | 973.57
17544 | 13.431 | 207.45 | 59.94 | 0.034298 | 175.74 | 1149.3 |  | 17544 | 207.45 | 13.431 | 59.94 | 0.034298 | 175.74 | 1149.3 | 973.56
17545 | 13.434 | 207.46 | 59.94 | 0.034305 | 175.75 | 1149.3 |  | 17545 | 207.46 | 13.434 | 59.94 | 0.034305 | 175.75 | 1149.3 | 973.55
17546 | 13.437 | 207.47 | 59.94 | 0.034311 | 175.76 | 1149.3 |  | 17546 | 207.47 | 13.437 | 59.94 | 0.034311 | 175.76 | 1149.3 | 973.54
17547 | 13.439 | 207.48 | 59.939 | 0.034318 | 175.77 | 1149.3 |  | 17547 | 207.48 | 13.439 | 59.939 | 0.034318 | 175.77 | 1149.3 | 973.53
17548 | 13.442 | 207.49 | 59.939 | 0.034324 | 175.78 | 1149.3 |  | 17548 | 207.49 | 13.442 | 59.939 | 0.034324 | 175.78 | 1149.3 | 973.52
17549 | 13.445 | 207.5 | 59.939 | 0.034331 | 175.79 | 1149.4 |  | 17549 | 207.5 | 13.445 | 59.939 | 0.034331 | 175.79 | 1149.4 | 973.61
17550 | 13.447 | 207.51 | 59.939 | 0.034337 | 175.8 | 1149.4 |  | 17550 | 207.51 | 13.447 | 59.939 | 0.034337 | 175.8 | 1149.4 | 973.6
17551 | 13.45 | 207.52 | 59.938 | 0.034344 | 175.81 | 1149.4 |  | 17551 | 207.52 | 13.45 | 59.938 | 0.034344 | 175.81 | 1149.4 | 973.59
17552 | 13.453 | 207.53 | 59.938 | 0.03435 | 175.82 | 1149.4 |  | 17552 | 207.53 | 13.453 | 59.938 | 0.03435 | 175.82 | 1149.4 | 973.58
17553 | 13.455 | 207.54 | 59.938 | 0.034357 | 175.83 | 1149.4 |  | 17553 | 207.54 | 13.455 | 59.938 | 0.034357 | 175.83 | 1149.4 | 973.57
17554 | 13.458 | 207.55 | 59.938 | 0.034363 | 175.84 | 1149.4 |  | 17554 | 207.55 | 13.458 | 59.938 | 0.034363 | 175.84 | 1149.4 | 973.56
17555 | 13.461 | 207.56 | 59.937 | 0.03437 | 175.85 | 1149.4 |  | 17555 | 207.56 | 13.461 | 59.937 | 0.03437 | 175.85 | 1149.4 | 973.55
17556 | 13.464 | 207.57 | 59.937 | 0.034376 | 175.86 | 1149.4 |  | 17556 | 207.57 | 13.464 | 59.937 | 0.034376 | 175.86 | 1149.4 | 973.54
17557 | 13.466 | 207.58 | 59.937 | 0.034382 | 175.87 | 1149.4 |  | 17557 | 207.58 | 13.466 | 59.937 | 0.034382 | 175.87 | 1149.4 | 973.53
17558 | 13.469 | 207.59 | 59.937 | 0.034389 | 175.88 | 1149.4 |  | 17558 | 207.59 | 13.469 | 59.937 | 0.034389 | 175.88 | 1149.4 | 973.52
17559 | 13.472 | 207.6 | 59.936 | 0.034395 | 175.89 | 1149.4 |  | 17559 | 207.6 | 13.472 | 59.936 | 0.034395 | 175.89 | 1149.4 | 973.51
17560 | 13.474 | 207.61 | 59.936 | 0.034402 | 175.91 | 1149.4 |  | 17560 | 207.61 | 13.474 | 59.936 | 0.034402 | 175.91 | 1149.4 | 973.49
17561 | 13.477 | 207.62 | 59.936 | 0.034408 | 175.92 | 1149.4 |  | 17561 | 207.62 | 13.477 | 59.936 | 0.034408 | 175.92 | 1149.4 | 973.48
17562 | 13.48 | 207.63 | 59.936 | 0.034415 | 175.93 | 1149.4 |  | 17562 | 207.63 | 13.48 | 59.936 | 0.034415 | 175.93 | 1149.4 | 973.47
17563 | 13.483 | 207.64 | 59.935 | 0.034421 | 175.94 | 1149.4 |  | 17563 | 207.64 | 13.483 | 59.935 | 0.034421 | 175.94 | 1149.4 | 973.46
17564 | 13.485 | 207.65 | 59.935 | 0.034428 | 175.95 | 1149.4 |  | 17564 | 207.65 | 13.485 | 59.935 | 0.034428 | 175.95 | 1149.4 | 973.45
17565 | 13.488 | 207.66 | 59.935 | 0.034434 | 175.96 | 1149.4 |  | 17565 | 207.66 | 13.488 | 59.935 | 0.034434 | 175.96 | 1149.4 | 973.44
17566 | 13.491 | 207.67 | 59.935 | 0.034441 | 175.97 | 1149.4 |  | 17566 | 207.67 | 13.491 | 59.935 | 0.034441 | 175.97 | 1149.4 | 973.43
17567 | 13.493 | 207.68 | 59.934 | 0.034447 | 175.98 | 1149.4 |  | 17567 | 207.68 | 13.493 | 59.934 | 0.034447 | 175.98 | 1149.4 | 973.42
17568 | 13.496 | 207.69 | 59.934 | 0.034454 | 175.99 | 1149.4 |  | 17568 | 207.69 | 13.496 | 59.934 | 0.034454 | 175.99 | 1149.4 | 973.41
17569 | 13.499 | 207.7 | 59.934 | 0.03446 | 176 | 1149.4 |  | 17569 | 207.7 | 13.499 | 59.934 | 0.03446 | 176 | 1149.4 | 973.4
17570 | 13.502 | 207.71 | 59.934 | 0.034467 | 176.01 | 1149.4 |  | 17570 | 207.71 | 13.502 | 59.934 | 0.034467 | 176.01 | 1149.4 | 973.39
17571 | 13.504 | 207.72 | 59.934 | 0.034473 | 176.02 | 1149.4 |  | 17571 | 207.72 | 13.504 | 59.934 | 0.034473 | 176.02 | 1149.4 | 973.38
17572 | 13.507 | 207.73 | 59.933 | 0.03448 | 176.03 | 1149.4 |  | 17572 | 207.73 | 13.507 | 59.933 | 0.03448 | 176.03 | 1149.4 | 973.37
17573 | 13.51 | 207.74 | 59.933 | 0.034486 | 176.04 | 1149.4 |  | 17573 | 207.74 | 13.51 | 59.933 | 0.034486 | 176.04 | 1149.4 | 973.36
17574 | 13.512 | 207.75 | 59.933 | 0.034493 | 176.05 | 1149.4 |  | 17574 | 207.75 | 13.512 | 59.933 | 0.034493 | 176.05 | 1149.4 | 973.35
17575 | 13.515 | 207.76 | 59.933 | 0.034499 | 176.06 | 1149.5 |  | 17575 | 207.76 | 13.515 | 59.933 | 0.034499 | 176.06 | 1149.5 | 973.44
17576 | 13.518 | 207.77 | 59.932 | 0.034506 | 176.07 | 1149.5 |  | 17576 | 207.77 | 13.518 | 59.932 | 0.034506 | 176.07 | 1149.5 | 973.43
17577 | 13.521 | 207.78 | 59.932 | 0.034512 | 176.08 | 1149.5 |  | 17577 | 207.78 | 13.521 | 59.932 | 0.034512 | 176.08 | 1149.5 | 973.42
17578 | 13.523 | 207.79 | 59.932 | 0.034519 | 176.09 | 1149.5 |  | 17578 | 207.79 | 13.523 | 59.932 | 0.034519 | 176.09 | 1149.5 | 973.41
17579 | 13.526 | 207.8 | 59.932 | 0.034525 | 176.1 | 1149.5 |  | 17579 | 207.8 | 13.526 | 59.932 | 0.034525 | 176.1 | 1149.5 | 973.4
17580 | 13.529 | 207.81 | 59.931 | 0.034532 | 176.11 | 1149.5 |  | 17580 | 207.81 | 13.529 | 59.931 | 0.034532 | 176.11 | 1149.5 | 973.39
17581 | 13.532 | 207.82 | 59.931 | 0.034538 | 176.12 | 1149.5 |  | 17581 | 207.82 | 13.532 | 59.931 | 0.034538 | 176.12 | 1149.5 | 973.38
17582 | 13.534 | 207.83 | 59.931 | 0.034545 | 176.13 | 1149.5 |  | 17582 | 207.83 | 13.534 | 59.931 | 0.034545 | 176.13 | 1149.5 | 973.37
17583 | 13.537 | 207.84 | 59.931 | 0.034551 | 176.14 | 1149.5 |  | 17583 | 207.84 | 13.537 | 59.931 | 0.034551 | 176.14 | 1149.5 | 973.36
17584 | 13.54 | 207.85 | 59.93 | 0.034558 | 176.15 | 1149.5 |  | 17584 | 207.85 | 13.54 | 59.93 | 0.034558 | 176.15 | 1149.5 | 973.35
17585 | 13.542 | 207.86 | 59.93 | 0.034564 | 176.16 | 1149.5 |  | 17585 | 207.86 | 13.542 | 59.93 | 0.034564 | 176.16 | 1149.5 | 973.34
17586 | 13.545 | 207.87 | 59.93 | 0.034571 | 176.17 | 1149.5 |  | 17586 | 207.87 | 13.545 | 59.93 | 0.034571 | 176.17 | 1149.5 | 973.33
17587 | 13.548 | 207.88 | 59.93 | 0.034577 | 176.18 | 1149.5 |  | 17587 | 207.88 | 13.548 | 59.93 | 0.034577 | 176.18 | 1149.5 | 973.32
17588 | 13.551 | 207.89 | 59.929 | 0.034584 | 176.19 | 1149.5 |  | 17588 | 207.89 | 13.551 | 59.929 | 0.034584 | 176.19 | 1149.5 | 973.31
17589 | 13.553 | 207.9 | 59.929 | 0.03459 | 176.2 | 1149.5 |  | 17589 | 207.9 | 13.553 | 59.929 | 0.03459 | 176.2 | 1149.5 | 973.3
17590 | 13.556 | 207.91 | 59.929 | 0.034597 | 176.21 | 1149.5 |  | 17590 | 207.91 | 13.556 | 59.929 | 0.034597 | 176.21 | 1149.5 | 973.29
17591 | 13.559 | 207.92 | 59.929 | 0.034603 | 176.22 | 1149.5 |  | 17591 | 207.92 | 13.559 | 59.929 | 0.034603 | 176.22 | 1149.5 | 973.28
17592 | 13.561 | 207.93 | 59.928 | 0.03461 | 176.23 | 1149.5 |  | 17592 | 207.93 | 13.561 | 59.928 | 0.03461 | 176.23 | 1149.5 | 973.27
17593 | 13.564 | 207.94 | 59.928 | 0.034616 | 176.24 | 1149.5 |  | 17593 | 207.94 | 13.564 | 59.928 | 0.034616 | 176.24 | 1149.5 | 973.26
17594 | 13.567 | 207.95 | 59.928 | 0.034623 | 176.25 | 1149.5 |  | 17594 | 207.95 | 13.567 | 59.928 | 0.034623 | 176.25 | 1149.5 | 973.25
17595 | 13.57 | 207.96 | 59.928 | 0.034629 | 176.26 | 1149.5 |  | 17595 | 207.96 | 13.57 | 59.928 | 0.034629 | 176.26 | 1149.5 | 973.24
17596 | 13.572 | 207.97 | 59.927 | 0.034636 | 176.27 | 1149.5 |  | 17596 | 207.97 | 13.572 | 59.927 | 0.034636 | 176.27 | 1149.5 | 973.23
17597 | 13.575 | 207.98 | 59.927 | 0.034642 | 176.28 | 1149.5 |  | 17597 | 207.98 | 13.575 | 59.927 | 0.034642 | 176.28 | 1149.5 | 973.22
17598 | 13.578 | 207.99 | 59.927 | 0.034649 | 176.29 | 1149.5 |  | 17598 | 207.99 | 13.578 | 59.927 | 0.034649 | 176.29 | 1149.5 | 973.21
17599 | 13.581 | 208 | 59.927 | 0.034655 | 176.3 | 1149.5 |  | 17599 | 208 | 13.581 | 59.927 | 0.034655 | 176.3 | 1149.5 | 973.2
17600 | 13.583 | 208.01 | 59.926 | 0.034662 | 176.31 | 1149.5 |  | 17600 | 208.01 | 13.583 | 59.926 | 0.034662 | 176.31 | 1149.5 | 973.19
17601 | 13.586 | 208.02 | 59.926 | 0.034668 | 176.32 | 1149.6 |  | 17601 | 208.02 | 13.586 | 59.926 | 0.034668 | 176.32 | 1149.6 | 973.28
17602 | 13.589 | 208.03 | 59.926 | 0.034675 | 176.33 | 1149.6 |  | 17602 | 208.03 | 13.589 | 59.926 | 0.034675 | 176.33 | 1149.6 | 973.27
17603 | 13.591 | 208.04 | 59.926 | 0.034681 | 176.34 | 1149.6 |  | 17603 | 208.04 | 13.591 | 59.926 | 0.034681 | 176.34 | 1149.6 | 973.26
17604 | 13.594 | 208.05 | 59.925 | 0.034688 | 176.35 | 1149.6 |  | 17604 | 208.05 | 13.594 | 59.925 | 0.034688 | 176.35 | 1149.6 | 973.25
17605 | 13.597 | 208.06 | 59.925 | 0.034694 | 176.36 | 1149.6 |  | 17605 | 208.06 | 13.597 | 59.925 | 0.034694 | 176.36 | 1149.6 | 973.24
17606 | 13.6 | 208.07 | 59.925 | 0.034701 | 176.37 | 1149.6 |  | 17606 | 208.07 | 13.6 | 59.925 | 0.034701 | 176.37 | 1149.6 | 973.23
17607 | 13.602 | 208.08 | 59.925 | 0.034707 | 176.38 | 1149.6 |  | 17607 | 208.08 | 13.602 | 59.925 | 0.034707 | 176.38 | 1149.6 | 973.22
17608 | 13.605 | 208.09 | 59.924 | 0.034714 | 176.39 | 1149.6 |  | 17608 | 208.09 | 13.605 | 59.924 | 0.034714 | 176.39 | 1149.6 | 973.21
17609 | 13.608 | 208.1 | 59.924 | 0.03472 | 176.4 | 1149.6 |  | 17609 | 208.1 | 13.608 | 59.924 | 0.03472 | 176.4 | 1149.6 | 973.2
17610 | 13.611 | 208.11 | 59.924 | 0.034727 | 176.41 | 1149.6 |  | 17610 | 208.11 | 13.611 | 59.924 | 0.034727 | 176.41 | 1149.6 | 973.19
17611 | 13.613 | 208.12 | 59.924 | 0.034733 | 176.42 | 1149.6 |  | 17611 | 208.12 | 13.613 | 59.924 | 0.034733 | 176.42 | 1149.6 | 973.18
17612 | 13.616 | 208.13 | 59.923 | 0.03474 | 176.43 | 1149.6 |  | 17612 | 208.13 | 13.616 | 59.923 | 0.03474 | 176.43 | 1149.6 | 973.17
17613 | 13.619 | 208.14 | 59.923 | 0.034747 | 176.44 | 1149.6 |  | 17613 | 208.14 | 13.619 | 59.923 | 0.034747 | 176.44 | 1149.6 | 973.16
17614 | 13.622 | 208.15 | 59.923 | 0.034753 | 176.45 | 1149.6 |  | 17614 | 208.15 | 13.622 | 59.923 | 0.034753 | 176.45 | 1149.6 | 973.15
17615 | 13.624 | 208.16 | 59.923 | 0.03476 | 176.46 | 1149.6 |  | 17615 | 208.16 | 13.624 | 59.923 | 0.03476 | 176.46 | 1149.6 | 973.14
17616 | 13.627 | 208.17 | 59.922 | 0.034766 | 176.47 | 1149.6 |  | 17616 | 208.17 | 13.627 | 59.922 | 0.034766 | 176.47 | 1149.6 | 973.13
17617 | 13.63 | 208.18 | 59.922 | 0.034773 | 176.48 | 1149.6 |  | 17617 | 208.18 | 13.63 | 59.922 | 0.034773 | 176.48 | 1149.6 | 973.12
17618 | 13.633 | 208.19 | 59.922 | 0.034779 | 176.49 | 1149.6 |  | 17618 | 208.19 | 13.633 | 59.922 | 0.034779 | 176.49 | 1149.6 | 973.11
17619 | 13.635 | 208.2 | 59.922 | 0.034786 | 176.5 | 1149.6 |  | 17619 | 208.2 | 13.635 | 59.922 | 0.034786 | 176.5 | 1149.6 | 973.1
17620 | 13.638 | 208.21 | 59.921 | 0.034792 | 176.51 | 1149.6 |  | 17620 | 208.21 | 13.638 | 59.921 | 0.034792 | 176.51 | 1149.6 | 973.09
17621 | 13.641 | 208.22 | 59.921 | 0.034799 | 176.52 | 1149.6 |  | 17621 | 208.22 | 13.641 | 59.921 | 0.034799 | 176.52 | 1149.6 | 973.08
17622 | 13.643 | 208.23 | 59.921 | 0.034805 | 176.53 | 1149.6 |  | 17622 | 208.23 | 13.643 | 59.921 | 0.034805 | 176.53 | 1149.6 | 973.07
17623 | 13.646 | 208.24 | 59.921 | 0.034812 | 176.54 | 1149.6 |  | 17623 | 208.24 | 13.646 | 59.921 | 0.034812 | 176.54 | 1149.6 | 973.06
17624 | 13.649 | 208.25 | 59.92 | 0.034818 | 176.55 | 1149.6 |  | 17624 | 208.25 | 13.649 | 59.92 | 0.034818 | 176.55 | 1149.6 | 973.05
17625 | 13.652 | 208.26 | 59.92 | 0.034825 | 176.56 | 1149.6 |  | 17625 | 208.26 | 13.652 | 59.92 | 0.034825 | 176.56 | 1149.6 | 973.04
17626 | 13.654 | 208.27 | 59.92 | 0.034832 | 176.57 | 1149.6 |  | 17626 | 208.27 | 13.654 | 59.92 | 0.034832 | 176.57 | 1149.6 | 973.03
17627 | 13.657 | 208.28 | 59.92 | 0.034838 | 176.58 | 1149.6 |  | 17627 | 208.28 | 13.657 | 59.92 | 0.034838 | 176.58 | 1149.6 | 973.02
17628 | 13.66 | 208.29 | 59.92 | 0.034845 | 176.59 | 1149.7 |  | 17628 | 208.29 | 13.66 | 59.92 | 0.034845 | 176.59 | 1149.7 | 973.11
17629 | 13.663 | 208.3 | 59.919 | 0.034851 | 176.6 | 1149.7 |  | 17629 | 208.3 | 13.663 | 59.919 | 0.034851 | 176.6 | 1149.7 | 973.1
17630 | 13.665 | 208.31 | 59.919 | 0.034858 | 176.61 | 1149.7 |  | 17630 | 208.31 | 13.665 | 59.919 | 0.034858 | 176.61 | 1149.7 | 973.09
17631 | 13.668 | 208.32 | 59.919 | 0.034864 | 176.62 | 1149.7 |  | 17631 | 208.32 | 13.668 | 59.919 | 0.034864 | 176.62 | 1149.7 | 973.08
17632 | 13.671 | 208.33 | 59.919 | 0.034871 | 176.63 | 1149.7 |  | 17632 | 208.33 | 13.671 | 59.919 | 0.034871 | 176.63 | 1149.7 | 973.07
17633 | 13.674 | 208.34 | 59.918 | 0.034877 | 176.64 | 1149.7 |  | 17633 | 208.34 | 13.674 | 59.918 | 0.034877 | 176.64 | 1149.7 | 973.06
17634 | 13.676 | 208.35 | 59.918 | 0.034884 | 176.65 | 1149.7 |  | 17634 | 208.35 | 13.676 | 59.918 | 0.034884 | 176.65 | 1149.7 | 973.05
17635 | 13.679 | 208.36 | 59.918 | 0.03489 | 176.66 | 1149.7 |  | 17635 | 208.36 | 13.679 | 59.918 | 0.03489 | 176.66 | 1149.7 | 973.04
17636 | 13.682 | 208.37 | 59.918 | 0.034897 | 176.67 | 1149.7 |  | 17636 | 208.37 | 13.682 | 59.918 | 0.034897 | 176.67 | 1149.7 | 973.03
17637 | 13.685 | 208.38 | 59.917 | 0.034904 | 176.68 | 1149.7 |  | 17637 | 208.38 | 13.685 | 59.917 | 0.034904 | 176.68 | 1149.7 | 973.02
17638 | 13.687 | 208.39 | 59.917 | 0.03491 | 176.69 | 1149.7 |  | 17638 | 208.39 | 13.687 | 59.917 | 0.03491 | 176.69 | 1149.7 | 973.01
17639 | 13.69 | 208.4 | 59.917 | 0.034917 | 176.7 | 1149.7 |  | 17639 | 208.4 | 13.69 | 59.917 | 0.034917 | 176.7 | 1149.7 | 973
17640 | 13.693 | 208.41 | 59.917 | 0.034923 | 176.71 | 1149.7 |  | 17640 | 208.41 | 13.693 | 59.917 | 0.034923 | 176.71 | 1149.7 | 972.99
17641 | 13.696 | 208.42 | 59.916 | 0.03493 | 176.72 | 1149.7 |  | 17641 | 208.42 | 13.696 | 59.916 | 0.03493 | 176.72 | 1149.7 | 972.98
17642 | 13.698 | 208.43 | 59.916 | 0.034936 | 176.73 | 1149.7 |  | 17642 | 208.43 | 13.698 | 59.916 | 0.034936 | 176.73 | 1149.7 | 972.97
17643 | 13.701 | 208.44 | 59.916 | 0.034943 | 176.74 | 1149.7 |  | 17643 | 208.44 | 13.701 | 59.916 | 0.034943 | 176.74 | 1149.7 | 972.96
17644 | 13.704 | 208.45 | 59.916 | 0.034949 | 176.75 | 1149.7 |  | 17644 | 208.45 | 13.704 | 59.916 | 0.034949 | 176.75 | 1149.7 | 972.95
17645 | 13.707 | 208.46 | 59.915 | 0.034956 | 176.76 | 1149.7 |  | 17645 | 208.46 | 13.707 | 59.915 | 0.034956 | 176.76 | 1149.7 | 972.94
17646 | 13.709 | 208.47 | 59.915 | 0.034963 | 176.77 | 1149.7 |  | 17646 | 208.47 | 13.709 | 59.915 | 0.034963 | 176.77 | 1149.7 | 972.93
17647 | 13.712 | 208.48 | 59.915 | 0.034969 | 176.78 | 1149.7 |  | 17647 | 208.48 | 13.712 | 59.915 | 0.034969 | 176.78 | 1149.7 | 972.92
17648 | 13.715 | 208.49 | 59.915 | 0.034976 | 176.79 | 1149.7 |  | 17648 | 208.49 | 13.715 | 59.915 | 0.034976 | 176.79 | 1149.7 | 972.91
17649 | 13.718 | 208.5 | 59.914 | 0.034982 | 176.8 | 1149.7 |  | 17649 | 208.5 | 13.718 | 59.914 | 0.034982 | 176.8 | 1149.7 | 972.9
17650 | 13.72 | 208.51 | 59.914 | 0.034989 | 176.81 | 1149.7 |  | 17650 | 208.51 | 13.72 | 59.914 | 0.034989 | 176.81 | 1149.7 | 972.89
17651 | 13.723 | 208.52 | 59.914 | 0.034995 | 176.82 | 1149.7 |  | 17651 | 208.52 | 13.723 | 59.914 | 0.034995 | 176.82 | 1149.7 | 972.88
17652 | 13.726 | 208.53 | 59.914 | 0.035002 | 176.83 | 1149.7 |  | 17652 | 208.53 | 13.726 | 59.914 | 0.035002 | 176.83 | 1149.7 | 972.87
17653 | 13.729 | 208.54 | 59.913 | 0.035009 | 176.84 | 1149.7 |  | 17653 | 208.54 | 13.729 | 59.913 | 0.035009 | 176.84 | 1149.7 | 972.86
17654 | 13.731 | 208.55 | 59.913 | 0.035015 | 176.85 | 1149.8 |  | 17654 | 208.55 | 13.731 | 59.913 | 0.035015 | 176.85 | 1149.8 | 972.95
17655 | 13.734 | 208.56 | 59.913 | 0.035022 | 176.86 | 1149.8 |  | 17655 | 208.56 | 13.734 | 59.913 | 0.035022 | 176.86 | 1149.8 | 972.94
17656 | 13.737 | 208.57 | 59.913 | 0.035028 | 176.87 | 1149.8 |  | 17656 | 208.57 | 13.737 | 59.913 | 0.035028 | 176.87 | 1149.8 | 972.93
17657 | 13.74 | 208.58 | 59.912 | 0.035035 | 176.88 | 1149.8 |  | 17657 | 208.58 | 13.74 | 59.912 | 0.035035 | 176.88 | 1149.8 | 972.92
17658 | 13.742 | 208.59 | 59.912 | 0.035041 | 176.89 | 1149.8 |  | 17658 | 208.59 | 13.742 | 59.912 | 0.035041 | 176.89 | 1149.8 | 972.91
17659 | 13.745 | 208.6 | 59.912 | 0.035048 | 176.9 | 1149.8 |  | 17659 | 208.6 | 13.745 | 59.912 | 0.035048 | 176.9 | 1149.8 | 972.9
17660 | 13.748 | 208.61 | 59.912 | 0.035055 | 176.91 | 1149.8 |  | 17660 | 208.61 | 13.748 | 59.912 | 0.035055 | 176.91 | 1149.8 | 972.89
17661 | 13.751 | 208.62 | 59.911 | 0.035061 | 176.92 | 1149.8 |  | 17661 | 208.62 | 13.751 | 59.911 | 0.035061 | 176.92 | 1149.8 | 972.88
17662 | 13.753 | 208.63 | 59.911 | 0.035068 | 176.93 | 1149.8 |  | 17662 | 208.63 | 13.753 | 59.911 | 0.035068 | 176.93 | 1149.8 | 972.87
17663 | 13.756 | 208.64 | 59.911 | 0.035074 | 176.94 | 1149.8 |  | 17663 | 208.64 | 13.756 | 59.911 | 0.035074 | 176.94 | 1149.8 | 972.86
17664 | 13.759 | 208.65 | 59.911 | 0.035081 | 176.95 | 1149.8 |  | 17664 | 208.65 | 13.759 | 59.911 | 0.035081 | 176.95 | 1149.8 | 972.85
17665 | 13.762 | 208.66 | 59.91 | 0.035087 | 176.96 | 1149.8 |  | 17665 | 208.66 | 13.762 | 59.91 | 0.035087 | 176.96 | 1149.8 | 972.84
17666 | 13.764 | 208.67 | 59.91 | 0.035094 | 176.97 | 1149.8 |  | 17666 | 208.67 | 13.764 | 59.91 | 0.035094 | 176.97 | 1149.8 | 972.83
17667 | 13.767 | 208.68 | 59.91 | 0.035101 | 176.98 | 1149.8 |  | 17667 | 208.68 | 13.767 | 59.91 | 0.035101 | 176.98 | 1149.8 | 972.82
17668 | 13.77 | 208.69 | 59.91 | 0.035107 | 176.99 | 1149.8 |  | 17668 | 208.69 | 13.77 | 59.91 | 0.035107 | 176.99 | 1149.8 | 972.81
17669 | 13.773 | 208.7 | 59.909 | 0.035114 | 177 | 1149.8 |  | 17669 | 208.7 | 13.773 | 59.909 | 0.035114 | 177 | 1149.8 | 972.8
17670 | 13.776 | 208.71 | 59.909 | 0.03512 | 177.01 | 1149.8 |  | 17670 | 208.71 | 13.776 | 59.909 | 0.03512 | 177.01 | 1149.8 | 972.79
17671 | 13.778 | 208.72 | 59.909 | 0.035127 | 177.02 | 1149.8 |  | 17671 | 208.72 | 13.778 | 59.909 | 0.035127 | 177.02 | 1149.8 | 972.78
17672 | 13.781 | 208.73 | 59.909 | 0.035134 | 177.03 | 1149.8 |  | 17672 | 208.73 | 13.781 | 59.909 | 0.035134 | 177.03 | 1149.8 | 972.77
17673 | 13.784 | 208.74 | 59.908 | 0.03514 | 177.04 | 1149.8 |  | 17673 | 208.74 | 13.784 | 59.908 | 0.03514 | 177.04 | 1149.8 | 972.76
17674 | 13.787 | 208.75 | 59.908 | 0.035147 | 177.05 | 1149.8 |  | 17674 | 208.75 | 13.787 | 59.908 | 0.035147 | 177.05 | 1149.8 | 972.75
17675 | 13.789 | 208.76 | 59.908 | 0.035153 | 177.06 | 1149.8 |  | 17675 | 208.76 | 13.789 | 59.908 | 0.035153 | 177.06 | 1149.8 | 972.74
17676 | 13.792 | 208.77 | 59.908 | 0.03516 | 177.07 | 1149.8 |  | 17676 | 208.77 | 13.792 | 59.908 | 0.03516 | 177.07 | 1149.8 | 972.73
17677 | 13.795 | 208.78 | 59.907 | 0.035166 | 177.08 | 1149.8 |  | 17677 | 208.78 | 13.795 | 59.907 | 0.035166 | 177.08 | 1149.8 | 972.72
17678 | 13.798 | 208.79 | 59.907 | 0.035173 | 177.09 | 1149.8 |  | 17678 | 208.79 | 13.798 | 59.907 | 0.035173 | 177.09 | 1149.8 | 972.71
17679 | 13.8 | 208.8 | 59.907 | 0.03518 | 177.1 | 1149.8 |  | 17679 | 208.8 | 13.8 | 59.907 | 0.03518 | 177.1 | 1149.8 | 972.7
17680 | 13.803 | 208.81 | 59.907 | 0.035186 | 177.11 | 1149.9 |  | 17680 | 208.81 | 13.803 | 59.907 | 0.035186 | 177.11 | 1149.9 | 972.79
17681 | 13.806 | 208.82 | 59.906 | 0.035193 | 177.12 | 1149.9 |  | 17681 | 208.82 | 13.806 | 59.906 | 0.035193 | 177.12 | 1149.9 | 972.78
17682 | 13.809 | 208.83 | 59.906 | 0.035199 | 177.13 | 1149.9 |  | 17682 | 208.83 | 13.809 | 59.906 | 0.035199 | 177.13 | 1149.9 | 972.77
17683 | 13.811 | 208.84 | 59.906 | 0.035206 | 177.14 | 1149.9 |  | 17683 | 208.84 | 13.811 | 59.906 | 0.035206 | 177.14 | 1149.9 | 972.76
17684 | 13.814 | 208.85 | 59.906 | 0.035213 | 177.15 | 1149.9 |  | 17684 | 208.85 | 13.814 | 59.906 | 0.035213 | 177.15 | 1149.9 | 972.75
17685 | 13.817 | 208.86 | 59.905 | 0.035219 | 177.16 | 1149.9 |  | 17685 | 208.86 | 13.817 | 59.905 | 0.035219 | 177.16 | 1149.9 | 972.74
17686 | 13.82 | 208.87 | 59.905 | 0.035226 | 177.17 | 1149.9 |  | 17686 | 208.87 | 13.82 | 59.905 | 0.035226 | 177.17 | 1149.9 | 972.73
17687 | 13.823 | 208.88 | 59.905 | 0.035232 | 177.18 | 1149.9 |  | 17687 | 208.88 | 13.823 | 59.905 | 0.035232 | 177.18 | 1149.9 | 972.72
17688 | 13.825 | 208.89 | 59.905 | 0.035239 | 177.19 | 1149.9 |  | 17688 | 208.89 | 13.825 | 59.905 | 0.035239 | 177.19 | 1149.9 | 972.71
17689 | 13.828 | 208.9 | 59.905 | 0.035246 | 177.2 | 1149.9 |  | 17689 | 208.9 | 13.828 | 59.905 | 0.035246 | 177.2 | 1149.9 | 972.7
17690 | 13.831 | 208.91 | 59.904 | 0.035252 | 177.21 | 1149.9 |  | 17690 | 208.91 | 13.831 | 59.904 | 0.035252 | 177.21 | 1149.9 | 972.69
17691 | 13.834 | 208.92 | 59.904 | 0.035259 | 177.23 | 1149.9 |  | 17691 | 208.92 | 13.834 | 59.904 | 0.035259 | 177.23 | 1149.9 | 972.67
17692 | 13.836 | 208.93 | 59.904 | 0.035265 | 177.24 | 1149.9 |  | 17692 | 208.93 | 13.836 | 59.904 | 0.035265 | 177.24 | 1149.9 | 972.66
17693 | 13.839 | 208.94 | 59.904 | 0.035272 | 177.25 | 1149.9 |  | 17693 | 208.94 | 13.839 | 59.904 | 0.035272 | 177.25 | 1149.9 | 972.65
17694 | 13.842 | 208.95 | 59.903 | 0.035279 | 177.26 | 1149.9 |  | 17694 | 208.95 | 13.842 | 59.903 | 0.035279 | 177.26 | 1149.9 | 972.64
17695 | 13.845 | 208.96 | 59.903 | 0.035285 | 177.27 | 1149.9 |  | 17695 | 208.96 | 13.845 | 59.903 | 0.035285 | 177.27 | 1149.9 | 972.63
17696 | 13.847 | 208.97 | 59.903 | 0.035292 | 177.28 | 1149.9 |  | 17696 | 208.97 | 13.847 | 59.903 | 0.035292 | 177.28 | 1149.9 | 972.62
17697 | 13.85 | 208.98 | 59.903 | 0.035299 | 177.29 | 1149.9 |  | 17697 | 208.98 | 13.85 | 59.903 | 0.035299 | 177.29 | 1149.9 | 972.61
17698 | 13.853 | 208.99 | 59.902 | 0.035305 | 177.3 | 1149.9 |  | 17698 | 208.99 | 13.853 | 59.902 | 0.035305 | 177.3 | 1149.9 | 972.6
17699 | 13.856 | 209 | 59.902 | 0.035312 | 177.31 | 1149.9 |  | 17699 | 209 | 13.856 | 59.902 | 0.035312 | 177.31 | 1149.9 | 972.59
17700 | 13.859 | 209.01 | 59.902 | 0.035318 | 177.32 | 1149.9 |  | 17700 | 209.01 | 13.859 | 59.902 | 0.035318 | 177.32 | 1149.9 | 972.58
17701 | 13.861 | 209.02 | 59.902 | 0.035325 | 177.33 | 1149.9 |  | 17701 | 209.02 | 13.861 | 59.902 | 0.035325 | 177.33 | 1149.9 | 972.57
17702 | 13.864 | 209.03 | 59.901 | 0.035332 | 177.34 | 1149.9 |  | 17702 | 209.03 | 13.864 | 59.901 | 0.035332 | 177.34 | 1149.9 | 972.56
17703 | 13.867 | 209.04 | 59.901 | 0.035338 | 177.35 | 1149.9 |  | 17703 | 209.04 | 13.867 | 59.901 | 0.035338 | 177.35 | 1149.9 | 972.55
17704 | 13.87 | 209.05 | 59.901 | 0.035345 | 177.36 | 1149.9 |  | 17704 | 209.05 | 13.87 | 59.901 | 0.035345 | 177.36 | 1149.9 | 972.54
17705 | 13.872 | 209.06 | 59.901 | 0.035351 | 177.37 | 1149.9 |  | 17705 | 209.06 | 13.872 | 59.901 | 0.035351 | 177.37 | 1149.9 | 972.53
17706 | 13.875 | 209.07 | 59.9 | 0.035358 | 177.38 | 1149.9 |  | 17706 | 209.07 | 13.875 | 59.9 | 0.035358 | 177.38 | 1149.9 | 972.52
17707 | 13.878 | 209.08 | 59.9 | 0.035365 | 177.39 | 1150 |  | 17707 | 209.08 | 13.878 | 59.9 | 0.035365 | 177.39 | 1150 | 972.61
17708 | 13.881 | 209.09 | 59.9 | 0.035371 | 177.4 | 1150 |  | 17708 | 209.09 | 13.881 | 59.9 | 0.035371 | 177.4 | 1150 | 972.6
17709 | 13.884 | 209.1 | 59.9 | 0.035378 | 177.41 | 1150 |  | 17709 | 209.1 | 13.884 | 59.9 | 0.035378 | 177.41 | 1150 | 972.59
17710 | 13.886 | 209.11 | 59.899 | 0.035385 | 177.42 | 1150 |  | 17710 | 209.11 | 13.886 | 59.899 | 0.035385 | 177.42 | 1150 | 972.58
17711 | 13.889 | 209.12 | 59.899 | 0.035391 | 177.43 | 1150 |  | 17711 | 209.12 | 13.889 | 59.899 | 0.035391 | 177.43 | 1150 | 972.57
17712 | 13.892 | 209.13 | 59.899 | 0.035398 | 177.44 | 1150 |  | 17712 | 209.13 | 13.892 | 59.899 | 0.035398 | 177.44 | 1150 | 972.56
17713 | 13.895 | 209.14 | 59.899 | 0.035404 | 177.45 | 1150 |  | 17713 | 209.14 | 13.895 | 59.899 | 0.035404 | 177.45 | 1150 | 972.55
17714 | 13.897 | 209.15 | 59.898 | 0.035411 | 177.46 | 1150 |  | 17714 | 209.15 | 13.897 | 59.898 | 0.035411 | 177.46 | 1150 | 972.54
17715 | 13.9 | 209.16 | 59.898 | 0.035418 | 177.47 | 1150 |  | 17715 | 209.16 | 13.9 | 59.898 | 0.035418 | 177.47 | 1150 | 972.53
17716 | 13.903 | 209.17 | 59.898 | 0.035424 | 177.48 | 1150 |  | 17716 | 209.17 | 13.903 | 59.898 | 0.035424 | 177.48 | 1150 | 972.52
17717 | 13.906 | 209.18 | 59.898 | 0.035431 | 177.49 | 1150 |  | 17717 | 209.18 | 13.906 | 59.898 | 0.035431 | 177.49 | 1150 | 972.51
17718 | 13.909 | 209.19 | 59.897 | 0.035438 | 177.5 | 1150 |  | 17718 | 209.19 | 13.909 | 59.897 | 0.035438 | 177.5 | 1150 | 972.5
17719 | 13.911 | 209.2 | 59.897 | 0.035444 | 177.51 | 1150 |  | 17719 | 209.2 | 13.911 | 59.897 | 0.035444 | 177.51 | 1150 | 972.49
17720 | 13.914 | 209.21 | 59.897 | 0.035451 | 177.52 | 1150 |  | 17720 | 209.21 | 13.914 | 59.897 | 0.035451 | 177.52 | 1150 | 972.48
17721 | 13.917 | 209.22 | 59.897 | 0.035458 | 177.53 | 1150 |  | 17721 | 209.22 | 13.917 | 59.897 | 0.035458 | 177.53 | 1150 | 972.47
17722 | 13.92 | 209.23 | 59.896 | 0.035464 | 177.54 | 1150 |  | 17722 | 209.23 | 13.92 | 59.896 | 0.035464 | 177.54 | 1150 | 972.46
17723 | 13.923 | 209.24 | 59.896 | 0.035471 | 177.55 | 1150 |  | 17723 | 209.24 | 13.923 | 59.896 | 0.035471 | 177.55 | 1150 | 972.45
17724 | 13.925 | 209.25 | 59.896 | 0.035477 | 177.56 | 1150 |  | 17724 | 209.25 | 13.925 | 59.896 | 0.035477 | 177.56 | 1150 | 972.44
17725 | 13.928 | 209.26 | 59.896 | 0.035484 | 177.57 | 1150 |  | 17725 | 209.26 | 13.928 | 59.896 | 0.035484 | 177.57 | 1150 | 972.43
17726 | 13.931 | 209.27 | 59.895 | 0.035491 | 177.58 | 1150 |  | 17726 | 209.27 | 13.931 | 59.895 | 0.035491 | 177.58 | 1150 | 972.42
17727 | 13.934 | 209.28 | 59.895 | 0.035497 | 177.59 | 1150 |  | 17727 | 209.28 | 13.934 | 59.895 | 0.035497 | 177.59 | 1150 | 972.41
17728 | 13.936 | 209.29 | 59.895 | 0.035504 | 177.6 | 1150 |  | 17728 | 209.29 | 13.936 | 59.895 | 0.035504 | 177.6 | 1150 | 972.4
17729 | 13.939 | 209.3 | 59.895 | 0.035511 | 177.61 | 1150 |  | 17729 | 209.3 | 13.939 | 59.895 | 0.035511 | 177.61 | 1150 | 972.39
17730 | 13.942 | 209.31 | 59.894 | 0.035517 | 177.62 | 1150 |  | 17730 | 209.31 | 13.942 | 59.894 | 0.035517 | 177.62 | 1150 | 972.38
17731 | 13.945 | 209.32 | 59.894 | 0.035524 | 177.63 | 1150 |  | 17731 | 209.32 | 13.945 | 59.894 | 0.035524 | 177.63 | 1150 | 972.37
17732 | 13.948 | 209.33 | 59.894 | 0.035531 | 177.64 | 1150 |  | 17732 | 209.33 | 13.948 | 59.894 | 0.035531 | 177.64 | 1150 | 972.36
17733 | 13.95 | 209.34 | 59.894 | 0.035537 | 177.65 | 1150.1 |  | 17733 | 209.34 | 13.95 | 59.894 | 0.035537 | 177.65 | 1150.1 | 972.45
17734 | 13.953 | 209.35 | 59.893 | 0.035544 | 177.66 | 1150.1 |  | 17734 | 209.35 | 13.953 | 59.893 | 0.035544 | 177.66 | 1150.1 | 972.44
17735 | 13.956 | 209.36 | 59.893 | 0.035551 | 177.67 | 1150.1 |  | 17735 | 209.36 | 13.956 | 59.893 | 0.035551 | 177.67 | 1150.1 | 972.43
17736 | 13.959 | 209.37 | 59.893 | 0.035557 | 177.68 | 1150.1 |  | 17736 | 209.37 | 13.959 | 59.893 | 0.035557 | 177.68 | 1150.1 | 972.42
17737 | 13.962 | 209.38 | 59.893 | 0.035564 | 177.69 | 1150.1 |  | 17737 | 209.38 | 13.962 | 59.893 | 0.035564 | 177.69 | 1150.1 | 972.41
17738 | 13.964 | 209.39 | 59.892 | 0.035571 | 177.7 | 1150.1 |  | 17738 | 209.39 | 13.964 | 59.892 | 0.035571 | 177.7 | 1150.1 | 972.4
17739 | 13.967 | 209.4 | 59.892 | 0.035577 | 177.71 | 1150.1 |  | 17739 | 209.4 | 13.967 | 59.892 | 0.035577 | 177.71 | 1150.1 | 972.39
17740 | 13.97 | 209.41 | 59.892 | 0.035584 | 177.72 | 1150.1 |  | 17740 | 209.41 | 13.97 | 59.892 | 0.035584 | 177.72 | 1150.1 | 972.38
17741 | 13.973 | 209.42 | 59.892 | 0.035591 | 177.73 | 1150.1 |  | 17741 | 209.42 | 13.973 | 59.892 | 0.035591 | 177.73 | 1150.1 | 972.37
17742 | 13.976 | 209.43 | 59.891 | 0.035597 | 177.74 | 1150.1 |  | 17742 | 209.43 | 13.976 | 59.891 | 0.035597 | 177.74 | 1150.1 | 972.36
17743 | 13.978 | 209.44 | 59.891 | 0.035604 | 177.75 | 1150.1 |  | 17743 | 209.44 | 13.978 | 59.891 | 0.035604 | 177.75 | 1150.1 | 972.35
17744 | 13.981 | 209.45 | 59.891 | 0.03561 | 177.76 | 1150.1 |  | 17744 | 209.45 | 13.981 | 59.891 | 0.03561 | 177.76 | 1150.1 | 972.34
17745 | 13.984 | 209.46 | 59.891 | 0.035617 | 177.77 | 1150.1 |  | 17745 | 209.46 | 13.984 | 59.891 | 0.035617 | 177.77 | 1150.1 | 972.33
17746 | 13.987 | 209.47 | 59.89 | 0.035624 | 177.78 | 1150.1 |  | 17746 | 209.47 | 13.987 | 59.89 | 0.035624 | 177.78 | 1150.1 | 972.32
17747 | 13.99 | 209.48 | 59.89 | 0.03563 | 177.79 | 1150.1 |  | 17747 | 209.48 | 13.99 | 59.89 | 0.03563 | 177.79 | 1150.1 | 972.31
17748 | 13.992 | 209.49 | 59.89 | 0.035637 | 177.8 | 1150.1 |  | 17748 | 209.49 | 13.992 | 59.89 | 0.035637 | 177.8 | 1150.1 | 972.3
17749 | 13.995 | 209.5 | 59.89 | 0.035644 | 177.81 | 1150.1 |  | 17749 | 209.5 | 13.995 | 59.89 | 0.035644 | 177.81 | 1150.1 | 972.29
17750 | 13.998 | 209.51 | 59.889 | 0.03565 | 177.82 | 1150.1 |  | 17750 | 209.51 | 13.998 | 59.889 | 0.03565 | 177.82 | 1150.1 | 972.28
17751 | 14.001 | 209.52 | 59.889 | 0.035657 | 177.83 | 1150.1 |  | 17751 | 209.52 | 14.001 | 59.889 | 0.035657 | 177.83 | 1150.1 | 972.27
17752 | 14.004 | 209.53 | 59.889 | 0.035664 | 177.84 | 1150.1 |  | 17752 | 209.53 | 14.004 | 59.889 | 0.035664 | 177.84 | 1150.1 | 972.26
17753 | 14.006 | 209.54 | 59.889 | 0.03567 | 177.85 | 1150.1 |  | 17753 | 209.54 | 14.006 | 59.889 | 0.03567 | 177.85 | 1150.1 | 972.25
17754 | 14.009 | 209.55 | 59.888 | 0.035677 | 177.86 | 1150.1 |  | 17754 | 209.55 | 14.009 | 59.888 | 0.035677 | 177.86 | 1150.1 | 972.24
17755 | 14.012 | 209.56 | 59.888 | 0.035684 | 177.87 | 1150.1 |  | 17755 | 209.56 | 14.012 | 59.888 | 0.035684 | 177.87 | 1150.1 | 972.23
17756 | 14.015 | 209.57 | 59.888 | 0.03569 | 177.88 | 1150.1 |  | 17756 | 209.57 | 14.015 | 59.888 | 0.03569 | 177.88 | 1150.1 | 972.22
17757 | 14.018 | 209.58 | 59.888 | 0.035697 | 177.89 | 1150.1 |  | 17757 | 209.58 | 14.018 | 59.888 | 0.035697 | 177.89 | 1150.1 | 972.21
17758 | 14.02 | 209.59 | 59.888 | 0.035704 | 177.9 | 1150.1 |  | 17758 | 209.59 | 14.02 | 59.888 | 0.035704 | 177.9 | 1150.1 | 972.2
17759 | 14.023 | 209.6 | 59.887 | 0.035711 | 177.91 | 1150.2 |  | 17759 | 209.6 | 14.023 | 59.887 | 0.035711 | 177.91 | 1150.2 | 972.29
17760 | 14.026 | 209.61 | 59.887 | 0.035717 | 177.92 | 1150.2 |  | 17760 | 209.61 | 14.026 | 59.887 | 0.035717 | 177.92 | 1150.2 | 972.28
17761 | 14.029 | 209.62 | 59.887 | 0.035724 | 177.93 | 1150.2 |  | 17761 | 209.62 | 14.029 | 59.887 | 0.035724 | 177.93 | 1150.2 | 972.27
17762 | 14.032 | 209.63 | 59.887 | 0.035731 | 177.94 | 1150.2 |  | 17762 | 209.63 | 14.032 | 59.887 | 0.035731 | 177.94 | 1150.2 | 972.26
17763 | 14.034 | 209.64 | 59.886 | 0.035737 | 177.95 | 1150.2 |  | 17763 | 209.64 | 14.034 | 59.886 | 0.035737 | 177.95 | 1150.2 | 972.25
17764 | 14.037 | 209.65 | 59.886 | 0.035744 | 177.96 | 1150.2 |  | 17764 | 209.65 | 14.037 | 59.886 | 0.035744 | 177.96 | 1150.2 | 972.24
17765 | 14.04 | 209.66 | 59.886 | 0.035751 | 177.97 | 1150.2 |  | 17765 | 209.66 | 14.04 | 59.886 | 0.035751 | 177.97 | 1150.2 | 972.23
17766 | 14.043 | 209.67 | 59.886 | 0.035757 | 177.98 | 1150.2 |  | 17766 | 209.67 | 14.043 | 59.886 | 0.035757 | 177.98 | 1150.2 | 972.22
17767 | 14.046 | 209.68 | 59.885 | 0.035764 | 177.99 | 1150.2 |  | 17767 | 209.68 | 14.046 | 59.885 | 0.035764 | 177.99 | 1150.2 | 972.21
17768 | 14.048 | 209.69 | 59.885 | 0.035771 | 178 | 1150.2 |  | 17768 | 209.69 | 14.048 | 59.885 | 0.035771 | 178 | 1150.2 | 972.2
17769 | 14.051 | 209.7 | 59.885 | 0.035777 | 178.01 | 1150.2 |  | 17769 | 209.7 | 14.051 | 59.885 | 0.035777 | 178.01 | 1150.2 | 972.19
17770 | 14.054 | 209.71 | 59.885 | 0.035784 | 178.02 | 1150.2 |  | 17770 | 209.71 | 14.054 | 59.885 | 0.035784 | 178.02 | 1150.2 | 972.18
17771 | 14.057 | 209.72 | 59.884 | 0.035791 | 178.03 | 1150.2 |  | 17771 | 209.72 | 14.057 | 59.884 | 0.035791 | 178.03 | 1150.2 | 972.17
17772 | 14.06 | 209.73 | 59.884 | 0.035797 | 178.04 | 1150.2 |  | 17772 | 209.73 | 14.06 | 59.884 | 0.035797 | 178.04 | 1150.2 | 972.16
17773 | 14.062 | 209.74 | 59.884 | 0.035804 | 178.05 | 1150.2 |  | 17773 | 209.74 | 14.062 | 59.884 | 0.035804 | 178.05 | 1150.2 | 972.15
17774 | 14.065 | 209.75 | 59.884 | 0.035811 | 178.06 | 1150.2 |  | 17774 | 209.75 | 14.065 | 59.884 | 0.035811 | 178.06 | 1150.2 | 972.14
17775 | 14.068 | 209.76 | 59.883 | 0.035817 | 178.07 | 1150.2 |  | 17775 | 209.76 | 14.068 | 59.883 | 0.035817 | 178.07 | 1150.2 | 972.13
17776 | 14.071 | 209.77 | 59.883 | 0.035824 | 178.08 | 1150.2 |  | 17776 | 209.77 | 14.071 | 59.883 | 0.035824 | 178.08 | 1150.2 | 972.12
17777 | 14.074 | 209.78 | 59.883 | 0.035831 | 178.09 | 1150.2 |  | 17777 | 209.78 | 14.074 | 59.883 | 0.035831 | 178.09 | 1150.2 | 972.11
17778 | 14.077 | 209.79 | 59.883 | 0.035838 | 178.1 | 1150.2 |  | 17778 | 209.79 | 14.077 | 59.883 | 0.035838 | 178.1 | 1150.2 | 972.1
17779 | 14.079 | 209.8 | 59.882 | 0.035844 | 178.11 | 1150.2 |  | 17779 | 209.8 | 14.079 | 59.882 | 0.035844 | 178.11 | 1150.2 | 972.09
17780 | 14.082 | 209.81 | 59.882 | 0.035851 | 178.12 | 1150.2 |  | 17780 | 209.81 | 14.082 | 59.882 | 0.035851 | 178.12 | 1150.2 | 972.08
17781 | 14.085 | 209.82 | 59.882 | 0.035858 | 178.13 | 1150.2 |  | 17781 | 209.82 | 14.085 | 59.882 | 0.035858 | 178.13 | 1150.2 | 972.07
17782 | 14.088 | 209.83 | 59.882 | 0.035864 | 178.14 | 1150.2 |  | 17782 | 209.83 | 14.088 | 59.882 | 0.035864 | 178.14 | 1150.2 | 972.06
17783 | 14.091 | 209.84 | 59.881 | 0.035871 | 178.15 | 1150.2 |  | 17783 | 209.84 | 14.091 | 59.881 | 0.035871 | 178.15 | 1150.2 | 972.05
17784 | 14.093 | 209.85 | 59.881 | 0.035878 | 178.16 | 1150.2 |  | 17784 | 209.85 | 14.093 | 59.881 | 0.035878 | 178.16 | 1150.2 | 972.04
17785 | 14.096 | 209.86 | 59.881 | 0.035884 | 178.17 | 1150.2 |  | 17785 | 209.86 | 14.096 | 59.881 | 0.035884 | 178.17 | 1150.2 | 972.03
17786 | 14.099 | 209.87 | 59.881 | 0.035891 | 178.18 | 1150.3 |  | 17786 | 209.87 | 14.099 | 59.881 | 0.035891 | 178.18 | 1150.3 | 972.12
17787 | 14.102 | 209.88 | 59.88 | 0.035898 | 178.19 | 1150.3 |  | 17787 | 209.88 | 14.102 | 59.88 | 0.035898 | 178.19 | 1150.3 | 972.11
17788 | 14.105 | 209.89 | 59.88 | 0.035905 | 178.2 | 1150.3 |  | 17788 | 209.89 | 14.105 | 59.88 | 0.035905 | 178.2 | 1150.3 | 972.1
17789 | 14.107 | 209.9 | 59.88 | 0.035911 | 178.21 | 1150.3 |  | 17789 | 209.9 | 14.107 | 59.88 | 0.035911 | 178.21 | 1150.3 | 972.09
17790 | 14.11 | 209.91 | 59.88 | 0.035918 | 178.22 | 1150.3 |  | 17790 | 209.91 | 14.11 | 59.88 | 0.035918 | 178.22 | 1150.3 | 972.08
17791 | 14.113 | 209.92 | 59.879 | 0.035925 | 178.23 | 1150.3 |  | 17791 | 209.92 | 14.113 | 59.879 | 0.035925 | 178.23 | 1150.3 | 972.07
17792 | 14.116 | 209.93 | 59.879 | 0.035931 | 178.24 | 1150.3 |  | 17792 | 209.93 | 14.116 | 59.879 | 0.035931 | 178.24 | 1150.3 | 972.06
17793 | 14.119 | 209.94 | 59.879 | 0.035938 | 178.25 | 1150.3 |  | 17793 | 209.94 | 14.119 | 59.879 | 0.035938 | 178.25 | 1150.3 | 972.05
17794 | 14.122 | 209.95 | 59.879 | 0.035945 | 178.26 | 1150.3 |  | 17794 | 209.95 | 14.122 | 59.879 | 0.035945 | 178.26 | 1150.3 | 972.04
17795 | 14.124 | 209.96 | 59.878 | 0.035952 | 178.27 | 1150.3 |  | 17795 | 209.96 | 14.124 | 59.878 | 0.035952 | 178.27 | 1150.3 | 972.03
17796 | 14.127 | 209.97 | 59.878 | 0.035958 | 178.28 | 1150.3 |  | 17796 | 209.97 | 14.127 | 59.878 | 0.035958 | 178.28 | 1150.3 | 972.02
17797 | 14.13 | 209.98 | 59.878 | 0.035965 | 178.29 | 1150.3 |  | 17797 | 209.98 | 14.13 | 59.878 | 0.035965 | 178.29 | 1150.3 | 972.01
17798 | 14.133 | 209.99 | 59.878 | 0.035972 | 178.3 | 1150.3 |  | 17798 | 209.99 | 14.133 | 59.878 | 0.035972 | 178.3 | 1150.3 | 972
17799 | 14.136 | 210 | 59.877 | 0.035978 | 178.31 | 1150.3 |  | 17799 | 210 | 14.136 | 59.877 | 0.035978 | 178.31 | 1150.3 | 971.99
17800 | 14.138 | 210.01 | 59.877 | 0.035985 | 178.32 | 1150.3 |  | 17800 | 210.01 | 14.138 | 59.877 | 0.035985 | 178.32 | 1150.3 | 971.98
17801 | 14.141 | 210.02 | 59.877 | 0.035992 | 178.33 | 1150.3 |  | 17801 | 210.02 | 14.141 | 59.877 | 0.035992 | 178.33 | 1150.3 | 971.97
17802 | 14.144 | 210.03 | 59.877 | 0.035999 | 178.34 | 1150.3 |  | 17802 | 210.03 | 14.144 | 59.877 | 0.035999 | 178.34 | 1150.3 | 971.96
17803 | 14.147 | 210.04 | 59.876 | 0.036005 | 178.35 | 1150.3 |  | 17803 | 210.04 | 14.147 | 59.876 | 0.036005 | 178.35 | 1150.3 | 971.95
17804 | 14.15 | 210.05 | 59.876 | 0.036012 | 178.36 | 1150.3 |  | 17804 | 210.05 | 14.15 | 59.876 | 0.036012 | 178.36 | 1150.3 | 971.94
17805 | 14.153 | 210.06 | 59.876 | 0.036019 | 178.37 | 1150.3 |  | 17805 | 210.06 | 14.153 | 59.876 | 0.036019 | 178.37 | 1150.3 | 971.93
17806 | 14.155 | 210.07 | 59.876 | 0.036025 | 178.38 | 1150.3 |  | 17806 | 210.07 | 14.155 | 59.876 | 0.036025 | 178.38 | 1150.3 | 971.92
17807 | 14.158 | 210.08 | 59.875 | 0.036032 | 178.39 | 1150.3 |  | 17807 | 210.08 | 14.158 | 59.875 | 0.036032 | 178.39 | 1150.3 | 971.91
17808 | 14.161 | 210.09 | 59.875 | 0.036039 | 178.4 | 1150.3 |  | 17808 | 210.09 | 14.161 | 59.875 | 0.036039 | 178.4 | 1150.3 | 971.9
17809 | 14.164 | 210.1 | 59.875 | 0.036046 | 178.41 | 1150.3 |  | 17809 | 210.1 | 14.164 | 59.875 | 0.036046 | 178.41 | 1150.3 | 971.89
17810 | 14.167 | 210.11 | 59.875 | 0.036052 | 178.42 | 1150.3 |  | 17810 | 210.11 | 14.167 | 59.875 | 0.036052 | 178.42 | 1150.3 | 971.88
17811 | 14.17 | 210.12 | 59.874 | 0.036059 | 178.43 | 1150.3 |  | 17811 | 210.12 | 14.17 | 59.874 | 0.036059 | 178.43 | 1150.3 | 971.87
17812 | 14.172 | 210.13 | 59.874 | 0.036066 | 178.44 | 1150.4 |  | 17812 | 210.13 | 14.172 | 59.874 | 0.036066 | 178.44 | 1150.4 | 971.96
17813 | 14.175 | 210.14 | 59.874 | 0.036073 | 178.45 | 1150.4 |  | 17813 | 210.14 | 14.175 | 59.874 | 0.036073 | 178.45 | 1150.4 | 971.95
17814 | 14.178 | 210.15 | 59.874 | 0.036079 | 178.46 | 1150.4 |  | 17814 | 210.15 | 14.178 | 59.874 | 0.036079 | 178.46 | 1150.4 | 971.94
17815 | 14.181 | 210.16 | 59.873 | 0.036086 | 178.47 | 1150.4 |  | 17815 | 210.16 | 14.181 | 59.873 | 0.036086 | 178.47 | 1150.4 | 971.93
17816 | 14.184 | 210.17 | 59.873 | 0.036093 | 178.48 | 1150.4 |  | 17816 | 210.17 | 14.184 | 59.873 | 0.036093 | 178.48 | 1150.4 | 971.92
17817 | 14.187 | 210.18 | 59.873 | 0.036099 | 178.49 | 1150.4 |  | 17817 | 210.18 | 14.187 | 59.873 | 0.036099 | 178.49 | 1150.4 | 971.91
17818 | 14.189 | 210.19 | 59.873 | 0.036106 | 178.5 | 1150.4 |  | 17818 | 210.19 | 14.189 | 59.873 | 0.036106 | 178.5 | 1150.4 | 971.9
17819 | 14.192 | 210.2 | 59.872 | 0.036113 | 178.52 | 1150.4 |  | 17819 | 210.2 | 14.192 | 59.872 | 0.036113 | 178.52 | 1150.4 | 971.88
17820 | 14.195 | 210.21 | 59.872 | 0.03612 | 178.53 | 1150.4 |  | 17820 | 210.21 | 14.195 | 59.872 | 0.03612 | 178.53 | 1150.4 | 971.87
17821 | 14.198 | 210.22 | 59.872 | 0.036126 | 178.54 | 1150.4 |  | 17821 | 210.22 | 14.198 | 59.872 | 0.036126 | 178.54 | 1150.4 | 971.86
17822 | 14.201 | 210.23 | 59.872 | 0.036133 | 178.55 | 1150.4 |  | 17822 | 210.23 | 14.201 | 59.872 | 0.036133 | 178.55 | 1150.4 | 971.85
17823 | 14.204 | 210.24 | 59.871 | 0.03614 | 178.56 | 1150.4 |  | 17823 | 210.24 | 14.204 | 59.871 | 0.03614 | 178.56 | 1150.4 | 971.84
17824 | 14.206 | 210.25 | 59.871 | 0.036147 | 178.57 | 1150.4 |  | 17824 | 210.25 | 14.206 | 59.871 | 0.036147 | 178.57 | 1150.4 | 971.83
17825 | 14.209 | 210.26 | 59.871 | 0.036153 | 178.58 | 1150.4 |  | 17825 | 210.26 | 14.209 | 59.871 | 0.036153 | 178.58 | 1150.4 | 971.82
17826 | 14.212 | 210.27 | 59.871 | 0.03616 | 178.59 | 1150.4 |  | 17826 | 210.27 | 14.212 | 59.871 | 0.03616 | 178.59 | 1150.4 | 971.81
17827 | 14.215 | 210.28 | 59.87 | 0.036167 | 178.6 | 1150.4 |  | 17827 | 210.28 | 14.215 | 59.87 | 0.036167 | 178.6 | 1150.4 | 971.8
17828 | 14.218 | 210.29 | 59.87 | 0.036174 | 178.61 | 1150.4 |  | 17828 | 210.29 | 14.218 | 59.87 | 0.036174 | 178.61 | 1150.4 | 971.79
17829 | 14.221 | 210.3 | 59.87 | 0.03618 | 178.62 | 1150.4 |  | 17829 | 210.3 | 14.221 | 59.87 | 0.03618 | 178.62 | 1150.4 | 971.78
17830 | 14.223 | 210.31 | 59.87 | 0.036187 | 178.63 | 1150.4 |  | 17830 | 210.31 | 14.223 | 59.87 | 0.036187 | 178.63 | 1150.4 | 971.77
17831 | 14.226 | 210.32 | 59.869 | 0.036194 | 178.64 | 1150.4 |  | 17831 | 210.32 | 14.226 | 59.869 | 0.036194 | 178.64 | 1150.4 | 971.76
17832 | 14.229 | 210.33 | 59.869 | 0.036201 | 178.65 | 1150.4 |  | 17832 | 210.33 | 14.229 | 59.869 | 0.036201 | 178.65 | 1150.4 | 971.75
17833 | 14.232 | 210.34 | 59.869 | 0.036207 | 178.66 | 1150.4 |  | 17833 | 210.34 | 14.232 | 59.869 | 0.036207 | 178.66 | 1150.4 | 971.74
17834 | 14.235 | 210.35 | 59.869 | 0.036214 | 178.67 | 1150.4 |  | 17834 | 210.35 | 14.235 | 59.869 | 0.036214 | 178.67 | 1150.4 | 971.73
17835 | 14.238 | 210.36 | 59.868 | 0.036221 | 178.68 | 1150.4 |  | 17835 | 210.36 | 14.238 | 59.868 | 0.036221 | 178.68 | 1150.4 | 971.72
17836 | 14.24 | 210.37 | 59.868 | 0.036228 | 178.69 | 1150.4 |  | 17836 | 210.37 | 14.24 | 59.868 | 0.036228 | 178.69 | 1150.4 | 971.71
17837 | 14.243 | 210.38 | 59.868 | 0.036234 | 178.7 | 1150.4 |  | 17837 | 210.38 | 14.243 | 59.868 | 0.036234 | 178.7 | 1150.4 | 971.7
17838 | 14.246 | 210.39 | 59.868 | 0.036241 | 178.71 | 1150.4 |  | 17838 | 210.39 | 14.246 | 59.868 | 0.036241 | 178.71 | 1150.4 | 971.69
17839 | 14.249 | 210.4 | 59.867 | 0.036248 | 178.72 | 1150.5 |  | 17839 | 210.4 | 14.249 | 59.867 | 0.036248 | 178.72 | 1150.5 | 971.78
17840 | 14.252 | 210.41 | 59.867 | 0.036255 | 178.73 | 1150.5 |  | 17840 | 210.41 | 14.252 | 59.867 | 0.036255 | 178.73 | 1150.5 | 971.77
17841 | 14.255 | 210.42 | 59.867 | 0.036261 | 178.74 | 1150.5 |  | 17841 | 210.42 | 14.255 | 59.867 | 0.036261 | 178.74 | 1150.5 | 971.76
17842 | 14.257 | 210.43 | 59.867 | 0.036268 | 178.75 | 1150.5 |  | 17842 | 210.43 | 14.257 | 59.867 | 0.036268 | 178.75 | 1150.5 | 971.75
17843 | 14.26 | 210.44 | 59.866 | 0.036275 | 178.76 | 1150.5 |  | 17843 | 210.44 | 14.26 | 59.866 | 0.036275 | 178.76 | 1150.5 | 971.74
17844 | 14.263 | 210.45 | 59.866 | 0.036282 | 178.77 | 1150.5 |  | 17844 | 210.45 | 14.263 | 59.866 | 0.036282 | 178.77 | 1150.5 | 971.73
17845 | 14.266 | 210.46 | 59.866 | 0.036288 | 178.78 | 1150.5 |  | 17845 | 210.46 | 14.266 | 59.866 | 0.036288 | 178.78 | 1150.5 | 971.72
17846 | 14.269 | 210.47 | 59.866 | 0.036295 | 178.79 | 1150.5 |  | 17846 | 210.47 | 14.269 | 59.866 | 0.036295 | 178.79 | 1150.5 | 971.71
17847 | 14.272 | 210.48 | 59.866 | 0.036302 | 178.8 | 1150.5 |  | 17847 | 210.48 | 14.272 | 59.866 | 0.036302 | 178.8 | 1150.5 | 971.7
17848 | 14.274 | 210.49 | 59.865 | 0.036309 | 178.81 | 1150.5 |  | 17848 | 210.49 | 14.274 | 59.865 | 0.036309 | 178.81 | 1150.5 | 971.69
17849 | 14.277 | 210.5 | 59.865 | 0.036316 | 178.82 | 1150.5 |  | 17849 | 210.5 | 14.277 | 59.865 | 0.036316 | 178.82 | 1150.5 | 971.68
17850 | 14.28 | 210.51 | 59.865 | 0.036322 | 178.83 | 1150.5 |  | 17850 | 210.51 | 14.28 | 59.865 | 0.036322 | 178.83 | 1150.5 | 971.67
17851 | 14.283 | 210.52 | 59.865 | 0.036329 | 178.84 | 1150.5 |  | 17851 | 210.52 | 14.283 | 59.865 | 0.036329 | 178.84 | 1150.5 | 971.66
17852 | 14.286 | 210.53 | 59.864 | 0.036336 | 178.85 | 1150.5 |  | 17852 | 210.53 | 14.286 | 59.864 | 0.036336 | 178.85 | 1150.5 | 971.65
17853 | 14.289 | 210.54 | 59.864 | 0.036343 | 178.86 | 1150.5 |  | 17853 | 210.54 | 14.289 | 59.864 | 0.036343 | 178.86 | 1150.5 | 971.64
17854 | 14.292 | 210.55 | 59.864 | 0.036349 | 178.87 | 1150.5 |  | 17854 | 210.55 | 14.292 | 59.864 | 0.036349 | 178.87 | 1150.5 | 971.63
17855 | 14.294 | 210.56 | 59.864 | 0.036356 | 178.88 | 1150.5 |  | 17855 | 210.56 | 14.294 | 59.864 | 0.036356 | 178.88 | 1150.5 | 971.62
17856 | 14.297 | 210.57 | 59.863 | 0.036363 | 178.89 | 1150.5 |  | 17856 | 210.57 | 14.297 | 59.863 | 0.036363 | 178.89 | 1150.5 | 971.61
17857 | 14.3 | 210.58 | 59.863 | 0.03637 | 178.9 | 1150.5 |  | 17857 | 210.58 | 14.3 | 59.863 | 0.03637 | 178.9 | 1150.5 | 971.6
17858 | 14.303 | 210.59 | 59.863 | 0.036377 | 178.91 | 1150.5 |  | 17858 | 210.59 | 14.303 | 59.863 | 0.036377 | 178.91 | 1150.5 | 971.59
17859 | 14.306 | 210.6 | 59.863 | 0.036383 | 178.92 | 1150.5 |  | 17859 | 210.6 | 14.306 | 59.863 | 0.036383 | 178.92 | 1150.5 | 971.58
17860 | 14.309 | 210.61 | 59.862 | 0.03639 | 178.93 | 1150.5 |  | 17860 | 210.61 | 14.309 | 59.862 | 0.03639 | 178.93 | 1150.5 | 971.57
17861 | 14.312 | 210.62 | 59.862 | 0.036397 | 178.94 | 1150.5 |  | 17861 | 210.62 | 14.312 | 59.862 | 0.036397 | 178.94 | 1150.5 | 971.56
17862 | 14.314 | 210.63 | 59.862 | 0.036404 | 178.95 | 1150.5 |  | 17862 | 210.63 | 14.314 | 59.862 | 0.036404 | 178.95 | 1150.5 | 971.55
17863 | 14.317 | 210.64 | 59.862 | 0.03641 | 178.96 | 1150.5 |  | 17863 | 210.64 | 14.317 | 59.862 | 0.03641 | 178.96 | 1150.5 | 971.54
17864 | 14.32 | 210.65 | 59.861 | 0.036417 | 178.97 | 1150.5 |  | 17864 | 210.65 | 14.32 | 59.861 | 0.036417 | 178.97 | 1150.5 | 971.53
17865 | 14.323 | 210.66 | 59.861 | 0.036424 | 178.98 | 1150.6 |  | 17865 | 210.66 | 14.323 | 59.861 | 0.036424 | 178.98 | 1150.6 | 971.62
17866 | 14.326 | 210.67 | 59.861 | 0.036431 | 178.99 | 1150.6 |  | 17866 | 210.67 | 14.326 | 59.861 | 0.036431 | 178.99 | 1150.6 | 971.61
17867 | 14.329 | 210.68 | 59.861 | 0.036438 | 179 | 1150.6 |  | 17867 | 210.68 | 14.329 | 59.861 | 0.036438 | 179 | 1150.6 | 971.6
17868 | 14.331 | 210.69 | 59.86 | 0.036444 | 179.01 | 1150.6 |  | 17868 | 210.69 | 14.331 | 59.86 | 0.036444 | 179.01 | 1150.6 | 971.59
17869 | 14.334 | 210.7 | 59.86 | 0.036451 | 179.02 | 1150.6 |  | 17869 | 210.7 | 14.334 | 59.86 | 0.036451 | 179.02 | 1150.6 | 971.58
17870 | 14.337 | 210.71 | 59.86 | 0.036458 | 179.03 | 1150.6 |  | 17870 | 210.71 | 14.337 | 59.86 | 0.036458 | 179.03 | 1150.6 | 971.57
17871 | 14.34 | 210.72 | 59.86 | 0.036465 | 179.04 | 1150.6 |  | 17871 | 210.72 | 14.34 | 59.86 | 0.036465 | 179.04 | 1150.6 | 971.56
17872 | 14.343 | 210.73 | 59.859 | 0.036472 | 179.05 | 1150.6 |  | 17872 | 210.73 | 14.343 | 59.859 | 0.036472 | 179.05 | 1150.6 | 971.55
17873 | 14.346 | 210.74 | 59.859 | 0.036478 | 179.06 | 1150.6 |  | 17873 | 210.74 | 14.346 | 59.859 | 0.036478 | 179.06 | 1150.6 | 971.54
17874 | 14.349 | 210.75 | 59.859 | 0.036485 | 179.07 | 1150.6 |  | 17874 | 210.75 | 14.349 | 59.859 | 0.036485 | 179.07 | 1150.6 | 971.53
17875 | 14.351 | 210.76 | 59.859 | 0.036492 | 179.08 | 1150.6 |  | 17875 | 210.76 | 14.351 | 59.859 | 0.036492 | 179.08 | 1150.6 | 971.52
17876 | 14.354 | 210.77 | 59.858 | 0.036499 | 179.09 | 1150.6 |  | 17876 | 210.77 | 14.354 | 59.858 | 0.036499 | 179.09 | 1150.6 | 971.51
17877 | 14.357 | 210.78 | 59.858 | 0.036505 | 179.1 | 1150.6 |  | 17877 | 210.78 | 14.357 | 59.858 | 0.036505 | 179.1 | 1150.6 | 971.5
17878 | 14.36 | 210.79 | 59.858 | 0.036512 | 179.11 | 1150.6 |  | 17878 | 210.79 | 14.36 | 59.858 | 0.036512 | 179.11 | 1150.6 | 971.49
17879 | 14.363 | 210.8 | 59.858 | 0.036519 | 179.12 | 1150.6 |  | 17879 | 210.8 | 14.363 | 59.858 | 0.036519 | 179.12 | 1150.6 | 971.48
17880 | 14.366 | 210.81 | 59.857 | 0.036526 | 179.13 | 1150.6 |  | 17880 | 210.81 | 14.366 | 59.857 | 0.036526 | 179.13 | 1150.6 | 971.47
17881 | 14.369 | 210.82 | 59.857 | 0.036533 | 179.14 | 1150.6 |  | 17881 | 210.82 | 14.369 | 59.857 | 0.036533 | 179.14 | 1150.6 | 971.46
17882 | 14.371 | 210.83 | 59.857 | 0.036539 | 179.15 | 1150.6 |  | 17882 | 210.83 | 14.371 | 59.857 | 0.036539 | 179.15 | 1150.6 | 971.45
17883 | 14.374 | 210.84 | 59.857 | 0.036546 | 179.16 | 1150.6 |  | 17883 | 210.84 | 14.374 | 59.857 | 0.036546 | 179.16 | 1150.6 | 971.44
17884 | 14.377 | 210.85 | 59.856 | 0.036553 | 179.17 | 1150.6 |  | 17884 | 210.85 | 14.377 | 59.856 | 0.036553 | 179.17 | 1150.6 | 971.43
17885 | 14.38 | 210.86 | 59.856 | 0.03656 | 179.18 | 1150.6 |  | 17885 | 210.86 | 14.38 | 59.856 | 0.03656 | 179.18 | 1150.6 | 971.42
17886 | 14.383 | 210.87 | 59.856 | 0.036567 | 179.19 | 1150.6 |  | 17886 | 210.87 | 14.383 | 59.856 | 0.036567 | 179.19 | 1150.6 | 971.41
17887 | 14.386 | 210.88 | 59.856 | 0.036574 | 179.2 | 1150.6 |  | 17887 | 210.88 | 14.386 | 59.856 | 0.036574 | 179.2 | 1150.6 | 971.4
17888 | 14.389 | 210.89 | 59.855 | 0.03658 | 179.21 | 1150.6 |  | 17888 | 210.89 | 14.389 | 59.855 | 0.03658 | 179.21 | 1150.6 | 971.39
17889 | 14.392 | 210.9 | 59.855 | 0.036587 | 179.22 | 1150.6 |  | 17889 | 210.9 | 14.392 | 59.855 | 0.036587 | 179.22 | 1150.6 | 971.38
17890 | 14.394 | 210.91 | 59.855 | 0.036594 | 179.23 | 1150.6 |  | 17890 | 210.91 | 14.394 | 59.855 | 0.036594 | 179.23 | 1150.6 | 971.37
17891 | 14.397 | 210.92 | 59.855 | 0.036601 | 179.24 | 1150.7 |  | 17891 | 210.92 | 14.397 | 59.855 | 0.036601 | 179.24 | 1150.7 | 971.46
17892 | 14.4 | 210.93 | 59.854 | 0.036608 | 179.25 | 1150.7 |  | 17892 | 210.93 | 14.4 | 59.854 | 0.036608 | 179.25 | 1150.7 | 971.45
17893 | 14.403 | 210.94 | 59.854 | 0.036614 | 179.26 | 1150.7 |  | 17893 | 210.94 | 14.403 | 59.854 | 0.036614 | 179.26 | 1150.7 | 971.44
17894 | 14.406 | 210.95 | 59.854 | 0.036621 | 179.27 | 1150.7 |  | 17894 | 210.95 | 14.406 | 59.854 | 0.036621 | 179.27 | 1150.7 | 971.43
17895 | 14.409 | 210.96 | 59.854 | 0.036628 | 179.28 | 1150.7 |  | 17895 | 210.96 | 14.409 | 59.854 | 0.036628 | 179.28 | 1150.7 | 971.42
17896 | 14.412 | 210.97 | 59.853 | 0.036635 | 179.29 | 1150.7 |  | 17896 | 210.97 | 14.412 | 59.853 | 0.036635 | 179.29 | 1150.7 | 971.41
17897 | 14.414 | 210.98 | 59.853 | 0.036642 | 179.3 | 1150.7 |  | 17897 | 210.98 | 14.414 | 59.853 | 0.036642 | 179.3 | 1150.7 | 971.4
17898 | 14.417 | 210.99 | 59.853 | 0.036648 | 179.31 | 1150.7 |  | 17898 | 210.99 | 14.417 | 59.853 | 0.036648 | 179.31 | 1150.7 | 971.39
17899 | 14.42 | 211 | 59.853 | 0.036655 | 179.32 | 1150.7 |  | 17899 | 211 | 14.42 | 59.853 | 0.036655 | 179.32 | 1150.7 | 971.38
17900 | 14.423 | 211.01 | 59.852 | 0.036662 | 179.33 | 1150.7 |  | 17900 | 211.01 | 14.423 | 59.852 | 0.036662 | 179.33 | 1150.7 | 971.37
17901 | 14.426 | 211.02 | 59.852 | 0.036669 | 179.34 | 1150.7 |  | 17901 | 211.02 | 14.426 | 59.852 | 0.036669 | 179.34 | 1150.7 | 971.36
17902 | 14.429 | 211.03 | 59.852 | 0.036676 | 179.35 | 1150.7 |  | 17902 | 211.03 | 14.429 | 59.852 | 0.036676 | 179.35 | 1150.7 | 971.35
17903 | 14.432 | 211.04 | 59.852 | 0.036683 | 179.36 | 1150.7 |  | 17903 | 211.04 | 14.432 | 59.852 | 0.036683 | 179.36 | 1150.7 | 971.34
17904 | 14.435 | 211.05 | 59.851 | 0.036689 | 179.37 | 1150.7 |  | 17904 | 211.05 | 14.435 | 59.851 | 0.036689 | 179.37 | 1150.7 | 971.33
17905 | 14.437 | 211.06 | 59.851 | 0.036696 | 179.38 | 1150.7 |  | 17905 | 211.06 | 14.437 | 59.851 | 0.036696 | 179.38 | 1150.7 | 971.32
17906 | 14.44 | 211.07 | 59.851 | 0.036703 | 179.39 | 1150.7 |  | 17906 | 211.07 | 14.44 | 59.851 | 0.036703 | 179.39 | 1150.7 | 971.31
17907 | 14.443 | 211.08 | 59.851 | 0.03671 | 179.4 | 1150.7 |  | 17907 | 211.08 | 14.443 | 59.851 | 0.03671 | 179.4 | 1150.7 | 971.3
17908 | 14.446 | 211.09 | 59.85 | 0.036717 | 179.41 | 1150.7 |  | 17908 | 211.09 | 14.446 | 59.85 | 0.036717 | 179.41 | 1150.7 | 971.29
17909 | 14.449 | 211.1 | 59.85 | 0.036724 | 179.42 | 1150.7 |  | 17909 | 211.1 | 14.449 | 59.85 | 0.036724 | 179.42 | 1150.7 | 971.28
17910 | 14.452 | 211.11 | 59.85 | 0.03673 | 179.43 | 1150.7 |  | 17910 | 211.11 | 14.452 | 59.85 | 0.03673 | 179.43 | 1150.7 | 971.27
17911 | 14.455 | 211.12 | 59.85 | 0.036737 | 179.44 | 1150.7 |  | 17911 | 211.12 | 14.455 | 59.85 | 0.036737 | 179.44 | 1150.7 | 971.26
17912 | 14.458 | 211.13 | 59.849 | 0.036744 | 179.45 | 1150.7 |  | 17912 | 211.13 | 14.458 | 59.849 | 0.036744 | 179.45 | 1150.7 | 971.25
17913 | 14.46 | 211.14 | 59.849 | 0.036751 | 179.46 | 1150.7 |  | 17913 | 211.14 | 14.46 | 59.849 | 0.036751 | 179.46 | 1150.7 | 971.24
17914 | 14.463 | 211.15 | 59.849 | 0.036758 | 179.47 | 1150.7 |  | 17914 | 211.15 | 14.463 | 59.849 | 0.036758 | 179.47 | 1150.7 | 971.23
17915 | 14.466 | 211.16 | 59.849 | 0.036765 | 179.48 | 1150.7 |  | 17915 | 211.16 | 14.466 | 59.849 | 0.036765 | 179.48 | 1150.7 | 971.22
17916 | 14.469 | 211.17 | 59.848 | 0.036771 | 179.49 | 1150.7 |  | 17916 | 211.17 | 14.469 | 59.848 | 0.036771 | 179.49 | 1150.7 | 971.21
17917 | 14.472 | 211.18 | 59.848 | 0.036778 | 179.5 | 1150.7 |  | 17917 | 211.18 | 14.472 | 59.848 | 0.036778 | 179.5 | 1150.7 | 971.2
17918 | 14.475 | 211.19 | 59.848 | 0.036785 | 179.51 | 1150.8 |  | 17918 | 211.19 | 14.475 | 59.848 | 0.036785 | 179.51 | 1150.8 | 971.29
17919 | 14.478 | 211.2 | 59.848 | 0.036792 | 179.52 | 1150.8 |  | 17919 | 211.2 | 14.478 | 59.848 | 0.036792 | 179.52 | 1150.8 | 971.28
17920 | 14.481 | 211.21 | 59.847 | 0.036799 | 179.53 | 1150.8 |  | 17920 | 211.21 | 14.481 | 59.847 | 0.036799 | 179.53 | 1150.8 | 971.27
17921 | 14.483 | 211.22 | 59.847 | 0.036806 | 179.54 | 1150.8 |  | 17921 | 211.22 | 14.483 | 59.847 | 0.036806 | 179.54 | 1150.8 | 971.26
17922 | 14.486 | 211.23 | 59.847 | 0.036812 | 179.55 | 1150.8 |  | 17922 | 211.23 | 14.486 | 59.847 | 0.036812 | 179.55 | 1150.8 | 971.25
17923 | 14.489 | 211.24 | 59.847 | 0.036819 | 179.56 | 1150.8 |  | 17923 | 211.24 | 14.489 | 59.847 | 0.036819 | 179.56 | 1150.8 | 971.24
17924 | 14.492 | 211.25 | 59.846 | 0.036826 | 179.57 | 1150.8 |  | 17924 | 211.25 | 14.492 | 59.846 | 0.036826 | 179.57 | 1150.8 | 971.23
17925 | 14.495 | 211.26 | 59.846 | 0.036833 | 179.58 | 1150.8 |  | 17925 | 211.26 | 14.495 | 59.846 | 0.036833 | 179.58 | 1150.8 | 971.22
17926 | 14.498 | 211.27 | 59.846 | 0.03684 | 179.59 | 1150.8 |  | 17926 | 211.27 | 14.498 | 59.846 | 0.03684 | 179.59 | 1150.8 | 971.21
17927 | 14.501 | 211.28 | 59.846 | 0.036847 | 179.6 | 1150.8 |  | 17927 | 211.28 | 14.501 | 59.846 | 0.036847 | 179.6 | 1150.8 | 971.2
17928 | 14.504 | 211.29 | 59.845 | 0.036854 | 179.61 | 1150.8 |  | 17928 | 211.29 | 14.504 | 59.845 | 0.036854 | 179.61 | 1150.8 | 971.19
17929 | 14.506 | 211.3 | 59.845 | 0.03686 | 179.62 | 1150.8 |  | 17929 | 211.3 | 14.506 | 59.845 | 0.03686 | 179.62 | 1150.8 | 971.18
17930 | 14.509 | 211.31 | 59.845 | 0.036867 | 179.63 | 1150.8 |  | 17930 | 211.31 | 14.509 | 59.845 | 0.036867 | 179.63 | 1150.8 | 971.17
17931 | 14.512 | 211.32 | 59.845 | 0.036874 | 179.64 | 1150.8 |  | 17931 | 211.32 | 14.512 | 59.845 | 0.036874 | 179.64 | 1150.8 | 971.16
17932 | 14.515 | 211.33 | 59.844 | 0.036881 | 179.65 | 1150.8 |  | 17932 | 211.33 | 14.515 | 59.844 | 0.036881 | 179.65 | 1150.8 | 971.15
17933 | 14.518 | 211.34 | 59.844 | 0.036888 | 179.66 | 1150.8 |  | 17933 | 211.34 | 14.518 | 59.844 | 0.036888 | 179.66 | 1150.8 | 971.14
17934 | 14.521 | 211.35 | 59.844 | 0.036895 | 179.67 | 1150.8 |  | 17934 | 211.35 | 14.521 | 59.844 | 0.036895 | 179.67 | 1150.8 | 971.13
17935 | 14.524 | 211.36 | 59.844 | 0.036901 | 179.68 | 1150.8 |  | 17935 | 211.36 | 14.524 | 59.844 | 0.036901 | 179.68 | 1150.8 | 971.12
17936 | 14.527 | 211.37 | 59.843 | 0.036908 | 179.69 | 1150.8 |  | 17936 | 211.37 | 14.527 | 59.843 | 0.036908 | 179.69 | 1150.8 | 971.11
17937 | 14.53 | 211.38 | 59.843 | 0.036915 | 179.7 | 1150.8 |  | 17937 | 211.38 | 14.53 | 59.843 | 0.036915 | 179.7 | 1150.8 | 971.1
17938 | 14.532 | 211.39 | 59.843 | 0.036922 | 179.71 | 1150.8 |  | 17938 | 211.39 | 14.532 | 59.843 | 0.036922 | 179.71 | 1150.8 | 971.09
17939 | 14.535 | 211.4 | 59.843 | 0.036929 | 179.72 | 1150.8 |  | 17939 | 211.4 | 14.535 | 59.843 | 0.036929 | 179.72 | 1150.8 | 971.08
17940 | 14.538 | 211.41 | 59.842 | 0.036936 | 179.73 | 1150.8 |  | 17940 | 211.41 | 14.538 | 59.842 | 0.036936 | 179.73 | 1150.8 | 971.07
17941 | 14.541 | 211.42 | 59.842 | 0.036943 | 179.74 | 1150.8 |  | 17941 | 211.42 | 14.541 | 59.842 | 0.036943 | 179.74 | 1150.8 | 971.06
17942 | 14.544 | 211.43 | 59.842 | 0.03695 | 179.75 | 1150.8 |  | 17942 | 211.43 | 14.544 | 59.842 | 0.03695 | 179.75 | 1150.8 | 971.05
17943 | 14.547 | 211.44 | 59.842 | 0.036956 | 179.77 | 1150.8 |  | 17943 | 211.44 | 14.547 | 59.842 | 0.036956 | 179.77 | 1150.8 | 971.03
17944 | 14.55 | 211.45 | 59.841 | 0.036963 | 179.78 | 1150.9 |  | 17944 | 211.45 | 14.55 | 59.841 | 0.036963 | 179.78 | 1150.9 | 971.12
17945 | 14.553 | 211.46 | 59.841 | 0.03697 | 179.79 | 1150.9 |  | 17945 | 211.46 | 14.553 | 59.841 | 0.03697 | 179.79 | 1150.9 | 971.11
17946 | 14.556 | 211.47 | 59.841 | 0.036977 | 179.8 | 1150.9 |  | 17946 | 211.47 | 14.556 | 59.841 | 0.036977 | 179.8 | 1150.9 | 971.1
17947 | 14.558 | 211.48 | 59.841 | 0.036984 | 179.81 | 1150.9 |  | 17947 | 211.48 | 14.558 | 59.841 | 0.036984 | 179.81 | 1150.9 | 971.09
17948 | 14.561 | 211.49 | 59.84 | 0.036991 | 179.82 | 1150.9 |  | 17948 | 211.49 | 14.561 | 59.84 | 0.036991 | 179.82 | 1150.9 | 971.08
17949 | 14.564 | 211.5 | 59.84 | 0.036998 | 179.83 | 1150.9 |  | 17949 | 211.5 | 14.564 | 59.84 | 0.036998 | 179.83 | 1150.9 | 971.07
17950 | 14.567 | 211.51 | 59.84 | 0.037004 | 179.84 | 1150.9 |  | 17950 | 211.51 | 14.567 | 59.84 | 0.037004 | 179.84 | 1150.9 | 971.06
17951 | 14.57 | 211.52 | 59.84 | 0.037011 | 179.85 | 1150.9 |  | 17951 | 211.52 | 14.57 | 59.84 | 0.037011 | 179.85 | 1150.9 | 971.05
17952 | 14.573 | 211.53 | 59.839 | 0.037018 | 179.86 | 1150.9 |  | 17952 | 211.53 | 14.573 | 59.839 | 0.037018 | 179.86 | 1150.9 | 971.04
17953 | 14.576 | 211.54 | 59.839 | 0.037025 | 179.87 | 1150.9 |  | 17953 | 211.54 | 14.576 | 59.839 | 0.037025 | 179.87 | 1150.9 | 971.03
17954 | 14.579 | 211.55 | 59.839 | 0.037032 | 179.88 | 1150.9 |  | 17954 | 211.55 | 14.579 | 59.839 | 0.037032 | 179.88 | 1150.9 | 971.02
17955 | 14.582 | 211.56 | 59.839 | 0.037039 | 179.89 | 1150.9 |  | 17955 | 211.56 | 14.582 | 59.839 | 0.037039 | 179.89 | 1150.9 | 971.01
17956 | 14.584 | 211.57 | 59.838 | 0.037046 | 179.9 | 1150.9 |  | 17956 | 211.57 | 14.584 | 59.838 | 0.037046 | 179.9 | 1150.9 | 971
17957 | 14.587 | 211.58 | 59.838 | 0.037053 | 179.91 | 1150.9 |  | 17957 | 211.58 | 14.587 | 59.838 | 0.037053 | 179.91 | 1150.9 | 970.99
17958 | 14.59 | 211.59 | 59.838 | 0.037059 | 179.92 | 1150.9 |  | 17958 | 211.59 | 14.59 | 59.838 | 0.037059 | 179.92 | 1150.9 | 970.98
17959 | 14.593 | 211.6 | 59.838 | 0.037066 | 179.93 | 1150.9 |  | 17959 | 211.6 | 14.593 | 59.838 | 0.037066 | 179.93 | 1150.9 | 970.97
17960 | 14.596 | 211.61 | 59.837 | 0.037073 | 179.94 | 1150.9 |  | 17960 | 211.61 | 14.596 | 59.837 | 0.037073 | 179.94 | 1150.9 | 970.96
17961 | 14.599 | 211.62 | 59.837 | 0.03708 | 179.95 | 1150.9 |  | 17961 | 211.62 | 14.599 | 59.837 | 0.03708 | 179.95 | 1150.9 | 970.95
17962 | 14.602 | 211.63 | 59.837 | 0.037087 | 179.96 | 1150.9 |  | 17962 | 211.63 | 14.602 | 59.837 | 0.037087 | 179.96 | 1150.9 | 970.94
17963 | 14.605 | 211.64 | 59.837 | 0.037094 | 179.97 | 1150.9 |  | 17963 | 211.64 | 14.605 | 59.837 | 0.037094 | 179.97 | 1150.9 | 970.93
17964 | 14.608 | 211.65 | 59.836 | 0.037101 | 179.98 | 1150.9 |  | 17964 | 211.65 | 14.608 | 59.836 | 0.037101 | 179.98 | 1150.9 | 970.92
17965 | 14.611 | 211.66 | 59.836 | 0.037108 | 179.99 | 1150.9 |  | 17965 | 211.66 | 14.611 | 59.836 | 0.037108 | 179.99 | 1150.9 | 970.91
17966 | 14.613 | 211.67 | 59.836 | 0.037115 | 180 | 1150.9 |  | 17966 | 211.67 | 14.613 | 59.836 | 0.037115 | 180 | 1150.9 | 970.9
17967 | 14.616 | 211.68 | 59.836 | 0.037121 | 180.01 | 1150.9 |  | 17967 | 211.68 | 14.616 | 59.836 | 0.037121 | 180.01 | 1150.9 | 970.89
17968 | 14.619 | 211.69 | 59.835 | 0.037128 | 180.02 | 1150.9 |  | 17968 | 211.69 | 14.619 | 59.835 | 0.037128 | 180.02 | 1150.9 | 970.88
17969 | 14.622 | 211.7 | 59.835 | 0.037135 | 180.03 | 1150.9 |  | 17969 | 211.7 | 14.622 | 59.835 | 0.037135 | 180.03 | 1150.9 | 970.87
17970 | 14.625 | 211.71 | 59.835 | 0.037142 | 180.04 | 1150.9 |  | 17970 | 211.71 | 14.625 | 59.835 | 0.037142 | 180.04 | 1150.9 | 970.86
17971 | 14.628 | 211.72 | 59.835 | 0.037149 | 180.05 | 1151 |  | 17971 | 211.72 | 14.628 | 59.835 | 0.037149 | 180.05 | 1151 | 970.95
17972 | 14.631 | 211.73 | 59.834 | 0.037156 | 180.06 | 1151 |  | 17972 | 211.73 | 14.631 | 59.834 | 0.037156 | 180.06 | 1151 | 970.94
17973 | 14.634 | 211.74 | 59.834 | 0.037163 | 180.07 | 1151 |  | 17973 | 211.74 | 14.634 | 59.834 | 0.037163 | 180.07 | 1151 | 970.93
17974 | 14.637 | 211.75 | 59.834 | 0.03717 | 180.08 | 1151 |  | 17974 | 211.75 | 14.637 | 59.834 | 0.03717 | 180.08 | 1151 | 970.92
17975 | 14.64 | 211.76 | 59.834 | 0.037177 | 180.09 | 1151 |  | 17975 | 211.76 | 14.64 | 59.834 | 0.037177 | 180.09 | 1151 | 970.91
17976 | 14.642 | 211.77 | 59.833 | 0.037184 | 180.1 | 1151 |  | 17976 | 211.77 | 14.642 | 59.833 | 0.037184 | 180.1 | 1151 | 970.9
17977 | 14.645 | 211.78 | 59.833 | 0.03719 | 180.11 | 1151 |  | 17977 | 211.78 | 14.645 | 59.833 | 0.03719 | 180.11 | 1151 | 970.89
17978 | 14.648 | 211.79 | 59.833 | 0.037197 | 180.12 | 1151 |  | 17978 | 211.79 | 14.648 | 59.833 | 0.037197 | 180.12 | 1151 | 970.88
17979 | 14.651 | 211.8 | 59.833 | 0.037204 | 180.13 | 1151 |  | 17979 | 211.8 | 14.651 | 59.833 | 0.037204 | 180.13 | 1151 | 970.87
17980 | 14.654 | 211.81 | 59.833 | 0.037211 | 180.14 | 1151 |  | 17980 | 211.81 | 14.654 | 59.833 | 0.037211 | 180.14 | 1151 | 970.86
17981 | 14.657 | 211.82 | 59.832 | 0.037218 | 180.15 | 1151 |  | 17981 | 211.82 | 14.657 | 59.832 | 0.037218 | 180.15 | 1151 | 970.85
17982 | 14.66 | 211.83 | 59.832 | 0.037225 | 180.16 | 1151 |  | 17982 | 211.83 | 14.66 | 59.832 | 0.037225 | 180.16 | 1151 | 970.84
17983 | 14.663 | 211.84 | 59.832 | 0.037232 | 180.17 | 1151 |  | 17983 | 211.84 | 14.663 | 59.832 | 0.037232 | 180.17 | 1151 | 970.83
17984 | 14.666 | 211.85 | 59.832 | 0.037239 | 180.18 | 1151 |  | 17984 | 211.85 | 14.666 | 59.832 | 0.037239 | 180.18 | 1151 | 970.82
17985 | 14.669 | 211.86 | 59.831 | 0.037246 | 180.19 | 1151 |  | 17985 | 211.86 | 14.669 | 59.831 | 0.037246 | 180.19 | 1151 | 970.81
17986 | 14.672 | 211.87 | 59.831 | 0.037253 | 180.2 | 1151 |  | 17986 | 211.87 | 14.672 | 59.831 | 0.037253 | 180.2 | 1151 | 970.8
17987 | 14.674 | 211.88 | 59.831 | 0.03726 | 180.21 | 1151 |  | 17987 | 211.88 | 14.674 | 59.831 | 0.03726 | 180.21 | 1151 | 970.79
17988 | 14.677 | 211.89 | 59.831 | 0.037266 | 180.22 | 1151 |  | 17988 | 211.89 | 14.677 | 59.831 | 0.037266 | 180.22 | 1151 | 970.78
17989 | 14.68 | 211.9 | 59.83 | 0.037273 | 180.23 | 1151 |  | 17989 | 211.9 | 14.68 | 59.83 | 0.037273 | 180.23 | 1151 | 970.77
17990 | 14.683 | 211.91 | 59.83 | 0.03728 | 180.24 | 1151 |  | 17990 | 211.91 | 14.683 | 59.83 | 0.03728 | 180.24 | 1151 | 970.76
17991 | 14.686 | 211.92 | 59.83 | 0.037287 | 180.25 | 1151 |  | 17991 | 211.92 | 14.686 | 59.83 | 0.037287 | 180.25 | 1151 | 970.75
17992 | 14.689 | 211.93 | 59.83 | 0.037294 | 180.26 | 1151 |  | 17992 | 211.93 | 14.689 | 59.83 | 0.037294 | 180.26 | 1151 | 970.74
17993 | 14.692 | 211.94 | 59.829 | 0.037301 | 180.27 | 1151 |  | 17993 | 211.94 | 14.692 | 59.829 | 0.037301 | 180.27 | 1151 | 970.73
17994 | 14.695 | 211.95 | 59.829 | 0.037308 | 180.28 | 1151 |  | 17994 | 211.95 | 14.695 | 59.829 | 0.037308 | 180.28 | 1151 | 970.72
17995 | 14.698 | 211.96 | 59.829 | 0.037315 | 180.29 | 1151 |  | 17995 | 211.96 | 14.698 | 59.829 | 0.037315 | 180.29 | 1151 | 970.71
17996 | 14.701 | 211.97 | 59.829 | 0.037322 | 180.3 | 1151 |  | 17996 | 211.97 | 14.701 | 59.829 | 0.037322 | 180.3 | 1151 | 970.7
17997 | 14.704 | 211.98 | 59.828 | 0.037329 | 180.31 | 1151.1 |  | 17997 | 211.98 | 14.704 | 59.828 | 0.037329 | 180.31 | 1151.1 | 970.79
17998 | 14.707 | 211.99 | 59.828 | 0.037336 | 180.32 | 1151.1 |  | 17998 | 211.99 | 14.707 | 59.828 | 0.037336 | 180.32 | 1151.1 | 970.78
17999 | 14.709 | 212 | 59.828 | 0.037343 | 180.33 | 1151.1 |  | 17999 | 212 | 14.709 | 59.828 | 0.037343 | 180.33 | 1151.1 | 970.77
18000 | 14.712 | 212.01 | 59.828 | 0.037349 | 180.34 | 1151.1 |  | 18000 | 212.01 | 14.712 | 59.828 | 0.037349 | 180.34 | 1151.1 | 970.76
18001 | 14.715 | 212.02 | 59.827 | 0.037356 | 180.35 | 1151.1 |  | 18001 | 212.02 | 14.715 | 59.827 | 0.037356 | 180.35 | 1151.1 | 970.75
18002 | 14.718 | 212.03 | 59.827 | 0.037363 | 180.36 | 1151.1 |  | 18002 | 212.03 | 14.718 | 59.827 | 0.037363 | 180.36 | 1151.1 | 970.74
18003 | 14.721 | 212.04 | 59.827 | 0.03737 | 180.37 | 1151.1 |  | 18003 | 212.04 | 14.721 | 59.827 | 0.03737 | 180.37 | 1151.1 | 970.73
18004 | 14.724 | 212.05 | 59.827 | 0.037377 | 180.38 | 1151.1 |  | 18004 | 212.05 | 14.724 | 59.827 | 0.037377 | 180.38 | 1151.1 | 970.72
18005 | 14.727 | 212.06 | 59.826 | 0.037384 | 180.39 | 1151.1 |  | 18005 | 212.06 | 14.727 | 59.826 | 0.037384 | 180.39 | 1151.1 | 970.71
18006 | 14.73 | 212.07 | 59.826 | 0.037391 | 180.4 | 1151.1 |  | 18006 | 212.07 | 14.73 | 59.826 | 0.037391 | 180.4 | 1151.1 | 970.7
18007 | 14.733 | 212.08 | 59.826 | 0.037398 | 180.41 | 1151.1 |  | 18007 | 212.08 | 14.733 | 59.826 | 0.037398 | 180.41 | 1151.1 | 970.69
18008 | 14.736 | 212.09 | 59.826 | 0.037405 | 180.42 | 1151.1 |  | 18008 | 212.09 | 14.736 | 59.826 | 0.037405 | 180.42 | 1151.1 | 970.68
18009 | 14.739 | 212.1 | 59.825 | 0.037412 | 180.43 | 1151.1 |  | 18009 | 212.1 | 14.739 | 59.825 | 0.037412 | 180.43 | 1151.1 | 970.67
18010 | 14.742 | 212.11 | 59.825 | 0.037419 | 180.44 | 1151.1 |  | 18010 | 212.11 | 14.742 | 59.825 | 0.037419 | 180.44 | 1151.1 | 970.66
18011 | 14.744 | 212.12 | 59.825 | 0.037426 | 180.45 | 1151.1 |  | 18011 | 212.12 | 14.744 | 59.825 | 0.037426 | 180.45 | 1151.1 | 970.65
18012 | 14.747 | 212.13 | 59.825 | 0.037433 | 180.46 | 1151.1 |  | 18012 | 212.13 | 14.747 | 59.825 | 0.037433 | 180.46 | 1151.1 | 970.64
18013 | 14.75 | 212.14 | 59.824 | 0.03744 | 180.47 | 1151.1 |  | 18013 | 212.14 | 14.75 | 59.824 | 0.03744 | 180.47 | 1151.1 | 970.63
18014 | 14.753 | 212.15 | 59.824 | 0.037447 | 180.48 | 1151.1 |  | 18014 | 212.15 | 14.753 | 59.824 | 0.037447 | 180.48 | 1151.1 | 970.62
18015 | 14.756 | 212.16 | 59.824 | 0.037453 | 180.49 | 1151.1 |  | 18015 | 212.16 | 14.756 | 59.824 | 0.037453 | 180.49 | 1151.1 | 970.61
18016 | 14.759 | 212.17 | 59.824 | 0.03746 | 180.5 | 1151.1 |  | 18016 | 212.17 | 14.759 | 59.824 | 0.03746 | 180.5 | 1151.1 | 970.6
18017 | 14.762 | 212.18 | 59.823 | 0.037467 | 180.51 | 1151.1 |  | 18017 | 212.18 | 14.762 | 59.823 | 0.037467 | 180.51 | 1151.1 | 970.59
18018 | 14.765 | 212.19 | 59.823 | 0.037474 | 180.52 | 1151.1 |  | 18018 | 212.19 | 14.765 | 59.823 | 0.037474 | 180.52 | 1151.1 | 970.58
18019 | 14.768 | 212.2 | 59.823 | 0.037481 | 180.53 | 1151.1 |  | 18019 | 212.2 | 14.768 | 59.823 | 0.037481 | 180.53 | 1151.1 | 970.57
18020 | 14.771 | 212.21 | 59.823 | 0.037488 | 180.54 | 1151.1 |  | 18020 | 212.21 | 14.771 | 59.823 | 0.037488 | 180.54 | 1151.1 | 970.56
18021 | 14.774 | 212.22 | 59.822 | 0.037495 | 180.55 | 1151.1 |  | 18021 | 212.22 | 14.774 | 59.822 | 0.037495 | 180.55 | 1151.1 | 970.55
18022 | 14.777 | 212.23 | 59.822 | 0.037502 | 180.56 | 1151.1 |  | 18022 | 212.23 | 14.777 | 59.822 | 0.037502 | 180.56 | 1151.1 | 970.54
18023 | 14.78 | 212.24 | 59.822 | 0.037509 | 180.57 | 1151.1 |  | 18023 | 212.24 | 14.78 | 59.822 | 0.037509 | 180.57 | 1151.1 | 970.53
18024 | 14.782 | 212.25 | 59.822 | 0.037516 | 180.58 | 1151.2 |  | 18024 | 212.25 | 14.782 | 59.822 | 0.037516 | 180.58 | 1151.2 | 970.62
18025 | 14.785 | 212.26 | 59.821 | 0.037523 | 180.59 | 1151.2 |  | 18025 | 212.26 | 14.785 | 59.821 | 0.037523 | 180.59 | 1151.2 | 970.61
18026 | 14.788 | 212.27 | 59.821 | 0.03753 | 180.6 | 1151.2 |  | 18026 | 212.27 | 14.788 | 59.821 | 0.03753 | 180.6 | 1151.2 | 970.6
18027 | 14.791 | 212.28 | 59.821 | 0.037537 | 180.61 | 1151.2 |  | 18027 | 212.28 | 14.791 | 59.821 | 0.037537 | 180.61 | 1151.2 | 970.59
18028 | 14.794 | 212.29 | 59.821 | 0.037544 | 180.62 | 1151.2 |  | 18028 | 212.29 | 14.794 | 59.821 | 0.037544 | 180.62 | 1151.2 | 970.58
18029 | 14.797 | 212.3 | 59.82 | 0.037551 | 180.63 | 1151.2 |  | 18029 | 212.3 | 14.797 | 59.82 | 0.037551 | 180.63 | 1151.2 | 970.57
18030 | 14.8 | 212.31 | 59.82 | 0.037558 | 180.64 | 1151.2 |  | 18030 | 212.31 | 14.8 | 59.82 | 0.037558 | 180.64 | 1151.2 | 970.56
18031 | 14.803 | 212.32 | 59.82 | 0.037565 | 180.65 | 1151.2 |  | 18031 | 212.32 | 14.803 | 59.82 | 0.037565 | 180.65 | 1151.2 | 970.55
18032 | 14.806 | 212.33 | 59.82 | 0.037572 | 180.66 | 1151.2 |  | 18032 | 212.33 | 14.806 | 59.82 | 0.037572 | 180.66 | 1151.2 | 970.54
18033 | 14.809 | 212.34 | 59.819 | 0.037579 | 180.67 | 1151.2 |  | 18033 | 212.34 | 14.809 | 59.819 | 0.037579 | 180.67 | 1151.2 | 970.53
18034 | 14.812 | 212.35 | 59.819 | 0.037586 | 180.68 | 1151.2 |  | 18034 | 212.35 | 14.812 | 59.819 | 0.037586 | 180.68 | 1151.2 | 970.52
18035 | 14.815 | 212.36 | 59.819 | 0.037592 | 180.69 | 1151.2 |  | 18035 | 212.36 | 14.815 | 59.819 | 0.037592 | 180.69 | 1151.2 | 970.51
18036 | 14.818 | 212.37 | 59.819 | 0.037599 | 180.7 | 1151.2 |  | 18036 | 212.37 | 14.818 | 59.819 | 0.037599 | 180.7 | 1151.2 | 970.5
18037 | 14.821 | 212.38 | 59.818 | 0.037606 | 180.71 | 1151.2 |  | 18037 | 212.38 | 14.821 | 59.818 | 0.037606 | 180.71 | 1151.2 | 970.49
18038 | 14.824 | 212.39 | 59.818 | 0.037613 | 180.72 | 1151.2 |  | 18038 | 212.39 | 14.824 | 59.818 | 0.037613 | 180.72 | 1151.2 | 970.48
18039 | 14.826 | 212.4 | 59.818 | 0.03762 | 180.73 | 1151.2 |  | 18039 | 212.4 | 14.826 | 59.818 | 0.03762 | 180.73 | 1151.2 | 970.47
18040 | 14.829 | 212.41 | 59.818 | 0.037627 | 180.74 | 1151.2 |  | 18040 | 212.41 | 14.829 | 59.818 | 0.037627 | 180.74 | 1151.2 | 970.46
18041 | 14.832 | 212.42 | 59.817 | 0.037634 | 180.75 | 1151.2 |  | 18041 | 212.42 | 14.832 | 59.817 | 0.037634 | 180.75 | 1151.2 | 970.45
18042 | 14.835 | 212.43 | 59.817 | 0.037641 | 180.76 | 1151.2 |  | 18042 | 212.43 | 14.835 | 59.817 | 0.037641 | 180.76 | 1151.2 | 970.44
18043 | 14.838 | 212.44 | 59.817 | 0.037648 | 180.77 | 1151.2 |  | 18043 | 212.44 | 14.838 | 59.817 | 0.037648 | 180.77 | 1151.2 | 970.43
18044 | 14.841 | 212.45 | 59.817 | 0.037655 | 180.78 | 1151.2 |  | 18044 | 212.45 | 14.841 | 59.817 | 0.037655 | 180.78 | 1151.2 | 970.42
18045 | 14.844 | 212.46 | 59.816 | 0.037662 | 180.79 | 1151.2 |  | 18045 | 212.46 | 14.844 | 59.816 | 0.037662 | 180.79 | 1151.2 | 970.41
18046 | 14.847 | 212.47 | 59.816 | 0.037669 | 180.8 | 1151.2 |  | 18046 | 212.47 | 14.847 | 59.816 | 0.037669 | 180.8 | 1151.2 | 970.4
18047 | 14.85 | 212.48 | 59.816 | 0.037676 | 180.81 | 1151.2 |  | 18047 | 212.48 | 14.85 | 59.816 | 0.037676 | 180.81 | 1151.2 | 970.39
18048 | 14.853 | 212.49 | 59.816 | 0.037683 | 180.82 | 1151.2 |  | 18048 | 212.49 | 14.853 | 59.816 | 0.037683 | 180.82 | 1151.2 | 970.38
18049 | 14.856 | 212.5 | 59.815 | 0.03769 | 180.83 | 1151.2 |  | 18049 | 212.5 | 14.856 | 59.815 | 0.03769 | 180.83 | 1151.2 | 970.37
18050 | 14.859 | 212.51 | 59.815 | 0.037697 | 180.84 | 1151.3 |  | 18050 | 212.51 | 14.859 | 59.815 | 0.037697 | 180.84 | 1151.3 | 970.46
18051 | 14.862 | 212.52 | 59.815 | 0.037704 | 180.85 | 1151.3 |  | 18051 | 212.52 | 14.862 | 59.815 | 0.037704 | 180.85 | 1151.3 | 970.45
18052 | 14.865 | 212.53 | 59.815 | 0.037711 | 180.86 | 1151.3 |  | 18052 | 212.53 | 14.865 | 59.815 | 0.037711 | 180.86 | 1151.3 | 970.44
18053 | 14.868 | 212.54 | 59.814 | 0.037718 | 180.87 | 1151.3 |  | 18053 | 212.54 | 14.868 | 59.814 | 0.037718 | 180.87 | 1151.3 | 970.43
18054 | 14.871 | 212.55 | 59.814 | 0.037725 | 180.88 | 1151.3 |  | 18054 | 212.55 | 14.871 | 59.814 | 0.037725 | 180.88 | 1151.3 | 970.42
18055 | 14.874 | 212.56 | 59.814 | 0.037732 | 180.89 | 1151.3 |  | 18055 | 212.56 | 14.874 | 59.814 | 0.037732 | 180.89 | 1151.3 | 970.41
18056 | 14.876 | 212.57 | 59.814 | 0.037739 | 180.9 | 1151.3 |  | 18056 | 212.57 | 14.876 | 59.814 | 0.037739 | 180.9 | 1151.3 | 970.4
18057 | 14.879 | 212.58 | 59.813 | 0.037746 | 180.91 | 1151.3 |  | 18057 | 212.58 | 14.879 | 59.813 | 0.037746 | 180.91 | 1151.3 | 970.39
18058 | 14.882 | 212.59 | 59.813 | 0.037753 | 180.92 | 1151.3 |  | 18058 | 212.59 | 14.882 | 59.813 | 0.037753 | 180.92 | 1151.3 | 970.38
18059 | 14.885 | 212.6 | 59.813 | 0.03776 | 180.93 | 1151.3 |  | 18059 | 212.6 | 14.885 | 59.813 | 0.03776 | 180.93 | 1151.3 | 970.37
18060 | 14.888 | 212.61 | 59.813 | 0.037767 | 180.94 | 1151.3 |  | 18060 | 212.61 | 14.888 | 59.813 | 0.037767 | 180.94 | 1151.3 | 970.36
18061 | 14.891 | 212.62 | 59.812 | 0.037774 | 180.95 | 1151.3 |  | 18061 | 212.62 | 14.891 | 59.812 | 0.037774 | 180.95 | 1151.3 | 970.35
18062 | 14.894 | 212.63 | 59.812 | 0.037781 | 180.96 | 1151.3 |  | 18062 | 212.63 | 14.894 | 59.812 | 0.037781 | 180.96 | 1151.3 | 970.34
18063 | 14.897 | 212.64 | 59.812 | 0.037788 | 180.97 | 1151.3 |  | 18063 | 212.64 | 14.897 | 59.812 | 0.037788 | 180.97 | 1151.3 | 970.33
18064 | 14.9 | 212.65 | 59.812 | 0.037795 | 180.98 | 1151.3 |  | 18064 | 212.65 | 14.9 | 59.812 | 0.037795 | 180.98 | 1151.3 | 970.32
18065 | 14.903 | 212.66 | 59.811 | 0.037802 | 181 | 1151.3 |  | 18065 | 212.66 | 14.903 | 59.811 | 0.037802 | 181 | 1151.3 | 970.3
18066 | 14.906 | 212.67 | 59.811 | 0.037809 | 181.01 | 1151.3 |  | 18066 | 212.67 | 14.906 | 59.811 | 0.037809 | 181.01 | 1151.3 | 970.29
18067 | 14.909 | 212.68 | 59.811 | 0.037816 | 181.02 | 1151.3 |  | 18067 | 212.68 | 14.909 | 59.811 | 0.037816 | 181.02 | 1151.3 | 970.28
18068 | 14.912 | 212.69 | 59.811 | 0.037823 | 181.03 | 1151.3 |  | 18068 | 212.69 | 14.912 | 59.811 | 0.037823 | 181.03 | 1151.3 | 970.27
18069 | 14.915 | 212.7 | 59.81 | 0.03783 | 181.04 | 1151.3 |  | 18069 | 212.7 | 14.915 | 59.81 | 0.03783 | 181.04 | 1151.3 | 970.26
18070 | 14.918 | 212.71 | 59.81 | 0.037837 | 181.05 | 1151.3 |  | 18070 | 212.71 | 14.918 | 59.81 | 0.037837 | 181.05 | 1151.3 | 970.25
18071 | 14.921 | 212.72 | 59.81 | 0.037844 | 181.06 | 1151.3 |  | 18071 | 212.72 | 14.921 | 59.81 | 0.037844 | 181.06 | 1151.3 | 970.24
18072 | 14.924 | 212.73 | 59.81 | 0.037851 | 181.07 | 1151.3 |  | 18072 | 212.73 | 14.924 | 59.81 | 0.037851 | 181.07 | 1151.3 | 970.23
18073 | 14.927 | 212.74 | 59.809 | 0.037858 | 181.08 | 1151.3 |  | 18073 | 212.74 | 14.927 | 59.809 | 0.037858 | 181.08 | 1151.3 | 970.22
18074 | 14.93 | 212.75 | 59.809 | 0.037865 | 181.09 | 1151.3 |  | 18074 | 212.75 | 14.93 | 59.809 | 0.037865 | 181.09 | 1151.3 | 970.21
18075 | 14.932 | 212.76 | 59.809 | 0.037872 | 181.1 | 1151.3 |  | 18075 | 212.76 | 14.932 | 59.809 | 0.037872 | 181.1 | 1151.3 | 970.2
18076 | 14.935 | 212.77 | 59.809 | 0.037879 | 181.11 | 1151.3 |  | 18076 | 212.77 | 14.935 | 59.809 | 0.037879 | 181.11 | 1151.3 | 970.19
18077 | 14.938 | 212.78 | 59.808 | 0.037886 | 181.12 | 1151.4 |  | 18077 | 212.78 | 14.938 | 59.808 | 0.037886 | 181.12 | 1151.4 | 970.28
18078 | 14.941 | 212.79 | 59.808 | 0.037893 | 181.13 | 1151.4 |  | 18078 | 212.79 | 14.941 | 59.808 | 0.037893 | 181.13 | 1151.4 | 970.27
18079 | 14.944 | 212.8 | 59.808 | 0.0379 | 181.14 | 1151.4 |  | 18079 | 212.8 | 14.944 | 59.808 | 0.0379 | 181.14 | 1151.4 | 970.26
18080 | 14.947 | 212.81 | 59.808 | 0.037907 | 181.15 | 1151.4 |  | 18080 | 212.81 | 14.947 | 59.808 | 0.037907 | 181.15 | 1151.4 | 970.25
18081 | 14.95 | 212.82 | 59.807 | 0.037914 | 181.16 | 1151.4 |  | 18081 | 212.82 | 14.95 | 59.807 | 0.037914 | 181.16 | 1151.4 | 970.24
18082 | 14.953 | 212.83 | 59.807 | 0.037921 | 181.17 | 1151.4 |  | 18082 | 212.83 | 14.953 | 59.807 | 0.037921 | 181.17 | 1151.4 | 970.23
18083 | 14.956 | 212.84 | 59.807 | 0.037928 | 181.18 | 1151.4 |  | 18083 | 212.84 | 14.956 | 59.807 | 0.037928 | 181.18 | 1151.4 | 970.22
18084 | 14.959 | 212.85 | 59.807 | 0.037935 | 181.19 | 1151.4 |  | 18084 | 212.85 | 14.959 | 59.807 | 0.037935 | 181.19 | 1151.4 | 970.21
18085 | 14.962 | 212.86 | 59.806 | 0.037942 | 181.2 | 1151.4 |  | 18085 | 212.86 | 14.962 | 59.806 | 0.037942 | 181.2 | 1151.4 | 970.2
18086 | 14.965 | 212.87 | 59.806 | 0.037949 | 181.21 | 1151.4 |  | 18086 | 212.87 | 14.965 | 59.806 | 0.037949 | 181.21 | 1151.4 | 970.19
18087 | 14.968 | 212.88 | 59.806 | 0.037956 | 181.22 | 1151.4 |  | 18087 | 212.88 | 14.968 | 59.806 | 0.037956 | 181.22 | 1151.4 | 970.18
18088 | 14.971 | 212.89 | 59.806 | 0.037963 | 181.23 | 1151.4 |  | 18088 | 212.89 | 14.971 | 59.806 | 0.037963 | 181.23 | 1151.4 | 970.17
18089 | 14.974 | 212.9 | 59.805 | 0.03797 | 181.24 | 1151.4 |  | 18089 | 212.9 | 14.974 | 59.805 | 0.03797 | 181.24 | 1151.4 | 970.16
18090 | 14.977 | 212.91 | 59.805 | 0.037977 | 181.25 | 1151.4 |  | 18090 | 212.91 | 14.977 | 59.805 | 0.037977 | 181.25 | 1151.4 | 970.15
18091 | 14.98 | 212.92 | 59.805 | 0.037984 | 181.26 | 1151.4 |  | 18091 | 212.92 | 14.98 | 59.805 | 0.037984 | 181.26 | 1151.4 | 970.14
18092 | 14.983 | 212.93 | 59.805 | 0.037991 | 181.27 | 1151.4 |  | 18092 | 212.93 | 14.983 | 59.805 | 0.037991 | 181.27 | 1151.4 | 970.13
18093 | 14.986 | 212.94 | 59.804 | 0.037998 | 181.28 | 1151.4 |  | 18093 | 212.94 | 14.986 | 59.804 | 0.037998 | 181.28 | 1151.4 | 970.12
18094 | 14.989 | 212.95 | 59.804 | 0.038005 | 181.29 | 1151.4 |  | 18094 | 212.95 | 14.989 | 59.804 | 0.038005 | 181.29 | 1151.4 | 970.11
18095 | 14.992 | 212.96 | 59.804 | 0.038012 | 181.3 | 1151.4 |  | 18095 | 212.96 | 14.992 | 59.804 | 0.038012 | 181.3 | 1151.4 | 970.1
18096 | 14.995 | 212.97 | 59.804 | 0.038019 | 181.31 | 1151.4 |  | 18096 | 212.97 | 14.995 | 59.804 | 0.038019 | 181.31 | 1151.4 | 970.09
18097 | 14.998 | 212.98 | 59.803 | 0.038026 | 181.32 | 1151.4 |  | 18097 | 212.98 | 14.998 | 59.803 | 0.038026 | 181.32 | 1151.4 | 970.08
18098 | 15.001 | 212.99 | 59.803 | 0.038033 | 181.33 | 1151.4 |  | 18098 | 212.99 | 15.001 | 59.803 | 0.038033 | 181.33 | 1151.4 | 970.07
18099 | 15.003 | 213 | 59.803 | 0.03804 | 181.34 | 1151.4 |  | 18099 | 213 | 15.003 | 59.803 | 0.03804 | 181.34 | 1151.4 | 970.06
18100 | 15.006 | 213.01 | 59.803 | 0.038047 | 181.35 | 1151.4 |  | 18100 | 213.01 | 15.006 | 59.803 | 0.038047 | 181.35 | 1151.4 | 970.05
18101 | 15.009 | 213.02 | 59.802 | 0.038054 | 181.36 | 1151.4 |  | 18101 | 213.02 | 15.009 | 59.802 | 0.038054 | 181.36 | 1151.4 | 970.04
18102 | 15.012 | 213.03 | 59.802 | 0.038061 | 181.37 | 1151.4 |  | 18102 | 213.03 | 15.012 | 59.802 | 0.038061 | 181.37 | 1151.4 | 970.03
18103 | 15.015 | 213.04 | 59.802 | 0.038068 | 181.38 | 1151.4 |  | 18103 | 213.04 | 15.015 | 59.802 | 0.038068 | 181.38 | 1151.4 | 970.02
18104 | 15.018 | 213.05 | 59.802 | 0.038075 | 181.39 | 1151.5 |  | 18104 | 213.05 | 15.018 | 59.802 | 0.038075 | 181.39 | 1151.5 | 970.11
18105 | 15.021 | 213.06 | 59.801 | 0.038082 | 181.4 | 1151.5 |  | 18105 | 213.06 | 15.021 | 59.801 | 0.038082 | 181.4 | 1151.5 | 970.1
18106 | 15.024 | 213.07 | 59.801 | 0.038089 | 181.41 | 1151.5 |  | 18106 | 213.07 | 15.024 | 59.801 | 0.038089 | 181.41 | 1151.5 | 970.09
18107 | 15.027 | 213.08 | 59.801 | 0.038097 | 181.42 | 1151.5 |  | 18107 | 213.08 | 15.027 | 59.801 | 0.038097 | 181.42 | 1151.5 | 970.08
18108 | 15.03 | 213.09 | 59.801 | 0.038104 | 181.43 | 1151.5 |  | 18108 | 213.09 | 15.03 | 59.801 | 0.038104 | 181.43 | 1151.5 | 970.07
18109 | 15.033 | 213.1 | 59.8 | 0.038111 | 181.44 | 1151.5 |  | 18109 | 213.1 | 15.033 | 59.8 | 0.038111 | 181.44 | 1151.5 | 970.06
18110 | 15.036 | 213.11 | 59.8 | 0.038118 | 181.45 | 1151.5 |  | 18110 | 213.11 | 15.036 | 59.8 | 0.038118 | 181.45 | 1151.5 | 970.05
18111 | 15.039 | 213.12 | 59.8 | 0.038125 | 181.46 | 1151.5 |  | 18111 | 213.12 | 15.039 | 59.8 | 0.038125 | 181.46 | 1151.5 | 970.04
18112 | 15.042 | 213.13 | 59.8 | 0.038132 | 181.47 | 1151.5 |  | 18112 | 213.13 | 15.042 | 59.8 | 0.038132 | 181.47 | 1151.5 | 970.03
18113 | 15.045 | 213.14 | 59.799 | 0.038139 | 181.48 | 1151.5 |  | 18113 | 213.14 | 15.045 | 59.799 | 0.038139 | 181.48 | 1151.5 | 970.02
18114 | 15.048 | 213.15 | 59.799 | 0.038146 | 181.49 | 1151.5 |  | 18114 | 213.15 | 15.048 | 59.799 | 0.038146 | 181.49 | 1151.5 | 970.01
18115 | 15.051 | 213.16 | 59.799 | 0.038153 | 181.5 | 1151.5 |  | 18115 | 213.16 | 15.051 | 59.799 | 0.038153 | 181.5 | 1151.5 | 970
18116 | 15.054 | 213.17 | 59.799 | 0.03816 | 181.51 | 1151.5 |  | 18116 | 213.17 | 15.054 | 59.799 | 0.03816 | 181.51 | 1151.5 | 969.99
18117 | 15.057 | 213.18 | 59.798 | 0.038167 | 181.52 | 1151.5 |  | 18117 | 213.18 | 15.057 | 59.798 | 0.038167 | 181.52 | 1151.5 | 969.98
18118 | 15.06 | 213.19 | 59.798 | 0.038174 | 181.53 | 1151.5 |  | 18118 | 213.19 | 15.06 | 59.798 | 0.038174 | 181.53 | 1151.5 | 969.97
18119 | 15.063 | 213.2 | 59.798 | 0.038181 | 181.54 | 1151.5 |  | 18119 | 213.2 | 15.063 | 59.798 | 0.038181 | 181.54 | 1151.5 | 969.96
18120 | 15.066 | 213.21 | 59.798 | 0.038188 | 181.55 | 1151.5 |  | 18120 | 213.21 | 15.066 | 59.798 | 0.038188 | 181.55 | 1151.5 | 969.95
18121 | 15.069 | 213.22 | 59.797 | 0.038195 | 181.56 | 1151.5 |  | 18121 | 213.22 | 15.069 | 59.797 | 0.038195 | 181.56 | 1151.5 | 969.94
18122 | 15.072 | 213.23 | 59.797 | 0.038202 | 181.57 | 1151.5 |  | 18122 | 213.23 | 15.072 | 59.797 | 0.038202 | 181.57 | 1151.5 | 969.93
18123 | 15.075 | 213.24 | 59.797 | 0.038209 | 181.58 | 1151.5 |  | 18123 | 213.24 | 15.075 | 59.797 | 0.038209 | 181.58 | 1151.5 | 969.92
18124 | 15.078 | 213.25 | 59.797 | 0.038216 | 181.59 | 1151.5 |  | 18124 | 213.25 | 15.078 | 59.797 | 0.038216 | 181.59 | 1151.5 | 969.91
18125 | 15.081 | 213.26 | 59.796 | 0.038223 | 181.6 | 1151.5 |  | 18125 | 213.26 | 15.081 | 59.796 | 0.038223 | 181.6 | 1151.5 | 969.9
18126 | 15.084 | 213.27 | 59.796 | 0.03823 | 181.61 | 1151.5 |  | 18126 | 213.27 | 15.084 | 59.796 | 0.03823 | 181.61 | 1151.5 | 969.89
18127 | 15.087 | 213.28 | 59.796 | 0.038237 | 181.62 | 1151.5 |  | 18127 | 213.28 | 15.087 | 59.796 | 0.038237 | 181.62 | 1151.5 | 969.88
18128 | 15.09 | 213.29 | 59.796 | 0.038245 | 181.63 | 1151.5 |  | 18128 | 213.29 | 15.09 | 59.796 | 0.038245 | 181.63 | 1151.5 | 969.87
18129 | 15.093 | 213.3 | 59.795 | 0.038252 | 181.64 | 1151.5 |  | 18129 | 213.3 | 15.093 | 59.795 | 0.038252 | 181.64 | 1151.5 | 969.86
18130 | 15.096 | 213.31 | 59.795 | 0.038259 | 181.65 | 1151.6 |  | 18130 | 213.31 | 15.096 | 59.795 | 0.038259 | 181.65 | 1151.6 | 969.95
18131 | 15.099 | 213.32 | 59.795 | 0.038266 | 181.66 | 1151.6 |  | 18131 | 213.32 | 15.099 | 59.795 | 0.038266 | 181.66 | 1151.6 | 969.94
18132 | 15.102 | 213.33 | 59.795 | 0.038273 | 181.67 | 1151.6 |  | 18132 | 213.33 | 15.102 | 59.795 | 0.038273 | 181.67 | 1151.6 | 969.93
18133 | 15.105 | 213.34 | 59.794 | 0.03828 | 181.68 | 1151.6 |  | 18133 | 213.34 | 15.105 | 59.794 | 0.03828 | 181.68 | 1151.6 | 969.92
18134 | 15.108 | 213.35 | 59.794 | 0.038287 | 181.69 | 1151.6 |  | 18134 | 213.35 | 15.108 | 59.794 | 0.038287 | 181.69 | 1151.6 | 969.91
18135 | 15.111 | 213.36 | 59.794 | 0.038294 | 181.7 | 1151.6 |  | 18135 | 213.36 | 15.111 | 59.794 | 0.038294 | 181.7 | 1151.6 | 969.9
18136 | 15.113 | 213.37 | 59.794 | 0.038301 | 181.71 | 1151.6 |  | 18136 | 213.37 | 15.113 | 59.794 | 0.038301 | 181.71 | 1151.6 | 969.89
18137 | 15.116 | 213.38 | 59.793 | 0.038308 | 181.72 | 1151.6 |  | 18137 | 213.38 | 15.116 | 59.793 | 0.038308 | 181.72 | 1151.6 | 969.88
18138 | 15.119 | 213.39 | 59.793 | 0.038315 | 181.73 | 1151.6 |  | 18138 | 213.39 | 15.119 | 59.793 | 0.038315 | 181.73 | 1151.6 | 969.87
18139 | 15.122 | 213.4 | 59.793 | 0.038322 | 181.74 | 1151.6 |  | 18139 | 213.4 | 15.122 | 59.793 | 0.038322 | 181.74 | 1151.6 | 969.86
18140 | 15.125 | 213.41 | 59.793 | 0.038329 | 181.75 | 1151.6 |  | 18140 | 213.41 | 15.125 | 59.793 | 0.038329 | 181.75 | 1151.6 | 969.85
18141 | 15.128 | 213.42 | 59.792 | 0.038336 | 181.76 | 1151.6 |  | 18141 | 213.42 | 15.128 | 59.792 | 0.038336 | 181.76 | 1151.6 | 969.84
18142 | 15.131 | 213.43 | 59.792 | 0.038343 | 181.77 | 1151.6 |  | 18142 | 213.43 | 15.131 | 59.792 | 0.038343 | 181.77 | 1151.6 | 969.83
18143 | 15.134 | 213.44 | 59.792 | 0.038351 | 181.78 | 1151.6 |  | 18143 | 213.44 | 15.134 | 59.792 | 0.038351 | 181.78 | 1151.6 | 969.82
18144 | 15.137 | 213.45 | 59.792 | 0.038358 | 181.79 | 1151.6 |  | 18144 | 213.45 | 15.137 | 59.792 | 0.038358 | 181.79 | 1151.6 | 969.81
18145 | 15.14 | 213.46 | 59.791 | 0.038365 | 181.8 | 1151.6 |  | 18145 | 213.46 | 15.14 | 59.791 | 0.038365 | 181.8 | 1151.6 | 969.8
18146 | 15.143 | 213.47 | 59.791 | 0.038372 | 181.81 | 1151.6 |  | 18146 | 213.47 | 15.143 | 59.791 | 0.038372 | 181.81 | 1151.6 | 969.79
18147 | 15.146 | 213.48 | 59.791 | 0.038379 | 181.82 | 1151.6 |  | 18147 | 213.48 | 15.146 | 59.791 | 0.038379 | 181.82 | 1151.6 | 969.78
18148 | 15.149 | 213.49 | 59.791 | 0.038386 | 181.83 | 1151.6 |  | 18148 | 213.49 | 15.149 | 59.791 | 0.038386 | 181.83 | 1151.6 | 969.77
18149 | 15.152 | 213.5 | 59.79 | 0.038393 | 181.84 | 1151.6 |  | 18149 | 213.5 | 15.152 | 59.79 | 0.038393 | 181.84 | 1151.6 | 969.76
18150 | 15.155 | 213.51 | 59.79 | 0.0384 | 181.85 | 1151.6 |  | 18150 | 213.51 | 15.155 | 59.79 | 0.0384 | 181.85 | 1151.6 | 969.75
18151 | 15.158 | 213.52 | 59.79 | 0.038407 | 181.86 | 1151.6 |  | 18151 | 213.52 | 15.158 | 59.79 | 0.038407 | 181.86 | 1151.6 | 969.74
18152 | 15.161 | 213.53 | 59.79 | 0.038414 | 181.87 | 1151.6 |  | 18152 | 213.53 | 15.161 | 59.79 | 0.038414 | 181.87 | 1151.6 | 969.73
18153 | 15.164 | 213.54 | 59.789 | 0.038421 | 181.88 | 1151.6 |  | 18153 | 213.54 | 15.164 | 59.789 | 0.038421 | 181.88 | 1151.6 | 969.72
18154 | 15.167 | 213.55 | 59.789 | 0.038428 | 181.89 | 1151.6 |  | 18154 | 213.55 | 15.167 | 59.789 | 0.038428 | 181.89 | 1151.6 | 969.71
18155 | 15.17 | 213.56 | 59.789 | 0.038436 | 181.9 | 1151.6 |  | 18155 | 213.56 | 15.17 | 59.789 | 0.038436 | 181.9 | 1151.6 | 969.7
18156 | 15.173 | 213.57 | 59.789 | 0.038443 | 181.91 | 1151.6 |  | 18156 | 213.57 | 15.173 | 59.789 | 0.038443 | 181.91 | 1151.6 | 969.69
18157 | 15.176 | 213.58 | 59.788 | 0.03845 | 181.92 | 1151.7 |  | 18157 | 213.58 | 15.176 | 59.788 | 0.03845 | 181.92 | 1151.7 | 969.78
18158 | 15.179 | 213.59 | 59.788 | 0.038457 | 181.93 | 1151.7 |  | 18158 | 213.59 | 15.179 | 59.788 | 0.038457 | 181.93 | 1151.7 | 969.77
18159 | 15.182 | 213.6 | 59.788 | 0.038464 | 181.94 | 1151.7 |  | 18159 | 213.6 | 15.182 | 59.788 | 0.038464 | 181.94 | 1151.7 | 969.76
18160 | 15.185 | 213.61 | 59.788 | 0.038471 | 181.95 | 1151.7 |  | 18160 | 213.61 | 15.185 | 59.788 | 0.038471 | 181.95 | 1151.7 | 969.75
18161 | 15.188 | 213.62 | 59.787 | 0.038478 | 181.96 | 1151.7 |  | 18161 | 213.62 | 15.188 | 59.787 | 0.038478 | 181.96 | 1151.7 | 969.74
18162 | 15.191 | 213.63 | 59.787 | 0.038485 | 181.97 | 1151.7 |  | 18162 | 213.63 | 15.191 | 59.787 | 0.038485 | 181.97 | 1151.7 | 969.73
18163 | 15.194 | 213.64 | 59.787 | 0.038492 | 181.98 | 1151.7 |  | 18163 | 213.64 | 15.194 | 59.787 | 0.038492 | 181.98 | 1151.7 | 969.72
18164 | 15.197 | 213.65 | 59.787 | 0.038499 | 181.99 | 1151.7 |  | 18164 | 213.65 | 15.197 | 59.787 | 0.038499 | 181.99 | 1151.7 | 969.71
18165 | 15.2 | 213.66 | 59.786 | 0.038507 | 182 | 1151.7 |  | 18165 | 213.66 | 15.2 | 59.786 | 0.038507 | 182 | 1151.7 | 969.7
18166 | 15.203 | 213.67 | 59.786 | 0.038514 | 182.01 | 1151.7 |  | 18166 | 213.67 | 15.203 | 59.786 | 0.038514 | 182.01 | 1151.7 | 969.69
18167 | 15.206 | 213.68 | 59.786 | 0.038521 | 182.02 | 1151.7 |  | 18167 | 213.68 | 15.206 | 59.786 | 0.038521 | 182.02 | 1151.7 | 969.68
18168 | 15.209 | 213.69 | 59.786 | 0.038528 | 182.03 | 1151.7 |  | 18168 | 213.69 | 15.209 | 59.786 | 0.038528 | 182.03 | 1151.7 | 969.67
18169 | 15.212 | 213.7 | 59.785 | 0.038535 | 182.04 | 1151.7 |  | 18169 | 213.7 | 15.212 | 59.785 | 0.038535 | 182.04 | 1151.7 | 969.66
18170 | 15.215 | 213.71 | 59.785 | 0.038542 | 182.05 | 1151.7 |  | 18170 | 213.71 | 15.215 | 59.785 | 0.038542 | 182.05 | 1151.7 | 969.65
18171 | 15.218 | 213.72 | 59.785 | 0.038549 | 182.06 | 1151.7 |  | 18171 | 213.72 | 15.218 | 59.785 | 0.038549 | 182.06 | 1151.7 | 969.64
18172 | 15.221 | 213.73 | 59.785 | 0.038556 | 182.07 | 1151.7 |  | 18172 | 213.73 | 15.221 | 59.785 | 0.038556 | 182.07 | 1151.7 | 969.63
18173 | 15.224 | 213.74 | 59.784 | 0.038563 | 182.08 | 1151.7 |  | 18173 | 213.74 | 15.224 | 59.784 | 0.038563 | 182.08 | 1151.7 | 969.62
18174 | 15.227 | 213.75 | 59.784 | 0.03857 | 182.09 | 1151.7 |  | 18174 | 213.75 | 15.227 | 59.784 | 0.03857 | 182.09 | 1151.7 | 969.61
18175 | 15.23 | 213.76 | 59.784 | 0.038578 | 182.1 | 1151.7 |  | 18175 | 213.76 | 15.23 | 59.784 | 0.038578 | 182.1 | 1151.7 | 969.6
18176 | 15.233 | 213.77 | 59.784 | 0.038585 | 182.11 | 1151.7 |  | 18176 | 213.77 | 15.233 | 59.784 | 0.038585 | 182.11 | 1151.7 | 969.59
18177 | 15.236 | 213.78 | 59.783 | 0.038592 | 182.12 | 1151.7 |  | 18177 | 213.78 | 15.236 | 59.783 | 0.038592 | 182.12 | 1151.7 | 969.58
18178 | 15.239 | 213.79 | 59.783 | 0.038599 | 182.13 | 1151.7 |  | 18178 | 213.79 | 15.239 | 59.783 | 0.038599 | 182.13 | 1151.7 | 969.57
18179 | 15.242 | 213.8 | 59.783 | 0.038606 | 182.14 | 1151.7 |  | 18179 | 213.8 | 15.242 | 59.783 | 0.038606 | 182.14 | 1151.7 | 969.56
18180 | 15.245 | 213.81 | 59.783 | 0.038613 | 182.15 | 1151.7 |  | 18180 | 213.81 | 15.245 | 59.783 | 0.038613 | 182.15 | 1151.7 | 969.55
18181 | 15.248 | 213.82 | 59.782 | 0.03862 | 182.16 | 1151.7 |  | 18181 | 213.82 | 15.248 | 59.782 | 0.03862 | 182.16 | 1151.7 | 969.54
18182 | 15.251 | 213.83 | 59.782 | 0.038627 | 182.17 | 1151.7 |  | 18182 | 213.83 | 15.251 | 59.782 | 0.038627 | 182.17 | 1151.7 | 969.53
18183 | 15.254 | 213.84 | 59.782 | 0.038634 | 182.19 | 1151.8 |  | 18183 | 213.84 | 15.254 | 59.782 | 0.038634 | 182.19 | 1151.8 | 969.61
18184 | 15.257 | 213.85 | 59.782 | 0.038642 | 182.2 | 1151.8 |  | 18184 | 213.85 | 15.257 | 59.782 | 0.038642 | 182.2 | 1151.8 | 969.6
18185 | 15.26 | 213.86 | 59.781 | 0.038649 | 182.21 | 1151.8 |  | 18185 | 213.86 | 15.26 | 59.781 | 0.038649 | 182.21 | 1151.8 | 969.59
18186 | 15.263 | 213.87 | 59.781 | 0.038656 | 182.22 | 1151.8 |  | 18186 | 213.87 | 15.263 | 59.781 | 0.038656 | 182.22 | 1151.8 | 969.58
18187 | 15.266 | 213.88 | 59.781 | 0.038663 | 182.23 | 1151.8 |  | 18187 | 213.88 | 15.266 | 59.781 | 0.038663 | 182.23 | 1151.8 | 969.57
18188 | 15.269 | 213.89 | 59.781 | 0.03867 | 182.24 | 1151.8 |  | 18188 | 213.89 | 15.269 | 59.781 | 0.03867 | 182.24 | 1151.8 | 969.56
18189 | 15.272 | 213.9 | 59.78 | 0.038677 | 182.25 | 1151.8 |  | 18189 | 213.9 | 15.272 | 59.78 | 0.038677 | 182.25 | 1151.8 | 969.55
18190 | 15.275 | 213.91 | 59.78 | 0.038684 | 182.26 | 1151.8 |  | 18190 | 213.91 | 15.275 | 59.78 | 0.038684 | 182.26 | 1151.8 | 969.54
18191 | 15.278 | 213.92 | 59.78 | 0.038691 | 182.27 | 1151.8 |  | 18191 | 213.92 | 15.278 | 59.78 | 0.038691 | 182.27 | 1151.8 | 969.53
18192 | 15.281 | 213.93 | 59.78 | 0.038699 | 182.28 | 1151.8 |  | 18192 | 213.93 | 15.281 | 59.78 | 0.038699 | 182.28 | 1151.8 | 969.52
18193 | 15.284 | 213.94 | 59.779 | 0.038706 | 182.29 | 1151.8 |  | 18193 | 213.94 | 15.284 | 59.779 | 0.038706 | 182.29 | 1151.8 | 969.51
18194 | 15.287 | 213.95 | 59.779 | 0.038713 | 182.3 | 1151.8 |  | 18194 | 213.95 | 15.287 | 59.779 | 0.038713 | 182.3 | 1151.8 | 969.5
18195 | 15.29 | 213.96 | 59.779 | 0.03872 | 182.31 | 1151.8 |  | 18195 | 213.96 | 15.29 | 59.779 | 0.03872 | 182.31 | 1151.8 | 969.49
18196 | 15.293 | 213.97 | 59.779 | 0.038727 | 182.32 | 1151.8 |  | 18196 | 213.97 | 15.293 | 59.779 | 0.038727 | 182.32 | 1151.8 | 969.48
18197 | 15.296 | 213.98 | 59.778 | 0.038734 | 182.33 | 1151.8 |  | 18197 | 213.98 | 15.296 | 59.778 | 0.038734 | 182.33 | 1151.8 | 969.47
18198 | 15.299 | 213.99 | 59.778 | 0.038741 | 182.34 | 1151.8 |  | 18198 | 213.99 | 15.299 | 59.778 | 0.038741 | 182.34 | 1151.8 | 969.46
18199 | 15.302 | 214 | 59.778 | 0.038749 | 182.35 | 1151.8 |  | 18199 | 214 | 15.302 | 59.778 | 0.038749 | 182.35 | 1151.8 | 969.45
18200 | 15.305 | 214.01 | 59.778 | 0.038756 | 182.36 | 1151.8 |  | 18200 | 214.01 | 15.305 | 59.778 | 0.038756 | 182.36 | 1151.8 | 969.44
18201 | 15.308 | 214.02 | 59.777 | 0.038763 | 182.37 | 1151.8 |  | 18201 | 214.02 | 15.308 | 59.777 | 0.038763 | 182.37 | 1151.8 | 969.43
18202 | 15.311 | 214.03 | 59.777 | 0.03877 | 182.38 | 1151.8 |  | 18202 | 214.03 | 15.311 | 59.777 | 0.03877 | 182.38 | 1151.8 | 969.42
18203 | 15.314 | 214.04 | 59.777 | 0.038777 | 182.39 | 1151.8 |  | 18203 | 214.04 | 15.314 | 59.777 | 0.038777 | 182.39 | 1151.8 | 969.41
18204 | 15.317 | 214.05 | 59.777 | 0.038784 | 182.4 | 1151.8 |  | 18204 | 214.05 | 15.317 | 59.777 | 0.038784 | 182.4 | 1151.8 | 969.4
18205 | 15.32 | 214.06 | 59.776 | 0.038791 | 182.41 | 1151.8 |  | 18205 | 214.06 | 15.32 | 59.776 | 0.038791 | 182.41 | 1151.8 | 969.39
18206 | 15.323 | 214.07 | 59.776 | 0.038799 | 182.42 | 1151.8 |  | 18206 | 214.07 | 15.323 | 59.776 | 0.038799 | 182.42 | 1151.8 | 969.38
18207 | 15.326 | 214.08 | 59.776 | 0.038806 | 182.43 | 1151.8 |  | 18207 | 214.08 | 15.326 | 59.776 | 0.038806 | 182.43 | 1151.8 | 969.37
18208 | 15.329 | 214.09 | 59.776 | 0.038813 | 182.44 | 1151.8 |  | 18208 | 214.09 | 15.329 | 59.776 | 0.038813 | 182.44 | 1151.8 | 969.36
18209 | 15.333 | 214.1 | 59.775 | 0.03882 | 182.45 | 1151.8 |  | 18209 | 214.1 | 15.333 | 59.775 | 0.03882 | 182.45 | 1151.8 | 969.35
18210 | 15.336 | 214.11 | 59.775 | 0.038827 | 182.46 | 1151.9 |  | 18210 | 214.11 | 15.336 | 59.775 | 0.038827 | 182.46 | 1151.9 | 969.44
18211 | 15.339 | 214.12 | 59.775 | 0.038834 | 182.47 | 1151.9 |  | 18211 | 214.12 | 15.339 | 59.775 | 0.038834 | 182.47 | 1151.9 | 969.43
18212 | 15.342 | 214.13 | 59.775 | 0.038841 | 182.48 | 1151.9 |  | 18212 | 214.13 | 15.342 | 59.775 | 0.038841 | 182.48 | 1151.9 | 969.42
18213 | 15.345 | 214.14 | 59.774 | 0.038849 | 182.49 | 1151.9 |  | 18213 | 214.14 | 15.345 | 59.774 | 0.038849 | 182.49 | 1151.9 | 969.41
18214 | 15.348 | 214.15 | 59.774 | 0.038856 | 182.5 | 1151.9 |  | 18214 | 214.15 | 15.348 | 59.774 | 0.038856 | 182.5 | 1151.9 | 969.4
18215 | 15.351 | 214.16 | 59.774 | 0.038863 | 182.51 | 1151.9 |  | 18215 | 214.16 | 15.351 | 59.774 | 0.038863 | 182.51 | 1151.9 | 969.39
18216 | 15.354 | 214.17 | 59.774 | 0.03887 | 182.52 | 1151.9 |  | 18216 | 214.17 | 15.354 | 59.774 | 0.03887 | 182.52 | 1151.9 | 969.38
18217 | 15.357 | 214.18 | 59.773 | 0.038877 | 182.53 | 1151.9 |  | 18217 | 214.18 | 15.357 | 59.773 | 0.038877 | 182.53 | 1151.9 | 969.37
18218 | 15.36 | 214.19 | 59.773 | 0.038884 | 182.54 | 1151.9 |  | 18218 | 214.19 | 15.36 | 59.773 | 0.038884 | 182.54 | 1151.9 | 969.36
18219 | 15.363 | 214.2 | 59.773 | 0.038891 | 182.55 | 1151.9 |  | 18219 | 214.2 | 15.363 | 59.773 | 0.038891 | 182.55 | 1151.9 | 969.35
18220 | 15.366 | 214.21 | 59.773 | 0.038899 | 182.56 | 1151.9 |  | 18220 | 214.21 | 15.366 | 59.773 | 0.038899 | 182.56 | 1151.9 | 969.34
18221 | 15.369 | 214.22 | 59.772 | 0.038906 | 182.57 | 1151.9 |  | 18221 | 214.22 | 15.369 | 59.772 | 0.038906 | 182.57 | 1151.9 | 969.33
18222 | 15.372 | 214.23 | 59.772 | 0.038913 | 182.58 | 1151.9 |  | 18222 | 214.23 | 15.372 | 59.772 | 0.038913 | 182.58 | 1151.9 | 969.32
18223 | 15.375 | 214.24 | 59.772 | 0.03892 | 182.59 | 1151.9 |  | 18223 | 214.24 | 15.375 | 59.772 | 0.03892 | 182.59 | 1151.9 | 969.31
18224 | 15.378 | 214.25 | 59.772 | 0.038927 | 182.6 | 1151.9 |  | 18224 | 214.25 | 15.378 | 59.772 | 0.038927 | 182.6 | 1151.9 | 969.3
18225 | 15.381 | 214.26 | 59.771 | 0.038934 | 182.61 | 1151.9 |  | 18225 | 214.26 | 15.381 | 59.771 | 0.038934 | 182.61 | 1151.9 | 969.29
18226 | 15.384 | 214.27 | 59.771 | 0.038942 | 182.62 | 1151.9 |  | 18226 | 214.27 | 15.384 | 59.771 | 0.038942 | 182.62 | 1151.9 | 969.28
18227 | 15.387 | 214.28 | 59.771 | 0.038949 | 182.63 | 1151.9 |  | 18227 | 214.28 | 15.387 | 59.771 | 0.038949 | 182.63 | 1151.9 | 969.27
18228 | 15.39 | 214.29 | 59.771 | 0.038956 | 182.64 | 1151.9 |  | 18228 | 214.29 | 15.39 | 59.771 | 0.038956 | 182.64 | 1151.9 | 969.26
18229 | 15.393 | 214.3 | 59.77 | 0.038963 | 182.65 | 1151.9 |  | 18229 | 214.3 | 15.393 | 59.77 | 0.038963 | 182.65 | 1151.9 | 969.25
18230 | 15.396 | 214.31 | 59.77 | 0.03897 | 182.66 | 1151.9 |  | 18230 | 214.31 | 15.396 | 59.77 | 0.03897 | 182.66 | 1151.9 | 969.24
18231 | 15.399 | 214.32 | 59.77 | 0.038977 | 182.67 | 1151.9 |  | 18231 | 214.32 | 15.399 | 59.77 | 0.038977 | 182.67 | 1151.9 | 969.23
18232 | 15.402 | 214.33 | 59.77 | 0.038985 | 182.68 | 1151.9 |  | 18232 | 214.33 | 15.402 | 59.77 | 0.038985 | 182.68 | 1151.9 | 969.22
18233 | 15.405 | 214.34 | 59.769 | 0.038992 | 182.69 | 1151.9 |  | 18233 | 214.34 | 15.405 | 59.769 | 0.038992 | 182.69 | 1151.9 | 969.21
18234 | 15.408 | 214.35 | 59.769 | 0.038999 | 182.7 | 1151.9 |  | 18234 | 214.35 | 15.408 | 59.769 | 0.038999 | 182.7 | 1151.9 | 969.2
18235 | 15.411 | 214.36 | 59.769 | 0.039006 | 182.71 | 1151.9 |  | 18235 | 214.36 | 15.411 | 59.769 | 0.039006 | 182.71 | 1151.9 | 969.19
18236 | 15.414 | 214.37 | 59.769 | 0.039013 | 182.72 | 1151.9 |  | 18236 | 214.37 | 15.414 | 59.769 | 0.039013 | 182.72 | 1151.9 | 969.18
18237 | 15.417 | 214.38 | 59.768 | 0.039021 | 182.73 | 1152 |  | 18237 | 214.38 | 15.417 | 59.768 | 0.039021 | 182.73 | 1152 | 969.27
18238 | 15.42 | 214.39 | 59.768 | 0.039028 | 182.74 | 1152 |  | 18238 | 214.39 | 15.42 | 59.768 | 0.039028 | 182.74 | 1152 | 969.26
18239 | 15.423 | 214.4 | 59.768 | 0.039035 | 182.75 | 1152 |  | 18239 | 214.4 | 15.423 | 59.768 | 0.039035 | 182.75 | 1152 | 969.25
18240 | 15.426 | 214.41 | 59.768 | 0.039042 | 182.76 | 1152 |  | 18240 | 214.41 | 15.426 | 59.768 | 0.039042 | 182.76 | 1152 | 969.24
18241 | 15.429 | 214.42 | 59.767 | 0.039049 | 182.77 | 1152 |  | 18241 | 214.42 | 15.429 | 59.767 | 0.039049 | 182.77 | 1152 | 969.23
18242 | 15.432 | 214.43 | 59.767 | 0.039056 | 182.78 | 1152 |  | 18242 | 214.43 | 15.432 | 59.767 | 0.039056 | 182.78 | 1152 | 969.22
18243 | 15.435 | 214.44 | 59.767 | 0.039064 | 182.79 | 1152 |  | 18243 | 214.44 | 15.435 | 59.767 | 0.039064 | 182.79 | 1152 | 969.21
18244 | 15.438 | 214.45 | 59.767 | 0.039071 | 182.8 | 1152 |  | 18244 | 214.45 | 15.438 | 59.767 | 0.039071 | 182.8 | 1152 | 969.2
18245 | 15.441 | 214.46 | 59.766 | 0.039078 | 182.81 | 1152 |  | 18245 | 214.46 | 15.441 | 59.766 | 0.039078 | 182.81 | 1152 | 969.19
18246 | 15.445 | 214.47 | 59.766 | 0.039085 | 182.82 | 1152 |  | 18246 | 214.47 | 15.445 | 59.766 | 0.039085 | 182.82 | 1152 | 969.18
18247 | 15.448 | 214.48 | 59.766 | 0.039092 | 182.83 | 1152 |  | 18247 | 214.48 | 15.448 | 59.766 | 0.039092 | 182.83 | 1152 | 969.17
18248 | 15.451 | 214.49 | 59.766 | 0.0391 | 182.84 | 1152 |  | 18248 | 214.49 | 15.451 | 59.766 | 0.0391 | 182.84 | 1152 | 969.16
18249 | 15.454 | 214.5 | 59.765 | 0.039107 | 182.85 | 1152 |  | 18249 | 214.5 | 15.454 | 59.765 | 0.039107 | 182.85 | 1152 | 969.15
18250 | 15.457 | 214.51 | 59.765 | 0.039114 | 182.86 | 1152 |  | 18250 | 214.51 | 15.457 | 59.765 | 0.039114 | 182.86 | 1152 | 969.14
18251 | 15.46 | 214.52 | 59.765 | 0.039121 | 182.87 | 1152 |  | 18251 | 214.52 | 15.46 | 59.765 | 0.039121 | 182.87 | 1152 | 969.13
18252 | 15.463 | 214.53 | 59.765 | 0.039128 | 182.88 | 1152 |  | 18252 | 214.53 | 15.463 | 59.765 | 0.039128 | 182.88 | 1152 | 969.12
18253 | 15.466 | 214.54 | 59.764 | 0.039135 | 182.89 | 1152 |  | 18253 | 214.54 | 15.466 | 59.764 | 0.039135 | 182.89 | 1152 | 969.11
18254 | 15.469 | 214.55 | 59.764 | 0.039143 | 182.9 | 1152 |  | 18254 | 214.55 | 15.469 | 59.764 | 0.039143 | 182.9 | 1152 | 969.1
18255 | 15.472 | 214.56 | 59.764 | 0.03915 | 182.91 | 1152 |  | 18255 | 214.56 | 15.472 | 59.764 | 0.03915 | 182.91 | 1152 | 969.09
18256 | 15.475 | 214.57 | 59.764 | 0.039157 | 182.92 | 1152 |  | 18256 | 214.57 | 15.475 | 59.764 | 0.039157 | 182.92 | 1152 | 969.08
18257 | 15.478 | 214.58 | 59.763 | 0.039164 | 182.93 | 1152 |  | 18257 | 214.58 | 15.478 | 59.763 | 0.039164 | 182.93 | 1152 | 969.07
18258 | 15.481 | 214.59 | 59.763 | 0.039171 | 182.94 | 1152 |  | 18258 | 214.59 | 15.481 | 59.763 | 0.039171 | 182.94 | 1152 | 969.06
18259 | 15.484 | 214.6 | 59.763 | 0.039179 | 182.95 | 1152 |  | 18259 | 214.6 | 15.484 | 59.763 | 0.039179 | 182.95 | 1152 | 969.05
18260 | 15.487 | 214.61 | 59.763 | 0.039186 | 182.96 | 1152 |  | 18260 | 214.61 | 15.487 | 59.763 | 0.039186 | 182.96 | 1152 | 969.04
18261 | 15.49 | 214.62 | 59.762 | 0.039193 | 182.97 | 1152 |  | 18261 | 214.62 | 15.49 | 59.762 | 0.039193 | 182.97 | 1152 | 969.03
18262 | 15.493 | 214.63 | 59.762 | 0.0392 | 182.98 | 1152 |  | 18262 | 214.63 | 15.493 | 59.762 | 0.0392 | 182.98 | 1152 | 969.02
18263 | 15.496 | 214.64 | 59.762 | 0.039207 | 182.99 | 1152.1 |  | 18263 | 214.64 | 15.496 | 59.762 | 0.039207 | 182.99 | 1152.1 | 969.11
18264 | 15.499 | 214.65 | 59.762 | 0.039215 | 183 | 1152.1 |  | 18264 | 214.65 | 15.499 | 59.762 | 0.039215 | 183 | 1152.1 | 969.1
18265 | 15.502 | 214.66 | 59.761 | 0.039222 | 183.01 | 1152.1 |  | 18265 | 214.66 | 15.502 | 59.761 | 0.039222 | 183.01 | 1152.1 | 969.09
18266 | 15.505 | 214.67 | 59.761 | 0.039229 | 183.02 | 1152.1 |  | 18266 | 214.67 | 15.505 | 59.761 | 0.039229 | 183.02 | 1152.1 | 969.08
18267 | 15.508 | 214.68 | 59.761 | 0.039236 | 183.03 | 1152.1 |  | 18267 | 214.68 | 15.508 | 59.761 | 0.039236 | 183.03 | 1152.1 | 969.07
18268 | 15.511 | 214.69 | 59.761 | 0.039244 | 183.04 | 1152.1 |  | 18268 | 214.69 | 15.511 | 59.761 | 0.039244 | 183.04 | 1152.1 | 969.06
18269 | 15.514 | 214.7 | 59.76 | 0.039251 | 183.05 | 1152.1 |  | 18269 | 214.7 | 15.514 | 59.76 | 0.039251 | 183.05 | 1152.1 | 969.05
18270 | 15.518 | 214.71 | 59.76 | 0.039258 | 183.06 | 1152.1 |  | 18270 | 214.71 | 15.518 | 59.76 | 0.039258 | 183.06 | 1152.1 | 969.04
18271 | 15.521 | 214.72 | 59.76 | 0.039265 | 183.07 | 1152.1 |  | 18271 | 214.72 | 15.521 | 59.76 | 0.039265 | 183.07 | 1152.1 | 969.03
18272 | 15.524 | 214.73 | 59.76 | 0.039272 | 183.08 | 1152.1 |  | 18272 | 214.73 | 15.524 | 59.76 | 0.039272 | 183.08 | 1152.1 | 969.02
18273 | 15.527 | 214.74 | 59.759 | 0.03928 | 183.09 | 1152.1 |  | 18273 | 214.74 | 15.527 | 59.759 | 0.03928 | 183.09 | 1152.1 | 969.01
18274 | 15.53 | 214.75 | 59.759 | 0.039287 | 183.1 | 1152.1 |  | 18274 | 214.75 | 15.53 | 59.759 | 0.039287 | 183.1 | 1152.1 | 969
18275 | 15.533 | 214.76 | 59.759 | 0.039294 | 183.11 | 1152.1 |  | 18275 | 214.76 | 15.533 | 59.759 | 0.039294 | 183.11 | 1152.1 | 968.99
18276 | 15.536 | 214.77 | 59.758 | 0.039301 | 183.12 | 1152.1 |  | 18276 | 214.77 | 15.536 | 59.758 | 0.039301 | 183.12 | 1152.1 | 968.98
18277 | 15.539 | 214.78 | 59.758 | 0.039308 | 183.13 | 1152.1 |  | 18277 | 214.78 | 15.539 | 59.758 | 0.039308 | 183.13 | 1152.1 | 968.97
18278 | 15.542 | 214.79 | 59.758 | 0.039316 | 183.14 | 1152.1 |  | 18278 | 214.79 | 15.542 | 59.758 | 0.039316 | 183.14 | 1152.1 | 968.96
18279 | 15.545 | 214.8 | 59.758 | 0.039323 | 183.15 | 1152.1 |  | 18279 | 214.8 | 15.545 | 59.758 | 0.039323 | 183.15 | 1152.1 | 968.95
18280 | 15.548 | 214.81 | 59.757 | 0.03933 | 183.16 | 1152.1 |  | 18280 | 214.81 | 15.548 | 59.757 | 0.03933 | 183.16 | 1152.1 | 968.94
18281 | 15.551 | 214.82 | 59.757 | 0.039337 | 183.17 | 1152.1 |  | 18281 | 214.82 | 15.551 | 59.757 | 0.039337 | 183.17 | 1152.1 | 968.93
18282 | 15.554 | 214.83 | 59.757 | 0.039345 | 183.18 | 1152.1 |  | 18282 | 214.83 | 15.554 | 59.757 | 0.039345 | 183.18 | 1152.1 | 968.92
18283 | 15.557 | 214.84 | 59.757 | 0.039352 | 183.19 | 1152.1 |  | 18283 | 214.84 | 15.557 | 59.757 | 0.039352 | 183.19 | 1152.1 | 968.91
18284 | 15.56 | 214.85 | 59.756 | 0.039359 | 183.2 | 1152.1 |  | 18284 | 214.85 | 15.56 | 59.756 | 0.039359 | 183.2 | 1152.1 | 968.9
18285 | 15.563 | 214.86 | 59.756 | 0.039366 | 183.21 | 1152.1 |  | 18285 | 214.86 | 15.563 | 59.756 | 0.039366 | 183.21 | 1152.1 | 968.89
18286 | 15.566 | 214.87 | 59.756 | 0.039373 | 183.22 | 1152.1 |  | 18286 | 214.87 | 15.566 | 59.756 | 0.039373 | 183.22 | 1152.1 | 968.88
18287 | 15.569 | 214.88 | 59.756 | 0.039381 | 183.23 | 1152.1 |  | 18287 | 214.88 | 15.569 | 59.756 | 0.039381 | 183.23 | 1152.1 | 968.87
18288 | 15.572 | 214.89 | 59.755 | 0.039388 | 183.24 | 1152.1 |  | 18288 | 214.89 | 15.572 | 59.755 | 0.039388 | 183.24 | 1152.1 | 968.86
18289 | 15.576 | 214.9 | 59.755 | 0.039395 | 183.25 | 1152.1 |  | 18289 | 214.9 | 15.576 | 59.755 | 0.039395 | 183.25 | 1152.1 | 968.85
18290 | 15.579 | 214.91 | 59.755 | 0.039402 | 183.26 | 1152.2 |  | 18290 | 214.91 | 15.579 | 59.755 | 0.039402 | 183.26 | 1152.2 | 968.94
18291 | 15.582 | 214.92 | 59.755 | 0.03941 | 183.27 | 1152.2 |  | 18291 | 214.92 | 15.582 | 59.755 | 0.03941 | 183.27 | 1152.2 | 968.93
18292 | 15.585 | 214.93 | 59.754 | 0.039417 | 183.28 | 1152.2 |  | 18292 | 214.93 | 15.585 | 59.754 | 0.039417 | 183.28 | 1152.2 | 968.92
18293 | 15.588 | 214.94 | 59.754 | 0.039424 | 183.29 | 1152.2 |  | 18293 | 214.94 | 15.588 | 59.754 | 0.039424 | 183.29 | 1152.2 | 968.91
18294 | 15.591 | 214.95 | 59.754 | 0.039431 | 183.3 | 1152.2 |  | 18294 | 214.95 | 15.591 | 59.754 | 0.039431 | 183.3 | 1152.2 | 968.9
18295 | 15.594 | 214.96 | 59.754 | 0.039439 | 183.31 | 1152.2 |  | 18295 | 214.96 | 15.594 | 59.754 | 0.039439 | 183.31 | 1152.2 | 968.89
18296 | 15.597 | 214.97 | 59.753 | 0.039446 | 183.32 | 1152.2 |  | 18296 | 214.97 | 15.597 | 59.753 | 0.039446 | 183.32 | 1152.2 | 968.88
18297 | 15.6 | 214.98 | 59.753 | 0.039453 | 183.33 | 1152.2 |  | 18297 | 214.98 | 15.6 | 59.753 | 0.039453 | 183.33 | 1152.2 | 968.87
18298 | 15.603 | 214.99 | 59.753 | 0.03946 | 183.34 | 1152.2 |  | 18298 | 214.99 | 15.603 | 59.753 | 0.03946 | 183.34 | 1152.2 | 968.86
18299 | 15.606 | 215 | 59.753 | 0.039468 | 183.36 | 1152.2 |  | 18299 | 215 | 15.606 | 59.753 | 0.039468 | 183.36 | 1152.2 | 968.84
18300 | 15.609 | 215.01 | 59.752 | 0.039475 | 183.37 | 1152.2 |  | 18300 | 215.01 | 15.609 | 59.752 | 0.039475 | 183.37 | 1152.2 | 968.83
18301 | 15.612 | 215.02 | 59.752 | 0.039482 | 183.38 | 1152.2 |  | 18301 | 215.02 | 15.612 | 59.752 | 0.039482 | 183.38 | 1152.2 | 968.82
18302 | 15.615 | 215.03 | 59.752 | 0.039489 | 183.39 | 1152.2 |  | 18302 | 215.03 | 15.615 | 59.752 | 0.039489 | 183.39 | 1152.2 | 968.81
18303 | 15.618 | 215.04 | 59.752 | 0.039497 | 183.4 | 1152.2 |  | 18303 | 215.04 | 15.618 | 59.752 | 0.039497 | 183.4 | 1152.2 | 968.8
18304 | 15.621 | 215.05 | 59.751 | 0.039504 | 183.41 | 1152.2 |  | 18304 | 215.05 | 15.621 | 59.751 | 0.039504 | 183.41 | 1152.2 | 968.79
18305 | 15.625 | 215.06 | 59.751 | 0.039511 | 183.42 | 1152.2 |  | 18305 | 215.06 | 15.625 | 59.751 | 0.039511 | 183.42 | 1152.2 | 968.78
18306 | 15.628 | 215.07 | 59.751 | 0.039518 | 183.43 | 1152.2 |  | 18306 | 215.07 | 15.628 | 59.751 | 0.039518 | 183.43 | 1152.2 | 968.77
18307 | 15.631 | 215.08 | 59.751 | 0.039526 | 183.44 | 1152.2 |  | 18307 | 215.08 | 15.631 | 59.751 | 0.039526 | 183.44 | 1152.2 | 968.76
18308 | 15.634 | 215.09 | 59.75 | 0.039533 | 183.45 | 1152.2 |  | 18308 | 215.09 | 15.634 | 59.75 | 0.039533 | 183.45 | 1152.2 | 968.75
18309 | 15.637 | 215.1 | 59.75 | 0.03954 | 183.46 | 1152.2 |  | 18309 | 215.1 | 15.637 | 59.75 | 0.03954 | 183.46 | 1152.2 | 968.74
18310 | 15.64 | 215.11 | 59.75 | 0.039547 | 183.47 | 1152.2 |  | 18310 | 215.11 | 15.64 | 59.75 | 0.039547 | 183.47 | 1152.2 | 968.73
18311 | 15.643 | 215.12 | 59.75 | 0.039555 | 183.48 | 1152.2 |  | 18311 | 215.12 | 15.643 | 59.75 | 0.039555 | 183.48 | 1152.2 | 968.72
18312 | 15.646 | 215.13 | 59.749 | 0.039562 | 183.49 | 1152.2 |  | 18312 | 215.13 | 15.646 | 59.749 | 0.039562 | 183.49 | 1152.2 | 968.71
18313 | 15.649 | 215.14 | 59.749 | 0.039569 | 183.5 | 1152.2 |  | 18313 | 215.14 | 15.649 | 59.749 | 0.039569 | 183.5 | 1152.2 | 968.7
18314 | 15.652 | 215.15 | 59.749 | 0.039576 | 183.51 | 1152.2 |  | 18314 | 215.15 | 15.652 | 59.749 | 0.039576 | 183.51 | 1152.2 | 968.69
18315 | 15.655 | 215.16 | 59.749 | 0.039584 | 183.52 | 1152.2 |  | 18315 | 215.16 | 15.655 | 59.749 | 0.039584 | 183.52 | 1152.2 | 968.68
18316 | 15.658 | 215.17 | 59.748 | 0.039591 | 183.53 | 1152.2 |  | 18316 | 215.17 | 15.658 | 59.748 | 0.039591 | 183.53 | 1152.2 | 968.67
18317 | 15.661 | 215.18 | 59.748 | 0.039598 | 183.54 | 1152.3 |  | 18317 | 215.18 | 15.661 | 59.748 | 0.039598 | 183.54 | 1152.3 | 968.76
18318 | 15.664 | 215.19 | 59.748 | 0.039605 | 183.55 | 1152.3 |  | 18318 | 215.19 | 15.664 | 59.748 | 0.039605 | 183.55 | 1152.3 | 968.75
18319 | 15.668 | 215.2 | 59.748 | 0.039613 | 183.56 | 1152.3 |  | 18319 | 215.2 | 15.668 | 59.748 | 0.039613 | 183.56 | 1152.3 | 968.74
18320 | 15.671 | 215.21 | 59.747 | 0.03962 | 183.57 | 1152.3 |  | 18320 | 215.21 | 15.671 | 59.747 | 0.03962 | 183.57 | 1152.3 | 968.73
18321 | 15.674 | 215.22 | 59.747 | 0.039627 | 183.58 | 1152.3 |  | 18321 | 215.22 | 15.674 | 59.747 | 0.039627 | 183.58 | 1152.3 | 968.72
18322 | 15.677 | 215.23 | 59.747 | 0.039634 | 183.59 | 1152.3 |  | 18322 | 215.23 | 15.677 | 59.747 | 0.039634 | 183.59 | 1152.3 | 968.71
18323 | 15.68 | 215.24 | 59.747 | 0.039642 | 183.6 | 1152.3 |  | 18323 | 215.24 | 15.68 | 59.747 | 0.039642 | 183.6 | 1152.3 | 968.7
18324 | 15.683 | 215.25 | 59.746 | 0.039649 | 183.61 | 1152.3 |  | 18324 | 215.25 | 15.683 | 59.746 | 0.039649 | 183.61 | 1152.3 | 968.69
18325 | 15.686 | 215.26 | 59.746 | 0.039656 | 183.62 | 1152.3 |  | 18325 | 215.26 | 15.686 | 59.746 | 0.039656 | 183.62 | 1152.3 | 968.68
18326 | 15.689 | 215.27 | 59.746 | 0.039664 | 183.63 | 1152.3 |  | 18326 | 215.27 | 15.689 | 59.746 | 0.039664 | 183.63 | 1152.3 | 968.67
18327 | 15.692 | 215.28 | 59.746 | 0.039671 | 183.64 | 1152.3 |  | 18327 | 215.28 | 15.692 | 59.746 | 0.039671 | 183.64 | 1152.3 | 968.66
18328 | 15.695 | 215.29 | 59.745 | 0.039678 | 183.65 | 1152.3 |  | 18328 | 215.29 | 15.695 | 59.745 | 0.039678 | 183.65 | 1152.3 | 968.65
18329 | 15.698 | 215.3 | 59.745 | 0.039685 | 183.66 | 1152.3 |  | 18329 | 215.3 | 15.698 | 59.745 | 0.039685 | 183.66 | 1152.3 | 968.64
18330 | 15.701 | 215.31 | 59.745 | 0.039693 | 183.67 | 1152.3 |  | 18330 | 215.31 | 15.701 | 59.745 | 0.039693 | 183.67 | 1152.3 | 968.63
18331 | 15.704 | 215.32 | 59.745 | 0.0397 | 183.68 | 1152.3 |  | 18331 | 215.32 | 15.704 | 59.745 | 0.0397 | 183.68 | 1152.3 | 968.62
18332 | 15.707 | 215.33 | 59.744 | 0.039707 | 183.69 | 1152.3 |  | 18332 | 215.33 | 15.707 | 59.744 | 0.039707 | 183.69 | 1152.3 | 968.61
18333 | 15.711 | 215.34 | 59.744 | 0.039714 | 183.7 | 1152.3 |  | 18333 | 215.34 | 15.711 | 59.744 | 0.039714 | 183.7 | 1152.3 | 968.6
18334 | 15.714 | 215.35 | 59.744 | 0.039722 | 183.71 | 1152.3 |  | 18334 | 215.35 | 15.714 | 59.744 | 0.039722 | 183.71 | 1152.3 | 968.59
18335 | 15.717 | 215.36 | 59.744 | 0.039729 | 183.72 | 1152.3 |  | 18335 | 215.36 | 15.717 | 59.744 | 0.039729 | 183.72 | 1152.3 | 968.58
18336 | 15.72 | 215.37 | 59.743 | 0.039736 | 183.73 | 1152.3 |  | 18336 | 215.37 | 15.72 | 59.743 | 0.039736 | 183.73 | 1152.3 | 968.57
18337 | 15.723 | 215.38 | 59.743 | 0.039744 | 183.74 | 1152.3 |  | 18337 | 215.38 | 15.723 | 59.743 | 0.039744 | 183.74 | 1152.3 | 968.56
18338 | 15.726 | 215.39 | 59.743 | 0.039751 | 183.75 | 1152.3 |  | 18338 | 215.39 | 15.726 | 59.743 | 0.039751 | 183.75 | 1152.3 | 968.55
18339 | 15.729 | 215.4 | 59.743 | 0.039758 | 183.76 | 1152.3 |  | 18339 | 215.4 | 15.729 | 59.743 | 0.039758 | 183.76 | 1152.3 | 968.54
18340 | 15.732 | 215.41 | 59.742 | 0.039765 | 183.77 | 1152.3 |  | 18340 | 215.41 | 15.732 | 59.742 | 0.039765 | 183.77 | 1152.3 | 968.53
18341 | 15.735 | 215.42 | 59.742 | 0.039773 | 183.78 | 1152.3 |  | 18341 | 215.42 | 15.735 | 59.742 | 0.039773 | 183.78 | 1152.3 | 968.52
18342 | 15.738 | 215.43 | 59.742 | 0.03978 | 183.79 | 1152.3 |  | 18342 | 215.43 | 15.738 | 59.742 | 0.03978 | 183.79 | 1152.3 | 968.51
18343 | 15.741 | 215.44 | 59.742 | 0.039787 | 183.8 | 1152.4 |  | 18343 | 215.44 | 15.741 | 59.742 | 0.039787 | 183.8 | 1152.4 | 968.6
18344 | 15.744 | 215.45 | 59.741 | 0.039795 | 183.81 | 1152.4 |  | 18344 | 215.45 | 15.744 | 59.741 | 0.039795 | 183.81 | 1152.4 | 968.59
18345 | 15.748 | 215.46 | 59.741 | 0.039802 | 183.82 | 1152.4 |  | 18345 | 215.46 | 15.748 | 59.741 | 0.039802 | 183.82 | 1152.4 | 968.58
18346 | 15.751 | 215.47 | 59.741 | 0.039809 | 183.83 | 1152.4 |  | 18346 | 215.47 | 15.751 | 59.741 | 0.039809 | 183.83 | 1152.4 | 968.57
18347 | 15.754 | 215.48 | 59.741 | 0.039817 | 183.84 | 1152.4 |  | 18347 | 215.48 | 15.754 | 59.741 | 0.039817 | 183.84 | 1152.4 | 968.56
18348 | 15.757 | 215.49 | 59.74 | 0.039824 | 183.85 | 1152.4 |  | 18348 | 215.49 | 15.757 | 59.74 | 0.039824 | 183.85 | 1152.4 | 968.55
18349 | 15.76 | 215.5 | 59.74 | 0.039831 | 183.86 | 1152.4 |  | 18349 | 215.5 | 15.76 | 59.74 | 0.039831 | 183.86 | 1152.4 | 968.54
18350 | 15.763 | 215.51 | 59.74 | 0.039838 | 183.87 | 1152.4 |  | 18350 | 215.51 | 15.763 | 59.74 | 0.039838 | 183.87 | 1152.4 | 968.53
18351 | 15.766 | 215.52 | 59.74 | 0.039846 | 183.88 | 1152.4 |  | 18351 | 215.52 | 15.766 | 59.74 | 0.039846 | 183.88 | 1152.4 | 968.52
18352 | 15.769 | 215.53 | 59.739 | 0.039853 | 183.89 | 1152.4 |  | 18352 | 215.53 | 15.769 | 59.739 | 0.039853 | 183.89 | 1152.4 | 968.51
18353 | 15.772 | 215.54 | 59.739 | 0.03986 | 183.9 | 1152.4 |  | 18353 | 215.54 | 15.772 | 59.739 | 0.03986 | 183.9 | 1152.4 | 968.5
18354 | 15.775 | 215.55 | 59.739 | 0.039868 | 183.91 | 1152.4 |  | 18354 | 215.55 | 15.775 | 59.739 | 0.039868 | 183.91 | 1152.4 | 968.49
18355 | 15.778 | 215.56 | 59.739 | 0.039875 | 183.92 | 1152.4 |  | 18355 | 215.56 | 15.778 | 59.739 | 0.039875 | 183.92 | 1152.4 | 968.48
18356 | 15.782 | 215.57 | 59.738 | 0.039882 | 183.93 | 1152.4 |  | 18356 | 215.57 | 15.782 | 59.738 | 0.039882 | 183.93 | 1152.4 | 968.47
18357 | 15.785 | 215.58 | 59.738 | 0.03989 | 183.94 | 1152.4 |  | 18357 | 215.58 | 15.785 | 59.738 | 0.03989 | 183.94 | 1152.4 | 968.46
18358 | 15.788 | 215.59 | 59.738 | 0.039897 | 183.95 | 1152.4 |  | 18358 | 215.59 | 15.788 | 59.738 | 0.039897 | 183.95 | 1152.4 | 968.45
18359 | 15.791 | 215.6 | 59.738 | 0.039904 | 183.96 | 1152.4 |  | 18359 | 215.6 | 15.791 | 59.738 | 0.039904 | 183.96 | 1152.4 | 968.44
18360 | 15.794 | 215.61 | 59.737 | 0.039911 | 183.97 | 1152.4 |  | 18360 | 215.61 | 15.794 | 59.737 | 0.039911 | 183.97 | 1152.4 | 968.43
18361 | 15.797 | 215.62 | 59.737 | 0.039919 | 183.98 | 1152.4 |  | 18361 | 215.62 | 15.797 | 59.737 | 0.039919 | 183.98 | 1152.4 | 968.42
18362 | 15.8 | 215.63 | 59.737 | 0.039926 | 183.99 | 1152.4 |  | 18362 | 215.63 | 15.8 | 59.737 | 0.039926 | 183.99 | 1152.4 | 968.41
18363 | 15.803 | 215.64 | 59.737 | 0.039933 | 184 | 1152.4 |  | 18363 | 215.64 | 15.803 | 59.737 | 0.039933 | 184 | 1152.4 | 968.4
18364 | 15.806 | 215.65 | 59.736 | 0.039941 | 184.01 | 1152.4 |  | 18364 | 215.65 | 15.806 | 59.736 | 0.039941 | 184.01 | 1152.4 | 968.39
18365 | 15.809 | 215.66 | 59.736 | 0.039948 | 184.02 | 1152.4 |  | 18365 | 215.66 | 15.809 | 59.736 | 0.039948 | 184.02 | 1152.4 | 968.38
18366 | 15.812 | 215.67 | 59.736 | 0.039955 | 184.03 | 1152.4 |  | 18366 | 215.67 | 15.812 | 59.736 | 0.039955 | 184.03 | 1152.4 | 968.37
18367 | 15.816 | 215.68 | 59.736 | 0.039963 | 184.04 | 1152.4 |  | 18367 | 215.68 | 15.816 | 59.736 | 0.039963 | 184.04 | 1152.4 | 968.36
18368 | 15.819 | 215.69 | 59.735 | 0.03997 | 184.05 | 1152.4 |  | 18368 | 215.69 | 15.819 | 59.735 | 0.03997 | 184.05 | 1152.4 | 968.35
18369 | 15.822 | 215.7 | 59.735 | 0.039977 | 184.06 | 1152.4 |  | 18369 | 215.7 | 15.822 | 59.735 | 0.039977 | 184.06 | 1152.4 | 968.34
18370 | 15.825 | 215.71 | 59.735 | 0.039985 | 184.07 | 1152.5 |  | 18370 | 215.71 | 15.825 | 59.735 | 0.039985 | 184.07 | 1152.5 | 968.43
18371 | 15.828 | 215.72 | 59.735 | 0.039992 | 184.08 | 1152.5 |  | 18371 | 215.72 | 15.828 | 59.735 | 0.039992 | 184.08 | 1152.5 | 968.42
18372 | 15.831 | 215.73 | 59.734 | 0.039999 | 184.09 | 1152.5 |  | 18372 | 215.73 | 15.831 | 59.734 | 0.039999 | 184.09 | 1152.5 | 968.41
18373 | 15.834 | 215.74 | 59.734 | 0.040007 | 184.1 | 1152.5 |  | 18373 | 215.74 | 15.834 | 59.734 | 0.040007 | 184.1 | 1152.5 | 968.4
18374 | 15.837 | 215.75 | 59.734 | 0.040014 | 184.11 | 1152.5 |  | 18374 | 215.75 | 15.837 | 59.734 | 0.040014 | 184.11 | 1152.5 | 968.39
18375 | 15.84 | 215.76 | 59.734 | 0.040021 | 184.12 | 1152.5 |  | 18375 | 215.76 | 15.84 | 59.734 | 0.040021 | 184.12 | 1152.5 | 968.38
18376 | 15.843 | 215.77 | 59.733 | 0.040029 | 184.13 | 1152.5 |  | 18376 | 215.77 | 15.843 | 59.733 | 0.040029 | 184.13 | 1152.5 | 968.37
18377 | 15.847 | 215.78 | 59.733 | 0.040036 | 184.14 | 1152.5 |  | 18377 | 215.78 | 15.847 | 59.733 | 0.040036 | 184.14 | 1152.5 | 968.36
18378 | 15.85 | 215.79 | 59.733 | 0.040043 | 184.15 | 1152.5 |  | 18378 | 215.79 | 15.85 | 59.733 | 0.040043 | 184.15 | 1152.5 | 968.35
18379 | 15.853 | 215.8 | 59.733 | 0.040051 | 184.16 | 1152.5 |  | 18379 | 215.8 | 15.853 | 59.733 | 0.040051 | 184.16 | 1152.5 | 968.34
18380 | 15.856 | 215.81 | 59.732 | 0.040058 | 184.17 | 1152.5 |  | 18380 | 215.81 | 15.856 | 59.732 | 0.040058 | 184.17 | 1152.5 | 968.33
18381 | 15.859 | 215.82 | 59.732 | 0.040065 | 184.18 | 1152.5 |  | 18381 | 215.82 | 15.859 | 59.732 | 0.040065 | 184.18 | 1152.5 | 968.32
18382 | 15.862 | 215.83 | 59.732 | 0.040073 | 184.19 | 1152.5 |  | 18382 | 215.83 | 15.862 | 59.732 | 0.040073 | 184.19 | 1152.5 | 968.31
18383 | 15.865 | 215.84 | 59.732 | 0.04008 | 184.2 | 1152.5 |  | 18383 | 215.84 | 15.865 | 59.732 | 0.04008 | 184.2 | 1152.5 | 968.3
18384 | 15.868 | 215.85 | 59.731 | 0.040087 | 184.21 | 1152.5 |  | 18384 | 215.85 | 15.868 | 59.731 | 0.040087 | 184.21 | 1152.5 | 968.29
18385 | 15.871 | 215.86 | 59.731 | 0.040095 | 184.22 | 1152.5 |  | 18385 | 215.86 | 15.871 | 59.731 | 0.040095 | 184.22 | 1152.5 | 968.28
18386 | 15.874 | 215.87 | 59.731 | 0.040102 | 184.23 | 1152.5 |  | 18386 | 215.87 | 15.874 | 59.731 | 0.040102 | 184.23 | 1152.5 | 968.27
18387 | 15.878 | 215.88 | 59.731 | 0.040109 | 184.24 | 1152.5 |  | 18387 | 215.88 | 15.878 | 59.731 | 0.040109 | 184.24 | 1152.5 | 968.26
18388 | 15.881 | 215.89 | 59.73 | 0.040117 | 184.25 | 1152.5 |  | 18388 | 215.89 | 15.881 | 59.73 | 0.040117 | 184.25 | 1152.5 | 968.25
18389 | 15.884 | 215.9 | 59.73 | 0.040124 | 184.26 | 1152.5 |  | 18389 | 215.9 | 15.884 | 59.73 | 0.040124 | 184.26 | 1152.5 | 968.24
18390 | 15.887 | 215.91 | 59.73 | 0.040131 | 184.27 | 1152.5 |  | 18390 | 215.91 | 15.887 | 59.73 | 0.040131 | 184.27 | 1152.5 | 968.23
18391 | 15.89 | 215.92 | 59.73 | 0.040139 | 184.28 | 1152.5 |  | 18391 | 215.92 | 15.89 | 59.73 | 0.040139 | 184.28 | 1152.5 | 968.22
18392 | 15.893 | 215.93 | 59.729 | 0.040146 | 184.29 | 1152.5 |  | 18392 | 215.93 | 15.893 | 59.729 | 0.040146 | 184.29 | 1152.5 | 968.21
18393 | 15.896 | 215.94 | 59.729 | 0.040153 | 184.3 | 1152.5 |  | 18393 | 215.94 | 15.896 | 59.729 | 0.040153 | 184.3 | 1152.5 | 968.2
18394 | 15.899 | 215.95 | 59.729 | 0.040161 | 184.31 | 1152.5 |  | 18394 | 215.95 | 15.899 | 59.729 | 0.040161 | 184.31 | 1152.5 | 968.19
18395 | 15.902 | 215.96 | 59.729 | 0.040168 | 184.32 | 1152.5 |  | 18395 | 215.96 | 15.902 | 59.729 | 0.040168 | 184.32 | 1152.5 | 968.18
18396 | 15.906 | 215.97 | 59.728 | 0.040175 | 184.33 | 1152.5 |  | 18396 | 215.97 | 15.906 | 59.728 | 0.040175 | 184.33 | 1152.5 | 968.17
18397 | 15.909 | 215.98 | 59.728 | 0.040183 | 184.34 | 1152.6 |  | 18397 | 215.98 | 15.909 | 59.728 | 0.040183 | 184.34 | 1152.6 | 968.26
18398 | 15.912 | 215.99 | 59.728 | 0.04019 | 184.35 | 1152.6 |  | 18398 | 215.99 | 15.912 | 59.728 | 0.04019 | 184.35 | 1152.6 | 968.25
18399 | 15.915 | 216 | 59.728 | 0.040197 | 184.36 | 1152.6 |  | 18399 | 216 | 15.915 | 59.728 | 0.040197 | 184.36 | 1152.6 | 968.24
18400 | 15.918 | 216.01 | 59.727 | 0.040205 | 184.37 | 1152.6 |  | 18400 | 216.01 | 15.918 | 59.727 | 0.040205 | 184.37 | 1152.6 | 968.23
18401 | 15.921 | 216.02 | 59.727 | 0.040212 | 184.38 | 1152.6 |  | 18401 | 216.02 | 15.921 | 59.727 | 0.040212 | 184.38 | 1152.6 | 968.22
18402 | 15.924 | 216.03 | 59.727 | 0.040219 | 184.39 | 1152.6 |  | 18402 | 216.03 | 15.924 | 59.727 | 0.040219 | 184.39 | 1152.6 | 968.21
18403 | 15.927 | 216.04 | 59.727 | 0.040227 | 184.4 | 1152.6 |  | 18403 | 216.04 | 15.927 | 59.727 | 0.040227 | 184.4 | 1152.6 | 968.2
18404 | 15.93 | 216.05 | 59.726 | 0.040234 | 184.41 | 1152.6 |  | 18404 | 216.05 | 15.93 | 59.726 | 0.040234 | 184.41 | 1152.6 | 968.19
18405 | 15.934 | 216.06 | 59.726 | 0.040242 | 184.42 | 1152.6 |  | 18405 | 216.06 | 15.934 | 59.726 | 0.040242 | 184.42 | 1152.6 | 968.18
18406 | 15.937 | 216.07 | 59.726 | 0.040249 | 184.43 | 1152.6 |  | 18406 | 216.07 | 15.937 | 59.726 | 0.040249 | 184.43 | 1152.6 | 968.17
18407 | 15.94 | 216.08 | 59.725 | 0.040256 | 184.44 | 1152.6 |  | 18407 | 216.08 | 15.94 | 59.725 | 0.040256 | 184.44 | 1152.6 | 968.16
18408 | 15.943 | 216.09 | 59.725 | 0.040264 | 184.45 | 1152.6 |  | 18408 | 216.09 | 15.943 | 59.725 | 0.040264 | 184.45 | 1152.6 | 968.15
18409 | 15.946 | 216.1 | 59.725 | 0.040271 | 184.46 | 1152.6 |  | 18409 | 216.1 | 15.946 | 59.725 | 0.040271 | 184.46 | 1152.6 | 968.14
18410 | 15.949 | 216.11 | 59.725 | 0.040278 | 184.47 | 1152.6 |  | 18410 | 216.11 | 15.949 | 59.725 | 0.040278 | 184.47 | 1152.6 | 968.13
18411 | 15.952 | 216.12 | 59.724 | 0.040286 | 184.48 | 1152.6 |  | 18411 | 216.12 | 15.952 | 59.724 | 0.040286 | 184.48 | 1152.6 | 968.12
18412 | 15.955 | 216.13 | 59.724 | 0.040293 | 184.49 | 1152.6 |  | 18412 | 216.13 | 15.955 | 59.724 | 0.040293 | 184.49 | 1152.6 | 968.11
18413 | 15.959 | 216.14 | 59.724 | 0.0403 | 184.51 | 1152.6 |  | 18413 | 216.14 | 15.959 | 59.724 | 0.0403 | 184.51 | 1152.6 | 968.09
18414 | 15.962 | 216.15 | 59.724 | 0.040308 | 184.52 | 1152.6 |  | 18414 | 216.15 | 15.962 | 59.724 | 0.040308 | 184.52 | 1152.6 | 968.08
18415 | 15.965 | 216.16 | 59.723 | 0.040315 | 184.53 | 1152.6 |  | 18415 | 216.16 | 15.965 | 59.723 | 0.040315 | 184.53 | 1152.6 | 968.07
18416 | 15.968 | 216.17 | 59.723 | 0.040323 | 184.54 | 1152.6 |  | 18416 | 216.17 | 15.968 | 59.723 | 0.040323 | 184.54 | 1152.6 | 968.06
18417 | 15.971 | 216.18 | 59.723 | 0.04033 | 184.55 | 1152.6 |  | 18417 | 216.18 | 15.971 | 59.723 | 0.04033 | 184.55 | 1152.6 | 968.05
18418 | 15.974 | 216.19 | 59.723 | 0.040337 | 184.56 | 1152.6 |  | 18418 | 216.19 | 15.974 | 59.723 | 0.040337 | 184.56 | 1152.6 | 968.04
18419 | 15.977 | 216.2 | 59.722 | 0.040345 | 184.57 | 1152.6 |  | 18419 | 216.2 | 15.977 | 59.722 | 0.040345 | 184.57 | 1152.6 | 968.03
18420 | 15.98 | 216.21 | 59.722 | 0.040352 | 184.58 | 1152.6 |  | 18420 | 216.21 | 15.98 | 59.722 | 0.040352 | 184.58 | 1152.6 | 968.02
18421 | 15.984 | 216.22 | 59.722 | 0.040359 | 184.59 | 1152.6 |  | 18421 | 216.22 | 15.984 | 59.722 | 0.040359 | 184.59 | 1152.6 | 968.01
18422 | 15.987 | 216.23 | 59.722 | 0.040367 | 184.6 | 1152.6 |  | 18422 | 216.23 | 15.987 | 59.722 | 0.040367 | 184.6 | 1152.6 | 968
18423 | 15.99 | 216.24 | 59.721 | 0.040374 | 184.61 | 1152.7 |  | 18423 | 216.24 | 15.99 | 59.721 | 0.040374 | 184.61 | 1152.7 | 968.09
18424 | 15.993 | 216.25 | 59.721 | 0.040382 | 184.62 | 1152.7 |  | 18424 | 216.25 | 15.993 | 59.721 | 0.040382 | 184.62 | 1152.7 | 968.08
18425 | 15.996 | 216.26 | 59.721 | 0.040389 | 184.63 | 1152.7 |  | 18425 | 216.26 | 15.996 | 59.721 | 0.040389 | 184.63 | 1152.7 | 968.07
18426 | 15.999 | 216.27 | 59.721 | 0.040396 | 184.64 | 1152.7 |  | 18426 | 216.27 | 15.999 | 59.721 | 0.040396 | 184.64 | 1152.7 | 968.06
18427 | 16.002 | 216.28 | 59.72 | 0.040404 | 184.65 | 1152.7 |  | 18427 | 216.28 | 16.002 | 59.72 | 0.040404 | 184.65 | 1152.7 | 968.05
18428 | 16.005 | 216.29 | 59.72 | 0.040411 | 184.66 | 1152.7 |  | 18428 | 216.29 | 16.005 | 59.72 | 0.040411 | 184.66 | 1152.7 | 968.04
18429 | 16.009 | 216.3 | 59.72 | 0.040419 | 184.67 | 1152.7 |  | 18429 | 216.3 | 16.009 | 59.72 | 0.040419 | 184.67 | 1152.7 | 968.03
18430 | 16.012 | 216.31 | 59.72 | 0.040426 | 184.68 | 1152.7 |  | 18430 | 216.31 | 16.012 | 59.72 | 0.040426 | 184.68 | 1152.7 | 968.02
18431 | 16.015 | 216.32 | 59.719 | 0.040433 | 184.69 | 1152.7 |  | 18431 | 216.32 | 16.015 | 59.719 | 0.040433 | 184.69 | 1152.7 | 968.01
18432 | 16.018 | 216.33 | 59.719 | 0.040441 | 184.7 | 1152.7 |  | 18432 | 216.33 | 16.018 | 59.719 | 0.040441 | 184.7 | 1152.7 | 968
18433 | 16.021 | 216.34 | 59.719 | 0.040448 | 184.71 | 1152.7 |  | 18433 | 216.34 | 16.021 | 59.719 | 0.040448 | 184.71 | 1152.7 | 967.99
18434 | 16.024 | 216.35 | 59.719 | 0.040455 | 184.72 | 1152.7 |  | 18434 | 216.35 | 16.024 | 59.719 | 0.040455 | 184.72 | 1152.7 | 967.98
18435 | 16.027 | 216.36 | 59.718 | 0.040463 | 184.73 | 1152.7 |  | 18435 | 216.36 | 16.027 | 59.718 | 0.040463 | 184.73 | 1152.7 | 967.97
18436 | 16.03 | 216.37 | 59.718 | 0.04047 | 184.74 | 1152.7 |  | 18436 | 216.37 | 16.03 | 59.718 | 0.04047 | 184.74 | 1152.7 | 967.96
18437 | 16.034 | 216.38 | 59.718 | 0.040478 | 184.75 | 1152.7 |  | 18437 | 216.38 | 16.034 | 59.718 | 0.040478 | 184.75 | 1152.7 | 967.95
18438 | 16.037 | 216.39 | 59.718 | 0.040485 | 184.76 | 1152.7 |  | 18438 | 216.39 | 16.037 | 59.718 | 0.040485 | 184.76 | 1152.7 | 967.94
18439 | 16.04 | 216.4 | 59.717 | 0.040492 | 184.77 | 1152.7 |  | 18439 | 216.4 | 16.04 | 59.717 | 0.040492 | 184.77 | 1152.7 | 967.93
18440 | 16.043 | 216.41 | 59.717 | 0.0405 | 184.78 | 1152.7 |  | 18440 | 216.41 | 16.043 | 59.717 | 0.0405 | 184.78 | 1152.7 | 967.92
18441 | 16.046 | 216.42 | 59.717 | 0.040507 | 184.79 | 1152.7 |  | 18441 | 216.42 | 16.046 | 59.717 | 0.040507 | 184.79 | 1152.7 | 967.91
18442 | 16.049 | 216.43 | 59.717 | 0.040515 | 184.8 | 1152.7 |  | 18442 | 216.43 | 16.049 | 59.717 | 0.040515 | 184.8 | 1152.7 | 967.9
18443 | 16.052 | 216.44 | 59.716 | 0.040522 | 184.81 | 1152.7 |  | 18443 | 216.44 | 16.052 | 59.716 | 0.040522 | 184.81 | 1152.7 | 967.89
18444 | 16.056 | 216.45 | 59.716 | 0.040529 | 184.82 | 1152.7 |  | 18444 | 216.45 | 16.056 | 59.716 | 0.040529 | 184.82 | 1152.7 | 967.88
18445 | 16.059 | 216.46 | 59.716 | 0.040537 | 184.83 | 1152.7 |  | 18445 | 216.46 | 16.059 | 59.716 | 0.040537 | 184.83 | 1152.7 | 967.87
18446 | 16.062 | 216.47 | 59.716 | 0.040544 | 184.84 | 1152.7 |  | 18446 | 216.47 | 16.062 | 59.716 | 0.040544 | 184.84 | 1152.7 | 967.86
18447 | 16.065 | 216.48 | 59.715 | 0.040552 | 184.85 | 1152.7 |  | 18447 | 216.48 | 16.065 | 59.715 | 0.040552 | 184.85 | 1152.7 | 967.85
18448 | 16.068 | 216.49 | 59.715 | 0.040559 | 184.86 | 1152.7 |  | 18448 | 216.49 | 16.068 | 59.715 | 0.040559 | 184.86 | 1152.7 | 967.84
18449 | 16.071 | 216.5 | 59.715 | 0.040566 | 184.87 | 1152.7 |  | 18449 | 216.5 | 16.071 | 59.715 | 0.040566 | 184.87 | 1152.7 | 967.83
18450 | 16.074 | 216.51 | 59.715 | 0.040574 | 184.88 | 1152.8 |  | 18450 | 216.51 | 16.074 | 59.715 | 0.040574 | 184.88 | 1152.8 | 967.92
18451 | 16.077 | 216.52 | 59.714 | 0.040581 | 184.89 | 1152.8 |  | 18451 | 216.52 | 16.077 | 59.714 | 0.040581 | 184.89 | 1152.8 | 967.91
18452 | 16.081 | 216.53 | 59.714 | 0.040589 | 184.9 | 1152.8 |  | 18452 | 216.53 | 16.081 | 59.714 | 0.040589 | 184.9 | 1152.8 | 967.9
18453 | 16.084 | 216.54 | 59.714 | 0.040596 | 184.91 | 1152.8 |  | 18453 | 216.54 | 16.084 | 59.714 | 0.040596 | 184.91 | 1152.8 | 967.89
18454 | 16.087 | 216.55 | 59.714 | 0.040604 | 184.92 | 1152.8 |  | 18454 | 216.55 | 16.087 | 59.714 | 0.040604 | 184.92 | 1152.8 | 967.88
18455 | 16.09 | 216.56 | 59.713 | 0.040611 | 184.93 | 1152.8 |  | 18455 | 216.56 | 16.09 | 59.713 | 0.040611 | 184.93 | 1152.8 | 967.87
18456 | 16.093 | 216.57 | 59.713 | 0.040618 | 184.94 | 1152.8 |  | 18456 | 216.57 | 16.093 | 59.713 | 0.040618 | 184.94 | 1152.8 | 967.86
18457 | 16.096 | 216.58 | 59.713 | 0.040626 | 184.95 | 1152.8 |  | 18457 | 216.58 | 16.096 | 59.713 | 0.040626 | 184.95 | 1152.8 | 967.85
18458 | 16.099 | 216.59 | 59.713 | 0.040633 | 184.96 | 1152.8 |  | 18458 | 216.59 | 16.099 | 59.713 | 0.040633 | 184.96 | 1152.8 | 967.84
18459 | 16.103 | 216.6 | 59.712 | 0.040641 | 184.97 | 1152.8 |  | 18459 | 216.6 | 16.103 | 59.712 | 0.040641 | 184.97 | 1152.8 | 967.83
18460 | 16.106 | 216.61 | 59.712 | 0.040648 | 184.98 | 1152.8 |  | 18460 | 216.61 | 16.106 | 59.712 | 0.040648 | 184.98 | 1152.8 | 967.82
18461 | 16.109 | 216.62 | 59.712 | 0.040655 | 184.99 | 1152.8 |  | 18461 | 216.62 | 16.109 | 59.712 | 0.040655 | 184.99 | 1152.8 | 967.81
18462 | 16.112 | 216.63 | 59.712 | 0.040663 | 185 | 1152.8 |  | 18462 | 216.63 | 16.112 | 59.712 | 0.040663 | 185 | 1152.8 | 967.8
18463 | 16.115 | 216.64 | 59.711 | 0.04067 | 185.01 | 1152.8 |  | 18463 | 216.64 | 16.115 | 59.711 | 0.04067 | 185.01 | 1152.8 | 967.79
18464 | 16.118 | 216.65 | 59.711 | 0.040678 | 185.02 | 1152.8 |  | 18464 | 216.65 | 16.118 | 59.711 | 0.040678 | 185.02 | 1152.8 | 967.78
18465 | 16.121 | 216.66 | 59.711 | 0.040685 | 185.03 | 1152.8 |  | 18465 | 216.66 | 16.121 | 59.711 | 0.040685 | 185.03 | 1152.8 | 967.77
18466 | 16.125 | 216.67 | 59.711 | 0.040693 | 185.04 | 1152.8 |  | 18466 | 216.67 | 16.125 | 59.711 | 0.040693 | 185.04 | 1152.8 | 967.76
18467 | 16.128 | 216.68 | 59.71 | 0.0407 | 185.05 | 1152.8 |  | 18467 | 216.68 | 16.128 | 59.71 | 0.0407 | 185.05 | 1152.8 | 967.75
18468 | 16.131 | 216.69 | 59.71 | 0.040707 | 185.06 | 1152.8 |  | 18468 | 216.69 | 16.131 | 59.71 | 0.040707 | 185.06 | 1152.8 | 967.74
18469 | 16.134 | 216.7 | 59.71 | 0.040715 | 185.07 | 1152.8 |  | 18469 | 216.7 | 16.134 | 59.71 | 0.040715 | 185.07 | 1152.8 | 967.73
18470 | 16.137 | 216.71 | 59.71 | 0.040722 | 185.08 | 1152.8 |  | 18470 | 216.71 | 16.137 | 59.71 | 0.040722 | 185.08 | 1152.8 | 967.72
18471 | 16.14 | 216.72 | 59.709 | 0.04073 | 185.09 | 1152.8 |  | 18471 | 216.72 | 16.14 | 59.709 | 0.04073 | 185.09 | 1152.8 | 967.71
18472 | 16.143 | 216.73 | 59.709 | 0.040737 | 185.1 | 1152.8 |  | 18472 | 216.73 | 16.143 | 59.709 | 0.040737 | 185.1 | 1152.8 | 967.7
18473 | 16.147 | 216.74 | 59.709 | 0.040745 | 185.11 | 1152.8 |  | 18473 | 216.74 | 16.147 | 59.709 | 0.040745 | 185.11 | 1152.8 | 967.69
18474 | 16.15 | 216.75 | 59.709 | 0.040752 | 185.12 | 1152.8 |  | 18474 | 216.75 | 16.15 | 59.709 | 0.040752 | 185.12 | 1152.8 | 967.68
18475 | 16.153 | 216.76 | 59.708 | 0.040759 | 185.13 | 1152.8 |  | 18475 | 216.76 | 16.153 | 59.708 | 0.040759 | 185.13 | 1152.8 | 967.67
18476 | 16.156 | 216.77 | 59.708 | 0.040767 | 185.14 | 1152.8 |  | 18476 | 216.77 | 16.156 | 59.708 | 0.040767 | 185.14 | 1152.8 | 967.66
18477 | 16.159 | 216.78 | 59.708 | 0.040774 | 185.15 | 1152.9 |  | 18477 | 216.78 | 16.159 | 59.708 | 0.040774 | 185.15 | 1152.9 | 967.75
18478 | 16.162 | 216.79 | 59.708 | 0.040782 | 185.16 | 1152.9 |  | 18478 | 216.79 | 16.162 | 59.708 | 0.040782 | 185.16 | 1152.9 | 967.74
18479 | 16.166 | 216.8 | 59.707 | 0.040789 | 185.17 | 1152.9 |  | 18479 | 216.8 | 16.166 | 59.707 | 0.040789 | 185.17 | 1152.9 | 967.73
18480 | 16.169 | 216.81 | 59.707 | 0.040797 | 185.18 | 1152.9 |  | 18480 | 216.81 | 16.169 | 59.707 | 0.040797 | 185.18 | 1152.9 | 967.72
18481 | 16.172 | 216.82 | 59.707 | 0.040804 | 185.19 | 1152.9 |  | 18481 | 216.82 | 16.172 | 59.707 | 0.040804 | 185.19 | 1152.9 | 967.71
18482 | 16.175 | 216.83 | 59.707 | 0.040812 | 185.2 | 1152.9 |  | 18482 | 216.83 | 16.175 | 59.707 | 0.040812 | 185.2 | 1152.9 | 967.7
18483 | 16.178 | 216.84 | 59.706 | 0.040819 | 185.21 | 1152.9 |  | 18483 | 216.84 | 16.178 | 59.706 | 0.040819 | 185.21 | 1152.9 | 967.69
18484 | 16.181 | 216.85 | 59.706 | 0.040826 | 185.22 | 1152.9 |  | 18484 | 216.85 | 16.181 | 59.706 | 0.040826 | 185.22 | 1152.9 | 967.68
18485 | 16.184 | 216.86 | 59.706 | 0.040834 | 185.23 | 1152.9 |  | 18485 | 216.86 | 16.184 | 59.706 | 0.040834 | 185.23 | 1152.9 | 967.67
18486 | 16.188 | 216.87 | 59.706 | 0.040841 | 185.24 | 1152.9 |  | 18486 | 216.87 | 16.188 | 59.706 | 0.040841 | 185.24 | 1152.9 | 967.66
18487 | 16.191 | 216.88 | 59.705 | 0.040849 | 185.25 | 1152.9 |  | 18487 | 216.88 | 16.191 | 59.705 | 0.040849 | 185.25 | 1152.9 | 967.65
18488 | 16.194 | 216.89 | 59.705 | 0.040856 | 185.26 | 1152.9 |  | 18488 | 216.89 | 16.194 | 59.705 | 0.040856 | 185.26 | 1152.9 | 967.64
18489 | 16.197 | 216.9 | 59.705 | 0.040864 | 185.27 | 1152.9 |  | 18489 | 216.9 | 16.197 | 59.705 | 0.040864 | 185.27 | 1152.9 | 967.63
18490 | 16.2 | 216.91 | 59.705 | 0.040871 | 185.28 | 1152.9 |  | 18490 | 216.91 | 16.2 | 59.705 | 0.040871 | 185.28 | 1152.9 | 967.62
18491 | 16.203 | 216.92 | 59.704 | 0.040879 | 185.29 | 1152.9 |  | 18491 | 216.92 | 16.203 | 59.704 | 0.040879 | 185.29 | 1152.9 | 967.61
18492 | 16.207 | 216.93 | 59.704 | 0.040886 | 185.3 | 1152.9 |  | 18492 | 216.93 | 16.207 | 59.704 | 0.040886 | 185.3 | 1152.9 | 967.6
18493 | 16.21 | 216.94 | 59.704 | 0.040893 | 185.31 | 1152.9 |  | 18493 | 216.94 | 16.21 | 59.704 | 0.040893 | 185.31 | 1152.9 | 967.59
18494 | 16.213 | 216.95 | 59.704 | 0.040901 | 185.32 | 1152.9 |  | 18494 | 216.95 | 16.213 | 59.704 | 0.040901 | 185.32 | 1152.9 | 967.58
18495 | 16.216 | 216.96 | 59.703 | 0.040908 | 185.33 | 1152.9 |  | 18495 | 216.96 | 16.216 | 59.703 | 0.040908 | 185.33 | 1152.9 | 967.57
18496 | 16.219 | 216.97 | 59.703 | 0.040916 | 185.34 | 1152.9 |  | 18496 | 216.97 | 16.219 | 59.703 | 0.040916 | 185.34 | 1152.9 | 967.56
18497 | 16.222 | 216.98 | 59.703 | 0.040923 | 185.35 | 1152.9 |  | 18497 | 216.98 | 16.222 | 59.703 | 0.040923 | 185.35 | 1152.9 | 967.55
18498 | 16.226 | 216.99 | 59.702 | 0.040931 | 185.36 | 1152.9 |  | 18498 | 216.99 | 16.226 | 59.702 | 0.040931 | 185.36 | 1152.9 | 967.54
18499 | 16.229 | 217 | 59.702 | 0.040938 | 185.37 | 1152.9 |  | 18499 | 217 | 16.229 | 59.702 | 0.040938 | 185.37 | 1152.9 | 967.53
18500 | 16.232 | 217.01 | 59.702 | 0.040946 | 185.38 | 1152.9 |  | 18500 | 217.01 | 16.232 | 59.702 | 0.040946 | 185.38 | 1152.9 | 967.52
18501 | 16.235 | 217.02 | 59.702 | 0.040953 | 185.39 | 1152.9 |  | 18501 | 217.02 | 16.235 | 59.702 | 0.040953 | 185.39 | 1152.9 | 967.51
18502 | 16.238 | 217.03 | 59.701 | 0.040961 | 185.4 | 1152.9 |  | 18502 | 217.03 | 16.238 | 59.701 | 0.040961 | 185.4 | 1152.9 | 967.5
18503 | 16.241 | 217.04 | 59.701 | 0.040968 | 185.41 | 1152.9 |  | 18503 | 217.04 | 16.241 | 59.701 | 0.040968 | 185.41 | 1152.9 | 967.49
18504 | 16.245 | 217.05 | 59.701 | 0.040976 | 185.42 | 1153 |  | 18504 | 217.05 | 16.245 | 59.701 | 0.040976 | 185.42 | 1153 | 967.58
18505 | 16.248 | 217.06 | 59.701 | 0.040983 | 185.43 | 1153 |  | 18505 | 217.06 | 16.248 | 59.701 | 0.040983 | 185.43 | 1153 | 967.57
18506 | 16.251 | 217.07 | 59.7 | 0.040991 | 185.44 | 1153 |  | 18506 | 217.07 | 16.251 | 59.7 | 0.040991 | 185.44 | 1153 | 967.56
18507 | 16.254 | 217.08 | 59.7 | 0.040998 | 185.45 | 1153 |  | 18507 | 217.08 | 16.254 | 59.7 | 0.040998 | 185.45 | 1153 | 967.55
18508 | 16.257 | 217.09 | 59.7 | 0.041005 | 185.46 | 1153 |  | 18508 | 217.09 | 16.257 | 59.7 | 0.041005 | 185.46 | 1153 | 967.54
18509 | 16.26 | 217.1 | 59.7 | 0.041013 | 185.47 | 1153 |  | 18509 | 217.1 | 16.26 | 59.7 | 0.041013 | 185.47 | 1153 | 967.53
18510 | 16.264 | 217.11 | 59.699 | 0.04102 | 185.48 | 1153 |  | 18510 | 217.11 | 16.264 | 59.699 | 0.04102 | 185.48 | 1153 | 967.52
18511 | 16.267 | 217.12 | 59.699 | 0.041028 | 185.49 | 1153 |  | 18511 | 217.12 | 16.267 | 59.699 | 0.041028 | 185.49 | 1153 | 967.51
18512 | 16.27 | 217.13 | 59.699 | 0.041035 | 185.5 | 1153 |  | 18512 | 217.13 | 16.27 | 59.699 | 0.041035 | 185.5 | 1153 | 967.5
18513 | 16.273 | 217.14 | 59.699 | 0.041043 | 185.51 | 1153 |  | 18513 | 217.14 | 16.273 | 59.699 | 0.041043 | 185.51 | 1153 | 967.49
18514 | 16.276 | 217.15 | 59.698 | 0.04105 | 185.52 | 1153 |  | 18514 | 217.15 | 16.276 | 59.698 | 0.04105 | 185.52 | 1153 | 967.48
18515 | 16.279 | 217.16 | 59.698 | 0.041058 | 185.53 | 1153 |  | 18515 | 217.16 | 16.279 | 59.698 | 0.041058 | 185.53 | 1153 | 967.47
18516 | 16.283 | 217.17 | 59.698 | 0.041065 | 185.54 | 1153 |  | 18516 | 217.17 | 16.283 | 59.698 | 0.041065 | 185.54 | 1153 | 967.46
18517 | 16.286 | 217.18 | 59.698 | 0.041073 | 185.55 | 1153 |  | 18517 | 217.18 | 16.286 | 59.698 | 0.041073 | 185.55 | 1153 | 967.45
18518 | 16.289 | 217.19 | 59.697 | 0.04108 | 185.56 | 1153 |  | 18518 | 217.19 | 16.289 | 59.697 | 0.04108 | 185.56 | 1153 | 967.44
18519 | 16.292 | 217.2 | 59.697 | 0.041088 | 185.57 | 1153 |  | 18519 | 217.2 | 16.292 | 59.697 | 0.041088 | 185.57 | 1153 | 967.43
18520 | 16.295 | 217.21 | 59.697 | 0.041095 | 185.58 | 1153 |  | 18520 | 217.21 | 16.295 | 59.697 | 0.041095 | 185.58 | 1153 | 967.42
18521 | 16.298 | 217.22 | 59.697 | 0.041103 | 185.59 | 1153 |  | 18521 | 217.22 | 16.298 | 59.697 | 0.041103 | 185.59 | 1153 | 967.41
18522 | 16.302 | 217.23 | 59.696 | 0.04111 | 185.6 | 1153 |  | 18522 | 217.23 | 16.302 | 59.696 | 0.04111 | 185.6 | 1153 | 967.4
18523 | 16.305 | 217.24 | 59.696 | 0.041118 | 185.61 | 1153 |  | 18523 | 217.24 | 16.305 | 59.696 | 0.041118 | 185.61 | 1153 | 967.39
18524 | 16.308 | 217.25 | 59.696 | 0.041125 | 185.63 | 1153 |  | 18524 | 217.25 | 16.308 | 59.696 | 0.041125 | 185.63 | 1153 | 967.37
18525 | 16.311 | 217.26 | 59.696 | 0.041133 | 185.64 | 1153 |  | 18525 | 217.26 | 16.311 | 59.696 | 0.041133 | 185.64 | 1153 | 967.36
18526 | 16.314 | 217.27 | 59.695 | 0.04114 | 185.65 | 1153 |  | 18526 | 217.27 | 16.314 | 59.695 | 0.04114 | 185.65 | 1153 | 967.35
18527 | 16.317 | 217.28 | 59.695 | 0.041148 | 185.66 | 1153 |  | 18527 | 217.28 | 16.317 | 59.695 | 0.041148 | 185.66 | 1153 | 967.34
18528 | 16.321 | 217.29 | 59.695 | 0.041155 | 185.67 | 1153 |  | 18528 | 217.29 | 16.321 | 59.695 | 0.041155 | 185.67 | 1153 | 967.33
18529 | 16.324 | 217.3 | 59.695 | 0.041163 | 185.68 | 1153 |  | 18529 | 217.3 | 16.324 | 59.695 | 0.041163 | 185.68 | 1153 | 967.32
18530 | 16.327 | 217.31 | 59.694 | 0.04117 | 185.69 | 1153 |  | 18530 | 217.31 | 16.327 | 59.694 | 0.04117 | 185.69 | 1153 | 967.31
18531 | 16.33 | 217.32 | 59.694 | 0.041178 | 185.7 | 1153.1 |  | 18531 | 217.32 | 16.33 | 59.694 | 0.041178 | 185.7 | 1153.1 | 967.4
18532 | 16.333 | 217.33 | 59.694 | 0.041185 | 185.71 | 1153.1 |  | 18532 | 217.33 | 16.333 | 59.694 | 0.041185 | 185.71 | 1153.1 | 967.39
18533 | 16.337 | 217.34 | 59.694 | 0.041193 | 185.72 | 1153.1 |  | 18533 | 217.34 | 16.337 | 59.694 | 0.041193 | 185.72 | 1153.1 | 967.38
18534 | 16.34 | 217.35 | 59.693 | 0.0412 | 185.73 | 1153.1 |  | 18534 | 217.35 | 16.34 | 59.693 | 0.0412 | 185.73 | 1153.1 | 967.37
18535 | 16.343 | 217.36 | 59.693 | 0.041208 | 185.74 | 1153.1 |  | 18535 | 217.36 | 16.343 | 59.693 | 0.041208 | 185.74 | 1153.1 | 967.36
18536 | 16.346 | 217.37 | 59.693 | 0.041215 | 185.75 | 1153.1 |  | 18536 | 217.37 | 16.346 | 59.693 | 0.041215 | 185.75 | 1153.1 | 967.35
18537 | 16.349 | 217.38 | 59.693 | 0.041223 | 185.76 | 1153.1 |  | 18537 | 217.38 | 16.349 | 59.693 | 0.041223 | 185.76 | 1153.1 | 967.34
18538 | 16.352 | 217.39 | 59.692 | 0.04123 | 185.77 | 1153.1 |  | 18538 | 217.39 | 16.352 | 59.692 | 0.04123 | 185.77 | 1153.1 | 967.33
18539 | 16.356 | 217.4 | 59.692 | 0.041238 | 185.78 | 1153.1 |  | 18539 | 217.4 | 16.356 | 59.692 | 0.041238 | 185.78 | 1153.1 | 967.32
18540 | 16.359 | 217.41 | 59.692 | 0.041245 | 185.79 | 1153.1 |  | 18540 | 217.41 | 16.359 | 59.692 | 0.041245 | 185.79 | 1153.1 | 967.31
18541 | 16.362 | 217.42 | 59.692 | 0.041253 | 185.8 | 1153.1 |  | 18541 | 217.42 | 16.362 | 59.692 | 0.041253 | 185.8 | 1153.1 | 967.3
18542 | 16.365 | 217.43 | 59.691 | 0.04126 | 185.81 | 1153.1 |  | 18542 | 217.43 | 16.365 | 59.691 | 0.04126 | 185.81 | 1153.1 | 967.29
18543 | 16.368 | 217.44 | 59.691 | 0.041268 | 185.82 | 1153.1 |  | 18543 | 217.44 | 16.368 | 59.691 | 0.041268 | 185.82 | 1153.1 | 967.28
18544 | 16.372 | 217.45 | 59.691 | 0.041275 | 185.83 | 1153.1 |  | 18544 | 217.45 | 16.372 | 59.691 | 0.041275 | 185.83 | 1153.1 | 967.27
18545 | 16.375 | 217.46 | 59.691 | 0.041283 | 185.84 | 1153.1 |  | 18545 | 217.46 | 16.375 | 59.691 | 0.041283 | 185.84 | 1153.1 | 967.26
18546 | 16.378 | 217.47 | 59.69 | 0.04129 | 185.85 | 1153.1 |  | 18546 | 217.47 | 16.378 | 59.69 | 0.04129 | 185.85 | 1153.1 | 967.25
18547 | 16.381 | 217.48 | 59.69 | 0.041298 | 185.86 | 1153.1 |  | 18547 | 217.48 | 16.381 | 59.69 | 0.041298 | 185.86 | 1153.1 | 967.24
18548 | 16.384 | 217.49 | 59.69 | 0.041305 | 185.87 | 1153.1 |  | 18548 | 217.49 | 16.384 | 59.69 | 0.041305 | 185.87 | 1153.1 | 967.23
18549 | 16.388 | 217.5 | 59.69 | 0.041313 | 185.88 | 1153.1 |  | 18549 | 217.5 | 16.388 | 59.69 | 0.041313 | 185.88 | 1153.1 | 967.22
18550 | 16.391 | 217.51 | 59.689 | 0.04132 | 185.89 | 1153.1 |  | 18550 | 217.51 | 16.391 | 59.689 | 0.04132 | 185.89 | 1153.1 | 967.21
18551 | 16.394 | 217.52 | 59.689 | 0.041328 | 185.9 | 1153.1 |  | 18551 | 217.52 | 16.394 | 59.689 | 0.041328 | 185.9 | 1153.1 | 967.2
18552 | 16.397 | 217.53 | 59.689 | 0.041335 | 185.91 | 1153.1 |  | 18552 | 217.53 | 16.397 | 59.689 | 0.041335 | 185.91 | 1153.1 | 967.19
18553 | 16.4 | 217.54 | 59.689 | 0.041343 | 185.92 | 1153.1 |  | 18553 | 217.54 | 16.4 | 59.689 | 0.041343 | 185.92 | 1153.1 | 967.18
18554 | 16.403 | 217.55 | 59.688 | 0.04135 | 185.93 | 1153.1 |  | 18554 | 217.55 | 16.403 | 59.688 | 0.04135 | 185.93 | 1153.1 | 967.17
18555 | 16.407 | 217.56 | 59.688 | 0.041358 | 185.94 | 1153.1 |  | 18555 | 217.56 | 16.407 | 59.688 | 0.041358 | 185.94 | 1153.1 | 967.16
18556 | 16.41 | 217.57 | 59.688 | 0.041365 | 185.95 | 1153.1 |  | 18556 | 217.57 | 16.41 | 59.688 | 0.041365 | 185.95 | 1153.1 | 967.15
18557 | 16.413 | 217.58 | 59.688 | 0.041373 | 185.96 | 1153.2 |  | 18557 | 217.58 | 16.413 | 59.688 | 0.041373 | 185.96 | 1153.2 | 967.24
18558 | 16.416 | 217.59 | 59.687 | 0.041381 | 185.97 | 1153.2 |  | 18558 | 217.59 | 16.416 | 59.687 | 0.041381 | 185.97 | 1153.2 | 967.23
18559 | 16.419 | 217.6 | 59.687 | 0.041388 | 185.98 | 1153.2 |  | 18559 | 217.6 | 16.419 | 59.687 | 0.041388 | 185.98 | 1153.2 | 967.22
18560 | 16.423 | 217.61 | 59.687 | 0.041396 | 185.99 | 1153.2 |  | 18560 | 217.61 | 16.423 | 59.687 | 0.041396 | 185.99 | 1153.2 | 967.21
18561 | 16.426 | 217.62 | 59.687 | 0.041403 | 186 | 1153.2 |  | 18561 | 217.62 | 16.426 | 59.687 | 0.041403 | 186 | 1153.2 | 967.2
18562 | 16.429 | 217.63 | 59.686 | 0.041411 | 186.01 | 1153.2 |  | 18562 | 217.63 | 16.429 | 59.686 | 0.041411 | 186.01 | 1153.2 | 967.19
18563 | 16.432 | 217.64 | 59.686 | 0.041418 | 186.02 | 1153.2 |  | 18563 | 217.64 | 16.432 | 59.686 | 0.041418 | 186.02 | 1153.2 | 967.18
18564 | 16.435 | 217.65 | 59.686 | 0.041426 | 186.03 | 1153.2 |  | 18564 | 217.65 | 16.435 | 59.686 | 0.041426 | 186.03 | 1153.2 | 967.17
18565 | 16.439 | 217.66 | 59.686 | 0.041433 | 186.04 | 1153.2 |  | 18565 | 217.66 | 16.439 | 59.686 | 0.041433 | 186.04 | 1153.2 | 967.16
18566 | 16.442 | 217.67 | 59.685 | 0.041441 | 186.05 | 1153.2 |  | 18566 | 217.67 | 16.442 | 59.685 | 0.041441 | 186.05 | 1153.2 | 967.15
18567 | 16.445 | 217.68 | 59.685 | 0.041448 | 186.06 | 1153.2 |  | 18567 | 217.68 | 16.445 | 59.685 | 0.041448 | 186.06 | 1153.2 | 967.14
18568 | 16.448 | 217.69 | 59.685 | 0.041456 | 186.07 | 1153.2 |  | 18568 | 217.69 | 16.448 | 59.685 | 0.041456 | 186.07 | 1153.2 | 967.13
18569 | 16.451 | 217.7 | 59.684 | 0.041463 | 186.08 | 1153.2 |  | 18569 | 217.7 | 16.451 | 59.684 | 0.041463 | 186.08 | 1153.2 | 967.12
18570 | 16.455 | 217.71 | 59.684 | 0.041471 | 186.09 | 1153.2 |  | 18570 | 217.71 | 16.455 | 59.684 | 0.041471 | 186.09 | 1153.2 | 967.11
18571 | 16.458 | 217.72 | 59.684 | 0.041478 | 186.1 | 1153.2 |  | 18571 | 217.72 | 16.458 | 59.684 | 0.041478 | 186.1 | 1153.2 | 967.1
18572 | 16.461 | 217.73 | 59.684 | 0.041486 | 186.11 | 1153.2 |  | 18572 | 217.73 | 16.461 | 59.684 | 0.041486 | 186.11 | 1153.2 | 967.09
18573 | 16.464 | 217.74 | 59.683 | 0.041494 | 186.12 | 1153.2 |  | 18573 | 217.74 | 16.464 | 59.683 | 0.041494 | 186.12 | 1153.2 | 967.08
18574 | 16.467 | 217.75 | 59.683 | 0.041501 | 186.13 | 1153.2 |  | 18574 | 217.75 | 16.467 | 59.683 | 0.041501 | 186.13 | 1153.2 | 967.07
18575 | 16.471 | 217.76 | 59.683 | 0.041509 | 186.14 | 1153.2 |  | 18575 | 217.76 | 16.471 | 59.683 | 0.041509 | 186.14 | 1153.2 | 967.06
18576 | 16.474 | 217.77 | 59.683 | 0.041516 | 186.15 | 1153.2 |  | 18576 | 217.77 | 16.474 | 59.683 | 0.041516 | 186.15 | 1153.2 | 967.05
18577 | 16.477 | 217.78 | 59.682 | 0.041524 | 186.16 | 1153.2 |  | 18577 | 217.78 | 16.477 | 59.682 | 0.041524 | 186.16 | 1153.2 | 967.04
18578 | 16.48 | 217.79 | 59.682 | 0.041531 | 186.17 | 1153.2 |  | 18578 | 217.79 | 16.48 | 59.682 | 0.041531 | 186.17 | 1153.2 | 967.03
18579 | 16.483 | 217.8 | 59.682 | 0.041539 | 186.18 | 1153.2 |  | 18579 | 217.8 | 16.483 | 59.682 | 0.041539 | 186.18 | 1153.2 | 967.02
18580 | 16.487 | 217.81 | 59.682 | 0.041546 | 186.19 | 1153.2 |  | 18580 | 217.81 | 16.487 | 59.682 | 0.041546 | 186.19 | 1153.2 | 967.01
18581 | 16.49 | 217.82 | 59.681 | 0.041554 | 186.2 | 1153.2 |  | 18581 | 217.82 | 16.49 | 59.681 | 0.041554 | 186.2 | 1153.2 | 967
18582 | 16.493 | 217.83 | 59.681 | 0.041562 | 186.21 | 1153.2 |  | 18582 | 217.83 | 16.493 | 59.681 | 0.041562 | 186.21 | 1153.2 | 966.99
18583 | 16.496 | 217.84 | 59.681 | 0.041569 | 186.22 | 1153.2 |  | 18583 | 217.84 | 16.496 | 59.681 | 0.041569 | 186.22 | 1153.2 | 966.98
18584 | 16.499 | 217.85 | 59.681 | 0.041577 | 186.23 | 1153.3 |  | 18584 | 217.85 | 16.499 | 59.681 | 0.041577 | 186.23 | 1153.3 | 967.07
18585 | 16.503 | 217.86 | 59.68 | 0.041584 | 186.24 | 1153.3 |  | 18585 | 217.86 | 16.503 | 59.68 | 0.041584 | 186.24 | 1153.3 | 967.06
18586 | 16.506 | 217.87 | 59.68 | 0.041592 | 186.25 | 1153.3 |  | 18586 | 217.87 | 16.506 | 59.68 | 0.041592 | 186.25 | 1153.3 | 967.05
18587 | 16.509 | 217.88 | 59.68 | 0.041599 | 186.26 | 1153.3 |  | 18587 | 217.88 | 16.509 | 59.68 | 0.041599 | 186.26 | 1153.3 | 967.04
18588 | 16.512 | 217.89 | 59.68 | 0.041607 | 186.27 | 1153.3 |  | 18588 | 217.89 | 16.512 | 59.68 | 0.041607 | 186.27 | 1153.3 | 967.03
18589 | 16.515 | 217.9 | 59.679 | 0.041614 | 186.28 | 1153.3 |  | 18589 | 217.9 | 16.515 | 59.679 | 0.041614 | 186.28 | 1153.3 | 967.02
18590 | 16.519 | 217.91 | 59.679 | 0.041622 | 186.29 | 1153.3 |  | 18590 | 217.91 | 16.519 | 59.679 | 0.041622 | 186.29 | 1153.3 | 967.01
18591 | 16.522 | 217.92 | 59.679 | 0.04163 | 186.3 | 1153.3 |  | 18591 | 217.92 | 16.522 | 59.679 | 0.04163 | 186.3 | 1153.3 | 967
18592 | 16.525 | 217.93 | 59.679 | 0.041637 | 186.31 | 1153.3 |  | 18592 | 217.93 | 16.525 | 59.679 | 0.041637 | 186.31 | 1153.3 | 966.99
18593 | 16.528 | 217.94 | 59.678 | 0.041645 | 186.32 | 1153.3 |  | 18593 | 217.94 | 16.528 | 59.678 | 0.041645 | 186.32 | 1153.3 | 966.98
18594 | 16.532 | 217.95 | 59.678 | 0.041652 | 186.33 | 1153.3 |  | 18594 | 217.95 | 16.532 | 59.678 | 0.041652 | 186.33 | 1153.3 | 966.97
18595 | 16.535 | 217.96 | 59.678 | 0.04166 | 186.34 | 1153.3 |  | 18595 | 217.96 | 16.535 | 59.678 | 0.04166 | 186.34 | 1153.3 | 966.96
18596 | 16.538 | 217.97 | 59.678 | 0.041667 | 186.35 | 1153.3 |  | 18596 | 217.97 | 16.538 | 59.678 | 0.041667 | 186.35 | 1153.3 | 966.95
18597 | 16.541 | 217.98 | 59.677 | 0.041675 | 186.36 | 1153.3 |  | 18597 | 217.98 | 16.541 | 59.677 | 0.041675 | 186.36 | 1153.3 | 966.94
18598 | 16.544 | 217.99 | 59.677 | 0.041683 | 186.37 | 1153.3 |  | 18598 | 217.99 | 16.544 | 59.677 | 0.041683 | 186.37 | 1153.3 | 966.93
18599 | 16.548 | 218 | 59.677 | 0.04169 | 186.38 | 1153.3 |  | 18599 | 218 | 16.548 | 59.677 | 0.04169 | 186.38 | 1153.3 | 966.92
18600 | 16.551 | 218.01 | 59.677 | 0.041698 | 186.39 | 1153.3 |  | 18600 | 218.01 | 16.551 | 59.677 | 0.041698 | 186.39 | 1153.3 | 966.91
18601 | 16.554 | 218.02 | 59.676 | 0.041705 | 186.4 | 1153.3 |  | 18601 | 218.02 | 16.554 | 59.676 | 0.041705 | 186.4 | 1153.3 | 966.9
18602 | 16.557 | 218.03 | 59.676 | 0.041713 | 186.41 | 1153.3 |  | 18602 | 218.03 | 16.557 | 59.676 | 0.041713 | 186.41 | 1153.3 | 966.89
18603 | 16.56 | 218.04 | 59.676 | 0.04172 | 186.42 | 1153.3 |  | 18603 | 218.04 | 16.56 | 59.676 | 0.04172 | 186.42 | 1153.3 | 966.88
18604 | 16.564 | 218.05 | 59.676 | 0.041728 | 186.43 | 1153.3 |  | 18604 | 218.05 | 16.564 | 59.676 | 0.041728 | 186.43 | 1153.3 | 966.87
18605 | 16.567 | 218.06 | 59.675 | 0.041736 | 186.44 | 1153.3 |  | 18605 | 218.06 | 16.567 | 59.675 | 0.041736 | 186.44 | 1153.3 | 966.86
18606 | 16.57 | 218.07 | 59.675 | 0.041743 | 186.45 | 1153.3 |  | 18606 | 218.07 | 16.57 | 59.675 | 0.041743 | 186.45 | 1153.3 | 966.85
18607 | 16.573 | 218.08 | 59.675 | 0.041751 | 186.46 | 1153.3 |  | 18607 | 218.08 | 16.573 | 59.675 | 0.041751 | 186.46 | 1153.3 | 966.84
18608 | 16.577 | 218.09 | 59.675 | 0.041758 | 186.47 | 1153.3 |  | 18608 | 218.09 | 16.577 | 59.675 | 0.041758 | 186.47 | 1153.3 | 966.83
18609 | 16.58 | 218.1 | 59.674 | 0.041766 | 186.48 | 1153.3 |  | 18609 | 218.1 | 16.58 | 59.674 | 0.041766 | 186.48 | 1153.3 | 966.82
18610 | 16.583 | 218.11 | 59.674 | 0.041774 | 186.49 | 1153.3 |  | 18610 | 218.11 | 16.583 | 59.674 | 0.041774 | 186.49 | 1153.3 | 966.81
18611 | 16.586 | 218.12 | 59.674 | 0.041781 | 186.5 | 1153.4 |  | 18611 | 218.12 | 16.586 | 59.674 | 0.041781 | 186.5 | 1153.4 | 966.9
18612 | 16.589 | 218.13 | 59.674 | 0.041789 | 186.51 | 1153.4 |  | 18612 | 218.13 | 16.589 | 59.674 | 0.041789 | 186.51 | 1153.4 | 966.89
18613 | 16.593 | 218.14 | 59.673 | 0.041796 | 186.52 | 1153.4 |  | 18613 | 218.14 | 16.593 | 59.673 | 0.041796 | 186.52 | 1153.4 | 966.88
18614 | 16.596 | 218.15 | 59.673 | 0.041804 | 186.53 | 1153.4 |  | 18614 | 218.15 | 16.596 | 59.673 | 0.041804 | 186.53 | 1153.4 | 966.87
18615 | 16.599 | 218.16 | 59.673 | 0.041811 | 186.54 | 1153.4 |  | 18615 | 218.16 | 16.599 | 59.673 | 0.041811 | 186.54 | 1153.4 | 966.86
18616 | 16.602 | 218.17 | 59.673 | 0.041819 | 186.55 | 1153.4 |  | 18616 | 218.17 | 16.602 | 59.673 | 0.041819 | 186.55 | 1153.4 | 966.85
18617 | 16.606 | 218.18 | 59.672 | 0.041827 | 186.56 | 1153.4 |  | 18617 | 218.18 | 16.606 | 59.672 | 0.041827 | 186.56 | 1153.4 | 966.84
18618 | 16.609 | 218.19 | 59.672 | 0.041834 | 186.57 | 1153.4 |  | 18618 | 218.19 | 16.609 | 59.672 | 0.041834 | 186.57 | 1153.4 | 966.83
18619 | 16.612 | 218.2 | 59.672 | 0.041842 | 186.58 | 1153.4 |  | 18619 | 218.2 | 16.612 | 59.672 | 0.041842 | 186.58 | 1153.4 | 966.82
18620 | 16.615 | 218.21 | 59.672 | 0.041849 | 186.59 | 1153.4 |  | 18620 | 218.21 | 16.615 | 59.672 | 0.041849 | 186.59 | 1153.4 | 966.81
18621 | 16.618 | 218.22 | 59.671 | 0.041857 | 186.6 | 1153.4 |  | 18621 | 218.22 | 16.618 | 59.671 | 0.041857 | 186.6 | 1153.4 | 966.8
18622 | 16.622 | 218.23 | 59.671 | 0.041865 | 186.61 | 1153.4 |  | 18622 | 218.23 | 16.622 | 59.671 | 0.041865 | 186.61 | 1153.4 | 966.79
18623 | 16.625 | 218.24 | 59.671 | 0.041872 | 186.62 | 1153.4 |  | 18623 | 218.24 | 16.625 | 59.671 | 0.041872 | 186.62 | 1153.4 | 966.78
18624 | 16.628 | 218.25 | 59.671 | 0.04188 | 186.63 | 1153.4 |  | 18624 | 218.25 | 16.628 | 59.671 | 0.04188 | 186.63 | 1153.4 | 966.77
18625 | 16.631 | 218.26 | 59.67 | 0.041887 | 186.64 | 1153.4 |  | 18625 | 218.26 | 16.631 | 59.67 | 0.041887 | 186.64 | 1153.4 | 966.76
18626 | 16.635 | 218.27 | 59.67 | 0.041895 | 186.65 | 1153.4 |  | 18626 | 218.27 | 16.635 | 59.67 | 0.041895 | 186.65 | 1153.4 | 966.75
18627 | 16.638 | 218.28 | 59.67 | 0.041903 | 186.66 | 1153.4 |  | 18627 | 218.28 | 16.638 | 59.67 | 0.041903 | 186.66 | 1153.4 | 966.74
18628 | 16.641 | 218.29 | 59.669 | 0.04191 | 186.67 | 1153.4 |  | 18628 | 218.29 | 16.641 | 59.669 | 0.04191 | 186.67 | 1153.4 | 966.73
18629 | 16.644 | 218.3 | 59.669 | 0.041918 | 186.68 | 1153.4 |  | 18629 | 218.3 | 16.644 | 59.669 | 0.041918 | 186.68 | 1153.4 | 966.72
18630 | 16.648 | 218.31 | 59.669 | 0.041926 | 186.69 | 1153.4 |  | 18630 | 218.31 | 16.648 | 59.669 | 0.041926 | 186.69 | 1153.4 | 966.71
18631 | 16.651 | 218.32 | 59.669 | 0.041933 | 186.7 | 1153.4 |  | 18631 | 218.32 | 16.651 | 59.669 | 0.041933 | 186.7 | 1153.4 | 966.7
18632 | 16.654 | 218.33 | 59.668 | 0.041941 | 186.71 | 1153.4 |  | 18632 | 218.33 | 16.654 | 59.668 | 0.041941 | 186.71 | 1153.4 | 966.69
18633 | 16.657 | 218.34 | 59.668 | 0.041948 | 186.73 | 1153.4 |  | 18633 | 218.34 | 16.657 | 59.668 | 0.041948 | 186.73 | 1153.4 | 966.67
18634 | 16.66 | 218.35 | 59.668 | 0.041956 | 186.74 | 1153.4 |  | 18634 | 218.35 | 16.66 | 59.668 | 0.041956 | 186.74 | 1153.4 | 966.66
18635 | 16.664 | 218.36 | 59.668 | 0.041964 | 186.75 | 1153.4 |  | 18635 | 218.36 | 16.664 | 59.668 | 0.041964 | 186.75 | 1153.4 | 966.65
18636 | 16.667 | 218.37 | 59.667 | 0.041971 | 186.76 | 1153.4 |  | 18636 | 218.37 | 16.667 | 59.667 | 0.041971 | 186.76 | 1153.4 | 966.64
18637 | 16.67 | 218.38 | 59.667 | 0.041979 | 186.77 | 1153.4 |  | 18637 | 218.38 | 16.67 | 59.667 | 0.041979 | 186.77 | 1153.4 | 966.63
18638 | 16.673 | 218.39 | 59.667 | 0.041986 | 186.78 | 1153.5 |  | 18638 | 218.39 | 16.673 | 59.667 | 0.041986 | 186.78 | 1153.5 | 966.72
18639 | 16.677 | 218.4 | 59.667 | 0.041994 | 186.79 | 1153.5 |  | 18639 | 218.4 | 16.677 | 59.667 | 0.041994 | 186.79 | 1153.5 | 966.71
18640 | 16.68 | 218.41 | 59.666 | 0.042002 | 186.8 | 1153.5 |  | 18640 | 218.41 | 16.68 | 59.666 | 0.042002 | 186.8 | 1153.5 | 966.7
18641 | 16.683 | 218.42 | 59.666 | 0.042009 | 186.81 | 1153.5 |  | 18641 | 218.42 | 16.683 | 59.666 | 0.042009 | 186.81 | 1153.5 | 966.69
18642 | 16.686 | 218.43 | 59.666 | 0.042017 | 186.82 | 1153.5 |  | 18642 | 218.43 | 16.686 | 59.666 | 0.042017 | 186.82 | 1153.5 | 966.68
18643 | 16.69 | 218.44 | 59.666 | 0.042025 | 186.83 | 1153.5 |  | 18643 | 218.44 | 16.69 | 59.666 | 0.042025 | 186.83 | 1153.5 | 966.67
18644 | 16.693 | 218.45 | 59.665 | 0.042032 | 186.84 | 1153.5 |  | 18644 | 218.45 | 16.693 | 59.665 | 0.042032 | 186.84 | 1153.5 | 966.66
18645 | 16.696 | 218.46 | 59.665 | 0.04204 | 186.85 | 1153.5 |  | 18645 | 218.46 | 16.696 | 59.665 | 0.04204 | 186.85 | 1153.5 | 966.65
18646 | 16.699 | 218.47 | 59.665 | 0.042047 | 186.86 | 1153.5 |  | 18646 | 218.47 | 16.699 | 59.665 | 0.042047 | 186.86 | 1153.5 | 966.64
18647 | 16.703 | 218.48 | 59.665 | 0.042055 | 186.87 | 1153.5 |  | 18647 | 218.48 | 16.703 | 59.665 | 0.042055 | 186.87 | 1153.5 | 966.63
18648 | 16.706 | 218.49 | 59.664 | 0.042063 | 186.88 | 1153.5 |  | 18648 | 218.49 | 16.706 | 59.664 | 0.042063 | 186.88 | 1153.5 | 966.62
18649 | 16.709 | 218.5 | 59.664 | 0.04207 | 186.89 | 1153.5 |  | 18649 | 218.5 | 16.709 | 59.664 | 0.04207 | 186.89 | 1153.5 | 966.61
18650 | 16.712 | 218.51 | 59.664 | 0.042078 | 186.9 | 1153.5 |  | 18650 | 218.51 | 16.712 | 59.664 | 0.042078 | 186.9 | 1153.5 | 966.6
18651 | 16.715 | 218.52 | 59.664 | 0.042086 | 186.91 | 1153.5 |  | 18651 | 218.52 | 16.715 | 59.664 | 0.042086 | 186.91 | 1153.5 | 966.59
18652 | 16.719 | 218.53 | 59.663 | 0.042093 | 186.92 | 1153.5 |  | 18652 | 218.53 | 16.719 | 59.663 | 0.042093 | 186.92 | 1153.5 | 966.58
18653 | 16.722 | 218.54 | 59.663 | 0.042101 | 186.93 | 1153.5 |  | 18653 | 218.54 | 16.722 | 59.663 | 0.042101 | 186.93 | 1153.5 | 966.57
18654 | 16.725 | 218.55 | 59.663 | 0.042108 | 186.94 | 1153.5 |  | 18654 | 218.55 | 16.725 | 59.663 | 0.042108 | 186.94 | 1153.5 | 966.56
18655 | 16.728 | 218.56 | 59.663 | 0.042116 | 186.95 | 1153.5 |  | 18655 | 218.56 | 16.728 | 59.663 | 0.042116 | 186.95 | 1153.5 | 966.55
18656 | 16.732 | 218.57 | 59.662 | 0.042124 | 186.96 | 1153.5 |  | 18656 | 218.57 | 16.732 | 59.662 | 0.042124 | 186.96 | 1153.5 | 966.54
18657 | 16.735 | 218.58 | 59.662 | 0.042131 | 186.97 | 1153.5 |  | 18657 | 218.58 | 16.735 | 59.662 | 0.042131 | 186.97 | 1153.5 | 966.53
18658 | 16.738 | 218.59 | 59.662 | 0.042139 | 186.98 | 1153.5 |  | 18658 | 218.59 | 16.738 | 59.662 | 0.042139 | 186.98 | 1153.5 | 966.52
18659 | 16.741 | 218.6 | 59.662 | 0.042147 | 186.99 | 1153.5 |  | 18659 | 218.6 | 16.741 | 59.662 | 0.042147 | 186.99 | 1153.5 | 966.51
18660 | 16.745 | 218.61 | 59.661 | 0.042154 | 187 | 1153.5 |  | 18660 | 218.61 | 16.745 | 59.661 | 0.042154 | 187 | 1153.5 | 966.5
18661 | 16.748 | 218.62 | 59.661 | 0.042162 | 187.01 | 1153.5 |  | 18661 | 218.62 | 16.748 | 59.661 | 0.042162 | 187.01 | 1153.5 | 966.49
18662 | 16.751 | 218.63 | 59.661 | 0.04217 | 187.02 | 1153.5 |  | 18662 | 218.63 | 16.751 | 59.661 | 0.04217 | 187.02 | 1153.5 | 966.48
18663 | 16.754 | 218.64 | 59.661 | 0.042177 | 187.03 | 1153.5 |  | 18663 | 218.64 | 16.754 | 59.661 | 0.042177 | 187.03 | 1153.5 | 966.47
18664 | 16.758 | 218.65 | 59.66 | 0.042185 | 187.04 | 1153.5 |  | 18664 | 218.65 | 16.758 | 59.66 | 0.042185 | 187.04 | 1153.5 | 966.46
18665 | 16.761 | 218.66 | 59.66 | 0.042193 | 187.05 | 1153.6 |  | 18665 | 218.66 | 16.761 | 59.66 | 0.042193 | 187.05 | 1153.6 | 966.55
18666 | 16.764 | 218.67 | 59.66 | 0.0422 | 187.06 | 1153.6 |  | 18666 | 218.67 | 16.764 | 59.66 | 0.0422 | 187.06 | 1153.6 | 966.54
18667 | 16.767 | 218.68 | 59.66 | 0.042208 | 187.07 | 1153.6 |  | 18667 | 218.68 | 16.767 | 59.66 | 0.042208 | 187.07 | 1153.6 | 966.53
18668 | 16.771 | 218.69 | 59.659 | 0.042215 | 187.08 | 1153.6 |  | 18668 | 218.69 | 16.771 | 59.659 | 0.042215 | 187.08 | 1153.6 | 966.52
18669 | 16.774 | 218.7 | 59.659 | 0.042223 | 187.09 | 1153.6 |  | 18669 | 218.7 | 16.774 | 59.659 | 0.042223 | 187.09 | 1153.6 | 966.51
18670 | 16.777 | 218.71 | 59.659 | 0.042231 | 187.1 | 1153.6 |  | 18670 | 218.71 | 16.777 | 59.659 | 0.042231 | 187.1 | 1153.6 | 966.5
18671 | 16.78 | 218.72 | 59.659 | 0.042238 | 187.11 | 1153.6 |  | 18671 | 218.72 | 16.78 | 59.659 | 0.042238 | 187.11 | 1153.6 | 966.49
18672 | 16.784 | 218.73 | 59.658 | 0.042246 | 187.12 | 1153.6 |  | 18672 | 218.73 | 16.784 | 59.658 | 0.042246 | 187.12 | 1153.6 | 966.48
18673 | 16.787 | 218.74 | 59.658 | 0.042254 | 187.13 | 1153.6 |  | 18673 | 218.74 | 16.787 | 59.658 | 0.042254 | 187.13 | 1153.6 | 966.47
18674 | 16.79 | 218.75 | 59.658 | 0.042261 | 187.14 | 1153.6 |  | 18674 | 218.75 | 16.79 | 59.658 | 0.042261 | 187.14 | 1153.6 | 966.46
18675 | 16.793 | 218.76 | 59.658 | 0.042269 | 187.15 | 1153.6 |  | 18675 | 218.76 | 16.793 | 59.658 | 0.042269 | 187.15 | 1153.6 | 966.45
18676 | 16.797 | 218.77 | 59.657 | 0.042277 | 187.16 | 1153.6 |  | 18676 | 218.77 | 16.797 | 59.657 | 0.042277 | 187.16 | 1153.6 | 966.44
18677 | 16.8 | 218.78 | 59.657 | 0.042284 | 187.17 | 1153.6 |  | 18677 | 218.78 | 16.8 | 59.657 | 0.042284 | 187.17 | 1153.6 | 966.43
18678 | 16.803 | 218.79 | 59.657 | 0.042292 | 187.18 | 1153.6 |  | 18678 | 218.79 | 16.803 | 59.657 | 0.042292 | 187.18 | 1153.6 | 966.42
18679 | 16.806 | 218.8 | 59.657 | 0.0423 | 187.19 | 1153.6 |  | 18679 | 218.8 | 16.806 | 59.657 | 0.0423 | 187.19 | 1153.6 | 966.41
18680 | 16.81 | 218.81 | 59.656 | 0.042307 | 187.2 | 1153.6 |  | 18680 | 218.81 | 16.81 | 59.656 | 0.042307 | 187.2 | 1153.6 | 966.4
18681 | 16.813 | 218.82 | 59.656 | 0.042315 | 187.21 | 1153.6 |  | 18681 | 218.82 | 16.813 | 59.656 | 0.042315 | 187.21 | 1153.6 | 966.39
18682 | 16.816 | 218.83 | 59.656 | 0.042323 | 187.22 | 1153.6 |  | 18682 | 218.83 | 16.816 | 59.656 | 0.042323 | 187.22 | 1153.6 | 966.38
18683 | 16.819 | 218.84 | 59.655 | 0.04233 | 187.23 | 1153.6 |  | 18683 | 218.84 | 16.819 | 59.655 | 0.04233 | 187.23 | 1153.6 | 966.37
18684 | 16.823 | 218.85 | 59.655 | 0.042338 | 187.24 | 1153.6 |  | 18684 | 218.85 | 16.823 | 59.655 | 0.042338 | 187.24 | 1153.6 | 966.36
18685 | 16.826 | 218.86 | 59.655 | 0.042346 | 187.25 | 1153.6 |  | 18685 | 218.86 | 16.826 | 59.655 | 0.042346 | 187.25 | 1153.6 | 966.35
18686 | 16.829 | 218.87 | 59.655 | 0.042353 | 187.26 | 1153.6 |  | 18686 | 218.87 | 16.829 | 59.655 | 0.042353 | 187.26 | 1153.6 | 966.34
18687 | 16.833 | 218.88 | 59.654 | 0.042361 | 187.27 | 1153.6 |  | 18687 | 218.88 | 16.833 | 59.654 | 0.042361 | 187.27 | 1153.6 | 966.33
18688 | 16.836 | 218.89 | 59.654 | 0.042369 | 187.28 | 1153.6 |  | 18688 | 218.89 | 16.836 | 59.654 | 0.042369 | 187.28 | 1153.6 | 966.32
18689 | 16.839 | 218.9 | 59.654 | 0.042376 | 187.29 | 1153.6 |  | 18689 | 218.9 | 16.839 | 59.654 | 0.042376 | 187.29 | 1153.6 | 966.31
18690 | 16.842 | 218.91 | 59.654 | 0.042384 | 187.3 | 1153.6 |  | 18690 | 218.91 | 16.842 | 59.654 | 0.042384 | 187.3 | 1153.6 | 966.3
18691 | 16.846 | 218.92 | 59.653 | 0.042392 | 187.31 | 1153.6 |  | 18691 | 218.92 | 16.846 | 59.653 | 0.042392 | 187.31 | 1153.6 | 966.29
18692 | 16.849 | 218.93 | 59.653 | 0.042399 | 187.32 | 1153.7 |  | 18692 | 218.93 | 16.849 | 59.653 | 0.042399 | 187.32 | 1153.7 | 966.38
18693 | 16.852 | 218.94 | 59.653 | 0.042407 | 187.33 | 1153.7 |  | 18693 | 218.94 | 16.852 | 59.653 | 0.042407 | 187.33 | 1153.7 | 966.37
18694 | 16.855 | 218.95 | 59.653 | 0.042415 | 187.34 | 1153.7 |  | 18694 | 218.95 | 16.855 | 59.653 | 0.042415 | 187.34 | 1153.7 | 966.36
18695 | 16.859 | 218.96 | 59.652 | 0.042423 | 187.35 | 1153.7 |  | 18695 | 218.96 | 16.859 | 59.652 | 0.042423 | 187.35 | 1153.7 | 966.35
18696 | 16.862 | 218.97 | 59.652 | 0.04243 | 187.36 | 1153.7 |  | 18696 | 218.97 | 16.862 | 59.652 | 0.04243 | 187.36 | 1153.7 | 966.34
18697 | 16.865 | 218.98 | 59.652 | 0.042438 | 187.37 | 1153.7 |  | 18697 | 218.98 | 16.865 | 59.652 | 0.042438 | 187.37 | 1153.7 | 966.33
18698 | 16.868 | 218.99 | 59.652 | 0.042446 | 187.38 | 1153.7 |  | 18698 | 218.99 | 16.868 | 59.652 | 0.042446 | 187.38 | 1153.7 | 966.32
18699 | 16.872 | 219 | 59.651 | 0.042453 | 187.39 | 1153.7 |  | 18699 | 219 | 16.872 | 59.651 | 0.042453 | 187.39 | 1153.7 | 966.31
18700 | 16.875 | 219.01 | 59.651 | 0.042461 | 187.4 | 1153.7 |  | 18700 | 219.01 | 16.875 | 59.651 | 0.042461 | 187.4 | 1153.7 | 966.3
18701 | 16.878 | 219.02 | 59.651 | 0.042469 | 187.41 | 1153.7 |  | 18701 | 219.02 | 16.878 | 59.651 | 0.042469 | 187.41 | 1153.7 | 966.29
18702 | 16.881 | 219.03 | 59.651 | 0.042476 | 187.42 | 1153.7 |  | 18702 | 219.03 | 16.881 | 59.651 | 0.042476 | 187.42 | 1153.7 | 966.28
18703 | 16.885 | 219.04 | 59.65 | 0.042484 | 187.43 | 1153.7 |  | 18703 | 219.04 | 16.885 | 59.65 | 0.042484 | 187.43 | 1153.7 | 966.27
18704 | 16.888 | 219.05 | 59.65 | 0.042492 | 187.44 | 1153.7 |  | 18704 | 219.05 | 16.888 | 59.65 | 0.042492 | 187.44 | 1153.7 | 966.26
18705 | 16.891 | 219.06 | 59.65 | 0.042499 | 187.45 | 1153.7 |  | 18705 | 219.06 | 16.891 | 59.65 | 0.042499 | 187.45 | 1153.7 | 966.25
18706 | 16.895 | 219.07 | 59.65 | 0.042507 | 187.46 | 1153.7 |  | 18706 | 219.07 | 16.895 | 59.65 | 0.042507 | 187.46 | 1153.7 | 966.24
18707 | 16.898 | 219.08 | 59.649 | 0.042515 | 187.47 | 1153.7 |  | 18707 | 219.08 | 16.898 | 59.649 | 0.042515 | 187.47 | 1153.7 | 966.23
18708 | 16.901 | 219.09 | 59.649 | 0.042522 | 187.48 | 1153.7 |  | 18708 | 219.09 | 16.901 | 59.649 | 0.042522 | 187.48 | 1153.7 | 966.22
18709 | 16.904 | 219.1 | 59.649 | 0.04253 | 187.49 | 1153.7 |  | 18709 | 219.1 | 16.904 | 59.649 | 0.04253 | 187.49 | 1153.7 | 966.21
18710 | 16.908 | 219.11 | 59.649 | 0.042538 | 187.5 | 1153.7 |  | 18710 | 219.11 | 16.908 | 59.649 | 0.042538 | 187.5 | 1153.7 | 966.2
18711 | 16.911 | 219.12 | 59.648 | 0.042546 | 187.51 | 1153.7 |  | 18711 | 219.12 | 16.911 | 59.648 | 0.042546 | 187.51 | 1153.7 | 966.19
18712 | 16.914 | 219.13 | 59.648 | 0.042553 | 187.52 | 1153.7 |  | 18712 | 219.13 | 16.914 | 59.648 | 0.042553 | 187.52 | 1153.7 | 966.18
18713 | 16.917 | 219.14 | 59.648 | 0.042561 | 187.53 | 1153.7 |  | 18713 | 219.14 | 16.917 | 59.648 | 0.042561 | 187.53 | 1153.7 | 966.17
18714 | 16.921 | 219.15 | 59.648 | 0.042569 | 187.54 | 1153.7 |  | 18714 | 219.15 | 16.921 | 59.648 | 0.042569 | 187.54 | 1153.7 | 966.16
18715 | 16.924 | 219.16 | 59.647 | 0.042576 | 187.55 | 1153.7 |  | 18715 | 219.16 | 16.924 | 59.647 | 0.042576 | 187.55 | 1153.7 | 966.15
18716 | 16.927 | 219.17 | 59.647 | 0.042584 | 187.56 | 1153.7 |  | 18716 | 219.17 | 16.927 | 59.647 | 0.042584 | 187.56 | 1153.7 | 966.14
18717 | 16.931 | 219.18 | 59.647 | 0.042592 | 187.57 | 1153.7 |  | 18717 | 219.18 | 16.931 | 59.647 | 0.042592 | 187.57 | 1153.7 | 966.13
18718 | 16.934 | 219.19 | 59.647 | 0.0426 | 187.58 | 1153.8 |  | 18718 | 219.19 | 16.934 | 59.647 | 0.0426 | 187.58 | 1153.8 | 966.22
18719 | 16.937 | 219.2 | 59.646 | 0.042607 | 187.59 | 1153.8 |  | 18719 | 219.2 | 16.937 | 59.646 | 0.042607 | 187.59 | 1153.8 | 966.21
18720 | 16.94 | 219.21 | 59.646 | 0.042615 | 187.6 | 1153.8 |  | 18720 | 219.21 | 16.94 | 59.646 | 0.042615 | 187.6 | 1153.8 | 966.2
18721 | 16.944 | 219.22 | 59.646 | 0.042623 | 187.61 | 1153.8 |  | 18721 | 219.22 | 16.944 | 59.646 | 0.042623 | 187.61 | 1153.8 | 966.19
18722 | 16.947 | 219.23 | 59.646 | 0.04263 | 187.62 | 1153.8 |  | 18722 | 219.23 | 16.947 | 59.646 | 0.04263 | 187.62 | 1153.8 | 966.18
18723 | 16.95 | 219.24 | 59.645 | 0.042638 | 187.63 | 1153.8 |  | 18723 | 219.24 | 16.95 | 59.645 | 0.042638 | 187.63 | 1153.8 | 966.17
18724 | 16.953 | 219.25 | 59.645 | 0.042646 | 187.64 | 1153.8 |  | 18724 | 219.25 | 16.953 | 59.645 | 0.042646 | 187.64 | 1153.8 | 966.16
18725 | 16.957 | 219.26 | 59.645 | 0.042654 | 187.65 | 1153.8 |  | 18725 | 219.26 | 16.957 | 59.645 | 0.042654 | 187.65 | 1153.8 | 966.15
18726 | 16.96 | 219.27 | 59.645 | 0.042661 | 187.66 | 1153.8 |  | 18726 | 219.27 | 16.96 | 59.645 | 0.042661 | 187.66 | 1153.8 | 966.14
18727 | 16.963 | 219.28 | 59.644 | 0.042669 | 187.67 | 1153.8 |  | 18727 | 219.28 | 16.963 | 59.644 | 0.042669 | 187.67 | 1153.8 | 966.13
18728 | 16.967 | 219.29 | 59.644 | 0.042677 | 187.68 | 1153.8 |  | 18728 | 219.29 | 16.967 | 59.644 | 0.042677 | 187.68 | 1153.8 | 966.12
18729 | 16.97 | 219.3 | 59.644 | 0.042684 | 187.69 | 1153.8 |  | 18729 | 219.3 | 16.97 | 59.644 | 0.042684 | 187.69 | 1153.8 | 966.11
18730 | 16.973 | 219.31 | 59.644 | 0.042692 | 187.7 | 1153.8 |  | 18730 | 219.31 | 16.973 | 59.644 | 0.042692 | 187.7 | 1153.8 | 966.1
18731 | 16.976 | 219.32 | 59.643 | 0.0427 | 187.71 | 1153.8 |  | 18731 | 219.32 | 16.976 | 59.643 | 0.0427 | 187.71 | 1153.8 | 966.09
18732 | 16.98 | 219.33 | 59.643 | 0.042708 | 187.72 | 1153.8 |  | 18732 | 219.33 | 16.98 | 59.643 | 0.042708 | 187.72 | 1153.8 | 966.08
18733 | 16.983 | 219.34 | 59.643 | 0.042715 | 187.73 | 1153.8 |  | 18733 | 219.34 | 16.983 | 59.643 | 0.042715 | 187.73 | 1153.8 | 966.07
18734 | 16.986 | 219.35 | 59.642 | 0.042723 | 187.74 | 1153.8 |  | 18734 | 219.35 | 16.986 | 59.642 | 0.042723 | 187.74 | 1153.8 | 966.06
18735 | 16.99 | 219.36 | 59.642 | 0.042731 | 187.75 | 1153.8 |  | 18735 | 219.36 | 16.99 | 59.642 | 0.042731 | 187.75 | 1153.8 | 966.05
18736 | 16.993 | 219.37 | 59.642 | 0.042738 | 187.76 | 1153.8 |  | 18736 | 219.37 | 16.993 | 59.642 | 0.042738 | 187.76 | 1153.8 | 966.04
18737 | 16.996 | 219.38 | 59.642 | 0.042746 | 187.77 | 1153.8 |  | 18737 | 219.38 | 16.996 | 59.642 | 0.042746 | 187.77 | 1153.8 | 966.03
18738 | 16.999 | 219.39 | 59.641 | 0.042754 | 187.78 | 1153.8 |  | 18738 | 219.39 | 16.999 | 59.641 | 0.042754 | 187.78 | 1153.8 | 966.02
18739 | 17.003 | 219.4 | 59.641 | 0.042762 | 187.79 | 1153.8 |  | 18739 | 219.4 | 17.003 | 59.641 | 0.042762 | 187.79 | 1153.8 | 966.01
18740 | 17.006 | 219.41 | 59.641 | 0.042769 | 187.81 | 1153.8 |  | 18740 | 219.41 | 17.006 | 59.641 | 0.042769 | 187.81 | 1153.8 | 965.99
18741 | 17.009 | 219.42 | 59.641 | 0.042777 | 187.82 | 1153.8 |  | 18741 | 219.42 | 17.009 | 59.641 | 0.042777 | 187.82 | 1153.8 | 965.98
18742 | 17.013 | 219.43 | 59.64 | 0.042785 | 187.83 | 1153.8 |  | 18742 | 219.43 | 17.013 | 59.64 | 0.042785 | 187.83 | 1153.8 | 965.97
18743 | 17.016 | 219.44 | 59.64 | 0.042793 | 187.84 | 1153.8 |  | 18743 | 219.44 | 17.016 | 59.64 | 0.042793 | 187.84 | 1153.8 | 965.96
18744 | 17.019 | 219.45 | 59.64 | 0.0428 | 187.85 | 1153.8 |  | 18744 | 219.45 | 17.019 | 59.64 | 0.0428 | 187.85 | 1153.8 | 965.95
18745 | 17.022 | 219.46 | 59.64 | 0.042808 | 187.86 | 1153.9 |  | 18745 | 219.46 | 17.022 | 59.64 | 0.042808 | 187.86 | 1153.9 | 966.04
18746 | 17.026 | 219.47 | 59.639 | 0.042816 | 187.87 | 1153.9 |  | 18746 | 219.47 | 17.026 | 59.639 | 0.042816 | 187.87 | 1153.9 | 966.03
18747 | 17.029 | 219.48 | 59.639 | 0.042824 | 187.88 | 1153.9 |  | 18747 | 219.48 | 17.029 | 59.639 | 0.042824 | 187.88 | 1153.9 | 966.02
18748 | 17.032 | 219.49 | 59.639 | 0.042831 | 187.89 | 1153.9 |  | 18748 | 219.49 | 17.032 | 59.639 | 0.042831 | 187.89 | 1153.9 | 966.01
18749 | 17.036 | 219.5 | 59.639 | 0.042839 | 187.9 | 1153.9 |  | 18749 | 219.5 | 17.036 | 59.639 | 0.042839 | 187.9 | 1153.9 | 966
18750 | 17.039 | 219.51 | 59.638 | 0.042847 | 187.91 | 1153.9 |  | 18750 | 219.51 | 17.039 | 59.638 | 0.042847 | 187.91 | 1153.9 | 965.99
18751 | 17.042 | 219.52 | 59.638 | 0.042855 | 187.92 | 1153.9 |  | 18751 | 219.52 | 17.042 | 59.638 | 0.042855 | 187.92 | 1153.9 | 965.98
18752 | 17.046 | 219.53 | 59.638 | 0.042862 | 187.93 | 1153.9 |  | 18752 | 219.53 | 17.046 | 59.638 | 0.042862 | 187.93 | 1153.9 | 965.97
18753 | 17.049 | 219.54 | 59.638 | 0.04287 | 187.94 | 1153.9 |  | 18753 | 219.54 | 17.049 | 59.638 | 0.04287 | 187.94 | 1153.9 | 965.96
18754 | 17.052 | 219.55 | 59.637 | 0.042878 | 187.95 | 1153.9 |  | 18754 | 219.55 | 17.052 | 59.637 | 0.042878 | 187.95 | 1153.9 | 965.95
18755 | 17.055 | 219.56 | 59.637 | 0.042886 | 187.96 | 1153.9 |  | 18755 | 219.56 | 17.055 | 59.637 | 0.042886 | 187.96 | 1153.9 | 965.94
18756 | 17.059 | 219.57 | 59.637 | 0.042893 | 187.97 | 1153.9 |  | 18756 | 219.57 | 17.059 | 59.637 | 0.042893 | 187.97 | 1153.9 | 965.93
18757 | 17.062 | 219.58 | 59.637 | 0.042901 | 187.98 | 1153.9 |  | 18757 | 219.58 | 17.062 | 59.637 | 0.042901 | 187.98 | 1153.9 | 965.92
18758 | 17.065 | 219.59 | 59.636 | 0.042909 | 187.99 | 1153.9 |  | 18758 | 219.59 | 17.065 | 59.636 | 0.042909 | 187.99 | 1153.9 | 965.91
18759 | 17.069 | 219.6 | 59.636 | 0.042917 | 188 | 1153.9 |  | 18759 | 219.6 | 17.069 | 59.636 | 0.042917 | 188 | 1153.9 | 965.9
18760 | 17.072 | 219.61 | 59.636 | 0.042924 | 188.01 | 1153.9 |  | 18760 | 219.61 | 17.072 | 59.636 | 0.042924 | 188.01 | 1153.9 | 965.89
18761 | 17.075 | 219.62 | 59.636 | 0.042932 | 188.02 | 1153.9 |  | 18761 | 219.62 | 17.075 | 59.636 | 0.042932 | 188.02 | 1153.9 | 965.88
18762 | 17.079 | 219.63 | 59.635 | 0.04294 | 188.03 | 1153.9 |  | 18762 | 219.63 | 17.079 | 59.635 | 0.04294 | 188.03 | 1153.9 | 965.87
18763 | 17.082 | 219.64 | 59.635 | 0.042948 | 188.04 | 1153.9 |  | 18763 | 219.64 | 17.082 | 59.635 | 0.042948 | 188.04 | 1153.9 | 965.86
18764 | 17.085 | 219.65 | 59.635 | 0.042955 | 188.05 | 1153.9 |  | 18764 | 219.65 | 17.085 | 59.635 | 0.042955 | 188.05 | 1153.9 | 965.85
18765 | 17.088 | 219.66 | 59.635 | 0.042963 | 188.06 | 1153.9 |  | 18765 | 219.66 | 17.088 | 59.635 | 0.042963 | 188.06 | 1153.9 | 965.84
18766 | 17.092 | 219.67 | 59.634 | 0.042971 | 188.07 | 1153.9 |  | 18766 | 219.67 | 17.092 | 59.634 | 0.042971 | 188.07 | 1153.9 | 965.83
18767 | 17.095 | 219.68 | 59.634 | 0.042979 | 188.08 | 1153.9 |  | 18767 | 219.68 | 17.095 | 59.634 | 0.042979 | 188.08 | 1153.9 | 965.82
18768 | 17.098 | 219.69 | 59.634 | 0.042986 | 188.09 | 1153.9 |  | 18768 | 219.69 | 17.098 | 59.634 | 0.042986 | 188.09 | 1153.9 | 965.81
18769 | 17.102 | 219.7 | 59.634 | 0.042994 | 188.1 | 1153.9 |  | 18769 | 219.7 | 17.102 | 59.634 | 0.042994 | 188.1 | 1153.9 | 965.8
18770 | 17.105 | 219.71 | 59.633 | 0.043002 | 188.11 | 1153.9 |  | 18770 | 219.71 | 17.105 | 59.633 | 0.043002 | 188.11 | 1153.9 | 965.79
18771 | 17.108 | 219.72 | 59.633 | 0.04301 | 188.12 | 1153.9 |  | 18771 | 219.72 | 17.108 | 59.633 | 0.04301 | 188.12 | 1153.9 | 965.78
18772 | 17.112 | 219.73 | 59.633 | 0.043017 | 188.13 | 1154 |  | 18772 | 219.73 | 17.112 | 59.633 | 0.043017 | 188.13 | 1154 | 965.87
18773 | 17.115 | 219.74 | 59.633 | 0.043025 | 188.14 | 1154 |  | 18773 | 219.74 | 17.115 | 59.633 | 0.043025 | 188.14 | 1154 | 965.86
18774 | 17.118 | 219.75 | 59.632 | 0.043033 | 188.15 | 1154 |  | 18774 | 219.75 | 17.118 | 59.632 | 0.043033 | 188.15 | 1154 | 965.85
18775 | 17.121 | 219.76 | 59.632 | 0.043041 | 188.16 | 1154 |  | 18775 | 219.76 | 17.121 | 59.632 | 0.043041 | 188.16 | 1154 | 965.84
18776 | 17.125 | 219.77 | 59.632 | 0.043049 | 188.17 | 1154 |  | 18776 | 219.77 | 17.125 | 59.632 | 0.043049 | 188.17 | 1154 | 965.83
18777 | 17.128 | 219.78 | 59.631 | 0.043056 | 188.18 | 1154 |  | 18777 | 219.78 | 17.128 | 59.631 | 0.043056 | 188.18 | 1154 | 965.82
18778 | 17.131 | 219.79 | 59.631 | 0.043064 | 188.19 | 1154 |  | 18778 | 219.79 | 17.131 | 59.631 | 0.043064 | 188.19 | 1154 | 965.81
18779 | 17.135 | 219.8 | 59.631 | 0.043072 | 188.2 | 1154 |  | 18779 | 219.8 | 17.135 | 59.631 | 0.043072 | 188.2 | 1154 | 965.8
18780 | 17.138 | 219.81 | 59.631 | 0.04308 | 188.21 | 1154 |  | 18780 | 219.81 | 17.138 | 59.631 | 0.04308 | 188.21 | 1154 | 965.79
18781 | 17.141 | 219.82 | 59.63 | 0.043087 | 188.22 | 1154 |  | 18781 | 219.82 | 17.141 | 59.63 | 0.043087 | 188.22 | 1154 | 965.78
18782 | 17.145 | 219.83 | 59.63 | 0.043095 | 188.23 | 1154 |  | 18782 | 219.83 | 17.145 | 59.63 | 0.043095 | 188.23 | 1154 | 965.77
18783 | 17.148 | 219.84 | 59.63 | 0.043103 | 188.24 | 1154 |  | 18783 | 219.84 | 17.148 | 59.63 | 0.043103 | 188.24 | 1154 | 965.76
18784 | 17.151 | 219.85 | 59.63 | 0.043111 | 188.25 | 1154 |  | 18784 | 219.85 | 17.151 | 59.63 | 0.043111 | 188.25 | 1154 | 965.75
18785 | 17.155 | 219.86 | 59.629 | 0.043119 | 188.26 | 1154 |  | 18785 | 219.86 | 17.155 | 59.629 | 0.043119 | 188.26 | 1154 | 965.74
18786 | 17.158 | 219.87 | 59.629 | 0.043126 | 188.27 | 1154 |  | 18786 | 219.87 | 17.158 | 59.629 | 0.043126 | 188.27 | 1154 | 965.73
18787 | 17.161 | 219.88 | 59.629 | 0.043134 | 188.28 | 1154 |  | 18787 | 219.88 | 17.161 | 59.629 | 0.043134 | 188.28 | 1154 | 965.72
18788 | 17.164 | 219.89 | 59.629 | 0.043142 | 188.29 | 1154 |  | 18788 | 219.89 | 17.164 | 59.629 | 0.043142 | 188.29 | 1154 | 965.71
18789 | 17.168 | 219.9 | 59.628 | 0.04315 | 188.3 | 1154 |  | 18789 | 219.9 | 17.168 | 59.628 | 0.04315 | 188.3 | 1154 | 965.7
18790 | 17.171 | 219.91 | 59.628 | 0.043158 | 188.31 | 1154 |  | 18790 | 219.91 | 17.171 | 59.628 | 0.043158 | 188.31 | 1154 | 965.69
18791 | 17.174 | 219.92 | 59.628 | 0.043165 | 188.32 | 1154 |  | 18791 | 219.92 | 17.174 | 59.628 | 0.043165 | 188.32 | 1154 | 965.68
18792 | 17.178 | 219.93 | 59.628 | 0.043173 | 188.33 | 1154 |  | 18792 | 219.93 | 17.178 | 59.628 | 0.043173 | 188.33 | 1154 | 965.67
18793 | 17.181 | 219.94 | 59.627 | 0.043181 | 188.34 | 1154 |  | 18793 | 219.94 | 17.181 | 59.627 | 0.043181 | 188.34 | 1154 | 965.66
18794 | 17.184 | 219.95 | 59.627 | 0.043189 | 188.35 | 1154 |  | 18794 | 219.95 | 17.184 | 59.627 | 0.043189 | 188.35 | 1154 | 965.65
18795 | 17.188 | 219.96 | 59.627 | 0.043197 | 188.36 | 1154 |  | 18795 | 219.96 | 17.188 | 59.627 | 0.043197 | 188.36 | 1154 | 965.64
18796 | 17.191 | 219.97 | 59.627 | 0.043204 | 188.37 | 1154 |  | 18796 | 219.97 | 17.191 | 59.627 | 0.043204 | 188.37 | 1154 | 965.63
18797 | 17.194 | 219.98 | 59.626 | 0.043212 | 188.38 | 1154 |  | 18797 | 219.98 | 17.194 | 59.626 | 0.043212 | 188.38 | 1154 | 965.62
18798 | 17.198 | 219.99 | 59.626 | 0.04322 | 188.39 | 1154 |  | 18798 | 219.99 | 17.198 | 59.626 | 0.04322 | 188.39 | 1154 | 965.61
18799 | 17.201 | 220 | 59.626 | 0.043228 | 188.4 | 1154.1 |  | 18799 | 220 | 17.201 | 59.626 | 0.043228 | 188.4 | 1154.1 | 965.7
| Vapor | Liquid
| Entropy | Entropy
| (Btu/lbm-R) | (Btu/lbm-R)
1 | 2.1882 | 4.1025e-06
2 | 2.1882 | 2.4615e-05
3 | 2.1881 | 4.5127e-05
4 | 2.1881 | 6.5638e-05
5 | 2.1881 | 8.6149e-05
6 | 2.188 | 0.00010666
7 | 2.188 | 0.00012717
8 | 2.188 | 0.00014768
9 | 2.1879 | 0.00016819
10 | 2.1879 | 0.00018869
11 | 2.1879 | 0.0002092
12 | 2.1878 | 0.00022971
13 | 2.1878 | 0.00025022
14 | 2.1877 | 0.00027072
15 | 2.1877 | 0.00029123
16 | 2.1877 | 0.00031173
17 | 2.1876 | 0.00033224
18 | 2.1876 | 0.00035274
19 | 2.1876 | 0.00037325
20 | 2.1875 | 0.00039375
21 | 2.1875 | 0.00041425
22 | 2.1875 | 0.00043475
23 | 2.1874 | 0.00045526
24 | 2.1874 | 0.00047576
25 | 2.1874 | 0.00049626
26 | 2.1873 | 0.00051676
27 | 2.1873 | 0.00053726
28 | 2.1872 | 0.00055776
29 | 2.1872 | 0.00057825
30 | 2.1872 | 0.00059875
31 | 2.1871 | 0.00061925
32 | 2.1871 | 0.00063975
33 | 2.1871 | 0.00066024
34 | 2.187 | 0.00068074
35 | 2.187 | 0.00070123
36 | 2.187 | 0.00072173
37 | 2.1869 | 0.00074222
38 | 2.1869 | 0.00076272
39 | 2.1869 | 0.00078321
40 | 2.1868 | 0.0008037
41 | 2.1868 | 0.0008242
42 | 2.1868 | 0.00084469
43 | 2.1867 | 0.00086518
44 | 2.1867 | 0.00088567
45 | 2.1866 | 0.00090616
46 | 2.1866 | 0.00092665
47 | 2.1866 | 0.00094714
48 | 2.1865 | 0.00096763
49 | 2.1865 | 0.00098812
50 | 2.1865 | 0.0010086
51 | 2.1864 | 0.0010291
52 | 2.1864 | 0.0010496
53 | 2.1864 | 0.0010701
54 | 2.1863 | 0.0010906
55 | 2.1863 | 0.001111
56 | 2.1863 | 0.0011315
57 | 2.1862 | 0.001152
58 | 2.1862 | 0.0011725
59 | 2.1861 | 0.001193
60 | 2.1861 | 0.0012135
61 | 2.1861 | 0.0012339
62 | 2.186 | 0.0012544
63 | 2.186 | 0.0012749
64 | 2.186 | 0.0012954
65 | 2.1859 | 0.0013159
66 | 2.1859 | 0.0013363
67 | 2.1859 | 0.0013568
68 | 2.1858 | 0.0013773
69 | 2.1858 | 0.0013978
70 | 2.1858 | 0.0014183
71 | 2.1857 | 0.0014387
72 | 2.1857 | 0.0014592
73 | 2.1857 | 0.0014797
74 | 2.1856 | 0.0015002
75 | 2.1856 | 0.0015206
76 | 2.1855 | 0.0015411
77 | 2.1855 | 0.0015616
78 | 2.1855 | 0.0015821
79 | 2.1854 | 0.0016025
80 | 2.1854 | 0.001623
81 | 2.1854 | 0.0016435
82 | 2.1853 | 0.0016639
83 | 2.1853 | 0.0016844
84 | 2.1853 | 0.0017049
85 | 2.1852 | 0.0017254
86 | 2.1852 | 0.0017458
87 | 2.1852 | 0.0017663
88 | 2.1851 | 0.0017868
89 | 2.1851 | 0.0018072
90 | 2.185 | 0.0018277
91 | 2.185 | 0.0018482
92 | 2.185 | 0.0018686
93 | 2.1849 | 0.0018891
94 | 2.1849 | 0.0019096
95 | 2.1849 | 0.00193
96 | 2.1848 | 0.0019505
97 | 2.1848 | 0.001971
98 | 2.1848 | 0.0019914
99 | 2.1847 | 0.0020119
100 | 2.1847 | 0.0020324
101 | 2.1847 | 0.0020528
102 | 2.1846 | 0.0020733
103 | 2.1846 | 0.0020937
104 | 2.1846 | 0.0021142
105 | 2.1845 | 0.0021347
106 | 2.1845 | 0.0021551
107 | 2.1844 | 0.0021756
108 | 2.1844 | 0.002196
109 | 2.1844 | 0.0022165
110 | 2.1843 | 0.0022369
111 | 2.1843 | 0.0022574
112 | 2.1843 | 0.0022779
113 | 2.1842 | 0.0022983
114 | 2.1842 | 0.0023188
115 | 2.1842 | 0.0023392
116 | 2.1841 | 0.0023597
117 | 2.1841 | 0.0023801
118 | 2.1841 | 0.0024006
119 | 2.184 | 0.002421
120 | 2.184 | 0.0024415
121 | 2.184 | 0.0024619
122 | 2.1839 | 0.0024824
123 | 2.1839 | 0.0025029
124 | 2.1838 | 0.0025233
125 | 2.1838 | 0.0025438
126 | 2.1838 | 0.0025642
127 | 2.1837 | 0.0025846
128 | 2.1837 | 0.0026051
129 | 2.1837 | 0.0026255
130 | 2.1836 | 0.002646
131 | 2.1836 | 0.0026664
132 | 2.1836 | 0.0026869
133 | 2.1835 | 0.0027073
134 | 2.1835 | 0.0027278
135 | 2.1835 | 0.0027482
136 | 2.1834 | 0.0027687
137 | 2.1834 | 0.0027891
138 | 2.1834 | 0.0028096
139 | 2.1833 | 0.00283
140 | 2.1833 | 0.0028504
141 | 2.1832 | 0.0028709
142 | 2.1832 | 0.0028913
143 | 2.1832 | 0.0029118
144 | 2.1831 | 0.0029322
145 | 2.1831 | 0.0029526
146 | 2.1831 | 0.0029731
147 | 2.183 | 0.0029935
148 | 2.183 | 0.003014
149 | 2.183 | 0.0030344
150 | 2.1829 | 0.0030548
151 | 2.1829 | 0.0030753
152 | 2.1829 | 0.0030957
153 | 2.1828 | 0.0031161
154 | 2.1828 | 0.0031366
155 | 2.1827 | 0.003157
156 | 2.1827 | 0.0031774
157 | 2.1827 | 0.0031979
158 | 2.1826 | 0.0032183
159 | 2.1826 | 0.0032387
160 | 2.1826 | 0.0032592
161 | 2.1825 | 0.0032796
162 | 2.1825 | 0.0033
163 | 2.1825 | 0.0033205
164 | 2.1824 | 0.0033409
165 | 2.1824 | 0.0033613
166 | 2.1824 | 0.0033818
167 | 2.1823 | 0.0034022
168 | 2.1823 | 0.0034226
169 | 2.1823 | 0.003443
170 | 2.1822 | 0.0034635
171 | 2.1822 | 0.0034839
172 | 2.1822 | 0.0035043
173 | 2.1821 | 0.0035248
174 | 2.1821 | 0.0035452
175 | 2.182 | 0.0035656
176 | 2.182 | 0.003586
177 | 2.182 | 0.0036065
178 | 2.1819 | 0.0036269
179 | 2.1819 | 0.0036473
180 | 2.1819 | 0.0036677
181 | 2.1818 | 0.0036881
182 | 2.1818 | 0.0037086
183 | 2.1818 | 0.003729
184 | 2.1817 | 0.0037494
185 | 2.1817 | 0.0037698
186 | 2.1817 | 0.0037902
187 | 2.1816 | 0.0038107
188 | 2.1816 | 0.0038311
189 | 2.1816 | 0.0038515
190 | 2.1815 | 0.0038719
191 | 2.1815 | 0.0038923
192 | 2.1814 | 0.0039128
193 | 2.1814 | 0.0039332
194 | 2.1814 | 0.0039536
195 | 2.1813 | 0.003974
196 | 2.1813 | 0.0039944
197 | 2.1813 | 0.0040148
198 | 2.1812 | 0.0040352
199 | 2.1812 | 0.0040557
200 | 2.1812 | 0.0040761
201 | 2.1811 | 0.0040965
202 | 2.1811 | 0.0041169
203 | 2.1811 | 0.0041373
204 | 2.181 | 0.0041577
205 | 2.181 | 0.0041781
206 | 2.181 | 0.0041985
207 | 2.1809 | 0.0042189
208 | 2.1809 | 0.0042393
209 | 2.1808 | 0.0042598
210 | 2.1808 | 0.0042802
211 | 2.1808 | 0.0043006
212 | 2.1807 | 0.004321
213 | 2.1807 | 0.0043414
214 | 2.1807 | 0.0043618
215 | 2.1806 | 0.0043822
216 | 2.1806 | 0.0044026
217 | 2.1806 | 0.004423
218 | 2.1805 | 0.0044434
219 | 2.1805 | 0.0044638
220 | 2.1805 | 0.0044842
221 | 2.1804 | 0.0045046
222 | 2.1804 | 0.004525
223 | 2.1804 | 0.0045454
224 | 2.1803 | 0.0045658
225 | 2.1803 | 0.0045862
226 | 2.1802 | 0.0046066
227 | 2.1802 | 0.004627
228 | 2.1802 | 0.0046474
229 | 2.1801 | 0.0046678
230 | 2.1801 | 0.0046882
231 | 2.1801 | 0.0047086
232 | 2.18 | 0.004729
233 | 2.18 | 0.0047494
234 | 2.18 | 0.0047698
235 | 2.1799 | 0.0047902
236 | 2.1799 | 0.0048106
237 | 2.1799 | 0.004831
238 | 2.1798 | 0.0048514
239 | 2.1798 | 0.0048718
240 | 2.1798 | 0.0048921
241 | 2.1797 | 0.0049125
242 | 2.1797 | 0.0049329
243 | 2.1797 | 0.0049533
244 | 2.1796 | 0.0049737
245 | 2.1796 | 0.0049941
246 | 2.1795 | 0.0050145
247 | 2.1795 | 0.0050349
248 | 2.1795 | 0.0050553
249 | 2.1794 | 0.0050757
250 | 2.1794 | 0.005096
251 | 2.1794 | 0.0051164
252 | 2.1793 | 0.0051368
253 | 2.1793 | 0.0051572
254 | 2.1793 | 0.0051776
255 | 2.1792 | 0.005198
256 | 2.1792 | 0.0052184
257 | 2.1792 | 0.0052387
258 | 2.1791 | 0.0052591
259 | 2.1791 | 0.0052795
260 | 2.1791 | 0.0052999
261 | 2.179 | 0.0053203
262 | 2.179 | 0.0053407
263 | 2.1789 | 0.005361
264 | 2.1789 | 0.0053814
265 | 2.1789 | 0.0054018
266 | 2.1788 | 0.0054222
267 | 2.1788 | 0.0054426
268 | 2.1788 | 0.0054629
269 | 2.1787 | 0.0054833
270 | 2.1787 | 0.0055037
271 | 2.1787 | 0.0055241
272 | 2.1786 | 0.0055444
273 | 2.1786 | 0.0055648
274 | 2.1786 | 0.0055852
275 | 2.1785 | 0.0056056
276 | 2.1785 | 0.0056259
277 | 2.1785 | 0.0056463
278 | 2.1784 | 0.0056667
279 | 2.1784 | 0.0056871
280 | 2.1784 | 0.0057074
281 | 2.1783 | 0.0057278
282 | 2.1783 | 0.0057482
283 | 2.1782 | 0.0057685
284 | 2.1782 | 0.0057889
285 | 2.1782 | 0.0058093
286 | 2.1781 | 0.0058297
287 | 2.1781 | 0.00585
288 | 2.1781 | 0.0058704
289 | 2.178 | 0.0058908
290 | 2.178 | 0.0059111
291 | 2.178 | 0.0059315
292 | 2.1779 | 0.0059519
293 | 2.1779 | 0.0059722
294 | 2.1779 | 0.0059926
295 | 2.1778 | 0.006013
296 | 2.1778 | 0.0060333
297 | 2.1778 | 0.0060537
298 | 2.1777 | 0.0060741
299 | 2.1777 | 0.0060944
300 | 2.1777 | 0.0061148
301 | 2.1776 | 0.0061351
302 | 2.1776 | 0.0061555
303 | 2.1775 | 0.0061759
304 | 2.1775 | 0.0061962
305 | 2.1775 | 0.0062166
306 | 2.1774 | 0.0062369
307 | 2.1774 | 0.0062573
308 | 2.1774 | 0.0062777
309 | 2.1773 | 0.006298
310 | 2.1773 | 0.0063184
311 | 2.1773 | 0.0063387
312 | 2.1772 | 0.0063591
313 | 2.1772 | 0.0063795
314 | 2.1772 | 0.0063998
315 | 2.1771 | 0.0064202
316 | 2.1771 | 0.0064405
317 | 2.1771 | 0.0064609
318 | 2.177 | 0.0064812
319 | 2.177 | 0.0065016
320 | 2.1769 | 0.0065219
321 | 2.1769 | 0.0065423
322 | 2.1769 | 0.0065626
323 | 2.1768 | 0.006583
324 | 2.1768 | 0.0066033
325 | 2.1768 | 0.0066237
326 | 2.1767 | 0.006644
327 | 2.1767 | 0.0066644
328 | 2.1767 | 0.0066847
329 | 2.1766 | 0.0067051
330 | 2.1766 | 0.0067254
331 | 2.1766 | 0.0067458
332 | 2.1765 | 0.0067661
333 | 2.1765 | 0.0067865
334 | 2.1765 | 0.0068068
335 | 2.1764 | 0.0068272
336 | 2.1764 | 0.0068475
337 | 2.1764 | 0.0068679
338 | 2.1763 | 0.0068882
339 | 2.1763 | 0.0069085
340 | 2.1763 | 0.0069289
341 | 2.1762 | 0.0069492
342 | 2.1762 | 0.0069696
343 | 2.1761 | 0.0069899
344 | 2.1761 | 0.0070102
345 | 2.1761 | 0.0070306
346 | 2.176 | 0.0070509
347 | 2.176 | 0.0070713
348 | 2.176 | 0.0070916
349 | 2.1759 | 0.0071119
350 | 2.1759 | 0.0071323
351 | 2.1759 | 0.0071526
352 | 2.1758 | 0.007173
353 | 2.1758 | 0.0071933
354 | 2.1758 | 0.0072136
355 | 2.1757 | 0.007234
356 | 2.1757 | 0.0072543
357 | 2.1757 | 0.0072746
358 | 2.1756 | 0.007295
359 | 2.1756 | 0.0073153
360 | 2.1756 | 0.0073356
361 | 2.1755 | 0.007356
362 | 2.1755 | 0.0073763
363 | 2.1754 | 0.0073966
364 | 2.1754 | 0.007417
365 | 2.1754 | 0.0074373
366 | 2.1753 | 0.0074576
367 | 2.1753 | 0.007478
368 | 2.1753 | 0.0074983
369 | 2.1752 | 0.0075186
370 | 2.1752 | 0.0075389
371 | 2.1752 | 0.0075593
372 | 2.1751 | 0.0075796
373 | 2.1751 | 0.0075999
374 | 2.1751 | 0.0076202
375 | 2.175 | 0.0076406
376 | 2.175 | 0.0076609
377 | 2.175 | 0.0076812
378 | 2.1749 | 0.0077015
379 | 2.1749 | 0.0077219
380 | 2.1749 | 0.0077422
381 | 2.1748 | 0.0077625
382 | 2.1748 | 0.0077828
383 | 2.1747 | 0.0078032
384 | 2.1747 | 0.0078235
385 | 2.1747 | 0.0078438
386 | 2.1746 | 0.0078641
387 | 2.1746 | 0.0078844
388 | 2.1746 | 0.0079048
389 | 2.1745 | 0.0079251
390 | 2.1745 | 0.0079454
391 | 2.1745 | 0.0079657
392 | 2.1744 | 0.007986
393 | 2.1744 | 0.0080064
394 | 2.1744 | 0.0080267
395 | 2.1743 | 0.008047
396 | 2.1743 | 0.0080673
397 | 2.1743 | 0.0080876
398 | 2.1742 | 0.0081079
399 | 2.1742 | 0.0081282
400 | 2.1742 | 0.0081486
401 | 2.1741 | 0.0081689
402 | 2.1741 | 0.0081892
403 | 2.1741 | 0.0082095
404 | 2.174 | 0.0082298
405 | 2.174 | 0.0082501
406 | 2.1739 | 0.0082704
407 | 2.1739 | 0.0082907
408 | 2.1739 | 0.0083111
409 | 2.1738 | 0.0083314
410 | 2.1738 | 0.0083517
411 | 2.1738 | 0.008372
412 | 2.1737 | 0.0083923
413 | 2.1737 | 0.0084126
414 | 2.1737 | 0.0084329
415 | 2.1736 | 0.0084532
416 | 2.1736 | 0.0084735
417 | 2.1736 | 0.0084938
418 | 2.1735 | 0.0085141
419 | 2.1735 | 0.0085344
420 | 2.1735 | 0.0085547
421 | 2.1734 | 0.008575
422 | 2.1734 | 0.0085953
423 | 2.1734 | 0.0086156
424 | 2.1733 | 0.0086359
425 | 2.1733 | 0.0086562
426 | 2.1732 | 0.0086765
427 | 2.1732 | 0.0086968
428 | 2.1732 | 0.0087171
429 | 2.1731 | 0.0087374
430 | 2.1731 | 0.0087577
431 | 2.1731 | 0.008778
432 | 2.173 | 0.0087983
433 | 2.173 | 0.0088186
434 | 2.173 | 0.0088389
435 | 2.1729 | 0.0088592
436 | 2.1729 | 0.0088795
437 | 2.1729 | 0.0088998
438 | 2.1728 | 0.0089201
439 | 2.1728 | 0.0089404
440 | 2.1728 | 0.0089607
441 | 2.1727 | 0.008981
442 | 2.1727 | 0.0090013
443 | 2.1727 | 0.0090216
444 | 2.1726 | 0.0090419
445 | 2.1726 | 0.0090622
446 | 2.1726 | 0.0090825
447 | 2.1725 | 0.0091027
448 | 2.1725 | 0.009123
449 | 2.1724 | 0.0091433
450 | 2.1724 | 0.0091636
451 | 2.1724 | 0.0091839
452 | 2.1723 | 0.0092042
453 | 2.1723 | 0.0092245
454 | 2.1723 | 0.0092448
455 | 2.1722 | 0.0092651
456 | 2.1722 | 0.0092853
457 | 2.1722 | 0.0093056
458 | 2.1721 | 0.0093259
459 | 2.1721 | 0.0093462
460 | 2.1721 | 0.0093665
461 | 2.172 | 0.0093868
462 | 2.172 | 0.009407
463 | 2.172 | 0.0094273
464 | 2.1719 | 0.0094476
465 | 2.1719 | 0.0094679
466 | 2.1719 | 0.0094882
467 | 2.1718 | 0.0095085
468 | 2.1718 | 0.0095287
469 | 2.1718 | 0.009549
470 | 2.1717 | 0.0095693
471 | 2.1717 | 0.0095896
472 | 2.1717 | 0.0096099
473 | 2.1716 | 0.0096301
474 | 2.1716 | 0.0096504
475 | 2.1715 | 0.0096707
476 | 2.1715 | 0.009691
477 | 2.1715 | 0.0097112
478 | 2.1714 | 0.0097315
479 | 2.1714 | 0.0097518
480 | 2.1714 | 0.0097721
481 | 2.1713 | 0.0097923
482 | 2.1713 | 0.0098126
483 | 2.1713 | 0.0098329
484 | 2.1712 | 0.0098532
485 | 2.1712 | 0.0098734
486 | 2.1712 | 0.0098937
487 | 2.1711 | 0.009914
488 | 2.1711 | 0.0099342
489 | 2.1711 | 0.0099545
490 | 2.171 | 0.0099748
491 | 2.171 | 0.0099951
492 | 2.171 | 0.010015
493 | 2.1709 | 0.010036
494 | 2.1709 | 0.010056
495 | 2.1709 | 0.010076
496 | 2.1708 | 0.010096
497 | 2.1708 | 0.010117
498 | 2.1707 | 0.010137
499 | 2.1707 | 0.010157
500 | 2.1707 | 0.010177
501 | 2.1706 | 0.010198
502 | 2.1706 | 0.010218
503 | 2.1706 | 0.010238
504 | 2.1705 | 0.010259
505 | 2.1705 | 0.010279
506 | 2.1705 | 0.010299
507 | 2.1704 | 0.010319
508 | 2.1704 | 0.01034
509 | 2.1704 | 0.01036
510 | 2.1703 | 0.01038
511 | 2.1703 | 0.0104
512 | 2.1703 | 0.010421
513 | 2.1702 | 0.010441
514 | 2.1702 | 0.010461
515 | 2.1702 | 0.010481
516 | 2.1701 | 0.010502
517 | 2.1701 | 0.010522
518 | 2.1701 | 0.010542
519 | 2.17 | 0.010562
520 | 2.17 | 0.010583
521 | 2.17 | 0.010603
522 | 2.1699 | 0.010623
523 | 2.1699 | 0.010643
524 | 2.1698 | 0.010664
525 | 2.1698 | 0.010684
526 | 2.1698 | 0.010704
527 | 2.1697 | 0.010724
528 | 2.1697 | 0.010745
529 | 2.1697 | 0.010765
530 | 2.1696 | 0.010785
531 | 2.1696 | 0.010805
532 | 2.1696 | 0.010826
533 | 2.1695 | 0.010846
534 | 2.1695 | 0.010866
535 | 2.1695 | 0.010886
536 | 2.1694 | 0.010907
537 | 2.1694 | 0.010927
538 | 2.1694 | 0.010947
539 | 2.1693 | 0.010967
540 | 2.1693 | 0.010988
541 | 2.1693 | 0.011008
542 | 2.1692 | 0.011028
543 | 2.1692 | 0.011048
544 | 2.1692 | 0.011069
545 | 2.1691 | 0.011089
546 | 2.1691 | 0.011109
547 | 2.1691 | 0.011129
548 | 2.169 | 0.01115
549 | 2.169 | 0.01117
550 | 2.1689 | 0.01119
551 | 2.1689 | 0.01121
552 | 2.1689 | 0.011231
553 | 2.1688 | 0.011251
554 | 2.1688 | 0.011271
555 | 2.1688 | 0.011291
556 | 2.1687 | 0.011312
557 | 2.1687 | 0.011332
558 | 2.1687 | 0.011352
559 | 2.1686 | 0.011372
560 | 2.1686 | 0.011392
561 | 2.1686 | 0.011413
562 | 2.1685 | 0.011433
563 | 2.1685 | 0.011453
564 | 2.1685 | 0.011473
565 | 2.1684 | 0.011494
566 | 2.1684 | 0.011514
567 | 2.1684 | 0.011534
568 | 2.1683 | 0.011554
569 | 2.1683 | 0.011575
570 | 2.1683 | 0.011595
571 | 2.1682 | 0.011615
572 | 2.1682 | 0.011635
573 | 2.1682 | 0.011655
574 | 2.1681 | 0.011676
575 | 2.1681 | 0.011696
576 | 2.168 | 0.011716
577 | 2.168 | 0.011736
578 | 2.168 | 0.011757
579 | 2.1679 | 0.011777
580 | 2.1679 | 0.011797
581 | 2.1679 | 0.011817
582 | 2.1678 | 0.011838
583 | 2.1678 | 0.011858
584 | 2.1678 | 0.011878
585 | 2.1677 | 0.011898
586 | 2.1677 | 0.011918
587 | 2.1677 | 0.011939
588 | 2.1676 | 0.011959
589 | 2.1676 | 0.011979
590 | 2.1676 | 0.011999
591 | 2.1675 | 0.01202
592 | 2.1675 | 0.01204
593 | 2.1675 | 0.01206
594 | 2.1674 | 0.01208
595 | 2.1674 | 0.0121
596 | 2.1674 | 0.012121
597 | 2.1673 | 0.012141
598 | 2.1673 | 0.012161
599 | 2.1673 | 0.012181
600 | 2.1672 | 0.012202
601 | 2.1672 | 0.012222
602 | 2.1672 | 0.012242
603 | 2.1671 | 0.012262
604 | 2.1671 | 0.012282
605 | 2.167 | 0.012303
606 | 2.167 | 0.012323
607 | 2.167 | 0.012343
608 | 2.1669 | 0.012363
609 | 2.1669 | 0.012383
610 | 2.1669 | 0.012404
611 | 2.1668 | 0.012424
612 | 2.1668 | 0.012444
613 | 2.1668 | 0.012464
614 | 2.1667 | 0.012484
615 | 2.1667 | 0.012505
616 | 2.1667 | 0.012525
617 | 2.1666 | 0.012545
618 | 2.1666 | 0.012565
619 | 2.1666 | 0.012586
620 | 2.1665 | 0.012606
621 | 2.1665 | 0.012626
622 | 2.1665 | 0.012646
623 | 2.1664 | 0.012666
624 | 2.1664 | 0.012687
625 | 2.1664 | 0.012707
626 | 2.1663 | 0.012727
627 | 2.1663 | 0.012747
628 | 2.1663 | 0.012767
629 | 2.1662 | 0.012788
630 | 2.1662 | 0.012808
631 | 2.1662 | 0.012828
632 | 2.1661 | 0.012848
633 | 2.1661 | 0.012868
634 | 2.166 | 0.012889
635 | 2.166 | 0.012909
636 | 2.166 | 0.012929
637 | 2.1659 | 0.012949
638 | 2.1659 | 0.012969
639 | 2.1659 | 0.01299
640 | 2.1658 | 0.01301
641 | 2.1658 | 0.01303
642 | 2.1658 | 0.01305
643 | 2.1657 | 0.01307
644 | 2.1657 | 0.013091
645 | 2.1657 | 0.013111
646 | 2.1656 | 0.013131
647 | 2.1656 | 0.013151
648 | 2.1656 | 0.013171
649 | 2.1655 | 0.013192
650 | 2.1655 | 0.013212
651 | 2.1655 | 0.013232
652 | 2.1654 | 0.013252
653 | 2.1654 | 0.013272
654 | 2.1654 | 0.013293
655 | 2.1653 | 0.013313
656 | 2.1653 | 0.013333
657 | 2.1653 | 0.013353
658 | 2.1652 | 0.013373
659 | 2.1652 | 0.013393
660 | 2.1652 | 0.013414
661 | 2.1651 | 0.013434
662 | 2.1651 | 0.013454
663 | 2.165 | 0.013474
664 | 2.165 | 0.013494
665 | 2.165 | 0.013515
666 | 2.1649 | 0.013535
667 | 2.1649 | 0.013555
668 | 2.1649 | 0.013575
669 | 2.1648 | 0.013595
670 | 2.1648 | 0.013616
671 | 2.1648 | 0.013636
672 | 2.1647 | 0.013656
673 | 2.1647 | 0.013676
674 | 2.1647 | 0.013696
675 | 2.1646 | 0.013716
676 | 2.1646 | 0.013737
677 | 2.1646 | 0.013757
678 | 2.1645 | 0.013777
679 | 2.1645 | 0.013797
680 | 2.1645 | 0.013817
681 | 2.1644 | 0.013837
682 | 2.1644 | 0.013858
683 | 2.1644 | 0.013878
684 | 2.1643 | 0.013898
685 | 2.1643 | 0.013918
686 | 2.1643 | 0.013938
687 | 2.1642 | 0.013959
688 | 2.1642 | 0.013979
689 | 2.1642 | 0.013999
690 | 2.1641 | 0.014019
691 | 2.1641 | 0.014039
692 | 2.1641 | 0.014059
693 | 2.164 | 0.01408
694 | 2.164 | 0.0141
695 | 2.1639 | 0.01412
696 | 2.1639 | 0.01414
697 | 2.1639 | 0.01416
698 | 2.1638 | 0.01418
699 | 2.1638 | 0.014201
700 | 2.1638 | 0.014221
701 | 2.1637 | 0.014241
702 | 2.1637 | 0.014261
703 | 2.1637 | 0.014281
704 | 2.1636 | 0.014301
705 | 2.1636 | 0.014322
706 | 2.1636 | 0.014342
707 | 2.1635 | 0.014362
708 | 2.1635 | 0.014382
709 | 2.1635 | 0.014402
710 | 2.1634 | 0.014422
711 | 2.1634 | 0.014443
712 | 2.1634 | 0.014463
713 | 2.1633 | 0.014483
714 | 2.1633 | 0.014503
715 | 2.1633 | 0.014523
716 | 2.1632 | 0.014543
717 | 2.1632 | 0.014564
718 | 2.1632 | 0.014584
719 | 2.1631 | 0.014604
720 | 2.1631 | 0.014624
721 | 2.1631 | 0.014644
722 | 2.163 | 0.014664
723 | 2.163 | 0.014685
724 | 2.163 | 0.014705
725 | 2.1629 | 0.014725
726 | 2.1629 | 0.014745
727 | 2.1629 | 0.014765
728 | 2.1628 | 0.014785
729 | 2.1628 | 0.014805
730 | 2.1627 | 0.014826
731 | 2.1627 | 0.014846
732 | 2.1627 | 0.014866
733 | 2.1626 | 0.014886
734 | 2.1626 | 0.014906
735 | 2.1626 | 0.014926
736 | 2.1625 | 0.014947
737 | 2.1625 | 0.014967
738 | 2.1625 | 0.014987
739 | 2.1624 | 0.015007
740 | 2.1624 | 0.015027
741 | 2.1624 | 0.015047
742 | 2.1623 | 0.015067
743 | 2.1623 | 0.015088
744 | 2.1623 | 0.015108
745 | 2.1622 | 0.015128
746 | 2.1622 | 0.015148
747 | 2.1622 | 0.015168
748 | 2.1621 | 0.015188
749 | 2.1621 | 0.015209
750 | 2.1621 | 0.015229
751 | 2.162 | 0.015249
752 | 2.162 | 0.015269
753 | 2.162 | 0.015289
754 | 2.1619 | 0.015309
755 | 2.1619 | 0.015329
756 | 2.1619 | 0.01535
757 | 2.1618 | 0.01537
758 | 2.1618 | 0.01539
759 | 2.1618 | 0.01541
760 | 2.1617 | 0.01543
761 | 2.1617 | 0.01545
762 | 2.1617 | 0.01547
763 | 2.1616 | 0.015491
764 | 2.1616 | 0.015511
765 | 2.1616 | 0.015531
766 | 2.1615 | 0.015551
767 | 2.1615 | 0.015571
768 | 2.1614 | 0.015591
769 | 2.1614 | 0.015611
770 | 2.1614 | 0.015631
771 | 2.1613 | 0.015652
772 | 2.1613 | 0.015672
773 | 2.1613 | 0.015692
774 | 2.1612 | 0.015712
775 | 2.1612 | 0.015732
776 | 2.1612 | 0.015752
777 | 2.1611 | 0.015772
778 | 2.1611 | 0.015793
779 | 2.1611 | 0.015813
780 | 2.161 | 0.015833
781 | 2.161 | 0.015853
782 | 2.161 | 0.015873
783 | 2.1609 | 0.015893
784 | 2.1609 | 0.015913
785 | 2.1609 | 0.015933
786 | 2.1608 | 0.015954
787 | 2.1608 | 0.015974
788 | 2.1608 | 0.015994
789 | 2.1607 | 0.016014
790 | 2.1607 | 0.016034
791 | 2.1607 | 0.016054
792 | 2.1606 | 0.016074
793 | 2.1606 | 0.016094
794 | 2.1606 | 0.016115
795 | 2.1605 | 0.016135
796 | 2.1605 | 0.016155
797 | 2.1605 | 0.016175
798 | 2.1604 | 0.016195
799 | 2.1604 | 0.016215
800 | 2.1604 | 0.016235
801 | 2.1603 | 0.016255
802 | 2.1603 | 0.016276
803 | 2.1603 | 0.016296
804 | 2.1602 | 0.016316
805 | 2.1602 | 0.016336
806 | 2.1601 | 0.016356
807 | 2.1601 | 0.016376
808 | 2.1601 | 0.016396
809 | 2.16 | 0.016416
810 | 2.16 | 0.016437
811 | 2.16 | 0.016457
812 | 2.1599 | 0.016477
813 | 2.1599 | 0.016497
814 | 2.1599 | 0.016517
815 | 2.1598 | 0.016537
816 | 2.1598 | 0.016557
817 | 2.1598 | 0.016577
818 | 2.1597 | 0.016597
819 | 2.1597 | 0.016618
820 | 2.1597 | 0.016638
821 | 2.1596 | 0.016658
822 | 2.1596 | 0.016678
823 | 2.1596 | 0.016698
824 | 2.1595 | 0.016718
825 | 2.1595 | 0.016738
826 | 2.1595 | 0.016758
827 | 2.1594 | 0.016778
828 | 2.1594 | 0.016799
829 | 2.1594 | 0.016819
830 | 2.1593 | 0.016839
831 | 2.1593 | 0.016859
832 | 2.1593 | 0.016879
833 | 2.1592 | 0.016899
834 | 2.1592 | 0.016919
835 | 2.1592 | 0.016939
836 | 2.1591 | 0.016959
837 | 2.1591 | 0.01698
838 | 2.1591 | 0.017
839 | 2.159 | 0.01702
840 | 2.159 | 0.01704
841 | 2.159 | 0.01706
842 | 2.1589 | 0.01708
843 | 2.1589 | 0.0171
844 | 2.1589 | 0.01712
845 | 2.1588 | 0.01714
846 | 2.1588 | 0.01716
847 | 2.1588 | 0.017181
848 | 2.1587 | 0.017201
849 | 2.1587 | 0.017221
850 | 2.1586 | 0.017241
851 | 2.1586 | 0.017261
852 | 2.1586 | 0.017281
853 | 2.1585 | 0.017301
854 | 2.1585 | 0.017321
855 | 2.1585 | 0.017341
856 | 2.1584 | 0.017361
857 | 2.1584 | 0.017382
858 | 2.1584 | 0.017402
859 | 2.1583 | 0.017422
860 | 2.1583 | 0.017442
861 | 2.1583 | 0.017462
862 | 2.1582 | 0.017482
863 | 2.1582 | 0.017502
864 | 2.1582 | 0.017522
865 | 2.1581 | 0.017542
866 | 2.1581 | 0.017562
867 | 2.1581 | 0.017582
868 | 2.158 | 0.017603
869 | 2.158 | 0.017623
870 | 2.158 | 0.017643
871 | 2.1579 | 0.017663
872 | 2.1579 | 0.017683
873 | 2.1579 | 0.017703
874 | 2.1578 | 0.017723
875 | 2.1578 | 0.017743
876 | 2.1578 | 0.017763
877 | 2.1577 | 0.017783
878 | 2.1577 | 0.017803
879 | 2.1577 | 0.017824
880 | 2.1576 | 0.017844
881 | 2.1576 | 0.017864
882 | 2.1576 | 0.017884
883 | 2.1575 | 0.017904
884 | 2.1575 | 0.017924
885 | 2.1575 | 0.017944
886 | 2.1574 | 0.017964
887 | 2.1574 | 0.017984
888 | 2.1574 | 0.018004
889 | 2.1573 | 0.018024
890 | 2.1573 | 0.018044
891 | 2.1573 | 0.018064
892 | 2.1572 | 0.018085
893 | 2.1572 | 0.018105
894 | 2.1572 | 0.018125
895 | 2.1571 | 0.018145
896 | 2.1571 | 0.018165
897 | 2.1571 | 0.018185
898 | 2.157 | 0.018205
899 | 2.157 | 0.018225
900 | 2.1569 | 0.018245
901 | 2.1569 | 0.018265
902 | 2.1569 | 0.018285
903 | 2.1568 | 0.018305
904 | 2.1568 | 0.018325
905 | 2.1568 | 0.018346
906 | 2.1567 | 0.018366
907 | 2.1567 | 0.018386
908 | 2.1567 | 0.018406
909 | 2.1566 | 0.018426
910 | 2.1566 | 0.018446
911 | 2.1566 | 0.018466
912 | 2.1565 | 0.018486
913 | 2.1565 | 0.018506
914 | 2.1565 | 0.018526
915 | 2.1564 | 0.018546
916 | 2.1564 | 0.018566
917 | 2.1564 | 0.018586
918 | 2.1563 | 0.018606
919 | 2.1563 | 0.018627
920 | 2.1563 | 0.018647
921 | 2.1562 | 0.018667
922 | 2.1562 | 0.018687
923 | 2.1562 | 0.018707
924 | 2.1561 | 0.018727
925 | 2.1561 | 0.018747
926 | 2.1561 | 0.018767
927 | 2.156 | 0.018787
928 | 2.156 | 0.018807
929 | 2.156 | 0.018827
930 | 2.1559 | 0.018847
931 | 2.1559 | 0.018867
932 | 2.1559 | 0.018887
933 | 2.1558 | 0.018907
934 | 2.1558 | 0.018927
935 | 2.1558 | 0.018948
936 | 2.1557 | 0.018968
937 | 2.1557 | 0.018988
938 | 2.1557 | 0.019008
939 | 2.1556 | 0.019028
940 | 2.1556 | 0.019048
941 | 2.1556 | 0.019068
942 | 2.1555 | 0.019088
943 | 2.1555 | 0.019108
944 | 2.1555 | 0.019128
945 | 2.1554 | 0.019148
946 | 2.1554 | 0.019168
947 | 2.1554 | 0.019188
948 | 2.1553 | 0.019208
949 | 2.1553 | 0.019228
950 | 2.1553 | 0.019248
951 | 2.1552 | 0.019268
952 | 2.1552 | 0.019288
953 | 2.1552 | 0.019309
954 | 2.1551 | 0.019329
955 | 2.1551 | 0.019349
956 | 2.155 | 0.019369
957 | 2.155 | 0.019389
958 | 2.155 | 0.019409
959 | 2.1549 | 0.019429
960 | 2.1549 | 0.019449
961 | 2.1549 | 0.019469
962 | 2.1548 | 0.019489
963 | 2.1548 | 0.019509
964 | 2.1548 | 0.019529
965 | 2.1547 | 0.019549
966 | 2.1547 | 0.019569
967 | 2.1547 | 0.019589
968 | 2.1546 | 0.019609
969 | 2.1546 | 0.019629
970 | 2.1546 | 0.019649
971 | 2.1545 | 0.019669
972 | 2.1545 | 0.019689
973 | 2.1545 | 0.019709
974 | 2.1544 | 0.019729
975 | 2.1544 | 0.01975
976 | 2.1544 | 0.01977
977 | 2.1543 | 0.01979
978 | 2.1543 | 0.01981
979 | 2.1543 | 0.01983
980 | 2.1542 | 0.01985
981 | 2.1542 | 0.01987
982 | 2.1542 | 0.01989
983 | 2.1541 | 0.01991
984 | 2.1541 | 0.01993
985 | 2.1541 | 0.01995
986 | 2.154 | 0.01997
987 | 2.154 | 0.01999
988 | 2.154 | 0.02001
989 | 2.1539 | 0.02003
990 | 2.1539 | 0.02005
991 | 2.1539 | 0.02007
992 | 2.1538 | 0.02009
993 | 2.1538 | 0.02011
994 | 2.1538 | 0.02013
995 | 2.1537 | 0.02015
996 | 2.1537 | 0.02017
997 | 2.1537 | 0.02019
998 | 2.1536 | 0.02021
999 | 2.1536 | 0.02023
1000 | 2.1536 | 0.02025
1001 | 2.1535 | 0.02027
1002 | 2.1535 | 0.02029
1003 | 2.1535 | 0.02031
1004 | 2.1534 | 0.020331
1005 | 2.1534 | 0.020351
1006 | 2.1534 | 0.020371
1007 | 2.1533 | 0.020391
1008 | 2.1533 | 0.020411
1009 | 2.1533 | 0.020431
1010 | 2.1532 | 0.020451
1011 | 2.1532 | 0.020471
1012 | 2.1532 | 0.020491
1013 | 2.1531 | 0.020511
1014 | 2.1531 | 0.020531
1015 | 2.1531 | 0.020551
1016 | 2.153 | 0.020571
1017 | 2.153 | 0.020591
1018 | 2.153 | 0.020611
1019 | 2.1529 | 0.020631
1020 | 2.1529 | 0.020651
1021 | 2.1529 | 0.020671
1022 | 2.1528 | 0.020691
1023 | 2.1528 | 0.020711
1024 | 2.1527 | 0.020731
1025 | 2.1527 | 0.020751
1026 | 2.1527 | 0.020771
1027 | 2.1526 | 0.020791
1028 | 2.1526 | 0.020811
1029 | 2.1526 | 0.020831
1030 | 2.1525 | 0.020851
1031 | 2.1525 | 0.020871
1032 | 2.1525 | 0.020891
1033 | 2.1524 | 0.020911
1034 | 2.1524 | 0.020931
1035 | 2.1524 | 0.020951
1036 | 2.1523 | 0.020971
1037 | 2.1523 | 0.020991
1038 | 2.1523 | 0.021011
1039 | 2.1522 | 0.021031
1040 | 2.1522 | 0.021051
1041 | 2.1522 | 0.021071
1042 | 2.1521 | 0.021091
1043 | 2.1521 | 0.021111
1044 | 2.1521 | 0.021131
1045 | 2.152 | 0.021151
1046 | 2.152 | 0.021171
1047 | 2.152 | 0.021191
1048 | 2.1519 | 0.021211
1049 | 2.1519 | 0.021231
1050 | 2.1519 | 0.021251
1051 | 2.1518 | 0.021271
1052 | 2.1518 | 0.021291
1053 | 2.1518 | 0.021311
1054 | 2.1517 | 0.021331
1055 | 2.1517 | 0.021351
1056 | 2.1517 | 0.021371
1057 | 2.1516 | 0.021391
1058 | 2.1516 | 0.021411
1059 | 2.1516 | 0.021431
1060 | 2.1515 | 0.021451
1061 | 2.1515 | 0.021471
1062 | 2.1515 | 0.021491
1063 | 2.1514 | 0.021511
1064 | 2.1514 | 0.021531
1065 | 2.1514 | 0.021551
1066 | 2.1513 | 0.021571
1067 | 2.1513 | 0.021591
1068 | 2.1513 | 0.021611
1069 | 2.1512 | 0.021631
1070 | 2.1512 | 0.021651
1071 | 2.1512 | 0.021671
1072 | 2.1511 | 0.021691
1073 | 2.1511 | 0.021711
1074 | 2.1511 | 0.021731
1075 | 2.151 | 0.021751
1076 | 2.151 | 0.021771
1077 | 2.151 | 0.021791
1078 | 2.1509 | 0.021811
1079 | 2.1509 | 0.021831
1080 | 2.1509 | 0.021851
1081 | 2.1508 | 0.021871
1082 | 2.1508 | 0.021891
1083 | 2.1508 | 0.021911
1084 | 2.1507 | 0.021931
1085 | 2.1507 | 0.021951
1086 | 2.1507 | 0.021971
1087 | 2.1506 | 0.021991
1088 | 2.1506 | 0.022011
1089 | 2.1506 | 0.022031
1090 | 2.1505 | 0.022051
1091 | 2.1505 | 0.022071
1092 | 2.1505 | 0.022091
1093 | 2.1504 | 0.022111
1094 | 2.1504 | 0.022131
1095 | 2.1504 | 0.022151
1096 | 2.1503 | 0.022171
1097 | 2.1503 | 0.022191
1098 | 2.1503 | 0.022211
1099 | 2.1502 | 0.022231
1100 | 2.1502 | 0.022251
1101 | 2.1502 | 0.022271
1102 | 2.1501 | 0.022291
1103 | 2.1501 | 0.022311
1104 | 2.1501 | 0.022331
1105 | 2.15 | 0.022351
1106 | 2.15 | 0.022371
1107 | 2.15 | 0.022391
1108 | 2.1499 | 0.022411
1109 | 2.1499 | 0.022431
1110 | 2.1499 | 0.022451
1111 | 2.1498 | 0.022471
1112 | 2.1498 | 0.022491
1113 | 2.1498 | 0.022511
1114 | 2.1497 | 0.022531
1115 | 2.1497 | 0.022551
1116 | 2.1497 | 0.022571
1117 | 2.1496 | 0.022591
1118 | 2.1496 | 0.022611
1119 | 2.1495 | 0.022631
1120 | 2.1495 | 0.022651
1121 | 2.1495 | 0.022671
1122 | 2.1494 | 0.022691
1123 | 2.1494 | 0.022711
1124 | 2.1494 | 0.02273
1125 | 2.1493 | 0.02275
1126 | 2.1493 | 0.02277
1127 | 2.1493 | 0.02279
1128 | 2.1492 | 0.02281
1129 | 2.1492 | 0.02283
1130 | 2.1492 | 0.02285
1131 | 2.1491 | 0.02287
1132 | 2.1491 | 0.02289
1133 | 2.1491 | 0.02291
1134 | 2.149 | 0.02293
1135 | 2.149 | 0.02295
1136 | 2.149 | 0.02297
1137 | 2.1489 | 0.02299
1138 | 2.1489 | 0.02301
1139 | 2.1489 | 0.02303
1140 | 2.1488 | 0.02305
1141 | 2.1488 | 0.02307
1142 | 2.1488 | 0.02309
1143 | 2.1487 | 0.02311
1144 | 2.1487 | 0.02313
1145 | 2.1487 | 0.02315
1146 | 2.1486 | 0.02317
1147 | 2.1486 | 0.02319
1148 | 2.1486 | 0.02321
1149 | 2.1485 | 0.02323
1150 | 2.1485 | 0.02325
1151 | 2.1485 | 0.02327
1152 | 2.1484 | 0.02329
1153 | 2.1484 | 0.023309
1154 | 2.1484 | 0.023329
1155 | 2.1483 | 0.023349
1156 | 2.1483 | 0.023369
1157 | 2.1483 | 0.023389
1158 | 2.1482 | 0.023409
1159 | 2.1482 | 0.023429
1160 | 2.1482 | 0.023449
1161 | 2.1481 | 0.023469
1162 | 2.1481 | 0.023489
1163 | 2.1481 | 0.023509
1164 | 2.148 | 0.023529
1165 | 2.148 | 0.023549
1166 | 2.148 | 0.023569
1167 | 2.1479 | 0.023589
1168 | 2.1479 | 0.023609
1169 | 2.1479 | 0.023629
1170 | 2.1478 | 0.023649
1171 | 2.1478 | 0.023669
1172 | 2.1478 | 0.023689
1173 | 2.1477 | 0.023709
1174 | 2.1477 | 0.023729
1175 | 2.1477 | 0.023748
1176 | 2.1476 | 0.023768
1177 | 2.1476 | 0.023788
1178 | 2.1476 | 0.023808
1179 | 2.1475 | 0.023828
1180 | 2.1475 | 0.023848
1181 | 2.1475 | 0.023868
1182 | 2.1474 | 0.023888
1183 | 2.1474 | 0.023908
1184 | 2.1474 | 0.023928
1185 | 2.1473 | 0.023948
1186 | 2.1473 | 0.023968
1187 | 2.1473 | 0.023988
1188 | 2.1472 | 0.024008
1189 | 2.1472 | 0.024028
1190 | 2.1472 | 0.024048
1191 | 2.1471 | 0.024068
1192 | 2.1471 | 0.024088
1193 | 2.1471 | 0.024107
1194 | 2.147 | 0.024127
1195 | 2.147 | 0.024147
1196 | 2.147 | 0.024167
1197 | 2.1469 | 0.024187
1198 | 2.1469 | 0.024207
1199 | 2.1469 | 0.024227
1200 | 2.1468 | 0.024247
1201 | 2.1468 | 0.024267
1202 | 2.1468 | 0.024287
1203 | 2.1467 | 0.024307
1204 | 2.1467 | 0.024327
1205 | 2.1467 | 0.024347
1206 | 2.1466 | 0.024367
1207 | 2.1466 | 0.024387
1208 | 2.1466 | 0.024407
1209 | 2.1465 | 0.024426
1210 | 2.1465 | 0.024446
1211 | 2.1465 | 0.024466
1212 | 2.1464 | 0.024486
1213 | 2.1464 | 0.024506
1214 | 2.1464 | 0.024526
1215 | 2.1463 | 0.024546
1216 | 2.1463 | 0.024566
1217 | 2.1463 | 0.024586
1218 | 2.1462 | 0.024606
1219 | 2.1462 | 0.024626
1220 | 2.1462 | 0.024646
1221 | 2.1461 | 0.024666
1222 | 2.1461 | 0.024686
1223 | 2.1461 | 0.024706
1224 | 2.146 | 0.024725
1225 | 2.146 | 0.024745
1226 | 2.146 | 0.024765
1227 | 2.1459 | 0.024785
1228 | 2.1459 | 0.024805
1229 | 2.1459 | 0.024825
1230 | 2.1458 | 0.024845
1231 | 2.1458 | 0.024865
1232 | 2.1458 | 0.024885
1233 | 2.1457 | 0.024905
1234 | 2.1457 | 0.024925
1235 | 2.1457 | 0.024945
1236 | 2.1456 | 0.024965
1237 | 2.1456 | 0.024984
1238 | 2.1456 | 0.025004
1239 | 2.1455 | 0.025024
1240 | 2.1455 | 0.025044
1241 | 2.1455 | 0.025064
1242 | 2.1454 | 0.025084
1243 | 2.1454 | 0.025104
1244 | 2.1454 | 0.025124
1245 | 2.1453 | 0.025144
1246 | 2.1453 | 0.025164
1247 | 2.1453 | 0.025184
1248 | 2.1452 | 0.025204
1249 | 2.1452 | 0.025223
1250 | 2.1452 | 0.025243
1251 | 2.1451 | 0.025263
1252 | 2.1451 | 0.025283
1253 | 2.1451 | 0.025303
1254 | 2.145 | 0.025323
1255 | 2.145 | 0.025343
1256 | 2.145 | 0.025363
1257 | 2.1449 | 0.025383
1258 | 2.1449 | 0.025403
1259 | 2.1449 | 0.025423
1260 | 2.1448 | 0.025443
1261 | 2.1448 | 0.025462
1262 | 2.1448 | 0.025482
1263 | 2.1447 | 0.025502
1264 | 2.1447 | 0.025522
1265 | 2.1447 | 0.025542
1266 | 2.1446 | 0.025562
1267 | 2.1446 | 0.025582
1268 | 2.1446 | 0.025602
1269 | 2.1445 | 0.025622
1270 | 2.1445 | 0.025642
1271 | 2.1445 | 0.025662
1272 | 2.1444 | 0.025681
1273 | 2.1444 | 0.025701
1274 | 2.1444 | 0.025721
1275 | 2.1443 | 0.025741
1276 | 2.1443 | 0.025761
1277 | 2.1443 | 0.025781
1278 | 2.1442 | 0.025801
1279 | 2.1442 | 0.025821
1280 | 2.1442 | 0.025841
1281 | 2.1441 | 0.025861
1282 | 2.1441 | 0.02588
1283 | 2.1441 | 0.0259
1284 | 2.144 | 0.02592
1285 | 2.144 | 0.02594
1286 | 2.144 | 0.02596
1287 | 2.1439 | 0.02598
1288 | 2.1439 | 0.026
1289 | 2.1439 | 0.02602
1290 | 2.1438 | 0.02604
1291 | 2.1438 | 0.02606
1292 | 2.1438 | 0.026079
1293 | 2.1437 | 0.026099
1294 | 2.1437 | 0.026119
1295 | 2.1437 | 0.026139
1296 | 2.1436 | 0.026159
1297 | 2.1436 | 0.026179
1298 | 2.1436 | 0.026199
1299 | 2.1435 | 0.026219
1300 | 2.1435 | 0.026239
1301 | 2.1435 | 0.026259
1302 | 2.1434 | 0.026278
1303 | 2.1434 | 0.026298
1304 | 2.1434 | 0.026318
1305 | 2.1433 | 0.026338
1306 | 2.1433 | 0.026358
1307 | 2.1433 | 0.026378
1308 | 2.1432 | 0.026398
1309 | 2.1432 | 0.026418
1310 | 2.1432 | 0.026438
1311 | 2.1431 | 0.026457
1312 | 2.1431 | 0.026477
1313 | 2.1431 | 0.026497
1314 | 2.143 | 0.026517
1315 | 2.143 | 0.026537
1316 | 2.143 | 0.026557
1317 | 2.1429 | 0.026577
1318 | 2.1429 | 0.026597
1319 | 2.1429 | 0.026617
1320 | 2.1428 | 0.026636
1321 | 2.1428 | 0.026656
1322 | 2.1428 | 0.026676
1323 | 2.1427 | 0.026696
1324 | 2.1427 | 0.026716
1325 | 2.1427 | 0.026736
1326 | 2.1426 | 0.026756
1327 | 2.1426 | 0.026776
1328 | 2.1426 | 0.026795
1329 | 2.1425 | 0.026815
1330 | 2.1425 | 0.026835
1331 | 2.1425 | 0.026855
1332 | 2.1424 | 0.026875
1333 | 2.1424 | 0.026895
1334 | 2.1424 | 0.026915
1335 | 2.1423 | 0.026935
1336 | 2.1423 | 0.026954
1337 | 2.1423 | 0.026974
1338 | 2.1422 | 0.026994
1339 | 2.1422 | 0.027014
1340 | 2.1422 | 0.027034
1341 | 2.1421 | 0.027054
1342 | 2.1421 | 0.027074
1343 | 2.1421 | 0.027094
1344 | 2.142 | 0.027113
1345 | 2.142 | 0.027133
1346 | 2.142 | 0.027153
1347 | 2.1419 | 0.027173
1348 | 2.1419 | 0.027193
1349 | 2.1419 | 0.027213
1350 | 2.1418 | 0.027233
1351 | 2.1418 | 0.027253
1352 | 2.1418 | 0.027272
1353 | 2.1417 | 0.027292
1354 | 2.1417 | 0.027312
1355 | 2.1417 | 0.027332
1356 | 2.1416 | 0.027352
1357 | 2.1416 | 0.027372
1358 | 2.1416 | 0.027392
1359 | 2.1415 | 0.027412
1360 | 2.1415 | 0.027431
1361 | 2.1415 | 0.027451
1362 | 2.1414 | 0.027471
1363 | 2.1414 | 0.027491
1364 | 2.1414 | 0.027511
1365 | 2.1413 | 0.027531
1366 | 2.1413 | 0.027551
1367 | 2.1413 | 0.02757
1368 | 2.1412 | 0.02759
1369 | 2.1412 | 0.02761
1370 | 2.1412 | 0.02763
1371 | 2.1411 | 0.02765
1372 | 2.1411 | 0.02767
1373 | 2.1411 | 0.02769
1374 | 2.141 | 0.027709
1375 | 2.141 | 0.027729
1376 | 2.141 | 0.027749
1377 | 2.1409 | 0.027769
1378 | 2.1409 | 0.027789
1379 | 2.1409 | 0.027809
1380 | 2.1408 | 0.027829
1381 | 2.1408 | 0.027848
1382 | 2.1408 | 0.027868
1383 | 2.1407 | 0.027888
1384 | 2.1407 | 0.027908
1385 | 2.1407 | 0.027928
1386 | 2.1406 | 0.027948
1387 | 2.1406 | 0.027968
1388 | 2.1406 | 0.027987
1389 | 2.1405 | 0.028007
1390 | 2.1405 | 0.028027
1391 | 2.1405 | 0.028047
1392 | 2.1404 | 0.028067
1393 | 2.1404 | 0.028087
1394 | 2.1404 | 0.028107
1395 | 2.1403 | 0.028126
1396 | 2.1403 | 0.028146
1397 | 2.1403 | 0.028166
1398 | 2.1402 | 0.028186
1399 | 2.1402 | 0.028206
1400 | 2.1402 | 0.028226
1401 | 2.1401 | 0.028246
1402 | 2.1401 | 0.028265
1403 | 2.1401 | 0.028285
1404 | 2.14 | 0.028305
1405 | 2.14 | 0.028325
1406 | 2.14 | 0.028345
1407 | 2.1399 | 0.028365
1408 | 2.1399 | 0.028384
1409 | 2.1399 | 0.028404
1410 | 2.1398 | 0.028424
1411 | 2.1398 | 0.028444
1412 | 2.1398 | 0.028464
1413 | 2.1397 | 0.028484
1414 | 2.1397 | 0.028504
1415 | 2.1397 | 0.028523
1416 | 2.1396 | 0.028543
1417 | 2.1396 | 0.028563
1418 | 2.1396 | 0.028583
1419 | 2.1395 | 0.028603
1420 | 2.1395 | 0.028623
1421 | 2.1395 | 0.028642
1422 | 2.1394 | 0.028662
1423 | 2.1394 | 0.028682
1424 | 2.1394 | 0.028702
1425 | 2.1393 | 0.028722
1426 | 2.1393 | 0.028742
1427 | 2.1393 | 0.028761
1428 | 2.1392 | 0.028781
1429 | 2.1392 | 0.028801
1430 | 2.1392 | 0.028821
1431 | 2.1391 | 0.028841
1432 | 2.1391 | 0.028861
1433 | 2.1391 | 0.02888
1434 | 2.1391 | 0.0289
1435 | 2.139 | 0.02892
1436 | 2.139 | 0.02894
1437 | 2.139 | 0.02896
1438 | 2.1389 | 0.02898
1439 | 2.1389 | 0.028999
1440 | 2.1389 | 0.029019
1441 | 2.1388 | 0.029039
1442 | 2.1388 | 0.029059
1443 | 2.1388 | 0.029079
1444 | 2.1387 | 0.029099
1445 | 2.1387 | 0.029118
1446 | 2.1387 | 0.029138
1447 | 2.1386 | 0.029158
1448 | 2.1386 | 0.029178
1449 | 2.1386 | 0.029198
1450 | 2.1385 | 0.029218
1451 | 2.1385 | 0.029237
1452 | 2.1385 | 0.029257
1453 | 2.1384 | 0.029277
1454 | 2.1384 | 0.029297
1455 | 2.1384 | 0.029317
1456 | 2.1383 | 0.029337
1457 | 2.1383 | 0.029356
1458 | 2.1383 | 0.029376
1459 | 2.1382 | 0.029396
1460 | 2.1382 | 0.029416
1461 | 2.1382 | 0.029436
1462 | 2.1381 | 0.029455
1463 | 2.1381 | 0.029475
1464 | 2.1381 | 0.029495
1465 | 2.138 | 0.029515
1466 | 2.138 | 0.029535
1467 | 2.138 | 0.029555
1468 | 2.1379 | 0.029574
1469 | 2.1379 | 0.029594
1470 | 2.1379 | 0.029614
1471 | 2.1378 | 0.029634
1472 | 2.1378 | 0.029654
1473 | 2.1378 | 0.029673
1474 | 2.1377 | 0.029693
1475 | 2.1377 | 0.029713
1476 | 2.1377 | 0.029733
1477 | 2.1376 | 0.029753
1478 | 2.1376 | 0.029773
1479 | 2.1376 | 0.029792
1480 | 2.1375 | 0.029812
1481 | 2.1375 | 0.029832
1482 | 2.1375 | 0.029852
1483 | 2.1374 | 0.029872
1484 | 2.1374 | 0.029891
1485 | 2.1374 | 0.029911
1486 | 2.1373 | 0.029931
1487 | 2.1373 | 0.029951
1488 | 2.1373 | 0.029971
1489 | 2.1372 | 0.02999
1490 | 2.1372 | 0.03001
1491 | 2.1372 | 0.03003
1492 | 2.1371 | 0.03005
1493 | 2.1371 | 0.03007
1494 | 2.1371 | 0.03009
1495 | 2.137 | 0.030109
1496 | 2.137 | 0.030129
1497 | 2.137 | 0.030149
1498 | 2.1369 | 0.030169
1499 | 2.1369 | 0.030189
1500 | 2.1369 | 0.030208
1501 | 2.1368 | 0.030228
1502 | 2.1368 | 0.030248
1503 | 2.1368 | 0.030268
1504 | 2.1367 | 0.030288
1505 | 2.1367 | 0.030307
1506 | 2.1367 | 0.030327
1507 | 2.1366 | 0.030347
1508 | 2.1366 | 0.030367
1509 | 2.1366 | 0.030387
1510 | 2.1365 | 0.030406
1511 | 2.1365 | 0.030426
1512 | 2.1365 | 0.030446
1513 | 2.1364 | 0.030466
1514 | 2.1364 | 0.030486
1515 | 2.1364 | 0.030505
1516 | 2.1363 | 0.030525
1517 | 2.1363 | 0.030545
1518 | 2.1363 | 0.030565
1519 | 2.1362 | 0.030585
1520 | 2.1362 | 0.030604
1521 | 2.1362 | 0.030624
1522 | 2.1361 | 0.030644
1523 | 2.1361 | 0.030664
1524 | 2.1361 | 0.030684
1525 | 2.136 | 0.030703
1526 | 2.136 | 0.030723
1527 | 2.136 | 0.030743
1528 | 2.136 | 0.030763
1529 | 2.1359 | 0.030782
1530 | 2.1359 | 0.030802
1531 | 2.1359 | 0.030822
1532 | 2.1358 | 0.030842
1533 | 2.1358 | 0.030862
1534 | 2.1358 | 0.030881
1535 | 2.1357 | 0.030901
1536 | 2.1357 | 0.030921
1537 | 2.1357 | 0.030941
1538 | 2.1356 | 0.030961
1539 | 2.1356 | 0.03098
1540 | 2.1356 | 0.031
1541 | 2.1355 | 0.03102
1542 | 2.1355 | 0.03104
1543 | 2.1355 | 0.03106
1544 | 2.1354 | 0.031079
1545 | 2.1354 | 0.031099
1546 | 2.1354 | 0.031119
1547 | 2.1353 | 0.031139
1548 | 2.1353 | 0.031158
1549 | 2.1353 | 0.031178
1550 | 2.1352 | 0.031198
1551 | 2.1352 | 0.031218
1552 | 2.1352 | 0.031238
1553 | 2.1351 | 0.031257
1554 | 2.1351 | 0.031277
1555 | 2.1351 | 0.031297
1556 | 2.135 | 0.031317
1557 | 2.135 | 0.031336
1558 | 2.135 | 0.031356
1559 | 2.1349 | 0.031376
1560 | 2.1349 | 0.031396
1561 | 2.1349 | 0.031416
1562 | 2.1348 | 0.031435
1563 | 2.1348 | 0.031455
1564 | 2.1348 | 0.031475
1565 | 2.1347 | 0.031495
1566 | 2.1347 | 0.031514
1567 | 2.1347 | 0.031534
1568 | 2.1346 | 0.031554
1569 | 2.1346 | 0.031574
1570 | 2.1346 | 0.031594
1571 | 2.1345 | 0.031613
1572 | 2.1345 | 0.031633
1573 | 2.1345 | 0.031653
1574 | 2.1344 | 0.031673
1575 | 2.1344 | 0.031692
1576 | 2.1344 | 0.031712
1577 | 2.1343 | 0.031732
1578 | 2.1343 | 0.031752
1579 | 2.1343 | 0.031772
1580 | 2.1342 | 0.031791
1581 | 2.1342 | 0.031811
1582 | 2.1342 | 0.031831
1583 | 2.1341 | 0.031851
1584 | 2.1341 | 0.03187
1585 | 2.1341 | 0.03189
1586 | 2.134 | 0.03191
1587 | 2.134 | 0.03193
1588 | 2.134 | 0.031949
1589 | 2.1339 | 0.031969
1590 | 2.1339 | 0.031989
1591 | 2.1339 | 0.032009
1592 | 2.1338 | 0.032028
1593 | 2.1338 | 0.032048
1594 | 2.1338 | 0.032068
1595 | 2.1337 | 0.032088
1596 | 2.1337 | 0.032108
1597 | 2.1337 | 0.032127
1598 | 2.1337 | 0.032147
1599 | 2.1336 | 0.032167
1600 | 2.1336 | 0.032187
1601 | 2.1336 | 0.032206
1602 | 2.1335 | 0.032226
1603 | 2.1335 | 0.032246
1604 | 2.1335 | 0.032266
1605 | 2.1334 | 0.032285
1606 | 2.1334 | 0.032305
1607 | 2.1334 | 0.032325
1608 | 2.1333 | 0.032345
1609 | 2.1333 | 0.032364
1610 | 2.1333 | 0.032384
1611 | 2.1332 | 0.032404
1612 | 2.1332 | 0.032424
1613 | 2.1332 | 0.032443
1614 | 2.1331 | 0.032463
1615 | 2.1331 | 0.032483
1616 | 2.1331 | 0.032503
1617 | 2.133 | 0.032522
1618 | 2.133 | 0.032542
1619 | 2.133 | 0.032562
1620 | 2.1329 | 0.032582
1621 | 2.1329 | 0.032601
1622 | 2.1329 | 0.032621
1623 | 2.1328 | 0.032641
1624 | 2.1328 | 0.032661
1625 | 2.1328 | 0.03268
1626 | 2.1327 | 0.0327
1627 | 2.1327 | 0.03272
1628 | 2.1327 | 0.03274
1629 | 2.1326 | 0.032759
1630 | 2.1326 | 0.032779
1631 | 2.1326 | 0.032799
1632 | 2.1325 | 0.032819
1633 | 2.1325 | 0.032838
1634 | 2.1325 | 0.032858
1635 | 2.1324 | 0.032878
1636 | 2.1324 | 0.032898
1637 | 2.1324 | 0.032917
1638 | 2.1323 | 0.032937
1639 | 2.1323 | 0.032957
1640 | 2.1323 | 0.032977
1641 | 2.1322 | 0.032996
1642 | 2.1322 | 0.033016
1643 | 2.1322 | 0.033036
1644 | 2.1321 | 0.033056
1645 | 2.1321 | 0.033075
1646 | 2.1321 | 0.033095
1647 | 2.132 | 0.033115
1648 | 2.132 | 0.033135
1649 | 2.132 | 0.033154
1650 | 2.1319 | 0.033174
1651 | 2.1319 | 0.033194
1652 | 2.1319 | 0.033214
1653 | 2.1319 | 0.033233
1654 | 2.1318 | 0.033253
1655 | 2.1318 | 0.033273
1656 | 2.1318 | 0.033292
1657 | 2.1317 | 0.033312
1658 | 2.1317 | 0.033332
1659 | 2.1317 | 0.033352
1660 | 2.1316 | 0.033371
1661 | 2.1316 | 0.033391
1662 | 2.1316 | 0.033411
1663 | 2.1315 | 0.033431
1664 | 2.1315 | 0.03345
1665 | 2.1315 | 0.03347
1666 | 2.1314 | 0.03349
1667 | 2.1314 | 0.03351
1668 | 2.1314 | 0.033529
1669 | 2.1313 | 0.033549
1670 | 2.1313 | 0.033569
1671 | 2.1313 | 0.033588
1672 | 2.1312 | 0.033608
1673 | 2.1312 | 0.033628
1674 | 2.1312 | 0.033648
1675 | 2.1311 | 0.033667
1676 | 2.1311 | 0.033687
1677 | 2.1311 | 0.033707
1678 | 2.131 | 0.033727
1679 | 2.131 | 0.033746
1680 | 2.131 | 0.033766
1681 | 2.1309 | 0.033786
1682 | 2.1309 | 0.033805
1683 | 2.1309 | 0.033825
1684 | 2.1308 | 0.033845
1685 | 2.1308 | 0.033865
1686 | 2.1308 | 0.033884
1687 | 2.1307 | 0.033904
1688 | 2.1307 | 0.033924
1689 | 2.1307 | 0.033944
1690 | 2.1306 | 0.033963
1691 | 2.1306 | 0.033983
1692 | 2.1306 | 0.034003
1693 | 2.1305 | 0.034022
1694 | 2.1305 | 0.034042
1695 | 2.1305 | 0.034062
1696 | 2.1304 | 0.034082
1697 | 2.1304 | 0.034101
1698 | 2.1304 | 0.034121
1699 | 2.1303 | 0.034141
1700 | 2.1303 | 0.03416
1701 | 2.1303 | 0.03418
1702 | 2.1302 | 0.0342
1703 | 2.1302 | 0.03422
1704 | 2.1302 | 0.034239
1705 | 2.1302 | 0.034259
1706 | 2.1301 | 0.034279
1707 | 2.1301 | 0.034298
1708 | 2.1301 | 0.034318
1709 | 2.13 | 0.034338
1710 | 2.13 | 0.034358
1711 | 2.13 | 0.034377
1712 | 2.1299 | 0.034397
1713 | 2.1299 | 0.034417
1714 | 2.1299 | 0.034436
1715 | 2.1298 | 0.034456
1716 | 2.1298 | 0.034476
1717 | 2.1298 | 0.034496
1718 | 2.1297 | 0.034515
1719 | 2.1297 | 0.034535
1720 | 2.1297 | 0.034555
1721 | 2.1296 | 0.034574
1722 | 2.1296 | 0.034594
1723 | 2.1296 | 0.034614
1724 | 2.1295 | 0.034634
1725 | 2.1295 | 0.034653
1726 | 2.1295 | 0.034673
1727 | 2.1294 | 0.034693
1728 | 2.1294 | 0.034712
1729 | 2.1294 | 0.034732
1730 | 2.1293 | 0.034752
1731 | 2.1293 | 0.034772
1732 | 2.1293 | 0.034791
1733 | 2.1292 | 0.034811
1734 | 2.1292 | 0.034831
1735 | 2.1292 | 0.03485
1736 | 2.1291 | 0.03487
1737 | 2.1291 | 0.03489
1738 | 2.1291 | 0.034909
1739 | 2.129 | 0.034929
1740 | 2.129 | 0.034949
1741 | 2.129 | 0.034969
1742 | 2.1289 | 0.034988
1743 | 2.1289 | 0.035008
1744 | 2.1289 | 0.035028
1745 | 2.1288 | 0.035047
1746 | 2.1288 | 0.035067
1747 | 2.1288 | 0.035087
1748 | 2.1288 | 0.035106
1749 | 2.1287 | 0.035126
1750 | 2.1287 | 0.035146
1751 | 2.1287 | 0.035165
1752 | 2.1286 | 0.035185
1753 | 2.1286 | 0.035205
1754 | 2.1286 | 0.035225
1755 | 2.1285 | 0.035244
1756 | 2.1285 | 0.035264
1757 | 2.1285 | 0.035284
1758 | 2.1284 | 0.035303
1759 | 2.1284 | 0.035323
1760 | 2.1284 | 0.035343
1761 | 2.1283 | 0.035362
1762 | 2.1283 | 0.035382
1763 | 2.1283 | 0.035402
1764 | 2.1282 | 0.035421
1765 | 2.1282 | 0.035441
1766 | 2.1282 | 0.035461
1767 | 2.1281 | 0.035481
1768 | 2.1281 | 0.0355
1769 | 2.1281 | 0.03552
1770 | 2.128 | 0.03554
1771 | 2.128 | 0.035559
1772 | 2.128 | 0.035579
1773 | 2.1279 | 0.035599
1774 | 2.1279 | 0.035618
1775 | 2.1279 | 0.035638
1776 | 2.1278 | 0.035658
1777 | 2.1278 | 0.035677
1778 | 2.1278 | 0.035697
1779 | 2.1277 | 0.035717
1780 | 2.1277 | 0.035736
1781 | 2.1277 | 0.035756
1782 | 2.1276 | 0.035776
1783 | 2.1276 | 0.035796
1784 | 2.1276 | 0.035815
1785 | 2.1275 | 0.035835
1786 | 2.1275 | 0.035855
1787 | 2.1275 | 0.035874
1788 | 2.1275 | 0.035894
1789 | 2.1274 | 0.035914
1790 | 2.1274 | 0.035933
1791 | 2.1274 | 0.035953
1792 | 2.1273 | 0.035973
1793 | 2.1273 | 0.035992
1794 | 2.1273 | 0.036012
1795 | 2.1272 | 0.036032
1796 | 2.1272 | 0.036051
1797 | 2.1272 | 0.036071
1798 | 2.1271 | 0.036091
1799 | 2.1271 | 0.03611
1800 | 2.1271 | 0.03613
1801 | 2.127 | 0.03615
1802 | 2.127 | 0.036169
1803 | 2.127 | 0.036189
1804 | 2.1269 | 0.036209
1805 | 2.1269 | 0.036228
1806 | 2.1269 | 0.036248
1807 | 2.1268 | 0.036268
1808 | 2.1268 | 0.036287
1809 | 2.1268 | 0.036307
1810 | 2.1267 | 0.036327
1811 | 2.1267 | 0.036346
1812 | 2.1267 | 0.036366
1813 | 2.1266 | 0.036386
1814 | 2.1266 | 0.036405
1815 | 2.1266 | 0.036425
1816 | 2.1265 | 0.036445
1817 | 2.1265 | 0.036464
1818 | 2.1265 | 0.036484
1819 | 2.1264 | 0.036504
1820 | 2.1264 | 0.036523
1821 | 2.1264 | 0.036543
1822 | 2.1263 | 0.036563
1823 | 2.1263 | 0.036582
1824 | 2.1263 | 0.036602
1825 | 2.1263 | 0.036622
1826 | 2.1262 | 0.036641
1827 | 2.1262 | 0.036661
1828 | 2.1262 | 0.036681
1829 | 2.1261 | 0.0367
1830 | 2.1261 | 0.03672
1831 | 2.1261 | 0.03674
1832 | 2.126 | 0.036759
1833 | 2.126 | 0.036779
1834 | 2.126 | 0.036799
1835 | 2.1259 | 0.036818
1836 | 2.1259 | 0.036838
1837 | 2.1259 | 0.036858
1838 | 2.1258 | 0.036877
1839 | 2.1258 | 0.036897
1840 | 2.1258 | 0.036917
1841 | 2.1257 | 0.036936
1842 | 2.1257 | 0.036956
1843 | 2.1257 | 0.036976
1844 | 2.1256 | 0.036995
1845 | 2.1256 | 0.037015
1846 | 2.1256 | 0.037035
1847 | 2.1255 | 0.037054
1848 | 2.1255 | 0.037074
1849 | 2.1255 | 0.037094
1850 | 2.1254 | 0.037113
1851 | 2.1254 | 0.037133
1852 | 2.1254 | 0.037153
1853 | 2.1253 | 0.037172
1854 | 2.1253 | 0.037192
1855 | 2.1253 | 0.037211
1856 | 2.1252 | 0.037231
1857 | 2.1252 | 0.037251
1858 | 2.1252 | 0.03727
1859 | 2.1251 | 0.03729
1860 | 2.1251 | 0.03731
1861 | 2.1251 | 0.037329
1862 | 2.1251 | 0.037349
1863 | 2.125 | 0.037369
1864 | 2.125 | 0.037388
1865 | 2.125 | 0.037408
1866 | 2.1249 | 0.037428
1867 | 2.1249 | 0.037447
1868 | 2.1249 | 0.037467
1869 | 2.1248 | 0.037487
1870 | 2.1248 | 0.037506
1871 | 2.1248 | 0.037526
1872 | 2.1247 | 0.037545
1873 | 2.1247 | 0.037565
1874 | 2.1247 | 0.037585
1875 | 2.1246 | 0.037604
1876 | 2.1246 | 0.037624
1877 | 2.1246 | 0.037644
1878 | 2.1245 | 0.037663
1879 | 2.1245 | 0.037683
1880 | 2.1245 | 0.037703
1881 | 2.1244 | 0.037722
1882 | 2.1244 | 0.037742
1883 | 2.1244 | 0.037762
1884 | 2.1243 | 0.037781
1885 | 2.1243 | 0.037801
1886 | 2.1243 | 0.03782
1887 | 2.1242 | 0.03784
1888 | 2.1242 | 0.03786
1889 | 2.1242 | 0.037879
1890 | 2.1241 | 0.037899
1891 | 2.1241 | 0.037919
1892 | 2.1241 | 0.037938
1893 | 2.124 | 0.037958
1894 | 2.124 | 0.037978
1895 | 2.124 | 0.037997
1896 | 2.124 | 0.038017
1897 | 2.1239 | 0.038036
1898 | 2.1239 | 0.038056
1899 | 2.1239 | 0.038076
1900 | 2.1238 | 0.038095
1901 | 2.1238 | 0.038115
1902 | 2.1238 | 0.038135
1903 | 2.1237 | 0.038154
1904 | 2.1237 | 0.038174
1905 | 2.1237 | 0.038193
1906 | 2.1236 | 0.038213
1907 | 2.1236 | 0.038233
1908 | 2.1236 | 0.038252
1909 | 2.1235 | 0.038272
1910 | 2.1235 | 0.038292
1911 | 2.1235 | 0.038311
1912 | 2.1234 | 0.038331
1913 | 2.1234 | 0.038351
1914 | 2.1234 | 0.03837
1915 | 2.1233 | 0.03839
1916 | 2.1233 | 0.038409
1917 | 2.1233 | 0.038429
1918 | 2.1232 | 0.038449
1919 | 2.1232 | 0.038468
1920 | 2.1232 | 0.038488
1921 | 2.1231 | 0.038507
1922 | 2.1231 | 0.038527
1923 | 2.1231 | 0.038547
1924 | 2.123 | 0.038566
1925 | 2.123 | 0.038586
1926 | 2.123 | 0.038606
1927 | 2.123 | 0.038625
1928 | 2.1229 | 0.038645
1929 | 2.1229 | 0.038664
1930 | 2.1229 | 0.038684
1931 | 2.1228 | 0.038704
1932 | 2.1228 | 0.038723
1933 | 2.1228 | 0.038743
1934 | 2.1227 | 0.038763
1935 | 2.1227 | 0.038782
1936 | 2.1227 | 0.038802
1937 | 2.1226 | 0.038821
1938 | 2.1226 | 0.038841
1939 | 2.1226 | 0.038861
1940 | 2.1225 | 0.03888
1941 | 2.1225 | 0.0389
1942 | 2.1225 | 0.038919
1943 | 2.1224 | 0.038939
1944 | 2.1224 | 0.038959
1945 | 2.1224 | 0.038978
1946 | 2.1223 | 0.038998
1947 | 2.1223 | 0.039018
1948 | 2.1223 | 0.039037
1949 | 2.1222 | 0.039057
1950 | 2.1222 | 0.039076
1951 | 2.1222 | 0.039096
1952 | 2.1221 | 0.039116
1953 | 2.1221 | 0.039135
1954 | 2.1221 | 0.039155
1955 | 2.1221 | 0.039174
1956 | 2.122 | 0.039194
1957 | 2.122 | 0.039214
1958 | 2.122 | 0.039233
1959 | 2.1219 | 0.039253
1960 | 2.1219 | 0.039272
1961 | 2.1219 | 0.039292
1962 | 2.1218 | 0.039312
1963 | 2.1218 | 0.039331
1964 | 2.1218 | 0.039351
1965 | 2.1217 | 0.03937
1966 | 2.1217 | 0.03939
1967 | 2.1217 | 0.03941
1968 | 2.1216 | 0.039429
1969 | 2.1216 | 0.039449
1970 | 2.1216 | 0.039468
1971 | 2.1215 | 0.039488
1972 | 2.1215 | 0.039508
1973 | 2.1215 | 0.039527
1974 | 2.1214 | 0.039547
1975 | 2.1214 | 0.039567
1976 | 2.1214 | 0.039586
1977 | 2.1213 | 0.039606
1978 | 2.1213 | 0.039625
1979 | 2.1213 | 0.039645
1980 | 2.1212 | 0.039664
1981 | 2.1212 | 0.039684
1982 | 2.1212 | 0.039704
1983 | 2.1211 | 0.039723
1984 | 2.1211 | 0.039743
1985 | 2.1211 | 0.039762
1986 | 2.1211 | 0.039782
1987 | 2.121 | 0.039802
1988 | 2.121 | 0.039821
1989 | 2.121 | 0.039841
1990 | 2.1209 | 0.03986
1991 | 2.1209 | 0.03988
1992 | 2.1209 | 0.0399
1993 | 2.1208 | 0.039919
1994 | 2.1208 | 0.039939
1995 | 2.1208 | 0.039958
1996 | 2.1207 | 0.039978
1997 | 2.1207 | 0.039998
1998 | 2.1207 | 0.040017
1999 | 2.1206 | 0.040037
2000 | 2.1206 | 0.040056
2001 | 2.1206 | 0.040076
2002 | 2.1205 | 0.040096
2003 | 2.1205 | 0.040115
2004 | 2.1205 | 0.040135
2005 | 2.1204 | 0.040154
2006 | 2.1204 | 0.040174
2007 | 2.1204 | 0.040193
2008 | 2.1203 | 0.040213
2009 | 2.1203 | 0.040233
2010 | 2.1203 | 0.040252
2011 | 2.1202 | 0.040272
2012 | 2.1202 | 0.040291
2013 | 2.1202 | 0.040311
2014 | 2.1202 | 0.040331
2015 | 2.1201 | 0.04035
2016 | 2.1201 | 0.04037
2017 | 2.1201 | 0.040389
2018 | 2.12 | 0.040409
2019 | 2.12 | 0.040428
2020 | 2.12 | 0.040448
2021 | 2.1199 | 0.040468
2022 | 2.1199 | 0.040487
2023 | 2.1199 | 0.040507
2024 | 2.1198 | 0.040526
2025 | 2.1198 | 0.040546
2026 | 2.1198 | 0.040566
2027 | 2.1197 | 0.040585
2028 | 2.1197 | 0.040605
2029 | 2.1197 | 0.040624
2030 | 2.1196 | 0.040644
2031 | 2.1196 | 0.040663
2032 | 2.1196 | 0.040683
2033 | 2.1195 | 0.040703
2034 | 2.1195 | 0.040722
2035 | 2.1195 | 0.040742
2036 | 2.1194 | 0.040761
2037 | 2.1194 | 0.040781
2038 | 2.1194 | 0.0408
2039 | 2.1194 | 0.04082
2040 | 2.1193 | 0.04084
2041 | 2.1193 | 0.040859
2042 | 2.1193 | 0.040879
2043 | 2.1192 | 0.040898
2044 | 2.1192 | 0.040918
2045 | 2.1192 | 0.040937
2046 | 2.1191 | 0.040957
2047 | 2.1191 | 0.040977
2048 | 2.1191 | 0.040996
2049 | 2.119 | 0.041016
2050 | 2.119 | 0.041035
2051 | 2.119 | 0.041055
2052 | 2.1189 | 0.041074
2053 | 2.1189 | 0.041094
2054 | 2.1189 | 0.041114
2055 | 2.1188 | 0.041133
2056 | 2.1188 | 0.041153
2057 | 2.1188 | 0.041172
2058 | 2.1187 | 0.041192
2059 | 2.1187 | 0.041211
2060 | 2.1187 | 0.041231
2061 | 2.1186 | 0.041251
2062 | 2.1186 | 0.04127
2063 | 2.1186 | 0.04129
2064 | 2.1185 | 0.041309
2065 | 2.1185 | 0.041329
2066 | 2.1185 | 0.041348
2067 | 2.1185 | 0.041368
2068 | 2.1184 | 0.041387
2069 | 2.1184 | 0.041407
2070 | 2.1184 | 0.041427
2071 | 2.1183 | 0.041446
2072 | 2.1183 | 0.041466
2073 | 2.1183 | 0.041485
2074 | 2.1182 | 0.041505
2075 | 2.1182 | 0.041524
2076 | 2.1182 | 0.041544
2077 | 2.1181 | 0.041563
2078 | 2.1181 | 0.041583
2079 | 2.1181 | 0.041603
2080 | 2.118 | 0.041622
2081 | 2.118 | 0.041642
2082 | 2.118 | 0.041661
2083 | 2.1179 | 0.041681
2084 | 2.1179 | 0.0417
2085 | 2.1179 | 0.04172
2086 | 2.1178 | 0.041739
2087 | 2.1178 | 0.041759
2088 | 2.1178 | 0.041779
2089 | 2.1177 | 0.041798
2090 | 2.1177 | 0.041818
2091 | 2.1177 | 0.041837
2092 | 2.1177 | 0.041857
2093 | 2.1176 | 0.041876
2094 | 2.1176 | 0.041896
2095 | 2.1176 | 0.041915
2096 | 2.1175 | 0.041935
2097 | 2.1175 | 0.041955
2098 | 2.1175 | 0.041974
2099 | 2.1174 | 0.041994
2100 | 2.1174 | 0.042013
2101 | 2.1174 | 0.042033
2102 | 2.1173 | 0.042052
2103 | 2.1173 | 0.042072
2104 | 2.1173 | 0.042091
2105 | 2.1172 | 0.042111
2106 | 2.1172 | 0.04213
2107 | 2.1172 | 0.04215
2108 | 2.1171 | 0.04217
2109 | 2.1171 | 0.042189
2110 | 2.1171 | 0.042209
2111 | 2.117 | 0.042228
2112 | 2.117 | 0.042248
2113 | 2.117 | 0.042267
2114 | 2.117 | 0.042287
2115 | 2.1169 | 0.042306
2116 | 2.1169 | 0.042326
2117 | 2.1169 | 0.042345
2118 | 2.1168 | 0.042365
2119 | 2.1168 | 0.042385
2120 | 2.1168 | 0.042404
2121 | 2.1167 | 0.042424
2122 | 2.1167 | 0.042443
2123 | 2.1167 | 0.042463
2124 | 2.1166 | 0.042482
2125 | 2.1166 | 0.042502
2126 | 2.1166 | 0.042521
2127 | 2.1165 | 0.042541
2128 | 2.1165 | 0.04256
2129 | 2.1165 | 0.04258
2130 | 2.1164 | 0.042599
2131 | 2.1164 | 0.042619
2132 | 2.1164 | 0.042638
2133 | 2.1163 | 0.042658
2134 | 2.1163 | 0.042678
2135 | 2.1163 | 0.042697
2136 | 2.1162 | 0.042717
2137 | 2.1162 | 0.042736
2138 | 2.1162 | 0.042756
2139 | 2.1162 | 0.042775
2140 | 2.1161 | 0.042795
2141 | 2.1161 | 0.042814
2142 | 2.1161 | 0.042834
2143 | 2.116 | 0.042853
2144 | 2.116 | 0.042873
2145 | 2.116 | 0.042892
2146 | 2.1159 | 0.042912
2147 | 2.1159 | 0.042931
2148 | 2.1159 | 0.042951
2149 | 2.1158 | 0.04297
2150 | 2.1158 | 0.04299
2151 | 2.1158 | 0.04301
2152 | 2.1157 | 0.043029
2153 | 2.1157 | 0.043049
2154 | 2.1157 | 0.043068
2155 | 2.1156 | 0.043088
2156 | 2.1156 | 0.043107
2157 | 2.1156 | 0.043127
2158 | 2.1155 | 0.043146
2159 | 2.1155 | 0.043166
2160 | 2.1155 | 0.043185
2161 | 2.1155 | 0.043205
2162 | 2.1154 | 0.043224
2163 | 2.1154 | 0.043244
2164 | 2.1154 | 0.043263
2165 | 2.1153 | 0.043283
2166 | 2.1153 | 0.043302
2167 | 2.1153 | 0.043322
2168 | 2.1152 | 0.043341
2169 | 2.1152 | 0.043361
2170 | 2.1152 | 0.04338
2171 | 2.1151 | 0.0434
2172 | 2.1151 | 0.043419
2173 | 2.1151 | 0.043439
2174 | 2.115 | 0.043459
2175 | 2.115 | 0.043478
2176 | 2.115 | 0.043498
2177 | 2.1149 | 0.043517
2178 | 2.1149 | 0.043537
2179 | 2.1149 | 0.043556
2180 | 2.1148 | 0.043576
2181 | 2.1148 | 0.043595
2182 | 2.1148 | 0.043615
2183 | 2.1147 | 0.043634
2184 | 2.1147 | 0.043654
2185 | 2.1147 | 0.043673
2186 | 2.1147 | 0.043693
2187 | 2.1146 | 0.043712
2188 | 2.1146 | 0.043732
2189 | 2.1146 | 0.043751
2190 | 2.1145 | 0.043771
2191 | 2.1145 | 0.04379
2192 | 2.1145 | 0.04381
2193 | 2.1144 | 0.043829
2194 | 2.1144 | 0.043849
2195 | 2.1144 | 0.043868
2196 | 2.1143 | 0.043888
2197 | 2.1143 | 0.043907
2198 | 2.1143 | 0.043927
2199 | 2.1142 | 0.043946
2200 | 2.1142 | 0.043966
2201 | 2.1142 | 0.043985
2202 | 2.1141 | 0.044005
2203 | 2.1141 | 0.044024
2204 | 2.1141 | 0.044044
2205 | 2.114 | 0.044063
2206 | 2.114 | 0.044083
2207 | 2.114 | 0.044102
2208 | 2.114 | 0.044122
2209 | 2.1139 | 0.044141
2210 | 2.1139 | 0.044161
2211 | 2.1139 | 0.04418
2212 | 2.1138 | 0.0442
2213 | 2.1138 | 0.044219
2214 | 2.1138 | 0.044239
2215 | 2.1137 | 0.044258
2216 | 2.1137 | 0.044278
2217 | 2.1137 | 0.044297
2218 | 2.1136 | 0.044317
2219 | 2.1136 | 0.044336
2220 | 2.1136 | 0.044356
2221 | 2.1135 | 0.044375
2222 | 2.1135 | 0.044395
2223 | 2.1135 | 0.044414
2224 | 2.1134 | 0.044434
2225 | 2.1134 | 0.044453
2226 | 2.1134 | 0.044473
2227 | 2.1134 | 0.044492
2228 | 2.1133 | 0.044512
2229 | 2.1133 | 0.044531
2230 | 2.1133 | 0.044551
2231 | 2.1132 | 0.04457
2232 | 2.1132 | 0.04459
2233 | 2.1132 | 0.044609
2234 | 2.1131 | 0.044629
2235 | 2.1131 | 0.044648
2236 | 2.1131 | 0.044668
2237 | 2.113 | 0.044687
2238 | 2.113 | 0.044707
2239 | 2.113 | 0.044726
2240 | 2.1129 | 0.044746
2241 | 2.1129 | 0.044765
2242 | 2.1129 | 0.044785
2243 | 2.1128 | 0.044804
2244 | 2.1128 | 0.044824
2245 | 2.1128 | 0.044843
2246 | 2.1127 | 0.044863
2247 | 2.1127 | 0.044882
2248 | 2.1127 | 0.044902
2249 | 2.1127 | 0.044921
2250 | 2.1126 | 0.044941
2251 | 2.1126 | 0.04496
2252 | 2.1126 | 0.04498
2253 | 2.1125 | 0.044999
2254 | 2.1125 | 0.045019
2255 | 2.1125 | 0.045038
2256 | 2.1124 | 0.045057
2257 | 2.1124 | 0.045077
2258 | 2.1124 | 0.045096
2259 | 2.1123 | 0.045116
2260 | 2.1123 | 0.045135
2261 | 2.1123 | 0.045155
2262 | 2.1122 | 0.045174
2263 | 2.1122 | 0.045194
2264 | 2.1122 | 0.045213
2265 | 2.1121 | 0.045233
2266 | 2.1121 | 0.045252
2267 | 2.1121 | 0.045272
2268 | 2.112 | 0.045291
2269 | 2.112 | 0.045311
2270 | 2.112 | 0.04533
2271 | 2.112 | 0.04535
2272 | 2.1119 | 0.045369
2273 | 2.1119 | 0.045389
2274 | 2.1119 | 0.045408
2275 | 2.1118 | 0.045428
2276 | 2.1118 | 0.045447
2277 | 2.1118 | 0.045467
2278 | 2.1117 | 0.045486
2279 | 2.1117 | 0.045505
2280 | 2.1117 | 0.045525
2281 | 2.1116 | 0.045544
2282 | 2.1116 | 0.045564
2283 | 2.1116 | 0.045583
2284 | 2.1115 | 0.045603
2285 | 2.1115 | 0.045622
2286 | 2.1115 | 0.045642
2287 | 2.1114 | 0.045661
2288 | 2.1114 | 0.045681
2289 | 2.1114 | 0.0457
2290 | 2.1114 | 0.04572
2291 | 2.1113 | 0.045739
2292 | 2.1113 | 0.045759
2293 | 2.1113 | 0.045778
2294 | 2.1112 | 0.045798
2295 | 2.1112 | 0.045817
2296 | 2.1112 | 0.045836
2297 | 2.1111 | 0.045856
2298 | 2.1111 | 0.045875
2299 | 2.1111 | 0.045895
2300 | 2.111 | 0.045914
2301 | 2.111 | 0.045934
2302 | 2.111 | 0.045953
2303 | 2.1109 | 0.045973
2304 | 2.1109 | 0.045992
2305 | 2.1109 | 0.046012
2306 | 2.1108 | 0.046031
2307 | 2.1108 | 0.046051
2308 | 2.1108 | 0.04607
2309 | 2.1108 | 0.046089
2310 | 2.1107 | 0.046109
2311 | 2.1107 | 0.046128
2312 | 2.1107 | 0.046148
2313 | 2.1106 | 0.046167
2314 | 2.1106 | 0.046187
2315 | 2.1106 | 0.046206
2316 | 2.1105 | 0.046226
2317 | 2.1105 | 0.046245
2318 | 2.1105 | 0.046265
2319 | 2.1104 | 0.046284
2320 | 2.1104 | 0.046303
2321 | 2.1104 | 0.046323
2322 | 2.1103 | 0.046342
2323 | 2.1103 | 0.046362
2324 | 2.1103 | 0.046381
2325 | 2.1102 | 0.046401
2326 | 2.1102 | 0.04642
2327 | 2.1102 | 0.04644
2328 | 2.1101 | 0.046459
2329 | 2.1101 | 0.046479
2330 | 2.1101 | 0.046498
2331 | 2.1101 | 0.046517
2332 | 2.11 | 0.046537
2333 | 2.11 | 0.046556
2334 | 2.11 | 0.046576
2335 | 2.1099 | 0.046595
2336 | 2.1099 | 0.046615
2337 | 2.1099 | 0.046634
2338 | 2.1098 | 0.046654
2339 | 2.1098 | 0.046673
2340 | 2.1098 | 0.046693
2341 | 2.1097 | 0.046712
2342 | 2.1097 | 0.046731
2343 | 2.1097 | 0.046751
2344 | 2.1096 | 0.04677
2345 | 2.1096 | 0.04679
2346 | 2.1096 | 0.046809
2347 | 2.1095 | 0.046829
2348 | 2.1095 | 0.046848
2349 | 2.1095 | 0.046868
2350 | 2.1095 | 0.046887
2351 | 2.1094 | 0.046906
2352 | 2.1094 | 0.046926
2353 | 2.1094 | 0.046945
2354 | 2.1093 | 0.046965
2355 | 2.1093 | 0.046984
2356 | 2.1093 | 0.047004
2357 | 2.1092 | 0.047023
2358 | 2.1092 | 0.047043
2359 | 2.1092 | 0.047062
2360 | 2.1091 | 0.047081
2361 | 2.1091 | 0.047101
2362 | 2.1091 | 0.04712
2363 | 2.109 | 0.04714
2364 | 2.109 | 0.047159
2365 | 2.109 | 0.047179
2366 | 2.1089 | 0.047198
2367 | 2.1089 | 0.047217
2368 | 2.1089 | 0.047237
2369 | 2.1089 | 0.047256
2370 | 2.1088 | 0.047276
2371 | 2.1088 | 0.047295
2372 | 2.1088 | 0.047315
2373 | 2.1087 | 0.047334
2374 | 2.1087 | 0.047354
2375 | 2.1087 | 0.047373
2376 | 2.1086 | 0.047392
2377 | 2.1086 | 0.047412
2378 | 2.1086 | 0.047431
2379 | 2.1085 | 0.047451
2380 | 2.1085 | 0.04747
2381 | 2.1085 | 0.04749
2382 | 2.1084 | 0.047509
2383 | 2.1084 | 0.047528
2384 | 2.1084 | 0.047548
2385 | 2.1084 | 0.047567
2386 | 2.1083 | 0.047587
2387 | 2.1083 | 0.047606
2388 | 2.1083 | 0.047626
2389 | 2.1082 | 0.047645
2390 | 2.1082 | 0.047664
2391 | 2.1082 | 0.047684
2392 | 2.1081 | 0.047703
2393 | 2.1081 | 0.047723
2394 | 2.1081 | 0.047742
2395 | 2.108 | 0.047762
2396 | 2.108 | 0.047781
2397 | 2.108 | 0.0478
2398 | 2.1079 | 0.04782
2399 | 2.1079 | 0.047839
2400 | 2.1079 | 0.047859
2401 | 2.1078 | 0.047878
2402 | 2.1078 | 0.047898
2403 | 2.1078 | 0.047917
2404 | 2.1078 | 0.047936
2405 | 2.1077 | 0.047956
2406 | 2.1077 | 0.047975
2407 | 2.1077 | 0.047995
2408 | 2.1076 | 0.048014
2409 | 2.1076 | 0.048033
2410 | 2.1076 | 0.048053
2411 | 2.1075 | 0.048072
2412 | 2.1075 | 0.048092
2413 | 2.1075 | 0.048111
2414 | 2.1074 | 0.048131
2415 | 2.1074 | 0.04815
2416 | 2.1074 | 0.048169
2417 | 2.1073 | 0.048189
2418 | 2.1073 | 0.048208
2419 | 2.1073 | 0.048228
2420 | 2.1072 | 0.048247
2421 | 2.1072 | 0.048266
2422 | 2.1072 | 0.048286
2423 | 2.1072 | 0.048305
2424 | 2.1071 | 0.048325
2425 | 2.1071 | 0.048344
2426 | 2.1071 | 0.048364
2427 | 2.107 | 0.048383
2428 | 2.107 | 0.048402
2429 | 2.107 | 0.048422
2430 | 2.1069 | 0.048441
2431 | 2.1069 | 0.048461
2432 | 2.1069 | 0.04848
2433 | 2.1068 | 0.048499
2434 | 2.1068 | 0.048519
2435 | 2.1068 | 0.048538
2436 | 2.1067 | 0.048558
2437 | 2.1067 | 0.048577
2438 | 2.1067 | 0.048596
2439 | 2.1067 | 0.048616
2440 | 2.1066 | 0.048635
2441 | 2.1066 | 0.048655
2442 | 2.1066 | 0.048674
2443 | 2.1065 | 0.048693
2444 | 2.1065 | 0.048713
2445 | 2.1065 | 0.048732
2446 | 2.1064 | 0.048752
2447 | 2.1064 | 0.048771
2448 | 2.1064 | 0.048791
2449 | 2.1063 | 0.04881
2450 | 2.1063 | 0.048829
2451 | 2.1063 | 0.048849
2452 | 2.1062 | 0.048868
2453 | 2.1062 | 0.048888
2454 | 2.1062 | 0.048907
2455 | 2.1061 | 0.048926
2456 | 2.1061 | 0.048946
2457 | 2.1061 | 0.048965
2458 | 2.1061 | 0.048985
2459 | 2.106 | 0.049004
2460 | 2.106 | 0.049023
2461 | 2.106 | 0.049043
2462 | 2.1059 | 0.049062
2463 | 2.1059 | 0.049082
2464 | 2.1059 | 0.049101
2465 | 2.1058 | 0.04912
2466 | 2.1058 | 0.04914
2467 | 2.1058 | 0.049159
2468 | 2.1057 | 0.049178
2469 | 2.1057 | 0.049198
2470 | 2.1057 | 0.049217
2471 | 2.1056 | 0.049237
2472 | 2.1056 | 0.049256
2473 | 2.1056 | 0.049275
2474 | 2.1056 | 0.049295
2475 | 2.1055 | 0.049314
2476 | 2.1055 | 0.049334
2477 | 2.1055 | 0.049353
2478 | 2.1054 | 0.049372
2479 | 2.1054 | 0.049392
2480 | 2.1054 | 0.049411
2481 | 2.1053 | 0.049431
2482 | 2.1053 | 0.04945
2483 | 2.1053 | 0.049469
2484 | 2.1052 | 0.049489
2485 | 2.1052 | 0.049508
2486 | 2.1052 | 0.049528
2487 | 2.1051 | 0.049547
2488 | 2.1051 | 0.049566
2489 | 2.1051 | 0.049586
2490 | 2.1051 | 0.049605
2491 | 2.105 | 0.049624
2492 | 2.105 | 0.049644
2493 | 2.105 | 0.049663
2494 | 2.1049 | 0.049683
2495 | 2.1049 | 0.049702
2496 | 2.1049 | 0.049721
2497 | 2.1048 | 0.049741
2498 | 2.1048 | 0.04976
2499 | 2.1048 | 0.04978
2500 | 2.1047 | 0.049799
2501 | 2.1047 | 0.049818
2502 | 2.1047 | 0.049838
2503 | 2.1046 | 0.049857
2504 | 2.1046 | 0.049876
2505 | 2.1046 | 0.049896
2506 | 2.1045 | 0.049915
2507 | 2.1045 | 0.049935
2508 | 2.1045 | 0.049954
2509 | 2.1045 | 0.049973
2510 | 2.1044 | 0.049993
2511 | 2.1044 | 0.050012
2512 | 2.1044 | 0.050031
2513 | 2.1043 | 0.050051
2514 | 2.1043 | 0.05007
2515 | 2.1043 | 0.05009
2516 | 2.1042 | 0.050109
2517 | 2.1042 | 0.050128
2518 | 2.1042 | 0.050148
2519 | 2.1041 | 0.050167
2520 | 2.1041 | 0.050187
2521 | 2.1041 | 0.050206
2522 | 2.104 | 0.050225
2523 | 2.104 | 0.050245
2524 | 2.104 | 0.050264
2525 | 2.104 | 0.050283
2526 | 2.1039 | 0.050303
2527 | 2.1039 | 0.050322
2528 | 2.1039 | 0.050341
2529 | 2.1038 | 0.050361
2530 | 2.1038 | 0.05038
2531 | 2.1038 | 0.0504
2532 | 2.1037 | 0.050419
2533 | 2.1037 | 0.050438
2534 | 2.1037 | 0.050458
2535 | 2.1036 | 0.050477
2536 | 2.1036 | 0.050496
2537 | 2.1036 | 0.050516
2538 | 2.1035 | 0.050535
2539 | 2.1035 | 0.050555
2540 | 2.1035 | 0.050574
2541 | 2.1035 | 0.050593
2542 | 2.1034 | 0.050613
2543 | 2.1034 | 0.050632
2544 | 2.1034 | 0.050651
2545 | 2.1033 | 0.050671
2546 | 2.1033 | 0.05069
2547 | 2.1033 | 0.050709
2548 | 2.1032 | 0.050729
2549 | 2.1032 | 0.050748
2550 | 2.1032 | 0.050768
2551 | 2.1031 | 0.050787
2552 | 2.1031 | 0.050806
2553 | 2.1031 | 0.050826
2554 | 2.103 | 0.050845
2555 | 2.103 | 0.050864
2556 | 2.103 | 0.050884
2557 | 2.103 | 0.050903
2558 | 2.1029 | 0.050922
2559 | 2.1029 | 0.050942
2560 | 2.1029 | 0.050961
2561 | 2.1028 | 0.050981
2562 | 2.1028 | 0.051
2563 | 2.1028 | 0.051019
2564 | 2.1027 | 0.051039
2565 | 2.1027 | 0.051058
2566 | 2.1027 | 0.051077
2567 | 2.1026 | 0.051097
2568 | 2.1026 | 0.051116
2569 | 2.1026 | 0.051135
2570 | 2.1025 | 0.051155
2571 | 2.1025 | 0.051174
2572 | 2.1025 | 0.051193
2573 | 2.1025 | 0.051213
2574 | 2.1024 | 0.051232
2575 | 2.1024 | 0.051251
2576 | 2.1024 | 0.051271
2577 | 2.1023 | 0.05129
2578 | 2.1023 | 0.05131
2579 | 2.1023 | 0.051329
2580 | 2.1022 | 0.051348
2581 | 2.1022 | 0.051368
2582 | 2.1022 | 0.051387
2583 | 2.1021 | 0.051406
2584 | 2.1021 | 0.051426
2585 | 2.1021 | 0.051445
2586 | 2.102 | 0.051464
2587 | 2.102 | 0.051484
2588 | 2.102 | 0.051503
2589 | 2.102 | 0.051522
2590 | 2.1019 | 0.051542
2591 | 2.1019 | 0.051561
2592 | 2.1019 | 0.05158
2593 | 2.1018 | 0.0516
2594 | 2.1018 | 0.051619
2595 | 2.1018 | 0.051638
2596 | 2.1017 | 0.051658
2597 | 2.1017 | 0.051677
2598 | 2.1017 | 0.051696
2599 | 2.1016 | 0.051716
2600 | 2.1016 | 0.051735
2601 | 2.1016 | 0.051754
2602 | 2.1015 | 0.051774
2603 | 2.1015 | 0.051793
2604 | 2.1015 | 0.051813
2605 | 2.1015 | 0.051832
2606 | 2.1014 | 0.051851
2607 | 2.1014 | 0.051871
2608 | 2.1014 | 0.05189
2609 | 2.1013 | 0.051909
2610 | 2.1013 | 0.051929
2611 | 2.1013 | 0.051948
2612 | 2.1012 | 0.051967
2613 | 2.1012 | 0.051987
2614 | 2.1012 | 0.052006
2615 | 2.1011 | 0.052025
2616 | 2.1011 | 0.052045
2617 | 2.1011 | 0.052064
2618 | 2.101 | 0.052083
2619 | 2.101 | 0.052103
2620 | 2.101 | 0.052122
2621 | 2.101 | 0.052141
2622 | 2.1009 | 0.052161
2623 | 2.1009 | 0.05218
2624 | 2.1009 | 0.052199
2625 | 2.1008 | 0.052219
2626 | 2.1008 | 0.052238
2627 | 2.1008 | 0.052257
2628 | 2.1007 | 0.052277
2629 | 2.1007 | 0.052296
2630 | 2.1007 | 0.052315
2631 | 2.1006 | 0.052335
2632 | 2.1006 | 0.052354
2633 | 2.1006 | 0.052373
2634 | 2.1006 | 0.052393
2635 | 2.1005 | 0.052412
2636 | 2.1005 | 0.052431
2637 | 2.1005 | 0.052451
2638 | 2.1004 | 0.05247
2639 | 2.1004 | 0.052489
2640 | 2.1004 | 0.052509
2641 | 2.1003 | 0.052528
2642 | 2.1003 | 0.052547
2643 | 2.1003 | 0.052566
2644 | 2.1002 | 0.052586
2645 | 2.1002 | 0.052605
2646 | 2.1002 | 0.052624
2647 | 2.1001 | 0.052644
2648 | 2.1001 | 0.052663
2649 | 2.1001 | 0.052682
2650 | 2.1001 | 0.052702
2651 | 2.1 | 0.052721
2652 | 2.1 | 0.05274
2653 | 2.1 | 0.05276
2654 | 2.0999 | 0.052779
2655 | 2.0999 | 0.052798
2656 | 2.0999 | 0.052818
2657 | 2.0998 | 0.052837
2658 | 2.0998 | 0.052856
2659 | 2.0998 | 0.052876
2660 | 2.0997 | 0.052895
2661 | 2.0997 | 0.052914
2662 | 2.0997 | 0.052934
2663 | 2.0996 | 0.052953
2664 | 2.0996 | 0.052972
2665 | 2.0996 | 0.052992
2666 | 2.0996 | 0.053011
2667 | 2.0995 | 0.05303
2668 | 2.0995 | 0.053049
2669 | 2.0995 | 0.053069
2670 | 2.0994 | 0.053088
2671 | 2.0994 | 0.053107
2672 | 2.0994 | 0.053127
2673 | 2.0993 | 0.053146
2674 | 2.0993 | 0.053165
2675 | 2.0993 | 0.053185
2676 | 2.0992 | 0.053204
2677 | 2.0992 | 0.053223
2678 | 2.0992 | 0.053243
2679 | 2.0992 | 0.053262
2680 | 2.0991 | 0.053281
2681 | 2.0991 | 0.053301
2682 | 2.0991 | 0.05332
2683 | 2.099 | 0.053339
2684 | 2.099 | 0.053358
2685 | 2.099 | 0.053378
2686 | 2.0989 | 0.053397
2687 | 2.0989 | 0.053416
2688 | 2.0989 | 0.053436
2689 | 2.0988 | 0.053455
2690 | 2.0988 | 0.053474
2691 | 2.0988 | 0.053494
2692 | 2.0987 | 0.053513
2693 | 2.0987 | 0.053532
2694 | 2.0987 | 0.053552
2695 | 2.0987 | 0.053571
2696 | 2.0986 | 0.05359
2697 | 2.0986 | 0.053609
2698 | 2.0986 | 0.053629
2699 | 2.0985 | 0.053648
2700 | 2.0985 | 0.053667
2701 | 2.0985 | 0.053687
2702 | 2.0984 | 0.053706
2703 | 2.0984 | 0.053725
2704 | 2.0984 | 0.053745
2705 | 2.0983 | 0.053764
2706 | 2.0983 | 0.053783
2707 | 2.0983 | 0.053802
2708 | 2.0983 | 0.053822
2709 | 2.0982 | 0.053841
2710 | 2.0982 | 0.05386
2711 | 2.0982 | 0.05388
2712 | 2.0981 | 0.053899
2713 | 2.0981 | 0.053918
2714 | 2.0981 | 0.053938
2715 | 2.098 | 0.053957
2716 | 2.098 | 0.053976
2717 | 2.098 | 0.053995
2718 | 2.0979 | 0.054015
2719 | 2.0979 | 0.054034
2720 | 2.0979 | 0.054053
2721 | 2.0978 | 0.054073
2722 | 2.0978 | 0.054092
2723 | 2.0978 | 0.054111
2724 | 2.0978 | 0.05413
2725 | 2.0977 | 0.05415
2726 | 2.0977 | 0.054169
2727 | 2.0977 | 0.054188
2728 | 2.0976 | 0.054208
2729 | 2.0976 | 0.054227
2730 | 2.0976 | 0.054246
2731 | 2.0975 | 0.054265
2732 | 2.0975 | 0.054285
2733 | 2.0975 | 0.054304
2734 | 2.0974 | 0.054323
2735 | 2.0974 | 0.054343
2736 | 2.0974 | 0.054362
2737 | 2.0974 | 0.054381
2738 | 2.0973 | 0.054401
2739 | 2.0973 | 0.05442
2740 | 2.0973 | 0.054439
2741 | 2.0972 | 0.054458
2742 | 2.0972 | 0.054478
2743 | 2.0972 | 0.054497
2744 | 2.0971 | 0.054516
2745 | 2.0971 | 0.054536
2746 | 2.0971 | 0.054555
2747 | 2.097 | 0.054574
2748 | 2.097 | 0.054593
2749 | 2.097 | 0.054613
2750 | 2.097 | 0.054632
2751 | 2.0969 | 0.054651
2752 | 2.0969 | 0.05467
2753 | 2.0969 | 0.05469
2754 | 2.0968 | 0.054709
2755 | 2.0968 | 0.054728
2756 | 2.0968 | 0.054748
2757 | 2.0967 | 0.054767
2758 | 2.0967 | 0.054786
2759 | 2.0967 | 0.054805
2760 | 2.0966 | 0.054825
2761 | 2.0966 | 0.054844
2762 | 2.0966 | 0.054863
2763 | 2.0965 | 0.054883
2764 | 2.0965 | 0.054902
2765 | 2.0965 | 0.054921
2766 | 2.0965 | 0.05494
2767 | 2.0964 | 0.05496
2768 | 2.0964 | 0.054979
2769 | 2.0964 | 0.054998
2770 | 2.0963 | 0.055017
2771 | 2.0963 | 0.055037
2772 | 2.0963 | 0.055056
2773 | 2.0962 | 0.055075
2774 | 2.0962 | 0.055095
2775 | 2.0962 | 0.055114
2776 | 2.0961 | 0.055133
2777 | 2.0961 | 0.055152
2778 | 2.0961 | 0.055172
2779 | 2.0961 | 0.055191
2780 | 2.096 | 0.05521
2781 | 2.096 | 0.055229
2782 | 2.096 | 0.055249
2783 | 2.0959 | 0.055268
2784 | 2.0959 | 0.055287
2785 | 2.0959 | 0.055307
2786 | 2.0958 | 0.055326
2787 | 2.0958 | 0.055345
2788 | 2.0958 | 0.055364
2789 | 2.0957 | 0.055384
2790 | 2.0957 | 0.055403
2791 | 2.0957 | 0.055422
2792 | 2.0957 | 0.055441
2793 | 2.0956 | 0.055461
2794 | 2.0956 | 0.05548
2795 | 2.0956 | 0.055499
2796 | 2.0955 | 0.055518
2797 | 2.0955 | 0.055538
2798 | 2.0955 | 0.055557
2799 | 2.0954 | 0.055576
2800 | 2.0954 | 0.055596
2801 | 2.0954 | 0.055615
2802 | 2.0953 | 0.055634
2803 | 2.0953 | 0.055653
2804 | 2.0953 | 0.055673
2805 | 2.0953 | 0.055692
2806 | 2.0952 | 0.055711
2807 | 2.0952 | 0.05573
2808 | 2.0952 | 0.05575
2809 | 2.0951 | 0.055769
2810 | 2.0951 | 0.055788
2811 | 2.0951 | 0.055807
2812 | 2.095 | 0.055827
2813 | 2.095 | 0.055846
2814 | 2.095 | 0.055865
2815 | 2.0949 | 0.055884
2816 | 2.0949 | 0.055904
2817 | 2.0949 | 0.055923
2818 | 2.0949 | 0.055942
2819 | 2.0948 | 0.055961
2820 | 2.0948 | 0.055981
2821 | 2.0948 | 0.056
2822 | 2.0947 | 0.056019
2823 | 2.0947 | 0.056038
2824 | 2.0947 | 0.056058
2825 | 2.0946 | 0.056077
2826 | 2.0946 | 0.056096
2827 | 2.0946 | 0.056115
2828 | 2.0945 | 0.056135
2829 | 2.0945 | 0.056154
2830 | 2.0945 | 0.056173
2831 | 2.0944 | 0.056192
2832 | 2.0944 | 0.056212
2833 | 2.0944 | 0.056231
2834 | 2.0944 | 0.05625
2835 | 2.0943 | 0.056269
2836 | 2.0943 | 0.056289
2837 | 2.0943 | 0.056308
2838 | 2.0942 | 0.056327
2839 | 2.0942 | 0.056346
2840 | 2.0942 | 0.056366
2841 | 2.0941 | 0.056385
2842 | 2.0941 | 0.056404
2843 | 2.0941 | 0.056423
2844 | 2.094 | 0.056443
2845 | 2.094 | 0.056462
2846 | 2.094 | 0.056481
2847 | 2.094 | 0.0565
2848 | 2.0939 | 0.05652
2849 | 2.0939 | 0.056539
2850 | 2.0939 | 0.056558
2851 | 2.0938 | 0.056577
2852 | 2.0938 | 0.056597
2853 | 2.0938 | 0.056616
2854 | 2.0937 | 0.056635
2855 | 2.0937 | 0.056654
2856 | 2.0937 | 0.056674
2857 | 2.0936 | 0.056693
2858 | 2.0936 | 0.056712
2859 | 2.0936 | 0.056731
2860 | 2.0936 | 0.056751
2861 | 2.0935 | 0.05677
2862 | 2.0935 | 0.056789
2863 | 2.0935 | 0.056808
2864 | 2.0934 | 0.056827
2865 | 2.0934 | 0.056847
2866 | 2.0934 | 0.056866
2867 | 2.0933 | 0.056885
2868 | 2.0933 | 0.056904
2869 | 2.0933 | 0.056924
2870 | 2.0932 | 0.056943
2871 | 2.0932 | 0.056962
2872 | 2.0932 | 0.056981
2873 | 2.0932 | 0.057001
2874 | 2.0931 | 0.05702
2875 | 2.0931 | 0.057039
2876 | 2.0931 | 0.057058
2877 | 2.093 | 0.057078
2878 | 2.093 | 0.057097
2879 | 2.093 | 0.057116
2880 | 2.0929 | 0.057135
2881 | 2.0929 | 0.057154
2882 | 2.0929 | 0.057174
2883 | 2.0928 | 0.057193
2884 | 2.0928 | 0.057212
2885 | 2.0928 | 0.057231
2886 | 2.0928 | 0.057251
2887 | 2.0927 | 0.05727
2888 | 2.0927 | 0.057289
2889 | 2.0927 | 0.057308
2890 | 2.0926 | 0.057327
2891 | 2.0926 | 0.057347
2892 | 2.0926 | 0.057366
2893 | 2.0925 | 0.057385
2894 | 2.0925 | 0.057404
2895 | 2.0925 | 0.057424
2896 | 2.0924 | 0.057443
2897 | 2.0924 | 0.057462
2898 | 2.0924 | 0.057481
2899 | 2.0924 | 0.057501
2900 | 2.0923 | 0.05752
2901 | 2.0923 | 0.057539
2902 | 2.0923 | 0.057558
2903 | 2.0922 | 0.057577
2904 | 2.0922 | 0.057597
2905 | 2.0922 | 0.057616
2906 | 2.0921 | 0.057635
2907 | 2.0921 | 0.057654
2908 | 2.0921 | 0.057673
2909 | 2.092 | 0.057693
2910 | 2.092 | 0.057712
2911 | 2.092 | 0.057731
2912 | 2.092 | 0.05775
2913 | 2.0919 | 0.05777
2914 | 2.0919 | 0.057789
2915 | 2.0919 | 0.057808
2916 | 2.0918 | 0.057827
2917 | 2.0918 | 0.057846
2918 | 2.0918 | 0.057866
2919 | 2.0917 | 0.057885
2920 | 2.0917 | 0.057904
2921 | 2.0917 | 0.057923
2922 | 2.0917 | 0.057943
2923 | 2.0916 | 0.057962
2924 | 2.0916 | 0.057981
2925 | 2.0916 | 0.058
2926 | 2.0915 | 0.058019
2927 | 2.0915 | 0.058039
2928 | 2.0915 | 0.058058
2929 | 2.0914 | 0.058077
2930 | 2.0914 | 0.058096
2931 | 2.0914 | 0.058115
2932 | 2.0913 | 0.058135
2933 | 2.0913 | 0.058154
2934 | 2.0913 | 0.058173
2935 | 2.0913 | 0.058192
2936 | 2.0912 | 0.058211
2937 | 2.0912 | 0.058231
2938 | 2.0912 | 0.05825
2939 | 2.0911 | 0.058269
2940 | 2.0911 | 0.058288
2941 | 2.0911 | 0.058308
2942 | 2.091 | 0.058327
2943 | 2.091 | 0.058346
2944 | 2.091 | 0.058365
2945 | 2.0909 | 0.058384
2946 | 2.0909 | 0.058404
2947 | 2.0909 | 0.058423
2948 | 2.0909 | 0.058442
2949 | 2.0908 | 0.058461
2950 | 2.0908 | 0.05848
2951 | 2.0908 | 0.0585
2952 | 2.0907 | 0.058519
2953 | 2.0907 | 0.058538
2954 | 2.0907 | 0.058557
2955 | 2.0906 | 0.058576
2956 | 2.0906 | 0.058596
2957 | 2.0906 | 0.058615
2958 | 2.0905 | 0.058634
2959 | 2.0905 | 0.058653
2960 | 2.0905 | 0.058672
2961 | 2.0905 | 0.058692
2962 | 2.0904 | 0.058711
2963 | 2.0904 | 0.05873
2964 | 2.0904 | 0.058749
2965 | 2.0903 | 0.058768
2966 | 2.0903 | 0.058788
2967 | 2.0903 | 0.058807
2968 | 2.0902 | 0.058826
2969 | 2.0902 | 0.058845
2970 | 2.0902 | 0.058864
2971 | 2.0901 | 0.058884
2972 | 2.0901 | 0.058903
2973 | 2.0901 | 0.058922
2974 | 2.0901 | 0.058941
2975 | 2.09 | 0.05896
2976 | 2.09 | 0.058979
2977 | 2.09 | 0.058999
2978 | 2.0899 | 0.059018
2979 | 2.0899 | 0.059037
2980 | 2.0899 | 0.059056
2981 | 2.0898 | 0.059075
2982 | 2.0898 | 0.059095
2983 | 2.0898 | 0.059114
2984 | 2.0898 | 0.059133
2985 | 2.0897 | 0.059152
2986 | 2.0897 | 0.059171
2987 | 2.0897 | 0.059191
2988 | 2.0896 | 0.05921
2989 | 2.0896 | 0.059229
2990 | 2.0896 | 0.059248
2991 | 2.0895 | 0.059267
2992 | 2.0895 | 0.059287
2993 | 2.0895 | 0.059306
2994 | 2.0894 | 0.059325
2995 | 2.0894 | 0.059344
2996 | 2.0894 | 0.059363
2997 | 2.0894 | 0.059382
2998 | 2.0893 | 0.059402
2999 | 2.0893 | 0.059421
3000 | 2.0893 | 0.05944
3001 | 2.0892 | 0.059459
3002 | 2.0892 | 0.059478
3003 | 2.0892 | 0.059498
3004 | 2.0891 | 0.059517
3005 | 2.0891 | 0.059536
3006 | 2.0891 | 0.059555
3007 | 2.089 | 0.059574
3008 | 2.089 | 0.059593
3009 | 2.089 | 0.059613
3010 | 2.089 | 0.059632
3011 | 2.0889 | 0.059651
3012 | 2.0889 | 0.05967
3013 | 2.0889 | 0.059689
3014 | 2.0888 | 0.059709
3015 | 2.0888 | 0.059728
3016 | 2.0888 | 0.059747
3017 | 2.0887 | 0.059766
3018 | 2.0887 | 0.059785
3019 | 2.0887 | 0.059804
3020 | 2.0887 | 0.059824
3021 | 2.0886 | 0.059843
3022 | 2.0886 | 0.059862
3023 | 2.0886 | 0.059881
3024 | 2.0885 | 0.0599
3025 | 2.0885 | 0.059919
3026 | 2.0885 | 0.059939
3027 | 2.0884 | 0.059958
3028 | 2.0884 | 0.059977
3029 | 2.0884 | 0.059996
3030 | 2.0883 | 0.060015
3031 | 2.0883 | 0.060034
3032 | 2.0883 | 0.060054
3033 | 2.0883 | 0.060073
3034 | 2.0882 | 0.060092
3035 | 2.0882 | 0.060111
3036 | 2.0882 | 0.06013
3037 | 2.0881 | 0.060149
3038 | 2.0881 | 0.060169
3039 | 2.0881 | 0.060188
3040 | 2.088 | 0.060207
3041 | 2.088 | 0.060226
3042 | 2.088 | 0.060245
3043 | 2.0879 | 0.060264
3044 | 2.0879 | 0.060284
3045 | 2.0879 | 0.060303
3046 | 2.0879 | 0.060322
3047 | 2.0878 | 0.060341
3048 | 2.0878 | 0.06036
3049 | 2.0878 | 0.060379
3050 | 2.0877 | 0.060399
3051 | 2.0877 | 0.060418
3052 | 2.0877 | 0.060437
3053 | 2.0876 | 0.060456
3054 | 2.0876 | 0.060475
3055 | 2.0876 | 0.060494
3056 | 2.0876 | 0.060514
3057 | 2.0875 | 0.060533
3058 | 2.0875 | 0.060552
3059 | 2.0875 | 0.060571
3060 | 2.0874 | 0.06059
3061 | 2.0874 | 0.060609
3062 | 2.0874 | 0.060629
3063 | 2.0873 | 0.060648
3064 | 2.0873 | 0.060667
3065 | 2.0873 | 0.060686
3066 | 2.0872 | 0.060705
3067 | 2.0872 | 0.060724
3068 | 2.0872 | 0.060744
3069 | 2.0872 | 0.060763
3070 | 2.0871 | 0.060782
3071 | 2.0871 | 0.060801
3072 | 2.0871 | 0.06082
3073 | 2.087 | 0.060839
3074 | 2.087 | 0.060858
3075 | 2.087 | 0.060878
3076 | 2.0869 | 0.060897
3077 | 2.0869 | 0.060916
3078 | 2.0869 | 0.060935
3079 | 2.0869 | 0.060954
3080 | 2.0868 | 0.060973
3081 | 2.0868 | 0.060993
3082 | 2.0868 | 0.061012
3083 | 2.0867 | 0.061031
3084 | 2.0867 | 0.06105
3085 | 2.0867 | 0.061069
3086 | 2.0866 | 0.061088
3087 | 2.0866 | 0.061107
3088 | 2.0866 | 0.061127
3089 | 2.0865 | 0.061146
3090 | 2.0865 | 0.061165
3091 | 2.0865 | 0.061184
3092 | 2.0865 | 0.061203
3093 | 2.0864 | 0.061222
3094 | 2.0864 | 0.061241
3095 | 2.0864 | 0.061261
3096 | 2.0863 | 0.06128
3097 | 2.0863 | 0.061299
3098 | 2.0863 | 0.061318
3099 | 2.0862 | 0.061337
3100 | 2.0862 | 0.061356
3101 | 2.0862 | 0.061375
3102 | 2.0862 | 0.061395
3103 | 2.0861 | 0.061414
3104 | 2.0861 | 0.061433
3105 | 2.0861 | 0.061452
3106 | 2.086 | 0.061471
3107 | 2.086 | 0.06149
3108 | 2.086 | 0.061509
3109 | 2.0859 | 0.061529
3110 | 2.0859 | 0.061548
3111 | 2.0859 | 0.061567
3112 | 2.0858 | 0.061586
3113 | 2.0858 | 0.061605
3114 | 2.0858 | 0.061624
3115 | 2.0858 | 0.061643
3116 | 2.0857 | 0.061663
3117 | 2.0857 | 0.061682
3118 | 2.0857 | 0.061701
3119 | 2.0856 | 0.06172
3120 | 2.0856 | 0.061739
3121 | 2.0856 | 0.061758
3122 | 2.0855 | 0.061777
3123 | 2.0855 | 0.061797
3124 | 2.0855 | 0.061816
3125 | 2.0855 | 0.061835
3126 | 2.0854 | 0.061854
3127 | 2.0854 | 0.061873
3128 | 2.0854 | 0.061892
3129 | 2.0853 | 0.061911
3130 | 2.0853 | 0.06193
3131 | 2.0853 | 0.06195
3132 | 2.0852 | 0.061969
3133 | 2.0852 | 0.061988
3134 | 2.0852 | 0.062007
3135 | 2.0851 | 0.062026
3136 | 2.0851 | 0.062045
3137 | 2.0851 | 0.062064
3138 | 2.0851 | 0.062084
3139 | 2.085 | 0.062103
3140 | 2.085 | 0.062122
3141 | 2.085 | 0.062141
3142 | 2.0849 | 0.06216
3143 | 2.0849 | 0.062179
3144 | 2.0849 | 0.062198
3145 | 2.0848 | 0.062217
3146 | 2.0848 | 0.062237
3147 | 2.0848 | 0.062256
3148 | 2.0848 | 0.062275
3149 | 2.0847 | 0.062294
3150 | 2.0847 | 0.062313
3151 | 2.0847 | 0.062332
3152 | 2.0846 | 0.062351
3153 | 2.0846 | 0.06237
3154 | 2.0846 | 0.06239
3155 | 2.0845 | 0.062409
3156 | 2.0845 | 0.062428
3157 | 2.0845 | 0.062447
3158 | 2.0845 | 0.062466
3159 | 2.0844 | 0.062485
3160 | 2.0844 | 0.062504
3161 | 2.0844 | 0.062523
3162 | 2.0843 | 0.062543
3163 | 2.0843 | 0.062562
3164 | 2.0843 | 0.062581
3165 | 2.0842 | 0.0626
3166 | 2.0842 | 0.062619
3167 | 2.0842 | 0.062638
3168 | 2.0841 | 0.062657
3169 | 2.0841 | 0.062676
3170 | 2.0841 | 0.062695
3171 | 2.0841 | 0.062715
3172 | 2.084 | 0.062734
3173 | 2.084 | 0.062753
3174 | 2.084 | 0.062772
3175 | 2.0839 | 0.062791
3176 | 2.0839 | 0.06281
3177 | 2.0839 | 0.062829
3178 | 2.0838 | 0.062848
3179 | 2.0838 | 0.062867
3180 | 2.0838 | 0.062887
3181 | 2.0838 | 0.062906
3182 | 2.0837 | 0.062925
3183 | 2.0837 | 0.062944
3184 | 2.0837 | 0.062963
3185 | 2.0836 | 0.062982
3186 | 2.0836 | 0.063001
3187 | 2.0836 | 0.06302
3188 | 2.0835 | 0.063039
3189 | 2.0835 | 0.063059
3190 | 2.0835 | 0.063078
3191 | 2.0835 | 0.063097
3192 | 2.0834 | 0.063116
3193 | 2.0834 | 0.063135
3194 | 2.0834 | 0.063154
3195 | 2.0833 | 0.063173
3196 | 2.0833 | 0.063192
3197 | 2.0833 | 0.063211
3198 | 2.0832 | 0.063231
3199 | 2.0832 | 0.06325
3200 | 2.0832 | 0.063269
3201 | 2.0831 | 0.063288
3202 | 2.0831 | 0.063307
3203 | 2.0831 | 0.063326
3204 | 2.0831 | 0.063345
3205 | 2.083 | 0.063364
3206 | 2.083 | 0.063383
3207 | 2.083 | 0.063403
3208 | 2.0829 | 0.063422
3209 | 2.0829 | 0.063441
3210 | 2.0829 | 0.06346
3211 | 2.0828 | 0.063479
3212 | 2.0828 | 0.063498
3213 | 2.0828 | 0.063517
3214 | 2.0828 | 0.063536
3215 | 2.0827 | 0.063555
3216 | 2.0827 | 0.063574
3217 | 2.0827 | 0.063594
3218 | 2.0826 | 0.063613
3219 | 2.0826 | 0.063632
3220 | 2.0826 | 0.063651
3221 | 2.0825 | 0.06367
3222 | 2.0825 | 0.063689
3223 | 2.0825 | 0.063708
3224 | 2.0825 | 0.063727
3225 | 2.0824 | 0.063746
3226 | 2.0824 | 0.063765
3227 | 2.0824 | 0.063784
3228 | 2.0823 | 0.063804
3229 | 2.0823 | 0.063823
3230 | 2.0823 | 0.063842
3231 | 2.0822 | 0.063861
3232 | 2.0822 | 0.06388
3233 | 2.0822 | 0.063899
3234 | 2.0822 | 0.063918
3235 | 2.0821 | 0.063937
3236 | 2.0821 | 0.063956
3237 | 2.0821 | 0.063975
3238 | 2.082 | 0.063994
3239 | 2.082 | 0.064014
3240 | 2.082 | 0.064033
3241 | 2.0819 | 0.064052
3242 | 2.0819 | 0.064071
3243 | 2.0819 | 0.06409
3244 | 2.0818 | 0.064109
3245 | 2.0818 | 0.064128
3246 | 2.0818 | 0.064147
3247 | 2.0818 | 0.064166
3248 | 2.0817 | 0.064185
3249 | 2.0817 | 0.064204
3250 | 2.0817 | 0.064224
3251 | 2.0816 | 0.064243
3252 | 2.0816 | 0.064262
3253 | 2.0816 | 0.064281
3254 | 2.0815 | 0.0643
3255 | 2.0815 | 0.064319
3256 | 2.0815 | 0.064338
3257 | 2.0815 | 0.064357
3258 | 2.0814 | 0.064376
3259 | 2.0814 | 0.064395
3260 | 2.0814 | 0.064414
3261 | 2.0813 | 0.064433
3262 | 2.0813 | 0.064453
3263 | 2.0813 | 0.064472
3264 | 2.0812 | 0.064491
3265 | 2.0812 | 0.06451
3266 | 2.0812 | 0.064529
3267 | 2.0812 | 0.064548
3268 | 2.0811 | 0.064567
3269 | 2.0811 | 0.064586
3270 | 2.0811 | 0.064605
3271 | 2.081 | 0.064624
3272 | 2.081 | 0.064643
3273 | 2.081 | 0.064662
3274 | 2.0809 | 0.064682
3275 | 2.0809 | 0.064701
3276 | 2.0809 | 0.06472
3277 | 2.0809 | 0.064739
3278 | 2.0808 | 0.064758
3279 | 2.0808 | 0.064777
3280 | 2.0808 | 0.064796
3281 | 2.0807 | 0.064815
3282 | 2.0807 | 0.064834
3283 | 2.0807 | 0.064853
3284 | 2.0806 | 0.064872
3285 | 2.0806 | 0.064891
3286 | 2.0806 | 0.06491
3287 | 2.0806 | 0.064929
3288 | 2.0805 | 0.064949
3289 | 2.0805 | 0.064968
3290 | 2.0805 | 0.064987
3291 | 2.0804 | 0.065006
3292 | 2.0804 | 0.065025
3293 | 2.0804 | 0.065044
3294 | 2.0803 | 0.065063
3295 | 2.0803 | 0.065082
3296 | 2.0803 | 0.065101
3297 | 2.0802 | 0.06512
3298 | 2.0802 | 0.065139
3299 | 2.0802 | 0.065158
3300 | 2.0802 | 0.065177
3301 | 2.0801 | 0.065196
3302 | 2.0801 | 0.065215
3303 | 2.0801 | 0.065235
3304 | 2.08 | 0.065254
3305 | 2.08 | 0.065273
3306 | 2.08 | 0.065292
3307 | 2.0799 | 0.065311
3308 | 2.0799 | 0.06533
3309 | 2.0799 | 0.065349
3310 | 2.0799 | 0.065368
3311 | 2.0798 | 0.065387
3312 | 2.0798 | 0.065406
3313 | 2.0798 | 0.065425
3314 | 2.0797 | 0.065444
3315 | 2.0797 | 0.065463
3316 | 2.0797 | 0.065482
3317 | 2.0796 | 0.065501
3318 | 2.0796 | 0.065521
3319 | 2.0796 | 0.06554
3320 | 2.0796 | 0.065559
3321 | 2.0795 | 0.065578
3322 | 2.0795 | 0.065597
3323 | 2.0795 | 0.065616
3324 | 2.0794 | 0.065635
3325 | 2.0794 | 0.065654
3326 | 2.0794 | 0.065673
3327 | 2.0793 | 0.065692
3328 | 2.0793 | 0.065711
3329 | 2.0793 | 0.06573
3330 | 2.0793 | 0.065749
3331 | 2.0792 | 0.065768
3332 | 2.0792 | 0.065787
3333 | 2.0792 | 0.065806
3334 | 2.0791 | 0.065825
3335 | 2.0791 | 0.065844
3336 | 2.0791 | 0.065864
3337 | 2.079 | 0.065883
3338 | 2.079 | 0.065902
3339 | 2.079 | 0.065921
3340 | 2.079 | 0.06594
3341 | 2.0789 | 0.065959
3342 | 2.0789 | 0.065978
3343 | 2.0789 | 0.065997
3344 | 2.0788 | 0.066016
3345 | 2.0788 | 0.066035
3346 | 2.0788 | 0.066054
3347 | 2.0787 | 0.066073
3348 | 2.0787 | 0.066092
3349 | 2.0787 | 0.066111
3350 | 2.0787 | 0.06613
3351 | 2.0786 | 0.066149
3352 | 2.0786 | 0.066168
3353 | 2.0786 | 0.066187
3354 | 2.0785 | 0.066206
3355 | 2.0785 | 0.066225
3356 | 2.0785 | 0.066244
3357 | 2.0784 | 0.066264
3358 | 2.0784 | 0.066283
3359 | 2.0784 | 0.066302
3360 | 2.0784 | 0.066321
3361 | 2.0783 | 0.06634
3362 | 2.0783 | 0.066359
3363 | 2.0783 | 0.066378
3364 | 2.0782 | 0.066397
3365 | 2.0782 | 0.066416
3366 | 2.0782 | 0.066435
3367 | 2.0781 | 0.066454
3368 | 2.0781 | 0.066473
3369 | 2.0781 | 0.066492
3370 | 2.0781 | 0.066511
3371 | 2.078 | 0.06653
3372 | 2.078 | 0.066549
3373 | 2.078 | 0.066568
3374 | 2.0779 | 0.066587
3375 | 2.0779 | 0.066606
3376 | 2.0779 | 0.066625
3377 | 2.0778 | 0.066644
3378 | 2.0778 | 0.066663
3379 | 2.0778 | 0.066682
3380 | 2.0778 | 0.066701
3381 | 2.0777 | 0.066721
3382 | 2.0777 | 0.06674
3383 | 2.0777 | 0.066759
3384 | 2.0776 | 0.066778
3385 | 2.0776 | 0.066797
3386 | 2.0776 | 0.066816
3387 | 2.0775 | 0.066835
3388 | 2.0775 | 0.066854
3389 | 2.0775 | 0.066873
3390 | 2.0775 | 0.066892
3391 | 2.0774 | 0.066911
3392 | 2.0774 | 0.06693
3393 | 2.0774 | 0.066949
3394 | 2.0773 | 0.066968
3395 | 2.0773 | 0.066987
3396 | 2.0773 | 0.067006
3397 | 2.0772 | 0.067025
3398 | 2.0772 | 0.067044
3399 | 2.0772 | 0.067063
3400 | 2.0772 | 0.067082
3401 | 2.0771 | 0.067101
3402 | 2.0771 | 0.06712
3403 | 2.0771 | 0.067139
3404 | 2.077 | 0.067158
3405 | 2.077 | 0.067177
3406 | 2.077 | 0.067196
3407 | 2.0769 | 0.067215
3408 | 2.0769 | 0.067234
3409 | 2.0769 | 0.067253
3410 | 2.0769 | 0.067272
3411 | 2.0768 | 0.067291
3412 | 2.0768 | 0.06731
3413 | 2.0768 | 0.067329
3414 | 2.0767 | 0.067348
3415 | 2.0767 | 0.067367
3416 | 2.0767 | 0.067387
3417 | 2.0766 | 0.067406
3418 | 2.0766 | 0.067425
3419 | 2.0766 | 0.067444
3420 | 2.0766 | 0.067463
3421 | 2.0765 | 0.067482
3422 | 2.0765 | 0.067501
3423 | 2.0765 | 0.06752
3424 | 2.0764 | 0.067539
3425 | 2.0764 | 0.067558
3426 | 2.0764 | 0.067577
3427 | 2.0763 | 0.067596
3428 | 2.0763 | 0.067615
3429 | 2.0763 | 0.067634
3430 | 2.0763 | 0.067653
3431 | 2.0762 | 0.067672
3432 | 2.0762 | 0.067691
3433 | 2.0762 | 0.06771
3434 | 2.0761 | 0.067729
3435 | 2.0761 | 0.067748
3436 | 2.0761 | 0.067767
3437 | 2.076 | 0.067786
3438 | 2.076 | 0.067805
3439 | 2.076 | 0.067824
3440 | 2.076 | 0.067843
3441 | 2.0759 | 0.067862
3442 | 2.0759 | 0.067881
3443 | 2.0759 | 0.0679
3444 | 2.0758 | 0.067919
3445 | 2.0758 | 0.067938
3446 | 2.0758 | 0.067957
3447 | 2.0757 | 0.067976
3448 | 2.0757 | 0.067995
3449 | 2.0757 | 0.068014
3450 | 2.0757 | 0.068033
3451 | 2.0756 | 0.068052
3452 | 2.0756 | 0.068071
3453 | 2.0756 | 0.06809
3454 | 2.0755 | 0.068109
3455 | 2.0755 | 0.068128
3456 | 2.0755 | 0.068147
3457 | 2.0754 | 0.068166
3458 | 2.0754 | 0.068185
3459 | 2.0754 | 0.068204
3460 | 2.0754 | 0.068223
3461 | 2.0753 | 0.068242
3462 | 2.0753 | 0.068261
3463 | 2.0753 | 0.06828
3464 | 2.0752 | 0.068299
3465 | 2.0752 | 0.068318
3466 | 2.0752 | 0.068337
3467 | 2.0752 | 0.068356
3468 | 2.0751 | 0.068375
3469 | 2.0751 | 0.068394
3470 | 2.0751 | 0.068413
3471 | 2.075 | 0.068432
3472 | 2.075 | 0.068451
3473 | 2.075 | 0.06847
3474 | 2.0749 | 0.068489
3475 | 2.0749 | 0.068508
3476 | 2.0749 | 0.068527
3477 | 2.0749 | 0.068546
3478 | 2.0748 | 0.068565
3479 | 2.0748 | 0.068584
3480 | 2.0748 | 0.068603
3481 | 2.0747 | 0.068622
3482 | 2.0747 | 0.068641
3483 | 2.0747 | 0.06866
3484 | 2.0746 | 0.068679
3485 | 2.0746 | 0.068698
3486 | 2.0746 | 0.068717
3487 | 2.0746 | 0.068736
3488 | 2.0745 | 0.068755
3489 | 2.0745 | 0.068774
3490 | 2.0745 | 0.068793
3491 | 2.0744 | 0.068812
3492 | 2.0744 | 0.068831
3493 | 2.0744 | 0.06885
3494 | 2.0743 | 0.068869
3495 | 2.0743 | 0.068888
3496 | 2.0743 | 0.068907
3497 | 2.0743 | 0.068926
3498 | 2.0742 | 0.068945
3499 | 2.0742 | 0.068964
3500 | 2.0742 | 0.068983
3501 | 2.0741 | 0.069002
3502 | 2.0741 | 0.069021
3503 | 2.0741 | 0.06904
3504 | 2.074 | 0.069059
3505 | 2.074 | 0.069078
3506 | 2.074 | 0.069097
3507 | 2.074 | 0.069116
3508 | 2.0739 | 0.069135
3509 | 2.0739 | 0.069154
3510 | 2.0739 | 0.069173
3511 | 2.0738 | 0.069192
3512 | 2.0738 | 0.069211
3513 | 2.0738 | 0.06923
3514 | 2.0737 | 0.069249
3515 | 2.0737 | 0.069268
3516 | 2.0737 | 0.069287
3517 | 2.0737 | 0.069306
3518 | 2.0736 | 0.069325
3519 | 2.0736 | 0.069344
3520 | 2.0736 | 0.069363
3521 | 2.0735 | 0.069382
3522 | 2.0735 | 0.069401
3523 | 2.0735 | 0.06942
3524 | 2.0734 | 0.069439
3525 | 2.0734 | 0.069458
3526 | 2.0734 | 0.069477
3527 | 2.0734 | 0.069496
3528 | 2.0733 | 0.069515
3529 | 2.0733 | 0.069534
3530 | 2.0733 | 0.069553
3531 | 2.0732 | 0.069572
3532 | 2.0732 | 0.069591
3533 | 2.0732 | 0.06961
3534 | 2.0732 | 0.069628
3535 | 2.0731 | 0.069647
3536 | 2.0731 | 0.069666
3537 | 2.0731 | 0.069685
3538 | 2.073 | 0.069704
3539 | 2.073 | 0.069723
3540 | 2.073 | 0.069742
3541 | 2.0729 | 0.069761
3542 | 2.0729 | 0.06978
3543 | 2.0729 | 0.069799
3544 | 2.0729 | 0.069818
3545 | 2.0728 | 0.069837
3546 | 2.0728 | 0.069856
3547 | 2.0728 | 0.069875
3548 | 2.0727 | 0.069894
3549 | 2.0727 | 0.069913
3550 | 2.0727 | 0.069932
3551 | 2.0726 | 0.069951
3552 | 2.0726 | 0.06997
3553 | 2.0726 | 0.069989
3554 | 2.0726 | 0.070008
3555 | 2.0725 | 0.070027
3556 | 2.0725 | 0.070046
3557 | 2.0725 | 0.070065
3558 | 2.0724 | 0.070084
3559 | 2.0724 | 0.070103
3560 | 2.0724 | 0.070122
3561 | 2.0723 | 0.070141
3562 | 2.0723 | 0.07016
3563 | 2.0723 | 0.070179
3564 | 2.0723 | 0.070198
3565 | 2.0722 | 0.070217
3566 | 2.0722 | 0.070236
3567 | 2.0722 | 0.070255
3568 | 2.0721 | 0.070273
3569 | 2.0721 | 0.070292
3570 | 2.0721 | 0.070311
3571 | 2.0721 | 0.07033
3572 | 2.072 | 0.070349
3573 | 2.072 | 0.070368
3574 | 2.072 | 0.070387
3575 | 2.0719 | 0.070406
3576 | 2.0719 | 0.070425
3577 | 2.0719 | 0.070444
3578 | 2.0718 | 0.070463
3579 | 2.0718 | 0.070482
3580 | 2.0718 | 0.070501
3581 | 2.0718 | 0.07052
3582 | 2.0717 | 0.070539
3583 | 2.0717 | 0.070558
3584 | 2.0717 | 0.070577
3585 | 2.0716 | 0.070596
3586 | 2.0716 | 0.070615
3587 | 2.0716 | 0.070634
3588 | 2.0715 | 0.070653
3589 | 2.0715 | 0.070672
3590 | 2.0715 | 0.070691
3591 | 2.0715 | 0.07071
3592 | 2.0714 | 0.070729
3593 | 2.0714 | 0.070747
3594 | 2.0714 | 0.070766
3595 | 2.0713 | 0.070785
3596 | 2.0713 | 0.070804
3597 | 2.0713 | 0.070823
3598 | 2.0712 | 0.070842
3599 | 2.0712 | 0.070861
3600 | 2.0712 | 0.07088
3601 | 2.0712 | 0.070899
3602 | 2.0711 | 0.070918
3603 | 2.0711 | 0.070937
3604 | 2.0711 | 0.070956
3605 | 2.071 | 0.070975
3606 | 2.071 | 0.070994
3607 | 2.071 | 0.071013
3608 | 2.071 | 0.071032
3609 | 2.0709 | 0.071051
3610 | 2.0709 | 0.07107
3611 | 2.0709 | 0.071089
3612 | 2.0708 | 0.071108
3613 | 2.0708 | 0.071127
3614 | 2.0708 | 0.071145
3615 | 2.0707 | 0.071164
3616 | 2.0707 | 0.071183
3617 | 2.0707 | 0.071202
3618 | 2.0707 | 0.071221
3619 | 2.0706 | 0.07124
3620 | 2.0706 | 0.071259
3621 | 2.0706 | 0.071278
3622 | 2.0705 | 0.071297
3623 | 2.0705 | 0.071316
3624 | 2.0705 | 0.071335
3625 | 2.0704 | 0.071354
3626 | 2.0704 | 0.071373
3627 | 2.0704 | 0.071392
3628 | 2.0704 | 0.071411
3629 | 2.0703 | 0.07143
3630 | 2.0703 | 0.071449
3631 | 2.0703 | 0.071468
3632 | 2.0702 | 0.071486
3633 | 2.0702 | 0.071505
3634 | 2.0702 | 0.071524
3635 | 2.0702 | 0.071543
3636 | 2.0701 | 0.071562
3637 | 2.0701 | 0.071581
3638 | 2.0701 | 0.0716
3639 | 2.07 | 0.071619
3640 | 2.07 | 0.071638
3641 | 2.07 | 0.071657
3642 | 2.0699 | 0.071676
3643 | 2.0699 | 0.071695
3644 | 2.0699 | 0.071714
3645 | 2.0699 | 0.071733
3646 | 2.0698 | 0.071752
3647 | 2.0698 | 0.071771
3648 | 2.0698 | 0.071789
3649 | 2.0697 | 0.071808
3650 | 2.0697 | 0.071827
3651 | 2.0697 | 0.071846
3652 | 2.0696 | 0.071865
3653 | 2.0696 | 0.071884
3654 | 2.0696 | 0.071903
3655 | 2.0696 | 0.071922
3656 | 2.0695 | 0.071941
3657 | 2.0695 | 0.07196
3658 | 2.0695 | 0.071979
3659 | 2.0694 | 0.071998
3660 | 2.0694 | 0.072017
3661 | 2.0694 | 0.072036
3662 | 2.0694 | 0.072054
3663 | 2.0693 | 0.072073
3664 | 2.0693 | 0.072092
3665 | 2.0693 | 0.072111
3666 | 2.0692 | 0.07213
3667 | 2.0692 | 0.072149
3668 | 2.0692 | 0.072168
3669 | 2.0691 | 0.072187
3670 | 2.0691 | 0.072206
3671 | 2.0691 | 0.072225
3672 | 2.0691 | 0.072244
3673 | 2.069 | 0.072263
3674 | 2.069 | 0.072282
3675 | 2.069 | 0.072301
3676 | 2.0689 | 0.072319
3677 | 2.0689 | 0.072338
3678 | 2.0689 | 0.072357
3679 | 2.0689 | 0.072376
3680 | 2.0688 | 0.072395
3681 | 2.0688 | 0.072414
3682 | 2.0688 | 0.072433
3683 | 2.0687 | 0.072452
3684 | 2.0687 | 0.072471
3685 | 2.0687 | 0.07249
3686 | 2.0686 | 0.072509
3687 | 2.0686 | 0.072528
3688 | 2.0686 | 0.072547
3689 | 2.0686 | 0.072565
3690 | 2.0685 | 0.072584
3691 | 2.0685 | 0.072603
3692 | 2.0685 | 0.072622
3693 | 2.0684 | 0.072641
3694 | 2.0684 | 0.07266
3695 | 2.0684 | 0.072679
3696 | 2.0683 | 0.072698
3697 | 2.0683 | 0.072717
3698 | 2.0683 | 0.072736
3699 | 2.0683 | 0.072755
3700 | 2.0682 | 0.072774
3701 | 2.0682 | 0.072792
3702 | 2.0682 | 0.072811
3703 | 2.0681 | 0.07283
3704 | 2.0681 | 0.072849
3705 | 2.0681 | 0.072868
3706 | 2.0681 | 0.072887
3707 | 2.068 | 0.072906
3708 | 2.068 | 0.072925
3709 | 2.068 | 0.072944
3710 | 2.0679 | 0.072963
3711 | 2.0679 | 0.072982
3712 | 2.0679 | 0.073
3713 | 2.0678 | 0.073019
3714 | 2.0678 | 0.073038
3715 | 2.0678 | 0.073057
3716 | 2.0678 | 0.073076
3717 | 2.0677 | 0.073095
3718 | 2.0677 | 0.073114
3719 | 2.0677 | 0.073133
3720 | 2.0676 | 0.073152
3721 | 2.0676 | 0.073171
3722 | 2.0676 | 0.07319
3723 | 2.0676 | 0.073208
3724 | 2.0675 | 0.073227
3725 | 2.0675 | 0.073246
3726 | 2.0675 | 0.073265
3727 | 2.0674 | 0.073284
3728 | 2.0674 | 0.073303
3729 | 2.0674 | 0.073322
3730 | 2.0673 | 0.073341
3731 | 2.0673 | 0.07336
3732 | 2.0673 | 0.073379
3733 | 2.0673 | 0.073398
3734 | 2.0672 | 0.073416
3735 | 2.0672 | 0.073435
3736 | 2.0672 | 0.073454
3737 | 2.0671 | 0.073473
3738 | 2.0671 | 0.073492
3739 | 2.0671 | 0.073511
3740 | 2.067 | 0.07353
3741 | 2.067 | 0.073549
3742 | 2.067 | 0.073568
3743 | 2.067 | 0.073587
3744 | 2.0669 | 0.073605
3745 | 2.0669 | 0.073624
3746 | 2.0669 | 0.073643
3747 | 2.0668 | 0.073662
3748 | 2.0668 | 0.073681
3749 | 2.0668 | 0.0737
3750 | 2.0668 | 0.073719
3751 | 2.0667 | 0.073738
3752 | 2.0667 | 0.073757
3753 | 2.0667 | 0.073775
3754 | 2.0666 | 0.073794
3755 | 2.0666 | 0.073813
3756 | 2.0666 | 0.073832
3757 | 2.0665 | 0.073851
3758 | 2.0665 | 0.07387
3759 | 2.0665 | 0.073889
3760 | 2.0665 | 0.073908
3761 | 2.0664 | 0.073927
3762 | 2.0664 | 0.073946
3763 | 2.0664 | 0.073964
3764 | 2.0663 | 0.073983
3765 | 2.0663 | 0.074002
3766 | 2.0663 | 0.074021
3767 | 2.0663 | 0.07404
3768 | 2.0662 | 0.074059
3769 | 2.0662 | 0.074078
3770 | 2.0662 | 0.074097
3771 | 2.0661 | 0.074116
3772 | 2.0661 | 0.074134
3773 | 2.0661 | 0.074153
3774 | 2.066 | 0.074172
3775 | 2.066 | 0.074191
3776 | 2.066 | 0.07421
3777 | 2.066 | 0.074229
3778 | 2.0659 | 0.074248
3779 | 2.0659 | 0.074267
3780 | 2.0659 | 0.074286
3781 | 2.0658 | 0.074304
3782 | 2.0658 | 0.074323
3783 | 2.0658 | 0.074342
3784 | 2.0658 | 0.074361
3785 | 2.0657 | 0.07438
3786 | 2.0657 | 0.074399
3787 | 2.0657 | 0.074418
3788 | 2.0656 | 0.074437
3789 | 2.0656 | 0.074455
3790 | 2.0656 | 0.074474
3791 | 2.0655 | 0.074493
3792 | 2.0655 | 0.074512
3793 | 2.0655 | 0.074531
3794 | 2.0655 | 0.07455
3795 | 2.0654 | 0.074569
3796 | 2.0654 | 0.074588
3797 | 2.0654 | 0.074607
3798 | 2.0653 | 0.074625
3799 | 2.0653 | 0.074644
3800 | 2.0653 | 0.074663
3801 | 2.0653 | 0.074682
3802 | 2.0652 | 0.074701
3803 | 2.0652 | 0.07472
3804 | 2.0652 | 0.074739
3805 | 2.0651 | 0.074758
3806 | 2.0651 | 0.074776
3807 | 2.0651 | 0.074795
3808 | 2.065 | 0.074814
3809 | 2.065 | 0.074833
3810 | 2.065 | 0.074852
3811 | 2.065 | 0.074871
3812 | 2.0649 | 0.07489
3813 | 2.0649 | 0.074909
3814 | 2.0649 | 0.074927
3815 | 2.0648 | 0.074946
3816 | 2.0648 | 0.074965
3817 | 2.0648 | 0.074984
3818 | 2.0648 | 0.075003
3819 | 2.0647 | 0.075022
3820 | 2.0647 | 0.075041
3821 | 2.0647 | 0.07506
3822 | 2.0646 | 0.075078
3823 | 2.0646 | 0.075097
3824 | 2.0646 | 0.075116
3825 | 2.0645 | 0.075135
3826 | 2.0645 | 0.075154
3827 | 2.0645 | 0.075173
3828 | 2.0645 | 0.075192
3829 | 2.0644 | 0.07521
3830 | 2.0644 | 0.075229
3831 | 2.0644 | 0.075248
3832 | 2.0643 | 0.075267
3833 | 2.0643 | 0.075286
3834 | 2.0643 | 0.075305
3835 | 2.0643 | 0.075324
3836 | 2.0642 | 0.075343
3837 | 2.0642 | 0.075361
3838 | 2.0642 | 0.07538
3839 | 2.0641 | 0.075399
3840 | 2.0641 | 0.075418
3841 | 2.0641 | 0.075437
3842 | 2.0641 | 0.075456
3843 | 2.064 | 0.075475
3844 | 2.064 | 0.075493
3845 | 2.064 | 0.075512
3846 | 2.0639 | 0.075531
3847 | 2.0639 | 0.07555
3848 | 2.0639 | 0.075569
3849 | 2.0638 | 0.075588
3850 | 2.0638 | 0.075607
3851 | 2.0638 | 0.075625
3852 | 2.0638 | 0.075644
3853 | 2.0637 | 0.075663
3854 | 2.0637 | 0.075682
3855 | 2.0637 | 0.075701
3856 | 2.0636 | 0.07572
3857 | 2.0636 | 0.075739
3858 | 2.0636 | 0.075757
3859 | 2.0636 | 0.075776
3860 | 2.0635 | 0.075795
3861 | 2.0635 | 0.075814
3862 | 2.0635 | 0.075833
3863 | 2.0634 | 0.075852
3864 | 2.0634 | 0.075871
3865 | 2.0634 | 0.075889
3866 | 2.0633 | 0.075908
3867 | 2.0633 | 0.075927
3868 | 2.0633 | 0.075946
3869 | 2.0633 | 0.075965
3870 | 2.0632 | 0.075984
3871 | 2.0632 | 0.076003
3872 | 2.0632 | 0.076021
3873 | 2.0631 | 0.07604
3874 | 2.0631 | 0.076059
3875 | 2.0631 | 0.076078
3876 | 2.0631 | 0.076097
3877 | 2.063 | 0.076116
3878 | 2.063 | 0.076134
3879 | 2.063 | 0.076153
3880 | 2.0629 | 0.076172
3881 | 2.0629 | 0.076191
3882 | 2.0629 | 0.07621
3883 | 2.0628 | 0.076229
3884 | 2.0628 | 0.076248
3885 | 2.0628 | 0.076266
3886 | 2.0628 | 0.076285
3887 | 2.0627 | 0.076304
3888 | 2.0627 | 0.076323
3889 | 2.0627 | 0.076342
3890 | 2.0626 | 0.076361
3891 | 2.0626 | 0.076379
3892 | 2.0626 | 0.076398
3893 | 2.0626 | 0.076417
3894 | 2.0625 | 0.076436
3895 | 2.0625 | 0.076455
3896 | 2.0625 | 0.076474
3897 | 2.0624 | 0.076493
3898 | 2.0624 | 0.076511
3899 | 2.0624 | 0.07653
3900 | 2.0624 | 0.076549
3901 | 2.0623 | 0.076568
3902 | 2.0623 | 0.076587
3903 | 2.0623 | 0.076606
3904 | 2.0622 | 0.076624
3905 | 2.0622 | 0.076643
3906 | 2.0622 | 0.076662
3907 | 2.0621 | 0.076681
3908 | 2.0621 | 0.0767
3909 | 2.0621 | 0.076719
3910 | 2.0621 | 0.076737
3911 | 2.062 | 0.076756
3912 | 2.062 | 0.076775
3913 | 2.062 | 0.076794
3914 | 2.0619 | 0.076813
3915 | 2.0619 | 0.076832
3916 | 2.0619 | 0.07685
3917 | 2.0619 | 0.076869
3918 | 2.0618 | 0.076888
3919 | 2.0618 | 0.076907
3920 | 2.0618 | 0.076926
3921 | 2.0617 | 0.076945
3922 | 2.0617 | 0.076963
3923 | 2.0617 | 0.076982
3924 | 2.0617 | 0.077001
3925 | 2.0616 | 0.07702
3926 | 2.0616 | 0.077039
3927 | 2.0616 | 0.077058
3928 | 2.0615 | 0.077076
3929 | 2.0615 | 0.077095
3930 | 2.0615 | 0.077114
3931 | 2.0614 | 0.077133
3932 | 2.0614 | 0.077152
3933 | 2.0614 | 0.077171
3934 | 2.0614 | 0.077189
3935 | 2.0613 | 0.077208
3936 | 2.0613 | 0.077227
3937 | 2.0613 | 0.077246
3938 | 2.0612 | 0.077265
3939 | 2.0612 | 0.077284
3940 | 2.0612 | 0.077302
3941 | 2.0612 | 0.077321
3942 | 2.0611 | 0.07734
3943 | 2.0611 | 0.077359
3944 | 2.0611 | 0.077378
3945 | 2.061 | 0.077396
3946 | 2.061 | 0.077415
3947 | 2.061 | 0.077434
3948 | 2.061 | 0.077453
3949 | 2.0609 | 0.077472
3950 | 2.0609 | 0.077491
3951 | 2.0609 | 0.077509
3952 | 2.0608 | 0.077528
3953 | 2.0608 | 0.077547
3954 | 2.0608 | 0.077566
3955 | 2.0607 | 0.077585
3956 | 2.0607 | 0.077604
3957 | 2.0607 | 0.077622
3958 | 2.0607 | 0.077641
3959 | 2.0606 | 0.07766
3960 | 2.0606 | 0.077679
3961 | 2.0606 | 0.077698
3962 | 2.0605 | 0.077716
3963 | 2.0605 | 0.077735
3964 | 2.0605 | 0.077754
3965 | 2.0605 | 0.077773
3966 | 2.0604 | 0.077792
3967 | 2.0604 | 0.077811
3968 | 2.0604 | 0.077829
3969 | 2.0603 | 0.077848
3970 | 2.0603 | 0.077867
3971 | 2.0603 | 0.077886
3972 | 2.0603 | 0.077905
3973 | 2.0602 | 0.077923
3974 | 2.0602 | 0.077942
3975 | 2.0602 | 0.077961
3976 | 2.0601 | 0.07798
3977 | 2.0601 | 0.077999
3978 | 2.0601 | 0.078017
3979 | 2.06 | 0.078036
3980 | 2.06 | 0.078055
3981 | 2.06 | 0.078074
3982 | 2.06 | 0.078093
3983 | 2.0599 | 0.078112
3984 | 2.0599 | 0.07813
3985 | 2.0599 | 0.078149
3986 | 2.0598 | 0.078168
3987 | 2.0598 | 0.078187
3988 | 2.0598 | 0.078206
3989 | 2.0598 | 0.078224
3990 | 2.0597 | 0.078243
3991 | 2.0597 | 0.078262
3992 | 2.0597 | 0.078281
3993 | 2.0596 | 0.0783
3994 | 2.0596 | 0.078318
3995 | 2.0596 | 0.078337
3996 | 2.0596 | 0.078356
3997 | 2.0595 | 0.078375
3998 | 2.0595 | 0.078394
3999 | 2.0595 | 0.078412
4000 | 2.0594 | 0.078431
4001 | 2.0594 | 0.07845
4002 | 2.0594 | 0.078469
4003 | 2.0593 | 0.078488
4004 | 2.0593 | 0.078506
4005 | 2.0593 | 0.078525
4006 | 2.0593 | 0.078544
4007 | 2.0592 | 0.078563
4008 | 2.0592 | 0.078582
4009 | 2.0592 | 0.0786
4010 | 2.0591 | 0.078619
4011 | 2.0591 | 0.078638
4012 | 2.0591 | 0.078657
4013 | 2.0591 | 0.078676
4014 | 2.059 | 0.078694
4015 | 2.059 | 0.078713
4016 | 2.059 | 0.078732
4017 | 2.0589 | 0.078751
4018 | 2.0589 | 0.07877
4019 | 2.0589 | 0.078788
4020 | 2.0589 | 0.078807
4021 | 2.0588 | 0.078826
4022 | 2.0588 | 0.078845
4023 | 2.0588 | 0.078864
4024 | 2.0587 | 0.078882
4025 | 2.0587 | 0.078901
4026 | 2.0587 | 0.07892
4027 | 2.0586 | 0.078939
4028 | 2.0586 | 0.078958
4029 | 2.0586 | 0.078976
4030 | 2.0586 | 0.078995
4031 | 2.0585 | 0.079014
4032 | 2.0585 | 0.079033
4033 | 2.0585 | 0.079052
4034 | 2.0584 | 0.07907
4035 | 2.0584 | 0.079089
4036 | 2.0584 | 0.079108
4037 | 2.0584 | 0.079127
4038 | 2.0583 | 0.079146
4039 | 2.0583 | 0.079164
4040 | 2.0583 | 0.079183
4041 | 2.0582 | 0.079202
4042 | 2.0582 | 0.079221
4043 | 2.0582 | 0.079239
4044 | 2.0582 | 0.079258
4045 | 2.0581 | 0.079277
4046 | 2.0581 | 0.079296
4047 | 2.0581 | 0.079315
4048 | 2.058 | 0.079333
4049 | 2.058 | 0.079352
4050 | 2.058 | 0.079371
4051 | 2.058 | 0.07939
4052 | 2.0579 | 0.079409
4053 | 2.0579 | 0.079427
4054 | 2.0579 | 0.079446
4055 | 2.0578 | 0.079465
4056 | 2.0578 | 0.079484
4057 | 2.0578 | 0.079502
4058 | 2.0577 | 0.079521
4059 | 2.0577 | 0.07954
4060 | 2.0577 | 0.079559
4061 | 2.0577 | 0.079578
4062 | 2.0576 | 0.079596
4063 | 2.0576 | 0.079615
4064 | 2.0576 | 0.079634
4065 | 2.0575 | 0.079653
4066 | 2.0575 | 0.079671
4067 | 2.0575 | 0.07969
4068 | 2.0575 | 0.079709
4069 | 2.0574 | 0.079728
4070 | 2.0574 | 0.079747
4071 | 2.0574 | 0.079765
4072 | 2.0573 | 0.079784
4073 | 2.0573 | 0.079803
4074 | 2.0573 | 0.079822
4075 | 2.0573 | 0.07984
4076 | 2.0572 | 0.079859
4077 | 2.0572 | 0.079878
4078 | 2.0572 | 0.079897
4079 | 2.0571 | 0.079916
4080 | 2.0571 | 0.079934
4081 | 2.0571 | 0.079953
4082 | 2.0571 | 0.079972
4083 | 2.057 | 0.079991
4084 | 2.057 | 0.080009
4085 | 2.057 | 0.080028
4086 | 2.0569 | 0.080047
4087 | 2.0569 | 0.080066
4088 | 2.0569 | 0.080085
4089 | 2.0569 | 0.080103
4090 | 2.0568 | 0.080122
4091 | 2.0568 | 0.080141
4092 | 2.0568 | 0.08016
4093 | 2.0567 | 0.080178
4094 | 2.0567 | 0.080197
4095 | 2.0567 | 0.080216
4096 | 2.0566 | 0.080235
4097 | 2.0566 | 0.080253
4098 | 2.0566 | 0.080272
4099 | 2.0566 | 0.080291
4100 | 2.0565 | 0.08031
4101 | 2.0565 | 0.080329
4102 | 2.0565 | 0.080347
4103 | 2.0564 | 0.080366
4104 | 2.0564 | 0.080385
4105 | 2.0564 | 0.080404
4106 | 2.0564 | 0.080422
4107 | 2.0563 | 0.080441
4108 | 2.0563 | 0.08046
4109 | 2.0563 | 0.080479
4110 | 2.0562 | 0.080497
4111 | 2.0562 | 0.080516
4112 | 2.0562 | 0.080535
4113 | 2.0562 | 0.080554
4114 | 2.0561 | 0.080572
4115 | 2.0561 | 0.080591
4116 | 2.0561 | 0.08061
4117 | 2.056 | 0.080629
4118 | 2.056 | 0.080648
4119 | 2.056 | 0.080666
4120 | 2.056 | 0.080685
4121 | 2.0559 | 0.080704
4122 | 2.0559 | 0.080723
4123 | 2.0559 | 0.080741
4124 | 2.0558 | 0.08076
4125 | 2.0558 | 0.080779
4126 | 2.0558 | 0.080798
4127 | 2.0558 | 0.080816
4128 | 2.0557 | 0.080835
4129 | 2.0557 | 0.080854
4130 | 2.0557 | 0.080873
4131 | 2.0556 | 0.080891
4132 | 2.0556 | 0.08091
4133 | 2.0556 | 0.080929
4134 | 2.0555 | 0.080948
4135 | 2.0555 | 0.080966
4136 | 2.0555 | 0.080985
4137 | 2.0555 | 0.081004
4138 | 2.0554 | 0.081023
4139 | 2.0554 | 0.081041
4140 | 2.0554 | 0.08106
4141 | 2.0553 | 0.081079
4142 | 2.0553 | 0.081098
4143 | 2.0553 | 0.081116
4144 | 2.0553 | 0.081135
4145 | 2.0552 | 0.081154
4146 | 2.0552 | 0.081173
4147 | 2.0552 | 0.081191
4148 | 2.0551 | 0.08121
4149 | 2.0551 | 0.081229
4150 | 2.0551 | 0.081248
4151 | 2.0551 | 0.081266
4152 | 2.055 | 0.081285
4153 | 2.055 | 0.081304
4154 | 2.055 | 0.081323
4155 | 2.0549 | 0.081341
4156 | 2.0549 | 0.08136
4157 | 2.0549 | 0.081379
4158 | 2.0549 | 0.081398
4159 | 2.0548 | 0.081416
4160 | 2.0548 | 0.081435
4161 | 2.0548 | 0.081454
4162 | 2.0547 | 0.081473
4163 | 2.0547 | 0.081491
4164 | 2.0547 | 0.08151
4165 | 2.0547 | 0.081529
4166 | 2.0546 | 0.081548
4167 | 2.0546 | 0.081566
4168 | 2.0546 | 0.081585
4169 | 2.0545 | 0.081604
4170 | 2.0545 | 0.081623
4171 | 2.0545 | 0.081641
4172 | 2.0545 | 0.08166
4173 | 2.0544 | 0.081679
4174 | 2.0544 | 0.081698
4175 | 2.0544 | 0.081716
4176 | 2.0543 | 0.081735
4177 | 2.0543 | 0.081754
4178 | 2.0543 | 0.081772
4179 | 2.0542 | 0.081791
4180 | 2.0542 | 0.08181
4181 | 2.0542 | 0.081829
4182 | 2.0542 | 0.081847
4183 | 2.0541 | 0.081866
4184 | 2.0541 | 0.081885
4185 | 2.0541 | 0.081904
4186 | 2.054 | 0.081922
4187 | 2.054 | 0.081941
4188 | 2.054 | 0.08196
4189 | 2.054 | 0.081979
4190 | 2.0539 | 0.081997
4191 | 2.0539 | 0.082016
4192 | 2.0539 | 0.082035
4193 | 2.0538 | 0.082054
4194 | 2.0538 | 0.082072
4195 | 2.0538 | 0.082091
4196 | 2.0538 | 0.08211
4197 | 2.0537 | 0.082128
4198 | 2.0537 | 0.082147
4199 | 2.0537 | 0.082166
4200 | 2.0536 | 0.082185
4201 | 2.0536 | 0.082203
4202 | 2.0536 | 0.082222
4203 | 2.0536 | 0.082241
4204 | 2.0535 | 0.08226
4205 | 2.0535 | 0.082278
4206 | 2.0535 | 0.082297
4207 | 2.0534 | 0.082316
4208 | 2.0534 | 0.082334
4209 | 2.0534 | 0.082353
4210 | 2.0534 | 0.082372
4211 | 2.0533 | 0.082391
4212 | 2.0533 | 0.082409
4213 | 2.0533 | 0.082428
4214 | 2.0532 | 0.082447
4215 | 2.0532 | 0.082466
4216 | 2.0532 | 0.082484
4217 | 2.0532 | 0.082503
4218 | 2.0531 | 0.082522
4219 | 2.0531 | 0.08254
4220 | 2.0531 | 0.082559
4221 | 2.053 | 0.082578
4222 | 2.053 | 0.082597
4223 | 2.053 | 0.082615
4224 | 2.053 | 0.082634
4225 | 2.0529 | 0.082653
4226 | 2.0529 | 0.082672
4227 | 2.0529 | 0.08269
4228 | 2.0528 | 0.082709
4229 | 2.0528 | 0.082728
4230 | 2.0528 | 0.082746
4231 | 2.0528 | 0.082765
4232 | 2.0527 | 0.082784
4233 | 2.0527 | 0.082803
4234 | 2.0527 | 0.082821
4235 | 2.0526 | 0.08284
4236 | 2.0526 | 0.082859
4237 | 2.0526 | 0.082877
4238 | 2.0525 | 0.082896
4239 | 2.0525 | 0.082915
4240 | 2.0525 | 0.082934
4241 | 2.0525 | 0.082952
4242 | 2.0524 | 0.082971
4243 | 2.0524 | 0.08299
4244 | 2.0524 | 0.083008
4245 | 2.0523 | 0.083027
4246 | 2.0523 | 0.083046
4247 | 2.0523 | 0.083065
4248 | 2.0523 | 0.083083
4249 | 2.0522 | 0.083102
4250 | 2.0522 | 0.083121
4251 | 2.0522 | 0.083139
4252 | 2.0521 | 0.083158
4253 | 2.0521 | 0.083177
4254 | 2.0521 | 0.083196
4255 | 2.0521 | 0.083214
4256 | 2.052 | 0.083233
4257 | 2.052 | 0.083252
4258 | 2.052 | 0.08327
4259 | 2.0519 | 0.083289
4260 | 2.0519 | 0.083308
4261 | 2.0519 | 0.083327
4262 | 2.0519 | 0.083345
4263 | 2.0518 | 0.083364
4264 | 2.0518 | 0.083383
4265 | 2.0518 | 0.083401
4266 | 2.0517 | 0.08342
4267 | 2.0517 | 0.083439
4268 | 2.0517 | 0.083457
4269 | 2.0517 | 0.083476
4270 | 2.0516 | 0.083495
4271 | 2.0516 | 0.083514
4272 | 2.0516 | 0.083532
4273 | 2.0515 | 0.083551
4274 | 2.0515 | 0.08357
4275 | 2.0515 | 0.083588
4276 | 2.0515 | 0.083607
4277 | 2.0514 | 0.083626
4278 | 2.0514 | 0.083645
4279 | 2.0514 | 0.083663
4280 | 2.0513 | 0.083682
4281 | 2.0513 | 0.083701
4282 | 2.0513 | 0.083719
4283 | 2.0513 | 0.083738
4284 | 2.0512 | 0.083757
4285 | 2.0512 | 0.083775
4286 | 2.0512 | 0.083794
4287 | 2.0511 | 0.083813
4288 | 2.0511 | 0.083832
4289 | 2.0511 | 0.08385
4290 | 2.0511 | 0.083869
4291 | 2.051 | 0.083888
4292 | 2.051 | 0.083906
4293 | 2.051 | 0.083925
4294 | 2.0509 | 0.083944
4295 | 2.0509 | 0.083962
4296 | 2.0509 | 0.083981
4297 | 2.0509 | 0.084
4298 | 2.0508 | 0.084018
4299 | 2.0508 | 0.084037
4300 | 2.0508 | 0.084056
4301 | 2.0507 | 0.084075
4302 | 2.0507 | 0.084093
4303 | 2.0507 | 0.084112
4304 | 2.0507 | 0.084131
4305 | 2.0506 | 0.084149
4306 | 2.0506 | 0.084168
4307 | 2.0506 | 0.084187
4308 | 2.0505 | 0.084205
4309 | 2.0505 | 0.084224
4310 | 2.0505 | 0.084243
4311 | 2.0505 | 0.084261
4312 | 2.0504 | 0.08428
4313 | 2.0504 | 0.084299
4314 | 2.0504 | 0.084318
4315 | 2.0503 | 0.084336
4316 | 2.0503 | 0.084355
4317 | 2.0503 | 0.084374
4318 | 2.0503 | 0.084392
4319 | 2.0502 | 0.084411
4320 | 2.0502 | 0.08443
4321 | 2.0502 | 0.084448
4322 | 2.0501 | 0.084467
4323 | 2.0501 | 0.084486
4324 | 2.0501 | 0.084504
4325 | 2.0501 | 0.084523
4326 | 2.05 | 0.084542
4327 | 2.05 | 0.08456
4328 | 2.05 | 0.084579
4329 | 2.0499 | 0.084598
4330 | 2.0499 | 0.084617
4331 | 2.0499 | 0.084635
4332 | 2.0499 | 0.084654
4333 | 2.0498 | 0.084673
4334 | 2.0498 | 0.084691
4335 | 2.0498 | 0.08471
4336 | 2.0497 | 0.084729
4337 | 2.0497 | 0.084747
4338 | 2.0497 | 0.084766
4339 | 2.0497 | 0.084785
4340 | 2.0496 | 0.084803
4341 | 2.0496 | 0.084822
4342 | 2.0496 | 0.084841
4343 | 2.0495 | 0.084859
4344 | 2.0495 | 0.084878
4345 | 2.0495 | 0.084897
4346 | 2.0494 | 0.084915
4347 | 2.0494 | 0.084934
4348 | 2.0494 | 0.084953
4349 | 2.0494 | 0.084971
4350 | 2.0493 | 0.08499
4351 | 2.0493 | 0.085009
4352 | 2.0493 | 0.085027
4353 | 2.0492 | 0.085046
4354 | 2.0492 | 0.085065
4355 | 2.0492 | 0.085083
4356 | 2.0492 | 0.085102
4357 | 2.0491 | 0.085121
4358 | 2.0491 | 0.08514
4359 | 2.0491 | 0.085158
4360 | 2.049 | 0.085177
4361 | 2.049 | 0.085196
4362 | 2.049 | 0.085214
4363 | 2.049 | 0.085233
4364 | 2.0489 | 0.085252
4365 | 2.0489 | 0.08527
4366 | 2.0489 | 0.085289
4367 | 2.0488 | 0.085308
4368 | 2.0488 | 0.085326
4369 | 2.0488 | 0.085345
4370 | 2.0488 | 0.085364
4371 | 2.0487 | 0.085382
4372 | 2.0487 | 0.085401
4373 | 2.0487 | 0.08542
4374 | 2.0486 | 0.085438
4375 | 2.0486 | 0.085457
4376 | 2.0486 | 0.085476
4377 | 2.0486 | 0.085494
4378 | 2.0485 | 0.085513
4379 | 2.0485 | 0.085532
4380 | 2.0485 | 0.08555
4381 | 2.0484 | 0.085569
4382 | 2.0484 | 0.085588
4383 | 2.0484 | 0.085606
4384 | 2.0484 | 0.085625
4385 | 2.0483 | 0.085644
4386 | 2.0483 | 0.085662
4387 | 2.0483 | 0.085681
4388 | 2.0482 | 0.0857
4389 | 2.0482 | 0.085718
4390 | 2.0482 | 0.085737
4391 | 2.0482 | 0.085756
4392 | 2.0481 | 0.085774
4393 | 2.0481 | 0.085793
4394 | 2.0481 | 0.085812
4395 | 2.048 | 0.08583
4396 | 2.048 | 0.085849
4397 | 2.048 | 0.085867
4398 | 2.048 | 0.085886
4399 | 2.0479 | 0.085905
4400 | 2.0479 | 0.085923
4401 | 2.0479 | 0.085942
4402 | 2.0478 | 0.085961
4403 | 2.0478 | 0.085979
4404 | 2.0478 | 0.085998
4405 | 2.0478 | 0.086017
4406 | 2.0477 | 0.086035
4407 | 2.0477 | 0.086054
4408 | 2.0477 | 0.086073
4409 | 2.0476 | 0.086091
4410 | 2.0476 | 0.08611
4411 | 2.0476 | 0.086129
4412 | 2.0476 | 0.086147
4413 | 2.0475 | 0.086166
4414 | 2.0475 | 0.086185
4415 | 2.0475 | 0.086203
4416 | 2.0475 | 0.086222
4417 | 2.0474 | 0.086241
4418 | 2.0474 | 0.086259
4419 | 2.0474 | 0.086278
4420 | 2.0473 | 0.086297
4421 | 2.0473 | 0.086315
4422 | 2.0473 | 0.086334
4423 | 2.0473 | 0.086353
4424 | 2.0472 | 0.086371
4425 | 2.0472 | 0.08639
4426 | 2.0472 | 0.086408
4427 | 2.0471 | 0.086427
4428 | 2.0471 | 0.086446
4429 | 2.0471 | 0.086464
4430 | 2.0471 | 0.086483
4431 | 2.047 | 0.086502
4432 | 2.047 | 0.08652
4433 | 2.047 | 0.086539
4434 | 2.0469 | 0.086558
4435 | 2.0469 | 0.086576
4436 | 2.0469 | 0.086595
4437 | 2.0469 | 0.086614
4438 | 2.0468 | 0.086632
4439 | 2.0468 | 0.086651
4440 | 2.0468 | 0.08667
4441 | 2.0467 | 0.086688
4442 | 2.0467 | 0.086707
4443 | 2.0467 | 0.086725
4444 | 2.0467 | 0.086744
4445 | 2.0466 | 0.086763
4446 | 2.0466 | 0.086781
4447 | 2.0466 | 0.0868
4448 | 2.0465 | 0.086819
4449 | 2.0465 | 0.086837
4450 | 2.0465 | 0.086856
4451 | 2.0465 | 0.086875
4452 | 2.0464 | 0.086893
4453 | 2.0464 | 0.086912
4454 | 2.0464 | 0.08693
4455 | 2.0463 | 0.086949
4456 | 2.0463 | 0.086968
4457 | 2.0463 | 0.086986
4458 | 2.0463 | 0.087005
4459 | 2.0462 | 0.087024
4460 | 2.0462 | 0.087042
4461 | 2.0462 | 0.087061
4462 | 2.0461 | 0.08708
4463 | 2.0461 | 0.087098
4464 | 2.0461 | 0.087117
4465 | 2.0461 | 0.087135
4466 | 2.046 | 0.087154
4467 | 2.046 | 0.087173
4468 | 2.046 | 0.087191
4469 | 2.0459 | 0.08721
4470 | 2.0459 | 0.087229
4471 | 2.0459 | 0.087247
4472 | 2.0459 | 0.087266
4473 | 2.0458 | 0.087285
4474 | 2.0458 | 0.087303
4475 | 2.0458 | 0.087322
4476 | 2.0457 | 0.08734
4477 | 2.0457 | 0.087359
4478 | 2.0457 | 0.087378
4479 | 2.0457 | 0.087396
4480 | 2.0456 | 0.087415
4481 | 2.0456 | 0.087434
4482 | 2.0456 | 0.087452
4483 | 2.0455 | 0.087471
4484 | 2.0455 | 0.087489
4485 | 2.0455 | 0.087508
4486 | 2.0455 | 0.087527
4487 | 2.0454 | 0.087545
4488 | 2.0454 | 0.087564
4489 | 2.0454 | 0.087583
4490 | 2.0453 | 0.087601
4491 | 2.0453 | 0.08762
4492 | 2.0453 | 0.087639
4493 | 2.0453 | 0.087657
4494 | 2.0452 | 0.087676
4495 | 2.0452 | 0.087694
4496 | 2.0452 | 0.087713
4497 | 2.0451 | 0.087732
4498 | 2.0451 | 0.08775
4499 | 2.0451 | 0.087769
4500 | 2.0451 | 0.087787
4501 | 2.045 | 0.087806
4502 | 2.045 | 0.087825
4503 | 2.045 | 0.087843
4504 | 2.0449 | 0.087862
4505 | 2.0449 | 0.087881
4506 | 2.0449 | 0.087899
4507 | 2.0449 | 0.087918
4508 | 2.0448 | 0.087936
4509 | 2.0448 | 0.087955
4510 | 2.0448 | 0.087974
4511 | 2.0447 | 0.087992
4512 | 2.0447 | 0.088011
4513 | 2.0447 | 0.08803
4514 | 2.0447 | 0.088048
4515 | 2.0446 | 0.088067
4516 | 2.0446 | 0.088085
4517 | 2.0446 | 0.088104
4518 | 2.0445 | 0.088123
4519 | 2.0445 | 0.088141
4520 | 2.0445 | 0.08816
4521 | 2.0445 | 0.088178
4522 | 2.0444 | 0.088197
4523 | 2.0444 | 0.088216
4524 | 2.0444 | 0.088234
4525 | 2.0443 | 0.088253
4526 | 2.0443 | 0.088272
4527 | 2.0443 | 0.08829
4528 | 2.0443 | 0.088309
4529 | 2.0442 | 0.088327
4530 | 2.0442 | 0.088346
4531 | 2.0442 | 0.088365
4532 | 2.0442 | 0.088383
4533 | 2.0441 | 0.088402
4534 | 2.0441 | 0.08842
4535 | 2.0441 | 0.088439
4536 | 2.044 | 0.088458
4537 | 2.044 | 0.088476
4538 | 2.044 | 0.088495
4539 | 2.044 | 0.088513
4540 | 2.0439 | 0.088532
4541 | 2.0439 | 0.088551
4542 | 2.0439 | 0.088569
4543 | 2.0438 | 0.088588
4544 | 2.0438 | 0.088607
4545 | 2.0438 | 0.088625
4546 | 2.0438 | 0.088644
4547 | 2.0437 | 0.088662
4548 | 2.0437 | 0.088681
4549 | 2.0437 | 0.0887
4550 | 2.0436 | 0.088718
4551 | 2.0436 | 0.088737
4552 | 2.0436 | 0.088755
4553 | 2.0436 | 0.088774
4554 | 2.0435 | 0.088793
4555 | 2.0435 | 0.088811
4556 | 2.0435 | 0.08883
4557 | 2.0434 | 0.088848
4558 | 2.0434 | 0.088867
4559 | 2.0434 | 0.088886
4560 | 2.0434 | 0.088904
4561 | 2.0433 | 0.088923
4562 | 2.0433 | 0.088941
4563 | 2.0433 | 0.08896
4564 | 2.0432 | 0.088979
4565 | 2.0432 | 0.088997
4566 | 2.0432 | 0.089016
4567 | 2.0432 | 0.089034
4568 | 2.0431 | 0.089053
4569 | 2.0431 | 0.089072
4570 | 2.0431 | 0.08909
4571 | 2.043 | 0.089109
4572 | 2.043 | 0.089127
4573 | 2.043 | 0.089146
4574 | 2.043 | 0.089165
4575 | 2.0429 | 0.089183
4576 | 2.0429 | 0.089202
4577 | 2.0429 | 0.08922
4578 | 2.0428 | 0.089239
4579 | 2.0428 | 0.089258
4580 | 2.0428 | 0.089276
4581 | 2.0428 | 0.089295
4582 | 2.0427 | 0.089313
4583 | 2.0427 | 0.089332
4584 | 2.0427 | 0.089351
4585 | 2.0426 | 0.089369
4586 | 2.0426 | 0.089388
4587 | 2.0426 | 0.089406
4588 | 2.0426 | 0.089425
4589 | 2.0425 | 0.089443
4590 | 2.0425 | 0.089462
4591 | 2.0425 | 0.089481
4592 | 2.0425 | 0.089499
4593 | 2.0424 | 0.089518
4594 | 2.0424 | 0.089536
4595 | 2.0424 | 0.089555
4596 | 2.0423 | 0.089574
4597 | 2.0423 | 0.089592
4598 | 2.0423 | 0.089611
4599 | 2.0423 | 0.089629
4600 | 2.0422 | 0.089648
4601 | 2.0422 | 0.089667
4602 | 2.0422 | 0.089685
4603 | 2.0421 | 0.089704
4604 | 2.0421 | 0.089722
4605 | 2.0421 | 0.089741
4606 | 2.0421 | 0.089759
4607 | 2.042 | 0.089778
4608 | 2.042 | 0.089797
4609 | 2.042 | 0.089815
4610 | 2.0419 | 0.089834
4611 | 2.0419 | 0.089852
4612 | 2.0419 | 0.089871
4613 | 2.0419 | 0.08989
4614 | 2.0418 | 0.089908
4615 | 2.0418 | 0.089927
4616 | 2.0418 | 0.089945
4617 | 2.0417 | 0.089964
4618 | 2.0417 | 0.089982
4619 | 2.0417 | 0.090001
4620 | 2.0417 | 0.09002
4621 | 2.0416 | 0.090038
4622 | 2.0416 | 0.090057
4623 | 2.0416 | 0.090075
4624 | 2.0415 | 0.090094
4625 | 2.0415 | 0.090113
4626 | 2.0415 | 0.090131
4627 | 2.0415 | 0.09015
4628 | 2.0414 | 0.090168
4629 | 2.0414 | 0.090187
4630 | 2.0414 | 0.090205
4631 | 2.0414 | 0.090224
4632 | 2.0413 | 0.090243
4633 | 2.0413 | 0.090261
4634 | 2.0413 | 0.09028
4635 | 2.0412 | 0.090298
4636 | 2.0412 | 0.090317
4637 | 2.0412 | 0.090335
4638 | 2.0412 | 0.090354
4639 | 2.0411 | 0.090373
4640 | 2.0411 | 0.090391
4641 | 2.0411 | 0.09041
4642 | 2.041 | 0.090428
4643 | 2.041 | 0.090447
4644 | 2.041 | 0.090465
4645 | 2.041 | 0.090484
4646 | 2.0409 | 0.090503
4647 | 2.0409 | 0.090521
4648 | 2.0409 | 0.09054
4649 | 2.0408 | 0.090558
4650 | 2.0408 | 0.090577
4651 | 2.0408 | 0.090595
4652 | 2.0408 | 0.090614
4653 | 2.0407 | 0.090633
4654 | 2.0407 | 0.090651
4655 | 2.0407 | 0.09067
4656 | 2.0406 | 0.090688
4657 | 2.0406 | 0.090707
4658 | 2.0406 | 0.090725
4659 | 2.0406 | 0.090744
4660 | 2.0405 | 0.090763
4661 | 2.0405 | 0.090781
4662 | 2.0405 | 0.0908
4663 | 2.0404 | 0.090818
4664 | 2.0404 | 0.090837
4665 | 2.0404 | 0.090855
4666 | 2.0404 | 0.090874
4667 | 2.0403 | 0.090892
4668 | 2.0403 | 0.090911
4669 | 2.0403 | 0.09093
4670 | 2.0403 | 0.090948
4671 | 2.0402 | 0.090967
4672 | 2.0402 | 0.090985
4673 | 2.0402 | 0.091004
4674 | 2.0401 | 0.091022
4675 | 2.0401 | 0.091041
4676 | 2.0401 | 0.09106
4677 | 2.0401 | 0.091078
4678 | 2.04 | 0.091097
4679 | 2.04 | 0.091115
4680 | 2.04 | 0.091134
4681 | 2.0399 | 0.091152
4682 | 2.0399 | 0.091171
4683 | 2.0399 | 0.091189
4684 | 2.0399 | 0.091208
4685 | 2.0398 | 0.091227
4686 | 2.0398 | 0.091245
4687 | 2.0398 | 0.091264
4688 | 2.0397 | 0.091282
4689 | 2.0397 | 0.091301
4690 | 2.0397 | 0.091319
4691 | 2.0397 | 0.091338
4692 | 2.0396 | 0.091356
4693 | 2.0396 | 0.091375
4694 | 2.0396 | 0.091394
4695 | 2.0395 | 0.091412
4696 | 2.0395 | 0.091431
4697 | 2.0395 | 0.091449
4698 | 2.0395 | 0.091468
4699 | 2.0394 | 0.091486
4700 | 2.0394 | 0.091505
4701 | 2.0394 | 0.091523
4702 | 2.0393 | 0.091542
4703 | 2.0393 | 0.09156
4704 | 2.0393 | 0.091579
4705 | 2.0393 | 0.091598
4706 | 2.0392 | 0.091616
4707 | 2.0392 | 0.091635
4708 | 2.0392 | 0.091653
4709 | 2.0392 | 0.091672
4710 | 2.0391 | 0.09169
4711 | 2.0391 | 0.091709
4712 | 2.0391 | 0.091727
4713 | 2.039 | 0.091746
4714 | 2.039 | 0.091765
4715 | 2.039 | 0.091783
4716 | 2.039 | 0.091802
4717 | 2.0389 | 0.09182
4718 | 2.0389 | 0.091839
4719 | 2.0389 | 0.091857
4720 | 2.0388 | 0.091876
4721 | 2.0388 | 0.091894
4722 | 2.0388 | 0.091913
4723 | 2.0388 | 0.091931
4724 | 2.0387 | 0.09195
4725 | 2.0387 | 0.091969
4726 | 2.0387 | 0.091987
4727 | 2.0386 | 0.092006
4728 | 2.0386 | 0.092024
4729 | 2.0386 | 0.092043
4730 | 2.0386 | 0.092061
4731 | 2.0385 | 0.09208
4732 | 2.0385 | 0.092098
4733 | 2.0385 | 0.092117
4734 | 2.0385 | 0.092135
4735 | 2.0384 | 0.092154
4736 | 2.0384 | 0.092172
4737 | 2.0384 | 0.092191
4738 | 2.0383 | 0.09221
4739 | 2.0383 | 0.092228
4740 | 2.0383 | 0.092247
4741 | 2.0383 | 0.092265
4742 | 2.0382 | 0.092284
4743 | 2.0382 | 0.092302
4744 | 2.0382 | 0.092321
4745 | 2.0381 | 0.092339
4746 | 2.0381 | 0.092358
4747 | 2.0381 | 0.092376
4748 | 2.0381 | 0.092395
4749 | 2.038 | 0.092413
4750 | 2.038 | 0.092432
4751 | 2.038 | 0.09245
4752 | 2.0379 | 0.092469
4753 | 2.0379 | 0.092488
4754 | 2.0379 | 0.092506
4755 | 2.0379 | 0.092525
4756 | 2.0378 | 0.092543
4757 | 2.0378 | 0.092562
4758 | 2.0378 | 0.09258
4759 | 2.0377 | 0.092599
4760 | 2.0377 | 0.092617
4761 | 2.0377 | 0.092636
4762 | 2.0377 | 0.092654
4763 | 2.0376 | 0.092673
4764 | 2.0376 | 0.092691
4765 | 2.0376 | 0.09271
4766 | 2.0376 | 0.092728
4767 | 2.0375 | 0.092747
4768 | 2.0375 | 0.092766
4769 | 2.0375 | 0.092784
4770 | 2.0374 | 0.092803
4771 | 2.0374 | 0.092821
4772 | 2.0374 | 0.09284
4773 | 2.0374 | 0.092858
4774 | 2.0373 | 0.092877
4775 | 2.0373 | 0.092895
4776 | 2.0373 | 0.092914
4777 | 2.0372 | 0.092932
4778 | 2.0372 | 0.092951
4779 | 2.0372 | 0.092969
4780 | 2.0372 | 0.092988
4781 | 2.0371 | 0.093006
4782 | 2.0371 | 0.093025
4783 | 2.0371 | 0.093043
4784 | 2.037 | 0.093062
4785 | 2.037 | 0.09308
4786 | 2.037 | 0.093099
4787 | 2.037 | 0.093117
4788 | 2.0369 | 0.093136
4789 | 2.0369 | 0.093155
4790 | 2.0369 | 0.093173
4791 | 2.0369 | 0.093192
4792 | 2.0368 | 0.09321
4793 | 2.0368 | 0.093229
4794 | 2.0368 | 0.093247
4795 | 2.0367 | 0.093266
4796 | 2.0367 | 0.093284
4797 | 2.0367 | 0.093303
4798 | 2.0367 | 0.093321
4799 | 2.0366 | 0.09334
4800 | 2.0366 | 0.093358
4801 | 2.0366 | 0.093377
4802 | 2.0365 | 0.093395
4803 | 2.0365 | 0.093414
4804 | 2.0365 | 0.093432
4805 | 2.0365 | 0.093451
4806 | 2.0364 | 0.093469
4807 | 2.0364 | 0.093488
4808 | 2.0364 | 0.093506
4809 | 2.0363 | 0.093525
4810 | 2.0363 | 0.093543
4811 | 2.0363 | 0.093562
4812 | 2.0363 | 0.09358
4813 | 2.0362 | 0.093599
4814 | 2.0362 | 0.093617
4815 | 2.0362 | 0.093636
4816 | 2.0362 | 0.093654
4817 | 2.0361 | 0.093673
4818 | 2.0361 | 0.093691
4819 | 2.0361 | 0.09371
4820 | 2.036 | 0.093728
4821 | 2.036 | 0.093747
4822 | 2.036 | 0.093765
4823 | 2.036 | 0.093784
4824 | 2.0359 | 0.093802
4825 | 2.0359 | 0.093821
4826 | 2.0359 | 0.093839
4827 | 2.0358 | 0.093858
4828 | 2.0358 | 0.093877
4829 | 2.0358 | 0.093895
4830 | 2.0358 | 0.093914
4831 | 2.0357 | 0.093932
4832 | 2.0357 | 0.093951
4833 | 2.0357 | 0.093969
4834 | 2.0356 | 0.093988
4835 | 2.0356 | 0.094006
4836 | 2.0356 | 0.094025
4837 | 2.0356 | 0.094043
4838 | 2.0355 | 0.094062
4839 | 2.0355 | 0.09408
4840 | 2.0355 | 0.094099
4841 | 2.0355 | 0.094117
4842 | 2.0354 | 0.094136
4843 | 2.0354 | 0.094154
4844 | 2.0354 | 0.094173
4845 | 2.0353 | 0.094191
4846 | 2.0353 | 0.09421
4847 | 2.0353 | 0.094228
4848 | 2.0353 | 0.094247
4849 | 2.0352 | 0.094265
4850 | 2.0352 | 0.094284
4851 | 2.0352 | 0.094302
4852 | 2.0351 | 0.094321
4853 | 2.0351 | 0.094339
4854 | 2.0351 | 0.094358
4855 | 2.0351 | 0.094376
4856 | 2.035 | 0.094395
4857 | 2.035 | 0.094413
4858 | 2.035 | 0.094432
4859 | 2.0349 | 0.09445
4860 | 2.0349 | 0.094469
4861 | 2.0349 | 0.094487
4862 | 2.0349 | 0.094506
4863 | 2.0348 | 0.094524
4864 | 2.0348 | 0.094543
4865 | 2.0348 | 0.094561
4866 | 2.0348 | 0.094579
4867 | 2.0347 | 0.094598
4868 | 2.0347 | 0.094616
4869 | 2.0347 | 0.094635
4870 | 2.0346 | 0.094653
4871 | 2.0346 | 0.094672
4872 | 2.0346 | 0.09469
4873 | 2.0346 | 0.094709
4874 | 2.0345 | 0.094727
4875 | 2.0345 | 0.094746
4876 | 2.0345 | 0.094764
4877 | 2.0344 | 0.094783
4878 | 2.0344 | 0.094801
4879 | 2.0344 | 0.09482
4880 | 2.0344 | 0.094838
4881 | 2.0343 | 0.094857
4882 | 2.0343 | 0.094875
4883 | 2.0343 | 0.094894
4884 | 2.0343 | 0.094912
4885 | 2.0342 | 0.094931
4886 | 2.0342 | 0.094949
4887 | 2.0342 | 0.094968
4888 | 2.0341 | 0.094986
4889 | 2.0341 | 0.095005
4890 | 2.0341 | 0.095023
4891 | 2.0341 | 0.095042
4892 | 2.034 | 0.09506
4893 | 2.034 | 0.095079
4894 | 2.034 | 0.095097
4895 | 2.0339 | 0.095116
4896 | 2.0339 | 0.095134
4897 | 2.0339 | 0.095153
4898 | 2.0339 | 0.095171
4899 | 2.0338 | 0.09519
4900 | 2.0338 | 0.095208
4901 | 2.0338 | 0.095227
4902 | 2.0338 | 0.095245
4903 | 2.0337 | 0.095263
4904 | 2.0337 | 0.095282
4905 | 2.0337 | 0.0953
4906 | 2.0336 | 0.095319
4907 | 2.0336 | 0.095337
4908 | 2.0336 | 0.095356
4909 | 2.0336 | 0.095374
4910 | 2.0335 | 0.095393
4911 | 2.0335 | 0.095411
4912 | 2.0335 | 0.09543
4913 | 2.0334 | 0.095448
4914 | 2.0334 | 0.095467
4915 | 2.0334 | 0.095485
4916 | 2.0334 | 0.095504
4917 | 2.0333 | 0.095522
4918 | 2.0333 | 0.095541
4919 | 2.0333 | 0.095559
4920 | 2.0332 | 0.095578
4921 | 2.0332 | 0.095596
4922 | 2.0332 | 0.095615
4923 | 2.0332 | 0.095633
4924 | 2.0331 | 0.095651
4925 | 2.0331 | 0.09567
4926 | 2.0331 | 0.095688
4927 | 2.0331 | 0.095707
4928 | 2.033 | 0.095725
4929 | 2.033 | 0.095744
4930 | 2.033 | 0.095762
4931 | 2.0329 | 0.095781
4932 | 2.0329 | 0.095799
4933 | 2.0329 | 0.095818
4934 | 2.0329 | 0.095836
4935 | 2.0328 | 0.095855
4936 | 2.0328 | 0.095873
4937 | 2.0328 | 0.095892
4938 | 2.0327 | 0.09591
4939 | 2.0327 | 0.095929
4940 | 2.0327 | 0.095947
4941 | 2.0327 | 0.095965
4942 | 2.0326 | 0.095984
4943 | 2.0326 | 0.096002
4944 | 2.0326 | 0.096021
4945 | 2.0326 | 0.096039
4946 | 2.0325 | 0.096058
4947 | 2.0325 | 0.096076
4948 | 2.0325 | 0.096095
4949 | 2.0324 | 0.096113
4950 | 2.0324 | 0.096132
4951 | 2.0324 | 0.09615
4952 | 2.0324 | 0.096169
4953 | 2.0323 | 0.096187
4954 | 2.0323 | 0.096206
4955 | 2.0323 | 0.096224
4956 | 2.0322 | 0.096242
4957 | 2.0322 | 0.096261
4958 | 2.0322 | 0.096279
4959 | 2.0322 | 0.096298
4960 | 2.0321 | 0.096316
4961 | 2.0321 | 0.096335
4962 | 2.0321 | 0.096353
4963 | 2.0321 | 0.096372
4964 | 2.032 | 0.09639
4965 | 2.032 | 0.096409
4966 | 2.032 | 0.096427
4967 | 2.0319 | 0.096445
4968 | 2.0319 | 0.096464
4969 | 2.0319 | 0.096482
4970 | 2.0319 | 0.096501
4971 | 2.0318 | 0.096519
4972 | 2.0318 | 0.096538
4973 | 2.0318 | 0.096556
4974 | 2.0317 | 0.096575
4975 | 2.0317 | 0.096593
4976 | 2.0317 | 0.096612
4977 | 2.0317 | 0.09663
4978 | 2.0316 | 0.096649
4979 | 2.0316 | 0.096667
4980 | 2.0316 | 0.096685
4981 | 2.0316 | 0.096704
4982 | 2.0315 | 0.096722
4983 | 2.0315 | 0.096741
4984 | 2.0315 | 0.096759
4985 | 2.0314 | 0.096778
4986 | 2.0314 | 0.096796
4987 | 2.0314 | 0.096815
4988 | 2.0314 | 0.096833
4989 | 2.0313 | 0.096851
4990 | 2.0313 | 0.09687
4991 | 2.0313 | 0.096888
4992 | 2.0312 | 0.096907
4993 | 2.0312 | 0.096925
4994 | 2.0312 | 0.096944
4995 | 2.0312 | 0.096962
4996 | 2.0311 | 0.096981
4997 | 2.0311 | 0.096999
4998 | 2.0311 | 0.097018
4999 | 2.0311 | 0.097036
5000 | 2.031 | 0.097054
5001 | 2.031 | 0.097073
5002 | 2.031 | 0.097091
5003 | 2.0309 | 0.09711
5004 | 2.0309 | 0.097128
5005 | 2.0309 | 0.097147
5006 | 2.0309 | 0.097165
5007 | 2.0308 | 0.097184
5008 | 2.0308 | 0.097202
5009 | 2.0308 | 0.09722
5010 | 2.0307 | 0.097239
5011 | 2.0307 | 0.097257
5012 | 2.0307 | 0.097276
5013 | 2.0307 | 0.097294
5014 | 2.0306 | 0.097313
5015 | 2.0306 | 0.097331
5016 | 2.0306 | 0.097349
5017 | 2.0306 | 0.097368
5018 | 2.0305 | 0.097386
5019 | 2.0305 | 0.097405
5020 | 2.0305 | 0.097423
5021 | 2.0304 | 0.097442
5022 | 2.0304 | 0.09746
5023 | 2.0304 | 0.097479
5024 | 2.0304 | 0.097497
5025 | 2.0303 | 0.097515
5026 | 2.0303 | 0.097534
5027 | 2.0303 | 0.097552
5028 | 2.0303 | 0.097571
5029 | 2.0302 | 0.097589
5030 | 2.0302 | 0.097608
5031 | 2.0302 | 0.097626
5032 | 2.0301 | 0.097644
5033 | 2.0301 | 0.097663
5034 | 2.0301 | 0.097681
5035 | 2.0301 | 0.0977
5036 | 2.03 | 0.097718
5037 | 2.03 | 0.097737
5038 | 2.03 | 0.097755
5039 | 2.0299 | 0.097774
5040 | 2.0299 | 0.097792
5041 | 2.0299 | 0.09781
5042 | 2.0299 | 0.097829
5043 | 2.0298 | 0.097847
5044 | 2.0298 | 0.097866
5045 | 2.0298 | 0.097884
5046 | 2.0298 | 0.097903
5047 | 2.0297 | 0.097921
5048 | 2.0297 | 0.097939
5049 | 2.0297 | 0.097958
5050 | 2.0296 | 0.097976
5051 | 2.0296 | 0.097995
5052 | 2.0296 | 0.098013
5053 | 2.0296 | 0.098032
5054 | 2.0295 | 0.09805
5055 | 2.0295 | 0.098068
5056 | 2.0295 | 0.098087
5057 | 2.0294 | 0.098105
5058 | 2.0294 | 0.098124
5059 | 2.0294 | 0.098142
5060 | 2.0294 | 0.098161
5061 | 2.0293 | 0.098179
5062 | 2.0293 | 0.098197
5063 | 2.0293 | 0.098216
5064 | 2.0293 | 0.098234
5065 | 2.0292 | 0.098253
5066 | 2.0292 | 0.098271
5067 | 2.0292 | 0.09829
5068 | 2.0291 | 0.098308
5069 | 2.0291 | 0.098326
5070 | 2.0291 | 0.098345
5071 | 2.0291 | 0.098363
5072 | 2.029 | 0.098382
5073 | 2.029 | 0.0984
5074 | 2.029 | 0.098418
5075 | 2.029 | 0.098437
5076 | 2.0289 | 0.098455
5077 | 2.0289 | 0.098474
5078 | 2.0289 | 0.098492
5079 | 2.0288 | 0.098511
5080 | 2.0288 | 0.098529
5081 | 2.0288 | 0.098547
5082 | 2.0288 | 0.098566
5083 | 2.0287 | 0.098584
5084 | 2.0287 | 0.098603
5085 | 2.0287 | 0.098621
5086 | 2.0286 | 0.098639
5087 | 2.0286 | 0.098658
5088 | 2.0286 | 0.098676
5089 | 2.0286 | 0.098695
5090 | 2.0285 | 0.098713
5091 | 2.0285 | 0.098732
5092 | 2.0285 | 0.09875
5093 | 2.0285 | 0.098768
5094 | 2.0284 | 0.098787
5095 | 2.0284 | 0.098805
5096 | 2.0284 | 0.098824
5097 | 2.0283 | 0.098842
5098 | 2.0283 | 0.09886
5099 | 2.0283 | 0.098879
5100 | 2.0283 | 0.098897
5101 | 2.0282 | 0.098916
5102 | 2.0282 | 0.098934
5103 | 2.0282 | 0.098953
5104 | 2.0282 | 0.098971
5105 | 2.0281 | 0.098989
5106 | 2.0281 | 0.099008
5107 | 2.0281 | 0.099026
5108 | 2.028 | 0.099045
5109 | 2.028 | 0.099063
5110 | 2.028 | 0.099081
5111 | 2.028 | 0.0991
5112 | 2.0279 | 0.099118
5113 | 2.0279 | 0.099137
5114 | 2.0279 | 0.099155
5115 | 2.0278 | 0.099173
5116 | 2.0278 | 0.099192
5117 | 2.0278 | 0.09921
5118 | 2.0278 | 0.099229
5119 | 2.0277 | 0.099247
5120 | 2.0277 | 0.099265
5121 | 2.0277 | 0.099284
5122 | 2.0277 | 0.099302
5123 | 2.0276 | 0.099321
5124 | 2.0276 | 0.099339
5125 | 2.0276 | 0.099357
5126 | 2.0275 | 0.099376
5127 | 2.0275 | 0.099394
5128 | 2.0275 | 0.099413
5129 | 2.0275 | 0.099431
5130 | 2.0274 | 0.099449
5131 | 2.0274 | 0.099468
5132 | 2.0274 | 0.099486
5133 | 2.0274 | 0.099505
5134 | 2.0273 | 0.099523
5135 | 2.0273 | 0.099541
5136 | 2.0273 | 0.09956
5137 | 2.0272 | 0.099578
5138 | 2.0272 | 0.099597
5139 | 2.0272 | 0.099615
5140 | 2.0272 | 0.099633
5141 | 2.0271 | 0.099652
5142 | 2.0271 | 0.09967
5143 | 2.0271 | 0.099689
5144 | 2.027 | 0.099707
5145 | 2.027 | 0.099725
5146 | 2.027 | 0.099744
5147 | 2.027 | 0.099762
5148 | 2.0269 | 0.099781
5149 | 2.0269 | 0.099799
5150 | 2.0269 | 0.099817
5151 | 2.0269 | 0.099836
5152 | 2.0268 | 0.099854
5153 | 2.0268 | 0.099873
5154 | 2.0268 | 0.099891
5155 | 2.0267 | 0.099909
5156 | 2.0267 | 0.099928
5157 | 2.0267 | 0.099946
5158 | 2.0267 | 0.099965
5159 | 2.0266 | 0.099983
5160 | 2.0266 | 0.1
5161 | 2.0266 | 0.10002
5162 | 2.0266 | 0.10004
5163 | 2.0265 | 0.10006
5164 | 2.0265 | 0.10007
5165 | 2.0265 | 0.10009
5166 | 2.0264 | 0.10011
5167 | 2.0264 | 0.10013
5168 | 2.0264 | 0.10015
5169 | 2.0264 | 0.10017
5170 | 2.0263 | 0.10019
5171 | 2.0263 | 0.1002
5172 | 2.0263 | 0.10022
5173 | 2.0262 | 0.10024
5174 | 2.0262 | 0.10026
5175 | 2.0262 | 0.10028
5176 | 2.0262 | 0.1003
5177 | 2.0261 | 0.10031
5178 | 2.0261 | 0.10033
5179 | 2.0261 | 0.10035
5180 | 2.0261 | 0.10037
5181 | 2.026 | 0.10039
5182 | 2.026 | 0.10041
5183 | 2.026 | 0.10042
5184 | 2.0259 | 0.10044
5185 | 2.0259 | 0.10046
5186 | 2.0259 | 0.10048
5187 | 2.0259 | 0.1005
5188 | 2.0258 | 0.10052
5189 | 2.0258 | 0.10053
5190 | 2.0258 | 0.10055
5191 | 2.0258 | 0.10057
5192 | 2.0257 | 0.10059
5193 | 2.0257 | 0.10061
5194 | 2.0257 | 0.10063
5195 | 2.0256 | 0.10064
5196 | 2.0256 | 0.10066
5197 | 2.0256 | 0.10068
5198 | 2.0256 | 0.1007
5199 | 2.0255 | 0.10072
5200 | 2.0255 | 0.10074
5201 | 2.0255 | 0.10076
5202 | 2.0255 | 0.10077
5203 | 2.0254 | 0.10079
5204 | 2.0254 | 0.10081
5205 | 2.0254 | 0.10083
5206 | 2.0253 | 0.10085
5207 | 2.0253 | 0.10087
5208 | 2.0253 | 0.10088
5209 | 2.0253 | 0.1009
5210 | 2.0252 | 0.10092
5211 | 2.0252 | 0.10094
5212 | 2.0252 | 0.10096
5213 | 2.0252 | 0.10098
5214 | 2.0251 | 0.10099
5215 | 2.0251 | 0.10101
5216 | 2.0251 | 0.10103
5217 | 2.025 | 0.10105
5218 | 2.025 | 0.10107
5219 | 2.025 | 0.10109
5220 | 2.025 | 0.1011
5221 | 2.0249 | 0.10112
5222 | 2.0249 | 0.10114
5223 | 2.0249 | 0.10116
5224 | 2.0248 | 0.10118
5225 | 2.0248 | 0.1012
5226 | 2.0248 | 0.10121
5227 | 2.0248 | 0.10123
5228 | 2.0247 | 0.10125
5229 | 2.0247 | 0.10127
5230 | 2.0247 | 0.10129
5231 | 2.0247 | 0.10131
5232 | 2.0246 | 0.10132
5233 | 2.0246 | 0.10134
5234 | 2.0246 | 0.10136
5235 | 2.0245 | 0.10138
5236 | 2.0245 | 0.1014
5237 | 2.0245 | 0.10142
5238 | 2.0245 | 0.10143
5239 | 2.0244 | 0.10145
5240 | 2.0244 | 0.10147
5241 | 2.0244 | 0.10149
5242 | 2.0244 | 0.10151
5243 | 2.0243 | 0.10153
5244 | 2.0243 | 0.10154
5245 | 2.0243 | 0.10156
5246 | 2.0242 | 0.10158
5247 | 2.0242 | 0.1016
5248 | 2.0242 | 0.10162
5249 | 2.0242 | 0.10164
5250 | 2.0241 | 0.10166
5251 | 2.0241 | 0.10167
5252 | 2.0241 | 0.10169
5253 | 2.0241 | 0.10171
5254 | 2.024 | 0.10173
5255 | 2.024 | 0.10175
5256 | 2.024 | 0.10177
5257 | 2.0239 | 0.10178
5258 | 2.0239 | 0.1018
5259 | 2.0239 | 0.10182
5260 | 2.0239 | 0.10184
5261 | 2.0238 | 0.10186
5262 | 2.0238 | 0.10188
5263 | 2.0238 | 0.10189
5264 | 2.0238 | 0.10191
5265 | 2.0237 | 0.10193
5266 | 2.0237 | 0.10195
5267 | 2.0237 | 0.10197
5268 | 2.0236 | 0.10199
5269 | 2.0236 | 0.102
5270 | 2.0236 | 0.10202
5271 | 2.0236 | 0.10204
5272 | 2.0235 | 0.10206
5273 | 2.0235 | 0.10208
5274 | 2.0235 | 0.1021
5275 | 2.0235 | 0.10211
5276 | 2.0234 | 0.10213
5277 | 2.0234 | 0.10215
5278 | 2.0234 | 0.10217
5279 | 2.0233 | 0.10219
5280 | 2.0233 | 0.10221
5281 | 2.0233 | 0.10222
5282 | 2.0233 | 0.10224
5283 | 2.0232 | 0.10226
5284 | 2.0232 | 0.10228
5285 | 2.0232 | 0.1023
5286 | 2.0232 | 0.10232
5287 | 2.0231 | 0.10233
5288 | 2.0231 | 0.10235
5289 | 2.0231 | 0.10237
5290 | 2.023 | 0.10239
5291 | 2.023 | 0.10241
5292 | 2.023 | 0.10243
5293 | 2.023 | 0.10244
5294 | 2.0229 | 0.10246
5295 | 2.0229 | 0.10248
5296 | 2.0229 | 0.1025
5297 | 2.0228 | 0.10252
5298 | 2.0228 | 0.10254
5299 | 2.0228 | 0.10255
5300 | 2.0228 | 0.10257
5301 | 2.0227 | 0.10259
5302 | 2.0227 | 0.10261
5303 | 2.0227 | 0.10263
5304 | 2.0227 | 0.10265
5305 | 2.0226 | 0.10266
5306 | 2.0226 | 0.10268
5307 | 2.0226 | 0.1027
5308 | 2.0225 | 0.10272
5309 | 2.0225 | 0.10274
5310 | 2.0225 | 0.10276
5311 | 2.0225 | 0.10277
5312 | 2.0224 | 0.10279
5313 | 2.0224 | 0.10281
5314 | 2.0224 | 0.10283
5315 | 2.0224 | 0.10285
5316 | 2.0223 | 0.10287
5317 | 2.0223 | 0.10288
5318 | 2.0223 | 0.1029
5319 | 2.0222 | 0.10292
5320 | 2.0222 | 0.10294
5321 | 2.0222 | 0.10296
5322 | 2.0222 | 0.10298
5323 | 2.0221 | 0.10299
5324 | 2.0221 | 0.10301
5325 | 2.0221 | 0.10303
5326 | 2.0221 | 0.10305
5327 | 2.022 | 0.10307
5328 | 2.022 | 0.10309
5329 | 2.022 | 0.1031
5330 | 2.0219 | 0.10312
5331 | 2.0219 | 0.10314
5332 | 2.0219 | 0.10316
5333 | 2.0219 | 0.10318
5334 | 2.0218 | 0.1032
5335 | 2.0218 | 0.10321
5336 | 2.0218 | 0.10323
5337 | 2.0218 | 0.10325
5338 | 2.0217 | 0.10327
5339 | 2.0217 | 0.10329
5340 | 2.0217 | 0.10331
5341 | 2.0216 | 0.10332
5342 | 2.0216 | 0.10334
5343 | 2.0216 | 0.10336
5344 | 2.0216 | 0.10338
5345 | 2.0215 | 0.1034
5346 | 2.0215 | 0.10342
5347 | 2.0215 | 0.10343
5348 | 2.0215 | 0.10345
5349 | 2.0214 | 0.10347
5350 | 2.0214 | 0.10349
5351 | 2.0214 | 0.10351
5352 | 2.0213 | 0.10353
5353 | 2.0213 | 0.10354
5354 | 2.0213 | 0.10356
5355 | 2.0213 | 0.10358
5356 | 2.0212 | 0.1036
5357 | 2.0212 | 0.10362
5358 | 2.0212 | 0.10364
5359 | 2.0212 | 0.10365
5360 | 2.0211 | 0.10367
5361 | 2.0211 | 0.10369
5362 | 2.0211 | 0.10371
5363 | 2.021 | 0.10373
5364 | 2.021 | 0.10375
5365 | 2.021 | 0.10376
5366 | 2.021 | 0.10378
5367 | 2.0209 | 0.1038
5368 | 2.0209 | 0.10382
5369 | 2.0209 | 0.10384
5370 | 2.0209 | 0.10386
5371 | 2.0208 | 0.10387
5372 | 2.0208 | 0.10389
5373 | 2.0208 | 0.10391
5374 | 2.0207 | 0.10393
5375 | 2.0207 | 0.10395
5376 | 2.0207 | 0.10397
5377 | 2.0207 | 0.10398
5378 | 2.0206 | 0.104
5379 | 2.0206 | 0.10402
5380 | 2.0206 | 0.10404
5381 | 2.0206 | 0.10406
5382 | 2.0205 | 0.10408
5383 | 2.0205 | 0.10409
5384 | 2.0205 | 0.10411
5385 | 2.0204 | 0.10413
5386 | 2.0204 | 0.10415
5387 | 2.0204 | 0.10417
5388 | 2.0204 | 0.10419
5389 | 2.0203 | 0.1042
5390 | 2.0203 | 0.10422
5391 | 2.0203 | 0.10424
5392 | 2.0203 | 0.10426
5393 | 2.0202 | 0.10428
5394 | 2.0202 | 0.1043
5395 | 2.0202 | 0.10431
5396 | 2.0201 | 0.10433
5397 | 2.0201 | 0.10435
5398 | 2.0201 | 0.10437
5399 | 2.0201 | 0.10439
5400 | 2.02 | 0.10441
5401 | 2.02 | 0.10442
5402 | 2.02 | 0.10444
5403 | 2.02 | 0.10446
5404 | 2.0199 | 0.10448
5405 | 2.0199 | 0.1045
5406 | 2.0199 | 0.10452
5407 | 2.0199 | 0.10453
5408 | 2.0198 | 0.10455
5409 | 2.0198 | 0.10457
5410 | 2.0198 | 0.10459
5411 | 2.0197 | 0.10461
5412 | 2.0197 | 0.10462
5413 | 2.0197 | 0.10464
5414 | 2.0197 | 0.10466
5415 | 2.0196 | 0.10468
5416 | 2.0196 | 0.1047
5417 | 2.0196 | 0.10472
5418 | 2.0196 | 0.10473
5419 | 2.0195 | 0.10475
5420 | 2.0195 | 0.10477
5421 | 2.0195 | 0.10479
5422 | 2.0194 | 0.10481
5423 | 2.0194 | 0.10483
5424 | 2.0194 | 0.10484
5425 | 2.0194 | 0.10486
5426 | 2.0193 | 0.10488
5427 | 2.0193 | 0.1049
5428 | 2.0193 | 0.10492
5429 | 2.0193 | 0.10494
5430 | 2.0192 | 0.10495
5431 | 2.0192 | 0.10497
5432 | 2.0192 | 0.10499
5433 | 2.0191 | 0.10501
5434 | 2.0191 | 0.10503
5435 | 2.0191 | 0.10505
5436 | 2.0191 | 0.10506
5437 | 2.019 | 0.10508
5438 | 2.019 | 0.1051
5439 | 2.019 | 0.10512
5440 | 2.019 | 0.10514
5441 | 2.0189 | 0.10516
5442 | 2.0189 | 0.10517
5443 | 2.0189 | 0.10519
5444 | 2.0188 | 0.10521
5445 | 2.0188 | 0.10523
5446 | 2.0188 | 0.10525
5447 | 2.0188 | 0.10527
5448 | 2.0187 | 0.10528
5449 | 2.0187 | 0.1053
5450 | 2.0187 | 0.10532
5451 | 2.0187 | 0.10534
5452 | 2.0186 | 0.10536
5453 | 2.0186 | 0.10538
5454 | 2.0186 | 0.10539
5455 | 2.0185 | 0.10541
5456 | 2.0185 | 0.10543
5457 | 2.0185 | 0.10545
5458 | 2.0185 | 0.10547
5459 | 2.0184 | 0.10548
5460 | 2.0184 | 0.1055
5461 | 2.0184 | 0.10552
5462 | 2.0184 | 0.10554
5463 | 2.0183 | 0.10556
5464 | 2.0183 | 0.10558
5465 | 2.0183 | 0.10559
5466 | 2.0182 | 0.10561
5467 | 2.0182 | 0.10563
5468 | 2.0182 | 0.10565
5469 | 2.0182 | 0.10567
5470 | 2.0181 | 0.10569
5471 | 2.0181 | 0.1057
5472 | 2.0181 | 0.10572
5473 | 2.0181 | 0.10574
5474 | 2.018 | 0.10576
5475 | 2.018 | 0.10578
5476 | 2.018 | 0.1058
5477 | 2.018 | 0.10581
5478 | 2.0179 | 0.10583
5479 | 2.0179 | 0.10585
5480 | 2.0179 | 0.10587
5481 | 2.0178 | 0.10589
5482 | 2.0178 | 0.10591
5483 | 2.0178 | 0.10592
5484 | 2.0178 | 0.10594
5485 | 2.0177 | 0.10596
5486 | 2.0177 | 0.10598
5487 | 2.0177 | 0.106
5488 | 2.0177 | 0.10602
5489 | 2.0176 | 0.10603
5490 | 2.0176 | 0.10605
5491 | 2.0176 | 0.10607
5492 | 2.0175 | 0.10609
5493 | 2.0175 | 0.10611
5494 | 2.0175 | 0.10612
5495 | 2.0175 | 0.10614
5496 | 2.0174 | 0.10616
5497 | 2.0174 | 0.10618
5498 | 2.0174 | 0.1062
5499 | 2.0174 | 0.10622
5500 | 2.0173 | 0.10623
5501 | 2.0173 | 0.10625
5502 | 2.0173 | 0.10627
5503 | 2.0172 | 0.10629
5504 | 2.0172 | 0.10631
5505 | 2.0172 | 0.10633
5506 | 2.0172 | 0.10634
5507 | 2.0171 | 0.10636
5508 | 2.0171 | 0.10638
5509 | 2.0171 | 0.1064
5510 | 2.0171 | 0.10642
5511 | 2.017 | 0.10644
5512 | 2.017 | 0.10645
5513 | 2.017 | 0.10647
5514 | 2.0169 | 0.10649
5515 | 2.0169 | 0.10651
5516 | 2.0169 | 0.10653
5517 | 2.0169 | 0.10654
5518 | 2.0168 | 0.10656
5519 | 2.0168 | 0.10658
5520 | 2.0168 | 0.1066
5521 | 2.0168 | 0.10662
5522 | 2.0167 | 0.10664
5523 | 2.0167 | 0.10665
5524 | 2.0167 | 0.10667
5525 | 2.0167 | 0.10669
5526 | 2.0166 | 0.10671
5527 | 2.0166 | 0.10673
5528 | 2.0166 | 0.10675
5529 | 2.0165 | 0.10676
5530 | 2.0165 | 0.10678
5531 | 2.0165 | 0.1068
5532 | 2.0165 | 0.10682
5533 | 2.0164 | 0.10684
5534 | 2.0164 | 0.10686
5535 | 2.0164 | 0.10687
5536 | 2.0164 | 0.10689
5537 | 2.0163 | 0.10691
5538 | 2.0163 | 0.10693
5539 | 2.0163 | 0.10695
5540 | 2.0162 | 0.10697
5541 | 2.0162 | 0.10698
5542 | 2.0162 | 0.107
5543 | 2.0162 | 0.10702
5544 | 2.0161 | 0.10704
5545 | 2.0161 | 0.10706
5546 | 2.0161 | 0.10707
5547 | 2.0161 | 0.10709
5548 | 2.016 | 0.10711
5549 | 2.016 | 0.10713
5550 | 2.016 | 0.10715
5551 | 2.0159 | 0.10717
5552 | 2.0159 | 0.10718
5553 | 2.0159 | 0.1072
5554 | 2.0159 | 0.10722
5555 | 2.0158 | 0.10724
5556 | 2.0158 | 0.10726
5557 | 2.0158 | 0.10728
5558 | 2.0158 | 0.10729
5559 | 2.0157 | 0.10731
5560 | 2.0157 | 0.10733
5561 | 2.0157 | 0.10735
5562 | 2.0157 | 0.10737
5563 | 2.0156 | 0.10739
5564 | 2.0156 | 0.1074
5565 | 2.0156 | 0.10742
5566 | 2.0155 | 0.10744
5567 | 2.0155 | 0.10746
5568 | 2.0155 | 0.10748
5569 | 2.0155 | 0.10749
5570 | 2.0154 | 0.10751
5571 | 2.0154 | 0.10753
5572 | 2.0154 | 0.10755
5573 | 2.0154 | 0.10757
5574 | 2.0153 | 0.10759
5575 | 2.0153 | 0.1076
5576 | 2.0153 | 0.10762
5577 | 2.0152 | 0.10764
5578 | 2.0152 | 0.10766
5579 | 2.0152 | 0.10768
5580 | 2.0152 | 0.1077
5581 | 2.0151 | 0.10771
5582 | 2.0151 | 0.10773
5583 | 2.0151 | 0.10775
5584 | 2.0151 | 0.10777
5585 | 2.015 | 0.10779
5586 | 2.015 | 0.1078
5587 | 2.015 | 0.10782
5588 | 2.0149 | 0.10784
5589 | 2.0149 | 0.10786
5590 | 2.0149 | 0.10788
5591 | 2.0149 | 0.1079
5592 | 2.0148 | 0.10791
5593 | 2.0148 | 0.10793
5594 | 2.0148 | 0.10795
5595 | 2.0148 | 0.10797
5596 | 2.0147 | 0.10799
5597 | 2.0147 | 0.10801
5598 | 2.0147 | 0.10802
5599 | 2.0147 | 0.10804
5600 | 2.0146 | 0.10806
5601 | 2.0146 | 0.10808
5602 | 2.0146 | 0.1081
5603 | 2.0145 | 0.10811
5604 | 2.0145 | 0.10813
5605 | 2.0145 | 0.10815
5606 | 2.0145 | 0.10817
5607 | 2.0144 | 0.10819
5608 | 2.0144 | 0.10821
5609 | 2.0144 | 0.10822
5610 | 2.0144 | 0.10824
5611 | 2.0143 | 0.10826
5612 | 2.0143 | 0.10828
5613 | 2.0143 | 0.1083
5614 | 2.0142 | 0.10832
5615 | 2.0142 | 0.10833
5616 | 2.0142 | 0.10835
5617 | 2.0142 | 0.10837
5618 | 2.0141 | 0.10839
5619 | 2.0141 | 0.10841
5620 | 2.0141 | 0.10842
5621 | 2.0141 | 0.10844
5622 | 2.014 | 0.10846
5623 | 2.014 | 0.10848
5624 | 2.014 | 0.1085
5625 | 2.014 | 0.10852
5626 | 2.0139 | 0.10853
5627 | 2.0139 | 0.10855
5628 | 2.0139 | 0.10857
5629 | 2.0138 | 0.10859
5630 | 2.0138 | 0.10861
5631 | 2.0138 | 0.10863
5632 | 2.0138 | 0.10864
5633 | 2.0137 | 0.10866
5634 | 2.0137 | 0.10868
5635 | 2.0137 | 0.1087
5636 | 2.0137 | 0.10872
5637 | 2.0136 | 0.10873
5638 | 2.0136 | 0.10875
5639 | 2.0136 | 0.10877
5640 | 2.0135 | 0.10879
5641 | 2.0135 | 0.10881
5642 | 2.0135 | 0.10883
5643 | 2.0135 | 0.10884
5644 | 2.0134 | 0.10886
5645 | 2.0134 | 0.10888
5646 | 2.0134 | 0.1089
5647 | 2.0134 | 0.10892
5648 | 2.0133 | 0.10894
5649 | 2.0133 | 0.10895
5650 | 2.0133 | 0.10897
5651 | 2.0133 | 0.10899
5652 | 2.0132 | 0.10901
5653 | 2.0132 | 0.10903
5654 | 2.0132 | 0.10904
5655 | 2.0131 | 0.10906
5656 | 2.0131 | 0.10908
5657 | 2.0131 | 0.1091
5658 | 2.0131 | 0.10912
5659 | 2.013 | 0.10914
5660 | 2.013 | 0.10915
5661 | 2.013 | 0.10917
5662 | 2.013 | 0.10919
5663 | 2.0129 | 0.10921
5664 | 2.0129 | 0.10923
5665 | 2.0129 | 0.10925
5666 | 2.0129 | 0.10926
5667 | 2.0128 | 0.10928
5668 | 2.0128 | 0.1093
5669 | 2.0128 | 0.10932
5670 | 2.0127 | 0.10934
5671 | 2.0127 | 0.10935
5672 | 2.0127 | 0.10937
5673 | 2.0127 | 0.10939
5674 | 2.0126 | 0.10941
5675 | 2.0126 | 0.10943
5676 | 2.0126 | 0.10945
5677 | 2.0126 | 0.10946
5678 | 2.0125 | 0.10948
5679 | 2.0125 | 0.1095
5680 | 2.0125 | 0.10952
5681 | 2.0124 | 0.10954
5682 | 2.0124 | 0.10955
5683 | 2.0124 | 0.10957
5684 | 2.0124 | 0.10959
5685 | 2.0123 | 0.10961
5686 | 2.0123 | 0.10963
5687 | 2.0123 | 0.10965
5688 | 2.0123 | 0.10966
5689 | 2.0122 | 0.10968
5690 | 2.0122 | 0.1097
5691 | 2.0122 | 0.10972
5692 | 2.0122 | 0.10974
5693 | 2.0121 | 0.10976
5694 | 2.0121 | 0.10977
5695 | 2.0121 | 0.10979
5696 | 2.012 | 0.10981
5697 | 2.012 | 0.10983
5698 | 2.012 | 0.10985
5699 | 2.012 | 0.10986
5700 | 2.0119 | 0.10988
5701 | 2.0119 | 0.1099
5702 | 2.0119 | 0.10992
5703 | 2.0119 | 0.10994
5704 | 2.0118 | 0.10996
5705 | 2.0118 | 0.10997
5706 | 2.0118 | 0.10999
5707 | 2.0118 | 0.11001
5708 | 2.0117 | 0.11003
5709 | 2.0117 | 0.11005
5710 | 2.0117 | 0.11006
5711 | 2.0116 | 0.11008
5712 | 2.0116 | 0.1101
5713 | 2.0116 | 0.11012
5714 | 2.0116 | 0.11014
5715 | 2.0115 | 0.11016
5716 | 2.0115 | 0.11017
5717 | 2.0115 | 0.11019
5718 | 2.0115 | 0.11021
5719 | 2.0114 | 0.11023
5720 | 2.0114 | 0.11025
5721 | 2.0114 | 0.11026
5722 | 2.0113 | 0.11028
5723 | 2.0113 | 0.1103
5724 | 2.0113 | 0.11032
5725 | 2.0113 | 0.11034
5726 | 2.0112 | 0.11036
5727 | 2.0112 | 0.11037
5728 | 2.0112 | 0.11039
5729 | 2.0112 | 0.11041
5730 | 2.0111 | 0.11043
5731 | 2.0111 | 0.11045
5732 | 2.0111 | 0.11046
5733 | 2.0111 | 0.11048
5734 | 2.011 | 0.1105
5735 | 2.011 | 0.11052
5736 | 2.011 | 0.11054
5737 | 2.0109 | 0.11056
5738 | 2.0109 | 0.11057
5739 | 2.0109 | 0.11059
5740 | 2.0109 | 0.11061
5741 | 2.0108 | 0.11063
5742 | 2.0108 | 0.11065
5743 | 2.0108 | 0.11067
5744 | 2.0108 | 0.11068
5745 | 2.0107 | 0.1107
5746 | 2.0107 | 0.11072
5747 | 2.0107 | 0.11074
5748 | 2.0107 | 0.11076
5749 | 2.0106 | 0.11077
5750 | 2.0106 | 0.11079
5751 | 2.0106 | 0.11081
5752 | 2.0105 | 0.11083
5753 | 2.0105 | 0.11085
5754 | 2.0105 | 0.11087
5755 | 2.0105 | 0.11088
5756 | 2.0104 | 0.1109
5757 | 2.0104 | 0.11092
5758 | 2.0104 | 0.11094
5759 | 2.0104 | 0.11096
5760 | 2.0103 | 0.11097
5761 | 2.0103 | 0.11099
5762 | 2.0103 | 0.11101
5763 | 2.0103 | 0.11103
5764 | 2.0102 | 0.11105
5765 | 2.0102 | 0.11107
5766 | 2.0102 | 0.11108
5767 | 2.0101 | 0.1111
5768 | 2.0101 | 0.11112
5769 | 2.0101 | 0.11114
5770 | 2.0101 | 0.11116
5771 | 2.01 | 0.11117
5772 | 2.01 | 0.11119
5773 | 2.01 | 0.11121
5774 | 2.01 | 0.11123
5775 | 2.0099 | 0.11125
5776 | 2.0099 | 0.11127
5777 | 2.0099 | 0.11128
5778 | 2.0099 | 0.1113
5779 | 2.0098 | 0.11132
5780 | 2.0098 | 0.11134
5781 | 2.0098 | 0.11136
5782 | 2.0097 | 0.11137
5783 | 2.0097 | 0.11139
5784 | 2.0097 | 0.11141
5785 | 2.0097 | 0.11143
5786 | 2.0096 | 0.11145
5787 | 2.0096 | 0.11147
5788 | 2.0096 | 0.11148
5789 | 2.0096 | 0.1115
5790 | 2.0095 | 0.11152
5791 | 2.0095 | 0.11154
5792 | 2.0095 | 0.11156
5793 | 2.0094 | 0.11157
5794 | 2.0094 | 0.11159
5795 | 2.0094 | 0.11161
5796 | 2.0094 | 0.11163
5797 | 2.0093 | 0.11165
5798 | 2.0093 | 0.11167
5799 | 2.0093 | 0.11168
5800 | 2.0093 | 0.1117
5801 | 2.0092 | 0.11172
5802 | 2.0092 | 0.11174
5803 | 2.0092 | 0.11176
5804 | 2.0092 | 0.11177
5805 | 2.0091 | 0.11179
5806 | 2.0091 | 0.11181
5807 | 2.0091 | 0.11183
5808 | 2.009 | 0.11185
5809 | 2.009 | 0.11187
5810 | 2.009 | 0.11188
5811 | 2.009 | 0.1119
5812 | 2.0089 | 0.11192
5813 | 2.0089 | 0.11194
5814 | 2.0089 | 0.11196
5815 | 2.0089 | 0.11197
5816 | 2.0088 | 0.11199
5817 | 2.0088 | 0.11201
5818 | 2.0088 | 0.11203
5819 | 2.0088 | 0.11205
5820 | 2.0087 | 0.11206
5821 | 2.0087 | 0.11208
5822 | 2.0087 | 0.1121
5823 | 2.0086 | 0.11212
5824 | 2.0086 | 0.11214
5825 | 2.0086 | 0.11216
5826 | 2.0086 | 0.11217
5827 | 2.0085 | 0.11219
5828 | 2.0085 | 0.11221
5829 | 2.0085 | 0.11223
5830 | 2.0085 | 0.11225
5831 | 2.0084 | 0.11226
5832 | 2.0084 | 0.11228
5833 | 2.0084 | 0.1123
5834 | 2.0084 | 0.11232
5835 | 2.0083 | 0.11234
5836 | 2.0083 | 0.11236
5837 | 2.0083 | 0.11237
5838 | 2.0082 | 0.11239
5839 | 2.0082 | 0.11241
5840 | 2.0082 | 0.11243
5841 | 2.0082 | 0.11245
5842 | 2.0081 | 0.11246
5843 | 2.0081 | 0.11248
5844 | 2.0081 | 0.1125
5845 | 2.0081 | 0.11252
5846 | 2.008 | 0.11254
5847 | 2.008 | 0.11256
5848 | 2.008 | 0.11257
5849 | 2.008 | 0.11259
5850 | 2.0079 | 0.11261
5851 | 2.0079 | 0.11263
5852 | 2.0079 | 0.11265
5853 | 2.0078 | 0.11266
5854 | 2.0078 | 0.11268
5855 | 2.0078 | 0.1127
5856 | 2.0078 | 0.11272
5857 | 2.0077 | 0.11274
5858 | 2.0077 | 0.11276
5859 | 2.0077 | 0.11277
5860 | 2.0077 | 0.11279
5861 | 2.0076 | 0.11281
5862 | 2.0076 | 0.11283
5863 | 2.0076 | 0.11285
5864 | 2.0076 | 0.11286
5865 | 2.0075 | 0.11288
5866 | 2.0075 | 0.1129
5867 | 2.0075 | 0.11292
5868 | 2.0075 | 0.11294
5869 | 2.0074 | 0.11295
5870 | 2.0074 | 0.11297
5871 | 2.0074 | 0.11299
5872 | 2.0073 | 0.11301
5873 | 2.0073 | 0.11303
5874 | 2.0073 | 0.11305
5875 | 2.0073 | 0.11306
5876 | 2.0072 | 0.11308
5877 | 2.0072 | 0.1131
5878 | 2.0072 | 0.11312
5879 | 2.0072 | 0.11314
5880 | 2.0071 | 0.11315
5881 | 2.0071 | 0.11317
5882 | 2.0071 | 0.11319
5883 | 2.0071 | 0.11321
5884 | 2.007 | 0.11323
5885 | 2.007 | 0.11325
5886 | 2.007 | 0.11326
5887 | 2.0069 | 0.11328
5888 | 2.0069 | 0.1133
5889 | 2.0069 | 0.11332
5890 | 2.0069 | 0.11334
5891 | 2.0068 | 0.11335
5892 | 2.0068 | 0.11337
5893 | 2.0068 | 0.11339
5894 | 2.0068 | 0.11341
5895 | 2.0067 | 0.11343
5896 | 2.0067 | 0.11344
5897 | 2.0067 | 0.11346
5898 | 2.0067 | 0.11348
5899 | 2.0066 | 0.1135
5900 | 2.0066 | 0.11352
5901 | 2.0066 | 0.11354
5902 | 2.0065 | 0.11355
5903 | 2.0065 | 0.11357
5904 | 2.0065 | 0.11359
5905 | 2.0065 | 0.11361
5906 | 2.0064 | 0.11363
5907 | 2.0064 | 0.11364
5908 | 2.0064 | 0.11366
5909 | 2.0064 | 0.11368
5910 | 2.0063 | 0.1137
5911 | 2.0063 | 0.11372
5912 | 2.0063 | 0.11373
5913 | 2.0063 | 0.11375
5914 | 2.0062 | 0.11377
5915 | 2.0062 | 0.11379
5916 | 2.0062 | 0.11381
5917 | 2.0061 | 0.11383
5918 | 2.0061 | 0.11384
5919 | 2.0061 | 0.11386
5920 | 2.0061 | 0.11388
5921 | 2.006 | 0.1139
5922 | 2.006 | 0.11392
5923 | 2.006 | 0.11393
5924 | 2.006 | 0.11395
5925 | 2.0059 | 0.11397
5926 | 2.0059 | 0.11399
5927 | 2.0059 | 0.11401
5928 | 2.0059 | 0.11403
5929 | 2.0058 | 0.11404
5930 | 2.0058 | 0.11406
5931 | 2.0058 | 0.11408
5932 | 2.0058 | 0.1141
5933 | 2.0057 | 0.11412
5934 | 2.0057 | 0.11413
5935 | 2.0057 | 0.11415
5936 | 2.0056 | 0.11417
5937 | 2.0056 | 0.11419
5938 | 2.0056 | 0.11421
5939 | 2.0056 | 0.11422
5940 | 2.0055 | 0.11424
5941 | 2.0055 | 0.11426
5942 | 2.0055 | 0.11428
5943 | 2.0055 | 0.1143
5944 | 2.0054 | 0.11432
5945 | 2.0054 | 0.11433
5946 | 2.0054 | 0.11435
5947 | 2.0054 | 0.11437
5948 | 2.0053 | 0.11439
5949 | 2.0053 | 0.11441
5950 | 2.0053 | 0.11442
5951 | 2.0052 | 0.11444
5952 | 2.0052 | 0.11446
5953 | 2.0052 | 0.11448
5954 | 2.0052 | 0.1145
5955 | 2.0051 | 0.11451
5956 | 2.0051 | 0.11453
5957 | 2.0051 | 0.11455
5958 | 2.0051 | 0.11457
5959 | 2.005 | 0.11459
5960 | 2.005 | 0.11461
5961 | 2.005 | 0.11462
5962 | 2.005 | 0.11464
5963 | 2.0049 | 0.11466
5964 | 2.0049 | 0.11468
5965 | 2.0049 | 0.1147
5966 | 2.0048 | 0.11471
5967 | 2.0048 | 0.11473
5968 | 2.0048 | 0.11475
5969 | 2.0048 | 0.11477
5970 | 2.0047 | 0.11479
5971 | 2.0047 | 0.1148
5972 | 2.0047 | 0.11482
5973 | 2.0047 | 0.11484
5974 | 2.0046 | 0.11486
5975 | 2.0046 | 0.11488
5976 | 2.0046 | 0.11489
5977 | 2.0046 | 0.11491
5978 | 2.0045 | 0.11493
5979 | 2.0045 | 0.11495
5980 | 2.0045 | 0.11497
5981 | 2.0045 | 0.11499
5982 | 2.0044 | 0.115
5983 | 2.0044 | 0.11502
5984 | 2.0044 | 0.11504
5985 | 2.0043 | 0.11506
5986 | 2.0043 | 0.11508
5987 | 2.0043 | 0.11509
5988 | 2.0043 | 0.11511
5989 | 2.0042 | 0.11513
5990 | 2.0042 | 0.11515
5991 | 2.0042 | 0.11517
5992 | 2.0042 | 0.11518
5993 | 2.0041 | 0.1152
5994 | 2.0041 | 0.11522
5995 | 2.0041 | 0.11524
5996 | 2.0041 | 0.11526
5997 | 2.004 | 0.11528
5998 | 2.004 | 0.11529
5999 | 2.004 | 0.11531
6000 | 2.0039 | 0.11533
6001 | 2.0039 | 0.11535
6002 | 2.0039 | 0.11537
6003 | 2.0039 | 0.11538
6004 | 2.0038 | 0.1154
6005 | 2.0038 | 0.11542
6006 | 2.0038 | 0.11544
6007 | 2.0038 | 0.11546
6008 | 2.0037 | 0.11547
6009 | 2.0037 | 0.11549
6010 | 2.0037 | 0.11551
6011 | 2.0037 | 0.11553
6012 | 2.0036 | 0.11555
6013 | 2.0036 | 0.11557
6014 | 2.0036 | 0.11558
6015 | 2.0036 | 0.1156
6016 | 2.0035 | 0.11562
6017 | 2.0035 | 0.11564
6018 | 2.0035 | 0.11566
6019 | 2.0034 | 0.11567
6020 | 2.0034 | 0.11569
6021 | 2.0034 | 0.11571
6022 | 2.0034 | 0.11573
6023 | 2.0033 | 0.11575
6024 | 2.0033 | 0.11576
6025 | 2.0033 | 0.11578
6026 | 2.0033 | 0.1158
6027 | 2.0032 | 0.11582
6028 | 2.0032 | 0.11584
6029 | 2.0032 | 0.11585
6030 | 2.0032 | 0.11587
6031 | 2.0031 | 0.11589
6032 | 2.0031 | 0.11591
6033 | 2.0031 | 0.11593
6034 | 2.0031 | 0.11595
6035 | 2.003 | 0.11596
6036 | 2.003 | 0.11598
6037 | 2.003 | 0.116
6038 | 2.0029 | 0.11602
6039 | 2.0029 | 0.11604
6040 | 2.0029 | 0.11605
6041 | 2.0029 | 0.11607
6042 | 2.0028 | 0.11609
6043 | 2.0028 | 0.11611
6044 | 2.0028 | 0.11613
6045 | 2.0028 | 0.11614
6046 | 2.0027 | 0.11616
6047 | 2.0027 | 0.11618
6048 | 2.0027 | 0.1162
6049 | 2.0027 | 0.11622
6050 | 2.0026 | 0.11623
6051 | 2.0026 | 0.11625
6052 | 2.0026 | 0.11627
6053 | 2.0026 | 0.11629
6054 | 2.0025 | 0.11631
6055 | 2.0025 | 0.11633
6056 | 2.0025 | 0.11634
6057 | 2.0024 | 0.11636
6058 | 2.0024 | 0.11638
6059 | 2.0024 | 0.1164
6060 | 2.0024 | 0.11642
6061 | 2.0023 | 0.11643
6062 | 2.0023 | 0.11645
6063 | 2.0023 | 0.11647
6064 | 2.0023 | 0.11649
6065 | 2.0022 | 0.11651
6066 | 2.0022 | 0.11652
6067 | 2.0022 | 0.11654
6068 | 2.0022 | 0.11656
6069 | 2.0021 | 0.11658
6070 | 2.0021 | 0.1166
6071 | 2.0021 | 0.11661
6072 | 2.002 | 0.11663
6073 | 2.002 | 0.11665
6074 | 2.002 | 0.11667
6075 | 2.002 | 0.11669
6076 | 2.0019 | 0.1167
6077 | 2.0019 | 0.11672
6078 | 2.0019 | 0.11674
6079 | 2.0019 | 0.11676
6080 | 2.0018 | 0.11678
6081 | 2.0018 | 0.1168
6082 | 2.0018 | 0.11681
6083 | 2.0018 | 0.11683
6084 | 2.0017 | 0.11685
6085 | 2.0017 | 0.11687
6086 | 2.0017 | 0.11689
6087 | 2.0017 | 0.1169
6088 | 2.0016 | 0.11692
6089 | 2.0016 | 0.11694
6090 | 2.0016 | 0.11696
6091 | 2.0015 | 0.11698
6092 | 2.0015 | 0.11699
6093 | 2.0015 | 0.11701
6094 | 2.0015 | 0.11703
6095 | 2.0014 | 0.11705
6096 | 2.0014 | 0.11707
6097 | 2.0014 | 0.11708
6098 | 2.0014 | 0.1171
6099 | 2.0013 | 0.11712
6100 | 2.0013 | 0.11714
6101 | 2.0013 | 0.11716
6102 | 2.0013 | 0.11717
6103 | 2.0012 | 0.11719
6104 | 2.0012 | 0.11721
6105 | 2.0012 | 0.11723
6106 | 2.0012 | 0.11725
6107 | 2.0011 | 0.11727
6108 | 2.0011 | 0.11728
6109 | 2.0011 | 0.1173
6110 | 2.001 | 0.11732
6111 | 2.001 | 0.11734
6112 | 2.001 | 0.11736
6113 | 2.001 | 0.11737
6114 | 2.0009 | 0.11739
6115 | 2.0009 | 0.11741
6116 | 2.0009 | 0.11743
6117 | 2.0009 | 0.11745
6118 | 2.0008 | 0.11746
6119 | 2.0008 | 0.11748
6120 | 2.0008 | 0.1175
6121 | 2.0008 | 0.11752
6122 | 2.0007 | 0.11754
6123 | 2.0007 | 0.11755
6124 | 2.0007 | 0.11757
6125 | 2.0007 | 0.11759
6126 | 2.0006 | 0.11761
6127 | 2.0006 | 0.11763
6128 | 2.0006 | 0.11764
6129 | 2.0005 | 0.11766
6130 | 2.0005 | 0.11768
6131 | 2.0005 | 0.1177
6132 | 2.0005 | 0.11772
6133 | 2.0004 | 0.11774
6134 | 2.0004 | 0.11775
6135 | 2.0004 | 0.11777
6136 | 2.0004 | 0.11779
6137 | 2.0003 | 0.11781
6138 | 2.0003 | 0.11783
6139 | 2.0003 | 0.11784
6140 | 2.0003 | 0.11786
6141 | 2.0002 | 0.11788
6142 | 2.0002 | 0.1179
6143 | 2.0002 | 0.11792
6144 | 2.0002 | 0.11793
6145 | 2.0001 | 0.11795
6146 | 2.0001 | 0.11797
6147 | 2.0001 | 0.11799
6148 | 2.0001 | 0.11801
6149 | 2 | 0.11802
6150 | 2 | 0.11804
6151 | 2 | 0.11806
6152 | 1.9999 | 0.11808
6153 | 1.9999 | 0.1181
6154 | 1.9999 | 0.11811
6155 | 1.9999 | 0.11813
6156 | 1.9998 | 0.11815
6157 | 1.9998 | 0.11817
6158 | 1.9998 | 0.11819
6159 | 1.9998 | 0.1182
6160 | 1.9997 | 0.11822
6161 | 1.9997 | 0.11824
6162 | 1.9997 | 0.11826
6163 | 1.9997 | 0.11828
6164 | 1.9996 | 0.11829
6165 | 1.9996 | 0.11831
6166 | 1.9996 | 0.11833
6167 | 1.9996 | 0.11835
6168 | 1.9995 | 0.11837
6169 | 1.9995 | 0.11839
6170 | 1.9995 | 0.1184
6171 | 1.9994 | 0.11842
6172 | 1.9994 | 0.11844
6173 | 1.9994 | 0.11846
6174 | 1.9994 | 0.11848
6175 | 1.9993 | 0.11849
6176 | 1.9993 | 0.11851
6177 | 1.9993 | 0.11853
6178 | 1.9993 | 0.11855
6179 | 1.9992 | 0.11857
6180 | 1.9992 | 0.11858
6181 | 1.9992 | 0.1186
6182 | 1.9992 | 0.11862
6183 | 1.9991 | 0.11864
6184 | 1.9991 | 0.11866
6185 | 1.9991 | 0.11867
6186 | 1.9991 | 0.11869
6187 | 1.999 | 0.11871
6188 | 1.999 | 0.11873
6189 | 1.999 | 0.11875
6190 | 1.9989 | 0.11876
6191 | 1.9989 | 0.11878
6192 | 1.9989 | 0.1188
6193 | 1.9989 | 0.11882
6194 | 1.9988 | 0.11884
6195 | 1.9988 | 0.11885
6196 | 1.9988 | 0.11887
6197 | 1.9988 | 0.11889
6198 | 1.9987 | 0.11891
6199 | 1.9987 | 0.11893
6200 | 1.9987 | 0.11894
6201 | 1.9987 | 0.11896
6202 | 1.9986 | 0.11898
6203 | 1.9986 | 0.119
6204 | 1.9986 | 0.11902
6205 | 1.9986 | 0.11903
6206 | 1.9985 | 0.11905
6207 | 1.9985 | 0.11907
6208 | 1.9985 | 0.11909
6209 | 1.9985 | 0.11911
6210 | 1.9984 | 0.11912
6211 | 1.9984 | 0.11914
6212 | 1.9984 | 0.11916
6213 | 1.9983 | 0.11918
6214 | 1.9983 | 0.1192
6215 | 1.9983 | 0.11922
6216 | 1.9983 | 0.11923
6217 | 1.9982 | 0.11925
6218 | 1.9982 | 0.11927
6219 | 1.9982 | 0.11929
6220 | 1.9982 | 0.11931
6221 | 1.9981 | 0.11932
6222 | 1.9981 | 0.11934
6223 | 1.9981 | 0.11936
6224 | 1.9981 | 0.11938
6225 | 1.998 | 0.1194
6226 | 1.998 | 0.11941
6227 | 1.998 | 0.11943
6228 | 1.998 | 0.11945
6229 | 1.9979 | 0.11947
6230 | 1.9979 | 0.11949
6231 | 1.9979 | 0.1195
6232 | 1.9978 | 0.11952
6233 | 1.9978 | 0.11954
6234 | 1.9978 | 0.11956
6235 | 1.9978 | 0.11958
6236 | 1.9977 | 0.11959
6237 | 1.9977 | 0.11961
6238 | 1.9977 | 0.11963
6239 | 1.9977 | 0.11965
6240 | 1.9976 | 0.11967
6241 | 1.9976 | 0.11968
6242 | 1.9976 | 0.1197
6243 | 1.9976 | 0.11972
6244 | 1.9975 | 0.11974
6245 | 1.9975 | 0.11976
6246 | 1.9975 | 0.11977
6247 | 1.9975 | 0.11979
6248 | 1.9974 | 0.11981
6249 | 1.9974 | 0.11983
6250 | 1.9974 | 0.11985
6251 | 1.9974 | 0.11986
6252 | 1.9973 | 0.11988
6253 | 1.9973 | 0.1199
6254 | 1.9973 | 0.11992
6255 | 1.9972 | 0.11994
6256 | 1.9972 | 0.11995
6257 | 1.9972 | 0.11997
6258 | 1.9972 | 0.11999
6259 | 1.9971 | 0.12001
6260 | 1.9971 | 0.12003
6261 | 1.9971 | 0.12004
6262 | 1.9971 | 0.12006
6263 | 1.997 | 0.12008
6264 | 1.997 | 0.1201
6265 | 1.997 | 0.12012
6266 | 1.997 | 0.12013
6267 | 1.9969 | 0.12015
6268 | 1.9969 | 0.12017
6269 | 1.9969 | 0.12019
6270 | 1.9969 | 0.12021
6271 | 1.9968 | 0.12022
6272 | 1.9968 | 0.12024
6273 | 1.9968 | 0.12026
6274 | 1.9968 | 0.12028
6275 | 1.9967 | 0.1203
6276 | 1.9967 | 0.12031
6277 | 1.9967 | 0.12033
6278 | 1.9966 | 0.12035
6279 | 1.9966 | 0.12037
6280 | 1.9966 | 0.12039
6281 | 1.9966 | 0.1204
6282 | 1.9965 | 0.12042
6283 | 1.9965 | 0.12044
6284 | 1.9965 | 0.12046
6285 | 1.9965 | 0.12048
6286 | 1.9964 | 0.12049
6287 | 1.9964 | 0.12051
6288 | 1.9964 | 0.12053
6289 | 1.9964 | 0.12055
6290 | 1.9963 | 0.12057
6291 | 1.9963 | 0.12058
6292 | 1.9963 | 0.1206
6293 | 1.9963 | 0.12062
6294 | 1.9962 | 0.12064
6295 | 1.9962 | 0.12066
6296 | 1.9962 | 0.12068
6297 | 1.9962 | 0.12069
6298 | 1.9961 | 0.12071
6299 | 1.9961 | 0.12073
6300 | 1.9961 | 0.12075
6301 | 1.996 | 0.12077
6302 | 1.996 | 0.12078
6303 | 1.996 | 0.1208
6304 | 1.996 | 0.12082
6305 | 1.9959 | 0.12084
6306 | 1.9959 | 0.12086
6307 | 1.9959 | 0.12087
6308 | 1.9959 | 0.12089
6309 | 1.9958 | 0.12091
6310 | 1.9958 | 0.12093
6311 | 1.9958 | 0.12095
6312 | 1.9958 | 0.12096
6313 | 1.9957 | 0.12098
6314 | 1.9957 | 0.121
6315 | 1.9957 | 0.12102
6316 | 1.9957 | 0.12104
6317 | 1.9956 | 0.12105
6318 | 1.9956 | 0.12107
6319 | 1.9956 | 0.12109
6320 | 1.9956 | 0.12111
6321 | 1.9955 | 0.12113
6322 | 1.9955 | 0.12114
6323 | 1.9955 | 0.12116
6324 | 1.9954 | 0.12118
6325 | 1.9954 | 0.1212
6326 | 1.9954 | 0.12122
6327 | 1.9954 | 0.12123
6328 | 1.9953 | 0.12125
6329 | 1.9953 | 0.12127
6330 | 1.9953 | 0.12129
6331 | 1.9953 | 0.12131
6332 | 1.9952 | 0.12132
6333 | 1.9952 | 0.12134
6334 | 1.9952 | 0.12136
6335 | 1.9952 | 0.12138
6336 | 1.9951 | 0.1214
6337 | 1.9951 | 0.12141
6338 | 1.9951 | 0.12143
6339 | 1.9951 | 0.12145
6340 | 1.995 | 0.12147
6341 | 1.995 | 0.12149
6342 | 1.995 | 0.1215
6343 | 1.995 | 0.12152
6344 | 1.9949 | 0.12154
6345 | 1.9949 | 0.12156
6346 | 1.9949 | 0.12158
6347 | 1.9948 | 0.12159
6348 | 1.9948 | 0.12161
6349 | 1.9948 | 0.12163
6350 | 1.9948 | 0.12165
6351 | 1.9947 | 0.12167
6352 | 1.9947 | 0.12168
6353 | 1.9947 | 0.1217
6354 | 1.9947 | 0.12172
6355 | 1.9946 | 0.12174
6356 | 1.9946 | 0.12176
6357 | 1.9946 | 0.12177
6358 | 1.9946 | 0.12179
6359 | 1.9945 | 0.12181
6360 | 1.9945 | 0.12183
6361 | 1.9945 | 0.12184
6362 | 1.9945 | 0.12186
6363 | 1.9944 | 0.12188
6364 | 1.9944 | 0.1219
6365 | 1.9944 | 0.12192
6366 | 1.9944 | 0.12193
6367 | 1.9943 | 0.12195
6368 | 1.9943 | 0.12197
6369 | 1.9943 | 0.12199
6370 | 1.9943 | 0.12201
6371 | 1.9942 | 0.12202
6372 | 1.9942 | 0.12204
6373 | 1.9942 | 0.12206
6374 | 1.9941 | 0.12208
6375 | 1.9941 | 0.1221
6376 | 1.9941 | 0.12211
6377 | 1.9941 | 0.12213
6378 | 1.994 | 0.12215
6379 | 1.994 | 0.12217
6380 | 1.994 | 0.12219
6381 | 1.994 | 0.1222
6382 | 1.9939 | 0.12222
6383 | 1.9939 | 0.12224
6384 | 1.9939 | 0.12226
6385 | 1.9939 | 0.12228
6386 | 1.9938 | 0.12229
6387 | 1.9938 | 0.12231
6388 | 1.9938 | 0.12233
6389 | 1.9938 | 0.12235
6390 | 1.9937 | 0.12237
6391 | 1.9937 | 0.12238
6392 | 1.9937 | 0.1224
6393 | 1.9937 | 0.12242
6394 | 1.9936 | 0.12244
6395 | 1.9936 | 0.12246
6396 | 1.9936 | 0.12247
6397 | 1.9936 | 0.12249
6398 | 1.9935 | 0.12251
6399 | 1.9935 | 0.12253
6400 | 1.9935 | 0.12255
6401 | 1.9934 | 0.12256
6402 | 1.9934 | 0.12258
6403 | 1.9934 | 0.1226
6404 | 1.9934 | 0.12262
6405 | 1.9933 | 0.12264
6406 | 1.9933 | 0.12265
6407 | 1.9933 | 0.12267
6408 | 1.9933 | 0.12269
6409 | 1.9932 | 0.12271
6410 | 1.9932 | 0.12273
6411 | 1.9932 | 0.12274
6412 | 1.9932 | 0.12276
6413 | 1.9931 | 0.12278
6414 | 1.9931 | 0.1228
6415 | 1.9931 | 0.12282
6416 | 1.9931 | 0.12283
6417 | 1.993 | 0.12285
6418 | 1.993 | 0.12287
6419 | 1.993 | 0.12289
6420 | 1.993 | 0.12291
6421 | 1.9929 | 0.12292
6422 | 1.9929 | 0.12294
6423 | 1.9929 | 0.12296
6424 | 1.9929 | 0.12298
6425 | 1.9928 | 0.123
6426 | 1.9928 | 0.12301
6427 | 1.9928 | 0.12303
6428 | 1.9927 | 0.12305
6429 | 1.9927 | 0.12307
6430 | 1.9927 | 0.12309
6431 | 1.9927 | 0.1231
6432 | 1.9926 | 0.12312
6433 | 1.9926 | 0.12314
6434 | 1.9926 | 0.12316
6435 | 1.9926 | 0.12318
6436 | 1.9925 | 0.12319
6437 | 1.9925 | 0.12321
6438 | 1.9925 | 0.12323
6439 | 1.9925 | 0.12325
6440 | 1.9924 | 0.12327
6441 | 1.9924 | 0.12328
6442 | 1.9924 | 0.1233
6443 | 1.9924 | 0.12332
6444 | 1.9923 | 0.12334
6445 | 1.9923 | 0.12335
6446 | 1.9923 | 0.12337
6447 | 1.9923 | 0.12339
6448 | 1.9922 | 0.12341
6449 | 1.9922 | 0.12343
6450 | 1.9922 | 0.12344
6451 | 1.9922 | 0.12346
6452 | 1.9921 | 0.12348
6453 | 1.9921 | 0.1235
6454 | 1.9921 | 0.12352
6455 | 1.992 | 0.12353
6456 | 1.992 | 0.12355
6457 | 1.992 | 0.12357
6458 | 1.992 | 0.12359
6459 | 1.9919 | 0.12361
6460 | 1.9919 | 0.12362
6461 | 1.9919 | 0.12364
6462 | 1.9919 | 0.12366
6463 | 1.9918 | 0.12368
6464 | 1.9918 | 0.1237
6465 | 1.9918 | 0.12371
6466 | 1.9918 | 0.12373
6467 | 1.9917 | 0.12375
6468 | 1.9917 | 0.12377
6469 | 1.9917 | 0.12379
6470 | 1.9917 | 0.1238
6471 | 1.9916 | 0.12382
6472 | 1.9916 | 0.12384
6473 | 1.9916 | 0.12386
6474 | 1.9916 | 0.12388
6475 | 1.9915 | 0.12389
6476 | 1.9915 | 0.12391
6477 | 1.9915 | 0.12393
6478 | 1.9915 | 0.12395
6479 | 1.9914 | 0.12397
6480 | 1.9914 | 0.12398
6481 | 1.9914 | 0.124
6482 | 1.9913 | 0.12402
6483 | 1.9913 | 0.12404
6484 | 1.9913 | 0.12406
6485 | 1.9913 | 0.12407
6486 | 1.9912 | 0.12409
6487 | 1.9912 | 0.12411
6488 | 1.9912 | 0.12413
6489 | 1.9912 | 0.12414
6490 | 1.9911 | 0.12416
6491 | 1.9911 | 0.12418
6492 | 1.9911 | 0.1242
6493 | 1.9911 | 0.12422
6494 | 1.991 | 0.12423
6495 | 1.991 | 0.12425
6496 | 1.991 | 0.12427
6497 | 1.991 | 0.12429
6498 | 1.9909 | 0.12431
6499 | 1.9909 | 0.12432
6500 | 1.9909 | 0.12434
6501 | 1.9909 | 0.12436
6502 | 1.9908 | 0.12438
6503 | 1.9908 | 0.1244
6504 | 1.9908 | 0.12441
6505 | 1.9908 | 0.12443
6506 | 1.9907 | 0.12445
6507 | 1.9907 | 0.12447
6508 | 1.9907 | 0.12449
6509 | 1.9907 | 0.1245
6510 | 1.9906 | 0.12452
6511 | 1.9906 | 0.12454
6512 | 1.9906 | 0.12456
6513 | 1.9905 | 0.12458
6514 | 1.9905 | 0.12459
6515 | 1.9905 | 0.12461
6516 | 1.9905 | 0.12463
6517 | 1.9904 | 0.12465
6518 | 1.9904 | 0.12467
6519 | 1.9904 | 0.12468
6520 | 1.9904 | 0.1247
6521 | 1.9903 | 0.12472
6522 | 1.9903 | 0.12474
6523 | 1.9903 | 0.12475
6524 | 1.9903 | 0.12477
6525 | 1.9902 | 0.12479
6526 | 1.9902 | 0.12481
6527 | 1.9902 | 0.12483
6528 | 1.9902 | 0.12484
6529 | 1.9901 | 0.12486
6530 | 1.9901 | 0.12488
6531 | 1.9901 | 0.1249
6532 | 1.9901 | 0.12492
6533 | 1.99 | 0.12493
6534 | 1.99 | 0.12495
6535 | 1.99 | 0.12497
6536 | 1.99 | 0.12499
6537 | 1.9899 | 0.12501
6538 | 1.9899 | 0.12502
6539 | 1.9899 | 0.12504
6540 | 1.9899 | 0.12506
6541 | 1.9898 | 0.12508
6542 | 1.9898 | 0.1251
6543 | 1.9898 | 0.12511
6544 | 1.9897 | 0.12513
6545 | 1.9897 | 0.12515
6546 | 1.9897 | 0.12517
6547 | 1.9897 | 0.12519
6548 | 1.9896 | 0.1252
6549 | 1.9896 | 0.12522
6550 | 1.9896 | 0.12524
6551 | 1.9896 | 0.12526
6552 | 1.9895 | 0.12528
6553 | 1.9895 | 0.12529
6554 | 1.9895 | 0.12531
6555 | 1.9895 | 0.12533
6556 | 1.9894 | 0.12535
6557 | 1.9894 | 0.12536
6558 | 1.9894 | 0.12538
6559 | 1.9894 | 0.1254
6560 | 1.9893 | 0.12542
6561 | 1.9893 | 0.12544
6562 | 1.9893 | 0.12545
6563 | 1.9893 | 0.12547
6564 | 1.9892 | 0.12549
6565 | 1.9892 | 0.12551
6566 | 1.9892 | 0.12553
6567 | 1.9892 | 0.12554
6568 | 1.9891 | 0.12556
6569 | 1.9891 | 0.12558
6570 | 1.9891 | 0.1256
6571 | 1.9891 | 0.12562
6572 | 1.989 | 0.12563
6573 | 1.989 | 0.12565
6574 | 1.989 | 0.12567
6575 | 1.989 | 0.12569
6576 | 1.9889 | 0.12571
6577 | 1.9889 | 0.12572
6578 | 1.9889 | 0.12574
6579 | 1.9888 | 0.12576
6580 | 1.9888 | 0.12578
6581 | 1.9888 | 0.12579
6582 | 1.9888 | 0.12581
6583 | 1.9887 | 0.12583
6584 | 1.9887 | 0.12585
6585 | 1.9887 | 0.12587
6586 | 1.9887 | 0.12588
6587 | 1.9886 | 0.1259
6588 | 1.9886 | 0.12592
6589 | 1.9886 | 0.12594
6590 | 1.9886 | 0.12596
6591 | 1.9885 | 0.12597
6592 | 1.9885 | 0.12599
6593 | 1.9885 | 0.12601
6594 | 1.9885 | 0.12603
6595 | 1.9884 | 0.12605
6596 | 1.9884 | 0.12606
6597 | 1.9884 | 0.12608
6598 | 1.9884 | 0.1261
6599 | 1.9883 | 0.12612
6600 | 1.9883 | 0.12614
6601 | 1.9883 | 0.12615
6602 | 1.9883 | 0.12617
6603 | 1.9882 | 0.12619
6604 | 1.9882 | 0.12621
6605 | 1.9882 | 0.12622
6606 | 1.9882 | 0.12624
6607 | 1.9881 | 0.12626
6608 | 1.9881 | 0.12628
6609 | 1.9881 | 0.1263
6610 | 1.9881 | 0.12631
6611 | 1.988 | 0.12633
6612 | 1.988 | 0.12635
6613 | 1.988 | 0.12637
6614 | 1.9879 | 0.12639
6615 | 1.9879 | 0.1264
6616 | 1.9879 | 0.12642
6617 | 1.9879 | 0.12644
6618 | 1.9878 | 0.12646
6619 | 1.9878 | 0.12648
6620 | 1.9878 | 0.12649
6621 | 1.9878 | 0.12651
6622 | 1.9877 | 0.12653
6623 | 1.9877 | 0.12655
6624 | 1.9877 | 0.12656
6625 | 1.9877 | 0.12658
6626 | 1.9876 | 0.1266
6627 | 1.9876 | 0.12662
6628 | 1.9876 | 0.12664
6629 | 1.9876 | 0.12665
6630 | 1.9875 | 0.12667
6631 | 1.9875 | 0.12669
6632 | 1.9875 | 0.12671
6633 | 1.9875 | 0.12673
6634 | 1.9874 | 0.12674
6635 | 1.9874 | 0.12676
6636 | 1.9874 | 0.12678
6637 | 1.9874 | 0.1268
6638 | 1.9873 | 0.12682
6639 | 1.9873 | 0.12683
6640 | 1.9873 | 0.12685
6641 | 1.9873 | 0.12687
6642 | 1.9872 | 0.12689
6643 | 1.9872 | 0.12691
6644 | 1.9872 | 0.12692
6645 | 1.9872 | 0.12694
6646 | 1.9871 | 0.12696
6647 | 1.9871 | 0.12698
6648 | 1.9871 | 0.12699
6649 | 1.987 | 0.12701
6650 | 1.987 | 0.12703
6651 | 1.987 | 0.12705
6652 | 1.987 | 0.12707
6653 | 1.9869 | 0.12708
6654 | 1.9869 | 0.1271
6655 | 1.9869 | 0.12712
6656 | 1.9869 | 0.12714
6657 | 1.9868 | 0.12716
6658 | 1.9868 | 0.12717
6659 | 1.9868 | 0.12719
6660 | 1.9868 | 0.12721
6661 | 1.9867 | 0.12723
6662 | 1.9867 | 0.12725
6663 | 1.9867 | 0.12726
6664 | 1.9867 | 0.12728
6665 | 1.9866 | 0.1273
6666 | 1.9866 | 0.12732
6667 | 1.9866 | 0.12733
6668 | 1.9866 | 0.12735
6669 | 1.9865 | 0.12737
6670 | 1.9865 | 0.12739
6671 | 1.9865 | 0.12741
6672 | 1.9865 | 0.12742
6673 | 1.9864 | 0.12744
6674 | 1.9864 | 0.12746
6675 | 1.9864 | 0.12748
6676 | 1.9864 | 0.1275
6677 | 1.9863 | 0.12751
6678 | 1.9863 | 0.12753
6679 | 1.9863 | 0.12755
6680 | 1.9863 | 0.12757
6681 | 1.9862 | 0.12758
6682 | 1.9862 | 0.1276
6683 | 1.9862 | 0.12762
6684 | 1.9862 | 0.12764
6685 | 1.9861 | 0.12766
6686 | 1.9861 | 0.12767
6687 | 1.9861 | 0.12769
6688 | 1.9861 | 0.12771
6689 | 1.986 | 0.12773
6690 | 1.986 | 0.12775
6691 | 1.986 | 0.12776
6692 | 1.9859 | 0.12778
6693 | 1.9859 | 0.1278
6694 | 1.9859 | 0.12782
6695 | 1.9859 | 0.12784
6696 | 1.9858 | 0.12785
6697 | 1.9858 | 0.12787
6698 | 1.9858 | 0.12789
6699 | 1.9858 | 0.12791
6700 | 1.9857 | 0.12792
6701 | 1.9857 | 0.12794
6702 | 1.9857 | 0.12796
6703 | 1.9857 | 0.12798
6704 | 1.9856 | 0.128
6705 | 1.9856 | 0.12801
6706 | 1.9856 | 0.12803
6707 | 1.9856 | 0.12805
6708 | 1.9855 | 0.12807
6709 | 1.9855 | 0.12809
6710 | 1.9855 | 0.1281
6711 | 1.9855 | 0.12812
6712 | 1.9854 | 0.12814
6713 | 1.9854 | 0.12816
6714 | 1.9854 | 0.12818
6715 | 1.9854 | 0.12819
6716 | 1.9853 | 0.12821
6717 | 1.9853 | 0.12823
6718 | 1.9853 | 0.12825
6719 | 1.9853 | 0.12826
6720 | 1.9852 | 0.12828
6721 | 1.9852 | 0.1283
6722 | 1.9852 | 0.12832
6723 | 1.9852 | 0.12834
6724 | 1.9851 | 0.12835
6725 | 1.9851 | 0.12837
6726 | 1.9851 | 0.12839
6727 | 1.9851 | 0.12841
6728 | 1.985 | 0.12843
6729 | 1.985 | 0.12844
6730 | 1.985 | 0.12846
6731 | 1.985 | 0.12848
6732 | 1.9849 | 0.1285
6733 | 1.9849 | 0.12851
6734 | 1.9849 | 0.12853
6735 | 1.9848 | 0.12855
6736 | 1.9848 | 0.12857
6737 | 1.9848 | 0.12859
6738 | 1.9848 | 0.1286
6739 | 1.9847 | 0.12862
6740 | 1.9847 | 0.12864
6741 | 1.9847 | 0.12866
6742 | 1.9847 | 0.12868
6743 | 1.9846 | 0.12869
6744 | 1.9846 | 0.12871
6745 | 1.9846 | 0.12873
6746 | 1.9846 | 0.12875
6747 | 1.9845 | 0.12876
6748 | 1.9845 | 0.12878
6749 | 1.9845 | 0.1288
6750 | 1.9845 | 0.12882
6751 | 1.9844 | 0.12884
6752 | 1.9844 | 0.12885
6753 | 1.9844 | 0.12887
6754 | 1.9844 | 0.12889
6755 | 1.9843 | 0.12891
6756 | 1.9843 | 0.12893
6757 | 1.9843 | 0.12894
6758 | 1.9843 | 0.12896
6759 | 1.9842 | 0.12898
6760 | 1.9842 | 0.129
6761 | 1.9842 | 0.12901
6762 | 1.9842 | 0.12903
6763 | 1.9841 | 0.12905
6764 | 1.9841 | 0.12907
6765 | 1.9841 | 0.12909
6766 | 1.9841 | 0.1291
6767 | 1.984 | 0.12912
6768 | 1.984 | 0.12914
6769 | 1.984 | 0.12916
6770 | 1.984 | 0.12918
6771 | 1.9839 | 0.12919
6772 | 1.9839 | 0.12921
6773 | 1.9839 | 0.12923
6774 | 1.9839 | 0.12925
6775 | 1.9838 | 0.12926
6776 | 1.9838 | 0.12928
6777 | 1.9838 | 0.1293
6778 | 1.9838 | 0.12932
6779 | 1.9837 | 0.12934
6780 | 1.9837 | 0.12935
6781 | 1.9837 | 0.12937
6782 | 1.9836 | 0.12939
6783 | 1.9836 | 0.12941
6784 | 1.9836 | 0.12943
6785 | 1.9836 | 0.12944
6786 | 1.9835 | 0.12946
6787 | 1.9835 | 0.12948
6788 | 1.9835 | 0.1295
6789 | 1.9835 | 0.12951
6790 | 1.9834 | 0.12953
6791 | 1.9834 | 0.12955
6792 | 1.9834 | 0.12957
6793 | 1.9834 | 0.12959
6794 | 1.9833 | 0.1296
6795 | 1.9833 | 0.12962
6796 | 1.9833 | 0.12964
6797 | 1.9833 | 0.12966
6798 | 1.9832 | 0.12968
6799 | 1.9832 | 0.12969
6800 | 1.9832 | 0.12971
6801 | 1.9832 | 0.12973
6802 | 1.9831 | 0.12975
6803 | 1.9831 | 0.12976
6804 | 1.9831 | 0.12978
6805 | 1.9831 | 0.1298
6806 | 1.983 | 0.12982
6807 | 1.983 | 0.12984
6808 | 1.983 | 0.12985
6809 | 1.983 | 0.12987
6810 | 1.9829 | 0.12989
6811 | 1.9829 | 0.12991
6812 | 1.9829 | 0.12993
6813 | 1.9829 | 0.12994
6814 | 1.9828 | 0.12996
6815 | 1.9828 | 0.12998
6816 | 1.9828 | 0.13
6817 | 1.9828 | 0.13001
6818 | 1.9827 | 0.13003
6819 | 1.9827 | 0.13005
6820 | 1.9827 | 0.13007
6821 | 1.9827 | 0.13009
6822 | 1.9826 | 0.1301
6823 | 1.9826 | 0.13012
6824 | 1.9826 | 0.13014
6825 | 1.9826 | 0.13016
6826 | 1.9825 | 0.13018
6827 | 1.9825 | 0.13019
6828 | 1.9825 | 0.13021
6829 | 1.9825 | 0.13023
6830 | 1.9824 | 0.13025
6831 | 1.9824 | 0.13026
6832 | 1.9824 | 0.13028
6833 | 1.9824 | 0.1303
6834 | 1.9823 | 0.13032
6835 | 1.9823 | 0.13034
6836 | 1.9823 | 0.13035
6837 | 1.9822 | 0.13037
6838 | 1.9822 | 0.13039
6839 | 1.9822 | 0.13041
6840 | 1.9822 | 0.13042
6841 | 1.9821 | 0.13044
6842 | 1.9821 | 0.13046
6843 | 1.9821 | 0.13048
6844 | 1.9821 | 0.1305
6845 | 1.982 | 0.13051
6846 | 1.982 | 0.13053
6847 | 1.982 | 0.13055
6848 | 1.982 | 0.13057
6849 | 1.9819 | 0.13059
6850 | 1.9819 | 0.1306
6851 | 1.9819 | 0.13062
6852 | 1.9819 | 0.13064
6853 | 1.9818 | 0.13066
6854 | 1.9818 | 0.13067
6855 | 1.9818 | 0.13069
6856 | 1.9818 | 0.13071
6857 | 1.9817 | 0.13073
6858 | 1.9817 | 0.13075
6859 | 1.9817 | 0.13076
6860 | 1.9817 | 0.13078
6861 | 1.9816 | 0.1308
6862 | 1.9816 | 0.13082
6863 | 1.9816 | 0.13083
6864 | 1.9816 | 0.13085
6865 | 1.9815 | 0.13087
6866 | 1.9815 | 0.13089
6867 | 1.9815 | 0.13091
6868 | 1.9815 | 0.13092
6869 | 1.9814 | 0.13094
6870 | 1.9814 | 0.13096
6871 | 1.9814 | 0.13098
6872 | 1.9814 | 0.131
6873 | 1.9813 | 0.13101
6874 | 1.9813 | 0.13103
6875 | 1.9813 | 0.13105
6876 | 1.9813 | 0.13107
6877 | 1.9812 | 0.13108
6878 | 1.9812 | 0.1311
6879 | 1.9812 | 0.13112
6880 | 1.9812 | 0.13114
6881 | 1.9811 | 0.13116
6882 | 1.9811 | 0.13117
6883 | 1.9811 | 0.13119
6884 | 1.9811 | 0.13121
6885 | 1.981 | 0.13123
6886 | 1.981 | 0.13124
6887 | 1.981 | 0.13126
6888 | 1.981 | 0.13128
6889 | 1.9809 | 0.1313
6890 | 1.9809 | 0.13132
6891 | 1.9809 | 0.13133
6892 | 1.9809 | 0.13135
6893 | 1.9808 | 0.13137
6894 | 1.9808 | 0.13139
6895 | 1.9808 | 0.13141
6896 | 1.9808 | 0.13142
6897 | 1.9807 | 0.13144
6898 | 1.9807 | 0.13146
6899 | 1.9807 | 0.13148
6900 | 1.9806 | 0.13149
6901 | 1.9806 | 0.13151
6902 | 1.9806 | 0.13153
6903 | 1.9806 | 0.13155
6904 | 1.9805 | 0.13157
6905 | 1.9805 | 0.13158
6906 | 1.9805 | 0.1316
6907 | 1.9805 | 0.13162
6908 | 1.9804 | 0.13164
6909 | 1.9804 | 0.13165
6910 | 1.9804 | 0.13167
6911 | 1.9804 | 0.13169
6912 | 1.9803 | 0.13171
6913 | 1.9803 | 0.13173
6914 | 1.9803 | 0.13174
6915 | 1.9803 | 0.13176
6916 | 1.9802 | 0.13178
6917 | 1.9802 | 0.1318
6918 | 1.9802 | 0.13181
6919 | 1.9802 | 0.13183
6920 | 1.9801 | 0.13185
6921 | 1.9801 | 0.13187
6922 | 1.9801 | 0.13189
6923 | 1.9801 | 0.1319
6924 | 1.98 | 0.13192
6925 | 1.98 | 0.13194
6926 | 1.98 | 0.13196
6927 | 1.98 | 0.13198
6928 | 1.9799 | 0.13199
6929 | 1.9799 | 0.13201
6930 | 1.9799 | 0.13203
6931 | 1.9799 | 0.13205
6932 | 1.9798 | 0.13206
6933 | 1.9798 | 0.13208
6934 | 1.9798 | 0.1321
6935 | 1.9798 | 0.13212
6936 | 1.9797 | 0.13214
6937 | 1.9797 | 0.13215
6938 | 1.9797 | 0.13217
6939 | 1.9797 | 0.13219
6940 | 1.9796 | 0.13221
6941 | 1.9796 | 0.13222
6942 | 1.9796 | 0.13224
6943 | 1.9796 | 0.13226
6944 | 1.9795 | 0.13228
6945 | 1.9795 | 0.1323
6946 | 1.9795 | 0.13231
6947 | 1.9795 | 0.13233
6948 | 1.9794 | 0.13235
6949 | 1.9794 | 0.13237
6950 | 1.9794 | 0.13238
6951 | 1.9794 | 0.1324
6952 | 1.9793 | 0.13242
6953 | 1.9793 | 0.13244
6954 | 1.9793 | 0.13246
6955 | 1.9793 | 0.13247
6956 | 1.9792 | 0.13249
6957 | 1.9792 | 0.13251
6958 | 1.9792 | 0.13253
6959 | 1.9792 | 0.13254
6960 | 1.9791 | 0.13256
6961 | 1.9791 | 0.13258
6962 | 1.9791 | 0.1326
6963 | 1.9791 | 0.13262
6964 | 1.979 | 0.13263
6965 | 1.979 | 0.13265
6966 | 1.979 | 0.13267
6967 | 1.979 | 0.13269
6968 | 1.9789 | 0.13271
6969 | 1.9789 | 0.13272
6970 | 1.9789 | 0.13274
6971 | 1.9789 | 0.13276
6972 | 1.9788 | 0.13278
6973 | 1.9788 | 0.13279
6974 | 1.9788 | 0.13281
6975 | 1.9788 | 0.13283
6976 | 1.9787 | 0.13285
6977 | 1.9787 | 0.13287
6978 | 1.9787 | 0.13288
6979 | 1.9787 | 0.1329
6980 | 1.9786 | 0.13292
6981 | 1.9786 | 0.13294
6982 | 1.9786 | 0.13295
6983 | 1.9786 | 0.13297
6984 | 1.9785 | 0.13299
6985 | 1.9785 | 0.13301
6986 | 1.9785 | 0.13303
6987 | 1.9784 | 0.13304
6988 | 1.9784 | 0.13306
6989 | 1.9784 | 0.13308
6990 | 1.9784 | 0.1331
6991 | 1.9783 | 0.13311
6992 | 1.9783 | 0.13313
6993 | 1.9783 | 0.13315
6994 | 1.9783 | 0.13317
6995 | 1.9782 | 0.13319
6996 | 1.9782 | 0.1332
6997 | 1.9782 | 0.13322
6998 | 1.9782 | 0.13324
6999 | 1.9781 | 0.13326
7000 | 1.9781 | 0.13327
7001 | 1.9781 | 0.13329
7002 | 1.9781 | 0.13331
7003 | 1.978 | 0.13333
7004 | 1.978 | 0.13335
7005 | 1.978 | 0.13336
7006 | 1.978 | 0.13338
7007 | 1.9779 | 0.1334
7008 | 1.9779 | 0.13342
7009 | 1.9779 | 0.13343
7010 | 1.9779 | 0.13345
7011 | 1.9778 | 0.13347
7012 | 1.9778 | 0.13349
7013 | 1.9778 | 0.13351
7014 | 1.9778 | 0.13352
7015 | 1.9777 | 0.13354
7016 | 1.9777 | 0.13356
7017 | 1.9777 | 0.13358
7018 | 1.9777 | 0.13359
7019 | 1.9776 | 0.13361
7020 | 1.9776 | 0.13363
7021 | 1.9776 | 0.13365
7022 | 1.9776 | 0.13367
7023 | 1.9775 | 0.13368
7024 | 1.9775 | 0.1337
7025 | 1.9775 | 0.13372
7026 | 1.9775 | 0.13374
7027 | 1.9774 | 0.13375
7028 | 1.9774 | 0.13377
7029 | 1.9774 | 0.13379
7030 | 1.9774 | 0.13381
7031 | 1.9773 | 0.13383
7032 | 1.9773 | 0.13384
7033 | 1.9773 | 0.13386
7034 | 1.9773 | 0.13388
7035 | 1.9772 | 0.1339
7036 | 1.9772 | 0.13391
7037 | 1.9772 | 0.13393
7038 | 1.9772 | 0.13395
7039 | 1.9771 | 0.13397
7040 | 1.9771 | 0.13399
7041 | 1.9771 | 0.134
7042 | 1.9771 | 0.13402
7043 | 1.977 | 0.13404
7044 | 1.977 | 0.13406
7045 | 1.977 | 0.13407
7046 | 1.977 | 0.13409
7047 | 1.9769 | 0.13411
7048 | 1.9769 | 0.13413
7049 | 1.9769 | 0.13415
7050 | 1.9769 | 0.13416
7051 | 1.9768 | 0.13418
7052 | 1.9768 | 0.1342
7053 | 1.9768 | 0.13422
7054 | 1.9768 | 0.13423
7055 | 1.9767 | 0.13425
7056 | 1.9767 | 0.13427
7057 | 1.9767 | 0.13429
7058 | 1.9767 | 0.13431
7059 | 1.9766 | 0.13432
7060 | 1.9766 | 0.13434
7061 | 1.9766 | 0.13436
7062 | 1.9766 | 0.13438
7063 | 1.9765 | 0.13439
7064 | 1.9765 | 0.13441
7065 | 1.9765 | 0.13443
7066 | 1.9765 | 0.13445
7067 | 1.9764 | 0.13447
7068 | 1.9764 | 0.13448
7069 | 1.9764 | 0.1345
7070 | 1.9764 | 0.13452
7071 | 1.9763 | 0.13454
7072 | 1.9763 | 0.13455
7073 | 1.9763 | 0.13457
7074 | 1.9763 | 0.13459
7075 | 1.9762 | 0.13461
7076 | 1.9762 | 0.13463
7077 | 1.9762 | 0.13464
7078 | 1.9762 | 0.13466
7079 | 1.9761 | 0.13468
7080 | 1.9761 | 0.1347
7081 | 1.9761 | 0.13471
7082 | 1.9761 | 0.13473
7083 | 1.976 | 0.13475
7084 | 1.976 | 0.13477
7085 | 1.976 | 0.13478
7086 | 1.976 | 0.1348
7087 | 1.9759 | 0.13482
7088 | 1.9759 | 0.13484
7089 | 1.9759 | 0.13486
7090 | 1.9759 | 0.13487
7091 | 1.9758 | 0.13489
7092 | 1.9758 | 0.13491
7093 | 1.9758 | 0.13493
7094 | 1.9758 | 0.13494
7095 | 1.9757 | 0.13496
7096 | 1.9757 | 0.13498
7097 | 1.9757 | 0.135
7098 | 1.9757 | 0.13502
7099 | 1.9756 | 0.13503
7100 | 1.9756 | 0.13505
7101 | 1.9756 | 0.13507
7102 | 1.9756 | 0.13509
7103 | 1.9755 | 0.1351
7104 | 1.9755 | 0.13512
7105 | 1.9755 | 0.13514
7106 | 1.9755 | 0.13516
7107 | 1.9754 | 0.13518
7108 | 1.9754 | 0.13519
7109 | 1.9754 | 0.13521
7110 | 1.9754 | 0.13523
7111 | 1.9753 | 0.13525
7112 | 1.9753 | 0.13526
7113 | 1.9753 | 0.13528
7114 | 1.9753 | 0.1353
7115 | 1.9752 | 0.13532
7116 | 1.9752 | 0.13534
7117 | 1.9752 | 0.13535
7118 | 1.9752 | 0.13537
7119 | 1.9751 | 0.13539
7120 | 1.9751 | 0.13541
7121 | 1.9751 | 0.13542
7122 | 1.9751 | 0.13544
7123 | 1.975 | 0.13546
7124 | 1.975 | 0.13548
7125 | 1.975 | 0.13549
7126 | 1.975 | 0.13551
7127 | 1.9749 | 0.13553
7128 | 1.9749 | 0.13555
7129 | 1.9749 | 0.13557
7130 | 1.9749 | 0.13558
7131 | 1.9748 | 0.1356
7132 | 1.9748 | 0.13562
7133 | 1.9748 | 0.13564
7134 | 1.9748 | 0.13565
7135 | 1.9747 | 0.13567
7136 | 1.9747 | 0.13569
7137 | 1.9747 | 0.13571
7138 | 1.9747 | 0.13573
7139 | 1.9746 | 0.13574
7140 | 1.9746 | 0.13576
7141 | 1.9746 | 0.13578
7142 | 1.9746 | 0.1358
7143 | 1.9745 | 0.13581
7144 | 1.9745 | 0.13583
7145 | 1.9745 | 0.13585
7146 | 1.9744 | 0.13587
7147 | 1.9744 | 0.13589
7148 | 1.9744 | 0.1359
7149 | 1.9744 | 0.13592
7150 | 1.9743 | 0.13594
7151 | 1.9743 | 0.13596
7152 | 1.9743 | 0.13597
7153 | 1.9743 | 0.13599
7154 | 1.9742 | 0.13601
7155 | 1.9742 | 0.13603
7156 | 1.9742 | 0.13604
7157 | 1.9742 | 0.13606
7158 | 1.9741 | 0.13608
7159 | 1.9741 | 0.1361
7160 | 1.9741 | 0.13612
7161 | 1.9741 | 0.13613
7162 | 1.974 | 0.13615
7163 | 1.974 | 0.13617
7164 | 1.974 | 0.13619
7165 | 1.974 | 0.1362
7166 | 1.9739 | 0.13622
7167 | 1.9739 | 0.13624
7168 | 1.9739 | 0.13626
7169 | 1.9739 | 0.13628
7170 | 1.9738 | 0.13629
7171 | 1.9738 | 0.13631
7172 | 1.9738 | 0.13633
7173 | 1.9738 | 0.13635
7174 | 1.9737 | 0.13636
7175 | 1.9737 | 0.13638
7176 | 1.9737 | 0.1364
7177 | 1.9737 | 0.13642
7178 | 1.9736 | 0.13644
7179 | 1.9736 | 0.13645
7180 | 1.9736 | 0.13647
7181 | 1.9736 | 0.13649
7182 | 1.9735 | 0.13651
7183 | 1.9735 | 0.13652
7184 | 1.9735 | 0.13654
7185 | 1.9735 | 0.13656
7186 | 1.9734 | 0.13658
7187 | 1.9734 | 0.13659
7188 | 1.9734 | 0.13661
7189 | 1.9734 | 0.13663
7190 | 1.9733 | 0.13665
7191 | 1.9733 | 0.13667
7192 | 1.9733 | 0.13668
7193 | 1.9733 | 0.1367
7194 | 1.9732 | 0.13672
7195 | 1.9732 | 0.13674
7196 | 1.9732 | 0.13675
7197 | 1.9732 | 0.13677
7198 | 1.9731 | 0.13679
7199 | 1.9731 | 0.13681
7200 | 1.9731 | 0.13683
7201 | 1.9731 | 0.13684
7202 | 1.973 | 0.13686
7203 | 1.973 | 0.13688
7204 | 1.973 | 0.1369
7205 | 1.973 | 0.13691
7206 | 1.9729 | 0.13693
7207 | 1.9729 | 0.13695
7208 | 1.9729 | 0.13697
7209 | 1.9729 | 0.13698
7210 | 1.9728 | 0.137
7211 | 1.9728 | 0.13702
7212 | 1.9728 | 0.13704
7213 | 1.9728 | 0.13706
7214 | 1.9727 | 0.13707
7215 | 1.9727 | 0.13709
7216 | 1.9727 | 0.13711
7217 | 1.9727 | 0.13713
7218 | 1.9726 | 0.13714
7219 | 1.9726 | 0.13716
7220 | 1.9726 | 0.13718
7221 | 1.9726 | 0.1372
7222 | 1.9725 | 0.13721
7223 | 1.9725 | 0.13723
7224 | 1.9725 | 0.13725
7225 | 1.9725 | 0.13727
7226 | 1.9724 | 0.13729
7227 | 1.9724 | 0.1373
7228 | 1.9724 | 0.13732
7229 | 1.9724 | 0.13734
7230 | 1.9723 | 0.13736
7231 | 1.9723 | 0.13737
7232 | 1.9723 | 0.13739
7233 | 1.9723 | 0.13741
7234 | 1.9722 | 0.13743
7235 | 1.9722 | 0.13745
7236 | 1.9722 | 0.13746
7237 | 1.9722 | 0.13748
7238 | 1.9721 | 0.1375
7239 | 1.9721 | 0.13752
7240 | 1.9721 | 0.13753
7241 | 1.9721 | 0.13755
7242 | 1.972 | 0.13757
7243 | 1.972 | 0.13759
7244 | 1.972 | 0.1376
7245 | 1.972 | 0.13762
7246 | 1.9719 | 0.13764
7247 | 1.9719 | 0.13766
7248 | 1.9719 | 0.13768
7249 | 1.9719 | 0.13769
7250 | 1.9718 | 0.13771
7251 | 1.9718 | 0.13773
7252 | 1.9718 | 0.13775
7253 | 1.9718 | 0.13776
7254 | 1.9718 | 0.13778
7255 | 1.9717 | 0.1378
7256 | 1.9717 | 0.13782
7257 | 1.9717 | 0.13783
7258 | 1.9717 | 0.13785
7259 | 1.9716 | 0.13787
7260 | 1.9716 | 0.13789
7261 | 1.9716 | 0.13791
7262 | 1.9716 | 0.13792
7263 | 1.9715 | 0.13794
7264 | 1.9715 | 0.13796
7265 | 1.9715 | 0.13798
7266 | 1.9715 | 0.13799
7267 | 1.9714 | 0.13801
7268 | 1.9714 | 0.13803
7269 | 1.9714 | 0.13805
7270 | 1.9714 | 0.13806
7271 | 1.9713 | 0.13808
7272 | 1.9713 | 0.1381
7273 | 1.9713 | 0.13812
7274 | 1.9713 | 0.13814
7275 | 1.9712 | 0.13815
7276 | 1.9712 | 0.13817
7277 | 1.9712 | 0.13819
7278 | 1.9712 | 0.13821
7279 | 1.9711 | 0.13822
7280 | 1.9711 | 0.13824
7281 | 1.9711 | 0.13826
7282 | 1.9711 | 0.13828
7283 | 1.971 | 0.13829
7284 | 1.971 | 0.13831
7285 | 1.971 | 0.13833
7286 | 1.971 | 0.13835
7287 | 1.9709 | 0.13837
7288 | 1.9709 | 0.13838
7289 | 1.9709 | 0.1384
7290 | 1.9709 | 0.13842
7291 | 1.9708 | 0.13844
7292 | 1.9708 | 0.13845
7293 | 1.9708 | 0.13847
7294 | 1.9708 | 0.13849
7295 | 1.9707 | 0.13851
7296 | 1.9707 | 0.13852
7297 | 1.9707 | 0.13854
7298 | 1.9707 | 0.13856
7299 | 1.9706 | 0.13858
7300 | 1.9706 | 0.1386
7301 | 1.9706 | 0.13861
7302 | 1.9706 | 0.13863
7303 | 1.9705 | 0.13865
7304 | 1.9705 | 0.13867
7305 | 1.9705 | 0.13868
7306 | 1.9705 | 0.1387
7307 | 1.9704 | 0.13872
7308 | 1.9704 | 0.13874
7309 | 1.9704 | 0.13875
7310 | 1.9704 | 0.13877
7311 | 1.9703 | 0.13879
7312 | 1.9703 | 0.13881
7313 | 1.9703 | 0.13883
7314 | 1.9703 | 0.13884
7315 | 1.9702 | 0.13886
7316 | 1.9702 | 0.13888
7317 | 1.9702 | 0.1389
7318 | 1.9702 | 0.13891
7319 | 1.9701 | 0.13893
7320 | 1.9701 | 0.13895
7321 | 1.9701 | 0.13897
7322 | 1.9701 | 0.13898
7323 | 1.97 | 0.139
7324 | 1.97 | 0.13902
7325 | 1.97 | 0.13904
7326 | 1.97 | 0.13906
7327 | 1.9699 | 0.13907
7328 | 1.9699 | 0.13909
7329 | 1.9699 | 0.13911
7330 | 1.9699 | 0.13913
7331 | 1.9698 | 0.13914
7332 | 1.9698 | 0.13916
7333 | 1.9698 | 0.13918
7334 | 1.9698 | 0.1392
7335 | 1.9697 | 0.13921
7336 | 1.9697 | 0.13923
7337 | 1.9697 | 0.13925
7338 | 1.9697 | 0.13927
7339 | 1.9696 | 0.13929
7340 | 1.9696 | 0.1393
7341 | 1.9696 | 0.13932
7342 | 1.9696 | 0.13934
7343 | 1.9695 | 0.13936
7344 | 1.9695 | 0.13937
7345 | 1.9695 | 0.13939
7346 | 1.9695 | 0.13941
7347 | 1.9694 | 0.13943
7348 | 1.9694 | 0.13944
7349 | 1.9694 | 0.13946
7350 | 1.9694 | 0.13948
7351 | 1.9693 | 0.1395
7352 | 1.9693 | 0.13952
7353 | 1.9693 | 0.13953
7354 | 1.9693 | 0.13955
7355 | 1.9692 | 0.13957
7356 | 1.9692 | 0.13959
7357 | 1.9692 | 0.1396
7358 | 1.9692 | 0.13962
7359 | 1.9691 | 0.13964
7360 | 1.9691 | 0.13966
7361 | 1.9691 | 0.13967
7362 | 1.9691 | 0.13969
7363 | 1.969 | 0.13971
7364 | 1.969 | 0.13973
7365 | 1.969 | 0.13974
7366 | 1.969 | 0.13976
7367 | 1.9689 | 0.13978
7368 | 1.9689 | 0.1398
7369 | 1.9689 | 0.13982
7370 | 1.9689 | 0.13983
7371 | 1.9688 | 0.13985
7372 | 1.9688 | 0.13987
7373 | 1.9688 | 0.13989
7374 | 1.9688 | 0.1399
7375 | 1.9687 | 0.13992
7376 | 1.9687 | 0.13994
7377 | 1.9687 | 0.13996
7378 | 1.9687 | 0.13997
7379 | 1.9686 | 0.13999
7380 | 1.9686 | 0.14001
7381 | 1.9686 | 0.14003
7382 | 1.9686 | 0.14005
7383 | 1.9685 | 0.14006
7384 | 1.9685 | 0.14008
7385 | 1.9685 | 0.1401
7386 | 1.9685 | 0.14012
7387 | 1.9684 | 0.14013
7388 | 1.9684 | 0.14015
7389 | 1.9684 | 0.14017
7390 | 1.9684 | 0.14019
7391 | 1.9683 | 0.1402
7392 | 1.9683 | 0.14022
7393 | 1.9683 | 0.14024
7394 | 1.9683 | 0.14026
7395 | 1.9682 | 0.14027
7396 | 1.9682 | 0.14029
7397 | 1.9682 | 0.14031
7398 | 1.9682 | 0.14033
7399 | 1.9681 | 0.14035
7400 | 1.9681 | 0.14036
7401 | 1.9681 | 0.14038
7402 | 1.9681 | 0.1404
7403 | 1.968 | 0.14042
7404 | 1.968 | 0.14043
7405 | 1.968 | 0.14045
7406 | 1.968 | 0.14047
7407 | 1.9679 | 0.14049
7408 | 1.9679 | 0.1405
7409 | 1.9679 | 0.14052
7410 | 1.9679 | 0.14054
7411 | 1.9678 | 0.14056
7412 | 1.9678 | 0.14058
7413 | 1.9678 | 0.14059
7414 | 1.9678 | 0.14061
7415 | 1.9678 | 0.14063
7416 | 1.9677 | 0.14065
7417 | 1.9677 | 0.14066
7418 | 1.9677 | 0.14068
7419 | 1.9677 | 0.1407
7420 | 1.9676 | 0.14072
7421 | 1.9676 | 0.14073
7422 | 1.9676 | 0.14075
7423 | 1.9676 | 0.14077
7424 | 1.9675 | 0.14079
7425 | 1.9675 | 0.1408
7426 | 1.9675 | 0.14082
7427 | 1.9675 | 0.14084
7428 | 1.9674 | 0.14086
7429 | 1.9674 | 0.14088
7430 | 1.9674 | 0.14089
7431 | 1.9674 | 0.14091
7432 | 1.9673 | 0.14093
7433 | 1.9673 | 0.14095
7434 | 1.9673 | 0.14096
7435 | 1.9673 | 0.14098
7436 | 1.9672 | 0.141
7437 | 1.9672 | 0.14102
7438 | 1.9672 | 0.14103
7439 | 1.9672 | 0.14105
7440 | 1.9671 | 0.14107
7441 | 1.9671 | 0.14109
7442 | 1.9671 | 0.1411
7443 | 1.9671 | 0.14112
7444 | 1.967 | 0.14114
7445 | 1.967 | 0.14116
7446 | 1.967 | 0.14118
7447 | 1.967 | 0.14119
7448 | 1.9669 | 0.14121
7449 | 1.9669 | 0.14123
7450 | 1.9669 | 0.14125
7451 | 1.9669 | 0.14126
7452 | 1.9668 | 0.14128
7453 | 1.9668 | 0.1413
7454 | 1.9668 | 0.14132
7455 | 1.9668 | 0.14133
7456 | 1.9667 | 0.14135
7457 | 1.9667 | 0.14137
7458 | 1.9667 | 0.14139
7459 | 1.9667 | 0.1414
7460 | 1.9666 | 0.14142
7461 | 1.9666 | 0.14144
7462 | 1.9666 | 0.14146
7463 | 1.9666 | 0.14148
7464 | 1.9665 | 0.14149
7465 | 1.9665 | 0.14151
7466 | 1.9665 | 0.14153
7467 | 1.9665 | 0.14155
7468 | 1.9664 | 0.14156
7469 | 1.9664 | 0.14158
7470 | 1.9664 | 0.1416
7471 | 1.9664 | 0.14162
7472 | 1.9663 | 0.14163
7473 | 1.9663 | 0.14165
7474 | 1.9663 | 0.14167
7475 | 1.9663 | 0.14169
7476 | 1.9662 | 0.1417
7477 | 1.9662 | 0.14172
7478 | 1.9662 | 0.14174
7479 | 1.9662 | 0.14176
7480 | 1.9661 | 0.14177
7481 | 1.9661 | 0.14179
7482 | 1.9661 | 0.14181
7483 | 1.9661 | 0.14183
7484 | 1.966 | 0.14185
7485 | 1.966 | 0.14186
7486 | 1.966 | 0.14188
7487 | 1.966 | 0.1419
7488 | 1.9659 | 0.14192
7489 | 1.9659 | 0.14193
7490 | 1.9659 | 0.14195
7491 | 1.9659 | 0.14197
7492 | 1.9658 | 0.14199
7493 | 1.9658 | 0.142
7494 | 1.9658 | 0.14202
7495 | 1.9658 | 0.14204
7496 | 1.9657 | 0.14206
7497 | 1.9657 | 0.14207
7498 | 1.9657 | 0.14209
7499 | 1.9657 | 0.14211
7500 | 1.9657 | 0.14213
7501 | 1.9656 | 0.14215
7502 | 1.9656 | 0.14216
7503 | 1.9656 | 0.14218
7504 | 1.9656 | 0.1422
7505 | 1.9655 | 0.14222
7506 | 1.9655 | 0.14223
7507 | 1.9655 | 0.14225
7508 | 1.9655 | 0.14227
7509 | 1.9654 | 0.14229
7510 | 1.9654 | 0.1423
7511 | 1.9654 | 0.14232
7512 | 1.9654 | 0.14234
7513 | 1.9653 | 0.14236
7514 | 1.9653 | 0.14237
7515 | 1.9653 | 0.14239
7516 | 1.9653 | 0.14241
7517 | 1.9652 | 0.14243
7518 | 1.9652 | 0.14244
7519 | 1.9652 | 0.14246
7520 | 1.9652 | 0.14248
7521 | 1.9651 | 0.1425
7522 | 1.9651 | 0.14252
7523 | 1.9651 | 0.14253
7524 | 1.9651 | 0.14255
7525 | 1.965 | 0.14257
7526 | 1.965 | 0.14259
7527 | 1.965 | 0.1426
7528 | 1.965 | 0.14262
7529 | 1.9649 | 0.14264
7530 | 1.9649 | 0.14266
7531 | 1.9649 | 0.14267
7532 | 1.9649 | 0.14269
7533 | 1.9648 | 0.14271
7534 | 1.9648 | 0.14273
7535 | 1.9648 | 0.14274
7536 | 1.9648 | 0.14276
7537 | 1.9647 | 0.14278
7538 | 1.9647 | 0.1428
7539 | 1.9647 | 0.14281
7540 | 1.9647 | 0.14283
7541 | 1.9646 | 0.14285
7542 | 1.9646 | 0.14287
7543 | 1.9646 | 0.14289
7544 | 1.9646 | 0.1429
7545 | 1.9645 | 0.14292
7546 | 1.9645 | 0.14294
7547 | 1.9645 | 0.14296
7548 | 1.9645 | 0.14297
7549 | 1.9644 | 0.14299
7550 | 1.9644 | 0.14301
7551 | 1.9644 | 0.14303
7552 | 1.9644 | 0.14304
7553 | 1.9643 | 0.14306
7554 | 1.9643 | 0.14308
7555 | 1.9643 | 0.1431
7556 | 1.9643 | 0.14311
7557 | 1.9642 | 0.14313
7558 | 1.9642 | 0.14315
7559 | 1.9642 | 0.14317
7560 | 1.9642 | 0.14318
7561 | 1.9641 | 0.1432
7562 | 1.9641 | 0.14322
7563 | 1.9641 | 0.14324
7564 | 1.9641 | 0.14326
7565 | 1.9641 | 0.14327
7566 | 1.964 | 0.14329
7567 | 1.964 | 0.14331
7568 | 1.964 | 0.14333
7569 | 1.964 | 0.14334
7570 | 1.9639 | 0.14336
7571 | 1.9639 | 0.14338
7572 | 1.9639 | 0.1434
7573 | 1.9639 | 0.14341
7574 | 1.9638 | 0.14343
7575 | 1.9638 | 0.14345
7576 | 1.9638 | 0.14347
7577 | 1.9638 | 0.14348
7578 | 1.9637 | 0.1435
7579 | 1.9637 | 0.14352
7580 | 1.9637 | 0.14354
7581 | 1.9637 | 0.14355
7582 | 1.9636 | 0.14357
7583 | 1.9636 | 0.14359
7584 | 1.9636 | 0.14361
7585 | 1.9636 | 0.14362
7586 | 1.9635 | 0.14364
7587 | 1.9635 | 0.14366
7588 | 1.9635 | 0.14368
7589 | 1.9635 | 0.1437
7590 | 1.9634 | 0.14371
7591 | 1.9634 | 0.14373
7592 | 1.9634 | 0.14375
7593 | 1.9634 | 0.14377
7594 | 1.9633 | 0.14378
7595 | 1.9633 | 0.1438
7596 | 1.9633 | 0.14382
7597 | 1.9633 | 0.14384
7598 | 1.9632 | 0.14385
7599 | 1.9632 | 0.14387
7600 | 1.9632 | 0.14389
7601 | 1.9632 | 0.14391
7602 | 1.9631 | 0.14392
7603 | 1.9631 | 0.14394
7604 | 1.9631 | 0.14396
7605 | 1.9631 | 0.14398
7606 | 1.963 | 0.14399
7607 | 1.963 | 0.14401
7608 | 1.963 | 0.14403
7609 | 1.963 | 0.14405
7610 | 1.9629 | 0.14406
7611 | 1.9629 | 0.14408
7612 | 1.9629 | 0.1441
7613 | 1.9629 | 0.14412
7614 | 1.9628 | 0.14414
7615 | 1.9628 | 0.14415
7616 | 1.9628 | 0.14417
7617 | 1.9628 | 0.14419
7618 | 1.9627 | 0.14421
7619 | 1.9627 | 0.14422
7620 | 1.9627 | 0.14424
7621 | 1.9627 | 0.14426
7622 | 1.9627 | 0.14428
7623 | 1.9626 | 0.14429
7624 | 1.9626 | 0.14431
7625 | 1.9626 | 0.14433
7626 | 1.9626 | 0.14435
7627 | 1.9625 | 0.14436
7628 | 1.9625 | 0.14438
7629 | 1.9625 | 0.1444
7630 | 1.9625 | 0.14442
7631 | 1.9624 | 0.14443
7632 | 1.9624 | 0.14445
7633 | 1.9624 | 0.14447
7634 | 1.9624 | 0.14449
7635 | 1.9623 | 0.1445
7636 | 1.9623 | 0.14452
7637 | 1.9623 | 0.14454
7638 | 1.9623 | 0.14456
7639 | 1.9622 | 0.14458
7640 | 1.9622 | 0.14459
7641 | 1.9622 | 0.14461
7642 | 1.9622 | 0.14463
7643 | 1.9621 | 0.14465
7644 | 1.9621 | 0.14466
7645 | 1.9621 | 0.14468
7646 | 1.9621 | 0.1447
7647 | 1.962 | 0.14472
7648 | 1.962 | 0.14473
7649 | 1.962 | 0.14475
7650 | 1.962 | 0.14477
7651 | 1.9619 | 0.14479
7652 | 1.9619 | 0.1448
7653 | 1.9619 | 0.14482
7654 | 1.9619 | 0.14484
7655 | 1.9618 | 0.14486
7656 | 1.9618 | 0.14487
7657 | 1.9618 | 0.14489
7658 | 1.9618 | 0.14491
7659 | 1.9617 | 0.14493
7660 | 1.9617 | 0.14494
7661 | 1.9617 | 0.14496
7662 | 1.9617 | 0.14498
7663 | 1.9616 | 0.145
7664 | 1.9616 | 0.14501
7665 | 1.9616 | 0.14503
7666 | 1.9616 | 0.14505
7667 | 1.9615 | 0.14507
7668 | 1.9615 | 0.14508
7669 | 1.9615 | 0.1451
7670 | 1.9615 | 0.14512
7671 | 1.9615 | 0.14514
7672 | 1.9614 | 0.14516
7673 | 1.9614 | 0.14517
7674 | 1.9614 | 0.14519
7675 | 1.9614 | 0.14521
7676 | 1.9613 | 0.14523
7677 | 1.9613 | 0.14524
7678 | 1.9613 | 0.14526
7679 | 1.9613 | 0.14528
7680 | 1.9612 | 0.1453
7681 | 1.9612 | 0.14531
7682 | 1.9612 | 0.14533
7683 | 1.9612 | 0.14535
7684 | 1.9611 | 0.14537
7685 | 1.9611 | 0.14538
7686 | 1.9611 | 0.1454
7687 | 1.9611 | 0.14542
7688 | 1.961 | 0.14544
7689 | 1.961 | 0.14545
7690 | 1.961 | 0.14547
7691 | 1.961 | 0.14549
7692 | 1.9609 | 0.14551
7693 | 1.9609 | 0.14552
7694 | 1.9609 | 0.14554
7695 | 1.9609 | 0.14556
7696 | 1.9608 | 0.14558
7697 | 1.9608 | 0.14559
7698 | 1.9608 | 0.14561
7699 | 1.9608 | 0.14563
7700 | 1.9607 | 0.14565
7701 | 1.9607 | 0.14566
7702 | 1.9607 | 0.14568
7703 | 1.9607 | 0.1457
7704 | 1.9606 | 0.14572
7705 | 1.9606 | 0.14574
7706 | 1.9606 | 0.14575
7707 | 1.9606 | 0.14577
7708 | 1.9605 | 0.14579
7709 | 1.9605 | 0.14581
7710 | 1.9605 | 0.14582
7711 | 1.9605 | 0.14584
7712 | 1.9604 | 0.14586
7713 | 1.9604 | 0.14588
7714 | 1.9604 | 0.14589
7715 | 1.9604 | 0.14591
7716 | 1.9604 | 0.14593
7717 | 1.9603 | 0.14595
7718 | 1.9603 | 0.14596
7719 | 1.9603 | 0.14598
7720 | 1.9603 | 0.146
7721 | 1.9602 | 0.14602
7722 | 1.9602 | 0.14603
7723 | 1.9602 | 0.14605
7724 | 1.9602 | 0.14607
7725 | 1.9601 | 0.14609
7726 | 1.9601 | 0.1461
7727 | 1.9601 | 0.14612
7728 | 1.9601 | 0.14614
7729 | 1.96 | 0.14616
7730 | 1.96 | 0.14617
7731 | 1.96 | 0.14619
7732 | 1.96 | 0.14621
7733 | 1.9599 | 0.14623
7734 | 1.9599 | 0.14624
7735 | 1.9599 | 0.14626
7736 | 1.9599 | 0.14628
7737 | 1.9598 | 0.1463
7738 | 1.9598 | 0.14631
7739 | 1.9598 | 0.14633
7740 | 1.9598 | 0.14635
7741 | 1.9597 | 0.14637
7742 | 1.9597 | 0.14638
7743 | 1.9597 | 0.1464
7744 | 1.9597 | 0.14642
7745 | 1.9596 | 0.14644
7746 | 1.9596 | 0.14645
7747 | 1.9596 | 0.14647
7748 | 1.9596 | 0.14649
7749 | 1.9595 | 0.14651
7750 | 1.9595 | 0.14653
7751 | 1.9595 | 0.14654
7752 | 1.9595 | 0.14656
7753 | 1.9594 | 0.14658
7754 | 1.9594 | 0.1466
7755 | 1.9594 | 0.14661
7756 | 1.9594 | 0.14663
7757 | 1.9594 | 0.14665
7758 | 1.9593 | 0.14667
7759 | 1.9593 | 0.14668
7760 | 1.9593 | 0.1467
7761 | 1.9593 | 0.14672
7762 | 1.9592 | 0.14674
7763 | 1.9592 | 0.14675
7764 | 1.9592 | 0.14677
7765 | 1.9592 | 0.14679
7766 | 1.9591 | 0.14681
7767 | 1.9591 | 0.14682
7768 | 1.9591 | 0.14684
7769 | 1.9591 | 0.14686
7770 | 1.959 | 0.14688
7771 | 1.959 | 0.14689
7772 | 1.959 | 0.14691
7773 | 1.959 | 0.14693
7774 | 1.9589 | 0.14695
7775 | 1.9589 | 0.14696
7776 | 1.9589 | 0.14698
7777 | 1.9589 | 0.147
7778 | 1.9588 | 0.14702
7779 | 1.9588 | 0.14703
7780 | 1.9588 | 0.14705
7781 | 1.9588 | 0.14707
7782 | 1.9587 | 0.14709
7783 | 1.9587 | 0.1471
7784 | 1.9587 | 0.14712
7785 | 1.9587 | 0.14714
7786 | 1.9586 | 0.14716
7787 | 1.9586 | 0.14717
7788 | 1.9586 | 0.14719
7789 | 1.9586 | 0.14721
7790 | 1.9585 | 0.14723
7791 | 1.9585 | 0.14724
7792 | 1.9585 | 0.14726
7793 | 1.9585 | 0.14728
7794 | 1.9585 | 0.1473
7795 | 1.9584 | 0.14731
7796 | 1.9584 | 0.14733
7797 | 1.9584 | 0.14735
7798 | 1.9584 | 0.14737
7799 | 1.9583 | 0.14738
7800 | 1.9583 | 0.1474
7801 | 1.9583 | 0.14742
7802 | 1.9583 | 0.14744
7803 | 1.9582 | 0.14746
7804 | 1.9582 | 0.14747
7805 | 1.9582 | 0.14749
7806 | 1.9582 | 0.14751
7807 | 1.9581 | 0.14753
7808 | 1.9581 | 0.14754
7809 | 1.9581 | 0.14756
7810 | 1.9581 | 0.14758
7811 | 1.958 | 0.1476
7812 | 1.958 | 0.14761
7813 | 1.958 | 0.14763
7814 | 1.958 | 0.14765
7815 | 1.9579 | 0.14767
7816 | 1.9579 | 0.14768
7817 | 1.9579 | 0.1477
7818 | 1.9579 | 0.14772
7819 | 1.9578 | 0.14774
7820 | 1.9578 | 0.14775
7821 | 1.9578 | 0.14777
7822 | 1.9578 | 0.14779
7823 | 1.9577 | 0.14781
7824 | 1.9577 | 0.14782
7825 | 1.9577 | 0.14784
7826 | 1.9577 | 0.14786
7827 | 1.9576 | 0.14788
7828 | 1.9576 | 0.14789
7829 | 1.9576 | 0.14791
7830 | 1.9576 | 0.14793
7831 | 1.9576 | 0.14795
7832 | 1.9575 | 0.14796
7833 | 1.9575 | 0.14798
7834 | 1.9575 | 0.148
7835 | 1.9575 | 0.14802
7836 | 1.9574 | 0.14803
7837 | 1.9574 | 0.14805
7838 | 1.9574 | 0.14807
7839 | 1.9574 | 0.14809
7840 | 1.9573 | 0.1481
7841 | 1.9573 | 0.14812
7842 | 1.9573 | 0.14814
7843 | 1.9573 | 0.14816
7844 | 1.9572 | 0.14817
7845 | 1.9572 | 0.14819
7846 | 1.9572 | 0.14821
7847 | 1.9572 | 0.14823
7848 | 1.9571 | 0.14824
7849 | 1.9571 | 0.14826
7850 | 1.9571 | 0.14828
7851 | 1.9571 | 0.1483
7852 | 1.957 | 0.14831
7853 | 1.957 | 0.14833
7854 | 1.957 | 0.14835
7855 | 1.957 | 0.14837
7856 | 1.9569 | 0.14838
7857 | 1.9569 | 0.1484
7858 | 1.9569 | 0.14842
7859 | 1.9569 | 0.14844
7860 | 1.9568 | 0.14845
7861 | 1.9568 | 0.14847
7862 | 1.9568 | 0.14849
7863 | 1.9568 | 0.14851
7864 | 1.9568 | 0.14852
7865 | 1.9567 | 0.14854
7866 | 1.9567 | 0.14856
7867 | 1.9567 | 0.14858
7868 | 1.9567 | 0.14859
7869 | 1.9566 | 0.14861
7870 | 1.9566 | 0.14863
7871 | 1.9566 | 0.14865
7872 | 1.9566 | 0.14866
7873 | 1.9565 | 0.14868
7874 | 1.9565 | 0.1487
7875 | 1.9565 | 0.14872
7876 | 1.9565 | 0.14873
7877 | 1.9564 | 0.14875
7878 | 1.9564 | 0.14877
7879 | 1.9564 | 0.14879
7880 | 1.9564 | 0.1488
7881 | 1.9563 | 0.14882
7882 | 1.9563 | 0.14884
7883 | 1.9563 | 0.14886
7884 | 1.9563 | 0.14887
7885 | 1.9562 | 0.14889
7886 | 1.9562 | 0.14891
7887 | 1.9562 | 0.14893
7888 | 1.9562 | 0.14894
7889 | 1.9561 | 0.14896
7890 | 1.9561 | 0.14898
7891 | 1.9561 | 0.149
7892 | 1.9561 | 0.14901
7893 | 1.956 | 0.14903
7894 | 1.956 | 0.14905
7895 | 1.956 | 0.14907
7896 | 1.956 | 0.14908
7897 | 1.956 | 0.1491
7898 | 1.9559 | 0.14912
7899 | 1.9559 | 0.14914
7900 | 1.9559 | 0.14915
7901 | 1.9559 | 0.14917
7902 | 1.9558 | 0.14919
7903 | 1.9558 | 0.14921
7904 | 1.9558 | 0.14922
7905 | 1.9558 | 0.14924
7906 | 1.9557 | 0.14926
7907 | 1.9557 | 0.14928
7908 | 1.9557 | 0.14929
7909 | 1.9557 | 0.14931
7910 | 1.9556 | 0.14933
7911 | 1.9556 | 0.14935
7912 | 1.9556 | 0.14936
7913 | 1.9556 | 0.14938
7914 | 1.9555 | 0.1494
7915 | 1.9555 | 0.14942
7916 | 1.9555 | 0.14943
7917 | 1.9555 | 0.14945
7918 | 1.9554 | 0.14947
7919 | 1.9554 | 0.14949
7920 | 1.9554 | 0.1495
7921 | 1.9554 | 0.14952
7922 | 1.9553 | 0.14954
7923 | 1.9553 | 0.14956
7924 | 1.9553 | 0.14957
7925 | 1.9553 | 0.14959
7926 | 1.9553 | 0.14961
7927 | 1.9552 | 0.14963
7928 | 1.9552 | 0.14964
7929 | 1.9552 | 0.14966
7930 | 1.9552 | 0.14968
7931 | 1.9551 | 0.1497
7932 | 1.9551 | 0.14971
7933 | 1.9551 | 0.14973
7934 | 1.9551 | 0.14975
7935 | 1.955 | 0.14977
7936 | 1.955 | 0.14978
7937 | 1.955 | 0.1498
7938 | 1.955 | 0.14982
7939 | 1.9549 | 0.14984
7940 | 1.9549 | 0.14985
7941 | 1.9549 | 0.14987
7942 | 1.9549 | 0.14989
7943 | 1.9548 | 0.14991
7944 | 1.9548 | 0.14992
7945 | 1.9548 | 0.14994
7946 | 1.9548 | 0.14996
7947 | 1.9547 | 0.14998
7948 | 1.9547 | 0.14999
7949 | 1.9547 | 0.15001
7950 | 1.9547 | 0.15003
7951 | 1.9546 | 0.15005
7952 | 1.9546 | 0.15006
7953 | 1.9546 | 0.15008
7954 | 1.9546 | 0.1501
7955 | 1.9545 | 0.15012
7956 | 1.9545 | 0.15013
7957 | 1.9545 | 0.15015
7958 | 1.9545 | 0.15017
7959 | 1.9545 | 0.15019
7960 | 1.9544 | 0.1502
7961 | 1.9544 | 0.15022
7962 | 1.9544 | 0.15024
7963 | 1.9544 | 0.15026
7964 | 1.9543 | 0.15027
7965 | 1.9543 | 0.15029
7966 | 1.9543 | 0.15031
7967 | 1.9543 | 0.15033
7968 | 1.9542 | 0.15034
7969 | 1.9542 | 0.15036
7970 | 1.9542 | 0.15038
7971 | 1.9542 | 0.1504
7972 | 1.9541 | 0.15041
7973 | 1.9541 | 0.15043
7974 | 1.9541 | 0.15045
7975 | 1.9541 | 0.15047
7976 | 1.954 | 0.15048
7977 | 1.954 | 0.1505
7978 | 1.954 | 0.15052
7979 | 1.954 | 0.15054
7980 | 1.9539 | 0.15055
7981 | 1.9539 | 0.15057
7982 | 1.9539 | 0.15059
7983 | 1.9539 | 0.15061
7984 | 1.9539 | 0.15062
7985 | 1.9538 | 0.15064
7986 | 1.9538 | 0.15066
7987 | 1.9538 | 0.15068
7988 | 1.9538 | 0.15069
7989 | 1.9537 | 0.15071
7990 | 1.9537 | 0.15073
7991 | 1.9537 | 0.15075
7992 | 1.9537 | 0.15076
7993 | 1.9536 | 0.15078
7994 | 1.9536 | 0.1508
7995 | 1.9536 | 0.15082
7996 | 1.9536 | 0.15083
7997 | 1.9535 | 0.15085
7998 | 1.9535 | 0.15087
7999 | 1.9535 | 0.15089
8000 | 1.9535 | 0.1509
8001 | 1.9534 | 0.15092
8002 | 1.9534 | 0.15094
8003 | 1.9534 | 0.15096
8004 | 1.9534 | 0.15097
8005 | 1.9533 | 0.15099
8006 | 1.9533 | 0.15101
8007 | 1.9533 | 0.15103
8008 | 1.9533 | 0.15104
8009 | 1.9532 | 0.15106
8010 | 1.9532 | 0.15108
8011 | 1.9532 | 0.1511
8012 | 1.9532 | 0.15111
8013 | 1.9532 | 0.15113
8014 | 1.9531 | 0.15115
8015 | 1.9531 | 0.15117
8016 | 1.9531 | 0.15118
8017 | 1.9531 | 0.1512
8018 | 1.953 | 0.15122
8019 | 1.953 | 0.15124
8020 | 1.953 | 0.15125
8021 | 1.953 | 0.15127
8022 | 1.9529 | 0.15129
8023 | 1.9529 | 0.15131
8024 | 1.9529 | 0.15132
8025 | 1.9529 | 0.15134
8026 | 1.9528 | 0.15136
8027 | 1.9528 | 0.15138
8028 | 1.9528 | 0.15139
8029 | 1.9528 | 0.15141
8030 | 1.9527 | 0.15143
8031 | 1.9527 | 0.15145
8032 | 1.9527 | 0.15146
8033 | 1.9527 | 0.15148
8034 | 1.9526 | 0.1515
8035 | 1.9526 | 0.15152
8036 | 1.9526 | 0.15153
8037 | 1.9526 | 0.15155
8038 | 1.9525 | 0.15157
8039 | 1.9525 | 0.15159
8040 | 1.9525 | 0.1516
8041 | 1.9525 | 0.15162
8042 | 1.9525 | 0.15164
8043 | 1.9524 | 0.15165
8044 | 1.9524 | 0.15167
8045 | 1.9524 | 0.15169
8046 | 1.9524 | 0.15171
8047 | 1.9523 | 0.15172
8048 | 1.9523 | 0.15174
8049 | 1.9523 | 0.15176
8050 | 1.9523 | 0.15178
8051 | 1.9522 | 0.15179
8052 | 1.9522 | 0.15181
8053 | 1.9522 | 0.15183
8054 | 1.9522 | 0.15185
8055 | 1.9521 | 0.15186
8056 | 1.9521 | 0.15188
8057 | 1.9521 | 0.1519
8058 | 1.9521 | 0.15192
8059 | 1.952 | 0.15193
8060 | 1.952 | 0.15195
8061 | 1.952 | 0.15197
8062 | 1.952 | 0.15199
8063 | 1.9519 | 0.152
8064 | 1.9519 | 0.15202
8065 | 1.9519 | 0.15204
8066 | 1.9519 | 0.15206
8067 | 1.9519 | 0.15207
8068 | 1.9518 | 0.15209
8069 | 1.9518 | 0.15211
8070 | 1.9518 | 0.15213
8071 | 1.9518 | 0.15214
8072 | 1.9517 | 0.15216
8073 | 1.9517 | 0.15218
8074 | 1.9517 | 0.1522
8075 | 1.9517 | 0.15221
8076 | 1.9516 | 0.15223
8077 | 1.9516 | 0.15225
8078 | 1.9516 | 0.15227
8079 | 1.9516 | 0.15228
8080 | 1.9515 | 0.1523
8081 | 1.9515 | 0.15232
8082 | 1.9515 | 0.15234
8083 | 1.9515 | 0.15235
8084 | 1.9514 | 0.15237
8085 | 1.9514 | 0.15239
8086 | 1.9514 | 0.15241
8087 | 1.9514 | 0.15242
8088 | 1.9513 | 0.15244
8089 | 1.9513 | 0.15246
8090 | 1.9513 | 0.15248
8091 | 1.9513 | 0.15249
8092 | 1.9513 | 0.15251
8093 | 1.9512 | 0.15253
8094 | 1.9512 | 0.15255
8095 | 1.9512 | 0.15256
8096 | 1.9512 | 0.15258
8097 | 1.9511 | 0.1526
8098 | 1.9511 | 0.15261
8099 | 1.9511 | 0.15263
8100 | 1.9511 | 0.15265
8101 | 1.951 | 0.15267
8102 | 1.951 | 0.15268
8103 | 1.951 | 0.1527
8104 | 1.951 | 0.15272
8105 | 1.9509 | 0.15274
8106 | 1.9509 | 0.15275
8107 | 1.9509 | 0.15277
8108 | 1.9509 | 0.15279
8109 | 1.9508 | 0.15281
8110 | 1.9508 | 0.15282
8111 | 1.9508 | 0.15284
8112 | 1.9508 | 0.15286
8113 | 1.9507 | 0.15288
8114 | 1.9507 | 0.15289
8115 | 1.9507 | 0.15291
8116 | 1.9507 | 0.15293
8117 | 1.9507 | 0.15295
8118 | 1.9506 | 0.15296
8119 | 1.9506 | 0.15298
8120 | 1.9506 | 0.153
8121 | 1.9506 | 0.15302
8122 | 1.9505 | 0.15303
8123 | 1.9505 | 0.15305
8124 | 1.9505 | 0.15307
8125 | 1.9505 | 0.15309
8126 | 1.9504 | 0.1531
8127 | 1.9504 | 0.15312
8128 | 1.9504 | 0.15314
8129 | 1.9504 | 0.15316
8130 | 1.9503 | 0.15317
8131 | 1.9503 | 0.15319
8132 | 1.9503 | 0.15321
8133 | 1.9503 | 0.15323
8134 | 1.9502 | 0.15324
8135 | 1.9502 | 0.15326
8136 | 1.9502 | 0.15328
8137 | 1.9502 | 0.1533
8138 | 1.9501 | 0.15331
8139 | 1.9501 | 0.15333
8140 | 1.9501 | 0.15335
8141 | 1.9501 | 0.15336
8142 | 1.9501 | 0.15338
8143 | 1.95 | 0.1534
8144 | 1.95 | 0.15342
8145 | 1.95 | 0.15343
8146 | 1.95 | 0.15345
8147 | 1.9499 | 0.15347
8148 | 1.9499 | 0.15349
8149 | 1.9499 | 0.1535
8150 | 1.9499 | 0.15352
8151 | 1.9498 | 0.15354
8152 | 1.9498 | 0.15356
8153 | 1.9498 | 0.15357
8154 | 1.9498 | 0.15359
8155 | 1.9497 | 0.15361
8156 | 1.9497 | 0.15363
8157 | 1.9497 | 0.15364
8158 | 1.9497 | 0.15366
8159 | 1.9496 | 0.15368
8160 | 1.9496 | 0.1537
8161 | 1.9496 | 0.15371
8162 | 1.9496 | 0.15373
8163 | 1.9496 | 0.15375
8164 | 1.9495 | 0.15377
8165 | 1.9495 | 0.15378
8166 | 1.9495 | 0.1538
8167 | 1.9495 | 0.15382
8168 | 1.9494 | 0.15384
8169 | 1.9494 | 0.15385
8170 | 1.9494 | 0.15387
8171 | 1.9494 | 0.15389
8172 | 1.9493 | 0.15391
8173 | 1.9493 | 0.15392
8174 | 1.9493 | 0.15394
8175 | 1.9493 | 0.15396
8176 | 1.9492 | 0.15397
8177 | 1.9492 | 0.15399
8178 | 1.9492 | 0.15401
8179 | 1.9492 | 0.15403
8180 | 1.9491 | 0.15404
8181 | 1.9491 | 0.15406
8182 | 1.9491 | 0.15408
8183 | 1.9491 | 0.1541
8184 | 1.949 | 0.15411
8185 | 1.949 | 0.15413
8186 | 1.949 | 0.15415
8187 | 1.949 | 0.15417
8188 | 1.949 | 0.15418
8189 | 1.9489 | 0.1542
8190 | 1.9489 | 0.15422
8191 | 1.9489 | 0.15424
8192 | 1.9489 | 0.15425
8193 | 1.9488 | 0.15427
8194 | 1.9488 | 0.15429
8195 | 1.9488 | 0.15431
8196 | 1.9488 | 0.15432
8197 | 1.9487 | 0.15434
8198 | 1.9487 | 0.15436
8199 | 1.9487 | 0.15438
8200 | 1.9487 | 0.15439
8201 | 1.9486 | 0.15441
8202 | 1.9486 | 0.15443
8203 | 1.9486 | 0.15445
8204 | 1.9486 | 0.15446
8205 | 1.9485 | 0.15448
8206 | 1.9485 | 0.1545
8207 | 1.9485 | 0.15451
8208 | 1.9485 | 0.15453
8209 | 1.9485 | 0.15455
8210 | 1.9484 | 0.15457
8211 | 1.9484 | 0.15458
8212 | 1.9484 | 0.1546
8213 | 1.9484 | 0.15462
8214 | 1.9483 | 0.15464
8215 | 1.9483 | 0.15465
8216 | 1.9483 | 0.15467
8217 | 1.9483 | 0.15469
8218 | 1.9482 | 0.15471
8219 | 1.9482 | 0.15472
8220 | 1.9482 | 0.15474
8221 | 1.9482 | 0.15476
8222 | 1.9481 | 0.15478
8223 | 1.9481 | 0.15479
8224 | 1.9481 | 0.15481
8225 | 1.9481 | 0.15483
8226 | 1.948 | 0.15485
8227 | 1.948 | 0.15486
8228 | 1.948 | 0.15488
8229 | 1.948 | 0.1549
8230 | 1.948 | 0.15492
8231 | 1.9479 | 0.15493
8232 | 1.9479 | 0.15495
8233 | 1.9479 | 0.15497
8234 | 1.9479 | 0.15499
8235 | 1.9478 | 0.155
8236 | 1.9478 | 0.15502
8237 | 1.9478 | 0.15504
8238 | 1.9478 | 0.15505
8239 | 1.9477 | 0.15507
8240 | 1.9477 | 0.15509
8241 | 1.9477 | 0.15511
8242 | 1.9477 | 0.15512
8243 | 1.9476 | 0.15514
8244 | 1.9476 | 0.15516
8245 | 1.9476 | 0.15518
8246 | 1.9476 | 0.15519
8247 | 1.9475 | 0.15521
8248 | 1.9475 | 0.15523
8249 | 1.9475 | 0.15525
8250 | 1.9475 | 0.15526
8251 | 1.9475 | 0.15528
8252 | 1.9474 | 0.1553
8253 | 1.9474 | 0.15532
8254 | 1.9474 | 0.15533
8255 | 1.9474 | 0.15535
8256 | 1.9473 | 0.15537
8257 | 1.9473 | 0.15539
8258 | 1.9473 | 0.1554
8259 | 1.9473 | 0.15542
8260 | 1.9472 | 0.15544
8261 | 1.9472 | 0.15545
8262 | 1.9472 | 0.15547
8263 | 1.9472 | 0.15549
8264 | 1.9471 | 0.15551
8265 | 1.9471 | 0.15552
8266 | 1.9471 | 0.15554
8267 | 1.9471 | 0.15556
8268 | 1.947 | 0.15558
8269 | 1.947 | 0.15559
8270 | 1.947 | 0.15561
8271 | 1.947 | 0.15563
8272 | 1.947 | 0.15565
8273 | 1.9469 | 0.15566
8274 | 1.9469 | 0.15568
8275 | 1.9469 | 0.1557
8276 | 1.9469 | 0.15572
8277 | 1.9468 | 0.15573
8278 | 1.9468 | 0.15575
8279 | 1.9468 | 0.15577
8280 | 1.9468 | 0.15579
8281 | 1.9467 | 0.1558
8282 | 1.9467 | 0.15582
8283 | 1.9467 | 0.15584
8284 | 1.9467 | 0.15585
8285 | 1.9466 | 0.15587
8286 | 1.9466 | 0.15589
8287 | 1.9466 | 0.15591
8288 | 1.9466 | 0.15592
8289 | 1.9465 | 0.15594
8290 | 1.9465 | 0.15596
8291 | 1.9465 | 0.15598
8292 | 1.9465 | 0.15599
8293 | 1.9465 | 0.15601
8294 | 1.9464 | 0.15603
8295 | 1.9464 | 0.15605
8296 | 1.9464 | 0.15606
8297 | 1.9464 | 0.15608
8298 | 1.9463 | 0.1561
8299 | 1.9463 | 0.15612
8300 | 1.9463 | 0.15613
8301 | 1.9463 | 0.15615
8302 | 1.9462 | 0.15617
8303 | 1.9462 | 0.15619
8304 | 1.9462 | 0.1562
8305 | 1.9462 | 0.15622
8306 | 1.9461 | 0.15624
8307 | 1.9461 | 0.15625
8308 | 1.9461 | 0.15627
8309 | 1.9461 | 0.15629
8310 | 1.946 | 0.15631
8311 | 1.946 | 0.15632
8312 | 1.946 | 0.15634
8313 | 1.946 | 0.15636
8314 | 1.946 | 0.15638
8315 | 1.9459 | 0.15639
8316 | 1.9459 | 0.15641
8317 | 1.9459 | 0.15643
8318 | 1.9459 | 0.15645
8319 | 1.9458 | 0.15646
8320 | 1.9458 | 0.15648
8321 | 1.9458 | 0.1565
8322 | 1.9458 | 0.15652
8323 | 1.9457 | 0.15653
8324 | 1.9457 | 0.15655
8325 | 1.9457 | 0.15657
8326 | 1.9457 | 0.15659
8327 | 1.9456 | 0.1566
8328 | 1.9456 | 0.15662
8329 | 1.9456 | 0.15664
8330 | 1.9456 | 0.15665
8331 | 1.9455 | 0.15667
8332 | 1.9455 | 0.15669
8333 | 1.9455 | 0.15671
8334 | 1.9455 | 0.15672
8335 | 1.9455 | 0.15674
8336 | 1.9454 | 0.15676
8337 | 1.9454 | 0.15678
8338 | 1.9454 | 0.15679
8339 | 1.9454 | 0.15681
8340 | 1.9453 | 0.15683
8341 | 1.9453 | 0.15685
8342 | 1.9453 | 0.15686
8343 | 1.9453 | 0.15688
8344 | 1.9452 | 0.1569
8345 | 1.9452 | 0.15692
8346 | 1.9452 | 0.15693
8347 | 1.9452 | 0.15695
8348 | 1.9451 | 0.15697
8349 | 1.9451 | 0.15698
8350 | 1.9451 | 0.157
8351 | 1.9451 | 0.15702
8352 | 1.9451 | 0.15704
8353 | 1.945 | 0.15705
8354 | 1.945 | 0.15707
8355 | 1.945 | 0.15709
8356 | 1.945 | 0.15711
8357 | 1.9449 | 0.15712
8358 | 1.9449 | 0.15714
8359 | 1.9449 | 0.15716
8360 | 1.9449 | 0.15718
8361 | 1.9448 | 0.15719
8362 | 1.9448 | 0.15721
8363 | 1.9448 | 0.15723
8364 | 1.9448 | 0.15725
8365 | 1.9447 | 0.15726
8366 | 1.9447 | 0.15728
8367 | 1.9447 | 0.1573
8368 | 1.9447 | 0.15731
8369 | 1.9446 | 0.15733
8370 | 1.9446 | 0.15735
8371 | 1.9446 | 0.15737
8372 | 1.9446 | 0.15738
8373 | 1.9446 | 0.1574
8374 | 1.9445 | 0.15742
8375 | 1.9445 | 0.15744
8376 | 1.9445 | 0.15745
8377 | 1.9445 | 0.15747
8378 | 1.9444 | 0.15749
8379 | 1.9444 | 0.15751
8380 | 1.9444 | 0.15752
8381 | 1.9444 | 0.15754
8382 | 1.9443 | 0.15756
8383 | 1.9443 | 0.15758
8384 | 1.9443 | 0.15759
8385 | 1.9443 | 0.15761
8386 | 1.9442 | 0.15763
8387 | 1.9442 | 0.15764
8388 | 1.9442 | 0.15766
8389 | 1.9442 | 0.15768
8390 | 1.9442 | 0.1577
8391 | 1.9441 | 0.15771
8392 | 1.9441 | 0.15773
8393 | 1.9441 | 0.15775
8394 | 1.9441 | 0.15777
8395 | 1.944 | 0.15778
8396 | 1.944 | 0.1578
8397 | 1.944 | 0.15782
8398 | 1.944 | 0.15784
8399 | 1.9439 | 0.15785
8400 | 1.9439 | 0.15787
8401 | 1.9439 | 0.15789
8402 | 1.9439 | 0.15791
8403 | 1.9438 | 0.15792
8404 | 1.9438 | 0.15794
8405 | 1.9438 | 0.15796
8406 | 1.9438 | 0.15797
8407 | 1.9437 | 0.15799
8408 | 1.9437 | 0.15801
8409 | 1.9437 | 0.15803
8410 | 1.9437 | 0.15804
8411 | 1.9437 | 0.15806
8412 | 1.9436 | 0.15808
8413 | 1.9436 | 0.1581
8414 | 1.9436 | 0.15811
8415 | 1.9436 | 0.15813
8416 | 1.9435 | 0.15815
8417 | 1.9435 | 0.15817
8418 | 1.9435 | 0.15818
8419 | 1.9435 | 0.1582
8420 | 1.9434 | 0.15822
8421 | 1.9434 | 0.15823
8422 | 1.9434 | 0.15825
8423 | 1.9434 | 0.15827
8424 | 1.9433 | 0.15829
8425 | 1.9433 | 0.1583
8426 | 1.9433 | 0.15832
8427 | 1.9433 | 0.15834
8428 | 1.9433 | 0.15836
8429 | 1.9432 | 0.15837
8430 | 1.9432 | 0.15839
8431 | 1.9432 | 0.15841
8432 | 1.9432 | 0.15843
8433 | 1.9431 | 0.15844
8434 | 1.9431 | 0.15846
8435 | 1.9431 | 0.15848
8436 | 1.9431 | 0.15849
8437 | 1.943 | 0.15851
8438 | 1.943 | 0.15853
8439 | 1.943 | 0.15855
8440 | 1.943 | 0.15856
8441 | 1.9429 | 0.15858
8442 | 1.9429 | 0.1586
8443 | 1.9429 | 0.15862
8444 | 1.9429 | 0.15863
8445 | 1.9429 | 0.15865
8446 | 1.9428 | 0.15867
8447 | 1.9428 | 0.15869
8448 | 1.9428 | 0.1587
8449 | 1.9428 | 0.15872
8450 | 1.9427 | 0.15874
8451 | 1.9427 | 0.15876
8452 | 1.9427 | 0.15877
8453 | 1.9427 | 0.15879
8454 | 1.9426 | 0.15881
8455 | 1.9426 | 0.15882
8456 | 1.9426 | 0.15884
8457 | 1.9426 | 0.15886
8458 | 1.9425 | 0.15888
8459 | 1.9425 | 0.15889
8460 | 1.9425 | 0.15891
8461 | 1.9425 | 0.15893
8462 | 1.9424 | 0.15895
8463 | 1.9424 | 0.15896
8464 | 1.9424 | 0.15898
8465 | 1.9424 | 0.159
8466 | 1.9424 | 0.15902
8467 | 1.9423 | 0.15903
8468 | 1.9423 | 0.15905
8469 | 1.9423 | 0.15907
8470 | 1.9423 | 0.15908
8471 | 1.9422 | 0.1591
8472 | 1.9422 | 0.15912
8473 | 1.9422 | 0.15914
8474 | 1.9422 | 0.15915
8475 | 1.9421 | 0.15917
8476 | 1.9421 | 0.15919
8477 | 1.9421 | 0.15921
8478 | 1.9421 | 0.15922
8479 | 1.942 | 0.15924
8480 | 1.942 | 0.15926
8481 | 1.942 | 0.15928
8482 | 1.942 | 0.15929
8483 | 1.942 | 0.15931
8484 | 1.9419 | 0.15933
8485 | 1.9419 | 0.15934
8486 | 1.9419 | 0.15936
8487 | 1.9419 | 0.15938
8488 | 1.9418 | 0.1594
8489 | 1.9418 | 0.15941
8490 | 1.9418 | 0.15943
8491 | 1.9418 | 0.15945
8492 | 1.9417 | 0.15947
8493 | 1.9417 | 0.15948
8494 | 1.9417 | 0.1595
8495 | 1.9417 | 0.15952
8496 | 1.9416 | 0.15954
8497 | 1.9416 | 0.15955
8498 | 1.9416 | 0.15957
8499 | 1.9416 | 0.15959
8500 | 1.9416 | 0.1596
8501 | 1.9415 | 0.15962
8502 | 1.9415 | 0.15964
8503 | 1.9415 | 0.15966
8504 | 1.9415 | 0.15967
8505 | 1.9414 | 0.15969
8506 | 1.9414 | 0.15971
8507 | 1.9414 | 0.15973
8508 | 1.9414 | 0.15974
8509 | 1.9413 | 0.15976
8510 | 1.9413 | 0.15978
8511 | 1.9413 | 0.1598
8512 | 1.9413 | 0.15981
8513 | 1.9412 | 0.15983
8514 | 1.9412 | 0.15985
8515 | 1.9412 | 0.15986
8516 | 1.9412 | 0.15988
8517 | 1.9412 | 0.1599
8518 | 1.9411 | 0.15992
8519 | 1.9411 | 0.15993
8520 | 1.9411 | 0.15995
8521 | 1.9411 | 0.15997
8522 | 1.941 | 0.15999
8523 | 1.941 | 0.16
8524 | 1.941 | 0.16002
8525 | 1.941 | 0.16004
8526 | 1.9409 | 0.16005
8527 | 1.9409 | 0.16007
8528 | 1.9409 | 0.16009
8529 | 1.9409 | 0.16011
8530 | 1.9408 | 0.16012
8531 | 1.9408 | 0.16014
8532 | 1.9408 | 0.16016
8533 | 1.9408 | 0.16018
8534 | 1.9408 | 0.16019
8535 | 1.9407 | 0.16021
8536 | 1.9407 | 0.16023
8537 | 1.9407 | 0.16025
8538 | 1.9407 | 0.16026
8539 | 1.9406 | 0.16028
8540 | 1.9406 | 0.1603
8541 | 1.9406 | 0.16031
8542 | 1.9406 | 0.16033
8543 | 1.9405 | 0.16035
8544 | 1.9405 | 0.16037
8545 | 1.9405 | 0.16038
8546 | 1.9405 | 0.1604
8547 | 1.9404 | 0.16042
8548 | 1.9404 | 0.16044
8549 | 1.9404 | 0.16045
8550 | 1.9404 | 0.16047
8551 | 1.9404 | 0.16049
8552 | 1.9403 | 0.16051
8553 | 1.9403 | 0.16052
8554 | 1.9403 | 0.16054
8555 | 1.9403 | 0.16056
8556 | 1.9402 | 0.16057
8557 | 1.9402 | 0.16059
8558 | 1.9402 | 0.16061
8559 | 1.9402 | 0.16063
8560 | 1.9401 | 0.16064
8561 | 1.9401 | 0.16066
8562 | 1.9401 | 0.16068
8563 | 1.9401 | 0.1607
8564 | 1.94 | 0.16071
8565 | 1.94 | 0.16073
8566 | 1.94 | 0.16075
8567 | 1.94 | 0.16076
8568 | 1.94 | 0.16078
8569 | 1.9399 | 0.1608
8570 | 1.9399 | 0.16082
8571 | 1.9399 | 0.16083
8572 | 1.9399 | 0.16085
8573 | 1.9398 | 0.16087
8574 | 1.9398 | 0.16089
8575 | 1.9398 | 0.1609
8576 | 1.9398 | 0.16092
8577 | 1.9397 | 0.16094
8578 | 1.9397 | 0.16096
8579 | 1.9397 | 0.16097
8580 | 1.9397 | 0.16099
8581 | 1.9396 | 0.16101
8582 | 1.9396 | 0.16102
8583 | 1.9396 | 0.16104
8584 | 1.9396 | 0.16106
8585 | 1.9396 | 0.16108
8586 | 1.9395 | 0.16109
8587 | 1.9395 | 0.16111
8588 | 1.9395 | 0.16113
8589 | 1.9395 | 0.16115
8590 | 1.9394 | 0.16116
8591 | 1.9394 | 0.16118
8592 | 1.9394 | 0.1612
8593 | 1.9394 | 0.16121
8594 | 1.9393 | 0.16123
8595 | 1.9393 | 0.16125
8596 | 1.9393 | 0.16127
8597 | 1.9393 | 0.16128
8598 | 1.9393 | 0.1613
8599 | 1.9392 | 0.16132
8600 | 1.9392 | 0.16134
8601 | 1.9392 | 0.16135
8602 | 1.9392 | 0.16137
8603 | 1.9391 | 0.16139
8604 | 1.9391 | 0.1614
8605 | 1.9391 | 0.16142
8606 | 1.9391 | 0.16144
8607 | 1.939 | 0.16146
8608 | 1.939 | 0.16147
8609 | 1.939 | 0.16149
8610 | 1.939 | 0.16151
8611 | 1.9389 | 0.16153
8612 | 1.9389 | 0.16154
8613 | 1.9389 | 0.16156
8614 | 1.9389 | 0.16158
8615 | 1.9389 | 0.1616
8616 | 1.9388 | 0.16161
8617 | 1.9388 | 0.16163
8618 | 1.9388 | 0.16165
8619 | 1.9388 | 0.16166
8620 | 1.9387 | 0.16168
8621 | 1.9387 | 0.1617
8622 | 1.9387 | 0.16172
8623 | 1.9387 | 0.16173
8624 | 1.9386 | 0.16175
8625 | 1.9386 | 0.16177
8626 | 1.9386 | 0.16179
8627 | 1.9386 | 0.1618
8628 | 1.9385 | 0.16182
8629 | 1.9385 | 0.16184
8630 | 1.9385 | 0.16185
8631 | 1.9385 | 0.16187
8632 | 1.9385 | 0.16189
8633 | 1.9384 | 0.16191
8634 | 1.9384 | 0.16192
8635 | 1.9384 | 0.16194
8636 | 1.9384 | 0.16196
8637 | 1.9383 | 0.16198
8638 | 1.9383 | 0.16199
8639 | 1.9383 | 0.16201
8640 | 1.9383 | 0.16203
8641 | 1.9382 | 0.16204
8642 | 1.9382 | 0.16206
8643 | 1.9382 | 0.16208
8644 | 1.9382 | 0.1621
8645 | 1.9381 | 0.16211
8646 | 1.9381 | 0.16213
8647 | 1.9381 | 0.16215
8648 | 1.9381 | 0.16217
8649 | 1.9381 | 0.16218
8650 | 1.938 | 0.1622
8651 | 1.938 | 0.16222
8652 | 1.938 | 0.16223
8653 | 1.938 | 0.16225
8654 | 1.9379 | 0.16227
8655 | 1.9379 | 0.16229
8656 | 1.9379 | 0.1623
8657 | 1.9379 | 0.16232
8658 | 1.9378 | 0.16234
8659 | 1.9378 | 0.16236
8660 | 1.9378 | 0.16237
8661 | 1.9378 | 0.16239
8662 | 1.9378 | 0.16241
8663 | 1.9377 | 0.16242
8664 | 1.9377 | 0.16244
8665 | 1.9377 | 0.16246
8666 | 1.9377 | 0.16248
8667 | 1.9376 | 0.16249
8668 | 1.9376 | 0.16251
8669 | 1.9376 | 0.16253
8670 | 1.9376 | 0.16255
8671 | 1.9375 | 0.16256
8672 | 1.9375 | 0.16258
8673 | 1.9375 | 0.1626
8674 | 1.9375 | 0.16261
8675 | 1.9374 | 0.16263
8676 | 1.9374 | 0.16265
8677 | 1.9374 | 0.16267
8678 | 1.9374 | 0.16268
8679 | 1.9374 | 0.1627
8680 | 1.9373 | 0.16272
8681 | 1.9373 | 0.16274
8682 | 1.9373 | 0.16275
8683 | 1.9373 | 0.16277
8684 | 1.9372 | 0.16279
8685 | 1.9372 | 0.16281
8686 | 1.9372 | 0.16282
8687 | 1.9372 | 0.16284
8688 | 1.9371 | 0.16286
8689 | 1.9371 | 0.16287
8690 | 1.9371 | 0.16289
8691 | 1.9371 | 0.16291
8692 | 1.9371 | 0.16293
8693 | 1.937 | 0.16294
8694 | 1.937 | 0.16296
8695 | 1.937 | 0.16298
8696 | 1.937 | 0.16299
8697 | 1.9369 | 0.16301
8698 | 1.9369 | 0.16303
8699 | 1.9369 | 0.16305
8700 | 1.9369 | 0.16306
8701 | 1.9368 | 0.16308
8702 | 1.9368 | 0.1631
8703 | 1.9368 | 0.16312
8704 | 1.9368 | 0.16313
8705 | 1.9367 | 0.16315
8706 | 1.9367 | 0.16317
8707 | 1.9367 | 0.16318
8708 | 1.9367 | 0.1632
8709 | 1.9367 | 0.16322
8710 | 1.9366 | 0.16324
8711 | 1.9366 | 0.16325
8712 | 1.9366 | 0.16327
8713 | 1.9366 | 0.16329
8714 | 1.9365 | 0.16331
8715 | 1.9365 | 0.16332
8716 | 1.9365 | 0.16334
8717 | 1.9365 | 0.16336
8718 | 1.9364 | 0.16337
8719 | 1.9364 | 0.16339
8720 | 1.9364 | 0.16341
8721 | 1.9364 | 0.16343
8722 | 1.9364 | 0.16344
8723 | 1.9363 | 0.16346
8724 | 1.9363 | 0.16348
8725 | 1.9363 | 0.1635
8726 | 1.9363 | 0.16351
8727 | 1.9362 | 0.16353
8728 | 1.9362 | 0.16355
8729 | 1.9362 | 0.16356
8730 | 1.9362 | 0.16358
8731 | 1.9361 | 0.1636
8732 | 1.9361 | 0.16362
8733 | 1.9361 | 0.16363
8734 | 1.9361 | 0.16365
8735 | 1.936 | 0.16367
8736 | 1.936 | 0.16369
8737 | 1.936 | 0.1637
8738 | 1.936 | 0.16372
8739 | 1.936 | 0.16374
8740 | 1.9359 | 0.16375
8741 | 1.9359 | 0.16377
8742 | 1.9359 | 0.16379
8743 | 1.9359 | 0.16381
8744 | 1.9358 | 0.16382
8745 | 1.9358 | 0.16384
8746 | 1.9358 | 0.16386
8747 | 1.9358 | 0.16388
8748 | 1.9357 | 0.16389
8749 | 1.9357 | 0.16391
8750 | 1.9357 | 0.16393
8751 | 1.9357 | 0.16394
8752 | 1.9357 | 0.16396
8753 | 1.9356 | 0.16398
8754 | 1.9356 | 0.164
8755 | 1.9356 | 0.16401
8756 | 1.9356 | 0.16403
8757 | 1.9355 | 0.16405
8758 | 1.9355 | 0.16407
8759 | 1.9355 | 0.16408
8760 | 1.9355 | 0.1641
8761 | 1.9354 | 0.16412
8762 | 1.9354 | 0.16413
8763 | 1.9354 | 0.16415
8764 | 1.9354 | 0.16417
8765 | 1.9353 | 0.16419
8766 | 1.9353 | 0.1642
8767 | 1.9353 | 0.16422
8768 | 1.9353 | 0.16424
8769 | 1.9353 | 0.16425
8770 | 1.9352 | 0.16427
8771 | 1.9352 | 0.16429
8772 | 1.9352 | 0.16431
8773 | 1.9352 | 0.16432
8774 | 1.9351 | 0.16434
8775 | 1.9351 | 0.16436
8776 | 1.9351 | 0.16438
8777 | 1.9351 | 0.16439
8778 | 1.935 | 0.16441
8779 | 1.935 | 0.16443
8780 | 1.935 | 0.16444
8781 | 1.935 | 0.16446
8782 | 1.935 | 0.16448
8783 | 1.9349 | 0.1645
8784 | 1.9349 | 0.16451
8785 | 1.9349 | 0.16453
8786 | 1.9349 | 0.16455
8787 | 1.9348 | 0.16457
8788 | 1.9348 | 0.16458
8789 | 1.9348 | 0.1646
8790 | 1.9348 | 0.16462
8791 | 1.9347 | 0.16463
8792 | 1.9347 | 0.16465
8793 | 1.9347 | 0.16467
8794 | 1.9347 | 0.16469
8795 | 1.9347 | 0.1647
8796 | 1.9346 | 0.16472
8797 | 1.9346 | 0.16474
8798 | 1.9346 | 0.16475
8799 | 1.9346 | 0.16477
8800 | 1.9345 | 0.16479
8801 | 1.9345 | 0.16481
8802 | 1.9345 | 0.16482
8803 | 1.9345 | 0.16484
8804 | 1.9344 | 0.16486
8805 | 1.9344 | 0.16488
8806 | 1.9344 | 0.16489
8807 | 1.9344 | 0.16491
8808 | 1.9343 | 0.16493
8809 | 1.9343 | 0.16494
8810 | 1.9343 | 0.16496
8811 | 1.9343 | 0.16498
8812 | 1.9343 | 0.165
8813 | 1.9342 | 0.16501
8814 | 1.9342 | 0.16503
8815 | 1.9342 | 0.16505
8816 | 1.9342 | 0.16507
8817 | 1.9341 | 0.16508
8818 | 1.9341 | 0.1651
8819 | 1.9341 | 0.16512
8820 | 1.9341 | 0.16513
8821 | 1.934 | 0.16515
8822 | 1.934 | 0.16517
8823 | 1.934 | 0.16519
8824 | 1.934 | 0.1652
8825 | 1.934 | 0.16522
8826 | 1.9339 | 0.16524
8827 | 1.9339 | 0.16525
8828 | 1.9339 | 0.16527
8829 | 1.9339 | 0.16529
8830 | 1.9338 | 0.16531
8831 | 1.9338 | 0.16532
8832 | 1.9338 | 0.16534
8833 | 1.9338 | 0.16536
8834 | 1.9337 | 0.16538
8835 | 1.9337 | 0.16539
8836 | 1.9337 | 0.16541
8837 | 1.9337 | 0.16543
8838 | 1.9337 | 0.16544
8839 | 1.9336 | 0.16546
8840 | 1.9336 | 0.16548
8841 | 1.9336 | 0.1655
8842 | 1.9336 | 0.16551
8843 | 1.9335 | 0.16553
8844 | 1.9335 | 0.16555
8845 | 1.9335 | 0.16556
8846 | 1.9335 | 0.16558
8847 | 1.9334 | 0.1656
8848 | 1.9334 | 0.16562
8849 | 1.9334 | 0.16563
8850 | 1.9334 | 0.16565
8851 | 1.9334 | 0.16567
8852 | 1.9333 | 0.16569
8853 | 1.9333 | 0.1657
8854 | 1.9333 | 0.16572
8855 | 1.9333 | 0.16574
8856 | 1.9332 | 0.16575
8857 | 1.9332 | 0.16577
8858 | 1.9332 | 0.16579
8859 | 1.9332 | 0.16581
8860 | 1.9331 | 0.16582
8861 | 1.9331 | 0.16584
8862 | 1.9331 | 0.16586
8863 | 1.9331 | 0.16587
8864 | 1.9331 | 0.16589
8865 | 1.933 | 0.16591
8866 | 1.933 | 0.16593
8867 | 1.933 | 0.16594
8868 | 1.933 | 0.16596
8869 | 1.9329 | 0.16598
8870 | 1.9329 | 0.166
8871 | 1.9329 | 0.16601
8872 | 1.9329 | 0.16603
8873 | 1.9328 | 0.16605
8874 | 1.9328 | 0.16606
8875 | 1.9328 | 0.16608
8876 | 1.9328 | 0.1661
8877 | 1.9327 | 0.16612
8878 | 1.9327 | 0.16613
8879 | 1.9327 | 0.16615
8880 | 1.9327 | 0.16617
8881 | 1.9327 | 0.16618
8882 | 1.9326 | 0.1662
8883 | 1.9326 | 0.16622
8884 | 1.9326 | 0.16624
8885 | 1.9326 | 0.16625
8886 | 1.9325 | 0.16627
8887 | 1.9325 | 0.16629
8888 | 1.9325 | 0.16631
8889 | 1.9325 | 0.16632
8890 | 1.9324 | 0.16634
8891 | 1.9324 | 0.16636
8892 | 1.9324 | 0.16637
8893 | 1.9324 | 0.16639
8894 | 1.9324 | 0.16641
8895 | 1.9323 | 0.16643
8896 | 1.9323 | 0.16644
8897 | 1.9323 | 0.16646
8898 | 1.9323 | 0.16648
8899 | 1.9322 | 0.16649
8900 | 1.9322 | 0.16651
8901 | 1.9322 | 0.16653
8902 | 1.9322 | 0.16655
8903 | 1.9321 | 0.16656
8904 | 1.9321 | 0.16658
8905 | 1.9321 | 0.1666
8906 | 1.9321 | 0.16662
8907 | 1.9321 | 0.16663
8908 | 1.932 | 0.16665
8909 | 1.932 | 0.16667
8910 | 1.932 | 0.16668
8911 | 1.932 | 0.1667
8912 | 1.9319 | 0.16672
8913 | 1.9319 | 0.16674
8914 | 1.9319 | 0.16675
8915 | 1.9319 | 0.16677
8916 | 1.9318 | 0.16679
8917 | 1.9318 | 0.1668
8918 | 1.9318 | 0.16682
8919 | 1.9318 | 0.16684
8920 | 1.9318 | 0.16686
8921 | 1.9317 | 0.16687
8922 | 1.9317 | 0.16689
8923 | 1.9317 | 0.16691
8924 | 1.9317 | 0.16692
8925 | 1.9316 | 0.16694
8926 | 1.9316 | 0.16696
8927 | 1.9316 | 0.16698
8928 | 1.9316 | 0.16699
8929 | 1.9315 | 0.16701
8930 | 1.9315 | 0.16703
8931 | 1.9315 | 0.16705
8932 | 1.9315 | 0.16706
8933 | 1.9315 | 0.16708
8934 | 1.9314 | 0.1671
8935 | 1.9314 | 0.16711
8936 | 1.9314 | 0.16713
8937 | 1.9314 | 0.16715
8938 | 1.9313 | 0.16717
8939 | 1.9313 | 0.16718
8940 | 1.9313 | 0.1672
8941 | 1.9313 | 0.16722
8942 | 1.9312 | 0.16723
8943 | 1.9312 | 0.16725
8944 | 1.9312 | 0.16727
8945 | 1.9312 | 0.16729
8946 | 1.9312 | 0.1673
8947 | 1.9311 | 0.16732
8948 | 1.9311 | 0.16734
8949 | 1.9311 | 0.16735
8950 | 1.9311 | 0.16737
8951 | 1.931 | 0.16739
8952 | 1.931 | 0.16741
8953 | 1.931 | 0.16742
8954 | 1.931 | 0.16744
8955 | 1.9309 | 0.16746
8956 | 1.9309 | 0.16748
8957 | 1.9309 | 0.16749
8958 | 1.9309 | 0.16751
8959 | 1.9309 | 0.16753
8960 | 1.9308 | 0.16754
8961 | 1.9308 | 0.16756
8962 | 1.9308 | 0.16758
8963 | 1.9308 | 0.1676
8964 | 1.9307 | 0.16761
8965 | 1.9307 | 0.16763
8966 | 1.9307 | 0.16765
8967 | 1.9307 | 0.16766
8968 | 1.9306 | 0.16768
8969 | 1.9306 | 0.1677
8970 | 1.9306 | 0.16772
8971 | 1.9306 | 0.16773
8972 | 1.9306 | 0.16775
8973 | 1.9305 | 0.16777
8974 | 1.9305 | 0.16778
8975 | 1.9305 | 0.1678
8976 | 1.9305 | 0.16782
8977 | 1.9304 | 0.16784
8978 | 1.9304 | 0.16785
8979 | 1.9304 | 0.16787
8980 | 1.9304 | 0.16789
8981 | 1.9303 | 0.1679
8982 | 1.9303 | 0.16792
8983 | 1.9303 | 0.16794
8984 | 1.9303 | 0.16796
8985 | 1.9303 | 0.16797
8986 | 1.9302 | 0.16799
8987 | 1.9302 | 0.16801
8988 | 1.9302 | 0.16803
8989 | 1.9302 | 0.16804
8990 | 1.9301 | 0.16806
8991 | 1.9301 | 0.16808
8992 | 1.9301 | 0.16809
8993 | 1.9301 | 0.16811
8994 | 1.93 | 0.16813
8995 | 1.93 | 0.16815
8996 | 1.93 | 0.16816
8997 | 1.93 | 0.16818
8998 | 1.93 | 0.1682
8999 | 1.9299 | 0.16821
9000 | 1.9299 | 0.16823
9001 | 1.9299 | 0.16825
9002 | 1.9299 | 0.16827
9003 | 1.9298 | 0.16828
9004 | 1.9298 | 0.1683
9005 | 1.9298 | 0.16832
9006 | 1.9298 | 0.16833
9007 | 1.9297 | 0.16835
9008 | 1.9297 | 0.16837
9009 | 1.9297 | 0.16839
9010 | 1.9297 | 0.1684
9011 | 1.9297 | 0.16842
9012 | 1.9296 | 0.16844
9013 | 1.9296 | 0.16845
9014 | 1.9296 | 0.16847
9015 | 1.9296 | 0.16849
9016 | 1.9295 | 0.16851
9017 | 1.9295 | 0.16852
9018 | 1.9295 | 0.16854
9019 | 1.9295 | 0.16856
9020 | 1.9294 | 0.16858
9021 | 1.9294 | 0.16859
9022 | 1.9294 | 0.16861
9023 | 1.9294 | 0.16863
9024 | 1.9294 | 0.16864
9025 | 1.9293 | 0.16866
9026 | 1.9293 | 0.16868
9027 | 1.9293 | 0.1687
9028 | 1.9293 | 0.16871
9029 | 1.9292 | 0.16873
9030 | 1.9292 | 0.16875
9031 | 1.9292 | 0.16876
9032 | 1.9292 | 0.16878
9033 | 1.9291 | 0.1688
9034 | 1.9291 | 0.16882
9035 | 1.9291 | 0.16883
9036 | 1.9291 | 0.16885
9037 | 1.9291 | 0.16887
9038 | 1.929 | 0.16888
9039 | 1.929 | 0.1689
9040 | 1.929 | 0.16892
9041 | 1.929 | 0.16894
9042 | 1.9289 | 0.16895
9043 | 1.9289 | 0.16897
9044 | 1.9289 | 0.16899
9045 | 1.9289 | 0.169
9046 | 1.9289 | 0.16902
9047 | 1.9288 | 0.16904
9048 | 1.9288 | 0.16906
9049 | 1.9288 | 0.16907
9050 | 1.9288 | 0.16909
9051 | 1.9287 | 0.16911
9052 | 1.9287 | 0.16912
9053 | 1.9287 | 0.16914
9054 | 1.9287 | 0.16916
9055 | 1.9286 | 0.16918
9056 | 1.9286 | 0.16919
9057 | 1.9286 | 0.16921
9058 | 1.9286 | 0.16923
9059 | 1.9286 | 0.16924
9060 | 1.9285 | 0.16926
9061 | 1.9285 | 0.16928
9062 | 1.9285 | 0.1693
9063 | 1.9285 | 0.16931
9064 | 1.9284 | 0.16933
9065 | 1.9284 | 0.16935
9066 | 1.9284 | 0.16936
9067 | 1.9284 | 0.16938
9068 | 1.9283 | 0.1694
9069 | 1.9283 | 0.16942
9070 | 1.9283 | 0.16943
9071 | 1.9283 | 0.16945
9072 | 1.9283 | 0.16947
9073 | 1.9282 | 0.16948
9074 | 1.9282 | 0.1695
9075 | 1.9282 | 0.16952
9076 | 1.9282 | 0.16954
9077 | 1.9281 | 0.16955
9078 | 1.9281 | 0.16957
9079 | 1.9281 | 0.16959
9080 | 1.9281 | 0.16961
9081 | 1.928 | 0.16962
9082 | 1.928 | 0.16964
9083 | 1.928 | 0.16966
9084 | 1.928 | 0.16967
9085 | 1.928 | 0.16969
9086 | 1.9279 | 0.16971
9087 | 1.9279 | 0.16973
9088 | 1.9279 | 0.16974
9089 | 1.9279 | 0.16976
9090 | 1.9278 | 0.16978
9091 | 1.9278 | 0.16979
9092 | 1.9278 | 0.16981
9093 | 1.9278 | 0.16983
9094 | 1.9277 | 0.16985
9095 | 1.9277 | 0.16986
9096 | 1.9277 | 0.16988
9097 | 1.9277 | 0.1699
9098 | 1.9277 | 0.16991
9099 | 1.9276 | 0.16993
9100 | 1.9276 | 0.16995
9101 | 1.9276 | 0.16997
9102 | 1.9276 | 0.16998
9103 | 1.9275 | 0.17
9104 | 1.9275 | 0.17002
9105 | 1.9275 | 0.17003
9106 | 1.9275 | 0.17005
9107 | 1.9275 | 0.17007
9108 | 1.9274 | 0.17009
9109 | 1.9274 | 0.1701
9110 | 1.9274 | 0.17012
9111 | 1.9274 | 0.17014
9112 | 1.9273 | 0.17015
9113 | 1.9273 | 0.17017
9114 | 1.9273 | 0.17019
9115 | 1.9273 | 0.17021
9116 | 1.9272 | 0.17022
9117 | 1.9272 | 0.17024
9118 | 1.9272 | 0.17026
9119 | 1.9272 | 0.17027
9120 | 1.9272 | 0.17029
9121 | 1.9271 | 0.17031
9122 | 1.9271 | 0.17033
9123 | 1.9271 | 0.17034
9124 | 1.9271 | 0.17036
9125 | 1.927 | 0.17038
9126 | 1.927 | 0.17039
9127 | 1.927 | 0.17041
9128 | 1.927 | 0.17043
9129 | 1.9269 | 0.17045
9130 | 1.9269 | 0.17046
9131 | 1.9269 | 0.17048
9132 | 1.9269 | 0.1705
9133 | 1.9269 | 0.17051
9134 | 1.9268 | 0.17053
9135 | 1.9268 | 0.17055
9136 | 1.9268 | 0.17057
9137 | 1.9268 | 0.17058
9138 | 1.9267 | 0.1706
9139 | 1.9267 | 0.17062
9140 | 1.9267 | 0.17063
9141 | 1.9267 | 0.17065
9142 | 1.9266 | 0.17067
9143 | 1.9266 | 0.17069
9144 | 1.9266 | 0.1707
9145 | 1.9266 | 0.17072
9146 | 1.9266 | 0.17074
9147 | 1.9265 | 0.17075
9148 | 1.9265 | 0.17077
9149 | 1.9265 | 0.17079
9150 | 1.9265 | 0.17081
9151 | 1.9264 | 0.17082
9152 | 1.9264 | 0.17084
9153 | 1.9264 | 0.17086
9154 | 1.9264 | 0.17087
9155 | 1.9264 | 0.17089
9156 | 1.9263 | 0.17091
9157 | 1.9263 | 0.17093
9158 | 1.9263 | 0.17094
9159 | 1.9263 | 0.17096
9160 | 1.9262 | 0.17098
9161 | 1.9262 | 0.17099
9162 | 1.9262 | 0.17101
9163 | 1.9262 | 0.17103
9164 | 1.9261 | 0.17105
9165 | 1.9261 | 0.17106
9166 | 1.9261 | 0.17108
9167 | 1.9261 | 0.1711
9168 | 1.9261 | 0.17111
9169 | 1.926 | 0.17113
9170 | 1.926 | 0.17115
9171 | 1.926 | 0.17117
9172 | 1.926 | 0.17118
9173 | 1.9259 | 0.1712
9174 | 1.9259 | 0.17122
9175 | 1.9259 | 0.17123
9176 | 1.9259 | 0.17125
9177 | 1.9258 | 0.17127
9178 | 1.9258 | 0.17129
9179 | 1.9258 | 0.1713
9180 | 1.9258 | 0.17132
9181 | 1.9258 | 0.17134
9182 | 1.9257 | 0.17135
9183 | 1.9257 | 0.17137
9184 | 1.9257 | 0.17139
9185 | 1.9257 | 0.17141
9186 | 1.9256 | 0.17142
9187 | 1.9256 | 0.17144
9188 | 1.9256 | 0.17146
9189 | 1.9256 | 0.17147
9190 | 1.9256 | 0.17149
9191 | 1.9255 | 0.17151
9192 | 1.9255 | 0.17152
9193 | 1.9255 | 0.17154
9194 | 1.9255 | 0.17156
9195 | 1.9254 | 0.17158
9196 | 1.9254 | 0.17159
9197 | 1.9254 | 0.17161
9198 | 1.9254 | 0.17163
9199 | 1.9253 | 0.17164
9200 | 1.9253 | 0.17166
9201 | 1.9253 | 0.17168
9202 | 1.9253 | 0.1717
9203 | 1.9253 | 0.17171
9204 | 1.9252 | 0.17173
9205 | 1.9252 | 0.17175
9206 | 1.9252 | 0.17176
9207 | 1.9252 | 0.17178
9208 | 1.9251 | 0.1718
9209 | 1.9251 | 0.17182
9210 | 1.9251 | 0.17183
9211 | 1.9251 | 0.17185
9212 | 1.925 | 0.17187
9213 | 1.925 | 0.17188
9214 | 1.925 | 0.1719
9215 | 1.925 | 0.17192
9216 | 1.925 | 0.17194
9217 | 1.9249 | 0.17195
9218 | 1.9249 | 0.17197
9219 | 1.9249 | 0.17199
9220 | 1.9249 | 0.172
9221 | 1.9248 | 0.17202
9222 | 1.9248 | 0.17204
9223 | 1.9248 | 0.17206
9224 | 1.9248 | 0.17207
9225 | 1.9248 | 0.17209
9226 | 1.9247 | 0.17211
9227 | 1.9247 | 0.17212
9228 | 1.9247 | 0.17214
9229 | 1.9247 | 0.17216
9230 | 1.9246 | 0.17218
9231 | 1.9246 | 0.17219
9232 | 1.9246 | 0.17221
9233 | 1.9246 | 0.17223
9234 | 1.9245 | 0.17224
9235 | 1.9245 | 0.17226
9236 | 1.9245 | 0.17228
9237 | 1.9245 | 0.1723
9238 | 1.9245 | 0.17231
9239 | 1.9244 | 0.17233
9240 | 1.9244 | 0.17235
9241 | 1.9244 | 0.17236
9242 | 1.9244 | 0.17238
9243 | 1.9243 | 0.1724
9244 | 1.9243 | 0.17242
9245 | 1.9243 | 0.17243
9246 | 1.9243 | 0.17245
9247 | 1.9243 | 0.17247
9248 | 1.9242 | 0.17248
9249 | 1.9242 | 0.1725
9250 | 1.9242 | 0.17252
9251 | 1.9242 | 0.17253
9252 | 1.9241 | 0.17255
9253 | 1.9241 | 0.17257
9254 | 1.9241 | 0.17259
9255 | 1.9241 | 0.1726
9256 | 1.924 | 0.17262
9257 | 1.924 | 0.17264
9258 | 1.924 | 0.17265
9259 | 1.924 | 0.17267
9260 | 1.924 | 0.17269
9261 | 1.9239 | 0.17271
9262 | 1.9239 | 0.17272
9263 | 1.9239 | 0.17274
9264 | 1.9239 | 0.17276
9265 | 1.9238 | 0.17277
9266 | 1.9238 | 0.17279
9267 | 1.9238 | 0.17281
9268 | 1.9238 | 0.17283
9269 | 1.9238 | 0.17284
9270 | 1.9237 | 0.17286
9271 | 1.9237 | 0.17288
9272 | 1.9237 | 0.17289
9273 | 1.9237 | 0.17291
9274 | 1.9236 | 0.17293
9275 | 1.9236 | 0.17295
9276 | 1.9236 | 0.17296
9277 | 1.9236 | 0.17298
9278 | 1.9235 | 0.173
9279 | 1.9235 | 0.17301
9280 | 1.9235 | 0.17303
9281 | 1.9235 | 0.17305
9282 | 1.9235 | 0.17307
9283 | 1.9234 | 0.17308
9284 | 1.9234 | 0.1731
9285 | 1.9234 | 0.17312
9286 | 1.9234 | 0.17313
9287 | 1.9233 | 0.17315
9288 | 1.9233 | 0.17317
9289 | 1.9233 | 0.17318
9290 | 1.9233 | 0.1732
9291 | 1.9233 | 0.17322
9292 | 1.9232 | 0.17324
9293 | 1.9232 | 0.17325
9294 | 1.9232 | 0.17327
9295 | 1.9232 | 0.17329
9296 | 1.9231 | 0.1733
9297 | 1.9231 | 0.17332
9298 | 1.9231 | 0.17334
9299 | 1.9231 | 0.17336
9300 | 1.923 | 0.17337
9301 | 1.923 | 0.17339
9302 | 1.923 | 0.17341
9303 | 1.923 | 0.17342
9304 | 1.923 | 0.17344
9305 | 1.9229 | 0.17346
9306 | 1.9229 | 0.17348
9307 | 1.9229 | 0.17349
9308 | 1.9229 | 0.17351
9309 | 1.9228 | 0.17353
9310 | 1.9228 | 0.17354
9311 | 1.9228 | 0.17356
9312 | 1.9228 | 0.17358
9313 | 1.9228 | 0.1736
9314 | 1.9227 | 0.17361
9315 | 1.9227 | 0.17363
9316 | 1.9227 | 0.17365
9317 | 1.9227 | 0.17366
9318 | 1.9226 | 0.17368
9319 | 1.9226 | 0.1737
9320 | 1.9226 | 0.17371
9321 | 1.9226 | 0.17373
9322 | 1.9225 | 0.17375
9323 | 1.9225 | 0.17377
9324 | 1.9225 | 0.17378
9325 | 1.9225 | 0.1738
9326 | 1.9225 | 0.17382
9327 | 1.9224 | 0.17383
9328 | 1.9224 | 0.17385
9329 | 1.9224 | 0.17387
9330 | 1.9224 | 0.17389
9331 | 1.9223 | 0.1739
9332 | 1.9223 | 0.17392
9333 | 1.9223 | 0.17394
9334 | 1.9223 | 0.17395
9335 | 1.9223 | 0.17397
9336 | 1.9222 | 0.17399
9337 | 1.9222 | 0.17401
9338 | 1.9222 | 0.17402
9339 | 1.9222 | 0.17404
9340 | 1.9221 | 0.17406
9341 | 1.9221 | 0.17407
9342 | 1.9221 | 0.17409
9343 | 1.9221 | 0.17411
9344 | 1.922 | 0.17412
9345 | 1.922 | 0.17414
9346 | 1.922 | 0.17416
9347 | 1.922 | 0.17418
9348 | 1.922 | 0.17419
9349 | 1.9219 | 0.17421
9350 | 1.9219 | 0.17423
9351 | 1.9219 | 0.17424
9352 | 1.9219 | 0.17426
9353 | 1.9218 | 0.17428
9354 | 1.9218 | 0.1743
9355 | 1.9218 | 0.17431
9356 | 1.9218 | 0.17433
9357 | 1.9218 | 0.17435
9358 | 1.9217 | 0.17436
9359 | 1.9217 | 0.17438
9360 | 1.9217 | 0.1744
9361 | 1.9217 | 0.17442
9362 | 1.9216 | 0.17443
9363 | 1.9216 | 0.17445
9364 | 1.9216 | 0.17447
9365 | 1.9216 | 0.17448
9366 | 1.9215 | 0.1745
9367 | 1.9215 | 0.17452
9368 | 1.9215 | 0.17453
9369 | 1.9215 | 0.17455
9370 | 1.9215 | 0.17457
9371 | 1.9214 | 0.17459
9372 | 1.9214 | 0.1746
9373 | 1.9214 | 0.17462
9374 | 1.9214 | 0.17464
9375 | 1.9213 | 0.17465
9376 | 1.9213 | 0.17467
9377 | 1.9213 | 0.17469
9378 | 1.9213 | 0.17471
9379 | 1.9213 | 0.17472
9380 | 1.9212 | 0.17474
9381 | 1.9212 | 0.17476
9382 | 1.9212 | 0.17477
9383 | 1.9212 | 0.17479
9384 | 1.9211 | 0.17481
9385 | 1.9211 | 0.17482
9386 | 1.9211 | 0.17484
9387 | 1.9211 | 0.17486
9388 | 1.9211 | 0.17488
9389 | 1.921 | 0.17489
9390 | 1.921 | 0.17491
9391 | 1.921 | 0.17493
9392 | 1.921 | 0.17494
9393 | 1.9209 | 0.17496
9394 | 1.9209 | 0.17498
9395 | 1.9209 | 0.175
9396 | 1.9209 | 0.17501
9397 | 1.9208 | 0.17503
9398 | 1.9208 | 0.17505
9399 | 1.9208 | 0.17506
9400 | 1.9208 | 0.17508
9401 | 1.9208 | 0.1751
9402 | 1.9207 | 0.17512
9403 | 1.9207 | 0.17513
9404 | 1.9207 | 0.17515
9405 | 1.9207 | 0.17517
9406 | 1.9206 | 0.17518
9407 | 1.9206 | 0.1752
9408 | 1.9206 | 0.17522
9409 | 1.9206 | 0.17523
9410 | 1.9206 | 0.17525
9411 | 1.9205 | 0.17527
9412 | 1.9205 | 0.17529
9413 | 1.9205 | 0.1753
9414 | 1.9205 | 0.17532
9415 | 1.9204 | 0.17534
9416 | 1.9204 | 0.17535
9417 | 1.9204 | 0.17537
9418 | 1.9204 | 0.17539
9419 | 1.9204 | 0.17541
9420 | 1.9203 | 0.17542
9421 | 1.9203 | 0.17544
9422 | 1.9203 | 0.17546
9423 | 1.9203 | 0.17547
9424 | 1.9202 | 0.17549
9425 | 1.9202 | 0.17551
9426 | 1.9202 | 0.17552
9427 | 1.9202 | 0.17554
9428 | 1.9201 | 0.17556
9429 | 1.9201 | 0.17558
9430 | 1.9201 | 0.17559
9431 | 1.9201 | 0.17561
9432 | 1.9201 | 0.17563
9433 | 1.92 | 0.17564
9434 | 1.92 | 0.17566
9435 | 1.92 | 0.17568
9436 | 1.92 | 0.1757
9437 | 1.9199 | 0.17571
9438 | 1.9199 | 0.17573
9439 | 1.9199 | 0.17575
9440 | 1.9199 | 0.17576
9441 | 1.9199 | 0.17578
9442 | 1.9198 | 0.1758
9443 | 1.9198 | 0.17581
9444 | 1.9198 | 0.17583
9445 | 1.9198 | 0.17585
9446 | 1.9197 | 0.17587
9447 | 1.9197 | 0.17588
9448 | 1.9197 | 0.1759
9449 | 1.9197 | 0.17592
9450 | 1.9196 | 0.17593
9451 | 1.9196 | 0.17595
9452 | 1.9196 | 0.17597
9453 | 1.9196 | 0.17599
9454 | 1.9196 | 0.176
9455 | 1.9195 | 0.17602
9456 | 1.9195 | 0.17604
9457 | 1.9195 | 0.17605
9458 | 1.9195 | 0.17607
9459 | 1.9194 | 0.17609
9460 | 1.9194 | 0.1761
9461 | 1.9194 | 0.17612
9462 | 1.9194 | 0.17614
9463 | 1.9194 | 0.17616
9464 | 1.9193 | 0.17617
9465 | 1.9193 | 0.17619
9466 | 1.9193 | 0.17621
9467 | 1.9193 | 0.17622
9468 | 1.9192 | 0.17624
9469 | 1.9192 | 0.17626
9470 | 1.9192 | 0.17627
9471 | 1.9192 | 0.17629
9472 | 1.9192 | 0.17631
9473 | 1.9191 | 0.17633
9474 | 1.9191 | 0.17634
9475 | 1.9191 | 0.17636
9476 | 1.9191 | 0.17638
9477 | 1.919 | 0.17639
9478 | 1.919 | 0.17641
9479 | 1.919 | 0.17643
9480 | 1.919 | 0.17645
9481 | 1.919 | 0.17646
9482 | 1.9189 | 0.17648
9483 | 1.9189 | 0.1765
9484 | 1.9189 | 0.17651
9485 | 1.9189 | 0.17653
9486 | 1.9188 | 0.17655
9487 | 1.9188 | 0.17656
9488 | 1.9188 | 0.17658
9489 | 1.9188 | 0.1766
9490 | 1.9187 | 0.17662
9491 | 1.9187 | 0.17663
9492 | 1.9187 | 0.17665
9493 | 1.9187 | 0.17667
9494 | 1.9187 | 0.17668
9495 | 1.9186 | 0.1767
9496 | 1.9186 | 0.17672
9497 | 1.9186 | 0.17674
9498 | 1.9186 | 0.17675
9499 | 1.9185 | 0.17677
9500 | 1.9185 | 0.17679
9501 | 1.9185 | 0.1768
9502 | 1.9185 | 0.17682
9503 | 1.9185 | 0.17684
9504 | 1.9184 | 0.17685
9505 | 1.9184 | 0.17687
9506 | 1.9184 | 0.17689
9507 | 1.9184 | 0.17691
9508 | 1.9183 | 0.17692
9509 | 1.9183 | 0.17694
9510 | 1.9183 | 0.17696
9511 | 1.9183 | 0.17697
9512 | 1.9183 | 0.17699
9513 | 1.9182 | 0.17701
9514 | 1.9182 | 0.17702
9515 | 1.9182 | 0.17704
9516 | 1.9182 | 0.17706
9517 | 1.9181 | 0.17708
9518 | 1.9181 | 0.17709
9519 | 1.9181 | 0.17711
9520 | 1.9181 | 0.17713
9521 | 1.918 | 0.17714
9522 | 1.918 | 0.17716
9523 | 1.918 | 0.17718
9524 | 1.918 | 0.17719
9525 | 1.918 | 0.17721
9526 | 1.9179 | 0.17723
9527 | 1.9179 | 0.17725
9528 | 1.9179 | 0.17726
9529 | 1.9179 | 0.17728
9530 | 1.9178 | 0.1773
9531 | 1.9178 | 0.17731
9532 | 1.9178 | 0.17733
9533 | 1.9178 | 0.17735
9534 | 1.9178 | 0.17737
9535 | 1.9177 | 0.17738
9536 | 1.9177 | 0.1774
9537 | 1.9177 | 0.17742
9538 | 1.9177 | 0.17743
9539 | 1.9176 | 0.17745
9540 | 1.9176 | 0.17747
9541 | 1.9176 | 0.17748
9542 | 1.9176 | 0.1775
9543 | 1.9176 | 0.17752
9544 | 1.9175 | 0.17754
9545 | 1.9175 | 0.17755
9546 | 1.9175 | 0.17757
9547 | 1.9175 | 0.17759
9548 | 1.9174 | 0.1776
9549 | 1.9174 | 0.17762
9550 | 1.9174 | 0.17764
9551 | 1.9174 | 0.17765
9552 | 1.9174 | 0.17767
9553 | 1.9173 | 0.17769
9554 | 1.9173 | 0.17771
9555 | 1.9173 | 0.17772
9556 | 1.9173 | 0.17774
9557 | 1.9172 | 0.17776
9558 | 1.9172 | 0.17777
9559 | 1.9172 | 0.17779
9560 | 1.9172 | 0.17781
9561 | 1.9172 | 0.17782
9562 | 1.9171 | 0.17784
9563 | 1.9171 | 0.17786
9564 | 1.9171 | 0.17788
9565 | 1.9171 | 0.17789
9566 | 1.917 | 0.17791
9567 | 1.917 | 0.17793
9568 | 1.917 | 0.17794
9569 | 1.917 | 0.17796
9570 | 1.9169 | 0.17798
9571 | 1.9169 | 0.178
9572 | 1.9169 | 0.17801
9573 | 1.9169 | 0.17803
9574 | 1.9169 | 0.17805
9575 | 1.9168 | 0.17806
9576 | 1.9168 | 0.17808
9577 | 1.9168 | 0.1781
9578 | 1.9168 | 0.17811
9579 | 1.9167 | 0.17813
9580 | 1.9167 | 0.17815
9581 | 1.9167 | 0.17817
9582 | 1.9167 | 0.17818
9583 | 1.9167 | 0.1782
9584 | 1.9166 | 0.17822
9585 | 1.9166 | 0.17823
9586 | 1.9166 | 0.17825
9587 | 1.9166 | 0.17827
9588 | 1.9165 | 0.17828
9589 | 1.9165 | 0.1783
9590 | 1.9165 | 0.17832
9591 | 1.9165 | 0.17834
9592 | 1.9165 | 0.17835
9593 | 1.9164 | 0.17837
9594 | 1.9164 | 0.17839
9595 | 1.9164 | 0.1784
9596 | 1.9164 | 0.17842
9597 | 1.9163 | 0.17844
9598 | 1.9163 | 0.17845
9599 | 1.9163 | 0.17847
9600 | 1.9163 | 0.17849
9601 | 1.9163 | 0.17851
9602 | 1.9162 | 0.17852
9603 | 1.9162 | 0.17854
9604 | 1.9162 | 0.17856
9605 | 1.9162 | 0.17857
9606 | 1.9161 | 0.17859
9607 | 1.9161 | 0.17861
9608 | 1.9161 | 0.17862
9609 | 1.9161 | 0.17864
9610 | 1.9161 | 0.17866
9611 | 1.916 | 0.17868
9612 | 1.916 | 0.17869
9613 | 1.916 | 0.17871
9614 | 1.916 | 0.17873
9615 | 1.9159 | 0.17874
9616 | 1.9159 | 0.17876
9617 | 1.9159 | 0.17878
9618 | 1.9159 | 0.17879
9619 | 1.9158 | 0.17881
9620 | 1.9158 | 0.17883
9621 | 1.9158 | 0.17885
9622 | 1.9158 | 0.17886
9623 | 1.9158 | 0.17888
9624 | 1.9157 | 0.1789
9625 | 1.9157 | 0.17891
9626 | 1.9157 | 0.17893
9627 | 1.9157 | 0.17895
9628 | 1.9156 | 0.17896
9629 | 1.9156 | 0.17898
9630 | 1.9156 | 0.179
9631 | 1.9156 | 0.17902
9632 | 1.9156 | 0.17903
9633 | 1.9155 | 0.17905
9634 | 1.9155 | 0.17907
9635 | 1.9155 | 0.17908
9636 | 1.9155 | 0.1791
9637 | 1.9154 | 0.17912
9638 | 1.9154 | 0.17913
9639 | 1.9154 | 0.17915
9640 | 1.9154 | 0.17917
9641 | 1.9154 | 0.17919
9642 | 1.9153 | 0.1792
9643 | 1.9153 | 0.17922
9644 | 1.9153 | 0.17924
9645 | 1.9153 | 0.17925
9646 | 1.9152 | 0.17927
9647 | 1.9152 | 0.17929
9648 | 1.9152 | 0.1793
9649 | 1.9152 | 0.17932
9650 | 1.9152 | 0.17934
9651 | 1.9151 | 0.17936
9652 | 1.9151 | 0.17937
9653 | 1.9151 | 0.17939
9654 | 1.9151 | 0.17941
9655 | 1.915 | 0.17942
9656 | 1.915 | 0.17944
9657 | 1.915 | 0.17946
9658 | 1.915 | 0.17947
9659 | 1.915 | 0.17949
9660 | 1.9149 | 0.17951
9661 | 1.9149 | 0.17953
9662 | 1.9149 | 0.17954
9663 | 1.9149 | 0.17956
9664 | 1.9148 | 0.17958
9665 | 1.9148 | 0.17959
9666 | 1.9148 | 0.17961
9667 | 1.9148 | 0.17963
9668 | 1.9148 | 0.17964
9669 | 1.9147 | 0.17966
9670 | 1.9147 | 0.17968
9671 | 1.9147 | 0.1797
9672 | 1.9147 | 0.17971
9673 | 1.9146 | 0.17973
9674 | 1.9146 | 0.17975
9675 | 1.9146 | 0.17976
9676 | 1.9146 | 0.17978
9677 | 1.9146 | 0.1798
9678 | 1.9145 | 0.17981
9679 | 1.9145 | 0.17983
9680 | 1.9145 | 0.17985
9681 | 1.9145 | 0.17987
9682 | 1.9144 | 0.17988
9683 | 1.9144 | 0.1799
9684 | 1.9144 | 0.17992
9685 | 1.9144 | 0.17993
9686 | 1.9144 | 0.17995
9687 | 1.9143 | 0.17997
9688 | 1.9143 | 0.17998
9689 | 1.9143 | 0.18
9690 | 1.9143 | 0.18002
9691 | 1.9142 | 0.18004
9692 | 1.9142 | 0.18005
9693 | 1.9142 | 0.18007
9694 | 1.9142 | 0.18009
9695 | 1.9142 | 0.1801
9696 | 1.9141 | 0.18012
9697 | 1.9141 | 0.18014
9698 | 1.9141 | 0.18015
9699 | 1.9141 | 0.18017
9700 | 1.914 | 0.18019
9701 | 1.914 | 0.18021
9702 | 1.914 | 0.18022
9703 | 1.914 | 0.18024
9704 | 1.9139 | 0.18026
9705 | 1.9139 | 0.18027
9706 | 1.9139 | 0.18029
9707 | 1.9139 | 0.18031
9708 | 1.9139 | 0.18032
9709 | 1.9138 | 0.18034
9710 | 1.9138 | 0.18036
9711 | 1.9138 | 0.18037
9712 | 1.9138 | 0.18039
9713 | 1.9137 | 0.18041
9714 | 1.9137 | 0.18043
9715 | 1.9137 | 0.18044
9716 | 1.9137 | 0.18046
9717 | 1.9137 | 0.18048
9718 | 1.9136 | 0.18049
9719 | 1.9136 | 0.18051
9720 | 1.9136 | 0.18053
9721 | 1.9136 | 0.18054
9722 | 1.9135 | 0.18056
9723 | 1.9135 | 0.18058
9724 | 1.9135 | 0.1806
9725 | 1.9135 | 0.18061
9726 | 1.9135 | 0.18063
9727 | 1.9134 | 0.18065
9728 | 1.9134 | 0.18066
9729 | 1.9134 | 0.18068
9730 | 1.9134 | 0.1807
9731 | 1.9133 | 0.18071
9732 | 1.9133 | 0.18073
9733 | 1.9133 | 0.18075
9734 | 1.9133 | 0.18077
9735 | 1.9133 | 0.18078
9736 | 1.9132 | 0.1808
9737 | 1.9132 | 0.18082
9738 | 1.9132 | 0.18083
9739 | 1.9132 | 0.18085
9740 | 1.9131 | 0.18087
9741 | 1.9131 | 0.18088
9742 | 1.9131 | 0.1809
9743 | 1.9131 | 0.18092
9744 | 1.9131 | 0.18094
9745 | 1.913 | 0.18095
9746 | 1.913 | 0.18097
9747 | 1.913 | 0.18099
9748 | 1.913 | 0.181
9749 | 1.9129 | 0.18102
9750 | 1.9129 | 0.18104
9751 | 1.9129 | 0.18105
9752 | 1.9129 | 0.18107
9753 | 1.9129 | 0.18109
9754 | 1.9128 | 0.1811
9755 | 1.9128 | 0.18112
9756 | 1.9128 | 0.18114
9757 | 1.9128 | 0.18116
9758 | 1.9127 | 0.18117
9759 | 1.9127 | 0.18119
9760 | 1.9127 | 0.18121
9761 | 1.9127 | 0.18122
9762 | 1.9127 | 0.18124
9763 | 1.9126 | 0.18126
9764 | 1.9126 | 0.18127
9765 | 1.9126 | 0.18129
9766 | 1.9126 | 0.18131
9767 | 1.9125 | 0.18133
9768 | 1.9125 | 0.18134
9769 | 1.9125 | 0.18136
9770 | 1.9125 | 0.18138
9771 | 1.9125 | 0.18139
9772 | 1.9124 | 0.18141
9773 | 1.9124 | 0.18143
9774 | 1.9124 | 0.18144
9775 | 1.9124 | 0.18146
9776 | 1.9123 | 0.18148
9777 | 1.9123 | 0.18149
9778 | 1.9123 | 0.18151
9779 | 1.9123 | 0.18153
9780 | 1.9123 | 0.18155
9781 | 1.9122 | 0.18156
9782 | 1.9122 | 0.18158
9783 | 1.9122 | 0.1816
9784 | 1.9122 | 0.18161
9785 | 1.9121 | 0.18163
9786 | 1.9121 | 0.18165
9787 | 1.9121 | 0.18166
9788 | 1.9121 | 0.18168
9789 | 1.9121 | 0.1817
9790 | 1.912 | 0.18172
9791 | 1.912 | 0.18173
9792 | 1.912 | 0.18175
9793 | 1.912 | 0.18177
9794 | 1.9119 | 0.18178
9795 | 1.9119 | 0.1818
9796 | 1.9119 | 0.18182
9797 | 1.9119 | 0.18183
9798 | 1.9119 | 0.18185
9799 | 1.9118 | 0.18187
9800 | 1.9118 | 0.18188
9801 | 1.9118 | 0.1819
9802 | 1.9118 | 0.18192
9803 | 1.9117 | 0.18194
9804 | 1.9117 | 0.18195
9805 | 1.9117 | 0.18197
9806 | 1.9117 | 0.18199
9807 | 1.9117 | 0.182
9808 | 1.9116 | 0.18202
9809 | 1.9116 | 0.18204
9810 | 1.9116 | 0.18205
9811 | 1.9116 | 0.18207
9812 | 1.9115 | 0.18209
9813 | 1.9115 | 0.18211
9814 | 1.9115 | 0.18212
9815 | 1.9115 | 0.18214
9816 | 1.9115 | 0.18216
9817 | 1.9114 | 0.18217
9818 | 1.9114 | 0.18219
9819 | 1.9114 | 0.18221
9820 | 1.9114 | 0.18222
9821 | 1.9113 | 0.18224
9822 | 1.9113 | 0.18226
9823 | 1.9113 | 0.18227
9824 | 1.9113 | 0.18229
9825 | 1.9113 | 0.18231
9826 | 1.9112 | 0.18233
9827 | 1.9112 | 0.18234
9828 | 1.9112 | 0.18236
9829 | 1.9112 | 0.18238
9830 | 1.9111 | 0.18239
9831 | 1.9111 | 0.18241
9832 | 1.9111 | 0.18243
9833 | 1.9111 | 0.18244
9834 | 1.9111 | 0.18246
9835 | 1.911 | 0.18248
9836 | 1.911 | 0.1825
9837 | 1.911 | 0.18251
9838 | 1.911 | 0.18253
9839 | 1.9109 | 0.18255
9840 | 1.9109 | 0.18256
9841 | 1.9109 | 0.18258
9842 | 1.9109 | 0.1826
9843 | 1.9109 | 0.18261
9844 | 1.9108 | 0.18263
9845 | 1.9108 | 0.18265
9846 | 1.9108 | 0.18266
9847 | 1.9108 | 0.18268
9848 | 1.9107 | 0.1827
9849 | 1.9107 | 0.18272
9850 | 1.9107 | 0.18273
9851 | 1.9107 | 0.18275
9852 | 1.9107 | 0.18277
9853 | 1.9106 | 0.18278
9854 | 1.9106 | 0.1828
9855 | 1.9106 | 0.18282
9856 | 1.9106 | 0.18283
9857 | 1.9105 | 0.18285
9858 | 1.9105 | 0.18287
9859 | 1.9105 | 0.18288
9860 | 1.9105 | 0.1829
9861 | 1.9105 | 0.18292
9862 | 1.9104 | 0.18294
9863 | 1.9104 | 0.18295
9864 | 1.9104 | 0.18297
9865 | 1.9104 | 0.18299
9866 | 1.9103 | 0.183
9867 | 1.9103 | 0.18302
9868 | 1.9103 | 0.18304
9869 | 1.9103 | 0.18305
9870 | 1.9103 | 0.18307
9871 | 1.9102 | 0.18309
9872 | 1.9102 | 0.1831
9873 | 1.9102 | 0.18312
9874 | 1.9102 | 0.18314
9875 | 1.9101 | 0.18316
9876 | 1.9101 | 0.18317
9877 | 1.9101 | 0.18319
9878 | 1.9101 | 0.18321
9879 | 1.9101 | 0.18322
9880 | 1.91 | 0.18324
9881 | 1.91 | 0.18326
9882 | 1.91 | 0.18327
9883 | 1.91 | 0.18329
9884 | 1.9099 | 0.18331
9885 | 1.9099 | 0.18332
9886 | 1.9099 | 0.18334
9887 | 1.9099 | 0.18336
9888 | 1.9099 | 0.18338
9889 | 1.9098 | 0.18339
9890 | 1.9098 | 0.18341
9891 | 1.9098 | 0.18343
9892 | 1.9098 | 0.18344
9893 | 1.9097 | 0.18346
9894 | 1.9097 | 0.18348
9895 | 1.9097 | 0.18349
9896 | 1.9097 | 0.18351
9897 | 1.9097 | 0.18353
9898 | 1.9096 | 0.18355
9899 | 1.9096 | 0.18356
9900 | 1.9096 | 0.18358
9901 | 1.9096 | 0.1836
9902 | 1.9096 | 0.18361
9903 | 1.9095 | 0.18363
9904 | 1.9095 | 0.18365
9905 | 1.9095 | 0.18366
9906 | 1.9095 | 0.18368
9907 | 1.9094 | 0.1837
9908 | 1.9094 | 0.18371
9909 | 1.9094 | 0.18373
9910 | 1.9094 | 0.18375
9911 | 1.9094 | 0.18377
9912 | 1.9093 | 0.18378
9913 | 1.9093 | 0.1838
9914 | 1.9093 | 0.18382
9915 | 1.9093 | 0.18383
9916 | 1.9092 | 0.18385
9917 | 1.9092 | 0.18387
9918 | 1.9092 | 0.18388
9919 | 1.9092 | 0.1839
9920 | 1.9092 | 0.18392
9921 | 1.9091 | 0.18393
9922 | 1.9091 | 0.18395
9923 | 1.9091 | 0.18397
9924 | 1.9091 | 0.18398
9925 | 1.909 | 0.184
9926 | 1.909 | 0.18402
9927 | 1.909 | 0.18404
9928 | 1.909 | 0.18405
9929 | 1.909 | 0.18407
9930 | 1.9089 | 0.18409
9931 | 1.9089 | 0.1841
9932 | 1.9089 | 0.18412
9933 | 1.9089 | 0.18414
9934 | 1.9088 | 0.18415
9935 | 1.9088 | 0.18417
9936 | 1.9088 | 0.18419
9937 | 1.9088 | 0.1842
9938 | 1.9088 | 0.18422
9939 | 1.9087 | 0.18424
9940 | 1.9087 | 0.18426
9941 | 1.9087 | 0.18427
9942 | 1.9087 | 0.18429
9943 | 1.9086 | 0.18431
9944 | 1.9086 | 0.18432
9945 | 1.9086 | 0.18434
9946 | 1.9086 | 0.18436
9947 | 1.9086 | 0.18437
9948 | 1.9085 | 0.18439
9949 | 1.9085 | 0.18441
9950 | 1.9085 | 0.18442
9951 | 1.9085 | 0.18444
9952 | 1.9084 | 0.18446
9953 | 1.9084 | 0.18448
9954 | 1.9084 | 0.18449
9955 | 1.9084 | 0.18451
9956 | 1.9084 | 0.18453
9957 | 1.9083 | 0.18454
9958 | 1.9083 | 0.18456
9959 | 1.9083 | 0.18458
9960 | 1.9083 | 0.18459
9961 | 1.9082 | 0.18461
9962 | 1.9082 | 0.18463
9963 | 1.9082 | 0.18464
9964 | 1.9082 | 0.18466
9965 | 1.9082 | 0.18468
9966 | 1.9081 | 0.1847
9967 | 1.9081 | 0.18471
9968 | 1.9081 | 0.18473
9969 | 1.9081 | 0.18475
9970 | 1.908 | 0.18476
9971 | 1.908 | 0.18478
9972 | 1.908 | 0.1848
9973 | 1.908 | 0.18481
9974 | 1.908 | 0.18483
9975 | 1.9079 | 0.18485
9976 | 1.9079 | 0.18486
9977 | 1.9079 | 0.18488
9978 | 1.9079 | 0.1849
9979 | 1.9078 | 0.18492
9980 | 1.9078 | 0.18493
9981 | 1.9078 | 0.18495
9982 | 1.9078 | 0.18497
9983 | 1.9078 | 0.18498
9984 | 1.9077 | 0.185
9985 | 1.9077 | 0.18502
9986 | 1.9077 | 0.18503
9987 | 1.9077 | 0.18505
9988 | 1.9077 | 0.18507
9989 | 1.9076 | 0.18508
9990 | 1.9076 | 0.1851
9991 | 1.9076 | 0.18512
9992 | 1.9076 | 0.18513
9993 | 1.9075 | 0.18515
9994 | 1.9075 | 0.18517
9995 | 1.9075 | 0.18519
9996 | 1.9075 | 0.1852
9997 | 1.9075 | 0.18522
9998 | 1.9074 | 0.18524
9999 | 1.9074 | 0.18525
10000 | 1.9074 | 0.18527
10001 | 1.9074 | 0.18529
10002 | 1.9073 | 0.1853
10003 | 1.9073 | 0.18532
10004 | 1.9073 | 0.18534
10005 | 1.9073 | 0.18535
10006 | 1.9073 | 0.18537
10007 | 1.9072 | 0.18539
10008 | 1.9072 | 0.18541
10009 | 1.9072 | 0.18542
10010 | 1.9072 | 0.18544
10011 | 1.9071 | 0.18546
10012 | 1.9071 | 0.18547
10013 | 1.9071 | 0.18549
10014 | 1.9071 | 0.18551
10015 | 1.9071 | 0.18552
10016 | 1.907 | 0.18554
10017 | 1.907 | 0.18556
10018 | 1.907 | 0.18557
10019 | 1.907 | 0.18559
10020 | 1.9069 | 0.18561
10021 | 1.9069 | 0.18562
10022 | 1.9069 | 0.18564
10023 | 1.9069 | 0.18566
10024 | 1.9069 | 0.18568
10025 | 1.9068 | 0.18569
10026 | 1.9068 | 0.18571
10027 | 1.9068 | 0.18573
10028 | 1.9068 | 0.18574
10029 | 1.9067 | 0.18576
10030 | 1.9067 | 0.18578
10031 | 1.9067 | 0.18579
10032 | 1.9067 | 0.18581
10033 | 1.9067 | 0.18583
10034 | 1.9066 | 0.18584
10035 | 1.9066 | 0.18586
10036 | 1.9066 | 0.18588
10037 | 1.9066 | 0.1859
10038 | 1.9066 | 0.18591
10039 | 1.9065 | 0.18593
10040 | 1.9065 | 0.18595
10041 | 1.9065 | 0.18596
10042 | 1.9065 | 0.18598
10043 | 1.9064 | 0.186
10044 | 1.9064 | 0.18601
10045 | 1.9064 | 0.18603
10046 | 1.9064 | 0.18605
10047 | 1.9064 | 0.18606
10048 | 1.9063 | 0.18608
10049 | 1.9063 | 0.1861
10050 | 1.9063 | 0.18611
10051 | 1.9063 | 0.18613
10052 | 1.9062 | 0.18615
10053 | 1.9062 | 0.18617
10054 | 1.9062 | 0.18618
10055 | 1.9062 | 0.1862
10056 | 1.9062 | 0.18622
10057 | 1.9061 | 0.18623
10058 | 1.9061 | 0.18625
10059 | 1.9061 | 0.18627
10060 | 1.9061 | 0.18628
10061 | 1.906 | 0.1863
10062 | 1.906 | 0.18632
10063 | 1.906 | 0.18633
10064 | 1.906 | 0.18635
10065 | 1.906 | 0.18637
10066 | 1.9059 | 0.18638
10067 | 1.9059 | 0.1864
10068 | 1.9059 | 0.18642
10069 | 1.9059 | 0.18644
10070 | 1.9058 | 0.18645
10071 | 1.9058 | 0.18647
10072 | 1.9058 | 0.18649
10073 | 1.9058 | 0.1865
10074 | 1.9058 | 0.18652
10075 | 1.9057 | 0.18654
10076 | 1.9057 | 0.18655
10077 | 1.9057 | 0.18657
10078 | 1.9057 | 0.18659
10079 | 1.9056 | 0.1866
10080 | 1.9056 | 0.18662
10081 | 1.9056 | 0.18664
10082 | 1.9056 | 0.18665
10083 | 1.9056 | 0.18667
10084 | 1.9055 | 0.18669
10085 | 1.9055 | 0.18671
10086 | 1.9055 | 0.18672
10087 | 1.9055 | 0.18674
10088 | 1.9055 | 0.18676
10089 | 1.9054 | 0.18677
10090 | 1.9054 | 0.18679
10091 | 1.9054 | 0.18681
10092 | 1.9054 | 0.18682
10093 | 1.9053 | 0.18684
10094 | 1.9053 | 0.18686
10095 | 1.9053 | 0.18687
10096 | 1.9053 | 0.18689
10097 | 1.9053 | 0.18691
10098 | 1.9052 | 0.18692
10099 | 1.9052 | 0.18694
10100 | 1.9052 | 0.18696
10101 | 1.9052 | 0.18698
10102 | 1.9051 | 0.18699
10103 | 1.9051 | 0.18701
10104 | 1.9051 | 0.18703
10105 | 1.9051 | 0.18704
10106 | 1.9051 | 0.18706
10107 | 1.905 | 0.18708
10108 | 1.905 | 0.18709
10109 | 1.905 | 0.18711
10110 | 1.905 | 0.18713
10111 | 1.9049 | 0.18714
10112 | 1.9049 | 0.18716
10113 | 1.9049 | 0.18718
10114 | 1.9049 | 0.18719
10115 | 1.9049 | 0.18721
10116 | 1.9048 | 0.18723
10117 | 1.9048 | 0.18725
10118 | 1.9048 | 0.18726
10119 | 1.9048 | 0.18728
10120 | 1.9048 | 0.1873
10121 | 1.9047 | 0.18731
10122 | 1.9047 | 0.18733
10123 | 1.9047 | 0.18735
10124 | 1.9047 | 0.18736
10125 | 1.9046 | 0.18738
10126 | 1.9046 | 0.1874
10127 | 1.9046 | 0.18741
10128 | 1.9046 | 0.18743
10129 | 1.9046 | 0.18745
10130 | 1.9045 | 0.18746
10131 | 1.9045 | 0.18748
10132 | 1.9045 | 0.1875
10133 | 1.9045 | 0.18752
10134 | 1.9044 | 0.18753
10135 | 1.9044 | 0.18755
10136 | 1.9044 | 0.18757
10137 | 1.9044 | 0.18758
10138 | 1.9044 | 0.1876
10139 | 1.9043 | 0.18762
10140 | 1.9043 | 0.18763
10141 | 1.9043 | 0.18765
10142 | 1.9043 | 0.18767
10143 | 1.9042 | 0.18768
10144 | 1.9042 | 0.1877
10145 | 1.9042 | 0.18772
10146 | 1.9042 | 0.18773
10147 | 1.9042 | 0.18775
10148 | 1.9041 | 0.18777
10149 | 1.9041 | 0.18778
10150 | 1.9041 | 0.1878
10151 | 1.9041 | 0.18782
10152 | 1.9041 | 0.18784
10153 | 1.904 | 0.18785
10154 | 1.904 | 0.18787
10155 | 1.904 | 0.18789
10156 | 1.904 | 0.1879
10157 | 1.9039 | 0.18792
10158 | 1.9039 | 0.18794
10159 | 1.9039 | 0.18795
10160 | 1.9039 | 0.18797
10161 | 1.9039 | 0.18799
10162 | 1.9038 | 0.188
10163 | 1.9038 | 0.18802
10164 | 1.9038 | 0.18804
10165 | 1.9038 | 0.18805
10166 | 1.9037 | 0.18807
10167 | 1.9037 | 0.18809
10168 | 1.9037 | 0.1881
10169 | 1.9037 | 0.18812
10170 | 1.9037 | 0.18814
10171 | 1.9036 | 0.18816
10172 | 1.9036 | 0.18817
10173 | 1.9036 | 0.18819
10174 | 1.9036 | 0.18821
10175 | 1.9035 | 0.18822
10176 | 1.9035 | 0.18824
10177 | 1.9035 | 0.18826
10178 | 1.9035 | 0.18827
10179 | 1.9035 | 0.18829
10180 | 1.9034 | 0.18831
10181 | 1.9034 | 0.18832
10182 | 1.9034 | 0.18834
10183 | 1.9034 | 0.18836
10184 | 1.9034 | 0.18837
10185 | 1.9033 | 0.18839
10186 | 1.9033 | 0.18841
10187 | 1.9033 | 0.18843
10188 | 1.9033 | 0.18844
10189 | 1.9032 | 0.18846
10190 | 1.9032 | 0.18848
10191 | 1.9032 | 0.18849
10192 | 1.9032 | 0.18851
10193 | 1.9032 | 0.18853
10194 | 1.9031 | 0.18854
10195 | 1.9031 | 0.18856
10196 | 1.9031 | 0.18858
10197 | 1.9031 | 0.18859
10198 | 1.903 | 0.18861
10199 | 1.903 | 0.18863
10200 | 1.903 | 0.18864
10201 | 1.903 | 0.18866
10202 | 1.903 | 0.18868
10203 | 1.9029 | 0.18869
10204 | 1.9029 | 0.18871
10205 | 1.9029 | 0.18873
10206 | 1.9029 | 0.18875
10207 | 1.9028 | 0.18876
10208 | 1.9028 | 0.18878
10209 | 1.9028 | 0.1888
10210 | 1.9028 | 0.18881
10211 | 1.9028 | 0.18883
10212 | 1.9027 | 0.18885
10213 | 1.9027 | 0.18886
10214 | 1.9027 | 0.18888
10215 | 1.9027 | 0.1889
10216 | 1.9027 | 0.18891
10217 | 1.9026 | 0.18893
10218 | 1.9026 | 0.18895
10219 | 1.9026 | 0.18896
10220 | 1.9026 | 0.18898
10221 | 1.9025 | 0.189
10222 | 1.9025 | 0.18901
10223 | 1.9025 | 0.18903
10224 | 1.9025 | 0.18905
10225 | 1.9025 | 0.18907
10226 | 1.9024 | 0.18908
10227 | 1.9024 | 0.1891
10228 | 1.9024 | 0.18912
10229 | 1.9024 | 0.18913
10230 | 1.9023 | 0.18915
10231 | 1.9023 | 0.18917
10232 | 1.9023 | 0.18918
10233 | 1.9023 | 0.1892
10234 | 1.9023 | 0.18922
10235 | 1.9022 | 0.18923
10236 | 1.9022 | 0.18925
10237 | 1.9022 | 0.18927
10238 | 1.9022 | 0.18928
10239 | 1.9022 | 0.1893
10240 | 1.9021 | 0.18932
10241 | 1.9021 | 0.18933
10242 | 1.9021 | 0.18935
10243 | 1.9021 | 0.18937
10244 | 1.902 | 0.18938
10245 | 1.902 | 0.1894
10246 | 1.902 | 0.18942
10247 | 1.902 | 0.18944
10248 | 1.902 | 0.18945
10249 | 1.9019 | 0.18947
10250 | 1.9019 | 0.18949
10251 | 1.9019 | 0.1895
10252 | 1.9019 | 0.18952
10253 | 1.9018 | 0.18954
10254 | 1.9018 | 0.18955
10255 | 1.9018 | 0.18957
10256 | 1.9018 | 0.18959
10257 | 1.9018 | 0.1896
10258 | 1.9017 | 0.18962
10259 | 1.9017 | 0.18964
10260 | 1.9017 | 0.18965
10261 | 1.9017 | 0.18967
10262 | 1.9016 | 0.18969
10263 | 1.9016 | 0.1897
10264 | 1.9016 | 0.18972
10265 | 1.9016 | 0.18974
10266 | 1.9016 | 0.18976
10267 | 1.9015 | 0.18977
10268 | 1.9015 | 0.18979
10269 | 1.9015 | 0.18981
10270 | 1.9015 | 0.18982
10271 | 1.9015 | 0.18984
10272 | 1.9014 | 0.18986
10273 | 1.9014 | 0.18987
10274 | 1.9014 | 0.18989
10275 | 1.9014 | 0.18991
10276 | 1.9013 | 0.18992
10277 | 1.9013 | 0.18994
10278 | 1.9013 | 0.18996
10279 | 1.9013 | 0.18997
10280 | 1.9013 | 0.18999
10281 | 1.9012 | 0.19001
10282 | 1.9012 | 0.19002
10283 | 1.9012 | 0.19004
10284 | 1.9012 | 0.19006
10285 | 1.9011 | 0.19007
10286 | 1.9011 | 0.19009
10287 | 1.9011 | 0.19011
10288 | 1.9011 | 0.19013
10289 | 1.9011 | 0.19014
10290 | 1.901 | 0.19016
10291 | 1.901 | 0.19018
10292 | 1.901 | 0.19019
10293 | 1.901 | 0.19021
10294 | 1.901 | 0.19023
10295 | 1.9009 | 0.19024
10296 | 1.9009 | 0.19026
10297 | 1.9009 | 0.19028
10298 | 1.9009 | 0.19029
10299 | 1.9008 | 0.19031
10300 | 1.9008 | 0.19033
10301 | 1.9008 | 0.19034
10302 | 1.9008 | 0.19036
10303 | 1.9008 | 0.19038
10304 | 1.9007 | 0.19039
10305 | 1.9007 | 0.19041
10306 | 1.9007 | 0.19043
10307 | 1.9007 | 0.19044
10308 | 1.9006 | 0.19046
10309 | 1.9006 | 0.19048
10310 | 1.9006 | 0.1905
10311 | 1.9006 | 0.19051
10312 | 1.9006 | 0.19053
10313 | 1.9005 | 0.19055
10314 | 1.9005 | 0.19056
10315 | 1.9005 | 0.19058
10316 | 1.9005 | 0.1906
10317 | 1.9005 | 0.19061
10318 | 1.9004 | 0.19063
10319 | 1.9004 | 0.19065
10320 | 1.9004 | 0.19066
10321 | 1.9004 | 0.19068
10322 | 1.9003 | 0.1907
10323 | 1.9003 | 0.19071
10324 | 1.9003 | 0.19073
10325 | 1.9003 | 0.19075
10326 | 1.9003 | 0.19076
10327 | 1.9002 | 0.19078
10328 | 1.9002 | 0.1908
10329 | 1.9002 | 0.19081
10330 | 1.9002 | 0.19083
10331 | 1.9001 | 0.19085
10332 | 1.9001 | 0.19086
10333 | 1.9001 | 0.19088
10334 | 1.9001 | 0.1909
10335 | 1.9001 | 0.19092
10336 | 1.9 | 0.19093
10337 | 1.9 | 0.19095
10338 | 1.9 | 0.19097
10339 | 1.9 | 0.19098
10340 | 1.9 | 0.191
10341 | 1.8999 | 0.19102
10342 | 1.8999 | 0.19103
10343 | 1.8999 | 0.19105
10344 | 1.8999 | 0.19107
10345 | 1.8998 | 0.19108
10346 | 1.8998 | 0.1911
10347 | 1.8998 | 0.19112
10348 | 1.8998 | 0.19113
10349 | 1.8998 | 0.19115
10350 | 1.8997 | 0.19117
10351 | 1.8997 | 0.19118
10352 | 1.8997 | 0.1912
10353 | 1.8997 | 0.19122
10354 | 1.8997 | 0.19123
10355 | 1.8996 | 0.19125
10356 | 1.8996 | 0.19127
10357 | 1.8996 | 0.19128
10358 | 1.8996 | 0.1913
10359 | 1.8995 | 0.19132
10360 | 1.8995 | 0.19134
10361 | 1.8995 | 0.19135
10362 | 1.8995 | 0.19137
10363 | 1.8995 | 0.19139
10364 | 1.8994 | 0.1914
10365 | 1.8994 | 0.19142
10366 | 1.8994 | 0.19144
10367 | 1.8994 | 0.19145
10368 | 1.8993 | 0.19147
10369 | 1.8993 | 0.19149
10370 | 1.8993 | 0.1915
10371 | 1.8993 | 0.19152
10372 | 1.8993 | 0.19154
10373 | 1.8992 | 0.19155
10374 | 1.8992 | 0.19157
10375 | 1.8992 | 0.19159
10376 | 1.8992 | 0.1916
10377 | 1.8992 | 0.19162
10378 | 1.8991 | 0.19164
10379 | 1.8991 | 0.19165
10380 | 1.8991 | 0.19167
10381 | 1.8991 | 0.19169
10382 | 1.899 | 0.1917
10383 | 1.899 | 0.19172
10384 | 1.899 | 0.19174
10385 | 1.899 | 0.19176
10386 | 1.899 | 0.19177
10387 | 1.8989 | 0.19179
10388 | 1.8989 | 0.19181
10389 | 1.8989 | 0.19182
10390 | 1.8989 | 0.19184
10391 | 1.8988 | 0.19186
10392 | 1.8988 | 0.19187
10393 | 1.8988 | 0.19189
10394 | 1.8988 | 0.19191
10395 | 1.8988 | 0.19192
10396 | 1.8987 | 0.19194
10397 | 1.8987 | 0.19196
10398 | 1.8987 | 0.19197
10399 | 1.8987 | 0.19199
10400 | 1.8987 | 0.19201
10401 | 1.8986 | 0.19202
10402 | 1.8986 | 0.19204
10403 | 1.8986 | 0.19206
10404 | 1.8986 | 0.19207
10405 | 1.8985 | 0.19209
10406 | 1.8985 | 0.19211
10407 | 1.8985 | 0.19212
10408 | 1.8985 | 0.19214
10409 | 1.8985 | 0.19216
10410 | 1.8984 | 0.19217
10411 | 1.8984 | 0.19219
10412 | 1.8984 | 0.19221
10413 | 1.8984 | 0.19223
10414 | 1.8984 | 0.19224
10415 | 1.8983 | 0.19226
10416 | 1.8983 | 0.19228
10417 | 1.8983 | 0.19229
10418 | 1.8983 | 0.19231
10419 | 1.8982 | 0.19233
10420 | 1.8982 | 0.19234
10421 | 1.8982 | 0.19236
10422 | 1.8982 | 0.19238
10423 | 1.8982 | 0.19239
10424 | 1.8981 | 0.19241
10425 | 1.8981 | 0.19243
10426 | 1.8981 | 0.19244
10427 | 1.8981 | 0.19246
10428 | 1.898 | 0.19248
10429 | 1.898 | 0.19249
10430 | 1.898 | 0.19251
10431 | 1.898 | 0.19253
10432 | 1.898 | 0.19254
10433 | 1.8979 | 0.19256
10434 | 1.8979 | 0.19258
10435 | 1.8979 | 0.19259
10436 | 1.8979 | 0.19261
10437 | 1.8979 | 0.19263
10438 | 1.8978 | 0.19264
10439 | 1.8978 | 0.19266
10440 | 1.8978 | 0.19268
10441 | 1.8978 | 0.1927
10442 | 1.8977 | 0.19271
10443 | 1.8977 | 0.19273
10444 | 1.8977 | 0.19275
10445 | 1.8977 | 0.19276
10446 | 1.8977 | 0.19278
10447 | 1.8976 | 0.1928
10448 | 1.8976 | 0.19281
10449 | 1.8976 | 0.19283
10450 | 1.8976 | 0.19285
10451 | 1.8976 | 0.19286
10452 | 1.8975 | 0.19288
10453 | 1.8975 | 0.1929
10454 | 1.8975 | 0.19291
10455 | 1.8975 | 0.19293
10456 | 1.8974 | 0.19295
10457 | 1.8974 | 0.19296
10458 | 1.8974 | 0.19298
10459 | 1.8974 | 0.193
10460 | 1.8974 | 0.19301
10461 | 1.8973 | 0.19303
10462 | 1.8973 | 0.19305
10463 | 1.8973 | 0.19306
10464 | 1.8973 | 0.19308
10465 | 1.8972 | 0.1931
10466 | 1.8972 | 0.19311
10467 | 1.8972 | 0.19313
10468 | 1.8972 | 0.19315
10469 | 1.8972 | 0.19316
10470 | 1.8971 | 0.19318
10471 | 1.8971 | 0.1932
10472 | 1.8971 | 0.19322
10473 | 1.8971 | 0.19323
10474 | 1.8971 | 0.19325
10475 | 1.897 | 0.19327
10476 | 1.897 | 0.19328
10477 | 1.897 | 0.1933
10478 | 1.897 | 0.19332
10479 | 1.8969 | 0.19333
10480 | 1.8969 | 0.19335
10481 | 1.8969 | 0.19337
10482 | 1.8969 | 0.19338
10483 | 1.8969 | 0.1934
10484 | 1.8968 | 0.19342
10485 | 1.8968 | 0.19343
10486 | 1.8968 | 0.19345
10487 | 1.8968 | 0.19347
10488 | 1.8968 | 0.19348
10489 | 1.8967 | 0.1935
10490 | 1.8967 | 0.19352
10491 | 1.8967 | 0.19353
10492 | 1.8967 | 0.19355
10493 | 1.8966 | 0.19357
10494 | 1.8966 | 0.19358
10495 | 1.8966 | 0.1936
10496 | 1.8966 | 0.19362
10497 | 1.8966 | 0.19363
10498 | 1.8965 | 0.19365
10499 | 1.8965 | 0.19367
10500 | 1.8965 | 0.19368
10501 | 1.8965 | 0.1937
10502 | 1.8965 | 0.19372
10503 | 1.8964 | 0.19373
10504 | 1.8964 | 0.19375
10505 | 1.8964 | 0.19377
10506 | 1.8964 | 0.19379
10507 | 1.8963 | 0.1938
10508 | 1.8963 | 0.19382
10509 | 1.8963 | 0.19384
10510 | 1.8963 | 0.19385
10511 | 1.8963 | 0.19387
10512 | 1.8962 | 0.19389
10513 | 1.8962 | 0.1939
10514 | 1.8962 | 0.19392
10515 | 1.8962 | 0.19394
10516 | 1.8961 | 0.19395
10517 | 1.8961 | 0.19397
10518 | 1.8961 | 0.19399
10519 | 1.8961 | 0.194
10520 | 1.8961 | 0.19402
10521 | 1.896 | 0.19404
10522 | 1.896 | 0.19405
10523 | 1.896 | 0.19407
10524 | 1.896 | 0.19409
10525 | 1.896 | 0.1941
10526 | 1.8959 | 0.19412
10527 | 1.8959 | 0.19414
10528 | 1.8959 | 0.19415
10529 | 1.8959 | 0.19417
10530 | 1.8958 | 0.19419
10531 | 1.8958 | 0.1942
10532 | 1.8958 | 0.19422
10533 | 1.8958 | 0.19424
10534 | 1.8958 | 0.19425
10535 | 1.8957 | 0.19427
10536 | 1.8957 | 0.19429
10537 | 1.8957 | 0.1943
10538 | 1.8957 | 0.19432
10539 | 1.8957 | 0.19434
10540 | 1.8956 | 0.19435
10541 | 1.8956 | 0.19437
10542 | 1.8956 | 0.19439
10543 | 1.8956 | 0.1944
10544 | 1.8955 | 0.19442
10545 | 1.8955 | 0.19444
10546 | 1.8955 | 0.19446
10547 | 1.8955 | 0.19447
10548 | 1.8955 | 0.19449
10549 | 1.8954 | 0.19451
10550 | 1.8954 | 0.19452
10551 | 1.8954 | 0.19454
10552 | 1.8954 | 0.19456
10553 | 1.8954 | 0.19457
10554 | 1.8953 | 0.19459
10555 | 1.8953 | 0.19461
10556 | 1.8953 | 0.19462
10557 | 1.8953 | 0.19464
10558 | 1.8952 | 0.19466
10559 | 1.8952 | 0.19467
10560 | 1.8952 | 0.19469
10561 | 1.8952 | 0.19471
10562 | 1.8952 | 0.19472
10563 | 1.8951 | 0.19474
10564 | 1.8951 | 0.19476
10565 | 1.8951 | 0.19477
10566 | 1.8951 | 0.19479
10567 | 1.8951 | 0.19481
10568 | 1.895 | 0.19482
10569 | 1.895 | 0.19484
10570 | 1.895 | 0.19486
10571 | 1.895 | 0.19487
10572 | 1.8949 | 0.19489
10573 | 1.8949 | 0.19491
10574 | 1.8949 | 0.19492
10575 | 1.8949 | 0.19494
10576 | 1.8949 | 0.19496
10577 | 1.8948 | 0.19497
10578 | 1.8948 | 0.19499
10579 | 1.8948 | 0.19501
10580 | 1.8948 | 0.19502
10581 | 1.8948 | 0.19504
10582 | 1.8947 | 0.19506
10583 | 1.8947 | 0.19507
10584 | 1.8947 | 0.19509
10585 | 1.8947 | 0.19511
10586 | 1.8946 | 0.19512
10587 | 1.8946 | 0.19514
10588 | 1.8946 | 0.19516
10589 | 1.8946 | 0.19518
10590 | 1.8946 | 0.19519
10591 | 1.8945 | 0.19521
10592 | 1.8945 | 0.19523
10593 | 1.8945 | 0.19524
10594 | 1.8945 | 0.19526
10595 | 1.8945 | 0.19528
10596 | 1.8944 | 0.19529
10597 | 1.8944 | 0.19531
10598 | 1.8944 | 0.19533
10599 | 1.8944 | 0.19534
10600 | 1.8943 | 0.19536
10601 | 1.8943 | 0.19538
10602 | 1.8943 | 0.19539
10603 | 1.8943 | 0.19541
10604 | 1.8943 | 0.19543
10605 | 1.8942 | 0.19544
10606 | 1.8942 | 0.19546
10607 | 1.8942 | 0.19548
10608 | 1.8942 | 0.19549
10609 | 1.8942 | 0.19551
10610 | 1.8941 | 0.19553
10611 | 1.8941 | 0.19554
10612 | 1.8941 | 0.19556
10613 | 1.8941 | 0.19558
10614 | 1.894 | 0.19559
10615 | 1.894 | 0.19561
10616 | 1.894 | 0.19563
10617 | 1.894 | 0.19564
10618 | 1.894 | 0.19566
10619 | 1.8939 | 0.19568
10620 | 1.8939 | 0.19569
10621 | 1.8939 | 0.19571
10622 | 1.8939 | 0.19573
10623 | 1.8939 | 0.19574
10624 | 1.8938 | 0.19576
10625 | 1.8938 | 0.19578
10626 | 1.8938 | 0.19579
10627 | 1.8938 | 0.19581
10628 | 1.8937 | 0.19583
10629 | 1.8937 | 0.19584
10630 | 1.8937 | 0.19586
10631 | 1.8937 | 0.19588
10632 | 1.8937 | 0.19589
10633 | 1.8936 | 0.19591
10634 | 1.8936 | 0.19593
10635 | 1.8936 | 0.19594
10636 | 1.8936 | 0.19596
10637 | 1.8936 | 0.19598
10638 | 1.8935 | 0.19599
10639 | 1.8935 | 0.19601
10640 | 1.8935 | 0.19603
10641 | 1.8935 | 0.19605
10642 | 1.8934 | 0.19606
10643 | 1.8934 | 0.19608
10644 | 1.8934 | 0.1961
10645 | 1.8934 | 0.19611
10646 | 1.8934 | 0.19613
10647 | 1.8933 | 0.19615
10648 | 1.8933 | 0.19616
10649 | 1.8933 | 0.19618
10650 | 1.8933 | 0.1962
10651 | 1.8933 | 0.19621
10652 | 1.8932 | 0.19623
10653 | 1.8932 | 0.19625
10654 | 1.8932 | 0.19626
10655 | 1.8932 | 0.19628
10656 | 1.8931 | 0.1963
10657 | 1.8931 | 0.19631
10658 | 1.8931 | 0.19633
10659 | 1.8931 | 0.19635
10660 | 1.8931 | 0.19636
10661 | 1.893 | 0.19638
10662 | 1.893 | 0.1964
10663 | 1.893 | 0.19641
10664 | 1.893 | 0.19643
10665 | 1.893 | 0.19645
10666 | 1.8929 | 0.19646
10667 | 1.8929 | 0.19648
10668 | 1.8929 | 0.1965
10669 | 1.8929 | 0.19651
10670 | 1.8928 | 0.19653
10671 | 1.8928 | 0.19655
10672 | 1.8928 | 0.19656
10673 | 1.8928 | 0.19658
10674 | 1.8928 | 0.1966
10675 | 1.8927 | 0.19661
10676 | 1.8927 | 0.19663
10677 | 1.8927 | 0.19665
10678 | 1.8927 | 0.19666
10679 | 1.8927 | 0.19668
10680 | 1.8926 | 0.1967
10681 | 1.8926 | 0.19671
10682 | 1.8926 | 0.19673
10683 | 1.8926 | 0.19675
10684 | 1.8925 | 0.19676
10685 | 1.8925 | 0.19678
10686 | 1.8925 | 0.1968
10687 | 1.8925 | 0.19681
10688 | 1.8925 | 0.19683
10689 | 1.8924 | 0.19685
10690 | 1.8924 | 0.19686
10691 | 1.8924 | 0.19688
10692 | 1.8924 | 0.1969
10693 | 1.8924 | 0.19691
10694 | 1.8923 | 0.19693
10695 | 1.8923 | 0.19695
10696 | 1.8923 | 0.19696
10697 | 1.8923 | 0.19698
10698 | 1.8922 | 0.197
10699 | 1.8922 | 0.19701
10700 | 1.8922 | 0.19703
10701 | 1.8922 | 0.19705
10702 | 1.8922 | 0.19706
10703 | 1.8921 | 0.19708
10704 | 1.8921 | 0.1971
10705 | 1.8921 | 0.19711
10706 | 1.8921 | 0.19713
10707 | 1.8921 | 0.19715
10708 | 1.892 | 0.19716
10709 | 1.892 | 0.19718
10710 | 1.892 | 0.1972
10711 | 1.892 | 0.19721
10712 | 1.8919 | 0.19723
10713 | 1.8919 | 0.19725
10714 | 1.8919 | 0.19727
10715 | 1.8919 | 0.19728
10716 | 1.8919 | 0.1973
10717 | 1.8918 | 0.19732
10718 | 1.8918 | 0.19733
10719 | 1.8918 | 0.19735
10720 | 1.8918 | 0.19737
10721 | 1.8918 | 0.19738
10722 | 1.8917 | 0.1974
10723 | 1.8917 | 0.19742
10724 | 1.8917 | 0.19743
10725 | 1.8917 | 0.19745
10726 | 1.8916 | 0.19747
10727 | 1.8916 | 0.19748
10728 | 1.8916 | 0.1975
10729 | 1.8916 | 0.19752
10730 | 1.8916 | 0.19753
10731 | 1.8915 | 0.19755
10732 | 1.8915 | 0.19757
10733 | 1.8915 | 0.19758
10734 | 1.8915 | 0.1976
10735 | 1.8915 | 0.19762
10736 | 1.8914 | 0.19763
10737 | 1.8914 | 0.19765
10738 | 1.8914 | 0.19767
10739 | 1.8914 | 0.19768
10740 | 1.8913 | 0.1977
10741 | 1.8913 | 0.19772
10742 | 1.8913 | 0.19773
10743 | 1.8913 | 0.19775
10744 | 1.8913 | 0.19777
10745 | 1.8912 | 0.19778
10746 | 1.8912 | 0.1978
10747 | 1.8912 | 0.19782
10748 | 1.8912 | 0.19783
10749 | 1.8912 | 0.19785
10750 | 1.8911 | 0.19787
10751 | 1.8911 | 0.19788
10752 | 1.8911 | 0.1979
10753 | 1.8911 | 0.19792
10754 | 1.8911 | 0.19793
10755 | 1.891 | 0.19795
10756 | 1.891 | 0.19797
10757 | 1.891 | 0.19798
10758 | 1.891 | 0.198
10759 | 1.8909 | 0.19802
10760 | 1.8909 | 0.19803
10761 | 1.8909 | 0.19805
10762 | 1.8909 | 0.19807
10763 | 1.8909 | 0.19808
10764 | 1.8908 | 0.1981
10765 | 1.8908 | 0.19812
10766 | 1.8908 | 0.19813
10767 | 1.8908 | 0.19815
10768 | 1.8908 | 0.19817
10769 | 1.8907 | 0.19818
10770 | 1.8907 | 0.1982
10771 | 1.8907 | 0.19822
10772 | 1.8907 | 0.19823
10773 | 1.8906 | 0.19825
10774 | 1.8906 | 0.19827
10775 | 1.8906 | 0.19828
10776 | 1.8906 | 0.1983
10777 | 1.8906 | 0.19832
10778 | 1.8905 | 0.19833
10779 | 1.8905 | 0.19835
10780 | 1.8905 | 0.19837
10781 | 1.8905 | 0.19838
10782 | 1.8905 | 0.1984
10783 | 1.8904 | 0.19842
10784 | 1.8904 | 0.19843
10785 | 1.8904 | 0.19845
10786 | 1.8904 | 0.19847
10787 | 1.8903 | 0.19848
10788 | 1.8903 | 0.1985
10789 | 1.8903 | 0.19852
10790 | 1.8903 | 0.19853
10791 | 1.8903 | 0.19855
10792 | 1.8902 | 0.19857
10793 | 1.8902 | 0.19858
10794 | 1.8902 | 0.1986
10795 | 1.8902 | 0.19862
10796 | 1.8902 | 0.19863
10797 | 1.8901 | 0.19865
10798 | 1.8901 | 0.19867
10799 | 1.8901 | 0.19868
10800 | 1.8901 | 0.1987
10801 | 1.8901 | 0.19872
10802 | 1.89 | 0.19873
10803 | 1.89 | 0.19875
10804 | 1.89 | 0.19877
10805 | 1.89 | 0.19878
10806 | 1.8899 | 0.1988
10807 | 1.8899 | 0.19882
10808 | 1.8899 | 0.19883
10809 | 1.8899 | 0.19885
10810 | 1.8899 | 0.19887
10811 | 1.8898 | 0.19888
10812 | 1.8898 | 0.1989
10813 | 1.8898 | 0.19892
10814 | 1.8898 | 0.19893
10815 | 1.8898 | 0.19895
10816 | 1.8897 | 0.19897
10817 | 1.8897 | 0.19898
10818 | 1.8897 | 0.199
10819 | 1.8897 | 0.19902
10820 | 1.8896 | 0.19903
10821 | 1.8896 | 0.19905
10822 | 1.8896 | 0.19907
10823 | 1.8896 | 0.19908
10824 | 1.8896 | 0.1991
10825 | 1.8895 | 0.19912
10826 | 1.8895 | 0.19913
10827 | 1.8895 | 0.19915
10828 | 1.8895 | 0.19917
10829 | 1.8895 | 0.19918
10830 | 1.8894 | 0.1992
10831 | 1.8894 | 0.19922
10832 | 1.8894 | 0.19923
10833 | 1.8894 | 0.19925
10834 | 1.8893 | 0.19927
10835 | 1.8893 | 0.19928
10836 | 1.8893 | 0.1993
10837 | 1.8893 | 0.19932
10838 | 1.8893 | 0.19933
10839 | 1.8892 | 0.19935
10840 | 1.8892 | 0.19937
10841 | 1.8892 | 0.19938
10842 | 1.8892 | 0.1994
10843 | 1.8892 | 0.19942
10844 | 1.8891 | 0.19943
10845 | 1.8891 | 0.19945
10846 | 1.8891 | 0.19947
10847 | 1.8891 | 0.19948
10848 | 1.8891 | 0.1995
10849 | 1.889 | 0.19952
10850 | 1.889 | 0.19953
10851 | 1.889 | 0.19955
10852 | 1.889 | 0.19957
10853 | 1.8889 | 0.19958
10854 | 1.8889 | 0.1996
10855 | 1.8889 | 0.19962
10856 | 1.8889 | 0.19963
10857 | 1.8889 | 0.19965
10858 | 1.8888 | 0.19967
10859 | 1.8888 | 0.19968
10860 | 1.8888 | 0.1997
10861 | 1.8888 | 0.19972
10862 | 1.8888 | 0.19973
10863 | 1.8887 | 0.19975
10864 | 1.8887 | 0.19977
10865 | 1.8887 | 0.19978
10866 | 1.8887 | 0.1998
10867 | 1.8886 | 0.19982
10868 | 1.8886 | 0.19983
10869 | 1.8886 | 0.19985
10870 | 1.8886 | 0.19987
10871 | 1.8886 | 0.19988
10872 | 1.8885 | 0.1999
10873 | 1.8885 | 0.19992
10874 | 1.8885 | 0.19993
10875 | 1.8885 | 0.19995
10876 | 1.8885 | 0.19997
10877 | 1.8884 | 0.19998
10878 | 1.8884 | 0.2
10879 | 1.8884 | 0.20002
10880 | 1.8884 | 0.20003
10881 | 1.8884 | 0.20005
10882 | 1.8883 | 0.20007
10883 | 1.8883 | 0.20008
10884 | 1.8883 | 0.2001
10885 | 1.8883 | 0.20012
10886 | 1.8882 | 0.20013
10887 | 1.8882 | 0.20015
10888 | 1.8882 | 0.20017
10889 | 1.8882 | 0.20018
10890 | 1.8882 | 0.2002
10891 | 1.8881 | 0.20022
10892 | 1.8881 | 0.20023
10893 | 1.8881 | 0.20025
10894 | 1.8881 | 0.20027
10895 | 1.8881 | 0.20028
10896 | 1.888 | 0.2003
10897 | 1.888 | 0.20032
10898 | 1.888 | 0.20033
10899 | 1.888 | 0.20035
10900 | 1.8879 | 0.20037
10901 | 1.8879 | 0.20038
10902 | 1.8879 | 0.2004
10903 | 1.8879 | 0.20042
10904 | 1.8879 | 0.20043
10905 | 1.8878 | 0.20045
10906 | 1.8878 | 0.20047
10907 | 1.8878 | 0.20048
10908 | 1.8878 | 0.2005
10909 | 1.8878 | 0.20052
10910 | 1.8877 | 0.20053
10911 | 1.8877 | 0.20055
10912 | 1.8877 | 0.20057
10913 | 1.8877 | 0.20058
10914 | 1.8877 | 0.2006
10915 | 1.8876 | 0.20062
10916 | 1.8876 | 0.20063
10917 | 1.8876 | 0.20065
10918 | 1.8876 | 0.20067
10919 | 1.8875 | 0.20068
10920 | 1.8875 | 0.2007
10921 | 1.8875 | 0.20072
10922 | 1.8875 | 0.20073
10923 | 1.8875 | 0.20075
10924 | 1.8874 | 0.20077
10925 | 1.8874 | 0.20078
10926 | 1.8874 | 0.2008
10927 | 1.8874 | 0.20082
10928 | 1.8874 | 0.20083
10929 | 1.8873 | 0.20085
10930 | 1.8873 | 0.20087
10931 | 1.8873 | 0.20088
10932 | 1.8873 | 0.2009
10933 | 1.8873 | 0.20092
10934 | 1.8872 | 0.20093
10935 | 1.8872 | 0.20095
10936 | 1.8872 | 0.20097
10937 | 1.8872 | 0.20098
10938 | 1.8871 | 0.201
10939 | 1.8871 | 0.20102
10940 | 1.8871 | 0.20103
10941 | 1.8871 | 0.20105
10942 | 1.8871 | 0.20107
10943 | 1.887 | 0.20108
10944 | 1.887 | 0.2011
10945 | 1.887 | 0.20112
10946 | 1.887 | 0.20113
10947 | 1.887 | 0.20115
10948 | 1.8869 | 0.20117
10949 | 1.8869 | 0.20118
10950 | 1.8869 | 0.2012
10951 | 1.8869 | 0.20122
10952 | 1.8868 | 0.20123
10953 | 1.8868 | 0.20125
10954 | 1.8868 | 0.20127
10955 | 1.8868 | 0.20128
10956 | 1.8868 | 0.2013
10957 | 1.8867 | 0.20132
10958 | 1.8867 | 0.20133
10959 | 1.8867 | 0.20135
10960 | 1.8867 | 0.20137
10961 | 1.8867 | 0.20138
10962 | 1.8866 | 0.2014
10963 | 1.8866 | 0.20142
10964 | 1.8866 | 0.20143
10965 | 1.8866 | 0.20145
10966 | 1.8866 | 0.20147
10967 | 1.8865 | 0.20148
10968 | 1.8865 | 0.2015
10969 | 1.8865 | 0.20152
10970 | 1.8865 | 0.20153
10971 | 1.8864 | 0.20155
10972 | 1.8864 | 0.20157
10973 | 1.8864 | 0.20158
10974 | 1.8864 | 0.2016
10975 | 1.8864 | 0.20162
10976 | 1.8863 | 0.20163
10977 | 1.8863 | 0.20165
10978 | 1.8863 | 0.20167
10979 | 1.8863 | 0.20168
10980 | 1.8863 | 0.2017
10981 | 1.8862 | 0.20172
10982 | 1.8862 | 0.20173
10983 | 1.8862 | 0.20175
10984 | 1.8862 | 0.20176
10985 | 1.8862 | 0.20178
10986 | 1.8861 | 0.2018
10987 | 1.8861 | 0.20181
10988 | 1.8861 | 0.20183
10989 | 1.8861 | 0.20185
10990 | 1.886 | 0.20186
10991 | 1.886 | 0.20188
10992 | 1.886 | 0.2019
10993 | 1.886 | 0.20191
10994 | 1.886 | 0.20193
10995 | 1.8859 | 0.20195
10996 | 1.8859 | 0.20196
10997 | 1.8859 | 0.20198
10998 | 1.8859 | 0.202
10999 | 1.8859 | 0.20201
11000 | 1.8858 | 0.20203
11001 | 1.8858 | 0.20205
11002 | 1.8858 | 0.20206
11003 | 1.8858 | 0.20208
11004 | 1.8858 | 0.2021
11005 | 1.8857 | 0.20211
11006 | 1.8857 | 0.20213
11007 | 1.8857 | 0.20215
11008 | 1.8857 | 0.20216
11009 | 1.8856 | 0.20218
11010 | 1.8856 | 0.2022
11011 | 1.8856 | 0.20221
11012 | 1.8856 | 0.20223
11013 | 1.8856 | 0.20225
11014 | 1.8855 | 0.20226
11015 | 1.8855 | 0.20228
11016 | 1.8855 | 0.2023
11017 | 1.8855 | 0.20231
11018 | 1.8855 | 0.20233
11019 | 1.8854 | 0.20235
11020 | 1.8854 | 0.20236
11021 | 1.8854 | 0.20238
11022 | 1.8854 | 0.2024
11023 | 1.8854 | 0.20241
11024 | 1.8853 | 0.20243
11025 | 1.8853 | 0.20245
11026 | 1.8853 | 0.20246
11027 | 1.8853 | 0.20248
11028 | 1.8852 | 0.2025
11029 | 1.8852 | 0.20251
11030 | 1.8852 | 0.20253
11031 | 1.8852 | 0.20255
11032 | 1.8852 | 0.20256
11033 | 1.8851 | 0.20258
11034 | 1.8851 | 0.2026
11035 | 1.8851 | 0.20261
11036 | 1.8851 | 0.20263
11037 | 1.8851 | 0.20265
11038 | 1.885 | 0.20266
11039 | 1.885 | 0.20268
11040 | 1.885 | 0.2027
11041 | 1.885 | 0.20271
11042 | 1.885 | 0.20273
11043 | 1.8849 | 0.20275
11044 | 1.8849 | 0.20276
11045 | 1.8849 | 0.20278
11046 | 1.8849 | 0.2028
11047 | 1.8848 | 0.20281
11048 | 1.8848 | 0.20283
11049 | 1.8848 | 0.20285
11050 | 1.8848 | 0.20286
11051 | 1.8848 | 0.20288
11052 | 1.8847 | 0.2029
11053 | 1.8847 | 0.20291
11054 | 1.8847 | 0.20293
11055 | 1.8847 | 0.20295
11056 | 1.8847 | 0.20296
11057 | 1.8846 | 0.20298
11058 | 1.8846 | 0.20299
11059 | 1.8846 | 0.20301
11060 | 1.8846 | 0.20303
11061 | 1.8846 | 0.20304
11062 | 1.8845 | 0.20306
11063 | 1.8845 | 0.20308
11064 | 1.8845 | 0.20309
11065 | 1.8845 | 0.20311
11066 | 1.8844 | 0.20313
11067 | 1.8844 | 0.20314
11068 | 1.8844 | 0.20316
11069 | 1.8844 | 0.20318
11070 | 1.8844 | 0.20319
11071 | 1.8843 | 0.20321
11072 | 1.8843 | 0.20323
11073 | 1.8843 | 0.20324
11074 | 1.8843 | 0.20326
11075 | 1.8843 | 0.20328
11076 | 1.8842 | 0.20329
11077 | 1.8842 | 0.20331
11078 | 1.8842 | 0.20333
11079 | 1.8842 | 0.20334
11080 | 1.8842 | 0.20336
11081 | 1.8841 | 0.20338
11082 | 1.8841 | 0.20339
11083 | 1.8841 | 0.20341
11084 | 1.8841 | 0.20343
11085 | 1.884 | 0.20344
11086 | 1.884 | 0.20346
11087 | 1.884 | 0.20348
11088 | 1.884 | 0.20349
11089 | 1.884 | 0.20351
11090 | 1.8839 | 0.20353
11091 | 1.8839 | 0.20354
11092 | 1.8839 | 0.20356
11093 | 1.8839 | 0.20358
11094 | 1.8839 | 0.20359
11095 | 1.8838 | 0.20361
11096 | 1.8838 | 0.20363
11097 | 1.8838 | 0.20364
11098 | 1.8838 | 0.20366
11099 | 1.8838 | 0.20368
11100 | 1.8837 | 0.20369
11101 | 1.8837 | 0.20371
11102 | 1.8837 | 0.20373
11103 | 1.8837 | 0.20374
11104 | 1.8836 | 0.20376
11105 | 1.8836 | 0.20378
11106 | 1.8836 | 0.20379
11107 | 1.8836 | 0.20381
11108 | 1.8836 | 0.20383
11109 | 1.8835 | 0.20384
11110 | 1.8835 | 0.20386
11111 | 1.8835 | 0.20387
11112 | 1.8835 | 0.20389
11113 | 1.8835 | 0.20391
11114 | 1.8834 | 0.20392
11115 | 1.8834 | 0.20394
11116 | 1.8834 | 0.20396
11117 | 1.8834 | 0.20397
11118 | 1.8834 | 0.20399
11119 | 1.8833 | 0.20401
11120 | 1.8833 | 0.20402
11121 | 1.8833 | 0.20404
11122 | 1.8833 | 0.20406
11123 | 1.8832 | 0.20407
11124 | 1.8832 | 0.20409
11125 | 1.8832 | 0.20411
11126 | 1.8832 | 0.20412
11127 | 1.8832 | 0.20414
11128 | 1.8831 | 0.20416
11129 | 1.8831 | 0.20417
11130 | 1.8831 | 0.20419
11131 | 1.8831 | 0.20421
11132 | 1.8831 | 0.20422
11133 | 1.883 | 0.20424
11134 | 1.883 | 0.20426
11135 | 1.883 | 0.20427
11136 | 1.883 | 0.20429
11137 | 1.883 | 0.20431
11138 | 1.8829 | 0.20432
11139 | 1.8829 | 0.20434
11140 | 1.8829 | 0.20436
11141 | 1.8829 | 0.20437
11142 | 1.8829 | 0.20439
11143 | 1.8828 | 0.20441
11144 | 1.8828 | 0.20442
11145 | 1.8828 | 0.20444
11146 | 1.8828 | 0.20446
11147 | 1.8827 | 0.20447
11148 | 1.8827 | 0.20449
11149 | 1.8827 | 0.20451
11150 | 1.8827 | 0.20452
11151 | 1.8827 | 0.20454
11152 | 1.8826 | 0.20456
11153 | 1.8826 | 0.20457
11154 | 1.8826 | 0.20459
11155 | 1.8826 | 0.2046
11156 | 1.8826 | 0.20462
11157 | 1.8825 | 0.20464
11158 | 1.8825 | 0.20465
11159 | 1.8825 | 0.20467
11160 | 1.8825 | 0.20469
11161 | 1.8825 | 0.2047
11162 | 1.8824 | 0.20472
11163 | 1.8824 | 0.20474
11164 | 1.8824 | 0.20475
11165 | 1.8824 | 0.20477
11166 | 1.8823 | 0.20479
11167 | 1.8823 | 0.2048
11168 | 1.8823 | 0.20482
11169 | 1.8823 | 0.20484
11170 | 1.8823 | 0.20485
11171 | 1.8822 | 0.20487
11172 | 1.8822 | 0.20489
11173 | 1.8822 | 0.2049
11174 | 1.8822 | 0.20492
11175 | 1.8822 | 0.20494
11176 | 1.8821 | 0.20495
11177 | 1.8821 | 0.20497
11178 | 1.8821 | 0.20499
11179 | 1.8821 | 0.205
11180 | 1.8821 | 0.20502
11181 | 1.882 | 0.20504
11182 | 1.882 | 0.20505
11183 | 1.882 | 0.20507
11184 | 1.882 | 0.20509
11185 | 1.882 | 0.2051
11186 | 1.8819 | 0.20512
11187 | 1.8819 | 0.20514
11188 | 1.8819 | 0.20515
11189 | 1.8819 | 0.20517
11190 | 1.8818 | 0.20519
11191 | 1.8818 | 0.2052
11192 | 1.8818 | 0.20522
11193 | 1.8818 | 0.20523
11194 | 1.8818 | 0.20525
11195 | 1.8817 | 0.20527
11196 | 1.8817 | 0.20528
11197 | 1.8817 | 0.2053
11198 | 1.8817 | 0.20532
11199 | 1.8817 | 0.20533
11200 | 1.8816 | 0.20535
11201 | 1.8816 | 0.20537
11202 | 1.8816 | 0.20538
11203 | 1.8816 | 0.2054
11204 | 1.8816 | 0.20542
11205 | 1.8815 | 0.20543
11206 | 1.8815 | 0.20545
11207 | 1.8815 | 0.20547
11208 | 1.8815 | 0.20548
11209 | 1.8814 | 0.2055
11210 | 1.8814 | 0.20552
11211 | 1.8814 | 0.20553
11212 | 1.8814 | 0.20555
11213 | 1.8814 | 0.20557
11214 | 1.8813 | 0.20558
11215 | 1.8813 | 0.2056
11216 | 1.8813 | 0.20562
11217 | 1.8813 | 0.20563
11218 | 1.8813 | 0.20565
11219 | 1.8812 | 0.20567
11220 | 1.8812 | 0.20568
11221 | 1.8812 | 0.2057
11222 | 1.8812 | 0.20572
11223 | 1.8812 | 0.20573
11224 | 1.8811 | 0.20575
11225 | 1.8811 | 0.20577
11226 | 1.8811 | 0.20578
11227 | 1.8811 | 0.2058
11228 | 1.8811 | 0.20581
11229 | 1.881 | 0.20583
11230 | 1.881 | 0.20585
11231 | 1.881 | 0.20586
11232 | 1.881 | 0.20588
11233 | 1.8809 | 0.2059
11234 | 1.8809 | 0.20591
11235 | 1.8809 | 0.20593
11236 | 1.8809 | 0.20595
11237 | 1.8809 | 0.20596
11238 | 1.8808 | 0.20598
11239 | 1.8808 | 0.206
11240 | 1.8808 | 0.20601
11241 | 1.8808 | 0.20603
11242 | 1.8808 | 0.20605
11243 | 1.8807 | 0.20606
11244 | 1.8807 | 0.20608
11245 | 1.8807 | 0.2061
11246 | 1.8807 | 0.20611
11247 | 1.8807 | 0.20613
11248 | 1.8806 | 0.20615
11249 | 1.8806 | 0.20616
11250 | 1.8806 | 0.20618
11251 | 1.8806 | 0.2062
11252 | 1.8806 | 0.20621
11253 | 1.8805 | 0.20623
11254 | 1.8805 | 0.20625
11255 | 1.8805 | 0.20626
11256 | 1.8805 | 0.20628
11257 | 1.8804 | 0.2063
11258 | 1.8804 | 0.20631
11259 | 1.8804 | 0.20633
11260 | 1.8804 | 0.20634
11261 | 1.8804 | 0.20636
11262 | 1.8803 | 0.20638
11263 | 1.8803 | 0.20639
11264 | 1.8803 | 0.20641
11265 | 1.8803 | 0.20643
11266 | 1.8803 | 0.20644
11267 | 1.8802 | 0.20646
11268 | 1.8802 | 0.20648
11269 | 1.8802 | 0.20649
11270 | 1.8802 | 0.20651
11271 | 1.8802 | 0.20653
11272 | 1.8801 | 0.20654
11273 | 1.8801 | 0.20656
11274 | 1.8801 | 0.20658
11275 | 1.8801 | 0.20659
11276 | 1.8801 | 0.20661
11277 | 1.88 | 0.20663
11278 | 1.88 | 0.20664
11279 | 1.88 | 0.20666
11280 | 1.88 | 0.20668
11281 | 1.8799 | 0.20669
11282 | 1.8799 | 0.20671
11283 | 1.8799 | 0.20673
11284 | 1.8799 | 0.20674
11285 | 1.8799 | 0.20676
11286 | 1.8798 | 0.20678
11287 | 1.8798 | 0.20679
11288 | 1.8798 | 0.20681
11289 | 1.8798 | 0.20682
11290 | 1.8798 | 0.20684
11291 | 1.8797 | 0.20686
11292 | 1.8797 | 0.20687
11293 | 1.8797 | 0.20689
11294 | 1.8797 | 0.20691
11295 | 1.8797 | 0.20692
11296 | 1.8796 | 0.20694
11297 | 1.8796 | 0.20696
11298 | 1.8796 | 0.20697
11299 | 1.8796 | 0.20699
11300 | 1.8796 | 0.20701
11301 | 1.8795 | 0.20702
11302 | 1.8795 | 0.20704
11303 | 1.8795 | 0.20706
11304 | 1.8795 | 0.20707
11305 | 1.8794 | 0.20709
11306 | 1.8794 | 0.20711
11307 | 1.8794 | 0.20712
11308 | 1.8794 | 0.20714
11309 | 1.8794 | 0.20716
11310 | 1.8793 | 0.20717
11311 | 1.8793 | 0.20719
11312 | 1.8793 | 0.20721
11313 | 1.8793 | 0.20722
11314 | 1.8793 | 0.20724
11315 | 1.8792 | 0.20726
11316 | 1.8792 | 0.20727
11317 | 1.8792 | 0.20729
11318 | 1.8792 | 0.2073
11319 | 1.8792 | 0.20732
11320 | 1.8791 | 0.20734
11321 | 1.8791 | 0.20735
11322 | 1.8791 | 0.20737
11323 | 1.8791 | 0.20739
11324 | 1.8791 | 0.2074
11325 | 1.879 | 0.20742
11326 | 1.879 | 0.20744
11327 | 1.879 | 0.20745
11328 | 1.879 | 0.20747
11329 | 1.8789 | 0.20749
11330 | 1.8789 | 0.2075
11331 | 1.8789 | 0.20752
11332 | 1.8789 | 0.20754
11333 | 1.8789 | 0.20755
11334 | 1.8788 | 0.20757
11335 | 1.8788 | 0.20759
11336 | 1.8788 | 0.2076
11337 | 1.8788 | 0.20762
11338 | 1.8788 | 0.20764
11339 | 1.8787 | 0.20765
11340 | 1.8787 | 0.20767
11341 | 1.8787 | 0.20769
11342 | 1.8787 | 0.2077
11343 | 1.8787 | 0.20772
11344 | 1.8786 | 0.20773
11345 | 1.8786 | 0.20775
11346 | 1.8786 | 0.20777
11347 | 1.8786 | 0.20778
11348 | 1.8786 | 0.2078
11349 | 1.8785 | 0.20782
11350 | 1.8785 | 0.20783
11351 | 1.8785 | 0.20785
11352 | 1.8785 | 0.20787
11353 | 1.8784 | 0.20788
11354 | 1.8784 | 0.2079
11355 | 1.8784 | 0.20792
11356 | 1.8784 | 0.20793
11357 | 1.8784 | 0.20795
11358 | 1.8783 | 0.20797
11359 | 1.8783 | 0.20798
11360 | 1.8783 | 0.208
11361 | 1.8783 | 0.20802
11362 | 1.8783 | 0.20803
11363 | 1.8782 | 0.20805
11364 | 1.8782 | 0.20807
11365 | 1.8782 | 0.20808
11366 | 1.8782 | 0.2081
11367 | 1.8782 | 0.20811
11368 | 1.8781 | 0.20813
11369 | 1.8781 | 0.20815
11370 | 1.8781 | 0.20816
11371 | 1.8781 | 0.20818
11372 | 1.8781 | 0.2082
11373 | 1.878 | 0.20821
11374 | 1.878 | 0.20823
11375 | 1.878 | 0.20825
11376 | 1.878 | 0.20826
11377 | 1.878 | 0.20828
11378 | 1.8779 | 0.2083
11379 | 1.8779 | 0.20831
11380 | 1.8779 | 0.20833
11381 | 1.8779 | 0.20835
11382 | 1.8778 | 0.20836
11383 | 1.8778 | 0.20838
11384 | 1.8778 | 0.2084
11385 | 1.8778 | 0.20841
11386 | 1.8778 | 0.20843
11387 | 1.8777 | 0.20845
11388 | 1.8777 | 0.20846
11389 | 1.8777 | 0.20848
11390 | 1.8777 | 0.20849
11391 | 1.8777 | 0.20851
11392 | 1.8776 | 0.20853
11393 | 1.8776 | 0.20854
11394 | 1.8776 | 0.20856
11395 | 1.8776 | 0.20858
11396 | 1.8776 | 0.20859
11397 | 1.8775 | 0.20861
11398 | 1.8775 | 0.20863
11399 | 1.8775 | 0.20864
11400 | 1.8775 | 0.20866
11401 | 1.8775 | 0.20868
11402 | 1.8774 | 0.20869
11403 | 1.8774 | 0.20871
11404 | 1.8774 | 0.20873
11405 | 1.8774 | 0.20874
11406 | 1.8774 | 0.20876
11407 | 1.8773 | 0.20878
11408 | 1.8773 | 0.20879
11409 | 1.8773 | 0.20881
11410 | 1.8773 | 0.20883
11411 | 1.8772 | 0.20884
11412 | 1.8772 | 0.20886
11413 | 1.8772 | 0.20887
11414 | 1.8772 | 0.20889
11415 | 1.8772 | 0.20891
11416 | 1.8771 | 0.20892
11417 | 1.8771 | 0.20894
11418 | 1.8771 | 0.20896
11419 | 1.8771 | 0.20897
11420 | 1.8771 | 0.20899
11421 | 1.877 | 0.20901
11422 | 1.877 | 0.20902
11423 | 1.877 | 0.20904
11424 | 1.877 | 0.20906
11425 | 1.877 | 0.20907
11426 | 1.8769 | 0.20909
11427 | 1.8769 | 0.20911
11428 | 1.8769 | 0.20912
11429 | 1.8769 | 0.20914
11430 | 1.8769 | 0.20916
11431 | 1.8768 | 0.20917
11432 | 1.8768 | 0.20919
11433 | 1.8768 | 0.20921
11434 | 1.8768 | 0.20922
11435 | 1.8768 | 0.20924
11436 | 1.8767 | 0.20925
11437 | 1.8767 | 0.20927
11438 | 1.8767 | 0.20929
11439 | 1.8767 | 0.2093
11440 | 1.8766 | 0.20932
11441 | 1.8766 | 0.20934
11442 | 1.8766 | 0.20935
11443 | 1.8766 | 0.20937
11444 | 1.8766 | 0.20939
11445 | 1.8765 | 0.2094
11446 | 1.8765 | 0.20942
11447 | 1.8765 | 0.20944
11448 | 1.8765 | 0.20945
11449 | 1.8765 | 0.20947
11450 | 1.8764 | 0.20949
11451 | 1.8764 | 0.2095
11452 | 1.8764 | 0.20952
11453 | 1.8764 | 0.20954
11454 | 1.8764 | 0.20955
11455 | 1.8763 | 0.20957
11456 | 1.8763 | 0.20958
11457 | 1.8763 | 0.2096
11458 | 1.8763 | 0.20962
11459 | 1.8763 | 0.20963
11460 | 1.8762 | 0.20965
11461 | 1.8762 | 0.20967
11462 | 1.8762 | 0.20968
11463 | 1.8762 | 0.2097
11464 | 1.8762 | 0.20972
11465 | 1.8761 | 0.20973
11466 | 1.8761 | 0.20975
11467 | 1.8761 | 0.20977
11468 | 1.8761 | 0.20978
11469 | 1.876 | 0.2098
11470 | 1.876 | 0.20982
11471 | 1.876 | 0.20983
11472 | 1.876 | 0.20985
11473 | 1.876 | 0.20987
11474 | 1.8759 | 0.20988
11475 | 1.8759 | 0.2099
11476 | 1.8759 | 0.20991
11477 | 1.8759 | 0.20993
11478 | 1.8759 | 0.20995
11479 | 1.8758 | 0.20996
11480 | 1.8758 | 0.20998
11481 | 1.8758 | 0.21
11482 | 1.8758 | 0.21001
11483 | 1.8758 | 0.21003
11484 | 1.8757 | 0.21005
11485 | 1.8757 | 0.21006
11486 | 1.8757 | 0.21008
11487 | 1.8757 | 0.2101
11488 | 1.8757 | 0.21011
11489 | 1.8756 | 0.21013
11490 | 1.8756 | 0.21015
11491 | 1.8756 | 0.21016
11492 | 1.8756 | 0.21018
11493 | 1.8756 | 0.2102
11494 | 1.8755 | 0.21021
11495 | 1.8755 | 0.21023
11496 | 1.8755 | 0.21024
11497 | 1.8755 | 0.21026
11498 | 1.8754 | 0.21028
11499 | 1.8754 | 0.21029
11500 | 1.8754 | 0.21031
11501 | 1.8754 | 0.21033
11502 | 1.8754 | 0.21034
11503 | 1.8753 | 0.21036
11504 | 1.8753 | 0.21038
11505 | 1.8753 | 0.21039
11506 | 1.8753 | 0.21041
11507 | 1.8753 | 0.21043
11508 | 1.8752 | 0.21044
11509 | 1.8752 | 0.21046
11510 | 1.8752 | 0.21048
11511 | 1.8752 | 0.21049
11512 | 1.8752 | 0.21051
11513 | 1.8751 | 0.21053
11514 | 1.8751 | 0.21054
11515 | 1.8751 | 0.21056
11516 | 1.8751 | 0.21057
11517 | 1.8751 | 0.21059
11518 | 1.875 | 0.21061
11519 | 1.875 | 0.21062
11520 | 1.875 | 0.21064
11521 | 1.875 | 0.21066
11522 | 1.875 | 0.21067
11523 | 1.8749 | 0.21069
11524 | 1.8749 | 0.21071
11525 | 1.8749 | 0.21072
11526 | 1.8749 | 0.21074
11527 | 1.8749 | 0.21076
11528 | 1.8748 | 0.21077
11529 | 1.8748 | 0.21079
11530 | 1.8748 | 0.21081
11531 | 1.8748 | 0.21082
11532 | 1.8747 | 0.21084
11533 | 1.8747 | 0.21086
11534 | 1.8747 | 0.21087
11535 | 1.8747 | 0.21089
11536 | 1.8747 | 0.2109
11537 | 1.8746 | 0.21092
11538 | 1.8746 | 0.21094
11539 | 1.8746 | 0.21095
11540 | 1.8746 | 0.21097
11541 | 1.8746 | 0.21099
11542 | 1.8745 | 0.211
11543 | 1.8745 | 0.21102
11544 | 1.8745 | 0.21104
11545 | 1.8745 | 0.21105
11546 | 1.8745 | 0.21107
11547 | 1.8744 | 0.21109
11548 | 1.8744 | 0.2111
11549 | 1.8744 | 0.21112
11550 | 1.8744 | 0.21114
11551 | 1.8744 | 0.21115
11552 | 1.8743 | 0.21117
11553 | 1.8743 | 0.21118
11554 | 1.8743 | 0.2112
11555 | 1.8743 | 0.21122
11556 | 1.8743 | 0.21123
11557 | 1.8742 | 0.21125
11558 | 1.8742 | 0.21127
11559 | 1.8742 | 0.21128
11560 | 1.8742 | 0.2113
11561 | 1.8741 | 0.21132
11562 | 1.8741 | 0.21133
11563 | 1.8741 | 0.21135
11564 | 1.8741 | 0.21137
11565 | 1.8741 | 0.21138
11566 | 1.874 | 0.2114
11567 | 1.874 | 0.21142
11568 | 1.874 | 0.21143
11569 | 1.874 | 0.21145
11570 | 1.874 | 0.21146
11571 | 1.8739 | 0.21148
11572 | 1.8739 | 0.2115
11573 | 1.8739 | 0.21151
11574 | 1.8739 | 0.21153
11575 | 1.8739 | 0.21155
11576 | 1.8738 | 0.21156
11577 | 1.8738 | 0.21158
11578 | 1.8738 | 0.2116
11579 | 1.8738 | 0.21161
11580 | 1.8738 | 0.21163
11581 | 1.8737 | 0.21165
11582 | 1.8737 | 0.21166
11583 | 1.8737 | 0.21168
11584 | 1.8737 | 0.2117
11585 | 1.8737 | 0.21171
11586 | 1.8736 | 0.21173
11587 | 1.8736 | 0.21174
11588 | 1.8736 | 0.21176
11589 | 1.8736 | 0.21178
11590 | 1.8736 | 0.21179
11591 | 1.8735 | 0.21181
11592 | 1.8735 | 0.21183
11593 | 1.8735 | 0.21184
11594 | 1.8735 | 0.21186
11595 | 1.8735 | 0.21188
11596 | 1.8734 | 0.21189
11597 | 1.8734 | 0.21191
11598 | 1.8734 | 0.21193
11599 | 1.8734 | 0.21194
11600 | 1.8733 | 0.21196
11601 | 1.8733 | 0.21198
11602 | 1.8733 | 0.21199
11603 | 1.8733 | 0.21201
11604 | 1.8733 | 0.21202
11605 | 1.8732 | 0.21204
11606 | 1.8732 | 0.21206
11607 | 1.8732 | 0.21207
11608 | 1.8732 | 0.21209
11609 | 1.8732 | 0.21211
11610 | 1.8731 | 0.21212
11611 | 1.8731 | 0.21214
11612 | 1.8731 | 0.21216
11613 | 1.8731 | 0.21217
11614 | 1.8731 | 0.21219
11615 | 1.873 | 0.21221
11616 | 1.873 | 0.21222
11617 | 1.873 | 0.21224
11618 | 1.873 | 0.21226
11619 | 1.873 | 0.21227
11620 | 1.8729 | 0.21229
11621 | 1.8729 | 0.2123
11622 | 1.8729 | 0.21232
11623 | 1.8729 | 0.21234
11624 | 1.8729 | 0.21235
11625 | 1.8728 | 0.21237
11626 | 1.8728 | 0.21239
11627 | 1.8728 | 0.2124
11628 | 1.8728 | 0.21242
11629 | 1.8728 | 0.21244
11630 | 1.8727 | 0.21245
11631 | 1.8727 | 0.21247
11632 | 1.8727 | 0.21249
11633 | 1.8727 | 0.2125
11634 | 1.8726 | 0.21252
11635 | 1.8726 | 0.21254
11636 | 1.8726 | 0.21255
11637 | 1.8726 | 0.21257
11638 | 1.8726 | 0.21258
11639 | 1.8725 | 0.2126
11640 | 1.8725 | 0.21262
11641 | 1.8725 | 0.21263
11642 | 1.8725 | 0.21265
11643 | 1.8725 | 0.21267
11644 | 1.8724 | 0.21268
11645 | 1.8724 | 0.2127
11646 | 1.8724 | 0.21272
11647 | 1.8724 | 0.21273
11648 | 1.8724 | 0.21275
11649 | 1.8723 | 0.21277
11650 | 1.8723 | 0.21278
11651 | 1.8723 | 0.2128
11652 | 1.8723 | 0.21281
11653 | 1.8723 | 0.21283
11654 | 1.8722 | 0.21285
11655 | 1.8722 | 0.21286
11656 | 1.8722 | 0.21288
11657 | 1.8722 | 0.2129
11658 | 1.8722 | 0.21291
11659 | 1.8721 | 0.21293
11660 | 1.8721 | 0.21295
11661 | 1.8721 | 0.21296
11662 | 1.8721 | 0.21298
11663 | 1.8721 | 0.213
11664 | 1.872 | 0.21301
11665 | 1.872 | 0.21303
11666 | 1.872 | 0.21305
11667 | 1.872 | 0.21306
11668 | 1.872 | 0.21308
11669 | 1.8719 | 0.21309
11670 | 1.8719 | 0.21311
11671 | 1.8719 | 0.21313
11672 | 1.8719 | 0.21314
11673 | 1.8719 | 0.21316
11674 | 1.8718 | 0.21318
11675 | 1.8718 | 0.21319
11676 | 1.8718 | 0.21321
11677 | 1.8718 | 0.21323
11678 | 1.8717 | 0.21324
11679 | 1.8717 | 0.21326
11680 | 1.8717 | 0.21328
11681 | 1.8717 | 0.21329
11682 | 1.8717 | 0.21331
11683 | 1.8716 | 0.21332
11684 | 1.8716 | 0.21334
11685 | 1.8716 | 0.21336
11686 | 1.8716 | 0.21337
11687 | 1.8716 | 0.21339
11688 | 1.8715 | 0.21341
11689 | 1.8715 | 0.21342
11690 | 1.8715 | 0.21344
11691 | 1.8715 | 0.21346
11692 | 1.8715 | 0.21347
11693 | 1.8714 | 0.21349
11694 | 1.8714 | 0.21351
11695 | 1.8714 | 0.21352
11696 | 1.8714 | 0.21354
11697 | 1.8714 | 0.21356
11698 | 1.8713 | 0.21357
11699 | 1.8713 | 0.21359
11700 | 1.8713 | 0.2136
11701 | 1.8713 | 0.21362
11702 | 1.8713 | 0.21364
11703 | 1.8712 | 0.21365
11704 | 1.8712 | 0.21367
11705 | 1.8712 | 0.21369
11706 | 1.8712 | 0.2137
11707 | 1.8712 | 0.21372
11708 | 1.8711 | 0.21374
11709 | 1.8711 | 0.21375
11710 | 1.8711 | 0.21377
11711 | 1.8711 | 0.21379
11712 | 1.8711 | 0.2138
11713 | 1.871 | 0.21382
11714 | 1.871 | 0.21383
11715 | 1.871 | 0.21385
11716 | 1.871 | 0.21387
11717 | 1.8709 | 0.21388
11718 | 1.8709 | 0.2139
11719 | 1.8709 | 0.21392
11720 | 1.8709 | 0.21393
11721 | 1.8709 | 0.21395
11722 | 1.8708 | 0.21397
11723 | 1.8708 | 0.21398
11724 | 1.8708 | 0.214
11725 | 1.8708 | 0.21402
11726 | 1.8708 | 0.21403
11727 | 1.8707 | 0.21405
11728 | 1.8707 | 0.21406
11729 | 1.8707 | 0.21408
11730 | 1.8707 | 0.2141
11731 | 1.8707 | 0.21411
11732 | 1.8706 | 0.21413
11733 | 1.8706 | 0.21415
11734 | 1.8706 | 0.21416
11735 | 1.8706 | 0.21418
11736 | 1.8706 | 0.2142
11737 | 1.8705 | 0.21421
11738 | 1.8705 | 0.21423
11739 | 1.8705 | 0.21425
11740 | 1.8705 | 0.21426
11741 | 1.8705 | 0.21428
11742 | 1.8704 | 0.21429
11743 | 1.8704 | 0.21431
11744 | 1.8704 | 0.21433
11745 | 1.8704 | 0.21434
11746 | 1.8704 | 0.21436
11747 | 1.8703 | 0.21438
11748 | 1.8703 | 0.21439
11749 | 1.8703 | 0.21441
11750 | 1.8703 | 0.21443
11751 | 1.8703 | 0.21444
11752 | 1.8702 | 0.21446
11753 | 1.8702 | 0.21448
11754 | 1.8702 | 0.21449
11755 | 1.8702 | 0.21451
11756 | 1.8702 | 0.21452
11757 | 1.8701 | 0.21454
11758 | 1.8701 | 0.21456
11759 | 1.8701 | 0.21457
11760 | 1.8701 | 0.21459
11761 | 1.8701 | 0.21461
11762 | 1.87 | 0.21462
11763 | 1.87 | 0.21464
11764 | 1.87 | 0.21466
11765 | 1.87 | 0.21467
11766 | 1.8699 | 0.21469
11767 | 1.8699 | 0.21471
11768 | 1.8699 | 0.21472
11769 | 1.8699 | 0.21474
11770 | 1.8699 | 0.21475
11771 | 1.8698 | 0.21477
11772 | 1.8698 | 0.21479
11773 | 1.8698 | 0.2148
11774 | 1.8698 | 0.21482
11775 | 1.8698 | 0.21484
11776 | 1.8697 | 0.21485
11777 | 1.8697 | 0.21487
11778 | 1.8697 | 0.21489
11779 | 1.8697 | 0.2149
11780 | 1.8697 | 0.21492
11781 | 1.8696 | 0.21494
11782 | 1.8696 | 0.21495
11783 | 1.8696 | 0.21497
11784 | 1.8696 | 0.21498
11785 | 1.8696 | 0.215
11786 | 1.8695 | 0.21502
11787 | 1.8695 | 0.21503
11788 | 1.8695 | 0.21505
11789 | 1.8695 | 0.21507
11790 | 1.8695 | 0.21508
11791 | 1.8694 | 0.2151
11792 | 1.8694 | 0.21512
11793 | 1.8694 | 0.21513
11794 | 1.8694 | 0.21515
11795 | 1.8694 | 0.21517
11796 | 1.8693 | 0.21518
11797 | 1.8693 | 0.2152
11798 | 1.8693 | 0.21521
11799 | 1.8693 | 0.21523
11800 | 1.8693 | 0.21525
11801 | 1.8692 | 0.21526
11802 | 1.8692 | 0.21528
11803 | 1.8692 | 0.2153
11804 | 1.8692 | 0.21531
11805 | 1.8692 | 0.21533
11806 | 1.8691 | 0.21535
11807 | 1.8691 | 0.21536
11808 | 1.8691 | 0.21538
11809 | 1.8691 | 0.2154
11810 | 1.8691 | 0.21541
11811 | 1.869 | 0.21543
11812 | 1.869 | 0.21544
11813 | 1.869 | 0.21546
11814 | 1.869 | 0.21548
11815 | 1.869 | 0.21549
11816 | 1.8689 | 0.21551
11817 | 1.8689 | 0.21553
11818 | 1.8689 | 0.21554
11819 | 1.8689 | 0.21556
11820 | 1.8688 | 0.21558
11821 | 1.8688 | 0.21559
11822 | 1.8688 | 0.21561
11823 | 1.8688 | 0.21562
11824 | 1.8688 | 0.21564
11825 | 1.8687 | 0.21566
11826 | 1.8687 | 0.21567
11827 | 1.8687 | 0.21569
11828 | 1.8687 | 0.21571
11829 | 1.8687 | 0.21572
11830 | 1.8686 | 0.21574
11831 | 1.8686 | 0.21576
11832 | 1.8686 | 0.21577
11833 | 1.8686 | 0.21579
11834 | 1.8686 | 0.21581
11835 | 1.8685 | 0.21582
11836 | 1.8685 | 0.21584
11837 | 1.8685 | 0.21585
11838 | 1.8685 | 0.21587
11839 | 1.8685 | 0.21589
11840 | 1.8684 | 0.2159
11841 | 1.8684 | 0.21592
11842 | 1.8684 | 0.21594
11843 | 1.8684 | 0.21595
11844 | 1.8684 | 0.21597
11845 | 1.8683 | 0.21599
11846 | 1.8683 | 0.216
11847 | 1.8683 | 0.21602
11848 | 1.8683 | 0.21604
11849 | 1.8683 | 0.21605
11850 | 1.8682 | 0.21607
11851 | 1.8682 | 0.21608
11852 | 1.8682 | 0.2161
11853 | 1.8682 | 0.21612
11854 | 1.8682 | 0.21613
11855 | 1.8681 | 0.21615
11856 | 1.8681 | 0.21617
11857 | 1.8681 | 0.21618
11858 | 1.8681 | 0.2162
11859 | 1.8681 | 0.21622
11860 | 1.868 | 0.21623
11861 | 1.868 | 0.21625
11862 | 1.868 | 0.21626
11863 | 1.868 | 0.21628
11864 | 1.868 | 0.2163
11865 | 1.8679 | 0.21631
11866 | 1.8679 | 0.21633
11867 | 1.8679 | 0.21635
11868 | 1.8679 | 0.21636
11869 | 1.8679 | 0.21638
11870 | 1.8678 | 0.2164
11871 | 1.8678 | 0.21641
11872 | 1.8678 | 0.21643
11873 | 1.8678 | 0.21645
11874 | 1.8678 | 0.21646
11875 | 1.8677 | 0.21648
11876 | 1.8677 | 0.21649
11877 | 1.8677 | 0.21651
11878 | 1.8677 | 0.21653
11879 | 1.8676 | 0.21654
11880 | 1.8676 | 0.21656
11881 | 1.8676 | 0.21658
11882 | 1.8676 | 0.21659
11883 | 1.8676 | 0.21661
11884 | 1.8675 | 0.21663
11885 | 1.8675 | 0.21664
11886 | 1.8675 | 0.21666
11887 | 1.8675 | 0.21667
11888 | 1.8675 | 0.21669
11889 | 1.8674 | 0.21671
11890 | 1.8674 | 0.21672
11891 | 1.8674 | 0.21674
11892 | 1.8674 | 0.21676
11893 | 1.8674 | 0.21677
11894 | 1.8673 | 0.21679
11895 | 1.8673 | 0.21681
11896 | 1.8673 | 0.21682
11897 | 1.8673 | 0.21684
11898 | 1.8673 | 0.21685
11899 | 1.8672 | 0.21687
11900 | 1.8672 | 0.21689
11901 | 1.8672 | 0.2169
11902 | 1.8672 | 0.21692
11903 | 1.8672 | 0.21694
11904 | 1.8671 | 0.21695
11905 | 1.8671 | 0.21697
11906 | 1.8671 | 0.21699
11907 | 1.8671 | 0.217
11908 | 1.8671 | 0.21702
11909 | 1.867 | 0.21704
11910 | 1.867 | 0.21705
11911 | 1.867 | 0.21707
11912 | 1.867 | 0.21708
11913 | 1.867 | 0.2171
11914 | 1.8669 | 0.21712
11915 | 1.8669 | 0.21713
11916 | 1.8669 | 0.21715
11917 | 1.8669 | 0.21717
11918 | 1.8669 | 0.21718
11919 | 1.8668 | 0.2172
11920 | 1.8668 | 0.21722
11921 | 1.8668 | 0.21723
11922 | 1.8668 | 0.21725
11923 | 1.8668 | 0.21726
11924 | 1.8667 | 0.21728
11925 | 1.8667 | 0.2173
11926 | 1.8667 | 0.21731
11927 | 1.8667 | 0.21733
11928 | 1.8667 | 0.21735
11929 | 1.8666 | 0.21736
11930 | 1.8666 | 0.21738
11931 | 1.8666 | 0.2174
11932 | 1.8666 | 0.21741
11933 | 1.8666 | 0.21743
11934 | 1.8665 | 0.21744
11935 | 1.8665 | 0.21746
11936 | 1.8665 | 0.21748
11937 | 1.8665 | 0.21749
11938 | 1.8665 | 0.21751
11939 | 1.8664 | 0.21753
11940 | 1.8664 | 0.21754
11941 | 1.8664 | 0.21756
11942 | 1.8664 | 0.21758
11943 | 1.8664 | 0.21759
11944 | 1.8663 | 0.21761
11945 | 1.8663 | 0.21762
11946 | 1.8663 | 0.21764
11947 | 1.8663 | 0.21766
11948 | 1.8663 | 0.21767
11949 | 1.8662 | 0.21769
11950 | 1.8662 | 0.21771
11951 | 1.8662 | 0.21772
11952 | 1.8662 | 0.21774
11953 | 1.8661 | 0.21776
11954 | 1.8661 | 0.21777
11955 | 1.8661 | 0.21779
11956 | 1.8661 | 0.21781
11957 | 1.8661 | 0.21782
11958 | 1.866 | 0.21784
11959 | 1.866 | 0.21785
11960 | 1.866 | 0.21787
11961 | 1.866 | 0.21789
11962 | 1.866 | 0.2179
11963 | 1.8659 | 0.21792
11964 | 1.8659 | 0.21794
11965 | 1.8659 | 0.21795
11966 | 1.8659 | 0.21797
11967 | 1.8659 | 0.21799
11968 | 1.8658 | 0.218
11969 | 1.8658 | 0.21802
11970 | 1.8658 | 0.21803
11971 | 1.8658 | 0.21805
11972 | 1.8658 | 0.21807
11973 | 1.8657 | 0.21808
11974 | 1.8657 | 0.2181
11975 | 1.8657 | 0.21812
11976 | 1.8657 | 0.21813
11977 | 1.8657 | 0.21815
11978 | 1.8656 | 0.21817
11979 | 1.8656 | 0.21818
11980 | 1.8656 | 0.2182
11981 | 1.8656 | 0.21821
11982 | 1.8656 | 0.21823
11983 | 1.8655 | 0.21825
11984 | 1.8655 | 0.21826
11985 | 1.8655 | 0.21828
11986 | 1.8655 | 0.2183
11987 | 1.8655 | 0.21831
11988 | 1.8654 | 0.21833
11989 | 1.8654 | 0.21835
11990 | 1.8654 | 0.21836
11991 | 1.8654 | 0.21838
11992 | 1.8654 | 0.21839
11993 | 1.8653 | 0.21841
11994 | 1.8653 | 0.21843
11995 | 1.8653 | 0.21844
11996 | 1.8653 | 0.21846
11997 | 1.8653 | 0.21848
11998 | 1.8652 | 0.21849
11999 | 1.8652 | 0.21851
12000 | 1.8652 | 0.21853
12001 | 1.8652 | 0.21854
12002 | 1.8652 | 0.21856
12003 | 1.8651 | 0.21857
12004 | 1.8651 | 0.21859
12005 | 1.8651 | 0.21861
12006 | 1.8651 | 0.21862
12007 | 1.8651 | 0.21864
12008 | 1.865 | 0.21866
12009 | 1.865 | 0.21867
12010 | 1.865 | 0.21869
12011 | 1.865 | 0.21871
12012 | 1.865 | 0.21872
12013 | 1.8649 | 0.21874
12014 | 1.8649 | 0.21875
12015 | 1.8649 | 0.21877
12016 | 1.8649 | 0.21879
12017 | 1.8649 | 0.2188
12018 | 1.8648 | 0.21882
12019 | 1.8648 | 0.21884
12020 | 1.8648 | 0.21885
12021 | 1.8648 | 0.21887
12022 | 1.8648 | 0.21889
12023 | 1.8647 | 0.2189
12024 | 1.8647 | 0.21892
12025 | 1.8647 | 0.21893
12026 | 1.8647 | 0.21895
12027 | 1.8647 | 0.21897
12028 | 1.8646 | 0.21898
12029 | 1.8646 | 0.219
12030 | 1.8646 | 0.21902
12031 | 1.8646 | 0.21903
12032 | 1.8646 | 0.21905
12033 | 1.8645 | 0.21907
12034 | 1.8645 | 0.21908
12035 | 1.8645 | 0.2191
12036 | 1.8645 | 0.21911
12037 | 1.8645 | 0.21913
12038 | 1.8644 | 0.21915
12039 | 1.8644 | 0.21916
12040 | 1.8644 | 0.21918
12041 | 1.8644 | 0.2192
12042 | 1.8644 | 0.21921
12043 | 1.8643 | 0.21923
12044 | 1.8643 | 0.21925
12045 | 1.8643 | 0.21926
12046 | 1.8643 | 0.21928
12047 | 1.8642 | 0.21929
12048 | 1.8642 | 0.21931
12049 | 1.8642 | 0.21933
12050 | 1.8642 | 0.21934
12051 | 1.8642 | 0.21936
12052 | 1.8641 | 0.21938
12053 | 1.8641 | 0.21939
12054 | 1.8641 | 0.21941
12055 | 1.8641 | 0.21943
12056 | 1.8641 | 0.21944
12057 | 1.864 | 0.21946
12058 | 1.864 | 0.21947
12059 | 1.864 | 0.21949
12060 | 1.864 | 0.21951
12061 | 1.864 | 0.21952
12062 | 1.8639 | 0.21954
12063 | 1.8639 | 0.21956
12064 | 1.8639 | 0.21957
12065 | 1.8639 | 0.21959
12066 | 1.8639 | 0.2196
12067 | 1.8638 | 0.21962
12068 | 1.8638 | 0.21964
12069 | 1.8638 | 0.21965
12070 | 1.8638 | 0.21967
12071 | 1.8638 | 0.21969
12072 | 1.8637 | 0.2197
12073 | 1.8637 | 0.21972
12074 | 1.8637 | 0.21974
12075 | 1.8637 | 0.21975
12076 | 1.8637 | 0.21977
12077 | 1.8636 | 0.21978
12078 | 1.8636 | 0.2198
12079 | 1.8636 | 0.21982
12080 | 1.8636 | 0.21983
12081 | 1.8636 | 0.21985
12082 | 1.8635 | 0.21987
12083 | 1.8635 | 0.21988
12084 | 1.8635 | 0.2199
12085 | 1.8635 | 0.21992
12086 | 1.8635 | 0.21993
12087 | 1.8634 | 0.21995
12088 | 1.8634 | 0.21996
12089 | 1.8634 | 0.21998
12090 | 1.8634 | 0.22
12091 | 1.8634 | 0.22001
12092 | 1.8633 | 0.22003
12093 | 1.8633 | 0.22005
12094 | 1.8633 | 0.22006
12095 | 1.8633 | 0.22008
12096 | 1.8633 | 0.2201
12097 | 1.8632 | 0.22011
12098 | 1.8632 | 0.22013
12099 | 1.8632 | 0.22014
12100 | 1.8632 | 0.22016
12101 | 1.8632 | 0.22018
12102 | 1.8631 | 0.22019
12103 | 1.8631 | 0.22021
12104 | 1.8631 | 0.22023
12105 | 1.8631 | 0.22024
12106 | 1.8631 | 0.22026
12107 | 1.863 | 0.22027
12108 | 1.863 | 0.22029
12109 | 1.863 | 0.22031
12110 | 1.863 | 0.22032
12111 | 1.863 | 0.22034
12112 | 1.8629 | 0.22036
12113 | 1.8629 | 0.22037
12114 | 1.8629 | 0.22039
12115 | 1.8629 | 0.22041
12116 | 1.8629 | 0.22042
12117 | 1.8628 | 0.22044
12118 | 1.8628 | 0.22045
12119 | 1.8628 | 0.22047
12120 | 1.8628 | 0.22049
12121 | 1.8628 | 0.2205
12122 | 1.8627 | 0.22052
12123 | 1.8627 | 0.22054
12124 | 1.8627 | 0.22055
12125 | 1.8627 | 0.22057
12126 | 1.8627 | 0.22059
12127 | 1.8626 | 0.2206
12128 | 1.8626 | 0.22062
12129 | 1.8626 | 0.22063
12130 | 1.8626 | 0.22065
12131 | 1.8626 | 0.22067
12132 | 1.8625 | 0.22068
12133 | 1.8625 | 0.2207
12134 | 1.8625 | 0.22072
12135 | 1.8625 | 0.22073
12136 | 1.8625 | 0.22075
12137 | 1.8624 | 0.22076
12138 | 1.8624 | 0.22078
12139 | 1.8624 | 0.2208
12140 | 1.8624 | 0.22081
12141 | 1.8624 | 0.22083
12142 | 1.8623 | 0.22085
12143 | 1.8623 | 0.22086
12144 | 1.8623 | 0.22088
12145 | 1.8623 | 0.2209
12146 | 1.8623 | 0.22091
12147 | 1.8622 | 0.22093
12148 | 1.8622 | 0.22094
12149 | 1.8622 | 0.22096
12150 | 1.8622 | 0.22098
12151 | 1.8622 | 0.22099
12152 | 1.8621 | 0.22101
12153 | 1.8621 | 0.22103
12154 | 1.8621 | 0.22104
12155 | 1.8621 | 0.22106
12156 | 1.8621 | 0.22108
12157 | 1.862 | 0.22109
12158 | 1.862 | 0.22111
12159 | 1.862 | 0.22112
12160 | 1.862 | 0.22114
12161 | 1.862 | 0.22116
12162 | 1.8619 | 0.22117
12163 | 1.8619 | 0.22119
12164 | 1.8619 | 0.22121
12165 | 1.8619 | 0.22122
12166 | 1.8619 | 0.22124
12167 | 1.8618 | 0.22125
12168 | 1.8618 | 0.22127
12169 | 1.8618 | 0.22129
12170 | 1.8618 | 0.2213
12171 | 1.8618 | 0.22132
12172 | 1.8617 | 0.22134
12173 | 1.8617 | 0.22135
12174 | 1.8617 | 0.22137
12175 | 1.8617 | 0.22139
12176 | 1.8617 | 0.2214
12177 | 1.8616 | 0.22142
12178 | 1.8616 | 0.22143
12179 | 1.8616 | 0.22145
12180 | 1.8616 | 0.22147
12181 | 1.8616 | 0.22148
12182 | 1.8615 | 0.2215
12183 | 1.8615 | 0.22152
12184 | 1.8615 | 0.22153
12185 | 1.8615 | 0.22155
12186 | 1.8615 | 0.22156
12187 | 1.8614 | 0.22158
12188 | 1.8614 | 0.2216
12189 | 1.8614 | 0.22161
12190 | 1.8614 | 0.22163
12191 | 1.8614 | 0.22165
12192 | 1.8613 | 0.22166
12193 | 1.8613 | 0.22168
12194 | 1.8613 | 0.2217
12195 | 1.8613 | 0.22171
12196 | 1.8613 | 0.22173
12197 | 1.8612 | 0.22174
12198 | 1.8612 | 0.22176
12199 | 1.8612 | 0.22178
12200 | 1.8612 | 0.22179
12201 | 1.8612 | 0.22181
12202 | 1.8611 | 0.22183
12203 | 1.8611 | 0.22184
12204 | 1.8611 | 0.22186
12205 | 1.8611 | 0.22187
12206 | 1.8611 | 0.22189
12207 | 1.861 | 0.22191
12208 | 1.861 | 0.22192
12209 | 1.861 | 0.22194
12210 | 1.861 | 0.22196
12211 | 1.861 | 0.22197
12212 | 1.8609 | 0.22199
12213 | 1.8609 | 0.22201
12214 | 1.8609 | 0.22202
12215 | 1.8609 | 0.22204
12216 | 1.8609 | 0.22205
12217 | 1.8608 | 0.22207
12218 | 1.8608 | 0.22209
12219 | 1.8608 | 0.2221
12220 | 1.8608 | 0.22212
12221 | 1.8608 | 0.22214
12222 | 1.8607 | 0.22215
12223 | 1.8607 | 0.22217
12224 | 1.8607 | 0.22218
12225 | 1.8607 | 0.2222
12226 | 1.8607 | 0.22222
12227 | 1.8606 | 0.22223
12228 | 1.8606 | 0.22225
12229 | 1.8606 | 0.22227
12230 | 1.8606 | 0.22228
12231 | 1.8606 | 0.2223
12232 | 1.8605 | 0.22232
12233 | 1.8605 | 0.22233
12234 | 1.8605 | 0.22235
12235 | 1.8605 | 0.22236
12236 | 1.8605 | 0.22238
12237 | 1.8604 | 0.2224
12238 | 1.8604 | 0.22241
12239 | 1.8604 | 0.22243
12240 | 1.8604 | 0.22245
12241 | 1.8604 | 0.22246
12242 | 1.8603 | 0.22248
12243 | 1.8603 | 0.22249
12244 | 1.8603 | 0.22251
12245 | 1.8603 | 0.22253
12246 | 1.8603 | 0.22254
12247 | 1.8602 | 0.22256
12248 | 1.8602 | 0.22258
12249 | 1.8602 | 0.22259
12250 | 1.8602 | 0.22261
12251 | 1.8602 | 0.22262
12252 | 1.8601 | 0.22264
12253 | 1.8601 | 0.22266
12254 | 1.8601 | 0.22267
12255 | 1.8601 | 0.22269
12256 | 1.8601 | 0.22271
12257 | 1.86 | 0.22272
12258 | 1.86 | 0.22274
12259 | 1.86 | 0.22276
12260 | 1.86 | 0.22277
12261 | 1.86 | 0.22279
12262 | 1.8599 | 0.2228
12263 | 1.8599 | 0.22282
12264 | 1.8599 | 0.22284
12265 | 1.8599 | 0.22285
12266 | 1.8599 | 0.22287
12267 | 1.8598 | 0.22289
12268 | 1.8598 | 0.2229
12269 | 1.8598 | 0.22292
12270 | 1.8598 | 0.22293
12271 | 1.8598 | 0.22295
12272 | 1.8597 | 0.22297
12273 | 1.8597 | 0.22298
12274 | 1.8597 | 0.223
12275 | 1.8597 | 0.22302
12276 | 1.8597 | 0.22303
12277 | 1.8596 | 0.22305
12278 | 1.8596 | 0.22306
12279 | 1.8596 | 0.22308
12280 | 1.8596 | 0.2231
12281 | 1.8596 | 0.22311
12282 | 1.8595 | 0.22313
12283 | 1.8595 | 0.22315
12284 | 1.8595 | 0.22316
12285 | 1.8595 | 0.22318
12286 | 1.8595 | 0.2232
12287 | 1.8594 | 0.22321
12288 | 1.8594 | 0.22323
12289 | 1.8594 | 0.22324
12290 | 1.8594 | 0.22326
12291 | 1.8594 | 0.22328
12292 | 1.8593 | 0.22329
12293 | 1.8593 | 0.22331
12294 | 1.8593 | 0.22333
12295 | 1.8593 | 0.22334
12296 | 1.8593 | 0.22336
12297 | 1.8592 | 0.22337
12298 | 1.8592 | 0.22339
12299 | 1.8592 | 0.22341
12300 | 1.8592 | 0.22342
12301 | 1.8592 | 0.22344
12302 | 1.8591 | 0.22346
12303 | 1.8591 | 0.22347
12304 | 1.8591 | 0.22349
12305 | 1.8591 | 0.2235
12306 | 1.8591 | 0.22352
12307 | 1.859 | 0.22354
12308 | 1.859 | 0.22355
12309 | 1.859 | 0.22357
12310 | 1.859 | 0.22359
12311 | 1.859 | 0.2236
12312 | 1.8589 | 0.22362
12313 | 1.8589 | 0.22363
12314 | 1.8589 | 0.22365
12315 | 1.8589 | 0.22367
12316 | 1.8589 | 0.22368
12317 | 1.8588 | 0.2237
12318 | 1.8588 | 0.22372
12319 | 1.8588 | 0.22373
12320 | 1.8588 | 0.22375
12321 | 1.8588 | 0.22377
12322 | 1.8587 | 0.22378
12323 | 1.8587 | 0.2238
12324 | 1.8587 | 0.22381
12325 | 1.8587 | 0.22383
12326 | 1.8587 | 0.22385
12327 | 1.8586 | 0.22386
12328 | 1.8586 | 0.22388
12329 | 1.8586 | 0.2239
12330 | 1.8586 | 0.22391
12331 | 1.8586 | 0.22393
12332 | 1.8585 | 0.22394
12333 | 1.8585 | 0.22396
12334 | 1.8585 | 0.22398
12335 | 1.8585 | 0.22399
12336 | 1.8585 | 0.22401
12337 | 1.8584 | 0.22403
12338 | 1.8584 | 0.22404
12339 | 1.8584 | 0.22406
12340 | 1.8584 | 0.22407
12341 | 1.8584 | 0.22409
12342 | 1.8583 | 0.22411
12343 | 1.8583 | 0.22412
12344 | 1.8583 | 0.22414
12345 | 1.8583 | 0.22416
12346 | 1.8583 | 0.22417
12347 | 1.8582 | 0.22419
12348 | 1.8582 | 0.2242
12349 | 1.8582 | 0.22422
12350 | 1.8582 | 0.22424
12351 | 1.8582 | 0.22425
12352 | 1.8581 | 0.22427
12353 | 1.8581 | 0.22429
12354 | 1.8581 | 0.2243
12355 | 1.8581 | 0.22432
12356 | 1.8581 | 0.22434
12357 | 1.858 | 0.22435
12358 | 1.858 | 0.22437
12359 | 1.858 | 0.22438
12360 | 1.858 | 0.2244
12361 | 1.858 | 0.22442
12362 | 1.8579 | 0.22443
12363 | 1.8579 | 0.22445
12364 | 1.8579 | 0.22447
12365 | 1.8579 | 0.22448
12366 | 1.8579 | 0.2245
12367 | 1.8578 | 0.22451
12368 | 1.8578 | 0.22453
12369 | 1.8578 | 0.22455
12370 | 1.8578 | 0.22456
12371 | 1.8578 | 0.22458
12372 | 1.8577 | 0.2246
12373 | 1.8577 | 0.22461
12374 | 1.8577 | 0.22463
12375 | 1.8577 | 0.22464
12376 | 1.8577 | 0.22466
12377 | 1.8576 | 0.22468
12378 | 1.8576 | 0.22469
12379 | 1.8576 | 0.22471
12380 | 1.8576 | 0.22473
12381 | 1.8576 | 0.22474
12382 | 1.8575 | 0.22476
12383 | 1.8575 | 0.22477
12384 | 1.8575 | 0.22479
12385 | 1.8575 | 0.22481
12386 | 1.8575 | 0.22482
12387 | 1.8574 | 0.22484
12388 | 1.8574 | 0.22486
12389 | 1.8574 | 0.22487
12390 | 1.8574 | 0.22489
12391 | 1.8574 | 0.2249
12392 | 1.8573 | 0.22492
12393 | 1.8573 | 0.22494
12394 | 1.8573 | 0.22495
12395 | 1.8573 | 0.22497
12396 | 1.8573 | 0.22499
12397 | 1.8572 | 0.225
12398 | 1.8572 | 0.22502
12399 | 1.8572 | 0.22503
12400 | 1.8572 | 0.22505
12401 | 1.8572 | 0.22507
12402 | 1.8571 | 0.22508
12403 | 1.8571 | 0.2251
12404 | 1.8571 | 0.22512
12405 | 1.8571 | 0.22513
12406 | 1.8571 | 0.22515
12407 | 1.857 | 0.22516
12408 | 1.857 | 0.22518
12409 | 1.857 | 0.2252
12410 | 1.857 | 0.22521
12411 | 1.857 | 0.22523
12412 | 1.8569 | 0.22525
12413 | 1.8569 | 0.22526
12414 | 1.8569 | 0.22528
12415 | 1.8569 | 0.22529
12416 | 1.8569 | 0.22531
12417 | 1.8568 | 0.22533
12418 | 1.8568 | 0.22534
12419 | 1.8568 | 0.22536
12420 | 1.8568 | 0.22538
12421 | 1.8568 | 0.22539
12422 | 1.8567 | 0.22541
12423 | 1.8567 | 0.22542
12424 | 1.8567 | 0.22544
12425 | 1.8567 | 0.22546
12426 | 1.8567 | 0.22547
12427 | 1.8567 | 0.22549
12428 | 1.8566 | 0.22551
12429 | 1.8566 | 0.22552
12430 | 1.8566 | 0.22554
12431 | 1.8566 | 0.22555
12432 | 1.8566 | 0.22557
12433 | 1.8565 | 0.22559
12434 | 1.8565 | 0.2256
12435 | 1.8565 | 0.22562
12436 | 1.8565 | 0.22564
12437 | 1.8565 | 0.22565
12438 | 1.8564 | 0.22567
12439 | 1.8564 | 0.22568
12440 | 1.8564 | 0.2257
12441 | 1.8564 | 0.22572
12442 | 1.8564 | 0.22573
12443 | 1.8563 | 0.22575
12444 | 1.8563 | 0.22577
12445 | 1.8563 | 0.22578
12446 | 1.8563 | 0.2258
12447 | 1.8563 | 0.22581
12448 | 1.8562 | 0.22583
12449 | 1.8562 | 0.22585
12450 | 1.8562 | 0.22586
12451 | 1.8562 | 0.22588
12452 | 1.8562 | 0.2259
12453 | 1.8561 | 0.22591
12454 | 1.8561 | 0.22593
12455 | 1.8561 | 0.22594
12456 | 1.8561 | 0.22596
12457 | 1.8561 | 0.22598
12458 | 1.856 | 0.22599
12459 | 1.856 | 0.22601
12460 | 1.856 | 0.22603
12461 | 1.856 | 0.22604
12462 | 1.856 | 0.22606
12463 | 1.8559 | 0.22607
12464 | 1.8559 | 0.22609
12465 | 1.8559 | 0.22611
12466 | 1.8559 | 0.22612
12467 | 1.8559 | 0.22614
12468 | 1.8558 | 0.22616
12469 | 1.8558 | 0.22617
12470 | 1.8558 | 0.22619
12471 | 1.8558 | 0.2262
12472 | 1.8558 | 0.22622
12473 | 1.8557 | 0.22624
12474 | 1.8557 | 0.22625
12475 | 1.8557 | 0.22627
12476 | 1.8557 | 0.22629
12477 | 1.8557 | 0.2263
12478 | 1.8556 | 0.22632
12479 | 1.8556 | 0.22633
12480 | 1.8556 | 0.22635
12481 | 1.8556 | 0.22637
12482 | 1.8556 | 0.22638
12483 | 1.8555 | 0.2264
12484 | 1.8555 | 0.22642
12485 | 1.8555 | 0.22643
12486 | 1.8555 | 0.22645
12487 | 1.8555 | 0.22646
12488 | 1.8554 | 0.22648
12489 | 1.8554 | 0.2265
12490 | 1.8554 | 0.22651
12491 | 1.8554 | 0.22653
12492 | 1.8554 | 0.22655
12493 | 1.8553 | 0.22656
12494 | 1.8553 | 0.22658
12495 | 1.8553 | 0.22659
12496 | 1.8553 | 0.22661
12497 | 1.8553 | 0.22663
12498 | 1.8552 | 0.22664
12499 | 1.8552 | 0.22666
12500 | 1.8552 | 0.22668
12501 | 1.8552 | 0.22669
12502 | 1.8552 | 0.22671
12503 | 1.8551 | 0.22672
12504 | 1.8551 | 0.22674
12505 | 1.8551 | 0.22676
12506 | 1.8551 | 0.22677
12507 | 1.8551 | 0.22679
12508 | 1.855 | 0.22681
12509 | 1.855 | 0.22682
12510 | 1.855 | 0.22684
12511 | 1.855 | 0.22685
12512 | 1.855 | 0.22687
12513 | 1.8549 | 0.22689
12514 | 1.8549 | 0.2269
12515 | 1.8549 | 0.22692
12516 | 1.8549 | 0.22694
12517 | 1.8549 | 0.22695
12518 | 1.8548 | 0.22697
12519 | 1.8548 | 0.22698
12520 | 1.8548 | 0.227
12521 | 1.8548 | 0.22702
12522 | 1.8548 | 0.22703
12523 | 1.8547 | 0.22705
12524 | 1.8547 | 0.22707
12525 | 1.8547 | 0.22708
12526 | 1.8547 | 0.2271
12527 | 1.8547 | 0.22711
12528 | 1.8547 | 0.22713
12529 | 1.8546 | 0.22715
12530 | 1.8546 | 0.22716
12531 | 1.8546 | 0.22718
12532 | 1.8546 | 0.2272
12533 | 1.8546 | 0.22721
12534 | 1.8545 | 0.22723
12535 | 1.8545 | 0.22724
12536 | 1.8545 | 0.22726
12537 | 1.8545 | 0.22728
12538 | 1.8545 | 0.22729
12539 | 1.8544 | 0.22731
12540 | 1.8544 | 0.22733
12541 | 1.8544 | 0.22734
12542 | 1.8544 | 0.22736
12543 | 1.8544 | 0.22737
12544 | 1.8543 | 0.22739
12545 | 1.8543 | 0.22741
12546 | 1.8543 | 0.22742
12547 | 1.8543 | 0.22744
12548 | 1.8543 | 0.22745
12549 | 1.8542 | 0.22747
12550 | 1.8542 | 0.22749
12551 | 1.8542 | 0.2275
12552 | 1.8542 | 0.22752
12553 | 1.8542 | 0.22754
12554 | 1.8541 | 0.22755
12555 | 1.8541 | 0.22757
12556 | 1.8541 | 0.22758
12557 | 1.8541 | 0.2276
12558 | 1.8541 | 0.22762
12559 | 1.854 | 0.22763
12560 | 1.854 | 0.22765
12561 | 1.854 | 0.22767
12562 | 1.854 | 0.22768
12563 | 1.854 | 0.2277
12564 | 1.8539 | 0.22771
12565 | 1.8539 | 0.22773
12566 | 1.8539 | 0.22775
12567 | 1.8539 | 0.22776
12568 | 1.8539 | 0.22778
12569 | 1.8538 | 0.2278
12570 | 1.8538 | 0.22781
12571 | 1.8538 | 0.22783
12572 | 1.8538 | 0.22784
12573 | 1.8538 | 0.22786
12574 | 1.8537 | 0.22788
12575 | 1.8537 | 0.22789
12576 | 1.8537 | 0.22791
12577 | 1.8537 | 0.22793
12578 | 1.8537 | 0.22794
12579 | 1.8536 | 0.22796
12580 | 1.8536 | 0.22797
12581 | 1.8536 | 0.22799
12582 | 1.8536 | 0.22801
12583 | 1.8536 | 0.22802
12584 | 1.8535 | 0.22804
12585 | 1.8535 | 0.22806
12586 | 1.8535 | 0.22807
12587 | 1.8535 | 0.22809
12588 | 1.8535 | 0.2281
12589 | 1.8534 | 0.22812
12590 | 1.8534 | 0.22814
12591 | 1.8534 | 0.22815
12592 | 1.8534 | 0.22817
12593 | 1.8534 | 0.22818
12594 | 1.8533 | 0.2282
12595 | 1.8533 | 0.22822
12596 | 1.8533 | 0.22823
12597 | 1.8533 | 0.22825
12598 | 1.8533 | 0.22827
12599 | 1.8533 | 0.22828
12600 | 1.8532 | 0.2283
12601 | 1.8532 | 0.22831
12602 | 1.8532 | 0.22833
12603 | 1.8532 | 0.22835
12604 | 1.8532 | 0.22836
12605 | 1.8531 | 0.22838
12606 | 1.8531 | 0.2284
12607 | 1.8531 | 0.22841
12608 | 1.8531 | 0.22843
12609 | 1.8531 | 0.22844
12610 | 1.853 | 0.22846
12611 | 1.853 | 0.22848
12612 | 1.853 | 0.22849
12613 | 1.853 | 0.22851
12614 | 1.853 | 0.22853
12615 | 1.8529 | 0.22854
12616 | 1.8529 | 0.22856
12617 | 1.8529 | 0.22857
12618 | 1.8529 | 0.22859
12619 | 1.8529 | 0.22861
12620 | 1.8528 | 0.22862
12621 | 1.8528 | 0.22864
12622 | 1.8528 | 0.22865
12623 | 1.8528 | 0.22867
12624 | 1.8528 | 0.22869
12625 | 1.8527 | 0.2287
12626 | 1.8527 | 0.22872
12627 | 1.8527 | 0.22874
12628 | 1.8527 | 0.22875
12629 | 1.8527 | 0.22877
12630 | 1.8526 | 0.22878
12631 | 1.8526 | 0.2288
12632 | 1.8526 | 0.22882
12633 | 1.8526 | 0.22883
12634 | 1.8526 | 0.22885
12635 | 1.8525 | 0.22887
12636 | 1.8525 | 0.22888
12637 | 1.8525 | 0.2289
12638 | 1.8525 | 0.22891
12639 | 1.8525 | 0.22893
12640 | 1.8524 | 0.22895
12641 | 1.8524 | 0.22896
12642 | 1.8524 | 0.22898
12643 | 1.8524 | 0.229
12644 | 1.8524 | 0.22901
12645 | 1.8523 | 0.22903
12646 | 1.8523 | 0.22904
12647 | 1.8523 | 0.22906
12648 | 1.8523 | 0.22908
12649 | 1.8523 | 0.22909
12650 | 1.8522 | 0.22911
12651 | 1.8522 | 0.22912
12652 | 1.8522 | 0.22914
12653 | 1.8522 | 0.22916
12654 | 1.8522 | 0.22917
12655 | 1.8521 | 0.22919
12656 | 1.8521 | 0.22921
12657 | 1.8521 | 0.22922
12658 | 1.8521 | 0.22924
12659 | 1.8521 | 0.22925
12660 | 1.8521 | 0.22927
12661 | 1.852 | 0.22929
12662 | 1.852 | 0.2293
12663 | 1.852 | 0.22932
12664 | 1.852 | 0.22934
12665 | 1.852 | 0.22935
12666 | 1.8519 | 0.22937
12667 | 1.8519 | 0.22938
12668 | 1.8519 | 0.2294
12669 | 1.8519 | 0.22942
12670 | 1.8519 | 0.22943
12671 | 1.8518 | 0.22945
12672 | 1.8518 | 0.22947
12673 | 1.8518 | 0.22948
12674 | 1.8518 | 0.2295
12675 | 1.8518 | 0.22951
12676 | 1.8517 | 0.22953
12677 | 1.8517 | 0.22955
12678 | 1.8517 | 0.22956
12679 | 1.8517 | 0.22958
12680 | 1.8517 | 0.22959
12681 | 1.8516 | 0.22961
12682 | 1.8516 | 0.22963
12683 | 1.8516 | 0.22964
12684 | 1.8516 | 0.22966
12685 | 1.8516 | 0.22968
12686 | 1.8515 | 0.22969
12687 | 1.8515 | 0.22971
12688 | 1.8515 | 0.22972
12689 | 1.8515 | 0.22974
12690 | 1.8515 | 0.22976
12691 | 1.8514 | 0.22977
12692 | 1.8514 | 0.22979
12693 | 1.8514 | 0.22981
12694 | 1.8514 | 0.22982
12695 | 1.8514 | 0.22984
12696 | 1.8513 | 0.22985
12697 | 1.8513 | 0.22987
12698 | 1.8513 | 0.22989
12699 | 1.8513 | 0.2299
12700 | 1.8513 | 0.22992
12701 | 1.8512 | 0.22993
12702 | 1.8512 | 0.22995
12703 | 1.8512 | 0.22997
12704 | 1.8512 | 0.22998
12705 | 1.8512 | 0.23
12706 | 1.8511 | 0.23002
12707 | 1.8511 | 0.23003
12708 | 1.8511 | 0.23005
12709 | 1.8511 | 0.23006
12710 | 1.8511 | 0.23008
12711 | 1.851 | 0.2301
12712 | 1.851 | 0.23011
12713 | 1.851 | 0.23013
12714 | 1.851 | 0.23014
12715 | 1.851 | 0.23016
12716 | 1.851 | 0.23018
12717 | 1.8509 | 0.23019
12718 | 1.8509 | 0.23021
12719 | 1.8509 | 0.23023
12720 | 1.8509 | 0.23024
12721 | 1.8509 | 0.23026
12722 | 1.8508 | 0.23027
12723 | 1.8508 | 0.23029
12724 | 1.8508 | 0.23031
12725 | 1.8508 | 0.23032
12726 | 1.8508 | 0.23034
12727 | 1.8507 | 0.23036
12728 | 1.8507 | 0.23037
12729 | 1.8507 | 0.23039
12730 | 1.8507 | 0.2304
12731 | 1.8507 | 0.23042
12732 | 1.8506 | 0.23044
12733 | 1.8506 | 0.23045
12734 | 1.8506 | 0.23047
12735 | 1.8506 | 0.23048
12736 | 1.8506 | 0.2305
12737 | 1.8505 | 0.23052
12738 | 1.8505 | 0.23053
12739 | 1.8505 | 0.23055
12740 | 1.8505 | 0.23057
12741 | 1.8505 | 0.23058
12742 | 1.8504 | 0.2306
12743 | 1.8504 | 0.23061
12744 | 1.8504 | 0.23063
12745 | 1.8504 | 0.23065
12746 | 1.8504 | 0.23066
12747 | 1.8503 | 0.23068
12748 | 1.8503 | 0.2307
12749 | 1.8503 | 0.23071
12750 | 1.8503 | 0.23073
12751 | 1.8503 | 0.23074
12752 | 1.8502 | 0.23076
12753 | 1.8502 | 0.23078
12754 | 1.8502 | 0.23079
12755 | 1.8502 | 0.23081
12756 | 1.8502 | 0.23082
12757 | 1.8501 | 0.23084
12758 | 1.8501 | 0.23086
12759 | 1.8501 | 0.23087
12760 | 1.8501 | 0.23089
12761 | 1.8501 | 0.23091
12762 | 1.8501 | 0.23092
12763 | 1.85 | 0.23094
12764 | 1.85 | 0.23095
12765 | 1.85 | 0.23097
12766 | 1.85 | 0.23099
12767 | 1.85 | 0.231
12768 | 1.8499 | 0.23102
12769 | 1.8499 | 0.23103
12770 | 1.8499 | 0.23105
12771 | 1.8499 | 0.23107
12772 | 1.8499 | 0.23108
12773 | 1.8498 | 0.2311
12774 | 1.8498 | 0.23112
12775 | 1.8498 | 0.23113
12776 | 1.8498 | 0.23115
12777 | 1.8498 | 0.23116
12778 | 1.8497 | 0.23118
12779 | 1.8497 | 0.2312
12780 | 1.8497 | 0.23121
12781 | 1.8497 | 0.23123
12782 | 1.8497 | 0.23124
12783 | 1.8496 | 0.23126
12784 | 1.8496 | 0.23128
12785 | 1.8496 | 0.23129
12786 | 1.8496 | 0.23131
12787 | 1.8496 | 0.23133
12788 | 1.8495 | 0.23134
12789 | 1.8495 | 0.23136
12790 | 1.8495 | 0.23137
12791 | 1.8495 | 0.23139
12792 | 1.8495 | 0.23141
12793 | 1.8494 | 0.23142
12794 | 1.8494 | 0.23144
12795 | 1.8494 | 0.23146
12796 | 1.8494 | 0.23147
12797 | 1.8494 | 0.23149
12798 | 1.8493 | 0.2315
12799 | 1.8493 | 0.23152
12800 | 1.8493 | 0.23154
12801 | 1.8493 | 0.23155
12802 | 1.8493 | 0.23157
12803 | 1.8492 | 0.23158
12804 | 1.8492 | 0.2316
12805 | 1.8492 | 0.23162
12806 | 1.8492 | 0.23163
12807 | 1.8492 | 0.23165
12808 | 1.8492 | 0.23167
12809 | 1.8491 | 0.23168
12810 | 1.8491 | 0.2317
12811 | 1.8491 | 0.23171
12812 | 1.8491 | 0.23173
12813 | 1.8491 | 0.23175
12814 | 1.849 | 0.23176
12815 | 1.849 | 0.23178
12816 | 1.849 | 0.23179
12817 | 1.849 | 0.23181
12818 | 1.849 | 0.23183
12819 | 1.8489 | 0.23184
12820 | 1.8489 | 0.23186
12821 | 1.8489 | 0.23188
12822 | 1.8489 | 0.23189
12823 | 1.8489 | 0.23191
12824 | 1.8488 | 0.23192
12825 | 1.8488 | 0.23194
12826 | 1.8488 | 0.23196
12827 | 1.8488 | 0.23197
12828 | 1.8488 | 0.23199
12829 | 1.8487 | 0.232
12830 | 1.8487 | 0.23202
12831 | 1.8487 | 0.23204
12832 | 1.8487 | 0.23205
12833 | 1.8487 | 0.23207
12834 | 1.8486 | 0.23209
12835 | 1.8486 | 0.2321
12836 | 1.8486 | 0.23212
12837 | 1.8486 | 0.23213
12838 | 1.8486 | 0.23215
12839 | 1.8485 | 0.23217
12840 | 1.8485 | 0.23218
12841 | 1.8485 | 0.2322
12842 | 1.8485 | 0.23221
12843 | 1.8485 | 0.23223
12844 | 1.8484 | 0.23225
12845 | 1.8484 | 0.23226
12846 | 1.8484 | 0.23228
12847 | 1.8484 | 0.2323
12848 | 1.8484 | 0.23231
12849 | 1.8484 | 0.23233
12850 | 1.8483 | 0.23234
12851 | 1.8483 | 0.23236
12852 | 1.8483 | 0.23238
12853 | 1.8483 | 0.23239
12854 | 1.8483 | 0.23241
12855 | 1.8482 | 0.23242
12856 | 1.8482 | 0.23244
12857 | 1.8482 | 0.23246
12858 | 1.8482 | 0.23247
12859 | 1.8482 | 0.23249
12860 | 1.8481 | 0.23251
12861 | 1.8481 | 0.23252
12862 | 1.8481 | 0.23254
12863 | 1.8481 | 0.23255
12864 | 1.8481 | 0.23257
12865 | 1.848 | 0.23259
12866 | 1.848 | 0.2326
12867 | 1.848 | 0.23262
12868 | 1.848 | 0.23263
12869 | 1.848 | 0.23265
12870 | 1.8479 | 0.23267
12871 | 1.8479 | 0.23268
12872 | 1.8479 | 0.2327
12873 | 1.8479 | 0.23272
12874 | 1.8479 | 0.23273
12875 | 1.8478 | 0.23275
12876 | 1.8478 | 0.23276
12877 | 1.8478 | 0.23278
12878 | 1.8478 | 0.2328
12879 | 1.8478 | 0.23281
12880 | 1.8477 | 0.23283
12881 | 1.8477 | 0.23284
12882 | 1.8477 | 0.23286
12883 | 1.8477 | 0.23288
12884 | 1.8477 | 0.23289
12885 | 1.8477 | 0.23291
12886 | 1.8476 | 0.23292
12887 | 1.8476 | 0.23294
12888 | 1.8476 | 0.23296
12889 | 1.8476 | 0.23297
12890 | 1.8476 | 0.23299
12891 | 1.8475 | 0.23301
12892 | 1.8475 | 0.23302
12893 | 1.8475 | 0.23304
12894 | 1.8475 | 0.23305
12895 | 1.8475 | 0.23307
12896 | 1.8474 | 0.23309
12897 | 1.8474 | 0.2331
12898 | 1.8474 | 0.23312
12899 | 1.8474 | 0.23313
12900 | 1.8474 | 0.23315
12901 | 1.8473 | 0.23317
12902 | 1.8473 | 0.23318
12903 | 1.8473 | 0.2332
12904 | 1.8473 | 0.23322
12905 | 1.8473 | 0.23323
12906 | 1.8472 | 0.23325
12907 | 1.8472 | 0.23326
12908 | 1.8472 | 0.23328
12909 | 1.8472 | 0.2333
12910 | 1.8472 | 0.23331
12911 | 1.8471 | 0.23333
12912 | 1.8471 | 0.23334
12913 | 1.8471 | 0.23336
12914 | 1.8471 | 0.23338
12915 | 1.8471 | 0.23339
12916 | 1.847 | 0.23341
12917 | 1.847 | 0.23343
12918 | 1.847 | 0.23344
12919 | 1.847 | 0.23346
12920 | 1.847 | 0.23347
12921 | 1.847 | 0.23349
12922 | 1.8469 | 0.23351
12923 | 1.8469 | 0.23352
12924 | 1.8469 | 0.23354
12925 | 1.8469 | 0.23355
12926 | 1.8469 | 0.23357
12927 | 1.8468 | 0.23359
12928 | 1.8468 | 0.2336
12929 | 1.8468 | 0.23362
12930 | 1.8468 | 0.23363
12931 | 1.8468 | 0.23365
12932 | 1.8467 | 0.23367
12933 | 1.8467 | 0.23368
12934 | 1.8467 | 0.2337
12935 | 1.8467 | 0.23372
12936 | 1.8467 | 0.23373
12937 | 1.8466 | 0.23375
12938 | 1.8466 | 0.23376
12939 | 1.8466 | 0.23378
12940 | 1.8466 | 0.2338
12941 | 1.8466 | 0.23381
12942 | 1.8465 | 0.23383
12943 | 1.8465 | 0.23384
12944 | 1.8465 | 0.23386
12945 | 1.8465 | 0.23388
12946 | 1.8465 | 0.23389
12947 | 1.8464 | 0.23391
12948 | 1.8464 | 0.23393
12949 | 1.8464 | 0.23394
12950 | 1.8464 | 0.23396
12951 | 1.8464 | 0.23397
12952 | 1.8463 | 0.23399
12953 | 1.8463 | 0.23401
12954 | 1.8463 | 0.23402
12955 | 1.8463 | 0.23404
12956 | 1.8463 | 0.23405
12957 | 1.8463 | 0.23407
12958 | 1.8462 | 0.23409
12959 | 1.8462 | 0.2341
12960 | 1.8462 | 0.23412
12961 | 1.8462 | 0.23413
12962 | 1.8462 | 0.23415
12963 | 1.8461 | 0.23417
12964 | 1.8461 | 0.23418
12965 | 1.8461 | 0.2342
12966 | 1.8461 | 0.23422
12967 | 1.8461 | 0.23423
12968 | 1.846 | 0.23425
12969 | 1.846 | 0.23426
12970 | 1.846 | 0.23428
12971 | 1.846 | 0.2343
12972 | 1.846 | 0.23431
12973 | 1.8459 | 0.23433
12974 | 1.8459 | 0.23434
12975 | 1.8459 | 0.23436
12976 | 1.8459 | 0.23438
12977 | 1.8459 | 0.23439
12978 | 1.8458 | 0.23441
12979 | 1.8458 | 0.23443
12980 | 1.8458 | 0.23444
12981 | 1.8458 | 0.23446
12982 | 1.8458 | 0.23447
12983 | 1.8457 | 0.23449
12984 | 1.8457 | 0.23451
12985 | 1.8457 | 0.23452
12986 | 1.8457 | 0.23454
12987 | 1.8457 | 0.23455
12988 | 1.8457 | 0.23457
12989 | 1.8456 | 0.23459
12990 | 1.8456 | 0.2346
12991 | 1.8456 | 0.23462
12992 | 1.8456 | 0.23463
12993 | 1.8456 | 0.23465
12994 | 1.8455 | 0.23467
12995 | 1.8455 | 0.23468
12996 | 1.8455 | 0.2347
12997 | 1.8455 | 0.23472
12998 | 1.8455 | 0.23473
12999 | 1.8454 | 0.23475
13000 | 1.8454 | 0.23476
13001 | 1.8454 | 0.23478
13002 | 1.8454 | 0.2348
13003 | 1.8454 | 0.23481
13004 | 1.8453 | 0.23483
13005 | 1.8453 | 0.23484
13006 | 1.8453 | 0.23486
13007 | 1.8453 | 0.23488
13008 | 1.8453 | 0.23489
13009 | 1.8452 | 0.23491
13010 | 1.8452 | 0.23492
13011 | 1.8452 | 0.23494
13012 | 1.8452 | 0.23496
13013 | 1.8452 | 0.23497
13014 | 1.8451 | 0.23499
13015 | 1.8451 | 0.23501
13016 | 1.8451 | 0.23502
13017 | 1.8451 | 0.23504
13018 | 1.8451 | 0.23505
13019 | 1.8451 | 0.23507
13020 | 1.845 | 0.23509
13021 | 1.845 | 0.2351
13022 | 1.845 | 0.23512
13023 | 1.845 | 0.23513
13024 | 1.845 | 0.23515
13025 | 1.8449 | 0.23517
13026 | 1.8449 | 0.23518
13027 | 1.8449 | 0.2352
13028 | 1.8449 | 0.23521
13029 | 1.8449 | 0.23523
13030 | 1.8448 | 0.23525
13031 | 1.8448 | 0.23526
13032 | 1.8448 | 0.23528
13033 | 1.8448 | 0.2353
13034 | 1.8448 | 0.23531
13035 | 1.8447 | 0.23533
13036 | 1.8447 | 0.23534
13037 | 1.8447 | 0.23536
13038 | 1.8447 | 0.23538
13039 | 1.8447 | 0.23539
13040 | 1.8446 | 0.23541
13041 | 1.8446 | 0.23542
13042 | 1.8446 | 0.23544
13043 | 1.8446 | 0.23546
13044 | 1.8446 | 0.23547
13045 | 1.8445 | 0.23549
13046 | 1.8445 | 0.2355
13047 | 1.8445 | 0.23552
13048 | 1.8445 | 0.23554
13049 | 1.8445 | 0.23555
13050 | 1.8445 | 0.23557
13051 | 1.8444 | 0.23558
13052 | 1.8444 | 0.2356
13053 | 1.8444 | 0.23562
13054 | 1.8444 | 0.23563
13055 | 1.8444 | 0.23565
13056 | 1.8443 | 0.23567
13057 | 1.8443 | 0.23568
13058 | 1.8443 | 0.2357
13059 | 1.8443 | 0.23571
13060 | 1.8443 | 0.23573
13061 | 1.8442 | 0.23575
13062 | 1.8442 | 0.23576
13063 | 1.8442 | 0.23578
13064 | 1.8442 | 0.23579
13065 | 1.8442 | 0.23581
13066 | 1.8441 | 0.23583
13067 | 1.8441 | 0.23584
13068 | 1.8441 | 0.23586
13069 | 1.8441 | 0.23587
13070 | 1.8441 | 0.23589
13071 | 1.844 | 0.23591
13072 | 1.844 | 0.23592
13073 | 1.844 | 0.23594
13074 | 1.844 | 0.23596
13075 | 1.844 | 0.23597
13076 | 1.8439 | 0.23599
13077 | 1.8439 | 0.236
13078 | 1.8439 | 0.23602
13079 | 1.8439 | 0.23604
13080 | 1.8439 | 0.23605
13081 | 1.8439 | 0.23607
13082 | 1.8438 | 0.23608
13083 | 1.8438 | 0.2361
13084 | 1.8438 | 0.23612
13085 | 1.8438 | 0.23613
13086 | 1.8438 | 0.23615
13087 | 1.8437 | 0.23616
13088 | 1.8437 | 0.23618
13089 | 1.8437 | 0.2362
13090 | 1.8437 | 0.23621
13091 | 1.8437 | 0.23623
13092 | 1.8436 | 0.23624
13093 | 1.8436 | 0.23626
13094 | 1.8436 | 0.23628
13095 | 1.8436 | 0.23629
13096 | 1.8436 | 0.23631
13097 | 1.8435 | 0.23633
13098 | 1.8435 | 0.23634
13099 | 1.8435 | 0.23636
13100 | 1.8435 | 0.23637
13101 | 1.8435 | 0.23639
13102 | 1.8434 | 0.23641
13103 | 1.8434 | 0.23642
13104 | 1.8434 | 0.23644
13105 | 1.8434 | 0.23645
13106 | 1.8434 | 0.23647
13107 | 1.8434 | 0.23649
13108 | 1.8433 | 0.2365
13109 | 1.8433 | 0.23652
13110 | 1.8433 | 0.23653
13111 | 1.8433 | 0.23655
13112 | 1.8433 | 0.23657
13113 | 1.8432 | 0.23658
13114 | 1.8432 | 0.2366
13115 | 1.8432 | 0.23661
13116 | 1.8432 | 0.23663
13117 | 1.8432 | 0.23665
13118 | 1.8431 | 0.23666
13119 | 1.8431 | 0.23668
13120 | 1.8431 | 0.2367
13121 | 1.8431 | 0.23671
13122 | 1.8431 | 0.23673
13123 | 1.843 | 0.23674
13124 | 1.843 | 0.23676
13125 | 1.843 | 0.23678
13126 | 1.843 | 0.23679
13127 | 1.843 | 0.23681
13128 | 1.8429 | 0.23682
13129 | 1.8429 | 0.23684
13130 | 1.8429 | 0.23686
13131 | 1.8429 | 0.23687
13132 | 1.8429 | 0.23689
13133 | 1.8428 | 0.2369
13134 | 1.8428 | 0.23692
13135 | 1.8428 | 0.23694
13136 | 1.8428 | 0.23695
13137 | 1.8428 | 0.23697
13138 | 1.8428 | 0.23698
13139 | 1.8427 | 0.237
13140 | 1.8427 | 0.23702
13141 | 1.8427 | 0.23703
13142 | 1.8427 | 0.23705
13143 | 1.8427 | 0.23707
13144 | 1.8426 | 0.23708
13145 | 1.8426 | 0.2371
13146 | 1.8426 | 0.23711
13147 | 1.8426 | 0.23713
13148 | 1.8426 | 0.23715
13149 | 1.8425 | 0.23716
13150 | 1.8425 | 0.23718
13151 | 1.8425 | 0.23719
13152 | 1.8425 | 0.23721
13153 | 1.8425 | 0.23723
13154 | 1.8424 | 0.23724
13155 | 1.8424 | 0.23726
13156 | 1.8424 | 0.23727
13157 | 1.8424 | 0.23729
13158 | 1.8424 | 0.23731
13159 | 1.8423 | 0.23732
13160 | 1.8423 | 0.23734
13161 | 1.8423 | 0.23735
13162 | 1.8423 | 0.23737
13163 | 1.8423 | 0.23739
13164 | 1.8423 | 0.2374
13165 | 1.8422 | 0.23742
13166 | 1.8422 | 0.23743
13167 | 1.8422 | 0.23745
13168 | 1.8422 | 0.23747
13169 | 1.8422 | 0.23748
13170 | 1.8421 | 0.2375
13171 | 1.8421 | 0.23752
13172 | 1.8421 | 0.23753
13173 | 1.8421 | 0.23755
13174 | 1.8421 | 0.23756
13175 | 1.842 | 0.23758
13176 | 1.842 | 0.2376
13177 | 1.842 | 0.23761
13178 | 1.842 | 0.23763
13179 | 1.842 | 0.23764
13180 | 1.8419 | 0.23766
13181 | 1.8419 | 0.23768
13182 | 1.8419 | 0.23769
13183 | 1.8419 | 0.23771
13184 | 1.8419 | 0.23772
13185 | 1.8418 | 0.23774
13186 | 1.8418 | 0.23776
13187 | 1.8418 | 0.23777
13188 | 1.8418 | 0.23779
13189 | 1.8418 | 0.2378
13190 | 1.8418 | 0.23782
13191 | 1.8417 | 0.23784
13192 | 1.8417 | 0.23785
13193 | 1.8417 | 0.23787
13194 | 1.8417 | 0.23788
13195 | 1.8417 | 0.2379
13196 | 1.8416 | 0.23792
13197 | 1.8416 | 0.23793
13198 | 1.8416 | 0.23795
13199 | 1.8416 | 0.23797
13200 | 1.8416 | 0.23798
13201 | 1.8415 | 0.238
13202 | 1.8415 | 0.23801
13203 | 1.8415 | 0.23803
13204 | 1.8415 | 0.23805
13205 | 1.8415 | 0.23806
13206 | 1.8414 | 0.23808
13207 | 1.8414 | 0.23809
13208 | 1.8414 | 0.23811
13209 | 1.8414 | 0.23813
13210 | 1.8414 | 0.23814
13211 | 1.8413 | 0.23816
13212 | 1.8413 | 0.23817
13213 | 1.8413 | 0.23819
13214 | 1.8413 | 0.23821
13215 | 1.8413 | 0.23822
13216 | 1.8413 | 0.23824
13217 | 1.8412 | 0.23825
13218 | 1.8412 | 0.23827
13219 | 1.8412 | 0.23829
13220 | 1.8412 | 0.2383
13221 | 1.8412 | 0.23832
13222 | 1.8411 | 0.23833
13223 | 1.8411 | 0.23835
13224 | 1.8411 | 0.23837
13225 | 1.8411 | 0.23838
13226 | 1.8411 | 0.2384
13227 | 1.841 | 0.23841
13228 | 1.841 | 0.23843
13229 | 1.841 | 0.23845
13230 | 1.841 | 0.23846
13231 | 1.841 | 0.23848
13232 | 1.8409 | 0.2385
13233 | 1.8409 | 0.23851
13234 | 1.8409 | 0.23853
13235 | 1.8409 | 0.23854
13236 | 1.8409 | 0.23856
13237 | 1.8408 | 0.23858
13238 | 1.8408 | 0.23859
13239 | 1.8408 | 0.23861
13240 | 1.8408 | 0.23862
13241 | 1.8408 | 0.23864
13242 | 1.8408 | 0.23866
13243 | 1.8407 | 0.23867
13244 | 1.8407 | 0.23869
13245 | 1.8407 | 0.2387
13246 | 1.8407 | 0.23872
13247 | 1.8407 | 0.23874
13248 | 1.8406 | 0.23875
13249 | 1.8406 | 0.23877
13250 | 1.8406 | 0.23878
13251 | 1.8406 | 0.2388
13252 | 1.8406 | 0.23882
13253 | 1.8405 | 0.23883
13254 | 1.8405 | 0.23885
13255 | 1.8405 | 0.23886
13256 | 1.8405 | 0.23888
13257 | 1.8405 | 0.2389
13258 | 1.8404 | 0.23891
13259 | 1.8404 | 0.23893
13260 | 1.8404 | 0.23894
13261 | 1.8404 | 0.23896
13262 | 1.8404 | 0.23898
13263 | 1.8404 | 0.23899
13264 | 1.8403 | 0.23901
13265 | 1.8403 | 0.23902
13266 | 1.8403 | 0.23904
13267 | 1.8403 | 0.23906
13268 | 1.8403 | 0.23907
13269 | 1.8402 | 0.23909
13270 | 1.8402 | 0.23911
13271 | 1.8402 | 0.23912
13272 | 1.8402 | 0.23914
13273 | 1.8402 | 0.23915
13274 | 1.8401 | 0.23917
13275 | 1.8401 | 0.23919
13276 | 1.8401 | 0.2392
13277 | 1.8401 | 0.23922
13278 | 1.8401 | 0.23923
13279 | 1.84 | 0.23925
13280 | 1.84 | 0.23927
13281 | 1.84 | 0.23928
13282 | 1.84 | 0.2393
13283 | 1.84 | 0.23931
13284 | 1.8399 | 0.23933
13285 | 1.8399 | 0.23935
13286 | 1.8399 | 0.23936
13287 | 1.8399 | 0.23938
13288 | 1.8399 | 0.23939
13289 | 1.8399 | 0.23941
13290 | 1.8398 | 0.23943
13291 | 1.8398 | 0.23944
13292 | 1.8398 | 0.23946
13293 | 1.8398 | 0.23947
13294 | 1.8398 | 0.23949
13295 | 1.8397 | 0.23951
13296 | 1.8397 | 0.23952
13297 | 1.8397 | 0.23954
13298 | 1.8397 | 0.23955
13299 | 1.8397 | 0.23957
13300 | 1.8396 | 0.23959
13301 | 1.8396 | 0.2396
13302 | 1.8396 | 0.23962
13303 | 1.8396 | 0.23963
13304 | 1.8396 | 0.23965
13305 | 1.8395 | 0.23967
13306 | 1.8395 | 0.23968
13307 | 1.8395 | 0.2397
13308 | 1.8395 | 0.23971
13309 | 1.8395 | 0.23973
13310 | 1.8395 | 0.23975
13311 | 1.8394 | 0.23976
13312 | 1.8394 | 0.23978
13313 | 1.8394 | 0.23979
13314 | 1.8394 | 0.23981
13315 | 1.8394 | 0.23983
13316 | 1.8393 | 0.23984
13317 | 1.8393 | 0.23986
13318 | 1.8393 | 0.23988
13319 | 1.8393 | 0.23989
13320 | 1.8393 | 0.23991
13321 | 1.8392 | 0.23992
13322 | 1.8392 | 0.23994
13323 | 1.8392 | 0.23996
13324 | 1.8392 | 0.23997
13325 | 1.8392 | 0.23999
13326 | 1.8391 | 0.24
13327 | 1.8391 | 0.24002
13328 | 1.8391 | 0.24004
13329 | 1.8391 | 0.24005
13330 | 1.8391 | 0.24007
13331 | 1.8391 | 0.24008
13332 | 1.839 | 0.2401
13333 | 1.839 | 0.24012
13334 | 1.839 | 0.24013
13335 | 1.839 | 0.24015
13336 | 1.839 | 0.24016
13337 | 1.8389 | 0.24018
13338 | 1.8389 | 0.2402
13339 | 1.8389 | 0.24021
13340 | 1.8389 | 0.24023
13341 | 1.8389 | 0.24024
13342 | 1.8388 | 0.24026
13343 | 1.8388 | 0.24028
13344 | 1.8388 | 0.24029
13345 | 1.8388 | 0.24031
13346 | 1.8388 | 0.24032
13347 | 1.8387 | 0.24034
13348 | 1.8387 | 0.24036
13349 | 1.8387 | 0.24037
13350 | 1.8387 | 0.24039
13351 | 1.8387 | 0.2404
13352 | 1.8386 | 0.24042
13353 | 1.8386 | 0.24044
13354 | 1.8386 | 0.24045
13355 | 1.8386 | 0.24047
13356 | 1.8386 | 0.24048
13357 | 1.8386 | 0.2405
13358 | 1.8385 | 0.24052
13359 | 1.8385 | 0.24053
13360 | 1.8385 | 0.24055
13361 | 1.8385 | 0.24056
13362 | 1.8385 | 0.24058
13363 | 1.8384 | 0.2406
13364 | 1.8384 | 0.24061
13365 | 1.8384 | 0.24063
13366 | 1.8384 | 0.24064
13367 | 1.8384 | 0.24066
13368 | 1.8383 | 0.24068
13369 | 1.8383 | 0.24069
13370 | 1.8383 | 0.24071
13371 | 1.8383 | 0.24072
13372 | 1.8383 | 0.24074
13373 | 1.8382 | 0.24076
13374 | 1.8382 | 0.24077
13375 | 1.8382 | 0.24079
13376 | 1.8382 | 0.2408
13377 | 1.8382 | 0.24082
13378 | 1.8382 | 0.24084
13379 | 1.8381 | 0.24085
13380 | 1.8381 | 0.24087
13381 | 1.8381 | 0.24088
13382 | 1.8381 | 0.2409
13383 | 1.8381 | 0.24092
13384 | 1.838 | 0.24093
13385 | 1.838 | 0.24095
13386 | 1.838 | 0.24096
13387 | 1.838 | 0.24098
13388 | 1.838 | 0.241
13389 | 1.8379 | 0.24101
13390 | 1.8379 | 0.24103
13391 | 1.8379 | 0.24105
13392 | 1.8379 | 0.24106
13393 | 1.8379 | 0.24108
13394 | 1.8378 | 0.24109
13395 | 1.8378 | 0.24111
13396 | 1.8378 | 0.24113
13397 | 1.8378 | 0.24114
13398 | 1.8378 | 0.24116
13399 | 1.8378 | 0.24117
13400 | 1.8377 | 0.24119
13401 | 1.8377 | 0.24121
13402 | 1.8377 | 0.24122
13403 | 1.8377 | 0.24124
13404 | 1.8377 | 0.24125
13405 | 1.8376 | 0.24127
13406 | 1.8376 | 0.24129
13407 | 1.8376 | 0.2413
13408 | 1.8376 | 0.24132
13409 | 1.8376 | 0.24133
13410 | 1.8375 | 0.24135
13411 | 1.8375 | 0.24137
13412 | 1.8375 | 0.24138
13413 | 1.8375 | 0.2414
13414 | 1.8375 | 0.24141
13415 | 1.8374 | 0.24143
13416 | 1.8374 | 0.24145
13417 | 1.8374 | 0.24146
13418 | 1.8374 | 0.24148
13419 | 1.8374 | 0.24149
13420 | 1.8374 | 0.24151
13421 | 1.8373 | 0.24153
13422 | 1.8373 | 0.24154
13423 | 1.8373 | 0.24156
13424 | 1.8373 | 0.24157
13425 | 1.8373 | 0.24159
13426 | 1.8372 | 0.24161
13427 | 1.8372 | 0.24162
13428 | 1.8372 | 0.24164
13429 | 1.8372 | 0.24165
13430 | 1.8372 | 0.24167
13431 | 1.8371 | 0.24169
13432 | 1.8371 | 0.2417
13433 | 1.8371 | 0.24172
13434 | 1.8371 | 0.24173
13435 | 1.8371 | 0.24175
13436 | 1.837 | 0.24177
13437 | 1.837 | 0.24178
13438 | 1.837 | 0.2418
13439 | 1.837 | 0.24181
13440 | 1.837 | 0.24183
13441 | 1.837 | 0.24185
13442 | 1.8369 | 0.24186
13443 | 1.8369 | 0.24188
13444 | 1.8369 | 0.24189
13445 | 1.8369 | 0.24191
13446 | 1.8369 | 0.24193
13447 | 1.8368 | 0.24194
13448 | 1.8368 | 0.24196
13449 | 1.8368 | 0.24197
13450 | 1.8368 | 0.24199
13451 | 1.8368 | 0.24201
13452 | 1.8367 | 0.24202
13453 | 1.8367 | 0.24204
13454 | 1.8367 | 0.24205
13455 | 1.8367 | 0.24207
13456 | 1.8367 | 0.24209
13457 | 1.8366 | 0.2421
13458 | 1.8366 | 0.24212
13459 | 1.8366 | 0.24213
13460 | 1.8366 | 0.24215
13461 | 1.8366 | 0.24217
13462 | 1.8366 | 0.24218
13463 | 1.8365 | 0.2422
13464 | 1.8365 | 0.24221
13465 | 1.8365 | 0.24223
13466 | 1.8365 | 0.24225
13467 | 1.8365 | 0.24226
13468 | 1.8364 | 0.24228
13469 | 1.8364 | 0.24229
13470 | 1.8364 | 0.24231
13471 | 1.8364 | 0.24233
13472 | 1.8364 | 0.24234
13473 | 1.8363 | 0.24236
13474 | 1.8363 | 0.24237
13475 | 1.8363 | 0.24239
13476 | 1.8363 | 0.24241
13477 | 1.8363 | 0.24242
13478 | 1.8363 | 0.24244
13479 | 1.8362 | 0.24245
13480 | 1.8362 | 0.24247
13481 | 1.8362 | 0.24249
13482 | 1.8362 | 0.2425
13483 | 1.8362 | 0.24252
13484 | 1.8361 | 0.24253
13485 | 1.8361 | 0.24255
13486 | 1.8361 | 0.24257
13487 | 1.8361 | 0.24258
13488 | 1.8361 | 0.2426
13489 | 1.836 | 0.24261
13490 | 1.836 | 0.24263
13491 | 1.836 | 0.24265
13492 | 1.836 | 0.24266
13493 | 1.836 | 0.24268
13494 | 1.8359 | 0.24269
13495 | 1.8359 | 0.24271
13496 | 1.8359 | 0.24273
13497 | 1.8359 | 0.24274
13498 | 1.8359 | 0.24276
13499 | 1.8359 | 0.24277
13500 | 1.8358 | 0.24279
13501 | 1.8358 | 0.24281
13502 | 1.8358 | 0.24282
13503 | 1.8358 | 0.24284
13504 | 1.8358 | 0.24285
13505 | 1.8357 | 0.24287
13506 | 1.8357 | 0.24289
13507 | 1.8357 | 0.2429
13508 | 1.8357 | 0.24292
13509 | 1.8357 | 0.24293
13510 | 1.8356 | 0.24295
13511 | 1.8356 | 0.24297
13512 | 1.8356 | 0.24298
13513 | 1.8356 | 0.243
13514 | 1.8356 | 0.24301
13515 | 1.8355 | 0.24303
13516 | 1.8355 | 0.24305
13517 | 1.8355 | 0.24306
13518 | 1.8355 | 0.24308
13519 | 1.8355 | 0.24309
13520 | 1.8355 | 0.24311
13521 | 1.8354 | 0.24313
13522 | 1.8354 | 0.24314
13523 | 1.8354 | 0.24316
13524 | 1.8354 | 0.24317
13525 | 1.8354 | 0.24319
13526 | 1.8353 | 0.24321
13527 | 1.8353 | 0.24322
13528 | 1.8353 | 0.24324
13529 | 1.8353 | 0.24325
13530 | 1.8353 | 0.24327
13531 | 1.8352 | 0.24329
13532 | 1.8352 | 0.2433
13533 | 1.8352 | 0.24332
13534 | 1.8352 | 0.24333
13535 | 1.8352 | 0.24335
13536 | 1.8352 | 0.24337
13537 | 1.8351 | 0.24338
13538 | 1.8351 | 0.2434
13539 | 1.8351 | 0.24341
13540 | 1.8351 | 0.24343
13541 | 1.8351 | 0.24345
13542 | 1.835 | 0.24346
13543 | 1.835 | 0.24348
13544 | 1.835 | 0.24349
13545 | 1.835 | 0.24351
13546 | 1.835 | 0.24352
13547 | 1.8349 | 0.24354
13548 | 1.8349 | 0.24356
13549 | 1.8349 | 0.24357
13550 | 1.8349 | 0.24359
13551 | 1.8349 | 0.2436
13552 | 1.8348 | 0.24362
13553 | 1.8348 | 0.24364
13554 | 1.8348 | 0.24365
13555 | 1.8348 | 0.24367
13556 | 1.8348 | 0.24368
13557 | 1.8348 | 0.2437
13558 | 1.8347 | 0.24372
13559 | 1.8347 | 0.24373
13560 | 1.8347 | 0.24375
13561 | 1.8347 | 0.24376
13562 | 1.8347 | 0.24378
13563 | 1.8346 | 0.2438
13564 | 1.8346 | 0.24381
13565 | 1.8346 | 0.24383
13566 | 1.8346 | 0.24384
13567 | 1.8346 | 0.24386
13568 | 1.8345 | 0.24388
13569 | 1.8345 | 0.24389
13570 | 1.8345 | 0.24391
13571 | 1.8345 | 0.24392
13572 | 1.8345 | 0.24394
13573 | 1.8344 | 0.24396
13574 | 1.8344 | 0.24397
13575 | 1.8344 | 0.24399
13576 | 1.8344 | 0.244
13577 | 1.8344 | 0.24402
13578 | 1.8344 | 0.24404
13579 | 1.8343 | 0.24405
13580 | 1.8343 | 0.24407
13581 | 1.8343 | 0.24408
13582 | 1.8343 | 0.2441
13583 | 1.8343 | 0.24412
13584 | 1.8342 | 0.24413
13585 | 1.8342 | 0.24415
13586 | 1.8342 | 0.24416
13587 | 1.8342 | 0.24418
13588 | 1.8342 | 0.2442
13589 | 1.8341 | 0.24421
13590 | 1.8341 | 0.24423
13591 | 1.8341 | 0.24424
13592 | 1.8341 | 0.24426
13593 | 1.8341 | 0.24428
13594 | 1.8341 | 0.24429
13595 | 1.834 | 0.24431
13596 | 1.834 | 0.24432
13597 | 1.834 | 0.24434
13598 | 1.834 | 0.24436
13599 | 1.834 | 0.24437
13600 | 1.8339 | 0.24439
13601 | 1.8339 | 0.2444
13602 | 1.8339 | 0.24442
13603 | 1.8339 | 0.24444
13604 | 1.8339 | 0.24445
13605 | 1.8338 | 0.24447
13606 | 1.8338 | 0.24448
13607 | 1.8338 | 0.2445
13608 | 1.8338 | 0.24452
13609 | 1.8338 | 0.24453
13610 | 1.8338 | 0.24455
13611 | 1.8337 | 0.24456
13612 | 1.8337 | 0.24458
13613 | 1.8337 | 0.2446
13614 | 1.8337 | 0.24461
13615 | 1.8337 | 0.24463
13616 | 1.8336 | 0.24464
13617 | 1.8336 | 0.24466
13618 | 1.8336 | 0.24467
13619 | 1.8336 | 0.24469
13620 | 1.8336 | 0.24471
13621 | 1.8335 | 0.24472
13622 | 1.8335 | 0.24474
13623 | 1.8335 | 0.24475
13624 | 1.8335 | 0.24477
13625 | 1.8335 | 0.24479
13626 | 1.8334 | 0.2448
13627 | 1.8334 | 0.24482
13628 | 1.8334 | 0.24483
13629 | 1.8334 | 0.24485
13630 | 1.8334 | 0.24487
13631 | 1.8334 | 0.24488
13632 | 1.8333 | 0.2449
13633 | 1.8333 | 0.24491
13634 | 1.8333 | 0.24493
13635 | 1.8333 | 0.24495
13636 | 1.8333 | 0.24496
13637 | 1.8332 | 0.24498
13638 | 1.8332 | 0.24499
13639 | 1.8332 | 0.24501
13640 | 1.8332 | 0.24503
13641 | 1.8332 | 0.24504
13642 | 1.8331 | 0.24506
13643 | 1.8331 | 0.24507
13644 | 1.8331 | 0.24509
13645 | 1.8331 | 0.24511
13646 | 1.8331 | 0.24512
13647 | 1.8331 | 0.24514
13648 | 1.833 | 0.24515
13649 | 1.833 | 0.24517
13650 | 1.833 | 0.24519
13651 | 1.833 | 0.2452
13652 | 1.833 | 0.24522
13653 | 1.8329 | 0.24523
13654 | 1.8329 | 0.24525
13655 | 1.8329 | 0.24527
13656 | 1.8329 | 0.24528
13657 | 1.8329 | 0.2453
13658 | 1.8328 | 0.24531
13659 | 1.8328 | 0.24533
13660 | 1.8328 | 0.24535
13661 | 1.8328 | 0.24536
13662 | 1.8328 | 0.24538
13663 | 1.8328 | 0.24539
13664 | 1.8327 | 0.24541
13665 | 1.8327 | 0.24542
13666 | 1.8327 | 0.24544
13667 | 1.8327 | 0.24546
13668 | 1.8327 | 0.24547
13669 | 1.8326 | 0.24549
13670 | 1.8326 | 0.2455
13671 | 1.8326 | 0.24552
13672 | 1.8326 | 0.24554
13673 | 1.8326 | 0.24555
13674 | 1.8325 | 0.24557
13675 | 1.8325 | 0.24558
13676 | 1.8325 | 0.2456
13677 | 1.8325 | 0.24562
13678 | 1.8325 | 0.24563
13679 | 1.8324 | 0.24565
13680 | 1.8324 | 0.24566
13681 | 1.8324 | 0.24568
13682 | 1.8324 | 0.2457
13683 | 1.8324 | 0.24571
13684 | 1.8324 | 0.24573
13685 | 1.8323 | 0.24574
13686 | 1.8323 | 0.24576
13687 | 1.8323 | 0.24578
13688 | 1.8323 | 0.24579
13689 | 1.8323 | 0.24581
13690 | 1.8322 | 0.24582
13691 | 1.8322 | 0.24584
13692 | 1.8322 | 0.24586
13693 | 1.8322 | 0.24587
13694 | 1.8322 | 0.24589
13695 | 1.8321 | 0.2459
13696 | 1.8321 | 0.24592
13697 | 1.8321 | 0.24594
13698 | 1.8321 | 0.24595
13699 | 1.8321 | 0.24597
13700 | 1.8321 | 0.24598
13701 | 1.832 | 0.246
13702 | 1.832 | 0.24601
13703 | 1.832 | 0.24603
13704 | 1.832 | 0.24605
13705 | 1.832 | 0.24606
13706 | 1.8319 | 0.24608
13707 | 1.8319 | 0.24609
13708 | 1.8319 | 0.24611
13709 | 1.8319 | 0.24613
13710 | 1.8319 | 0.24614
13711 | 1.8318 | 0.24616
13712 | 1.8318 | 0.24617
13713 | 1.8318 | 0.24619
13714 | 1.8318 | 0.24621
13715 | 1.8318 | 0.24622
13716 | 1.8318 | 0.24624
13717 | 1.8317 | 0.24625
13718 | 1.8317 | 0.24627
13719 | 1.8317 | 0.24629
13720 | 1.8317 | 0.2463
13721 | 1.8317 | 0.24632
13722 | 1.8316 | 0.24633
13723 | 1.8316 | 0.24635
13724 | 1.8316 | 0.24637
13725 | 1.8316 | 0.24638
13726 | 1.8316 | 0.2464
13727 | 1.8315 | 0.24641
13728 | 1.8315 | 0.24643
13729 | 1.8315 | 0.24645
13730 | 1.8315 | 0.24646
13731 | 1.8315 | 0.24648
13732 | 1.8315 | 0.24649
13733 | 1.8314 | 0.24651
13734 | 1.8314 | 0.24652
13735 | 1.8314 | 0.24654
13736 | 1.8314 | 0.24656
13737 | 1.8314 | 0.24657
13738 | 1.8313 | 0.24659
13739 | 1.8313 | 0.2466
13740 | 1.8313 | 0.24662
13741 | 1.8313 | 0.24664
13742 | 1.8313 | 0.24665
13743 | 1.8312 | 0.24667
13744 | 1.8312 | 0.24668
13745 | 1.8312 | 0.2467
13746 | 1.8312 | 0.24672
13747 | 1.8312 | 0.24673
13748 | 1.8312 | 0.24675
13749 | 1.8311 | 0.24676
13750 | 1.8311 | 0.24678
13751 | 1.8311 | 0.2468
13752 | 1.8311 | 0.24681
13753 | 1.8311 | 0.24683
13754 | 1.831 | 0.24684
13755 | 1.831 | 0.24686
13756 | 1.831 | 0.24688
13757 | 1.831 | 0.24689
13758 | 1.831 | 0.24691
13759 | 1.8309 | 0.24692
13760 | 1.8309 | 0.24694
13761 | 1.8309 | 0.24696
13762 | 1.8309 | 0.24697
13763 | 1.8309 | 0.24699
13764 | 1.8309 | 0.247
13765 | 1.8308 | 0.24702
13766 | 1.8308 | 0.24703
13767 | 1.8308 | 0.24705
13768 | 1.8308 | 0.24707
13769 | 1.8308 | 0.24708
13770 | 1.8307 | 0.2471
13771 | 1.8307 | 0.24711
13772 | 1.8307 | 0.24713
13773 | 1.8307 | 0.24715
13774 | 1.8307 | 0.24716
13775 | 1.8306 | 0.24718
13776 | 1.8306 | 0.24719
13777 | 1.8306 | 0.24721
13778 | 1.8306 | 0.24723
13779 | 1.8306 | 0.24724
13780 | 1.8306 | 0.24726
13781 | 1.8305 | 0.24727
13782 | 1.8305 | 0.24729
13783 | 1.8305 | 0.24731
13784 | 1.8305 | 0.24732
13785 | 1.8305 | 0.24734
13786 | 1.8304 | 0.24735
13787 | 1.8304 | 0.24737
13788 | 1.8304 | 0.24739
13789 | 1.8304 | 0.2474
13790 | 1.8304 | 0.24742
13791 | 1.8303 | 0.24743
13792 | 1.8303 | 0.24745
13793 | 1.8303 | 0.24746
13794 | 1.8303 | 0.24748
13795 | 1.8303 | 0.2475
13796 | 1.8303 | 0.24751
13797 | 1.8302 | 0.24753
13798 | 1.8302 | 0.24754
13799 | 1.8302 | 0.24756
13800 | 1.8302 | 0.24758
13801 | 1.8302 | 0.24759
13802 | 1.8301 | 0.24761
13803 | 1.8301 | 0.24762
13804 | 1.8301 | 0.24764
13805 | 1.8301 | 0.24766
13806 | 1.8301 | 0.24767
13807 | 1.83 | 0.24769
13808 | 1.83 | 0.2477
13809 | 1.83 | 0.24772
13810 | 1.83 | 0.24774
13811 | 1.83 | 0.24775
13812 | 1.83 | 0.24777
13813 | 1.8299 | 0.24778
13814 | 1.8299 | 0.2478
13815 | 1.8299 | 0.24781
13816 | 1.8299 | 0.24783
13817 | 1.8299 | 0.24785
13818 | 1.8298 | 0.24786
13819 | 1.8298 | 0.24788
13820 | 1.8298 | 0.24789
13821 | 1.8298 | 0.24791
13822 | 1.8298 | 0.24793
13823 | 1.8297 | 0.24794
13824 | 1.8297 | 0.24796
13825 | 1.8297 | 0.24797
13826 | 1.8297 | 0.24799
13827 | 1.8297 | 0.24801
13828 | 1.8297 | 0.24802
13829 | 1.8296 | 0.24804
13830 | 1.8296 | 0.24805
13831 | 1.8296 | 0.24807
13832 | 1.8296 | 0.24809
13833 | 1.8296 | 0.2481
13834 | 1.8295 | 0.24812
13835 | 1.8295 | 0.24813
13836 | 1.8295 | 0.24815
13837 | 1.8295 | 0.24817
13838 | 1.8295 | 0.24818
13839 | 1.8294 | 0.2482
13840 | 1.8294 | 0.24821
13841 | 1.8294 | 0.24823
13842 | 1.8294 | 0.24824
13843 | 1.8294 | 0.24826
13844 | 1.8294 | 0.24828
13845 | 1.8293 | 0.24829
13846 | 1.8293 | 0.24831
13847 | 1.8293 | 0.24832
13848 | 1.8293 | 0.24834
13849 | 1.8293 | 0.24836
13850 | 1.8292 | 0.24837
13851 | 1.8292 | 0.24839
13852 | 1.8292 | 0.2484
13853 | 1.8292 | 0.24842
13854 | 1.8292 | 0.24844
13855 | 1.8291 | 0.24845
13856 | 1.8291 | 0.24847
13857 | 1.8291 | 0.24848
13858 | 1.8291 | 0.2485
13859 | 1.8291 | 0.24852
13860 | 1.8291 | 0.24853
13861 | 1.829 | 0.24855
13862 | 1.829 | 0.24856
13863 | 1.829 | 0.24858
13864 | 1.829 | 0.24859
13865 | 1.829 | 0.24861
13866 | 1.8289 | 0.24863
13867 | 1.8289 | 0.24864
13868 | 1.8289 | 0.24866
13869 | 1.8289 | 0.24867
13870 | 1.8289 | 0.24869
13871 | 1.8288 | 0.24871
13872 | 1.8288 | 0.24872
13873 | 1.8288 | 0.24874
13874 | 1.8288 | 0.24875
13875 | 1.8288 | 0.24877
13876 | 1.8288 | 0.24879
13877 | 1.8287 | 0.2488
13878 | 1.8287 | 0.24882
13879 | 1.8287 | 0.24883
13880 | 1.8287 | 0.24885
13881 | 1.8287 | 0.24886
13882 | 1.8286 | 0.24888
13883 | 1.8286 | 0.2489
13884 | 1.8286 | 0.24891
13885 | 1.8286 | 0.24893
13886 | 1.8286 | 0.24894
13887 | 1.8285 | 0.24896
13888 | 1.8285 | 0.24898
13889 | 1.8285 | 0.24899
13890 | 1.8285 | 0.24901
13891 | 1.8285 | 0.24902
13892 | 1.8285 | 0.24904
13893 | 1.8284 | 0.24906
13894 | 1.8284 | 0.24907
13895 | 1.8284 | 0.24909
13896 | 1.8284 | 0.2491
13897 | 1.8284 | 0.24912
13898 | 1.8283 | 0.24914
13899 | 1.8283 | 0.24915
13900 | 1.8283 | 0.24917
13901 | 1.8283 | 0.24918
13902 | 1.8283 | 0.2492
13903 | 1.8282 | 0.24921
13904 | 1.8282 | 0.24923
13905 | 1.8282 | 0.24925
13906 | 1.8282 | 0.24926
13907 | 1.8282 | 0.24928
13908 | 1.8282 | 0.24929
13909 | 1.8281 | 0.24931
13910 | 1.8281 | 0.24933
13911 | 1.8281 | 0.24934
13912 | 1.8281 | 0.24936
13913 | 1.8281 | 0.24937
13914 | 1.828 | 0.24939
13915 | 1.828 | 0.24941
13916 | 1.828 | 0.24942
13917 | 1.828 | 0.24944
13918 | 1.828 | 0.24945
13919 | 1.828 | 0.24947
13920 | 1.8279 | 0.24948
13921 | 1.8279 | 0.2495
13922 | 1.8279 | 0.24952
13923 | 1.8279 | 0.24953
13924 | 1.8279 | 0.24955
13925 | 1.8278 | 0.24956
13926 | 1.8278 | 0.24958
13927 | 1.8278 | 0.2496
13928 | 1.8278 | 0.24961
13929 | 1.8278 | 0.24963
13930 | 1.8277 | 0.24964
13931 | 1.8277 | 0.24966
13932 | 1.8277 | 0.24968
13933 | 1.8277 | 0.24969
13934 | 1.8277 | 0.24971
13935 | 1.8277 | 0.24972
13936 | 1.8276 | 0.24974
13937 | 1.8276 | 0.24975
13938 | 1.8276 | 0.24977
13939 | 1.8276 | 0.24979
13940 | 1.8276 | 0.2498
13941 | 1.8275 | 0.24982
13942 | 1.8275 | 0.24983
13943 | 1.8275 | 0.24985
13944 | 1.8275 | 0.24987
13945 | 1.8275 | 0.24988
13946 | 1.8274 | 0.2499
13947 | 1.8274 | 0.24991
13948 | 1.8274 | 0.24993
13949 | 1.8274 | 0.24995
13950 | 1.8274 | 0.24996
13951 | 1.8274 | 0.24998
13952 | 1.8273 | 0.24999
13953 | 1.8273 | 0.25001
13954 | 1.8273 | 0.25002
13955 | 1.8273 | 0.25004
13956 | 1.8273 | 0.25006
13957 | 1.8272 | 0.25007
13958 | 1.8272 | 0.25009
13959 | 1.8272 | 0.2501
13960 | 1.8272 | 0.25012
13961 | 1.8272 | 0.25014
13962 | 1.8271 | 0.25015
13963 | 1.8271 | 0.25017
13964 | 1.8271 | 0.25018
13965 | 1.8271 | 0.2502
13966 | 1.8271 | 0.25022
13967 | 1.8271 | 0.25023
13968 | 1.827 | 0.25025
13969 | 1.827 | 0.25026
13970 | 1.827 | 0.25028
13971 | 1.827 | 0.25029
13972 | 1.827 | 0.25031
13973 | 1.8269 | 0.25033
13974 | 1.8269 | 0.25034
13975 | 1.8269 | 0.25036
13976 | 1.8269 | 0.25037
13977 | 1.8269 | 0.25039
13978 | 1.8269 | 0.25041
13979 | 1.8268 | 0.25042
13980 | 1.8268 | 0.25044
13981 | 1.8268 | 0.25045
13982 | 1.8268 | 0.25047
13983 | 1.8268 | 0.25049
13984 | 1.8267 | 0.2505
13985 | 1.8267 | 0.25052
13986 | 1.8267 | 0.25053
13987 | 1.8267 | 0.25055
13988 | 1.8267 | 0.25056
13989 | 1.8266 | 0.25058
13990 | 1.8266 | 0.2506
13991 | 1.8266 | 0.25061
13992 | 1.8266 | 0.25063
13993 | 1.8266 | 0.25064
13994 | 1.8266 | 0.25066
13995 | 1.8265 | 0.25068
13996 | 1.8265 | 0.25069
13997 | 1.8265 | 0.25071
13998 | 1.8265 | 0.25072
13999 | 1.8265 | 0.25074
14000 | 1.8264 | 0.25076
14001 | 1.8264 | 0.25077
14002 | 1.8264 | 0.25079
14003 | 1.8264 | 0.2508
14004 | 1.8264 | 0.25082
14005 | 1.8264 | 0.25083
14006 | 1.8263 | 0.25085
14007 | 1.8263 | 0.25087
14008 | 1.8263 | 0.25088
14009 | 1.8263 | 0.2509
14010 | 1.8263 | 0.25091
14011 | 1.8262 | 0.25093
14012 | 1.8262 | 0.25095
14013 | 1.8262 | 0.25096
14014 | 1.8262 | 0.25098
14015 | 1.8262 | 0.25099
14016 | 1.8261 | 0.25101
14017 | 1.8261 | 0.25103
14018 | 1.8261 | 0.25104
14019 | 1.8261 | 0.25106
14020 | 1.8261 | 0.25107
14021 | 1.8261 | 0.25109
14022 | 1.826 | 0.2511
14023 | 1.826 | 0.25112
14024 | 1.826 | 0.25114
14025 | 1.826 | 0.25115
14026 | 1.826 | 0.25117
14027 | 1.8259 | 0.25118
14028 | 1.8259 | 0.2512
14029 | 1.8259 | 0.25122
14030 | 1.8259 | 0.25123
14031 | 1.8259 | 0.25125
14032 | 1.8258 | 0.25126
14033 | 1.8258 | 0.25128
14034 | 1.8258 | 0.25129
14035 | 1.8258 | 0.25131
14036 | 1.8258 | 0.25133
14037 | 1.8258 | 0.25134
14038 | 1.8257 | 0.25136
14039 | 1.8257 | 0.25137
14040 | 1.8257 | 0.25139
14041 | 1.8257 | 0.25141
14042 | 1.8257 | 0.25142
14043 | 1.8256 | 0.25144
14044 | 1.8256 | 0.25145
14045 | 1.8256 | 0.25147
14046 | 1.8256 | 0.25149
14047 | 1.8256 | 0.2515
14048 | 1.8256 | 0.25152
14049 | 1.8255 | 0.25153
14050 | 1.8255 | 0.25155
14051 | 1.8255 | 0.25156
14052 | 1.8255 | 0.25158
14053 | 1.8255 | 0.2516
14054 | 1.8254 | 0.25161
14055 | 1.8254 | 0.25163
14056 | 1.8254 | 0.25164
14057 | 1.8254 | 0.25166
14058 | 1.8254 | 0.25168
14059 | 1.8253 | 0.25169
14060 | 1.8253 | 0.25171
14061 | 1.8253 | 0.25172
14062 | 1.8253 | 0.25174
14063 | 1.8253 | 0.25175
14064 | 1.8253 | 0.25177
14065 | 1.8252 | 0.25179
14066 | 1.8252 | 0.2518
14067 | 1.8252 | 0.25182
14068 | 1.8252 | 0.25183
14069 | 1.8252 | 0.25185
14070 | 1.8251 | 0.25187
14071 | 1.8251 | 0.25188
14072 | 1.8251 | 0.2519
14073 | 1.8251 | 0.25191
14074 | 1.8251 | 0.25193
14075 | 1.8251 | 0.25195
14076 | 1.825 | 0.25196
14077 | 1.825 | 0.25198
14078 | 1.825 | 0.25199
14079 | 1.825 | 0.25201
14080 | 1.825 | 0.25202
14081 | 1.8249 | 0.25204
14082 | 1.8249 | 0.25206
14083 | 1.8249 | 0.25207
14084 | 1.8249 | 0.25209
14085 | 1.8249 | 0.2521
14086 | 1.8248 | 0.25212
14087 | 1.8248 | 0.25214
14088 | 1.8248 | 0.25215
14089 | 1.8248 | 0.25217
14090 | 1.8248 | 0.25218
14091 | 1.8248 | 0.2522
14092 | 1.8247 | 0.25221
14093 | 1.8247 | 0.25223
14094 | 1.8247 | 0.25225
14095 | 1.8247 | 0.25226
14096 | 1.8247 | 0.25228
14097 | 1.8246 | 0.25229
14098 | 1.8246 | 0.25231
14099 | 1.8246 | 0.25233
14100 | 1.8246 | 0.25234
14101 | 1.8246 | 0.25236
14102 | 1.8246 | 0.25237
14103 | 1.8245 | 0.25239
14104 | 1.8245 | 0.2524
14105 | 1.8245 | 0.25242
14106 | 1.8245 | 0.25244
14107 | 1.8245 | 0.25245
14108 | 1.8244 | 0.25247
14109 | 1.8244 | 0.25248
14110 | 1.8244 | 0.2525
14111 | 1.8244 | 0.25252
14112 | 1.8244 | 0.25253
14113 | 1.8243 | 0.25255
14114 | 1.8243 | 0.25256
14115 | 1.8243 | 0.25258
14116 | 1.8243 | 0.25259
14117 | 1.8243 | 0.25261
14118 | 1.8243 | 0.25263
14119 | 1.8242 | 0.25264
14120 | 1.8242 | 0.25266
14121 | 1.8242 | 0.25267
14122 | 1.8242 | 0.25269
14123 | 1.8242 | 0.25271
14124 | 1.8241 | 0.25272
14125 | 1.8241 | 0.25274
14126 | 1.8241 | 0.25275
14127 | 1.8241 | 0.25277
14128 | 1.8241 | 0.25278
14129 | 1.8241 | 0.2528
14130 | 1.824 | 0.25282
14131 | 1.824 | 0.25283
14132 | 1.824 | 0.25285
14133 | 1.824 | 0.25286
14134 | 1.824 | 0.25288
14135 | 1.8239 | 0.2529
14136 | 1.8239 | 0.25291
14137 | 1.8239 | 0.25293
14138 | 1.8239 | 0.25294
14139 | 1.8239 | 0.25296
14140 | 1.8238 | 0.25298
14141 | 1.8238 | 0.25299
14142 | 1.8238 | 0.25301
14143 | 1.8238 | 0.25302
14144 | 1.8238 | 0.25304
14145 | 1.8238 | 0.25305
14146 | 1.8237 | 0.25307
14147 | 1.8237 | 0.25309
14148 | 1.8237 | 0.2531
14149 | 1.8237 | 0.25312
14150 | 1.8237 | 0.25313
14151 | 1.8236 | 0.25315
14152 | 1.8236 | 0.25317
14153 | 1.8236 | 0.25318
14154 | 1.8236 | 0.2532
14155 | 1.8236 | 0.25321
14156 | 1.8236 | 0.25323
14157 | 1.8235 | 0.25324
14158 | 1.8235 | 0.25326
14159 | 1.8235 | 0.25328
14160 | 1.8235 | 0.25329
14161 | 1.8235 | 0.25331
14162 | 1.8234 | 0.25332
14163 | 1.8234 | 0.25334
14164 | 1.8234 | 0.25336
14165 | 1.8234 | 0.25337
14166 | 1.8234 | 0.25339
14167 | 1.8233 | 0.2534
14168 | 1.8233 | 0.25342
14169 | 1.8233 | 0.25343
14170 | 1.8233 | 0.25345
14171 | 1.8233 | 0.25347
14172 | 1.8233 | 0.25348
14173 | 1.8232 | 0.2535
14174 | 1.8232 | 0.25351
14175 | 1.8232 | 0.25353
14176 | 1.8232 | 0.25355
14177 | 1.8232 | 0.25356
14178 | 1.8231 | 0.25358
14179 | 1.8231 | 0.25359
14180 | 1.8231 | 0.25361
14181 | 1.8231 | 0.25362
14182 | 1.8231 | 0.25364
14183 | 1.8231 | 0.25366
14184 | 1.823 | 0.25367
14185 | 1.823 | 0.25369
14186 | 1.823 | 0.2537
14187 | 1.823 | 0.25372
14188 | 1.823 | 0.25374
14189 | 1.8229 | 0.25375
14190 | 1.8229 | 0.25377
14191 | 1.8229 | 0.25378
14192 | 1.8229 | 0.2538
14193 | 1.8229 | 0.25381
14194 | 1.8229 | 0.25383
14195 | 1.8228 | 0.25385
14196 | 1.8228 | 0.25386
14197 | 1.8228 | 0.25388
14198 | 1.8228 | 0.25389
14199 | 1.8228 | 0.25391
14200 | 1.8227 | 0.25392
14201 | 1.8227 | 0.25394
14202 | 1.8227 | 0.25396
14203 | 1.8227 | 0.25397
14204 | 1.8227 | 0.25399
14205 | 1.8226 | 0.254
14206 | 1.8226 | 0.25402
14207 | 1.8226 | 0.25404
14208 | 1.8226 | 0.25405
14209 | 1.8226 | 0.25407
14210 | 1.8226 | 0.25408
14211 | 1.8225 | 0.2541
14212 | 1.8225 | 0.25411
14213 | 1.8225 | 0.25413
14214 | 1.8225 | 0.25415
14215 | 1.8225 | 0.25416
14216 | 1.8224 | 0.25418
14217 | 1.8224 | 0.25419
14218 | 1.8224 | 0.25421
14219 | 1.8224 | 0.25423
14220 | 1.8224 | 0.25424
14221 | 1.8224 | 0.25426
14222 | 1.8223 | 0.25427
14223 | 1.8223 | 0.25429
14224 | 1.8223 | 0.2543
14225 | 1.8223 | 0.25432
14226 | 1.8223 | 0.25434
14227 | 1.8222 | 0.25435
14228 | 1.8222 | 0.25437
14229 | 1.8222 | 0.25438
14230 | 1.8222 | 0.2544
14231 | 1.8222 | 0.25442
14232 | 1.8222 | 0.25443
14233 | 1.8221 | 0.25445
14234 | 1.8221 | 0.25446
14235 | 1.8221 | 0.25448
14236 | 1.8221 | 0.25449
14237 | 1.8221 | 0.25451
14238 | 1.822 | 0.25453
14239 | 1.822 | 0.25454
14240 | 1.822 | 0.25456
14241 | 1.822 | 0.25457
14242 | 1.822 | 0.25459
14243 | 1.8219 | 0.25461
14244 | 1.8219 | 0.25462
14245 | 1.8219 | 0.25464
14246 | 1.8219 | 0.25465
14247 | 1.8219 | 0.25467
14248 | 1.8219 | 0.25468
14249 | 1.8218 | 0.2547
14250 | 1.8218 | 0.25472
14251 | 1.8218 | 0.25473
14252 | 1.8218 | 0.25475
14253 | 1.8218 | 0.25476
14254 | 1.8217 | 0.25478
14255 | 1.8217 | 0.25479
14256 | 1.8217 | 0.25481
14257 | 1.8217 | 0.25483
14258 | 1.8217 | 0.25484
14259 | 1.8217 | 0.25486
14260 | 1.8216 | 0.25487
14261 | 1.8216 | 0.25489
14262 | 1.8216 | 0.25491
14263 | 1.8216 | 0.25492
14264 | 1.8216 | 0.25494
14265 | 1.8215 | 0.25495
14266 | 1.8215 | 0.25497
14267 | 1.8215 | 0.25498
14268 | 1.8215 | 0.255
14269 | 1.8215 | 0.25502
14270 | 1.8215 | 0.25503
14271 | 1.8214 | 0.25505
14272 | 1.8214 | 0.25506
14273 | 1.8214 | 0.25508
14274 | 1.8214 | 0.2551
14275 | 1.8214 | 0.25511
14276 | 1.8213 | 0.25513
14277 | 1.8213 | 0.25514
14278 | 1.8213 | 0.25516
14279 | 1.8213 | 0.25517
14280 | 1.8213 | 0.25519
14281 | 1.8212 | 0.25521
14282 | 1.8212 | 0.25522
14283 | 1.8212 | 0.25524
14284 | 1.8212 | 0.25525
14285 | 1.8212 | 0.25527
14286 | 1.8212 | 0.25528
14287 | 1.8211 | 0.2553
14288 | 1.8211 | 0.25532
14289 | 1.8211 | 0.25533
14290 | 1.8211 | 0.25535
14291 | 1.8211 | 0.25536
14292 | 1.821 | 0.25538
14293 | 1.821 | 0.2554
14294 | 1.821 | 0.25541
14295 | 1.821 | 0.25543
14296 | 1.821 | 0.25544
14297 | 1.821 | 0.25546
14298 | 1.8209 | 0.25547
14299 | 1.8209 | 0.25549
14300 | 1.8209 | 0.25551
14301 | 1.8209 | 0.25552
14302 | 1.8209 | 0.25554
14303 | 1.8208 | 0.25555
14304 | 1.8208 | 0.25557
14305 | 1.8208 | 0.25559
14306 | 1.8208 | 0.2556
14307 | 1.8208 | 0.25562
14308 | 1.8208 | 0.25563
14309 | 1.8207 | 0.25565
14310 | 1.8207 | 0.25566
14311 | 1.8207 | 0.25568
14312 | 1.8207 | 0.2557
14313 | 1.8207 | 0.25571
14314 | 1.8206 | 0.25573
14315 | 1.8206 | 0.25574
14316 | 1.8206 | 0.25576
14317 | 1.8206 | 0.25577
14318 | 1.8206 | 0.25579
14319 | 1.8206 | 0.25581
14320 | 1.8205 | 0.25582
14321 | 1.8205 | 0.25584
14322 | 1.8205 | 0.25585
14323 | 1.8205 | 0.25587
14324 | 1.8205 | 0.25589
14325 | 1.8204 | 0.2559
14326 | 1.8204 | 0.25592
14327 | 1.8204 | 0.25593
14328 | 1.8204 | 0.25595
14329 | 1.8204 | 0.25596
14330 | 1.8203 | 0.25598
14331 | 1.8203 | 0.256
14332 | 1.8203 | 0.25601
14333 | 1.8203 | 0.25603
14334 | 1.8203 | 0.25604
14335 | 1.8203 | 0.25606
14336 | 1.8202 | 0.25607
14337 | 1.8202 | 0.25609
14338 | 1.8202 | 0.25611
14339 | 1.8202 | 0.25612
14340 | 1.8202 | 0.25614
14341 | 1.8201 | 0.25615
14342 | 1.8201 | 0.25617
14343 | 1.8201 | 0.25619
14344 | 1.8201 | 0.2562
14345 | 1.8201 | 0.25622
14346 | 1.8201 | 0.25623
14347 | 1.82 | 0.25625
14348 | 1.82 | 0.25626
14349 | 1.82 | 0.25628
14350 | 1.82 | 0.2563
14351 | 1.82 | 0.25631
14352 | 1.8199 | 0.25633
14353 | 1.8199 | 0.25634
14354 | 1.8199 | 0.25636
14355 | 1.8199 | 0.25637
14356 | 1.8199 | 0.25639
14357 | 1.8199 | 0.25641
14358 | 1.8198 | 0.25642
14359 | 1.8198 | 0.25644
14360 | 1.8198 | 0.25645
14361 | 1.8198 | 0.25647
14362 | 1.8198 | 0.25649
14363 | 1.8197 | 0.2565
14364 | 1.8197 | 0.25652
14365 | 1.8197 | 0.25653
14366 | 1.8197 | 0.25655
14367 | 1.8197 | 0.25656
14368 | 1.8197 | 0.25658
14369 | 1.8196 | 0.2566
14370 | 1.8196 | 0.25661
14371 | 1.8196 | 0.25663
14372 | 1.8196 | 0.25664
14373 | 1.8196 | 0.25666
14374 | 1.8195 | 0.25667
14375 | 1.8195 | 0.25669
14376 | 1.8195 | 0.25671
14377 | 1.8195 | 0.25672
14378 | 1.8195 | 0.25674
14379 | 1.8195 | 0.25675
14380 | 1.8194 | 0.25677
14381 | 1.8194 | 0.25679
14382 | 1.8194 | 0.2568
14383 | 1.8194 | 0.25682
14384 | 1.8194 | 0.25683
14385 | 1.8193 | 0.25685
14386 | 1.8193 | 0.25686
14387 | 1.8193 | 0.25688
14388 | 1.8193 | 0.2569
14389 | 1.8193 | 0.25691
14390 | 1.8193 | 0.25693
14391 | 1.8192 | 0.25694
14392 | 1.8192 | 0.25696
14393 | 1.8192 | 0.25697
14394 | 1.8192 | 0.25699
14395 | 1.8192 | 0.25701
14396 | 1.8191 | 0.25702
14397 | 1.8191 | 0.25704
14398 | 1.8191 | 0.25705
14399 | 1.8191 | 0.25707
14400 | 1.8191 | 0.25709
14401 | 1.819 | 0.2571
14402 | 1.819 | 0.25712
14403 | 1.819 | 0.25713
14404 | 1.819 | 0.25715
14405 | 1.819 | 0.25716
14406 | 1.819 | 0.25718
14407 | 1.8189 | 0.2572
14408 | 1.8189 | 0.25721
14409 | 1.8189 | 0.25723
14410 | 1.8189 | 0.25724
14411 | 1.8189 | 0.25726
14412 | 1.8188 | 0.25727
14413 | 1.8188 | 0.25729
14414 | 1.8188 | 0.25731
14415 | 1.8188 | 0.25732
14416 | 1.8188 | 0.25734
14417 | 1.8188 | 0.25735
14418 | 1.8187 | 0.25737
14419 | 1.8187 | 0.25738
14420 | 1.8187 | 0.2574
14421 | 1.8187 | 0.25742
14422 | 1.8187 | 0.25743
14423 | 1.8186 | 0.25745
14424 | 1.8186 | 0.25746
14425 | 1.8186 | 0.25748
14426 | 1.8186 | 0.2575
14427 | 1.8186 | 0.25751
14428 | 1.8186 | 0.25753
14429 | 1.8185 | 0.25754
14430 | 1.8185 | 0.25756
14431 | 1.8185 | 0.25757
14432 | 1.8185 | 0.25759
14433 | 1.8185 | 0.25761
14434 | 1.8184 | 0.25762
14435 | 1.8184 | 0.25764
14436 | 1.8184 | 0.25765
14437 | 1.8184 | 0.25767
14438 | 1.8184 | 0.25768
14439 | 1.8184 | 0.2577
14440 | 1.8183 | 0.25772
14441 | 1.8183 | 0.25773
14442 | 1.8183 | 0.25775
14443 | 1.8183 | 0.25776
14444 | 1.8183 | 0.25778
14445 | 1.8182 | 0.25779
14446 | 1.8182 | 0.25781
14447 | 1.8182 | 0.25783
14448 | 1.8182 | 0.25784
14449 | 1.8182 | 0.25786
14450 | 1.8182 | 0.25787
14451 | 1.8181 | 0.25789
14452 | 1.8181 | 0.25791
14453 | 1.8181 | 0.25792
14454 | 1.8181 | 0.25794
14455 | 1.8181 | 0.25795
14456 | 1.818 | 0.25797
14457 | 1.818 | 0.25798
14458 | 1.818 | 0.258
14459 | 1.818 | 0.25802
14460 | 1.818 | 0.25803
14461 | 1.818 | 0.25805
14462 | 1.8179 | 0.25806
14463 | 1.8179 | 0.25808
14464 | 1.8179 | 0.25809
14465 | 1.8179 | 0.25811
14466 | 1.8179 | 0.25813
14467 | 1.8178 | 0.25814
14468 | 1.8178 | 0.25816
14469 | 1.8178 | 0.25817
14470 | 1.8178 | 0.25819
14471 | 1.8178 | 0.2582
14472 | 1.8178 | 0.25822
14473 | 1.8177 | 0.25824
14474 | 1.8177 | 0.25825
14475 | 1.8177 | 0.25827
14476 | 1.8177 | 0.25828
14477 | 1.8177 | 0.2583
14478 | 1.8176 | 0.25832
14479 | 1.8176 | 0.25833
14480 | 1.8176 | 0.25835
14481 | 1.8176 | 0.25836
14482 | 1.8176 | 0.25838
14483 | 1.8176 | 0.25839
14484 | 1.8175 | 0.25841
14485 | 1.8175 | 0.25843
14486 | 1.8175 | 0.25844
14487 | 1.8175 | 0.25846
14488 | 1.8175 | 0.25847
14489 | 1.8174 | 0.25849
14490 | 1.8174 | 0.2585
14491 | 1.8174 | 0.25852
14492 | 1.8174 | 0.25854
14493 | 1.8174 | 0.25855
14494 | 1.8174 | 0.25857
14495 | 1.8173 | 0.25858
14496 | 1.8173 | 0.2586
14497 | 1.8173 | 0.25861
14498 | 1.8173 | 0.25863
14499 | 1.8173 | 0.25865
14500 | 1.8172 | 0.25866
14501 | 1.8172 | 0.25868
14502 | 1.8172 | 0.25869
14503 | 1.8172 | 0.25871
14504 | 1.8172 | 0.25872
14505 | 1.8172 | 0.25874
14506 | 1.8171 | 0.25876
14507 | 1.8171 | 0.25877
14508 | 1.8171 | 0.25879
14509 | 1.8171 | 0.2588
14510 | 1.8171 | 0.25882
14511 | 1.817 | 0.25884
14512 | 1.817 | 0.25885
14513 | 1.817 | 0.25887
14514 | 1.817 | 0.25888
14515 | 1.817 | 0.2589
14516 | 1.817 | 0.25891
14517 | 1.8169 | 0.25893
14518 | 1.8169 | 0.25895
14519 | 1.8169 | 0.25896
14520 | 1.8169 | 0.25898
14521 | 1.8169 | 0.25899
14522 | 1.8168 | 0.25901
14523 | 1.8168 | 0.25902
14524 | 1.8168 | 0.25904
14525 | 1.8168 | 0.25906
14526 | 1.8168 | 0.25907
14527 | 1.8168 | 0.25909
14528 | 1.8167 | 0.2591
14529 | 1.8167 | 0.25912
14530 | 1.8167 | 0.25913
14531 | 1.8167 | 0.25915
14532 | 1.8167 | 0.25917
14533 | 1.8166 | 0.25918
14534 | 1.8166 | 0.2592
14535 | 1.8166 | 0.25921
14536 | 1.8166 | 0.25923
14537 | 1.8166 | 0.25924
14538 | 1.8166 | 0.25926
14539 | 1.8165 | 0.25928
14540 | 1.8165 | 0.25929
14541 | 1.8165 | 0.25931
14542 | 1.8165 | 0.25932
14543 | 1.8165 | 0.25934
14544 | 1.8164 | 0.25935
14545 | 1.8164 | 0.25937
14546 | 1.8164 | 0.25939
14547 | 1.8164 | 0.2594
14548 | 1.8164 | 0.25942
14549 | 1.8164 | 0.25943
14550 | 1.8163 | 0.25945
14551 | 1.8163 | 0.25947
14552 | 1.8163 | 0.25948
14553 | 1.8163 | 0.2595
14554 | 1.8163 | 0.25951
14555 | 1.8162 | 0.25953
14556 | 1.8162 | 0.25954
14557 | 1.8162 | 0.25956
14558 | 1.8162 | 0.25958
14559 | 1.8162 | 0.25959
14560 | 1.8162 | 0.25961
14561 | 1.8161 | 0.25962
14562 | 1.8161 | 0.25964
14563 | 1.8161 | 0.25965
14564 | 1.8161 | 0.25967
14565 | 1.8161 | 0.25969
14566 | 1.816 | 0.2597
14567 | 1.816 | 0.25972
14568 | 1.816 | 0.25973
14569 | 1.816 | 0.25975
14570 | 1.816 | 0.25976
14571 | 1.816 | 0.25978
14572 | 1.8159 | 0.2598
14573 | 1.8159 | 0.25981
14574 | 1.8159 | 0.25983
14575 | 1.8159 | 0.25984
14576 | 1.8159 | 0.25986
14577 | 1.8158 | 0.25987
14578 | 1.8158 | 0.25989
14579 | 1.8158 | 0.25991
14580 | 1.8158 | 0.25992
14581 | 1.8158 | 0.25994
14582 | 1.8158 | 0.25995
14583 | 1.8157 | 0.25997
14584 | 1.8157 | 0.25998
14585 | 1.8157 | 0.26
14586 | 1.8157 | 0.26002
14587 | 1.8157 | 0.26003
14588 | 1.8156 | 0.26005
14589 | 1.8156 | 0.26006
14590 | 1.8156 | 0.26008
14591 | 1.8156 | 0.26009
14592 | 1.8156 | 0.26011
14593 | 1.8156 | 0.26013
14594 | 1.8155 | 0.26014
14595 | 1.8155 | 0.26016
14596 | 1.8155 | 0.26017
14597 | 1.8155 | 0.26019
14598 | 1.8155 | 0.2602
14599 | 1.8154 | 0.26022
14600 | 1.8154 | 0.26024
14601 | 1.8154 | 0.26025
14602 | 1.8154 | 0.26027
14603 | 1.8154 | 0.26028
14604 | 1.8154 | 0.2603
14605 | 1.8153 | 0.26031
14606 | 1.8153 | 0.26033
14607 | 1.8153 | 0.26035
14608 | 1.8153 | 0.26036
14609 | 1.8153 | 0.26038
14610 | 1.8152 | 0.26039
14611 | 1.8152 | 0.26041
14612 | 1.8152 | 0.26042
14613 | 1.8152 | 0.26044
14614 | 1.8152 | 0.26046
14615 | 1.8152 | 0.26047
14616 | 1.8151 | 0.26049
14617 | 1.8151 | 0.2605
14618 | 1.8151 | 0.26052
14619 | 1.8151 | 0.26053
14620 | 1.8151 | 0.26055
14621 | 1.815 | 0.26057
14622 | 1.815 | 0.26058
14623 | 1.815 | 0.2606
14624 | 1.815 | 0.26061
14625 | 1.815 | 0.26063
14626 | 1.815 | 0.26065
14627 | 1.8149 | 0.26066
14628 | 1.8149 | 0.26068
14629 | 1.8149 | 0.26069
14630 | 1.8149 | 0.26071
14631 | 1.8149 | 0.26072
14632 | 1.8148 | 0.26074
14633 | 1.8148 | 0.26076
14634 | 1.8148 | 0.26077
14635 | 1.8148 | 0.26079
14636 | 1.8148 | 0.2608
14637 | 1.8148 | 0.26082
14638 | 1.8147 | 0.26083
14639 | 1.8147 | 0.26085
14640 | 1.8147 | 0.26087
14641 | 1.8147 | 0.26088
14642 | 1.8147 | 0.2609
14643 | 1.8146 | 0.26091
14644 | 1.8146 | 0.26093
14645 | 1.8146 | 0.26094
14646 | 1.8146 | 0.26096
14647 | 1.8146 | 0.26098
14648 | 1.8146 | 0.26099
14649 | 1.8145 | 0.26101
14650 | 1.8145 | 0.26102
14651 | 1.8145 | 0.26104
14652 | 1.8145 | 0.26105
14653 | 1.8145 | 0.26107
14654 | 1.8144 | 0.26109
14655 | 1.8144 | 0.2611
14656 | 1.8144 | 0.26112
14657 | 1.8144 | 0.26113
14658 | 1.8144 | 0.26115
14659 | 1.8144 | 0.26116
14660 | 1.8143 | 0.26118
14661 | 1.8143 | 0.2612
14662 | 1.8143 | 0.26121
14663 | 1.8143 | 0.26123
14664 | 1.8143 | 0.26124
14665 | 1.8142 | 0.26126
14666 | 1.8142 | 0.26127
14667 | 1.8142 | 0.26129
14668 | 1.8142 | 0.26131
14669 | 1.8142 | 0.26132
14670 | 1.8142 | 0.26134
14671 | 1.8141 | 0.26135
14672 | 1.8141 | 0.26137
14673 | 1.8141 | 0.26138
14674 | 1.8141 | 0.2614
14675 | 1.8141 | 0.26142
14676 | 1.814 | 0.26143
14677 | 1.814 | 0.26145
14678 | 1.814 | 0.26146
14679 | 1.814 | 0.26148
14680 | 1.814 | 0.26149
14681 | 1.814 | 0.26151
14682 | 1.8139 | 0.26153
14683 | 1.8139 | 0.26154
14684 | 1.8139 | 0.26156
14685 | 1.8139 | 0.26157
14686 | 1.8139 | 0.26159
14687 | 1.8138 | 0.2616
14688 | 1.8138 | 0.26162
14689 | 1.8138 | 0.26164
14690 | 1.8138 | 0.26165
14691 | 1.8138 | 0.26167
14692 | 1.8138 | 0.26168
14693 | 1.8137 | 0.2617
14694 | 1.8137 | 0.26171
14695 | 1.8137 | 0.26173
14696 | 1.8137 | 0.26175
14697 | 1.8137 | 0.26176
14698 | 1.8136 | 0.26178
14699 | 1.8136 | 0.26179
14700 | 1.8136 | 0.26181
14701 | 1.8136 | 0.26182
14702 | 1.8136 | 0.26184
14703 | 1.8136 | 0.26186
14704 | 1.8135 | 0.26187
14705 | 1.8135 | 0.26189
14706 | 1.8135 | 0.2619
14707 | 1.8135 | 0.26192
14708 | 1.8135 | 0.26193
14709 | 1.8135 | 0.26195
14710 | 1.8134 | 0.26197
14711 | 1.8134 | 0.26198
14712 | 1.8134 | 0.262
14713 | 1.8134 | 0.26201
14714 | 1.8134 | 0.26203
14715 | 1.8133 | 0.26204
14716 | 1.8133 | 0.26206
14717 | 1.8133 | 0.26208
14718 | 1.8133 | 0.26209
14719 | 1.8133 | 0.26211
14720 | 1.8133 | 0.26212
14721 | 1.8132 | 0.26214
14722 | 1.8132 | 0.26215
14723 | 1.8132 | 0.26217
14724 | 1.8132 | 0.26219
14725 | 1.8132 | 0.2622
14726 | 1.8131 | 0.26222
14727 | 1.8131 | 0.26223
14728 | 1.8131 | 0.26225
14729 | 1.8131 | 0.26226
14730 | 1.8131 | 0.26228
14731 | 1.8131 | 0.26229
14732 | 1.813 | 0.26231
14733 | 1.813 | 0.26233
14734 | 1.813 | 0.26234
14735 | 1.813 | 0.26236
14736 | 1.813 | 0.26237
14737 | 1.8129 | 0.26239
14738 | 1.8129 | 0.2624
14739 | 1.8129 | 0.26242
14740 | 1.8129 | 0.26244
14741 | 1.8129 | 0.26245
14742 | 1.8129 | 0.26247
14743 | 1.8128 | 0.26248
14744 | 1.8128 | 0.2625
14745 | 1.8128 | 0.26251
14746 | 1.8128 | 0.26253
14747 | 1.8128 | 0.26255
14748 | 1.8127 | 0.26256
14749 | 1.8127 | 0.26258
14750 | 1.8127 | 0.26259
14751 | 1.8127 | 0.26261
14752 | 1.8127 | 0.26262
14753 | 1.8127 | 0.26264
14754 | 1.8126 | 0.26266
14755 | 1.8126 | 0.26267
14756 | 1.8126 | 0.26269
14757 | 1.8126 | 0.2627
14758 | 1.8126 | 0.26272
14759 | 1.8125 | 0.26273
14760 | 1.8125 | 0.26275
14761 | 1.8125 | 0.26277
14762 | 1.8125 | 0.26278
14763 | 1.8125 | 0.2628
14764 | 1.8125 | 0.26281
14765 | 1.8124 | 0.26283
14766 | 1.8124 | 0.26284
14767 | 1.8124 | 0.26286
14768 | 1.8124 | 0.26288
14769 | 1.8124 | 0.26289
14770 | 1.8124 | 0.26291
14771 | 1.8123 | 0.26292
14772 | 1.8123 | 0.26294
14773 | 1.8123 | 0.26295
14774 | 1.8123 | 0.26297
14775 | 1.8123 | 0.26299
14776 | 1.8122 | 0.263
14777 | 1.8122 | 0.26302
14778 | 1.8122 | 0.26303
14779 | 1.8122 | 0.26305
14780 | 1.8122 | 0.26306
14781 | 1.8122 | 0.26308
14782 | 1.8121 | 0.2631
14783 | 1.8121 | 0.26311
14784 | 1.8121 | 0.26313
14785 | 1.8121 | 0.26314
14786 | 1.8121 | 0.26316
14787 | 1.812 | 0.26317
14788 | 1.812 | 0.26319
14789 | 1.812 | 0.26321
14790 | 1.812 | 0.26322
14791 | 1.812 | 0.26324
14792 | 1.812 | 0.26325
14793 | 1.8119 | 0.26327
14794 | 1.8119 | 0.26328
14795 | 1.8119 | 0.2633
14796 | 1.8119 | 0.26332
14797 | 1.8119 | 0.26333
14798 | 1.8118 | 0.26335
14799 | 1.8118 | 0.26336
14800 | 1.8118 | 0.26338
14801 | 1.8118 | 0.26339
14802 | 1.8118 | 0.26341
14803 | 1.8118 | 0.26342
14804 | 1.8117 | 0.26344
14805 | 1.8117 | 0.26346
14806 | 1.8117 | 0.26347
14807 | 1.8117 | 0.26349
14808 | 1.8117 | 0.2635
14809 | 1.8116 | 0.26352
14810 | 1.8116 | 0.26353
14811 | 1.8116 | 0.26355
14812 | 1.8116 | 0.26357
14813 | 1.8116 | 0.26358
14814 | 1.8116 | 0.2636
14815 | 1.8115 | 0.26361
14816 | 1.8115 | 0.26363
14817 | 1.8115 | 0.26364
14818 | 1.8115 | 0.26366
14819 | 1.8115 | 0.26368
14820 | 1.8115 | 0.26369
14821 | 1.8114 | 0.26371
14822 | 1.8114 | 0.26372
14823 | 1.8114 | 0.26374
14824 | 1.8114 | 0.26375
14825 | 1.8114 | 0.26377
14826 | 1.8113 | 0.26379
14827 | 1.8113 | 0.2638
14828 | 1.8113 | 0.26382
14829 | 1.8113 | 0.26383
14830 | 1.8113 | 0.26385
14831 | 1.8113 | 0.26386
14832 | 1.8112 | 0.26388
14833 | 1.8112 | 0.2639
14834 | 1.8112 | 0.26391
14835 | 1.8112 | 0.26393
14836 | 1.8112 | 0.26394
14837 | 1.8111 | 0.26396
14838 | 1.8111 | 0.26397
14839 | 1.8111 | 0.26399
14840 | 1.8111 | 0.26401
14841 | 1.8111 | 0.26402
14842 | 1.8111 | 0.26404
14843 | 1.811 | 0.26405
14844 | 1.811 | 0.26407
14845 | 1.811 | 0.26408
14846 | 1.811 | 0.2641
14847 | 1.811 | 0.26411
14848 | 1.8109 | 0.26413
14849 | 1.8109 | 0.26415
14850 | 1.8109 | 0.26416
14851 | 1.8109 | 0.26418
14852 | 1.8109 | 0.26419
14853 | 1.8109 | 0.26421
14854 | 1.8108 | 0.26422
14855 | 1.8108 | 0.26424
14856 | 1.8108 | 0.26426
14857 | 1.8108 | 0.26427
14858 | 1.8108 | 0.26429
14859 | 1.8107 | 0.2643
14860 | 1.8107 | 0.26432
14861 | 1.8107 | 0.26433
14862 | 1.8107 | 0.26435
14863 | 1.8107 | 0.26437
14864 | 1.8107 | 0.26438
14865 | 1.8106 | 0.2644
14866 | 1.8106 | 0.26441
14867 | 1.8106 | 0.26443
14868 | 1.8106 | 0.26444
14869 | 1.8106 | 0.26446
14870 | 1.8106 | 0.26448
14871 | 1.8105 | 0.26449
14872 | 1.8105 | 0.26451
14873 | 1.8105 | 0.26452
14874 | 1.8105 | 0.26454
14875 | 1.8105 | 0.26455
14876 | 1.8104 | 0.26457
14877 | 1.8104 | 0.26458
14878 | 1.8104 | 0.2646
14879 | 1.8104 | 0.26462
14880 | 1.8104 | 0.26463
14881 | 1.8104 | 0.26465
14882 | 1.8103 | 0.26466
14883 | 1.8103 | 0.26468
14884 | 1.8103 | 0.26469
14885 | 1.8103 | 0.26471
14886 | 1.8103 | 0.26473
14887 | 1.8102 | 0.26474
14888 | 1.8102 | 0.26476
14889 | 1.8102 | 0.26477
14890 | 1.8102 | 0.26479
14891 | 1.8102 | 0.2648
14892 | 1.8102 | 0.26482
14893 | 1.8101 | 0.26484
14894 | 1.8101 | 0.26485
14895 | 1.8101 | 0.26487
14896 | 1.8101 | 0.26488
14897 | 1.8101 | 0.2649
14898 | 1.81 | 0.26491
14899 | 1.81 | 0.26493
14900 | 1.81 | 0.26495
14901 | 1.81 | 0.26496
14902 | 1.81 | 0.26498
14903 | 1.81 | 0.26499
14904 | 1.8099 | 0.26501
14905 | 1.8099 | 0.26502
14906 | 1.8099 | 0.26504
14907 | 1.8099 | 0.26505
14908 | 1.8099 | 0.26507
14909 | 1.8099 | 0.26509
14910 | 1.8098 | 0.2651
14911 | 1.8098 | 0.26512
14912 | 1.8098 | 0.26513
14913 | 1.8098 | 0.26515
14914 | 1.8098 | 0.26516
14915 | 1.8097 | 0.26518
14916 | 1.8097 | 0.2652
14917 | 1.8097 | 0.26521
14918 | 1.8097 | 0.26523
14919 | 1.8097 | 0.26524
14920 | 1.8097 | 0.26526
14921 | 1.8096 | 0.26527
14922 | 1.8096 | 0.26529
14923 | 1.8096 | 0.26531
14924 | 1.8096 | 0.26532
14925 | 1.8096 | 0.26534
14926 | 1.8095 | 0.26535
14927 | 1.8095 | 0.26537
14928 | 1.8095 | 0.26538
14929 | 1.8095 | 0.2654
14930 | 1.8095 | 0.26541
14931 | 1.8095 | 0.26543
14932 | 1.8094 | 0.26545
14933 | 1.8094 | 0.26546
14934 | 1.8094 | 0.26548
14935 | 1.8094 | 0.26549
14936 | 1.8094 | 0.26551
14937 | 1.8094 | 0.26552
14938 | 1.8093 | 0.26554
14939 | 1.8093 | 0.26556
14940 | 1.8093 | 0.26557
14941 | 1.8093 | 0.26559
14942 | 1.8093 | 0.2656
14943 | 1.8092 | 0.26562
14944 | 1.8092 | 0.26563
14945 | 1.8092 | 0.26565
14946 | 1.8092 | 0.26567
14947 | 1.8092 | 0.26568
14948 | 1.8092 | 0.2657
14949 | 1.8091 | 0.26571
14950 | 1.8091 | 0.26573
14951 | 1.8091 | 0.26574
14952 | 1.8091 | 0.26576
14953 | 1.8091 | 0.26578
14954 | 1.809 | 0.26579
14955 | 1.809 | 0.26581
14956 | 1.809 | 0.26582
14957 | 1.809 | 0.26584
14958 | 1.809 | 0.26585
14959 | 1.809 | 0.26587
14960 | 1.8089 | 0.26588
14961 | 1.8089 | 0.2659
14962 | 1.8089 | 0.26592
14963 | 1.8089 | 0.26593
14964 | 1.8089 | 0.26595
14965 | 1.8089 | 0.26596
14966 | 1.8088 | 0.26598
14967 | 1.8088 | 0.26599
14968 | 1.8088 | 0.26601
14969 | 1.8088 | 0.26603
14970 | 1.8088 | 0.26604
14971 | 1.8087 | 0.26606
14972 | 1.8087 | 0.26607
14973 | 1.8087 | 0.26609
14974 | 1.8087 | 0.2661
14975 | 1.8087 | 0.26612
14976 | 1.8087 | 0.26613
14977 | 1.8086 | 0.26615
14978 | 1.8086 | 0.26617
14979 | 1.8086 | 0.26618
14980 | 1.8086 | 0.2662
14981 | 1.8086 | 0.26621
14982 | 1.8085 | 0.26623
14983 | 1.8085 | 0.26624
14984 | 1.8085 | 0.26626
14985 | 1.8085 | 0.26628
14986 | 1.8085 | 0.26629
14987 | 1.8085 | 0.26631
14988 | 1.8084 | 0.26632
14989 | 1.8084 | 0.26634
14990 | 1.8084 | 0.26635
14991 | 1.8084 | 0.26637
14992 | 1.8084 | 0.26639
14993 | 1.8083 | 0.2664
14994 | 1.8083 | 0.26642
14995 | 1.8083 | 0.26643
14996 | 1.8083 | 0.26645
14997 | 1.8083 | 0.26646
14998 | 1.8083 | 0.26648
14999 | 1.8082 | 0.26649
15000 | 1.8082 | 0.26651
15001 | 1.8082 | 0.26653
15002 | 1.8082 | 0.26654
15003 | 1.8082 | 0.26656
15004 | 1.8082 | 0.26657
15005 | 1.8081 | 0.26659
15006 | 1.8081 | 0.2666
15007 | 1.8081 | 0.26662
15008 | 1.8081 | 0.26664
15009 | 1.8081 | 0.26665
15010 | 1.808 | 0.26667
15011 | 1.808 | 0.26668
15012 | 1.808 | 0.2667
15013 | 1.808 | 0.26671
15014 | 1.808 | 0.26673
15015 | 1.808 | 0.26674
15016 | 1.8079 | 0.26676
15017 | 1.8079 | 0.26678
15018 | 1.8079 | 0.26679
15019 | 1.8079 | 0.26681
15020 | 1.8079 | 0.26682
15021 | 1.8078 | 0.26684
15022 | 1.8078 | 0.26685
15023 | 1.8078 | 0.26687
15024 | 1.8078 | 0.26689
15025 | 1.8078 | 0.2669
15026 | 1.8078 | 0.26692
15027 | 1.8077 | 0.26693
15028 | 1.8077 | 0.26695
15029 | 1.8077 | 0.26696
15030 | 1.8077 | 0.26698
15031 | 1.8077 | 0.267
15032 | 1.8077 | 0.26701
15033 | 1.8076 | 0.26703
15034 | 1.8076 | 0.26704
15035 | 1.8076 | 0.26706
15036 | 1.8076 | 0.26707
15037 | 1.8076 | 0.26709
15038 | 1.8075 | 0.2671
15039 | 1.8075 | 0.26712
15040 | 1.8075 | 0.26714
15041 | 1.8075 | 0.26715
15042 | 1.8075 | 0.26717
15043 | 1.8075 | 0.26718
15044 | 1.8074 | 0.2672
15045 | 1.8074 | 0.26721
15046 | 1.8074 | 0.26723
15047 | 1.8074 | 0.26725
15048 | 1.8074 | 0.26726
15049 | 1.8074 | 0.26728
15050 | 1.8073 | 0.26729
15051 | 1.8073 | 0.26731
15052 | 1.8073 | 0.26732
15053 | 1.8073 | 0.26734
15054 | 1.8073 | 0.26735
15055 | 1.8072 | 0.26737
15056 | 1.8072 | 0.26739
15057 | 1.8072 | 0.2674
15058 | 1.8072 | 0.26742
15059 | 1.8072 | 0.26743
15060 | 1.8072 | 0.26745
15061 | 1.8071 | 0.26746
15062 | 1.8071 | 0.26748
15063 | 1.8071 | 0.2675
15064 | 1.8071 | 0.26751
15065 | 1.8071 | 0.26753
15066 | 1.807 | 0.26754
15067 | 1.807 | 0.26756
15068 | 1.807 | 0.26757
15069 | 1.807 | 0.26759
15070 | 1.807 | 0.2676
15071 | 1.807 | 0.26762
15072 | 1.8069 | 0.26764
15073 | 1.8069 | 0.26765
15074 | 1.8069 | 0.26767
15075 | 1.8069 | 0.26768
15076 | 1.8069 | 0.2677
15077 | 1.8069 | 0.26771
15078 | 1.8068 | 0.26773
15079 | 1.8068 | 0.26775
15080 | 1.8068 | 0.26776
15081 | 1.8068 | 0.26778
15082 | 1.8068 | 0.26779
15083 | 1.8067 | 0.26781
15084 | 1.8067 | 0.26782
15085 | 1.8067 | 0.26784
15086 | 1.8067 | 0.26785
15087 | 1.8067 | 0.26787
15088 | 1.8067 | 0.26789
15089 | 1.8066 | 0.2679
15090 | 1.8066 | 0.26792
15091 | 1.8066 | 0.26793
15092 | 1.8066 | 0.26795
15093 | 1.8066 | 0.26796
15094 | 1.8065 | 0.26798
15095 | 1.8065 | 0.268
15096 | 1.8065 | 0.26801
15097 | 1.8065 | 0.26803
15098 | 1.8065 | 0.26804
15099 | 1.8065 | 0.26806
15100 | 1.8064 | 0.26807
15101 | 1.8064 | 0.26809
15102 | 1.8064 | 0.2681
15103 | 1.8064 | 0.26812
15104 | 1.8064 | 0.26814
15105 | 1.8064 | 0.26815
15106 | 1.8063 | 0.26817
15107 | 1.8063 | 0.26818
15108 | 1.8063 | 0.2682
15109 | 1.8063 | 0.26821
15110 | 1.8063 | 0.26823
15111 | 1.8062 | 0.26824
15112 | 1.8062 | 0.26826
15113 | 1.8062 | 0.26828
15114 | 1.8062 | 0.26829
15115 | 1.8062 | 0.26831
15116 | 1.8062 | 0.26832
15117 | 1.8061 | 0.26834
15118 | 1.8061 | 0.26835
15119 | 1.8061 | 0.26837
15120 | 1.8061 | 0.26839
15121 | 1.8061 | 0.2684
15122 | 1.8061 | 0.26842
15123 | 1.806 | 0.26843
15124 | 1.806 | 0.26845
15125 | 1.806 | 0.26846
15126 | 1.806 | 0.26848
15127 | 1.806 | 0.26849
15128 | 1.8059 | 0.26851
15129 | 1.8059 | 0.26853
15130 | 1.8059 | 0.26854
15131 | 1.8059 | 0.26856
15132 | 1.8059 | 0.26857
15133 | 1.8059 | 0.26859
15134 | 1.8058 | 0.2686
15135 | 1.8058 | 0.26862
15136 | 1.8058 | 0.26864
15137 | 1.8058 | 0.26865
15138 | 1.8058 | 0.26867
15139 | 1.8057 | 0.26868
15140 | 1.8057 | 0.2687
15141 | 1.8057 | 0.26871
15142 | 1.8057 | 0.26873
15143 | 1.8057 | 0.26874
15144 | 1.8057 | 0.26876
15145 | 1.8056 | 0.26878
15146 | 1.8056 | 0.26879
15147 | 1.8056 | 0.26881
15148 | 1.8056 | 0.26882
15149 | 1.8056 | 0.26884
15150 | 1.8056 | 0.26885
15151 | 1.8055 | 0.26887
15152 | 1.8055 | 0.26888
15153 | 1.8055 | 0.2689
15154 | 1.8055 | 0.26892
15155 | 1.8055 | 0.26893
15156 | 1.8054 | 0.26895
15157 | 1.8054 | 0.26896
15158 | 1.8054 | 0.26898
15159 | 1.8054 | 0.26899
15160 | 1.8054 | 0.26901
15161 | 1.8054 | 0.26903
15162 | 1.8053 | 0.26904
15163 | 1.8053 | 0.26906
15164 | 1.8053 | 0.26907
15165 | 1.8053 | 0.26909
15166 | 1.8053 | 0.2691
15167 | 1.8053 | 0.26912
15168 | 1.8052 | 0.26913
15169 | 1.8052 | 0.26915
15170 | 1.8052 | 0.26917
15171 | 1.8052 | 0.26918
15172 | 1.8052 | 0.2692
15173 | 1.8051 | 0.26921
15174 | 1.8051 | 0.26923
15175 | 1.8051 | 0.26924
15176 | 1.8051 | 0.26926
15177 | 1.8051 | 0.26928
15178 | 1.8051 | 0.26929
15179 | 1.805 | 0.26931
15180 | 1.805 | 0.26932
15181 | 1.805 | 0.26934
15182 | 1.805 | 0.26935
15183 | 1.805 | 0.26937
15184 | 1.805 | 0.26938
15185 | 1.8049 | 0.2694
15186 | 1.8049 | 0.26942
15187 | 1.8049 | 0.26943
15188 | 1.8049 | 0.26945
15189 | 1.8049 | 0.26946
15190 | 1.8048 | 0.26948
15191 | 1.8048 | 0.26949
15192 | 1.8048 | 0.26951
15193 | 1.8048 | 0.26952
15194 | 1.8048 | 0.26954
15195 | 1.8048 | 0.26956
15196 | 1.8047 | 0.26957
15197 | 1.8047 | 0.26959
15198 | 1.8047 | 0.2696
15199 | 1.8047 | 0.26962
15200 | 1.8047 | 0.26963
15201 | 1.8046 | 0.26965
15202 | 1.8046 | 0.26966
15203 | 1.8046 | 0.26968
15204 | 1.8046 | 0.2697
15205 | 1.8046 | 0.26971
15206 | 1.8046 | 0.26973
15207 | 1.8045 | 0.26974
15208 | 1.8045 | 0.26976
15209 | 1.8045 | 0.26977
15210 | 1.8045 | 0.26979
15211 | 1.8045 | 0.26981
15212 | 1.8045 | 0.26982
15213 | 1.8044 | 0.26984
15214 | 1.8044 | 0.26985
15215 | 1.8044 | 0.26987
15216 | 1.8044 | 0.26988
15217 | 1.8044 | 0.2699
15218 | 1.8043 | 0.26991
15219 | 1.8043 | 0.26993
15220 | 1.8043 | 0.26995
15221 | 1.8043 | 0.26996
15222 | 1.8043 | 0.26998
15223 | 1.8043 | 0.26999
15224 | 1.8042 | 0.27001
15225 | 1.8042 | 0.27002
15226 | 1.8042 | 0.27004
15227 | 1.8042 | 0.27005
15228 | 1.8042 | 0.27007
15229 | 1.8042 | 0.27009
15230 | 1.8041 | 0.2701
15231 | 1.8041 | 0.27012
15232 | 1.8041 | 0.27013
15233 | 1.8041 | 0.27015
15234 | 1.8041 | 0.27016
15235 | 1.804 | 0.27018
15236 | 1.804 | 0.2702
15237 | 1.804 | 0.27021
15238 | 1.804 | 0.27023
15239 | 1.804 | 0.27024
15240 | 1.804 | 0.27026
15241 | 1.8039 | 0.27027
15242 | 1.8039 | 0.27029
15243 | 1.8039 | 0.2703
15244 | 1.8039 | 0.27032
15245 | 1.8039 | 0.27034
15246 | 1.8039 | 0.27035
15247 | 1.8038 | 0.27037
15248 | 1.8038 | 0.27038
15249 | 1.8038 | 0.2704
15250 | 1.8038 | 0.27041
15251 | 1.8038 | 0.27043
15252 | 1.8037 | 0.27044
15253 | 1.8037 | 0.27046
15254 | 1.8037 | 0.27048
15255 | 1.8037 | 0.27049
15256 | 1.8037 | 0.27051
15257 | 1.8037 | 0.27052
15258 | 1.8036 | 0.27054
15259 | 1.8036 | 0.27055
15260 | 1.8036 | 0.27057
15261 | 1.8036 | 0.27058
15262 | 1.8036 | 0.2706
15263 | 1.8036 | 0.27062
15264 | 1.8035 | 0.27063
15265 | 1.8035 | 0.27065
15266 | 1.8035 | 0.27066
15267 | 1.8035 | 0.27068
15268 | 1.8035 | 0.27069
15269 | 1.8034 | 0.27071
15270 | 1.8034 | 0.27072
15271 | 1.8034 | 0.27074
15272 | 1.8034 | 0.27076
15273 | 1.8034 | 0.27077
15274 | 1.8034 | 0.27079
15275 | 1.8033 | 0.2708
15276 | 1.8033 | 0.27082
15277 | 1.8033 | 0.27083
15278 | 1.8033 | 0.27085
15279 | 1.8033 | 0.27087
15280 | 1.8033 | 0.27088
15281 | 1.8032 | 0.2709
15282 | 1.8032 | 0.27091
15283 | 1.8032 | 0.27093
15284 | 1.8032 | 0.27094
15285 | 1.8032 | 0.27096
15286 | 1.8031 | 0.27097
15287 | 1.8031 | 0.27099
15288 | 1.8031 | 0.27101
15289 | 1.8031 | 0.27102
15290 | 1.8031 | 0.27104
15291 | 1.8031 | 0.27105
15292 | 1.803 | 0.27107
15293 | 1.803 | 0.27108
15294 | 1.803 | 0.2711
15295 | 1.803 | 0.27111
15296 | 1.803 | 0.27113
15297 | 1.803 | 0.27115
15298 | 1.8029 | 0.27116
15299 | 1.8029 | 0.27118
15300 | 1.8029 | 0.27119
15301 | 1.8029 | 0.27121
15302 | 1.8029 | 0.27122
15303 | 1.8028 | 0.27124
15304 | 1.8028 | 0.27125
15305 | 1.8028 | 0.27127
15306 | 1.8028 | 0.27129
15307 | 1.8028 | 0.2713
15308 | 1.8028 | 0.27132
15309 | 1.8027 | 0.27133
15310 | 1.8027 | 0.27135
15311 | 1.8027 | 0.27136
15312 | 1.8027 | 0.27138
15313 | 1.8027 | 0.27139
15314 | 1.8027 | 0.27141
15315 | 1.8026 | 0.27143
15316 | 1.8026 | 0.27144
15317 | 1.8026 | 0.27146
15318 | 1.8026 | 0.27147
15319 | 1.8026 | 0.27149
15320 | 1.8025 | 0.2715
15321 | 1.8025 | 0.27152
15322 | 1.8025 | 0.27153
15323 | 1.8025 | 0.27155
15324 | 1.8025 | 0.27157
15325 | 1.8025 | 0.27158
15326 | 1.8024 | 0.2716
15327 | 1.8024 | 0.27161
15328 | 1.8024 | 0.27163
15329 | 1.8024 | 0.27164
15330 | 1.8024 | 0.27166
15331 | 1.8024 | 0.27167
15332 | 1.8023 | 0.27169
15333 | 1.8023 | 0.27171
15334 | 1.8023 | 0.27172
15335 | 1.8023 | 0.27174
15336 | 1.8023 | 0.27175
15337 | 1.8022 | 0.27177
15338 | 1.8022 | 0.27178
15339 | 1.8022 | 0.2718
15340 | 1.8022 | 0.27181
15341 | 1.8022 | 0.27183
15342 | 1.8022 | 0.27185
15343 | 1.8021 | 0.27186
15344 | 1.8021 | 0.27188
15345 | 1.8021 | 0.27189
15346 | 1.8021 | 0.27191
15347 | 1.8021 | 0.27192
15348 | 1.8021 | 0.27194
15349 | 1.802 | 0.27195
15350 | 1.802 | 0.27197
15351 | 1.802 | 0.27199
15352 | 1.802 | 0.272
15353 | 1.802 | 0.27202
15354 | 1.8019 | 0.27203
15355 | 1.8019 | 0.27205
15356 | 1.8019 | 0.27206
15357 | 1.8019 | 0.27208
15358 | 1.8019 | 0.27209
15359 | 1.8019 | 0.27211
15360 | 1.8018 | 0.27213
15361 | 1.8018 | 0.27214
15362 | 1.8018 | 0.27216
15363 | 1.8018 | 0.27217
15364 | 1.8018 | 0.27219
15365 | 1.8018 | 0.2722
15366 | 1.8017 | 0.27222
15367 | 1.8017 | 0.27223
15368 | 1.8017 | 0.27225
15369 | 1.8017 | 0.27227
15370 | 1.8017 | 0.27228
15371 | 1.8016 | 0.2723
15372 | 1.8016 | 0.27231
15373 | 1.8016 | 0.27233
15374 | 1.8016 | 0.27234
15375 | 1.8016 | 0.27236
15376 | 1.8016 | 0.27237
15377 | 1.8015 | 0.27239
15378 | 1.8015 | 0.27241
15379 | 1.8015 | 0.27242
15380 | 1.8015 | 0.27244
15381 | 1.8015 | 0.27245
15382 | 1.8015 | 0.27247
15383 | 1.8014 | 0.27248
15384 | 1.8014 | 0.2725
15385 | 1.8014 | 0.27251
15386 | 1.8014 | 0.27253
15387 | 1.8014 | 0.27255
15388 | 1.8013 | 0.27256
15389 | 1.8013 | 0.27258
15390 | 1.8013 | 0.27259
15391 | 1.8013 | 0.27261
15392 | 1.8013 | 0.27262
15393 | 1.8013 | 0.27264
15394 | 1.8012 | 0.27265
15395 | 1.8012 | 0.27267
15396 | 1.8012 | 0.27269
15397 | 1.8012 | 0.2727
15398 | 1.8012 | 0.27272
15399 | 1.8012 | 0.27273
15400 | 1.8011 | 0.27275
15401 | 1.8011 | 0.27276
15402 | 1.8011 | 0.27278
15403 | 1.8011 | 0.27279
15404 | 1.8011 | 0.27281
15405 | 1.8011 | 0.27283
15406 | 1.801 | 0.27284
15407 | 1.801 | 0.27286
15408 | 1.801 | 0.27287
15409 | 1.801 | 0.27289
15410 | 1.801 | 0.2729
15411 | 1.8009 | 0.27292
15412 | 1.8009 | 0.27293
15413 | 1.8009 | 0.27295
15414 | 1.8009 | 0.27297
15415 | 1.8009 | 0.27298
15416 | 1.8009 | 0.273
15417 | 1.8008 | 0.27301
15418 | 1.8008 | 0.27303
15419 | 1.8008 | 0.27304
15420 | 1.8008 | 0.27306
15421 | 1.8008 | 0.27307
15422 | 1.8008 | 0.27309
15423 | 1.8007 | 0.27311
15424 | 1.8007 | 0.27312
15425 | 1.8007 | 0.27314
15426 | 1.8007 | 0.27315
15427 | 1.8007 | 0.27317
15428 | 1.8006 | 0.27318
15429 | 1.8006 | 0.2732
15430 | 1.8006 | 0.27321
15431 | 1.8006 | 0.27323
15432 | 1.8006 | 0.27325
15433 | 1.8006 | 0.27326
15434 | 1.8005 | 0.27328
15435 | 1.8005 | 0.27329
15436 | 1.8005 | 0.27331
15437 | 1.8005 | 0.27332
15438 | 1.8005 | 0.27334
15439 | 1.8005 | 0.27335
15440 | 1.8004 | 0.27337
15441 | 1.8004 | 0.27339
15442 | 1.8004 | 0.2734
15443 | 1.8004 | 0.27342
15444 | 1.8004 | 0.27343
15445 | 1.8003 | 0.27345
15446 | 1.8003 | 0.27346
15447 | 1.8003 | 0.27348
15448 | 1.8003 | 0.27349
15449 | 1.8003 | 0.27351
15450 | 1.8003 | 0.27353
15451 | 1.8002 | 0.27354
15452 | 1.8002 | 0.27356
15453 | 1.8002 | 0.27357
15454 | 1.8002 | 0.27359
15455 | 1.8002 | 0.2736
15456 | 1.8002 | 0.27362
15457 | 1.8001 | 0.27363
15458 | 1.8001 | 0.27365
15459 | 1.8001 | 0.27367
15460 | 1.8001 | 0.27368
15461 | 1.8001 | 0.2737
15462 | 1.8001 | 0.27371
15463 | 1.8 | 0.27373
15464 | 1.8 | 0.27374
15465 | 1.8 | 0.27376
15466 | 1.8 | 0.27377
15467 | 1.8 | 0.27379
15468 | 1.7999 | 0.2738
15469 | 1.7999 | 0.27382
15470 | 1.7999 | 0.27384
15471 | 1.7999 | 0.27385
15472 | 1.7999 | 0.27387
15473 | 1.7999 | 0.27388
15474 | 1.7998 | 0.2739
15475 | 1.7998 | 0.27391
15476 | 1.7998 | 0.27393
15477 | 1.7998 | 0.27394
15478 | 1.7998 | 0.27396
15479 | 1.7998 | 0.27398
15480 | 1.7997 | 0.27399
15481 | 1.7997 | 0.27401
15482 | 1.7997 | 0.27402
15483 | 1.7997 | 0.27404
15484 | 1.7997 | 0.27405
15485 | 1.7996 | 0.27407
15486 | 1.7996 | 0.27408
15487 | 1.7996 | 0.2741
15488 | 1.7996 | 0.27412
15489 | 1.7996 | 0.27413
15490 | 1.7996 | 0.27415
15491 | 1.7995 | 0.27416
15492 | 1.7995 | 0.27418
15493 | 1.7995 | 0.27419
15494 | 1.7995 | 0.27421
15495 | 1.7995 | 0.27422
15496 | 1.7995 | 0.27424
15497 | 1.7994 | 0.27426
15498 | 1.7994 | 0.27427
15499 | 1.7994 | 0.27429
15500 | 1.7994 | 0.2743
15501 | 1.7994 | 0.27432
15502 | 1.7993 | 0.27433
15503 | 1.7993 | 0.27435
15504 | 1.7993 | 0.27436
15505 | 1.7993 | 0.27438
15506 | 1.7993 | 0.2744
15507 | 1.7993 | 0.27441
15508 | 1.7992 | 0.27443
15509 | 1.7992 | 0.27444
15510 | 1.7992 | 0.27446
15511 | 1.7992 | 0.27447
15512 | 1.7992 | 0.27449
15513 | 1.7992 | 0.2745
15514 | 1.7991 | 0.27452
15515 | 1.7991 | 0.27453
15516 | 1.7991 | 0.27455
15517 | 1.7991 | 0.27457
15518 | 1.7991 | 0.27458
15519 | 1.7991 | 0.2746
15520 | 1.799 | 0.27461
15521 | 1.799 | 0.27463
15522 | 1.799 | 0.27464
15523 | 1.799 | 0.27466
15524 | 1.799 | 0.27467
15525 | 1.7989 | 0.27469
15526 | 1.7989 | 0.27471
15527 | 1.7989 | 0.27472
15528 | 1.7989 | 0.27474
15529 | 1.7989 | 0.27475
15530 | 1.7989 | 0.27477
15531 | 1.7988 | 0.27478
15532 | 1.7988 | 0.2748
15533 | 1.7988 | 0.27481
15534 | 1.7988 | 0.27483
15535 | 1.7988 | 0.27485
15536 | 1.7988 | 0.27486
15537 | 1.7987 | 0.27488
15538 | 1.7987 | 0.27489
15539 | 1.7987 | 0.27491
15540 | 1.7987 | 0.27492
15541 | 1.7987 | 0.27494
15542 | 1.7987 | 0.27495
15543 | 1.7986 | 0.27497
15544 | 1.7986 | 0.27498
15545 | 1.7986 | 0.275
15546 | 1.7986 | 0.27502
15547 | 1.7986 | 0.27503
15548 | 1.7985 | 0.27505
15549 | 1.7985 | 0.27506
15550 | 1.7985 | 0.27508
15551 | 1.7985 | 0.27509
15552 | 1.7985 | 0.27511
15553 | 1.7985 | 0.27512
15554 | 1.7984 | 0.27514
15555 | 1.7984 | 0.27516
15556 | 1.7984 | 0.27517
15557 | 1.7984 | 0.27519
15558 | 1.7984 | 0.2752
15559 | 1.7984 | 0.27522
15560 | 1.7983 | 0.27523
15561 | 1.7983 | 0.27525
15562 | 1.7983 | 0.27526
15563 | 1.7983 | 0.27528
15564 | 1.7983 | 0.2753
15565 | 1.7982 | 0.27531
15566 | 1.7982 | 0.27533
15567 | 1.7982 | 0.27534
15568 | 1.7982 | 0.27536
15569 | 1.7982 | 0.27537
15570 | 1.7982 | 0.27539
15571 | 1.7981 | 0.2754
15572 | 1.7981 | 0.27542
15573 | 1.7981 | 0.27543
15574 | 1.7981 | 0.27545
15575 | 1.7981 | 0.27547
15576 | 1.7981 | 0.27548
15577 | 1.798 | 0.2755
15578 | 1.798 | 0.27551
15579 | 1.798 | 0.27553
15580 | 1.798 | 0.27554
15581 | 1.798 | 0.27556
15582 | 1.798 | 0.27557
15583 | 1.7979 | 0.27559
15584 | 1.7979 | 0.27561
15585 | 1.7979 | 0.27562
15586 | 1.7979 | 0.27564
15587 | 1.7979 | 0.27565
15588 | 1.7978 | 0.27567
15589 | 1.7978 | 0.27568
15590 | 1.7978 | 0.2757
15591 | 1.7978 | 0.27571
15592 | 1.7978 | 0.27573
15593 | 1.7978 | 0.27575
15594 | 1.7977 | 0.27576
15595 | 1.7977 | 0.27578
15596 | 1.7977 | 0.27579
15597 | 1.7977 | 0.27581
15598 | 1.7977 | 0.27582
15599 | 1.7977 | 0.27584
15600 | 1.7976 | 0.27585
15601 | 1.7976 | 0.27587
15602 | 1.7976 | 0.27588
15603 | 1.7976 | 0.2759
15604 | 1.7976 | 0.27592
15605 | 1.7976 | 0.27593
15606 | 1.7975 | 0.27595
15607 | 1.7975 | 0.27596
15608 | 1.7975 | 0.27598
15609 | 1.7975 | 0.27599
15610 | 1.7975 | 0.27601
15611 | 1.7974 | 0.27602
15612 | 1.7974 | 0.27604
15613 | 1.7974 | 0.27606
15614 | 1.7974 | 0.27607
15615 | 1.7974 | 0.27609
15616 | 1.7974 | 0.2761
15617 | 1.7973 | 0.27612
15618 | 1.7973 | 0.27613
15619 | 1.7973 | 0.27615
15620 | 1.7973 | 0.27616
15621 | 1.7973 | 0.27618
15622 | 1.7973 | 0.27619
15623 | 1.7972 | 0.27621
15624 | 1.7972 | 0.27623
15625 | 1.7972 | 0.27624
15626 | 1.7972 | 0.27626
15627 | 1.7972 | 0.27627
15628 | 1.7971 | 0.27629
15629 | 1.7971 | 0.2763
15630 | 1.7971 | 0.27632
15631 | 1.7971 | 0.27633
15632 | 1.7971 | 0.27635
15633 | 1.7971 | 0.27637
15634 | 1.797 | 0.27638
15635 | 1.797 | 0.2764
15636 | 1.797 | 0.27641
15637 | 1.797 | 0.27643
15638 | 1.797 | 0.27644
15639 | 1.797 | 0.27646
15640 | 1.7969 | 0.27647
15641 | 1.7969 | 0.27649
15642 | 1.7969 | 0.2765
15643 | 1.7969 | 0.27652
15644 | 1.7969 | 0.27654
15645 | 1.7969 | 0.27655
15646 | 1.7968 | 0.27657
15647 | 1.7968 | 0.27658
15648 | 1.7968 | 0.2766
15649 | 1.7968 | 0.27661
15650 | 1.7968 | 0.27663
15651 | 1.7967 | 0.27664
15652 | 1.7967 | 0.27666
15653 | 1.7967 | 0.27668
15654 | 1.7967 | 0.27669
15655 | 1.7967 | 0.27671
15656 | 1.7967 | 0.27672
15657 | 1.7966 | 0.27674
15658 | 1.7966 | 0.27675
15659 | 1.7966 | 0.27677
15660 | 1.7966 | 0.27678
15661 | 1.7966 | 0.2768
15662 | 1.7966 | 0.27681
15663 | 1.7965 | 0.27683
15664 | 1.7965 | 0.27685
15665 | 1.7965 | 0.27686
15666 | 1.7965 | 0.27688
15667 | 1.7965 | 0.27689
15668 | 1.7965 | 0.27691
15669 | 1.7964 | 0.27692
15670 | 1.7964 | 0.27694
15671 | 1.7964 | 0.27695
15672 | 1.7964 | 0.27697
15673 | 1.7964 | 0.27698
15674 | 1.7963 | 0.277
15675 | 1.7963 | 0.27702
15676 | 1.7963 | 0.27703
15677 | 1.7963 | 0.27705
15678 | 1.7963 | 0.27706
15679 | 1.7963 | 0.27708
15680 | 1.7962 | 0.27709
15681 | 1.7962 | 0.27711
15682 | 1.7962 | 0.27712
15683 | 1.7962 | 0.27714
15684 | 1.7962 | 0.27716
15685 | 1.7962 | 0.27717
15686 | 1.7961 | 0.27719
15687 | 1.7961 | 0.2772
15688 | 1.7961 | 0.27722
15689 | 1.7961 | 0.27723
15690 | 1.7961 | 0.27725
15691 | 1.7961 | 0.27726
15692 | 1.796 | 0.27728
15693 | 1.796 | 0.27729
15694 | 1.796 | 0.27731
15695 | 1.796 | 0.27733
15696 | 1.796 | 0.27734
15697 | 1.7959 | 0.27736
15698 | 1.7959 | 0.27737
15699 | 1.7959 | 0.27739
15700 | 1.7959 | 0.2774
15701 | 1.7959 | 0.27742
15702 | 1.7959 | 0.27743
15703 | 1.7958 | 0.27745
15704 | 1.7958 | 0.27746
15705 | 1.7958 | 0.27748
15706 | 1.7958 | 0.2775
15707 | 1.7958 | 0.27751
15708 | 1.7958 | 0.27753
15709 | 1.7957 | 0.27754
15710 | 1.7957 | 0.27756
15711 | 1.7957 | 0.27757
15712 | 1.7957 | 0.27759
15713 | 1.7957 | 0.2776
15714 | 1.7957 | 0.27762
15715 | 1.7956 | 0.27764
15716 | 1.7956 | 0.27765
15717 | 1.7956 | 0.27767
15718 | 1.7956 | 0.27768
15719 | 1.7956 | 0.2777
15720 | 1.7955 | 0.27771
15721 | 1.7955 | 0.27773
15722 | 1.7955 | 0.27774
15723 | 1.7955 | 0.27776
15724 | 1.7955 | 0.27777
15725 | 1.7955 | 0.27779
15726 | 1.7954 | 0.27781
15727 | 1.7954 | 0.27782
15728 | 1.7954 | 0.27784
15729 | 1.7954 | 0.27785
15730 | 1.7954 | 0.27787
15731 | 1.7954 | 0.27788
15732 | 1.7953 | 0.2779
15733 | 1.7953 | 0.27791
15734 | 1.7953 | 0.27793
15735 | 1.7953 | 0.27794
15736 | 1.7953 | 0.27796
15737 | 1.7953 | 0.27798
15738 | 1.7952 | 0.27799
15739 | 1.7952 | 0.27801
15740 | 1.7952 | 0.27802
15741 | 1.7952 | 0.27804
15742 | 1.7952 | 0.27805
15743 | 1.7952 | 0.27807
15744 | 1.7951 | 0.27808
15745 | 1.7951 | 0.2781
15746 | 1.7951 | 0.27811
15747 | 1.7951 | 0.27813
15748 | 1.7951 | 0.27815
15749 | 1.795 | 0.27816
15750 | 1.795 | 0.27818
15751 | 1.795 | 0.27819
15752 | 1.795 | 0.27821
15753 | 1.795 | 0.27822
15754 | 1.795 | 0.27824
15755 | 1.7949 | 0.27825
15756 | 1.7949 | 0.27827
15757 | 1.7949 | 0.27829
15758 | 1.7949 | 0.2783
15759 | 1.7949 | 0.27832
15760 | 1.7949 | 0.27833
15761 | 1.7948 | 0.27835
15762 | 1.7948 | 0.27836
15763 | 1.7948 | 0.27838
15764 | 1.7948 | 0.27839
15765 | 1.7948 | 0.27841
15766 | 1.7948 | 0.27842
15767 | 1.7947 | 0.27844
15768 | 1.7947 | 0.27846
15769 | 1.7947 | 0.27847
15770 | 1.7947 | 0.27849
15771 | 1.7947 | 0.2785
15772 | 1.7946 | 0.27852
15773 | 1.7946 | 0.27853
15774 | 1.7946 | 0.27855
15775 | 1.7946 | 0.27856
15776 | 1.7946 | 0.27858
15777 | 1.7946 | 0.27859
15778 | 1.7945 | 0.27861
15779 | 1.7945 | 0.27863
15780 | 1.7945 | 0.27864
15781 | 1.7945 | 0.27866
15782 | 1.7945 | 0.27867
15783 | 1.7945 | 0.27869
15784 | 1.7944 | 0.2787
15785 | 1.7944 | 0.27872
15786 | 1.7944 | 0.27873
15787 | 1.7944 | 0.27875
15788 | 1.7944 | 0.27876
15789 | 1.7944 | 0.27878
15790 | 1.7943 | 0.2788
15791 | 1.7943 | 0.27881
15792 | 1.7943 | 0.27883
15793 | 1.7943 | 0.27884
15794 | 1.7943 | 0.27886
15795 | 1.7943 | 0.27887
15796 | 1.7942 | 0.27889
15797 | 1.7942 | 0.2789
15798 | 1.7942 | 0.27892
15799 | 1.7942 | 0.27893
15800 | 1.7942 | 0.27895
15801 | 1.7941 | 0.27897
15802 | 1.7941 | 0.27898
15803 | 1.7941 | 0.279
15804 | 1.7941 | 0.27901
15805 | 1.7941 | 0.27903
15806 | 1.7941 | 0.27904
15807 | 1.794 | 0.27906
15808 | 1.794 | 0.27907
15809 | 1.794 | 0.27909
15810 | 1.794 | 0.2791
15811 | 1.794 | 0.27912
15812 | 1.794 | 0.27914
15813 | 1.7939 | 0.27915
15814 | 1.7939 | 0.27917
15815 | 1.7939 | 0.27918
15816 | 1.7939 | 0.2792
15817 | 1.7939 | 0.27921
15818 | 1.7939 | 0.27923
15819 | 1.7938 | 0.27924
15820 | 1.7938 | 0.27926
15821 | 1.7938 | 0.27927
15822 | 1.7938 | 0.27929
15823 | 1.7938 | 0.27931
15824 | 1.7937 | 0.27932
15825 | 1.7937 | 0.27934
15826 | 1.7937 | 0.27935
15827 | 1.7937 | 0.27937
15828 | 1.7937 | 0.27938
15829 | 1.7937 | 0.2794
15830 | 1.7936 | 0.27941
15831 | 1.7936 | 0.27943
15832 | 1.7936 | 0.27944
15833 | 1.7936 | 0.27946
15834 | 1.7936 | 0.27948
15835 | 1.7936 | 0.27949
15836 | 1.7935 | 0.27951
15837 | 1.7935 | 0.27952
15838 | 1.7935 | 0.27954
15839 | 1.7935 | 0.27955
15840 | 1.7935 | 0.27957
15841 | 1.7935 | 0.27958
15842 | 1.7934 | 0.2796
15843 | 1.7934 | 0.27961
15844 | 1.7934 | 0.27963
15845 | 1.7934 | 0.27965
15846 | 1.7934 | 0.27966
15847 | 1.7934 | 0.27968
15848 | 1.7933 | 0.27969
15849 | 1.7933 | 0.27971
15850 | 1.7933 | 0.27972
15851 | 1.7933 | 0.27974
15852 | 1.7933 | 0.27975
15853 | 1.7932 | 0.27977
15854 | 1.7932 | 0.27978
15855 | 1.7932 | 0.2798
15856 | 1.7932 | 0.27982
15857 | 1.7932 | 0.27983
15858 | 1.7932 | 0.27985
15859 | 1.7931 | 0.27986
15860 | 1.7931 | 0.27988
15861 | 1.7931 | 0.27989
15862 | 1.7931 | 0.27991
15863 | 1.7931 | 0.27992
15864 | 1.7931 | 0.27994
15865 | 1.793 | 0.27995
15866 | 1.793 | 0.27997
15867 | 1.793 | 0.27999
15868 | 1.793 | 0.28
15869 | 1.793 | 0.28002
15870 | 1.793 | 0.28003
15871 | 1.7929 | 0.28005
15872 | 1.7929 | 0.28006
15873 | 1.7929 | 0.28008
15874 | 1.7929 | 0.28009
15875 | 1.7929 | 0.28011
15876 | 1.7929 | 0.28012
15877 | 1.7928 | 0.28014
15878 | 1.7928 | 0.28016
15879 | 1.7928 | 0.28017
15880 | 1.7928 | 0.28019
15881 | 1.7928 | 0.2802
15882 | 1.7927 | 0.28022
15883 | 1.7927 | 0.28023
15884 | 1.7927 | 0.28025
15885 | 1.7927 | 0.28026
15886 | 1.7927 | 0.28028
15887 | 1.7927 | 0.28029
15888 | 1.7926 | 0.28031
15889 | 1.7926 | 0.28033
15890 | 1.7926 | 0.28034
15891 | 1.7926 | 0.28036
15892 | 1.7926 | 0.28037
15893 | 1.7926 | 0.28039
15894 | 1.7925 | 0.2804
15895 | 1.7925 | 0.28042
15896 | 1.7925 | 0.28043
15897 | 1.7925 | 0.28045
15898 | 1.7925 | 0.28046
15899 | 1.7925 | 0.28048
15900 | 1.7924 | 0.2805
15901 | 1.7924 | 0.28051
15902 | 1.7924 | 0.28053
15903 | 1.7924 | 0.28054
15904 | 1.7924 | 0.28056
15905 | 1.7924 | 0.28057
15906 | 1.7923 | 0.28059
15907 | 1.7923 | 0.2806
15908 | 1.7923 | 0.28062
15909 | 1.7923 | 0.28063
15910 | 1.7923 | 0.28065
15911 | 1.7922 | 0.28066
15912 | 1.7922 | 0.28068
15913 | 1.7922 | 0.2807
15914 | 1.7922 | 0.28071
15915 | 1.7922 | 0.28073
15916 | 1.7922 | 0.28074
15917 | 1.7921 | 0.28076
15918 | 1.7921 | 0.28077
15919 | 1.7921 | 0.28079
15920 | 1.7921 | 0.2808
15921 | 1.7921 | 0.28082
15922 | 1.7921 | 0.28083
15923 | 1.792 | 0.28085
15924 | 1.792 | 0.28087
15925 | 1.792 | 0.28088
15926 | 1.792 | 0.2809
15927 | 1.792 | 0.28091
15928 | 1.792 | 0.28093
15929 | 1.7919 | 0.28094
15930 | 1.7919 | 0.28096
15931 | 1.7919 | 0.28097
15932 | 1.7919 | 0.28099
15933 | 1.7919 | 0.281
15934 | 1.7919 | 0.28102
15935 | 1.7918 | 0.28104
15936 | 1.7918 | 0.28105
15937 | 1.7918 | 0.28107
15938 | 1.7918 | 0.28108
15939 | 1.7918 | 0.2811
15940 | 1.7917 | 0.28111
15941 | 1.7917 | 0.28113
15942 | 1.7917 | 0.28114
15943 | 1.7917 | 0.28116
15944 | 1.7917 | 0.28117
15945 | 1.7917 | 0.28119
15946 | 1.7916 | 0.28121
15947 | 1.7916 | 0.28122
15948 | 1.7916 | 0.28124
15949 | 1.7916 | 0.28125
15950 | 1.7916 | 0.28127
15951 | 1.7916 | 0.28128
15952 | 1.7915 | 0.2813
15953 | 1.7915 | 0.28131
15954 | 1.7915 | 0.28133
15955 | 1.7915 | 0.28134
15956 | 1.7915 | 0.28136
15957 | 1.7915 | 0.28137
15958 | 1.7914 | 0.28139
15959 | 1.7914 | 0.28141
15960 | 1.7914 | 0.28142
15961 | 1.7914 | 0.28144
15962 | 1.7914 | 0.28145
15963 | 1.7914 | 0.28147
15964 | 1.7913 | 0.28148
15965 | 1.7913 | 0.2815
15966 | 1.7913 | 0.28151
15967 | 1.7913 | 0.28153
15968 | 1.7913 | 0.28154
15969 | 1.7912 | 0.28156
15970 | 1.7912 | 0.28158
15971 | 1.7912 | 0.28159
15972 | 1.7912 | 0.28161
15973 | 1.7912 | 0.28162
15974 | 1.7912 | 0.28164
15975 | 1.7911 | 0.28165
15976 | 1.7911 | 0.28167
15977 | 1.7911 | 0.28168
15978 | 1.7911 | 0.2817
15979 | 1.7911 | 0.28171
15980 | 1.7911 | 0.28173
15981 | 1.791 | 0.28174
15982 | 1.791 | 0.28176
15983 | 1.791 | 0.28178
15984 | 1.791 | 0.28179
15985 | 1.791 | 0.28181
15986 | 1.791 | 0.28182
15987 | 1.7909 | 0.28184
15988 | 1.7909 | 0.28185
15989 | 1.7909 | 0.28187
15990 | 1.7909 | 0.28188
15991 | 1.7909 | 0.2819
15992 | 1.7909 | 0.28191
15993 | 1.7908 | 0.28193
15994 | 1.7908 | 0.28195
15995 | 1.7908 | 0.28196
15996 | 1.7908 | 0.28198
15997 | 1.7908 | 0.28199
15998 | 1.7908 | 0.28201
15999 | 1.7907 | 0.28202
16000 | 1.7907 | 0.28204
16001 | 1.7907 | 0.28205
16002 | 1.7907 | 0.28207
16003 | 1.7907 | 0.28208
16004 | 1.7906 | 0.2821
16005 | 1.7906 | 0.28211
16006 | 1.7906 | 0.28213
16007 | 1.7906 | 0.28215
16008 | 1.7906 | 0.28216
16009 | 1.7906 | 0.28218
16010 | 1.7905 | 0.28219
16011 | 1.7905 | 0.28221
16012 | 1.7905 | 0.28222
16013 | 1.7905 | 0.28224
16014 | 1.7905 | 0.28225
16015 | 1.7905 | 0.28227
16016 | 1.7904 | 0.28228
16017 | 1.7904 | 0.2823
16018 | 1.7904 | 0.28232
16019 | 1.7904 | 0.28233
16020 | 1.7904 | 0.28235
16021 | 1.7904 | 0.28236
16022 | 1.7903 | 0.28238
16023 | 1.7903 | 0.28239
16024 | 1.7903 | 0.28241
16025 | 1.7903 | 0.28242
16026 | 1.7903 | 0.28244
16027 | 1.7903 | 0.28245
16028 | 1.7902 | 0.28247
16029 | 1.7902 | 0.28248
16030 | 1.7902 | 0.2825
16031 | 1.7902 | 0.28252
16032 | 1.7902 | 0.28253
16033 | 1.7902 | 0.28255
16034 | 1.7901 | 0.28256
16035 | 1.7901 | 0.28258
16036 | 1.7901 | 0.28259
16037 | 1.7901 | 0.28261
16038 | 1.7901 | 0.28262
16039 | 1.79 | 0.28264
16040 | 1.79 | 0.28265
16041 | 1.79 | 0.28267
16042 | 1.79 | 0.28269
16043 | 1.79 | 0.2827
16044 | 1.79 | 0.28272
16045 | 1.7899 | 0.28273
16046 | 1.7899 | 0.28275
16047 | 1.7899 | 0.28276
16048 | 1.7899 | 0.28278
16049 | 1.7899 | 0.28279
16050 | 1.7899 | 0.28281
16051 | 1.7898 | 0.28282
16052 | 1.7898 | 0.28284
16053 | 1.7898 | 0.28285
16054 | 1.7898 | 0.28287
16055 | 1.7898 | 0.28289
16056 | 1.7898 | 0.2829
16057 | 1.7897 | 0.28292
16058 | 1.7897 | 0.28293
16059 | 1.7897 | 0.28295
16060 | 1.7897 | 0.28296
16061 | 1.7897 | 0.28298
16062 | 1.7897 | 0.28299
16063 | 1.7896 | 0.28301
16064 | 1.7896 | 0.28302
16065 | 1.7896 | 0.28304
16066 | 1.7896 | 0.28305
16067 | 1.7896 | 0.28307
16068 | 1.7896 | 0.28309
16069 | 1.7895 | 0.2831
16070 | 1.7895 | 0.28312
16071 | 1.7895 | 0.28313
16072 | 1.7895 | 0.28315
16073 | 1.7895 | 0.28316
16074 | 1.7894 | 0.28318
16075 | 1.7894 | 0.28319
16076 | 1.7894 | 0.28321
16077 | 1.7894 | 0.28322
16078 | 1.7894 | 0.28324
16079 | 1.7894 | 0.28326
16080 | 1.7893 | 0.28327
16081 | 1.7893 | 0.28329
16082 | 1.7893 | 0.2833
16083 | 1.7893 | 0.28332
16084 | 1.7893 | 0.28333
16085 | 1.7893 | 0.28335
16086 | 1.7892 | 0.28336
16087 | 1.7892 | 0.28338
16088 | 1.7892 | 0.28339
16089 | 1.7892 | 0.28341
16090 | 1.7892 | 0.28342
16091 | 1.7892 | 0.28344
16092 | 1.7891 | 0.28346
16093 | 1.7891 | 0.28347
16094 | 1.7891 | 0.28349
16095 | 1.7891 | 0.2835
16096 | 1.7891 | 0.28352
16097 | 1.7891 | 0.28353
16098 | 1.789 | 0.28355
16099 | 1.789 | 0.28356
16100 | 1.789 | 0.28358
16101 | 1.789 | 0.28359
16102 | 1.789 | 0.28361
16103 | 1.789 | 0.28362
16104 | 1.7889 | 0.28364
16105 | 1.7889 | 0.28366
16106 | 1.7889 | 0.28367
16107 | 1.7889 | 0.28369
16108 | 1.7889 | 0.2837
16109 | 1.7888 | 0.28372
16110 | 1.7888 | 0.28373
16111 | 1.7888 | 0.28375
16112 | 1.7888 | 0.28376
16113 | 1.7888 | 0.28378
16114 | 1.7888 | 0.28379
16115 | 1.7887 | 0.28381
16116 | 1.7887 | 0.28382
16117 | 1.7887 | 0.28384
16118 | 1.7887 | 0.28386
16119 | 1.7887 | 0.28387
16120 | 1.7887 | 0.28389
16121 | 1.7886 | 0.2839
16122 | 1.7886 | 0.28392
16123 | 1.7886 | 0.28393
16124 | 1.7886 | 0.28395
16125 | 1.7886 | 0.28396
16126 | 1.7886 | 0.28398
16127 | 1.7885 | 0.28399
16128 | 1.7885 | 0.28401
16129 | 1.7885 | 0.28402
16130 | 1.7885 | 0.28404
16131 | 1.7885 | 0.28406
16132 | 1.7885 | 0.28407
16133 | 1.7884 | 0.28409
16134 | 1.7884 | 0.2841
16135 | 1.7884 | 0.28412
16136 | 1.7884 | 0.28413
16137 | 1.7884 | 0.28415
16138 | 1.7884 | 0.28416
16139 | 1.7883 | 0.28418
16140 | 1.7883 | 0.28419
16141 | 1.7883 | 0.28421
16142 | 1.7883 | 0.28422
16143 | 1.7883 | 0.28424
16144 | 1.7883 | 0.28426
16145 | 1.7882 | 0.28427
16146 | 1.7882 | 0.28429
16147 | 1.7882 | 0.2843
16148 | 1.7882 | 0.28432
16149 | 1.7882 | 0.28433
16150 | 1.7881 | 0.28435
16151 | 1.7881 | 0.28436
16152 | 1.7881 | 0.28438
16153 | 1.7881 | 0.28439
16154 | 1.7881 | 0.28441
16155 | 1.7881 | 0.28442
16156 | 1.788 | 0.28444
16157 | 1.788 | 0.28446
16158 | 1.788 | 0.28447
16159 | 1.788 | 0.28449
16160 | 1.788 | 0.2845
16161 | 1.788 | 0.28452
16162 | 1.7879 | 0.28453
16163 | 1.7879 | 0.28455
16164 | 1.7879 | 0.28456
16165 | 1.7879 | 0.28458
16166 | 1.7879 | 0.28459
16167 | 1.7879 | 0.28461
16168 | 1.7878 | 0.28462
16169 | 1.7878 | 0.28464
16170 | 1.7878 | 0.28466
16171 | 1.7878 | 0.28467
16172 | 1.7878 | 0.28469
16173 | 1.7878 | 0.2847
16174 | 1.7877 | 0.28472
16175 | 1.7877 | 0.28473
16176 | 1.7877 | 0.28475
16177 | 1.7877 | 0.28476
16178 | 1.7877 | 0.28478
16179 | 1.7877 | 0.28479
16180 | 1.7876 | 0.28481
16181 | 1.7876 | 0.28482
16182 | 1.7876 | 0.28484
16183 | 1.7876 | 0.28486
16184 | 1.7876 | 0.28487
16185 | 1.7876 | 0.28489
16186 | 1.7875 | 0.2849
16187 | 1.7875 | 0.28492
16188 | 1.7875 | 0.28493
16189 | 1.7875 | 0.28495
16190 | 1.7875 | 0.28496
16191 | 1.7874 | 0.28498
16192 | 1.7874 | 0.28499
16193 | 1.7874 | 0.28501
16194 | 1.7874 | 0.28502
16195 | 1.7874 | 0.28504
16196 | 1.7874 | 0.28506
16197 | 1.7873 | 0.28507
16198 | 1.7873 | 0.28509
16199 | 1.7873 | 0.2851
16200 | 1.7873 | 0.28512
16201 | 1.7873 | 0.28513
16202 | 1.7873 | 0.28515
16203 | 1.7872 | 0.28516
16204 | 1.7872 | 0.28518
16205 | 1.7872 | 0.28519
16206 | 1.7872 | 0.28521
16207 | 1.7872 | 0.28522
16208 | 1.7872 | 0.28524
16209 | 1.7871 | 0.28526
16210 | 1.7871 | 0.28527
16211 | 1.7871 | 0.28529
16212 | 1.7871 | 0.2853
16213 | 1.7871 | 0.28532
16214 | 1.7871 | 0.28533
16215 | 1.787 | 0.28535
16216 | 1.787 | 0.28536
16217 | 1.787 | 0.28538
16218 | 1.787 | 0.28539
16219 | 1.787 | 0.28541
16220 | 1.787 | 0.28542
16221 | 1.7869 | 0.28544
16222 | 1.7869 | 0.28546
16223 | 1.7869 | 0.28547
16224 | 1.7869 | 0.28549
16225 | 1.7869 | 0.2855
16226 | 1.7869 | 0.28552
16227 | 1.7868 | 0.28553
16228 | 1.7868 | 0.28555
16229 | 1.7868 | 0.28556
16230 | 1.7868 | 0.28558
16231 | 1.7868 | 0.28559
16232 | 1.7868 | 0.28561
16233 | 1.7867 | 0.28562
16234 | 1.7867 | 0.28564
16235 | 1.7867 | 0.28565
16236 | 1.7867 | 0.28567
16237 | 1.7867 | 0.28569
16238 | 1.7866 | 0.2857
16239 | 1.7866 | 0.28572
16240 | 1.7866 | 0.28573
16241 | 1.7866 | 0.28575
16242 | 1.7866 | 0.28576
16243 | 1.7866 | 0.28578
16244 | 1.7865 | 0.28579
16245 | 1.7865 | 0.28581
16246 | 1.7865 | 0.28582
16247 | 1.7865 | 0.28584
16248 | 1.7865 | 0.28585
16249 | 1.7865 | 0.28587
16250 | 1.7864 | 0.28589
16251 | 1.7864 | 0.2859
16252 | 1.7864 | 0.28592
16253 | 1.7864 | 0.28593
16254 | 1.7864 | 0.28595
16255 | 1.7864 | 0.28596
16256 | 1.7863 | 0.28598
16257 | 1.7863 | 0.28599
16258 | 1.7863 | 0.28601
16259 | 1.7863 | 0.28602
16260 | 1.7863 | 0.28604
16261 | 1.7863 | 0.28605
16262 | 1.7862 | 0.28607
16263 | 1.7862 | 0.28608
16264 | 1.7862 | 0.2861
16265 | 1.7862 | 0.28612
16266 | 1.7862 | 0.28613
16267 | 1.7862 | 0.28615
16268 | 1.7861 | 0.28616
16269 | 1.7861 | 0.28618
16270 | 1.7861 | 0.28619
16271 | 1.7861 | 0.28621
16272 | 1.7861 | 0.28622
16273 | 1.7861 | 0.28624
16274 | 1.786 | 0.28625
16275 | 1.786 | 0.28627
16276 | 1.786 | 0.28628
16277 | 1.786 | 0.2863
16278 | 1.786 | 0.28632
16279 | 1.786 | 0.28633
16280 | 1.7859 | 0.28635
16281 | 1.7859 | 0.28636
16282 | 1.7859 | 0.28638
16283 | 1.7859 | 0.28639
16284 | 1.7859 | 0.28641
16285 | 1.7859 | 0.28642
16286 | 1.7858 | 0.28644
16287 | 1.7858 | 0.28645
16288 | 1.7858 | 0.28647
16289 | 1.7858 | 0.28648
16290 | 1.7858 | 0.2865
16291 | 1.7857 | 0.28651
16292 | 1.7857 | 0.28653
16293 | 1.7857 | 0.28655
16294 | 1.7857 | 0.28656
16295 | 1.7857 | 0.28658
16296 | 1.7857 | 0.28659
16297 | 1.7856 | 0.28661
16298 | 1.7856 | 0.28662
16299 | 1.7856 | 0.28664
16300 | 1.7856 | 0.28665
16301 | 1.7856 | 0.28667
16302 | 1.7856 | 0.28668
16303 | 1.7855 | 0.2867
16304 | 1.7855 | 0.28671
16305 | 1.7855 | 0.28673
16306 | 1.7855 | 0.28675
16307 | 1.7855 | 0.28676
16308 | 1.7855 | 0.28678
16309 | 1.7854 | 0.28679
16310 | 1.7854 | 0.28681
16311 | 1.7854 | 0.28682
16312 | 1.7854 | 0.28684
16313 | 1.7854 | 0.28685
16314 | 1.7854 | 0.28687
16315 | 1.7853 | 0.28688
16316 | 1.7853 | 0.2869
16317 | 1.7853 | 0.28691
16318 | 1.7853 | 0.28693
16319 | 1.7853 | 0.28694
16320 | 1.7853 | 0.28696
16321 | 1.7852 | 0.28698
16322 | 1.7852 | 0.28699
16323 | 1.7852 | 0.28701
16324 | 1.7852 | 0.28702
16325 | 1.7852 | 0.28704
16326 | 1.7852 | 0.28705
16327 | 1.7851 | 0.28707
16328 | 1.7851 | 0.28708
16329 | 1.7851 | 0.2871
16330 | 1.7851 | 0.28711
16331 | 1.7851 | 0.28713
16332 | 1.7851 | 0.28714
16333 | 1.785 | 0.28716
16334 | 1.785 | 0.28717
16335 | 1.785 | 0.28719
16336 | 1.785 | 0.28721
16337 | 1.785 | 0.28722
16338 | 1.785 | 0.28724
16339 | 1.7849 | 0.28725
16340 | 1.7849 | 0.28727
16341 | 1.7849 | 0.28728
16342 | 1.7849 | 0.2873
16343 | 1.7849 | 0.28731
16344 | 1.7849 | 0.28733
16345 | 1.7848 | 0.28734
16346 | 1.7848 | 0.28736
16347 | 1.7848 | 0.28737
16348 | 1.7848 | 0.28739
16349 | 1.7848 | 0.28741
16350 | 1.7847 | 0.28742
16351 | 1.7847 | 0.28744
16352 | 1.7847 | 0.28745
16353 | 1.7847 | 0.28747
16354 | 1.7847 | 0.28748
16355 | 1.7847 | 0.2875
16356 | 1.7846 | 0.28751
16357 | 1.7846 | 0.28753
16358 | 1.7846 | 0.28754
16359 | 1.7846 | 0.28756
16360 | 1.7846 | 0.28757
16361 | 1.7846 | 0.28759
16362 | 1.7845 | 0.2876
16363 | 1.7845 | 0.28762
16364 | 1.7845 | 0.28764
16365 | 1.7845 | 0.28765
16366 | 1.7845 | 0.28767
16367 | 1.7845 | 0.28768
16368 | 1.7844 | 0.2877
16369 | 1.7844 | 0.28771
16370 | 1.7844 | 0.28773
16371 | 1.7844 | 0.28774
16372 | 1.7844 | 0.28776
16373 | 1.7844 | 0.28777
16374 | 1.7843 | 0.28779
16375 | 1.7843 | 0.2878
16376 | 1.7843 | 0.28782
16377 | 1.7843 | 0.28783
16378 | 1.7843 | 0.28785
16379 | 1.7843 | 0.28787
16380 | 1.7842 | 0.28788
16381 | 1.7842 | 0.2879
16382 | 1.7842 | 0.28791
16383 | 1.7842 | 0.28793
16384 | 1.7842 | 0.28794
16385 | 1.7842 | 0.28796
16386 | 1.7841 | 0.28797
16387 | 1.7841 | 0.28799
16388 | 1.7841 | 0.288
16389 | 1.7841 | 0.28802
16390 | 1.7841 | 0.28803
16391 | 1.7841 | 0.28805
16392 | 1.784 | 0.28806
16393 | 1.784 | 0.28808
16394 | 1.784 | 0.2881
16395 | 1.784 | 0.28811
16396 | 1.784 | 0.28813
16397 | 1.784 | 0.28814
16398 | 1.7839 | 0.28816
16399 | 1.7839 | 0.28817
16400 | 1.7839 | 0.28819
16401 | 1.7839 | 0.2882
16402 | 1.7839 | 0.28822
16403 | 1.7839 | 0.28823
16404 | 1.7838 | 0.28825
16405 | 1.7838 | 0.28826
16406 | 1.7838 | 0.28828
16407 | 1.7838 | 0.28829
16408 | 1.7838 | 0.28831
16409 | 1.7838 | 0.28833
16410 | 1.7837 | 0.28834
16411 | 1.7837 | 0.28836
16412 | 1.7837 | 0.28837
16413 | 1.7837 | 0.28839
16414 | 1.7837 | 0.2884
16415 | 1.7836 | 0.28842
16416 | 1.7836 | 0.28843
16417 | 1.7836 | 0.28845
16418 | 1.7836 | 0.28846
16419 | 1.7836 | 0.28848
16420 | 1.7836 | 0.28849
16421 | 1.7835 | 0.28851
16422 | 1.7835 | 0.28852
16423 | 1.7835 | 0.28854
16424 | 1.7835 | 0.28856
16425 | 1.7835 | 0.28857
16426 | 1.7835 | 0.28859
16427 | 1.7834 | 0.2886
16428 | 1.7834 | 0.28862
16429 | 1.7834 | 0.28863
16430 | 1.7834 | 0.28865
16431 | 1.7834 | 0.28866
16432 | 1.7834 | 0.28868
16433 | 1.7833 | 0.28869
16434 | 1.7833 | 0.28871
16435 | 1.7833 | 0.28872
16436 | 1.7833 | 0.28874
16437 | 1.7833 | 0.28875
16438 | 1.7833 | 0.28877
16439 | 1.7832 | 0.28878
16440 | 1.7832 | 0.2888
16441 | 1.7832 | 0.28882
16442 | 1.7832 | 0.28883
16443 | 1.7832 | 0.28885
16444 | 1.7832 | 0.28886
16445 | 1.7831 | 0.28888
16446 | 1.7831 | 0.28889
16447 | 1.7831 | 0.28891
16448 | 1.7831 | 0.28892
16449 | 1.7831 | 0.28894
16450 | 1.7831 | 0.28895
16451 | 1.783 | 0.28897
16452 | 1.783 | 0.28898
16453 | 1.783 | 0.289
16454 | 1.783 | 0.28901
16455 | 1.783 | 0.28903
16456 | 1.783 | 0.28905
16457 | 1.7829 | 0.28906
16458 | 1.7829 | 0.28908
16459 | 1.7829 | 0.28909
16460 | 1.7829 | 0.28911
16461 | 1.7829 | 0.28912
16462 | 1.7829 | 0.28914
16463 | 1.7828 | 0.28915
16464 | 1.7828 | 0.28917
16465 | 1.7828 | 0.28918
16466 | 1.7828 | 0.2892
16467 | 1.7828 | 0.28921
16468 | 1.7828 | 0.28923
16469 | 1.7827 | 0.28924
16470 | 1.7827 | 0.28926
16471 | 1.7827 | 0.28928
16472 | 1.7827 | 0.28929
16473 | 1.7827 | 0.28931
16474 | 1.7827 | 0.28932
16475 | 1.7826 | 0.28934
16476 | 1.7826 | 0.28935
16477 | 1.7826 | 0.28937
16478 | 1.7826 | 0.28938
16479 | 1.7826 | 0.2894
16480 | 1.7826 | 0.28941
16481 | 1.7825 | 0.28943
16482 | 1.7825 | 0.28944
16483 | 1.7825 | 0.28946
16484 | 1.7825 | 0.28947
16485 | 1.7825 | 0.28949
16486 | 1.7825 | 0.2895
16487 | 1.7824 | 0.28952
16488 | 1.7824 | 0.28954
16489 | 1.7824 | 0.28955
16490 | 1.7824 | 0.28957
16491 | 1.7824 | 0.28958
16492 | 1.7824 | 0.2896
16493 | 1.7823 | 0.28961
16494 | 1.7823 | 0.28963
16495 | 1.7823 | 0.28964
16496 | 1.7823 | 0.28966
16497 | 1.7823 | 0.28967
16498 | 1.7822 | 0.28969
16499 | 1.7822 | 0.2897
16500 | 1.7822 | 0.28972
16501 | 1.7822 | 0.28973
16502 | 1.7822 | 0.28975
16503 | 1.7822 | 0.28977
16504 | 1.7821 | 0.28978
16505 | 1.7821 | 0.2898
16506 | 1.7821 | 0.28981
16507 | 1.7821 | 0.28983
16508 | 1.7821 | 0.28984
16509 | 1.7821 | 0.28986
16510 | 1.782 | 0.28987
16511 | 1.782 | 0.28989
16512 | 1.782 | 0.2899
16513 | 1.782 | 0.28992
16514 | 1.782 | 0.28993
16515 | 1.782 | 0.28995
16516 | 1.7819 | 0.28996
16517 | 1.7819 | 0.28998
16518 | 1.7819 | 0.28999
16519 | 1.7819 | 0.29001
16520 | 1.7819 | 0.29003
16521 | 1.7819 | 0.29004
16522 | 1.7818 | 0.29006
16523 | 1.7818 | 0.29007
16524 | 1.7818 | 0.29009
16525 | 1.7818 | 0.2901
16526 | 1.7818 | 0.29012
16527 | 1.7818 | 0.29013
16528 | 1.7817 | 0.29015
16529 | 1.7817 | 0.29016
16530 | 1.7817 | 0.29018
16531 | 1.7817 | 0.29019
16532 | 1.7817 | 0.29021
16533 | 1.7817 | 0.29022
16534 | 1.7816 | 0.29024
16535 | 1.7816 | 0.29025
16536 | 1.7816 | 0.29027
16537 | 1.7816 | 0.29029
16538 | 1.7816 | 0.2903
16539 | 1.7816 | 0.29032
16540 | 1.7815 | 0.29033
16541 | 1.7815 | 0.29035
16542 | 1.7815 | 0.29036
16543 | 1.7815 | 0.29038
16544 | 1.7815 | 0.29039
16545 | 1.7815 | 0.29041
16546 | 1.7814 | 0.29042
16547 | 1.7814 | 0.29044
16548 | 1.7814 | 0.29045
16549 | 1.7814 | 0.29047
16550 | 1.7814 | 0.29048
16551 | 1.7814 | 0.2905
16552 | 1.7813 | 0.29051
16553 | 1.7813 | 0.29053
16554 | 1.7813 | 0.29055
16555 | 1.7813 | 0.29056
16556 | 1.7813 | 0.29058
16557 | 1.7813 | 0.29059
16558 | 1.7812 | 0.29061
16559 | 1.7812 | 0.29062
16560 | 1.7812 | 0.29064
16561 | 1.7812 | 0.29065
16562 | 1.7812 | 0.29067
16563 | 1.7812 | 0.29068
16564 | 1.7811 | 0.2907
16565 | 1.7811 | 0.29071
16566 | 1.7811 | 0.29073
16567 | 1.7811 | 0.29074
16568 | 1.7811 | 0.29076
16569 | 1.7811 | 0.29077
16570 | 1.781 | 0.29079
16571 | 1.781 | 0.29081
16572 | 1.781 | 0.29082
16573 | 1.781 | 0.29084
16574 | 1.781 | 0.29085
16575 | 1.781 | 0.29087
16576 | 1.7809 | 0.29088
16577 | 1.7809 | 0.2909
16578 | 1.7809 | 0.29091
16579 | 1.7809 | 0.29093
16580 | 1.7809 | 0.29094
16581 | 1.7809 | 0.29096
16582 | 1.7808 | 0.29097
16583 | 1.7808 | 0.29099
16584 | 1.7808 | 0.291
16585 | 1.7808 | 0.29102
16586 | 1.7808 | 0.29103
16587 | 1.7808 | 0.29105
16588 | 1.7807 | 0.29107
16589 | 1.7807 | 0.29108
16590 | 1.7807 | 0.2911
16591 | 1.7807 | 0.29111
16592 | 1.7807 | 0.29113
16593 | 1.7807 | 0.29114
16594 | 1.7806 | 0.29116
16595 | 1.7806 | 0.29117
16596 | 1.7806 | 0.29119
16597 | 1.7806 | 0.2912
16598 | 1.7806 | 0.29122
16599 | 1.7806 | 0.29123
16600 | 1.7805 | 0.29125
16601 | 1.7805 | 0.29126
16602 | 1.7805 | 0.29128
16603 | 1.7805 | 0.29129
16604 | 1.7805 | 0.29131
16605 | 1.7805 | 0.29133
16606 | 1.7804 | 0.29134
16607 | 1.7804 | 0.29136
16608 | 1.7804 | 0.29137
16609 | 1.7804 | 0.29139
16610 | 1.7804 | 0.2914
16611 | 1.7804 | 0.29142
16612 | 1.7803 | 0.29143
16613 | 1.7803 | 0.29145
16614 | 1.7803 | 0.29146
16615 | 1.7803 | 0.29148
16616 | 1.7803 | 0.29149
16617 | 1.7802 | 0.29151
16618 | 1.7802 | 0.29152
16619 | 1.7802 | 0.29154
16620 | 1.7802 | 0.29155
16621 | 1.7802 | 0.29157
16622 | 1.7802 | 0.29159
16623 | 1.7801 | 0.2916
16624 | 1.7801 | 0.29162
16625 | 1.7801 | 0.29163
16626 | 1.7801 | 0.29165
16627 | 1.7801 | 0.29166
16628 | 1.7801 | 0.29168
16629 | 1.78 | 0.29169
16630 | 1.78 | 0.29171
16631 | 1.78 | 0.29172
16632 | 1.78 | 0.29174
16633 | 1.78 | 0.29175
16634 | 1.78 | 0.29177
16635 | 1.7799 | 0.29178
16636 | 1.7799 | 0.2918
16637 | 1.7799 | 0.29181
16638 | 1.7799 | 0.29183
16639 | 1.7799 | 0.29184
16640 | 1.7799 | 0.29186
16641 | 1.7798 | 0.29188
16642 | 1.7798 | 0.29189
16643 | 1.7798 | 0.29191
16644 | 1.7798 | 0.29192
16645 | 1.7798 | 0.29194
16646 | 1.7798 | 0.29195
16647 | 1.7797 | 0.29197
16648 | 1.7797 | 0.29198
16649 | 1.7797 | 0.292
16650 | 1.7797 | 0.29201
16651 | 1.7797 | 0.29203
16652 | 1.7797 | 0.29204
16653 | 1.7796 | 0.29206
16654 | 1.7796 | 0.29207
16655 | 1.7796 | 0.29209
16656 | 1.7796 | 0.2921
16657 | 1.7796 | 0.29212
16658 | 1.7796 | 0.29214
16659 | 1.7795 | 0.29215
16660 | 1.7795 | 0.29217
16661 | 1.7795 | 0.29218
16662 | 1.7795 | 0.2922
16663 | 1.7795 | 0.29221
16664 | 1.7795 | 0.29223
16665 | 1.7794 | 0.29224
16666 | 1.7794 | 0.29226
16667 | 1.7794 | 0.29227
16668 | 1.7794 | 0.29229
16669 | 1.7794 | 0.2923
16670 | 1.7794 | 0.29232
16671 | 1.7793 | 0.29233
16672 | 1.7793 | 0.29235
16673 | 1.7793 | 0.29236
16674 | 1.7793 | 0.29238
16675 | 1.7793 | 0.29239
16676 | 1.7793 | 0.29241
16677 | 1.7792 | 0.29243
16678 | 1.7792 | 0.29244
16679 | 1.7792 | 0.29246
16680 | 1.7792 | 0.29247
16681 | 1.7792 | 0.29249
16682 | 1.7792 | 0.2925
16683 | 1.7791 | 0.29252
16684 | 1.7791 | 0.29253
16685 | 1.7791 | 0.29255
16686 | 1.7791 | 0.29256
16687 | 1.7791 | 0.29258
16688 | 1.7791 | 0.29259
16689 | 1.779 | 0.29261
16690 | 1.779 | 0.29262
16691 | 1.779 | 0.29264
16692 | 1.779 | 0.29265
16693 | 1.779 | 0.29267
16694 | 1.779 | 0.29268
16695 | 1.7789 | 0.2927
16696 | 1.7789 | 0.29272
16697 | 1.7789 | 0.29273
16698 | 1.7789 | 0.29275
16699 | 1.7789 | 0.29276
16700 | 1.7789 | 0.29278
16701 | 1.7788 | 0.29279
16702 | 1.7788 | 0.29281
16703 | 1.7788 | 0.29282
16704 | 1.7788 | 0.29284
16705 | 1.7788 | 0.29285
16706 | 1.7788 | 0.29287
16707 | 1.7787 | 0.29288
16708 | 1.7787 | 0.2929
16709 | 1.7787 | 0.29291
16710 | 1.7787 | 0.29293
16711 | 1.7787 | 0.29294
16712 | 1.7787 | 0.29296
16713 | 1.7786 | 0.29298
16714 | 1.7786 | 0.29299
16715 | 1.7786 | 0.29301
16716 | 1.7786 | 0.29302
16717 | 1.7786 | 0.29304
16718 | 1.7786 | 0.29305
16719 | 1.7785 | 0.29307
16720 | 1.7785 | 0.29308
16721 | 1.7785 | 0.2931
16722 | 1.7785 | 0.29311
16723 | 1.7785 | 0.29313
16724 | 1.7785 | 0.29314
16725 | 1.7784 | 0.29316
16726 | 1.7784 | 0.29317
16727 | 1.7784 | 0.29319
16728 | 1.7784 | 0.2932
16729 | 1.7784 | 0.29322
16730 | 1.7784 | 0.29323
16731 | 1.7783 | 0.29325
16732 | 1.7783 | 0.29326
16733 | 1.7783 | 0.29328
16734 | 1.7783 | 0.2933
16735 | 1.7783 | 0.29331
16736 | 1.7783 | 0.29333
16737 | 1.7782 | 0.29334
16738 | 1.7782 | 0.29336
16739 | 1.7782 | 0.29337
16740 | 1.7782 | 0.29339
16741 | 1.7782 | 0.2934
16742 | 1.7782 | 0.29342
16743 | 1.7781 | 0.29343
16744 | 1.7781 | 0.29345
16745 | 1.7781 | 0.29346
16746 | 1.7781 | 0.29348
16747 | 1.7781 | 0.29349
16748 | 1.7781 | 0.29351
16749 | 1.778 | 0.29352
16750 | 1.778 | 0.29354
16751 | 1.778 | 0.29355
16752 | 1.778 | 0.29357
16753 | 1.778 | 0.29359
16754 | 1.778 | 0.2936
16755 | 1.7779 | 0.29362
16756 | 1.7779 | 0.29363
16757 | 1.7779 | 0.29365
16758 | 1.7779 | 0.29366
16759 | 1.7779 | 0.29368
16760 | 1.7779 | 0.29369
16761 | 1.7778 | 0.29371
16762 | 1.7778 | 0.29372
16763 | 1.7778 | 0.29374
16764 | 1.7778 | 0.29375
16765 | 1.7778 | 0.29377
16766 | 1.7778 | 0.29378
16767 | 1.7777 | 0.2938
16768 | 1.7777 | 0.29381
16769 | 1.7777 | 0.29383
16770 | 1.7777 | 0.29384
16771 | 1.7777 | 0.29386
16772 | 1.7777 | 0.29388
16773 | 1.7776 | 0.29389
16774 | 1.7776 | 0.29391
16775 | 1.7776 | 0.29392
16776 | 1.7776 | 0.29394
16777 | 1.7776 | 0.29395
16778 | 1.7776 | 0.29397
16779 | 1.7775 | 0.29398
16780 | 1.7775 | 0.294
16781 | 1.7775 | 0.29401
16782 | 1.7775 | 0.29403
16783 | 1.7775 | 0.29404
16784 | 1.7775 | 0.29406
16785 | 1.7774 | 0.29407
16786 | 1.7774 | 0.29409
16787 | 1.7774 | 0.2941
16788 | 1.7774 | 0.29412
16789 | 1.7774 | 0.29413
16790 | 1.7774 | 0.29415
16791 | 1.7773 | 0.29416
16792 | 1.7773 | 0.29418
16793 | 1.7773 | 0.2942
16794 | 1.7773 | 0.29421
16795 | 1.7773 | 0.29423
16796 | 1.7773 | 0.29424
16797 | 1.7772 | 0.29426
16798 | 1.7772 | 0.29427
16799 | 1.7772 | 0.29429
16800 | 1.7772 | 0.2943
16801 | 1.7772 | 0.29432
16802 | 1.7772 | 0.29433
16803 | 1.7771 | 0.29435
16804 | 1.7771 | 0.29436
16805 | 1.7771 | 0.29438
16806 | 1.7771 | 0.29439
16807 | 1.7771 | 0.29441
16808 | 1.7771 | 0.29442
16809 | 1.777 | 0.29444
16810 | 1.777 | 0.29445
16811 | 1.777 | 0.29447
16812 | 1.777 | 0.29449
16813 | 1.777 | 0.2945
16814 | 1.777 | 0.29452
16815 | 1.7769 | 0.29453
16816 | 1.7769 | 0.29455
16817 | 1.7769 | 0.29456
16818 | 1.7769 | 0.29458
16819 | 1.7769 | 0.29459
16820 | 1.7769 | 0.29461
16821 | 1.7768 | 0.29462
16822 | 1.7768 | 0.29464
16823 | 1.7768 | 0.29465
16824 | 1.7768 | 0.29467
16825 | 1.7768 | 0.29468
16826 | 1.7768 | 0.2947
16827 | 1.7767 | 0.29471
16828 | 1.7767 | 0.29473
16829 | 1.7767 | 0.29474
16830 | 1.7767 | 0.29476
16831 | 1.7767 | 0.29477
16832 | 1.7767 | 0.29479
16833 | 1.7766 | 0.29481
16834 | 1.7766 | 0.29482
16835 | 1.7766 | 0.29484
16836 | 1.7766 | 0.29485
16837 | 1.7766 | 0.29487
16838 | 1.7766 | 0.29488
16839 | 1.7765 | 0.2949
16840 | 1.7765 | 0.29491
16841 | 1.7765 | 0.29493
16842 | 1.7765 | 0.29494
16843 | 1.7765 | 0.29496
16844 | 1.7765 | 0.29497
16845 | 1.7764 | 0.29499
16846 | 1.7764 | 0.295
16847 | 1.7764 | 0.29502
16848 | 1.7764 | 0.29503
16849 | 1.7764 | 0.29505
16850 | 1.7764 | 0.29506
16851 | 1.7763 | 0.29508
16852 | 1.7763 | 0.29509
16853 | 1.7763 | 0.29511
16854 | 1.7763 | 0.29513
16855 | 1.7763 | 0.29514
16856 | 1.7763 | 0.29516
16857 | 1.7762 | 0.29517
16858 | 1.7762 | 0.29519
16859 | 1.7762 | 0.2952
16860 | 1.7762 | 0.29522
16861 | 1.7762 | 0.29523
16862 | 1.7762 | 0.29525
16863 | 1.7761 | 0.29526
16864 | 1.7761 | 0.29528
16865 | 1.7761 | 0.29529
16866 | 1.7761 | 0.29531
16867 | 1.7761 | 0.29532
16868 | 1.7761 | 0.29534
16869 | 1.776 | 0.29535
16870 | 1.776 | 0.29537
16871 | 1.776 | 0.29538
16872 | 1.776 | 0.2954
16873 | 1.776 | 0.29541
16874 | 1.776 | 0.29543
16875 | 1.7759 | 0.29544
16876 | 1.7759 | 0.29546
16877 | 1.7759 | 0.29548
16878 | 1.7759 | 0.29549
16879 | 1.7759 | 0.29551
16880 | 1.7759 | 0.29552
16881 | 1.7758 | 0.29554
16882 | 1.7758 | 0.29555
16883 | 1.7758 | 0.29557
16884 | 1.7758 | 0.29558
16885 | 1.7758 | 0.2956
16886 | 1.7758 | 0.29561
16887 | 1.7757 | 0.29563
16888 | 1.7757 | 0.29564
16889 | 1.7757 | 0.29566
16890 | 1.7757 | 0.29567
16891 | 1.7757 | 0.29569
16892 | 1.7757 | 0.2957
16893 | 1.7756 | 0.29572
16894 | 1.7756 | 0.29573
16895 | 1.7756 | 0.29575
16896 | 1.7756 | 0.29576
16897 | 1.7756 | 0.29578
16898 | 1.7756 | 0.2958
16899 | 1.7755 | 0.29581
16900 | 1.7755 | 0.29583
16901 | 1.7755 | 0.29584
16902 | 1.7755 | 0.29586
16903 | 1.7755 | 0.29587
16904 | 1.7755 | 0.29589
16905 | 1.7754 | 0.2959
16906 | 1.7754 | 0.29592
16907 | 1.7754 | 0.29593
16908 | 1.7754 | 0.29595
16909 | 1.7754 | 0.29596
16910 | 1.7754 | 0.29598
16911 | 1.7753 | 0.29599
16912 | 1.7753 | 0.29601
16913 | 1.7753 | 0.29602
16914 | 1.7753 | 0.29604
16915 | 1.7753 | 0.29605
16916 | 1.7753 | 0.29607
16917 | 1.7752 | 0.29608
16918 | 1.7752 | 0.2961
16919 | 1.7752 | 0.29611
16920 | 1.7752 | 0.29613
16921 | 1.7752 | 0.29615
16922 | 1.7752 | 0.29616
16923 | 1.7751 | 0.29618
16924 | 1.7751 | 0.29619
16925 | 1.7751 | 0.29621
16926 | 1.7751 | 0.29622
16927 | 1.7751 | 0.29624
16928 | 1.7751 | 0.29625
16929 | 1.7751 | 0.29627
16930 | 1.775 | 0.29628
16931 | 1.775 | 0.2963
16932 | 1.775 | 0.29631
16933 | 1.775 | 0.29633
16934 | 1.775 | 0.29634
16935 | 1.775 | 0.29636
16936 | 1.7749 | 0.29637
16937 | 1.7749 | 0.29639
16938 | 1.7749 | 0.2964
16939 | 1.7749 | 0.29642
16940 | 1.7749 | 0.29643
16941 | 1.7749 | 0.29645
16942 | 1.7748 | 0.29646
16943 | 1.7748 | 0.29648
16944 | 1.7748 | 0.2965
16945 | 1.7748 | 0.29651
16946 | 1.7748 | 0.29653
16947 | 1.7748 | 0.29654
16948 | 1.7747 | 0.29656
16949 | 1.7747 | 0.29657
16950 | 1.7747 | 0.29659
16951 | 1.7747 | 0.2966
16952 | 1.7747 | 0.29662
16953 | 1.7747 | 0.29663
16954 | 1.7746 | 0.29665
16955 | 1.7746 | 0.29666
16956 | 1.7746 | 0.29668
16957 | 1.7746 | 0.29669
16958 | 1.7746 | 0.29671
16959 | 1.7746 | 0.29672
16960 | 1.7745 | 0.29674
16961 | 1.7745 | 0.29675
16962 | 1.7745 | 0.29677
16963 | 1.7745 | 0.29678
16964 | 1.7745 | 0.2968
16965 | 1.7745 | 0.29681
16966 | 1.7744 | 0.29683
16967 | 1.7744 | 0.29685
16968 | 1.7744 | 0.29686
16969 | 1.7744 | 0.29688
16970 | 1.7744 | 0.29689
16971 | 1.7744 | 0.29691
16972 | 1.7743 | 0.29692
16973 | 1.7743 | 0.29694
16974 | 1.7743 | 0.29695
16975 | 1.7743 | 0.29697
16976 | 1.7743 | 0.29698
16977 | 1.7743 | 0.297
16978 | 1.7742 | 0.29701
16979 | 1.7742 | 0.29703
16980 | 1.7742 | 0.29704
16981 | 1.7742 | 0.29706
16982 | 1.7742 | 0.29707
16983 | 1.7742 | 0.29709
16984 | 1.7741 | 0.2971
16985 | 1.7741 | 0.29712
16986 | 1.7741 | 0.29713
16987 | 1.7741 | 0.29715
16988 | 1.7741 | 0.29716
16989 | 1.7741 | 0.29718
16990 | 1.774 | 0.29719
16991 | 1.774 | 0.29721
16992 | 1.774 | 0.29723
16993 | 1.774 | 0.29724
16994 | 1.774 | 0.29726
16995 | 1.774 | 0.29727
16996 | 1.7739 | 0.29729
16997 | 1.7739 | 0.2973
16998 | 1.7739 | 0.29732
16999 | 1.7739 | 0.29733
17000 | 1.7739 | 0.29735
17001 | 1.7739 | 0.29736
17002 | 1.7738 | 0.29738
17003 | 1.7738 | 0.29739
17004 | 1.7738 | 0.29741
17005 | 1.7738 | 0.29742
17006 | 1.7738 | 0.29744
17007 | 1.7738 | 0.29745
17008 | 1.7737 | 0.29747
17009 | 1.7737 | 0.29748
17010 | 1.7737 | 0.2975
17011 | 1.7737 | 0.29751
17012 | 1.7737 | 0.29753
17013 | 1.7737 | 0.29754
17014 | 1.7736 | 0.29756
17015 | 1.7736 | 0.29757
17016 | 1.7736 | 0.29759
17017 | 1.7736 | 0.29761
17018 | 1.7736 | 0.29762
17019 | 1.7736 | 0.29764
17020 | 1.7735 | 0.29765
17021 | 1.7735 | 0.29767
17022 | 1.7735 | 0.29768
17023 | 1.7735 | 0.2977
17024 | 1.7735 | 0.29771
17025 | 1.7735 | 0.29773
17026 | 1.7734 | 0.29774
17027 | 1.7734 | 0.29776
17028 | 1.7734 | 0.29777
17029 | 1.7734 | 0.29779
17030 | 1.7734 | 0.2978
17031 | 1.7734 | 0.29782
17032 | 1.7733 | 0.29783
17033 | 1.7733 | 0.29785
17034 | 1.7733 | 0.29786
17035 | 1.7733 | 0.29788
17036 | 1.7733 | 0.29789
17037 | 1.7733 | 0.29791
17038 | 1.7732 | 0.29792
17039 | 1.7732 | 0.29794
17040 | 1.7732 | 0.29795
17041 | 1.7732 | 0.29797
17042 | 1.7732 | 0.29799
17043 | 1.7732 | 0.298
17044 | 1.7731 | 0.29802
17045 | 1.7731 | 0.29803
17046 | 1.7731 | 0.29805
17047 | 1.7731 | 0.29806
17048 | 1.7731 | 0.29808
17049 | 1.7731 | 0.29809
17050 | 1.7731 | 0.29811
17051 | 1.773 | 0.29812
17052 | 1.773 | 0.29814
17053 | 1.773 | 0.29815
17054 | 1.773 | 0.29817
17055 | 1.773 | 0.29818
17056 | 1.773 | 0.2982
17057 | 1.7729 | 0.29821
17058 | 1.7729 | 0.29823
17059 | 1.7729 | 0.29824
17060 | 1.7729 | 0.29826
17061 | 1.7729 | 0.29827
17062 | 1.7729 | 0.29829
17063 | 1.7728 | 0.2983
17064 | 1.7728 | 0.29832
17065 | 1.7728 | 0.29833
17066 | 1.7728 | 0.29835
17067 | 1.7728 | 0.29836
17068 | 1.7728 | 0.29838
17069 | 1.7727 | 0.2984
17070 | 1.7727 | 0.29841
17071 | 1.7727 | 0.29843
17072 | 1.7727 | 0.29844
17073 | 1.7727 | 0.29846
17074 | 1.7727 | 0.29847
17075 | 1.7726 | 0.29849
17076 | 1.7726 | 0.2985
17077 | 1.7726 | 0.29852
17078 | 1.7726 | 0.29853
17079 | 1.7726 | 0.29855
17080 | 1.7726 | 0.29856
17081 | 1.7725 | 0.29858
17082 | 1.7725 | 0.29859
17083 | 1.7725 | 0.29861
17084 | 1.7725 | 0.29862
17085 | 1.7725 | 0.29864
17086 | 1.7725 | 0.29865
17087 | 1.7724 | 0.29867
17088 | 1.7724 | 0.29868
17089 | 1.7724 | 0.2987
17090 | 1.7724 | 0.29871
17091 | 1.7724 | 0.29873
17092 | 1.7724 | 0.29874
17093 | 1.7723 | 0.29876
17094 | 1.7723 | 0.29877
17095 | 1.7723 | 0.29879
17096 | 1.7723 | 0.29881
17097 | 1.7723 | 0.29882
17098 | 1.7723 | 0.29884
17099 | 1.7722 | 0.29885
17100 | 1.7722 | 0.29887
17101 | 1.7722 | 0.29888
17102 | 1.7722 | 0.2989
17103 | 1.7722 | 0.29891
17104 | 1.7722 | 0.29893
17105 | 1.7721 | 0.29894
17106 | 1.7721 | 0.29896
17107 | 1.7721 | 0.29897
17108 | 1.7721 | 0.29899
17109 | 1.7721 | 0.299
17110 | 1.7721 | 0.29902
17111 | 1.772 | 0.29903
17112 | 1.772 | 0.29905
17113 | 1.772 | 0.29906
17114 | 1.772 | 0.29908
17115 | 1.772 | 0.29909
17116 | 1.772 | 0.29911
17117 | 1.7719 | 0.29912
17118 | 1.7719 | 0.29914
17119 | 1.7719 | 0.29915
17120 | 1.7719 | 0.29917
17121 | 1.7719 | 0.29918
17122 | 1.7719 | 0.2992
17123 | 1.7718 | 0.29922
17124 | 1.7718 | 0.29923
17125 | 1.7718 | 0.29925
17126 | 1.7718 | 0.29926
17127 | 1.7718 | 0.29928
17128 | 1.7718 | 0.29929
17129 | 1.7717 | 0.29931
17130 | 1.7717 | 0.29932
17131 | 1.7717 | 0.29934
17132 | 1.7717 | 0.29935
17133 | 1.7717 | 0.29937
17134 | 1.7717 | 0.29938
17135 | 1.7717 | 0.2994
17136 | 1.7716 | 0.29941
17137 | 1.7716 | 0.29943
17138 | 1.7716 | 0.29944
17139 | 1.7716 | 0.29946
17140 | 1.7716 | 0.29947
17141 | 1.7716 | 0.29949
17142 | 1.7715 | 0.2995
17143 | 1.7715 | 0.29952
17144 | 1.7715 | 0.29953
17145 | 1.7715 | 0.29955
17146 | 1.7715 | 0.29956
17147 | 1.7715 | 0.29958
17148 | 1.7714 | 0.29959
17149 | 1.7714 | 0.29961
17150 | 1.7714 | 0.29962
17151 | 1.7714 | 0.29964
17152 | 1.7714 | 0.29966
17153 | 1.7714 | 0.29967
17154 | 1.7713 | 0.29969
17155 | 1.7713 | 0.2997
17156 | 1.7713 | 0.29972
17157 | 1.7713 | 0.29973
17158 | 1.7713 | 0.29975
17159 | 1.7713 | 0.29976
17160 | 1.7712 | 0.29978
17161 | 1.7712 | 0.29979
17162 | 1.7712 | 0.29981
17163 | 1.7712 | 0.29982
17164 | 1.7712 | 0.29984
17165 | 1.7712 | 0.29985
17166 | 1.7711 | 0.29987
17167 | 1.7711 | 0.29988
17168 | 1.7711 | 0.2999
17169 | 1.7711 | 0.29991
17170 | 1.7711 | 0.29993
17171 | 1.7711 | 0.29994
17172 | 1.771 | 0.29996
17173 | 1.771 | 0.29997
17174 | 1.771 | 0.29999
17175 | 1.771 | 0.3
17176 | 1.771 | 0.30002
17177 | 1.771 | 0.30003
17178 | 1.7709 | 0.30005
17179 | 1.7709 | 0.30006
17180 | 1.7709 | 0.30008
17181 | 1.7709 | 0.3001
17182 | 1.7709 | 0.30011
17183 | 1.7709 | 0.30013
17184 | 1.7708 | 0.30014
17185 | 1.7708 | 0.30016
17186 | 1.7708 | 0.30017
17187 | 1.7708 | 0.30019
17188 | 1.7708 | 0.3002
17189 | 1.7708 | 0.30022
17190 | 1.7707 | 0.30023
17191 | 1.7707 | 0.30025
17192 | 1.7707 | 0.30026
17193 | 1.7707 | 0.30028
17194 | 1.7707 | 0.30029
17195 | 1.7707 | 0.30031
17196 | 1.7706 | 0.30032
17197 | 1.7706 | 0.30034
17198 | 1.7706 | 0.30035
17199 | 1.7706 | 0.30037
17200 | 1.7706 | 0.30038
17201 | 1.7706 | 0.3004
17202 | 1.7706 | 0.30041
17203 | 1.7705 | 0.30043
17204 | 1.7705 | 0.30044
17205 | 1.7705 | 0.30046
17206 | 1.7705 | 0.30047
17207 | 1.7705 | 0.30049
17208 | 1.7705 | 0.3005
17209 | 1.7704 | 0.30052
17210 | 1.7704 | 0.30053
17211 | 1.7704 | 0.30055
17212 | 1.7704 | 0.30057
17213 | 1.7704 | 0.30058
17214 | 1.7704 | 0.3006
17215 | 1.7703 | 0.30061
17216 | 1.7703 | 0.30063
17217 | 1.7703 | 0.30064
17218 | 1.7703 | 0.30066
17219 | 1.7703 | 0.30067
17220 | 1.7703 | 0.30069
17221 | 1.7702 | 0.3007
17222 | 1.7702 | 0.30072
17223 | 1.7702 | 0.30073
17224 | 1.7702 | 0.30075
17225 | 1.7702 | 0.30076
17226 | 1.7702 | 0.30078
17227 | 1.7701 | 0.30079
17228 | 1.7701 | 0.30081
17229 | 1.7701 | 0.30082
17230 | 1.7701 | 0.30084
17231 | 1.7701 | 0.30085
17232 | 1.7701 | 0.30087
17233 | 1.77 | 0.30088
17234 | 1.77 | 0.3009
17235 | 1.77 | 0.30091
17236 | 1.77 | 0.30093
17237 | 1.77 | 0.30094
17238 | 1.77 | 0.30096
17239 | 1.7699 | 0.30097
17240 | 1.7699 | 0.30099
17241 | 1.7699 | 0.301
17242 | 1.7699 | 0.30102
17243 | 1.7699 | 0.30103
17244 | 1.7699 | 0.30105
17245 | 1.7698 | 0.30107
17246 | 1.7698 | 0.30108
17247 | 1.7698 | 0.3011
17248 | 1.7698 | 0.30111
17249 | 1.7698 | 0.30113
17250 | 1.7698 | 0.30114
17251 | 1.7697 | 0.30116
17252 | 1.7697 | 0.30117
17253 | 1.7697 | 0.30119
17254 | 1.7697 | 0.3012
17255 | 1.7697 | 0.30122
17256 | 1.7697 | 0.30123
17257 | 1.7697 | 0.30125
17258 | 1.7696 | 0.30126
17259 | 1.7696 | 0.30128
17260 | 1.7696 | 0.30129
17261 | 1.7696 | 0.30131
17262 | 1.7696 | 0.30132
17263 | 1.7696 | 0.30134
17264 | 1.7695 | 0.30135
17265 | 1.7695 | 0.30137
17266 | 1.7695 | 0.30138
17267 | 1.7695 | 0.3014
17268 | 1.7695 | 0.30141
17269 | 1.7695 | 0.30143
17270 | 1.7694 | 0.30144
17271 | 1.7694 | 0.30146
17272 | 1.7694 | 0.30147
17273 | 1.7694 | 0.30149
17274 | 1.7694 | 0.3015
17275 | 1.7694 | 0.30152
17276 | 1.7693 | 0.30153
17277 | 1.7693 | 0.30155
17278 | 1.7693 | 0.30157
17279 | 1.7693 | 0.30158
17280 | 1.7693 | 0.3016
17281 | 1.7693 | 0.30161
17282 | 1.7692 | 0.30163
17283 | 1.7692 | 0.30164
17284 | 1.7692 | 0.30166
17285 | 1.7692 | 0.30167
17286 | 1.7692 | 0.30169
17287 | 1.7692 | 0.3017
17288 | 1.7691 | 0.30172
17289 | 1.7691 | 0.30173
17290 | 1.7691 | 0.30175
17291 | 1.7691 | 0.30176
17292 | 1.7691 | 0.30178
17293 | 1.7691 | 0.30179
17294 | 1.769 | 0.30181
17295 | 1.769 | 0.30182
17296 | 1.769 | 0.30184
17297 | 1.769 | 0.30185
17298 | 1.769 | 0.30187
17299 | 1.769 | 0.30188
17300 | 1.7689 | 0.3019
17301 | 1.7689 | 0.30191
17302 | 1.7689 | 0.30193
17303 | 1.7689 | 0.30194
17304 | 1.7689 | 0.30196
17305 | 1.7689 | 0.30197
17306 | 1.7688 | 0.30199
17307 | 1.7688 | 0.302
17308 | 1.7688 | 0.30202
17309 | 1.7688 | 0.30203
17310 | 1.7688 | 0.30205
17311 | 1.7688 | 0.30206
17312 | 1.7688 | 0.30208
17313 | 1.7687 | 0.3021
17314 | 1.7687 | 0.30211
17315 | 1.7687 | 0.30213
17316 | 1.7687 | 0.30214
17317 | 1.7687 | 0.30216
17318 | 1.7687 | 0.30217
17319 | 1.7686 | 0.30219
17320 | 1.7686 | 0.3022
17321 | 1.7686 | 0.30222
17322 | 1.7686 | 0.30223
17323 | 1.7686 | 0.30225
17324 | 1.7686 | 0.30226
17325 | 1.7685 | 0.30228
17326 | 1.7685 | 0.30229
17327 | 1.7685 | 0.30231
17328 | 1.7685 | 0.30232
17329 | 1.7685 | 0.30234
17330 | 1.7685 | 0.30235
17331 | 1.7684 | 0.30237
17332 | 1.7684 | 0.30238
17333 | 1.7684 | 0.3024
17334 | 1.7684 | 0.30241
17335 | 1.7684 | 0.30243
17336 | 1.7684 | 0.30244
17337 | 1.7683 | 0.30246
17338 | 1.7683 | 0.30247
17339 | 1.7683 | 0.30249
17340 | 1.7683 | 0.3025
17341 | 1.7683 | 0.30252
17342 | 1.7683 | 0.30253
17343 | 1.7682 | 0.30255
17344 | 1.7682 | 0.30256
17345 | 1.7682 | 0.30258
17346 | 1.7682 | 0.30259
17347 | 1.7682 | 0.30261
17348 | 1.7682 | 0.30262
17349 | 1.7681 | 0.30264
17350 | 1.7681 | 0.30265
17351 | 1.7681 | 0.30267
17352 | 1.7681 | 0.30269
17353 | 1.7681 | 0.3027
17354 | 1.7681 | 0.30272
17355 | 1.768 | 0.30273
17356 | 1.768 | 0.30275
17357 | 1.768 | 0.30276
17358 | 1.768 | 0.30278
17359 | 1.768 | 0.30279
17360 | 1.768 | 0.30281
17361 | 1.768 | 0.30282
17362 | 1.7679 | 0.30284
17363 | 1.7679 | 0.30285
17364 | 1.7679 | 0.30287
17365 | 1.7679 | 0.30288
17366 | 1.7679 | 0.3029
17367 | 1.7679 | 0.30291
17368 | 1.7678 | 0.30293
17369 | 1.7678 | 0.30294
17370 | 1.7678 | 0.30296
17371 | 1.7678 | 0.30297
17372 | 1.7678 | 0.30299
17373 | 1.7678 | 0.303
17374 | 1.7677 | 0.30302
17375 | 1.7677 | 0.30303
17376 | 1.7677 | 0.30305
17377 | 1.7677 | 0.30306
17378 | 1.7677 | 0.30308
17379 | 1.7677 | 0.30309
17380 | 1.7676 | 0.30311
17381 | 1.7676 | 0.30312
17382 | 1.7676 | 0.30314
17383 | 1.7676 | 0.30315
17384 | 1.7676 | 0.30317
17385 | 1.7676 | 0.30318
17386 | 1.7675 | 0.3032
17387 | 1.7675 | 0.30321
17388 | 1.7675 | 0.30323
17389 | 1.7675 | 0.30324
17390 | 1.7675 | 0.30326
17391 | 1.7675 | 0.30328
17392 | 1.7674 | 0.30329
17393 | 1.7674 | 0.30331
17394 | 1.7674 | 0.30332
17395 | 1.7674 | 0.30334
17396 | 1.7674 | 0.30335
17397 | 1.7674 | 0.30337
17398 | 1.7673 | 0.30338
17399 | 1.7673 | 0.3034
17400 | 1.7673 | 0.30341
17401 | 1.7673 | 0.30343
17402 | 1.7673 | 0.30344
17403 | 1.7673 | 0.30346
17404 | 1.7673 | 0.30347
17405 | 1.7672 | 0.30349
17406 | 1.7672 | 0.3035
17407 | 1.7672 | 0.30352
17408 | 1.7672 | 0.30353
17409 | 1.7672 | 0.30355
17410 | 1.7672 | 0.30356
17411 | 1.7671 | 0.30358
17412 | 1.7671 | 0.30359
17413 | 1.7671 | 0.30361
17414 | 1.7671 | 0.30362
17415 | 1.7671 | 0.30364
17416 | 1.7671 | 0.30365
17417 | 1.767 | 0.30367
17418 | 1.767 | 0.30368
17419 | 1.767 | 0.3037
17420 | 1.767 | 0.30371
17421 | 1.767 | 0.30373
17422 | 1.767 | 0.30374
17423 | 1.7669 | 0.30376
17424 | 1.7669 | 0.30377
17425 | 1.7669 | 0.30379
17426 | 1.7669 | 0.3038
17427 | 1.7669 | 0.30382
17428 | 1.7669 | 0.30383
17429 | 1.7668 | 0.30385
17430 | 1.7668 | 0.30386
17431 | 1.7668 | 0.30388
17432 | 1.7668 | 0.30389
17433 | 1.7668 | 0.30391
17434 | 1.7668 | 0.30393
17435 | 1.7667 | 0.30394
17436 | 1.7667 | 0.30396
17437 | 1.7667 | 0.30397
17438 | 1.7667 | 0.30399
17439 | 1.7667 | 0.304
17440 | 1.7667 | 0.30402
17441 | 1.7667 | 0.30403
17442 | 1.7666 | 0.30405
17443 | 1.7666 | 0.30406
17444 | 1.7666 | 0.30408
17445 | 1.7666 | 0.30409
17446 | 1.7666 | 0.30411
17447 | 1.7666 | 0.30412
17448 | 1.7665 | 0.30414
17449 | 1.7665 | 0.30415
17450 | 1.7665 | 0.30417
17451 | 1.7665 | 0.30418
17452 | 1.7665 | 0.3042
17453 | 1.7665 | 0.30421
17454 | 1.7664 | 0.30423
17455 | 1.7664 | 0.30424
17456 | 1.7664 | 0.30426
17457 | 1.7664 | 0.30427
17458 | 1.7664 | 0.30429
17459 | 1.7664 | 0.3043
17460 | 1.7663 | 0.30432
17461 | 1.7663 | 0.30433
17462 | 1.7663 | 0.30435
17463 | 1.7663 | 0.30436
17464 | 1.7663 | 0.30438
17465 | 1.7663 | 0.30439
17466 | 1.7662 | 0.30441
17467 | 1.7662 | 0.30442
17468 | 1.7662 | 0.30444
17469 | 1.7662 | 0.30445
17470 | 1.7662 | 0.30447
17471 | 1.7662 | 0.30448
17472 | 1.7661 | 0.3045
17473 | 1.7661 | 0.30451
17474 | 1.7661 | 0.30453
17475 | 1.7661 | 0.30454
17476 | 1.7661 | 0.30456
17477 | 1.7661 | 0.30457
17478 | 1.766 | 0.30459
17479 | 1.766 | 0.3046
17480 | 1.766 | 0.30462
17481 | 1.766 | 0.30464
17482 | 1.766 | 0.30465
17483 | 1.766 | 0.30467
17484 | 1.766 | 0.30468
17485 | 1.7659 | 0.3047
17486 | 1.7659 | 0.30471
17487 | 1.7659 | 0.30473
17488 | 1.7659 | 0.30474
17489 | 1.7659 | 0.30476
17490 | 1.7659 | 0.30477
17491 | 1.7658 | 0.30479
17492 | 1.7658 | 0.3048
17493 | 1.7658 | 0.30482
17494 | 1.7658 | 0.30483
17495 | 1.7658 | 0.30485
17496 | 1.7658 | 0.30486
17497 | 1.7657 | 0.30488
17498 | 1.7657 | 0.30489
17499 | 1.7657 | 0.30491
17500 | 1.7657 | 0.30492
17501 | 1.7657 | 0.30494
17502 | 1.7657 | 0.30495
17503 | 1.7656 | 0.30497
17504 | 1.7656 | 0.30498
17505 | 1.7656 | 0.305
17506 | 1.7656 | 0.30501
17507 | 1.7656 | 0.30503
17508 | 1.7656 | 0.30504
17509 | 1.7655 | 0.30506
17510 | 1.7655 | 0.30507
17511 | 1.7655 | 0.30509
17512 | 1.7655 | 0.3051
17513 | 1.7655 | 0.30512
17514 | 1.7655 | 0.30513
17515 | 1.7654 | 0.30515
17516 | 1.7654 | 0.30516
17517 | 1.7654 | 0.30518
17518 | 1.7654 | 0.30519
17519 | 1.7654 | 0.30521
17520 | 1.7654 | 0.30522
17521 | 1.7654 | 0.30524
17522 | 1.7653 | 0.30525
17523 | 1.7653 | 0.30527
17524 | 1.7653 | 0.30528
17525 | 1.7653 | 0.3053
17526 | 1.7653 | 0.30531
17527 | 1.7653 | 0.30533
17528 | 1.7652 | 0.30534
17529 | 1.7652 | 0.30536
17530 | 1.7652 | 0.30537
17531 | 1.7652 | 0.30539
17532 | 1.7652 | 0.30541
17533 | 1.7652 | 0.30542
17534 | 1.7651 | 0.30544
17535 | 1.7651 | 0.30545
17536 | 1.7651 | 0.30547
17537 | 1.7651 | 0.30548
17538 | 1.7651 | 0.3055
17539 | 1.7651 | 0.30551
17540 | 1.765 | 0.30553
17541 | 1.765 | 0.30554
17542 | 1.765 | 0.30556
17543 | 1.765 | 0.30557
17544 | 1.765 | 0.30559
17545 | 1.765 | 0.3056
17546 | 1.7649 | 0.30562
17547 | 1.7649 | 0.30563
17548 | 1.7649 | 0.30565
17549 | 1.7649 | 0.30566
17550 | 1.7649 | 0.30568
17551 | 1.7649 | 0.30569
17552 | 1.7649 | 0.30571
17553 | 1.7648 | 0.30572
17554 | 1.7648 | 0.30574
17555 | 1.7648 | 0.30575
17556 | 1.7648 | 0.30577
17557 | 1.7648 | 0.30578
17558 | 1.7648 | 0.3058
17559 | 1.7647 | 0.30581
17560 | 1.7647 | 0.30583
17561 | 1.7647 | 0.30584
17562 | 1.7647 | 0.30586
17563 | 1.7647 | 0.30587
17564 | 1.7647 | 0.30589
17565 | 1.7646 | 0.3059
17566 | 1.7646 | 0.30592
17567 | 1.7646 | 0.30593
17568 | 1.7646 | 0.30595
17569 | 1.7646 | 0.30596
17570 | 1.7646 | 0.30598
17571 | 1.7645 | 0.30599
17572 | 1.7645 | 0.30601
17573 | 1.7645 | 0.30602
17574 | 1.7645 | 0.30604
17575 | 1.7645 | 0.30605
17576 | 1.7645 | 0.30607
17577 | 1.7644 | 0.30608
17578 | 1.7644 | 0.3061
17579 | 1.7644 | 0.30611
17580 | 1.7644 | 0.30613
17581 | 1.7644 | 0.30614
17582 | 1.7644 | 0.30616
17583 | 1.7643 | 0.30617
17584 | 1.7643 | 0.30619
17585 | 1.7643 | 0.3062
17586 | 1.7643 | 0.30622
17587 | 1.7643 | 0.30623
17588 | 1.7643 | 0.30625
17589 | 1.7643 | 0.30627
17590 | 1.7642 | 0.30628
17591 | 1.7642 | 0.3063
17592 | 1.7642 | 0.30631
17593 | 1.7642 | 0.30633
17594 | 1.7642 | 0.30634
17595 | 1.7642 | 0.30636
17596 | 1.7641 | 0.30637
17597 | 1.7641 | 0.30639
17598 | 1.7641 | 0.3064
17599 | 1.7641 | 0.30642
17600 | 1.7641 | 0.30643
17601 | 1.7641 | 0.30645
17602 | 1.764 | 0.30646
17603 | 1.764 | 0.30648
17604 | 1.764 | 0.30649
17605 | 1.764 | 0.30651
17606 | 1.764 | 0.30652
17607 | 1.764 | 0.30654
17608 | 1.7639 | 0.30655
17609 | 1.7639 | 0.30657
17610 | 1.7639 | 0.30658
17611 | 1.7639 | 0.3066
17612 | 1.7639 | 0.30661
17613 | 1.7639 | 0.30663
17614 | 1.7638 | 0.30664
17615 | 1.7638 | 0.30666
17616 | 1.7638 | 0.30667
17617 | 1.7638 | 0.30669
17618 | 1.7638 | 0.3067
17619 | 1.7638 | 0.30672
17620 | 1.7638 | 0.30673
17621 | 1.7637 | 0.30675
17622 | 1.7637 | 0.30676
17623 | 1.7637 | 0.30678
17624 | 1.7637 | 0.30679
17625 | 1.7637 | 0.30681
17626 | 1.7637 | 0.30682
17627 | 1.7636 | 0.30684
17628 | 1.7636 | 0.30685
17629 | 1.7636 | 0.30687
17630 | 1.7636 | 0.30688
17631 | 1.7636 | 0.3069
17632 | 1.7636 | 0.30691
17633 | 1.7635 | 0.30693
17634 | 1.7635 | 0.30694
17635 | 1.7635 | 0.30696
17636 | 1.7635 | 0.30697
17637 | 1.7635 | 0.30699
17638 | 1.7635 | 0.307
17639 | 1.7634 | 0.30702
17640 | 1.7634 | 0.30703
17641 | 1.7634 | 0.30705
17642 | 1.7634 | 0.30706
17643 | 1.7634 | 0.30708
17644 | 1.7634 | 0.30709
17645 | 1.7633 | 0.30711
17646 | 1.7633 | 0.30712
17647 | 1.7633 | 0.30714
17648 | 1.7633 | 0.30715
17649 | 1.7633 | 0.30717
17650 | 1.7633 | 0.30718
17651 | 1.7633 | 0.3072
17652 | 1.7632 | 0.30721
17653 | 1.7632 | 0.30723
17654 | 1.7632 | 0.30724
17655 | 1.7632 | 0.30726
17656 | 1.7632 | 0.30728
17657 | 1.7632 | 0.30729
17658 | 1.7631 | 0.30731
17659 | 1.7631 | 0.30732
17660 | 1.7631 | 0.30734
17661 | 1.7631 | 0.30735
17662 | 1.7631 | 0.30737
17663 | 1.7631 | 0.30738
17664 | 1.763 | 0.3074
17665 | 1.763 | 0.30741
17666 | 1.763 | 0.30743
17667 | 1.763 | 0.30744
17668 | 1.763 | 0.30746
17669 | 1.763 | 0.30747
17670 | 1.7629 | 0.30749
17671 | 1.7629 | 0.3075
17672 | 1.7629 | 0.30752
17673 | 1.7629 | 0.30753
17674 | 1.7629 | 0.30755
17675 | 1.7629 | 0.30756
17676 | 1.7628 | 0.30758
17677 | 1.7628 | 0.30759
17678 | 1.7628 | 0.30761
17679 | 1.7628 | 0.30762
17680 | 1.7628 | 0.30764
17681 | 1.7628 | 0.30765
17682 | 1.7628 | 0.30767
17683 | 1.7627 | 0.30768
17684 | 1.7627 | 0.3077
17685 | 1.7627 | 0.30771
17686 | 1.7627 | 0.30773
17687 | 1.7627 | 0.30774
17688 | 1.7627 | 0.30776
17689 | 1.7626 | 0.30777
17690 | 1.7626 | 0.30779
17691 | 1.7626 | 0.3078
17692 | 1.7626 | 0.30782
17693 | 1.7626 | 0.30783
17694 | 1.7626 | 0.30785
17695 | 1.7625 | 0.30786
17696 | 1.7625 | 0.30788
17697 | 1.7625 | 0.30789
17698 | 1.7625 | 0.30791
17699 | 1.7625 | 0.30792
17700 | 1.7625 | 0.30794
17701 | 1.7624 | 0.30795
17702 | 1.7624 | 0.30797
17703 | 1.7624 | 0.30798
17704 | 1.7624 | 0.308
17705 | 1.7624 | 0.30801
17706 | 1.7624 | 0.30803
17707 | 1.7623 | 0.30804
17708 | 1.7623 | 0.30806
17709 | 1.7623 | 0.30807
17710 | 1.7623 | 0.30809
17711 | 1.7623 | 0.3081
17712 | 1.7623 | 0.30812
17713 | 1.7623 | 0.30813
17714 | 1.7622 | 0.30815
17715 | 1.7622 | 0.30816
17716 | 1.7622 | 0.30818
17717 | 1.7622 | 0.30819
17718 | 1.7622 | 0.30821
17719 | 1.7622 | 0.30822
17720 | 1.7621 | 0.30824
17721 | 1.7621 | 0.30825
17722 | 1.7621 | 0.30827
17723 | 1.7621 | 0.30828
17724 | 1.7621 | 0.3083
17725 | 1.7621 | 0.30831
17726 | 1.762 | 0.30833
17727 | 1.762 | 0.30834
17728 | 1.762 | 0.30836
17729 | 1.762 | 0.30837
17730 | 1.762 | 0.30839
17731 | 1.762 | 0.3084
17732 | 1.7619 | 0.30842
17733 | 1.7619 | 0.30843
17734 | 1.7619 | 0.30845
17735 | 1.7619 | 0.30846
17736 | 1.7619 | 0.30848
17737 | 1.7619 | 0.30849
17738 | 1.7619 | 0.30851
17739 | 1.7618 | 0.30852
17740 | 1.7618 | 0.30854
17741 | 1.7618 | 0.30855
17742 | 1.7618 | 0.30857
17743 | 1.7618 | 0.30859
17744 | 1.7618 | 0.3086
17745 | 1.7617 | 0.30862
17746 | 1.7617 | 0.30863
17747 | 1.7617 | 0.30865
17748 | 1.7617 | 0.30866
17749 | 1.7617 | 0.30868
17750 | 1.7617 | 0.30869
17751 | 1.7616 | 0.30871
17752 | 1.7616 | 0.30872
17753 | 1.7616 | 0.30874
17754 | 1.7616 | 0.30875
17755 | 1.7616 | 0.30877
17756 | 1.7616 | 0.30878
17757 | 1.7615 | 0.3088
17758 | 1.7615 | 0.30881
17759 | 1.7615 | 0.30883
17760 | 1.7615 | 0.30884
17761 | 1.7615 | 0.30886
17762 | 1.7615 | 0.30887
17763 | 1.7614 | 0.30889
17764 | 1.7614 | 0.3089
17765 | 1.7614 | 0.30892
17766 | 1.7614 | 0.30893
17767 | 1.7614 | 0.30895
17768 | 1.7614 | 0.30896
17769 | 1.7614 | 0.30898
17770 | 1.7613 | 0.30899
17771 | 1.7613 | 0.30901
17772 | 1.7613 | 0.30902
17773 | 1.7613 | 0.30904
17774 | 1.7613 | 0.30905
17775 | 1.7613 | 0.30907
17776 | 1.7612 | 0.30908
17777 | 1.7612 | 0.3091
17778 | 1.7612 | 0.30911
17779 | 1.7612 | 0.30913
17780 | 1.7612 | 0.30914
17781 | 1.7612 | 0.30916
17782 | 1.7611 | 0.30917
17783 | 1.7611 | 0.30919
17784 | 1.7611 | 0.3092
17785 | 1.7611 | 0.30922
17786 | 1.7611 | 0.30923
17787 | 1.7611 | 0.30925
17788 | 1.761 | 0.30926
17789 | 1.761 | 0.30928
17790 | 1.761 | 0.30929
17791 | 1.761 | 0.30931
17792 | 1.761 | 0.30932
17793 | 1.761 | 0.30934
17794 | 1.761 | 0.30935
17795 | 1.7609 | 0.30937
17796 | 1.7609 | 0.30938
17797 | 1.7609 | 0.3094
17798 | 1.7609 | 0.30941
17799 | 1.7609 | 0.30943
17800 | 1.7609 | 0.30944
17801 | 1.7608 | 0.30946
17802 | 1.7608 | 0.30947
17803 | 1.7608 | 0.30949
17804 | 1.7608 | 0.3095
17805 | 1.7608 | 0.30952
17806 | 1.7608 | 0.30953
17807 | 1.7607 | 0.30955
17808 | 1.7607 | 0.30956
17809 | 1.7607 | 0.30958
17810 | 1.7607 | 0.30959
17811 | 1.7607 | 0.30961
17812 | 1.7607 | 0.30962
17813 | 1.7606 | 0.30964
17814 | 1.7606 | 0.30965
17815 | 1.7606 | 0.30967
17816 | 1.7606 | 0.30968
17817 | 1.7606 | 0.3097
17818 | 1.7606 | 0.30971
17819 | 1.7606 | 0.30973
17820 | 1.7605 | 0.30974
17821 | 1.7605 | 0.30976
17822 | 1.7605 | 0.30977
17823 | 1.7605 | 0.30979
17824 | 1.7605 | 0.3098
17825 | 1.7605 | 0.30982
17826 | 1.7604 | 0.30983
17827 | 1.7604 | 0.30985
17828 | 1.7604 | 0.30986
17829 | 1.7604 | 0.30988
17830 | 1.7604 | 0.30989
17831 | 1.7604 | 0.30991
17832 | 1.7603 | 0.30992
17833 | 1.7603 | 0.30994
17834 | 1.7603 | 0.30995
17835 | 1.7603 | 0.30997
17836 | 1.7603 | 0.30998
17837 | 1.7603 | 0.31
17838 | 1.7602 | 0.31001
17839 | 1.7602 | 0.31003
17840 | 1.7602 | 0.31004
17841 | 1.7602 | 0.31006
17842 | 1.7602 | 0.31007
17843 | 1.7602 | 0.31009
17844 | 1.7602 | 0.3101
17845 | 1.7601 | 0.31012
17846 | 1.7601 | 0.31013
17847 | 1.7601 | 0.31015
17848 | 1.7601 | 0.31016
17849 | 1.7601 | 0.31018
17850 | 1.7601 | 0.31019
17851 | 1.76 | 0.31021
17852 | 1.76 | 0.31022
17853 | 1.76 | 0.31024
17854 | 1.76 | 0.31025
17855 | 1.76 | 0.31027
17856 | 1.76 | 0.31028
17857 | 1.7599 | 0.3103
17858 | 1.7599 | 0.31031
17859 | 1.7599 | 0.31033
17860 | 1.7599 | 0.31034
17861 | 1.7599 | 0.31036
17862 | 1.7599 | 0.31037
17863 | 1.7598 | 0.31039
17864 | 1.7598 | 0.3104
17865 | 1.7598 | 0.31042
17866 | 1.7598 | 0.31043
17867 | 1.7598 | 0.31045
17868 | 1.7598 | 0.31046
17869 | 1.7598 | 0.31048
17870 | 1.7597 | 0.31049
17871 | 1.7597 | 0.31051
17872 | 1.7597 | 0.31052
17873 | 1.7597 | 0.31054
17874 | 1.7597 | 0.31055
17875 | 1.7597 | 0.31057
17876 | 1.7596 | 0.31058
17877 | 1.7596 | 0.3106
17878 | 1.7596 | 0.31061
17879 | 1.7596 | 0.31063
17880 | 1.7596 | 0.31064
17881 | 1.7596 | 0.31066
17882 | 1.7595 | 0.31067
17883 | 1.7595 | 0.31069
17884 | 1.7595 | 0.3107
17885 | 1.7595 | 0.31072
17886 | 1.7595 | 0.31073
17887 | 1.7595 | 0.31075
17888 | 1.7594 | 0.31077
17889 | 1.7594 | 0.31078
17890 | 1.7594 | 0.3108
17891 | 1.7594 | 0.31081
17892 | 1.7594 | 0.31083
17893 | 1.7594 | 0.31084
17894 | 1.7594 | 0.31086
17895 | 1.7593 | 0.31087
17896 | 1.7593 | 0.31089
17897 | 1.7593 | 0.3109
17898 | 1.7593 | 0.31092
17899 | 1.7593 | 0.31093
17900 | 1.7593 | 0.31095
17901 | 1.7592 | 0.31096
17902 | 1.7592 | 0.31098
17903 | 1.7592 | 0.31099
17904 | 1.7592 | 0.31101
17905 | 1.7592 | 0.31102
17906 | 1.7592 | 0.31104
17907 | 1.7591 | 0.31105
17908 | 1.7591 | 0.31107
17909 | 1.7591 | 0.31108
17910 | 1.7591 | 0.3111
17911 | 1.7591 | 0.31111
17912 | 1.7591 | 0.31113
17913 | 1.759 | 0.31114
17914 | 1.759 | 0.31116
17915 | 1.759 | 0.31117
17916 | 1.759 | 0.31119
17917 | 1.759 | 0.3112
17918 | 1.759 | 0.31122
17919 | 1.759 | 0.31123
17920 | 1.7589 | 0.31125
17921 | 1.7589 | 0.31126
17922 | 1.7589 | 0.31128
17923 | 1.7589 | 0.31129
17924 | 1.7589 | 0.31131
17925 | 1.7589 | 0.31132
17926 | 1.7588 | 0.31134
17927 | 1.7588 | 0.31135
17928 | 1.7588 | 0.31137
17929 | 1.7588 | 0.31138
17930 | 1.7588 | 0.3114
17931 | 1.7588 | 0.31141
17932 | 1.7587 | 0.31143
17933 | 1.7587 | 0.31144
17934 | 1.7587 | 0.31146
17935 | 1.7587 | 0.31147
17936 | 1.7587 | 0.31149
17937 | 1.7587 | 0.3115
17938 | 1.7586 | 0.31152
17939 | 1.7586 | 0.31153
17940 | 1.7586 | 0.31155
17941 | 1.7586 | 0.31156
17942 | 1.7586 | 0.31158
17943 | 1.7586 | 0.31159
17944 | 1.7586 | 0.31161
17945 | 1.7585 | 0.31162
17946 | 1.7585 | 0.31164
17947 | 1.7585 | 0.31165
17948 | 1.7585 | 0.31167
17949 | 1.7585 | 0.31168
17950 | 1.7585 | 0.3117
17951 | 1.7584 | 0.31171
17952 | 1.7584 | 0.31173
17953 | 1.7584 | 0.31174
17954 | 1.7584 | 0.31176
17955 | 1.7584 | 0.31177
17956 | 1.7584 | 0.31179
17957 | 1.7583 | 0.3118
17958 | 1.7583 | 0.31182
17959 | 1.7583 | 0.31183
17960 | 1.7583 | 0.31185
17961 | 1.7583 | 0.31186
17962 | 1.7583 | 0.31188
17963 | 1.7583 | 0.31189
17964 | 1.7582 | 0.31191
17965 | 1.7582 | 0.31192
17966 | 1.7582 | 0.31194
17967 | 1.7582 | 0.31195
17968 | 1.7582 | 0.31197
17969 | 1.7582 | 0.31198
17970 | 1.7581 | 0.312
17971 | 1.7581 | 0.31201
17972 | 1.7581 | 0.31203
17973 | 1.7581 | 0.31204
17974 | 1.7581 | 0.31206
17975 | 1.7581 | 0.31207
17976 | 1.758 | 0.31209
17977 | 1.758 | 0.3121
17978 | 1.758 | 0.31212
17979 | 1.758 | 0.31213
17980 | 1.758 | 0.31215
17981 | 1.758 | 0.31216
17982 | 1.7579 | 0.31218
17983 | 1.7579 | 0.31219
17984 | 1.7579 | 0.31221
17985 | 1.7579 | 0.31222
17986 | 1.7579 | 0.31224
17987 | 1.7579 | 0.31225
17988 | 1.7579 | 0.31227
17989 | 1.7578 | 0.31228
17990 | 1.7578 | 0.3123
17991 | 1.7578 | 0.31231
17992 | 1.7578 | 0.31233
17993 | 1.7578 | 0.31234
17994 | 1.7578 | 0.31236
17995 | 1.7577 | 0.31237
17996 | 1.7577 | 0.31239
17997 | 1.7577 | 0.3124
17998 | 1.7577 | 0.31242
17999 | 1.7577 | 0.31243
18000 | 1.7577 | 0.31245
18001 | 1.7576 | 0.31246
18002 | 1.7576 | 0.31248
18003 | 1.7576 | 0.31249
18004 | 1.7576 | 0.31251
18005 | 1.7576 | 0.31252
18006 | 1.7576 | 0.31254
18007 | 1.7575 | 0.31255
18008 | 1.7575 | 0.31257
18009 | 1.7575 | 0.31258
18010 | 1.7575 | 0.3126
18011 | 1.7575 | 0.31261
18012 | 1.7575 | 0.31263
18013 | 1.7575 | 0.31264
18014 | 1.7574 | 0.31266
18015 | 1.7574 | 0.31267
18016 | 1.7574 | 0.31269
18017 | 1.7574 | 0.3127
18018 | 1.7574 | 0.31272
18019 | 1.7574 | 0.31273
18020 | 1.7573 | 0.31275
18021 | 1.7573 | 0.31276
18022 | 1.7573 | 0.31278
18023 | 1.7573 | 0.31279
18024 | 1.7573 | 0.31281
18025 | 1.7573 | 0.31282
18026 | 1.7572 | 0.31284
18027 | 1.7572 | 0.31285
18028 | 1.7572 | 0.31287
18029 | 1.7572 | 0.31288
18030 | 1.7572 | 0.3129
18031 | 1.7572 | 0.31291
18032 | 1.7572 | 0.31293
18033 | 1.7571 | 0.31294
18034 | 1.7571 | 0.31296
18035 | 1.7571 | 0.31297
18036 | 1.7571 | 0.31299
18037 | 1.7571 | 0.313
18038 | 1.7571 | 0.31302
18039 | 1.757 | 0.31303
18040 | 1.757 | 0.31305
18041 | 1.757 | 0.31306
18042 | 1.757 | 0.31308
18043 | 1.757 | 0.31309
18044 | 1.757 | 0.31311
18045 | 1.7569 | 0.31312
18046 | 1.7569 | 0.31314
18047 | 1.7569 | 0.31315
18048 | 1.7569 | 0.31317
18049 | 1.7569 | 0.31318
18050 | 1.7569 | 0.3132
18051 | 1.7568 | 0.31321
18052 | 1.7568 | 0.31323
18053 | 1.7568 | 0.31324
18054 | 1.7568 | 0.31326
18055 | 1.7568 | 0.31327
18056 | 1.7568 | 0.31329
18057 | 1.7568 | 0.3133
18058 | 1.7567 | 0.31332
18059 | 1.7567 | 0.31333
18060 | 1.7567 | 0.31335
18061 | 1.7567 | 0.31336
18062 | 1.7567 | 0.31338
18063 | 1.7567 | 0.31339
18064 | 1.7566 | 0.31341
18065 | 1.7566 | 0.31342
18066 | 1.7566 | 0.31344
18067 | 1.7566 | 0.31345
18068 | 1.7566 | 0.31347
18069 | 1.7566 | 0.31348
18070 | 1.7565 | 0.3135
18071 | 1.7565 | 0.31351
18072 | 1.7565 | 0.31353
18073 | 1.7565 | 0.31354
18074 | 1.7565 | 0.31356
18075 | 1.7565 | 0.31357
18076 | 1.7565 | 0.31359
18077 | 1.7564 | 0.3136
18078 | 1.7564 | 0.31362
18079 | 1.7564 | 0.31363
18080 | 1.7564 | 0.31365
18081 | 1.7564 | 0.31366
18082 | 1.7564 | 0.31368
18083 | 1.7563 | 0.31369
18084 | 1.7563 | 0.3137
18085 | 1.7563 | 0.31372
18086 | 1.7563 | 0.31373
18087 | 1.7563 | 0.31375
18088 | 1.7563 | 0.31376
18089 | 1.7562 | 0.31378
18090 | 1.7562 | 0.31379
18091 | 1.7562 | 0.31381
18092 | 1.7562 | 0.31382
18093 | 1.7562 | 0.31384
18094 | 1.7562 | 0.31385
18095 | 1.7562 | 0.31387
18096 | 1.7561 | 0.31388
18097 | 1.7561 | 0.3139
18098 | 1.7561 | 0.31391
18099 | 1.7561 | 0.31393
18100 | 1.7561 | 0.31394
18101 | 1.7561 | 0.31396
18102 | 1.756 | 0.31397
18103 | 1.756 | 0.31399
18104 | 1.756 | 0.314
18105 | 1.756 | 0.31402
18106 | 1.756 | 0.31403
18107 | 1.756 | 0.31405
18108 | 1.7559 | 0.31406
18109 | 1.7559 | 0.31408
18110 | 1.7559 | 0.31409
18111 | 1.7559 | 0.31411
18112 | 1.7559 | 0.31412
18113 | 1.7559 | 0.31414
18114 | 1.7559 | 0.31415
18115 | 1.7558 | 0.31417
18116 | 1.7558 | 0.31418
18117 | 1.7558 | 0.3142
18118 | 1.7558 | 0.31421
18119 | 1.7558 | 0.31423
18120 | 1.7558 | 0.31424
18121 | 1.7557 | 0.31426
18122 | 1.7557 | 0.31427
18123 | 1.7557 | 0.31429
18124 | 1.7557 | 0.3143
18125 | 1.7557 | 0.31432
18126 | 1.7557 | 0.31433
18127 | 1.7556 | 0.31435
18128 | 1.7556 | 0.31436
18129 | 1.7556 | 0.31438
18130 | 1.7556 | 0.31439
18131 | 1.7556 | 0.31441
18132 | 1.7556 | 0.31442
18133 | 1.7555 | 0.31444
18134 | 1.7555 | 0.31445
18135 | 1.7555 | 0.31447
18136 | 1.7555 | 0.31448
18137 | 1.7555 | 0.3145
18138 | 1.7555 | 0.31451
18139 | 1.7555 | 0.31453
18140 | 1.7554 | 0.31454
18141 | 1.7554 | 0.31456
18142 | 1.7554 | 0.31457
18143 | 1.7554 | 0.31459
18144 | 1.7554 | 0.3146
18145 | 1.7554 | 0.31462
18146 | 1.7553 | 0.31463
18147 | 1.7553 | 0.31465
18148 | 1.7553 | 0.31466
18149 | 1.7553 | 0.31468
18150 | 1.7553 | 0.31469
18151 | 1.7553 | 0.31471
18152 | 1.7552 | 0.31472
18153 | 1.7552 | 0.31474
18154 | 1.7552 | 0.31475
18155 | 1.7552 | 0.31477
18156 | 1.7552 | 0.31478
18157 | 1.7552 | 0.3148
18158 | 1.7552 | 0.31481
18159 | 1.7551 | 0.31483
18160 | 1.7551 | 0.31484
18161 | 1.7551 | 0.31486
18162 | 1.7551 | 0.31487
18163 | 1.7551 | 0.31489
18164 | 1.7551 | 0.3149
18165 | 1.755 | 0.31492
18166 | 1.755 | 0.31493
18167 | 1.755 | 0.31495
18168 | 1.755 | 0.31496
18169 | 1.755 | 0.31498
18170 | 1.755 | 0.31499
18171 | 1.7549 | 0.31501
18172 | 1.7549 | 0.31502
18173 | 1.7549 | 0.31504
18174 | 1.7549 | 0.31505
18175 | 1.7549 | 0.31507
18176 | 1.7549 | 0.31508
18177 | 1.7549 | 0.3151
18178 | 1.7548 | 0.31511
18179 | 1.7548 | 0.31513
18180 | 1.7548 | 0.31514
18181 | 1.7548 | 0.31516
18182 | 1.7548 | 0.31517
18183 | 1.7548 | 0.31519
18184 | 1.7547 | 0.3152
18185 | 1.7547 | 0.31522
18186 | 1.7547 | 0.31523
18187 | 1.7547 | 0.31525
18188 | 1.7547 | 0.31526
18189 | 1.7547 | 0.31528
18190 | 1.7546 | 0.31529
18191 | 1.7546 | 0.31531
18192 | 1.7546 | 0.31532
18193 | 1.7546 | 0.31534
18194 | 1.7546 | 0.31535
18195 | 1.7546 | 0.31537
18196 | 1.7546 | 0.31538
18197 | 1.7545 | 0.3154
18198 | 1.7545 | 0.31541
18199 | 1.7545 | 0.31543
18200 | 1.7545 | 0.31544
18201 | 1.7545 | 0.31546
18202 | 1.7545 | 0.31547
18203 | 1.7544 | 0.31549
18204 | 1.7544 | 0.3155
18205 | 1.7544 | 0.31552
18206 | 1.7544 | 0.31553
18207 | 1.7544 | 0.31555
18208 | 1.7544 | 0.31556
18209 | 1.7543 | 0.31558
18210 | 1.7543 | 0.31559
18211 | 1.7543 | 0.31561
18212 | 1.7543 | 0.31562
18213 | 1.7543 | 0.31564
18214 | 1.7543 | 0.31565
18215 | 1.7543 | 0.31567
18216 | 1.7542 | 0.31568
18217 | 1.7542 | 0.3157
18218 | 1.7542 | 0.31571
18219 | 1.7542 | 0.31573
18220 | 1.7542 | 0.31574
18221 | 1.7542 | 0.31576
18222 | 1.7541 | 0.31577
18223 | 1.7541 | 0.31579
18224 | 1.7541 | 0.3158
18225 | 1.7541 | 0.31582
18226 | 1.7541 | 0.31583
18227 | 1.7541 | 0.31585
18228 | 1.754 | 0.31586
18229 | 1.754 | 0.31588
18230 | 1.754 | 0.31589
18231 | 1.754 | 0.3159
18232 | 1.754 | 0.31592
18233 | 1.754 | 0.31593
18234 | 1.754 | 0.31595
18235 | 1.7539 | 0.31596
18236 | 1.7539 | 0.31598
18237 | 1.7539 | 0.31599
18238 | 1.7539 | 0.31601
18239 | 1.7539 | 0.31602
18240 | 1.7539 | 0.31604
18241 | 1.7538 | 0.31605
18242 | 1.7538 | 0.31607
18243 | 1.7538 | 0.31608
18244 | 1.7538 | 0.3161
18245 | 1.7538 | 0.31611
18246 | 1.7538 | 0.31613
18247 | 1.7537 | 0.31614
18248 | 1.7537 | 0.31616
18249 | 1.7537 | 0.31617
18250 | 1.7537 | 0.31619
18251 | 1.7537 | 0.3162
18252 | 1.7537 | 0.31622
18253 | 1.7537 | 0.31623
18254 | 1.7536 | 0.31625
18255 | 1.7536 | 0.31626
18256 | 1.7536 | 0.31628
18257 | 1.7536 | 0.31629
18258 | 1.7536 | 0.31631
18259 | 1.7536 | 0.31632
18260 | 1.7535 | 0.31634
18261 | 1.7535 | 0.31635
18262 | 1.7535 | 0.31637
18263 | 1.7535 | 0.31638
18264 | 1.7535 | 0.3164
18265 | 1.7535 | 0.31641
18266 | 1.7534 | 0.31643
18267 | 1.7534 | 0.31644
18268 | 1.7534 | 0.31646
18269 | 1.7534 | 0.31647
18270 | 1.7534 | 0.31649
18271 | 1.7534 | 0.3165
18272 | 1.7534 | 0.31652
18273 | 1.7533 | 0.31653
18274 | 1.7533 | 0.31655
18275 | 1.7533 | 0.31656
18276 | 1.7533 | 0.31658
18277 | 1.7533 | 0.31659
18278 | 1.7533 | 0.31661
18279 | 1.7532 | 0.31662
18280 | 1.7532 | 0.31664
18281 | 1.7532 | 0.31665
18282 | 1.7532 | 0.31667
18283 | 1.7532 | 0.31668
18284 | 1.7532 | 0.3167
18285 | 1.7531 | 0.31671
18286 | 1.7531 | 0.31673
18287 | 1.7531 | 0.31674
18288 | 1.7531 | 0.31676
18289 | 1.7531 | 0.31677
18290 | 1.7531 | 0.31679
18291 | 1.7531 | 0.3168
18292 | 1.753 | 0.31682
18293 | 1.753 | 0.31683
18294 | 1.753 | 0.31685
18295 | 1.753 | 0.31686
18296 | 1.753 | 0.31688
18297 | 1.753 | 0.31689
18298 | 1.7529 | 0.31691
18299 | 1.7529 | 0.31692
18300 | 1.7529 | 0.31694
18301 | 1.7529 | 0.31695
18302 | 1.7529 | 0.31697
18303 | 1.7529 | 0.31698
18304 | 1.7528 | 0.317
18305 | 1.7528 | 0.31701
18306 | 1.7528 | 0.31703
18307 | 1.7528 | 0.31704
18308 | 1.7528 | 0.31706
18309 | 1.7528 | 0.31707
18310 | 1.7528 | 0.31709
18311 | 1.7527 | 0.3171
18312 | 1.7527 | 0.31712
18313 | 1.7527 | 0.31713
18314 | 1.7527 | 0.31715
18315 | 1.7527 | 0.31716
18316 | 1.7527 | 0.31717
18317 | 1.7526 | 0.31719
18318 | 1.7526 | 0.3172
18319 | 1.7526 | 0.31722
18320 | 1.7526 | 0.31723
18321 | 1.7526 | 0.31725
18322 | 1.7526 | 0.31726
18323 | 1.7526 | 0.31728
18324 | 1.7525 | 0.31729
18325 | 1.7525 | 0.31731
18326 | 1.7525 | 0.31732
18327 | 1.7525 | 0.31734
18328 | 1.7525 | 0.31735
18329 | 1.7525 | 0.31737
18330 | 1.7524 | 0.31738
18331 | 1.7524 | 0.3174
18332 | 1.7524 | 0.31741
18333 | 1.7524 | 0.31743
18334 | 1.7524 | 0.31744
18335 | 1.7524 | 0.31746
18336 | 1.7523 | 0.31747
18337 | 1.7523 | 0.31749
18338 | 1.7523 | 0.3175
18339 | 1.7523 | 0.31752
18340 | 1.7523 | 0.31753
18341 | 1.7523 | 0.31755
18342 | 1.7523 | 0.31756
18343 | 1.7522 | 0.31758
18344 | 1.7522 | 0.31759
18345 | 1.7522 | 0.31761
18346 | 1.7522 | 0.31762
18347 | 1.7522 | 0.31764
18348 | 1.7522 | 0.31765
18349 | 1.7521 | 0.31767
18350 | 1.7521 | 0.31768
18351 | 1.7521 | 0.3177
18352 | 1.7521 | 0.31771
18353 | 1.7521 | 0.31773
18354 | 1.7521 | 0.31774
18355 | 1.752 | 0.31776
18356 | 1.752 | 0.31777
18357 | 1.752 | 0.31779
18358 | 1.752 | 0.3178
18359 | 1.752 | 0.31782
18360 | 1.752 | 0.31783
18361 | 1.752 | 0.31785
18362 | 1.7519 | 0.31786
18363 | 1.7519 | 0.31788
18364 | 1.7519 | 0.31789
18365 | 1.7519 | 0.31791
18366 | 1.7519 | 0.31792
18367 | 1.7519 | 0.31794
18368 | 1.7518 | 0.31795
18369 | 1.7518 | 0.31797
18370 | 1.7518 | 0.31798
18371 | 1.7518 | 0.318
18372 | 1.7518 | 0.31801
18373 | 1.7518 | 0.31803
18374 | 1.7517 | 0.31804
18375 | 1.7517 | 0.31806
18376 | 1.7517 | 0.31807
18377 | 1.7517 | 0.31809
18378 | 1.7517 | 0.3181
18379 | 1.7517 | 0.31812
18380 | 1.7517 | 0.31813
18381 | 1.7516 | 0.31815
18382 | 1.7516 | 0.31816
18383 | 1.7516 | 0.31818
18384 | 1.7516 | 0.31819
18385 | 1.7516 | 0.3182
18386 | 1.7516 | 0.31822
18387 | 1.7515 | 0.31823
18388 | 1.7515 | 0.31825
18389 | 1.7515 | 0.31826
18390 | 1.7515 | 0.31828
18391 | 1.7515 | 0.31829
18392 | 1.7515 | 0.31831
18393 | 1.7515 | 0.31832
18394 | 1.7514 | 0.31834
18395 | 1.7514 | 0.31835
18396 | 1.7514 | 0.31837
18397 | 1.7514 | 0.31838
18398 | 1.7514 | 0.3184
18399 | 1.7514 | 0.31841
18400 | 1.7513 | 0.31843
18401 | 1.7513 | 0.31844
18402 | 1.7513 | 0.31846
18403 | 1.7513 | 0.31847
18404 | 1.7513 | 0.31849
18405 | 1.7513 | 0.3185
18406 | 1.7512 | 0.31852
18407 | 1.7512 | 0.31853
18408 | 1.7512 | 0.31855
18409 | 1.7512 | 0.31856
18410 | 1.7512 | 0.31858
18411 | 1.7512 | 0.31859
18412 | 1.7512 | 0.31861
18413 | 1.7511 | 0.31862
18414 | 1.7511 | 0.31864
18415 | 1.7511 | 0.31865
18416 | 1.7511 | 0.31867
18417 | 1.7511 | 0.31868
18418 | 1.7511 | 0.3187
18419 | 1.751 | 0.31871
18420 | 1.751 | 0.31873
18421 | 1.751 | 0.31874
18422 | 1.751 | 0.31876
18423 | 1.751 | 0.31877
18424 | 1.751 | 0.31879
18425 | 1.7509 | 0.3188
18426 | 1.7509 | 0.31882
18427 | 1.7509 | 0.31883
18428 | 1.7509 | 0.31885
18429 | 1.7509 | 0.31886
18430 | 1.7509 | 0.31888
18431 | 1.7509 | 0.31889
18432 | 1.7508 | 0.31891
18433 | 1.7508 | 0.31892
18434 | 1.7508 | 0.31894
18435 | 1.7508 | 0.31895
18436 | 1.7508 | 0.31897
18437 | 1.7508 | 0.31898
18438 | 1.7507 | 0.319
18439 | 1.7507 | 0.31901
18440 | 1.7507 | 0.31903
18441 | 1.7507 | 0.31904
18442 | 1.7507 | 0.31906
18443 | 1.7507 | 0.31907
18444 | 1.7507 | 0.31908
18445 | 1.7506 | 0.3191
18446 | 1.7506 | 0.31911
18447 | 1.7506 | 0.31913
18448 | 1.7506 | 0.31914
18449 | 1.7506 | 0.31916
18450 | 1.7506 | 0.31917
18451 | 1.7505 | 0.31919
18452 | 1.7505 | 0.3192
18453 | 1.7505 | 0.31922
18454 | 1.7505 | 0.31923
18455 | 1.7505 | 0.31925
18456 | 1.7505 | 0.31926
18457 | 1.7504 | 0.31928
18458 | 1.7504 | 0.31929
18459 | 1.7504 | 0.31931
18460 | 1.7504 | 0.31932
18461 | 1.7504 | 0.31934
18462 | 1.7504 | 0.31935
18463 | 1.7504 | 0.31937
18464 | 1.7503 | 0.31938
18465 | 1.7503 | 0.3194
18466 | 1.7503 | 0.31941
18467 | 1.7503 | 0.31943
18468 | 1.7503 | 0.31944
18469 | 1.7503 | 0.31946
18470 | 1.7502 | 0.31947
18471 | 1.7502 | 0.31949
18472 | 1.7502 | 0.3195
18473 | 1.7502 | 0.31952
18474 | 1.7502 | 0.31953
18475 | 1.7502 | 0.31955
18476 | 1.7502 | 0.31956
18477 | 1.7501 | 0.31958
18478 | 1.7501 | 0.31959
18479 | 1.7501 | 0.31961
18480 | 1.7501 | 0.31962
18481 | 1.7501 | 0.31964
18482 | 1.7501 | 0.31965
18483 | 1.75 | 0.31967
18484 | 1.75 | 0.31968
18485 | 1.75 | 0.3197
18486 | 1.75 | 0.31971
18487 | 1.75 | 0.31973
18488 | 1.75 | 0.31974
18489 | 1.7499 | 0.31976
18490 | 1.7499 | 0.31977
18491 | 1.7499 | 0.31979
18492 | 1.7499 | 0.3198
18493 | 1.7499 | 0.31982
18494 | 1.7499 | 0.31983
18495 | 1.7499 | 0.31984
18496 | 1.7498 | 0.31986
18497 | 1.7498 | 0.31987
18498 | 1.7498 | 0.31989
18499 | 1.7498 | 0.3199
18500 | 1.7498 | 0.31992
18501 | 1.7498 | 0.31993
18502 | 1.7497 | 0.31995
18503 | 1.7497 | 0.31996
18504 | 1.7497 | 0.31998
18505 | 1.7497 | 0.31999
18506 | 1.7497 | 0.32001
18507 | 1.7497 | 0.32002
18508 | 1.7497 | 0.32004
18509 | 1.7496 | 0.32005
18510 | 1.7496 | 0.32007
18511 | 1.7496 | 0.32008
18512 | 1.7496 | 0.3201
18513 | 1.7496 | 0.32011
18514 | 1.7496 | 0.32013
18515 | 1.7495 | 0.32014
18516 | 1.7495 | 0.32016
18517 | 1.7495 | 0.32017
18518 | 1.7495 | 0.32019
18519 | 1.7495 | 0.3202
18520 | 1.7495 | 0.32022
18521 | 1.7494 | 0.32023
18522 | 1.7494 | 0.32025
18523 | 1.7494 | 0.32026
18524 | 1.7494 | 0.32028
18525 | 1.7494 | 0.32029
18526 | 1.7494 | 0.32031
18527 | 1.7494 | 0.32032
18528 | 1.7493 | 0.32034
18529 | 1.7493 | 0.32035
18530 | 1.7493 | 0.32037
18531 | 1.7493 | 0.32038
18532 | 1.7493 | 0.3204
18533 | 1.7493 | 0.32041
18534 | 1.7492 | 0.32043
18535 | 1.7492 | 0.32044
18536 | 1.7492 | 0.32046
18537 | 1.7492 | 0.32047
18538 | 1.7492 | 0.32049
18539 | 1.7492 | 0.3205
18540 | 1.7492 | 0.32052
18541 | 1.7491 | 0.32053
18542 | 1.7491 | 0.32054
18543 | 1.7491 | 0.32056
18544 | 1.7491 | 0.32057
18545 | 1.7491 | 0.32059
18546 | 1.7491 | 0.3206
18547 | 1.749 | 0.32062
18548 | 1.749 | 0.32063
18549 | 1.749 | 0.32065
18550 | 1.749 | 0.32066
18551 | 1.749 | 0.32068
18552 | 1.749 | 0.32069
18553 | 1.7489 | 0.32071
18554 | 1.7489 | 0.32072
18555 | 1.7489 | 0.32074
18556 | 1.7489 | 0.32075
18557 | 1.7489 | 0.32077
18558 | 1.7489 | 0.32078
18559 | 1.7489 | 0.3208
18560 | 1.7488 | 0.32081
18561 | 1.7488 | 0.32083
18562 | 1.7488 | 0.32084
18563 | 1.7488 | 0.32086
18564 | 1.7488 | 0.32087
18565 | 1.7488 | 0.32089
18566 | 1.7487 | 0.3209
18567 | 1.7487 | 0.32092
18568 | 1.7487 | 0.32093
18569 | 1.7487 | 0.32095
18570 | 1.7487 | 0.32096
18571 | 1.7487 | 0.32098
18572 | 1.7487 | 0.32099
18573 | 1.7486 | 0.32101
18574 | 1.7486 | 0.32102
18575 | 1.7486 | 0.32104
18576 | 1.7486 | 0.32105
18577 | 1.7486 | 0.32107
18578 | 1.7486 | 0.32108
18579 | 1.7485 | 0.3211
18580 | 1.7485 | 0.32111
18581 | 1.7485 | 0.32113
18582 | 1.7485 | 0.32114
18583 | 1.7485 | 0.32116
18584 | 1.7485 | 0.32117
18585 | 1.7484 | 0.32119
18586 | 1.7484 | 0.3212
18587 | 1.7484 | 0.32121
18588 | 1.7484 | 0.32123
18589 | 1.7484 | 0.32124
18590 | 1.7484 | 0.32126
18591 | 1.7484 | 0.32127
18592 | 1.7483 | 0.32129
18593 | 1.7483 | 0.3213
18594 | 1.7483 | 0.32132
18595 | 1.7483 | 0.32133
18596 | 1.7483 | 0.32135
18597 | 1.7483 | 0.32136
18598 | 1.7482 | 0.32138
18599 | 1.7482 | 0.32139
18600 | 1.7482 | 0.32141
18601 | 1.7482 | 0.32142
18602 | 1.7482 | 0.32144
18603 | 1.7482 | 0.32145
18604 | 1.7482 | 0.32147
18605 | 1.7481 | 0.32148
18606 | 1.7481 | 0.3215
18607 | 1.7481 | 0.32151
18608 | 1.7481 | 0.32153
18609 | 1.7481 | 0.32154
18610 | 1.7481 | 0.32156
18611 | 1.748 | 0.32157
18612 | 1.748 | 0.32159
18613 | 1.748 | 0.3216
18614 | 1.748 | 0.32162
18615 | 1.748 | 0.32163
18616 | 1.748 | 0.32165
18617 | 1.748 | 0.32166
18618 | 1.7479 | 0.32168
18619 | 1.7479 | 0.32169
18620 | 1.7479 | 0.32171
18621 | 1.7479 | 0.32172
18622 | 1.7479 | 0.32174
18623 | 1.7479 | 0.32175
18624 | 1.7478 | 0.32177
18625 | 1.7478 | 0.32178
18626 | 1.7478 | 0.32179
18627 | 1.7478 | 0.32181
18628 | 1.7478 | 0.32182
18629 | 1.7478 | 0.32184
18630 | 1.7477 | 0.32185
18631 | 1.7477 | 0.32187
18632 | 1.7477 | 0.32188
18633 | 1.7477 | 0.3219
18634 | 1.7477 | 0.32191
18635 | 1.7477 | 0.32193
18636 | 1.7477 | 0.32194
18637 | 1.7476 | 0.32196
18638 | 1.7476 | 0.32197
18639 | 1.7476 | 0.32199
18640 | 1.7476 | 0.322
18641 | 1.7476 | 0.32202
18642 | 1.7476 | 0.32203
18643 | 1.7475 | 0.32205
18644 | 1.7475 | 0.32206
18645 | 1.7475 | 0.32208
18646 | 1.7475 | 0.32209
18647 | 1.7475 | 0.32211
18648 | 1.7475 | 0.32212
18649 | 1.7475 | 0.32214
18650 | 1.7474 | 0.32215
18651 | 1.7474 | 0.32217
18652 | 1.7474 | 0.32218
18653 | 1.7474 | 0.3222
18654 | 1.7474 | 0.32221
18655 | 1.7474 | 0.32223
18656 | 1.7473 | 0.32224
18657 | 1.7473 | 0.32226
18658 | 1.7473 | 0.32227
18659 | 1.7473 | 0.32229
18660 | 1.7473 | 0.3223
18661 | 1.7473 | 0.32232
18662 | 1.7473 | 0.32233
18663 | 1.7472 | 0.32235
18664 | 1.7472 | 0.32236
18665 | 1.7472 | 0.32237
18666 | 1.7472 | 0.32239
18667 | 1.7472 | 0.3224
18668 | 1.7472 | 0.32242
18669 | 1.7471 | 0.32243
18670 | 1.7471 | 0.32245
18671 | 1.7471 | 0.32246
18672 | 1.7471 | 0.32248
18673 | 1.7471 | 0.32249
18674 | 1.7471 | 0.32251
18675 | 1.747 | 0.32252
18676 | 1.747 | 0.32254
18677 | 1.747 | 0.32255
18678 | 1.747 | 0.32257
18679 | 1.747 | 0.32258
18680 | 1.747 | 0.3226
18681 | 1.747 | 0.32261
18682 | 1.7469 | 0.32263
18683 | 1.7469 | 0.32264
18684 | 1.7469 | 0.32266
18685 | 1.7469 | 0.32267
18686 | 1.7469 | 0.32269
18687 | 1.7469 | 0.3227
18688 | 1.7468 | 0.32272
18689 | 1.7468 | 0.32273
18690 | 1.7468 | 0.32275
18691 | 1.7468 | 0.32276
18692 | 1.7468 | 0.32278
18693 | 1.7468 | 0.32279
18694 | 1.7468 | 0.32281
18695 | 1.7467 | 0.32282
18696 | 1.7467 | 0.32284
18697 | 1.7467 | 0.32285
18698 | 1.7467 | 0.32287
18699 | 1.7467 | 0.32288
18700 | 1.7467 | 0.32289
18701 | 1.7466 | 0.32291
18702 | 1.7466 | 0.32292
18703 | 1.7466 | 0.32294
18704 | 1.7466 | 0.32295
18705 | 1.7466 | 0.32297
18706 | 1.7466 | 0.32298
18707 | 1.7466 | 0.323
18708 | 1.7465 | 0.32301
18709 | 1.7465 | 0.32303
18710 | 1.7465 | 0.32304
18711 | 1.7465 | 0.32306
18712 | 1.7465 | 0.32307
18713 | 1.7465 | 0.32309
18714 | 1.7464 | 0.3231
18715 | 1.7464 | 0.32312
18716 | 1.7464 | 0.32313
18717 | 1.7464 | 0.32315
18718 | 1.7464 | 0.32316
18719 | 1.7464 | 0.32318
18720 | 1.7464 | 0.32319
18721 | 1.7463 | 0.32321
18722 | 1.7463 | 0.32322
18723 | 1.7463 | 0.32324
18724 | 1.7463 | 0.32325
18725 | 1.7463 | 0.32327
18726 | 1.7463 | 0.32328
18727 | 1.7462 | 0.3233
18728 | 1.7462 | 0.32331
18729 | 1.7462 | 0.32333
18730 | 1.7462 | 0.32334
18731 | 1.7462 | 0.32336
18732 | 1.7462 | 0.32337
18733 | 1.7461 | 0.32339
18734 | 1.7461 | 0.3234
18735 | 1.7461 | 0.32341
18736 | 1.7461 | 0.32343
18737 | 1.7461 | 0.32344
18738 | 1.7461 | 0.32346
18739 | 1.7461 | 0.32347
18740 | 1.746 | 0.32349
18741 | 1.746 | 0.3235
18742 | 1.746 | 0.32352
18743 | 1.746 | 0.32353
18744 | 1.746 | 0.32355
18745 | 1.746 | 0.32356
18746 | 1.7459 | 0.32358
18747 | 1.7459 | 0.32359
18748 | 1.7459 | 0.32361
18749 | 1.7459 | 0.32362
18750 | 1.7459 | 0.32364
18751 | 1.7459 | 0.32365
18752 | 1.7459 | 0.32367
18753 | 1.7458 | 0.32368
18754 | 1.7458 | 0.3237
18755 | 1.7458 | 0.32371
18756 | 1.7458 | 0.32373
18757 | 1.7458 | 0.32374
18758 | 1.7458 | 0.32376
18759 | 1.7457 | 0.32377
18760 | 1.7457 | 0.32379
18761 | 1.7457 | 0.3238
18762 | 1.7457 | 0.32382
18763 | 1.7457 | 0.32383
18764 | 1.7457 | 0.32385
18765 | 1.7457 | 0.32386
18766 | 1.7456 | 0.32388
18767 | 1.7456 | 0.32389
18768 | 1.7456 | 0.3239
18769 | 1.7456 | 0.32392
18770 | 1.7456 | 0.32393
18771 | 1.7456 | 0.32395
18772 | 1.7455 | 0.32396
18773 | 1.7455 | 0.32398
18774 | 1.7455 | 0.32399
18775 | 1.7455 | 0.32401
18776 | 1.7455 | 0.32402
18777 | 1.7455 | 0.32404
18778 | 1.7455 | 0.32405
18779 | 1.7454 | 0.32407
18780 | 1.7454 | 0.32408
18781 | 1.7454 | 0.3241
18782 | 1.7454 | 0.32411
18783 | 1.7454 | 0.32413
18784 | 1.7454 | 0.32414
18785 | 1.7453 | 0.32416
18786 | 1.7453 | 0.32417
18787 | 1.7453 | 0.32419
18788 | 1.7453 | 0.3242
18789 | 1.7453 | 0.32422
18790 | 1.7453 | 0.32423
18791 | 1.7453 | 0.32425
18792 | 1.7452 | 0.32426
18793 | 1.7452 | 0.32428
18794 | 1.7452 | 0.32429
18795 | 1.7452 | 0.32431
18796 | 1.7452 | 0.32432
18797 | 1.7452 | 0.32434
18798 | 1.7451 | 0.32435
18799 | 1.7451 | 0.32436

## water 0-150
4:00 | water: | V/L | sat. | T=0.0 | to | 150 | ?F
| Liquid | Vapor | Liquid | Vapor
| Temperature | Pressure | Density | Density | Enthalpy | Enthalpy
| (F) | (psia) | (lbm/ft^3) | (lbm/ft^3) | (Btu/lbm) | (Btu/lbm)
1 | 33 | 0.092292 | 62.417 | 0.00031466 | 0.99048 | 1076.4
2 | 34 | 0.096068 | 62.419 | 0.00032688 | 1.9984 | 1076.8
3 | 35 | 0.09998 | 62.421 | 0.00033951 | 3.0059 | 1077.2
4 | 36 | 0.10403 | 62.422 | 0.00035256 | 4.013 | 1077.7
5 | 37 | 0.10823 | 62.423 | 0.00036605 | 5.0197 | 1078.1
6 | 38 | 0.11258 | 62.423 | 0.00038 | 6.0261 | 1078.5
7 | 39 | 0.11708 | 62.423 | 0.0003944 | 7.0321 | 1079
8 | 40 | 0.12173 | 62.423 | 0.00040928 | 8.0377 | 1079.4
9 | 41 | 0.12656 | 62.423 | 0.00042465 | 9.043 | 1079.9
10 | 42 | 0.13155 | 62.422 | 0.00044052 | 10.048 | 1080.3
11 | 43 | 0.13671 | 62.421 | 0.0004569 | 11.053 | 1080.7
12 | 44 | 0.14205 | 62.42 | 0.00047382 | 12.057 | 1081.2
13 | 45 | 0.14757 | 62.418 | 0.00049128 | 13.061 | 1081.6
14 | 46 | 0.15329 | 62.416 | 0.0005093 | 14.065 | 1082
15 | 47 | 0.15919 | 62.414 | 0.00052789 | 15.069 | 1082.5
16 | 48 | 0.1653 | 62.412 | 0.00054707 | 16.072 | 1082.9
17 | 49 | 0.17161 | 62.409 | 0.00056686 | 17.075 | 1083.4
18 | 50 | 0.17814 | 62.406 | 0.00058726 | 18.078 | 1083.8
19 | 51 | 0.18488 | 62.403 | 0.00060831 | 19.081 | 1084.2
20 | 52 | 0.19184 | 62.4 | 0.00063 | 20.083 | 1084.7
21 | 53 | 0.19904 | 62.396 | 0.00065237 | 21.085 | 1085.1
22 | 54 | 0.20647 | 62.392 | 0.00067542 | 22.087 | 1085.5
23 | 55 | 0.21414 | 62.388 | 0.00069918 | 23.089 | 1086
24 | 56 | 0.22207 | 62.384 | 0.00072367 | 24.091 | 1086.4
25 | 57 | 0.23025 | 62.379 | 0.00074889 | 25.093 | 1086.8
26 | 58 | 0.23869 | 62.374 | 0.00077488 | 26.094 | 1087.3
27 | 59 | 0.2474 | 62.369 | 0.00080164 | 27.095 | 1087.7
28 | 60 | 0.2564 | 62.364 | 0.0008292 | 28.096 | 1088.2
29 | 61 | 0.26568 | 62.358 | 0.00085758 | 29.097 | 1088.6
30 | 62 | 0.27525 | 62.352 | 0.0008868 | 30.098 | 1089
31 | 63 | 0.28512 | 62.346 | 0.00091687 | 31.099 | 1089.5
32 | 64 | 0.2953 | 62.34 | 0.00094783 | 32.099 | 1089.9
33 | 65 | 0.3058 | 62.334 | 0.00097969 | 33.1 | 1090.3
34 | 66 | 0.31663 | 62.327 | 0.0010125 | 34.1 | 1090.8
35 | 67 | 0.32779 | 62.32 | 0.0010462 | 35.101 | 1091.2
36 | 68 | 0.33929 | 62.313 | 0.0010809 | 36.101 | 1091.6
37 | 69 | 0.35114 | 62.306 | 0.0011166 | 37.101 | 1092.1
38 | 70 | 0.36336 | 62.298 | 0.0011533 | 38.101 | 1092.5
39 | 71 | 0.37594 | 62.291 | 0.001191 | 39.101 | 1092.9
40 | 72 | 0.38891 | 62.283 | 0.0012298 | 40.101 | 1093.4
41 | 73 | 0.40226 | 62.275 | 0.0012696 | 41.1 | 1093.8
42 | 74 | 0.41601 | 62.267 | 0.0013106 | 42.1 | 1094.2
43 | 75 | 0.43017 | 62.258 | 0.0013528 | 43.1 | 1094.7
44 | 76 | 0.44475 | 62.25 | 0.001396 | 44.099 | 1095.1
45 | 77 | 0.45976 | 62.241 | 0.0014405 | 45.099 | 1095.5
46 | 78 | 0.47521 | 62.232 | 0.0014862 | 46.098 | 1096
47 | 79 | 0.49111 | 62.223 | 0.0015331 | 47.097 | 1096.4
48 | 80 | 0.50747 | 62.213 | 0.0015813 | 48.097 | 1096.8
49 | 81 | 0.5243 | 62.204 | 0.0016308 | 49.096 | 1097.3
50 | 82 | 0.54162 | 62.194 | 0.0016816 | 50.095 | 1097.7
51 | 83 | 0.55943 | 62.184 | 0.0017338 | 51.095 | 1098.1
52 | 84 | 0.57776 | 62.174 | 0.0017874 | 52.094 | 1098.6
53 | 85 | 0.5966 | 62.164 | 0.0018423 | 53.093 | 1099
54 | 86 | 0.61597 | 62.154 | 0.0018988 | 54.092 | 1099.4
55 | 87 | 0.63589 | 62.143 | 0.0019567 | 55.091 | 1099.9
56 | 88 | 0.65637 | 62.132 | 0.0020161 | 56.09 | 1100.3
57 | 89 | 0.67741 | 62.122 | 0.002077 | 57.089 | 1100.7
58 | 90 | 0.69904 | 62.11 | 0.0021395 | 58.088 | 1101.1
59 | 91 | 0.72127 | 62.099 | 0.0022036 | 59.087 | 1101.6
60 | 92 | 0.7441 | 62.088 | 0.0022694 | 60.086 | 1102
61 | 93 | 0.76757 | 62.076 | 0.0023368 | 61.085 | 1102.4
62 | 94 | 0.79167 | 62.065 | 0.0024059 | 62.084 | 1102.9
63 | 95 | 0.81642 | 62.053 | 0.0024768 | 63.083 | 1103.3
64 | 96 | 0.84184 | 62.041 | 0.0025494 | 64.082 | 1103.7
65 | 97 | 0.86795 | 62.029 | 0.0026239 | 65.081 | 1104.2
66 | 98 | 0.89475 | 62.016 | 0.0027002 | 66.08 | 1104.6
67 | 99 | 0.92226 | 62.004 | 0.0027784 | 67.079 | 1105
68 | 100 | 0.95051 | 61.991 | 0.0028585 | 68.078 | 1105.4
69 | 101 | 0.9795 | 61.979 | 0.0029406 | 69.077 | 1105.9
70 | 102 | 1.0092 | 61.966 | 0.0030246 | 70.076 | 1106.3
71 | 103 | 1.0398 | 61.953 | 0.0031108 | 71.075 | 1106.7
72 | 104 | 1.0711 | 61.939 | 0.0031989 | 72.074 | 1107.2
73 | 105 | 1.1032 | 61.926 | 0.0032893 | 73.073 | 1107.6
74 | 106 | 1.1362 | 61.913 | 0.0033817 | 74.073 | 1108
75 | 107 | 1.17 | 61.899 | 0.0034764 | 75.072 | 1108.4
76 | 108 | 1.2047 | 61.885 | 0.0035733 | 76.071 | 1108.9
77 | 109 | 1.2402 | 61.871 | 0.0036725 | 77.07 | 1109.3
78 | 110 | 1.2767 | 61.857 | 0.0037741 | 78.069 | 1109.7
79 | 111 | 1.3141 | 61.843 | 0.003878 | 79.068 | 1110.1
80 | 112 | 1.3524 | 61.829 | 0.0039843 | 80.067 | 1110.6
81 | 113 | 1.3916 | 61.814 | 0.0040931 | 81.067 | 1111
82 | 114 | 1.4319 | 61.8 | 0.0042044 | 82.066 | 1111.4
83 | 115 | 1.4731 | 61.785 | 0.0043182 | 83.065 | 1111.8
84 | 116 | 1.5154 | 61.77 | 0.0044347 | 84.064 | 1112.3
85 | 117 | 1.5587 | 61.755 | 0.0045538 | 85.064 | 1112.7
86 | 118 | 1.603 | 61.74 | 0.0046756 | 86.063 | 1113.1
87 | 119 | 1.6485 | 61.725 | 0.0048001 | 87.063 | 1113.5
88 | 120 | 1.695 | 61.71 | 0.0049274 | 88.062 | 1114
89 | 121 | 1.7427 | 61.694 | 0.0050576 | 89.061 | 1114.4
90 | 122 | 1.7915 | 61.679 | 0.0051907 | 90.061 | 1114.8
91 | 123 | 1.8415 | 61.663 | 0.0053267 | 91.061 | 1115.2
92 | 124 | 1.8926 | 61.647 | 0.0054657 | 92.06 | 1115.6
93 | 125 | 1.945 | 61.631 | 0.0056078 | 93.06 | 1116.1
94 | 126 | 1.9986 | 61.615 | 0.0057529 | 94.059 | 1116.5
95 | 127 | 2.0535 | 61.599 | 0.0059013 | 95.059 | 1116.9
96 | 128 | 2.1097 | 61.582 | 0.0060528 | 96.059 | 1117.3
97 | 129 | 2.1671 | 61.566 | 0.0062076 | 97.059 | 1117.7
98 | 130 | 2.2259 | 61.549 | 0.0063657 | 98.059 | 1118.2
99 | 131 | 2.2861 | 61.532 | 0.0065272 | 99.059 | 1118.6
100 | 132 | 2.3476 | 61.516 | 0.0066921 | 100.06 | 1119
101 | 133 | 2.4106 | 61.499 | 0.0068605 | 101.06 | 1119.4
102 | 134 | 2.475 | 61.482 | 0.0070325 | 102.06 | 1119.8
103 | 135 | 2.5408 | 61.464 | 0.0072081 | 103.06 | 1120.3
104 | 136 | 2.6082 | 61.447 | 0.0073873 | 104.06 | 1120.7
105 | 137 | 2.677 | 61.43 | 0.0075703 | 105.06 | 1121.1
106 | 138 | 2.7474 | 61.412 | 0.0077571 | 106.06 | 1121.5
107 | 139 | 2.8194 | 61.394 | 0.0079477 | 107.06 | 1121.9
108 | 140 | 2.893 | 61.377 | 0.0081422 | 108.06 | 1122.3
109 | 141 | 2.9682 | 61.359 | 0.0083407 | 109.06 | 1122.8
110 | 142 | 3.045 | 61.341 | 0.0085432 | 110.06 | 1123.2
111 | 143 | 3.1236 | 61.323 | 0.0087498 | 111.06 | 1123.6
112 | 144 | 3.2039 | 61.304 | 0.0089607 | 112.06 | 1124
113 | 145 | 3.2859 | 61.286 | 0.0091757 | 113.06 | 1124.4
114 | 146 | 3.3696 | 61.268 | 0.009395 | 114.06 | 1124.8
115 | 147 | 3.4552 | 61.249 | 0.0096187 | 115.07 | 1125.3
116 | 148 | 3.5427 | 61.23 | 0.0098469 | 116.07 | 1125.7
117 | 149 | 3.632 | 61.212 | 0.01008 | 117.07 | 1126.1
118 | 150 | 3.7232 | 61.193 | 0.010317 | 118.07 | 1126.5
| Liquid | Vapor
| Entropy | Entropy
| (Btu/lbm-R) | (Btu/lbm-R)
1 | 0.0020119 | 2.1847
2 | 0.0040557 | 2.1812
3 | 0.0060944 | 2.1777
4 | 0.0081282 | 2.1742
5 | 0.010157 | 2.1707
6 | 0.012181 | 2.1673
7 | 0.014201 | 2.1638
8 | 0.016215 | 2.1604
9 | 0.018225 | 2.157
10 | 0.02023 | 2.1536
11 | 0.022231 | 2.1502
12 | 0.024227 | 2.1469
13 | 0.026219 | 2.1435
14 | 0.028206 | 2.1402
15 | 0.030189 | 2.1369
16 | 0.032167 | 2.1336
17 | 0.034141 | 2.1303
18 | 0.03611 | 2.1271
19 | 0.038076 | 2.1239
20 | 0.040037 | 2.1206
21 | 0.041994 | 2.1174
22 | 0.043946 | 2.1142
23 | 0.045895 | 2.1111
24 | 0.047839 | 2.1079
25 | 0.04978 | 2.1048
26 | 0.051716 | 2.1016
27 | 0.053648 | 2.0985
28 | 0.055576 | 2.0954
29 | 0.057501 | 2.0924
30 | 0.059421 | 2.0893
31 | 0.061337 | 2.0862
32 | 0.06325 | 2.0832
33 | 0.065158 | 2.0802
34 | 0.067063 | 2.0772
35 | 0.068964 | 2.0742
36 | 0.070861 | 2.0712
37 | 0.072755 | 2.0683
38 | 0.074644 | 2.0653
39 | 0.07653 | 2.0624
40 | 0.078412 | 2.0595
41 | 0.080291 | 2.0566
42 | 0.082166 | 2.0537
43 | 0.084037 | 2.0508
44 | 0.085905 | 2.0479
45 | 0.087769 | 2.0451
46 | 0.089629 | 2.0423
47 | 0.091486 | 2.0394
48 | 0.09334 | 2.0366
49 | 0.09519 | 2.0338
50 | 0.097036 | 2.0311
51 | 0.098879 | 2.0283
52 | 0.10072 | 2.0255
53 | 0.10255 | 2.0228
54 | 0.10439 | 2.0201
55 | 0.10622 | 2.0174
56 | 0.10804 | 2.0147
57 | 0.10986 | 2.012
58 | 0.11168 | 2.0093
59 | 0.1135 | 2.0066
60 | 0.11531 | 2.004
61 | 0.11712 | 2.0013
62 | 0.11893 | 1.9987
63 | 0.12073 | 1.9961
64 | 0.12253 | 1.9935
65 | 0.12432 | 1.9909
66 | 0.12612 | 1.9883
67 | 0.12791 | 1.9858
68 | 0.12969 | 1.9832
69 | 0.13148 | 1.9807
70 | 0.13326 | 1.9781
71 | 0.13503 | 1.9756
72 | 0.13681 | 1.9731
73 | 0.13858 | 1.9706
74 | 0.14035 | 1.9681
75 | 0.14211 | 1.9657
76 | 0.14387 | 1.9632
77 | 0.14563 | 1.9608
78 | 0.14738 | 1.9583
79 | 0.14914 | 1.9559
80 | 0.15089 | 1.9535
81 | 0.15263 | 1.9511
82 | 0.15438 | 1.9487
83 | 0.15612 | 1.9463
84 | 0.15785 | 1.9439
85 | 0.15959 | 1.9416
86 | 0.16132 | 1.9392
87 | 0.16305 | 1.9369
88 | 0.16477 | 1.9346
89 | 0.16649 | 1.9322
90 | 0.16821 | 1.9299
91 | 0.16993 | 1.9276
92 | 0.17164 | 1.9253
93 | 0.17336 | 1.9231
94 | 0.17506 | 1.9208
95 | 0.17677 | 1.9185
96 | 0.17847 | 1.9163
97 | 0.18017 | 1.9141
98 | 0.18187 | 1.9118
99 | 0.18356 | 1.9096
100 | 0.18525 | 1.9074
101 | 0.18694 | 1.9052
102 | 0.18863 | 1.903
103 | 0.19031 | 1.9008
104 | 0.19199 | 1.8987
105 | 0.19367 | 1.8965
106 | 0.19534 | 1.8944
107 | 0.19701 | 1.8922
108 | 0.19868 | 1.8901
109 | 0.20035 | 1.888
110 | 0.20201 | 1.8859
111 | 0.20368 | 1.8838
112 | 0.20533 | 1.8817
113 | 0.20699 | 1.8796
114 | 0.20864 | 1.8775
115 | 0.21029 | 1.8754
116 | 0.21194 | 1.8734
117 | 0.21359 | 1.8713
118 | 0.21523 | 1.8693

## Air at atmospheric pressure
Look up pressure | [6 empty] | Look up enthalpy
2:00 | Air | (dry): | p | = | 14.696 | psia | 2:00 | = | Air | (dry): | p | 14.696 | psia | (75.57/1.2691/23.16) | Reference state for enthalpy and entropy is 0°F at atmospheric pressure
| Temperature | Pressure | Density | Enthalpy | Entropy |  |  | Enthalpy | Temperature | Pressure | Density | Entropy
| (F) | (psia) | (lbm/ft^3) | (Btu/lbm) | (Btu/lbm-R) |  |  | (Btu/lbm) | (F) | (psia) | (lbm/ft^3) | (Btu/lbm-R)
1 | -312.57 | 14.696 | 0.28076 | -75.977 | -0.27841 |  | 1 | -75.977 | -312.57 | 14.696 | 0.28076 | -0.27841
2 | 32 | 14.696 | 0.080724 | 7.6909 | 0.016175 |  | 2 | 7.6909 | 32 | 14.696 | 0.080724 | 0.016175
3 | 32.01 | 14.696 | 0.080722 | 7.6933 | 0.01618 |  | 3 | 7.6933 | 32.01 | 14.696 | 0.080722 | 0.01618
4 | 32.02 | 14.696 | 0.08072 | 7.6957 | 0.016185 |  | 4 | 7.6957 | 32.02 | 14.696 | 0.08072 | 0.016185
5 | 32.03 | 14.696 | 0.080719 | 7.6982 | 0.016189 |  | 5 | 7.6982 | 32.03 | 14.696 | 0.080719 | 0.016189
6 | 32.04 | 14.696 | 0.080717 | 7.7006 | 0.016194 |  | 6 | 7.7006 | 32.04 | 14.696 | 0.080717 | 0.016194
7 | 32.05 | 14.696 | 0.080715 | 7.703 | 0.016199 |  | 7 | 7.703 | 32.05 | 14.696 | 0.080715 | 0.016199
8 | 32.06 | 14.696 | 0.080714 | 7.7054 | 0.016204 |  | 8 | 7.7054 | 32.06 | 14.696 | 0.080714 | 0.016204
9 | 32.07 | 14.696 | 0.080712 | 7.7078 | 0.016209 |  | 9 | 7.7078 | 32.07 | 14.696 | 0.080712 | 0.016209
10 | 32.08 | 14.696 | 0.080711 | 7.7102 | 0.016214 |  | 10 | 7.7102 | 32.08 | 14.696 | 0.080711 | 0.016214
11 | 32.09 | 14.696 | 0.080709 | 7.7126 | 0.016219 |  | 11 | 7.7126 | 32.09 | 14.696 | 0.080709 | 0.016219
12 | 32.1 | 14.696 | 0.080707 | 7.715 | 0.016224 |  | 12 | 7.715 | 32.1 | 14.696 | 0.080707 | 0.016224
13 | 32.11 | 14.696 | 0.080706 | 7.7174 | 0.016229 |  | 13 | 7.7174 | 32.11 | 14.696 | 0.080706 | 0.016229
14 | 32.12 | 14.696 | 0.080704 | 7.7198 | 0.016233 |  | 14 | 7.7198 | 32.12 | 14.696 | 0.080704 | 0.016233
15 | 32.13 | 14.696 | 0.080702 | 7.7222 | 0.016238 |  | 15 | 7.7222 | 32.13 | 14.696 | 0.080702 | 0.016238
16 | 32.14 | 14.696 | 0.080701 | 7.7246 | 0.016243 |  | 16 | 7.7246 | 32.14 | 14.696 | 0.080701 | 0.016243
17 | 32.15 | 14.696 | 0.080699 | 7.727 | 0.016248 |  | 17 | 7.727 | 32.15 | 14.696 | 0.080699 | 0.016248
18 | 32.16 | 14.696 | 0.080697 | 7.7294 | 0.016253 |  | 18 | 7.7294 | 32.16 | 14.696 | 0.080697 | 0.016253
19 | 32.17 | 14.696 | 0.080696 | 7.7318 | 0.016258 |  | 19 | 7.7318 | 32.17 | 14.696 | 0.080696 | 0.016258 |  |  |  | Temperature | Pressure | Density | Enthalpy | Entropy | Temperature | Pressure | Density | Enthalpy | Entropy
20 | 32.18 | 14.696 | 0.080694 | 7.7342 | 0.016263 |  | 20 | 7.7342 | 32.18 | 14.696 | 0.080694 | 0.016263 |  |  |  | (F) | (psia) | (lbm/ft^3) | (Btu/lbm) | (Btu/lbm-R) | (F) | (psia) | (lbm/ft^3) | (Btu/lbm) | (Btu/lbm-R)
21 | 32.19 | 14.696 | 0.080692 | 7.7366 | 0.016268 |  | 21 | 7.7366 | 32.19 | 14.696 | 0.080692 | 0.016268 |  |  |  | 40 | 14.696 | 0.079427 | 173.7 | 0.91028 | 40 | 10 | 0.054037 | 173.74 | 0.93676
22 | 32.2 | 14.696 | 0.080691 | 7.739 | 0.016272 |  | 22 | 7.739 | 32.2 | 14.696 | 0.080691 | 0.016272 |  |  |  | 45 | 14.696 | 0.078637 | 174.9 | 0.91268 | 45 | 10 | 0.053501 | 174.94 | 0.93915
23 | 32.21 | 14.696 | 0.080689 | 7.7414 | 0.016277 |  | 23 | 7.7414 | 32.21 | 14.696 | 0.080689 | 0.016277 |  |  |  | 50 | 14.696 | 0.077863 | 176.1 | 0.91505 | 50 | 10 | 0.052975 | 176.14 | 0.94152
24 | 32.22 | 14.696 | 0.080687 | 7.7438 | 0.016282 |  | 24 | 7.7438 | 32.22 | 14.696 | 0.080687 | 0.016282 |  |  |  | 60 | 14.696 | 0.076361 | 178.51 | 0.91972 | 60 | 10 | 0.051953 | 178.54 | 0.94619
25 | 32.23 | 14.696 | 0.080686 | 7.7462 | 0.016287 |  | 25 | 7.7462 | 32.23 | 14.696 | 0.080686 | 0.016287 |  |  |  | 80 | 14.696 | 0.073523 | 183.32 | 0.9288 | 80 | 10 | 0.050024 | 183.35 | 0.95526
26 | 32.24 | 14.696 | 0.080684 | 7.7486 | 0.016292 |  | 26 | 7.7486 | 32.24 | 14.696 | 0.080684 | 0.016292 |  |  |  | 100 | 14.696 | 0.070889 | 188.13 | 0.93755 | 100 | 10 | 0.048233 | 188.16 | 0.96401
27 | 32.25 | 14.696 | 0.080683 | 7.751 | 0.016297 |  | 27 | 7.751 | 32.25 | 14.696 | 0.080683 | 0.016297
28 | 32.26 | 14.696 | 0.080681 | 7.7534 | 0.016302 |  | 28 | 7.7534 | 32.26 | 14.696 | 0.080681 | 0.016302 |  |  |  |  | 0.0057176
29 | 32.27 | 14.696 | 0.080679 | 7.7558 | 0.016307 |  | 29 | 7.7558 | 32.27 | 14.696 | 0.080679 | 0.016307
30 | 32.28 | 14.696 | 0.080678 | 7.7582 | 0.016312 |  | 30 | 7.7582 | 32.28 | 14.696 | 0.080678 | 0.016312
31 | 32.29 | 14.696 | 0.080676 | 7.7606 | 0.016316 |  | 31 | 7.7606 | 32.29 | 14.696 | 0.080676 | 0.016316
32 | 32.3 | 14.696 | 0.080674 | 7.763 | 0.016321 |  | 32 | 7.763 | 32.3 | 14.696 | 0.080674 | 0.016321
33 | 32.31 | 14.696 | 0.080673 | 7.7655 | 0.016326 |  | 33 | 7.7655 | 32.31 | 14.696 | 0.080673 | 0.016326
34 | 32.32 | 14.696 | 0.080671 | 7.7679 | 0.016331 |  | 34 | 7.7679 | 32.32 | 14.696 | 0.080671 | 0.016331
35 | 32.33 | 14.696 | 0.080669 | 7.7703 | 0.016336 |  | 35 | 7.7703 | 32.33 | 14.696 | 0.080669 | 0.016336
36 | 32.34 | 14.696 | 0.080668 | 7.7727 | 0.016341 |  | 36 | 7.7727 | 32.34 | 14.696 | 0.080668 | 0.016341
37 | 32.35 | 14.696 | 0.080666 | 7.7751 | 0.016346 |  | 37 | 7.7751 | 32.35 | 14.696 | 0.080666 | 0.016346
38 | 32.36 | 14.696 | 0.080664 | 7.7775 | 0.016351 |  | 38 | 7.7775 | 32.36 | 14.696 | 0.080664 | 0.016351
39 | 32.37 | 14.696 | 0.080663 | 7.7799 | 0.016356 |  | 39 | 7.7799 | 32.37 | 14.696 | 0.080663 | 0.016356
40 | 32.38 | 14.696 | 0.080661 | 7.7823 | 0.01636 |  | 40 | 7.7823 | 32.38 | 14.696 | 0.080661 | 0.01636
41 | 32.39 | 14.696 | 0.08066 | 7.7847 | 0.016365 |  | 41 | 7.7847 | 32.39 | 14.696 | 0.08066 | 0.016365
42 | 32.4 | 14.696 | 0.080658 | 7.7871 | 0.01637 |  | 42 | 7.7871 | 32.4 | 14.696 | 0.080658 | 0.01637
43 | 32.41 | 14.696 | 0.080656 | 7.7895 | 0.016375 |  | 43 | 7.7895 | 32.41 | 14.696 | 0.080656 | 0.016375
44 | 32.42 | 14.696 | 0.080655 | 7.7919 | 0.01638 |  | 44 | 7.7919 | 32.42 | 14.696 | 0.080655 | 0.01638
45 | 32.43 | 14.696 | 0.080653 | 7.7943 | 0.016385 |  | 45 | 7.7943 | 32.43 | 14.696 | 0.080653 | 0.016385
46 | 32.44 | 14.696 | 0.080651 | 7.7967 | 0.01639 |  | 46 | 7.7967 | 32.44 | 14.696 | 0.080651 | 0.01639
47 | 32.45 | 14.696 | 0.08065 | 7.7991 | 0.016395 |  | 47 | 7.7991 | 32.45 | 14.696 | 0.08065 | 0.016395
48 | 32.46 | 14.696 | 0.080648 | 7.8015 | 0.0164 |  | 48 | 7.8015 | 32.46 | 14.696 | 0.080648 | 0.0164
49 | 32.47 | 14.696 | 0.080646 | 7.8039 | 0.016404 |  | 49 | 7.8039 | 32.47 | 14.696 | 0.080646 | 0.016404
50 | 32.48 | 14.696 | 0.080645 | 7.8063 | 0.016409 |  | 50 | 7.8063 | 32.48 | 14.696 | 0.080645 | 0.016409
51 | 32.49 | 14.696 | 0.080643 | 7.8087 | 0.016414 |  | 51 | 7.8087 | 32.49 | 14.696 | 0.080643 | 0.016414
52 | 32.5 | 14.696 | 0.080641 | 7.8111 | 0.016419 |  | 52 | 7.8111 | 32.5 | 14.696 | 0.080641 | 0.016419
53 | 32.51 | 14.696 | 0.08064 | 7.8135 | 0.016424 |  | 53 | 7.8135 | 32.51 | 14.696 | 0.08064 | 0.016424
54 | 32.52 | 14.696 | 0.080638 | 7.8159 | 0.016429 |  | 54 | 7.8159 | 32.52 | 14.696 | 0.080638 | 0.016429
55 | 32.53 | 14.696 | 0.080637 | 7.8183 | 0.016434 |  | 55 | 7.8183 | 32.53 | 14.696 | 0.080637 | 0.016434
56 | 32.54 | 14.696 | 0.080635 | 7.8207 | 0.016439 |  | 56 | 7.8207 | 32.54 | 14.696 | 0.080635 | 0.016439
57 | 32.55 | 14.696 | 0.080633 | 7.8231 | 0.016443 |  | 57 | 7.8231 | 32.55 | 14.696 | 0.080633 | 0.016443
58 | 32.56 | 14.696 | 0.080632 | 7.8255 | 0.016448 |  | 58 | 7.8255 | 32.56 | 14.696 | 0.080632 | 0.016448
59 | 32.57 | 14.696 | 0.08063 | 7.8279 | 0.016453 |  | 59 | 7.8279 | 32.57 | 14.696 | 0.08063 | 0.016453
60 | 32.58 | 14.696 | 0.080628 | 7.8304 | 0.016458 |  | 60 | 7.8304 | 32.58 | 14.696 | 0.080628 | 0.016458
61 | 32.59 | 14.696 | 0.080627 | 7.8328 | 0.016463 |  | 61 | 7.8328 | 32.59 | 14.696 | 0.080627 | 0.016463
62 | 32.6 | 14.696 | 0.080625 | 7.8352 | 0.016468 |  | 62 | 7.8352 | 32.6 | 14.696 | 0.080625 | 0.016468
63 | 32.61 | 14.696 | 0.080623 | 7.8376 | 0.016473 |  | 63 | 7.8376 | 32.61 | 14.696 | 0.080623 | 0.016473
64 | 32.62 | 14.696 | 0.080622 | 7.84 | 0.016478 |  | 64 | 7.84 | 32.62 | 14.696 | 0.080622 | 0.016478
65 | 32.63 | 14.696 | 0.08062 | 7.8424 | 0.016483 |  | 65 | 7.8424 | 32.63 | 14.696 | 0.08062 | 0.016483
66 | 32.64 | 14.696 | 0.080618 | 7.8448 | 0.016487 |  | 66 | 7.8448 | 32.64 | 14.696 | 0.080618 | 0.016487
67 | 32.65 | 14.696 | 0.080617 | 7.8472 | 0.016492 |  | 67 | 7.8472 | 32.65 | 14.696 | 0.080617 | 0.016492
68 | 32.66 | 14.696 | 0.080615 | 7.8496 | 0.016497 |  | 68 | 7.8496 | 32.66 | 14.696 | 0.080615 | 0.016497
69 | 32.67 | 14.696 | 0.080613 | 7.852 | 0.016502 |  | 69 | 7.852 | 32.67 | 14.696 | 0.080613 | 0.016502
70 | 32.68 | 14.696 | 0.080612 | 7.8544 | 0.016507 |  | 70 | 7.8544 | 32.68 | 14.696 | 0.080612 | 0.016507
71 | 32.69 | 14.696 | 0.08061 | 7.8568 | 0.016512 |  | 71 | 7.8568 | 32.69 | 14.696 | 0.08061 | 0.016512
72 | 32.7 | 14.696 | 0.080609 | 7.8592 | 0.016517 |  | 72 | 7.8592 | 32.7 | 14.696 | 0.080609 | 0.016517
73 | 32.71 | 14.696 | 0.080607 | 7.8616 | 0.016522 |  | 73 | 7.8616 | 32.71 | 14.696 | 0.080607 | 0.016522
74 | 32.72 | 14.696 | 0.080605 | 7.864 | 0.016526 |  | 74 | 7.864 | 32.72 | 14.696 | 0.080605 | 0.016526
75 | 32.73 | 14.696 | 0.080604 | 7.8664 | 0.016531 |  | 75 | 7.8664 | 32.73 | 14.696 | 0.080604 | 0.016531
76 | 32.74 | 14.696 | 0.080602 | 7.8688 | 0.016536 |  | 76 | 7.8688 | 32.74 | 14.696 | 0.080602 | 0.016536
77 | 32.75 | 14.696 | 0.0806 | 7.8712 | 0.016541 |  | 77 | 7.8712 | 32.75 | 14.696 | 0.0806 | 0.016541
78 | 32.76 | 14.696 | 0.080599 | 7.8736 | 0.016546 |  | 78 | 7.8736 | 32.76 | 14.696 | 0.080599 | 0.016546
79 | 32.77 | 14.696 | 0.080597 | 7.876 | 0.016551 |  | 79 | 7.876 | 32.77 | 14.696 | 0.080597 | 0.016551
80 | 32.78 | 14.696 | 0.080595 | 7.8784 | 0.016556 |  | 80 | 7.8784 | 32.78 | 14.696 | 0.080595 | 0.016556
81 | 32.79 | 14.696 | 0.080594 | 7.8808 | 0.016561 |  | 81 | 7.8808 | 32.79 | 14.696 | 0.080594 | 0.016561
82 | 32.8 | 14.696 | 0.080592 | 7.8832 | 0.016566 |  | 82 | 7.8832 | 32.8 | 14.696 | 0.080592 | 0.016566
83 | 32.81 | 14.696 | 0.08059 | 7.8856 | 0.01657 |  | 83 | 7.8856 | 32.81 | 14.696 | 0.08059 | 0.01657
84 | 32.82 | 14.696 | 0.080589 | 7.888 | 0.016575 |  | 84 | 7.888 | 32.82 | 14.696 | 0.080589 | 0.016575
85 | 32.83 | 14.696 | 0.080587 | 7.8904 | 0.01658 |  | 85 | 7.8904 | 32.83 | 14.696 | 0.080587 | 0.01658
86 | 32.84 | 14.696 | 0.080586 | 7.8928 | 0.016585 |  | 86 | 7.8928 | 32.84 | 14.696 | 0.080586 | 0.016585
87 | 32.85 | 14.696 | 0.080584 | 7.8953 | 0.01659 |  | 87 | 7.8953 | 32.85 | 14.696 | 0.080584 | 0.01659
88 | 32.86 | 14.696 | 0.080582 | 7.8977 | 0.016595 |  | 88 | 7.8977 | 32.86 | 14.696 | 0.080582 | 0.016595
89 | 32.87 | 14.696 | 0.080581 | 7.9001 | 0.0166 |  | 89 | 7.9001 | 32.87 | 14.696 | 0.080581 | 0.0166
90 | 32.88 | 14.696 | 0.080579 | 7.9025 | 0.016605 |  | 90 | 7.9025 | 32.88 | 14.696 | 0.080579 | 0.016605
91 | 32.89 | 14.696 | 0.080577 | 7.9049 | 0.016609 |  | 91 | 7.9049 | 32.89 | 14.696 | 0.080577 | 0.016609
92 | 32.9 | 14.696 | 0.080576 | 7.9073 | 0.016614 |  | 92 | 7.9073 | 32.9 | 14.696 | 0.080576 | 0.016614
93 | 32.91 | 14.696 | 0.080574 | 7.9097 | 0.016619 |  | 93 | 7.9097 | 32.91 | 14.696 | 0.080574 | 0.016619
94 | 32.92 | 14.696 | 0.080572 | 7.9121 | 0.016624 |  | 94 | 7.9121 | 32.92 | 14.696 | 0.080572 | 0.016624
95 | 32.93 | 14.696 | 0.080571 | 7.9145 | 0.016629 |  | 95 | 7.9145 | 32.93 | 14.696 | 0.080571 | 0.016629
96 | 32.94 | 14.696 | 0.080569 | 7.9169 | 0.016634 |  | 96 | 7.9169 | 32.94 | 14.696 | 0.080569 | 0.016634
97 | 32.95 | 14.696 | 0.080568 | 7.9193 | 0.016639 |  | 97 | 7.9193 | 32.95 | 14.696 | 0.080568 | 0.016639
98 | 32.96 | 14.696 | 0.080566 | 7.9217 | 0.016644 |  | 98 | 7.9217 | 32.96 | 14.696 | 0.080566 | 0.016644
99 | 32.97 | 14.696 | 0.080564 | 7.9241 | 0.016648 |  | 99 | 7.9241 | 32.97 | 14.696 | 0.080564 | 0.016648
100 | 32.98 | 14.696 | 0.080563 | 7.9265 | 0.016653 |  | 100 | 7.9265 | 32.98 | 14.696 | 0.080563 | 0.016653
101 | 32.99 | 14.696 | 0.080561 | 7.9289 | 0.016658 |  | 101 | 7.9289 | 32.99 | 14.696 | 0.080561 | 0.016658
102 | 33 | 14.696 | 0.080559 | 7.9313 | 0.016663 |  | 102 | 7.9313 | 33 | 14.696 | 0.080559 | 0.016663
103 | 33.01 | 14.696 | 0.080558 | 7.9337 | 0.016668 |  | 103 | 7.9337 | 33.01 | 14.696 | 0.080558 | 0.016668
104 | 33.02 | 14.696 | 0.080556 | 7.9361 | 0.016673 |  | 104 | 7.9361 | 33.02 | 14.696 | 0.080556 | 0.016673
105 | 33.03 | 14.696 | 0.080554 | 7.9385 | 0.016678 |  | 105 | 7.9385 | 33.03 | 14.696 | 0.080554 | 0.016678
106 | 33.04 | 14.696 | 0.080553 | 7.9409 | 0.016683 |  | 106 | 7.9409 | 33.04 | 14.696 | 0.080553 | 0.016683
107 | 33.05 | 14.696 | 0.080551 | 7.9433 | 0.016688 |  | 107 | 7.9433 | 33.05 | 14.696 | 0.080551 | 0.016688
108 | 33.06 | 14.696 | 0.080549 | 7.9457 | 0.016692 |  | 108 | 7.9457 | 33.06 | 14.696 | 0.080549 | 0.016692
109 | 33.07 | 14.696 | 0.080548 | 7.9481 | 0.016697 |  | 109 | 7.9481 | 33.07 | 14.696 | 0.080548 | 0.016697
110 | 33.08 | 14.696 | 0.080546 | 7.9505 | 0.016702 |  | 110 | 7.9505 | 33.08 | 14.696 | 0.080546 | 0.016702
111 | 33.09 | 14.696 | 0.080545 | 7.9529 | 0.016707 |  | 111 | 7.9529 | 33.09 | 14.696 | 0.080545 | 0.016707
112 | 33.1 | 14.696 | 0.080543 | 7.9553 | 0.016712 |  | 112 | 7.9553 | 33.1 | 14.696 | 0.080543 | 0.016712
113 | 33.11 | 14.696 | 0.080541 | 7.9577 | 0.016717 |  | 113 | 7.9577 | 33.11 | 14.696 | 0.080541 | 0.016717
114 | 33.12 | 14.696 | 0.08054 | 7.9601 | 0.016722 |  | 114 | 7.9601 | 33.12 | 14.696 | 0.08054 | 0.016722
115 | 33.13 | 14.696 | 0.080538 | 7.9626 | 0.016727 |  | 115 | 7.9626 | 33.13 | 14.696 | 0.080538 | 0.016727
116 | 33.14 | 14.696 | 0.080536 | 7.965 | 0.016731 |  | 116 | 7.965 | 33.14 | 14.696 | 0.080536 | 0.016731
117 | 33.15 | 14.696 | 0.080535 | 7.9674 | 0.016736 |  | 117 | 7.9674 | 33.15 | 14.696 | 0.080535 | 0.016736
118 | 33.16 | 14.696 | 0.080533 | 7.9698 | 0.016741 |  | 118 | 7.9698 | 33.16 | 14.696 | 0.080533 | 0.016741
119 | 33.17 | 14.696 | 0.080531 | 7.9722 | 0.016746 |  | 119 | 7.9722 | 33.17 | 14.696 | 0.080531 | 0.016746
120 | 33.18 | 14.696 | 0.08053 | 7.9746 | 0.016751 |  | 120 | 7.9746 | 33.18 | 14.696 | 0.08053 | 0.016751
121 | 33.19 | 14.696 | 0.080528 | 7.977 | 0.016756 |  | 121 | 7.977 | 33.19 | 14.696 | 0.080528 | 0.016756
122 | 33.2 | 14.696 | 0.080526 | 7.9794 | 0.016761 |  | 122 | 7.9794 | 33.2 | 14.696 | 0.080526 | 0.016761
123 | 33.21 | 14.696 | 0.080525 | 7.9818 | 0.016766 |  | 123 | 7.9818 | 33.21 | 14.696 | 0.080525 | 0.016766
124 | 33.22 | 14.696 | 0.080523 | 7.9842 | 0.01677 |  | 124 | 7.9842 | 33.22 | 14.696 | 0.080523 | 0.01677
125 | 33.23 | 14.696 | 0.080522 | 7.9866 | 0.016775 |  | 125 | 7.9866 | 33.23 | 14.696 | 0.080522 | 0.016775
126 | 33.24 | 14.696 | 0.08052 | 7.989 | 0.01678 |  | 126 | 7.989 | 33.24 | 14.696 | 0.08052 | 0.01678
127 | 33.25 | 14.696 | 0.080518 | 7.9914 | 0.016785 |  | 127 | 7.9914 | 33.25 | 14.696 | 0.080518 | 0.016785
128 | 33.26 | 14.696 | 0.080517 | 7.9938 | 0.01679 |  | 128 | 7.9938 | 33.26 | 14.696 | 0.080517 | 0.01679
129 | 33.27 | 14.696 | 0.080515 | 7.9962 | 0.016795 |  | 129 | 7.9962 | 33.27 | 14.696 | 0.080515 | 0.016795
130 | 33.28 | 14.696 | 0.080513 | 7.9986 | 0.0168 |  | 130 | 7.9986 | 33.28 | 14.696 | 0.080513 | 0.0168
131 | 33.29 | 14.696 | 0.080512 | 8.001 | 0.016805 |  | 131 | 8.001 | 33.29 | 14.696 | 0.080512 | 0.016805
132 | 33.3 | 14.696 | 0.08051 | 8.0034 | 0.016809 |  | 132 | 8.0034 | 33.3 | 14.696 | 0.08051 | 0.016809
133 | 33.31 | 14.696 | 0.080508 | 8.0058 | 0.016814 |  | 133 | 8.0058 | 33.31 | 14.696 | 0.080508 | 0.016814
134 | 33.32 | 14.696 | 0.080507 | 8.0082 | 0.016819 |  | 134 | 8.0082 | 33.32 | 14.696 | 0.080507 | 0.016819
135 | 33.33 | 14.696 | 0.080505 | 8.0106 | 0.016824 |  | 135 | 8.0106 | 33.33 | 14.696 | 0.080505 | 0.016824
136 | 33.34 | 14.696 | 0.080504 | 8.013 | 0.016829 |  | 136 | 8.013 | 33.34 | 14.696 | 0.080504 | 0.016829
137 | 33.35 | 14.696 | 0.080502 | 8.0154 | 0.016834 |  | 137 | 8.0154 | 33.35 | 14.696 | 0.080502 | 0.016834
138 | 33.36 | 14.696 | 0.0805 | 8.0178 | 0.016839 |  | 138 | 8.0178 | 33.36 | 14.696 | 0.0805 | 0.016839
139 | 33.37 | 14.696 | 0.080499 | 8.0202 | 0.016844 |  | 139 | 8.0202 | 33.37 | 14.696 | 0.080499 | 0.016844
140 | 33.38 | 14.696 | 0.080497 | 8.0226 | 0.016848 |  | 140 | 8.0226 | 33.38 | 14.696 | 0.080497 | 0.016848
141 | 33.39 | 14.696 | 0.080495 | 8.025 | 0.016853 |  | 141 | 8.025 | 33.39 | 14.696 | 0.080495 | 0.016853
142 | 33.4 | 14.696 | 0.080494 | 8.0275 | 0.016858 |  | 142 | 8.0275 | 33.4 | 14.696 | 0.080494 | 0.016858
143 | 33.41 | 14.696 | 0.080492 | 8.0299 | 0.016863 |  | 143 | 8.0299 | 33.41 | 14.696 | 0.080492 | 0.016863
144 | 33.42 | 14.696 | 0.08049 | 8.0323 | 0.016868 |  | 144 | 8.0323 | 33.42 | 14.696 | 0.08049 | 0.016868
145 | 33.43 | 14.696 | 0.080489 | 8.0347 | 0.016873 |  | 145 | 8.0347 | 33.43 | 14.696 | 0.080489 | 0.016873
146 | 33.44 | 14.696 | 0.080487 | 8.0371 | 0.016878 |  | 146 | 8.0371 | 33.44 | 14.696 | 0.080487 | 0.016878
147 | 33.45 | 14.696 | 0.080486 | 8.0395 | 0.016883 |  | 147 | 8.0395 | 33.45 | 14.696 | 0.080486 | 0.016883
148 | 33.46 | 14.696 | 0.080484 | 8.0419 | 0.016887 |  | 148 | 8.0419 | 33.46 | 14.696 | 0.080484 | 0.016887
149 | 33.47 | 14.696 | 0.080482 | 8.0443 | 0.016892 |  | 149 | 8.0443 | 33.47 | 14.696 | 0.080482 | 0.016892
150 | 33.48 | 14.696 | 0.080481 | 8.0467 | 0.016897 |  | 150 | 8.0467 | 33.48 | 14.696 | 0.080481 | 0.016897
151 | 33.49 | 14.696 | 0.080479 | 8.0491 | 0.016902 |  | 151 | 8.0491 | 33.49 | 14.696 | 0.080479 | 0.016902
152 | 33.5 | 14.696 | 0.080477 | 8.0515 | 0.016907 |  | 152 | 8.0515 | 33.5 | 14.696 | 0.080477 | 0.016907
153 | 33.51 | 14.696 | 0.080476 | 8.0539 | 0.016912 |  | 153 | 8.0539 | 33.51 | 14.696 | 0.080476 | 0.016912
154 | 33.52 | 14.696 | 0.080474 | 8.0563 | 0.016917 |  | 154 | 8.0563 | 33.52 | 14.696 | 0.080474 | 0.016917
155 | 33.53 | 14.696 | 0.080472 | 8.0587 | 0.016922 |  | 155 | 8.0587 | 33.53 | 14.696 | 0.080472 | 0.016922
156 | 33.54 | 14.696 | 0.080471 | 8.0611 | 0.016926 |  | 156 | 8.0611 | 33.54 | 14.696 | 0.080471 | 0.016926
157 | 33.55 | 14.696 | 0.080469 | 8.0635 | 0.016931 |  | 157 | 8.0635 | 33.55 | 14.696 | 0.080469 | 0.016931
158 | 33.56 | 14.696 | 0.080468 | 8.0659 | 0.016936 |  | 158 | 8.0659 | 33.56 | 14.696 | 0.080468 | 0.016936
159 | 33.57 | 14.696 | 0.080466 | 8.0683 | 0.016941 |  | 159 | 8.0683 | 33.57 | 14.696 | 0.080466 | 0.016941
160 | 33.58 | 14.696 | 0.080464 | 8.0707 | 0.016946 |  | 160 | 8.0707 | 33.58 | 14.696 | 0.080464 | 0.016946
161 | 33.59 | 14.696 | 0.080463 | 8.0731 | 0.016951 |  | 161 | 8.0731 | 33.59 | 14.696 | 0.080463 | 0.016951
162 | 33.6 | 14.696 | 0.080461 | 8.0755 | 0.016956 |  | 162 | 8.0755 | 33.6 | 14.696 | 0.080461 | 0.016956
163 | 33.61 | 14.696 | 0.080459 | 8.0779 | 0.016961 |  | 163 | 8.0779 | 33.61 | 14.696 | 0.080459 | 0.016961
164 | 33.62 | 14.696 | 0.080458 | 8.0803 | 0.016965 |  | 164 | 8.0803 | 33.62 | 14.696 | 0.080458 | 0.016965
165 | 33.63 | 14.696 | 0.080456 | 8.0827 | 0.01697 |  | 165 | 8.0827 | 33.63 | 14.696 | 0.080456 | 0.01697
166 | 33.64 | 14.696 | 0.080454 | 8.0851 | 0.016975 |  | 166 | 8.0851 | 33.64 | 14.696 | 0.080454 | 0.016975
167 | 33.65 | 14.696 | 0.080453 | 8.0875 | 0.01698 |  | 167 | 8.0875 | 33.65 | 14.696 | 0.080453 | 0.01698
168 | 33.66 | 14.696 | 0.080451 | 8.0899 | 0.016985 |  | 168 | 8.0899 | 33.66 | 14.696 | 0.080451 | 0.016985
169 | 33.67 | 14.696 | 0.08045 | 8.0924 | 0.01699 |  | 169 | 8.0924 | 33.67 | 14.696 | 0.08045 | 0.01699
170 | 33.68 | 14.696 | 0.080448 | 8.0948 | 0.016995 |  | 170 | 8.0948 | 33.68 | 14.696 | 0.080448 | 0.016995
171 | 33.69 | 14.696 | 0.080446 | 8.0972 | 0.017 |  | 171 | 8.0972 | 33.69 | 14.696 | 0.080446 | 0.017
172 | 33.7 | 14.696 | 0.080445 | 8.0996 | 0.017004 |  | 172 | 8.0996 | 33.7 | 14.696 | 0.080445 | 0.017004
173 | 33.71 | 14.696 | 0.080443 | 8.102 | 0.017009 |  | 173 | 8.102 | 33.71 | 14.696 | 0.080443 | 0.017009
174 | 33.72 | 14.696 | 0.080441 | 8.1044 | 0.017014 |  | 174 | 8.1044 | 33.72 | 14.696 | 0.080441 | 0.017014
175 | 33.73 | 14.696 | 0.08044 | 8.1068 | 0.017019 |  | 175 | 8.1068 | 33.73 | 14.696 | 0.08044 | 0.017019
176 | 33.74 | 14.696 | 0.080438 | 8.1092 | 0.017024 |  | 176 | 8.1092 | 33.74 | 14.696 | 0.080438 | 0.017024
177 | 33.75 | 14.696 | 0.080436 | 8.1116 | 0.017029 |  | 177 | 8.1116 | 33.75 | 14.696 | 0.080436 | 0.017029
178 | 33.76 | 14.696 | 0.080435 | 8.114 | 0.017034 |  | 178 | 8.114 | 33.76 | 14.696 | 0.080435 | 0.017034
179 | 33.77 | 14.696 | 0.080433 | 8.1164 | 0.017038 |  | 179 | 8.1164 | 33.77 | 14.696 | 0.080433 | 0.017038
180 | 33.78 | 14.696 | 0.080432 | 8.1188 | 0.017043 |  | 180 | 8.1188 | 33.78 | 14.696 | 0.080432 | 0.017043
181 | 33.79 | 14.696 | 0.08043 | 8.1212 | 0.017048 |  | 181 | 8.1212 | 33.79 | 14.696 | 0.08043 | 0.017048
182 | 33.8 | 14.696 | 0.080428 | 8.1236 | 0.017053 |  | 182 | 8.1236 | 33.8 | 14.696 | 0.080428 | 0.017053
183 | 33.81 | 14.696 | 0.080427 | 8.126 | 0.017058 |  | 183 | 8.126 | 33.81 | 14.696 | 0.080427 | 0.017058
184 | 33.82 | 14.696 | 0.080425 | 8.1284 | 0.017063 |  | 184 | 8.1284 | 33.82 | 14.696 | 0.080425 | 0.017063
185 | 33.83 | 14.696 | 0.080423 | 8.1308 | 0.017068 |  | 185 | 8.1308 | 33.83 | 14.696 | 0.080423 | 0.017068
186 | 33.84 | 14.696 | 0.080422 | 8.1332 | 0.017073 |  | 186 | 8.1332 | 33.84 | 14.696 | 0.080422 | 0.017073
187 | 33.85 | 14.696 | 0.08042 | 8.1356 | 0.017077 |  | 187 | 8.1356 | 33.85 | 14.696 | 0.08042 | 0.017077
188 | 33.86 | 14.696 | 0.080418 | 8.138 | 0.017082 |  | 188 | 8.138 | 33.86 | 14.696 | 0.080418 | 0.017082
189 | 33.87 | 14.696 | 0.080417 | 8.1404 | 0.017087 |  | 189 | 8.1404 | 33.87 | 14.696 | 0.080417 | 0.017087
190 | 33.88 | 14.696 | 0.080415 | 8.1428 | 0.017092 |  | 190 | 8.1428 | 33.88 | 14.696 | 0.080415 | 0.017092
191 | 33.89 | 14.696 | 0.080414 | 8.1452 | 0.017097 |  | 191 | 8.1452 | 33.89 | 14.696 | 0.080414 | 0.017097
192 | 33.9 | 14.696 | 0.080412 | 8.1476 | 0.017102 |  | 192 | 8.1476 | 33.9 | 14.696 | 0.080412 | 0.017102
193 | 33.91 | 14.696 | 0.08041 | 8.15 | 0.017107 |  | 193 | 8.15 | 33.91 | 14.696 | 0.08041 | 0.017107
194 | 33.92 | 14.696 | 0.080409 | 8.1524 | 0.017112 |  | 194 | 8.1524 | 33.92 | 14.696 | 0.080409 | 0.017112
195 | 33.93 | 14.696 | 0.080407 | 8.1548 | 0.017116 |  | 195 | 8.1548 | 33.93 | 14.696 | 0.080407 | 0.017116
196 | 33.94 | 14.696 | 0.080405 | 8.1573 | 0.017121 |  | 196 | 8.1573 | 33.94 | 14.696 | 0.080405 | 0.017121
197 | 33.95 | 14.696 | 0.080404 | 8.1597 | 0.017126 |  | 197 | 8.1597 | 33.95 | 14.696 | 0.080404 | 0.017126
198 | 33.96 | 14.696 | 0.080402 | 8.1621 | 0.017131 |  | 198 | 8.1621 | 33.96 | 14.696 | 0.080402 | 0.017131
199 | 33.97 | 14.696 | 0.0804 | 8.1645 | 0.017136 |  | 199 | 8.1645 | 33.97 | 14.696 | 0.0804 | 0.017136
200 | 33.98 | 14.696 | 0.080399 | 8.1669 | 0.017141 |  | 200 | 8.1669 | 33.98 | 14.696 | 0.080399 | 0.017141
201 | 33.99 | 14.696 | 0.080397 | 8.1693 | 0.017146 |  | 201 | 8.1693 | 33.99 | 14.696 | 0.080397 | 0.017146
202 | 34 | 14.696 | 0.080396 | 8.1717 | 0.017151 |  | 202 | 8.1717 | 34 | 14.696 | 0.080396 | 0.017151
203 | 34.01 | 14.696 | 0.080394 | 8.1741 | 0.017155 |  | 203 | 8.1741 | 34.01 | 14.696 | 0.080394 | 0.017155
204 | 34.02 | 14.696 | 0.080392 | 8.1765 | 0.01716 |  | 204 | 8.1765 | 34.02 | 14.696 | 0.080392 | 0.01716
205 | 34.03 | 14.696 | 0.080391 | 8.1789 | 0.017165 |  | 205 | 8.1789 | 34.03 | 14.696 | 0.080391 | 0.017165
206 | 34.04 | 14.696 | 0.080389 | 8.1813 | 0.01717 |  | 206 | 8.1813 | 34.04 | 14.696 | 0.080389 | 0.01717
207 | 34.05 | 14.696 | 0.080387 | 8.1837 | 0.017175 |  | 207 | 8.1837 | 34.05 | 14.696 | 0.080387 | 0.017175
208 | 34.06 | 14.696 | 0.080386 | 8.1861 | 0.01718 |  | 208 | 8.1861 | 34.06 | 14.696 | 0.080386 | 0.01718
209 | 34.07 | 14.696 | 0.080384 | 8.1885 | 0.017185 |  | 209 | 8.1885 | 34.07 | 14.696 | 0.080384 | 0.017185
210 | 34.08 | 14.696 | 0.080382 | 8.1909 | 0.017189 |  | 210 | 8.1909 | 34.08 | 14.696 | 0.080382 | 0.017189
211 | 34.09 | 14.696 | 0.080381 | 8.1933 | 0.017194 |  | 211 | 8.1933 | 34.09 | 14.696 | 0.080381 | 0.017194
212 | 34.1 | 14.696 | 0.080379 | 8.1957 | 0.017199 |  | 212 | 8.1957 | 34.1 | 14.696 | 0.080379 | 0.017199
213 | 34.11 | 14.696 | 0.080378 | 8.1981 | 0.017204 |  | 213 | 8.1981 | 34.11 | 14.696 | 0.080378 | 0.017204
214 | 34.12 | 14.696 | 0.080376 | 8.2005 | 0.017209 |  | 214 | 8.2005 | 34.12 | 14.696 | 0.080376 | 0.017209
215 | 34.13 | 14.696 | 0.080374 | 8.2029 | 0.017214 |  | 215 | 8.2029 | 34.13 | 14.696 | 0.080374 | 0.017214
216 | 34.14 | 14.696 | 0.080373 | 8.2053 | 0.017219 |  | 216 | 8.2053 | 34.14 | 14.696 | 0.080373 | 0.017219
217 | 34.15 | 14.696 | 0.080371 | 8.2077 | 0.017224 |  | 217 | 8.2077 | 34.15 | 14.696 | 0.080371 | 0.017224
218 | 34.16 | 14.696 | 0.080369 | 8.2101 | 0.017228 |  | 218 | 8.2101 | 34.16 | 14.696 | 0.080369 | 0.017228
219 | 34.17 | 14.696 | 0.080368 | 8.2125 | 0.017233 |  | 219 | 8.2125 | 34.17 | 14.696 | 0.080368 | 0.017233
220 | 34.18 | 14.696 | 0.080366 | 8.2149 | 0.017238 |  | 220 | 8.2149 | 34.18 | 14.696 | 0.080366 | 0.017238
221 | 34.19 | 14.696 | 0.080365 | 8.2173 | 0.017243 |  | 221 | 8.2173 | 34.19 | 14.696 | 0.080365 | 0.017243
222 | 34.2 | 14.696 | 0.080363 | 8.2197 | 0.017248 |  | 222 | 8.2197 | 34.2 | 14.696 | 0.080363 | 0.017248
223 | 34.21 | 14.696 | 0.080361 | 8.2222 | 0.017253 |  | 223 | 8.2222 | 34.21 | 14.696 | 0.080361 | 0.017253
224 | 34.22 | 14.696 | 0.08036 | 8.2246 | 0.017258 |  | 224 | 8.2246 | 34.22 | 14.696 | 0.08036 | 0.017258
225 | 34.23 | 14.696 | 0.080358 | 8.227 | 0.017262 |  | 225 | 8.227 | 34.23 | 14.696 | 0.080358 | 0.017262
226 | 34.24 | 14.696 | 0.080356 | 8.2294 | 0.017267 |  | 226 | 8.2294 | 34.24 | 14.696 | 0.080356 | 0.017267
227 | 34.25 | 14.696 | 0.080355 | 8.2318 | 0.017272 |  | 227 | 8.2318 | 34.25 | 14.696 | 0.080355 | 0.017272
228 | 34.26 | 14.696 | 0.080353 | 8.2342 | 0.017277 |  | 228 | 8.2342 | 34.26 | 14.696 | 0.080353 | 0.017277
229 | 34.27 | 14.696 | 0.080351 | 8.2366 | 0.017282 |  | 229 | 8.2366 | 34.27 | 14.696 | 0.080351 | 0.017282
230 | 34.28 | 14.696 | 0.08035 | 8.239 | 0.017287 |  | 230 | 8.239 | 34.28 | 14.696 | 0.08035 | 0.017287
231 | 34.29 | 14.696 | 0.080348 | 8.2414 | 0.017292 |  | 231 | 8.2414 | 34.29 | 14.696 | 0.080348 | 0.017292
232 | 34.3 | 14.696 | 0.080347 | 8.2438 | 0.017297 |  | 232 | 8.2438 | 34.3 | 14.696 | 0.080347 | 0.017297
233 | 34.31 | 14.696 | 0.080345 | 8.2462 | 0.017301 |  | 233 | 8.2462 | 34.31 | 14.696 | 0.080345 | 0.017301
234 | 34.32 | 14.696 | 0.080343 | 8.2486 | 0.017306 |  | 234 | 8.2486 | 34.32 | 14.696 | 0.080343 | 0.017306
235 | 34.33 | 14.696 | 0.080342 | 8.251 | 0.017311 |  | 235 | 8.251 | 34.33 | 14.696 | 0.080342 | 0.017311
236 | 34.34 | 14.696 | 0.08034 | 8.2534 | 0.017316 |  | 236 | 8.2534 | 34.34 | 14.696 | 0.08034 | 0.017316
237 | 34.35 | 14.696 | 0.080338 | 8.2558 | 0.017321 |  | 237 | 8.2558 | 34.35 | 14.696 | 0.080338 | 0.017321
238 | 34.36 | 14.696 | 0.080337 | 8.2582 | 0.017326 |  | 238 | 8.2582 | 34.36 | 14.696 | 0.080337 | 0.017326
239 | 34.37 | 14.696 | 0.080335 | 8.2606 | 0.017331 |  | 239 | 8.2606 | 34.37 | 14.696 | 0.080335 | 0.017331
240 | 34.38 | 14.696 | 0.080333 | 8.263 | 0.017335 |  | 240 | 8.263 | 34.38 | 14.696 | 0.080333 | 0.017335
241 | 34.39 | 14.696 | 0.080332 | 8.2654 | 0.01734 |  | 241 | 8.2654 | 34.39 | 14.696 | 0.080332 | 0.01734
242 | 34.4 | 14.696 | 0.08033 | 8.2678 | 0.017345 |  | 242 | 8.2678 | 34.4 | 14.696 | 0.08033 | 0.017345
243 | 34.41 | 14.696 | 0.080329 | 8.2702 | 0.01735 |  | 243 | 8.2702 | 34.41 | 14.696 | 0.080329 | 0.01735
244 | 34.42 | 14.696 | 0.080327 | 8.2726 | 0.017355 |  | 244 | 8.2726 | 34.42 | 14.696 | 0.080327 | 0.017355
245 | 34.43 | 14.696 | 0.080325 | 8.275 | 0.01736 |  | 245 | 8.275 | 34.43 | 14.696 | 0.080325 | 0.01736
246 | 34.44 | 14.696 | 0.080324 | 8.2774 | 0.017365 |  | 246 | 8.2774 | 34.44 | 14.696 | 0.080324 | 0.017365
247 | 34.45 | 14.696 | 0.080322 | 8.2798 | 0.01737 |  | 247 | 8.2798 | 34.45 | 14.696 | 0.080322 | 0.01737
248 | 34.46 | 14.696 | 0.08032 | 8.2822 | 0.017374 |  | 248 | 8.2822 | 34.46 | 14.696 | 0.08032 | 0.017374
249 | 34.47 | 14.696 | 0.080319 | 8.2846 | 0.017379 |  | 249 | 8.2846 | 34.47 | 14.696 | 0.080319 | 0.017379
250 | 34.48 | 14.696 | 0.080317 | 8.2871 | 0.017384 |  | 250 | 8.2871 | 34.48 | 14.696 | 0.080317 | 0.017384
251 | 34.49 | 14.696 | 0.080316 | 8.2895 | 0.017389 |  | 251 | 8.2895 | 34.49 | 14.696 | 0.080316 | 0.017389
252 | 34.5 | 14.696 | 0.080314 | 8.2919 | 0.017394 |  | 252 | 8.2919 | 34.5 | 14.696 | 0.080314 | 0.017394
253 | 34.51 | 14.696 | 0.080312 | 8.2943 | 0.017399 |  | 253 | 8.2943 | 34.51 | 14.696 | 0.080312 | 0.017399
254 | 34.52 | 14.696 | 0.080311 | 8.2967 | 0.017404 |  | 254 | 8.2967 | 34.52 | 14.696 | 0.080311 | 0.017404
255 | 34.53 | 14.696 | 0.080309 | 8.2991 | 0.017408 |  | 255 | 8.2991 | 34.53 | 14.696 | 0.080309 | 0.017408
256 | 34.54 | 14.696 | 0.080307 | 8.3015 | 0.017413 |  | 256 | 8.3015 | 34.54 | 14.696 | 0.080307 | 0.017413
257 | 34.55 | 14.696 | 0.080306 | 8.3039 | 0.017418 |  | 257 | 8.3039 | 34.55 | 14.696 | 0.080306 | 0.017418
258 | 34.56 | 14.696 | 0.080304 | 8.3063 | 0.017423 |  | 258 | 8.3063 | 34.56 | 14.696 | 0.080304 | 0.017423
259 | 34.57 | 14.696 | 0.080303 | 8.3087 | 0.017428 |  | 259 | 8.3087 | 34.57 | 14.696 | 0.080303 | 0.017428
260 | 34.58 | 14.696 | 0.080301 | 8.3111 | 0.017433 |  | 260 | 8.3111 | 34.58 | 14.696 | 0.080301 | 0.017433
261 | 34.59 | 14.696 | 0.080299 | 8.3135 | 0.017438 |  | 261 | 8.3135 | 34.59 | 14.696 | 0.080299 | 0.017438
262 | 34.6 | 14.696 | 0.080298 | 8.3159 | 0.017442 |  | 262 | 8.3159 | 34.6 | 14.696 | 0.080298 | 0.017442
263 | 34.61 | 14.696 | 0.080296 | 8.3183 | 0.017447 |  | 263 | 8.3183 | 34.61 | 14.696 | 0.080296 | 0.017447
264 | 34.62 | 14.696 | 0.080294 | 8.3207 | 0.017452 |  | 264 | 8.3207 | 34.62 | 14.696 | 0.080294 | 0.017452
265 | 34.63 | 14.696 | 0.080293 | 8.3231 | 0.017457 |  | 265 | 8.3231 | 34.63 | 14.696 | 0.080293 | 0.017457
266 | 34.64 | 14.696 | 0.080291 | 8.3255 | 0.017462 |  | 266 | 8.3255 | 34.64 | 14.696 | 0.080291 | 0.017462
267 | 34.65 | 14.696 | 0.080289 | 8.3279 | 0.017467 |  | 267 | 8.3279 | 34.65 | 14.696 | 0.080289 | 0.017467
268 | 34.66 | 14.696 | 0.080288 | 8.3303 | 0.017472 |  | 268 | 8.3303 | 34.66 | 14.696 | 0.080288 | 0.017472
269 | 34.67 | 14.696 | 0.080286 | 8.3327 | 0.017477 |  | 269 | 8.3327 | 34.67 | 14.696 | 0.080286 | 0.017477
270 | 34.68 | 14.696 | 0.080285 | 8.3351 | 0.017481 |  | 270 | 8.3351 | 34.68 | 14.696 | 0.080285 | 0.017481
271 | 34.69 | 14.696 | 0.080283 | 8.3375 | 0.017486 |  | 271 | 8.3375 | 34.69 | 14.696 | 0.080283 | 0.017486
272 | 34.7 | 14.696 | 0.080281 | 8.3399 | 0.017491 |  | 272 | 8.3399 | 34.7 | 14.696 | 0.080281 | 0.017491
273 | 34.71 | 14.696 | 0.08028 | 8.3423 | 0.017496 |  | 273 | 8.3423 | 34.71 | 14.696 | 0.08028 | 0.017496
274 | 34.72 | 14.696 | 0.080278 | 8.3447 | 0.017501 |  | 274 | 8.3447 | 34.72 | 14.696 | 0.080278 | 0.017501
275 | 34.73 | 14.696 | 0.080276 | 8.3471 | 0.017506 |  | 275 | 8.3471 | 34.73 | 14.696 | 0.080276 | 0.017506
276 | 34.74 | 14.696 | 0.080275 | 8.3495 | 0.017511 |  | 276 | 8.3495 | 34.74 | 14.696 | 0.080275 | 0.017511
277 | 34.75 | 14.696 | 0.080273 | 8.352 | 0.017515 |  | 277 | 8.352 | 34.75 | 14.696 | 0.080273 | 0.017515
278 | 34.76 | 14.696 | 0.080272 | 8.3544 | 0.01752 |  | 278 | 8.3544 | 34.76 | 14.696 | 0.080272 | 0.01752
279 | 34.77 | 14.696 | 0.08027 | 8.3568 | 0.017525 |  | 279 | 8.3568 | 34.77 | 14.696 | 0.08027 | 0.017525
280 | 34.78 | 14.696 | 0.080268 | 8.3592 | 0.01753 |  | 280 | 8.3592 | 34.78 | 14.696 | 0.080268 | 0.01753
281 | 34.79 | 14.696 | 0.080267 | 8.3616 | 0.017535 |  | 281 | 8.3616 | 34.79 | 14.696 | 0.080267 | 0.017535
282 | 34.8 | 14.696 | 0.080265 | 8.364 | 0.01754 |  | 282 | 8.364 | 34.8 | 14.696 | 0.080265 | 0.01754
283 | 34.81 | 14.696 | 0.080263 | 8.3664 | 0.017545 |  | 283 | 8.3664 | 34.81 | 14.696 | 0.080263 | 0.017545
284 | 34.82 | 14.696 | 0.080262 | 8.3688 | 0.017549 |  | 284 | 8.3688 | 34.82 | 14.696 | 0.080262 | 0.017549
285 | 34.83 | 14.696 | 0.08026 | 8.3712 | 0.017554 |  | 285 | 8.3712 | 34.83 | 14.696 | 0.08026 | 0.017554
286 | 34.84 | 14.696 | 0.080259 | 8.3736 | 0.017559 |  | 286 | 8.3736 | 34.84 | 14.696 | 0.080259 | 0.017559
287 | 34.85 | 14.696 | 0.080257 | 8.376 | 0.017564 |  | 287 | 8.376 | 34.85 | 14.696 | 0.080257 | 0.017564
288 | 34.86 | 14.696 | 0.080255 | 8.3784 | 0.017569 |  | 288 | 8.3784 | 34.86 | 14.696 | 0.080255 | 0.017569
289 | 34.87 | 14.696 | 0.080254 | 8.3808 | 0.017574 |  | 289 | 8.3808 | 34.87 | 14.696 | 0.080254 | 0.017574
290 | 34.88 | 14.696 | 0.080252 | 8.3832 | 0.017579 |  | 290 | 8.3832 | 34.88 | 14.696 | 0.080252 | 0.017579
291 | 34.89 | 14.696 | 0.08025 | 8.3856 | 0.017583 |  | 291 | 8.3856 | 34.89 | 14.696 | 0.08025 | 0.017583
292 | 34.9 | 14.696 | 0.080249 | 8.388 | 0.017588 |  | 292 | 8.388 | 34.9 | 14.696 | 0.080249 | 0.017588
293 | 34.91 | 14.696 | 0.080247 | 8.3904 | 0.017593 |  | 293 | 8.3904 | 34.91 | 14.696 | 0.080247 | 0.017593
294 | 34.92 | 14.696 | 0.080245 | 8.3928 | 0.017598 |  | 294 | 8.3928 | 34.92 | 14.696 | 0.080245 | 0.017598
295 | 34.93 | 14.696 | 0.080244 | 8.3952 | 0.017603 |  | 295 | 8.3952 | 34.93 | 14.696 | 0.080244 | 0.017603
296 | 34.94 | 14.696 | 0.080242 | 8.3976 | 0.017608 |  | 296 | 8.3976 | 34.94 | 14.696 | 0.080242 | 0.017608
297 | 34.95 | 14.696 | 0.080241 | 8.4 | 0.017613 |  | 297 | 8.4 | 34.95 | 14.696 | 0.080241 | 0.017613
298 | 34.96 | 14.696 | 0.080239 | 8.4024 | 0.017617 |  | 298 | 8.4024 | 34.96 | 14.696 | 0.080239 | 0.017617
299 | 34.97 | 14.696 | 0.080237 | 8.4048 | 0.017622 |  | 299 | 8.4048 | 34.97 | 14.696 | 0.080237 | 0.017622
300 | 34.98 | 14.696 | 0.080236 | 8.4072 | 0.017627 |  | 300 | 8.4072 | 34.98 | 14.696 | 0.080236 | 0.017627
301 | 34.99 | 14.696 | 0.080234 | 8.4096 | 0.017632 |  | 301 | 8.4096 | 34.99 | 14.696 | 0.080234 | 0.017632
302 | 35 | 14.696 | 0.080232 | 8.412 | 0.017637 |  | 302 | 8.412 | 35 | 14.696 | 0.080232 | 0.017637
303 | 35.01 | 14.696 | 0.080231 | 8.4144 | 0.017642 |  | 303 | 8.4144 | 35.01 | 14.696 | 0.080231 | 0.017642
304 | 35.02 | 14.696 | 0.080229 | 8.4169 | 0.017647 |  | 304 | 8.4169 | 35.02 | 14.696 | 0.080229 | 0.017647
305 | 35.03 | 14.696 | 0.080228 | 8.4193 | 0.017651 |  | 305 | 8.4193 | 35.03 | 14.696 | 0.080228 | 0.017651
306 | 35.04 | 14.696 | 0.080226 | 8.4217 | 0.017656 |  | 306 | 8.4217 | 35.04 | 14.696 | 0.080226 | 0.017656
307 | 35.05 | 14.696 | 0.080224 | 8.4241 | 0.017661 |  | 307 | 8.4241 | 35.05 | 14.696 | 0.080224 | 0.017661
308 | 35.06 | 14.696 | 0.080223 | 8.4265 | 0.017666 |  | 308 | 8.4265 | 35.06 | 14.696 | 0.080223 | 0.017666
309 | 35.07 | 14.696 | 0.080221 | 8.4289 | 0.017671 |  | 309 | 8.4289 | 35.07 | 14.696 | 0.080221 | 0.017671
310 | 35.08 | 14.696 | 0.080219 | 8.4313 | 0.017676 |  | 310 | 8.4313 | 35.08 | 14.696 | 0.080219 | 0.017676
311 | 35.09 | 14.696 | 0.080218 | 8.4337 | 0.017681 |  | 311 | 8.4337 | 35.09 | 14.696 | 0.080218 | 0.017681
312 | 35.1 | 14.696 | 0.080216 | 8.4361 | 0.017686 |  | 312 | 8.4361 | 35.1 | 14.696 | 0.080216 | 0.017686
313 | 35.11 | 14.696 | 0.080215 | 8.4385 | 0.01769 |  | 313 | 8.4385 | 35.11 | 14.696 | 0.080215 | 0.01769
314 | 35.12 | 14.696 | 0.080213 | 8.4409 | 0.017695 |  | 314 | 8.4409 | 35.12 | 14.696 | 0.080213 | 0.017695
315 | 35.13 | 14.696 | 0.080211 | 8.4433 | 0.0177 |  | 315 | 8.4433 | 35.13 | 14.696 | 0.080211 | 0.0177
316 | 35.14 | 14.696 | 0.08021 | 8.4457 | 0.017705 |  | 316 | 8.4457 | 35.14 | 14.696 | 0.08021 | 0.017705
317 | 35.15 | 14.696 | 0.080208 | 8.4481 | 0.01771 |  | 317 | 8.4481 | 35.15 | 14.696 | 0.080208 | 0.01771
318 | 35.16 | 14.696 | 0.080206 | 8.4505 | 0.017715 |  | 318 | 8.4505 | 35.16 | 14.696 | 0.080206 | 0.017715
319 | 35.17 | 14.696 | 0.080205 | 8.4529 | 0.01772 |  | 319 | 8.4529 | 35.17 | 14.696 | 0.080205 | 0.01772
320 | 35.18 | 14.696 | 0.080203 | 8.4553 | 0.017724 |  | 320 | 8.4553 | 35.18 | 14.696 | 0.080203 | 0.017724
321 | 35.19 | 14.696 | 0.080202 | 8.4577 | 0.017729 |  | 321 | 8.4577 | 35.19 | 14.696 | 0.080202 | 0.017729
322 | 35.2 | 14.696 | 0.0802 | 8.4601 | 0.017734 |  | 322 | 8.4601 | 35.2 | 14.696 | 0.0802 | 0.017734
323 | 35.21 | 14.696 | 0.080198 | 8.4625 | 0.017739 |  | 323 | 8.4625 | 35.21 | 14.696 | 0.080198 | 0.017739
324 | 35.22 | 14.696 | 0.080197 | 8.4649 | 0.017744 |  | 324 | 8.4649 | 35.22 | 14.696 | 0.080197 | 0.017744
325 | 35.23 | 14.696 | 0.080195 | 8.4673 | 0.017749 |  | 325 | 8.4673 | 35.23 | 14.696 | 0.080195 | 0.017749
326 | 35.24 | 14.696 | 0.080193 | 8.4697 | 0.017754 |  | 326 | 8.4697 | 35.24 | 14.696 | 0.080193 | 0.017754
327 | 35.25 | 14.696 | 0.080192 | 8.4721 | 0.017758 |  | 327 | 8.4721 | 35.25 | 14.696 | 0.080192 | 0.017758
328 | 35.26 | 14.696 | 0.08019 | 8.4745 | 0.017763 |  | 328 | 8.4745 | 35.26 | 14.696 | 0.08019 | 0.017763
329 | 35.27 | 14.696 | 0.080189 | 8.4769 | 0.017768 |  | 329 | 8.4769 | 35.27 | 14.696 | 0.080189 | 0.017768
330 | 35.28 | 14.696 | 0.080187 | 8.4793 | 0.017773 |  | 330 | 8.4793 | 35.28 | 14.696 | 0.080187 | 0.017773
331 | 35.29 | 14.696 | 0.080185 | 8.4818 | 0.017778 |  | 331 | 8.4818 | 35.29 | 14.696 | 0.080185 | 0.017778
332 | 35.3 | 14.696 | 0.080184 | 8.4842 | 0.017783 |  | 332 | 8.4842 | 35.3 | 14.696 | 0.080184 | 0.017783
333 | 35.31 | 14.696 | 0.080182 | 8.4866 | 0.017788 |  | 333 | 8.4866 | 35.31 | 14.696 | 0.080182 | 0.017788
334 | 35.32 | 14.696 | 0.08018 | 8.489 | 0.017792 |  | 334 | 8.489 | 35.32 | 14.696 | 0.08018 | 0.017792
335 | 35.33 | 14.696 | 0.080179 | 8.4914 | 0.017797 |  | 335 | 8.4914 | 35.33 | 14.696 | 0.080179 | 0.017797
336 | 35.34 | 14.696 | 0.080177 | 8.4938 | 0.017802 |  | 336 | 8.4938 | 35.34 | 14.696 | 0.080177 | 0.017802
337 | 35.35 | 14.696 | 0.080176 | 8.4962 | 0.017807 |  | 337 | 8.4962 | 35.35 | 14.696 | 0.080176 | 0.017807
338 | 35.36 | 14.696 | 0.080174 | 8.4986 | 0.017812 |  | 338 | 8.4986 | 35.36 | 14.696 | 0.080174 | 0.017812
339 | 35.37 | 14.696 | 0.080172 | 8.501 | 0.017817 |  | 339 | 8.501 | 35.37 | 14.696 | 0.080172 | 0.017817
340 | 35.38 | 14.696 | 0.080171 | 8.5034 | 0.017821 |  | 340 | 8.5034 | 35.38 | 14.696 | 0.080171 | 0.017821
341 | 35.39 | 14.696 | 0.080169 | 8.5058 | 0.017826 |  | 341 | 8.5058 | 35.39 | 14.696 | 0.080169 | 0.017826
342 | 35.4 | 14.696 | 0.080167 | 8.5082 | 0.017831 |  | 342 | 8.5082 | 35.4 | 14.696 | 0.080167 | 0.017831
343 | 35.41 | 14.696 | 0.080166 | 8.5106 | 0.017836 |  | 343 | 8.5106 | 35.41 | 14.696 | 0.080166 | 0.017836
344 | 35.42 | 14.696 | 0.080164 | 8.513 | 0.017841 |  | 344 | 8.513 | 35.42 | 14.696 | 0.080164 | 0.017841
345 | 35.43 | 14.696 | 0.080163 | 8.5154 | 0.017846 |  | 345 | 8.5154 | 35.43 | 14.696 | 0.080163 | 0.017846
346 | 35.44 | 14.696 | 0.080161 | 8.5178 | 0.017851 |  | 346 | 8.5178 | 35.44 | 14.696 | 0.080161 | 0.017851
347 | 35.45 | 14.696 | 0.080159 | 8.5202 | 0.017855 |  | 347 | 8.5202 | 35.45 | 14.696 | 0.080159 | 0.017855
348 | 35.46 | 14.696 | 0.080158 | 8.5226 | 0.01786 |  | 348 | 8.5226 | 35.46 | 14.696 | 0.080158 | 0.01786
349 | 35.47 | 14.696 | 0.080156 | 8.525 | 0.017865 |  | 349 | 8.525 | 35.47 | 14.696 | 0.080156 | 0.017865
350 | 35.48 | 14.696 | 0.080154 | 8.5274 | 0.01787 |  | 350 | 8.5274 | 35.48 | 14.696 | 0.080154 | 0.01787
351 | 35.49 | 14.696 | 0.080153 | 8.5298 | 0.017875 |  | 351 | 8.5298 | 35.49 | 14.696 | 0.080153 | 0.017875
352 | 35.5 | 14.696 | 0.080151 | 8.5322 | 0.01788 |  | 352 | 8.5322 | 35.5 | 14.696 | 0.080151 | 0.01788
353 | 35.51 | 14.696 | 0.08015 | 8.5346 | 0.017885 |  | 353 | 8.5346 | 35.51 | 14.696 | 0.08015 | 0.017885
354 | 35.52 | 14.696 | 0.080148 | 8.537 | 0.017889 |  | 354 | 8.537 | 35.52 | 14.696 | 0.080148 | 0.017889
355 | 35.53 | 14.696 | 0.080146 | 8.5394 | 0.017894 |  | 355 | 8.5394 | 35.53 | 14.696 | 0.080146 | 0.017894
356 | 35.54 | 14.696 | 0.080145 | 8.5418 | 0.017899 |  | 356 | 8.5418 | 35.54 | 14.696 | 0.080145 | 0.017899
357 | 35.55 | 14.696 | 0.080143 | 8.5442 | 0.017904 |  | 357 | 8.5442 | 35.55 | 14.696 | 0.080143 | 0.017904
358 | 35.56 | 14.696 | 0.080141 | 8.5467 | 0.017909 |  | 358 | 8.5467 | 35.56 | 14.696 | 0.080141 | 0.017909
359 | 35.57 | 14.696 | 0.08014 | 8.5491 | 0.017914 |  | 359 | 8.5491 | 35.57 | 14.696 | 0.08014 | 0.017914
360 | 35.58 | 14.696 | 0.080138 | 8.5515 | 0.017919 |  | 360 | 8.5515 | 35.58 | 14.696 | 0.080138 | 0.017919
361 | 35.59 | 14.696 | 0.080137 | 8.5539 | 0.017923 |  | 361 | 8.5539 | 35.59 | 14.696 | 0.080137 | 0.017923
362 | 35.6 | 14.696 | 0.080135 | 8.5563 | 0.017928 |  | 362 | 8.5563 | 35.6 | 14.696 | 0.080135 | 0.017928
363 | 35.61 | 14.696 | 0.080133 | 8.5587 | 0.017933 |  | 363 | 8.5587 | 35.61 | 14.696 | 0.080133 | 0.017933
364 | 35.62 | 14.696 | 0.080132 | 8.5611 | 0.017938 |  | 364 | 8.5611 | 35.62 | 14.696 | 0.080132 | 0.017938
365 | 35.63 | 14.696 | 0.08013 | 8.5635 | 0.017943 |  | 365 | 8.5635 | 35.63 | 14.696 | 0.08013 | 0.017943
366 | 35.64 | 14.696 | 0.080128 | 8.5659 | 0.017948 |  | 366 | 8.5659 | 35.64 | 14.696 | 0.080128 | 0.017948
367 | 35.65 | 14.696 | 0.080127 | 8.5683 | 0.017953 |  | 367 | 8.5683 | 35.65 | 14.696 | 0.080127 | 0.017953
368 | 35.66 | 14.696 | 0.080125 | 8.5707 | 0.017957 |  | 368 | 8.5707 | 35.66 | 14.696 | 0.080125 | 0.017957
369 | 35.67 | 14.696 | 0.080124 | 8.5731 | 0.017962 |  | 369 | 8.5731 | 35.67 | 14.696 | 0.080124 | 0.017962
370 | 35.68 | 14.696 | 0.080122 | 8.5755 | 0.017967 |  | 370 | 8.5755 | 35.68 | 14.696 | 0.080122 | 0.017967
371 | 35.69 | 14.696 | 0.08012 | 8.5779 | 0.017972 |  | 371 | 8.5779 | 35.69 | 14.696 | 0.08012 | 0.017972
372 | 35.7 | 14.696 | 0.080119 | 8.5803 | 0.017977 |  | 372 | 8.5803 | 35.7 | 14.696 | 0.080119 | 0.017977
373 | 35.71 | 14.696 | 0.080117 | 8.5827 | 0.017982 |  | 373 | 8.5827 | 35.71 | 14.696 | 0.080117 | 0.017982
374 | 35.72 | 14.696 | 0.080115 | 8.5851 | 0.017987 |  | 374 | 8.5851 | 35.72 | 14.696 | 0.080115 | 0.017987
375 | 35.73 | 14.696 | 0.080114 | 8.5875 | 0.017991 |  | 375 | 8.5875 | 35.73 | 14.696 | 0.080114 | 0.017991
376 | 35.74 | 14.696 | 0.080112 | 8.5899 | 0.017996 |  | 376 | 8.5899 | 35.74 | 14.696 | 0.080112 | 0.017996
377 | 35.75 | 14.696 | 0.080111 | 8.5923 | 0.018001 |  | 377 | 8.5923 | 35.75 | 14.696 | 0.080111 | 0.018001
378 | 35.76 | 14.696 | 0.080109 | 8.5947 | 0.018006 |  | 378 | 8.5947 | 35.76 | 14.696 | 0.080109 | 0.018006
379 | 35.77 | 14.696 | 0.080107 | 8.5971 | 0.018011 |  | 379 | 8.5971 | 35.77 | 14.696 | 0.080107 | 0.018011
380 | 35.78 | 14.696 | 0.080106 | 8.5995 | 0.018016 |  | 380 | 8.5995 | 35.78 | 14.696 | 0.080106 | 0.018016
381 | 35.79 | 14.696 | 0.080104 | 8.6019 | 0.01802 |  | 381 | 8.6019 | 35.79 | 14.696 | 0.080104 | 0.01802
382 | 35.8 | 14.696 | 0.080102 | 8.6043 | 0.018025 |  | 382 | 8.6043 | 35.8 | 14.696 | 0.080102 | 0.018025
383 | 35.81 | 14.696 | 0.080101 | 8.6067 | 0.01803 |  | 383 | 8.6067 | 35.81 | 14.696 | 0.080101 | 0.01803
384 | 35.82 | 14.696 | 0.080099 | 8.6091 | 0.018035 |  | 384 | 8.6091 | 35.82 | 14.696 | 0.080099 | 0.018035
385 | 35.83 | 14.696 | 0.080098 | 8.6116 | 0.01804 |  | 385 | 8.6116 | 35.83 | 14.696 | 0.080098 | 0.01804
386 | 35.84 | 14.696 | 0.080096 | 8.614 | 0.018045 |  | 386 | 8.614 | 35.84 | 14.696 | 0.080096 | 0.018045
387 | 35.85 | 14.696 | 0.080094 | 8.6164 | 0.01805 |  | 387 | 8.6164 | 35.85 | 14.696 | 0.080094 | 0.01805
388 | 35.86 | 14.696 | 0.080093 | 8.6188 | 0.018054 |  | 388 | 8.6188 | 35.86 | 14.696 | 0.080093 | 0.018054
389 | 35.87 | 14.696 | 0.080091 | 8.6212 | 0.018059 |  | 389 | 8.6212 | 35.87 | 14.696 | 0.080091 | 0.018059
390 | 35.88 | 14.696 | 0.080089 | 8.6236 | 0.018064 |  | 390 | 8.6236 | 35.88 | 14.696 | 0.080089 | 0.018064
391 | 35.89 | 14.696 | 0.080088 | 8.626 | 0.018069 |  | 391 | 8.626 | 35.89 | 14.696 | 0.080088 | 0.018069
392 | 35.9 | 14.696 | 0.080086 | 8.6284 | 0.018074 |  | 392 | 8.6284 | 35.9 | 14.696 | 0.080086 | 0.018074
393 | 35.91 | 14.696 | 0.080085 | 8.6308 | 0.018079 |  | 393 | 8.6308 | 35.91 | 14.696 | 0.080085 | 0.018079
394 | 35.92 | 14.696 | 0.080083 | 8.6332 | 0.018084 |  | 394 | 8.6332 | 35.92 | 14.696 | 0.080083 | 0.018084
395 | 35.93 | 14.696 | 0.080081 | 8.6356 | 0.018088 |  | 395 | 8.6356 | 35.93 | 14.696 | 0.080081 | 0.018088
396 | 35.94 | 14.696 | 0.08008 | 8.638 | 0.018093 |  | 396 | 8.638 | 35.94 | 14.696 | 0.08008 | 0.018093
397 | 35.95 | 14.696 | 0.080078 | 8.6404 | 0.018098 |  | 397 | 8.6404 | 35.95 | 14.696 | 0.080078 | 0.018098
398 | 35.96 | 14.696 | 0.080077 | 8.6428 | 0.018103 |  | 398 | 8.6428 | 35.96 | 14.696 | 0.080077 | 0.018103
399 | 35.97 | 14.696 | 0.080075 | 8.6452 | 0.018108 |  | 399 | 8.6452 | 35.97 | 14.696 | 0.080075 | 0.018108
400 | 35.98 | 14.696 | 0.080073 | 8.6476 | 0.018113 |  | 400 | 8.6476 | 35.98 | 14.696 | 0.080073 | 0.018113
401 | 35.99 | 14.696 | 0.080072 | 8.65 | 0.018118 |  | 401 | 8.65 | 35.99 | 14.696 | 0.080072 | 0.018118
402 | 36 | 14.696 | 0.08007 | 8.6524 | 0.018122 |  | 402 | 8.6524 | 36 | 14.696 | 0.08007 | 0.018122
403 | 36.01 | 14.696 | 0.080068 | 8.6548 | 0.018127 |  | 403 | 8.6548 | 36.01 | 14.696 | 0.080068 | 0.018127
404 | 36.02 | 14.696 | 0.080067 | 8.6572 | 0.018132 |  | 404 | 8.6572 | 36.02 | 14.696 | 0.080067 | 0.018132
405 | 36.03 | 14.696 | 0.080065 | 8.6596 | 0.018137 |  | 405 | 8.6596 | 36.03 | 14.696 | 0.080065 | 0.018137
406 | 36.04 | 14.696 | 0.080064 | 8.662 | 0.018142 |  | 406 | 8.662 | 36.04 | 14.696 | 0.080064 | 0.018142
407 | 36.05 | 14.696 | 0.080062 | 8.6644 | 0.018147 |  | 407 | 8.6644 | 36.05 | 14.696 | 0.080062 | 0.018147
408 | 36.06 | 14.696 | 0.08006 | 8.6668 | 0.018151 |  | 408 | 8.6668 | 36.06 | 14.696 | 0.08006 | 0.018151
409 | 36.07 | 14.696 | 0.080059 | 8.6692 | 0.018156 |  | 409 | 8.6692 | 36.07 | 14.696 | 0.080059 | 0.018156
410 | 36.08 | 14.696 | 0.080057 | 8.6716 | 0.018161 |  | 410 | 8.6716 | 36.08 | 14.696 | 0.080057 | 0.018161
411 | 36.09 | 14.696 | 0.080055 | 8.674 | 0.018166 |  | 411 | 8.674 | 36.09 | 14.696 | 0.080055 | 0.018166
412 | 36.1 | 14.696 | 0.080054 | 8.6765 | 0.018171 |  | 412 | 8.6765 | 36.1 | 14.696 | 0.080054 | 0.018171
413 | 36.11 | 14.696 | 0.080052 | 8.6789 | 0.018176 |  | 413 | 8.6789 | 36.11 | 14.696 | 0.080052 | 0.018176
414 | 36.12 | 14.696 | 0.080051 | 8.6813 | 0.018181 |  | 414 | 8.6813 | 36.12 | 14.696 | 0.080051 | 0.018181
415 | 36.13 | 14.696 | 0.080049 | 8.6837 | 0.018185 |  | 415 | 8.6837 | 36.13 | 14.696 | 0.080049 | 0.018185
416 | 36.14 | 14.696 | 0.080047 | 8.6861 | 0.01819 |  | 416 | 8.6861 | 36.14 | 14.696 | 0.080047 | 0.01819
417 | 36.15 | 14.696 | 0.080046 | 8.6885 | 0.018195 |  | 417 | 8.6885 | 36.15 | 14.696 | 0.080046 | 0.018195
418 | 36.16 | 14.696 | 0.080044 | 8.6909 | 0.0182 |  | 418 | 8.6909 | 36.16 | 14.696 | 0.080044 | 0.0182
419 | 36.17 | 14.696 | 0.080042 | 8.6933 | 0.018205 |  | 419 | 8.6933 | 36.17 | 14.696 | 0.080042 | 0.018205
420 | 36.18 | 14.696 | 0.080041 | 8.6957 | 0.01821 |  | 420 | 8.6957 | 36.18 | 14.696 | 0.080041 | 0.01821
421 | 36.19 | 14.696 | 0.080039 | 8.6981 | 0.018214 |  | 421 | 8.6981 | 36.19 | 14.696 | 0.080039 | 0.018214
422 | 36.2 | 14.696 | 0.080038 | 8.7005 | 0.018219 |  | 422 | 8.7005 | 36.2 | 14.696 | 0.080038 | 0.018219
423 | 36.21 | 14.696 | 0.080036 | 8.7029 | 0.018224 |  | 423 | 8.7029 | 36.21 | 14.696 | 0.080036 | 0.018224
424 | 36.22 | 14.696 | 0.080034 | 8.7053 | 0.018229 |  | 424 | 8.7053 | 36.22 | 14.696 | 0.080034 | 0.018229
425 | 36.23 | 14.696 | 0.080033 | 8.7077 | 0.018234 |  | 425 | 8.7077 | 36.23 | 14.696 | 0.080033 | 0.018234
426 | 36.24 | 14.696 | 0.080031 | 8.7101 | 0.018239 |  | 426 | 8.7101 | 36.24 | 14.696 | 0.080031 | 0.018239
427 | 36.25 | 14.696 | 0.08003 | 8.7125 | 0.018244 |  | 427 | 8.7125 | 36.25 | 14.696 | 0.08003 | 0.018244
428 | 36.26 | 14.696 | 0.080028 | 8.7149 | 0.018248 |  | 428 | 8.7149 | 36.26 | 14.696 | 0.080028 | 0.018248
429 | 36.27 | 14.696 | 0.080026 | 8.7173 | 0.018253 |  | 429 | 8.7173 | 36.27 | 14.696 | 0.080026 | 0.018253
430 | 36.28 | 14.696 | 0.080025 | 8.7197 | 0.018258 |  | 430 | 8.7197 | 36.28 | 14.696 | 0.080025 | 0.018258
431 | 36.29 | 14.696 | 0.080023 | 8.7221 | 0.018263 |  | 431 | 8.7221 | 36.29 | 14.696 | 0.080023 | 0.018263
432 | 36.3 | 14.696 | 0.080021 | 8.7245 | 0.018268 |  | 432 | 8.7245 | 36.3 | 14.696 | 0.080021 | 0.018268
433 | 36.31 | 14.696 | 0.08002 | 8.7269 | 0.018273 |  | 433 | 8.7269 | 36.31 | 14.696 | 0.08002 | 0.018273
434 | 36.32 | 14.696 | 0.080018 | 8.7293 | 0.018277 |  | 434 | 8.7293 | 36.32 | 14.696 | 0.080018 | 0.018277
435 | 36.33 | 14.696 | 0.080017 | 8.7317 | 0.018282 |  | 435 | 8.7317 | 36.33 | 14.696 | 0.080017 | 0.018282
436 | 36.34 | 14.696 | 0.080015 | 8.7341 | 0.018287 |  | 436 | 8.7341 | 36.34 | 14.696 | 0.080015 | 0.018287
437 | 36.35 | 14.696 | 0.080013 | 8.7365 | 0.018292 |  | 437 | 8.7365 | 36.35 | 14.696 | 0.080013 | 0.018292
438 | 36.36 | 14.696 | 0.080012 | 8.7389 | 0.018297 |  | 438 | 8.7389 | 36.36 | 14.696 | 0.080012 | 0.018297
439 | 36.37 | 14.696 | 0.08001 | 8.7414 | 0.018302 |  | 439 | 8.7414 | 36.37 | 14.696 | 0.08001 | 0.018302
440 | 36.38 | 14.696 | 0.080008 | 8.7438 | 0.018307 |  | 440 | 8.7438 | 36.38 | 14.696 | 0.080008 | 0.018307
441 | 36.39 | 14.696 | 0.080007 | 8.7462 | 0.018311 |  | 441 | 8.7462 | 36.39 | 14.696 | 0.080007 | 0.018311
442 | 36.4 | 14.696 | 0.080005 | 8.7486 | 0.018316 |  | 442 | 8.7486 | 36.4 | 14.696 | 0.080005 | 0.018316
443 | 36.41 | 14.696 | 0.080004 | 8.751 | 0.018321 |  | 443 | 8.751 | 36.41 | 14.696 | 0.080004 | 0.018321
444 | 36.42 | 14.696 | 0.080002 | 8.7534 | 0.018326 |  | 444 | 8.7534 | 36.42 | 14.696 | 0.080002 | 0.018326
445 | 36.43 | 14.696 | 0.08 | 8.7558 | 0.018331 |  | 445 | 8.7558 | 36.43 | 14.696 | 0.08 | 0.018331
446 | 36.44 | 14.696 | 0.079999 | 8.7582 | 0.018336 |  | 446 | 8.7582 | 36.44 | 14.696 | 0.079999 | 0.018336
447 | 36.45 | 14.696 | 0.079997 | 8.7606 | 0.01834 |  | 447 | 8.7606 | 36.45 | 14.696 | 0.079997 | 0.01834
448 | 36.46 | 14.696 | 0.079996 | 8.763 | 0.018345 |  | 448 | 8.763 | 36.46 | 14.696 | 0.079996 | 0.018345
449 | 36.47 | 14.696 | 0.079994 | 8.7654 | 0.01835 |  | 449 | 8.7654 | 36.47 | 14.696 | 0.079994 | 0.01835
450 | 36.48 | 14.696 | 0.079992 | 8.7678 | 0.018355 |  | 450 | 8.7678 | 36.48 | 14.696 | 0.079992 | 0.018355
451 | 36.49 | 14.696 | 0.079991 | 8.7702 | 0.01836 |  | 451 | 8.7702 | 36.49 | 14.696 | 0.079991 | 0.01836
452 | 36.5 | 14.696 | 0.079989 | 8.7726 | 0.018365 |  | 452 | 8.7726 | 36.5 | 14.696 | 0.079989 | 0.018365
453 | 36.51 | 14.696 | 0.079987 | 8.775 | 0.01837 |  | 453 | 8.775 | 36.51 | 14.696 | 0.079987 | 0.01837
454 | 36.52 | 14.696 | 0.079986 | 8.7774 | 0.018374 |  | 454 | 8.7774 | 36.52 | 14.696 | 0.079986 | 0.018374
455 | 36.53 | 14.696 | 0.079984 | 8.7798 | 0.018379 |  | 455 | 8.7798 | 36.53 | 14.696 | 0.079984 | 0.018379
456 | 36.54 | 14.696 | 0.079983 | 8.7822 | 0.018384 |  | 456 | 8.7822 | 36.54 | 14.696 | 0.079983 | 0.018384
457 | 36.55 | 14.696 | 0.079981 | 8.7846 | 0.018389 |  | 457 | 8.7846 | 36.55 | 14.696 | 0.079981 | 0.018389
458 | 36.56 | 14.696 | 0.079979 | 8.787 | 0.018394 |  | 458 | 8.787 | 36.56 | 14.696 | 0.079979 | 0.018394
459 | 36.57 | 14.696 | 0.079978 | 8.7894 | 0.018399 |  | 459 | 8.7894 | 36.57 | 14.696 | 0.079978 | 0.018399
460 | 36.58 | 14.696 | 0.079976 | 8.7918 | 0.018403 |  | 460 | 8.7918 | 36.58 | 14.696 | 0.079976 | 0.018403
461 | 36.59 | 14.696 | 0.079975 | 8.7942 | 0.018408 |  | 461 | 8.7942 | 36.59 | 14.696 | 0.079975 | 0.018408
462 | 36.6 | 14.696 | 0.079973 | 8.7966 | 0.018413 |  | 462 | 8.7966 | 36.6 | 14.696 | 0.079973 | 0.018413
463 | 36.61 | 14.696 | 0.079971 | 8.799 | 0.018418 |  | 463 | 8.799 | 36.61 | 14.696 | 0.079971 | 0.018418
464 | 36.62 | 14.696 | 0.07997 | 8.8014 | 0.018423 |  | 464 | 8.8014 | 36.62 | 14.696 | 0.07997 | 0.018423
465 | 36.63 | 14.696 | 0.079968 | 8.8038 | 0.018428 |  | 465 | 8.8038 | 36.63 | 14.696 | 0.079968 | 0.018428
466 | 36.64 | 14.696 | 0.079966 | 8.8063 | 0.018433 |  | 466 | 8.8063 | 36.64 | 14.696 | 0.079966 | 0.018433
467 | 36.65 | 14.696 | 0.079965 | 8.8087 | 0.018437 |  | 467 | 8.8087 | 36.65 | 14.696 | 0.079965 | 0.018437
468 | 36.66 | 14.696 | 0.079963 | 8.8111 | 0.018442 |  | 468 | 8.8111 | 36.66 | 14.696 | 0.079963 | 0.018442
469 | 36.67 | 14.696 | 0.079962 | 8.8135 | 0.018447 |  | 469 | 8.8135 | 36.67 | 14.696 | 0.079962 | 0.018447
470 | 36.68 | 14.696 | 0.07996 | 8.8159 | 0.018452 |  | 470 | 8.8159 | 36.68 | 14.696 | 0.07996 | 0.018452
471 | 36.69 | 14.696 | 0.079958 | 8.8183 | 0.018457 |  | 471 | 8.8183 | 36.69 | 14.696 | 0.079958 | 0.018457
472 | 36.7 | 14.696 | 0.079957 | 8.8207 | 0.018462 |  | 472 | 8.8207 | 36.7 | 14.696 | 0.079957 | 0.018462
473 | 36.71 | 14.696 | 0.079955 | 8.8231 | 0.018466 |  | 473 | 8.8231 | 36.71 | 14.696 | 0.079955 | 0.018466
474 | 36.72 | 14.696 | 0.079953 | 8.8255 | 0.018471 |  | 474 | 8.8255 | 36.72 | 14.696 | 0.079953 | 0.018471
475 | 36.73 | 14.696 | 0.079952 | 8.8279 | 0.018476 |  | 475 | 8.8279 | 36.73 | 14.696 | 0.079952 | 0.018476
476 | 36.74 | 14.696 | 0.07995 | 8.8303 | 0.018481 |  | 476 | 8.8303 | 36.74 | 14.696 | 0.07995 | 0.018481
477 | 36.75 | 14.696 | 0.079949 | 8.8327 | 0.018486 |  | 477 | 8.8327 | 36.75 | 14.696 | 0.079949 | 0.018486
478 | 36.76 | 14.696 | 0.079947 | 8.8351 | 0.018491 |  | 478 | 8.8351 | 36.76 | 14.696 | 0.079947 | 0.018491
479 | 36.77 | 14.696 | 0.079945 | 8.8375 | 0.018495 |  | 479 | 8.8375 | 36.77 | 14.696 | 0.079945 | 0.018495
480 | 36.78 | 14.696 | 0.079944 | 8.8399 | 0.0185 |  | 480 | 8.8399 | 36.78 | 14.696 | 0.079944 | 0.0185
481 | 36.79 | 14.696 | 0.079942 | 8.8423 | 0.018505 |  | 481 | 8.8423 | 36.79 | 14.696 | 0.079942 | 0.018505
482 | 36.8 | 14.696 | 0.079941 | 8.8447 | 0.01851 |  | 482 | 8.8447 | 36.8 | 14.696 | 0.079941 | 0.01851
483 | 36.81 | 14.696 | 0.079939 | 8.8471 | 0.018515 |  | 483 | 8.8471 | 36.81 | 14.696 | 0.079939 | 0.018515
484 | 36.82 | 14.696 | 0.079937 | 8.8495 | 0.01852 |  | 484 | 8.8495 | 36.82 | 14.696 | 0.079937 | 0.01852
485 | 36.83 | 14.696 | 0.079936 | 8.8519 | 0.018525 |  | 485 | 8.8519 | 36.83 | 14.696 | 0.079936 | 0.018525
486 | 36.84 | 14.696 | 0.079934 | 8.8543 | 0.018529 |  | 486 | 8.8543 | 36.84 | 14.696 | 0.079934 | 0.018529
487 | 36.85 | 14.696 | 0.079932 | 8.8567 | 0.018534 |  | 487 | 8.8567 | 36.85 | 14.696 | 0.079932 | 0.018534
488 | 36.86 | 14.696 | 0.079931 | 8.8591 | 0.018539 |  | 488 | 8.8591 | 36.86 | 14.696 | 0.079931 | 0.018539
489 | 36.87 | 14.696 | 0.079929 | 8.8615 | 0.018544 |  | 489 | 8.8615 | 36.87 | 14.696 | 0.079929 | 0.018544
490 | 36.88 | 14.696 | 0.079928 | 8.8639 | 0.018549 |  | 490 | 8.8639 | 36.88 | 14.696 | 0.079928 | 0.018549
491 | 36.89 | 14.696 | 0.079926 | 8.8663 | 0.018554 |  | 491 | 8.8663 | 36.89 | 14.696 | 0.079926 | 0.018554
492 | 36.9 | 14.696 | 0.079924 | 8.8688 | 0.018558 |  | 492 | 8.8688 | 36.9 | 14.696 | 0.079924 | 0.018558
493 | 36.91 | 14.696 | 0.079923 | 8.8712 | 0.018563 |  | 493 | 8.8712 | 36.91 | 14.696 | 0.079923 | 0.018563
494 | 36.92 | 14.696 | 0.079921 | 8.8736 | 0.018568 |  | 494 | 8.8736 | 36.92 | 14.696 | 0.079921 | 0.018568
495 | 36.93 | 14.696 | 0.07992 | 8.876 | 0.018573 |  | 495 | 8.876 | 36.93 | 14.696 | 0.07992 | 0.018573
496 | 36.94 | 14.696 | 0.079918 | 8.8784 | 0.018578 |  | 496 | 8.8784 | 36.94 | 14.696 | 0.079918 | 0.018578
497 | 36.95 | 14.696 | 0.079916 | 8.8808 | 0.018583 |  | 497 | 8.8808 | 36.95 | 14.696 | 0.079916 | 0.018583
498 | 36.96 | 14.696 | 0.079915 | 8.8832 | 0.018587 |  | 498 | 8.8832 | 36.96 | 14.696 | 0.079915 | 0.018587
499 | 36.97 | 14.696 | 0.079913 | 8.8856 | 0.018592 |  | 499 | 8.8856 | 36.97 | 14.696 | 0.079913 | 0.018592
500 | 36.98 | 14.696 | 0.079911 | 8.888 | 0.018597 |  | 500 | 8.888 | 36.98 | 14.696 | 0.079911 | 0.018597
501 | 36.99 | 14.696 | 0.07991 | 8.8904 | 0.018602 |  | 501 | 8.8904 | 36.99 | 14.696 | 0.07991 | 0.018602
502 | 37 | 14.696 | 0.079908 | 8.8928 | 0.018607 |  | 502 | 8.8928 | 37 | 14.696 | 0.079908 | 0.018607
503 | 37.01 | 14.696 | 0.079907 | 8.8952 | 0.018612 |  | 503 | 8.8952 | 37.01 | 14.696 | 0.079907 | 0.018612
504 | 37.02 | 14.696 | 0.079905 | 8.8976 | 0.018616 |  | 504 | 8.8976 | 37.02 | 14.696 | 0.079905 | 0.018616
505 | 37.03 | 14.696 | 0.079903 | 8.9 | 0.018621 |  | 505 | 8.9 | 37.03 | 14.696 | 0.079903 | 0.018621
506 | 37.04 | 14.696 | 0.079902 | 8.9024 | 0.018626 |  | 506 | 8.9024 | 37.04 | 14.696 | 0.079902 | 0.018626
507 | 37.05 | 14.696 | 0.0799 | 8.9048 | 0.018631 |  | 507 | 8.9048 | 37.05 | 14.696 | 0.0799 | 0.018631
508 | 37.06 | 14.696 | 0.079899 | 8.9072 | 0.018636 |  | 508 | 8.9072 | 37.06 | 14.696 | 0.079899 | 0.018636
509 | 37.07 | 14.696 | 0.079897 | 8.9096 | 0.018641 |  | 509 | 8.9096 | 37.07 | 14.696 | 0.079897 | 0.018641
510 | 37.08 | 14.696 | 0.079895 | 8.912 | 0.018646 |  | 510 | 8.912 | 37.08 | 14.696 | 0.079895 | 0.018646
511 | 37.09 | 14.696 | 0.079894 | 8.9144 | 0.01865 |  | 511 | 8.9144 | 37.09 | 14.696 | 0.079894 | 0.01865
512 | 37.1 | 14.696 | 0.079892 | 8.9168 | 0.018655 |  | 512 | 8.9168 | 37.1 | 14.696 | 0.079892 | 0.018655
513 | 37.11 | 14.696 | 0.079891 | 8.9192 | 0.01866 |  | 513 | 8.9192 | 37.11 | 14.696 | 0.079891 | 0.01866
514 | 37.12 | 14.696 | 0.079889 | 8.9216 | 0.018665 |  | 514 | 8.9216 | 37.12 | 14.696 | 0.079889 | 0.018665
515 | 37.13 | 14.696 | 0.079887 | 8.924 | 0.01867 |  | 515 | 8.924 | 37.13 | 14.696 | 0.079887 | 0.01867
516 | 37.14 | 14.696 | 0.079886 | 8.9264 | 0.018675 |  | 516 | 8.9264 | 37.14 | 14.696 | 0.079886 | 0.018675
517 | 37.15 | 14.696 | 0.079884 | 8.9288 | 0.018679 |  | 517 | 8.9288 | 37.15 | 14.696 | 0.079884 | 0.018679
518 | 37.16 | 14.696 | 0.079882 | 8.9312 | 0.018684 |  | 518 | 8.9312 | 37.16 | 14.696 | 0.079882 | 0.018684
519 | 37.17 | 14.696 | 0.079881 | 8.9337 | 0.018689 |  | 519 | 8.9337 | 37.17 | 14.696 | 0.079881 | 0.018689
520 | 37.18 | 14.696 | 0.079879 | 8.9361 | 0.018694 |  | 520 | 8.9361 | 37.18 | 14.696 | 0.079879 | 0.018694
521 | 37.19 | 14.696 | 0.079878 | 8.9385 | 0.018699 |  | 521 | 8.9385 | 37.19 | 14.696 | 0.079878 | 0.018699
522 | 37.2 | 14.696 | 0.079876 | 8.9409 | 0.018704 |  | 522 | 8.9409 | 37.2 | 14.696 | 0.079876 | 0.018704
523 | 37.21 | 14.696 | 0.079874 | 8.9433 | 0.018708 |  | 523 | 8.9433 | 37.21 | 14.696 | 0.079874 | 0.018708
524 | 37.22 | 14.696 | 0.079873 | 8.9457 | 0.018713 |  | 524 | 8.9457 | 37.22 | 14.696 | 0.079873 | 0.018713
525 | 37.23 | 14.696 | 0.079871 | 8.9481 | 0.018718 |  | 525 | 8.9481 | 37.23 | 14.696 | 0.079871 | 0.018718
526 | 37.24 | 14.696 | 0.07987 | 8.9505 | 0.018723 |  | 526 | 8.9505 | 37.24 | 14.696 | 0.07987 | 0.018723
527 | 37.25 | 14.696 | 0.079868 | 8.9529 | 0.018728 |  | 527 | 8.9529 | 37.25 | 14.696 | 0.079868 | 0.018728
528 | 37.26 | 14.696 | 0.079866 | 8.9553 | 0.018733 |  | 528 | 8.9553 | 37.26 | 14.696 | 0.079866 | 0.018733
529 | 37.27 | 14.696 | 0.079865 | 8.9577 | 0.018737 |  | 529 | 8.9577 | 37.27 | 14.696 | 0.079865 | 0.018737
530 | 37.28 | 14.696 | 0.079863 | 8.9601 | 0.018742 |  | 530 | 8.9601 | 37.28 | 14.696 | 0.079863 | 0.018742
531 | 37.29 | 14.696 | 0.079861 | 8.9625 | 0.018747 |  | 531 | 8.9625 | 37.29 | 14.696 | 0.079861 | 0.018747
532 | 37.3 | 14.696 | 0.07986 | 8.9649 | 0.018752 |  | 532 | 8.9649 | 37.3 | 14.696 | 0.07986 | 0.018752
533 | 37.31 | 14.696 | 0.079858 | 8.9673 | 0.018757 |  | 533 | 8.9673 | 37.31 | 14.696 | 0.079858 | 0.018757
534 | 37.32 | 14.696 | 0.079857 | 8.9697 | 0.018762 |  | 534 | 8.9697 | 37.32 | 14.696 | 0.079857 | 0.018762
535 | 37.33 | 14.696 | 0.079855 | 8.9721 | 0.018766 |  | 535 | 8.9721 | 37.33 | 14.696 | 0.079855 | 0.018766
536 | 37.34 | 14.696 | 0.079853 | 8.9745 | 0.018771 |  | 536 | 8.9745 | 37.34 | 14.696 | 0.079853 | 0.018771
537 | 37.35 | 14.696 | 0.079852 | 8.9769 | 0.018776 |  | 537 | 8.9769 | 37.35 | 14.696 | 0.079852 | 0.018776
538 | 37.36 | 14.696 | 0.07985 | 8.9793 | 0.018781 |  | 538 | 8.9793 | 37.36 | 14.696 | 0.07985 | 0.018781
539 | 37.37 | 14.696 | 0.079849 | 8.9817 | 0.018786 |  | 539 | 8.9817 | 37.37 | 14.696 | 0.079849 | 0.018786
540 | 37.38 | 14.696 | 0.079847 | 8.9841 | 0.018791 |  | 540 | 8.9841 | 37.38 | 14.696 | 0.079847 | 0.018791
541 | 37.39 | 14.696 | 0.079845 | 8.9865 | 0.018795 |  | 541 | 8.9865 | 37.39 | 14.696 | 0.079845 | 0.018795
542 | 37.4 | 14.696 | 0.079844 | 8.9889 | 0.0188 |  | 542 | 8.9889 | 37.4 | 14.696 | 0.079844 | 0.0188
543 | 37.41 | 14.696 | 0.079842 | 8.9913 | 0.018805 |  | 543 | 8.9913 | 37.41 | 14.696 | 0.079842 | 0.018805
544 | 37.42 | 14.696 | 0.079841 | 8.9937 | 0.01881 |  | 544 | 8.9937 | 37.42 | 14.696 | 0.079841 | 0.01881
545 | 37.43 | 14.696 | 0.079839 | 8.9962 | 0.018815 |  | 545 | 8.9962 | 37.43 | 14.696 | 0.079839 | 0.018815
546 | 37.44 | 14.696 | 0.079837 | 8.9986 | 0.01882 |  | 546 | 8.9986 | 37.44 | 14.696 | 0.079837 | 0.01882
547 | 37.45 | 14.696 | 0.079836 | 9.001 | 0.018825 |  | 547 | 9.001 | 37.45 | 14.696 | 0.079836 | 0.018825
548 | 37.46 | 14.696 | 0.079834 | 9.0034 | 0.018829 |  | 548 | 9.0034 | 37.46 | 14.696 | 0.079834 | 0.018829
549 | 37.47 | 14.696 | 0.079832 | 9.0058 | 0.018834 |  | 549 | 9.0058 | 37.47 | 14.696 | 0.079832 | 0.018834
550 | 37.48 | 14.696 | 0.079831 | 9.0082 | 0.018839 |  | 550 | 9.0082 | 37.48 | 14.696 | 0.079831 | 0.018839
551 | 37.49 | 14.696 | 0.079829 | 9.0106 | 0.018844 |  | 551 | 9.0106 | 37.49 | 14.696 | 0.079829 | 0.018844
552 | 37.5 | 14.696 | 0.079828 | 9.013 | 0.018849 |  | 552 | 9.013 | 37.5 | 14.696 | 0.079828 | 0.018849
553 | 37.51 | 14.696 | 0.079826 | 9.0154 | 0.018854 |  | 553 | 9.0154 | 37.51 | 14.696 | 0.079826 | 0.018854
554 | 37.52 | 14.696 | 0.079824 | 9.0178 | 0.018858 |  | 554 | 9.0178 | 37.52 | 14.696 | 0.079824 | 0.018858
555 | 37.53 | 14.696 | 0.079823 | 9.0202 | 0.018863 |  | 555 | 9.0202 | 37.53 | 14.696 | 0.079823 | 0.018863
556 | 37.54 | 14.696 | 0.079821 | 9.0226 | 0.018868 |  | 556 | 9.0226 | 37.54 | 14.696 | 0.079821 | 0.018868
557 | 37.55 | 14.696 | 0.07982 | 9.025 | 0.018873 |  | 557 | 9.025 | 37.55 | 14.696 | 0.07982 | 0.018873
558 | 37.56 | 14.696 | 0.079818 | 9.0274 | 0.018878 |  | 558 | 9.0274 | 37.56 | 14.696 | 0.079818 | 0.018878
559 | 37.57 | 14.696 | 0.079816 | 9.0298 | 0.018883 |  | 559 | 9.0298 | 37.57 | 14.696 | 0.079816 | 0.018883
560 | 37.58 | 14.696 | 0.079815 | 9.0322 | 0.018887 |  | 560 | 9.0322 | 37.58 | 14.696 | 0.079815 | 0.018887
561 | 37.59 | 14.696 | 0.079813 | 9.0346 | 0.018892 |  | 561 | 9.0346 | 37.59 | 14.696 | 0.079813 | 0.018892
562 | 37.6 | 14.696 | 0.079812 | 9.037 | 0.018897 |  | 562 | 9.037 | 37.6 | 14.696 | 0.079812 | 0.018897
563 | 37.61 | 14.696 | 0.07981 | 9.0394 | 0.018902 |  | 563 | 9.0394 | 37.61 | 14.696 | 0.07981 | 0.018902
564 | 37.62 | 14.696 | 0.079808 | 9.0418 | 0.018907 |  | 564 | 9.0418 | 37.62 | 14.696 | 0.079808 | 0.018907
565 | 37.63 | 14.696 | 0.079807 | 9.0442 | 0.018912 |  | 565 | 9.0442 | 37.63 | 14.696 | 0.079807 | 0.018912
566 | 37.64 | 14.696 | 0.079805 | 9.0466 | 0.018916 |  | 566 | 9.0466 | 37.64 | 14.696 | 0.079805 | 0.018916
567 | 37.65 | 14.696 | 0.079803 | 9.049 | 0.018921 |  | 567 | 9.049 | 37.65 | 14.696 | 0.079803 | 0.018921
568 | 37.66 | 14.696 | 0.079802 | 9.0514 | 0.018926 |  | 568 | 9.0514 | 37.66 | 14.696 | 0.079802 | 0.018926
569 | 37.67 | 14.696 | 0.0798 | 9.0538 | 0.018931 |  | 569 | 9.0538 | 37.67 | 14.696 | 0.0798 | 0.018931
570 | 37.68 | 14.696 | 0.079799 | 9.0562 | 0.018936 |  | 570 | 9.0562 | 37.68 | 14.696 | 0.079799 | 0.018936
571 | 37.69 | 14.696 | 0.079797 | 9.0586 | 0.018941 |  | 571 | 9.0586 | 37.69 | 14.696 | 0.079797 | 0.018941
572 | 37.7 | 14.696 | 0.079795 | 9.0611 | 0.018945 |  | 572 | 9.0611 | 37.7 | 14.696 | 0.079795 | 0.018945
573 | 37.71 | 14.696 | 0.079794 | 9.0635 | 0.01895 |  | 573 | 9.0635 | 37.71 | 14.696 | 0.079794 | 0.01895
574 | 37.72 | 14.696 | 0.079792 | 9.0659 | 0.018955 |  | 574 | 9.0659 | 37.72 | 14.696 | 0.079792 | 0.018955
575 | 37.73 | 14.696 | 0.079791 | 9.0683 | 0.01896 |  | 575 | 9.0683 | 37.73 | 14.696 | 0.079791 | 0.01896
576 | 37.74 | 14.696 | 0.079789 | 9.0707 | 0.018965 |  | 576 | 9.0707 | 37.74 | 14.696 | 0.079789 | 0.018965
577 | 37.75 | 14.696 | 0.079787 | 9.0731 | 0.01897 |  | 577 | 9.0731 | 37.75 | 14.696 | 0.079787 | 0.01897
578 | 37.76 | 14.696 | 0.079786 | 9.0755 | 0.018974 |  | 578 | 9.0755 | 37.76 | 14.696 | 0.079786 | 0.018974
579 | 37.77 | 14.696 | 0.079784 | 9.0779 | 0.018979 |  | 579 | 9.0779 | 37.77 | 14.696 | 0.079784 | 0.018979
580 | 37.78 | 14.696 | 0.079783 | 9.0803 | 0.018984 |  | 580 | 9.0803 | 37.78 | 14.696 | 0.079783 | 0.018984
581 | 37.79 | 14.696 | 0.079781 | 9.0827 | 0.018989 |  | 581 | 9.0827 | 37.79 | 14.696 | 0.079781 | 0.018989
582 | 37.8 | 14.696 | 0.079779 | 9.0851 | 0.018994 |  | 582 | 9.0851 | 37.8 | 14.696 | 0.079779 | 0.018994
583 | 37.81 | 14.696 | 0.079778 | 9.0875 | 0.018999 |  | 583 | 9.0875 | 37.81 | 14.696 | 0.079778 | 0.018999
584 | 37.82 | 14.696 | 0.079776 | 9.0899 | 0.019003 |  | 584 | 9.0899 | 37.82 | 14.696 | 0.079776 | 0.019003
585 | 37.83 | 14.696 | 0.079774 | 9.0923 | 0.019008 |  | 585 | 9.0923 | 37.83 | 14.696 | 0.079774 | 0.019008
586 | 37.84 | 14.696 | 0.079773 | 9.0947 | 0.019013 |  | 586 | 9.0947 | 37.84 | 14.696 | 0.079773 | 0.019013
587 | 37.85 | 14.696 | 0.079771 | 9.0971 | 0.019018 |  | 587 | 9.0971 | 37.85 | 14.696 | 0.079771 | 0.019018
588 | 37.86 | 14.696 | 0.07977 | 9.0995 | 0.019023 |  | 588 | 9.0995 | 37.86 | 14.696 | 0.07977 | 0.019023
589 | 37.87 | 14.696 | 0.079768 | 9.1019 | 0.019028 |  | 589 | 9.1019 | 37.87 | 14.696 | 0.079768 | 0.019028
590 | 37.88 | 14.696 | 0.079766 | 9.1043 | 0.019032 |  | 590 | 9.1043 | 37.88 | 14.696 | 0.079766 | 0.019032
591 | 37.89 | 14.696 | 0.079765 | 9.1067 | 0.019037 |  | 591 | 9.1067 | 37.89 | 14.696 | 0.079765 | 0.019037
592 | 37.9 | 14.696 | 0.079763 | 9.1091 | 0.019042 |  | 592 | 9.1091 | 37.9 | 14.696 | 0.079763 | 0.019042
593 | 37.91 | 14.696 | 0.079762 | 9.1115 | 0.019047 |  | 593 | 9.1115 | 37.91 | 14.696 | 0.079762 | 0.019047
594 | 37.92 | 14.696 | 0.07976 | 9.1139 | 0.019052 |  | 594 | 9.1139 | 37.92 | 14.696 | 0.07976 | 0.019052
595 | 37.93 | 14.696 | 0.079758 | 9.1163 | 0.019056 |  | 595 | 9.1163 | 37.93 | 14.696 | 0.079758 | 0.019056
596 | 37.94 | 14.696 | 0.079757 | 9.1187 | 0.019061 |  | 596 | 9.1187 | 37.94 | 14.696 | 0.079757 | 0.019061
597 | 37.95 | 14.696 | 0.079755 | 9.1211 | 0.019066 |  | 597 | 9.1211 | 37.95 | 14.696 | 0.079755 | 0.019066
598 | 37.96 | 14.696 | 0.079754 | 9.1235 | 0.019071 |  | 598 | 9.1235 | 37.96 | 14.696 | 0.079754 | 0.019071
599 | 37.97 | 14.696 | 0.079752 | 9.126 | 0.019076 |  | 599 | 9.126 | 37.97 | 14.696 | 0.079752 | 0.019076
600 | 37.98 | 14.696 | 0.07975 | 9.1284 | 0.019081 |  | 600 | 9.1284 | 37.98 | 14.696 | 0.07975 | 0.019081
601 | 37.99 | 14.696 | 0.079749 | 9.1308 | 0.019085 |  | 601 | 9.1308 | 37.99 | 14.696 | 0.079749 | 0.019085
602 | 38 | 14.696 | 0.079747 | 9.1332 | 0.01909 |  | 602 | 9.1332 | 38 | 14.696 | 0.079747 | 0.01909
603 | 38.01 | 14.696 | 0.079746 | 9.1356 | 0.019095 |  | 603 | 9.1356 | 38.01 | 14.696 | 0.079746 | 0.019095
604 | 38.02 | 14.696 | 0.079744 | 9.138 | 0.0191 |  | 604 | 9.138 | 38.02 | 14.696 | 0.079744 | 0.0191
605 | 38.03 | 14.696 | 0.079742 | 9.1404 | 0.019105 |  | 605 | 9.1404 | 38.03 | 14.696 | 0.079742 | 0.019105
606 | 38.04 | 14.696 | 0.079741 | 9.1428 | 0.01911 |  | 606 | 9.1428 | 38.04 | 14.696 | 0.079741 | 0.01911
607 | 38.05 | 14.696 | 0.079739 | 9.1452 | 0.019114 |  | 607 | 9.1452 | 38.05 | 14.696 | 0.079739 | 0.019114
608 | 38.06 | 14.696 | 0.079737 | 9.1476 | 0.019119 |  | 608 | 9.1476 | 38.06 | 14.696 | 0.079737 | 0.019119
609 | 38.07 | 14.696 | 0.079736 | 9.15 | 0.019124 |  | 609 | 9.15 | 38.07 | 14.696 | 0.079736 | 0.019124
610 | 38.08 | 14.696 | 0.079734 | 9.1524 | 0.019129 |  | 610 | 9.1524 | 38.08 | 14.696 | 0.079734 | 0.019129
611 | 38.09 | 14.696 | 0.079733 | 9.1548 | 0.019134 |  | 611 | 9.1548 | 38.09 | 14.696 | 0.079733 | 0.019134
612 | 38.1 | 14.696 | 0.079731 | 9.1572 | 0.019139 |  | 612 | 9.1572 | 38.1 | 14.696 | 0.079731 | 0.019139
613 | 38.11 | 14.696 | 0.079729 | 9.1596 | 0.019143 |  | 613 | 9.1596 | 38.11 | 14.696 | 0.079729 | 0.019143
614 | 38.12 | 14.696 | 0.079728 | 9.162 | 0.019148 |  | 614 | 9.162 | 38.12 | 14.696 | 0.079728 | 0.019148
615 | 38.13 | 14.696 | 0.079726 | 9.1644 | 0.019153 |  | 615 | 9.1644 | 38.13 | 14.696 | 0.079726 | 0.019153
616 | 38.14 | 14.696 | 0.079725 | 9.1668 | 0.019158 |  | 616 | 9.1668 | 38.14 | 14.696 | 0.079725 | 0.019158
617 | 38.15 | 14.696 | 0.079723 | 9.1692 | 0.019163 |  | 617 | 9.1692 | 38.15 | 14.696 | 0.079723 | 0.019163
618 | 38.16 | 14.696 | 0.079721 | 9.1716 | 0.019168 |  | 618 | 9.1716 | 38.16 | 14.696 | 0.079721 | 0.019168
619 | 38.17 | 14.696 | 0.07972 | 9.174 | 0.019172 |  | 619 | 9.174 | 38.17 | 14.696 | 0.07972 | 0.019172
620 | 38.18 | 14.696 | 0.079718 | 9.1764 | 0.019177 |  | 620 | 9.1764 | 38.18 | 14.696 | 0.079718 | 0.019177
621 | 38.19 | 14.696 | 0.079717 | 9.1788 | 0.019182 |  | 621 | 9.1788 | 38.19 | 14.696 | 0.079717 | 0.019182
622 | 38.2 | 14.696 | 0.079715 | 9.1812 | 0.019187 |  | 622 | 9.1812 | 38.2 | 14.696 | 0.079715 | 0.019187
623 | 38.21 | 14.696 | 0.079713 | 9.1836 | 0.019192 |  | 623 | 9.1836 | 38.21 | 14.696 | 0.079713 | 0.019192
624 | 38.22 | 14.696 | 0.079712 | 9.186 | 0.019197 |  | 624 | 9.186 | 38.22 | 14.696 | 0.079712 | 0.019197
625 | 38.23 | 14.696 | 0.07971 | 9.1885 | 0.019201 |  | 625 | 9.1885 | 38.23 | 14.696 | 0.07971 | 0.019201
626 | 38.24 | 14.696 | 0.079709 | 9.1909 | 0.019206 |  | 626 | 9.1909 | 38.24 | 14.696 | 0.079709 | 0.019206
627 | 38.25 | 14.696 | 0.079707 | 9.1933 | 0.019211 |  | 627 | 9.1933 | 38.25 | 14.696 | 0.079707 | 0.019211
628 | 38.26 | 14.696 | 0.079705 | 9.1957 | 0.019216 |  | 628 | 9.1957 | 38.26 | 14.696 | 0.079705 | 0.019216
629 | 38.27 | 14.696 | 0.079704 | 9.1981 | 0.019221 |  | 629 | 9.1981 | 38.27 | 14.696 | 0.079704 | 0.019221
630 | 38.28 | 14.696 | 0.079702 | 9.2005 | 0.019226 |  | 630 | 9.2005 | 38.28 | 14.696 | 0.079702 | 0.019226
631 | 38.29 | 14.696 | 0.079701 | 9.2029 | 0.01923 |  | 631 | 9.2029 | 38.29 | 14.696 | 0.079701 | 0.01923
632 | 38.3 | 14.696 | 0.079699 | 9.2053 | 0.019235 |  | 632 | 9.2053 | 38.3 | 14.696 | 0.079699 | 0.019235
633 | 38.31 | 14.696 | 0.079697 | 9.2077 | 0.01924 |  | 633 | 9.2077 | 38.31 | 14.696 | 0.079697 | 0.01924
634 | 38.32 | 14.696 | 0.079696 | 9.2101 | 0.019245 |  | 634 | 9.2101 | 38.32 | 14.696 | 0.079696 | 0.019245
635 | 38.33 | 14.696 | 0.079694 | 9.2125 | 0.01925 |  | 635 | 9.2125 | 38.33 | 14.696 | 0.079694 | 0.01925
636 | 38.34 | 14.696 | 0.079693 | 9.2149 | 0.019254 |  | 636 | 9.2149 | 38.34 | 14.696 | 0.079693 | 0.019254
637 | 38.35 | 14.696 | 0.079691 | 9.2173 | 0.019259 |  | 637 | 9.2173 | 38.35 | 14.696 | 0.079691 | 0.019259
638 | 38.36 | 14.696 | 0.079689 | 9.2197 | 0.019264 |  | 638 | 9.2197 | 38.36 | 14.696 | 0.079689 | 0.019264
639 | 38.37 | 14.696 | 0.079688 | 9.2221 | 0.019269 |  | 639 | 9.2221 | 38.37 | 14.696 | 0.079688 | 0.019269
640 | 38.38 | 14.696 | 0.079686 | 9.2245 | 0.019274 |  | 640 | 9.2245 | 38.38 | 14.696 | 0.079686 | 0.019274
641 | 38.39 | 14.696 | 0.079684 | 9.2269 | 0.019279 |  | 641 | 9.2269 | 38.39 | 14.696 | 0.079684 | 0.019279
642 | 38.4 | 14.696 | 0.079683 | 9.2293 | 0.019283 |  | 642 | 9.2293 | 38.4 | 14.696 | 0.079683 | 0.019283
643 | 38.41 | 14.696 | 0.079681 | 9.2317 | 0.019288 |  | 643 | 9.2317 | 38.41 | 14.696 | 0.079681 | 0.019288
644 | 38.42 | 14.696 | 0.07968 | 9.2341 | 0.019293 |  | 644 | 9.2341 | 38.42 | 14.696 | 0.07968 | 0.019293
645 | 38.43 | 14.696 | 0.079678 | 9.2365 | 0.019298 |  | 645 | 9.2365 | 38.43 | 14.696 | 0.079678 | 0.019298
646 | 38.44 | 14.696 | 0.079676 | 9.2389 | 0.019303 |  | 646 | 9.2389 | 38.44 | 14.696 | 0.079676 | 0.019303
647 | 38.45 | 14.696 | 0.079675 | 9.2413 | 0.019308 |  | 647 | 9.2413 | 38.45 | 14.696 | 0.079675 | 0.019308
648 | 38.46 | 14.696 | 0.079673 | 9.2437 | 0.019312 |  | 648 | 9.2437 | 38.46 | 14.696 | 0.079673 | 0.019312
649 | 38.47 | 14.696 | 0.079672 | 9.2461 | 0.019317 |  | 649 | 9.2461 | 38.47 | 14.696 | 0.079672 | 0.019317
650 | 38.48 | 14.696 | 0.07967 | 9.2485 | 0.019322 |  | 650 | 9.2485 | 38.48 | 14.696 | 0.07967 | 0.019322
651 | 38.49 | 14.696 | 0.079668 | 9.251 | 0.019327 |  | 651 | 9.251 | 38.49 | 14.696 | 0.079668 | 0.019327
652 | 38.5 | 14.696 | 0.079667 | 9.2534 | 0.019332 |  | 652 | 9.2534 | 38.5 | 14.696 | 0.079667 | 0.019332
653 | 38.51 | 14.696 | 0.079665 | 9.2558 | 0.019337 |  | 653 | 9.2558 | 38.51 | 14.696 | 0.079665 | 0.019337
654 | 38.52 | 14.696 | 0.079664 | 9.2582 | 0.019341 |  | 654 | 9.2582 | 38.52 | 14.696 | 0.079664 | 0.019341
655 | 38.53 | 14.696 | 0.079662 | 9.2606 | 0.019346 |  | 655 | 9.2606 | 38.53 | 14.696 | 0.079662 | 0.019346
656 | 38.54 | 14.696 | 0.07966 | 9.263 | 0.019351 |  | 656 | 9.263 | 38.54 | 14.696 | 0.07966 | 0.019351
657 | 38.55 | 14.696 | 0.079659 | 9.2654 | 0.019356 |  | 657 | 9.2654 | 38.55 | 14.696 | 0.079659 | 0.019356
658 | 38.56 | 14.696 | 0.079657 | 9.2678 | 0.019361 |  | 658 | 9.2678 | 38.56 | 14.696 | 0.079657 | 0.019361
659 | 38.57 | 14.696 | 0.079656 | 9.2702 | 0.019365 |  | 659 | 9.2702 | 38.57 | 14.696 | 0.079656 | 0.019365
660 | 38.58 | 14.696 | 0.079654 | 9.2726 | 0.01937 |  | 660 | 9.2726 | 38.58 | 14.696 | 0.079654 | 0.01937
661 | 38.59 | 14.696 | 0.079652 | 9.275 | 0.019375 |  | 661 | 9.275 | 38.59 | 14.696 | 0.079652 | 0.019375
662 | 38.6 | 14.696 | 0.079651 | 9.2774 | 0.01938 |  | 662 | 9.2774 | 38.6 | 14.696 | 0.079651 | 0.01938
663 | 38.61 | 14.696 | 0.079649 | 9.2798 | 0.019385 |  | 663 | 9.2798 | 38.61 | 14.696 | 0.079649 | 0.019385
664 | 38.62 | 14.696 | 0.079648 | 9.2822 | 0.01939 |  | 664 | 9.2822 | 38.62 | 14.696 | 0.079648 | 0.01939
665 | 38.63 | 14.696 | 0.079646 | 9.2846 | 0.019394 |  | 665 | 9.2846 | 38.63 | 14.696 | 0.079646 | 0.019394
666 | 38.64 | 14.696 | 0.079644 | 9.287 | 0.019399 |  | 666 | 9.287 | 38.64 | 14.696 | 0.079644 | 0.019399
667 | 38.65 | 14.696 | 0.079643 | 9.2894 | 0.019404 |  | 667 | 9.2894 | 38.65 | 14.696 | 0.079643 | 0.019404
668 | 38.66 | 14.696 | 0.079641 | 9.2918 | 0.019409 |  | 668 | 9.2918 | 38.66 | 14.696 | 0.079641 | 0.019409
669 | 38.67 | 14.696 | 0.07964 | 9.2942 | 0.019414 |  | 669 | 9.2942 | 38.67 | 14.696 | 0.07964 | 0.019414
670 | 38.68 | 14.696 | 0.079638 | 9.2966 | 0.019419 |  | 670 | 9.2966 | 38.68 | 14.696 | 0.079638 | 0.019419
671 | 38.69 | 14.696 | 0.079636 | 9.299 | 0.019423 |  | 671 | 9.299 | 38.69 | 14.696 | 0.079636 | 0.019423
672 | 38.7 | 14.696 | 0.079635 | 9.3014 | 0.019428 |  | 672 | 9.3014 | 38.7 | 14.696 | 0.079635 | 0.019428
673 | 38.71 | 14.696 | 0.079633 | 9.3038 | 0.019433 |  | 673 | 9.3038 | 38.71 | 14.696 | 0.079633 | 0.019433
674 | 38.72 | 14.696 | 0.079632 | 9.3062 | 0.019438 |  | 674 | 9.3062 | 38.72 | 14.696 | 0.079632 | 0.019438
675 | 38.73 | 14.696 | 0.07963 | 9.3086 | 0.019443 |  | 675 | 9.3086 | 38.73 | 14.696 | 0.07963 | 0.019443
676 | 38.74 | 14.696 | 0.079628 | 9.311 | 0.019447 |  | 676 | 9.311 | 38.74 | 14.696 | 0.079628 | 0.019447
677 | 38.75 | 14.696 | 0.079627 | 9.3134 | 0.019452 |  | 677 | 9.3134 | 38.75 | 14.696 | 0.079627 | 0.019452
678 | 38.76 | 14.696 | 0.079625 | 9.3159 | 0.019457 |  | 678 | 9.3159 | 38.76 | 14.696 | 0.079625 | 0.019457
679 | 38.77 | 14.696 | 0.079624 | 9.3183 | 0.019462 |  | 679 | 9.3183 | 38.77 | 14.696 | 0.079624 | 0.019462
680 | 38.78 | 14.696 | 0.079622 | 9.3207 | 0.019467 |  | 680 | 9.3207 | 38.78 | 14.696 | 0.079622 | 0.019467
681 | 38.79 | 14.696 | 0.07962 | 9.3231 | 0.019472 |  | 681 | 9.3231 | 38.79 | 14.696 | 0.07962 | 0.019472
682 | 38.8 | 14.696 | 0.079619 | 9.3255 | 0.019476 |  | 682 | 9.3255 | 38.8 | 14.696 | 0.079619 | 0.019476
683 | 38.81 | 14.696 | 0.079617 | 9.3279 | 0.019481 |  | 683 | 9.3279 | 38.81 | 14.696 | 0.079617 | 0.019481
684 | 38.82 | 14.696 | 0.079616 | 9.3303 | 0.019486 |  | 684 | 9.3303 | 38.82 | 14.696 | 0.079616 | 0.019486
685 | 38.83 | 14.696 | 0.079614 | 9.3327 | 0.019491 |  | 685 | 9.3327 | 38.83 | 14.696 | 0.079614 | 0.019491
686 | 38.84 | 14.696 | 0.079612 | 9.3351 | 0.019496 |  | 686 | 9.3351 | 38.84 | 14.696 | 0.079612 | 0.019496
687 | 38.85 | 14.696 | 0.079611 | 9.3375 | 0.019501 |  | 687 | 9.3375 | 38.85 | 14.696 | 0.079611 | 0.019501
688 | 38.86 | 14.696 | 0.079609 | 9.3399 | 0.019505 |  | 688 | 9.3399 | 38.86 | 14.696 | 0.079609 | 0.019505
689 | 38.87 | 14.696 | 0.079608 | 9.3423 | 0.01951 |  | 689 | 9.3423 | 38.87 | 14.696 | 0.079608 | 0.01951
690 | 38.88 | 14.696 | 0.079606 | 9.3447 | 0.019515 |  | 690 | 9.3447 | 38.88 | 14.696 | 0.079606 | 0.019515
691 | 38.89 | 14.696 | 0.079604 | 9.3471 | 0.01952 |  | 691 | 9.3471 | 38.89 | 14.696 | 0.079604 | 0.01952
692 | 38.9 | 14.696 | 0.079603 | 9.3495 | 0.019525 |  | 692 | 9.3495 | 38.9 | 14.696 | 0.079603 | 0.019525
693 | 38.91 | 14.696 | 0.079601 | 9.3519 | 0.019529 |  | 693 | 9.3519 | 38.91 | 14.696 | 0.079601 | 0.019529
694 | 38.92 | 14.696 | 0.079599 | 9.3543 | 0.019534 |  | 694 | 9.3543 | 38.92 | 14.696 | 0.079599 | 0.019534
695 | 38.93 | 14.696 | 0.079598 | 9.3567 | 0.019539 |  | 695 | 9.3567 | 38.93 | 14.696 | 0.079598 | 0.019539
696 | 38.94 | 14.696 | 0.079596 | 9.3591 | 0.019544 |  | 696 | 9.3591 | 38.94 | 14.696 | 0.079596 | 0.019544
697 | 38.95 | 14.696 | 0.079595 | 9.3615 | 0.019549 |  | 697 | 9.3615 | 38.95 | 14.696 | 0.079595 | 0.019549
698 | 38.96 | 14.696 | 0.079593 | 9.3639 | 0.019554 |  | 698 | 9.3639 | 38.96 | 14.696 | 0.079593 | 0.019554
699 | 38.97 | 14.696 | 0.079591 | 9.3663 | 0.019558 |  | 699 | 9.3663 | 38.97 | 14.696 | 0.079591 | 0.019558
700 | 38.98 | 14.696 | 0.07959 | 9.3687 | 0.019563 |  | 700 | 9.3687 | 38.98 | 14.696 | 0.07959 | 0.019563
701 | 38.99 | 14.696 | 0.079588 | 9.3711 | 0.019568 |  | 701 | 9.3711 | 38.99 | 14.696 | 0.079588 | 0.019568
702 | 39 | 14.696 | 0.079587 | 9.3735 | 0.019573 |  | 702 | 9.3735 | 39 | 14.696 | 0.079587 | 0.019573
703 | 39.01 | 14.696 | 0.079585 | 9.3759 | 0.019578 |  | 703 | 9.3759 | 39.01 | 14.696 | 0.079585 | 0.019578
704 | 39.02 | 14.696 | 0.079583 | 9.3784 | 0.019582 |  | 704 | 9.3784 | 39.02 | 14.696 | 0.079583 | 0.019582
705 | 39.03 | 14.696 | 0.079582 | 9.3808 | 0.019587 |  | 705 | 9.3808 | 39.03 | 14.696 | 0.079582 | 0.019587
706 | 39.04 | 14.696 | 0.07958 | 9.3832 | 0.019592 |  | 706 | 9.3832 | 39.04 | 14.696 | 0.07958 | 0.019592
707 | 39.05 | 14.696 | 0.079579 | 9.3856 | 0.019597 |  | 707 | 9.3856 | 39.05 | 14.696 | 0.079579 | 0.019597
708 | 39.06 | 14.696 | 0.079577 | 9.388 | 0.019602 |  | 708 | 9.388 | 39.06 | 14.696 | 0.079577 | 0.019602
709 | 39.07 | 14.696 | 0.079575 | 9.3904 | 0.019607 |  | 709 | 9.3904 | 39.07 | 14.696 | 0.079575 | 0.019607
710 | 39.08 | 14.696 | 0.079574 | 9.3928 | 0.019611 |  | 710 | 9.3928 | 39.08 | 14.696 | 0.079574 | 0.019611
711 | 39.09 | 14.696 | 0.079572 | 9.3952 | 0.019616 |  | 711 | 9.3952 | 39.09 | 14.696 | 0.079572 | 0.019616
712 | 39.1 | 14.696 | 0.079571 | 9.3976 | 0.019621 |  | 712 | 9.3976 | 39.1 | 14.696 | 0.079571 | 0.019621
713 | 39.11 | 14.696 | 0.079569 | 9.4 | 0.019626 |  | 713 | 9.4 | 39.11 | 14.696 | 0.079569 | 0.019626
714 | 39.12 | 14.696 | 0.079567 | 9.4024 | 0.019631 |  | 714 | 9.4024 | 39.12 | 14.696 | 0.079567 | 0.019631
715 | 39.13 | 14.696 | 0.079566 | 9.4048 | 0.019635 |  | 715 | 9.4048 | 39.13 | 14.696 | 0.079566 | 0.019635
716 | 39.14 | 14.696 | 0.079564 | 9.4072 | 0.01964 |  | 716 | 9.4072 | 39.14 | 14.696 | 0.079564 | 0.01964
717 | 39.15 | 14.696 | 0.079563 | 9.4096 | 0.019645 |  | 717 | 9.4096 | 39.15 | 14.696 | 0.079563 | 0.019645
718 | 39.16 | 14.696 | 0.079561 | 9.412 | 0.01965 |  | 718 | 9.412 | 39.16 | 14.696 | 0.079561 | 0.01965
719 | 39.17 | 14.696 | 0.079559 | 9.4144 | 0.019655 |  | 719 | 9.4144 | 39.17 | 14.696 | 0.079559 | 0.019655
720 | 39.18 | 14.696 | 0.079558 | 9.4168 | 0.01966 |  | 720 | 9.4168 | 39.18 | 14.696 | 0.079558 | 0.01966
721 | 39.19 | 14.696 | 0.079556 | 9.4192 | 0.019664 |  | 721 | 9.4192 | 39.19 | 14.696 | 0.079556 | 0.019664
722 | 39.2 | 14.696 | 0.079555 | 9.4216 | 0.019669 |  | 722 | 9.4216 | 39.2 | 14.696 | 0.079555 | 0.019669
723 | 39.21 | 14.696 | 0.079553 | 9.424 | 0.019674 |  | 723 | 9.424 | 39.21 | 14.696 | 0.079553 | 0.019674
724 | 39.22 | 14.696 | 0.079551 | 9.4264 | 0.019679 |  | 724 | 9.4264 | 39.22 | 14.696 | 0.079551 | 0.019679
725 | 39.23 | 14.696 | 0.07955 | 9.4288 | 0.019684 |  | 725 | 9.4288 | 39.23 | 14.696 | 0.07955 | 0.019684
726 | 39.24 | 14.696 | 0.079548 | 9.4312 | 0.019688 |  | 726 | 9.4312 | 39.24 | 14.696 | 0.079548 | 0.019688
727 | 39.25 | 14.696 | 0.079547 | 9.4336 | 0.019693 |  | 727 | 9.4336 | 39.25 | 14.696 | 0.079547 | 0.019693
728 | 39.26 | 14.696 | 0.079545 | 9.436 | 0.019698 |  | 728 | 9.436 | 39.26 | 14.696 | 0.079545 | 0.019698
729 | 39.27 | 14.696 | 0.079543 | 9.4384 | 0.019703 |  | 729 | 9.4384 | 39.27 | 14.696 | 0.079543 | 0.019703
730 | 39.28 | 14.696 | 0.079542 | 9.4408 | 0.019708 |  | 730 | 9.4408 | 39.28 | 14.696 | 0.079542 | 0.019708
731 | 39.29 | 14.696 | 0.07954 | 9.4433 | 0.019713 |  | 731 | 9.4433 | 39.29 | 14.696 | 0.07954 | 0.019713
732 | 39.3 | 14.696 | 0.079539 | 9.4457 | 0.019717 |  | 732 | 9.4457 | 39.3 | 14.696 | 0.079539 | 0.019717
733 | 39.31 | 14.696 | 0.079537 | 9.4481 | 0.019722 |  | 733 | 9.4481 | 39.31 | 14.696 | 0.079537 | 0.019722
734 | 39.32 | 14.696 | 0.079535 | 9.4505 | 0.019727 |  | 734 | 9.4505 | 39.32 | 14.696 | 0.079535 | 0.019727
735 | 39.33 | 14.696 | 0.079534 | 9.4529 | 0.019732 |  | 735 | 9.4529 | 39.33 | 14.696 | 0.079534 | 0.019732
736 | 39.34 | 14.696 | 0.079532 | 9.4553 | 0.019737 |  | 736 | 9.4553 | 39.34 | 14.696 | 0.079532 | 0.019737
737 | 39.35 | 14.696 | 0.079531 | 9.4577 | 0.019741 |  | 737 | 9.4577 | 39.35 | 14.696 | 0.079531 | 0.019741
738 | 39.36 | 14.696 | 0.079529 | 9.4601 | 0.019746 |  | 738 | 9.4601 | 39.36 | 14.696 | 0.079529 | 0.019746
739 | 39.37 | 14.696 | 0.079527 | 9.4625 | 0.019751 |  | 739 | 9.4625 | 39.37 | 14.696 | 0.079527 | 0.019751
740 | 39.38 | 14.696 | 0.079526 | 9.4649 | 0.019756 |  | 740 | 9.4649 | 39.38 | 14.696 | 0.079526 | 0.019756
741 | 39.39 | 14.696 | 0.079524 | 9.4673 | 0.019761 |  | 741 | 9.4673 | 39.39 | 14.696 | 0.079524 | 0.019761
742 | 39.4 | 14.696 | 0.079523 | 9.4697 | 0.019766 |  | 742 | 9.4697 | 39.4 | 14.696 | 0.079523 | 0.019766
743 | 39.41 | 14.696 | 0.079521 | 9.4721 | 0.01977 |  | 743 | 9.4721 | 39.41 | 14.696 | 0.079521 | 0.01977
744 | 39.42 | 14.696 | 0.079519 | 9.4745 | 0.019775 |  | 744 | 9.4745 | 39.42 | 14.696 | 0.079519 | 0.019775
745 | 39.43 | 14.696 | 0.079518 | 9.4769 | 0.01978 |  | 745 | 9.4769 | 39.43 | 14.696 | 0.079518 | 0.01978
746 | 39.44 | 14.696 | 0.079516 | 9.4793 | 0.019785 |  | 746 | 9.4793 | 39.44 | 14.696 | 0.079516 | 0.019785
747 | 39.45 | 14.696 | 0.079515 | 9.4817 | 0.01979 |  | 747 | 9.4817 | 39.45 | 14.696 | 0.079515 | 0.01979
748 | 39.46 | 14.696 | 0.079513 | 9.4841 | 0.019794 |  | 748 | 9.4841 | 39.46 | 14.696 | 0.079513 | 0.019794
749 | 39.47 | 14.696 | 0.079511 | 9.4865 | 0.019799 |  | 749 | 9.4865 | 39.47 | 14.696 | 0.079511 | 0.019799
750 | 39.48 | 14.696 | 0.07951 | 9.4889 | 0.019804 |  | 750 | 9.4889 | 39.48 | 14.696 | 0.07951 | 0.019804
751 | 39.49 | 14.696 | 0.079508 | 9.4913 | 0.019809 |  | 751 | 9.4913 | 39.49 | 14.696 | 0.079508 | 0.019809
752 | 39.5 | 14.696 | 0.079507 | 9.4937 | 0.019814 |  | 752 | 9.4937 | 39.5 | 14.696 | 0.079507 | 0.019814
753 | 39.51 | 14.696 | 0.079505 | 9.4961 | 0.019819 |  | 753 | 9.4961 | 39.51 | 14.696 | 0.079505 | 0.019819
754 | 39.52 | 14.696 | 0.079503 | 9.4985 | 0.019823 |  | 754 | 9.4985 | 39.52 | 14.696 | 0.079503 | 0.019823
755 | 39.53 | 14.696 | 0.079502 | 9.5009 | 0.019828 |  | 755 | 9.5009 | 39.53 | 14.696 | 0.079502 | 0.019828
756 | 39.54 | 14.696 | 0.0795 | 9.5033 | 0.019833 |  | 756 | 9.5033 | 39.54 | 14.696 | 0.0795 | 0.019833
757 | 39.55 | 14.696 | 0.079499 | 9.5058 | 0.019838 |  | 757 | 9.5058 | 39.55 | 14.696 | 0.079499 | 0.019838
758 | 39.56 | 14.696 | 0.079497 | 9.5082 | 0.019843 |  | 758 | 9.5082 | 39.56 | 14.696 | 0.079497 | 0.019843
759 | 39.57 | 14.696 | 0.079496 | 9.5106 | 0.019847 |  | 759 | 9.5106 | 39.57 | 14.696 | 0.079496 | 0.019847
760 | 39.58 | 14.696 | 0.079494 | 9.513 | 0.019852 |  | 760 | 9.513 | 39.58 | 14.696 | 0.079494 | 0.019852
761 | 39.59 | 14.696 | 0.079492 | 9.5154 | 0.019857 |  | 761 | 9.5154 | 39.59 | 14.696 | 0.079492 | 0.019857
762 | 39.6 | 14.696 | 0.079491 | 9.5178 | 0.019862 |  | 762 | 9.5178 | 39.6 | 14.696 | 0.079491 | 0.019862
763 | 39.61 | 14.696 | 0.079489 | 9.5202 | 0.019867 |  | 763 | 9.5202 | 39.61 | 14.696 | 0.079489 | 0.019867
764 | 39.62 | 14.696 | 0.079488 | 9.5226 | 0.019872 |  | 764 | 9.5226 | 39.62 | 14.696 | 0.079488 | 0.019872
765 | 39.63 | 14.696 | 0.079486 | 9.525 | 0.019876 |  | 765 | 9.525 | 39.63 | 14.696 | 0.079486 | 0.019876
766 | 39.64 | 14.696 | 0.079484 | 9.5274 | 0.019881 |  | 766 | 9.5274 | 39.64 | 14.696 | 0.079484 | 0.019881
767 | 39.65 | 14.696 | 0.079483 | 9.5298 | 0.019886 |  | 767 | 9.5298 | 39.65 | 14.696 | 0.079483 | 0.019886
768 | 39.66 | 14.696 | 0.079481 | 9.5322 | 0.019891 |  | 768 | 9.5322 | 39.66 | 14.696 | 0.079481 | 0.019891
769 | 39.67 | 14.696 | 0.07948 | 9.5346 | 0.019896 |  | 769 | 9.5346 | 39.67 | 14.696 | 0.07948 | 0.019896
770 | 39.68 | 14.696 | 0.079478 | 9.537 | 0.0199 |  | 770 | 9.537 | 39.68 | 14.696 | 0.079478 | 0.0199
771 | 39.69 | 14.696 | 0.079476 | 9.5394 | 0.019905 |  | 771 | 9.5394 | 39.69 | 14.696 | 0.079476 | 0.019905
772 | 39.7 | 14.696 | 0.079475 | 9.5418 | 0.01991 |  | 772 | 9.5418 | 39.7 | 14.696 | 0.079475 | 0.01991
773 | 39.71 | 14.696 | 0.079473 | 9.5442 | 0.019915 |  | 773 | 9.5442 | 39.71 | 14.696 | 0.079473 | 0.019915
774 | 39.72 | 14.696 | 0.079472 | 9.5466 | 0.01992 |  | 774 | 9.5466 | 39.72 | 14.696 | 0.079472 | 0.01992
775 | 39.73 | 14.696 | 0.07947 | 9.549 | 0.019924 |  | 775 | 9.549 | 39.73 | 14.696 | 0.07947 | 0.019924
776 | 39.74 | 14.696 | 0.079468 | 9.5514 | 0.019929 |  | 776 | 9.5514 | 39.74 | 14.696 | 0.079468 | 0.019929
777 | 39.75 | 14.696 | 0.079467 | 9.5538 | 0.019934 |  | 777 | 9.5538 | 39.75 | 14.696 | 0.079467 | 0.019934
778 | 39.76 | 14.696 | 0.079465 | 9.5562 | 0.019939 |  | 778 | 9.5562 | 39.76 | 14.696 | 0.079465 | 0.019939
779 | 39.77 | 14.696 | 0.079464 | 9.5586 | 0.019944 |  | 779 | 9.5586 | 39.77 | 14.696 | 0.079464 | 0.019944
780 | 39.78 | 14.696 | 0.079462 | 9.561 | 0.019949 |  | 780 | 9.561 | 39.78 | 14.696 | 0.079462 | 0.019949
781 | 39.79 | 14.696 | 0.07946 | 9.5634 | 0.019953 |  | 781 | 9.5634 | 39.79 | 14.696 | 0.07946 | 0.019953
782 | 39.8 | 14.696 | 0.079459 | 9.5658 | 0.019958 |  | 782 | 9.5658 | 39.8 | 14.696 | 0.079459 | 0.019958
783 | 39.81 | 14.696 | 0.079457 | 9.5683 | 0.019963 |  | 783 | 9.5683 | 39.81 | 14.696 | 0.079457 | 0.019963
784 | 39.82 | 14.696 | 0.079456 | 9.5707 | 0.019968 |  | 784 | 9.5707 | 39.82 | 14.696 | 0.079456 | 0.019968
785 | 39.83 | 14.696 | 0.079454 | 9.5731 | 0.019973 |  | 785 | 9.5731 | 39.83 | 14.696 | 0.079454 | 0.019973
786 | 39.84 | 14.696 | 0.079452 | 9.5755 | 0.019977 |  | 786 | 9.5755 | 39.84 | 14.696 | 0.079452 | 0.019977
787 | 39.85 | 14.696 | 0.079451 | 9.5779 | 0.019982 |  | 787 | 9.5779 | 39.85 | 14.696 | 0.079451 | 0.019982
788 | 39.86 | 14.696 | 0.079449 | 9.5803 | 0.019987 |  | 788 | 9.5803 | 39.86 | 14.696 | 0.079449 | 0.019987
789 | 39.87 | 14.696 | 0.079448 | 9.5827 | 0.019992 |  | 789 | 9.5827 | 39.87 | 14.696 | 0.079448 | 0.019992
790 | 39.88 | 14.696 | 0.079446 | 9.5851 | 0.019997 |  | 790 | 9.5851 | 39.88 | 14.696 | 0.079446 | 0.019997
791 | 39.89 | 14.696 | 0.079444 | 9.5875 | 0.020001 |  | 791 | 9.5875 | 39.89 | 14.696 | 0.079444 | 0.020001
792 | 39.9 | 14.696 | 0.079443 | 9.5899 | 0.020006 |  | 792 | 9.5899 | 39.9 | 14.696 | 0.079443 | 0.020006
793 | 39.91 | 14.696 | 0.079441 | 9.5923 | 0.020011 |  | 793 | 9.5923 | 39.91 | 14.696 | 0.079441 | 0.020011
794 | 39.92 | 14.696 | 0.07944 | 9.5947 | 0.020016 |  | 794 | 9.5947 | 39.92 | 14.696 | 0.07944 | 0.020016
795 | 39.93 | 14.696 | 0.079438 | 9.5971 | 0.020021 |  | 795 | 9.5971 | 39.93 | 14.696 | 0.079438 | 0.020021
796 | 39.94 | 14.696 | 0.079436 | 9.5995 | 0.020026 |  | 796 | 9.5995 | 39.94 | 14.696 | 0.079436 | 0.020026
797 | 39.95 | 14.696 | 0.079435 | 9.6019 | 0.02003 |  | 797 | 9.6019 | 39.95 | 14.696 | 0.079435 | 0.02003
798 | 39.96 | 14.696 | 0.079433 | 9.6043 | 0.020035 |  | 798 | 9.6043 | 39.96 | 14.696 | 0.079433 | 0.020035
799 | 39.97 | 14.696 | 0.079432 | 9.6067 | 0.02004 |  | 799 | 9.6067 | 39.97 | 14.696 | 0.079432 | 0.02004
800 | 39.98 | 14.696 | 0.07943 | 9.6091 | 0.020045 |  | 800 | 9.6091 | 39.98 | 14.696 | 0.07943 | 0.020045
801 | 39.99 | 14.696 | 0.079428 | 9.6115 | 0.02005 |  | 801 | 9.6115 | 39.99 | 14.696 | 0.079428 | 0.02005
802 | 40 | 14.696 | 0.079427 | 9.6139 | 0.020054 |  | 802 | 9.6139 | 40 | 14.696 | 0.079427 | 0.020054
803 | 40.01 | 14.696 | 0.079425 | 9.6163 | 0.020059 |  | 803 | 9.6163 | 40.01 | 14.696 | 0.079425 | 0.020059
804 | 40.02 | 14.696 | 0.079424 | 9.6187 | 0.020064 |  | 804 | 9.6187 | 40.02 | 14.696 | 0.079424 | 0.020064
805 | 40.03 | 14.696 | 0.079422 | 9.6211 | 0.020069 |  | 805 | 9.6211 | 40.03 | 14.696 | 0.079422 | 0.020069
806 | 40.04 | 14.696 | 0.07942 | 9.6235 | 0.020074 |  | 806 | 9.6235 | 40.04 | 14.696 | 0.07942 | 0.020074
807 | 40.05 | 14.696 | 0.079419 | 9.6259 | 0.020078 |  | 807 | 9.6259 | 40.05 | 14.696 | 0.079419 | 0.020078
808 | 40.06 | 14.696 | 0.079417 | 9.6283 | 0.020083 |  | 808 | 9.6283 | 40.06 | 14.696 | 0.079417 | 0.020083
809 | 40.07 | 14.696 | 0.079416 | 9.6308 | 0.020088 |  | 809 | 9.6308 | 40.07 | 14.696 | 0.079416 | 0.020088
810 | 40.08 | 14.696 | 0.079414 | 9.6332 | 0.020093 |  | 810 | 9.6332 | 40.08 | 14.696 | 0.079414 | 0.020093
811 | 40.09 | 14.696 | 0.079413 | 9.6356 | 0.020098 |  | 811 | 9.6356 | 40.09 | 14.696 | 0.079413 | 0.020098
812 | 40.1 | 14.696 | 0.079411 | 9.638 | 0.020102 |  | 812 | 9.638 | 40.1 | 14.696 | 0.079411 | 0.020102
813 | 40.11 | 14.696 | 0.079409 | 9.6404 | 0.020107 |  | 813 | 9.6404 | 40.11 | 14.696 | 0.079409 | 0.020107
814 | 40.12 | 14.696 | 0.079408 | 9.6428 | 0.020112 |  | 814 | 9.6428 | 40.12 | 14.696 | 0.079408 | 0.020112
815 | 40.13 | 14.696 | 0.079406 | 9.6452 | 0.020117 |  | 815 | 9.6452 | 40.13 | 14.696 | 0.079406 | 0.020117
816 | 40.14 | 14.696 | 0.079405 | 9.6476 | 0.020122 |  | 816 | 9.6476 | 40.14 | 14.696 | 0.079405 | 0.020122
817 | 40.15 | 14.696 | 0.079403 | 9.65 | 0.020127 |  | 817 | 9.65 | 40.15 | 14.696 | 0.079403 | 0.020127
818 | 40.16 | 14.696 | 0.079401 | 9.6524 | 0.020131 |  | 818 | 9.6524 | 40.16 | 14.696 | 0.079401 | 0.020131
819 | 40.17 | 14.696 | 0.0794 | 9.6548 | 0.020136 |  | 819 | 9.6548 | 40.17 | 14.696 | 0.0794 | 0.020136
820 | 40.18 | 14.696 | 0.079398 | 9.6572 | 0.020141 |  | 820 | 9.6572 | 40.18 | 14.696 | 0.079398 | 0.020141
821 | 40.19 | 14.696 | 0.079397 | 9.6596 | 0.020146 |  | 821 | 9.6596 | 40.19 | 14.696 | 0.079397 | 0.020146
822 | 40.2 | 14.696 | 0.079395 | 9.662 | 0.020151 |  | 822 | 9.662 | 40.2 | 14.696 | 0.079395 | 0.020151
823 | 40.21 | 14.696 | 0.079393 | 9.6644 | 0.020155 |  | 823 | 9.6644 | 40.21 | 14.696 | 0.079393 | 0.020155
824 | 40.22 | 14.696 | 0.079392 | 9.6668 | 0.02016 |  | 824 | 9.6668 | 40.22 | 14.696 | 0.079392 | 0.02016
825 | 40.23 | 14.696 | 0.07939 | 9.6692 | 0.020165 |  | 825 | 9.6692 | 40.23 | 14.696 | 0.07939 | 0.020165
826 | 40.24 | 14.696 | 0.079389 | 9.6716 | 0.02017 |  | 826 | 9.6716 | 40.24 | 14.696 | 0.079389 | 0.02017
827 | 40.25 | 14.696 | 0.079387 | 9.674 | 0.020175 |  | 827 | 9.674 | 40.25 | 14.696 | 0.079387 | 0.020175
828 | 40.26 | 14.696 | 0.079385 | 9.6764 | 0.020179 |  | 828 | 9.6764 | 40.26 | 14.696 | 0.079385 | 0.020179
829 | 40.27 | 14.696 | 0.079384 | 9.6788 | 0.020184 |  | 829 | 9.6788 | 40.27 | 14.696 | 0.079384 | 0.020184
830 | 40.28 | 14.696 | 0.079382 | 9.6812 | 0.020189 |  | 830 | 9.6812 | 40.28 | 14.696 | 0.079382 | 0.020189
831 | 40.29 | 14.696 | 0.079381 | 9.6836 | 0.020194 |  | 831 | 9.6836 | 40.29 | 14.696 | 0.079381 | 0.020194
832 | 40.3 | 14.696 | 0.079379 | 9.686 | 0.020199 |  | 832 | 9.686 | 40.3 | 14.696 | 0.079379 | 0.020199
833 | 40.31 | 14.696 | 0.079377 | 9.6884 | 0.020203 |  | 833 | 9.6884 | 40.31 | 14.696 | 0.079377 | 0.020203
834 | 40.32 | 14.696 | 0.079376 | 9.6908 | 0.020208 |  | 834 | 9.6908 | 40.32 | 14.696 | 0.079376 | 0.020208
835 | 40.33 | 14.696 | 0.079374 | 9.6933 | 0.020213 |  | 835 | 9.6933 | 40.33 | 14.696 | 0.079374 | 0.020213
836 | 40.34 | 14.696 | 0.079373 | 9.6957 | 0.020218 |  | 836 | 9.6957 | 40.34 | 14.696 | 0.079373 | 0.020218
837 | 40.35 | 14.696 | 0.079371 | 9.6981 | 0.020223 |  | 837 | 9.6981 | 40.35 | 14.696 | 0.079371 | 0.020223
838 | 40.36 | 14.696 | 0.079369 | 9.7005 | 0.020228 |  | 838 | 9.7005 | 40.36 | 14.696 | 0.079369 | 0.020228
839 | 40.37 | 14.696 | 0.079368 | 9.7029 | 0.020232 |  | 839 | 9.7029 | 40.37 | 14.696 | 0.079368 | 0.020232
840 | 40.38 | 14.696 | 0.079366 | 9.7053 | 0.020237 |  | 840 | 9.7053 | 40.38 | 14.696 | 0.079366 | 0.020237
841 | 40.39 | 14.696 | 0.079365 | 9.7077 | 0.020242 |  | 841 | 9.7077 | 40.39 | 14.696 | 0.079365 | 0.020242
842 | 40.4 | 14.696 | 0.079363 | 9.7101 | 0.020247 |  | 842 | 9.7101 | 40.4 | 14.696 | 0.079363 | 0.020247
843 | 40.41 | 14.696 | 0.079362 | 9.7125 | 0.020252 |  | 843 | 9.7125 | 40.41 | 14.696 | 0.079362 | 0.020252
844 | 40.42 | 14.696 | 0.07936 | 9.7149 | 0.020256 |  | 844 | 9.7149 | 40.42 | 14.696 | 0.07936 | 0.020256
845 | 40.43 | 14.696 | 0.079358 | 9.7173 | 0.020261 |  | 845 | 9.7173 | 40.43 | 14.696 | 0.079358 | 0.020261
846 | 40.44 | 14.696 | 0.079357 | 9.7197 | 0.020266 |  | 846 | 9.7197 | 40.44 | 14.696 | 0.079357 | 0.020266
847 | 40.45 | 14.696 | 0.079355 | 9.7221 | 0.020271 |  | 847 | 9.7221 | 40.45 | 14.696 | 0.079355 | 0.020271
848 | 40.46 | 14.696 | 0.079354 | 9.7245 | 0.020276 |  | 848 | 9.7245 | 40.46 | 14.696 | 0.079354 | 0.020276
849 | 40.47 | 14.696 | 0.079352 | 9.7269 | 0.02028 |  | 849 | 9.7269 | 40.47 | 14.696 | 0.079352 | 0.02028
850 | 40.48 | 14.696 | 0.07935 | 9.7293 | 0.020285 |  | 850 | 9.7293 | 40.48 | 14.696 | 0.07935 | 0.020285
851 | 40.49 | 14.696 | 0.079349 | 9.7317 | 0.02029 |  | 851 | 9.7317 | 40.49 | 14.696 | 0.079349 | 0.02029
852 | 40.5 | 14.696 | 0.079347 | 9.7341 | 0.020295 |  | 852 | 9.7341 | 40.5 | 14.696 | 0.079347 | 0.020295
853 | 40.51 | 14.696 | 0.079346 | 9.7365 | 0.0203 |  | 853 | 9.7365 | 40.51 | 14.696 | 0.079346 | 0.0203
854 | 40.52 | 14.696 | 0.079344 | 9.7389 | 0.020304 |  | 854 | 9.7389 | 40.52 | 14.696 | 0.079344 | 0.020304
855 | 40.53 | 14.696 | 0.079342 | 9.7413 | 0.020309 |  | 855 | 9.7413 | 40.53 | 14.696 | 0.079342 | 0.020309
856 | 40.54 | 14.696 | 0.079341 | 9.7437 | 0.020314 |  | 856 | 9.7437 | 40.54 | 14.696 | 0.079341 | 0.020314
857 | 40.55 | 14.696 | 0.079339 | 9.7461 | 0.020319 |  | 857 | 9.7461 | 40.55 | 14.696 | 0.079339 | 0.020319
858 | 40.56 | 14.696 | 0.079338 | 9.7485 | 0.020324 |  | 858 | 9.7485 | 40.56 | 14.696 | 0.079338 | 0.020324
859 | 40.57 | 14.696 | 0.079336 | 9.7509 | 0.020328 |  | 859 | 9.7509 | 40.57 | 14.696 | 0.079336 | 0.020328
860 | 40.58 | 14.696 | 0.079334 | 9.7533 | 0.020333 |  | 860 | 9.7533 | 40.58 | 14.696 | 0.079334 | 0.020333
861 | 40.59 | 14.696 | 0.079333 | 9.7558 | 0.020338 |  | 861 | 9.7558 | 40.59 | 14.696 | 0.079333 | 0.020338
862 | 40.6 | 14.696 | 0.079331 | 9.7582 | 0.020343 |  | 862 | 9.7582 | 40.6 | 14.696 | 0.079331 | 0.020343
863 | 40.61 | 14.696 | 0.07933 | 9.7606 | 0.020348 |  | 863 | 9.7606 | 40.61 | 14.696 | 0.07933 | 0.020348
864 | 40.62 | 14.696 | 0.079328 | 9.763 | 0.020352 |  | 864 | 9.763 | 40.62 | 14.696 | 0.079328 | 0.020352
865 | 40.63 | 14.696 | 0.079327 | 9.7654 | 0.020357 |  | 865 | 9.7654 | 40.63 | 14.696 | 0.079327 | 0.020357
866 | 40.64 | 14.696 | 0.079325 | 9.7678 | 0.020362 |  | 866 | 9.7678 | 40.64 | 14.696 | 0.079325 | 0.020362
867 | 40.65 | 14.696 | 0.079323 | 9.7702 | 0.020367 |  | 867 | 9.7702 | 40.65 | 14.696 | 0.079323 | 0.020367
868 | 40.66 | 14.696 | 0.079322 | 9.7726 | 0.020372 |  | 868 | 9.7726 | 40.66 | 14.696 | 0.079322 | 0.020372
869 | 40.67 | 14.696 | 0.07932 | 9.775 | 0.020376 |  | 869 | 9.775 | 40.67 | 14.696 | 0.07932 | 0.020376
870 | 40.68 | 14.696 | 0.079319 | 9.7774 | 0.020381 |  | 870 | 9.7774 | 40.68 | 14.696 | 0.079319 | 0.020381
871 | 40.69 | 14.696 | 0.079317 | 9.7798 | 0.020386 |  | 871 | 9.7798 | 40.69 | 14.696 | 0.079317 | 0.020386
872 | 40.7 | 14.696 | 0.079315 | 9.7822 | 0.020391 |  | 872 | 9.7822 | 40.7 | 14.696 | 0.079315 | 0.020391
873 | 40.71 | 14.696 | 0.079314 | 9.7846 | 0.020396 |  | 873 | 9.7846 | 40.71 | 14.696 | 0.079314 | 0.020396
874 | 40.72 | 14.696 | 0.079312 | 9.787 | 0.020401 |  | 874 | 9.787 | 40.72 | 14.696 | 0.079312 | 0.020401
875 | 40.73 | 14.696 | 0.079311 | 9.7894 | 0.020405 |  | 875 | 9.7894 | 40.73 | 14.696 | 0.079311 | 0.020405
876 | 40.74 | 14.696 | 0.079309 | 9.7918 | 0.02041 |  | 876 | 9.7918 | 40.74 | 14.696 | 0.079309 | 0.02041
877 | 40.75 | 14.696 | 0.079307 | 9.7942 | 0.020415 |  | 877 | 9.7942 | 40.75 | 14.696 | 0.079307 | 0.020415
878 | 40.76 | 14.696 | 0.079306 | 9.7966 | 0.02042 |  | 878 | 9.7966 | 40.76 | 14.696 | 0.079306 | 0.02042
879 | 40.77 | 14.696 | 0.079304 | 9.799 | 0.020425 |  | 879 | 9.799 | 40.77 | 14.696 | 0.079304 | 0.020425
880 | 40.78 | 14.696 | 0.079303 | 9.8014 | 0.020429 |  | 880 | 9.8014 | 40.78 | 14.696 | 0.079303 | 0.020429
881 | 40.79 | 14.696 | 0.079301 | 9.8038 | 0.020434 |  | 881 | 9.8038 | 40.79 | 14.696 | 0.079301 | 0.020434
882 | 40.8 | 14.696 | 0.079299 | 9.8062 | 0.020439 |  | 882 | 9.8062 | 40.8 | 14.696 | 0.079299 | 0.020439
883 | 40.81 | 14.696 | 0.079298 | 9.8086 | 0.020444 |  | 883 | 9.8086 | 40.81 | 14.696 | 0.079298 | 0.020444
884 | 40.82 | 14.696 | 0.079296 | 9.811 | 0.020449 |  | 884 | 9.811 | 40.82 | 14.696 | 0.079296 | 0.020449
885 | 40.83 | 14.696 | 0.079295 | 9.8134 | 0.020453 |  | 885 | 9.8134 | 40.83 | 14.696 | 0.079295 | 0.020453
886 | 40.84 | 14.696 | 0.079293 | 9.8158 | 0.020458 |  | 886 | 9.8158 | 40.84 | 14.696 | 0.079293 | 0.020458
887 | 40.85 | 14.696 | 0.079292 | 9.8183 | 0.020463 |  | 887 | 9.8183 | 40.85 | 14.696 | 0.079292 | 0.020463
888 | 40.86 | 14.696 | 0.07929 | 9.8207 | 0.020468 |  | 888 | 9.8207 | 40.86 | 14.696 | 0.07929 | 0.020468
889 | 40.87 | 14.696 | 0.079288 | 9.8231 | 0.020473 |  | 889 | 9.8231 | 40.87 | 14.696 | 0.079288 | 0.020473
890 | 40.88 | 14.696 | 0.079287 | 9.8255 | 0.020477 |  | 890 | 9.8255 | 40.88 | 14.696 | 0.079287 | 0.020477
891 | 40.89 | 14.696 | 0.079285 | 9.8279 | 0.020482 |  | 891 | 9.8279 | 40.89 | 14.696 | 0.079285 | 0.020482
892 | 40.9 | 14.696 | 0.079284 | 9.8303 | 0.020487 |  | 892 | 9.8303 | 40.9 | 14.696 | 0.079284 | 0.020487
893 | 40.91 | 14.696 | 0.079282 | 9.8327 | 0.020492 |  | 893 | 9.8327 | 40.91 | 14.696 | 0.079282 | 0.020492
894 | 40.92 | 14.696 | 0.07928 | 9.8351 | 0.020497 |  | 894 | 9.8351 | 40.92 | 14.696 | 0.07928 | 0.020497
895 | 40.93 | 14.696 | 0.079279 | 9.8375 | 0.020501 |  | 895 | 9.8375 | 40.93 | 14.696 | 0.079279 | 0.020501
896 | 40.94 | 14.696 | 0.079277 | 9.8399 | 0.020506 |  | 896 | 9.8399 | 40.94 | 14.696 | 0.079277 | 0.020506
897 | 40.95 | 14.696 | 0.079276 | 9.8423 | 0.020511 |  | 897 | 9.8423 | 40.95 | 14.696 | 0.079276 | 0.020511
898 | 40.96 | 14.696 | 0.079274 | 9.8447 | 0.020516 |  | 898 | 9.8447 | 40.96 | 14.696 | 0.079274 | 0.020516
899 | 40.97 | 14.696 | 0.079272 | 9.8471 | 0.020521 |  | 899 | 9.8471 | 40.97 | 14.696 | 0.079272 | 0.020521
900 | 40.98 | 14.696 | 0.079271 | 9.8495 | 0.020525 |  | 900 | 9.8495 | 40.98 | 14.696 | 0.079271 | 0.020525
901 | 40.99 | 14.696 | 0.079269 | 9.8519 | 0.02053 |  | 901 | 9.8519 | 40.99 | 14.696 | 0.079269 | 0.02053
902 | 41 | 14.696 | 0.079268 | 9.8543 | 0.020535 |  | 902 | 9.8543 | 41 | 14.696 | 0.079268 | 0.020535
903 | 41.01 | 14.696 | 0.079266 | 9.8567 | 0.02054 |  | 903 | 9.8567 | 41.01 | 14.696 | 0.079266 | 0.02054
904 | 41.02 | 14.696 | 0.079265 | 9.8591 | 0.020545 |  | 904 | 9.8591 | 41.02 | 14.696 | 0.079265 | 0.020545
905 | 41.03 | 14.696 | 0.079263 | 9.8615 | 0.020549 |  | 905 | 9.8615 | 41.03 | 14.696 | 0.079263 | 0.020549
906 | 41.04 | 14.696 | 0.079261 | 9.8639 | 0.020554 |  | 906 | 9.8639 | 41.04 | 14.696 | 0.079261 | 0.020554
907 | 41.05 | 14.696 | 0.07926 | 9.8663 | 0.020559 |  | 907 | 9.8663 | 41.05 | 14.696 | 0.07926 | 0.020559
908 | 41.06 | 14.696 | 0.079258 | 9.8687 | 0.020564 |  | 908 | 9.8687 | 41.06 | 14.696 | 0.079258 | 0.020564
909 | 41.07 | 14.696 | 0.079257 | 9.8711 | 0.020569 |  | 909 | 9.8711 | 41.07 | 14.696 | 0.079257 | 0.020569
910 | 41.08 | 14.696 | 0.079255 | 9.8735 | 0.020573 |  | 910 | 9.8735 | 41.08 | 14.696 | 0.079255 | 0.020573
911 | 41.09 | 14.696 | 0.079253 | 9.8759 | 0.020578 |  | 911 | 9.8759 | 41.09 | 14.696 | 0.079253 | 0.020578
912 | 41.1 | 14.696 | 0.079252 | 9.8783 | 0.020583 |  | 912 | 9.8783 | 41.1 | 14.696 | 0.079252 | 0.020583
913 | 41.11 | 14.696 | 0.07925 | 9.8808 | 0.020588 |  | 913 | 9.8808 | 41.11 | 14.696 | 0.07925 | 0.020588
914 | 41.12 | 14.696 | 0.079249 | 9.8832 | 0.020593 |  | 914 | 9.8832 | 41.12 | 14.696 | 0.079249 | 0.020593
915 | 41.13 | 14.696 | 0.079247 | 9.8856 | 0.020597 |  | 915 | 9.8856 | 41.13 | 14.696 | 0.079247 | 0.020597
916 | 41.14 | 14.696 | 0.079245 | 9.888 | 0.020602 |  | 916 | 9.888 | 41.14 | 14.696 | 0.079245 | 0.020602
917 | 41.15 | 14.696 | 0.079244 | 9.8904 | 0.020607 |  | 917 | 9.8904 | 41.15 | 14.696 | 0.079244 | 0.020607
918 | 41.16 | 14.696 | 0.079242 | 9.8928 | 0.020612 |  | 918 | 9.8928 | 41.16 | 14.696 | 0.079242 | 0.020612
919 | 41.17 | 14.696 | 0.079241 | 9.8952 | 0.020617 |  | 919 | 9.8952 | 41.17 | 14.696 | 0.079241 | 0.020617
920 | 41.18 | 14.696 | 0.079239 | 9.8976 | 0.020621 |  | 920 | 9.8976 | 41.18 | 14.696 | 0.079239 | 0.020621
921 | 41.19 | 14.696 | 0.079238 | 9.9 | 0.020626 |  | 921 | 9.9 | 41.19 | 14.696 | 0.079238 | 0.020626
922 | 41.2 | 14.696 | 0.079236 | 9.9024 | 0.020631 |  | 922 | 9.9024 | 41.2 | 14.696 | 0.079236 | 0.020631
923 | 41.21 | 14.696 | 0.079234 | 9.9048 | 0.020636 |  | 923 | 9.9048 | 41.21 | 14.696 | 0.079234 | 0.020636
924 | 41.22 | 14.696 | 0.079233 | 9.9072 | 0.020641 |  | 924 | 9.9072 | 41.22 | 14.696 | 0.079233 | 0.020641
925 | 41.23 | 14.696 | 0.079231 | 9.9096 | 0.020645 |  | 925 | 9.9096 | 41.23 | 14.696 | 0.079231 | 0.020645
926 | 41.24 | 14.696 | 0.07923 | 9.912 | 0.02065 |  | 926 | 9.912 | 41.24 | 14.696 | 0.07923 | 0.02065
927 | 41.25 | 14.696 | 0.079228 | 9.9144 | 0.020655 |  | 927 | 9.9144 | 41.25 | 14.696 | 0.079228 | 0.020655
928 | 41.26 | 14.696 | 0.079226 | 9.9168 | 0.02066 |  | 928 | 9.9168 | 41.26 | 14.696 | 0.079226 | 0.02066
929 | 41.27 | 14.696 | 0.079225 | 9.9192 | 0.020665 |  | 929 | 9.9192 | 41.27 | 14.696 | 0.079225 | 0.020665
930 | 41.28 | 14.696 | 0.079223 | 9.9216 | 0.020669 |  | 930 | 9.9216 | 41.28 | 14.696 | 0.079223 | 0.020669
931 | 41.29 | 14.696 | 0.079222 | 9.924 | 0.020674 |  | 931 | 9.924 | 41.29 | 14.696 | 0.079222 | 0.020674
932 | 41.3 | 14.696 | 0.07922 | 9.9264 | 0.020679 |  | 932 | 9.9264 | 41.3 | 14.696 | 0.07922 | 0.020679
933 | 41.31 | 14.696 | 0.079218 | 9.9288 | 0.020684 |  | 933 | 9.9288 | 41.31 | 14.696 | 0.079218 | 0.020684
934 | 41.32 | 14.696 | 0.079217 | 9.9312 | 0.020689 |  | 934 | 9.9312 | 41.32 | 14.696 | 0.079217 | 0.020689
935 | 41.33 | 14.696 | 0.079215 | 9.9336 | 0.020693 |  | 935 | 9.9336 | 41.33 | 14.696 | 0.079215 | 0.020693
936 | 41.34 | 14.696 | 0.079214 | 9.936 | 0.020698 |  | 936 | 9.936 | 41.34 | 14.696 | 0.079214 | 0.020698
937 | 41.35 | 14.696 | 0.079212 | 9.9384 | 0.020703 |  | 937 | 9.9384 | 41.35 | 14.696 | 0.079212 | 0.020703
938 | 41.36 | 14.696 | 0.079211 | 9.9408 | 0.020708 |  | 938 | 9.9408 | 41.36 | 14.696 | 0.079211 | 0.020708
939 | 41.37 | 14.696 | 0.079209 | 9.9433 | 0.020713 |  | 939 | 9.9433 | 41.37 | 14.696 | 0.079209 | 0.020713
940 | 41.38 | 14.696 | 0.079207 | 9.9457 | 0.020717 |  | 940 | 9.9457 | 41.38 | 14.696 | 0.079207 | 0.020717
941 | 41.39 | 14.696 | 0.079206 | 9.9481 | 0.020722 |  | 941 | 9.9481 | 41.39 | 14.696 | 0.079206 | 0.020722
942 | 41.4 | 14.696 | 0.079204 | 9.9505 | 0.020727 |  | 942 | 9.9505 | 41.4 | 14.696 | 0.079204 | 0.020727
943 | 41.41 | 14.696 | 0.079203 | 9.9529 | 0.020732 |  | 943 | 9.9529 | 41.41 | 14.696 | 0.079203 | 0.020732
944 | 41.42 | 14.696 | 0.079201 | 9.9553 | 0.020737 |  | 944 | 9.9553 | 41.42 | 14.696 | 0.079201 | 0.020737
945 | 41.43 | 14.696 | 0.079199 | 9.9577 | 0.020741 |  | 945 | 9.9577 | 41.43 | 14.696 | 0.079199 | 0.020741
946 | 41.44 | 14.696 | 0.079198 | 9.9601 | 0.020746 |  | 946 | 9.9601 | 41.44 | 14.696 | 0.079198 | 0.020746
947 | 41.45 | 14.696 | 0.079196 | 9.9625 | 0.020751 |  | 947 | 9.9625 | 41.45 | 14.696 | 0.079196 | 0.020751
948 | 41.46 | 14.696 | 0.079195 | 9.9649 | 0.020756 |  | 948 | 9.9649 | 41.46 | 14.696 | 0.079195 | 0.020756
949 | 41.47 | 14.696 | 0.079193 | 9.9673 | 0.020761 |  | 949 | 9.9673 | 41.47 | 14.696 | 0.079193 | 0.020761
950 | 41.48 | 14.696 | 0.079192 | 9.9697 | 0.020765 |  | 950 | 9.9697 | 41.48 | 14.696 | 0.079192 | 0.020765
951 | 41.49 | 14.696 | 0.07919 | 9.9721 | 0.02077 |  | 951 | 9.9721 | 41.49 | 14.696 | 0.07919 | 0.02077
952 | 41.5 | 14.696 | 0.079188 | 9.9745 | 0.020775 |  | 952 | 9.9745 | 41.5 | 14.696 | 0.079188 | 0.020775
953 | 41.51 | 14.696 | 0.079187 | 9.9769 | 0.02078 |  | 953 | 9.9769 | 41.51 | 14.696 | 0.079187 | 0.02078
954 | 41.52 | 14.696 | 0.079185 | 9.9793 | 0.020785 |  | 954 | 9.9793 | 41.52 | 14.696 | 0.079185 | 0.020785
955 | 41.53 | 14.696 | 0.079184 | 9.9817 | 0.020789 |  | 955 | 9.9817 | 41.53 | 14.696 | 0.079184 | 0.020789
956 | 41.54 | 14.696 | 0.079182 | 9.9841 | 0.020794 |  | 956 | 9.9841 | 41.54 | 14.696 | 0.079182 | 0.020794
957 | 41.55 | 14.696 | 0.07918 | 9.9865 | 0.020799 |  | 957 | 9.9865 | 41.55 | 14.696 | 0.07918 | 0.020799
958 | 41.56 | 14.696 | 0.079179 | 9.9889 | 0.020804 |  | 958 | 9.9889 | 41.56 | 14.696 | 0.079179 | 0.020804
959 | 41.57 | 14.696 | 0.079177 | 9.9913 | 0.020809 |  | 959 | 9.9913 | 41.57 | 14.696 | 0.079177 | 0.020809
960 | 41.58 | 14.696 | 0.079176 | 9.9937 | 0.020813 |  | 960 | 9.9937 | 41.58 | 14.696 | 0.079176 | 0.020813
961 | 41.59 | 14.696 | 0.079174 | 9.9961 | 0.020818 |  | 961 | 9.9961 | 41.59 | 14.696 | 0.079174 | 0.020818
962 | 41.6 | 14.696 | 0.079172 | 9.9985 | 0.020823 |  | 962 | 9.9985 | 41.6 | 14.696 | 0.079172 | 0.020823
963 | 41.61 | 14.696 | 0.079171 | 10.001 | 0.020828 |  | 963 | 10.001 | 41.61 | 14.696 | 0.079171 | 0.020828
964 | 41.62 | 14.696 | 0.079169 | 10.003 | 0.020832 |  | 964 | 10.003 | 41.62 | 14.696 | 0.079169 | 0.020832
965 | 41.63 | 14.696 | 0.079168 | 10.006 | 0.020837 |  | 965 | 10.006 | 41.63 | 14.696 | 0.079168 | 0.020837
966 | 41.64 | 14.696 | 0.079166 | 10.008 | 0.020842 |  | 966 | 10.008 | 41.64 | 14.696 | 0.079166 | 0.020842
967 | 41.65 | 14.696 | 0.079165 | 10.011 | 0.020847 |  | 967 | 10.011 | 41.65 | 14.696 | 0.079165 | 0.020847
968 | 41.66 | 14.696 | 0.079163 | 10.013 | 0.020852 |  | 968 | 10.013 | 41.66 | 14.696 | 0.079163 | 0.020852
969 | 41.67 | 14.696 | 0.079161 | 10.015 | 0.020856 |  | 969 | 10.015 | 41.67 | 14.696 | 0.079161 | 0.020856
970 | 41.68 | 14.696 | 0.07916 | 10.018 | 0.020861 |  | 970 | 10.018 | 41.68 | 14.696 | 0.07916 | 0.020861
971 | 41.69 | 14.696 | 0.079158 | 10.02 | 0.020866 |  | 971 | 10.02 | 41.69 | 14.696 | 0.079158 | 0.020866
972 | 41.7 | 14.696 | 0.079157 | 10.023 | 0.020871 |  | 972 | 10.023 | 41.7 | 14.696 | 0.079157 | 0.020871
973 | 41.71 | 14.696 | 0.079155 | 10.025 | 0.020876 |  | 973 | 10.025 | 41.71 | 14.696 | 0.079155 | 0.020876
974 | 41.72 | 14.696 | 0.079153 | 10.027 | 0.02088 |  | 974 | 10.027 | 41.72 | 14.696 | 0.079153 | 0.02088
975 | 41.73 | 14.696 | 0.079152 | 10.03 | 0.020885 |  | 975 | 10.03 | 41.73 | 14.696 | 0.079152 | 0.020885
976 | 41.74 | 14.696 | 0.07915 | 10.032 | 0.02089 |  | 976 | 10.032 | 41.74 | 14.696 | 0.07915 | 0.02089
977 | 41.75 | 14.696 | 0.079149 | 10.035 | 0.020895 |  | 977 | 10.035 | 41.75 | 14.696 | 0.079149 | 0.020895
978 | 41.76 | 14.696 | 0.079147 | 10.037 | 0.0209 |  | 978 | 10.037 | 41.76 | 14.696 | 0.079147 | 0.0209
979 | 41.77 | 14.696 | 0.079146 | 10.039 | 0.020904 |  | 979 | 10.039 | 41.77 | 14.696 | 0.079146 | 0.020904
980 | 41.78 | 14.696 | 0.079144 | 10.042 | 0.020909 |  | 980 | 10.042 | 41.78 | 14.696 | 0.079144 | 0.020909
981 | 41.79 | 14.696 | 0.079142 | 10.044 | 0.020914 |  | 981 | 10.044 | 41.79 | 14.696 | 0.079142 | 0.020914
982 | 41.8 | 14.696 | 0.079141 | 10.047 | 0.020919 |  | 982 | 10.047 | 41.8 | 14.696 | 0.079141 | 0.020919
983 | 41.81 | 14.696 | 0.079139 | 10.049 | 0.020924 |  | 983 | 10.049 | 41.81 | 14.696 | 0.079139 | 0.020924
984 | 41.82 | 14.696 | 0.079138 | 10.051 | 0.020928 |  | 984 | 10.051 | 41.82 | 14.696 | 0.079138 | 0.020928
985 | 41.83 | 14.696 | 0.079136 | 10.054 | 0.020933 |  | 985 | 10.054 | 41.83 | 14.696 | 0.079136 | 0.020933
986 | 41.84 | 14.696 | 0.079134 | 10.056 | 0.020938 |  | 986 | 10.056 | 41.84 | 14.696 | 0.079134 | 0.020938
987 | 41.85 | 14.696 | 0.079133 | 10.059 | 0.020943 |  | 987 | 10.059 | 41.85 | 14.696 | 0.079133 | 0.020943
988 | 41.86 | 14.696 | 0.079131 | 10.061 | 0.020948 |  | 988 | 10.061 | 41.86 | 14.696 | 0.079131 | 0.020948
989 | 41.87 | 14.696 | 0.07913 | 10.063 | 0.020952 |  | 989 | 10.063 | 41.87 | 14.696 | 0.07913 | 0.020952
990 | 41.88 | 14.696 | 0.079128 | 10.066 | 0.020957 |  | 990 | 10.066 | 41.88 | 14.696 | 0.079128 | 0.020957
991 | 41.89 | 14.696 | 0.079127 | 10.068 | 0.020962 |  | 991 | 10.068 | 41.89 | 14.696 | 0.079127 | 0.020962
992 | 41.9 | 14.696 | 0.079125 | 10.071 | 0.020967 |  | 992 | 10.071 | 41.9 | 14.696 | 0.079125 | 0.020967
993 | 41.91 | 14.696 | 0.079123 | 10.073 | 0.020972 |  | 993 | 10.073 | 41.91 | 14.696 | 0.079123 | 0.020972
994 | 41.92 | 14.696 | 0.079122 | 10.075 | 0.020976 |  | 994 | 10.075 | 41.92 | 14.696 | 0.079122 | 0.020976
995 | 41.93 | 14.696 | 0.07912 | 10.078 | 0.020981 |  | 995 | 10.078 | 41.93 | 14.696 | 0.07912 | 0.020981
996 | 41.94 | 14.696 | 0.079119 | 10.08 | 0.020986 |  | 996 | 10.08 | 41.94 | 14.696 | 0.079119 | 0.020986
997 | 41.95 | 14.696 | 0.079117 | 10.083 | 0.020991 |  | 997 | 10.083 | 41.95 | 14.696 | 0.079117 | 0.020991
998 | 41.96 | 14.696 | 0.079115 | 10.085 | 0.020995 |  | 998 | 10.085 | 41.96 | 14.696 | 0.079115 | 0.020995
999 | 41.97 | 14.696 | 0.079114 | 10.087 | 0.021 |  | 999 | 10.087 | 41.97 | 14.696 | 0.079114 | 0.021
1000 | 41.98 | 14.696 | 0.079112 | 10.09 | 0.021005 |  | 1000 | 10.09 | 41.98 | 14.696 | 0.079112 | 0.021005
1001 | 41.99 | 14.696 | 0.079111 | 10.092 | 0.02101 |  | 1001 | 10.092 | 41.99 | 14.696 | 0.079111 | 0.02101
1002 | 42 | 14.696 | 0.079109 | 10.095 | 0.021015 |  | 1002 | 10.095 | 42 | 14.696 | 0.079109 | 0.021015
1003 | 42.01 | 14.696 | 0.079108 | 10.097 | 0.021019 |  | 1003 | 10.097 | 42.01 | 14.696 | 0.079108 | 0.021019
1004 | 42.02 | 14.696 | 0.079106 | 10.1 | 0.021024 |  | 1004 | 10.1 | 42.02 | 14.696 | 0.079106 | 0.021024
1005 | 42.03 | 14.696 | 0.079104 | 10.102 | 0.021029 |  | 1005 | 10.102 | 42.03 | 14.696 | 0.079104 | 0.021029
1006 | 42.04 | 14.696 | 0.079103 | 10.104 | 0.021034 |  | 1006 | 10.104 | 42.04 | 14.696 | 0.079103 | 0.021034
1007 | 42.05 | 14.696 | 0.079101 | 10.107 | 0.021039 |  | 1007 | 10.107 | 42.05 | 14.696 | 0.079101 | 0.021039
1008 | 42.06 | 14.696 | 0.0791 | 10.109 | 0.021043 |  | 1008 | 10.109 | 42.06 | 14.696 | 0.0791 | 0.021043
1009 | 42.07 | 14.696 | 0.079098 | 10.112 | 0.021048 |  | 1009 | 10.112 | 42.07 | 14.696 | 0.079098 | 0.021048
1010 | 42.08 | 14.696 | 0.079096 | 10.114 | 0.021053 |  | 1010 | 10.114 | 42.08 | 14.696 | 0.079096 | 0.021053
1011 | 42.09 | 14.696 | 0.079095 | 10.116 | 0.021058 |  | 1011 | 10.116 | 42.09 | 14.696 | 0.079095 | 0.021058
1012 | 42.1 | 14.696 | 0.079093 | 10.119 | 0.021063 |  | 1012 | 10.119 | 42.1 | 14.696 | 0.079093 | 0.021063
1013 | 42.11 | 14.696 | 0.079092 | 10.121 | 0.021067 |  | 1013 | 10.121 | 42.11 | 14.696 | 0.079092 | 0.021067
1014 | 42.12 | 14.696 | 0.07909 | 10.124 | 0.021072 |  | 1014 | 10.124 | 42.12 | 14.696 | 0.07909 | 0.021072
1015 | 42.13 | 14.696 | 0.079089 | 10.126 | 0.021077 |  | 1015 | 10.126 | 42.13 | 14.696 | 0.079089 | 0.021077
1016 | 42.14 | 14.696 | 0.079087 | 10.128 | 0.021082 |  | 1016 | 10.128 | 42.14 | 14.696 | 0.079087 | 0.021082
1017 | 42.15 | 14.696 | 0.079085 | 10.131 | 0.021087 |  | 1017 | 10.131 | 42.15 | 14.696 | 0.079085 | 0.021087
1018 | 42.16 | 14.696 | 0.079084 | 10.133 | 0.021091 |  | 1018 | 10.133 | 42.16 | 14.696 | 0.079084 | 0.021091
1019 | 42.17 | 14.696 | 0.079082 | 10.136 | 0.021096 |  | 1019 | 10.136 | 42.17 | 14.696 | 0.079082 | 0.021096
1020 | 42.18 | 14.696 | 0.079081 | 10.138 | 0.021101 |  | 1020 | 10.138 | 42.18 | 14.696 | 0.079081 | 0.021101
1021 | 42.19 | 14.696 | 0.079079 | 10.14 | 0.021106 |  | 1021 | 10.14 | 42.19 | 14.696 | 0.079079 | 0.021106
1022 | 42.2 | 14.696 | 0.079078 | 10.143 | 0.02111 |  | 1022 | 10.143 | 42.2 | 14.696 | 0.079078 | 0.02111
1023 | 42.21 | 14.696 | 0.079076 | 10.145 | 0.021115 |  | 1023 | 10.145 | 42.21 | 14.696 | 0.079076 | 0.021115
1024 | 42.22 | 14.696 | 0.079074 | 10.148 | 0.02112 |  | 1024 | 10.148 | 42.22 | 14.696 | 0.079074 | 0.02112
1025 | 42.23 | 14.696 | 0.079073 | 10.15 | 0.021125 |  | 1025 | 10.15 | 42.23 | 14.696 | 0.079073 | 0.021125
1026 | 42.24 | 14.696 | 0.079071 | 10.152 | 0.02113 |  | 1026 | 10.152 | 42.24 | 14.696 | 0.079071 | 0.02113
1027 | 42.25 | 14.696 | 0.07907 | 10.155 | 0.021134 |  | 1027 | 10.155 | 42.25 | 14.696 | 0.07907 | 0.021134
1028 | 42.26 | 14.696 | 0.079068 | 10.157 | 0.021139 |  | 1028 | 10.157 | 42.26 | 14.696 | 0.079068 | 0.021139
1029 | 42.27 | 14.696 | 0.079066 | 10.16 | 0.021144 |  | 1029 | 10.16 | 42.27 | 14.696 | 0.079066 | 0.021144
1030 | 42.28 | 14.696 | 0.079065 | 10.162 | 0.021149 |  | 1030 | 10.162 | 42.28 | 14.696 | 0.079065 | 0.021149
1031 | 42.29 | 14.696 | 0.079063 | 10.164 | 0.021154 |  | 1031 | 10.164 | 42.29 | 14.696 | 0.079063 | 0.021154
1032 | 42.3 | 14.696 | 0.079062 | 10.167 | 0.021158 |  | 1032 | 10.167 | 42.3 | 14.696 | 0.079062 | 0.021158
1033 | 42.31 | 14.696 | 0.07906 | 10.169 | 0.021163 |  | 1033 | 10.169 | 42.31 | 14.696 | 0.07906 | 0.021163
1034 | 42.32 | 14.696 | 0.079059 | 10.172 | 0.021168 |  | 1034 | 10.172 | 42.32 | 14.696 | 0.079059 | 0.021168
1035 | 42.33 | 14.696 | 0.079057 | 10.174 | 0.021173 |  | 1035 | 10.174 | 42.33 | 14.696 | 0.079057 | 0.021173
1036 | 42.34 | 14.696 | 0.079055 | 10.176 | 0.021178 |  | 1036 | 10.176 | 42.34 | 14.696 | 0.079055 | 0.021178
1037 | 42.35 | 14.696 | 0.079054 | 10.179 | 0.021182 |  | 1037 | 10.179 | 42.35 | 14.696 | 0.079054 | 0.021182
1038 | 42.36 | 14.696 | 0.079052 | 10.181 | 0.021187 |  | 1038 | 10.181 | 42.36 | 14.696 | 0.079052 | 0.021187
1039 | 42.37 | 14.696 | 0.079051 | 10.184 | 0.021192 |  | 1039 | 10.184 | 42.37 | 14.696 | 0.079051 | 0.021192
1040 | 42.38 | 14.696 | 0.079049 | 10.186 | 0.021197 |  | 1040 | 10.186 | 42.38 | 14.696 | 0.079049 | 0.021197
1041 | 42.39 | 14.696 | 0.079047 | 10.188 | 0.021201 |  | 1041 | 10.188 | 42.39 | 14.696 | 0.079047 | 0.021201
1042 | 42.4 | 14.696 | 0.079046 | 10.191 | 0.021206 |  | 1042 | 10.191 | 42.4 | 14.696 | 0.079046 | 0.021206
1043 | 42.41 | 14.696 | 0.079044 | 10.193 | 0.021211 |  | 1043 | 10.193 | 42.41 | 14.696 | 0.079044 | 0.021211
1044 | 42.42 | 14.696 | 0.079043 | 10.196 | 0.021216 |  | 1044 | 10.196 | 42.42 | 14.696 | 0.079043 | 0.021216
1045 | 42.43 | 14.696 | 0.079041 | 10.198 | 0.021221 |  | 1045 | 10.198 | 42.43 | 14.696 | 0.079041 | 0.021221
1046 | 42.44 | 14.696 | 0.07904 | 10.2 | 0.021225 |  | 1046 | 10.2 | 42.44 | 14.696 | 0.07904 | 0.021225
1047 | 42.45 | 14.696 | 0.079038 | 10.203 | 0.02123 |  | 1047 | 10.203 | 42.45 | 14.696 | 0.079038 | 0.02123
1048 | 42.46 | 14.696 | 0.079036 | 10.205 | 0.021235 |  | 1048 | 10.205 | 42.46 | 14.696 | 0.079036 | 0.021235
1049 | 42.47 | 14.696 | 0.079035 | 10.208 | 0.02124 |  | 1049 | 10.208 | 42.47 | 14.696 | 0.079035 | 0.02124
1050 | 42.48 | 14.696 | 0.079033 | 10.21 | 0.021245 |  | 1050 | 10.21 | 42.48 | 14.696 | 0.079033 | 0.021245
1051 | 42.49 | 14.696 | 0.079032 | 10.212 | 0.021249 |  | 1051 | 10.212 | 42.49 | 14.696 | 0.079032 | 0.021249
1052 | 42.5 | 14.696 | 0.07903 | 10.215 | 0.021254 |  | 1052 | 10.215 | 42.5 | 14.696 | 0.07903 | 0.021254
1053 | 42.51 | 14.696 | 0.079029 | 10.217 | 0.021259 |  | 1053 | 10.217 | 42.51 | 14.696 | 0.079029 | 0.021259
1054 | 42.52 | 14.696 | 0.079027 | 10.22 | 0.021264 |  | 1054 | 10.22 | 42.52 | 14.696 | 0.079027 | 0.021264
1055 | 42.53 | 14.696 | 0.079025 | 10.222 | 0.021268 |  | 1055 | 10.222 | 42.53 | 14.696 | 0.079025 | 0.021268
1056 | 42.54 | 14.696 | 0.079024 | 10.225 | 0.021273 |  | 1056 | 10.225 | 42.54 | 14.696 | 0.079024 | 0.021273
1057 | 42.55 | 14.696 | 0.079022 | 10.227 | 0.021278 |  | 1057 | 10.227 | 42.55 | 14.696 | 0.079022 | 0.021278
1058 | 42.56 | 14.696 | 0.079021 | 10.229 | 0.021283 |  | 1058 | 10.229 | 42.56 | 14.696 | 0.079021 | 0.021283
1059 | 42.57 | 14.696 | 0.079019 | 10.232 | 0.021288 |  | 1059 | 10.232 | 42.57 | 14.696 | 0.079019 | 0.021288
1060 | 42.58 | 14.696 | 0.079017 | 10.234 | 0.021292 |  | 1060 | 10.234 | 42.58 | 14.696 | 0.079017 | 0.021292
1061 | 42.59 | 14.696 | 0.079016 | 10.237 | 0.021297 |  | 1061 | 10.237 | 42.59 | 14.696 | 0.079016 | 0.021297
1062 | 42.6 | 14.696 | 0.079014 | 10.239 | 0.021302 |  | 1062 | 10.239 | 42.6 | 14.696 | 0.079014 | 0.021302
1063 | 42.61 | 14.696 | 0.079013 | 10.241 | 0.021307 |  | 1063 | 10.241 | 42.61 | 14.696 | 0.079013 | 0.021307
1064 | 42.62 | 14.696 | 0.079011 | 10.244 | 0.021312 |  | 1064 | 10.244 | 42.62 | 14.696 | 0.079011 | 0.021312
1065 | 42.63 | 14.696 | 0.07901 | 10.246 | 0.021316 |  | 1065 | 10.246 | 42.63 | 14.696 | 0.07901 | 0.021316
1066 | 42.64 | 14.696 | 0.079008 | 10.249 | 0.021321 |  | 1066 | 10.249 | 42.64 | 14.696 | 0.079008 | 0.021321
1067 | 42.65 | 14.696 | 0.079006 | 10.251 | 0.021326 |  | 1067 | 10.251 | 42.65 | 14.696 | 0.079006 | 0.021326
1068 | 42.66 | 14.696 | 0.079005 | 10.253 | 0.021331 |  | 1068 | 10.253 | 42.66 | 14.696 | 0.079005 | 0.021331
1069 | 42.67 | 14.696 | 0.079003 | 10.256 | 0.021335 |  | 1069 | 10.256 | 42.67 | 14.696 | 0.079003 | 0.021335
1070 | 42.68 | 14.696 | 0.079002 | 10.258 | 0.02134 |  | 1070 | 10.258 | 42.68 | 14.696 | 0.079002 | 0.02134
1071 | 42.69 | 14.696 | 0.079 | 10.261 | 0.021345 |  | 1071 | 10.261 | 42.69 | 14.696 | 0.079 | 0.021345
1072 | 42.7 | 14.696 | 0.078999 | 10.263 | 0.02135 |  | 1072 | 10.263 | 42.7 | 14.696 | 0.078999 | 0.02135
1073 | 42.71 | 14.696 | 0.078997 | 10.265 | 0.021355 |  | 1073 | 10.265 | 42.71 | 14.696 | 0.078997 | 0.021355
1074 | 42.72 | 14.696 | 0.078995 | 10.268 | 0.021359 |  | 1074 | 10.268 | 42.72 | 14.696 | 0.078995 | 0.021359
1075 | 42.73 | 14.696 | 0.078994 | 10.27 | 0.021364 |  | 1075 | 10.27 | 42.73 | 14.696 | 0.078994 | 0.021364
1076 | 42.74 | 14.696 | 0.078992 | 10.273 | 0.021369 |  | 1076 | 10.273 | 42.74 | 14.696 | 0.078992 | 0.021369
1077 | 42.75 | 14.696 | 0.078991 | 10.275 | 0.021374 |  | 1077 | 10.275 | 42.75 | 14.696 | 0.078991 | 0.021374
1078 | 42.76 | 14.696 | 0.078989 | 10.277 | 0.021379 |  | 1078 | 10.277 | 42.76 | 14.696 | 0.078989 | 0.021379
1079 | 42.77 | 14.696 | 0.078988 | 10.28 | 0.021383 |  | 1079 | 10.28 | 42.77 | 14.696 | 0.078988 | 0.021383
1080 | 42.78 | 14.696 | 0.078986 | 10.282 | 0.021388 |  | 1080 | 10.282 | 42.78 | 14.696 | 0.078986 | 0.021388
1081 | 42.79 | 14.696 | 0.078984 | 10.285 | 0.021393 |  | 1081 | 10.285 | 42.79 | 14.696 | 0.078984 | 0.021393
1082 | 42.8 | 14.696 | 0.078983 | 10.287 | 0.021398 |  | 1082 | 10.287 | 42.8 | 14.696 | 0.078983 | 0.021398
1083 | 42.81 | 14.696 | 0.078981 | 10.289 | 0.021402 |  | 1083 | 10.289 | 42.81 | 14.696 | 0.078981 | 0.021402
1084 | 42.82 | 14.696 | 0.07898 | 10.292 | 0.021407 |  | 1084 | 10.292 | 42.82 | 14.696 | 0.07898 | 0.021407
1085 | 42.83 | 14.696 | 0.078978 | 10.294 | 0.021412 |  | 1085 | 10.294 | 42.83 | 14.696 | 0.078978 | 0.021412
1086 | 42.84 | 14.696 | 0.078976 | 10.297 | 0.021417 |  | 1086 | 10.297 | 42.84 | 14.696 | 0.078976 | 0.021417
1087 | 42.85 | 14.696 | 0.078975 | 10.299 | 0.021422 |  | 1087 | 10.299 | 42.85 | 14.696 | 0.078975 | 0.021422
1088 | 42.86 | 14.696 | 0.078973 | 10.301 | 0.021426 |  | 1088 | 10.301 | 42.86 | 14.696 | 0.078973 | 0.021426
1089 | 42.87 | 14.696 | 0.078972 | 10.304 | 0.021431 |  | 1089 | 10.304 | 42.87 | 14.696 | 0.078972 | 0.021431
1090 | 42.88 | 14.696 | 0.07897 | 10.306 | 0.021436 |  | 1090 | 10.306 | 42.88 | 14.696 | 0.07897 | 0.021436
1091 | 42.89 | 14.696 | 0.078969 | 10.309 | 0.021441 |  | 1091 | 10.309 | 42.89 | 14.696 | 0.078969 | 0.021441
1092 | 42.9 | 14.696 | 0.078967 | 10.311 | 0.021446 |  | 1092 | 10.311 | 42.9 | 14.696 | 0.078967 | 0.021446
1093 | 42.91 | 14.696 | 0.078965 | 10.313 | 0.02145 |  | 1093 | 10.313 | 42.91 | 14.696 | 0.078965 | 0.02145
1094 | 42.92 | 14.696 | 0.078964 | 10.316 | 0.021455 |  | 1094 | 10.316 | 42.92 | 14.696 | 0.078964 | 0.021455
1095 | 42.93 | 14.696 | 0.078962 | 10.318 | 0.02146 |  | 1095 | 10.318 | 42.93 | 14.696 | 0.078962 | 0.02146
1096 | 42.94 | 14.696 | 0.078961 | 10.321 | 0.021465 |  | 1096 | 10.321 | 42.94 | 14.696 | 0.078961 | 0.021465
1097 | 42.95 | 14.696 | 0.078959 | 10.323 | 0.021469 |  | 1097 | 10.323 | 42.95 | 14.696 | 0.078959 | 0.021469
1098 | 42.96 | 14.696 | 0.078958 | 10.325 | 0.021474 |  | 1098 | 10.325 | 42.96 | 14.696 | 0.078958 | 0.021474
1099 | 42.97 | 14.696 | 0.078956 | 10.328 | 0.021479 |  | 1099 | 10.328 | 42.97 | 14.696 | 0.078956 | 0.021479
1100 | 42.98 | 14.696 | 0.078954 | 10.33 | 0.021484 |  | 1100 | 10.33 | 42.98 | 14.696 | 0.078954 | 0.021484
1101 | 42.99 | 14.696 | 0.078953 | 10.333 | 0.021489 |  | 1101 | 10.333 | 42.99 | 14.696 | 0.078953 | 0.021489
1102 | 43 | 14.696 | 0.078951 | 10.335 | 0.021493 |  | 1102 | 10.335 | 43 | 14.696 | 0.078951 | 0.021493
1103 | 43.01 | 14.696 | 0.07895 | 10.337 | 0.021498 |  | 1103 | 10.337 | 43.01 | 14.696 | 0.07895 | 0.021498
1104 | 43.02 | 14.696 | 0.078948 | 10.34 | 0.021503 |  | 1104 | 10.34 | 43.02 | 14.696 | 0.078948 | 0.021503
1105 | 43.03 | 14.696 | 0.078947 | 10.342 | 0.021508 |  | 1105 | 10.342 | 43.03 | 14.696 | 0.078947 | 0.021508
1106 | 43.04 | 14.696 | 0.078945 | 10.345 | 0.021512 |  | 1106 | 10.345 | 43.04 | 14.696 | 0.078945 | 0.021512
1107 | 43.05 | 14.696 | 0.078943 | 10.347 | 0.021517 |  | 1107 | 10.347 | 43.05 | 14.696 | 0.078943 | 0.021517
1108 | 43.06 | 14.696 | 0.078942 | 10.35 | 0.021522 |  | 1108 | 10.35 | 43.06 | 14.696 | 0.078942 | 0.021522
1109 | 43.07 | 14.696 | 0.07894 | 10.352 | 0.021527 |  | 1109 | 10.352 | 43.07 | 14.696 | 0.07894 | 0.021527
1110 | 43.08 | 14.696 | 0.078939 | 10.354 | 0.021532 |  | 1110 | 10.354 | 43.08 | 14.696 | 0.078939 | 0.021532
1111 | 43.09 | 14.696 | 0.078937 | 10.357 | 0.021536 |  | 1111 | 10.357 | 43.09 | 14.696 | 0.078937 | 0.021536
1112 | 43.1 | 14.696 | 0.078935 | 10.359 | 0.021541 |  | 1112 | 10.359 | 43.1 | 14.696 | 0.078935 | 0.021541
1113 | 43.11 | 14.696 | 0.078934 | 10.362 | 0.021546 |  | 1113 | 10.362 | 43.11 | 14.696 | 0.078934 | 0.021546
1114 | 43.12 | 14.696 | 0.078932 | 10.364 | 0.021551 |  | 1114 | 10.364 | 43.12 | 14.696 | 0.078932 | 0.021551
1115 | 43.13 | 14.696 | 0.078931 | 10.366 | 0.021556 |  | 1115 | 10.366 | 43.13 | 14.696 | 0.078931 | 0.021556
1116 | 43.14 | 14.696 | 0.078929 | 10.369 | 0.02156 |  | 1116 | 10.369 | 43.14 | 14.696 | 0.078929 | 0.02156
1117 | 43.15 | 14.696 | 0.078928 | 10.371 | 0.021565 |  | 1117 | 10.371 | 43.15 | 14.696 | 0.078928 | 0.021565
1118 | 43.16 | 14.696 | 0.078926 | 10.374 | 0.02157 |  | 1118 | 10.374 | 43.16 | 14.696 | 0.078926 | 0.02157
1119 | 43.17 | 14.696 | 0.078924 | 10.376 | 0.021575 |  | 1119 | 10.376 | 43.17 | 14.696 | 0.078924 | 0.021575
1120 | 43.18 | 14.696 | 0.078923 | 10.378 | 0.021579 |  | 1120 | 10.378 | 43.18 | 14.696 | 0.078923 | 0.021579
1121 | 43.19 | 14.696 | 0.078921 | 10.381 | 0.021584 |  | 1121 | 10.381 | 43.19 | 14.696 | 0.078921 | 0.021584
1122 | 43.2 | 14.696 | 0.07892 | 10.383 | 0.021589 |  | 1122 | 10.383 | 43.2 | 14.696 | 0.07892 | 0.021589
1123 | 43.21 | 14.696 | 0.078918 | 10.386 | 0.021594 |  | 1123 | 10.386 | 43.21 | 14.696 | 0.078918 | 0.021594
1124 | 43.22 | 14.696 | 0.078917 | 10.388 | 0.021599 |  | 1124 | 10.388 | 43.22 | 14.696 | 0.078917 | 0.021599
1125 | 43.23 | 14.696 | 0.078915 | 10.39 | 0.021603 |  | 1125 | 10.39 | 43.23 | 14.696 | 0.078915 | 0.021603
1126 | 43.24 | 14.696 | 0.078913 | 10.393 | 0.021608 |  | 1126 | 10.393 | 43.24 | 14.696 | 0.078913 | 0.021608
1127 | 43.25 | 14.696 | 0.078912 | 10.395 | 0.021613 |  | 1127 | 10.395 | 43.25 | 14.696 | 0.078912 | 0.021613
1128 | 43.26 | 14.696 | 0.07891 | 10.398 | 0.021618 |  | 1128 | 10.398 | 43.26 | 14.696 | 0.07891 | 0.021618
1129 | 43.27 | 14.696 | 0.078909 | 10.4 | 0.021622 |  | 1129 | 10.4 | 43.27 | 14.696 | 0.078909 | 0.021622
1130 | 43.28 | 14.696 | 0.078907 | 10.402 | 0.021627 |  | 1130 | 10.402 | 43.28 | 14.696 | 0.078907 | 0.021627
1131 | 43.29 | 14.696 | 0.078906 | 10.405 | 0.021632 |  | 1131 | 10.405 | 43.29 | 14.696 | 0.078906 | 0.021632
1132 | 43.3 | 14.696 | 0.078904 | 10.407 | 0.021637 |  | 1132 | 10.407 | 43.3 | 14.696 | 0.078904 | 0.021637
1133 | 43.31 | 14.696 | 0.078902 | 10.41 | 0.021642 |  | 1133 | 10.41 | 43.31 | 14.696 | 0.078902 | 0.021642
1134 | 43.32 | 14.696 | 0.078901 | 10.412 | 0.021646 |  | 1134 | 10.412 | 43.32 | 14.696 | 0.078901 | 0.021646
1135 | 43.33 | 14.696 | 0.078899 | 10.414 | 0.021651 |  | 1135 | 10.414 | 43.33 | 14.696 | 0.078899 | 0.021651
1136 | 43.34 | 14.696 | 0.078898 | 10.417 | 0.021656 |  | 1136 | 10.417 | 43.34 | 14.696 | 0.078898 | 0.021656
1137 | 43.35 | 14.696 | 0.078896 | 10.419 | 0.021661 |  | 1137 | 10.419 | 43.35 | 14.696 | 0.078896 | 0.021661
1138 | 43.36 | 14.696 | 0.078895 | 10.422 | 0.021665 |  | 1138 | 10.422 | 43.36 | 14.696 | 0.078895 | 0.021665
1139 | 43.37 | 14.696 | 0.078893 | 10.424 | 0.02167 |  | 1139 | 10.424 | 43.37 | 14.696 | 0.078893 | 0.02167
1140 | 43.38 | 14.696 | 0.078891 | 10.426 | 0.021675 |  | 1140 | 10.426 | 43.38 | 14.696 | 0.078891 | 0.021675
1141 | 43.39 | 14.696 | 0.07889 | 10.429 | 0.02168 |  | 1141 | 10.429 | 43.39 | 14.696 | 0.07889 | 0.02168
1142 | 43.4 | 14.696 | 0.078888 | 10.431 | 0.021685 |  | 1142 | 10.431 | 43.4 | 14.696 | 0.078888 | 0.021685
1143 | 43.41 | 14.696 | 0.078887 | 10.434 | 0.021689 |  | 1143 | 10.434 | 43.41 | 14.696 | 0.078887 | 0.021689
1144 | 43.42 | 14.696 | 0.078885 | 10.436 | 0.021694 |  | 1144 | 10.436 | 43.42 | 14.696 | 0.078885 | 0.021694
1145 | 43.43 | 14.696 | 0.078884 | 10.438 | 0.021699 |  | 1145 | 10.438 | 43.43 | 14.696 | 0.078884 | 0.021699
1146 | 43.44 | 14.696 | 0.078882 | 10.441 | 0.021704 |  | 1146 | 10.441 | 43.44 | 14.696 | 0.078882 | 0.021704
1147 | 43.45 | 14.696 | 0.07888 | 10.443 | 0.021708 |  | 1147 | 10.443 | 43.45 | 14.696 | 0.07888 | 0.021708
1148 | 43.46 | 14.696 | 0.078879 | 10.446 | 0.021713 |  | 1148 | 10.446 | 43.46 | 14.696 | 0.078879 | 0.021713
1149 | 43.47 | 14.696 | 0.078877 | 10.448 | 0.021718 |  | 1149 | 10.448 | 43.47 | 14.696 | 0.078877 | 0.021718
1150 | 43.48 | 14.696 | 0.078876 | 10.45 | 0.021723 |  | 1150 | 10.45 | 43.48 | 14.696 | 0.078876 | 0.021723
1151 | 43.49 | 14.696 | 0.078874 | 10.453 | 0.021728 |  | 1151 | 10.453 | 43.49 | 14.696 | 0.078874 | 0.021728
1152 | 43.5 | 14.696 | 0.078873 | 10.455 | 0.021732 |  | 1152 | 10.455 | 43.5 | 14.696 | 0.078873 | 0.021732
1153 | 43.51 | 14.696 | 0.078871 | 10.458 | 0.021737 |  | 1153 | 10.458 | 43.51 | 14.696 | 0.078871 | 0.021737
1154 | 43.52 | 14.696 | 0.078869 | 10.46 | 0.021742 |  | 1154 | 10.46 | 43.52 | 14.696 | 0.078869 | 0.021742
1155 | 43.53 | 14.696 | 0.078868 | 10.462 | 0.021747 |  | 1155 | 10.462 | 43.53 | 14.696 | 0.078868 | 0.021747
1156 | 43.54 | 14.696 | 0.078866 | 10.465 | 0.021751 |  | 1156 | 10.465 | 43.54 | 14.696 | 0.078866 | 0.021751
1157 | 43.55 | 14.696 | 0.078865 | 10.467 | 0.021756 |  | 1157 | 10.467 | 43.55 | 14.696 | 0.078865 | 0.021756
1158 | 43.56 | 14.696 | 0.078863 | 10.47 | 0.021761 |  | 1158 | 10.47 | 43.56 | 14.696 | 0.078863 | 0.021761
1159 | 43.57 | 14.696 | 0.078862 | 10.472 | 0.021766 |  | 1159 | 10.472 | 43.57 | 14.696 | 0.078862 | 0.021766
1160 | 43.58 | 14.696 | 0.07886 | 10.475 | 0.021771 |  | 1160 | 10.475 | 43.58 | 14.696 | 0.07886 | 0.021771
1161 | 43.59 | 14.696 | 0.078858 | 10.477 | 0.021775 |  | 1161 | 10.477 | 43.59 | 14.696 | 0.078858 | 0.021775
1162 | 43.6 | 14.696 | 0.078857 | 10.479 | 0.02178 |  | 1162 | 10.479 | 43.6 | 14.696 | 0.078857 | 0.02178
1163 | 43.61 | 14.696 | 0.078855 | 10.482 | 0.021785 |  | 1163 | 10.482 | 43.61 | 14.696 | 0.078855 | 0.021785
1164 | 43.62 | 14.696 | 0.078854 | 10.484 | 0.02179 |  | 1164 | 10.484 | 43.62 | 14.696 | 0.078854 | 0.02179
1165 | 43.63 | 14.696 | 0.078852 | 10.487 | 0.021794 |  | 1165 | 10.487 | 43.63 | 14.696 | 0.078852 | 0.021794
1166 | 43.64 | 14.696 | 0.078851 | 10.489 | 0.021799 |  | 1166 | 10.489 | 43.64 | 14.696 | 0.078851 | 0.021799
1167 | 43.65 | 14.696 | 0.078849 | 10.491 | 0.021804 |  | 1167 | 10.491 | 43.65 | 14.696 | 0.078849 | 0.021804
1168 | 43.66 | 14.696 | 0.078847 | 10.494 | 0.021809 |  | 1168 | 10.494 | 43.66 | 14.696 | 0.078847 | 0.021809
1169 | 43.67 | 14.696 | 0.078846 | 10.496 | 0.021814 |  | 1169 | 10.496 | 43.67 | 14.696 | 0.078846 | 0.021814
1170 | 43.68 | 14.696 | 0.078844 | 10.499 | 0.021818 |  | 1170 | 10.499 | 43.68 | 14.696 | 0.078844 | 0.021818
1171 | 43.69 | 14.696 | 0.078843 | 10.501 | 0.021823 |  | 1171 | 10.501 | 43.69 | 14.696 | 0.078843 | 0.021823
1172 | 43.7 | 14.696 | 0.078841 | 10.503 | 0.021828 |  | 1172 | 10.503 | 43.7 | 14.696 | 0.078841 | 0.021828
1173 | 43.71 | 14.696 | 0.07884 | 10.506 | 0.021833 |  | 1173 | 10.506 | 43.71 | 14.696 | 0.07884 | 0.021833
1174 | 43.72 | 14.696 | 0.078838 | 10.508 | 0.021837 |  | 1174 | 10.508 | 43.72 | 14.696 | 0.078838 | 0.021837
1175 | 43.73 | 14.696 | 0.078836 | 10.511 | 0.021842 |  | 1175 | 10.511 | 43.73 | 14.696 | 0.078836 | 0.021842
1176 | 43.74 | 14.696 | 0.078835 | 10.513 | 0.021847 |  | 1176 | 10.513 | 43.74 | 14.696 | 0.078835 | 0.021847
1177 | 43.75 | 14.696 | 0.078833 | 10.515 | 0.021852 |  | 1177 | 10.515 | 43.75 | 14.696 | 0.078833 | 0.021852
1178 | 43.76 | 14.696 | 0.078832 | 10.518 | 0.021857 |  | 1178 | 10.518 | 43.76 | 14.696 | 0.078832 | 0.021857
1179 | 43.77 | 14.696 | 0.07883 | 10.52 | 0.021861 |  | 1179 | 10.52 | 43.77 | 14.696 | 0.07883 | 0.021861
1180 | 43.78 | 14.696 | 0.078829 | 10.523 | 0.021866 |  | 1180 | 10.523 | 43.78 | 14.696 | 0.078829 | 0.021866
1181 | 43.79 | 14.696 | 0.078827 | 10.525 | 0.021871 |  | 1181 | 10.525 | 43.79 | 14.696 | 0.078827 | 0.021871
1182 | 43.8 | 14.696 | 0.078825 | 10.527 | 0.021876 |  | 1182 | 10.527 | 43.8 | 14.696 | 0.078825 | 0.021876
1183 | 43.81 | 14.696 | 0.078824 | 10.53 | 0.02188 |  | 1183 | 10.53 | 43.81 | 14.696 | 0.078824 | 0.02188
1184 | 43.82 | 14.696 | 0.078822 | 10.532 | 0.021885 |  | 1184 | 10.532 | 43.82 | 14.696 | 0.078822 | 0.021885
1185 | 43.83 | 14.696 | 0.078821 | 10.535 | 0.02189 |  | 1185 | 10.535 | 43.83 | 14.696 | 0.078821 | 0.02189
1186 | 43.84 | 14.696 | 0.078819 | 10.537 | 0.021895 |  | 1186 | 10.537 | 43.84 | 14.696 | 0.078819 | 0.021895
1187 | 43.85 | 14.696 | 0.078818 | 10.539 | 0.021899 |  | 1187 | 10.539 | 43.85 | 14.696 | 0.078818 | 0.021899
1188 | 43.86 | 14.696 | 0.078816 | 10.542 | 0.021904 |  | 1188 | 10.542 | 43.86 | 14.696 | 0.078816 | 0.021904
1189 | 43.87 | 14.696 | 0.078814 | 10.544 | 0.021909 |  | 1189 | 10.544 | 43.87 | 14.696 | 0.078814 | 0.021909
1190 | 43.88 | 14.696 | 0.078813 | 10.547 | 0.021914 |  | 1190 | 10.547 | 43.88 | 14.696 | 0.078813 | 0.021914
1191 | 43.89 | 14.696 | 0.078811 | 10.549 | 0.021919 |  | 1191 | 10.549 | 43.89 | 14.696 | 0.078811 | 0.021919
1192 | 43.9 | 14.696 | 0.07881 | 10.551 | 0.021923 |  | 1192 | 10.551 | 43.9 | 14.696 | 0.07881 | 0.021923
1193 | 43.91 | 14.696 | 0.078808 | 10.554 | 0.021928 |  | 1193 | 10.554 | 43.91 | 14.696 | 0.078808 | 0.021928
1194 | 43.92 | 14.696 | 0.078807 | 10.556 | 0.021933 |  | 1194 | 10.556 | 43.92 | 14.696 | 0.078807 | 0.021933
1195 | 43.93 | 14.696 | 0.078805 | 10.559 | 0.021938 |  | 1195 | 10.559 | 43.93 | 14.696 | 0.078805 | 0.021938
1196 | 43.94 | 14.696 | 0.078803 | 10.561 | 0.021942 |  | 1196 | 10.561 | 43.94 | 14.696 | 0.078803 | 0.021942
1197 | 43.95 | 14.696 | 0.078802 | 10.563 | 0.021947 |  | 1197 | 10.563 | 43.95 | 14.696 | 0.078802 | 0.021947
1198 | 43.96 | 14.696 | 0.0788 | 10.566 | 0.021952 |  | 1198 | 10.566 | 43.96 | 14.696 | 0.0788 | 0.021952
1199 | 43.97 | 14.696 | 0.078799 | 10.568 | 0.021957 |  | 1199 | 10.568 | 43.97 | 14.696 | 0.078799 | 0.021957
1200 | 43.98 | 14.696 | 0.078797 | 10.571 | 0.021962 |  | 1200 | 10.571 | 43.98 | 14.696 | 0.078797 | 0.021962
1201 | 43.99 | 14.696 | 0.078796 | 10.573 | 0.021966 |  | 1201 | 10.573 | 43.99 | 14.696 | 0.078796 | 0.021966
1202 | 44 | 14.696 | 0.078794 | 10.575 | 0.021971 |  | 1202 | 10.575 | 44 | 14.696 | 0.078794 | 0.021971
1203 | 44.01 | 14.696 | 0.078792 | 10.578 | 0.021976 |  | 1203 | 10.578 | 44.01 | 14.696 | 0.078792 | 0.021976
1204 | 44.02 | 14.696 | 0.078791 | 10.58 | 0.021981 |  | 1204 | 10.58 | 44.02 | 14.696 | 0.078791 | 0.021981
1205 | 44.03 | 14.696 | 0.078789 | 10.583 | 0.021985 |  | 1205 | 10.583 | 44.03 | 14.696 | 0.078789 | 0.021985
1206 | 44.04 | 14.696 | 0.078788 | 10.585 | 0.02199 |  | 1206 | 10.585 | 44.04 | 14.696 | 0.078788 | 0.02199
1207 | 44.05 | 14.696 | 0.078786 | 10.587 | 0.021995 |  | 1207 | 10.587 | 44.05 | 14.696 | 0.078786 | 0.021995
1208 | 44.06 | 14.696 | 0.078785 | 10.59 | 0.022 |  | 1208 | 10.59 | 44.06 | 14.696 | 0.078785 | 0.022
1209 | 44.07 | 14.696 | 0.078783 | 10.592 | 0.022005 |  | 1209 | 10.592 | 44.07 | 14.696 | 0.078783 | 0.022005
1210 | 44.08 | 14.696 | 0.078781 | 10.595 | 0.022009 |  | 1210 | 10.595 | 44.08 | 14.696 | 0.078781 | 0.022009
1211 | 44.09 | 14.696 | 0.07878 | 10.597 | 0.022014 |  | 1211 | 10.597 | 44.09 | 14.696 | 0.07878 | 0.022014
1212 | 44.1 | 14.696 | 0.078778 | 10.6 | 0.022019 |  | 1212 | 10.6 | 44.1 | 14.696 | 0.078778 | 0.022019
1213 | 44.11 | 14.696 | 0.078777 | 10.602 | 0.022024 |  | 1213 | 10.602 | 44.11 | 14.696 | 0.078777 | 0.022024
1214 | 44.12 | 14.696 | 0.078775 | 10.604 | 0.022028 |  | 1214 | 10.604 | 44.12 | 14.696 | 0.078775 | 0.022028
1215 | 44.13 | 14.696 | 0.078774 | 10.607 | 0.022033 |  | 1215 | 10.607 | 44.13 | 14.696 | 0.078774 | 0.022033
1216 | 44.14 | 14.696 | 0.078772 | 10.609 | 0.022038 |  | 1216 | 10.609 | 44.14 | 14.696 | 0.078772 | 0.022038
1217 | 44.15 | 14.696 | 0.07877 | 10.612 | 0.022043 |  | 1217 | 10.612 | 44.15 | 14.696 | 0.07877 | 0.022043
1218 | 44.16 | 14.696 | 0.078769 | 10.614 | 0.022047 |  | 1218 | 10.614 | 44.16 | 14.696 | 0.078769 | 0.022047
1219 | 44.17 | 14.696 | 0.078767 | 10.616 | 0.022052 |  | 1219 | 10.616 | 44.17 | 14.696 | 0.078767 | 0.022052
1220 | 44.18 | 14.696 | 0.078766 | 10.619 | 0.022057 |  | 1220 | 10.619 | 44.18 | 14.696 | 0.078766 | 0.022057
1221 | 44.19 | 14.696 | 0.078764 | 10.621 | 0.022062 |  | 1221 | 10.621 | 44.19 | 14.696 | 0.078764 | 0.022062
1222 | 44.2 | 14.696 | 0.078763 | 10.624 | 0.022067 |  | 1222 | 10.624 | 44.2 | 14.696 | 0.078763 | 0.022067
1223 | 44.21 | 14.696 | 0.078761 | 10.626 | 0.022071 |  | 1223 | 10.626 | 44.21 | 14.696 | 0.078761 | 0.022071
1224 | 44.22 | 14.696 | 0.078759 | 10.628 | 0.022076 |  | 1224 | 10.628 | 44.22 | 14.696 | 0.078759 | 0.022076
1225 | 44.23 | 14.696 | 0.078758 | 10.631 | 0.022081 |  | 1225 | 10.631 | 44.23 | 14.696 | 0.078758 | 0.022081
1226 | 44.24 | 14.696 | 0.078756 | 10.633 | 0.022086 |  | 1226 | 10.633 | 44.24 | 14.696 | 0.078756 | 0.022086
1227 | 44.25 | 14.696 | 0.078755 | 10.636 | 0.02209 |  | 1227 | 10.636 | 44.25 | 14.696 | 0.078755 | 0.02209
1228 | 44.26 | 14.696 | 0.078753 | 10.638 | 0.022095 |  | 1228 | 10.638 | 44.26 | 14.696 | 0.078753 | 0.022095
1229 | 44.27 | 14.696 | 0.078752 | 10.64 | 0.0221 |  | 1229 | 10.64 | 44.27 | 14.696 | 0.078752 | 0.0221
1230 | 44.28 | 14.696 | 0.07875 | 10.643 | 0.022105 |  | 1230 | 10.643 | 44.28 | 14.696 | 0.07875 | 0.022105
1231 | 44.29 | 14.696 | 0.078748 | 10.645 | 0.022109 |  | 1231 | 10.645 | 44.29 | 14.696 | 0.078748 | 0.022109
1232 | 44.3 | 14.696 | 0.078747 | 10.648 | 0.022114 |  | 1232 | 10.648 | 44.3 | 14.696 | 0.078747 | 0.022114
1233 | 44.31 | 14.696 | 0.078745 | 10.65 | 0.022119 |  | 1233 | 10.65 | 44.31 | 14.696 | 0.078745 | 0.022119
1234 | 44.32 | 14.696 | 0.078744 | 10.652 | 0.022124 |  | 1234 | 10.652 | 44.32 | 14.696 | 0.078744 | 0.022124
1235 | 44.33 | 14.696 | 0.078742 | 10.655 | 0.022129 |  | 1235 | 10.655 | 44.33 | 14.696 | 0.078742 | 0.022129
1236 | 44.34 | 14.696 | 0.078741 | 10.657 | 0.022133 |  | 1236 | 10.657 | 44.34 | 14.696 | 0.078741 | 0.022133
1237 | 44.35 | 14.696 | 0.078739 | 10.66 | 0.022138 |  | 1237 | 10.66 | 44.35 | 14.696 | 0.078739 | 0.022138
1238 | 44.36 | 14.696 | 0.078738 | 10.662 | 0.022143 |  | 1238 | 10.662 | 44.36 | 14.696 | 0.078738 | 0.022143
1239 | 44.37 | 14.696 | 0.078736 | 10.664 | 0.022148 |  | 1239 | 10.664 | 44.37 | 14.696 | 0.078736 | 0.022148
1240 | 44.38 | 14.696 | 0.078734 | 10.667 | 0.022152 |  | 1240 | 10.667 | 44.38 | 14.696 | 0.078734 | 0.022152
1241 | 44.39 | 14.696 | 0.078733 | 10.669 | 0.022157 |  | 1241 | 10.669 | 44.39 | 14.696 | 0.078733 | 0.022157
1242 | 44.4 | 14.696 | 0.078731 | 10.672 | 0.022162 |  | 1242 | 10.672 | 44.4 | 14.696 | 0.078731 | 0.022162
1243 | 44.41 | 14.696 | 0.07873 | 10.674 | 0.022167 |  | 1243 | 10.674 | 44.41 | 14.696 | 0.07873 | 0.022167
1244 | 44.42 | 14.696 | 0.078728 | 10.676 | 0.022171 |  | 1244 | 10.676 | 44.42 | 14.696 | 0.078728 | 0.022171
1245 | 44.43 | 14.696 | 0.078727 | 10.679 | 0.022176 |  | 1245 | 10.679 | 44.43 | 14.696 | 0.078727 | 0.022176
1246 | 44.44 | 14.696 | 0.078725 | 10.681 | 0.022181 |  | 1246 | 10.681 | 44.44 | 14.696 | 0.078725 | 0.022181
1247 | 44.45 | 14.696 | 0.078723 | 10.684 | 0.022186 |  | 1247 | 10.684 | 44.45 | 14.696 | 0.078723 | 0.022186
1248 | 44.46 | 14.696 | 0.078722 | 10.686 | 0.022191 |  | 1248 | 10.686 | 44.46 | 14.696 | 0.078722 | 0.022191
1249 | 44.47 | 14.696 | 0.07872 | 10.688 | 0.022195 |  | 1249 | 10.688 | 44.47 | 14.696 | 0.07872 | 0.022195
1250 | 44.48 | 14.696 | 0.078719 | 10.691 | 0.0222 |  | 1250 | 10.691 | 44.48 | 14.696 | 0.078719 | 0.0222
1251 | 44.49 | 14.696 | 0.078717 | 10.693 | 0.022205 |  | 1251 | 10.693 | 44.49 | 14.696 | 0.078717 | 0.022205
1252 | 44.5 | 14.696 | 0.078716 | 10.696 | 0.02221 |  | 1252 | 10.696 | 44.5 | 14.696 | 0.078716 | 0.02221
1253 | 44.51 | 14.696 | 0.078714 | 10.698 | 0.022214 |  | 1253 | 10.698 | 44.51 | 14.696 | 0.078714 | 0.022214
1254 | 44.52 | 14.696 | 0.078712 | 10.7 | 0.022219 |  | 1254 | 10.7 | 44.52 | 14.696 | 0.078712 | 0.022219
1255 | 44.53 | 14.696 | 0.078711 | 10.703 | 0.022224 |  | 1255 | 10.703 | 44.53 | 14.696 | 0.078711 | 0.022224
1256 | 44.54 | 14.696 | 0.078709 | 10.705 | 0.022229 |  | 1256 | 10.705 | 44.54 | 14.696 | 0.078709 | 0.022229
1257 | 44.55 | 14.696 | 0.078708 | 10.708 | 0.022233 |  | 1257 | 10.708 | 44.55 | 14.696 | 0.078708 | 0.022233
1258 | 44.56 | 14.696 | 0.078706 | 10.71 | 0.022238 |  | 1258 | 10.71 | 44.56 | 14.696 | 0.078706 | 0.022238
1259 | 44.57 | 14.696 | 0.078705 | 10.712 | 0.022243 |  | 1259 | 10.712 | 44.57 | 14.696 | 0.078705 | 0.022243
1260 | 44.58 | 14.696 | 0.078703 | 10.715 | 0.022248 |  | 1260 | 10.715 | 44.58 | 14.696 | 0.078703 | 0.022248
1261 | 44.59 | 14.696 | 0.078701 | 10.717 | 0.022253 |  | 1261 | 10.717 | 44.59 | 14.696 | 0.078701 | 0.022253
1262 | 44.6 | 14.696 | 0.0787 | 10.72 | 0.022257 |  | 1262 | 10.72 | 44.6 | 14.696 | 0.0787 | 0.022257
1263 | 44.61 | 14.696 | 0.078698 | 10.722 | 0.022262 |  | 1263 | 10.722 | 44.61 | 14.696 | 0.078698 | 0.022262
1264 | 44.62 | 14.696 | 0.078697 | 10.725 | 0.022267 |  | 1264 | 10.725 | 44.62 | 14.696 | 0.078697 | 0.022267
1265 | 44.63 | 14.696 | 0.078695 | 10.727 | 0.022272 |  | 1265 | 10.727 | 44.63 | 14.696 | 0.078695 | 0.022272
1266 | 44.64 | 14.696 | 0.078694 | 10.729 | 0.022276 |  | 1266 | 10.729 | 44.64 | 14.696 | 0.078694 | 0.022276
1267 | 44.65 | 14.696 | 0.078692 | 10.732 | 0.022281 |  | 1267 | 10.732 | 44.65 | 14.696 | 0.078692 | 0.022281
1268 | 44.66 | 14.696 | 0.078691 | 10.734 | 0.022286 |  | 1268 | 10.734 | 44.66 | 14.696 | 0.078691 | 0.022286
1269 | 44.67 | 14.696 | 0.078689 | 10.737 | 0.022291 |  | 1269 | 10.737 | 44.67 | 14.696 | 0.078689 | 0.022291
1270 | 44.68 | 14.696 | 0.078687 | 10.739 | 0.022295 |  | 1270 | 10.739 | 44.68 | 14.696 | 0.078687 | 0.022295
1271 | 44.69 | 14.696 | 0.078686 | 10.741 | 0.0223 |  | 1271 | 10.741 | 44.69 | 14.696 | 0.078686 | 0.0223
1272 | 44.7 | 14.696 | 0.078684 | 10.744 | 0.022305 |  | 1272 | 10.744 | 44.7 | 14.696 | 0.078684 | 0.022305
1273 | 44.71 | 14.696 | 0.078683 | 10.746 | 0.02231 |  | 1273 | 10.746 | 44.71 | 14.696 | 0.078683 | 0.02231
1274 | 44.72 | 14.696 | 0.078681 | 10.749 | 0.022314 |  | 1274 | 10.749 | 44.72 | 14.696 | 0.078681 | 0.022314
1275 | 44.73 | 14.696 | 0.07868 | 10.751 | 0.022319 |  | 1275 | 10.751 | 44.73 | 14.696 | 0.07868 | 0.022319
1276 | 44.74 | 14.696 | 0.078678 | 10.753 | 0.022324 |  | 1276 | 10.753 | 44.74 | 14.696 | 0.078678 | 0.022324
1277 | 44.75 | 14.696 | 0.078676 | 10.756 | 0.022329 |  | 1277 | 10.756 | 44.75 | 14.696 | 0.078676 | 0.022329
1278 | 44.76 | 14.696 | 0.078675 | 10.758 | 0.022334 |  | 1278 | 10.758 | 44.76 | 14.696 | 0.078675 | 0.022334
1279 | 44.77 | 14.696 | 0.078673 | 10.761 | 0.022338 |  | 1279 | 10.761 | 44.77 | 14.696 | 0.078673 | 0.022338
1280 | 44.78 | 14.696 | 0.078672 | 10.763 | 0.022343 |  | 1280 | 10.763 | 44.78 | 14.696 | 0.078672 | 0.022343
1281 | 44.79 | 14.696 | 0.07867 | 10.765 | 0.022348 |  | 1281 | 10.765 | 44.79 | 14.696 | 0.07867 | 0.022348
1282 | 44.8 | 14.696 | 0.078669 | 10.768 | 0.022353 |  | 1282 | 10.768 | 44.8 | 14.696 | 0.078669 | 0.022353
1283 | 44.81 | 14.696 | 0.078667 | 10.77 | 0.022357 |  | 1283 | 10.77 | 44.81 | 14.696 | 0.078667 | 0.022357
1284 | 44.82 | 14.696 | 0.078665 | 10.773 | 0.022362 |  | 1284 | 10.773 | 44.82 | 14.696 | 0.078665 | 0.022362
1285 | 44.83 | 14.696 | 0.078664 | 10.775 | 0.022367 |  | 1285 | 10.775 | 44.83 | 14.696 | 0.078664 | 0.022367
1286 | 44.84 | 14.696 | 0.078662 | 10.777 | 0.022372 |  | 1286 | 10.777 | 44.84 | 14.696 | 0.078662 | 0.022372
1287 | 44.85 | 14.696 | 0.078661 | 10.78 | 0.022376 |  | 1287 | 10.78 | 44.85 | 14.696 | 0.078661 | 0.022376
1288 | 44.86 | 14.696 | 0.078659 | 10.782 | 0.022381 |  | 1288 | 10.782 | 44.86 | 14.696 | 0.078659 | 0.022381
1289 | 44.87 | 14.696 | 0.078658 | 10.785 | 0.022386 |  | 1289 | 10.785 | 44.87 | 14.696 | 0.078658 | 0.022386
1290 | 44.88 | 14.696 | 0.078656 | 10.787 | 0.022391 |  | 1290 | 10.787 | 44.88 | 14.696 | 0.078656 | 0.022391
1291 | 44.89 | 14.696 | 0.078655 | 10.789 | 0.022396 |  | 1291 | 10.789 | 44.89 | 14.696 | 0.078655 | 0.022396
1292 | 44.9 | 14.696 | 0.078653 | 10.792 | 0.0224 |  | 1292 | 10.792 | 44.9 | 14.696 | 0.078653 | 0.0224
1293 | 44.91 | 14.696 | 0.078651 | 10.794 | 0.022405 |  | 1293 | 10.794 | 44.91 | 14.696 | 0.078651 | 0.022405
1294 | 44.92 | 14.696 | 0.07865 | 10.797 | 0.02241 |  | 1294 | 10.797 | 44.92 | 14.696 | 0.07865 | 0.02241
1295 | 44.93 | 14.696 | 0.078648 | 10.799 | 0.022415 |  | 1295 | 10.799 | 44.93 | 14.696 | 0.078648 | 0.022415
1296 | 44.94 | 14.696 | 0.078647 | 10.801 | 0.022419 |  | 1296 | 10.801 | 44.94 | 14.696 | 0.078647 | 0.022419
1297 | 44.95 | 14.696 | 0.078645 | 10.804 | 0.022424 |  | 1297 | 10.804 | 44.95 | 14.696 | 0.078645 | 0.022424
1298 | 44.96 | 14.696 | 0.078644 | 10.806 | 0.022429 |  | 1298 | 10.806 | 44.96 | 14.696 | 0.078644 | 0.022429
1299 | 44.97 | 14.696 | 0.078642 | 10.809 | 0.022434 |  | 1299 | 10.809 | 44.97 | 14.696 | 0.078642 | 0.022434
1300 | 44.98 | 14.696 | 0.07864 | 10.811 | 0.022438 |  | 1300 | 10.811 | 44.98 | 14.696 | 0.07864 | 0.022438
1301 | 44.99 | 14.696 | 0.078639 | 10.813 | 0.022443 |  | 1301 | 10.813 | 44.99 | 14.696 | 0.078639 | 0.022443
1302 | 45 | 14.696 | 0.078637 | 10.816 | 0.022448 |  | 1302 | 10.816 | 45 | 14.696 | 0.078637 | 0.022448
1303 | 45.01 | 14.696 | 0.078636 | 10.818 | 0.022453 |  | 1303 | 10.818 | 45.01 | 14.696 | 0.078636 | 0.022453
1304 | 45.02 | 14.696 | 0.078634 | 10.821 | 0.022457 |  | 1304 | 10.821 | 45.02 | 14.696 | 0.078634 | 0.022457
1305 | 45.03 | 14.696 | 0.078633 | 10.823 | 0.022462 |  | 1305 | 10.823 | 45.03 | 14.696 | 0.078633 | 0.022462
1306 | 45.04 | 14.696 | 0.078631 | 10.825 | 0.022467 |  | 1306 | 10.825 | 45.04 | 14.696 | 0.078631 | 0.022467
1307 | 45.05 | 14.696 | 0.07863 | 10.828 | 0.022472 |  | 1307 | 10.828 | 45.05 | 14.696 | 0.07863 | 0.022472
1308 | 45.06 | 14.696 | 0.078628 | 10.83 | 0.022476 |  | 1308 | 10.83 | 45.06 | 14.696 | 0.078628 | 0.022476
1309 | 45.07 | 14.696 | 0.078626 | 10.833 | 0.022481 |  | 1309 | 10.833 | 45.07 | 14.696 | 0.078626 | 0.022481
1310 | 45.08 | 14.696 | 0.078625 | 10.835 | 0.022486 |  | 1310 | 10.835 | 45.08 | 14.696 | 0.078625 | 0.022486
1311 | 45.09 | 14.696 | 0.078623 | 10.838 | 0.022491 |  | 1311 | 10.838 | 45.09 | 14.696 | 0.078623 | 0.022491
1312 | 45.1 | 14.696 | 0.078622 | 10.84 | 0.022496 |  | 1312 | 10.84 | 45.1 | 14.696 | 0.078622 | 0.022496
1313 | 45.11 | 14.696 | 0.07862 | 10.842 | 0.0225 |  | 1313 | 10.842 | 45.11 | 14.696 | 0.07862 | 0.0225
1314 | 45.12 | 14.696 | 0.078619 | 10.845 | 0.022505 |  | 1314 | 10.845 | 45.12 | 14.696 | 0.078619 | 0.022505
1315 | 45.13 | 14.696 | 0.078617 | 10.847 | 0.02251 |  | 1315 | 10.847 | 45.13 | 14.696 | 0.078617 | 0.02251
1316 | 45.14 | 14.696 | 0.078615 | 10.85 | 0.022515 |  | 1316 | 10.85 | 45.14 | 14.696 | 0.078615 | 0.022515
1317 | 45.15 | 14.696 | 0.078614 | 10.852 | 0.022519 |  | 1317 | 10.852 | 45.15 | 14.696 | 0.078614 | 0.022519
1318 | 45.16 | 14.696 | 0.078612 | 10.854 | 0.022524 |  | 1318 | 10.854 | 45.16 | 14.696 | 0.078612 | 0.022524
1319 | 45.17 | 14.696 | 0.078611 | 10.857 | 0.022529 |  | 1319 | 10.857 | 45.17 | 14.696 | 0.078611 | 0.022529
1320 | 45.18 | 14.696 | 0.078609 | 10.859 | 0.022534 |  | 1320 | 10.859 | 45.18 | 14.696 | 0.078609 | 0.022534
1321 | 45.19 | 14.696 | 0.078608 | 10.862 | 0.022538 |  | 1321 | 10.862 | 45.19 | 14.696 | 0.078608 | 0.022538
1322 | 45.2 | 14.696 | 0.078606 | 10.864 | 0.022543 |  | 1322 | 10.864 | 45.2 | 14.696 | 0.078606 | 0.022543
1323 | 45.21 | 14.696 | 0.078605 | 10.866 | 0.022548 |  | 1323 | 10.866 | 45.21 | 14.696 | 0.078605 | 0.022548
1324 | 45.22 | 14.696 | 0.078603 | 10.869 | 0.022553 |  | 1324 | 10.869 | 45.22 | 14.696 | 0.078603 | 0.022553
1325 | 45.23 | 14.696 | 0.078601 | 10.871 | 0.022557 |  | 1325 | 10.871 | 45.23 | 14.696 | 0.078601 | 0.022557
1326 | 45.24 | 14.696 | 0.0786 | 10.874 | 0.022562 |  | 1326 | 10.874 | 45.24 | 14.696 | 0.0786 | 0.022562
1327 | 45.25 | 14.696 | 0.078598 | 10.876 | 0.022567 |  | 1327 | 10.876 | 45.25 | 14.696 | 0.078598 | 0.022567
1328 | 45.26 | 14.696 | 0.078597 | 10.878 | 0.022572 |  | 1328 | 10.878 | 45.26 | 14.696 | 0.078597 | 0.022572
1329 | 45.27 | 14.696 | 0.078595 | 10.881 | 0.022576 |  | 1329 | 10.881 | 45.27 | 14.696 | 0.078595 | 0.022576
1330 | 45.28 | 14.696 | 0.078594 | 10.883 | 0.022581 |  | 1330 | 10.883 | 45.28 | 14.696 | 0.078594 | 0.022581
1331 | 45.29 | 14.696 | 0.078592 | 10.886 | 0.022586 |  | 1331 | 10.886 | 45.29 | 14.696 | 0.078592 | 0.022586
1332 | 45.3 | 14.696 | 0.07859 | 10.888 | 0.022591 |  | 1332 | 10.888 | 45.3 | 14.696 | 0.07859 | 0.022591
1333 | 45.31 | 14.696 | 0.078589 | 10.89 | 0.022596 |  | 1333 | 10.89 | 45.31 | 14.696 | 0.078589 | 0.022596
1334 | 45.32 | 14.696 | 0.078587 | 10.893 | 0.0226 |  | 1334 | 10.893 | 45.32 | 14.696 | 0.078587 | 0.0226
1335 | 45.33 | 14.696 | 0.078586 | 10.895 | 0.022605 |  | 1335 | 10.895 | 45.33 | 14.696 | 0.078586 | 0.022605
1336 | 45.34 | 14.696 | 0.078584 | 10.898 | 0.02261 |  | 1336 | 10.898 | 45.34 | 14.696 | 0.078584 | 0.02261
1337 | 45.35 | 14.696 | 0.078583 | 10.9 | 0.022615 |  | 1337 | 10.9 | 45.35 | 14.696 | 0.078583 | 0.022615
1338 | 45.36 | 14.696 | 0.078581 | 10.902 | 0.022619 |  | 1338 | 10.902 | 45.36 | 14.696 | 0.078581 | 0.022619
1339 | 45.37 | 14.696 | 0.07858 | 10.905 | 0.022624 |  | 1339 | 10.905 | 45.37 | 14.696 | 0.07858 | 0.022624
1340 | 45.38 | 14.696 | 0.078578 | 10.907 | 0.022629 |  | 1340 | 10.907 | 45.38 | 14.696 | 0.078578 | 0.022629
1341 | 45.39 | 14.696 | 0.078576 | 10.91 | 0.022634 |  | 1341 | 10.91 | 45.39 | 14.696 | 0.078576 | 0.022634
1342 | 45.4 | 14.696 | 0.078575 | 10.912 | 0.022638 |  | 1342 | 10.912 | 45.4 | 14.696 | 0.078575 | 0.022638
1343 | 45.41 | 14.696 | 0.078573 | 10.914 | 0.022643 |  | 1343 | 10.914 | 45.41 | 14.696 | 0.078573 | 0.022643
1344 | 45.42 | 14.696 | 0.078572 | 10.917 | 0.022648 |  | 1344 | 10.917 | 45.42 | 14.696 | 0.078572 | 0.022648
1345 | 45.43 | 14.696 | 0.07857 | 10.919 | 0.022653 |  | 1345 | 10.919 | 45.43 | 14.696 | 0.07857 | 0.022653
1346 | 45.44 | 14.696 | 0.078569 | 10.922 | 0.022657 |  | 1346 | 10.922 | 45.44 | 14.696 | 0.078569 | 0.022657
1347 | 45.45 | 14.696 | 0.078567 | 10.924 | 0.022662 |  | 1347 | 10.924 | 45.45 | 14.696 | 0.078567 | 0.022662
1348 | 45.46 | 14.696 | 0.078565 | 10.926 | 0.022667 |  | 1348 | 10.926 | 45.46 | 14.696 | 0.078565 | 0.022667
1349 | 45.47 | 14.696 | 0.078564 | 10.929 | 0.022672 |  | 1349 | 10.929 | 45.47 | 14.696 | 0.078564 | 0.022672
1350 | 45.48 | 14.696 | 0.078562 | 10.931 | 0.022676 |  | 1350 | 10.931 | 45.48 | 14.696 | 0.078562 | 0.022676
1351 | 45.49 | 14.696 | 0.078561 | 10.934 | 0.022681 |  | 1351 | 10.934 | 45.49 | 14.696 | 0.078561 | 0.022681
1352 | 45.5 | 14.696 | 0.078559 | 10.936 | 0.022686 |  | 1352 | 10.936 | 45.5 | 14.696 | 0.078559 | 0.022686
1353 | 45.51 | 14.696 | 0.078558 | 10.938 | 0.022691 |  | 1353 | 10.938 | 45.51 | 14.696 | 0.078558 | 0.022691
1354 | 45.52 | 14.696 | 0.078556 | 10.941 | 0.022695 |  | 1354 | 10.941 | 45.52 | 14.696 | 0.078556 | 0.022695
1355 | 45.53 | 14.696 | 0.078555 | 10.943 | 0.0227 |  | 1355 | 10.943 | 45.53 | 14.696 | 0.078555 | 0.0227
1356 | 45.54 | 14.696 | 0.078553 | 10.946 | 0.022705 |  | 1356 | 10.946 | 45.54 | 14.696 | 0.078553 | 0.022705
1357 | 45.55 | 14.696 | 0.078551 | 10.948 | 0.02271 |  | 1357 | 10.948 | 45.55 | 14.696 | 0.078551 | 0.02271
1358 | 45.56 | 14.696 | 0.07855 | 10.95 | 0.022715 |  | 1358 | 10.95 | 45.56 | 14.696 | 0.07855 | 0.022715
1359 | 45.57 | 14.696 | 0.078548 | 10.953 | 0.022719 |  | 1359 | 10.953 | 45.57 | 14.696 | 0.078548 | 0.022719
1360 | 45.58 | 14.696 | 0.078547 | 10.955 | 0.022724 |  | 1360 | 10.955 | 45.58 | 14.696 | 0.078547 | 0.022724
1361 | 45.59 | 14.696 | 0.078545 | 10.958 | 0.022729 |  | 1361 | 10.958 | 45.59 | 14.696 | 0.078545 | 0.022729
1362 | 45.6 | 14.696 | 0.078544 | 10.96 | 0.022734 |  | 1362 | 10.96 | 45.6 | 14.696 | 0.078544 | 0.022734
1363 | 45.61 | 14.696 | 0.078542 | 10.963 | 0.022738 |  | 1363 | 10.963 | 45.61 | 14.696 | 0.078542 | 0.022738
1364 | 45.62 | 14.696 | 0.078541 | 10.965 | 0.022743 |  | 1364 | 10.965 | 45.62 | 14.696 | 0.078541 | 0.022743
1365 | 45.63 | 14.696 | 0.078539 | 10.967 | 0.022748 |  | 1365 | 10.967 | 45.63 | 14.696 | 0.078539 | 0.022748
1366 | 45.64 | 14.696 | 0.078537 | 10.97 | 0.022753 |  | 1366 | 10.97 | 45.64 | 14.696 | 0.078537 | 0.022753
1367 | 45.65 | 14.696 | 0.078536 | 10.972 | 0.022757 |  | 1367 | 10.972 | 45.65 | 14.696 | 0.078536 | 0.022757
1368 | 45.66 | 14.696 | 0.078534 | 10.975 | 0.022762 |  | 1368 | 10.975 | 45.66 | 14.696 | 0.078534 | 0.022762
1369 | 45.67 | 14.696 | 0.078533 | 10.977 | 0.022767 |  | 1369 | 10.977 | 45.67 | 14.696 | 0.078533 | 0.022767
1370 | 45.68 | 14.696 | 0.078531 | 10.979 | 0.022772 |  | 1370 | 10.979 | 45.68 | 14.696 | 0.078531 | 0.022772
1371 | 45.69 | 14.696 | 0.07853 | 10.982 | 0.022776 |  | 1371 | 10.982 | 45.69 | 14.696 | 0.07853 | 0.022776
1372 | 45.7 | 14.696 | 0.078528 | 10.984 | 0.022781 |  | 1372 | 10.984 | 45.7 | 14.696 | 0.078528 | 0.022781
1373 | 45.71 | 14.696 | 0.078527 | 10.987 | 0.022786 |  | 1373 | 10.987 | 45.71 | 14.696 | 0.078527 | 0.022786
1374 | 45.72 | 14.696 | 0.078525 | 10.989 | 0.022791 |  | 1374 | 10.989 | 45.72 | 14.696 | 0.078525 | 0.022791
1375 | 45.73 | 14.696 | 0.078523 | 10.991 | 0.022795 |  | 1375 | 10.991 | 45.73 | 14.696 | 0.078523 | 0.022795
1376 | 45.74 | 14.696 | 0.078522 | 10.994 | 0.0228 |  | 1376 | 10.994 | 45.74 | 14.696 | 0.078522 | 0.0228
1377 | 45.75 | 14.696 | 0.07852 | 10.996 | 0.022805 |  | 1377 | 10.996 | 45.75 | 14.696 | 0.07852 | 0.022805
1378 | 45.76 | 14.696 | 0.078519 | 10.999 | 0.02281 |  | 1378 | 10.999 | 45.76 | 14.696 | 0.078519 | 0.02281
1379 | 45.77 | 14.696 | 0.078517 | 11.001 | 0.022814 |  | 1379 | 11.001 | 45.77 | 14.696 | 0.078517 | 0.022814
1380 | 45.78 | 14.696 | 0.078516 | 11.003 | 0.022819 |  | 1380 | 11.003 | 45.78 | 14.696 | 0.078516 | 0.022819
1381 | 45.79 | 14.696 | 0.078514 | 11.006 | 0.022824 |  | 1381 | 11.006 | 45.79 | 14.696 | 0.078514 | 0.022824
1382 | 45.8 | 14.696 | 0.078512 | 11.008 | 0.022829 |  | 1382 | 11.008 | 45.8 | 14.696 | 0.078512 | 0.022829
1383 | 45.81 | 14.696 | 0.078511 | 11.011 | 0.022833 |  | 1383 | 11.011 | 45.81 | 14.696 | 0.078511 | 0.022833
1384 | 45.82 | 14.696 | 0.078509 | 11.013 | 0.022838 |  | 1384 | 11.013 | 45.82 | 14.696 | 0.078509 | 0.022838
1385 | 45.83 | 14.696 | 0.078508 | 11.015 | 0.022843 |  | 1385 | 11.015 | 45.83 | 14.696 | 0.078508 | 0.022843
1386 | 45.84 | 14.696 | 0.078506 | 11.018 | 0.022848 |  | 1386 | 11.018 | 45.84 | 14.696 | 0.078506 | 0.022848
1387 | 45.85 | 14.696 | 0.078505 | 11.02 | 0.022852 |  | 1387 | 11.02 | 45.85 | 14.696 | 0.078505 | 0.022852
1388 | 45.86 | 14.696 | 0.078503 | 11.023 | 0.022857 |  | 1388 | 11.023 | 45.86 | 14.696 | 0.078503 | 0.022857
1389 | 45.87 | 14.696 | 0.078502 | 11.025 | 0.022862 |  | 1389 | 11.025 | 45.87 | 14.696 | 0.078502 | 0.022862
1390 | 45.88 | 14.696 | 0.0785 | 11.027 | 0.022867 |  | 1390 | 11.027 | 45.88 | 14.696 | 0.0785 | 0.022867
1391 | 45.89 | 14.696 | 0.078498 | 11.03 | 0.022871 |  | 1391 | 11.03 | 45.89 | 14.696 | 0.078498 | 0.022871
1392 | 45.9 | 14.696 | 0.078497 | 11.032 | 0.022876 |  | 1392 | 11.032 | 45.9 | 14.696 | 0.078497 | 0.022876
1393 | 45.91 | 14.696 | 0.078495 | 11.035 | 0.022881 |  | 1393 | 11.035 | 45.91 | 14.696 | 0.078495 | 0.022881
1394 | 45.92 | 14.696 | 0.078494 | 11.037 | 0.022886 |  | 1394 | 11.037 | 45.92 | 14.696 | 0.078494 | 0.022886
1395 | 45.93 | 14.696 | 0.078492 | 11.039 | 0.02289 |  | 1395 | 11.039 | 45.93 | 14.696 | 0.078492 | 0.02289
1396 | 45.94 | 14.696 | 0.078491 | 11.042 | 0.022895 |  | 1396 | 11.042 | 45.94 | 14.696 | 0.078491 | 0.022895
1397 | 45.95 | 14.696 | 0.078489 | 11.044 | 0.0229 |  | 1397 | 11.044 | 45.95 | 14.696 | 0.078489 | 0.0229
1398 | 45.96 | 14.696 | 0.078488 | 11.047 | 0.022905 |  | 1398 | 11.047 | 45.96 | 14.696 | 0.078488 | 0.022905
1399 | 45.97 | 14.696 | 0.078486 | 11.049 | 0.02291 |  | 1399 | 11.049 | 45.97 | 14.696 | 0.078486 | 0.02291
1400 | 45.98 | 14.696 | 0.078484 | 11.051 | 0.022914 |  | 1400 | 11.051 | 45.98 | 14.696 | 0.078484 | 0.022914
1401 | 45.99 | 14.696 | 0.078483 | 11.054 | 0.022919 |  | 1401 | 11.054 | 45.99 | 14.696 | 0.078483 | 0.022919
1402 | 46 | 14.696 | 0.078481 | 11.056 | 0.022924 |  | 1402 | 11.056 | 46 | 14.696 | 0.078481 | 0.022924
1403 | 46.01 | 14.696 | 0.07848 | 11.059 | 0.022929 |  | 1403 | 11.059 | 46.01 | 14.696 | 0.07848 | 0.022929
1404 | 46.02 | 14.696 | 0.078478 | 11.061 | 0.022933 |  | 1404 | 11.061 | 46.02 | 14.696 | 0.078478 | 0.022933
1405 | 46.03 | 14.696 | 0.078477 | 11.063 | 0.022938 |  | 1405 | 11.063 | 46.03 | 14.696 | 0.078477 | 0.022938
1406 | 46.04 | 14.696 | 0.078475 | 11.066 | 0.022943 |  | 1406 | 11.066 | 46.04 | 14.696 | 0.078475 | 0.022943
1407 | 46.05 | 14.696 | 0.078474 | 11.068 | 0.022948 |  | 1407 | 11.068 | 46.05 | 14.696 | 0.078474 | 0.022948
1408 | 46.06 | 14.696 | 0.078472 | 11.071 | 0.022952 |  | 1408 | 11.071 | 46.06 | 14.696 | 0.078472 | 0.022952
1409 | 46.07 | 14.696 | 0.07847 | 11.073 | 0.022957 |  | 1409 | 11.073 | 46.07 | 14.696 | 0.07847 | 0.022957
1410 | 46.08 | 14.696 | 0.078469 | 11.075 | 0.022962 |  | 1410 | 11.075 | 46.08 | 14.696 | 0.078469 | 0.022962
1411 | 46.09 | 14.696 | 0.078467 | 11.078 | 0.022967 |  | 1411 | 11.078 | 46.09 | 14.696 | 0.078467 | 0.022967
1412 | 46.1 | 14.696 | 0.078466 | 11.08 | 0.022971 |  | 1412 | 11.08 | 46.1 | 14.696 | 0.078466 | 0.022971
1413 | 46.11 | 14.696 | 0.078464 | 11.083 | 0.022976 |  | 1413 | 11.083 | 46.11 | 14.696 | 0.078464 | 0.022976
1414 | 46.12 | 14.696 | 0.078463 | 11.085 | 0.022981 |  | 1414 | 11.085 | 46.12 | 14.696 | 0.078463 | 0.022981
1415 | 46.13 | 14.696 | 0.078461 | 11.088 | 0.022986 |  | 1415 | 11.088 | 46.13 | 14.696 | 0.078461 | 0.022986
1416 | 46.14 | 14.696 | 0.07846 | 11.09 | 0.02299 |  | 1416 | 11.09 | 46.14 | 14.696 | 0.07846 | 0.02299
1417 | 46.15 | 14.696 | 0.078458 | 11.092 | 0.022995 |  | 1417 | 11.092 | 46.15 | 14.696 | 0.078458 | 0.022995
1418 | 46.16 | 14.696 | 0.078456 | 11.095 | 0.023 |  | 1418 | 11.095 | 46.16 | 14.696 | 0.078456 | 0.023
1419 | 46.17 | 14.696 | 0.078455 | 11.097 | 0.023005 |  | 1419 | 11.097 | 46.17 | 14.696 | 0.078455 | 0.023005
1420 | 46.18 | 14.696 | 0.078453 | 11.1 | 0.023009 |  | 1420 | 11.1 | 46.18 | 14.696 | 0.078453 | 0.023009
1421 | 46.19 | 14.696 | 0.078452 | 11.102 | 0.023014 |  | 1421 | 11.102 | 46.19 | 14.696 | 0.078452 | 0.023014
1422 | 46.2 | 14.696 | 0.07845 | 11.104 | 0.023019 |  | 1422 | 11.104 | 46.2 | 14.696 | 0.07845 | 0.023019
1423 | 46.21 | 14.696 | 0.078449 | 11.107 | 0.023024 |  | 1423 | 11.107 | 46.21 | 14.696 | 0.078449 | 0.023024
1424 | 46.22 | 14.696 | 0.078447 | 11.109 | 0.023028 |  | 1424 | 11.109 | 46.22 | 14.696 | 0.078447 | 0.023028
1425 | 46.23 | 14.696 | 0.078446 | 11.112 | 0.023033 |  | 1425 | 11.112 | 46.23 | 14.696 | 0.078446 | 0.023033
1426 | 46.24 | 14.696 | 0.078444 | 11.114 | 0.023038 |  | 1426 | 11.114 | 46.24 | 14.696 | 0.078444 | 0.023038
1427 | 46.25 | 14.696 | 0.078442 | 11.116 | 0.023043 |  | 1427 | 11.116 | 46.25 | 14.696 | 0.078442 | 0.023043
1428 | 46.26 | 14.696 | 0.078441 | 11.119 | 0.023047 |  | 1428 | 11.119 | 46.26 | 14.696 | 0.078441 | 0.023047
1429 | 46.27 | 14.696 | 0.078439 | 11.121 | 0.023052 |  | 1429 | 11.121 | 46.27 | 14.696 | 0.078439 | 0.023052
1430 | 46.28 | 14.696 | 0.078438 | 11.124 | 0.023057 |  | 1430 | 11.124 | 46.28 | 14.696 | 0.078438 | 0.023057
1431 | 46.29 | 14.696 | 0.078436 | 11.126 | 0.023062 |  | 1431 | 11.126 | 46.29 | 14.696 | 0.078436 | 0.023062
1432 | 46.3 | 14.696 | 0.078435 | 11.128 | 0.023066 |  | 1432 | 11.128 | 46.3 | 14.696 | 0.078435 | 0.023066
1433 | 46.31 | 14.696 | 0.078433 | 11.131 | 0.023071 |  | 1433 | 11.131 | 46.31 | 14.696 | 0.078433 | 0.023071
1434 | 46.32 | 14.696 | 0.078432 | 11.133 | 0.023076 |  | 1434 | 11.133 | 46.32 | 14.696 | 0.078432 | 0.023076
1435 | 46.33 | 14.696 | 0.07843 | 11.136 | 0.023081 |  | 1435 | 11.136 | 46.33 | 14.696 | 0.07843 | 0.023081
1436 | 46.34 | 14.696 | 0.078428 | 11.138 | 0.023085 |  | 1436 | 11.138 | 46.34 | 14.696 | 0.078428 | 0.023085
1437 | 46.35 | 14.696 | 0.078427 | 11.14 | 0.02309 |  | 1437 | 11.14 | 46.35 | 14.696 | 0.078427 | 0.02309
1438 | 46.36 | 14.696 | 0.078425 | 11.143 | 0.023095 |  | 1438 | 11.143 | 46.36 | 14.696 | 0.078425 | 0.023095
1439 | 46.37 | 14.696 | 0.078424 | 11.145 | 0.0231 |  | 1439 | 11.145 | 46.37 | 14.696 | 0.078424 | 0.0231
1440 | 46.38 | 14.696 | 0.078422 | 11.148 | 0.023104 |  | 1440 | 11.148 | 46.38 | 14.696 | 0.078422 | 0.023104
1441 | 46.39 | 14.696 | 0.078421 | 11.15 | 0.023109 |  | 1441 | 11.15 | 46.39 | 14.696 | 0.078421 | 0.023109
1442 | 46.4 | 14.696 | 0.078419 | 11.152 | 0.023114 |  | 1442 | 11.152 | 46.4 | 14.696 | 0.078419 | 0.023114
1443 | 46.41 | 14.696 | 0.078418 | 11.155 | 0.023119 |  | 1443 | 11.155 | 46.41 | 14.696 | 0.078418 | 0.023119
1444 | 46.42 | 14.696 | 0.078416 | 11.157 | 0.023123 |  | 1444 | 11.157 | 46.42 | 14.696 | 0.078416 | 0.023123
1445 | 46.43 | 14.696 | 0.078414 | 11.16 | 0.023128 |  | 1445 | 11.16 | 46.43 | 14.696 | 0.078414 | 0.023128
1446 | 46.44 | 14.696 | 0.078413 | 11.162 | 0.023133 |  | 1446 | 11.162 | 46.44 | 14.696 | 0.078413 | 0.023133
1447 | 46.45 | 14.696 | 0.078411 | 11.164 | 0.023138 |  | 1447 | 11.164 | 46.45 | 14.696 | 0.078411 | 0.023138
1448 | 46.46 | 14.696 | 0.07841 | 11.167 | 0.023142 |  | 1448 | 11.167 | 46.46 | 14.696 | 0.07841 | 0.023142
1449 | 46.47 | 14.696 | 0.078408 | 11.169 | 0.023147 |  | 1449 | 11.169 | 46.47 | 14.696 | 0.078408 | 0.023147
1450 | 46.48 | 14.696 | 0.078407 | 11.172 | 0.023152 |  | 1450 | 11.172 | 46.48 | 14.696 | 0.078407 | 0.023152
1451 | 46.49 | 14.696 | 0.078405 | 11.174 | 0.023157 |  | 1451 | 11.174 | 46.49 | 14.696 | 0.078405 | 0.023157
1452 | 46.5 | 14.696 | 0.078404 | 11.176 | 0.023161 |  | 1452 | 11.176 | 46.5 | 14.696 | 0.078404 | 0.023161
1453 | 46.51 | 14.696 | 0.078402 | 11.179 | 0.023166 |  | 1453 | 11.179 | 46.51 | 14.696 | 0.078402 | 0.023166
1454 | 46.52 | 14.696 | 0.0784 | 11.181 | 0.023171 |  | 1454 | 11.181 | 46.52 | 14.696 | 0.0784 | 0.023171
1455 | 46.53 | 14.696 | 0.078399 | 11.184 | 0.023176 |  | 1455 | 11.184 | 46.53 | 14.696 | 0.078399 | 0.023176
1456 | 46.54 | 14.696 | 0.078397 | 11.186 | 0.02318 |  | 1456 | 11.186 | 46.54 | 14.696 | 0.078397 | 0.02318
1457 | 46.55 | 14.696 | 0.078396 | 11.188 | 0.023185 |  | 1457 | 11.188 | 46.55 | 14.696 | 0.078396 | 0.023185
1458 | 46.56 | 14.696 | 0.078394 | 11.191 | 0.02319 |  | 1458 | 11.191 | 46.56 | 14.696 | 0.078394 | 0.02319
1459 | 46.57 | 14.696 | 0.078393 | 11.193 | 0.023195 |  | 1459 | 11.193 | 46.57 | 14.696 | 0.078393 | 0.023195
1460 | 46.58 | 14.696 | 0.078391 | 11.196 | 0.023199 |  | 1460 | 11.196 | 46.58 | 14.696 | 0.078391 | 0.023199
1461 | 46.59 | 14.696 | 0.07839 | 11.198 | 0.023204 |  | 1461 | 11.198 | 46.59 | 14.696 | 0.07839 | 0.023204
1462 | 46.6 | 14.696 | 0.078388 | 11.201 | 0.023209 |  | 1462 | 11.201 | 46.6 | 14.696 | 0.078388 | 0.023209
1463 | 46.61 | 14.696 | 0.078386 | 11.203 | 0.023214 |  | 1463 | 11.203 | 46.61 | 14.696 | 0.078386 | 0.023214
1464 | 46.62 | 14.696 | 0.078385 | 11.205 | 0.023218 |  | 1464 | 11.205 | 46.62 | 14.696 | 0.078385 | 0.023218
1465 | 46.63 | 14.696 | 0.078383 | 11.208 | 0.023223 |  | 1465 | 11.208 | 46.63 | 14.696 | 0.078383 | 0.023223
1466 | 46.64 | 14.696 | 0.078382 | 11.21 | 0.023228 |  | 1466 | 11.21 | 46.64 | 14.696 | 0.078382 | 0.023228
1467 | 46.65 | 14.696 | 0.07838 | 11.213 | 0.023233 |  | 1467 | 11.213 | 46.65 | 14.696 | 0.07838 | 0.023233
1468 | 46.66 | 14.696 | 0.078379 | 11.215 | 0.023237 |  | 1468 | 11.215 | 46.66 | 14.696 | 0.078379 | 0.023237
1469 | 46.67 | 14.696 | 0.078377 | 11.217 | 0.023242 |  | 1469 | 11.217 | 46.67 | 14.696 | 0.078377 | 0.023242
1470 | 46.68 | 14.696 | 0.078376 | 11.22 | 0.023247 |  | 1470 | 11.22 | 46.68 | 14.696 | 0.078376 | 0.023247
1471 | 46.69 | 14.696 | 0.078374 | 11.222 | 0.023252 |  | 1471 | 11.222 | 46.69 | 14.696 | 0.078374 | 0.023252
1472 | 46.7 | 14.696 | 0.078372 | 11.225 | 0.023256 |  | 1472 | 11.225 | 46.7 | 14.696 | 0.078372 | 0.023256
1473 | 46.71 | 14.696 | 0.078371 | 11.227 | 0.023261 |  | 1473 | 11.227 | 46.71 | 14.696 | 0.078371 | 0.023261
1474 | 46.72 | 14.696 | 0.078369 | 11.229 | 0.023266 |  | 1474 | 11.229 | 46.72 | 14.696 | 0.078369 | 0.023266
1475 | 46.73 | 14.696 | 0.078368 | 11.232 | 0.023271 |  | 1475 | 11.232 | 46.73 | 14.696 | 0.078368 | 0.023271
1476 | 46.74 | 14.696 | 0.078366 | 11.234 | 0.023275 |  | 1476 | 11.234 | 46.74 | 14.696 | 0.078366 | 0.023275
1477 | 46.75 | 14.696 | 0.078365 | 11.237 | 0.02328 |  | 1477 | 11.237 | 46.75 | 14.696 | 0.078365 | 0.02328
1478 | 46.76 | 14.696 | 0.078363 | 11.239 | 0.023285 |  | 1478 | 11.239 | 46.76 | 14.696 | 0.078363 | 0.023285
1479 | 46.77 | 14.696 | 0.078362 | 11.241 | 0.02329 |  | 1479 | 11.241 | 46.77 | 14.696 | 0.078362 | 0.02329
1480 | 46.78 | 14.696 | 0.07836 | 11.244 | 0.023294 |  | 1480 | 11.244 | 46.78 | 14.696 | 0.07836 | 0.023294
1481 | 46.79 | 14.696 | 0.078359 | 11.246 | 0.023299 |  | 1481 | 11.246 | 46.79 | 14.696 | 0.078359 | 0.023299
1482 | 46.8 | 14.696 | 0.078357 | 11.249 | 0.023304 |  | 1482 | 11.249 | 46.8 | 14.696 | 0.078357 | 0.023304
1483 | 46.81 | 14.696 | 0.078355 | 11.251 | 0.023309 |  | 1483 | 11.251 | 46.81 | 14.696 | 0.078355 | 0.023309
1484 | 46.82 | 14.696 | 0.078354 | 11.253 | 0.023313 |  | 1484 | 11.253 | 46.82 | 14.696 | 0.078354 | 0.023313
1485 | 46.83 | 14.696 | 0.078352 | 11.256 | 0.023318 |  | 1485 | 11.256 | 46.83 | 14.696 | 0.078352 | 0.023318
1486 | 46.84 | 14.696 | 0.078351 | 11.258 | 0.023323 |  | 1486 | 11.258 | 46.84 | 14.696 | 0.078351 | 0.023323
1487 | 46.85 | 14.696 | 0.078349 | 11.261 | 0.023328 |  | 1487 | 11.261 | 46.85 | 14.696 | 0.078349 | 0.023328
1488 | 46.86 | 14.696 | 0.078348 | 11.263 | 0.023332 |  | 1488 | 11.263 | 46.86 | 14.696 | 0.078348 | 0.023332
1489 | 46.87 | 14.696 | 0.078346 | 11.265 | 0.023337 |  | 1489 | 11.265 | 46.87 | 14.696 | 0.078346 | 0.023337
1490 | 46.88 | 14.696 | 0.078345 | 11.268 | 0.023342 |  | 1490 | 11.268 | 46.88 | 14.696 | 0.078345 | 0.023342
1491 | 46.89 | 14.696 | 0.078343 | 11.27 | 0.023347 |  | 1491 | 11.27 | 46.89 | 14.696 | 0.078343 | 0.023347
1492 | 46.9 | 14.696 | 0.078341 | 11.273 | 0.023351 |  | 1492 | 11.273 | 46.9 | 14.696 | 0.078341 | 0.023351
1493 | 46.91 | 14.696 | 0.07834 | 11.275 | 0.023356 |  | 1493 | 11.275 | 46.91 | 14.696 | 0.07834 | 0.023356
1494 | 46.92 | 14.696 | 0.078338 | 11.277 | 0.023361 |  | 1494 | 11.277 | 46.92 | 14.696 | 0.078338 | 0.023361
1495 | 46.93 | 14.696 | 0.078337 | 11.28 | 0.023366 |  | 1495 | 11.28 | 46.93 | 14.696 | 0.078337 | 0.023366
1496 | 46.94 | 14.696 | 0.078335 | 11.282 | 0.02337 |  | 1496 | 11.282 | 46.94 | 14.696 | 0.078335 | 0.02337
1497 | 46.95 | 14.696 | 0.078334 | 11.285 | 0.023375 |  | 1497 | 11.285 | 46.95 | 14.696 | 0.078334 | 0.023375
1498 | 46.96 | 14.696 | 0.078332 | 11.287 | 0.02338 |  | 1498 | 11.287 | 46.96 | 14.696 | 0.078332 | 0.02338
1499 | 46.97 | 14.696 | 0.078331 | 11.289 | 0.023384 |  | 1499 | 11.289 | 46.97 | 14.696 | 0.078331 | 0.023384
1500 | 46.98 | 14.696 | 0.078329 | 11.292 | 0.023389 |  | 1500 | 11.292 | 46.98 | 14.696 | 0.078329 | 0.023389
1501 | 46.99 | 14.696 | 0.078327 | 11.294 | 0.023394 |  | 1501 | 11.294 | 46.99 | 14.696 | 0.078327 | 0.023394
1502 | 47 | 14.696 | 0.078326 | 11.297 | 0.023399 |  | 1502 | 11.297 | 47 | 14.696 | 0.078326 | 0.023399
1503 | 47.01 | 14.696 | 0.078324 | 11.299 | 0.023403 |  | 1503 | 11.299 | 47.01 | 14.696 | 0.078324 | 0.023403
1504 | 47.02 | 14.696 | 0.078323 | 11.301 | 0.023408 |  | 1504 | 11.301 | 47.02 | 14.696 | 0.078323 | 0.023408
1505 | 47.03 | 14.696 | 0.078321 | 11.304 | 0.023413 |  | 1505 | 11.304 | 47.03 | 14.696 | 0.078321 | 0.023413
1506 | 47.04 | 14.696 | 0.07832 | 11.306 | 0.023418 |  | 1506 | 11.306 | 47.04 | 14.696 | 0.07832 | 0.023418
1507 | 47.05 | 14.696 | 0.078318 | 11.309 | 0.023422 |  | 1507 | 11.309 | 47.05 | 14.696 | 0.078318 | 0.023422
1508 | 47.06 | 14.696 | 0.078317 | 11.311 | 0.023427 |  | 1508 | 11.311 | 47.06 | 14.696 | 0.078317 | 0.023427
1509 | 47.07 | 14.696 | 0.078315 | 11.313 | 0.023432 |  | 1509 | 11.313 | 47.07 | 14.696 | 0.078315 | 0.023432
1510 | 47.08 | 14.696 | 0.078314 | 11.316 | 0.023437 |  | 1510 | 11.316 | 47.08 | 14.696 | 0.078314 | 0.023437
1511 | 47.09 | 14.696 | 0.078312 | 11.318 | 0.023441 |  | 1511 | 11.318 | 47.09 | 14.696 | 0.078312 | 0.023441
1512 | 47.1 | 14.696 | 0.07831 | 11.321 | 0.023446 |  | 1512 | 11.321 | 47.1 | 14.696 | 0.07831 | 0.023446
1513 | 47.11 | 14.696 | 0.078309 | 11.323 | 0.023451 |  | 1513 | 11.323 | 47.11 | 14.696 | 0.078309 | 0.023451
1514 | 47.12 | 14.696 | 0.078307 | 11.326 | 0.023456 |  | 1514 | 11.326 | 47.12 | 14.696 | 0.078307 | 0.023456
1515 | 47.13 | 14.696 | 0.078306 | 11.328 | 0.02346 |  | 1515 | 11.328 | 47.13 | 14.696 | 0.078306 | 0.02346
1516 | 47.14 | 14.696 | 0.078304 | 11.33 | 0.023465 |  | 1516 | 11.33 | 47.14 | 14.696 | 0.078304 | 0.023465
1517 | 47.15 | 14.696 | 0.078303 | 11.333 | 0.02347 |  | 1517 | 11.333 | 47.15 | 14.696 | 0.078303 | 0.02347
1518 | 47.16 | 14.696 | 0.078301 | 11.335 | 0.023475 |  | 1518 | 11.335 | 47.16 | 14.696 | 0.078301 | 0.023475
1519 | 47.17 | 14.696 | 0.0783 | 11.338 | 0.023479 |  | 1519 | 11.338 | 47.17 | 14.696 | 0.0783 | 0.023479
1520 | 47.18 | 14.696 | 0.078298 | 11.34 | 0.023484 |  | 1520 | 11.34 | 47.18 | 14.696 | 0.078298 | 0.023484
1521 | 47.19 | 14.696 | 0.078296 | 11.342 | 0.023489 |  | 1521 | 11.342 | 47.19 | 14.696 | 0.078296 | 0.023489
1522 | 47.2 | 14.696 | 0.078295 | 11.345 | 0.023494 |  | 1522 | 11.345 | 47.2 | 14.696 | 0.078295 | 0.023494
1523 | 47.21 | 14.696 | 0.078293 | 11.347 | 0.023498 |  | 1523 | 11.347 | 47.21 | 14.696 | 0.078293 | 0.023498
1524 | 47.22 | 14.696 | 0.078292 | 11.35 | 0.023503 |  | 1524 | 11.35 | 47.22 | 14.696 | 0.078292 | 0.023503
1525 | 47.23 | 14.696 | 0.07829 | 11.352 | 0.023508 |  | 1525 | 11.352 | 47.23 | 14.696 | 0.07829 | 0.023508
1526 | 47.24 | 14.696 | 0.078289 | 11.354 | 0.023513 |  | 1526 | 11.354 | 47.24 | 14.696 | 0.078289 | 0.023513
1527 | 47.25 | 14.696 | 0.078287 | 11.357 | 0.023517 |  | 1527 | 11.357 | 47.25 | 14.696 | 0.078287 | 0.023517
1528 | 47.26 | 14.696 | 0.078286 | 11.359 | 0.023522 |  | 1528 | 11.359 | 47.26 | 14.696 | 0.078286 | 0.023522
1529 | 47.27 | 14.696 | 0.078284 | 11.362 | 0.023527 |  | 1529 | 11.362 | 47.27 | 14.696 | 0.078284 | 0.023527
1530 | 47.28 | 14.696 | 0.078283 | 11.364 | 0.023532 |  | 1530 | 11.364 | 47.28 | 14.696 | 0.078283 | 0.023532
1531 | 47.29 | 14.696 | 0.078281 | 11.366 | 0.023536 |  | 1531 | 11.366 | 47.29 | 14.696 | 0.078281 | 0.023536
1532 | 47.3 | 14.696 | 0.078279 | 11.369 | 0.023541 |  | 1532 | 11.369 | 47.3 | 14.696 | 0.078279 | 0.023541
1533 | 47.31 | 14.696 | 0.078278 | 11.371 | 0.023546 |  | 1533 | 11.371 | 47.31 | 14.696 | 0.078278 | 0.023546
1534 | 47.32 | 14.696 | 0.078276 | 11.374 | 0.02355 |  | 1534 | 11.374 | 47.32 | 14.696 | 0.078276 | 0.02355
1535 | 47.33 | 14.696 | 0.078275 | 11.376 | 0.023555 |  | 1535 | 11.376 | 47.33 | 14.696 | 0.078275 | 0.023555
1536 | 47.34 | 14.696 | 0.078273 | 11.378 | 0.02356 |  | 1536 | 11.378 | 47.34 | 14.696 | 0.078273 | 0.02356
1537 | 47.35 | 14.696 | 0.078272 | 11.381 | 0.023565 |  | 1537 | 11.381 | 47.35 | 14.696 | 0.078272 | 0.023565
1538 | 47.36 | 14.696 | 0.07827 | 11.383 | 0.023569 |  | 1538 | 11.383 | 47.36 | 14.696 | 0.07827 | 0.023569
1539 | 47.37 | 14.696 | 0.078269 | 11.386 | 0.023574 |  | 1539 | 11.386 | 47.37 | 14.696 | 0.078269 | 0.023574
1540 | 47.38 | 14.696 | 0.078267 | 11.388 | 0.023579 |  | 1540 | 11.388 | 47.38 | 14.696 | 0.078267 | 0.023579
1541 | 47.39 | 14.696 | 0.078265 | 11.39 | 0.023584 |  | 1541 | 11.39 | 47.39 | 14.696 | 0.078265 | 0.023584
1542 | 47.4 | 14.696 | 0.078264 | 11.393 | 0.023588 |  | 1542 | 11.393 | 47.4 | 14.696 | 0.078264 | 0.023588
1543 | 47.41 | 14.696 | 0.078262 | 11.395 | 0.023593 |  | 1543 | 11.395 | 47.41 | 14.696 | 0.078262 | 0.023593
1544 | 47.42 | 14.696 | 0.078261 | 11.398 | 0.023598 |  | 1544 | 11.398 | 47.42 | 14.696 | 0.078261 | 0.023598
1545 | 47.43 | 14.696 | 0.078259 | 11.4 | 0.023603 |  | 1545 | 11.4 | 47.43 | 14.696 | 0.078259 | 0.023603
1546 | 47.44 | 14.696 | 0.078258 | 11.402 | 0.023607 |  | 1546 | 11.402 | 47.44 | 14.696 | 0.078258 | 0.023607
1547 | 47.45 | 14.696 | 0.078256 | 11.405 | 0.023612 |  | 1547 | 11.405 | 47.45 | 14.696 | 0.078256 | 0.023612
1548 | 47.46 | 14.696 | 0.078255 | 11.407 | 0.023617 |  | 1548 | 11.407 | 47.46 | 14.696 | 0.078255 | 0.023617
1549 | 47.47 | 14.696 | 0.078253 | 11.41 | 0.023622 |  | 1549 | 11.41 | 47.47 | 14.696 | 0.078253 | 0.023622
1550 | 47.48 | 14.696 | 0.078252 | 11.412 | 0.023626 |  | 1550 | 11.412 | 47.48 | 14.696 | 0.078252 | 0.023626
1551 | 47.49 | 14.696 | 0.07825 | 11.414 | 0.023631 |  | 1551 | 11.414 | 47.49 | 14.696 | 0.07825 | 0.023631
1552 | 47.5 | 14.696 | 0.078248 | 11.417 | 0.023636 |  | 1552 | 11.417 | 47.5 | 14.696 | 0.078248 | 0.023636
1553 | 47.51 | 14.696 | 0.078247 | 11.419 | 0.023641 |  | 1553 | 11.419 | 47.51 | 14.696 | 0.078247 | 0.023641
1554 | 47.52 | 14.696 | 0.078245 | 11.422 | 0.023645 |  | 1554 | 11.422 | 47.52 | 14.696 | 0.078245 | 0.023645
1555 | 47.53 | 14.696 | 0.078244 | 11.424 | 0.02365 |  | 1555 | 11.424 | 47.53 | 14.696 | 0.078244 | 0.02365
1556 | 47.54 | 14.696 | 0.078242 | 11.426 | 0.023655 |  | 1556 | 11.426 | 47.54 | 14.696 | 0.078242 | 0.023655
1557 | 47.55 | 14.696 | 0.078241 | 11.429 | 0.02366 |  | 1557 | 11.429 | 47.55 | 14.696 | 0.078241 | 0.02366
1558 | 47.56 | 14.696 | 0.078239 | 11.431 | 0.023664 |  | 1558 | 11.431 | 47.56 | 14.696 | 0.078239 | 0.023664
1559 | 47.57 | 14.696 | 0.078238 | 11.434 | 0.023669 |  | 1559 | 11.434 | 47.57 | 14.696 | 0.078238 | 0.023669
1560 | 47.58 | 14.696 | 0.078236 | 11.436 | 0.023674 |  | 1560 | 11.436 | 47.58 | 14.696 | 0.078236 | 0.023674
1561 | 47.59 | 14.696 | 0.078235 | 11.439 | 0.023678 |  | 1561 | 11.439 | 47.59 | 14.696 | 0.078235 | 0.023678
1562 | 47.6 | 14.696 | 0.078233 | 11.441 | 0.023683 |  | 1562 | 11.441 | 47.6 | 14.696 | 0.078233 | 0.023683
1563 | 47.61 | 14.696 | 0.078231 | 11.443 | 0.023688 |  | 1563 | 11.443 | 47.61 | 14.696 | 0.078231 | 0.023688
1564 | 47.62 | 14.696 | 0.07823 | 11.446 | 0.023693 |  | 1564 | 11.446 | 47.62 | 14.696 | 0.07823 | 0.023693
1565 | 47.63 | 14.696 | 0.078228 | 11.448 | 0.023697 |  | 1565 | 11.448 | 47.63 | 14.696 | 0.078228 | 0.023697
1566 | 47.64 | 14.696 | 0.078227 | 11.451 | 0.023702 |  | 1566 | 11.451 | 47.64 | 14.696 | 0.078227 | 0.023702
1567 | 47.65 | 14.696 | 0.078225 | 11.453 | 0.023707 |  | 1567 | 11.453 | 47.65 | 14.696 | 0.078225 | 0.023707
1568 | 47.66 | 14.696 | 0.078224 | 11.455 | 0.023712 |  | 1568 | 11.455 | 47.66 | 14.696 | 0.078224 | 0.023712
1569 | 47.67 | 14.696 | 0.078222 | 11.458 | 0.023716 |  | 1569 | 11.458 | 47.67 | 14.696 | 0.078222 | 0.023716
1570 | 47.68 | 14.696 | 0.078221 | 11.46 | 0.023721 |  | 1570 | 11.46 | 47.68 | 14.696 | 0.078221 | 0.023721
1571 | 47.69 | 14.696 | 0.078219 | 11.463 | 0.023726 |  | 1571 | 11.463 | 47.69 | 14.696 | 0.078219 | 0.023726
1572 | 47.7 | 14.696 | 0.078218 | 11.465 | 0.023731 |  | 1572 | 11.465 | 47.7 | 14.696 | 0.078218 | 0.023731
1573 | 47.71 | 14.696 | 0.078216 | 11.467 | 0.023735 |  | 1573 | 11.467 | 47.71 | 14.696 | 0.078216 | 0.023735
1574 | 47.72 | 14.696 | 0.078214 | 11.47 | 0.02374 |  | 1574 | 11.47 | 47.72 | 14.696 | 0.078214 | 0.02374
1575 | 47.73 | 14.696 | 0.078213 | 11.472 | 0.023745 |  | 1575 | 11.472 | 47.73 | 14.696 | 0.078213 | 0.023745
1576 | 47.74 | 14.696 | 0.078211 | 11.475 | 0.02375 |  | 1576 | 11.475 | 47.74 | 14.696 | 0.078211 | 0.02375
1577 | 47.75 | 14.696 | 0.07821 | 11.477 | 0.023754 |  | 1577 | 11.477 | 47.75 | 14.696 | 0.07821 | 0.023754
1578 | 47.76 | 14.696 | 0.078208 | 11.479 | 0.023759 |  | 1578 | 11.479 | 47.76 | 14.696 | 0.078208 | 0.023759
1579 | 47.77 | 14.696 | 0.078207 | 11.482 | 0.023764 |  | 1579 | 11.482 | 47.77 | 14.696 | 0.078207 | 0.023764
1580 | 47.78 | 14.696 | 0.078205 | 11.484 | 0.023769 |  | 1580 | 11.484 | 47.78 | 14.696 | 0.078205 | 0.023769
1581 | 47.79 | 14.696 | 0.078204 | 11.487 | 0.023773 |  | 1581 | 11.487 | 47.79 | 14.696 | 0.078204 | 0.023773
1582 | 47.8 | 14.696 | 0.078202 | 11.489 | 0.023778 |  | 1582 | 11.489 | 47.8 | 14.696 | 0.078202 | 0.023778
1583 | 47.81 | 14.696 | 0.078201 | 11.491 | 0.023783 |  | 1583 | 11.491 | 47.81 | 14.696 | 0.078201 | 0.023783
1584 | 47.82 | 14.696 | 0.078199 | 11.494 | 0.023787 |  | 1584 | 11.494 | 47.82 | 14.696 | 0.078199 | 0.023787
1585 | 47.83 | 14.696 | 0.078197 | 11.496 | 0.023792 |  | 1585 | 11.496 | 47.83 | 14.696 | 0.078197 | 0.023792
1586 | 47.84 | 14.696 | 0.078196 | 11.499 | 0.023797 |  | 1586 | 11.499 | 47.84 | 14.696 | 0.078196 | 0.023797
1587 | 47.85 | 14.696 | 0.078194 | 11.501 | 0.023802 |  | 1587 | 11.501 | 47.85 | 14.696 | 0.078194 | 0.023802
1588 | 47.86 | 14.696 | 0.078193 | 11.503 | 0.023806 |  | 1588 | 11.503 | 47.86 | 14.696 | 0.078193 | 0.023806
1589 | 47.87 | 14.696 | 0.078191 | 11.506 | 0.023811 |  | 1589 | 11.506 | 47.87 | 14.696 | 0.078191 | 0.023811
1590 | 47.88 | 14.696 | 0.07819 | 11.508 | 0.023816 |  | 1590 | 11.508 | 47.88 | 14.696 | 0.07819 | 0.023816
1591 | 47.89 | 14.696 | 0.078188 | 11.511 | 0.023821 |  | 1591 | 11.511 | 47.89 | 14.696 | 0.078188 | 0.023821
1592 | 47.9 | 14.696 | 0.078187 | 11.513 | 0.023825 |  | 1592 | 11.513 | 47.9 | 14.696 | 0.078187 | 0.023825
1593 | 47.91 | 14.696 | 0.078185 | 11.515 | 0.02383 |  | 1593 | 11.515 | 47.91 | 14.696 | 0.078185 | 0.02383
1594 | 47.92 | 14.696 | 0.078184 | 11.518 | 0.023835 |  | 1594 | 11.518 | 47.92 | 14.696 | 0.078184 | 0.023835
1595 | 47.93 | 14.696 | 0.078182 | 11.52 | 0.02384 |  | 1595 | 11.52 | 47.93 | 14.696 | 0.078182 | 0.02384
1596 | 47.94 | 14.696 | 0.07818 | 11.523 | 0.023844 |  | 1596 | 11.523 | 47.94 | 14.696 | 0.07818 | 0.023844
1597 | 47.95 | 14.696 | 0.078179 | 11.525 | 0.023849 |  | 1597 | 11.525 | 47.95 | 14.696 | 0.078179 | 0.023849
1598 | 47.96 | 14.696 | 0.078177 | 11.527 | 0.023854 |  | 1598 | 11.527 | 47.96 | 14.696 | 0.078177 | 0.023854
1599 | 47.97 | 14.696 | 0.078176 | 11.53 | 0.023859 |  | 1599 | 11.53 | 47.97 | 14.696 | 0.078176 | 0.023859
1600 | 47.98 | 14.696 | 0.078174 | 11.532 | 0.023863 |  | 1600 | 11.532 | 47.98 | 14.696 | 0.078174 | 0.023863
1601 | 47.99 | 14.696 | 0.078173 | 11.535 | 0.023868 |  | 1601 | 11.535 | 47.99 | 14.696 | 0.078173 | 0.023868
1602 | 48 | 14.696 | 0.078171 | 11.537 | 0.023873 |  | 1602 | 11.537 | 48 | 14.696 | 0.078171 | 0.023873
1603 | 48.01 | 14.696 | 0.07817 | 11.539 | 0.023877 |  | 1603 | 11.539 | 48.01 | 14.696 | 0.07817 | 0.023877
1604 | 48.02 | 14.696 | 0.078168 | 11.542 | 0.023882 |  | 1604 | 11.542 | 48.02 | 14.696 | 0.078168 | 0.023882
1605 | 48.03 | 14.696 | 0.078167 | 11.544 | 0.023887 |  | 1605 | 11.544 | 48.03 | 14.696 | 0.078167 | 0.023887
1606 | 48.04 | 14.696 | 0.078165 | 11.547 | 0.023892 |  | 1606 | 11.547 | 48.04 | 14.696 | 0.078165 | 0.023892
1607 | 48.05 | 14.696 | 0.078163 | 11.549 | 0.023896 |  | 1607 | 11.549 | 48.05 | 14.696 | 0.078163 | 0.023896
1608 | 48.06 | 14.696 | 0.078162 | 11.551 | 0.023901 |  | 1608 | 11.551 | 48.06 | 14.696 | 0.078162 | 0.023901
1609 | 48.07 | 14.696 | 0.07816 | 11.554 | 0.023906 |  | 1609 | 11.554 | 48.07 | 14.696 | 0.07816 | 0.023906
1610 | 48.08 | 14.696 | 0.078159 | 11.556 | 0.023911 |  | 1610 | 11.556 | 48.08 | 14.696 | 0.078159 | 0.023911
1611 | 48.09 | 14.696 | 0.078157 | 11.559 | 0.023915 |  | 1611 | 11.559 | 48.09 | 14.696 | 0.078157 | 0.023915
1612 | 48.1 | 14.696 | 0.078156 | 11.561 | 0.02392 |  | 1612 | 11.561 | 48.1 | 14.696 | 0.078156 | 0.02392
1613 | 48.11 | 14.696 | 0.078154 | 11.564 | 0.023925 |  | 1613 | 11.564 | 48.11 | 14.696 | 0.078154 | 0.023925
1614 | 48.12 | 14.696 | 0.078153 | 11.566 | 0.02393 |  | 1614 | 11.566 | 48.12 | 14.696 | 0.078153 | 0.02393
1615 | 48.13 | 14.696 | 0.078151 | 11.568 | 0.023934 |  | 1615 | 11.568 | 48.13 | 14.696 | 0.078151 | 0.023934
1616 | 48.14 | 14.696 | 0.07815 | 11.571 | 0.023939 |  | 1616 | 11.571 | 48.14 | 14.696 | 0.07815 | 0.023939
1617 | 48.15 | 14.696 | 0.078148 | 11.573 | 0.023944 |  | 1617 | 11.573 | 48.15 | 14.696 | 0.078148 | 0.023944
1618 | 48.16 | 14.696 | 0.078146 | 11.576 | 0.023948 |  | 1618 | 11.576 | 48.16 | 14.696 | 0.078146 | 0.023948
1619 | 48.17 | 14.696 | 0.078145 | 11.578 | 0.023953 |  | 1619 | 11.578 | 48.17 | 14.696 | 0.078145 | 0.023953
1620 | 48.18 | 14.696 | 0.078143 | 11.58 | 0.023958 |  | 1620 | 11.58 | 48.18 | 14.696 | 0.078143 | 0.023958
1621 | 48.19 | 14.696 | 0.078142 | 11.583 | 0.023963 |  | 1621 | 11.583 | 48.19 | 14.696 | 0.078142 | 0.023963
1622 | 48.2 | 14.696 | 0.07814 | 11.585 | 0.023967 |  | 1622 | 11.585 | 48.2 | 14.696 | 0.07814 | 0.023967
1623 | 48.21 | 14.696 | 0.078139 | 11.588 | 0.023972 |  | 1623 | 11.588 | 48.21 | 14.696 | 0.078139 | 0.023972
1624 | 48.22 | 14.696 | 0.078137 | 11.59 | 0.023977 |  | 1624 | 11.59 | 48.22 | 14.696 | 0.078137 | 0.023977
1625 | 48.23 | 14.696 | 0.078136 | 11.592 | 0.023982 |  | 1625 | 11.592 | 48.23 | 14.696 | 0.078136 | 0.023982
1626 | 48.24 | 14.696 | 0.078134 | 11.595 | 0.023986 |  | 1626 | 11.595 | 48.24 | 14.696 | 0.078134 | 0.023986
1627 | 48.25 | 14.696 | 0.078133 | 11.597 | 0.023991 |  | 1627 | 11.597 | 48.25 | 14.696 | 0.078133 | 0.023991
1628 | 48.26 | 14.696 | 0.078131 | 11.6 | 0.023996 |  | 1628 | 11.6 | 48.26 | 14.696 | 0.078131 | 0.023996
1629 | 48.27 | 14.696 | 0.078129 | 11.602 | 0.024001 |  | 1629 | 11.602 | 48.27 | 14.696 | 0.078129 | 0.024001
1630 | 48.28 | 14.696 | 0.078128 | 11.604 | 0.024005 |  | 1630 | 11.604 | 48.28 | 14.696 | 0.078128 | 0.024005
1631 | 48.29 | 14.696 | 0.078126 | 11.607 | 0.02401 |  | 1631 | 11.607 | 48.29 | 14.696 | 0.078126 | 0.02401
1632 | 48.3 | 14.696 | 0.078125 | 11.609 | 0.024015 |  | 1632 | 11.609 | 48.3 | 14.696 | 0.078125 | 0.024015
1633 | 48.31 | 14.696 | 0.078123 | 11.612 | 0.024019 |  | 1633 | 11.612 | 48.31 | 14.696 | 0.078123 | 0.024019
1634 | 48.32 | 14.696 | 0.078122 | 11.614 | 0.024024 |  | 1634 | 11.614 | 48.32 | 14.696 | 0.078122 | 0.024024
1635 | 48.33 | 14.696 | 0.07812 | 11.616 | 0.024029 |  | 1635 | 11.616 | 48.33 | 14.696 | 0.07812 | 0.024029
1636 | 48.34 | 14.696 | 0.078119 | 11.619 | 0.024034 |  | 1636 | 11.619 | 48.34 | 14.696 | 0.078119 | 0.024034
1637 | 48.35 | 14.696 | 0.078117 | 11.621 | 0.024038 |  | 1637 | 11.621 | 48.35 | 14.696 | 0.078117 | 0.024038
1638 | 48.36 | 14.696 | 0.078116 | 11.624 | 0.024043 |  | 1638 | 11.624 | 48.36 | 14.696 | 0.078116 | 0.024043
1639 | 48.37 | 14.696 | 0.078114 | 11.626 | 0.024048 |  | 1639 | 11.626 | 48.37 | 14.696 | 0.078114 | 0.024048
1640 | 48.38 | 14.696 | 0.078112 | 11.628 | 0.024053 |  | 1640 | 11.628 | 48.38 | 14.696 | 0.078112 | 0.024053
1641 | 48.39 | 14.696 | 0.078111 | 11.631 | 0.024057 |  | 1641 | 11.631 | 48.39 | 14.696 | 0.078111 | 0.024057
1642 | 48.4 | 14.696 | 0.078109 | 11.633 | 0.024062 |  | 1642 | 11.633 | 48.4 | 14.696 | 0.078109 | 0.024062
1643 | 48.41 | 14.696 | 0.078108 | 11.636 | 0.024067 |  | 1643 | 11.636 | 48.41 | 14.696 | 0.078108 | 0.024067
1644 | 48.42 | 14.696 | 0.078106 | 11.638 | 0.024072 |  | 1644 | 11.638 | 48.42 | 14.696 | 0.078106 | 0.024072
1645 | 48.43 | 14.696 | 0.078105 | 11.64 | 0.024076 |  | 1645 | 11.64 | 48.43 | 14.696 | 0.078105 | 0.024076
1646 | 48.44 | 14.696 | 0.078103 | 11.643 | 0.024081 |  | 1646 | 11.643 | 48.44 | 14.696 | 0.078103 | 0.024081
1647 | 48.45 | 14.696 | 0.078102 | 11.645 | 0.024086 |  | 1647 | 11.645 | 48.45 | 14.696 | 0.078102 | 0.024086
1648 | 48.46 | 14.696 | 0.0781 | 11.648 | 0.02409 |  | 1648 | 11.648 | 48.46 | 14.696 | 0.0781 | 0.02409
1649 | 48.47 | 14.696 | 0.078099 | 11.65 | 0.024095 |  | 1649 | 11.65 | 48.47 | 14.696 | 0.078099 | 0.024095
1650 | 48.48 | 14.696 | 0.078097 | 11.652 | 0.0241 |  | 1650 | 11.652 | 48.48 | 14.696 | 0.078097 | 0.0241
1651 | 48.49 | 14.696 | 0.078096 | 11.655 | 0.024105 |  | 1651 | 11.655 | 48.49 | 14.696 | 0.078096 | 0.024105
1652 | 48.5 | 14.696 | 0.078094 | 11.657 | 0.024109 |  | 1652 | 11.657 | 48.5 | 14.696 | 0.078094 | 0.024109
1653 | 48.51 | 14.696 | 0.078092 | 11.66 | 0.024114 |  | 1653 | 11.66 | 48.51 | 14.696 | 0.078092 | 0.024114
1654 | 48.52 | 14.696 | 0.078091 | 11.662 | 0.024119 |  | 1654 | 11.662 | 48.52 | 14.696 | 0.078091 | 0.024119
1655 | 48.53 | 14.696 | 0.078089 | 11.664 | 0.024124 |  | 1655 | 11.664 | 48.53 | 14.696 | 0.078089 | 0.024124
1656 | 48.54 | 14.696 | 0.078088 | 11.667 | 0.024128 |  | 1656 | 11.667 | 48.54 | 14.696 | 0.078088 | 0.024128
1657 | 48.55 | 14.696 | 0.078086 | 11.669 | 0.024133 |  | 1657 | 11.669 | 48.55 | 14.696 | 0.078086 | 0.024133
1658 | 48.56 | 14.696 | 0.078085 | 11.672 | 0.024138 |  | 1658 | 11.672 | 48.56 | 14.696 | 0.078085 | 0.024138
1659 | 48.57 | 14.696 | 0.078083 | 11.674 | 0.024142 |  | 1659 | 11.674 | 48.57 | 14.696 | 0.078083 | 0.024142
1660 | 48.58 | 14.696 | 0.078082 | 11.677 | 0.024147 |  | 1660 | 11.677 | 48.58 | 14.696 | 0.078082 | 0.024147
1661 | 48.59 | 14.696 | 0.07808 | 11.679 | 0.024152 |  | 1661 | 11.679 | 48.59 | 14.696 | 0.07808 | 0.024152
1662 | 48.6 | 14.696 | 0.078079 | 11.681 | 0.024157 |  | 1662 | 11.681 | 48.6 | 14.696 | 0.078079 | 0.024157
1663 | 48.61 | 14.696 | 0.078077 | 11.684 | 0.024161 |  | 1663 | 11.684 | 48.61 | 14.696 | 0.078077 | 0.024161
1664 | 48.62 | 14.696 | 0.078075 | 11.686 | 0.024166 |  | 1664 | 11.686 | 48.62 | 14.696 | 0.078075 | 0.024166
1665 | 48.63 | 14.696 | 0.078074 | 11.689 | 0.024171 |  | 1665 | 11.689 | 48.63 | 14.696 | 0.078074 | 0.024171
1666 | 48.64 | 14.696 | 0.078072 | 11.691 | 0.024176 |  | 1666 | 11.691 | 48.64 | 14.696 | 0.078072 | 0.024176
1667 | 48.65 | 14.696 | 0.078071 | 11.693 | 0.02418 |  | 1667 | 11.693 | 48.65 | 14.696 | 0.078071 | 0.02418
1668 | 48.66 | 14.696 | 0.078069 | 11.696 | 0.024185 |  | 1668 | 11.696 | 48.66 | 14.696 | 0.078069 | 0.024185
1669 | 48.67 | 14.696 | 0.078068 | 11.698 | 0.02419 |  | 1669 | 11.698 | 48.67 | 14.696 | 0.078068 | 0.02419
1670 | 48.68 | 14.696 | 0.078066 | 11.701 | 0.024195 |  | 1670 | 11.701 | 48.68 | 14.696 | 0.078066 | 0.024195
1671 | 48.69 | 14.696 | 0.078065 | 11.703 | 0.024199 |  | 1671 | 11.703 | 48.69 | 14.696 | 0.078065 | 0.024199
1672 | 48.7 | 14.696 | 0.078063 | 11.705 | 0.024204 |  | 1672 | 11.705 | 48.7 | 14.696 | 0.078063 | 0.024204
1673 | 48.71 | 14.696 | 0.078062 | 11.708 | 0.024209 |  | 1673 | 11.708 | 48.71 | 14.696 | 0.078062 | 0.024209
1674 | 48.72 | 14.696 | 0.07806 | 11.71 | 0.024213 |  | 1674 | 11.71 | 48.72 | 14.696 | 0.07806 | 0.024213
1675 | 48.73 | 14.696 | 0.078059 | 11.713 | 0.024218 |  | 1675 | 11.713 | 48.73 | 14.696 | 0.078059 | 0.024218
1676 | 48.74 | 14.696 | 0.078057 | 11.715 | 0.024223 |  | 1676 | 11.715 | 48.74 | 14.696 | 0.078057 | 0.024223
1677 | 48.75 | 14.696 | 0.078055 | 11.717 | 0.024228 |  | 1677 | 11.717 | 48.75 | 14.696 | 0.078055 | 0.024228
1678 | 48.76 | 14.696 | 0.078054 | 11.72 | 0.024232 |  | 1678 | 11.72 | 48.76 | 14.696 | 0.078054 | 0.024232
1679 | 48.77 | 14.696 | 0.078052 | 11.722 | 0.024237 |  | 1679 | 11.722 | 48.77 | 14.696 | 0.078052 | 0.024237
1680 | 48.78 | 14.696 | 0.078051 | 11.725 | 0.024242 |  | 1680 | 11.725 | 48.78 | 14.696 | 0.078051 | 0.024242
1681 | 48.79 | 14.696 | 0.078049 | 11.727 | 0.024247 |  | 1681 | 11.727 | 48.79 | 14.696 | 0.078049 | 0.024247
1682 | 48.8 | 14.696 | 0.078048 | 11.729 | 0.024251 |  | 1682 | 11.729 | 48.8 | 14.696 | 0.078048 | 0.024251
1683 | 48.81 | 14.696 | 0.078046 | 11.732 | 0.024256 |  | 1683 | 11.732 | 48.81 | 14.696 | 0.078046 | 0.024256
1684 | 48.82 | 14.696 | 0.078045 | 11.734 | 0.024261 |  | 1684 | 11.734 | 48.82 | 14.696 | 0.078045 | 0.024261
1685 | 48.83 | 14.696 | 0.078043 | 11.737 | 0.024265 |  | 1685 | 11.737 | 48.83 | 14.696 | 0.078043 | 0.024265
1686 | 48.84 | 14.696 | 0.078042 | 11.739 | 0.02427 |  | 1686 | 11.739 | 48.84 | 14.696 | 0.078042 | 0.02427
1687 | 48.85 | 14.696 | 0.07804 | 11.741 | 0.024275 |  | 1687 | 11.741 | 48.85 | 14.696 | 0.07804 | 0.024275
1688 | 48.86 | 14.696 | 0.078039 | 11.744 | 0.02428 |  | 1688 | 11.744 | 48.86 | 14.696 | 0.078039 | 0.02428
1689 | 48.87 | 14.696 | 0.078037 | 11.746 | 0.024284 |  | 1689 | 11.746 | 48.87 | 14.696 | 0.078037 | 0.024284
1690 | 48.88 | 14.696 | 0.078035 | 11.749 | 0.024289 |  | 1690 | 11.749 | 48.88 | 14.696 | 0.078035 | 0.024289
1691 | 48.89 | 14.696 | 0.078034 | 11.751 | 0.024294 |  | 1691 | 11.751 | 48.89 | 14.696 | 0.078034 | 0.024294
1692 | 48.9 | 14.696 | 0.078032 | 11.753 | 0.024299 |  | 1692 | 11.753 | 48.9 | 14.696 | 0.078032 | 0.024299
1693 | 48.91 | 14.696 | 0.078031 | 11.756 | 0.024303 |  | 1693 | 11.756 | 48.91 | 14.696 | 0.078031 | 0.024303
1694 | 48.92 | 14.696 | 0.078029 | 11.758 | 0.024308 |  | 1694 | 11.758 | 48.92 | 14.696 | 0.078029 | 0.024308
1695 | 48.93 | 14.696 | 0.078028 | 11.761 | 0.024313 |  | 1695 | 11.761 | 48.93 | 14.696 | 0.078028 | 0.024313
1696 | 48.94 | 14.696 | 0.078026 | 11.763 | 0.024317 |  | 1696 | 11.763 | 48.94 | 14.696 | 0.078026 | 0.024317
1697 | 48.95 | 14.696 | 0.078025 | 11.765 | 0.024322 |  | 1697 | 11.765 | 48.95 | 14.696 | 0.078025 | 0.024322
1698 | 48.96 | 14.696 | 0.078023 | 11.768 | 0.024327 |  | 1698 | 11.768 | 48.96 | 14.696 | 0.078023 | 0.024327
1699 | 48.97 | 14.696 | 0.078022 | 11.77 | 0.024332 |  | 1699 | 11.77 | 48.97 | 14.696 | 0.078022 | 0.024332
1700 | 48.98 | 14.696 | 0.07802 | 11.773 | 0.024336 |  | 1700 | 11.773 | 48.98 | 14.696 | 0.07802 | 0.024336
1701 | 48.99 | 14.696 | 0.078019 | 11.775 | 0.024341 |  | 1701 | 11.775 | 48.99 | 14.696 | 0.078019 | 0.024341
1702 | 49 | 14.696 | 0.078017 | 11.777 | 0.024346 |  | 1702 | 11.777 | 49 | 14.696 | 0.078017 | 0.024346
1703 | 49.01 | 14.696 | 0.078015 | 11.78 | 0.024351 |  | 1703 | 11.78 | 49.01 | 14.696 | 0.078015 | 0.024351
1704 | 49.02 | 14.696 | 0.078014 | 11.782 | 0.024355 |  | 1704 | 11.782 | 49.02 | 14.696 | 0.078014 | 0.024355
1705 | 49.03 | 14.696 | 0.078012 | 11.785 | 0.02436 |  | 1705 | 11.785 | 49.03 | 14.696 | 0.078012 | 0.02436
1706 | 49.04 | 14.696 | 0.078011 | 11.787 | 0.024365 |  | 1706 | 11.787 | 49.04 | 14.696 | 0.078011 | 0.024365
1707 | 49.05 | 14.696 | 0.078009 | 11.789 | 0.024369 |  | 1707 | 11.789 | 49.05 | 14.696 | 0.078009 | 0.024369
1708 | 49.06 | 14.696 | 0.078008 | 11.792 | 0.024374 |  | 1708 | 11.792 | 49.06 | 14.696 | 0.078008 | 0.024374
1709 | 49.07 | 14.696 | 0.078006 | 11.794 | 0.024379 |  | 1709 | 11.794 | 49.07 | 14.696 | 0.078006 | 0.024379
1710 | 49.08 | 14.696 | 0.078005 | 11.797 | 0.024384 |  | 1710 | 11.797 | 49.08 | 14.696 | 0.078005 | 0.024384
1711 | 49.09 | 14.696 | 0.078003 | 11.799 | 0.024388 |  | 1711 | 11.799 | 49.09 | 14.696 | 0.078003 | 0.024388
1712 | 49.1 | 14.696 | 0.078002 | 11.802 | 0.024393 |  | 1712 | 11.802 | 49.1 | 14.696 | 0.078002 | 0.024393
1713 | 49.11 | 14.696 | 0.078 | 11.804 | 0.024398 |  | 1713 | 11.804 | 49.11 | 14.696 | 0.078 | 0.024398
1714 | 49.12 | 14.696 | 0.077999 | 11.806 | 0.024403 |  | 1714 | 11.806 | 49.12 | 14.696 | 0.077999 | 0.024403
1715 | 49.13 | 14.696 | 0.077997 | 11.809 | 0.024407 |  | 1715 | 11.809 | 49.13 | 14.696 | 0.077997 | 0.024407
1716 | 49.14 | 14.696 | 0.077995 | 11.811 | 0.024412 |  | 1716 | 11.811 | 49.14 | 14.696 | 0.077995 | 0.024412
1717 | 49.15 | 14.696 | 0.077994 | 11.814 | 0.024417 |  | 1717 | 11.814 | 49.15 | 14.696 | 0.077994 | 0.024417
1718 | 49.16 | 14.696 | 0.077992 | 11.816 | 0.024421 |  | 1718 | 11.816 | 49.16 | 14.696 | 0.077992 | 0.024421
1719 | 49.17 | 14.696 | 0.077991 | 11.818 | 0.024426 |  | 1719 | 11.818 | 49.17 | 14.696 | 0.077991 | 0.024426
1720 | 49.18 | 14.696 | 0.077989 | 11.821 | 0.024431 |  | 1720 | 11.821 | 49.18 | 14.696 | 0.077989 | 0.024431
1721 | 49.19 | 14.696 | 0.077988 | 11.823 | 0.024436 |  | 1721 | 11.823 | 49.19 | 14.696 | 0.077988 | 0.024436
1722 | 49.2 | 14.696 | 0.077986 | 11.826 | 0.02444 |  | 1722 | 11.826 | 49.2 | 14.696 | 0.077986 | 0.02444
1723 | 49.21 | 14.696 | 0.077985 | 11.828 | 0.024445 |  | 1723 | 11.828 | 49.21 | 14.696 | 0.077985 | 0.024445
1724 | 49.22 | 14.696 | 0.077983 | 11.83 | 0.02445 |  | 1724 | 11.83 | 49.22 | 14.696 | 0.077983 | 0.02445
1725 | 49.23 | 14.696 | 0.077982 | 11.833 | 0.024454 |  | 1725 | 11.833 | 49.23 | 14.696 | 0.077982 | 0.024454
1726 | 49.24 | 14.696 | 0.07798 | 11.835 | 0.024459 |  | 1726 | 11.835 | 49.24 | 14.696 | 0.07798 | 0.024459
1727 | 49.25 | 14.696 | 0.077979 | 11.838 | 0.024464 |  | 1727 | 11.838 | 49.25 | 14.696 | 0.077979 | 0.024464
1728 | 49.26 | 14.696 | 0.077977 | 11.84 | 0.024469 |  | 1728 | 11.84 | 49.26 | 14.696 | 0.077977 | 0.024469
1729 | 49.27 | 14.696 | 0.077975 | 11.842 | 0.024473 |  | 1729 | 11.842 | 49.27 | 14.696 | 0.077975 | 0.024473
1730 | 49.28 | 14.696 | 0.077974 | 11.845 | 0.024478 |  | 1730 | 11.845 | 49.28 | 14.696 | 0.077974 | 0.024478
1731 | 49.29 | 14.696 | 0.077972 | 11.847 | 0.024483 |  | 1731 | 11.847 | 49.29 | 14.696 | 0.077972 | 0.024483
1732 | 49.3 | 14.696 | 0.077971 | 11.85 | 0.024488 |  | 1732 | 11.85 | 49.3 | 14.696 | 0.077971 | 0.024488
1733 | 49.31 | 14.696 | 0.077969 | 11.852 | 0.024492 |  | 1733 | 11.852 | 49.31 | 14.696 | 0.077969 | 0.024492
1734 | 49.32 | 14.696 | 0.077968 | 11.854 | 0.024497 |  | 1734 | 11.854 | 49.32 | 14.696 | 0.077968 | 0.024497
1735 | 49.33 | 14.696 | 0.077966 | 11.857 | 0.024502 |  | 1735 | 11.857 | 49.33 | 14.696 | 0.077966 | 0.024502
1736 | 49.34 | 14.696 | 0.077965 | 11.859 | 0.024506 |  | 1736 | 11.859 | 49.34 | 14.696 | 0.077965 | 0.024506
1737 | 49.35 | 14.696 | 0.077963 | 11.862 | 0.024511 |  | 1737 | 11.862 | 49.35 | 14.696 | 0.077963 | 0.024511
1738 | 49.36 | 14.696 | 0.077962 | 11.864 | 0.024516 |  | 1738 | 11.864 | 49.36 | 14.696 | 0.077962 | 0.024516
1739 | 49.37 | 14.696 | 0.07796 | 11.866 | 0.024521 |  | 1739 | 11.866 | 49.37 | 14.696 | 0.07796 | 0.024521
1740 | 49.38 | 14.696 | 0.077959 | 11.869 | 0.024525 |  | 1740 | 11.869 | 49.38 | 14.696 | 0.077959 | 0.024525
1741 | 49.39 | 14.696 | 0.077957 | 11.871 | 0.02453 |  | 1741 | 11.871 | 49.39 | 14.696 | 0.077957 | 0.02453
1742 | 49.4 | 14.696 | 0.077955 | 11.874 | 0.024535 |  | 1742 | 11.874 | 49.4 | 14.696 | 0.077955 | 0.024535
1743 | 49.41 | 14.696 | 0.077954 | 11.876 | 0.02454 |  | 1743 | 11.876 | 49.41 | 14.696 | 0.077954 | 0.02454
1744 | 49.42 | 14.696 | 0.077952 | 11.878 | 0.024544 |  | 1744 | 11.878 | 49.42 | 14.696 | 0.077952 | 0.024544
1745 | 49.43 | 14.696 | 0.077951 | 11.881 | 0.024549 |  | 1745 | 11.881 | 49.43 | 14.696 | 0.077951 | 0.024549
1746 | 49.44 | 14.696 | 0.077949 | 11.883 | 0.024554 |  | 1746 | 11.883 | 49.44 | 14.696 | 0.077949 | 0.024554
1747 | 49.45 | 14.696 | 0.077948 | 11.886 | 0.024558 |  | 1747 | 11.886 | 49.45 | 14.696 | 0.077948 | 0.024558
1748 | 49.46 | 14.696 | 0.077946 | 11.888 | 0.024563 |  | 1748 | 11.888 | 49.46 | 14.696 | 0.077946 | 0.024563
1749 | 49.47 | 14.696 | 0.077945 | 11.89 | 0.024568 |  | 1749 | 11.89 | 49.47 | 14.696 | 0.077945 | 0.024568
1750 | 49.48 | 14.696 | 0.077943 | 11.893 | 0.024573 |  | 1750 | 11.893 | 49.48 | 14.696 | 0.077943 | 0.024573
1751 | 49.49 | 14.696 | 0.077942 | 11.895 | 0.024577 |  | 1751 | 11.895 | 49.49 | 14.696 | 0.077942 | 0.024577
1752 | 49.5 | 14.696 | 0.07794 | 11.898 | 0.024582 |  | 1752 | 11.898 | 49.5 | 14.696 | 0.07794 | 0.024582
1753 | 49.51 | 14.696 | 0.077939 | 11.9 | 0.024587 |  | 1753 | 11.9 | 49.51 | 14.696 | 0.077939 | 0.024587
1754 | 49.52 | 14.696 | 0.077937 | 11.902 | 0.024591 |  | 1754 | 11.902 | 49.52 | 14.696 | 0.077937 | 0.024591
1755 | 49.53 | 14.696 | 0.077936 | 11.905 | 0.024596 |  | 1755 | 11.905 | 49.53 | 14.696 | 0.077936 | 0.024596
1756 | 49.54 | 14.696 | 0.077934 | 11.907 | 0.024601 |  | 1756 | 11.907 | 49.54 | 14.696 | 0.077934 | 0.024601
1757 | 49.55 | 14.696 | 0.077932 | 11.91 | 0.024606 |  | 1757 | 11.91 | 49.55 | 14.696 | 0.077932 | 0.024606
1758 | 49.56 | 14.696 | 0.077931 | 11.912 | 0.02461 |  | 1758 | 11.912 | 49.56 | 14.696 | 0.077931 | 0.02461
1759 | 49.57 | 14.696 | 0.077929 | 11.915 | 0.024615 |  | 1759 | 11.915 | 49.57 | 14.696 | 0.077929 | 0.024615
1760 | 49.58 | 14.696 | 0.077928 | 11.917 | 0.02462 |  | 1760 | 11.917 | 49.58 | 14.696 | 0.077928 | 0.02462
1761 | 49.59 | 14.696 | 0.077926 | 11.919 | 0.024624 |  | 1761 | 11.919 | 49.59 | 14.696 | 0.077926 | 0.024624
1762 | 49.6 | 14.696 | 0.077925 | 11.922 | 0.024629 |  | 1762 | 11.922 | 49.6 | 14.696 | 0.077925 | 0.024629
1763 | 49.61 | 14.696 | 0.077923 | 11.924 | 0.024634 |  | 1763 | 11.924 | 49.61 | 14.696 | 0.077923 | 0.024634
1764 | 49.62 | 14.696 | 0.077922 | 11.927 | 0.024639 |  | 1764 | 11.927 | 49.62 | 14.696 | 0.077922 | 0.024639
1765 | 49.63 | 14.696 | 0.07792 | 11.929 | 0.024643 |  | 1765 | 11.929 | 49.63 | 14.696 | 0.07792 | 0.024643
1766 | 49.64 | 14.696 | 0.077919 | 11.931 | 0.024648 |  | 1766 | 11.931 | 49.64 | 14.696 | 0.077919 | 0.024648
1767 | 49.65 | 14.696 | 0.077917 | 11.934 | 0.024653 |  | 1767 | 11.934 | 49.65 | 14.696 | 0.077917 | 0.024653
1768 | 49.66 | 14.696 | 0.077916 | 11.936 | 0.024658 |  | 1768 | 11.936 | 49.66 | 14.696 | 0.077916 | 0.024658
1769 | 49.67 | 14.696 | 0.077914 | 11.939 | 0.024662 |  | 1769 | 11.939 | 49.67 | 14.696 | 0.077914 | 0.024662
1770 | 49.68 | 14.696 | 0.077912 | 11.941 | 0.024667 |  | 1770 | 11.941 | 49.68 | 14.696 | 0.077912 | 0.024667
1771 | 49.69 | 14.696 | 0.077911 | 11.943 | 0.024672 |  | 1771 | 11.943 | 49.69 | 14.696 | 0.077911 | 0.024672
1772 | 49.7 | 14.696 | 0.077909 | 11.946 | 0.024676 |  | 1772 | 11.946 | 49.7 | 14.696 | 0.077909 | 0.024676
1773 | 49.71 | 14.696 | 0.077908 | 11.948 | 0.024681 |  | 1773 | 11.948 | 49.71 | 14.696 | 0.077908 | 0.024681
1774 | 49.72 | 14.696 | 0.077906 | 11.951 | 0.024686 |  | 1774 | 11.951 | 49.72 | 14.696 | 0.077906 | 0.024686
1775 | 49.73 | 14.696 | 0.077905 | 11.953 | 0.024691 |  | 1775 | 11.953 | 49.73 | 14.696 | 0.077905 | 0.024691
1776 | 49.74 | 14.696 | 0.077903 | 11.955 | 0.024695 |  | 1776 | 11.955 | 49.74 | 14.696 | 0.077903 | 0.024695
1777 | 49.75 | 14.696 | 0.077902 | 11.958 | 0.0247 |  | 1777 | 11.958 | 49.75 | 14.696 | 0.077902 | 0.0247
1778 | 49.76 | 14.696 | 0.0779 | 11.96 | 0.024705 |  | 1778 | 11.96 | 49.76 | 14.696 | 0.0779 | 0.024705
1779 | 49.77 | 14.696 | 0.077899 | 11.963 | 0.024709 |  | 1779 | 11.963 | 49.77 | 14.696 | 0.077899 | 0.024709
1780 | 49.78 | 14.696 | 0.077897 | 11.965 | 0.024714 |  | 1780 | 11.965 | 49.78 | 14.696 | 0.077897 | 0.024714
1781 | 49.79 | 14.696 | 0.077896 | 11.967 | 0.024719 |  | 1781 | 11.967 | 49.79 | 14.696 | 0.077896 | 0.024719
1782 | 49.8 | 14.696 | 0.077894 | 11.97 | 0.024724 |  | 1782 | 11.97 | 49.8 | 14.696 | 0.077894 | 0.024724
1783 | 49.81 | 14.696 | 0.077893 | 11.972 | 0.024728 |  | 1783 | 11.972 | 49.81 | 14.696 | 0.077893 | 0.024728
1784 | 49.82 | 14.696 | 0.077891 | 11.975 | 0.024733 |  | 1784 | 11.975 | 49.82 | 14.696 | 0.077891 | 0.024733
1785 | 49.83 | 14.696 | 0.077889 | 11.977 | 0.024738 |  | 1785 | 11.977 | 49.83 | 14.696 | 0.077889 | 0.024738
1786 | 49.84 | 14.696 | 0.077888 | 11.979 | 0.024742 |  | 1786 | 11.979 | 49.84 | 14.696 | 0.077888 | 0.024742
1787 | 49.85 | 14.696 | 0.077886 | 11.982 | 0.024747 |  | 1787 | 11.982 | 49.85 | 14.696 | 0.077886 | 0.024747
1788 | 49.86 | 14.696 | 0.077885 | 11.984 | 0.024752 |  | 1788 | 11.984 | 49.86 | 14.696 | 0.077885 | 0.024752
1789 | 49.87 | 14.696 | 0.077883 | 11.987 | 0.024757 |  | 1789 | 11.987 | 49.87 | 14.696 | 0.077883 | 0.024757
1790 | 49.88 | 14.696 | 0.077882 | 11.989 | 0.024761 |  | 1790 | 11.989 | 49.88 | 14.696 | 0.077882 | 0.024761
1791 | 49.89 | 14.696 | 0.07788 | 11.991 | 0.024766 |  | 1791 | 11.991 | 49.89 | 14.696 | 0.07788 | 0.024766
1792 | 49.9 | 14.696 | 0.077879 | 11.994 | 0.024771 |  | 1792 | 11.994 | 49.9 | 14.696 | 0.077879 | 0.024771
1793 | 49.91 | 14.696 | 0.077877 | 11.996 | 0.024776 |  | 1793 | 11.996 | 49.91 | 14.696 | 0.077877 | 0.024776
1794 | 49.92 | 14.696 | 0.077876 | 11.999 | 0.02478 |  | 1794 | 11.999 | 49.92 | 14.696 | 0.077876 | 0.02478
1795 | 49.93 | 14.696 | 0.077874 | 12.001 | 0.024785 |  | 1795 | 12.001 | 49.93 | 14.696 | 0.077874 | 0.024785
1796 | 49.94 | 14.696 | 0.077873 | 12.003 | 0.02479 |  | 1796 | 12.003 | 49.94 | 14.696 | 0.077873 | 0.02479
1797 | 49.95 | 14.696 | 0.077871 | 12.006 | 0.024794 |  | 1797 | 12.006 | 49.95 | 14.696 | 0.077871 | 0.024794
1798 | 49.96 | 14.696 | 0.07787 | 12.008 | 0.024799 |  | 1798 | 12.008 | 49.96 | 14.696 | 0.07787 | 0.024799
1799 | 49.97 | 14.696 | 0.077868 | 12.011 | 0.024804 |  | 1799 | 12.011 | 49.97 | 14.696 | 0.077868 | 0.024804
1800 | 49.98 | 14.696 | 0.077866 | 12.013 | 0.024809 |  | 1800 | 12.013 | 49.98 | 14.696 | 0.077866 | 0.024809
1801 | 49.99 | 14.696 | 0.077865 | 12.015 | 0.024813 |  | 1801 | 12.015 | 49.99 | 14.696 | 0.077865 | 0.024813
1802 | 50 | 14.696 | 0.077863 | 12.018 | 0.024818 |  | 1802 | 12.018 | 50 | 14.696 | 0.077863 | 0.024818
1803 | 50.01 | 14.696 | 0.077862 | 12.02 | 0.024823 |  | 1803 | 12.02 | 50.01 | 14.696 | 0.077862 | 0.024823
1804 | 50.02 | 14.696 | 0.07786 | 12.023 | 0.024827 |  | 1804 | 12.023 | 50.02 | 14.696 | 0.07786 | 0.024827
1805 | 50.03 | 14.696 | 0.077859 | 12.025 | 0.024832 |  | 1805 | 12.025 | 50.03 | 14.696 | 0.077859 | 0.024832
1806 | 50.04 | 14.696 | 0.077857 | 12.027 | 0.024837 |  | 1806 | 12.027 | 50.04 | 14.696 | 0.077857 | 0.024837
1807 | 50.05 | 14.696 | 0.077856 | 12.03 | 0.024842 |  | 1807 | 12.03 | 50.05 | 14.696 | 0.077856 | 0.024842
1808 | 50.06 | 14.696 | 0.077854 | 12.032 | 0.024846 |  | 1808 | 12.032 | 50.06 | 14.696 | 0.077854 | 0.024846
1809 | 50.07 | 14.696 | 0.077853 | 12.035 | 0.024851 |  | 1809 | 12.035 | 50.07 | 14.696 | 0.077853 | 0.024851
1810 | 50.08 | 14.696 | 0.077851 | 12.037 | 0.024856 |  | 1810 | 12.037 | 50.08 | 14.696 | 0.077851 | 0.024856
1811 | 50.09 | 14.696 | 0.07785 | 12.04 | 0.02486 |  | 1811 | 12.04 | 50.09 | 14.696 | 0.07785 | 0.02486
1812 | 50.1 | 14.696 | 0.077848 | 12.042 | 0.024865 |  | 1812 | 12.042 | 50.1 | 14.696 | 0.077848 | 0.024865
1813 | 50.11 | 14.696 | 0.077847 | 12.044 | 0.02487 |  | 1813 | 12.044 | 50.11 | 14.696 | 0.077847 | 0.02487
1814 | 50.12 | 14.696 | 0.077845 | 12.047 | 0.024875 |  | 1814 | 12.047 | 50.12 | 14.696 | 0.077845 | 0.024875
1815 | 50.13 | 14.696 | 0.077843 | 12.049 | 0.024879 |  | 1815 | 12.049 | 50.13 | 14.696 | 0.077843 | 0.024879
1816 | 50.14 | 14.696 | 0.077842 | 12.052 | 0.024884 |  | 1816 | 12.052 | 50.14 | 14.696 | 0.077842 | 0.024884
1817 | 50.15 | 14.696 | 0.07784 | 12.054 | 0.024889 |  | 1817 | 12.054 | 50.15 | 14.696 | 0.07784 | 0.024889
1818 | 50.16 | 14.696 | 0.077839 | 12.056 | 0.024893 |  | 1818 | 12.056 | 50.16 | 14.696 | 0.077839 | 0.024893
1819 | 50.17 | 14.696 | 0.077837 | 12.059 | 0.024898 |  | 1819 | 12.059 | 50.17 | 14.696 | 0.077837 | 0.024898
1820 | 50.18 | 14.696 | 0.077836 | 12.061 | 0.024903 |  | 1820 | 12.061 | 50.18 | 14.696 | 0.077836 | 0.024903
1821 | 50.19 | 14.696 | 0.077834 | 12.064 | 0.024908 |  | 1821 | 12.064 | 50.19 | 14.696 | 0.077834 | 0.024908
1822 | 50.2 | 14.696 | 0.077833 | 12.066 | 0.024912 |  | 1822 | 12.066 | 50.2 | 14.696 | 0.077833 | 0.024912
1823 | 50.21 | 14.696 | 0.077831 | 12.068 | 0.024917 |  | 1823 | 12.068 | 50.21 | 14.696 | 0.077831 | 0.024917
1824 | 50.22 | 14.696 | 0.07783 | 12.071 | 0.024922 |  | 1824 | 12.071 | 50.22 | 14.696 | 0.07783 | 0.024922
1825 | 50.23 | 14.696 | 0.077828 | 12.073 | 0.024926 |  | 1825 | 12.073 | 50.23 | 14.696 | 0.077828 | 0.024926
1826 | 50.24 | 14.696 | 0.077827 | 12.076 | 0.024931 |  | 1826 | 12.076 | 50.24 | 14.696 | 0.077827 | 0.024931
1827 | 50.25 | 14.696 | 0.077825 | 12.078 | 0.024936 |  | 1827 | 12.078 | 50.25 | 14.696 | 0.077825 | 0.024936
1828 | 50.26 | 14.696 | 0.077824 | 12.08 | 0.024941 |  | 1828 | 12.08 | 50.26 | 14.696 | 0.077824 | 0.024941
1829 | 50.27 | 14.696 | 0.077822 | 12.083 | 0.024945 |  | 1829 | 12.083 | 50.27 | 14.696 | 0.077822 | 0.024945
1830 | 50.28 | 14.696 | 0.077821 | 12.085 | 0.02495 |  | 1830 | 12.085 | 50.28 | 14.696 | 0.077821 | 0.02495
1831 | 50.29 | 14.696 | 0.077819 | 12.088 | 0.024955 |  | 1831 | 12.088 | 50.29 | 14.696 | 0.077819 | 0.024955
1832 | 50.3 | 14.696 | 0.077817 | 12.09 | 0.024959 |  | 1832 | 12.09 | 50.3 | 14.696 | 0.077817 | 0.024959
1833 | 50.31 | 14.696 | 0.077816 | 12.092 | 0.024964 |  | 1833 | 12.092 | 50.31 | 14.696 | 0.077816 | 0.024964
1834 | 50.32 | 14.696 | 0.077814 | 12.095 | 0.024969 |  | 1834 | 12.095 | 50.32 | 14.696 | 0.077814 | 0.024969
1835 | 50.33 | 14.696 | 0.077813 | 12.097 | 0.024974 |  | 1835 | 12.097 | 50.33 | 14.696 | 0.077813 | 0.024974
1836 | 50.34 | 14.696 | 0.077811 | 12.1 | 0.024978 |  | 1836 | 12.1 | 50.34 | 14.696 | 0.077811 | 0.024978
1837 | 50.35 | 14.696 | 0.07781 | 12.102 | 0.024983 |  | 1837 | 12.102 | 50.35 | 14.696 | 0.07781 | 0.024983
1838 | 50.36 | 14.696 | 0.077808 | 12.104 | 0.024988 |  | 1838 | 12.104 | 50.36 | 14.696 | 0.077808 | 0.024988
1839 | 50.37 | 14.696 | 0.077807 | 12.107 | 0.024992 |  | 1839 | 12.107 | 50.37 | 14.696 | 0.077807 | 0.024992
1840 | 50.38 | 14.696 | 0.077805 | 12.109 | 0.024997 |  | 1840 | 12.109 | 50.38 | 14.696 | 0.077805 | 0.024997
1841 | 50.39 | 14.696 | 0.077804 | 12.112 | 0.025002 |  | 1841 | 12.112 | 50.39 | 14.696 | 0.077804 | 0.025002
1842 | 50.4 | 14.696 | 0.077802 | 12.114 | 0.025007 |  | 1842 | 12.114 | 50.4 | 14.696 | 0.077802 | 0.025007
1843 | 50.41 | 14.696 | 0.077801 | 12.116 | 0.025011 |  | 1843 | 12.116 | 50.41 | 14.696 | 0.077801 | 0.025011
1844 | 50.42 | 14.696 | 0.077799 | 12.119 | 0.025016 |  | 1844 | 12.119 | 50.42 | 14.696 | 0.077799 | 0.025016
1845 | 50.43 | 14.696 | 0.077798 | 12.121 | 0.025021 |  | 1845 | 12.121 | 50.43 | 14.696 | 0.077798 | 0.025021
1846 | 50.44 | 14.696 | 0.077796 | 12.124 | 0.025025 |  | 1846 | 12.124 | 50.44 | 14.696 | 0.077796 | 0.025025
1847 | 50.45 | 14.696 | 0.077795 | 12.126 | 0.02503 |  | 1847 | 12.126 | 50.45 | 14.696 | 0.077795 | 0.02503
1848 | 50.46 | 14.696 | 0.077793 | 12.128 | 0.025035 |  | 1848 | 12.128 | 50.46 | 14.696 | 0.077793 | 0.025035
1849 | 50.47 | 14.696 | 0.077791 | 12.131 | 0.02504 |  | 1849 | 12.131 | 50.47 | 14.696 | 0.077791 | 0.02504
1850 | 50.48 | 14.696 | 0.07779 | 12.133 | 0.025044 |  | 1850 | 12.133 | 50.48 | 14.696 | 0.07779 | 0.025044
1851 | 50.49 | 14.696 | 0.077788 | 12.136 | 0.025049 |  | 1851 | 12.136 | 50.49 | 14.696 | 0.077788 | 0.025049
1852 | 50.5 | 14.696 | 0.077787 | 12.138 | 0.025054 |  | 1852 | 12.138 | 50.5 | 14.696 | 0.077787 | 0.025054
1853 | 50.51 | 14.696 | 0.077785 | 12.14 | 0.025058 |  | 1853 | 12.14 | 50.51 | 14.696 | 0.077785 | 0.025058
1854 | 50.52 | 14.696 | 0.077784 | 12.143 | 0.025063 |  | 1854 | 12.143 | 50.52 | 14.696 | 0.077784 | 0.025063
1855 | 50.53 | 14.696 | 0.077782 | 12.145 | 0.025068 |  | 1855 | 12.145 | 50.53 | 14.696 | 0.077782 | 0.025068
1856 | 50.54 | 14.696 | 0.077781 | 12.148 | 0.025073 |  | 1856 | 12.148 | 50.54 | 14.696 | 0.077781 | 0.025073
1857 | 50.55 | 14.696 | 0.077779 | 12.15 | 0.025077 |  | 1857 | 12.15 | 50.55 | 14.696 | 0.077779 | 0.025077
1858 | 50.56 | 14.696 | 0.077778 | 12.153 | 0.025082 |  | 1858 | 12.153 | 50.56 | 14.696 | 0.077778 | 0.025082
1859 | 50.57 | 14.696 | 0.077776 | 12.155 | 0.025087 |  | 1859 | 12.155 | 50.57 | 14.696 | 0.077776 | 0.025087
1860 | 50.58 | 14.696 | 0.077775 | 12.157 | 0.025091 |  | 1860 | 12.157 | 50.58 | 14.696 | 0.077775 | 0.025091
1861 | 50.59 | 14.696 | 0.077773 | 12.16 | 0.025096 |  | 1861 | 12.16 | 50.59 | 14.696 | 0.077773 | 0.025096
1862 | 50.6 | 14.696 | 0.077772 | 12.162 | 0.025101 |  | 1862 | 12.162 | 50.6 | 14.696 | 0.077772 | 0.025101
1863 | 50.61 | 14.696 | 0.07777 | 12.165 | 0.025106 |  | 1863 | 12.165 | 50.61 | 14.696 | 0.07777 | 0.025106
1864 | 50.62 | 14.696 | 0.077769 | 12.167 | 0.02511 |  | 1864 | 12.167 | 50.62 | 14.696 | 0.077769 | 0.02511
1865 | 50.63 | 14.696 | 0.077767 | 12.169 | 0.025115 |  | 1865 | 12.169 | 50.63 | 14.696 | 0.077767 | 0.025115
1866 | 50.64 | 14.696 | 0.077765 | 12.172 | 0.02512 |  | 1866 | 12.172 | 50.64 | 14.696 | 0.077765 | 0.02512
1867 | 50.65 | 14.696 | 0.077764 | 12.174 | 0.025124 |  | 1867 | 12.174 | 50.65 | 14.696 | 0.077764 | 0.025124
1868 | 50.66 | 14.696 | 0.077762 | 12.177 | 0.025129 |  | 1868 | 12.177 | 50.66 | 14.696 | 0.077762 | 0.025129
1869 | 50.67 | 14.696 | 0.077761 | 12.179 | 0.025134 |  | 1869 | 12.179 | 50.67 | 14.696 | 0.077761 | 0.025134
1870 | 50.68 | 14.696 | 0.077759 | 12.181 | 0.025139 |  | 1870 | 12.181 | 50.68 | 14.696 | 0.077759 | 0.025139
1871 | 50.69 | 14.696 | 0.077758 | 12.184 | 0.025143 |  | 1871 | 12.184 | 50.69 | 14.696 | 0.077758 | 0.025143
1872 | 50.7 | 14.696 | 0.077756 | 12.186 | 0.025148 |  | 1872 | 12.186 | 50.7 | 14.696 | 0.077756 | 0.025148
1873 | 50.71 | 14.696 | 0.077755 | 12.189 | 0.025153 |  | 1873 | 12.189 | 50.71 | 14.696 | 0.077755 | 0.025153
1874 | 50.72 | 14.696 | 0.077753 | 12.191 | 0.025157 |  | 1874 | 12.191 | 50.72 | 14.696 | 0.077753 | 0.025157
1875 | 50.73 | 14.696 | 0.077752 | 12.193 | 0.025162 |  | 1875 | 12.193 | 50.73 | 14.696 | 0.077752 | 0.025162
1876 | 50.74 | 14.696 | 0.07775 | 12.196 | 0.025167 |  | 1876 | 12.196 | 50.74 | 14.696 | 0.07775 | 0.025167
1877 | 50.75 | 14.696 | 0.077749 | 12.198 | 0.025171 |  | 1877 | 12.198 | 50.75 | 14.696 | 0.077749 | 0.025171
1878 | 50.76 | 14.696 | 0.077747 | 12.201 | 0.025176 |  | 1878 | 12.201 | 50.76 | 14.696 | 0.077747 | 0.025176
1879 | 50.77 | 14.696 | 0.077746 | 12.203 | 0.025181 |  | 1879 | 12.203 | 50.77 | 14.696 | 0.077746 | 0.025181
1880 | 50.78 | 14.696 | 0.077744 | 12.205 | 0.025186 |  | 1880 | 12.205 | 50.78 | 14.696 | 0.077744 | 0.025186
1881 | 50.79 | 14.696 | 0.077743 | 12.208 | 0.02519 |  | 1881 | 12.208 | 50.79 | 14.696 | 0.077743 | 0.02519
1882 | 50.8 | 14.696 | 0.077741 | 12.21 | 0.025195 |  | 1882 | 12.21 | 50.8 | 14.696 | 0.077741 | 0.025195
1883 | 50.81 | 14.696 | 0.077739 | 12.213 | 0.0252 |  | 1883 | 12.213 | 50.81 | 14.696 | 0.077739 | 0.0252
1884 | 50.82 | 14.696 | 0.077738 | 12.215 | 0.025204 |  | 1884 | 12.215 | 50.82 | 14.696 | 0.077738 | 0.025204
1885 | 50.83 | 14.696 | 0.077736 | 12.217 | 0.025209 |  | 1885 | 12.217 | 50.83 | 14.696 | 0.077736 | 0.025209
1886 | 50.84 | 14.696 | 0.077735 | 12.22 | 0.025214 |  | 1886 | 12.22 | 50.84 | 14.696 | 0.077735 | 0.025214
1887 | 50.85 | 14.696 | 0.077733 | 12.222 | 0.025219 |  | 1887 | 12.222 | 50.85 | 14.696 | 0.077733 | 0.025219
1888 | 50.86 | 14.696 | 0.077732 | 12.225 | 0.025223 |  | 1888 | 12.225 | 50.86 | 14.696 | 0.077732 | 0.025223
1889 | 50.87 | 14.696 | 0.07773 | 12.227 | 0.025228 |  | 1889 | 12.227 | 50.87 | 14.696 | 0.07773 | 0.025228
1890 | 50.88 | 14.696 | 0.077729 | 12.229 | 0.025233 |  | 1890 | 12.229 | 50.88 | 14.696 | 0.077729 | 0.025233
1891 | 50.89 | 14.696 | 0.077727 | 12.232 | 0.025237 |  | 1891 | 12.232 | 50.89 | 14.696 | 0.077727 | 0.025237
1892 | 50.9 | 14.696 | 0.077726 | 12.234 | 0.025242 |  | 1892 | 12.234 | 50.9 | 14.696 | 0.077726 | 0.025242
1893 | 50.91 | 14.696 | 0.077724 | 12.237 | 0.025247 |  | 1893 | 12.237 | 50.91 | 14.696 | 0.077724 | 0.025247
1894 | 50.92 | 14.696 | 0.077723 | 12.239 | 0.025252 |  | 1894 | 12.239 | 50.92 | 14.696 | 0.077723 | 0.025252
1895 | 50.93 | 14.696 | 0.077721 | 12.241 | 0.025256 |  | 1895 | 12.241 | 50.93 | 14.696 | 0.077721 | 0.025256
1896 | 50.94 | 14.696 | 0.07772 | 12.244 | 0.025261 |  | 1896 | 12.244 | 50.94 | 14.696 | 0.07772 | 0.025261
1897 | 50.95 | 14.696 | 0.077718 | 12.246 | 0.025266 |  | 1897 | 12.246 | 50.95 | 14.696 | 0.077718 | 0.025266
1898 | 50.96 | 14.696 | 0.077717 | 12.249 | 0.02527 |  | 1898 | 12.249 | 50.96 | 14.696 | 0.077717 | 0.02527
1899 | 50.97 | 14.696 | 0.077715 | 12.251 | 0.025275 |  | 1899 | 12.251 | 50.97 | 14.696 | 0.077715 | 0.025275
1900 | 50.98 | 14.696 | 0.077714 | 12.253 | 0.02528 |  | 1900 | 12.253 | 50.98 | 14.696 | 0.077714 | 0.02528
1901 | 50.99 | 14.696 | 0.077712 | 12.256 | 0.025284 |  | 1901 | 12.256 | 50.99 | 14.696 | 0.077712 | 0.025284
1902 | 51 | 14.696 | 0.07771 | 12.258 | 0.025289 |  | 1902 | 12.258 | 51 | 14.696 | 0.07771 | 0.025289
1903 | 51.01 | 14.696 | 0.077709 | 12.261 | 0.025294 |  | 1903 | 12.261 | 51.01 | 14.696 | 0.077709 | 0.025294
1904 | 51.02 | 14.696 | 0.077707 | 12.263 | 0.025299 |  | 1904 | 12.263 | 51.02 | 14.696 | 0.077707 | 0.025299
1905 | 51.03 | 14.696 | 0.077706 | 12.266 | 0.025303 |  | 1905 | 12.266 | 51.03 | 14.696 | 0.077706 | 0.025303
1906 | 51.04 | 14.696 | 0.077704 | 12.268 | 0.025308 |  | 1906 | 12.268 | 51.04 | 14.696 | 0.077704 | 0.025308
1907 | 51.05 | 14.696 | 0.077703 | 12.27 | 0.025313 |  | 1907 | 12.27 | 51.05 | 14.696 | 0.077703 | 0.025313
1908 | 51.06 | 14.696 | 0.077701 | 12.273 | 0.025317 |  | 1908 | 12.273 | 51.06 | 14.696 | 0.077701 | 0.025317
1909 | 51.07 | 14.696 | 0.0777 | 12.275 | 0.025322 |  | 1909 | 12.275 | 51.07 | 14.696 | 0.0777 | 0.025322
1910 | 51.08 | 14.696 | 0.077698 | 12.278 | 0.025327 |  | 1910 | 12.278 | 51.08 | 14.696 | 0.077698 | 0.025327
1911 | 51.09 | 14.696 | 0.077697 | 12.28 | 0.025332 |  | 1911 | 12.28 | 51.09 | 14.696 | 0.077697 | 0.025332
1912 | 51.1 | 14.696 | 0.077695 | 12.282 | 0.025336 |  | 1912 | 12.282 | 51.1 | 14.696 | 0.077695 | 0.025336
1913 | 51.11 | 14.696 | 0.077694 | 12.285 | 0.025341 |  | 1913 | 12.285 | 51.11 | 14.696 | 0.077694 | 0.025341
1914 | 51.12 | 14.696 | 0.077692 | 12.287 | 0.025346 |  | 1914 | 12.287 | 51.12 | 14.696 | 0.077692 | 0.025346
1915 | 51.13 | 14.696 | 0.077691 | 12.29 | 0.02535 |  | 1915 | 12.29 | 51.13 | 14.696 | 0.077691 | 0.02535
1916 | 51.14 | 14.696 | 0.077689 | 12.292 | 0.025355 |  | 1916 | 12.292 | 51.14 | 14.696 | 0.077689 | 0.025355
1917 | 51.15 | 14.696 | 0.077688 | 12.294 | 0.02536 |  | 1917 | 12.294 | 51.15 | 14.696 | 0.077688 | 0.02536
1918 | 51.16 | 14.696 | 0.077686 | 12.297 | 0.025365 |  | 1918 | 12.297 | 51.16 | 14.696 | 0.077686 | 0.025365
1919 | 51.17 | 14.696 | 0.077685 | 12.299 | 0.025369 |  | 1919 | 12.299 | 51.17 | 14.696 | 0.077685 | 0.025369
1920 | 51.18 | 14.696 | 0.077683 | 12.302 | 0.025374 |  | 1920 | 12.302 | 51.18 | 14.696 | 0.077683 | 0.025374
1921 | 51.19 | 14.696 | 0.077681 | 12.304 | 0.025379 |  | 1921 | 12.304 | 51.19 | 14.696 | 0.077681 | 0.025379
1922 | 51.2 | 14.696 | 0.07768 | 12.306 | 0.025383 |  | 1922 | 12.306 | 51.2 | 14.696 | 0.07768 | 0.025383
1923 | 51.21 | 14.696 | 0.077678 | 12.309 | 0.025388 |  | 1923 | 12.309 | 51.21 | 14.696 | 0.077678 | 0.025388
1924 | 51.22 | 14.696 | 0.077677 | 12.311 | 0.025393 |  | 1924 | 12.311 | 51.22 | 14.696 | 0.077677 | 0.025393
1925 | 51.23 | 14.696 | 0.077675 | 12.314 | 0.025397 |  | 1925 | 12.314 | 51.23 | 14.696 | 0.077675 | 0.025397
1926 | 51.24 | 14.696 | 0.077674 | 12.316 | 0.025402 |  | 1926 | 12.316 | 51.24 | 14.696 | 0.077674 | 0.025402
1927 | 51.25 | 14.696 | 0.077672 | 12.318 | 0.025407 |  | 1927 | 12.318 | 51.25 | 14.696 | 0.077672 | 0.025407
1928 | 51.26 | 14.696 | 0.077671 | 12.321 | 0.025412 |  | 1928 | 12.321 | 51.26 | 14.696 | 0.077671 | 0.025412
1929 | 51.27 | 14.696 | 0.077669 | 12.323 | 0.025416 |  | 1929 | 12.323 | 51.27 | 14.696 | 0.077669 | 0.025416
1930 | 51.28 | 14.696 | 0.077668 | 12.326 | 0.025421 |  | 1930 | 12.326 | 51.28 | 14.696 | 0.077668 | 0.025421
1931 | 51.29 | 14.696 | 0.077666 | 12.328 | 0.025426 |  | 1931 | 12.328 | 51.29 | 14.696 | 0.077666 | 0.025426
1932 | 51.3 | 14.696 | 0.077665 | 12.33 | 0.02543 |  | 1932 | 12.33 | 51.3 | 14.696 | 0.077665 | 0.02543
1933 | 51.31 | 14.696 | 0.077663 | 12.333 | 0.025435 |  | 1933 | 12.333 | 51.31 | 14.696 | 0.077663 | 0.025435
1934 | 51.32 | 14.696 | 0.077662 | 12.335 | 0.02544 |  | 1934 | 12.335 | 51.32 | 14.696 | 0.077662 | 0.02544
1935 | 51.33 | 14.696 | 0.07766 | 12.338 | 0.025445 |  | 1935 | 12.338 | 51.33 | 14.696 | 0.07766 | 0.025445
1936 | 51.34 | 14.696 | 0.077659 | 12.34 | 0.025449 |  | 1936 | 12.34 | 51.34 | 14.696 | 0.077659 | 0.025449
1937 | 51.35 | 14.696 | 0.077657 | 12.342 | 0.025454 |  | 1937 | 12.342 | 51.35 | 14.696 | 0.077657 | 0.025454
1938 | 51.36 | 14.696 | 0.077656 | 12.345 | 0.025459 |  | 1938 | 12.345 | 51.36 | 14.696 | 0.077656 | 0.025459
1939 | 51.37 | 14.696 | 0.077654 | 12.347 | 0.025463 |  | 1939 | 12.347 | 51.37 | 14.696 | 0.077654 | 0.025463
1940 | 51.38 | 14.696 | 0.077652 | 12.35 | 0.025468 |  | 1940 | 12.35 | 51.38 | 14.696 | 0.077652 | 0.025468
1941 | 51.39 | 14.696 | 0.077651 | 12.352 | 0.025473 |  | 1941 | 12.352 | 51.39 | 14.696 | 0.077651 | 0.025473
1942 | 51.4 | 14.696 | 0.077649 | 12.354 | 0.025477 |  | 1942 | 12.354 | 51.4 | 14.696 | 0.077649 | 0.025477
1943 | 51.41 | 14.696 | 0.077648 | 12.357 | 0.025482 |  | 1943 | 12.357 | 51.41 | 14.696 | 0.077648 | 0.025482
1944 | 51.42 | 14.696 | 0.077646 | 12.359 | 0.025487 |  | 1944 | 12.359 | 51.42 | 14.696 | 0.077646 | 0.025487
1945 | 51.43 | 14.696 | 0.077645 | 12.362 | 0.025492 |  | 1945 | 12.362 | 51.43 | 14.696 | 0.077645 | 0.025492
1946 | 51.44 | 14.696 | 0.077643 | 12.364 | 0.025496 |  | 1946 | 12.364 | 51.44 | 14.696 | 0.077643 | 0.025496
1947 | 51.45 | 14.696 | 0.077642 | 12.366 | 0.025501 |  | 1947 | 12.366 | 51.45 | 14.696 | 0.077642 | 0.025501
1948 | 51.46 | 14.696 | 0.07764 | 12.369 | 0.025506 |  | 1948 | 12.369 | 51.46 | 14.696 | 0.07764 | 0.025506
1949 | 51.47 | 14.696 | 0.077639 | 12.371 | 0.02551 |  | 1949 | 12.371 | 51.47 | 14.696 | 0.077639 | 0.02551
1950 | 51.48 | 14.696 | 0.077637 | 12.374 | 0.025515 |  | 1950 | 12.374 | 51.48 | 14.696 | 0.077637 | 0.025515
1951 | 51.49 | 14.696 | 0.077636 | 12.376 | 0.02552 |  | 1951 | 12.376 | 51.49 | 14.696 | 0.077636 | 0.02552
1952 | 51.5 | 14.696 | 0.077634 | 12.378 | 0.025524 |  | 1952 | 12.378 | 51.5 | 14.696 | 0.077634 | 0.025524
1953 | 51.51 | 14.696 | 0.077633 | 12.381 | 0.025529 |  | 1953 | 12.381 | 51.51 | 14.696 | 0.077633 | 0.025529
1954 | 51.52 | 14.696 | 0.077631 | 12.383 | 0.025534 |  | 1954 | 12.383 | 51.52 | 14.696 | 0.077631 | 0.025534
1955 | 51.53 | 14.696 | 0.07763 | 12.386 | 0.025539 |  | 1955 | 12.386 | 51.53 | 14.696 | 0.07763 | 0.025539
1956 | 51.54 | 14.696 | 0.077628 | 12.388 | 0.025543 |  | 1956 | 12.388 | 51.54 | 14.696 | 0.077628 | 0.025543
1957 | 51.55 | 14.696 | 0.077627 | 12.391 | 0.025548 |  | 1957 | 12.391 | 51.55 | 14.696 | 0.077627 | 0.025548
1958 | 51.56 | 14.696 | 0.077625 | 12.393 | 0.025553 |  | 1958 | 12.393 | 51.56 | 14.696 | 0.077625 | 0.025553
1959 | 51.57 | 14.696 | 0.077624 | 12.395 | 0.025557 |  | 1959 | 12.395 | 51.57 | 14.696 | 0.077624 | 0.025557
1960 | 51.58 | 14.696 | 0.077622 | 12.398 | 0.025562 |  | 1960 | 12.398 | 51.58 | 14.696 | 0.077622 | 0.025562
1961 | 51.59 | 14.696 | 0.07762 | 12.4 | 0.025567 |  | 1961 | 12.4 | 51.59 | 14.696 | 0.07762 | 0.025567
1962 | 51.6 | 14.696 | 0.077619 | 12.403 | 0.025572 |  | 1962 | 12.403 | 51.6 | 14.696 | 0.077619 | 0.025572
1963 | 51.61 | 14.696 | 0.077617 | 12.405 | 0.025576 |  | 1963 | 12.405 | 51.61 | 14.696 | 0.077617 | 0.025576
1964 | 51.62 | 14.696 | 0.077616 | 12.407 | 0.025581 |  | 1964 | 12.407 | 51.62 | 14.696 | 0.077616 | 0.025581
1965 | 51.63 | 14.696 | 0.077614 | 12.41 | 0.025586 |  | 1965 | 12.41 | 51.63 | 14.696 | 0.077614 | 0.025586
1966 | 51.64 | 14.696 | 0.077613 | 12.412 | 0.02559 |  | 1966 | 12.412 | 51.64 | 14.696 | 0.077613 | 0.02559
1967 | 51.65 | 14.696 | 0.077611 | 12.415 | 0.025595 |  | 1967 | 12.415 | 51.65 | 14.696 | 0.077611 | 0.025595
1968 | 51.66 | 14.696 | 0.07761 | 12.417 | 0.0256 |  | 1968 | 12.417 | 51.66 | 14.696 | 0.07761 | 0.0256
1969 | 51.67 | 14.696 | 0.077608 | 12.419 | 0.025604 |  | 1969 | 12.419 | 51.67 | 14.696 | 0.077608 | 0.025604
1970 | 51.68 | 14.696 | 0.077607 | 12.422 | 0.025609 |  | 1970 | 12.422 | 51.68 | 14.696 | 0.077607 | 0.025609
1971 | 51.69 | 14.696 | 0.077605 | 12.424 | 0.025614 |  | 1971 | 12.424 | 51.69 | 14.696 | 0.077605 | 0.025614
1972 | 51.7 | 14.696 | 0.077604 | 12.427 | 0.025619 |  | 1972 | 12.427 | 51.7 | 14.696 | 0.077604 | 0.025619
1973 | 51.71 | 14.696 | 0.077602 | 12.429 | 0.025623 |  | 1973 | 12.429 | 51.71 | 14.696 | 0.077602 | 0.025623
1974 | 51.72 | 14.696 | 0.077601 | 12.431 | 0.025628 |  | 1974 | 12.431 | 51.72 | 14.696 | 0.077601 | 0.025628
1975 | 51.73 | 14.696 | 0.077599 | 12.434 | 0.025633 |  | 1975 | 12.434 | 51.73 | 14.696 | 0.077599 | 0.025633
1976 | 51.74 | 14.696 | 0.077598 | 12.436 | 0.025637 |  | 1976 | 12.436 | 51.74 | 14.696 | 0.077598 | 0.025637
1977 | 51.75 | 14.696 | 0.077596 | 12.439 | 0.025642 |  | 1977 | 12.439 | 51.75 | 14.696 | 0.077596 | 0.025642
1978 | 51.76 | 14.696 | 0.077595 | 12.441 | 0.025647 |  | 1978 | 12.441 | 51.76 | 14.696 | 0.077595 | 0.025647
1979 | 51.77 | 14.696 | 0.077593 | 12.443 | 0.025651 |  | 1979 | 12.443 | 51.77 | 14.696 | 0.077593 | 0.025651
1980 | 51.78 | 14.696 | 0.077592 | 12.446 | 0.025656 |  | 1980 | 12.446 | 51.78 | 14.696 | 0.077592 | 0.025656
1981 | 51.79 | 14.696 | 0.07759 | 12.448 | 0.025661 |  | 1981 | 12.448 | 51.79 | 14.696 | 0.07759 | 0.025661
1982 | 51.8 | 14.696 | 0.077589 | 12.451 | 0.025666 |  | 1982 | 12.451 | 51.8 | 14.696 | 0.077589 | 0.025666
1983 | 51.81 | 14.696 | 0.077587 | 12.453 | 0.02567 |  | 1983 | 12.453 | 51.81 | 14.696 | 0.077587 | 0.02567
1984 | 51.82 | 14.696 | 0.077585 | 12.455 | 0.025675 |  | 1984 | 12.455 | 51.82 | 14.696 | 0.077585 | 0.025675
1985 | 51.83 | 14.696 | 0.077584 | 12.458 | 0.02568 |  | 1985 | 12.458 | 51.83 | 14.696 | 0.077584 | 0.02568
1986 | 51.84 | 14.696 | 0.077582 | 12.46 | 0.025684 |  | 1986 | 12.46 | 51.84 | 14.696 | 0.077582 | 0.025684
1987 | 51.85 | 14.696 | 0.077581 | 12.463 | 0.025689 |  | 1987 | 12.463 | 51.85 | 14.696 | 0.077581 | 0.025689
1988 | 51.86 | 14.696 | 0.077579 | 12.465 | 0.025694 |  | 1988 | 12.465 | 51.86 | 14.696 | 0.077579 | 0.025694
1989 | 51.87 | 14.696 | 0.077578 | 12.467 | 0.025698 |  | 1989 | 12.467 | 51.87 | 14.696 | 0.077578 | 0.025698
1990 | 51.88 | 14.696 | 0.077576 | 12.47 | 0.025703 |  | 1990 | 12.47 | 51.88 | 14.696 | 0.077576 | 0.025703
1991 | 51.89 | 14.696 | 0.077575 | 12.472 | 0.025708 |  | 1991 | 12.472 | 51.89 | 14.696 | 0.077575 | 0.025708
1992 | 51.9 | 14.696 | 0.077573 | 12.475 | 0.025713 |  | 1992 | 12.475 | 51.9 | 14.696 | 0.077573 | 0.025713
1993 | 51.91 | 14.696 | 0.077572 | 12.477 | 0.025717 |  | 1993 | 12.477 | 51.91 | 14.696 | 0.077572 | 0.025717
1994 | 51.92 | 14.696 | 0.07757 | 12.479 | 0.025722 |  | 1994 | 12.479 | 51.92 | 14.696 | 0.07757 | 0.025722
1995 | 51.93 | 14.696 | 0.077569 | 12.482 | 0.025727 |  | 1995 | 12.482 | 51.93 | 14.696 | 0.077569 | 0.025727
1996 | 51.94 | 14.696 | 0.077567 | 12.484 | 0.025731 |  | 1996 | 12.484 | 51.94 | 14.696 | 0.077567 | 0.025731
1997 | 51.95 | 14.696 | 0.077566 | 12.487 | 0.025736 |  | 1997 | 12.487 | 51.95 | 14.696 | 0.077566 | 0.025736
1998 | 51.96 | 14.696 | 0.077564 | 12.489 | 0.025741 |  | 1998 | 12.489 | 51.96 | 14.696 | 0.077564 | 0.025741
1999 | 51.97 | 14.696 | 0.077563 | 12.491 | 0.025745 |  | 1999 | 12.491 | 51.97 | 14.696 | 0.077563 | 0.025745
2000 | 51.98 | 14.696 | 0.077561 | 12.494 | 0.02575 |  | 2000 | 12.494 | 51.98 | 14.696 | 0.077561 | 0.02575
2001 | 51.99 | 14.696 | 0.07756 | 12.496 | 0.025755 |  | 2001 | 12.496 | 51.99 | 14.696 | 0.07756 | 0.025755
2002 | 52 | 14.696 | 0.077558 | 12.499 | 0.02576 |  | 2002 | 12.499 | 52 | 14.696 | 0.077558 | 0.02576
2003 | 52.01 | 14.696 | 0.077557 | 12.501 | 0.025764 |  | 2003 | 12.501 | 52.01 | 14.696 | 0.077557 | 0.025764
2004 | 52.02 | 14.696 | 0.077555 | 12.504 | 0.025769 |  | 2004 | 12.504 | 52.02 | 14.696 | 0.077555 | 0.025769
2005 | 52.03 | 14.696 | 0.077554 | 12.506 | 0.025774 |  | 2005 | 12.506 | 52.03 | 14.696 | 0.077554 | 0.025774
2006 | 52.04 | 14.696 | 0.077552 | 12.508 | 0.025778 |  | 2006 | 12.508 | 52.04 | 14.696 | 0.077552 | 0.025778
2007 | 52.05 | 14.696 | 0.07755 | 12.511 | 0.025783 |  | 2007 | 12.511 | 52.05 | 14.696 | 0.07755 | 0.025783
2008 | 52.06 | 14.696 | 0.077549 | 12.513 | 0.025788 |  | 2008 | 12.513 | 52.06 | 14.696 | 0.077549 | 0.025788
2009 | 52.07 | 14.696 | 0.077547 | 12.516 | 0.025792 |  | 2009 | 12.516 | 52.07 | 14.696 | 0.077547 | 0.025792
2010 | 52.08 | 14.696 | 0.077546 | 12.518 | 0.025797 |  | 2010 | 12.518 | 52.08 | 14.696 | 0.077546 | 0.025797
2011 | 52.09 | 14.696 | 0.077544 | 12.52 | 0.025802 |  | 2011 | 12.52 | 52.09 | 14.696 | 0.077544 | 0.025802
2012 | 52.1 | 14.696 | 0.077543 | 12.523 | 0.025807 |  | 2012 | 12.523 | 52.1 | 14.696 | 0.077543 | 0.025807
2013 | 52.11 | 14.696 | 0.077541 | 12.525 | 0.025811 |  | 2013 | 12.525 | 52.11 | 14.696 | 0.077541 | 0.025811
2014 | 52.12 | 14.696 | 0.07754 | 12.528 | 0.025816 |  | 2014 | 12.528 | 52.12 | 14.696 | 0.07754 | 0.025816
2015 | 52.13 | 14.696 | 0.077538 | 12.53 | 0.025821 |  | 2015 | 12.53 | 52.13 | 14.696 | 0.077538 | 0.025821
2016 | 52.14 | 14.696 | 0.077537 | 12.532 | 0.025825 |  | 2016 | 12.532 | 52.14 | 14.696 | 0.077537 | 0.025825
2017 | 52.15 | 14.696 | 0.077535 | 12.535 | 0.02583 |  | 2017 | 12.535 | 52.15 | 14.696 | 0.077535 | 0.02583
2018 | 52.16 | 14.696 | 0.077534 | 12.537 | 0.025835 |  | 2018 | 12.537 | 52.16 | 14.696 | 0.077534 | 0.025835
2019 | 52.17 | 14.696 | 0.077532 | 12.54 | 0.025839 |  | 2019 | 12.54 | 52.17 | 14.696 | 0.077532 | 0.025839
2020 | 52.18 | 14.696 | 0.077531 | 12.542 | 0.025844 |  | 2020 | 12.542 | 52.18 | 14.696 | 0.077531 | 0.025844
2021 | 52.19 | 14.696 | 0.077529 | 12.544 | 0.025849 |  | 2021 | 12.544 | 52.19 | 14.696 | 0.077529 | 0.025849
2022 | 52.2 | 14.696 | 0.077528 | 12.547 | 0.025853 |  | 2022 | 12.547 | 52.2 | 14.696 | 0.077528 | 0.025853
2023 | 52.21 | 14.696 | 0.077526 | 12.549 | 0.025858 |  | 2023 | 12.549 | 52.21 | 14.696 | 0.077526 | 0.025858
2024 | 52.22 | 14.696 | 0.077525 | 12.552 | 0.025863 |  | 2024 | 12.552 | 52.22 | 14.696 | 0.077525 | 0.025863
2025 | 52.23 | 14.696 | 0.077523 | 12.554 | 0.025868 |  | 2025 | 12.554 | 52.23 | 14.696 | 0.077523 | 0.025868
2026 | 52.24 | 14.696 | 0.077522 | 12.556 | 0.025872 |  | 2026 | 12.556 | 52.24 | 14.696 | 0.077522 | 0.025872
2027 | 52.25 | 14.696 | 0.07752 | 12.559 | 0.025877 |  | 2027 | 12.559 | 52.25 | 14.696 | 0.07752 | 0.025877
2028 | 52.26 | 14.696 | 0.077519 | 12.561 | 0.025882 |  | 2028 | 12.561 | 52.26 | 14.696 | 0.077519 | 0.025882
2029 | 52.27 | 14.696 | 0.077517 | 12.564 | 0.025886 |  | 2029 | 12.564 | 52.27 | 14.696 | 0.077517 | 0.025886
2030 | 52.28 | 14.696 | 0.077516 | 12.566 | 0.025891 |  | 2030 | 12.566 | 52.28 | 14.696 | 0.077516 | 0.025891
2031 | 52.29 | 14.696 | 0.077514 | 12.568 | 0.025896 |  | 2031 | 12.568 | 52.29 | 14.696 | 0.077514 | 0.025896
2032 | 52.3 | 14.696 | 0.077513 | 12.571 | 0.0259 |  | 2032 | 12.571 | 52.3 | 14.696 | 0.077513 | 0.0259
2033 | 52.31 | 14.696 | 0.077511 | 12.573 | 0.025905 |  | 2033 | 12.573 | 52.31 | 14.696 | 0.077511 | 0.025905
2034 | 52.32 | 14.696 | 0.077509 | 12.576 | 0.02591 |  | 2034 | 12.576 | 52.32 | 14.696 | 0.077509 | 0.02591
2035 | 52.33 | 14.696 | 0.077508 | 12.578 | 0.025915 |  | 2035 | 12.578 | 52.33 | 14.696 | 0.077508 | 0.025915
2036 | 52.34 | 14.696 | 0.077506 | 12.58 | 0.025919 |  | 2036 | 12.58 | 52.34 | 14.696 | 0.077506 | 0.025919
2037 | 52.35 | 14.696 | 0.077505 | 12.583 | 0.025924 |  | 2037 | 12.583 | 52.35 | 14.696 | 0.077505 | 0.025924
2038 | 52.36 | 14.696 | 0.077503 | 12.585 | 0.025929 |  | 2038 | 12.585 | 52.36 | 14.696 | 0.077503 | 0.025929
2039 | 52.37 | 14.696 | 0.077502 | 12.588 | 0.025933 |  | 2039 | 12.588 | 52.37 | 14.696 | 0.077502 | 0.025933
2040 | 52.38 | 14.696 | 0.0775 | 12.59 | 0.025938 |  | 2040 | 12.59 | 52.38 | 14.696 | 0.0775 | 0.025938
2041 | 52.39 | 14.696 | 0.077499 | 12.592 | 0.025943 |  | 2041 | 12.592 | 52.39 | 14.696 | 0.077499 | 0.025943
2042 | 52.4 | 14.696 | 0.077497 | 12.595 | 0.025947 |  | 2042 | 12.595 | 52.4 | 14.696 | 0.077497 | 0.025947
2043 | 52.41 | 14.696 | 0.077496 | 12.597 | 0.025952 |  | 2043 | 12.597 | 52.41 | 14.696 | 0.077496 | 0.025952
2044 | 52.42 | 14.696 | 0.077494 | 12.6 | 0.025957 |  | 2044 | 12.6 | 52.42 | 14.696 | 0.077494 | 0.025957
2045 | 52.43 | 14.696 | 0.077493 | 12.602 | 0.025961 |  | 2045 | 12.602 | 52.43 | 14.696 | 0.077493 | 0.025961
2046 | 52.44 | 14.696 | 0.077491 | 12.604 | 0.025966 |  | 2046 | 12.604 | 52.44 | 14.696 | 0.077491 | 0.025966
2047 | 52.45 | 14.696 | 0.07749 | 12.607 | 0.025971 |  | 2047 | 12.607 | 52.45 | 14.696 | 0.07749 | 0.025971
2048 | 52.46 | 14.696 | 0.077488 | 12.609 | 0.025976 |  | 2048 | 12.609 | 52.46 | 14.696 | 0.077488 | 0.025976
2049 | 52.47 | 14.696 | 0.077487 | 12.612 | 0.02598 |  | 2049 | 12.612 | 52.47 | 14.696 | 0.077487 | 0.02598
2050 | 52.48 | 14.696 | 0.077485 | 12.614 | 0.025985 |  | 2050 | 12.614 | 52.48 | 14.696 | 0.077485 | 0.025985
2051 | 52.49 | 14.696 | 0.077484 | 12.617 | 0.02599 |  | 2051 | 12.617 | 52.49 | 14.696 | 0.077484 | 0.02599
2052 | 52.5 | 14.696 | 0.077482 | 12.619 | 0.025994 |  | 2052 | 12.619 | 52.5 | 14.696 | 0.077482 | 0.025994
2053 | 52.51 | 14.696 | 0.077481 | 12.621 | 0.025999 |  | 2053 | 12.621 | 52.51 | 14.696 | 0.077481 | 0.025999
2054 | 52.52 | 14.696 | 0.077479 | 12.624 | 0.026004 |  | 2054 | 12.624 | 52.52 | 14.696 | 0.077479 | 0.026004
2055 | 52.53 | 14.696 | 0.077478 | 12.626 | 0.026008 |  | 2055 | 12.626 | 52.53 | 14.696 | 0.077478 | 0.026008
2056 | 52.54 | 14.696 | 0.077476 | 12.629 | 0.026013 |  | 2056 | 12.629 | 52.54 | 14.696 | 0.077476 | 0.026013
2057 | 52.55 | 14.696 | 0.077475 | 12.631 | 0.026018 |  | 2057 | 12.631 | 52.55 | 14.696 | 0.077475 | 0.026018
2058 | 52.56 | 14.696 | 0.077473 | 12.633 | 0.026023 |  | 2058 | 12.633 | 52.56 | 14.696 | 0.077473 | 0.026023
2059 | 52.57 | 14.696 | 0.077472 | 12.636 | 0.026027 |  | 2059 | 12.636 | 52.57 | 14.696 | 0.077472 | 0.026027
2060 | 52.58 | 14.696 | 0.07747 | 12.638 | 0.026032 |  | 2060 | 12.638 | 52.58 | 14.696 | 0.07747 | 0.026032
2061 | 52.59 | 14.696 | 0.077468 | 12.641 | 0.026037 |  | 2061 | 12.641 | 52.59 | 14.696 | 0.077468 | 0.026037
2062 | 52.6 | 14.696 | 0.077467 | 12.643 | 0.026041 |  | 2062 | 12.643 | 52.6 | 14.696 | 0.077467 | 0.026041
2063 | 52.61 | 14.696 | 0.077465 | 12.645 | 0.026046 |  | 2063 | 12.645 | 52.61 | 14.696 | 0.077465 | 0.026046
2064 | 52.62 | 14.696 | 0.077464 | 12.648 | 0.026051 |  | 2064 | 12.648 | 52.62 | 14.696 | 0.077464 | 0.026051
2065 | 52.63 | 14.696 | 0.077462 | 12.65 | 0.026055 |  | 2065 | 12.65 | 52.63 | 14.696 | 0.077462 | 0.026055
2066 | 52.64 | 14.696 | 0.077461 | 12.653 | 0.02606 |  | 2066 | 12.653 | 52.64 | 14.696 | 0.077461 | 0.02606
2067 | 52.65 | 14.696 | 0.077459 | 12.655 | 0.026065 |  | 2067 | 12.655 | 52.65 | 14.696 | 0.077459 | 0.026065
2068 | 52.66 | 14.696 | 0.077458 | 12.657 | 0.026069 |  | 2068 | 12.657 | 52.66 | 14.696 | 0.077458 | 0.026069
2069 | 52.67 | 14.696 | 0.077456 | 12.66 | 0.026074 |  | 2069 | 12.66 | 52.67 | 14.696 | 0.077456 | 0.026074
2070 | 52.68 | 14.696 | 0.077455 | 12.662 | 0.026079 |  | 2070 | 12.662 | 52.68 | 14.696 | 0.077455 | 0.026079
2071 | 52.69 | 14.696 | 0.077453 | 12.665 | 0.026084 |  | 2071 | 12.665 | 52.69 | 14.696 | 0.077453 | 0.026084
2072 | 52.7 | 14.696 | 0.077452 | 12.667 | 0.026088 |  | 2072 | 12.667 | 52.7 | 14.696 | 0.077452 | 0.026088
2073 | 52.71 | 14.696 | 0.07745 | 12.669 | 0.026093 |  | 2073 | 12.669 | 52.71 | 14.696 | 0.07745 | 0.026093
2074 | 52.72 | 14.696 | 0.077449 | 12.672 | 0.026098 |  | 2074 | 12.672 | 52.72 | 14.696 | 0.077449 | 0.026098
2075 | 52.73 | 14.696 | 0.077447 | 12.674 | 0.026102 |  | 2075 | 12.674 | 52.73 | 14.696 | 0.077447 | 0.026102
2076 | 52.74 | 14.696 | 0.077446 | 12.677 | 0.026107 |  | 2076 | 12.677 | 52.74 | 14.696 | 0.077446 | 0.026107
2077 | 52.75 | 14.696 | 0.077444 | 12.679 | 0.026112 |  | 2077 | 12.679 | 52.75 | 14.696 | 0.077444 | 0.026112
2078 | 52.76 | 14.696 | 0.077443 | 12.681 | 0.026116 |  | 2078 | 12.681 | 52.76 | 14.696 | 0.077443 | 0.026116
2079 | 52.77 | 14.696 | 0.077441 | 12.684 | 0.026121 |  | 2079 | 12.684 | 52.77 | 14.696 | 0.077441 | 0.026121
2080 | 52.78 | 14.696 | 0.07744 | 12.686 | 0.026126 |  | 2080 | 12.686 | 52.78 | 14.696 | 0.07744 | 0.026126
2081 | 52.79 | 14.696 | 0.077438 | 12.689 | 0.02613 |  | 2081 | 12.689 | 52.79 | 14.696 | 0.077438 | 0.02613
2082 | 52.8 | 14.696 | 0.077437 | 12.691 | 0.026135 |  | 2082 | 12.691 | 52.8 | 14.696 | 0.077437 | 0.026135
2083 | 52.81 | 14.696 | 0.077435 | 12.693 | 0.02614 |  | 2083 | 12.693 | 52.81 | 14.696 | 0.077435 | 0.02614
2084 | 52.82 | 14.696 | 0.077434 | 12.696 | 0.026145 |  | 2084 | 12.696 | 52.82 | 14.696 | 0.077434 | 0.026145
2085 | 52.83 | 14.696 | 0.077432 | 12.698 | 0.026149 |  | 2085 | 12.698 | 52.83 | 14.696 | 0.077432 | 0.026149
2086 | 52.84 | 14.696 | 0.077431 | 12.701 | 0.026154 |  | 2086 | 12.701 | 52.84 | 14.696 | 0.077431 | 0.026154
2087 | 52.85 | 14.696 | 0.077429 | 12.703 | 0.026159 |  | 2087 | 12.703 | 52.85 | 14.696 | 0.077429 | 0.026159
2088 | 52.86 | 14.696 | 0.077428 | 12.705 | 0.026163 |  | 2088 | 12.705 | 52.86 | 14.696 | 0.077428 | 0.026163
2089 | 52.87 | 14.696 | 0.077426 | 12.708 | 0.026168 |  | 2089 | 12.708 | 52.87 | 14.696 | 0.077426 | 0.026168
2090 | 52.88 | 14.696 | 0.077425 | 12.71 | 0.026173 |  | 2090 | 12.71 | 52.88 | 14.696 | 0.077425 | 0.026173
2091 | 52.89 | 14.696 | 0.077423 | 12.713 | 0.026177 |  | 2091 | 12.713 | 52.89 | 14.696 | 0.077423 | 0.026177
2092 | 52.9 | 14.696 | 0.077421 | 12.715 | 0.026182 |  | 2092 | 12.715 | 52.9 | 14.696 | 0.077421 | 0.026182
2093 | 52.91 | 14.696 | 0.07742 | 12.717 | 0.026187 |  | 2093 | 12.717 | 52.91 | 14.696 | 0.07742 | 0.026187
2094 | 52.92 | 14.696 | 0.077418 | 12.72 | 0.026191 |  | 2094 | 12.72 | 52.92 | 14.696 | 0.077418 | 0.026191
2095 | 52.93 | 14.696 | 0.077417 | 12.722 | 0.026196 |  | 2095 | 12.722 | 52.93 | 14.696 | 0.077417 | 0.026196
2096 | 52.94 | 14.696 | 0.077415 | 12.725 | 0.026201 |  | 2096 | 12.725 | 52.94 | 14.696 | 0.077415 | 0.026201
2097 | 52.95 | 14.696 | 0.077414 | 12.727 | 0.026205 |  | 2097 | 12.727 | 52.95 | 14.696 | 0.077414 | 0.026205
2098 | 52.96 | 14.696 | 0.077412 | 12.73 | 0.02621 |  | 2098 | 12.73 | 52.96 | 14.696 | 0.077412 | 0.02621
2099 | 52.97 | 14.696 | 0.077411 | 12.732 | 0.026215 |  | 2099 | 12.732 | 52.97 | 14.696 | 0.077411 | 0.026215
2100 | 52.98 | 14.696 | 0.077409 | 12.734 | 0.02622 |  | 2100 | 12.734 | 52.98 | 14.696 | 0.077409 | 0.02622
2101 | 52.99 | 14.696 | 0.077408 | 12.737 | 0.026224 |  | 2101 | 12.737 | 52.99 | 14.696 | 0.077408 | 0.026224
2102 | 53 | 14.696 | 0.077406 | 12.739 | 0.026229 |  | 2102 | 12.739 | 53 | 14.696 | 0.077406 | 0.026229
2103 | 53.01 | 14.696 | 0.077405 | 12.742 | 0.026234 |  | 2103 | 12.742 | 53.01 | 14.696 | 0.077405 | 0.026234
2104 | 53.02 | 14.696 | 0.077403 | 12.744 | 0.026238 |  | 2104 | 12.744 | 53.02 | 14.696 | 0.077403 | 0.026238
2105 | 53.03 | 14.696 | 0.077402 | 12.746 | 0.026243 |  | 2105 | 12.746 | 53.03 | 14.696 | 0.077402 | 0.026243
2106 | 53.04 | 14.696 | 0.0774 | 12.749 | 0.026248 |  | 2106 | 12.749 | 53.04 | 14.696 | 0.0774 | 0.026248
2107 | 53.05 | 14.696 | 0.077399 | 12.751 | 0.026252 |  | 2107 | 12.751 | 53.05 | 14.696 | 0.077399 | 0.026252
2108 | 53.06 | 14.696 | 0.077397 | 12.754 | 0.026257 |  | 2108 | 12.754 | 53.06 | 14.696 | 0.077397 | 0.026257
2109 | 53.07 | 14.696 | 0.077396 | 12.756 | 0.026262 |  | 2109 | 12.756 | 53.07 | 14.696 | 0.077396 | 0.026262
2110 | 53.08 | 14.696 | 0.077394 | 12.758 | 0.026266 |  | 2110 | 12.758 | 53.08 | 14.696 | 0.077394 | 0.026266
2111 | 53.09 | 14.696 | 0.077393 | 12.761 | 0.026271 |  | 2111 | 12.761 | 53.09 | 14.696 | 0.077393 | 0.026271
2112 | 53.1 | 14.696 | 0.077391 | 12.763 | 0.026276 |  | 2112 | 12.763 | 53.1 | 14.696 | 0.077391 | 0.026276
2113 | 53.11 | 14.696 | 0.07739 | 12.766 | 0.026281 |  | 2113 | 12.766 | 53.11 | 14.696 | 0.07739 | 0.026281
2114 | 53.12 | 14.696 | 0.077388 | 12.768 | 0.026285 |  | 2114 | 12.768 | 53.12 | 14.696 | 0.077388 | 0.026285
2115 | 53.13 | 14.696 | 0.077387 | 12.77 | 0.02629 |  | 2115 | 12.77 | 53.13 | 14.696 | 0.077387 | 0.02629
2116 | 53.14 | 14.696 | 0.077385 | 12.773 | 0.026295 |  | 2116 | 12.773 | 53.14 | 14.696 | 0.077385 | 0.026295
2117 | 53.15 | 14.696 | 0.077384 | 12.775 | 0.026299 |  | 2117 | 12.775 | 53.15 | 14.696 | 0.077384 | 0.026299
2118 | 53.16 | 14.696 | 0.077382 | 12.778 | 0.026304 |  | 2118 | 12.778 | 53.16 | 14.696 | 0.077382 | 0.026304
2119 | 53.17 | 14.696 | 0.077381 | 12.78 | 0.026309 |  | 2119 | 12.78 | 53.17 | 14.696 | 0.077381 | 0.026309
2120 | 53.18 | 14.696 | 0.077379 | 12.782 | 0.026313 |  | 2120 | 12.782 | 53.18 | 14.696 | 0.077379 | 0.026313
2121 | 53.19 | 14.696 | 0.077378 | 12.785 | 0.026318 |  | 2121 | 12.785 | 53.19 | 14.696 | 0.077378 | 0.026318
2122 | 53.2 | 14.696 | 0.077376 | 12.787 | 0.026323 |  | 2122 | 12.787 | 53.2 | 14.696 | 0.077376 | 0.026323
2123 | 53.21 | 14.696 | 0.077375 | 12.79 | 0.026327 |  | 2123 | 12.79 | 53.21 | 14.696 | 0.077375 | 0.026327
2124 | 53.22 | 14.696 | 0.077373 | 12.792 | 0.026332 |  | 2124 | 12.792 | 53.22 | 14.696 | 0.077373 | 0.026332
2125 | 53.23 | 14.696 | 0.077372 | 12.794 | 0.026337 |  | 2125 | 12.794 | 53.23 | 14.696 | 0.077372 | 0.026337
2126 | 53.24 | 14.696 | 0.07737 | 12.797 | 0.026341 |  | 2126 | 12.797 | 53.24 | 14.696 | 0.07737 | 0.026341
2127 | 53.25 | 14.696 | 0.077368 | 12.799 | 0.026346 |  | 2127 | 12.799 | 53.25 | 14.696 | 0.077368 | 0.026346
2128 | 53.26 | 14.696 | 0.077367 | 12.802 | 0.026351 |  | 2128 | 12.802 | 53.26 | 14.696 | 0.077367 | 0.026351
2129 | 53.27 | 14.696 | 0.077365 | 12.804 | 0.026356 |  | 2129 | 12.804 | 53.27 | 14.696 | 0.077365 | 0.026356
2130 | 53.28 | 14.696 | 0.077364 | 12.806 | 0.02636 |  | 2130 | 12.806 | 53.28 | 14.696 | 0.077364 | 0.02636
2131 | 53.29 | 14.696 | 0.077362 | 12.809 | 0.026365 |  | 2131 | 12.809 | 53.29 | 14.696 | 0.077362 | 0.026365
2132 | 53.3 | 14.696 | 0.077361 | 12.811 | 0.02637 |  | 2132 | 12.811 | 53.3 | 14.696 | 0.077361 | 0.02637
2133 | 53.31 | 14.696 | 0.077359 | 12.814 | 0.026374 |  | 2133 | 12.814 | 53.31 | 14.696 | 0.077359 | 0.026374
2134 | 53.32 | 14.696 | 0.077358 | 12.816 | 0.026379 |  | 2134 | 12.816 | 53.32 | 14.696 | 0.077358 | 0.026379
2135 | 53.33 | 14.696 | 0.077356 | 12.818 | 0.026384 |  | 2135 | 12.818 | 53.33 | 14.696 | 0.077356 | 0.026384
2136 | 53.34 | 14.696 | 0.077355 | 12.821 | 0.026388 |  | 2136 | 12.821 | 53.34 | 14.696 | 0.077355 | 0.026388
2137 | 53.35 | 14.696 | 0.077353 | 12.823 | 0.026393 |  | 2137 | 12.823 | 53.35 | 14.696 | 0.077353 | 0.026393
2138 | 53.36 | 14.696 | 0.077352 | 12.826 | 0.026398 |  | 2138 | 12.826 | 53.36 | 14.696 | 0.077352 | 0.026398
2139 | 53.37 | 14.696 | 0.07735 | 12.828 | 0.026402 |  | 2139 | 12.828 | 53.37 | 14.696 | 0.07735 | 0.026402
2140 | 53.38 | 14.696 | 0.077349 | 12.83 | 0.026407 |  | 2140 | 12.83 | 53.38 | 14.696 | 0.077349 | 0.026407
2141 | 53.39 | 14.696 | 0.077347 | 12.833 | 0.026412 |  | 2141 | 12.833 | 53.39 | 14.696 | 0.077347 | 0.026412
2142 | 53.4 | 14.696 | 0.077346 | 12.835 | 0.026416 |  | 2142 | 12.835 | 53.4 | 14.696 | 0.077346 | 0.026416
2143 | 53.41 | 14.696 | 0.077344 | 12.838 | 0.026421 |  | 2143 | 12.838 | 53.41 | 14.696 | 0.077344 | 0.026421
2144 | 53.42 | 14.696 | 0.077343 | 12.84 | 0.026426 |  | 2144 | 12.84 | 53.42 | 14.696 | 0.077343 | 0.026426
2145 | 53.43 | 14.696 | 0.077341 | 12.843 | 0.02643 |  | 2145 | 12.843 | 53.43 | 14.696 | 0.077341 | 0.02643
2146 | 53.44 | 14.696 | 0.07734 | 12.845 | 0.026435 |  | 2146 | 12.845 | 53.44 | 14.696 | 0.07734 | 0.026435
2147 | 53.45 | 14.696 | 0.077338 | 12.847 | 0.02644 |  | 2147 | 12.847 | 53.45 | 14.696 | 0.077338 | 0.02644
2148 | 53.46 | 14.696 | 0.077337 | 12.85 | 0.026445 |  | 2148 | 12.85 | 53.46 | 14.696 | 0.077337 | 0.026445
2149 | 53.47 | 14.696 | 0.077335 | 12.852 | 0.026449 |  | 2149 | 12.852 | 53.47 | 14.696 | 0.077335 | 0.026449
2150 | 53.48 | 14.696 | 0.077334 | 12.855 | 0.026454 |  | 2150 | 12.855 | 53.48 | 14.696 | 0.077334 | 0.026454
2151 | 53.49 | 14.696 | 0.077332 | 12.857 | 0.026459 |  | 2151 | 12.857 | 53.49 | 14.696 | 0.077332 | 0.026459
2152 | 53.5 | 14.696 | 0.077331 | 12.859 | 0.026463 |  | 2152 | 12.859 | 53.5 | 14.696 | 0.077331 | 0.026463
2153 | 53.51 | 14.696 | 0.077329 | 12.862 | 0.026468 |  | 2153 | 12.862 | 53.51 | 14.696 | 0.077329 | 0.026468
2154 | 53.52 | 14.696 | 0.077328 | 12.864 | 0.026473 |  | 2154 | 12.864 | 53.52 | 14.696 | 0.077328 | 0.026473
2155 | 53.53 | 14.696 | 0.077326 | 12.867 | 0.026477 |  | 2155 | 12.867 | 53.53 | 14.696 | 0.077326 | 0.026477
2156 | 53.54 | 14.696 | 0.077325 | 12.869 | 0.026482 |  | 2156 | 12.869 | 53.54 | 14.696 | 0.077325 | 0.026482
2157 | 53.55 | 14.696 | 0.077323 | 12.871 | 0.026487 |  | 2157 | 12.871 | 53.55 | 14.696 | 0.077323 | 0.026487
2158 | 53.56 | 14.696 | 0.077322 | 12.874 | 0.026491 |  | 2158 | 12.874 | 53.56 | 14.696 | 0.077322 | 0.026491
2159 | 53.57 | 14.696 | 0.07732 | 12.876 | 0.026496 |  | 2159 | 12.876 | 53.57 | 14.696 | 0.07732 | 0.026496
2160 | 53.58 | 14.696 | 0.077319 | 12.879 | 0.026501 |  | 2160 | 12.879 | 53.58 | 14.696 | 0.077319 | 0.026501
2161 | 53.59 | 14.696 | 0.077317 | 12.881 | 0.026505 |  | 2161 | 12.881 | 53.59 | 14.696 | 0.077317 | 0.026505
2162 | 53.6 | 14.696 | 0.077316 | 12.883 | 0.02651 |  | 2162 | 12.883 | 53.6 | 14.696 | 0.077316 | 0.02651
2163 | 53.61 | 14.696 | 0.077314 | 12.886 | 0.026515 |  | 2163 | 12.886 | 53.61 | 14.696 | 0.077314 | 0.026515
2164 | 53.62 | 14.696 | 0.077313 | 12.888 | 0.02652 |  | 2164 | 12.888 | 53.62 | 14.696 | 0.077313 | 0.02652
2165 | 53.63 | 14.696 | 0.077311 | 12.891 | 0.026524 |  | 2165 | 12.891 | 53.63 | 14.696 | 0.077311 | 0.026524
2166 | 53.64 | 14.696 | 0.07731 | 12.893 | 0.026529 |  | 2166 | 12.893 | 53.64 | 14.696 | 0.07731 | 0.026529
2167 | 53.65 | 14.696 | 0.077308 | 12.895 | 0.026534 |  | 2167 | 12.895 | 53.65 | 14.696 | 0.077308 | 0.026534
2168 | 53.66 | 14.696 | 0.077307 | 12.898 | 0.026538 |  | 2168 | 12.898 | 53.66 | 14.696 | 0.077307 | 0.026538
2169 | 53.67 | 14.696 | 0.077305 | 12.9 | 0.026543 |  | 2169 | 12.9 | 53.67 | 14.696 | 0.077305 | 0.026543
2170 | 53.68 | 14.696 | 0.077303 | 12.903 | 0.026548 |  | 2170 | 12.903 | 53.68 | 14.696 | 0.077303 | 0.026548
2171 | 53.69 | 14.696 | 0.077302 | 12.905 | 0.026552 |  | 2171 | 12.905 | 53.69 | 14.696 | 0.077302 | 0.026552
2172 | 53.7 | 14.696 | 0.0773 | 12.907 | 0.026557 |  | 2172 | 12.907 | 53.7 | 14.696 | 0.0773 | 0.026557
2173 | 53.71 | 14.696 | 0.077299 | 12.91 | 0.026562 |  | 2173 | 12.91 | 53.71 | 14.696 | 0.077299 | 0.026562
2174 | 53.72 | 14.696 | 0.077297 | 12.912 | 0.026566 |  | 2174 | 12.912 | 53.72 | 14.696 | 0.077297 | 0.026566
2175 | 53.73 | 14.696 | 0.077296 | 12.915 | 0.026571 |  | 2175 | 12.915 | 53.73 | 14.696 | 0.077296 | 0.026571
2176 | 53.74 | 14.696 | 0.077294 | 12.917 | 0.026576 |  | 2176 | 12.917 | 53.74 | 14.696 | 0.077294 | 0.026576
2177 | 53.75 | 14.696 | 0.077293 | 12.919 | 0.02658 |  | 2177 | 12.919 | 53.75 | 14.696 | 0.077293 | 0.02658
2178 | 53.76 | 14.696 | 0.077291 | 12.922 | 0.026585 |  | 2178 | 12.922 | 53.76 | 14.696 | 0.077291 | 0.026585
2179 | 53.77 | 14.696 | 0.07729 | 12.924 | 0.02659 |  | 2179 | 12.924 | 53.77 | 14.696 | 0.07729 | 0.02659
2180 | 53.78 | 14.696 | 0.077288 | 12.927 | 0.026594 |  | 2180 | 12.927 | 53.78 | 14.696 | 0.077288 | 0.026594
2181 | 53.79 | 14.696 | 0.077287 | 12.929 | 0.026599 |  | 2181 | 12.929 | 53.79 | 14.696 | 0.077287 | 0.026599
2182 | 53.8 | 14.696 | 0.077285 | 12.931 | 0.026604 |  | 2182 | 12.931 | 53.8 | 14.696 | 0.077285 | 0.026604
2183 | 53.81 | 14.696 | 0.077284 | 12.934 | 0.026608 |  | 2183 | 12.934 | 53.81 | 14.696 | 0.077284 | 0.026608
2184 | 53.82 | 14.696 | 0.077282 | 12.936 | 0.026613 |  | 2184 | 12.936 | 53.82 | 14.696 | 0.077282 | 0.026613
2185 | 53.83 | 14.696 | 0.077281 | 12.939 | 0.026618 |  | 2185 | 12.939 | 53.83 | 14.696 | 0.077281 | 0.026618
2186 | 53.84 | 14.696 | 0.077279 | 12.941 | 0.026623 |  | 2186 | 12.941 | 53.84 | 14.696 | 0.077279 | 0.026623
2187 | 53.85 | 14.696 | 0.077278 | 12.943 | 0.026627 |  | 2187 | 12.943 | 53.85 | 14.696 | 0.077278 | 0.026627
2188 | 53.86 | 14.696 | 0.077276 | 12.946 | 0.026632 |  | 2188 | 12.946 | 53.86 | 14.696 | 0.077276 | 0.026632
2189 | 53.87 | 14.696 | 0.077275 | 12.948 | 0.026637 |  | 2189 | 12.948 | 53.87 | 14.696 | 0.077275 | 0.026637
2190 | 53.88 | 14.696 | 0.077273 | 12.951 | 0.026641 |  | 2190 | 12.951 | 53.88 | 14.696 | 0.077273 | 0.026641
2191 | 53.89 | 14.696 | 0.077272 | 12.953 | 0.026646 |  | 2191 | 12.953 | 53.89 | 14.696 | 0.077272 | 0.026646
2192 | 53.9 | 14.696 | 0.07727 | 12.956 | 0.026651 |  | 2192 | 12.956 | 53.9 | 14.696 | 0.07727 | 0.026651
2193 | 53.91 | 14.696 | 0.077269 | 12.958 | 0.026655 |  | 2193 | 12.958 | 53.91 | 14.696 | 0.077269 | 0.026655
2194 | 53.92 | 14.696 | 0.077267 | 12.96 | 0.02666 |  | 2194 | 12.96 | 53.92 | 14.696 | 0.077267 | 0.02666
2195 | 53.93 | 14.696 | 0.077266 | 12.963 | 0.026665 |  | 2195 | 12.963 | 53.93 | 14.696 | 0.077266 | 0.026665
2196 | 53.94 | 14.696 | 0.077264 | 12.965 | 0.026669 |  | 2196 | 12.965 | 53.94 | 14.696 | 0.077264 | 0.026669
2197 | 53.95 | 14.696 | 0.077263 | 12.968 | 0.026674 |  | 2197 | 12.968 | 53.95 | 14.696 | 0.077263 | 0.026674
2198 | 53.96 | 14.696 | 0.077261 | 12.97 | 0.026679 |  | 2198 | 12.97 | 53.96 | 14.696 | 0.077261 | 0.026679
2199 | 53.97 | 14.696 | 0.07726 | 12.972 | 0.026683 |  | 2199 | 12.972 | 53.97 | 14.696 | 0.07726 | 0.026683
2200 | 53.98 | 14.696 | 0.077258 | 12.975 | 0.026688 |  | 2200 | 12.975 | 53.98 | 14.696 | 0.077258 | 0.026688
2201 | 53.99 | 14.696 | 0.077257 | 12.977 | 0.026693 |  | 2201 | 12.977 | 53.99 | 14.696 | 0.077257 | 0.026693
2202 | 54 | 14.696 | 0.077255 | 12.98 | 0.026697 |  | 2202 | 12.98 | 54 | 14.696 | 0.077255 | 0.026697
2203 | 54.01 | 14.696 | 0.077254 | 12.982 | 0.026702 |  | 2203 | 12.982 | 54.01 | 14.696 | 0.077254 | 0.026702
2204 | 54.02 | 14.696 | 0.077252 | 12.984 | 0.026707 |  | 2204 | 12.984 | 54.02 | 14.696 | 0.077252 | 0.026707
2205 | 54.03 | 14.696 | 0.077251 | 12.987 | 0.026711 |  | 2205 | 12.987 | 54.03 | 14.696 | 0.077251 | 0.026711
2206 | 54.04 | 14.696 | 0.077249 | 12.989 | 0.026716 |  | 2206 | 12.989 | 54.04 | 14.696 | 0.077249 | 0.026716
2207 | 54.05 | 14.696 | 0.077248 | 12.992 | 0.026721 |  | 2207 | 12.992 | 54.05 | 14.696 | 0.077248 | 0.026721
2208 | 54.06 | 14.696 | 0.077246 | 12.994 | 0.026726 |  | 2208 | 12.994 | 54.06 | 14.696 | 0.077246 | 0.026726
2209 | 54.07 | 14.696 | 0.077245 | 12.996 | 0.02673 |  | 2209 | 12.996 | 54.07 | 14.696 | 0.077245 | 0.02673
2210 | 54.08 | 14.696 | 0.077243 | 12.999 | 0.026735 |  | 2210 | 12.999 | 54.08 | 14.696 | 0.077243 | 0.026735
2211 | 54.09 | 14.696 | 0.077242 | 13.001 | 0.02674 |  | 2211 | 13.001 | 54.09 | 14.696 | 0.077242 | 0.02674
2212 | 54.1 | 14.696 | 0.07724 | 13.004 | 0.026744 |  | 2212 | 13.004 | 54.1 | 14.696 | 0.07724 | 0.026744
2213 | 54.11 | 14.696 | 0.077239 | 13.006 | 0.026749 |  | 2213 | 13.006 | 54.11 | 14.696 | 0.077239 | 0.026749
2214 | 54.12 | 14.696 | 0.077237 | 13.008 | 0.026754 |  | 2214 | 13.008 | 54.12 | 14.696 | 0.077237 | 0.026754
2215 | 54.13 | 14.696 | 0.077236 | 13.011 | 0.026758 |  | 2215 | 13.011 | 54.13 | 14.696 | 0.077236 | 0.026758
2216 | 54.14 | 14.696 | 0.077234 | 13.013 | 0.026763 |  | 2216 | 13.013 | 54.14 | 14.696 | 0.077234 | 0.026763
2217 | 54.15 | 14.696 | 0.077233 | 13.016 | 0.026768 |  | 2217 | 13.016 | 54.15 | 14.696 | 0.077233 | 0.026768
2218 | 54.16 | 14.696 | 0.077231 | 13.018 | 0.026772 |  | 2218 | 13.018 | 54.16 | 14.696 | 0.077231 | 0.026772
2219 | 54.17 | 14.696 | 0.07723 | 13.02 | 0.026777 |  | 2219 | 13.02 | 54.17 | 14.696 | 0.07723 | 0.026777
2220 | 54.18 | 14.696 | 0.077228 | 13.023 | 0.026782 |  | 2220 | 13.023 | 54.18 | 14.696 | 0.077228 | 0.026782
2221 | 54.19 | 14.696 | 0.077227 | 13.025 | 0.026786 |  | 2221 | 13.025 | 54.19 | 14.696 | 0.077227 | 0.026786
2222 | 54.2 | 14.696 | 0.077225 | 13.028 | 0.026791 |  | 2222 | 13.028 | 54.2 | 14.696 | 0.077225 | 0.026791
2223 | 54.21 | 14.696 | 0.077224 | 13.03 | 0.026796 |  | 2223 | 13.03 | 54.21 | 14.696 | 0.077224 | 0.026796
2224 | 54.22 | 14.696 | 0.077222 | 13.032 | 0.0268 |  | 2224 | 13.032 | 54.22 | 14.696 | 0.077222 | 0.0268
2225 | 54.23 | 14.696 | 0.07722 | 13.035 | 0.026805 |  | 2225 | 13.035 | 54.23 | 14.696 | 0.07722 | 0.026805
2226 | 54.24 | 14.696 | 0.077219 | 13.037 | 0.02681 |  | 2226 | 13.037 | 54.24 | 14.696 | 0.077219 | 0.02681
2227 | 54.25 | 14.696 | 0.077217 | 13.04 | 0.026814 |  | 2227 | 13.04 | 54.25 | 14.696 | 0.077217 | 0.026814
2228 | 54.26 | 14.696 | 0.077216 | 13.042 | 0.026819 |  | 2228 | 13.042 | 54.26 | 14.696 | 0.077216 | 0.026819
2229 | 54.27 | 14.696 | 0.077214 | 13.044 | 0.026824 |  | 2229 | 13.044 | 54.27 | 14.696 | 0.077214 | 0.026824
2230 | 54.28 | 14.696 | 0.077213 | 13.047 | 0.026828 |  | 2230 | 13.047 | 54.28 | 14.696 | 0.077213 | 0.026828
2231 | 54.29 | 14.696 | 0.077211 | 13.049 | 0.026833 |  | 2231 | 13.049 | 54.29 | 14.696 | 0.077211 | 0.026833
2232 | 54.3 | 14.696 | 0.07721 | 13.052 | 0.026838 |  | 2232 | 13.052 | 54.3 | 14.696 | 0.07721 | 0.026838
2233 | 54.31 | 14.696 | 0.077208 | 13.054 | 0.026842 |  | 2233 | 13.054 | 54.31 | 14.696 | 0.077208 | 0.026842
2234 | 54.32 | 14.696 | 0.077207 | 13.056 | 0.026847 |  | 2234 | 13.056 | 54.32 | 14.696 | 0.077207 | 0.026847
2235 | 54.33 | 14.696 | 0.077205 | 13.059 | 0.026852 |  | 2235 | 13.059 | 54.33 | 14.696 | 0.077205 | 0.026852
2236 | 54.34 | 14.696 | 0.077204 | 13.061 | 0.026857 |  | 2236 | 13.061 | 54.34 | 14.696 | 0.077204 | 0.026857
2237 | 54.35 | 14.696 | 0.077202 | 13.064 | 0.026861 |  | 2237 | 13.064 | 54.35 | 14.696 | 0.077202 | 0.026861
2238 | 54.36 | 14.696 | 0.077201 | 13.066 | 0.026866 |  | 2238 | 13.066 | 54.36 | 14.696 | 0.077201 | 0.026866
2239 | 54.37 | 14.696 | 0.077199 | 13.069 | 0.026871 |  | 2239 | 13.069 | 54.37 | 14.696 | 0.077199 | 0.026871
2240 | 54.38 | 14.696 | 0.077198 | 13.071 | 0.026875 |  | 2240 | 13.071 | 54.38 | 14.696 | 0.077198 | 0.026875
2241 | 54.39 | 14.696 | 0.077196 | 13.073 | 0.02688 |  | 2241 | 13.073 | 54.39 | 14.696 | 0.077196 | 0.02688
2242 | 54.4 | 14.696 | 0.077195 | 13.076 | 0.026885 |  | 2242 | 13.076 | 54.4 | 14.696 | 0.077195 | 0.026885
2243 | 54.41 | 14.696 | 0.077193 | 13.078 | 0.026889 |  | 2243 | 13.078 | 54.41 | 14.696 | 0.077193 | 0.026889
2244 | 54.42 | 14.696 | 0.077192 | 13.081 | 0.026894 |  | 2244 | 13.081 | 54.42 | 14.696 | 0.077192 | 0.026894
2245 | 54.43 | 14.696 | 0.07719 | 13.083 | 0.026899 |  | 2245 | 13.083 | 54.43 | 14.696 | 0.07719 | 0.026899
2246 | 54.44 | 14.696 | 0.077189 | 13.085 | 0.026903 |  | 2246 | 13.085 | 54.44 | 14.696 | 0.077189 | 0.026903
2247 | 54.45 | 14.696 | 0.077187 | 13.088 | 0.026908 |  | 2247 | 13.088 | 54.45 | 14.696 | 0.077187 | 0.026908
2248 | 54.46 | 14.696 | 0.077186 | 13.09 | 0.026913 |  | 2248 | 13.09 | 54.46 | 14.696 | 0.077186 | 0.026913
2249 | 54.47 | 14.696 | 0.077184 | 13.093 | 0.026917 |  | 2249 | 13.093 | 54.47 | 14.696 | 0.077184 | 0.026917
2250 | 54.48 | 14.696 | 0.077183 | 13.095 | 0.026922 |  | 2250 | 13.095 | 54.48 | 14.696 | 0.077183 | 0.026922
2251 | 54.49 | 14.696 | 0.077181 | 13.097 | 0.026927 |  | 2251 | 13.097 | 54.49 | 14.696 | 0.077181 | 0.026927
2252 | 54.5 | 14.696 | 0.07718 | 13.1 | 0.026931 |  | 2252 | 13.1 | 54.5 | 14.696 | 0.07718 | 0.026931
2253 | 54.51 | 14.696 | 0.077178 | 13.102 | 0.026936 |  | 2253 | 13.102 | 54.51 | 14.696 | 0.077178 | 0.026936
2254 | 54.52 | 14.696 | 0.077177 | 13.105 | 0.026941 |  | 2254 | 13.105 | 54.52 | 14.696 | 0.077177 | 0.026941
2255 | 54.53 | 14.696 | 0.077175 | 13.107 | 0.026945 |  | 2255 | 13.107 | 54.53 | 14.696 | 0.077175 | 0.026945
2256 | 54.54 | 14.696 | 0.077174 | 13.109 | 0.02695 |  | 2256 | 13.109 | 54.54 | 14.696 | 0.077174 | 0.02695
2257 | 54.55 | 14.696 | 0.077172 | 13.112 | 0.026955 |  | 2257 | 13.112 | 54.55 | 14.696 | 0.077172 | 0.026955
2258 | 54.56 | 14.696 | 0.077171 | 13.114 | 0.026959 |  | 2258 | 13.114 | 54.56 | 14.696 | 0.077171 | 0.026959
2259 | 54.57 | 14.696 | 0.077169 | 13.117 | 0.026964 |  | 2259 | 13.117 | 54.57 | 14.696 | 0.077169 | 0.026964
2260 | 54.58 | 14.696 | 0.077168 | 13.119 | 0.026969 |  | 2260 | 13.119 | 54.58 | 14.696 | 0.077168 | 0.026969
2261 | 54.59 | 14.696 | 0.077166 | 13.121 | 0.026973 |  | 2261 | 13.121 | 54.59 | 14.696 | 0.077166 | 0.026973
2262 | 54.6 | 14.696 | 0.077165 | 13.124 | 0.026978 |  | 2262 | 13.124 | 54.6 | 14.696 | 0.077165 | 0.026978
2263 | 54.61 | 14.696 | 0.077163 | 13.126 | 0.026983 |  | 2263 | 13.126 | 54.61 | 14.696 | 0.077163 | 0.026983
2264 | 54.62 | 14.696 | 0.077162 | 13.129 | 0.026987 |  | 2264 | 13.129 | 54.62 | 14.696 | 0.077162 | 0.026987
2265 | 54.63 | 14.696 | 0.07716 | 13.131 | 0.026992 |  | 2265 | 13.131 | 54.63 | 14.696 | 0.07716 | 0.026992
2266 | 54.64 | 14.696 | 0.077159 | 13.133 | 0.026997 |  | 2266 | 13.133 | 54.64 | 14.696 | 0.077159 | 0.026997
2267 | 54.65 | 14.696 | 0.077157 | 13.136 | 0.027001 |  | 2267 | 13.136 | 54.65 | 14.696 | 0.077157 | 0.027001
2268 | 54.66 | 14.696 | 0.077156 | 13.138 | 0.027006 |  | 2268 | 13.138 | 54.66 | 14.696 | 0.077156 | 0.027006
2269 | 54.67 | 14.696 | 0.077154 | 13.141 | 0.027011 |  | 2269 | 13.141 | 54.67 | 14.696 | 0.077154 | 0.027011
2270 | 54.68 | 14.696 | 0.077153 | 13.143 | 0.027015 |  | 2270 | 13.143 | 54.68 | 14.696 | 0.077153 | 0.027015
2271 | 54.69 | 14.696 | 0.077151 | 13.145 | 0.02702 |  | 2271 | 13.145 | 54.69 | 14.696 | 0.077151 | 0.02702
2272 | 54.7 | 14.696 | 0.07715 | 13.148 | 0.027025 |  | 2272 | 13.148 | 54.7 | 14.696 | 0.07715 | 0.027025
2273 | 54.71 | 14.696 | 0.077148 | 13.15 | 0.02703 |  | 2273 | 13.15 | 54.71 | 14.696 | 0.077148 | 0.02703
2274 | 54.72 | 14.696 | 0.077147 | 13.153 | 0.027034 |  | 2274 | 13.153 | 54.72 | 14.696 | 0.077147 | 0.027034
2275 | 54.73 | 14.696 | 0.077145 | 13.155 | 0.027039 |  | 2275 | 13.155 | 54.73 | 14.696 | 0.077145 | 0.027039
2276 | 54.74 | 14.696 | 0.077144 | 13.157 | 0.027044 |  | 2276 | 13.157 | 54.74 | 14.696 | 0.077144 | 0.027044
2277 | 54.75 | 14.696 | 0.077142 | 13.16 | 0.027048 |  | 2277 | 13.16 | 54.75 | 14.696 | 0.077142 | 0.027048
2278 | 54.76 | 14.696 | 0.077141 | 13.162 | 0.027053 |  | 2278 | 13.162 | 54.76 | 14.696 | 0.077141 | 0.027053
2279 | 54.77 | 14.696 | 0.077139 | 13.165 | 0.027058 |  | 2279 | 13.165 | 54.77 | 14.696 | 0.077139 | 0.027058
2280 | 54.78 | 14.696 | 0.077138 | 13.167 | 0.027062 |  | 2280 | 13.167 | 54.78 | 14.696 | 0.077138 | 0.027062
2281 | 54.79 | 14.696 | 0.077136 | 13.169 | 0.027067 |  | 2281 | 13.169 | 54.79 | 14.696 | 0.077136 | 0.027067
2282 | 54.8 | 14.696 | 0.077135 | 13.172 | 0.027072 |  | 2282 | 13.172 | 54.8 | 14.696 | 0.077135 | 0.027072
2283 | 54.81 | 14.696 | 0.077133 | 13.174 | 0.027076 |  | 2283 | 13.174 | 54.81 | 14.696 | 0.077133 | 0.027076
2284 | 54.82 | 14.696 | 0.077132 | 13.177 | 0.027081 |  | 2284 | 13.177 | 54.82 | 14.696 | 0.077132 | 0.027081
2285 | 54.83 | 14.696 | 0.07713 | 13.179 | 0.027086 |  | 2285 | 13.179 | 54.83 | 14.696 | 0.07713 | 0.027086
2286 | 54.84 | 14.696 | 0.077129 | 13.182 | 0.02709 |  | 2286 | 13.182 | 54.84 | 14.696 | 0.077129 | 0.02709
2287 | 54.85 | 14.696 | 0.077127 | 13.184 | 0.027095 |  | 2287 | 13.184 | 54.85 | 14.696 | 0.077127 | 0.027095
2288 | 54.86 | 14.696 | 0.077126 | 13.186 | 0.0271 |  | 2288 | 13.186 | 54.86 | 14.696 | 0.077126 | 0.0271
2289 | 54.87 | 14.696 | 0.077124 | 13.189 | 0.027104 |  | 2289 | 13.189 | 54.87 | 14.696 | 0.077124 | 0.027104
2290 | 54.88 | 14.696 | 0.077123 | 13.191 | 0.027109 |  | 2290 | 13.191 | 54.88 | 14.696 | 0.077123 | 0.027109
2291 | 54.89 | 14.696 | 0.077121 | 13.194 | 0.027114 |  | 2291 | 13.194 | 54.89 | 14.696 | 0.077121 | 0.027114
2292 | 54.9 | 14.696 | 0.07712 | 13.196 | 0.027118 |  | 2292 | 13.196 | 54.9 | 14.696 | 0.07712 | 0.027118
2293 | 54.91 | 14.696 | 0.077118 | 13.198 | 0.027123 |  | 2293 | 13.198 | 54.91 | 14.696 | 0.077118 | 0.027123
2294 | 54.92 | 14.696 | 0.077117 | 13.201 | 0.027128 |  | 2294 | 13.201 | 54.92 | 14.696 | 0.077117 | 0.027128
2295 | 54.93 | 14.696 | 0.077115 | 13.203 | 0.027132 |  | 2295 | 13.203 | 54.93 | 14.696 | 0.077115 | 0.027132
2296 | 54.94 | 14.696 | 0.077114 | 13.206 | 0.027137 |  | 2296 | 13.206 | 54.94 | 14.696 | 0.077114 | 0.027137
2297 | 54.95 | 14.696 | 0.077112 | 13.208 | 0.027142 |  | 2297 | 13.208 | 54.95 | 14.696 | 0.077112 | 0.027142
2298 | 54.96 | 14.696 | 0.077111 | 13.21 | 0.027146 |  | 2298 | 13.21 | 54.96 | 14.696 | 0.077111 | 0.027146
2299 | 54.97 | 14.696 | 0.077109 | 13.213 | 0.027151 |  | 2299 | 13.213 | 54.97 | 14.696 | 0.077109 | 0.027151
2300 | 54.98 | 14.696 | 0.077108 | 13.215 | 0.027156 |  | 2300 | 13.215 | 54.98 | 14.696 | 0.077108 | 0.027156
2301 | 54.99 | 14.696 | 0.077106 | 13.218 | 0.02716 |  | 2301 | 13.218 | 54.99 | 14.696 | 0.077106 | 0.02716
2302 | 55 | 14.696 | 0.077105 | 13.22 | 0.027165 |  | 2302 | 13.22 | 55 | 14.696 | 0.077105 | 0.027165
2303 | 55.01 | 14.696 | 0.077103 | 13.222 | 0.02717 |  | 2303 | 13.222 | 55.01 | 14.696 | 0.077103 | 0.02717
2304 | 55.02 | 14.696 | 0.077102 | 13.225 | 0.027174 |  | 2304 | 13.225 | 55.02 | 14.696 | 0.077102 | 0.027174
2305 | 55.03 | 14.696 | 0.0771 | 13.227 | 0.027179 |  | 2305 | 13.227 | 55.03 | 14.696 | 0.0771 | 0.027179
2306 | 55.04 | 14.696 | 0.077099 | 13.23 | 0.027184 |  | 2306 | 13.23 | 55.04 | 14.696 | 0.077099 | 0.027184
2307 | 55.05 | 14.696 | 0.077097 | 13.232 | 0.027188 |  | 2307 | 13.232 | 55.05 | 14.696 | 0.077097 | 0.027188
2308 | 55.06 | 14.696 | 0.077096 | 13.234 | 0.027193 |  | 2308 | 13.234 | 55.06 | 14.696 | 0.077096 | 0.027193
2309 | 55.07 | 14.696 | 0.077094 | 13.237 | 0.027198 |  | 2309 | 13.237 | 55.07 | 14.696 | 0.077094 | 0.027198
2310 | 55.08 | 14.696 | 0.077093 | 13.239 | 0.027202 |  | 2310 | 13.239 | 55.08 | 14.696 | 0.077093 | 0.027202
2311 | 55.09 | 14.696 | 0.077091 | 13.242 | 0.027207 |  | 2311 | 13.242 | 55.09 | 14.696 | 0.077091 | 0.027207
2312 | 55.1 | 14.696 | 0.07709 | 13.244 | 0.027212 |  | 2312 | 13.244 | 55.1 | 14.696 | 0.07709 | 0.027212
2313 | 55.11 | 14.696 | 0.077088 | 13.246 | 0.027216 |  | 2313 | 13.246 | 55.11 | 14.696 | 0.077088 | 0.027216
2314 | 55.12 | 14.696 | 0.077087 | 13.249 | 0.027221 |  | 2314 | 13.249 | 55.12 | 14.696 | 0.077087 | 0.027221
2315 | 55.13 | 14.696 | 0.077085 | 13.251 | 0.027226 |  | 2315 | 13.251 | 55.13 | 14.696 | 0.077085 | 0.027226
2316 | 55.14 | 14.696 | 0.077084 | 13.254 | 0.02723 |  | 2316 | 13.254 | 55.14 | 14.696 | 0.077084 | 0.02723
2317 | 55.15 | 14.696 | 0.077082 | 13.256 | 0.027235 |  | 2317 | 13.256 | 55.15 | 14.696 | 0.077082 | 0.027235
2318 | 55.16 | 14.696 | 0.077081 | 13.258 | 0.02724 |  | 2318 | 13.258 | 55.16 | 14.696 | 0.077081 | 0.02724
2319 | 55.17 | 14.696 | 0.077079 | 13.261 | 0.027244 |  | 2319 | 13.261 | 55.17 | 14.696 | 0.077079 | 0.027244
2320 | 55.18 | 14.696 | 0.077078 | 13.263 | 0.027249 |  | 2320 | 13.263 | 55.18 | 14.696 | 0.077078 | 0.027249
2321 | 55.19 | 14.696 | 0.077076 | 13.266 | 0.027254 |  | 2321 | 13.266 | 55.19 | 14.696 | 0.077076 | 0.027254
2322 | 55.2 | 14.696 | 0.077075 | 13.268 | 0.027258 |  | 2322 | 13.268 | 55.2 | 14.696 | 0.077075 | 0.027258
2323 | 55.21 | 14.696 | 0.077073 | 13.27 | 0.027263 |  | 2323 | 13.27 | 55.21 | 14.696 | 0.077073 | 0.027263
2324 | 55.22 | 14.696 | 0.077072 | 13.273 | 0.027268 |  | 2324 | 13.273 | 55.22 | 14.696 | 0.077072 | 0.027268
2325 | 55.23 | 14.696 | 0.07707 | 13.275 | 0.027272 |  | 2325 | 13.275 | 55.23 | 14.696 | 0.07707 | 0.027272
2326 | 55.24 | 14.696 | 0.077069 | 13.278 | 0.027277 |  | 2326 | 13.278 | 55.24 | 14.696 | 0.077069 | 0.027277
2327 | 55.25 | 14.696 | 0.077067 | 13.28 | 0.027282 |  | 2327 | 13.28 | 55.25 | 14.696 | 0.077067 | 0.027282
2328 | 55.26 | 14.696 | 0.077066 | 13.282 | 0.027286 |  | 2328 | 13.282 | 55.26 | 14.696 | 0.077066 | 0.027286
2329 | 55.27 | 14.696 | 0.077064 | 13.285 | 0.027291 |  | 2329 | 13.285 | 55.27 | 14.696 | 0.077064 | 0.027291
2330 | 55.28 | 14.696 | 0.077063 | 13.287 | 0.027296 |  | 2330 | 13.287 | 55.28 | 14.696 | 0.077063 | 0.027296
2331 | 55.29 | 14.696 | 0.077061 | 13.29 | 0.0273 |  | 2331 | 13.29 | 55.29 | 14.696 | 0.077061 | 0.0273
2332 | 55.3 | 14.696 | 0.07706 | 13.292 | 0.027305 |  | 2332 | 13.292 | 55.3 | 14.696 | 0.07706 | 0.027305
2333 | 55.31 | 14.696 | 0.077058 | 13.295 | 0.02731 |  | 2333 | 13.295 | 55.31 | 14.696 | 0.077058 | 0.02731
2334 | 55.32 | 14.696 | 0.077057 | 13.297 | 0.027314 |  | 2334 | 13.297 | 55.32 | 14.696 | 0.077057 | 0.027314
2335 | 55.33 | 14.696 | 0.077055 | 13.299 | 0.027319 |  | 2335 | 13.299 | 55.33 | 14.696 | 0.077055 | 0.027319
2336 | 55.34 | 14.696 | 0.077054 | 13.302 | 0.027324 |  | 2336 | 13.302 | 55.34 | 14.696 | 0.077054 | 0.027324
2337 | 55.35 | 14.696 | 0.077052 | 13.304 | 0.027328 |  | 2337 | 13.304 | 55.35 | 14.696 | 0.077052 | 0.027328
2338 | 55.36 | 14.696 | 0.077051 | 13.307 | 0.027333 |  | 2338 | 13.307 | 55.36 | 14.696 | 0.077051 | 0.027333
2339 | 55.37 | 14.696 | 0.077049 | 13.309 | 0.027338 |  | 2339 | 13.309 | 55.37 | 14.696 | 0.077049 | 0.027338
2340 | 55.38 | 14.696 | 0.077048 | 13.311 | 0.027342 |  | 2340 | 13.311 | 55.38 | 14.696 | 0.077048 | 0.027342
2341 | 55.39 | 14.696 | 0.077046 | 13.314 | 0.027347 |  | 2341 | 13.314 | 55.39 | 14.696 | 0.077046 | 0.027347
2342 | 55.4 | 14.696 | 0.077045 | 13.316 | 0.027352 |  | 2342 | 13.316 | 55.4 | 14.696 | 0.077045 | 0.027352
2343 | 55.41 | 14.696 | 0.077043 | 13.319 | 0.027356 |  | 2343 | 13.319 | 55.41 | 14.696 | 0.077043 | 0.027356
2344 | 55.42 | 14.696 | 0.077042 | 13.321 | 0.027361 |  | 2344 | 13.321 | 55.42 | 14.696 | 0.077042 | 0.027361
2345 | 55.43 | 14.696 | 0.07704 | 13.323 | 0.027366 |  | 2345 | 13.323 | 55.43 | 14.696 | 0.07704 | 0.027366
2346 | 55.44 | 14.696 | 0.077039 | 13.326 | 0.02737 |  | 2346 | 13.326 | 55.44 | 14.696 | 0.077039 | 0.02737
2347 | 55.45 | 14.696 | 0.077037 | 13.328 | 0.027375 |  | 2347 | 13.328 | 55.45 | 14.696 | 0.077037 | 0.027375
2348 | 55.46 | 14.696 | 0.077036 | 13.331 | 0.02738 |  | 2348 | 13.331 | 55.46 | 14.696 | 0.077036 | 0.02738
2349 | 55.47 | 14.696 | 0.077034 | 13.333 | 0.027384 |  | 2349 | 13.333 | 55.47 | 14.696 | 0.077034 | 0.027384
2350 | 55.48 | 14.696 | 0.077033 | 13.335 | 0.027389 |  | 2350 | 13.335 | 55.48 | 14.696 | 0.077033 | 0.027389
2351 | 55.49 | 14.696 | 0.077031 | 13.338 | 0.027394 |  | 2351 | 13.338 | 55.49 | 14.696 | 0.077031 | 0.027394
2352 | 55.5 | 14.696 | 0.07703 | 13.34 | 0.027398 |  | 2352 | 13.34 | 55.5 | 14.696 | 0.07703 | 0.027398
2353 | 55.51 | 14.696 | 0.077028 | 13.343 | 0.027403 |  | 2353 | 13.343 | 55.51 | 14.696 | 0.077028 | 0.027403
2354 | 55.52 | 14.696 | 0.077027 | 13.345 | 0.027408 |  | 2354 | 13.345 | 55.52 | 14.696 | 0.077027 | 0.027408
2355 | 55.53 | 14.696 | 0.077025 | 13.347 | 0.027412 |  | 2355 | 13.347 | 55.53 | 14.696 | 0.077025 | 0.027412
2356 | 55.54 | 14.696 | 0.077024 | 13.35 | 0.027417 |  | 2356 | 13.35 | 55.54 | 14.696 | 0.077024 | 0.027417
2357 | 55.55 | 14.696 | 0.077022 | 13.352 | 0.027422 |  | 2357 | 13.352 | 55.55 | 14.696 | 0.077022 | 0.027422
2358 | 55.56 | 14.696 | 0.077021 | 13.355 | 0.027426 |  | 2358 | 13.355 | 55.56 | 14.696 | 0.077021 | 0.027426
2359 | 55.57 | 14.696 | 0.077019 | 13.357 | 0.027431 |  | 2359 | 13.357 | 55.57 | 14.696 | 0.077019 | 0.027431
2360 | 55.58 | 14.696 | 0.077018 | 13.359 | 0.027436 |  | 2360 | 13.359 | 55.58 | 14.696 | 0.077018 | 0.027436
2361 | 55.59 | 14.696 | 0.077016 | 13.362 | 0.02744 |  | 2361 | 13.362 | 55.59 | 14.696 | 0.077016 | 0.02744
2362 | 55.6 | 14.696 | 0.077015 | 13.364 | 0.027445 |  | 2362 | 13.364 | 55.6 | 14.696 | 0.077015 | 0.027445
2363 | 55.61 | 14.696 | 0.077013 | 13.367 | 0.02745 |  | 2363 | 13.367 | 55.61 | 14.696 | 0.077013 | 0.02745
2364 | 55.62 | 14.696 | 0.077012 | 13.369 | 0.027454 |  | 2364 | 13.369 | 55.62 | 14.696 | 0.077012 | 0.027454
2365 | 55.63 | 14.696 | 0.07701 | 13.371 | 0.027459 |  | 2365 | 13.371 | 55.63 | 14.696 | 0.07701 | 0.027459
2366 | 55.64 | 14.696 | 0.077009 | 13.374 | 0.027464 |  | 2366 | 13.374 | 55.64 | 14.696 | 0.077009 | 0.027464
2367 | 55.65 | 14.696 | 0.077007 | 13.376 | 0.027468 |  | 2367 | 13.376 | 55.65 | 14.696 | 0.077007 | 0.027468
2368 | 55.66 | 14.696 | 0.077006 | 13.379 | 0.027473 |  | 2368 | 13.379 | 55.66 | 14.696 | 0.077006 | 0.027473
2369 | 55.67 | 14.696 | 0.077004 | 13.381 | 0.027478 |  | 2369 | 13.381 | 55.67 | 14.696 | 0.077004 | 0.027478
2370 | 55.68 | 14.696 | 0.077003 | 13.383 | 0.027482 |  | 2370 | 13.383 | 55.68 | 14.696 | 0.077003 | 0.027482
2371 | 55.69 | 14.696 | 0.077001 | 13.386 | 0.027487 |  | 2371 | 13.386 | 55.69 | 14.696 | 0.077001 | 0.027487
2372 | 55.7 | 14.696 | 0.077 | 13.388 | 0.027492 |  | 2372 | 13.388 | 55.7 | 14.696 | 0.077 | 0.027492
2373 | 55.71 | 14.696 | 0.076998 | 13.391 | 0.027496 |  | 2373 | 13.391 | 55.71 | 14.696 | 0.076998 | 0.027496
2374 | 55.72 | 14.696 | 0.076997 | 13.393 | 0.027501 |  | 2374 | 13.393 | 55.72 | 14.696 | 0.076997 | 0.027501
2375 | 55.73 | 14.696 | 0.076995 | 13.395 | 0.027506 |  | 2375 | 13.395 | 55.73 | 14.696 | 0.076995 | 0.027506
2376 | 55.74 | 14.696 | 0.076994 | 13.398 | 0.02751 |  | 2376 | 13.398 | 55.74 | 14.696 | 0.076994 | 0.02751
2377 | 55.75 | 14.696 | 0.076992 | 13.4 | 0.027515 |  | 2377 | 13.4 | 55.75 | 14.696 | 0.076992 | 0.027515
2378 | 55.76 | 14.696 | 0.076991 | 13.403 | 0.02752 |  | 2378 | 13.403 | 55.76 | 14.696 | 0.076991 | 0.02752
2379 | 55.77 | 14.696 | 0.076989 | 13.405 | 0.027524 |  | 2379 | 13.405 | 55.77 | 14.696 | 0.076989 | 0.027524
2380 | 55.78 | 14.696 | 0.076988 | 13.408 | 0.027529 |  | 2380 | 13.408 | 55.78 | 14.696 | 0.076988 | 0.027529
2381 | 55.79 | 14.696 | 0.076986 | 13.41 | 0.027534 |  | 2381 | 13.41 | 55.79 | 14.696 | 0.076986 | 0.027534
2382 | 55.8 | 14.696 | 0.076985 | 13.412 | 0.027538 |  | 2382 | 13.412 | 55.8 | 14.696 | 0.076985 | 0.027538
2383 | 55.81 | 14.696 | 0.076983 | 13.415 | 0.027543 |  | 2383 | 13.415 | 55.81 | 14.696 | 0.076983 | 0.027543
2384 | 55.82 | 14.696 | 0.076982 | 13.417 | 0.027548 |  | 2384 | 13.417 | 55.82 | 14.696 | 0.076982 | 0.027548
2385 | 55.83 | 14.696 | 0.07698 | 13.42 | 0.027552 |  | 2385 | 13.42 | 55.83 | 14.696 | 0.07698 | 0.027552
2386 | 55.84 | 14.696 | 0.076979 | 13.422 | 0.027557 |  | 2386 | 13.422 | 55.84 | 14.696 | 0.076979 | 0.027557
2387 | 55.85 | 14.696 | 0.076977 | 13.424 | 0.027562 |  | 2387 | 13.424 | 55.85 | 14.696 | 0.076977 | 0.027562
2388 | 55.86 | 14.696 | 0.076976 | 13.427 | 0.027566 |  | 2388 | 13.427 | 55.86 | 14.696 | 0.076976 | 0.027566
2389 | 55.87 | 14.696 | 0.076974 | 13.429 | 0.027571 |  | 2389 | 13.429 | 55.87 | 14.696 | 0.076974 | 0.027571
2390 | 55.88 | 14.696 | 0.076973 | 13.432 | 0.027576 |  | 2390 | 13.432 | 55.88 | 14.696 | 0.076973 | 0.027576
2391 | 55.89 | 14.696 | 0.076971 | 13.434 | 0.02758 |  | 2391 | 13.434 | 55.89 | 14.696 | 0.076971 | 0.02758
2392 | 55.9 | 14.696 | 0.07697 | 13.436 | 0.027585 |  | 2392 | 13.436 | 55.9 | 14.696 | 0.07697 | 0.027585
2393 | 55.91 | 14.696 | 0.076968 | 13.439 | 0.02759 |  | 2393 | 13.439 | 55.91 | 14.696 | 0.076968 | 0.02759
2394 | 55.92 | 14.696 | 0.076967 | 13.441 | 0.027594 |  | 2394 | 13.441 | 55.92 | 14.696 | 0.076967 | 0.027594
2395 | 55.93 | 14.696 | 0.076965 | 13.444 | 0.027599 |  | 2395 | 13.444 | 55.93 | 14.696 | 0.076965 | 0.027599
2396 | 55.94 | 14.696 | 0.076964 | 13.446 | 0.027604 |  | 2396 | 13.446 | 55.94 | 14.696 | 0.076964 | 0.027604
2397 | 55.95 | 14.696 | 0.076962 | 13.448 | 0.027608 |  | 2397 | 13.448 | 55.95 | 14.696 | 0.076962 | 0.027608
2398 | 55.96 | 14.696 | 0.076961 | 13.451 | 0.027613 |  | 2398 | 13.451 | 55.96 | 14.696 | 0.076961 | 0.027613
2399 | 55.97 | 14.696 | 0.076959 | 13.453 | 0.027618 |  | 2399 | 13.453 | 55.97 | 14.696 | 0.076959 | 0.027618
2400 | 55.98 | 14.696 | 0.076958 | 13.456 | 0.027622 |  | 2400 | 13.456 | 55.98 | 14.696 | 0.076958 | 0.027622
2401 | 55.99 | 14.696 | 0.076956 | 13.458 | 0.027627 |  | 2401 | 13.458 | 55.99 | 14.696 | 0.076956 | 0.027627
2402 | 56 | 14.696 | 0.076955 | 13.46 | 0.027632 |  | 2402 | 13.46 | 56 | 14.696 | 0.076955 | 0.027632
2403 | 56.01 | 14.696 | 0.076953 | 13.463 | 0.027636 |  | 2403 | 13.463 | 56.01 | 14.696 | 0.076953 | 0.027636
2404 | 56.02 | 14.696 | 0.076952 | 13.465 | 0.027641 |  | 2404 | 13.465 | 56.02 | 14.696 | 0.076952 | 0.027641
2405 | 56.03 | 14.696 | 0.07695 | 13.468 | 0.027646 |  | 2405 | 13.468 | 56.03 | 14.696 | 0.07695 | 0.027646
2406 | 56.04 | 14.696 | 0.076949 | 13.47 | 0.02765 |  | 2406 | 13.47 | 56.04 | 14.696 | 0.076949 | 0.02765
2407 | 56.05 | 14.696 | 0.076947 | 13.472 | 0.027655 |  | 2407 | 13.472 | 56.05 | 14.696 | 0.076947 | 0.027655
2408 | 56.06 | 14.696 | 0.076946 | 13.475 | 0.02766 |  | 2408 | 13.475 | 56.06 | 14.696 | 0.076946 | 0.02766
2409 | 56.07 | 14.696 | 0.076944 | 13.477 | 0.027664 |  | 2409 | 13.477 | 56.07 | 14.696 | 0.076944 | 0.027664
2410 | 56.08 | 14.696 | 0.076943 | 13.48 | 0.027669 |  | 2410 | 13.48 | 56.08 | 14.696 | 0.076943 | 0.027669
2411 | 56.09 | 14.696 | 0.076941 | 13.482 | 0.027674 |  | 2411 | 13.482 | 56.09 | 14.696 | 0.076941 | 0.027674
2412 | 56.1 | 14.696 | 0.07694 | 13.484 | 0.027678 |  | 2412 | 13.484 | 56.1 | 14.696 | 0.07694 | 0.027678
2413 | 56.11 | 14.696 | 0.076938 | 13.487 | 0.027683 |  | 2413 | 13.487 | 56.11 | 14.696 | 0.076938 | 0.027683
2414 | 56.12 | 14.696 | 0.076937 | 13.489 | 0.027688 |  | 2414 | 13.489 | 56.12 | 14.696 | 0.076937 | 0.027688
2415 | 56.13 | 14.696 | 0.076935 | 13.492 | 0.027692 |  | 2415 | 13.492 | 56.13 | 14.696 | 0.076935 | 0.027692
2416 | 56.14 | 14.696 | 0.076934 | 13.494 | 0.027697 |  | 2416 | 13.494 | 56.14 | 14.696 | 0.076934 | 0.027697
2417 | 56.15 | 14.696 | 0.076932 | 13.496 | 0.027702 |  | 2417 | 13.496 | 56.15 | 14.696 | 0.076932 | 0.027702
2418 | 56.16 | 14.696 | 0.076931 | 13.499 | 0.027706 |  | 2418 | 13.499 | 56.16 | 14.696 | 0.076931 | 0.027706
2419 | 56.17 | 14.696 | 0.076929 | 13.501 | 0.027711 |  | 2419 | 13.501 | 56.17 | 14.696 | 0.076929 | 0.027711
2420 | 56.18 | 14.696 | 0.076928 | 13.504 | 0.027716 |  | 2420 | 13.504 | 56.18 | 14.696 | 0.076928 | 0.027716
2421 | 56.19 | 14.696 | 0.076926 | 13.506 | 0.02772 |  | 2421 | 13.506 | 56.19 | 14.696 | 0.076926 | 0.02772
2422 | 56.2 | 14.696 | 0.076925 | 13.508 | 0.027725 |  | 2422 | 13.508 | 56.2 | 14.696 | 0.076925 | 0.027725
2423 | 56.21 | 14.696 | 0.076923 | 13.511 | 0.02773 |  | 2423 | 13.511 | 56.21 | 14.696 | 0.076923 | 0.02773
2424 | 56.22 | 14.696 | 0.076922 | 13.513 | 0.027734 |  | 2424 | 13.513 | 56.22 | 14.696 | 0.076922 | 0.027734
2425 | 56.23 | 14.696 | 0.07692 | 13.516 | 0.027739 |  | 2425 | 13.516 | 56.23 | 14.696 | 0.07692 | 0.027739
2426 | 56.24 | 14.696 | 0.076919 | 13.518 | 0.027744 |  | 2426 | 13.518 | 56.24 | 14.696 | 0.076919 | 0.027744
2427 | 56.25 | 14.696 | 0.076917 | 13.521 | 0.027748 |  | 2427 | 13.521 | 56.25 | 14.696 | 0.076917 | 0.027748
2428 | 56.26 | 14.696 | 0.076916 | 13.523 | 0.027753 |  | 2428 | 13.523 | 56.26 | 14.696 | 0.076916 | 0.027753
2429 | 56.27 | 14.696 | 0.076914 | 13.525 | 0.027758 |  | 2429 | 13.525 | 56.27 | 14.696 | 0.076914 | 0.027758
2430 | 56.28 | 14.696 | 0.076913 | 13.528 | 0.027762 |  | 2430 | 13.528 | 56.28 | 14.696 | 0.076913 | 0.027762
2431 | 56.29 | 14.696 | 0.076911 | 13.53 | 0.027767 |  | 2431 | 13.53 | 56.29 | 14.696 | 0.076911 | 0.027767
2432 | 56.3 | 14.696 | 0.07691 | 13.533 | 0.027772 |  | 2432 | 13.533 | 56.3 | 14.696 | 0.07691 | 0.027772
2433 | 56.31 | 14.696 | 0.076908 | 13.535 | 0.027776 |  | 2433 | 13.535 | 56.31 | 14.696 | 0.076908 | 0.027776
2434 | 56.32 | 14.696 | 0.076907 | 13.537 | 0.027781 |  | 2434 | 13.537 | 56.32 | 14.696 | 0.076907 | 0.027781
2435 | 56.33 | 14.696 | 0.076905 | 13.54 | 0.027786 |  | 2435 | 13.54 | 56.33 | 14.696 | 0.076905 | 0.027786
2436 | 56.34 | 14.696 | 0.076904 | 13.542 | 0.02779 |  | 2436 | 13.542 | 56.34 | 14.696 | 0.076904 | 0.02779
2437 | 56.35 | 14.696 | 0.076902 | 13.545 | 0.027795 |  | 2437 | 13.545 | 56.35 | 14.696 | 0.076902 | 0.027795
2438 | 56.36 | 14.696 | 0.076901 | 13.547 | 0.0278 |  | 2438 | 13.547 | 56.36 | 14.696 | 0.076901 | 0.0278
2439 | 56.37 | 14.696 | 0.076899 | 13.549 | 0.027804 |  | 2439 | 13.549 | 56.37 | 14.696 | 0.076899 | 0.027804
2440 | 56.38 | 14.696 | 0.076898 | 13.552 | 0.027809 |  | 2440 | 13.552 | 56.38 | 14.696 | 0.076898 | 0.027809
2441 | 56.39 | 14.696 | 0.076896 | 13.554 | 0.027813 |  | 2441 | 13.554 | 56.39 | 14.696 | 0.076896 | 0.027813
2442 | 56.4 | 14.696 | 0.076895 | 13.557 | 0.027818 |  | 2442 | 13.557 | 56.4 | 14.696 | 0.076895 | 0.027818
2443 | 56.41 | 14.696 | 0.076893 | 13.559 | 0.027823 |  | 2443 | 13.559 | 56.41 | 14.696 | 0.076893 | 0.027823
2444 | 56.42 | 14.696 | 0.076892 | 13.561 | 0.027827 |  | 2444 | 13.561 | 56.42 | 14.696 | 0.076892 | 0.027827
2445 | 56.43 | 14.696 | 0.07689 | 13.564 | 0.027832 |  | 2445 | 13.564 | 56.43 | 14.696 | 0.07689 | 0.027832
2446 | 56.44 | 14.696 | 0.076889 | 13.566 | 0.027837 |  | 2446 | 13.566 | 56.44 | 14.696 | 0.076889 | 0.027837
2447 | 56.45 | 14.696 | 0.076887 | 13.569 | 0.027841 |  | 2447 | 13.569 | 56.45 | 14.696 | 0.076887 | 0.027841
2448 | 56.46 | 14.696 | 0.076886 | 13.571 | 0.027846 |  | 2448 | 13.571 | 56.46 | 14.696 | 0.076886 | 0.027846
2449 | 56.47 | 14.696 | 0.076884 | 13.573 | 0.027851 |  | 2449 | 13.573 | 56.47 | 14.696 | 0.076884 | 0.027851
2450 | 56.48 | 14.696 | 0.076883 | 13.576 | 0.027855 |  | 2450 | 13.576 | 56.48 | 14.696 | 0.076883 | 0.027855
2451 | 56.49 | 14.696 | 0.076881 | 13.578 | 0.02786 |  | 2451 | 13.578 | 56.49 | 14.696 | 0.076881 | 0.02786
2452 | 56.5 | 14.696 | 0.07688 | 13.581 | 0.027865 |  | 2452 | 13.581 | 56.5 | 14.696 | 0.07688 | 0.027865
2453 | 56.51 | 14.696 | 0.076878 | 13.583 | 0.027869 |  | 2453 | 13.583 | 56.51 | 14.696 | 0.076878 | 0.027869
2454 | 56.52 | 14.696 | 0.076877 | 13.585 | 0.027874 |  | 2454 | 13.585 | 56.52 | 14.696 | 0.076877 | 0.027874
2455 | 56.53 | 14.696 | 0.076875 | 13.588 | 0.027879 |  | 2455 | 13.588 | 56.53 | 14.696 | 0.076875 | 0.027879
2456 | 56.54 | 14.696 | 0.076874 | 13.59 | 0.027883 |  | 2456 | 13.59 | 56.54 | 14.696 | 0.076874 | 0.027883
2457 | 56.55 | 14.696 | 0.076872 | 13.593 | 0.027888 |  | 2457 | 13.593 | 56.55 | 14.696 | 0.076872 | 0.027888
2458 | 56.56 | 14.696 | 0.076871 | 13.595 | 0.027893 |  | 2458 | 13.595 | 56.56 | 14.696 | 0.076871 | 0.027893
2459 | 56.57 | 14.696 | 0.076869 | 13.597 | 0.027897 |  | 2459 | 13.597 | 56.57 | 14.696 | 0.076869 | 0.027897
2460 | 56.58 | 14.696 | 0.076868 | 13.6 | 0.027902 |  | 2460 | 13.6 | 56.58 | 14.696 | 0.076868 | 0.027902
2461 | 56.59 | 14.696 | 0.076866 | 13.602 | 0.027907 |  | 2461 | 13.602 | 56.59 | 14.696 | 0.076866 | 0.027907
2462 | 56.6 | 14.696 | 0.076865 | 13.605 | 0.027911 |  | 2462 | 13.605 | 56.6 | 14.696 | 0.076865 | 0.027911
2463 | 56.61 | 14.696 | 0.076863 | 13.607 | 0.027916 |  | 2463 | 13.607 | 56.61 | 14.696 | 0.076863 | 0.027916
2464 | 56.62 | 14.696 | 0.076862 | 13.609 | 0.027921 |  | 2464 | 13.609 | 56.62 | 14.696 | 0.076862 | 0.027921
2465 | 56.63 | 14.696 | 0.07686 | 13.612 | 0.027925 |  | 2465 | 13.612 | 56.63 | 14.696 | 0.07686 | 0.027925
2466 | 56.64 | 14.696 | 0.076859 | 13.614 | 0.02793 |  | 2466 | 13.614 | 56.64 | 14.696 | 0.076859 | 0.02793
2467 | 56.65 | 14.696 | 0.076857 | 13.617 | 0.027935 |  | 2467 | 13.617 | 56.65 | 14.696 | 0.076857 | 0.027935
2468 | 56.66 | 14.696 | 0.076856 | 13.619 | 0.027939 |  | 2468 | 13.619 | 56.66 | 14.696 | 0.076856 | 0.027939
2469 | 56.67 | 14.696 | 0.076854 | 13.621 | 0.027944 |  | 2469 | 13.621 | 56.67 | 14.696 | 0.076854 | 0.027944
2470 | 56.68 | 14.696 | 0.076853 | 13.624 | 0.027949 |  | 2470 | 13.624 | 56.68 | 14.696 | 0.076853 | 0.027949
2471 | 56.69 | 14.696 | 0.076851 | 13.626 | 0.027953 |  | 2471 | 13.626 | 56.69 | 14.696 | 0.076851 | 0.027953
2472 | 56.7 | 14.696 | 0.07685 | 13.629 | 0.027958 |  | 2472 | 13.629 | 56.7 | 14.696 | 0.07685 | 0.027958
2473 | 56.71 | 14.696 | 0.076848 | 13.631 | 0.027963 |  | 2473 | 13.631 | 56.71 | 14.696 | 0.076848 | 0.027963
2474 | 56.72 | 14.696 | 0.076847 | 13.634 | 0.027967 |  | 2474 | 13.634 | 56.72 | 14.696 | 0.076847 | 0.027967
2475 | 56.73 | 14.696 | 0.076846 | 13.636 | 0.027972 |  | 2475 | 13.636 | 56.73 | 14.696 | 0.076846 | 0.027972
2476 | 56.74 | 14.696 | 0.076844 | 13.638 | 0.027977 |  | 2476 | 13.638 | 56.74 | 14.696 | 0.076844 | 0.027977
2477 | 56.75 | 14.696 | 0.076843 | 13.641 | 0.027981 |  | 2477 | 13.641 | 56.75 | 14.696 | 0.076843 | 0.027981
2478 | 56.76 | 14.696 | 0.076841 | 13.643 | 0.027986 |  | 2478 | 13.643 | 56.76 | 14.696 | 0.076841 | 0.027986
2479 | 56.77 | 14.696 | 0.07684 | 13.646 | 0.02799 |  | 2479 | 13.646 | 56.77 | 14.696 | 0.07684 | 0.02799
2480 | 56.78 | 14.696 | 0.076838 | 13.648 | 0.027995 |  | 2480 | 13.648 | 56.78 | 14.696 | 0.076838 | 0.027995
2481 | 56.79 | 14.696 | 0.076837 | 13.65 | 0.028 |  | 2481 | 13.65 | 56.79 | 14.696 | 0.076837 | 0.028
2482 | 56.8 | 14.696 | 0.076835 | 13.653 | 0.028004 |  | 2482 | 13.653 | 56.8 | 14.696 | 0.076835 | 0.028004
2483 | 56.81 | 14.696 | 0.076834 | 13.655 | 0.028009 |  | 2483 | 13.655 | 56.81 | 14.696 | 0.076834 | 0.028009
2484 | 56.82 | 14.696 | 0.076832 | 13.658 | 0.028014 |  | 2484 | 13.658 | 56.82 | 14.696 | 0.076832 | 0.028014
2485 | 56.83 | 14.696 | 0.076831 | 13.66 | 0.028018 |  | 2485 | 13.66 | 56.83 | 14.696 | 0.076831 | 0.028018
2486 | 56.84 | 14.696 | 0.076829 | 13.662 | 0.028023 |  | 2486 | 13.662 | 56.84 | 14.696 | 0.076829 | 0.028023
2487 | 56.85 | 14.696 | 0.076828 | 13.665 | 0.028028 |  | 2487 | 13.665 | 56.85 | 14.696 | 0.076828 | 0.028028
2488 | 56.86 | 14.696 | 0.076826 | 13.667 | 0.028032 |  | 2488 | 13.667 | 56.86 | 14.696 | 0.076826 | 0.028032
2489 | 56.87 | 14.696 | 0.076825 | 13.67 | 0.028037 |  | 2489 | 13.67 | 56.87 | 14.696 | 0.076825 | 0.028037
2490 | 56.88 | 14.696 | 0.076823 | 13.672 | 0.028042 |  | 2490 | 13.672 | 56.88 | 14.696 | 0.076823 | 0.028042
2491 | 56.89 | 14.696 | 0.076822 | 13.674 | 0.028046 |  | 2491 | 13.674 | 56.89 | 14.696 | 0.076822 | 0.028046
2492 | 56.9 | 14.696 | 0.07682 | 13.677 | 0.028051 |  | 2492 | 13.677 | 56.9 | 14.696 | 0.07682 | 0.028051
2493 | 56.91 | 14.696 | 0.076819 | 13.679 | 0.028056 |  | 2493 | 13.679 | 56.91 | 14.696 | 0.076819 | 0.028056
2494 | 56.92 | 14.696 | 0.076817 | 13.682 | 0.02806 |  | 2494 | 13.682 | 56.92 | 14.696 | 0.076817 | 0.02806
2495 | 56.93 | 14.696 | 0.076816 | 13.684 | 0.028065 |  | 2495 | 13.684 | 56.93 | 14.696 | 0.076816 | 0.028065
2496 | 56.94 | 14.696 | 0.076814 | 13.686 | 0.02807 |  | 2496 | 13.686 | 56.94 | 14.696 | 0.076814 | 0.02807
2497 | 56.95 | 14.696 | 0.076813 | 13.689 | 0.028074 |  | 2497 | 13.689 | 56.95 | 14.696 | 0.076813 | 0.028074
2498 | 56.96 | 14.696 | 0.076811 | 13.691 | 0.028079 |  | 2498 | 13.691 | 56.96 | 14.696 | 0.076811 | 0.028079
2499 | 56.97 | 14.696 | 0.07681 | 13.694 | 0.028084 |  | 2499 | 13.694 | 56.97 | 14.696 | 0.07681 | 0.028084
2500 | 56.98 | 14.696 | 0.076808 | 13.696 | 0.028088 |  | 2500 | 13.696 | 56.98 | 14.696 | 0.076808 | 0.028088
2501 | 56.99 | 14.696 | 0.076807 | 13.698 | 0.028093 |  | 2501 | 13.698 | 56.99 | 14.696 | 0.076807 | 0.028093
2502 | 57 | 14.696 | 0.076805 | 13.701 | 0.028098 |  | 2502 | 13.701 | 57 | 14.696 | 0.076805 | 0.028098
2503 | 57.01 | 14.696 | 0.076804 | 13.703 | 0.028102 |  | 2503 | 13.703 | 57.01 | 14.696 | 0.076804 | 0.028102
2504 | 57.02 | 14.696 | 0.076802 | 13.706 | 0.028107 |  | 2504 | 13.706 | 57.02 | 14.696 | 0.076802 | 0.028107
2505 | 57.03 | 14.696 | 0.076801 | 13.708 | 0.028111 |  | 2505 | 13.708 | 57.03 | 14.696 | 0.076801 | 0.028111
2506 | 57.04 | 14.696 | 0.076799 | 13.71 | 0.028116 |  | 2506 | 13.71 | 57.04 | 14.696 | 0.076799 | 0.028116
2507 | 57.05 | 14.696 | 0.076798 | 13.713 | 0.028121 |  | 2507 | 13.713 | 57.05 | 14.696 | 0.076798 | 0.028121
2508 | 57.06 | 14.696 | 0.076796 | 13.715 | 0.028125 |  | 2508 | 13.715 | 57.06 | 14.696 | 0.076796 | 0.028125
2509 | 57.07 | 14.696 | 0.076795 | 13.718 | 0.02813 |  | 2509 | 13.718 | 57.07 | 14.696 | 0.076795 | 0.02813
2510 | 57.08 | 14.696 | 0.076793 | 13.72 | 0.028135 |  | 2510 | 13.72 | 57.08 | 14.696 | 0.076793 | 0.028135
2511 | 57.09 | 14.696 | 0.076792 | 13.722 | 0.028139 |  | 2511 | 13.722 | 57.09 | 14.696 | 0.076792 | 0.028139
2512 | 57.1 | 14.696 | 0.07679 | 13.725 | 0.028144 |  | 2512 | 13.725 | 57.1 | 14.696 | 0.07679 | 0.028144
2513 | 57.11 | 14.696 | 0.076789 | 13.727 | 0.028149 |  | 2513 | 13.727 | 57.11 | 14.696 | 0.076789 | 0.028149
2514 | 57.12 | 14.696 | 0.076787 | 13.73 | 0.028153 |  | 2514 | 13.73 | 57.12 | 14.696 | 0.076787 | 0.028153
2515 | 57.13 | 14.696 | 0.076786 | 13.732 | 0.028158 |  | 2515 | 13.732 | 57.13 | 14.696 | 0.076786 | 0.028158
2516 | 57.14 | 14.696 | 0.076784 | 13.734 | 0.028163 |  | 2516 | 13.734 | 57.14 | 14.696 | 0.076784 | 0.028163
2517 | 57.15 | 14.696 | 0.076783 | 13.737 | 0.028167 |  | 2517 | 13.737 | 57.15 | 14.696 | 0.076783 | 0.028167
2518 | 57.16 | 14.696 | 0.076781 | 13.739 | 0.028172 |  | 2518 | 13.739 | 57.16 | 14.696 | 0.076781 | 0.028172
2519 | 57.17 | 14.696 | 0.07678 | 13.742 | 0.028177 |  | 2519 | 13.742 | 57.17 | 14.696 | 0.07678 | 0.028177
2520 | 57.18 | 14.696 | 0.076778 | 13.744 | 0.028181 |  | 2520 | 13.744 | 57.18 | 14.696 | 0.076778 | 0.028181
2521 | 57.19 | 14.696 | 0.076777 | 13.747 | 0.028186 |  | 2521 | 13.747 | 57.19 | 14.696 | 0.076777 | 0.028186
2522 | 57.2 | 14.696 | 0.076775 | 13.749 | 0.028191 |  | 2522 | 13.749 | 57.2 | 14.696 | 0.076775 | 0.028191
2523 | 57.21 | 14.696 | 0.076774 | 13.751 | 0.028195 |  | 2523 | 13.751 | 57.21 | 14.696 | 0.076774 | 0.028195
2524 | 57.22 | 14.696 | 0.076772 | 13.754 | 0.0282 |  | 2524 | 13.754 | 57.22 | 14.696 | 0.076772 | 0.0282
2525 | 57.23 | 14.696 | 0.076771 | 13.756 | 0.028205 |  | 2525 | 13.756 | 57.23 | 14.696 | 0.076771 | 0.028205
2526 | 57.24 | 14.696 | 0.076769 | 13.759 | 0.028209 |  | 2526 | 13.759 | 57.24 | 14.696 | 0.076769 | 0.028209
2527 | 57.25 | 14.696 | 0.076768 | 13.761 | 0.028214 |  | 2527 | 13.761 | 57.25 | 14.696 | 0.076768 | 0.028214
2528 | 57.26 | 14.696 | 0.076766 | 13.763 | 0.028218 |  | 2528 | 13.763 | 57.26 | 14.696 | 0.076766 | 0.028218
2529 | 57.27 | 14.696 | 0.076765 | 13.766 | 0.028223 |  | 2529 | 13.766 | 57.27 | 14.696 | 0.076765 | 0.028223
2530 | 57.28 | 14.696 | 0.076764 | 13.768 | 0.028228 |  | 2530 | 13.768 | 57.28 | 14.696 | 0.076764 | 0.028228
2531 | 57.29 | 14.696 | 0.076762 | 13.771 | 0.028232 |  | 2531 | 13.771 | 57.29 | 14.696 | 0.076762 | 0.028232
2532 | 57.3 | 14.696 | 0.076761 | 13.773 | 0.028237 |  | 2532 | 13.773 | 57.3 | 14.696 | 0.076761 | 0.028237
2533 | 57.31 | 14.696 | 0.076759 | 13.775 | 0.028242 |  | 2533 | 13.775 | 57.31 | 14.696 | 0.076759 | 0.028242
2534 | 57.32 | 14.696 | 0.076758 | 13.778 | 0.028246 |  | 2534 | 13.778 | 57.32 | 14.696 | 0.076758 | 0.028246
2535 | 57.33 | 14.696 | 0.076756 | 13.78 | 0.028251 |  | 2535 | 13.78 | 57.33 | 14.696 | 0.076756 | 0.028251
2536 | 57.34 | 14.696 | 0.076755 | 13.783 | 0.028256 |  | 2536 | 13.783 | 57.34 | 14.696 | 0.076755 | 0.028256
2537 | 57.35 | 14.696 | 0.076753 | 13.785 | 0.02826 |  | 2537 | 13.785 | 57.35 | 14.696 | 0.076753 | 0.02826
2538 | 57.36 | 14.696 | 0.076752 | 13.787 | 0.028265 |  | 2538 | 13.787 | 57.36 | 14.696 | 0.076752 | 0.028265
2539 | 57.37 | 14.696 | 0.07675 | 13.79 | 0.02827 |  | 2539 | 13.79 | 57.37 | 14.696 | 0.07675 | 0.02827
2540 | 57.38 | 14.696 | 0.076749 | 13.792 | 0.028274 |  | 2540 | 13.792 | 57.38 | 14.696 | 0.076749 | 0.028274
2541 | 57.39 | 14.696 | 0.076747 | 13.795 | 0.028279 |  | 2541 | 13.795 | 57.39 | 14.696 | 0.076747 | 0.028279
2542 | 57.4 | 14.696 | 0.076746 | 13.797 | 0.028284 |  | 2542 | 13.797 | 57.4 | 14.696 | 0.076746 | 0.028284
2543 | 57.41 | 14.696 | 0.076744 | 13.799 | 0.028288 |  | 2543 | 13.799 | 57.41 | 14.696 | 0.076744 | 0.028288
2544 | 57.42 | 14.696 | 0.076743 | 13.802 | 0.028293 |  | 2544 | 13.802 | 57.42 | 14.696 | 0.076743 | 0.028293
2545 | 57.43 | 14.696 | 0.076741 | 13.804 | 0.028298 |  | 2545 | 13.804 | 57.43 | 14.696 | 0.076741 | 0.028298
2546 | 57.44 | 14.696 | 0.07674 | 13.807 | 0.028302 |  | 2546 | 13.807 | 57.44 | 14.696 | 0.07674 | 0.028302
2547 | 57.45 | 14.696 | 0.076738 | 13.809 | 0.028307 |  | 2547 | 13.809 | 57.45 | 14.696 | 0.076738 | 0.028307
2548 | 57.46 | 14.696 | 0.076737 | 13.811 | 0.028311 |  | 2548 | 13.811 | 57.46 | 14.696 | 0.076737 | 0.028311
2549 | 57.47 | 14.696 | 0.076735 | 13.814 | 0.028316 |  | 2549 | 13.814 | 57.47 | 14.696 | 0.076735 | 0.028316
2550 | 57.48 | 14.696 | 0.076734 | 13.816 | 0.028321 |  | 2550 | 13.816 | 57.48 | 14.696 | 0.076734 | 0.028321
2551 | 57.49 | 14.696 | 0.076732 | 13.819 | 0.028325 |  | 2551 | 13.819 | 57.49 | 14.696 | 0.076732 | 0.028325
2552 | 57.5 | 14.696 | 0.076731 | 13.821 | 0.02833 |  | 2552 | 13.821 | 57.5 | 14.696 | 0.076731 | 0.02833
2553 | 57.51 | 14.696 | 0.076729 | 13.823 | 0.028335 |  | 2553 | 13.823 | 57.51 | 14.696 | 0.076729 | 0.028335
2554 | 57.52 | 14.696 | 0.076728 | 13.826 | 0.028339 |  | 2554 | 13.826 | 57.52 | 14.696 | 0.076728 | 0.028339
2555 | 57.53 | 14.696 | 0.076726 | 13.828 | 0.028344 |  | 2555 | 13.828 | 57.53 | 14.696 | 0.076726 | 0.028344
2556 | 57.54 | 14.696 | 0.076725 | 13.831 | 0.028349 |  | 2556 | 13.831 | 57.54 | 14.696 | 0.076725 | 0.028349
2557 | 57.55 | 14.696 | 0.076723 | 13.833 | 0.028353 |  | 2557 | 13.833 | 57.55 | 14.696 | 0.076723 | 0.028353
2558 | 57.56 | 14.696 | 0.076722 | 13.835 | 0.028358 |  | 2558 | 13.835 | 57.56 | 14.696 | 0.076722 | 0.028358
2559 | 57.57 | 14.696 | 0.07672 | 13.838 | 0.028363 |  | 2559 | 13.838 | 57.57 | 14.696 | 0.07672 | 0.028363
2560 | 57.58 | 14.696 | 0.076719 | 13.84 | 0.028367 |  | 2560 | 13.84 | 57.58 | 14.696 | 0.076719 | 0.028367
2561 | 57.59 | 14.696 | 0.076717 | 13.843 | 0.028372 |  | 2561 | 13.843 | 57.59 | 14.696 | 0.076717 | 0.028372
2562 | 57.6 | 14.696 | 0.076716 | 13.845 | 0.028377 |  | 2562 | 13.845 | 57.6 | 14.696 | 0.076716 | 0.028377
2563 | 57.61 | 14.696 | 0.076714 | 13.847 | 0.028381 |  | 2563 | 13.847 | 57.61 | 14.696 | 0.076714 | 0.028381
2564 | 57.62 | 14.696 | 0.076713 | 13.85 | 0.028386 |  | 2564 | 13.85 | 57.62 | 14.696 | 0.076713 | 0.028386
2565 | 57.63 | 14.696 | 0.076711 | 13.852 | 0.028391 |  | 2565 | 13.852 | 57.63 | 14.696 | 0.076711 | 0.028391
2566 | 57.64 | 14.696 | 0.07671 | 13.855 | 0.028395 |  | 2566 | 13.855 | 57.64 | 14.696 | 0.07671 | 0.028395
2567 | 57.65 | 14.696 | 0.076708 | 13.857 | 0.0284 |  | 2567 | 13.857 | 57.65 | 14.696 | 0.076708 | 0.0284
2568 | 57.66 | 14.696 | 0.076707 | 13.86 | 0.028404 |  | 2568 | 13.86 | 57.66 | 14.696 | 0.076707 | 0.028404
2569 | 57.67 | 14.696 | 0.076705 | 13.862 | 0.028409 |  | 2569 | 13.862 | 57.67 | 14.696 | 0.076705 | 0.028409
2570 | 57.68 | 14.696 | 0.076704 | 13.864 | 0.028414 |  | 2570 | 13.864 | 57.68 | 14.696 | 0.076704 | 0.028414
2571 | 57.69 | 14.696 | 0.076702 | 13.867 | 0.028418 |  | 2571 | 13.867 | 57.69 | 14.696 | 0.076702 | 0.028418
2572 | 57.7 | 14.696 | 0.076701 | 13.869 | 0.028423 |  | 2572 | 13.869 | 57.7 | 14.696 | 0.076701 | 0.028423
2573 | 57.71 | 14.696 | 0.0767 | 13.872 | 0.028428 |  | 2573 | 13.872 | 57.71 | 14.696 | 0.0767 | 0.028428
2574 | 57.72 | 14.696 | 0.076698 | 13.874 | 0.028432 |  | 2574 | 13.874 | 57.72 | 14.696 | 0.076698 | 0.028432
2575 | 57.73 | 14.696 | 0.076697 | 13.876 | 0.028437 |  | 2575 | 13.876 | 57.73 | 14.696 | 0.076697 | 0.028437
2576 | 57.74 | 14.696 | 0.076695 | 13.879 | 0.028442 |  | 2576 | 13.879 | 57.74 | 14.696 | 0.076695 | 0.028442
2577 | 57.75 | 14.696 | 0.076694 | 13.881 | 0.028446 |  | 2577 | 13.881 | 57.75 | 14.696 | 0.076694 | 0.028446
2578 | 57.76 | 14.696 | 0.076692 | 13.884 | 0.028451 |  | 2578 | 13.884 | 57.76 | 14.696 | 0.076692 | 0.028451
2579 | 57.77 | 14.696 | 0.076691 | 13.886 | 0.028456 |  | 2579 | 13.886 | 57.77 | 14.696 | 0.076691 | 0.028456
2580 | 57.78 | 14.696 | 0.076689 | 13.888 | 0.02846 |  | 2580 | 13.888 | 57.78 | 14.696 | 0.076689 | 0.02846
2581 | 57.79 | 14.696 | 0.076688 | 13.891 | 0.028465 |  | 2581 | 13.891 | 57.79 | 14.696 | 0.076688 | 0.028465
2582 | 57.8 | 14.696 | 0.076686 | 13.893 | 0.02847 |  | 2582 | 13.893 | 57.8 | 14.696 | 0.076686 | 0.02847
2583 | 57.81 | 14.696 | 0.076685 | 13.896 | 0.028474 |  | 2583 | 13.896 | 57.81 | 14.696 | 0.076685 | 0.028474
2584 | 57.82 | 14.696 | 0.076683 | 13.898 | 0.028479 |  | 2584 | 13.898 | 57.82 | 14.696 | 0.076683 | 0.028479
2585 | 57.83 | 14.696 | 0.076682 | 13.9 | 0.028483 |  | 2585 | 13.9 | 57.83 | 14.696 | 0.076682 | 0.028483
2586 | 57.84 | 14.696 | 0.07668 | 13.903 | 0.028488 |  | 2586 | 13.903 | 57.84 | 14.696 | 0.07668 | 0.028488
2587 | 57.85 | 14.696 | 0.076679 | 13.905 | 0.028493 |  | 2587 | 13.905 | 57.85 | 14.696 | 0.076679 | 0.028493
2588 | 57.86 | 14.696 | 0.076677 | 13.908 | 0.028497 |  | 2588 | 13.908 | 57.86 | 14.696 | 0.076677 | 0.028497
2589 | 57.87 | 14.696 | 0.076676 | 13.91 | 0.028502 |  | 2589 | 13.91 | 57.87 | 14.696 | 0.076676 | 0.028502
2590 | 57.88 | 14.696 | 0.076674 | 13.912 | 0.028507 |  | 2590 | 13.912 | 57.88 | 14.696 | 0.076674 | 0.028507
2591 | 57.89 | 14.696 | 0.076673 | 13.915 | 0.028511 |  | 2591 | 13.915 | 57.89 | 14.696 | 0.076673 | 0.028511
2592 | 57.9 | 14.696 | 0.076671 | 13.917 | 0.028516 |  | 2592 | 13.917 | 57.9 | 14.696 | 0.076671 | 0.028516
2593 | 57.91 | 14.696 | 0.07667 | 13.92 | 0.028521 |  | 2593 | 13.92 | 57.91 | 14.696 | 0.07667 | 0.028521
2594 | 57.92 | 14.696 | 0.076668 | 13.922 | 0.028525 |  | 2594 | 13.922 | 57.92 | 14.696 | 0.076668 | 0.028525
2595 | 57.93 | 14.696 | 0.076667 | 13.924 | 0.02853 |  | 2595 | 13.924 | 57.93 | 14.696 | 0.076667 | 0.02853
2596 | 57.94 | 14.696 | 0.076665 | 13.927 | 0.028535 |  | 2596 | 13.927 | 57.94 | 14.696 | 0.076665 | 0.028535
2597 | 57.95 | 14.696 | 0.076664 | 13.929 | 0.028539 |  | 2597 | 13.929 | 57.95 | 14.696 | 0.076664 | 0.028539
2598 | 57.96 | 14.696 | 0.076662 | 13.932 | 0.028544 |  | 2598 | 13.932 | 57.96 | 14.696 | 0.076662 | 0.028544
2599 | 57.97 | 14.696 | 0.076661 | 13.934 | 0.028548 |  | 2599 | 13.934 | 57.97 | 14.696 | 0.076661 | 0.028548
2600 | 57.98 | 14.696 | 0.076659 | 13.936 | 0.028553 |  | 2600 | 13.936 | 57.98 | 14.696 | 0.076659 | 0.028553
2601 | 57.99 | 14.696 | 0.076658 | 13.939 | 0.028558 |  | 2601 | 13.939 | 57.99 | 14.696 | 0.076658 | 0.028558
2602 | 58 | 14.696 | 0.076656 | 13.941 | 0.028562 |  | 2602 | 13.941 | 58 | 14.696 | 0.076656 | 0.028562
2603 | 58.01 | 14.696 | 0.076655 | 13.944 | 0.028567 |  | 2603 | 13.944 | 58.01 | 14.696 | 0.076655 | 0.028567
2604 | 58.02 | 14.696 | 0.076653 | 13.946 | 0.028572 |  | 2604 | 13.946 | 58.02 | 14.696 | 0.076653 | 0.028572
2605 | 58.03 | 14.696 | 0.076652 | 13.948 | 0.028576 |  | 2605 | 13.948 | 58.03 | 14.696 | 0.076652 | 0.028576
2606 | 58.04 | 14.696 | 0.07665 | 13.951 | 0.028581 |  | 2606 | 13.951 | 58.04 | 14.696 | 0.07665 | 0.028581
2607 | 58.05 | 14.696 | 0.076649 | 13.953 | 0.028586 |  | 2607 | 13.953 | 58.05 | 14.696 | 0.076649 | 0.028586
2608 | 58.06 | 14.696 | 0.076647 | 13.956 | 0.02859 |  | 2608 | 13.956 | 58.06 | 14.696 | 0.076647 | 0.02859
2609 | 58.07 | 14.696 | 0.076646 | 13.958 | 0.028595 |  | 2609 | 13.958 | 58.07 | 14.696 | 0.076646 | 0.028595
2610 | 58.08 | 14.696 | 0.076645 | 13.96 | 0.0286 |  | 2610 | 13.96 | 58.08 | 14.696 | 0.076645 | 0.0286
2611 | 58.09 | 14.696 | 0.076643 | 13.963 | 0.028604 |  | 2611 | 13.963 | 58.09 | 14.696 | 0.076643 | 0.028604
2612 | 58.1 | 14.696 | 0.076642 | 13.965 | 0.028609 |  | 2612 | 13.965 | 58.1 | 14.696 | 0.076642 | 0.028609
2613 | 58.11 | 14.696 | 0.07664 | 13.968 | 0.028614 |  | 2613 | 13.968 | 58.11 | 14.696 | 0.07664 | 0.028614
2614 | 58.12 | 14.696 | 0.076639 | 13.97 | 0.028618 |  | 2614 | 13.97 | 58.12 | 14.696 | 0.076639 | 0.028618
2615 | 58.13 | 14.696 | 0.076637 | 13.973 | 0.028623 |  | 2615 | 13.973 | 58.13 | 14.696 | 0.076637 | 0.028623
2616 | 58.14 | 14.696 | 0.076636 | 13.975 | 0.028627 |  | 2616 | 13.975 | 58.14 | 14.696 | 0.076636 | 0.028627
2617 | 58.15 | 14.696 | 0.076634 | 13.977 | 0.028632 |  | 2617 | 13.977 | 58.15 | 14.696 | 0.076634 | 0.028632
2618 | 58.16 | 14.696 | 0.076633 | 13.98 | 0.028637 |  | 2618 | 13.98 | 58.16 | 14.696 | 0.076633 | 0.028637
2619 | 58.17 | 14.696 | 0.076631 | 13.982 | 0.028641 |  | 2619 | 13.982 | 58.17 | 14.696 | 0.076631 | 0.028641
2620 | 58.18 | 14.696 | 0.07663 | 13.985 | 0.028646 |  | 2620 | 13.985 | 58.18 | 14.696 | 0.07663 | 0.028646
2621 | 58.19 | 14.696 | 0.076628 | 13.987 | 0.028651 |  | 2621 | 13.987 | 58.19 | 14.696 | 0.076628 | 0.028651
2622 | 58.2 | 14.696 | 0.076627 | 13.989 | 0.028655 |  | 2622 | 13.989 | 58.2 | 14.696 | 0.076627 | 0.028655
2623 | 58.21 | 14.696 | 0.076625 | 13.992 | 0.02866 |  | 2623 | 13.992 | 58.21 | 14.696 | 0.076625 | 0.02866
2624 | 58.22 | 14.696 | 0.076624 | 13.994 | 0.028665 |  | 2624 | 13.994 | 58.22 | 14.696 | 0.076624 | 0.028665
2625 | 58.23 | 14.696 | 0.076622 | 13.997 | 0.028669 |  | 2625 | 13.997 | 58.23 | 14.696 | 0.076622 | 0.028669
2626 | 58.24 | 14.696 | 0.076621 | 13.999 | 0.028674 |  | 2626 | 13.999 | 58.24 | 14.696 | 0.076621 | 0.028674
2627 | 58.25 | 14.696 | 0.076619 | 14.001 | 0.028679 |  | 2627 | 14.001 | 58.25 | 14.696 | 0.076619 | 0.028679
2628 | 58.26 | 14.696 | 0.076618 | 14.004 | 0.028683 |  | 2628 | 14.004 | 58.26 | 14.696 | 0.076618 | 0.028683
2629 | 58.27 | 14.696 | 0.076616 | 14.006 | 0.028688 |  | 2629 | 14.006 | 58.27 | 14.696 | 0.076616 | 0.028688
2630 | 58.28 | 14.696 | 0.076615 | 14.009 | 0.028692 |  | 2630 | 14.009 | 58.28 | 14.696 | 0.076615 | 0.028692
2631 | 58.29 | 14.696 | 0.076613 | 14.011 | 0.028697 |  | 2631 | 14.011 | 58.29 | 14.696 | 0.076613 | 0.028697
2632 | 58.3 | 14.696 | 0.076612 | 14.013 | 0.028702 |  | 2632 | 14.013 | 58.3 | 14.696 | 0.076612 | 0.028702
2633 | 58.31 | 14.696 | 0.07661 | 14.016 | 0.028706 |  | 2633 | 14.016 | 58.31 | 14.696 | 0.07661 | 0.028706
2634 | 58.32 | 14.696 | 0.076609 | 14.018 | 0.028711 |  | 2634 | 14.018 | 58.32 | 14.696 | 0.076609 | 0.028711
2635 | 58.33 | 14.696 | 0.076607 | 14.021 | 0.028716 |  | 2635 | 14.021 | 58.33 | 14.696 | 0.076607 | 0.028716
2636 | 58.34 | 14.696 | 0.076606 | 14.023 | 0.02872 |  | 2636 | 14.023 | 58.34 | 14.696 | 0.076606 | 0.02872
2637 | 58.35 | 14.696 | 0.076604 | 14.025 | 0.028725 |  | 2637 | 14.025 | 58.35 | 14.696 | 0.076604 | 0.028725
2638 | 58.36 | 14.696 | 0.076603 | 14.028 | 0.02873 |  | 2638 | 14.028 | 58.36 | 14.696 | 0.076603 | 0.02873
2639 | 58.37 | 14.696 | 0.076601 | 14.03 | 0.028734 |  | 2639 | 14.03 | 58.37 | 14.696 | 0.076601 | 0.028734
2640 | 58.38 | 14.696 | 0.0766 | 14.033 | 0.028739 |  | 2640 | 14.033 | 58.38 | 14.696 | 0.0766 | 0.028739
2641 | 58.39 | 14.696 | 0.076599 | 14.035 | 0.028744 |  | 2641 | 14.035 | 58.39 | 14.696 | 0.076599 | 0.028744
2642 | 58.4 | 14.696 | 0.076597 | 14.037 | 0.028748 |  | 2642 | 14.037 | 58.4 | 14.696 | 0.076597 | 0.028748
2643 | 58.41 | 14.696 | 0.076596 | 14.04 | 0.028753 |  | 2643 | 14.04 | 58.41 | 14.696 | 0.076596 | 0.028753
2644 | 58.42 | 14.696 | 0.076594 | 14.042 | 0.028757 |  | 2644 | 14.042 | 58.42 | 14.696 | 0.076594 | 0.028757
2645 | 58.43 | 14.696 | 0.076593 | 14.045 | 0.028762 |  | 2645 | 14.045 | 58.43 | 14.696 | 0.076593 | 0.028762
2646 | 58.44 | 14.696 | 0.076591 | 14.047 | 0.028767 |  | 2646 | 14.047 | 58.44 | 14.696 | 0.076591 | 0.028767
2647 | 58.45 | 14.696 | 0.07659 | 14.049 | 0.028771 |  | 2647 | 14.049 | 58.45 | 14.696 | 0.07659 | 0.028771
2648 | 58.46 | 14.696 | 0.076588 | 14.052 | 0.028776 |  | 2648 | 14.052 | 58.46 | 14.696 | 0.076588 | 0.028776
2649 | 58.47 | 14.696 | 0.076587 | 14.054 | 0.028781 |  | 2649 | 14.054 | 58.47 | 14.696 | 0.076587 | 0.028781
2650 | 58.48 | 14.696 | 0.076585 | 14.057 | 0.028785 |  | 2650 | 14.057 | 58.48 | 14.696 | 0.076585 | 0.028785
2651 | 58.49 | 14.696 | 0.076584 | 14.059 | 0.02879 |  | 2651 | 14.059 | 58.49 | 14.696 | 0.076584 | 0.02879
2652 | 58.5 | 14.696 | 0.076582 | 14.061 | 0.028795 |  | 2652 | 14.061 | 58.5 | 14.696 | 0.076582 | 0.028795
2653 | 58.51 | 14.696 | 0.076581 | 14.064 | 0.028799 |  | 2653 | 14.064 | 58.51 | 14.696 | 0.076581 | 0.028799
2654 | 58.52 | 14.696 | 0.076579 | 14.066 | 0.028804 |  | 2654 | 14.066 | 58.52 | 14.696 | 0.076579 | 0.028804
2655 | 58.53 | 14.696 | 0.076578 | 14.069 | 0.028808 |  | 2655 | 14.069 | 58.53 | 14.696 | 0.076578 | 0.028808
2656 | 58.54 | 14.696 | 0.076576 | 14.071 | 0.028813 |  | 2656 | 14.071 | 58.54 | 14.696 | 0.076576 | 0.028813
2657 | 58.55 | 14.696 | 0.076575 | 14.074 | 0.028818 |  | 2657 | 14.074 | 58.55 | 14.696 | 0.076575 | 0.028818
2658 | 58.56 | 14.696 | 0.076573 | 14.076 | 0.028822 |  | 2658 | 14.076 | 58.56 | 14.696 | 0.076573 | 0.028822
2659 | 58.57 | 14.696 | 0.076572 | 14.078 | 0.028827 |  | 2659 | 14.078 | 58.57 | 14.696 | 0.076572 | 0.028827
2660 | 58.58 | 14.696 | 0.07657 | 14.081 | 0.028832 |  | 2660 | 14.081 | 58.58 | 14.696 | 0.07657 | 0.028832
2661 | 58.59 | 14.696 | 0.076569 | 14.083 | 0.028836 |  | 2661 | 14.083 | 58.59 | 14.696 | 0.076569 | 0.028836
2662 | 58.6 | 14.696 | 0.076567 | 14.086 | 0.028841 |  | 2662 | 14.086 | 58.6 | 14.696 | 0.076567 | 0.028841
2663 | 58.61 | 14.696 | 0.076566 | 14.088 | 0.028846 |  | 2663 | 14.088 | 58.61 | 14.696 | 0.076566 | 0.028846
2664 | 58.62 | 14.696 | 0.076564 | 14.09 | 0.02885 |  | 2664 | 14.09 | 58.62 | 14.696 | 0.076564 | 0.02885
2665 | 58.63 | 14.696 | 0.076563 | 14.093 | 0.028855 |  | 2665 | 14.093 | 58.63 | 14.696 | 0.076563 | 0.028855
2666 | 58.64 | 14.696 | 0.076561 | 14.095 | 0.02886 |  | 2666 | 14.095 | 58.64 | 14.696 | 0.076561 | 0.02886
2667 | 58.65 | 14.696 | 0.07656 | 14.098 | 0.028864 |  | 2667 | 14.098 | 58.65 | 14.696 | 0.07656 | 0.028864
2668 | 58.66 | 14.696 | 0.076559 | 14.1 | 0.028869 |  | 2668 | 14.1 | 58.66 | 14.696 | 0.076559 | 0.028869
2669 | 58.67 | 14.696 | 0.076557 | 14.102 | 0.028873 |  | 2669 | 14.102 | 58.67 | 14.696 | 0.076557 | 0.028873
2670 | 58.68 | 14.696 | 0.076556 | 14.105 | 0.028878 |  | 2670 | 14.105 | 58.68 | 14.696 | 0.076556 | 0.028878
2671 | 58.69 | 14.696 | 0.076554 | 14.107 | 0.028883 |  | 2671 | 14.107 | 58.69 | 14.696 | 0.076554 | 0.028883
2672 | 58.7 | 14.696 | 0.076553 | 14.11 | 0.028887 |  | 2672 | 14.11 | 58.7 | 14.696 | 0.076553 | 0.028887
2673 | 58.71 | 14.696 | 0.076551 | 14.112 | 0.028892 |  | 2673 | 14.112 | 58.71 | 14.696 | 0.076551 | 0.028892
2674 | 58.72 | 14.696 | 0.07655 | 14.114 | 0.028897 |  | 2674 | 14.114 | 58.72 | 14.696 | 0.07655 | 0.028897
2675 | 58.73 | 14.696 | 0.076548 | 14.117 | 0.028901 |  | 2675 | 14.117 | 58.73 | 14.696 | 0.076548 | 0.028901
2676 | 58.74 | 14.696 | 0.076547 | 14.119 | 0.028906 |  | 2676 | 14.119 | 58.74 | 14.696 | 0.076547 | 0.028906
2677 | 58.75 | 14.696 | 0.076545 | 14.122 | 0.028911 |  | 2677 | 14.122 | 58.75 | 14.696 | 0.076545 | 0.028911
2678 | 58.76 | 14.696 | 0.076544 | 14.124 | 0.028915 |  | 2678 | 14.124 | 58.76 | 14.696 | 0.076544 | 0.028915
2679 | 58.77 | 14.696 | 0.076542 | 14.126 | 0.02892 |  | 2679 | 14.126 | 58.77 | 14.696 | 0.076542 | 0.02892
2680 | 58.78 | 14.696 | 0.076541 | 14.129 | 0.028924 |  | 2680 | 14.129 | 58.78 | 14.696 | 0.076541 | 0.028924
2681 | 58.79 | 14.696 | 0.076539 | 14.131 | 0.028929 |  | 2681 | 14.131 | 58.79 | 14.696 | 0.076539 | 0.028929
2682 | 58.8 | 14.696 | 0.076538 | 14.134 | 0.028934 |  | 2682 | 14.134 | 58.8 | 14.696 | 0.076538 | 0.028934
2683 | 58.81 | 14.696 | 0.076536 | 14.136 | 0.028938 |  | 2683 | 14.136 | 58.81 | 14.696 | 0.076536 | 0.028938
2684 | 58.82 | 14.696 | 0.076535 | 14.138 | 0.028943 |  | 2684 | 14.138 | 58.82 | 14.696 | 0.076535 | 0.028943
2685 | 58.83 | 14.696 | 0.076533 | 14.141 | 0.028948 |  | 2685 | 14.141 | 58.83 | 14.696 | 0.076533 | 0.028948
2686 | 58.84 | 14.696 | 0.076532 | 14.143 | 0.028952 |  | 2686 | 14.143 | 58.84 | 14.696 | 0.076532 | 0.028952
2687 | 58.85 | 14.696 | 0.07653 | 14.146 | 0.028957 |  | 2687 | 14.146 | 58.85 | 14.696 | 0.07653 | 0.028957
2688 | 58.86 | 14.696 | 0.076529 | 14.148 | 0.028962 |  | 2688 | 14.148 | 58.86 | 14.696 | 0.076529 | 0.028962
2689 | 58.87 | 14.696 | 0.076527 | 14.15 | 0.028966 |  | 2689 | 14.15 | 58.87 | 14.696 | 0.076527 | 0.028966
2690 | 58.88 | 14.696 | 0.076526 | 14.153 | 0.028971 |  | 2690 | 14.153 | 58.88 | 14.696 | 0.076526 | 0.028971
2691 | 58.89 | 14.696 | 0.076524 | 14.155 | 0.028975 |  | 2691 | 14.155 | 58.89 | 14.696 | 0.076524 | 0.028975
2692 | 58.9 | 14.696 | 0.076523 | 14.158 | 0.02898 |  | 2692 | 14.158 | 58.9 | 14.696 | 0.076523 | 0.02898
2693 | 58.91 | 14.696 | 0.076521 | 14.16 | 0.028985 |  | 2693 | 14.16 | 58.91 | 14.696 | 0.076521 | 0.028985
2694 | 58.92 | 14.696 | 0.07652 | 14.162 | 0.028989 |  | 2694 | 14.162 | 58.92 | 14.696 | 0.07652 | 0.028989
2695 | 58.93 | 14.696 | 0.076519 | 14.165 | 0.028994 |  | 2695 | 14.165 | 58.93 | 14.696 | 0.076519 | 0.028994
2696 | 58.94 | 14.696 | 0.076517 | 14.167 | 0.028999 |  | 2696 | 14.167 | 58.94 | 14.696 | 0.076517 | 0.028999
2697 | 58.95 | 14.696 | 0.076516 | 14.17 | 0.029003 |  | 2697 | 14.17 | 58.95 | 14.696 | 0.076516 | 0.029003
2698 | 58.96 | 14.696 | 0.076514 | 14.172 | 0.029008 |  | 2698 | 14.172 | 58.96 | 14.696 | 0.076514 | 0.029008
2699 | 58.97 | 14.696 | 0.076513 | 14.174 | 0.029013 |  | 2699 | 14.174 | 58.97 | 14.696 | 0.076513 | 0.029013
2700 | 58.98 | 14.696 | 0.076511 | 14.177 | 0.029017 |  | 2700 | 14.177 | 58.98 | 14.696 | 0.076511 | 0.029017
2701 | 58.99 | 14.696 | 0.07651 | 14.179 | 0.029022 |  | 2701 | 14.179 | 58.99 | 14.696 | 0.07651 | 0.029022
2702 | 59 | 14.696 | 0.076508 | 14.182 | 0.029026 |  | 2702 | 14.182 | 59 | 14.696 | 0.076508 | 0.029026
2703 | 59.01 | 14.696 | 0.076507 | 14.184 | 0.029031 |  | 2703 | 14.184 | 59.01 | 14.696 | 0.076507 | 0.029031
2704 | 59.02 | 14.696 | 0.076505 | 14.187 | 0.029036 |  | 2704 | 14.187 | 59.02 | 14.696 | 0.076505 | 0.029036
2705 | 59.03 | 14.696 | 0.076504 | 14.189 | 0.02904 |  | 2705 | 14.189 | 59.03 | 14.696 | 0.076504 | 0.02904
2706 | 59.04 | 14.696 | 0.076502 | 14.191 | 0.029045 |  | 2706 | 14.191 | 59.04 | 14.696 | 0.076502 | 0.029045
2707 | 59.05 | 14.696 | 0.076501 | 14.194 | 0.02905 |  | 2707 | 14.194 | 59.05 | 14.696 | 0.076501 | 0.02905
2708 | 59.06 | 14.696 | 0.076499 | 14.196 | 0.029054 |  | 2708 | 14.196 | 59.06 | 14.696 | 0.076499 | 0.029054
2709 | 59.07 | 14.696 | 0.076498 | 14.199 | 0.029059 |  | 2709 | 14.199 | 59.07 | 14.696 | 0.076498 | 0.029059
2710 | 59.08 | 14.696 | 0.076496 | 14.201 | 0.029064 |  | 2710 | 14.201 | 59.08 | 14.696 | 0.076496 | 0.029064
2711 | 59.09 | 14.696 | 0.076495 | 14.203 | 0.029068 |  | 2711 | 14.203 | 59.09 | 14.696 | 0.076495 | 0.029068
2712 | 59.1 | 14.696 | 0.076493 | 14.206 | 0.029073 |  | 2712 | 14.206 | 59.1 | 14.696 | 0.076493 | 0.029073
2713 | 59.11 | 14.696 | 0.076492 | 14.208 | 0.029077 |  | 2713 | 14.208 | 59.11 | 14.696 | 0.076492 | 0.029077
2714 | 59.12 | 14.696 | 0.07649 | 14.211 | 0.029082 |  | 2714 | 14.211 | 59.12 | 14.696 | 0.07649 | 0.029082
2715 | 59.13 | 14.696 | 0.076489 | 14.213 | 0.029087 |  | 2715 | 14.213 | 59.13 | 14.696 | 0.076489 | 0.029087
2716 | 59.14 | 14.696 | 0.076487 | 14.215 | 0.029091 |  | 2716 | 14.215 | 59.14 | 14.696 | 0.076487 | 0.029091
2717 | 59.15 | 14.696 | 0.076486 | 14.218 | 0.029096 |  | 2717 | 14.218 | 59.15 | 14.696 | 0.076486 | 0.029096
2718 | 59.16 | 14.696 | 0.076485 | 14.22 | 0.029101 |  | 2718 | 14.22 | 59.16 | 14.696 | 0.076485 | 0.029101
2719 | 59.17 | 14.696 | 0.076483 | 14.223 | 0.029105 |  | 2719 | 14.223 | 59.17 | 14.696 | 0.076483 | 0.029105
2720 | 59.18 | 14.696 | 0.076482 | 14.225 | 0.02911 |  | 2720 | 14.225 | 59.18 | 14.696 | 0.076482 | 0.02911
2721 | 59.19 | 14.696 | 0.07648 | 14.227 | 0.029115 |  | 2721 | 14.227 | 59.19 | 14.696 | 0.07648 | 0.029115
2722 | 59.2 | 14.696 | 0.076479 | 14.23 | 0.029119 |  | 2722 | 14.23 | 59.2 | 14.696 | 0.076479 | 0.029119
2723 | 59.21 | 14.696 | 0.076477 | 14.232 | 0.029124 |  | 2723 | 14.232 | 59.21 | 14.696 | 0.076477 | 0.029124
2724 | 59.22 | 14.696 | 0.076476 | 14.235 | 0.029128 |  | 2724 | 14.235 | 59.22 | 14.696 | 0.076476 | 0.029128
2725 | 59.23 | 14.696 | 0.076474 | 14.237 | 0.029133 |  | 2725 | 14.237 | 59.23 | 14.696 | 0.076474 | 0.029133
2726 | 59.24 | 14.696 | 0.076473 | 14.239 | 0.029138 |  | 2726 | 14.239 | 59.24 | 14.696 | 0.076473 | 0.029138
2727 | 59.25 | 14.696 | 0.076471 | 14.242 | 0.029142 |  | 2727 | 14.242 | 59.25 | 14.696 | 0.076471 | 0.029142
2728 | 59.26 | 14.696 | 0.07647 | 14.244 | 0.029147 |  | 2728 | 14.244 | 59.26 | 14.696 | 0.07647 | 0.029147
2729 | 59.27 | 14.696 | 0.076468 | 14.247 | 0.029152 |  | 2729 | 14.247 | 59.27 | 14.696 | 0.076468 | 0.029152
2730 | 59.28 | 14.696 | 0.076467 | 14.249 | 0.029156 |  | 2730 | 14.249 | 59.28 | 14.696 | 0.076467 | 0.029156
2731 | 59.29 | 14.696 | 0.076465 | 14.251 | 0.029161 |  | 2731 | 14.251 | 59.29 | 14.696 | 0.076465 | 0.029161
2732 | 59.3 | 14.696 | 0.076464 | 14.254 | 0.029165 |  | 2732 | 14.254 | 59.3 | 14.696 | 0.076464 | 0.029165
2733 | 59.31 | 14.696 | 0.076462 | 14.256 | 0.02917 |  | 2733 | 14.256 | 59.31 | 14.696 | 0.076462 | 0.02917
2734 | 59.32 | 14.696 | 0.076461 | 14.259 | 0.029175 |  | 2734 | 14.259 | 59.32 | 14.696 | 0.076461 | 0.029175
2735 | 59.33 | 14.696 | 0.076459 | 14.261 | 0.029179 |  | 2735 | 14.261 | 59.33 | 14.696 | 0.076459 | 0.029179
2736 | 59.34 | 14.696 | 0.076458 | 14.263 | 0.029184 |  | 2736 | 14.263 | 59.34 | 14.696 | 0.076458 | 0.029184
2737 | 59.35 | 14.696 | 0.076456 | 14.266 | 0.029189 |  | 2737 | 14.266 | 59.35 | 14.696 | 0.076456 | 0.029189
2738 | 59.36 | 14.696 | 0.076455 | 14.268 | 0.029193 |  | 2738 | 14.268 | 59.36 | 14.696 | 0.076455 | 0.029193
2739 | 59.37 | 14.696 | 0.076453 | 14.271 | 0.029198 |  | 2739 | 14.271 | 59.37 | 14.696 | 0.076453 | 0.029198
2740 | 59.38 | 14.696 | 0.076452 | 14.273 | 0.029203 |  | 2740 | 14.273 | 59.38 | 14.696 | 0.076452 | 0.029203
2741 | 59.39 | 14.696 | 0.076451 | 14.275 | 0.029207 |  | 2741 | 14.275 | 59.39 | 14.696 | 0.076451 | 0.029207
2742 | 59.4 | 14.696 | 0.076449 | 14.278 | 0.029212 |  | 2742 | 14.278 | 59.4 | 14.696 | 0.076449 | 0.029212
2743 | 59.41 | 14.696 | 0.076448 | 14.28 | 0.029216 |  | 2743 | 14.28 | 59.41 | 14.696 | 0.076448 | 0.029216
2744 | 59.42 | 14.696 | 0.076446 | 14.283 | 0.029221 |  | 2744 | 14.283 | 59.42 | 14.696 | 0.076446 | 0.029221
2745 | 59.43 | 14.696 | 0.076445 | 14.285 | 0.029226 |  | 2745 | 14.285 | 59.43 | 14.696 | 0.076445 | 0.029226
2746 | 59.44 | 14.696 | 0.076443 | 14.287 | 0.02923 |  | 2746 | 14.287 | 59.44 | 14.696 | 0.076443 | 0.02923
2747 | 59.45 | 14.696 | 0.076442 | 14.29 | 0.029235 |  | 2747 | 14.29 | 59.45 | 14.696 | 0.076442 | 0.029235
2748 | 59.46 | 14.696 | 0.07644 | 14.292 | 0.02924 |  | 2748 | 14.292 | 59.46 | 14.696 | 0.07644 | 0.02924
2749 | 59.47 | 14.696 | 0.076439 | 14.295 | 0.029244 |  | 2749 | 14.295 | 59.47 | 14.696 | 0.076439 | 0.029244
2750 | 59.48 | 14.696 | 0.076437 | 14.297 | 0.029249 |  | 2750 | 14.297 | 59.48 | 14.696 | 0.076437 | 0.029249
2751 | 59.49 | 14.696 | 0.076436 | 14.3 | 0.029253 |  | 2751 | 14.3 | 59.49 | 14.696 | 0.076436 | 0.029253
2752 | 59.5 | 14.696 | 0.076434 | 14.302 | 0.029258 |  | 2752 | 14.302 | 59.5 | 14.696 | 0.076434 | 0.029258
2753 | 59.51 | 14.696 | 0.076433 | 14.304 | 0.029263 |  | 2753 | 14.304 | 59.51 | 14.696 | 0.076433 | 0.029263
2754 | 59.52 | 14.696 | 0.076431 | 14.307 | 0.029267 |  | 2754 | 14.307 | 59.52 | 14.696 | 0.076431 | 0.029267
2755 | 59.53 | 14.696 | 0.07643 | 14.309 | 0.029272 |  | 2755 | 14.309 | 59.53 | 14.696 | 0.07643 | 0.029272
2756 | 59.54 | 14.696 | 0.076428 | 14.312 | 0.029277 |  | 2756 | 14.312 | 59.54 | 14.696 | 0.076428 | 0.029277
2757 | 59.55 | 14.696 | 0.076427 | 14.314 | 0.029281 |  | 2757 | 14.314 | 59.55 | 14.696 | 0.076427 | 0.029281
2758 | 59.56 | 14.696 | 0.076425 | 14.316 | 0.029286 |  | 2758 | 14.316 | 59.56 | 14.696 | 0.076425 | 0.029286
2759 | 59.57 | 14.696 | 0.076424 | 14.319 | 0.029291 |  | 2759 | 14.319 | 59.57 | 14.696 | 0.076424 | 0.029291
2760 | 59.58 | 14.696 | 0.076422 | 14.321 | 0.029295 |  | 2760 | 14.321 | 59.58 | 14.696 | 0.076422 | 0.029295
2761 | 59.59 | 14.696 | 0.076421 | 14.324 | 0.0293 |  | 2761 | 14.324 | 59.59 | 14.696 | 0.076421 | 0.0293
2762 | 59.6 | 14.696 | 0.076419 | 14.326 | 0.029304 |  | 2762 | 14.326 | 59.6 | 14.696 | 0.076419 | 0.029304
2763 | 59.61 | 14.696 | 0.076418 | 14.328 | 0.029309 |  | 2763 | 14.328 | 59.61 | 14.696 | 0.076418 | 0.029309
2764 | 59.62 | 14.696 | 0.076417 | 14.331 | 0.029314 |  | 2764 | 14.331 | 59.62 | 14.696 | 0.076417 | 0.029314
2765 | 59.63 | 14.696 | 0.076415 | 14.333 | 0.029318 |  | 2765 | 14.333 | 59.63 | 14.696 | 0.076415 | 0.029318
2766 | 59.64 | 14.696 | 0.076414 | 14.336 | 0.029323 |  | 2766 | 14.336 | 59.64 | 14.696 | 0.076414 | 0.029323
2767 | 59.65 | 14.696 | 0.076412 | 14.338 | 0.029328 |  | 2767 | 14.338 | 59.65 | 14.696 | 0.076412 | 0.029328
2768 | 59.66 | 14.696 | 0.076411 | 14.34 | 0.029332 |  | 2768 | 14.34 | 59.66 | 14.696 | 0.076411 | 0.029332
2769 | 59.67 | 14.696 | 0.076409 | 14.343 | 0.029337 |  | 2769 | 14.343 | 59.67 | 14.696 | 0.076409 | 0.029337
2770 | 59.68 | 14.696 | 0.076408 | 14.345 | 0.029341 |  | 2770 | 14.345 | 59.68 | 14.696 | 0.076408 | 0.029341
2771 | 59.69 | 14.696 | 0.076406 | 14.348 | 0.029346 |  | 2771 | 14.348 | 59.69 | 14.696 | 0.076406 | 0.029346
2772 | 59.7 | 14.696 | 0.076405 | 14.35 | 0.029351 |  | 2772 | 14.35 | 59.7 | 14.696 | 0.076405 | 0.029351
2773 | 59.71 | 14.696 | 0.076403 | 14.352 | 0.029355 |  | 2773 | 14.352 | 59.71 | 14.696 | 0.076403 | 0.029355
2774 | 59.72 | 14.696 | 0.076402 | 14.355 | 0.02936 |  | 2774 | 14.355 | 59.72 | 14.696 | 0.076402 | 0.02936
2775 | 59.73 | 14.696 | 0.0764 | 14.357 | 0.029365 |  | 2775 | 14.357 | 59.73 | 14.696 | 0.0764 | 0.029365
2776 | 59.74 | 14.696 | 0.076399 | 14.36 | 0.029369 |  | 2776 | 14.36 | 59.74 | 14.696 | 0.076399 | 0.029369
2777 | 59.75 | 14.696 | 0.076397 | 14.362 | 0.029374 |  | 2777 | 14.362 | 59.75 | 14.696 | 0.076397 | 0.029374
2778 | 59.76 | 14.696 | 0.076396 | 14.364 | 0.029379 |  | 2778 | 14.364 | 59.76 | 14.696 | 0.076396 | 0.029379
2779 | 59.77 | 14.696 | 0.076394 | 14.367 | 0.029383 |  | 2779 | 14.367 | 59.77 | 14.696 | 0.076394 | 0.029383
2780 | 59.78 | 14.696 | 0.076393 | 14.369 | 0.029388 |  | 2780 | 14.369 | 59.78 | 14.696 | 0.076393 | 0.029388
2781 | 59.79 | 14.696 | 0.076391 | 14.372 | 0.029392 |  | 2781 | 14.372 | 59.79 | 14.696 | 0.076391 | 0.029392
2782 | 59.8 | 14.696 | 0.07639 | 14.374 | 0.029397 |  | 2782 | 14.374 | 59.8 | 14.696 | 0.07639 | 0.029397
2783 | 59.81 | 14.696 | 0.076389 | 14.376 | 0.029402 |  | 2783 | 14.376 | 59.81 | 14.696 | 0.076389 | 0.029402
2784 | 59.82 | 14.696 | 0.076387 | 14.379 | 0.029406 |  | 2784 | 14.379 | 59.82 | 14.696 | 0.076387 | 0.029406
2785 | 59.83 | 14.696 | 0.076386 | 14.381 | 0.029411 |  | 2785 | 14.381 | 59.83 | 14.696 | 0.076386 | 0.029411
2786 | 59.84 | 14.696 | 0.076384 | 14.384 | 0.029416 |  | 2786 | 14.384 | 59.84 | 14.696 | 0.076384 | 0.029416
2787 | 59.85 | 14.696 | 0.076383 | 14.386 | 0.02942 |  | 2787 | 14.386 | 59.85 | 14.696 | 0.076383 | 0.02942
2788 | 59.86 | 14.696 | 0.076381 | 14.388 | 0.029425 |  | 2788 | 14.388 | 59.86 | 14.696 | 0.076381 | 0.029425
2789 | 59.87 | 14.696 | 0.07638 | 14.391 | 0.029429 |  | 2789 | 14.391 | 59.87 | 14.696 | 0.07638 | 0.029429
2790 | 59.88 | 14.696 | 0.076378 | 14.393 | 0.029434 |  | 2790 | 14.393 | 59.88 | 14.696 | 0.076378 | 0.029434
2791 | 59.89 | 14.696 | 0.076377 | 14.396 | 0.029439 |  | 2791 | 14.396 | 59.89 | 14.696 | 0.076377 | 0.029439
2792 | 59.9 | 14.696 | 0.076375 | 14.398 | 0.029443 |  | 2792 | 14.398 | 59.9 | 14.696 | 0.076375 | 0.029443
2793 | 59.91 | 14.696 | 0.076374 | 14.401 | 0.029448 |  | 2793 | 14.401 | 59.91 | 14.696 | 0.076374 | 0.029448
2794 | 59.92 | 14.696 | 0.076372 | 14.403 | 0.029453 |  | 2794 | 14.403 | 59.92 | 14.696 | 0.076372 | 0.029453
2795 | 59.93 | 14.696 | 0.076371 | 14.405 | 0.029457 |  | 2795 | 14.405 | 59.93 | 14.696 | 0.076371 | 0.029457
2796 | 59.94 | 14.696 | 0.076369 | 14.408 | 0.029462 |  | 2796 | 14.408 | 59.94 | 14.696 | 0.076369 | 0.029462
2797 | 59.95 | 14.696 | 0.076368 | 14.41 | 0.029466 |  | 2797 | 14.41 | 59.95 | 14.696 | 0.076368 | 0.029466
2798 | 59.96 | 14.696 | 0.076366 | 14.413 | 0.029471 |  | 2798 | 14.413 | 59.96 | 14.696 | 0.076366 | 0.029471
2799 | 59.97 | 14.696 | 0.076365 | 14.415 | 0.029476 |  | 2799 | 14.415 | 59.97 | 14.696 | 0.076365 | 0.029476
2800 | 59.98 | 14.696 | 0.076363 | 14.417 | 0.02948 |  | 2800 | 14.417 | 59.98 | 14.696 | 0.076363 | 0.02948
2801 | 59.99 | 14.696 | 0.076362 | 14.42 | 0.029485 |  | 2801 | 14.42 | 59.99 | 14.696 | 0.076362 | 0.029485
2802 | 60 | 14.696 | 0.076361 | 14.422 | 0.02949 |  | 2802 | 14.422 | 60 | 14.696 | 0.076361 | 0.02949
2803 | 60.01 | 14.696 | 0.076359 | 14.425 | 0.029494 |  | 2803 | 14.425 | 60.01 | 14.696 | 0.076359 | 0.029494
2804 | 60.02 | 14.696 | 0.076358 | 14.427 | 0.029499 |  | 2804 | 14.427 | 60.02 | 14.696 | 0.076358 | 0.029499
2805 | 60.03 | 14.696 | 0.076356 | 14.429 | 0.029503 |  | 2805 | 14.429 | 60.03 | 14.696 | 0.076356 | 0.029503
2806 | 60.04 | 14.696 | 0.076355 | 14.432 | 0.029508 |  | 2806 | 14.432 | 60.04 | 14.696 | 0.076355 | 0.029508
2807 | 60.05 | 14.696 | 0.076353 | 14.434 | 0.029513 |  | 2807 | 14.434 | 60.05 | 14.696 | 0.076353 | 0.029513
2808 | 60.06 | 14.696 | 0.076352 | 14.437 | 0.029517 |  | 2808 | 14.437 | 60.06 | 14.696 | 0.076352 | 0.029517
2809 | 60.07 | 14.696 | 0.07635 | 14.439 | 0.029522 |  | 2809 | 14.439 | 60.07 | 14.696 | 0.07635 | 0.029522
2810 | 60.08 | 14.696 | 0.076349 | 14.441 | 0.029527 |  | 2810 | 14.441 | 60.08 | 14.696 | 0.076349 | 0.029527
2811 | 60.09 | 14.696 | 0.076347 | 14.444 | 0.029531 |  | 2811 | 14.444 | 60.09 | 14.696 | 0.076347 | 0.029531
2812 | 60.1 | 14.696 | 0.076346 | 14.446 | 0.029536 |  | 2812 | 14.446 | 60.1 | 14.696 | 0.076346 | 0.029536
2813 | 60.11 | 14.696 | 0.076344 | 14.449 | 0.02954 |  | 2813 | 14.449 | 60.11 | 14.696 | 0.076344 | 0.02954
2814 | 60.12 | 14.696 | 0.076343 | 14.451 | 0.029545 |  | 2814 | 14.451 | 60.12 | 14.696 | 0.076343 | 0.029545
2815 | 60.13 | 14.696 | 0.076341 | 14.453 | 0.02955 |  | 2815 | 14.453 | 60.13 | 14.696 | 0.076341 | 0.02955
2816 | 60.14 | 14.696 | 0.07634 | 14.456 | 0.029554 |  | 2816 | 14.456 | 60.14 | 14.696 | 0.07634 | 0.029554
2817 | 60.15 | 14.696 | 0.076338 | 14.458 | 0.029559 |  | 2817 | 14.458 | 60.15 | 14.696 | 0.076338 | 0.029559
2818 | 60.16 | 14.696 | 0.076337 | 14.461 | 0.029564 |  | 2818 | 14.461 | 60.16 | 14.696 | 0.076337 | 0.029564
2819 | 60.17 | 14.696 | 0.076335 | 14.463 | 0.029568 |  | 2819 | 14.463 | 60.17 | 14.696 | 0.076335 | 0.029568
2820 | 60.18 | 14.696 | 0.076334 | 14.465 | 0.029573 |  | 2820 | 14.465 | 60.18 | 14.696 | 0.076334 | 0.029573
2821 | 60.19 | 14.696 | 0.076333 | 14.468 | 0.029577 |  | 2821 | 14.468 | 60.19 | 14.696 | 0.076333 | 0.029577
2822 | 60.2 | 14.696 | 0.076331 | 14.47 | 0.029582 |  | 2822 | 14.47 | 60.2 | 14.696 | 0.076331 | 0.029582
2823 | 60.21 | 14.696 | 0.07633 | 14.473 | 0.029587 |  | 2823 | 14.473 | 60.21 | 14.696 | 0.07633 | 0.029587
2824 | 60.22 | 14.696 | 0.076328 | 14.475 | 0.029591 |  | 2824 | 14.475 | 60.22 | 14.696 | 0.076328 | 0.029591
2825 | 60.23 | 14.696 | 0.076327 | 14.477 | 0.029596 |  | 2825 | 14.477 | 60.23 | 14.696 | 0.076327 | 0.029596
2826 | 60.24 | 14.696 | 0.076325 | 14.48 | 0.029601 |  | 2826 | 14.48 | 60.24 | 14.696 | 0.076325 | 0.029601
2827 | 60.25 | 14.696 | 0.076324 | 14.482 | 0.029605 |  | 2827 | 14.482 | 60.25 | 14.696 | 0.076324 | 0.029605
2828 | 60.26 | 14.696 | 0.076322 | 14.485 | 0.02961 |  | 2828 | 14.485 | 60.26 | 14.696 | 0.076322 | 0.02961
2829 | 60.27 | 14.696 | 0.076321 | 14.487 | 0.029614 |  | 2829 | 14.487 | 60.27 | 14.696 | 0.076321 | 0.029614
2830 | 60.28 | 14.696 | 0.076319 | 14.489 | 0.029619 |  | 2830 | 14.489 | 60.28 | 14.696 | 0.076319 | 0.029619
2831 | 60.29 | 14.696 | 0.076318 | 14.492 | 0.029624 |  | 2831 | 14.492 | 60.29 | 14.696 | 0.076318 | 0.029624
2832 | 60.3 | 14.696 | 0.076316 | 14.494 | 0.029628 |  | 2832 | 14.494 | 60.3 | 14.696 | 0.076316 | 0.029628
2833 | 60.31 | 14.696 | 0.076315 | 14.497 | 0.029633 |  | 2833 | 14.497 | 60.31 | 14.696 | 0.076315 | 0.029633
2834 | 60.32 | 14.696 | 0.076313 | 14.499 | 0.029638 |  | 2834 | 14.499 | 60.32 | 14.696 | 0.076313 | 0.029638
2835 | 60.33 | 14.696 | 0.076312 | 14.501 | 0.029642 |  | 2835 | 14.501 | 60.33 | 14.696 | 0.076312 | 0.029642
2836 | 60.34 | 14.696 | 0.07631 | 14.504 | 0.029647 |  | 2836 | 14.504 | 60.34 | 14.696 | 0.07631 | 0.029647
2837 | 60.35 | 14.696 | 0.076309 | 14.506 | 0.029651 |  | 2837 | 14.506 | 60.35 | 14.696 | 0.076309 | 0.029651
2838 | 60.36 | 14.696 | 0.076307 | 14.509 | 0.029656 |  | 2838 | 14.509 | 60.36 | 14.696 | 0.076307 | 0.029656
2839 | 60.37 | 14.696 | 0.076306 | 14.511 | 0.029661 |  | 2839 | 14.511 | 60.37 | 14.696 | 0.076306 | 0.029661
2840 | 60.38 | 14.696 | 0.076305 | 14.514 | 0.029665 |  | 2840 | 14.514 | 60.38 | 14.696 | 0.076305 | 0.029665
2841 | 60.39 | 14.696 | 0.076303 | 14.516 | 0.02967 |  | 2841 | 14.516 | 60.39 | 14.696 | 0.076303 | 0.02967
2842 | 60.4 | 14.696 | 0.076302 | 14.518 | 0.029675 |  | 2842 | 14.518 | 60.4 | 14.696 | 0.076302 | 0.029675
2843 | 60.41 | 14.696 | 0.0763 | 14.521 | 0.029679 |  | 2843 | 14.521 | 60.41 | 14.696 | 0.0763 | 0.029679
2844 | 60.42 | 14.696 | 0.076299 | 14.523 | 0.029684 |  | 2844 | 14.523 | 60.42 | 14.696 | 0.076299 | 0.029684
2845 | 60.43 | 14.696 | 0.076297 | 14.526 | 0.029688 |  | 2845 | 14.526 | 60.43 | 14.696 | 0.076297 | 0.029688
2846 | 60.44 | 14.696 | 0.076296 | 14.528 | 0.029693 |  | 2846 | 14.528 | 60.44 | 14.696 | 0.076296 | 0.029693
2847 | 60.45 | 14.696 | 0.076294 | 14.53 | 0.029698 |  | 2847 | 14.53 | 60.45 | 14.696 | 0.076294 | 0.029698
2848 | 60.46 | 14.696 | 0.076293 | 14.533 | 0.029702 |  | 2848 | 14.533 | 60.46 | 14.696 | 0.076293 | 0.029702
2849 | 60.47 | 14.696 | 0.076291 | 14.535 | 0.029707 |  | 2849 | 14.535 | 60.47 | 14.696 | 0.076291 | 0.029707
2850 | 60.48 | 14.696 | 0.07629 | 14.538 | 0.029712 |  | 2850 | 14.538 | 60.48 | 14.696 | 0.07629 | 0.029712
2851 | 60.49 | 14.696 | 0.076288 | 14.54 | 0.029716 |  | 2851 | 14.54 | 60.49 | 14.696 | 0.076288 | 0.029716
2852 | 60.5 | 14.696 | 0.076287 | 14.542 | 0.029721 |  | 2852 | 14.542 | 60.5 | 14.696 | 0.076287 | 0.029721
2853 | 60.51 | 14.696 | 0.076285 | 14.545 | 0.029725 |  | 2853 | 14.545 | 60.51 | 14.696 | 0.076285 | 0.029725
2854 | 60.52 | 14.696 | 0.076284 | 14.547 | 0.02973 |  | 2854 | 14.547 | 60.52 | 14.696 | 0.076284 | 0.02973
2855 | 60.53 | 14.696 | 0.076282 | 14.55 | 0.029735 |  | 2855 | 14.55 | 60.53 | 14.696 | 0.076282 | 0.029735
2856 | 60.54 | 14.696 | 0.076281 | 14.552 | 0.029739 |  | 2856 | 14.552 | 60.54 | 14.696 | 0.076281 | 0.029739
2857 | 60.55 | 14.696 | 0.07628 | 14.554 | 0.029744 |  | 2857 | 14.554 | 60.55 | 14.696 | 0.07628 | 0.029744
2858 | 60.56 | 14.696 | 0.076278 | 14.557 | 0.029749 |  | 2858 | 14.557 | 60.56 | 14.696 | 0.076278 | 0.029749
2859 | 60.57 | 14.696 | 0.076277 | 14.559 | 0.029753 |  | 2859 | 14.559 | 60.57 | 14.696 | 0.076277 | 0.029753
2860 | 60.58 | 14.696 | 0.076275 | 14.562 | 0.029758 |  | 2860 | 14.562 | 60.58 | 14.696 | 0.076275 | 0.029758
2861 | 60.59 | 14.696 | 0.076274 | 14.564 | 0.029762 |  | 2861 | 14.564 | 60.59 | 14.696 | 0.076274 | 0.029762
2862 | 60.6 | 14.696 | 0.076272 | 14.566 | 0.029767 |  | 2862 | 14.566 | 60.6 | 14.696 | 0.076272 | 0.029767
2863 | 60.61 | 14.696 | 0.076271 | 14.569 | 0.029772 |  | 2863 | 14.569 | 60.61 | 14.696 | 0.076271 | 0.029772
2864 | 60.62 | 14.696 | 0.076269 | 14.571 | 0.029776 |  | 2864 | 14.571 | 60.62 | 14.696 | 0.076269 | 0.029776
2865 | 60.63 | 14.696 | 0.076268 | 14.574 | 0.029781 |  | 2865 | 14.574 | 60.63 | 14.696 | 0.076268 | 0.029781
2866 | 60.64 | 14.696 | 0.076266 | 14.576 | 0.029786 |  | 2866 | 14.576 | 60.64 | 14.696 | 0.076266 | 0.029786
2867 | 60.65 | 14.696 | 0.076265 | 14.578 | 0.02979 |  | 2867 | 14.578 | 60.65 | 14.696 | 0.076265 | 0.02979
2868 | 60.66 | 14.696 | 0.076263 | 14.581 | 0.029795 |  | 2868 | 14.581 | 60.66 | 14.696 | 0.076263 | 0.029795
2869 | 60.67 | 14.696 | 0.076262 | 14.583 | 0.029799 |  | 2869 | 14.583 | 60.67 | 14.696 | 0.076262 | 0.029799
2870 | 60.68 | 14.696 | 0.07626 | 14.586 | 0.029804 |  | 2870 | 14.586 | 60.68 | 14.696 | 0.07626 | 0.029804
2871 | 60.69 | 14.696 | 0.076259 | 14.588 | 0.029809 |  | 2871 | 14.588 | 60.69 | 14.696 | 0.076259 | 0.029809
2872 | 60.7 | 14.696 | 0.076257 | 14.59 | 0.029813 |  | 2872 | 14.59 | 60.7 | 14.696 | 0.076257 | 0.029813
2873 | 60.71 | 14.696 | 0.076256 | 14.593 | 0.029818 |  | 2873 | 14.593 | 60.71 | 14.696 | 0.076256 | 0.029818
2874 | 60.72 | 14.696 | 0.076255 | 14.595 | 0.029822 |  | 2874 | 14.595 | 60.72 | 14.696 | 0.076255 | 0.029822
2875 | 60.73 | 14.696 | 0.076253 | 14.598 | 0.029827 |  | 2875 | 14.598 | 60.73 | 14.696 | 0.076253 | 0.029827
2876 | 60.74 | 14.696 | 0.076252 | 14.6 | 0.029832 |  | 2876 | 14.6 | 60.74 | 14.696 | 0.076252 | 0.029832
2877 | 60.75 | 14.696 | 0.07625 | 14.602 | 0.029836 |  | 2877 | 14.602 | 60.75 | 14.696 | 0.07625 | 0.029836
2878 | 60.76 | 14.696 | 0.076249 | 14.605 | 0.029841 |  | 2878 | 14.605 | 60.76 | 14.696 | 0.076249 | 0.029841
2879 | 60.77 | 14.696 | 0.076247 | 14.607 | 0.029846 |  | 2879 | 14.607 | 60.77 | 14.696 | 0.076247 | 0.029846
2880 | 60.78 | 14.696 | 0.076246 | 14.61 | 0.02985 |  | 2880 | 14.61 | 60.78 | 14.696 | 0.076246 | 0.02985
2881 | 60.79 | 14.696 | 0.076244 | 14.612 | 0.029855 |  | 2881 | 14.612 | 60.79 | 14.696 | 0.076244 | 0.029855
2882 | 60.8 | 14.696 | 0.076243 | 14.614 | 0.029859 |  | 2882 | 14.614 | 60.8 | 14.696 | 0.076243 | 0.029859
2883 | 60.81 | 14.696 | 0.076241 | 14.617 | 0.029864 |  | 2883 | 14.617 | 60.81 | 14.696 | 0.076241 | 0.029864
2884 | 60.82 | 14.696 | 0.07624 | 14.619 | 0.029869 |  | 2884 | 14.619 | 60.82 | 14.696 | 0.07624 | 0.029869
2885 | 60.83 | 14.696 | 0.076238 | 14.622 | 0.029873 |  | 2885 | 14.622 | 60.83 | 14.696 | 0.076238 | 0.029873
2886 | 60.84 | 14.696 | 0.076237 | 14.624 | 0.029878 |  | 2886 | 14.624 | 60.84 | 14.696 | 0.076237 | 0.029878
2887 | 60.85 | 14.696 | 0.076235 | 14.627 | 0.029883 |  | 2887 | 14.627 | 60.85 | 14.696 | 0.076235 | 0.029883
2888 | 60.86 | 14.696 | 0.076234 | 14.629 | 0.029887 |  | 2888 | 14.629 | 60.86 | 14.696 | 0.076234 | 0.029887
2889 | 60.87 | 14.696 | 0.076232 | 14.631 | 0.029892 |  | 2889 | 14.631 | 60.87 | 14.696 | 0.076232 | 0.029892
2890 | 60.88 | 14.696 | 0.076231 | 14.634 | 0.029896 |  | 2890 | 14.634 | 60.88 | 14.696 | 0.076231 | 0.029896
2891 | 60.89 | 14.696 | 0.07623 | 14.636 | 0.029901 |  | 2891 | 14.636 | 60.89 | 14.696 | 0.07623 | 0.029901
2892 | 60.9 | 14.696 | 0.076228 | 14.639 | 0.029906 |  | 2892 | 14.639 | 60.9 | 14.696 | 0.076228 | 0.029906
2893 | 60.91 | 14.696 | 0.076227 | 14.641 | 0.02991 |  | 2893 | 14.641 | 60.91 | 14.696 | 0.076227 | 0.02991
2894 | 60.92 | 14.696 | 0.076225 | 14.643 | 0.029915 |  | 2894 | 14.643 | 60.92 | 14.696 | 0.076225 | 0.029915
2895 | 60.93 | 14.696 | 0.076224 | 14.646 | 0.029919 |  | 2895 | 14.646 | 60.93 | 14.696 | 0.076224 | 0.029919
2896 | 60.94 | 14.696 | 0.076222 | 14.648 | 0.029924 |  | 2896 | 14.648 | 60.94 | 14.696 | 0.076222 | 0.029924
2897 | 60.95 | 14.696 | 0.076221 | 14.651 | 0.029929 |  | 2897 | 14.651 | 60.95 | 14.696 | 0.076221 | 0.029929
2898 | 60.96 | 14.696 | 0.076219 | 14.653 | 0.029933 |  | 2898 | 14.653 | 60.96 | 14.696 | 0.076219 | 0.029933
2899 | 60.97 | 14.696 | 0.076218 | 14.655 | 0.029938 |  | 2899 | 14.655 | 60.97 | 14.696 | 0.076218 | 0.029938
2900 | 60.98 | 14.696 | 0.076216 | 14.658 | 0.029943 |  | 2900 | 14.658 | 60.98 | 14.696 | 0.076216 | 0.029943
2901 | 60.99 | 14.696 | 0.076215 | 14.66 | 0.029947 |  | 2901 | 14.66 | 60.99 | 14.696 | 0.076215 | 0.029947
2902 | 61 | 14.696 | 0.076213 | 14.663 | 0.029952 |  | 2902 | 14.663 | 61 | 14.696 | 0.076213 | 0.029952
2903 | 61.01 | 14.696 | 0.076212 | 14.665 | 0.029956 |  | 2903 | 14.665 | 61.01 | 14.696 | 0.076212 | 0.029956
2904 | 61.02 | 14.696 | 0.07621 | 14.667 | 0.029961 |  | 2904 | 14.667 | 61.02 | 14.696 | 0.07621 | 0.029961
2905 | 61.03 | 14.696 | 0.076209 | 14.67 | 0.029966 |  | 2905 | 14.67 | 61.03 | 14.696 | 0.076209 | 0.029966
2906 | 61.04 | 14.696 | 0.076208 | 14.672 | 0.02997 |  | 2906 | 14.672 | 61.04 | 14.696 | 0.076208 | 0.02997
2907 | 61.05 | 14.696 | 0.076206 | 14.675 | 0.029975 |  | 2907 | 14.675 | 61.05 | 14.696 | 0.076206 | 0.029975
2908 | 61.06 | 14.696 | 0.076205 | 14.677 | 0.02998 |  | 2908 | 14.677 | 61.06 | 14.696 | 0.076205 | 0.02998
2909 | 61.07 | 14.696 | 0.076203 | 14.679 | 0.029984 |  | 2909 | 14.679 | 61.07 | 14.696 | 0.076203 | 0.029984
2910 | 61.08 | 14.696 | 0.076202 | 14.682 | 0.029989 |  | 2910 | 14.682 | 61.08 | 14.696 | 0.076202 | 0.029989
2911 | 61.09 | 14.696 | 0.0762 | 14.684 | 0.029993 |  | 2911 | 14.684 | 61.09 | 14.696 | 0.0762 | 0.029993
2912 | 61.1 | 14.696 | 0.076199 | 14.687 | 0.029998 |  | 2912 | 14.687 | 61.1 | 14.696 | 0.076199 | 0.029998
2913 | 61.11 | 14.696 | 0.076197 | 14.689 | 0.030003 |  | 2913 | 14.689 | 61.11 | 14.696 | 0.076197 | 0.030003
2914 | 61.12 | 14.696 | 0.076196 | 14.691 | 0.030007 |  | 2914 | 14.691 | 61.12 | 14.696 | 0.076196 | 0.030007
2915 | 61.13 | 14.696 | 0.076194 | 14.694 | 0.030012 |  | 2915 | 14.694 | 61.13 | 14.696 | 0.076194 | 0.030012
2916 | 61.14 | 14.696 | 0.076193 | 14.696 | 0.030016 |  | 2916 | 14.696 | 61.14 | 14.696 | 0.076193 | 0.030016
2917 | 61.15 | 14.696 | 0.076191 | 14.699 | 0.030021 |  | 2917 | 14.699 | 61.15 | 14.696 | 0.076191 | 0.030021
2918 | 61.16 | 14.696 | 0.07619 | 14.701 | 0.030026 |  | 2918 | 14.701 | 61.16 | 14.696 | 0.07619 | 0.030026
2919 | 61.17 | 14.696 | 0.076188 | 14.703 | 0.03003 |  | 2919 | 14.703 | 61.17 | 14.696 | 0.076188 | 0.03003
2920 | 61.18 | 14.696 | 0.076187 | 14.706 | 0.030035 |  | 2920 | 14.706 | 61.18 | 14.696 | 0.076187 | 0.030035
2921 | 61.19 | 14.696 | 0.076186 | 14.708 | 0.03004 |  | 2921 | 14.708 | 61.19 | 14.696 | 0.076186 | 0.03004
2922 | 61.2 | 14.696 | 0.076184 | 14.711 | 0.030044 |  | 2922 | 14.711 | 61.2 | 14.696 | 0.076184 | 0.030044
2923 | 61.21 | 14.696 | 0.076183 | 14.713 | 0.030049 |  | 2923 | 14.713 | 61.21 | 14.696 | 0.076183 | 0.030049
2924 | 61.22 | 14.696 | 0.076181 | 14.715 | 0.030053 |  | 2924 | 14.715 | 61.22 | 14.696 | 0.076181 | 0.030053
2925 | 61.23 | 14.696 | 0.07618 | 14.718 | 0.030058 |  | 2925 | 14.718 | 61.23 | 14.696 | 0.07618 | 0.030058
2926 | 61.24 | 14.696 | 0.076178 | 14.72 | 0.030063 |  | 2926 | 14.72 | 61.24 | 14.696 | 0.076178 | 0.030063
2927 | 61.25 | 14.696 | 0.076177 | 14.723 | 0.030067 |  | 2927 | 14.723 | 61.25 | 14.696 | 0.076177 | 0.030067
2928 | 61.26 | 14.696 | 0.076175 | 14.725 | 0.030072 |  | 2928 | 14.725 | 61.26 | 14.696 | 0.076175 | 0.030072
2929 | 61.27 | 14.696 | 0.076174 | 14.728 | 0.030076 |  | 2929 | 14.728 | 61.27 | 14.696 | 0.076174 | 0.030076
2930 | 61.28 | 14.696 | 0.076172 | 14.73 | 0.030081 |  | 2930 | 14.73 | 61.28 | 14.696 | 0.076172 | 0.030081
2931 | 61.29 | 14.696 | 0.076171 | 14.732 | 0.030086 |  | 2931 | 14.732 | 61.29 | 14.696 | 0.076171 | 0.030086
2932 | 61.3 | 14.696 | 0.076169 | 14.735 | 0.03009 |  | 2932 | 14.735 | 61.3 | 14.696 | 0.076169 | 0.03009
2933 | 61.31 | 14.696 | 0.076168 | 14.737 | 0.030095 |  | 2933 | 14.737 | 61.31 | 14.696 | 0.076168 | 0.030095
2934 | 61.32 | 14.696 | 0.076166 | 14.74 | 0.0301 |  | 2934 | 14.74 | 61.32 | 14.696 | 0.076166 | 0.0301
2935 | 61.33 | 14.696 | 0.076165 | 14.742 | 0.030104 |  | 2935 | 14.742 | 61.33 | 14.696 | 0.076165 | 0.030104
2936 | 61.34 | 14.696 | 0.076164 | 14.744 | 0.030109 |  | 2936 | 14.744 | 61.34 | 14.696 | 0.076164 | 0.030109
2937 | 61.35 | 14.696 | 0.076162 | 14.747 | 0.030113 |  | 2937 | 14.747 | 61.35 | 14.696 | 0.076162 | 0.030113
2938 | 61.36 | 14.696 | 0.076161 | 14.749 | 0.030118 |  | 2938 | 14.749 | 61.36 | 14.696 | 0.076161 | 0.030118
2939 | 61.37 | 14.696 | 0.076159 | 14.752 | 0.030123 |  | 2939 | 14.752 | 61.37 | 14.696 | 0.076159 | 0.030123
2940 | 61.38 | 14.696 | 0.076158 | 14.754 | 0.030127 |  | 2940 | 14.754 | 61.38 | 14.696 | 0.076158 | 0.030127
2941 | 61.39 | 14.696 | 0.076156 | 14.756 | 0.030132 |  | 2941 | 14.756 | 61.39 | 14.696 | 0.076156 | 0.030132
2942 | 61.4 | 14.696 | 0.076155 | 14.759 | 0.030136 |  | 2942 | 14.759 | 61.4 | 14.696 | 0.076155 | 0.030136
2943 | 61.41 | 14.696 | 0.076153 | 14.761 | 0.030141 |  | 2943 | 14.761 | 61.41 | 14.696 | 0.076153 | 0.030141
2944 | 61.42 | 14.696 | 0.076152 | 14.764 | 0.030146 |  | 2944 | 14.764 | 61.42 | 14.696 | 0.076152 | 0.030146
2945 | 61.43 | 14.696 | 0.07615 | 14.766 | 0.03015 |  | 2945 | 14.766 | 61.43 | 14.696 | 0.07615 | 0.03015
2946 | 61.44 | 14.696 | 0.076149 | 14.768 | 0.030155 |  | 2946 | 14.768 | 61.44 | 14.696 | 0.076149 | 0.030155
2947 | 61.45 | 14.696 | 0.076147 | 14.771 | 0.03016 |  | 2947 | 14.771 | 61.45 | 14.696 | 0.076147 | 0.03016
2948 | 61.46 | 14.696 | 0.076146 | 14.773 | 0.030164 |  | 2948 | 14.773 | 61.46 | 14.696 | 0.076146 | 0.030164
2949 | 61.47 | 14.696 | 0.076144 | 14.776 | 0.030169 |  | 2949 | 14.776 | 61.47 | 14.696 | 0.076144 | 0.030169
2950 | 61.48 | 14.696 | 0.076143 | 14.778 | 0.030173 |  | 2950 | 14.778 | 61.48 | 14.696 | 0.076143 | 0.030173
2951 | 61.49 | 14.696 | 0.076142 | 14.78 | 0.030178 |  | 2951 | 14.78 | 61.49 | 14.696 | 0.076142 | 0.030178
2952 | 61.5 | 14.696 | 0.07614 | 14.783 | 0.030183 |  | 2952 | 14.783 | 61.5 | 14.696 | 0.07614 | 0.030183
2953 | 61.51 | 14.696 | 0.076139 | 14.785 | 0.030187 |  | 2953 | 14.785 | 61.51 | 14.696 | 0.076139 | 0.030187
2954 | 61.52 | 14.696 | 0.076137 | 14.788 | 0.030192 |  | 2954 | 14.788 | 61.52 | 14.696 | 0.076137 | 0.030192
2955 | 61.53 | 14.696 | 0.076136 | 14.79 | 0.030196 |  | 2955 | 14.79 | 61.53 | 14.696 | 0.076136 | 0.030196
2956 | 61.54 | 14.696 | 0.076134 | 14.792 | 0.030201 |  | 2956 | 14.792 | 61.54 | 14.696 | 0.076134 | 0.030201
2957 | 61.55 | 14.696 | 0.076133 | 14.795 | 0.030206 |  | 2957 | 14.795 | 61.55 | 14.696 | 0.076133 | 0.030206
2958 | 61.56 | 14.696 | 0.076131 | 14.797 | 0.03021 |  | 2958 | 14.797 | 61.56 | 14.696 | 0.076131 | 0.03021
2959 | 61.57 | 14.696 | 0.07613 | 14.8 | 0.030215 |  | 2959 | 14.8 | 61.57 | 14.696 | 0.07613 | 0.030215
2960 | 61.58 | 14.696 | 0.076128 | 14.802 | 0.03022 |  | 2960 | 14.802 | 61.58 | 14.696 | 0.076128 | 0.03022
2961 | 61.59 | 14.696 | 0.076127 | 14.804 | 0.030224 |  | 2961 | 14.804 | 61.59 | 14.696 | 0.076127 | 0.030224
2962 | 61.6 | 14.696 | 0.076125 | 14.807 | 0.030229 |  | 2962 | 14.807 | 61.6 | 14.696 | 0.076125 | 0.030229
2963 | 61.61 | 14.696 | 0.076124 | 14.809 | 0.030233 |  | 2963 | 14.809 | 61.61 | 14.696 | 0.076124 | 0.030233
2964 | 61.62 | 14.696 | 0.076122 | 14.812 | 0.030238 |  | 2964 | 14.812 | 61.62 | 14.696 | 0.076122 | 0.030238
2965 | 61.63 | 14.696 | 0.076121 | 14.814 | 0.030243 |  | 2965 | 14.814 | 61.63 | 14.696 | 0.076121 | 0.030243
2966 | 61.64 | 14.696 | 0.07612 | 14.816 | 0.030247 |  | 2966 | 14.816 | 61.64 | 14.696 | 0.07612 | 0.030247
2967 | 61.65 | 14.696 | 0.076118 | 14.819 | 0.030252 |  | 2967 | 14.819 | 61.65 | 14.696 | 0.076118 | 0.030252
2968 | 61.66 | 14.696 | 0.076117 | 14.821 | 0.030256 |  | 2968 | 14.821 | 61.66 | 14.696 | 0.076117 | 0.030256
2969 | 61.67 | 14.696 | 0.076115 | 14.824 | 0.030261 |  | 2969 | 14.824 | 61.67 | 14.696 | 0.076115 | 0.030261
2970 | 61.68 | 14.696 | 0.076114 | 14.826 | 0.030266 |  | 2970 | 14.826 | 61.68 | 14.696 | 0.076114 | 0.030266
2971 | 61.69 | 14.696 | 0.076112 | 14.828 | 0.03027 |  | 2971 | 14.828 | 61.69 | 14.696 | 0.076112 | 0.03027
2972 | 61.7 | 14.696 | 0.076111 | 14.831 | 0.030275 |  | 2972 | 14.831 | 61.7 | 14.696 | 0.076111 | 0.030275
2973 | 61.71 | 14.696 | 0.076109 | 14.833 | 0.030279 |  | 2973 | 14.833 | 61.71 | 14.696 | 0.076109 | 0.030279
2974 | 61.72 | 14.696 | 0.076108 | 14.836 | 0.030284 |  | 2974 | 14.836 | 61.72 | 14.696 | 0.076108 | 0.030284
2975 | 61.73 | 14.696 | 0.076106 | 14.838 | 0.030289 |  | 2975 | 14.838 | 61.73 | 14.696 | 0.076106 | 0.030289
2976 | 61.74 | 14.696 | 0.076105 | 14.841 | 0.030293 |  | 2976 | 14.841 | 61.74 | 14.696 | 0.076105 | 0.030293
2977 | 61.75 | 14.696 | 0.076103 | 14.843 | 0.030298 |  | 2977 | 14.843 | 61.75 | 14.696 | 0.076103 | 0.030298
2978 | 61.76 | 14.696 | 0.076102 | 14.845 | 0.030303 |  | 2978 | 14.845 | 61.76 | 14.696 | 0.076102 | 0.030303
2979 | 61.77 | 14.696 | 0.076101 | 14.848 | 0.030307 |  | 2979 | 14.848 | 61.77 | 14.696 | 0.076101 | 0.030307
2980 | 61.78 | 14.696 | 0.076099 | 14.85 | 0.030312 |  | 2980 | 14.85 | 61.78 | 14.696 | 0.076099 | 0.030312
2981 | 61.79 | 14.696 | 0.076098 | 14.853 | 0.030316 |  | 2981 | 14.853 | 61.79 | 14.696 | 0.076098 | 0.030316
2982 | 61.8 | 14.696 | 0.076096 | 14.855 | 0.030321 |  | 2982 | 14.855 | 61.8 | 14.696 | 0.076096 | 0.030321
2983 | 61.81 | 14.696 | 0.076095 | 14.857 | 0.030326 |  | 2983 | 14.857 | 61.81 | 14.696 | 0.076095 | 0.030326
2984 | 61.82 | 14.696 | 0.076093 | 14.86 | 0.03033 |  | 2984 | 14.86 | 61.82 | 14.696 | 0.076093 | 0.03033
2985 | 61.83 | 14.696 | 0.076092 | 14.862 | 0.030335 |  | 2985 | 14.862 | 61.83 | 14.696 | 0.076092 | 0.030335
2986 | 61.84 | 14.696 | 0.07609 | 14.865 | 0.030339 |  | 2986 | 14.865 | 61.84 | 14.696 | 0.07609 | 0.030339
2987 | 61.85 | 14.696 | 0.076089 | 14.867 | 0.030344 |  | 2987 | 14.867 | 61.85 | 14.696 | 0.076089 | 0.030344
2988 | 61.86 | 14.696 | 0.076087 | 14.869 | 0.030349 |  | 2988 | 14.869 | 61.86 | 14.696 | 0.076087 | 0.030349
2989 | 61.87 | 14.696 | 0.076086 | 14.872 | 0.030353 |  | 2989 | 14.872 | 61.87 | 14.696 | 0.076086 | 0.030353
2990 | 61.88 | 14.696 | 0.076084 | 14.874 | 0.030358 |  | 2990 | 14.874 | 61.88 | 14.696 | 0.076084 | 0.030358
2991 | 61.89 | 14.696 | 0.076083 | 14.877 | 0.030362 |  | 2991 | 14.877 | 61.89 | 14.696 | 0.076083 | 0.030362
2992 | 61.9 | 14.696 | 0.076082 | 14.879 | 0.030367 |  | 2992 | 14.879 | 61.9 | 14.696 | 0.076082 | 0.030367
2993 | 61.91 | 14.696 | 0.07608 | 14.881 | 0.030372 |  | 2993 | 14.881 | 61.91 | 14.696 | 0.07608 | 0.030372
2994 | 61.92 | 14.696 | 0.076079 | 14.884 | 0.030376 |  | 2994 | 14.884 | 61.92 | 14.696 | 0.076079 | 0.030376
2995 | 61.93 | 14.696 | 0.076077 | 14.886 | 0.030381 |  | 2995 | 14.886 | 61.93 | 14.696 | 0.076077 | 0.030381
2996 | 61.94 | 14.696 | 0.076076 | 14.889 | 0.030386 |  | 2996 | 14.889 | 61.94 | 14.696 | 0.076076 | 0.030386
2997 | 61.95 | 14.696 | 0.076074 | 14.891 | 0.03039 |  | 2997 | 14.891 | 61.95 | 14.696 | 0.076074 | 0.03039
2998 | 61.96 | 14.696 | 0.076073 | 14.893 | 0.030395 |  | 2998 | 14.893 | 61.96 | 14.696 | 0.076073 | 0.030395
2999 | 61.97 | 14.696 | 0.076071 | 14.896 | 0.030399 |  | 2999 | 14.896 | 61.97 | 14.696 | 0.076071 | 0.030399
3000 | 61.98 | 14.696 | 0.07607 | 14.898 | 0.030404 |  | 3000 | 14.898 | 61.98 | 14.696 | 0.07607 | 0.030404
3001 | 61.99 | 14.696 | 0.076068 | 14.901 | 0.030409 |  | 3001 | 14.901 | 61.99 | 14.696 | 0.076068 | 0.030409
3002 | 62 | 14.696 | 0.076067 | 14.903 | 0.030413 |  | 3002 | 14.903 | 62 | 14.696 | 0.076067 | 0.030413
3003 | 62.01 | 14.696 | 0.076065 | 14.905 | 0.030418 |  | 3003 | 14.905 | 62.01 | 14.696 | 0.076065 | 0.030418
3004 | 62.02 | 14.696 | 0.076064 | 14.908 | 0.030422 |  | 3004 | 14.908 | 62.02 | 14.696 | 0.076064 | 0.030422
3005 | 62.03 | 14.696 | 0.076062 | 14.91 | 0.030427 |  | 3005 | 14.91 | 62.03 | 14.696 | 0.076062 | 0.030427
3006 | 62.04 | 14.696 | 0.076061 | 14.913 | 0.030432 |  | 3006 | 14.913 | 62.04 | 14.696 | 0.076061 | 0.030432
3007 | 62.05 | 14.696 | 0.07606 | 14.915 | 0.030436 |  | 3007 | 14.915 | 62.05 | 14.696 | 0.07606 | 0.030436
3008 | 62.06 | 14.696 | 0.076058 | 14.917 | 0.030441 |  | 3008 | 14.917 | 62.06 | 14.696 | 0.076058 | 0.030441
3009 | 62.07 | 14.696 | 0.076057 | 14.92 | 0.030445 |  | 3009 | 14.92 | 62.07 | 14.696 | 0.076057 | 0.030445
3010 | 62.08 | 14.696 | 0.076055 | 14.922 | 0.03045 |  | 3010 | 14.922 | 62.08 | 14.696 | 0.076055 | 0.03045
3011 | 62.09 | 14.696 | 0.076054 | 14.925 | 0.030455 |  | 3011 | 14.925 | 62.09 | 14.696 | 0.076054 | 0.030455
3012 | 62.1 | 14.696 | 0.076052 | 14.927 | 0.030459 |  | 3012 | 14.927 | 62.1 | 14.696 | 0.076052 | 0.030459
3013 | 62.11 | 14.696 | 0.076051 | 14.929 | 0.030464 |  | 3013 | 14.929 | 62.11 | 14.696 | 0.076051 | 0.030464
3014 | 62.12 | 14.696 | 0.076049 | 14.932 | 0.030468 |  | 3014 | 14.932 | 62.12 | 14.696 | 0.076049 | 0.030468
3015 | 62.13 | 14.696 | 0.076048 | 14.934 | 0.030473 |  | 3015 | 14.934 | 62.13 | 14.696 | 0.076048 | 0.030473
3016 | 62.14 | 14.696 | 0.076046 | 14.937 | 0.030478 |  | 3016 | 14.937 | 62.14 | 14.696 | 0.076046 | 0.030478
3017 | 62.15 | 14.696 | 0.076045 | 14.939 | 0.030482 |  | 3017 | 14.939 | 62.15 | 14.696 | 0.076045 | 0.030482
3018 | 62.16 | 14.696 | 0.076043 | 14.942 | 0.030487 |  | 3018 | 14.942 | 62.16 | 14.696 | 0.076043 | 0.030487
3019 | 62.17 | 14.696 | 0.076042 | 14.944 | 0.030492 |  | 3019 | 14.944 | 62.17 | 14.696 | 0.076042 | 0.030492
3020 | 62.18 | 14.696 | 0.076041 | 14.946 | 0.030496 |  | 3020 | 14.946 | 62.18 | 14.696 | 0.076041 | 0.030496
3021 | 62.19 | 14.696 | 0.076039 | 14.949 | 0.030501 |  | 3021 | 14.949 | 62.19 | 14.696 | 0.076039 | 0.030501
3022 | 62.2 | 14.696 | 0.076038 | 14.951 | 0.030505 |  | 3022 | 14.951 | 62.2 | 14.696 | 0.076038 | 0.030505
3023 | 62.21 | 14.696 | 0.076036 | 14.954 | 0.03051 |  | 3023 | 14.954 | 62.21 | 14.696 | 0.076036 | 0.03051
3024 | 62.22 | 14.696 | 0.076035 | 14.956 | 0.030515 |  | 3024 | 14.956 | 62.22 | 14.696 | 0.076035 | 0.030515
3025 | 62.23 | 14.696 | 0.076033 | 14.958 | 0.030519 |  | 3025 | 14.958 | 62.23 | 14.696 | 0.076033 | 0.030519
3026 | 62.24 | 14.696 | 0.076032 | 14.961 | 0.030524 |  | 3026 | 14.961 | 62.24 | 14.696 | 0.076032 | 0.030524
3027 | 62.25 | 14.696 | 0.07603 | 14.963 | 0.030528 |  | 3027 | 14.963 | 62.25 | 14.696 | 0.07603 | 0.030528
3028 | 62.26 | 14.696 | 0.076029 | 14.966 | 0.030533 |  | 3028 | 14.966 | 62.26 | 14.696 | 0.076029 | 0.030533
3029 | 62.27 | 14.696 | 0.076027 | 14.968 | 0.030538 |  | 3029 | 14.968 | 62.27 | 14.696 | 0.076027 | 0.030538
3030 | 62.28 | 14.696 | 0.076026 | 14.97 | 0.030542 |  | 3030 | 14.97 | 62.28 | 14.696 | 0.076026 | 0.030542
3031 | 62.29 | 14.696 | 0.076024 | 14.973 | 0.030547 |  | 3031 | 14.973 | 62.29 | 14.696 | 0.076024 | 0.030547
3032 | 62.3 | 14.696 | 0.076023 | 14.975 | 0.030551 |  | 3032 | 14.975 | 62.3 | 14.696 | 0.076023 | 0.030551
3033 | 62.31 | 14.696 | 0.076022 | 14.978 | 0.030556 |  | 3033 | 14.978 | 62.31 | 14.696 | 0.076022 | 0.030556
3034 | 62.32 | 14.696 | 0.07602 | 14.98 | 0.030561 |  | 3034 | 14.98 | 62.32 | 14.696 | 0.07602 | 0.030561
3035 | 62.33 | 14.696 | 0.076019 | 14.982 | 0.030565 |  | 3035 | 14.982 | 62.33 | 14.696 | 0.076019 | 0.030565
3036 | 62.34 | 14.696 | 0.076017 | 14.985 | 0.03057 |  | 3036 | 14.985 | 62.34 | 14.696 | 0.076017 | 0.03057
3037 | 62.35 | 14.696 | 0.076016 | 14.987 | 0.030574 |  | 3037 | 14.987 | 62.35 | 14.696 | 0.076016 | 0.030574
3038 | 62.36 | 14.696 | 0.076014 | 14.99 | 0.030579 |  | 3038 | 14.99 | 62.36 | 14.696 | 0.076014 | 0.030579
3039 | 62.37 | 14.696 | 0.076013 | 14.992 | 0.030584 |  | 3039 | 14.992 | 62.37 | 14.696 | 0.076013 | 0.030584
3040 | 62.38 | 14.696 | 0.076011 | 14.994 | 0.030588 |  | 3040 | 14.994 | 62.38 | 14.696 | 0.076011 | 0.030588
3041 | 62.39 | 14.696 | 0.07601 | 14.997 | 0.030593 |  | 3041 | 14.997 | 62.39 | 14.696 | 0.07601 | 0.030593
3042 | 62.4 | 14.696 | 0.076008 | 14.999 | 0.030597 |  | 3042 | 14.999 | 62.4 | 14.696 | 0.076008 | 0.030597
3043 | 62.41 | 14.696 | 0.076007 | 15.002 | 0.030602 |  | 3043 | 15.002 | 62.41 | 14.696 | 0.076007 | 0.030602
3044 | 62.42 | 14.696 | 0.076006 | 15.004 | 0.030607 |  | 3044 | 15.004 | 62.42 | 14.696 | 0.076006 | 0.030607
3045 | 62.43 | 14.696 | 0.076004 | 15.006 | 0.030611 |  | 3045 | 15.006 | 62.43 | 14.696 | 0.076004 | 0.030611
3046 | 62.44 | 14.696 | 0.076003 | 15.009 | 0.030616 |  | 3046 | 15.009 | 62.44 | 14.696 | 0.076003 | 0.030616
3047 | 62.45 | 14.696 | 0.076001 | 15.011 | 0.030621 |  | 3047 | 15.011 | 62.45 | 14.696 | 0.076001 | 0.030621
3048 | 62.46 | 14.696 | 0.076 | 15.014 | 0.030625 |  | 3048 | 15.014 | 62.46 | 14.696 | 0.076 | 0.030625
3049 | 62.47 | 14.696 | 0.075998 | 15.016 | 0.03063 |  | 3049 | 15.016 | 62.47 | 14.696 | 0.075998 | 0.03063
3050 | 62.48 | 14.696 | 0.075997 | 15.018 | 0.030634 |  | 3050 | 15.018 | 62.48 | 14.696 | 0.075997 | 0.030634
3051 | 62.49 | 14.696 | 0.075995 | 15.021 | 0.030639 |  | 3051 | 15.021 | 62.49 | 14.696 | 0.075995 | 0.030639
3052 | 62.5 | 14.696 | 0.075994 | 15.023 | 0.030644 |  | 3052 | 15.023 | 62.5 | 14.696 | 0.075994 | 0.030644
3053 | 62.51 | 14.696 | 0.075992 | 15.026 | 0.030648 |  | 3053 | 15.026 | 62.51 | 14.696 | 0.075992 | 0.030648
3054 | 62.52 | 14.696 | 0.075991 | 15.028 | 0.030653 |  | 3054 | 15.028 | 62.52 | 14.696 | 0.075991 | 0.030653
3055 | 62.53 | 14.696 | 0.075989 | 15.03 | 0.030657 |  | 3055 | 15.03 | 62.53 | 14.696 | 0.075989 | 0.030657
3056 | 62.54 | 14.696 | 0.075988 | 15.033 | 0.030662 |  | 3056 | 15.033 | 62.54 | 14.696 | 0.075988 | 0.030662
3057 | 62.55 | 14.696 | 0.075987 | 15.035 | 0.030667 |  | 3057 | 15.035 | 62.55 | 14.696 | 0.075987 | 0.030667
3058 | 62.56 | 14.696 | 0.075985 | 15.038 | 0.030671 |  | 3058 | 15.038 | 62.56 | 14.696 | 0.075985 | 0.030671
3059 | 62.57 | 14.696 | 0.075984 | 15.04 | 0.030676 |  | 3059 | 15.04 | 62.57 | 14.696 | 0.075984 | 0.030676
3060 | 62.58 | 14.696 | 0.075982 | 15.042 | 0.03068 |  | 3060 | 15.042 | 62.58 | 14.696 | 0.075982 | 0.03068
3061 | 62.59 | 14.696 | 0.075981 | 15.045 | 0.030685 |  | 3061 | 15.045 | 62.59 | 14.696 | 0.075981 | 0.030685
3062 | 62.6 | 14.696 | 0.075979 | 15.047 | 0.03069 |  | 3062 | 15.047 | 62.6 | 14.696 | 0.075979 | 0.03069
3063 | 62.61 | 14.696 | 0.075978 | 15.05 | 0.030694 |  | 3063 | 15.05 | 62.61 | 14.696 | 0.075978 | 0.030694
3064 | 62.62 | 14.696 | 0.075976 | 15.052 | 0.030699 |  | 3064 | 15.052 | 62.62 | 14.696 | 0.075976 | 0.030699
3065 | 62.63 | 14.696 | 0.075975 | 15.055 | 0.030703 |  | 3065 | 15.055 | 62.63 | 14.696 | 0.075975 | 0.030703
3066 | 62.64 | 14.696 | 0.075973 | 15.057 | 0.030708 |  | 3066 | 15.057 | 62.64 | 14.696 | 0.075973 | 0.030708
3067 | 62.65 | 14.696 | 0.075972 | 15.059 | 0.030713 |  | 3067 | 15.059 | 62.65 | 14.696 | 0.075972 | 0.030713
3068 | 62.66 | 14.696 | 0.07597 | 15.062 | 0.030717 |  | 3068 | 15.062 | 62.66 | 14.696 | 0.07597 | 0.030717
3069 | 62.67 | 14.696 | 0.075969 | 15.064 | 0.030722 |  | 3069 | 15.064 | 62.67 | 14.696 | 0.075969 | 0.030722
3070 | 62.68 | 14.696 | 0.075968 | 15.067 | 0.030726 |  | 3070 | 15.067 | 62.68 | 14.696 | 0.075968 | 0.030726
3071 | 62.69 | 14.696 | 0.075966 | 15.069 | 0.030731 |  | 3071 | 15.069 | 62.69 | 14.696 | 0.075966 | 0.030731
3072 | 62.7 | 14.696 | 0.075965 | 15.071 | 0.030736 |  | 3072 | 15.071 | 62.7 | 14.696 | 0.075965 | 0.030736
3073 | 62.71 | 14.696 | 0.075963 | 15.074 | 0.03074 |  | 3073 | 15.074 | 62.71 | 14.696 | 0.075963 | 0.03074
3074 | 62.72 | 14.696 | 0.075962 | 15.076 | 0.030745 |  | 3074 | 15.076 | 62.72 | 14.696 | 0.075962 | 0.030745
3075 | 62.73 | 14.696 | 0.07596 | 15.079 | 0.030749 |  | 3075 | 15.079 | 62.73 | 14.696 | 0.07596 | 0.030749
3076 | 62.74 | 14.696 | 0.075959 | 15.081 | 0.030754 |  | 3076 | 15.081 | 62.74 | 14.696 | 0.075959 | 0.030754
3077 | 62.75 | 14.696 | 0.075957 | 15.083 | 0.030759 |  | 3077 | 15.083 | 62.75 | 14.696 | 0.075957 | 0.030759
3078 | 62.76 | 14.696 | 0.075956 | 15.086 | 0.030763 |  | 3078 | 15.086 | 62.76 | 14.696 | 0.075956 | 0.030763
3079 | 62.77 | 14.696 | 0.075954 | 15.088 | 0.030768 |  | 3079 | 15.088 | 62.77 | 14.696 | 0.075954 | 0.030768
3080 | 62.78 | 14.696 | 0.075953 | 15.091 | 0.030772 |  | 3080 | 15.091 | 62.78 | 14.696 | 0.075953 | 0.030772
3081 | 62.79 | 14.696 | 0.075952 | 15.093 | 0.030777 |  | 3081 | 15.093 | 62.79 | 14.696 | 0.075952 | 0.030777
3082 | 62.8 | 14.696 | 0.07595 | 15.095 | 0.030782 |  | 3082 | 15.095 | 62.8 | 14.696 | 0.07595 | 0.030782
3083 | 62.81 | 14.696 | 0.075949 | 15.098 | 0.030786 |  | 3083 | 15.098 | 62.81 | 14.696 | 0.075949 | 0.030786
3084 | 62.82 | 14.696 | 0.075947 | 15.1 | 0.030791 |  | 3084 | 15.1 | 62.82 | 14.696 | 0.075947 | 0.030791
3085 | 62.83 | 14.696 | 0.075946 | 15.103 | 0.030795 |  | 3085 | 15.103 | 62.83 | 14.696 | 0.075946 | 0.030795
3086 | 62.84 | 14.696 | 0.075944 | 15.105 | 0.0308 |  | 3086 | 15.105 | 62.84 | 14.696 | 0.075944 | 0.0308
3087 | 62.85 | 14.696 | 0.075943 | 15.107 | 0.030805 |  | 3087 | 15.107 | 62.85 | 14.696 | 0.075943 | 0.030805
3088 | 62.86 | 14.696 | 0.075941 | 15.11 | 0.030809 |  | 3088 | 15.11 | 62.86 | 14.696 | 0.075941 | 0.030809
3089 | 62.87 | 14.696 | 0.07594 | 15.112 | 0.030814 |  | 3089 | 15.112 | 62.87 | 14.696 | 0.07594 | 0.030814
3090 | 62.88 | 14.696 | 0.075938 | 15.115 | 0.030818 |  | 3090 | 15.115 | 62.88 | 14.696 | 0.075938 | 0.030818
3091 | 62.89 | 14.696 | 0.075937 | 15.117 | 0.030823 |  | 3091 | 15.117 | 62.89 | 14.696 | 0.075937 | 0.030823
3092 | 62.9 | 14.696 | 0.075935 | 15.119 | 0.030828 |  | 3092 | 15.119 | 62.9 | 14.696 | 0.075935 | 0.030828
3093 | 62.91 | 14.696 | 0.075934 | 15.122 | 0.030832 |  | 3093 | 15.122 | 62.91 | 14.696 | 0.075934 | 0.030832
3094 | 62.92 | 14.696 | 0.075933 | 15.124 | 0.030837 |  | 3094 | 15.124 | 62.92 | 14.696 | 0.075933 | 0.030837
3095 | 62.93 | 14.696 | 0.075931 | 15.127 | 0.030841 |  | 3095 | 15.127 | 62.93 | 14.696 | 0.075931 | 0.030841
3096 | 62.94 | 14.696 | 0.07593 | 15.129 | 0.030846 |  | 3096 | 15.129 | 62.94 | 14.696 | 0.07593 | 0.030846
3097 | 62.95 | 14.696 | 0.075928 | 15.131 | 0.030851 |  | 3097 | 15.131 | 62.95 | 14.696 | 0.075928 | 0.030851
3098 | 62.96 | 14.696 | 0.075927 | 15.134 | 0.030855 |  | 3098 | 15.134 | 62.96 | 14.696 | 0.075927 | 0.030855
3099 | 62.97 | 14.696 | 0.075925 | 15.136 | 0.03086 |  | 3099 | 15.136 | 62.97 | 14.696 | 0.075925 | 0.03086
3100 | 62.98 | 14.696 | 0.075924 | 15.139 | 0.030864 |  | 3100 | 15.139 | 62.98 | 14.696 | 0.075924 | 0.030864
3101 | 62.99 | 14.696 | 0.075922 | 15.141 | 0.030869 |  | 3101 | 15.141 | 62.99 | 14.696 | 0.075922 | 0.030869
3102 | 63 | 14.696 | 0.075921 | 15.143 | 0.030874 |  | 3102 | 15.143 | 63 | 14.696 | 0.075921 | 0.030874
3103 | 63.01 | 14.696 | 0.075919 | 15.146 | 0.030878 |  | 3103 | 15.146 | 63.01 | 14.696 | 0.075919 | 0.030878
3104 | 63.02 | 14.696 | 0.075918 | 15.148 | 0.030883 |  | 3104 | 15.148 | 63.02 | 14.696 | 0.075918 | 0.030883
3105 | 63.03 | 14.696 | 0.075917 | 15.151 | 0.030887 |  | 3105 | 15.151 | 63.03 | 14.696 | 0.075917 | 0.030887
3106 | 63.04 | 14.696 | 0.075915 | 15.153 | 0.030892 |  | 3106 | 15.153 | 63.04 | 14.696 | 0.075915 | 0.030892
3107 | 63.05 | 14.696 | 0.075914 | 15.156 | 0.030897 |  | 3107 | 15.156 | 63.05 | 14.696 | 0.075914 | 0.030897
3108 | 63.06 | 14.696 | 0.075912 | 15.158 | 0.030901 |  | 3108 | 15.158 | 63.06 | 14.696 | 0.075912 | 0.030901
3109 | 63.07 | 14.696 | 0.075911 | 15.16 | 0.030906 |  | 3109 | 15.16 | 63.07 | 14.696 | 0.075911 | 0.030906
3110 | 63.08 | 14.696 | 0.075909 | 15.163 | 0.03091 |  | 3110 | 15.163 | 63.08 | 14.696 | 0.075909 | 0.03091
3111 | 63.09 | 14.696 | 0.075908 | 15.165 | 0.030915 |  | 3111 | 15.165 | 63.09 | 14.696 | 0.075908 | 0.030915
3112 | 63.1 | 14.696 | 0.075906 | 15.168 | 0.03092 |  | 3112 | 15.168 | 63.1 | 14.696 | 0.075906 | 0.03092
3113 | 63.11 | 14.696 | 0.075905 | 15.17 | 0.030924 |  | 3113 | 15.17 | 63.11 | 14.696 | 0.075905 | 0.030924
3114 | 63.12 | 14.696 | 0.075903 | 15.172 | 0.030929 |  | 3114 | 15.172 | 63.12 | 14.696 | 0.075903 | 0.030929
3115 | 63.13 | 14.696 | 0.075902 | 15.175 | 0.030933 |  | 3115 | 15.175 | 63.13 | 14.696 | 0.075902 | 0.030933
3116 | 63.14 | 14.696 | 0.075901 | 15.177 | 0.030938 |  | 3116 | 15.177 | 63.14 | 14.696 | 0.075901 | 0.030938
3117 | 63.15 | 14.696 | 0.075899 | 15.18 | 0.030943 |  | 3117 | 15.18 | 63.15 | 14.696 | 0.075899 | 0.030943
3118 | 63.16 | 14.696 | 0.075898 | 15.182 | 0.030947 |  | 3118 | 15.182 | 63.16 | 14.696 | 0.075898 | 0.030947
3119 | 63.17 | 14.696 | 0.075896 | 15.184 | 0.030952 |  | 3119 | 15.184 | 63.17 | 14.696 | 0.075896 | 0.030952
3120 | 63.18 | 14.696 | 0.075895 | 15.187 | 0.030956 |  | 3120 | 15.187 | 63.18 | 14.696 | 0.075895 | 0.030956
3121 | 63.19 | 14.696 | 0.075893 | 15.189 | 0.030961 |  | 3121 | 15.189 | 63.19 | 14.696 | 0.075893 | 0.030961
3122 | 63.2 | 14.696 | 0.075892 | 15.192 | 0.030966 |  | 3122 | 15.192 | 63.2 | 14.696 | 0.075892 | 0.030966
3123 | 63.21 | 14.696 | 0.07589 | 15.194 | 0.03097 |  | 3123 | 15.194 | 63.21 | 14.696 | 0.07589 | 0.03097
3124 | 63.22 | 14.696 | 0.075889 | 15.196 | 0.030975 |  | 3124 | 15.196 | 63.22 | 14.696 | 0.075889 | 0.030975
3125 | 63.23 | 14.696 | 0.075887 | 15.199 | 0.030979 |  | 3125 | 15.199 | 63.23 | 14.696 | 0.075887 | 0.030979
3126 | 63.24 | 14.696 | 0.075886 | 15.201 | 0.030984 |  | 3126 | 15.201 | 63.24 | 14.696 | 0.075886 | 0.030984
3127 | 63.25 | 14.696 | 0.075885 | 15.204 | 0.030989 |  | 3127 | 15.204 | 63.25 | 14.696 | 0.075885 | 0.030989
3128 | 63.26 | 14.696 | 0.075883 | 15.206 | 0.030993 |  | 3128 | 15.206 | 63.26 | 14.696 | 0.075883 | 0.030993
3129 | 63.27 | 14.696 | 0.075882 | 15.208 | 0.030998 |  | 3129 | 15.208 | 63.27 | 14.696 | 0.075882 | 0.030998
3130 | 63.28 | 14.696 | 0.07588 | 15.211 | 0.031002 |  | 3130 | 15.211 | 63.28 | 14.696 | 0.07588 | 0.031002
3131 | 63.29 | 14.696 | 0.075879 | 15.213 | 0.031007 |  | 3131 | 15.213 | 63.29 | 14.696 | 0.075879 | 0.031007
3132 | 63.3 | 14.696 | 0.075877 | 15.216 | 0.031012 |  | 3132 | 15.216 | 63.3 | 14.696 | 0.075877 | 0.031012
3133 | 63.31 | 14.696 | 0.075876 | 15.218 | 0.031016 |  | 3133 | 15.218 | 63.31 | 14.696 | 0.075876 | 0.031016
3134 | 63.32 | 14.696 | 0.075874 | 15.22 | 0.031021 |  | 3134 | 15.22 | 63.32 | 14.696 | 0.075874 | 0.031021
3135 | 63.33 | 14.696 | 0.075873 | 15.223 | 0.031025 |  | 3135 | 15.223 | 63.33 | 14.696 | 0.075873 | 0.031025
3136 | 63.34 | 14.696 | 0.075871 | 15.225 | 0.03103 |  | 3136 | 15.225 | 63.34 | 14.696 | 0.075871 | 0.03103
3137 | 63.35 | 14.696 | 0.07587 | 15.228 | 0.031035 |  | 3137 | 15.228 | 63.35 | 14.696 | 0.07587 | 0.031035
3138 | 63.36 | 14.696 | 0.075869 | 15.23 | 0.031039 |  | 3138 | 15.23 | 63.36 | 14.696 | 0.075869 | 0.031039
3139 | 63.37 | 14.696 | 0.075867 | 15.232 | 0.031044 |  | 3139 | 15.232 | 63.37 | 14.696 | 0.075867 | 0.031044
3140 | 63.38 | 14.696 | 0.075866 | 15.235 | 0.031048 |  | 3140 | 15.235 | 63.38 | 14.696 | 0.075866 | 0.031048
3141 | 63.39 | 14.696 | 0.075864 | 15.237 | 0.031053 |  | 3141 | 15.237 | 63.39 | 14.696 | 0.075864 | 0.031053
3142 | 63.4 | 14.696 | 0.075863 | 15.24 | 0.031058 |  | 3142 | 15.24 | 63.4 | 14.696 | 0.075863 | 0.031058
3143 | 63.41 | 14.696 | 0.075861 | 15.242 | 0.031062 |  | 3143 | 15.242 | 63.41 | 14.696 | 0.075861 | 0.031062
3144 | 63.42 | 14.696 | 0.07586 | 15.244 | 0.031067 |  | 3144 | 15.244 | 63.42 | 14.696 | 0.07586 | 0.031067
3145 | 63.43 | 14.696 | 0.075858 | 15.247 | 0.031071 |  | 3145 | 15.247 | 63.43 | 14.696 | 0.075858 | 0.031071
3146 | 63.44 | 14.696 | 0.075857 | 15.249 | 0.031076 |  | 3146 | 15.249 | 63.44 | 14.696 | 0.075857 | 0.031076
3147 | 63.45 | 14.696 | 0.075855 | 15.252 | 0.031081 |  | 3147 | 15.252 | 63.45 | 14.696 | 0.075855 | 0.031081
3148 | 63.46 | 14.696 | 0.075854 | 15.254 | 0.031085 |  | 3148 | 15.254 | 63.46 | 14.696 | 0.075854 | 0.031085
3149 | 63.47 | 14.696 | 0.075853 | 15.257 | 0.03109 |  | 3149 | 15.257 | 63.47 | 14.696 | 0.075853 | 0.03109
3150 | 63.48 | 14.696 | 0.075851 | 15.259 | 0.031094 |  | 3150 | 15.259 | 63.48 | 14.696 | 0.075851 | 0.031094
3151 | 63.49 | 14.696 | 0.07585 | 15.261 | 0.031099 |  | 3151 | 15.261 | 63.49 | 14.696 | 0.07585 | 0.031099
3152 | 63.5 | 14.696 | 0.075848 | 15.264 | 0.031104 |  | 3152 | 15.264 | 63.5 | 14.696 | 0.075848 | 0.031104
3153 | 63.51 | 14.696 | 0.075847 | 15.266 | 0.031108 |  | 3153 | 15.266 | 63.51 | 14.696 | 0.075847 | 0.031108
3154 | 63.52 | 14.696 | 0.075845 | 15.269 | 0.031113 |  | 3154 | 15.269 | 63.52 | 14.696 | 0.075845 | 0.031113
3155 | 63.53 | 14.696 | 0.075844 | 15.271 | 0.031117 |  | 3155 | 15.271 | 63.53 | 14.696 | 0.075844 | 0.031117
3156 | 63.54 | 14.696 | 0.075842 | 15.273 | 0.031122 |  | 3156 | 15.273 | 63.54 | 14.696 | 0.075842 | 0.031122
3157 | 63.55 | 14.696 | 0.075841 | 15.276 | 0.031127 |  | 3157 | 15.276 | 63.55 | 14.696 | 0.075841 | 0.031127
3158 | 63.56 | 14.696 | 0.075839 | 15.278 | 0.031131 |  | 3158 | 15.278 | 63.56 | 14.696 | 0.075839 | 0.031131
3159 | 63.57 | 14.696 | 0.075838 | 15.281 | 0.031136 |  | 3159 | 15.281 | 63.57 | 14.696 | 0.075838 | 0.031136
3160 | 63.58 | 14.696 | 0.075837 | 15.283 | 0.03114 |  | 3160 | 15.283 | 63.58 | 14.696 | 0.075837 | 0.03114
3161 | 63.59 | 14.696 | 0.075835 | 15.285 | 0.031145 |  | 3161 | 15.285 | 63.59 | 14.696 | 0.075835 | 0.031145
3162 | 63.6 | 14.696 | 0.075834 | 15.288 | 0.03115 |  | 3162 | 15.288 | 63.6 | 14.696 | 0.075834 | 0.03115
3163 | 63.61 | 14.696 | 0.075832 | 15.29 | 0.031154 |  | 3163 | 15.29 | 63.61 | 14.696 | 0.075832 | 0.031154
3164 | 63.62 | 14.696 | 0.075831 | 15.293 | 0.031159 |  | 3164 | 15.293 | 63.62 | 14.696 | 0.075831 | 0.031159
3165 | 63.63 | 14.696 | 0.075829 | 15.295 | 0.031163 |  | 3165 | 15.295 | 63.63 | 14.696 | 0.075829 | 0.031163
3166 | 63.64 | 14.696 | 0.075828 | 15.297 | 0.031168 |  | 3166 | 15.297 | 63.64 | 14.696 | 0.075828 | 0.031168
3167 | 63.65 | 14.696 | 0.075826 | 15.3 | 0.031173 |  | 3167 | 15.3 | 63.65 | 14.696 | 0.075826 | 0.031173
3168 | 63.66 | 14.696 | 0.075825 | 15.302 | 0.031177 |  | 3168 | 15.302 | 63.66 | 14.696 | 0.075825 | 0.031177
3169 | 63.67 | 14.696 | 0.075823 | 15.305 | 0.031182 |  | 3169 | 15.305 | 63.67 | 14.696 | 0.075823 | 0.031182
3170 | 63.68 | 14.696 | 0.075822 | 15.307 | 0.031186 |  | 3170 | 15.307 | 63.68 | 14.696 | 0.075822 | 0.031186
3171 | 63.69 | 14.696 | 0.075821 | 15.309 | 0.031191 |  | 3171 | 15.309 | 63.69 | 14.696 | 0.075821 | 0.031191
3172 | 63.7 | 14.696 | 0.075819 | 15.312 | 0.031195 |  | 3172 | 15.312 | 63.7 | 14.696 | 0.075819 | 0.031195
3173 | 63.71 | 14.696 | 0.075818 | 15.314 | 0.0312 |  | 3173 | 15.314 | 63.71 | 14.696 | 0.075818 | 0.0312
3174 | 63.72 | 14.696 | 0.075816 | 15.317 | 0.031205 |  | 3174 | 15.317 | 63.72 | 14.696 | 0.075816 | 0.031205
3175 | 63.73 | 14.696 | 0.075815 | 15.319 | 0.031209 |  | 3175 | 15.319 | 63.73 | 14.696 | 0.075815 | 0.031209
3176 | 63.74 | 14.696 | 0.075813 | 15.321 | 0.031214 |  | 3176 | 15.321 | 63.74 | 14.696 | 0.075813 | 0.031214
3177 | 63.75 | 14.696 | 0.075812 | 15.324 | 0.031218 |  | 3177 | 15.324 | 63.75 | 14.696 | 0.075812 | 0.031218
3178 | 63.76 | 14.696 | 0.07581 | 15.326 | 0.031223 |  | 3178 | 15.326 | 63.76 | 14.696 | 0.07581 | 0.031223
3179 | 63.77 | 14.696 | 0.075809 | 15.329 | 0.031228 |  | 3179 | 15.329 | 63.77 | 14.696 | 0.075809 | 0.031228
3180 | 63.78 | 14.696 | 0.075807 | 15.331 | 0.031232 |  | 3180 | 15.331 | 63.78 | 14.696 | 0.075807 | 0.031232
3181 | 63.79 | 14.696 | 0.075806 | 15.333 | 0.031237 |  | 3181 | 15.333 | 63.79 | 14.696 | 0.075806 | 0.031237
3182 | 63.8 | 14.696 | 0.075805 | 15.336 | 0.031241 |  | 3182 | 15.336 | 63.8 | 14.696 | 0.075805 | 0.031241
3183 | 63.81 | 14.696 | 0.075803 | 15.338 | 0.031246 |  | 3183 | 15.338 | 63.81 | 14.696 | 0.075803 | 0.031246
3184 | 63.82 | 14.696 | 0.075802 | 15.341 | 0.031251 |  | 3184 | 15.341 | 63.82 | 14.696 | 0.075802 | 0.031251
3185 | 63.83 | 14.696 | 0.0758 | 15.343 | 0.031255 |  | 3185 | 15.343 | 63.83 | 14.696 | 0.0758 | 0.031255
3186 | 63.84 | 14.696 | 0.075799 | 15.345 | 0.03126 |  | 3186 | 15.345 | 63.84 | 14.696 | 0.075799 | 0.03126
3187 | 63.85 | 14.696 | 0.075797 | 15.348 | 0.031264 |  | 3187 | 15.348 | 63.85 | 14.696 | 0.075797 | 0.031264
3188 | 63.86 | 14.696 | 0.075796 | 15.35 | 0.031269 |  | 3188 | 15.35 | 63.86 | 14.696 | 0.075796 | 0.031269
3189 | 63.87 | 14.696 | 0.075794 | 15.353 | 0.031274 |  | 3189 | 15.353 | 63.87 | 14.696 | 0.075794 | 0.031274
3190 | 63.88 | 14.696 | 0.075793 | 15.355 | 0.031278 |  | 3190 | 15.355 | 63.88 | 14.696 | 0.075793 | 0.031278
3191 | 63.89 | 14.696 | 0.075791 | 15.357 | 0.031283 |  | 3191 | 15.357 | 63.89 | 14.696 | 0.075791 | 0.031283
3192 | 63.9 | 14.696 | 0.07579 | 15.36 | 0.031287 |  | 3192 | 15.36 | 63.9 | 14.696 | 0.07579 | 0.031287
3193 | 63.91 | 14.696 | 0.075789 | 15.362 | 0.031292 |  | 3193 | 15.362 | 63.91 | 14.696 | 0.075789 | 0.031292
3194 | 63.92 | 14.696 | 0.075787 | 15.365 | 0.031297 |  | 3194 | 15.365 | 63.92 | 14.696 | 0.075787 | 0.031297
3195 | 63.93 | 14.696 | 0.075786 | 15.367 | 0.031301 |  | 3195 | 15.367 | 63.93 | 14.696 | 0.075786 | 0.031301
3196 | 63.94 | 14.696 | 0.075784 | 15.37 | 0.031306 |  | 3196 | 15.37 | 63.94 | 14.696 | 0.075784 | 0.031306
3197 | 63.95 | 14.696 | 0.075783 | 15.372 | 0.03131 |  | 3197 | 15.372 | 63.95 | 14.696 | 0.075783 | 0.03131
3198 | 63.96 | 14.696 | 0.075781 | 15.374 | 0.031315 |  | 3198 | 15.374 | 63.96 | 14.696 | 0.075781 | 0.031315
3199 | 63.97 | 14.696 | 0.07578 | 15.377 | 0.03132 |  | 3199 | 15.377 | 63.97 | 14.696 | 0.07578 | 0.03132
3200 | 63.98 | 14.696 | 0.075778 | 15.379 | 0.031324 |  | 3200 | 15.379 | 63.98 | 14.696 | 0.075778 | 0.031324
3201 | 63.99 | 14.696 | 0.075777 | 15.382 | 0.031329 |  | 3201 | 15.382 | 63.99 | 14.696 | 0.075777 | 0.031329
3202 | 64 | 14.696 | 0.075776 | 15.384 | 0.031333 |  | 3202 | 15.384 | 64 | 14.696 | 0.075776 | 0.031333
3203 | 64.01 | 14.696 | 0.075774 | 15.386 | 0.031338 |  | 3203 | 15.386 | 64.01 | 14.696 | 0.075774 | 0.031338
3204 | 64.02 | 14.696 | 0.075773 | 15.389 | 0.031342 |  | 3204 | 15.389 | 64.02 | 14.696 | 0.075773 | 0.031342
3205 | 64.03 | 14.696 | 0.075771 | 15.391 | 0.031347 |  | 3205 | 15.391 | 64.03 | 14.696 | 0.075771 | 0.031347
3206 | 64.04 | 14.696 | 0.07577 | 15.394 | 0.031352 |  | 3206 | 15.394 | 64.04 | 14.696 | 0.07577 | 0.031352
3207 | 64.05 | 14.696 | 0.075768 | 15.396 | 0.031356 |  | 3207 | 15.396 | 64.05 | 14.696 | 0.075768 | 0.031356
3208 | 64.06 | 14.696 | 0.075767 | 15.398 | 0.031361 |  | 3208 | 15.398 | 64.06 | 14.696 | 0.075767 | 0.031361
3209 | 64.07 | 14.696 | 0.075765 | 15.401 | 0.031365 |  | 3209 | 15.401 | 64.07 | 14.696 | 0.075765 | 0.031365
3210 | 64.08 | 14.696 | 0.075764 | 15.403 | 0.03137 |  | 3210 | 15.403 | 64.08 | 14.696 | 0.075764 | 0.03137
3211 | 64.09 | 14.696 | 0.075762 | 15.406 | 0.031375 |  | 3211 | 15.406 | 64.09 | 14.696 | 0.075762 | 0.031375
3212 | 64.1 | 14.696 | 0.075761 | 15.408 | 0.031379 |  | 3212 | 15.408 | 64.1 | 14.696 | 0.075761 | 0.031379
3213 | 64.11 | 14.696 | 0.07576 | 15.41 | 0.031384 |  | 3213 | 15.41 | 64.11 | 14.696 | 0.07576 | 0.031384
3214 | 64.12 | 14.696 | 0.075758 | 15.413 | 0.031388 |  | 3214 | 15.413 | 64.12 | 14.696 | 0.075758 | 0.031388
3215 | 64.13 | 14.696 | 0.075757 | 15.415 | 0.031393 |  | 3215 | 15.415 | 64.13 | 14.696 | 0.075757 | 0.031393
3216 | 64.14 | 14.696 | 0.075755 | 15.418 | 0.031398 |  | 3216 | 15.418 | 64.14 | 14.696 | 0.075755 | 0.031398
3217 | 64.15 | 14.696 | 0.075754 | 15.42 | 0.031402 |  | 3217 | 15.42 | 64.15 | 14.696 | 0.075754 | 0.031402
3218 | 64.16 | 14.696 | 0.075752 | 15.422 | 0.031407 |  | 3218 | 15.422 | 64.16 | 14.696 | 0.075752 | 0.031407
3219 | 64.17 | 14.696 | 0.075751 | 15.425 | 0.031411 |  | 3219 | 15.425 | 64.17 | 14.696 | 0.075751 | 0.031411
3220 | 64.18 | 14.696 | 0.075749 | 15.427 | 0.031416 |  | 3220 | 15.427 | 64.18 | 14.696 | 0.075749 | 0.031416
3221 | 64.19 | 14.696 | 0.075748 | 15.43 | 0.031421 |  | 3221 | 15.43 | 64.19 | 14.696 | 0.075748 | 0.031421
3222 | 64.2 | 14.696 | 0.075746 | 15.432 | 0.031425 |  | 3222 | 15.432 | 64.2 | 14.696 | 0.075746 | 0.031425
3223 | 64.21 | 14.696 | 0.075745 | 15.434 | 0.03143 |  | 3223 | 15.434 | 64.21 | 14.696 | 0.075745 | 0.03143
3224 | 64.22 | 14.696 | 0.075744 | 15.437 | 0.031434 |  | 3224 | 15.437 | 64.22 | 14.696 | 0.075744 | 0.031434
3225 | 64.23 | 14.696 | 0.075742 | 15.439 | 0.031439 |  | 3225 | 15.439 | 64.23 | 14.696 | 0.075742 | 0.031439
3226 | 64.24 | 14.696 | 0.075741 | 15.442 | 0.031443 |  | 3226 | 15.442 | 64.24 | 14.696 | 0.075741 | 0.031443
3227 | 64.25 | 14.696 | 0.075739 | 15.444 | 0.031448 |  | 3227 | 15.444 | 64.25 | 14.696 | 0.075739 | 0.031448
3228 | 64.26 | 14.696 | 0.075738 | 15.446 | 0.031453 |  | 3228 | 15.446 | 64.26 | 14.696 | 0.075738 | 0.031453
3229 | 64.27 | 14.696 | 0.075736 | 15.449 | 0.031457 |  | 3229 | 15.449 | 64.27 | 14.696 | 0.075736 | 0.031457
3230 | 64.28 | 14.696 | 0.075735 | 15.451 | 0.031462 |  | 3230 | 15.451 | 64.28 | 14.696 | 0.075735 | 0.031462
3231 | 64.29 | 14.696 | 0.075733 | 15.454 | 0.031466 |  | 3231 | 15.454 | 64.29 | 14.696 | 0.075733 | 0.031466
3232 | 64.3 | 14.696 | 0.075732 | 15.456 | 0.031471 |  | 3232 | 15.456 | 64.3 | 14.696 | 0.075732 | 0.031471
3233 | 64.31 | 14.696 | 0.075731 | 15.458 | 0.031476 |  | 3233 | 15.458 | 64.31 | 14.696 | 0.075731 | 0.031476
3234 | 64.32 | 14.696 | 0.075729 | 15.461 | 0.03148 |  | 3234 | 15.461 | 64.32 | 14.696 | 0.075729 | 0.03148
3235 | 64.33 | 14.696 | 0.075728 | 15.463 | 0.031485 |  | 3235 | 15.463 | 64.33 | 14.696 | 0.075728 | 0.031485
3236 | 64.34 | 14.696 | 0.075726 | 15.466 | 0.031489 |  | 3236 | 15.466 | 64.34 | 14.696 | 0.075726 | 0.031489
3237 | 64.35 | 14.696 | 0.075725 | 15.468 | 0.031494 |  | 3237 | 15.468 | 64.35 | 14.696 | 0.075725 | 0.031494
3238 | 64.36 | 14.696 | 0.075723 | 15.471 | 0.031499 |  | 3238 | 15.471 | 64.36 | 14.696 | 0.075723 | 0.031499
3239 | 64.37 | 14.696 | 0.075722 | 15.473 | 0.031503 |  | 3239 | 15.473 | 64.37 | 14.696 | 0.075722 | 0.031503
3240 | 64.38 | 14.696 | 0.07572 | 15.475 | 0.031508 |  | 3240 | 15.475 | 64.38 | 14.696 | 0.07572 | 0.031508
3241 | 64.39 | 14.696 | 0.075719 | 15.478 | 0.031512 |  | 3241 | 15.478 | 64.39 | 14.696 | 0.075719 | 0.031512
3242 | 64.4 | 14.696 | 0.075718 | 15.48 | 0.031517 |  | 3242 | 15.48 | 64.4 | 14.696 | 0.075718 | 0.031517
3243 | 64.41 | 14.696 | 0.075716 | 15.483 | 0.031521 |  | 3243 | 15.483 | 64.41 | 14.696 | 0.075716 | 0.031521
3244 | 64.42 | 14.696 | 0.075715 | 15.485 | 0.031526 |  | 3244 | 15.485 | 64.42 | 14.696 | 0.075715 | 0.031526
3245 | 64.43 | 14.696 | 0.075713 | 15.487 | 0.031531 |  | 3245 | 15.487 | 64.43 | 14.696 | 0.075713 | 0.031531
3246 | 64.44 | 14.696 | 0.075712 | 15.49 | 0.031535 |  | 3246 | 15.49 | 64.44 | 14.696 | 0.075712 | 0.031535
3247 | 64.45 | 14.696 | 0.07571 | 15.492 | 0.03154 |  | 3247 | 15.492 | 64.45 | 14.696 | 0.07571 | 0.03154
3248 | 64.46 | 14.696 | 0.075709 | 15.495 | 0.031544 |  | 3248 | 15.495 | 64.46 | 14.696 | 0.075709 | 0.031544
3249 | 64.47 | 14.696 | 0.075707 | 15.497 | 0.031549 |  | 3249 | 15.497 | 64.47 | 14.696 | 0.075707 | 0.031549
3250 | 64.48 | 14.696 | 0.075706 | 15.499 | 0.031554 |  | 3250 | 15.499 | 64.48 | 14.696 | 0.075706 | 0.031554
3251 | 64.49 | 14.696 | 0.075704 | 15.502 | 0.031558 |  | 3251 | 15.502 | 64.49 | 14.696 | 0.075704 | 0.031558
3252 | 64.5 | 14.696 | 0.075703 | 15.504 | 0.031563 |  | 3252 | 15.504 | 64.5 | 14.696 | 0.075703 | 0.031563
3253 | 64.51 | 14.696 | 0.075702 | 15.507 | 0.031567 |  | 3253 | 15.507 | 64.51 | 14.696 | 0.075702 | 0.031567
3254 | 64.52 | 14.696 | 0.0757 | 15.509 | 0.031572 |  | 3254 | 15.509 | 64.52 | 14.696 | 0.0757 | 0.031572
3255 | 64.53 | 14.696 | 0.075699 | 15.511 | 0.031577 |  | 3255 | 15.511 | 64.53 | 14.696 | 0.075699 | 0.031577
3256 | 64.54 | 14.696 | 0.075697 | 15.514 | 0.031581 |  | 3256 | 15.514 | 64.54 | 14.696 | 0.075697 | 0.031581
3257 | 64.55 | 14.696 | 0.075696 | 15.516 | 0.031586 |  | 3257 | 15.516 | 64.55 | 14.696 | 0.075696 | 0.031586
3258 | 64.56 | 14.696 | 0.075694 | 15.519 | 0.03159 |  | 3258 | 15.519 | 64.56 | 14.696 | 0.075694 | 0.03159
3259 | 64.57 | 14.696 | 0.075693 | 15.521 | 0.031595 |  | 3259 | 15.521 | 64.57 | 14.696 | 0.075693 | 0.031595
3260 | 64.58 | 14.696 | 0.075691 | 15.523 | 0.031599 |  | 3260 | 15.523 | 64.58 | 14.696 | 0.075691 | 0.031599
3261 | 64.59 | 14.696 | 0.07569 | 15.526 | 0.031604 |  | 3261 | 15.526 | 64.59 | 14.696 | 0.07569 | 0.031604
3262 | 64.6 | 14.696 | 0.075689 | 15.528 | 0.031609 |  | 3262 | 15.528 | 64.6 | 14.696 | 0.075689 | 0.031609
3263 | 64.61 | 14.696 | 0.075687 | 15.531 | 0.031613 |  | 3263 | 15.531 | 64.61 | 14.696 | 0.075687 | 0.031613
3264 | 64.62 | 14.696 | 0.075686 | 15.533 | 0.031618 |  | 3264 | 15.533 | 64.62 | 14.696 | 0.075686 | 0.031618
3265 | 64.63 | 14.696 | 0.075684 | 15.535 | 0.031622 |  | 3265 | 15.535 | 64.63 | 14.696 | 0.075684 | 0.031622
3266 | 64.64 | 14.696 | 0.075683 | 15.538 | 0.031627 |  | 3266 | 15.538 | 64.64 | 14.696 | 0.075683 | 0.031627
3267 | 64.65 | 14.696 | 0.075681 | 15.54 | 0.031632 |  | 3267 | 15.54 | 64.65 | 14.696 | 0.075681 | 0.031632
3268 | 64.66 | 14.696 | 0.07568 | 15.543 | 0.031636 |  | 3268 | 15.543 | 64.66 | 14.696 | 0.07568 | 0.031636
3269 | 64.67 | 14.696 | 0.075678 | 15.545 | 0.031641 |  | 3269 | 15.545 | 64.67 | 14.696 | 0.075678 | 0.031641
3270 | 64.68 | 14.696 | 0.075677 | 15.547 | 0.031645 |  | 3270 | 15.547 | 64.68 | 14.696 | 0.075677 | 0.031645
3271 | 64.69 | 14.696 | 0.075676 | 15.55 | 0.03165 |  | 3271 | 15.55 | 64.69 | 14.696 | 0.075676 | 0.03165
3272 | 64.7 | 14.696 | 0.075674 | 15.552 | 0.031654 |  | 3272 | 15.552 | 64.7 | 14.696 | 0.075674 | 0.031654
3273 | 64.71 | 14.696 | 0.075673 | 15.555 | 0.031659 |  | 3273 | 15.555 | 64.71 | 14.696 | 0.075673 | 0.031659
3274 | 64.72 | 14.696 | 0.075671 | 15.557 | 0.031664 |  | 3274 | 15.557 | 64.72 | 14.696 | 0.075671 | 0.031664
3275 | 64.73 | 14.696 | 0.07567 | 15.559 | 0.031668 |  | 3275 | 15.559 | 64.73 | 14.696 | 0.07567 | 0.031668
3276 | 64.74 | 14.696 | 0.075668 | 15.562 | 0.031673 |  | 3276 | 15.562 | 64.74 | 14.696 | 0.075668 | 0.031673
3277 | 64.75 | 14.696 | 0.075667 | 15.564 | 0.031677 |  | 3277 | 15.564 | 64.75 | 14.696 | 0.075667 | 0.031677
3278 | 64.76 | 14.696 | 0.075665 | 15.567 | 0.031682 |  | 3278 | 15.567 | 64.76 | 14.696 | 0.075665 | 0.031682
3279 | 64.77 | 14.696 | 0.075664 | 15.569 | 0.031687 |  | 3279 | 15.569 | 64.77 | 14.696 | 0.075664 | 0.031687
3280 | 64.78 | 14.696 | 0.075662 | 15.572 | 0.031691 |  | 3280 | 15.572 | 64.78 | 14.696 | 0.075662 | 0.031691
3281 | 64.79 | 14.696 | 0.075661 | 15.574 | 0.031696 |  | 3281 | 15.574 | 64.79 | 14.696 | 0.075661 | 0.031696
3282 | 64.8 | 14.696 | 0.07566 | 15.576 | 0.0317 |  | 3282 | 15.576 | 64.8 | 14.696 | 0.07566 | 0.0317
3283 | 64.81 | 14.696 | 0.075658 | 15.579 | 0.031705 |  | 3283 | 15.579 | 64.81 | 14.696 | 0.075658 | 0.031705
3284 | 64.82 | 14.696 | 0.075657 | 15.581 | 0.03171 |  | 3284 | 15.581 | 64.82 | 14.696 | 0.075657 | 0.03171
3285 | 64.83 | 14.696 | 0.075655 | 15.584 | 0.031714 |  | 3285 | 15.584 | 64.83 | 14.696 | 0.075655 | 0.031714
3286 | 64.84 | 14.696 | 0.075654 | 15.586 | 0.031719 |  | 3286 | 15.586 | 64.84 | 14.696 | 0.075654 | 0.031719
3287 | 64.85 | 14.696 | 0.075652 | 15.588 | 0.031723 |  | 3287 | 15.588 | 64.85 | 14.696 | 0.075652 | 0.031723
3288 | 64.86 | 14.696 | 0.075651 | 15.591 | 0.031728 |  | 3288 | 15.591 | 64.86 | 14.696 | 0.075651 | 0.031728
3289 | 64.87 | 14.696 | 0.075649 | 15.593 | 0.031732 |  | 3289 | 15.593 | 64.87 | 14.696 | 0.075649 | 0.031732
3290 | 64.88 | 14.696 | 0.075648 | 15.596 | 0.031737 |  | 3290 | 15.596 | 64.88 | 14.696 | 0.075648 | 0.031737
3291 | 64.89 | 14.696 | 0.075647 | 15.598 | 0.031742 |  | 3291 | 15.598 | 64.89 | 14.696 | 0.075647 | 0.031742
3292 | 64.9 | 14.696 | 0.075645 | 15.6 | 0.031746 |  | 3292 | 15.6 | 64.9 | 14.696 | 0.075645 | 0.031746
3293 | 64.91 | 14.696 | 0.075644 | 15.603 | 0.031751 |  | 3293 | 15.603 | 64.91 | 14.696 | 0.075644 | 0.031751
3294 | 64.92 | 14.696 | 0.075642 | 15.605 | 0.031755 |  | 3294 | 15.605 | 64.92 | 14.696 | 0.075642 | 0.031755
3295 | 64.93 | 14.696 | 0.075641 | 15.608 | 0.03176 |  | 3295 | 15.608 | 64.93 | 14.696 | 0.075641 | 0.03176
3296 | 64.94 | 14.696 | 0.075639 | 15.61 | 0.031765 |  | 3296 | 15.61 | 64.94 | 14.696 | 0.075639 | 0.031765
3297 | 64.95 | 14.696 | 0.075638 | 15.612 | 0.031769 |  | 3297 | 15.612 | 64.95 | 14.696 | 0.075638 | 0.031769
3298 | 64.96 | 14.696 | 0.075636 | 15.615 | 0.031774 |  | 3298 | 15.615 | 64.96 | 14.696 | 0.075636 | 0.031774
3299 | 64.97 | 14.696 | 0.075635 | 15.617 | 0.031778 |  | 3299 | 15.617 | 64.97 | 14.696 | 0.075635 | 0.031778
3300 | 64.98 | 14.696 | 0.075634 | 15.62 | 0.031783 |  | 3300 | 15.62 | 64.98 | 14.696 | 0.075634 | 0.031783
3301 | 64.99 | 14.696 | 0.075632 | 15.622 | 0.031787 |  | 3301 | 15.622 | 64.99 | 14.696 | 0.075632 | 0.031787
3302 | 65 | 14.696 | 0.075631 | 15.624 | 0.031792 |  | 3302 | 15.624 | 65 | 14.696 | 0.075631 | 0.031792
3303 | 65.01 | 14.696 | 0.075629 | 15.627 | 0.031797 |  | 3303 | 15.627 | 65.01 | 14.696 | 0.075629 | 0.031797
3304 | 65.02 | 14.696 | 0.075628 | 15.629 | 0.031801 |  | 3304 | 15.629 | 65.02 | 14.696 | 0.075628 | 0.031801
3305 | 65.03 | 14.696 | 0.075626 | 15.632 | 0.031806 |  | 3305 | 15.632 | 65.03 | 14.696 | 0.075626 | 0.031806
3306 | 65.04 | 14.696 | 0.075625 | 15.634 | 0.03181 |  | 3306 | 15.634 | 65.04 | 14.696 | 0.075625 | 0.03181
3307 | 65.05 | 14.696 | 0.075623 | 15.636 | 0.031815 |  | 3307 | 15.636 | 65.05 | 14.696 | 0.075623 | 0.031815
3308 | 65.06 | 14.696 | 0.075622 | 15.639 | 0.03182 |  | 3308 | 15.639 | 65.06 | 14.696 | 0.075622 | 0.03182
3309 | 65.07 | 14.696 | 0.075621 | 15.641 | 0.031824 |  | 3309 | 15.641 | 65.07 | 14.696 | 0.075621 | 0.031824
3310 | 65.08 | 14.696 | 0.075619 | 15.644 | 0.031829 |  | 3310 | 15.644 | 65.08 | 14.696 | 0.075619 | 0.031829
3311 | 65.09 | 14.696 | 0.075618 | 15.646 | 0.031833 |  | 3311 | 15.646 | 65.09 | 14.696 | 0.075618 | 0.031833
3312 | 65.1 | 14.696 | 0.075616 | 15.648 | 0.031838 |  | 3312 | 15.648 | 65.1 | 14.696 | 0.075616 | 0.031838
3313 | 65.11 | 14.696 | 0.075615 | 15.651 | 0.031842 |  | 3313 | 15.651 | 65.11 | 14.696 | 0.075615 | 0.031842
3314 | 65.12 | 14.696 | 0.075613 | 15.653 | 0.031847 |  | 3314 | 15.653 | 65.12 | 14.696 | 0.075613 | 0.031847
3315 | 65.13 | 14.696 | 0.075612 | 15.656 | 0.031852 |  | 3315 | 15.656 | 65.13 | 14.696 | 0.075612 | 0.031852
3316 | 65.14 | 14.696 | 0.07561 | 15.658 | 0.031856 |  | 3316 | 15.658 | 65.14 | 14.696 | 0.07561 | 0.031856
3317 | 65.15 | 14.696 | 0.075609 | 15.66 | 0.031861 |  | 3317 | 15.66 | 65.15 | 14.696 | 0.075609 | 0.031861
3318 | 65.16 | 14.696 | 0.075608 | 15.663 | 0.031865 |  | 3318 | 15.663 | 65.16 | 14.696 | 0.075608 | 0.031865
3319 | 65.17 | 14.696 | 0.075606 | 15.665 | 0.03187 |  | 3319 | 15.665 | 65.17 | 14.696 | 0.075606 | 0.03187
3320 | 65.18 | 14.696 | 0.075605 | 15.668 | 0.031875 |  | 3320 | 15.668 | 65.18 | 14.696 | 0.075605 | 0.031875
3321 | 65.19 | 14.696 | 0.075603 | 15.67 | 0.031879 |  | 3321 | 15.67 | 65.19 | 14.696 | 0.075603 | 0.031879
3322 | 65.2 | 14.696 | 0.075602 | 15.672 | 0.031884 |  | 3322 | 15.672 | 65.2 | 14.696 | 0.075602 | 0.031884
3323 | 65.21 | 14.696 | 0.0756 | 15.675 | 0.031888 |  | 3323 | 15.675 | 65.21 | 14.696 | 0.0756 | 0.031888
3324 | 65.22 | 14.696 | 0.075599 | 15.677 | 0.031893 |  | 3324 | 15.677 | 65.22 | 14.696 | 0.075599 | 0.031893
3325 | 65.23 | 14.696 | 0.075597 | 15.68 | 0.031897 |  | 3325 | 15.68 | 65.23 | 14.696 | 0.075597 | 0.031897
3326 | 65.24 | 14.696 | 0.075596 | 15.682 | 0.031902 |  | 3326 | 15.682 | 65.24 | 14.696 | 0.075596 | 0.031902
3327 | 65.25 | 14.696 | 0.075595 | 15.685 | 0.031907 |  | 3327 | 15.685 | 65.25 | 14.696 | 0.075595 | 0.031907
3328 | 65.26 | 14.696 | 0.075593 | 15.687 | 0.031911 |  | 3328 | 15.687 | 65.26 | 14.696 | 0.075593 | 0.031911
3329 | 65.27 | 14.696 | 0.075592 | 15.689 | 0.031916 |  | 3329 | 15.689 | 65.27 | 14.696 | 0.075592 | 0.031916
3330 | 65.28 | 14.696 | 0.07559 | 15.692 | 0.03192 |  | 3330 | 15.692 | 65.28 | 14.696 | 0.07559 | 0.03192
3331 | 65.29 | 14.696 | 0.075589 | 15.694 | 0.031925 |  | 3331 | 15.694 | 65.29 | 14.696 | 0.075589 | 0.031925
3332 | 65.3 | 14.696 | 0.075587 | 15.697 | 0.031929 |  | 3332 | 15.697 | 65.3 | 14.696 | 0.075587 | 0.031929
3333 | 65.31 | 14.696 | 0.075586 | 15.699 | 0.031934 |  | 3333 | 15.699 | 65.31 | 14.696 | 0.075586 | 0.031934
3334 | 65.32 | 14.696 | 0.075584 | 15.701 | 0.031939 |  | 3334 | 15.701 | 65.32 | 14.696 | 0.075584 | 0.031939
3335 | 65.33 | 14.696 | 0.075583 | 15.704 | 0.031943 |  | 3335 | 15.704 | 65.33 | 14.696 | 0.075583 | 0.031943
3336 | 65.34 | 14.696 | 0.075582 | 15.706 | 0.031948 |  | 3336 | 15.706 | 65.34 | 14.696 | 0.075582 | 0.031948
3337 | 65.35 | 14.696 | 0.07558 | 15.709 | 0.031952 |  | 3337 | 15.709 | 65.35 | 14.696 | 0.07558 | 0.031952
3338 | 65.36 | 14.696 | 0.075579 | 15.711 | 0.031957 |  | 3338 | 15.711 | 65.36 | 14.696 | 0.075579 | 0.031957
3339 | 65.37 | 14.696 | 0.075577 | 15.713 | 0.031962 |  | 3339 | 15.713 | 65.37 | 14.696 | 0.075577 | 0.031962
3340 | 65.38 | 14.696 | 0.075576 | 15.716 | 0.031966 |  | 3340 | 15.716 | 65.38 | 14.696 | 0.075576 | 0.031966
3341 | 65.39 | 14.696 | 0.075574 | 15.718 | 0.031971 |  | 3341 | 15.718 | 65.39 | 14.696 | 0.075574 | 0.031971
3342 | 65.4 | 14.696 | 0.075573 | 15.721 | 0.031975 |  | 3342 | 15.721 | 65.4 | 14.696 | 0.075573 | 0.031975
3343 | 65.41 | 14.696 | 0.075571 | 15.723 | 0.03198 |  | 3343 | 15.723 | 65.41 | 14.696 | 0.075571 | 0.03198
3344 | 65.42 | 14.696 | 0.07557 | 15.725 | 0.031984 |  | 3344 | 15.725 | 65.42 | 14.696 | 0.07557 | 0.031984
3345 | 65.43 | 14.696 | 0.075569 | 15.728 | 0.031989 |  | 3345 | 15.728 | 65.43 | 14.696 | 0.075569 | 0.031989
3346 | 65.44 | 14.696 | 0.075567 | 15.73 | 0.031994 |  | 3346 | 15.73 | 65.44 | 14.696 | 0.075567 | 0.031994
3347 | 65.45 | 14.696 | 0.075566 | 15.733 | 0.031998 |  | 3347 | 15.733 | 65.45 | 14.696 | 0.075566 | 0.031998
3348 | 65.46 | 14.696 | 0.075564 | 15.735 | 0.032003 |  | 3348 | 15.735 | 65.46 | 14.696 | 0.075564 | 0.032003
3349 | 65.47 | 14.696 | 0.075563 | 15.737 | 0.032007 |  | 3349 | 15.737 | 65.47 | 14.696 | 0.075563 | 0.032007
3350 | 65.48 | 14.696 | 0.075561 | 15.74 | 0.032012 |  | 3350 | 15.74 | 65.48 | 14.696 | 0.075561 | 0.032012
3351 | 65.49 | 14.696 | 0.07556 | 15.742 | 0.032016 |  | 3351 | 15.742 | 65.49 | 14.696 | 0.07556 | 0.032016
3352 | 65.5 | 14.696 | 0.075558 | 15.745 | 0.032021 |  | 3352 | 15.745 | 65.5 | 14.696 | 0.075558 | 0.032021
3353 | 65.51 | 14.696 | 0.075557 | 15.747 | 0.032026 |  | 3353 | 15.747 | 65.51 | 14.696 | 0.075557 | 0.032026
3354 | 65.52 | 14.696 | 0.075556 | 15.749 | 0.03203 |  | 3354 | 15.749 | 65.52 | 14.696 | 0.075556 | 0.03203
3355 | 65.53 | 14.696 | 0.075554 | 15.752 | 0.032035 |  | 3355 | 15.752 | 65.53 | 14.696 | 0.075554 | 0.032035
3356 | 65.54 | 14.696 | 0.075553 | 15.754 | 0.032039 |  | 3356 | 15.754 | 65.54 | 14.696 | 0.075553 | 0.032039
3357 | 65.55 | 14.696 | 0.075551 | 15.757 | 0.032044 |  | 3357 | 15.757 | 65.55 | 14.696 | 0.075551 | 0.032044
3358 | 65.56 | 14.696 | 0.07555 | 15.759 | 0.032049 |  | 3358 | 15.759 | 65.56 | 14.696 | 0.07555 | 0.032049
3359 | 65.57 | 14.696 | 0.075548 | 15.761 | 0.032053 |  | 3359 | 15.761 | 65.57 | 14.696 | 0.075548 | 0.032053
3360 | 65.58 | 14.696 | 0.075547 | 15.764 | 0.032058 |  | 3360 | 15.764 | 65.58 | 14.696 | 0.075547 | 0.032058
3361 | 65.59 | 14.696 | 0.075545 | 15.766 | 0.032062 |  | 3361 | 15.766 | 65.59 | 14.696 | 0.075545 | 0.032062
3362 | 65.6 | 14.696 | 0.075544 | 15.769 | 0.032067 |  | 3362 | 15.769 | 65.6 | 14.696 | 0.075544 | 0.032067
3363 | 65.61 | 14.696 | 0.075543 | 15.771 | 0.032071 |  | 3363 | 15.771 | 65.61 | 14.696 | 0.075543 | 0.032071
3364 | 65.62 | 14.696 | 0.075541 | 15.773 | 0.032076 |  | 3364 | 15.773 | 65.62 | 14.696 | 0.075541 | 0.032076
3365 | 65.63 | 14.696 | 0.07554 | 15.776 | 0.032081 |  | 3365 | 15.776 | 65.63 | 14.696 | 0.07554 | 0.032081
3366 | 65.64 | 14.696 | 0.075538 | 15.778 | 0.032085 |  | 3366 | 15.778 | 65.64 | 14.696 | 0.075538 | 0.032085
3367 | 65.65 | 14.696 | 0.075537 | 15.781 | 0.03209 |  | 3367 | 15.781 | 65.65 | 14.696 | 0.075537 | 0.03209
3368 | 65.66 | 14.696 | 0.075535 | 15.783 | 0.032094 |  | 3368 | 15.783 | 65.66 | 14.696 | 0.075535 | 0.032094
3369 | 65.67 | 14.696 | 0.075534 | 15.786 | 0.032099 |  | 3369 | 15.786 | 65.67 | 14.696 | 0.075534 | 0.032099
3370 | 65.68 | 14.696 | 0.075532 | 15.788 | 0.032103 |  | 3370 | 15.788 | 65.68 | 14.696 | 0.075532 | 0.032103
3371 | 65.69 | 14.696 | 0.075531 | 15.79 | 0.032108 |  | 3371 | 15.79 | 65.69 | 14.696 | 0.075531 | 0.032108
3372 | 65.7 | 14.696 | 0.07553 | 15.793 | 0.032113 |  | 3372 | 15.793 | 65.7 | 14.696 | 0.07553 | 0.032113
3373 | 65.71 | 14.696 | 0.075528 | 15.795 | 0.032117 |  | 3373 | 15.795 | 65.71 | 14.696 | 0.075528 | 0.032117
3374 | 65.72 | 14.696 | 0.075527 | 15.798 | 0.032122 |  | 3374 | 15.798 | 65.72 | 14.696 | 0.075527 | 0.032122
3375 | 65.73 | 14.696 | 0.075525 | 15.8 | 0.032126 |  | 3375 | 15.8 | 65.73 | 14.696 | 0.075525 | 0.032126
3376 | 65.74 | 14.696 | 0.075524 | 15.802 | 0.032131 |  | 3376 | 15.802 | 65.74 | 14.696 | 0.075524 | 0.032131
3377 | 65.75 | 14.696 | 0.075522 | 15.805 | 0.032136 |  | 3377 | 15.805 | 65.75 | 14.696 | 0.075522 | 0.032136
3378 | 65.76 | 14.696 | 0.075521 | 15.807 | 0.03214 |  | 3378 | 15.807 | 65.76 | 14.696 | 0.075521 | 0.03214
3379 | 65.77 | 14.696 | 0.07552 | 15.81 | 0.032145 |  | 3379 | 15.81 | 65.77 | 14.696 | 0.07552 | 0.032145
3380 | 65.78 | 14.696 | 0.075518 | 15.812 | 0.032149 |  | 3380 | 15.812 | 65.78 | 14.696 | 0.075518 | 0.032149
3381 | 65.79 | 14.696 | 0.075517 | 15.814 | 0.032154 |  | 3381 | 15.814 | 65.79 | 14.696 | 0.075517 | 0.032154
3382 | 65.8 | 14.696 | 0.075515 | 15.817 | 0.032158 |  | 3382 | 15.817 | 65.8 | 14.696 | 0.075515 | 0.032158
3383 | 65.81 | 14.696 | 0.075514 | 15.819 | 0.032163 |  | 3383 | 15.819 | 65.81 | 14.696 | 0.075514 | 0.032163
3384 | 65.82 | 14.696 | 0.075512 | 15.822 | 0.032168 |  | 3384 | 15.822 | 65.82 | 14.696 | 0.075512 | 0.032168
3385 | 65.83 | 14.696 | 0.075511 | 15.824 | 0.032172 |  | 3385 | 15.824 | 65.83 | 14.696 | 0.075511 | 0.032172
3386 | 65.84 | 14.696 | 0.075509 | 15.826 | 0.032177 |  | 3386 | 15.826 | 65.84 | 14.696 | 0.075509 | 0.032177
3387 | 65.85 | 14.696 | 0.075508 | 15.829 | 0.032181 |  | 3387 | 15.829 | 65.85 | 14.696 | 0.075508 | 0.032181
3388 | 65.86 | 14.696 | 0.075507 | 15.831 | 0.032186 |  | 3388 | 15.831 | 65.86 | 14.696 | 0.075507 | 0.032186
3389 | 65.87 | 14.696 | 0.075505 | 15.834 | 0.03219 |  | 3389 | 15.834 | 65.87 | 14.696 | 0.075505 | 0.03219
3390 | 65.88 | 14.696 | 0.075504 | 15.836 | 0.032195 |  | 3390 | 15.836 | 65.88 | 14.696 | 0.075504 | 0.032195
3391 | 65.89 | 14.696 | 0.075502 | 15.838 | 0.0322 |  | 3391 | 15.838 | 65.89 | 14.696 | 0.075502 | 0.0322
3392 | 65.9 | 14.696 | 0.075501 | 15.841 | 0.032204 |  | 3392 | 15.841 | 65.9 | 14.696 | 0.075501 | 0.032204
3393 | 65.91 | 14.696 | 0.075499 | 15.843 | 0.032209 |  | 3393 | 15.843 | 65.91 | 14.696 | 0.075499 | 0.032209
3394 | 65.92 | 14.696 | 0.075498 | 15.846 | 0.032213 |  | 3394 | 15.846 | 65.92 | 14.696 | 0.075498 | 0.032213
3395 | 65.93 | 14.696 | 0.075496 | 15.848 | 0.032218 |  | 3395 | 15.848 | 65.93 | 14.696 | 0.075496 | 0.032218
3396 | 65.94 | 14.696 | 0.075495 | 15.85 | 0.032222 |  | 3396 | 15.85 | 65.94 | 14.696 | 0.075495 | 0.032222
3397 | 65.95 | 14.696 | 0.075494 | 15.853 | 0.032227 |  | 3397 | 15.853 | 65.95 | 14.696 | 0.075494 | 0.032227
3398 | 65.96 | 14.696 | 0.075492 | 15.855 | 0.032232 |  | 3398 | 15.855 | 65.96 | 14.696 | 0.075492 | 0.032232
3399 | 65.97 | 14.696 | 0.075491 | 15.858 | 0.032236 |  | 3399 | 15.858 | 65.97 | 14.696 | 0.075491 | 0.032236
3400 | 65.98 | 14.696 | 0.075489 | 15.86 | 0.032241 |  | 3400 | 15.86 | 65.98 | 14.696 | 0.075489 | 0.032241
3401 | 65.99 | 14.696 | 0.075488 | 15.862 | 0.032245 |  | 3401 | 15.862 | 65.99 | 14.696 | 0.075488 | 0.032245
3402 | 66 | 14.696 | 0.075486 | 15.865 | 0.03225 |  | 3402 | 15.865 | 66 | 14.696 | 0.075486 | 0.03225
3403 | 66.01 | 14.696 | 0.075485 | 15.867 | 0.032254 |  | 3403 | 15.867 | 66.01 | 14.696 | 0.075485 | 0.032254
3404 | 66.02 | 14.696 | 0.075483 | 15.87 | 0.032259 |  | 3404 | 15.87 | 66.02 | 14.696 | 0.075483 | 0.032259
3405 | 66.03 | 14.696 | 0.075482 | 15.872 | 0.032264 |  | 3405 | 15.872 | 66.03 | 14.696 | 0.075482 | 0.032264
3406 | 66.04 | 14.696 | 0.075481 | 15.874 | 0.032268 |  | 3406 | 15.874 | 66.04 | 14.696 | 0.075481 | 0.032268
3407 | 66.05 | 14.696 | 0.075479 | 15.877 | 0.032273 |  | 3407 | 15.877 | 66.05 | 14.696 | 0.075479 | 0.032273
3408 | 66.06 | 14.696 | 0.075478 | 15.879 | 0.032277 |  | 3408 | 15.879 | 66.06 | 14.696 | 0.075478 | 0.032277
3409 | 66.07 | 14.696 | 0.075476 | 15.882 | 0.032282 |  | 3409 | 15.882 | 66.07 | 14.696 | 0.075476 | 0.032282
3410 | 66.08 | 14.696 | 0.075475 | 15.884 | 0.032286 |  | 3410 | 15.884 | 66.08 | 14.696 | 0.075475 | 0.032286
3411 | 66.09 | 14.696 | 0.075473 | 15.887 | 0.032291 |  | 3411 | 15.887 | 66.09 | 14.696 | 0.075473 | 0.032291
3412 | 66.1 | 14.696 | 0.075472 | 15.889 | 0.032296 |  | 3412 | 15.889 | 66.1 | 14.696 | 0.075472 | 0.032296
3413 | 66.11 | 14.696 | 0.075471 | 15.891 | 0.0323 |  | 3413 | 15.891 | 66.11 | 14.696 | 0.075471 | 0.0323
3414 | 66.12 | 14.696 | 0.075469 | 15.894 | 0.032305 |  | 3414 | 15.894 | 66.12 | 14.696 | 0.075469 | 0.032305
3415 | 66.13 | 14.696 | 0.075468 | 15.896 | 0.032309 |  | 3415 | 15.896 | 66.13 | 14.696 | 0.075468 | 0.032309
3416 | 66.14 | 14.696 | 0.075466 | 15.899 | 0.032314 |  | 3416 | 15.899 | 66.14 | 14.696 | 0.075466 | 0.032314
3417 | 66.15 | 14.696 | 0.075465 | 15.901 | 0.032319 |  | 3417 | 15.901 | 66.15 | 14.696 | 0.075465 | 0.032319
3418 | 66.16 | 14.696 | 0.075463 | 15.903 | 0.032323 |  | 3418 | 15.903 | 66.16 | 14.696 | 0.075463 | 0.032323
3419 | 66.17 | 14.696 | 0.075462 | 15.906 | 0.032328 |  | 3419 | 15.906 | 66.17 | 14.696 | 0.075462 | 0.032328
3420 | 66.18 | 14.696 | 0.07546 | 15.908 | 0.032332 |  | 3420 | 15.908 | 66.18 | 14.696 | 0.07546 | 0.032332
3421 | 66.19 | 14.696 | 0.075459 | 15.911 | 0.032337 |  | 3421 | 15.911 | 66.19 | 14.696 | 0.075459 | 0.032337
3422 | 66.2 | 14.696 | 0.075458 | 15.913 | 0.032341 |  | 3422 | 15.913 | 66.2 | 14.696 | 0.075458 | 0.032341
3423 | 66.21 | 14.696 | 0.075456 | 15.915 | 0.032346 |  | 3423 | 15.915 | 66.21 | 14.696 | 0.075456 | 0.032346
3424 | 66.22 | 14.696 | 0.075455 | 15.918 | 0.032351 |  | 3424 | 15.918 | 66.22 | 14.696 | 0.075455 | 0.032351
3425 | 66.23 | 14.696 | 0.075453 | 15.92 | 0.032355 |  | 3425 | 15.92 | 66.23 | 14.696 | 0.075453 | 0.032355
3426 | 66.24 | 14.696 | 0.075452 | 15.923 | 0.03236 |  | 3426 | 15.923 | 66.24 | 14.696 | 0.075452 | 0.03236
3427 | 66.25 | 14.696 | 0.07545 | 15.925 | 0.032364 |  | 3427 | 15.925 | 66.25 | 14.696 | 0.07545 | 0.032364
3428 | 66.26 | 14.696 | 0.075449 | 15.927 | 0.032369 |  | 3428 | 15.927 | 66.26 | 14.696 | 0.075449 | 0.032369
3429 | 66.27 | 14.696 | 0.075448 | 15.93 | 0.032373 |  | 3429 | 15.93 | 66.27 | 14.696 | 0.075448 | 0.032373
3430 | 66.28 | 14.696 | 0.075446 | 15.932 | 0.032378 |  | 3430 | 15.932 | 66.28 | 14.696 | 0.075446 | 0.032378
3431 | 66.29 | 14.696 | 0.075445 | 15.935 | 0.032383 |  | 3431 | 15.935 | 66.29 | 14.696 | 0.075445 | 0.032383
3432 | 66.3 | 14.696 | 0.075443 | 15.937 | 0.032387 |  | 3432 | 15.937 | 66.3 | 14.696 | 0.075443 | 0.032387
3433 | 66.31 | 14.696 | 0.075442 | 15.939 | 0.032392 |  | 3433 | 15.939 | 66.31 | 14.696 | 0.075442 | 0.032392
3434 | 66.32 | 14.696 | 0.07544 | 15.942 | 0.032396 |  | 3434 | 15.942 | 66.32 | 14.696 | 0.07544 | 0.032396
3435 | 66.33 | 14.696 | 0.075439 | 15.944 | 0.032401 |  | 3435 | 15.944 | 66.33 | 14.696 | 0.075439 | 0.032401
3436 | 66.34 | 14.696 | 0.075437 | 15.947 | 0.032405 |  | 3436 | 15.947 | 66.34 | 14.696 | 0.075437 | 0.032405
3437 | 66.35 | 14.696 | 0.075436 | 15.949 | 0.03241 |  | 3437 | 15.949 | 66.35 | 14.696 | 0.075436 | 0.03241
3438 | 66.36 | 14.696 | 0.075435 | 15.951 | 0.032415 |  | 3438 | 15.951 | 66.36 | 14.696 | 0.075435 | 0.032415
3439 | 66.37 | 14.696 | 0.075433 | 15.954 | 0.032419 |  | 3439 | 15.954 | 66.37 | 14.696 | 0.075433 | 0.032419
3440 | 66.38 | 14.696 | 0.075432 | 15.956 | 0.032424 |  | 3440 | 15.956 | 66.38 | 14.696 | 0.075432 | 0.032424
3441 | 66.39 | 14.696 | 0.07543 | 15.959 | 0.032428 |  | 3441 | 15.959 | 66.39 | 14.696 | 0.07543 | 0.032428
3442 | 66.4 | 14.696 | 0.075429 | 15.961 | 0.032433 |  | 3442 | 15.961 | 66.4 | 14.696 | 0.075429 | 0.032433
3443 | 66.41 | 14.696 | 0.075427 | 15.963 | 0.032437 |  | 3443 | 15.963 | 66.41 | 14.696 | 0.075427 | 0.032437
3444 | 66.42 | 14.696 | 0.075426 | 15.966 | 0.032442 |  | 3444 | 15.966 | 66.42 | 14.696 | 0.075426 | 0.032442
3445 | 66.43 | 14.696 | 0.075424 | 15.968 | 0.032447 |  | 3445 | 15.968 | 66.43 | 14.696 | 0.075424 | 0.032447
3446 | 66.44 | 14.696 | 0.075423 | 15.971 | 0.032451 |  | 3446 | 15.971 | 66.44 | 14.696 | 0.075423 | 0.032451
3447 | 66.45 | 14.696 | 0.075422 | 15.973 | 0.032456 |  | 3447 | 15.973 | 66.45 | 14.696 | 0.075422 | 0.032456
3448 | 66.46 | 14.696 | 0.07542 | 15.975 | 0.03246 |  | 3448 | 15.975 | 66.46 | 14.696 | 0.07542 | 0.03246
3449 | 66.47 | 14.696 | 0.075419 | 15.978 | 0.032465 |  | 3449 | 15.978 | 66.47 | 14.696 | 0.075419 | 0.032465
3450 | 66.48 | 14.696 | 0.075417 | 15.98 | 0.032469 |  | 3450 | 15.98 | 66.48 | 14.696 | 0.075417 | 0.032469
3451 | 66.49 | 14.696 | 0.075416 | 15.983 | 0.032474 |  | 3451 | 15.983 | 66.49 | 14.696 | 0.075416 | 0.032474
3452 | 66.5 | 14.696 | 0.075414 | 15.985 | 0.032479 |  | 3452 | 15.985 | 66.5 | 14.696 | 0.075414 | 0.032479
3453 | 66.51 | 14.696 | 0.075413 | 15.988 | 0.032483 |  | 3453 | 15.988 | 66.51 | 14.696 | 0.075413 | 0.032483
3454 | 66.52 | 14.696 | 0.075412 | 15.99 | 0.032488 |  | 3454 | 15.99 | 66.52 | 14.696 | 0.075412 | 0.032488
3455 | 66.53 | 14.696 | 0.07541 | 15.992 | 0.032492 |  | 3455 | 15.992 | 66.53 | 14.696 | 0.07541 | 0.032492
3456 | 66.54 | 14.696 | 0.075409 | 15.995 | 0.032497 |  | 3456 | 15.995 | 66.54 | 14.696 | 0.075409 | 0.032497
3457 | 66.55 | 14.696 | 0.075407 | 15.997 | 0.032501 |  | 3457 | 15.997 | 66.55 | 14.696 | 0.075407 | 0.032501
3458 | 66.56 | 14.696 | 0.075406 | 16 | 0.032506 |  | 3458 | 16 | 66.56 | 14.696 | 0.075406 | 0.032506
3459 | 66.57 | 14.696 | 0.075404 | 16.002 | 0.032511 |  | 3459 | 16.002 | 66.57 | 14.696 | 0.075404 | 0.032511
3460 | 66.58 | 14.696 | 0.075403 | 16.004 | 0.032515 |  | 3460 | 16.004 | 66.58 | 14.696 | 0.075403 | 0.032515
3461 | 66.59 | 14.696 | 0.075401 | 16.007 | 0.03252 |  | 3461 | 16.007 | 66.59 | 14.696 | 0.075401 | 0.03252
3462 | 66.6 | 14.696 | 0.0754 | 16.009 | 0.032524 |  | 3462 | 16.009 | 66.6 | 14.696 | 0.0754 | 0.032524
3463 | 66.61 | 14.696 | 0.075399 | 16.012 | 0.032529 |  | 3463 | 16.012 | 66.61 | 14.696 | 0.075399 | 0.032529
3464 | 66.62 | 14.696 | 0.075397 | 16.014 | 0.032533 |  | 3464 | 16.014 | 66.62 | 14.696 | 0.075397 | 0.032533
3465 | 66.63 | 14.696 | 0.075396 | 16.016 | 0.032538 |  | 3465 | 16.016 | 66.63 | 14.696 | 0.075396 | 0.032538
3466 | 66.64 | 14.696 | 0.075394 | 16.019 | 0.032542 |  | 3466 | 16.019 | 66.64 | 14.696 | 0.075394 | 0.032542
3467 | 66.65 | 14.696 | 0.075393 | 16.021 | 0.032547 |  | 3467 | 16.021 | 66.65 | 14.696 | 0.075393 | 0.032547
3468 | 66.66 | 14.696 | 0.075391 | 16.024 | 0.032552 |  | 3468 | 16.024 | 66.66 | 14.696 | 0.075391 | 0.032552
3469 | 66.67 | 14.696 | 0.07539 | 16.026 | 0.032556 |  | 3469 | 16.026 | 66.67 | 14.696 | 0.07539 | 0.032556
3470 | 66.68 | 14.696 | 0.075389 | 16.028 | 0.032561 |  | 3470 | 16.028 | 66.68 | 14.696 | 0.075389 | 0.032561
3471 | 66.69 | 14.696 | 0.075387 | 16.031 | 0.032565 |  | 3471 | 16.031 | 66.69 | 14.696 | 0.075387 | 0.032565
3472 | 66.7 | 14.696 | 0.075386 | 16.033 | 0.03257 |  | 3472 | 16.033 | 66.7 | 14.696 | 0.075386 | 0.03257
3473 | 66.71 | 14.696 | 0.075384 | 16.036 | 0.032574 |  | 3473 | 16.036 | 66.71 | 14.696 | 0.075384 | 0.032574
3474 | 66.72 | 14.696 | 0.075383 | 16.038 | 0.032579 |  | 3474 | 16.038 | 66.72 | 14.696 | 0.075383 | 0.032579
3475 | 66.73 | 14.696 | 0.075381 | 16.04 | 0.032584 |  | 3475 | 16.04 | 66.73 | 14.696 | 0.075381 | 0.032584
3476 | 66.74 | 14.696 | 0.07538 | 16.043 | 0.032588 |  | 3476 | 16.043 | 66.74 | 14.696 | 0.07538 | 0.032588
3477 | 66.75 | 14.696 | 0.075379 | 16.045 | 0.032593 |  | 3477 | 16.045 | 66.75 | 14.696 | 0.075379 | 0.032593
3478 | 66.76 | 14.696 | 0.075377 | 16.048 | 0.032597 |  | 3478 | 16.048 | 66.76 | 14.696 | 0.075377 | 0.032597
3479 | 66.77 | 14.696 | 0.075376 | 16.05 | 0.032602 |  | 3479 | 16.05 | 66.77 | 14.696 | 0.075376 | 0.032602
3480 | 66.78 | 14.696 | 0.075374 | 16.052 | 0.032606 |  | 3480 | 16.052 | 66.78 | 14.696 | 0.075374 | 0.032606
3481 | 66.79 | 14.696 | 0.075373 | 16.055 | 0.032611 |  | 3481 | 16.055 | 66.79 | 14.696 | 0.075373 | 0.032611
3482 | 66.8 | 14.696 | 0.075371 | 16.057 | 0.032616 |  | 3482 | 16.057 | 66.8 | 14.696 | 0.075371 | 0.032616
3483 | 66.81 | 14.696 | 0.07537 | 16.06 | 0.03262 |  | 3483 | 16.06 | 66.81 | 14.696 | 0.07537 | 0.03262
3484 | 66.82 | 14.696 | 0.075368 | 16.062 | 0.032625 |  | 3484 | 16.062 | 66.82 | 14.696 | 0.075368 | 0.032625
3485 | 66.83 | 14.696 | 0.075367 | 16.064 | 0.032629 |  | 3485 | 16.064 | 66.83 | 14.696 | 0.075367 | 0.032629
3486 | 66.84 | 14.696 | 0.075366 | 16.067 | 0.032634 |  | 3486 | 16.067 | 66.84 | 14.696 | 0.075366 | 0.032634
3487 | 66.85 | 14.696 | 0.075364 | 16.069 | 0.032638 |  | 3487 | 16.069 | 66.85 | 14.696 | 0.075364 | 0.032638
3488 | 66.86 | 14.696 | 0.075363 | 16.072 | 0.032643 |  | 3488 | 16.072 | 66.86 | 14.696 | 0.075363 | 0.032643
3489 | 66.87 | 14.696 | 0.075361 | 16.074 | 0.032648 |  | 3489 | 16.074 | 66.87 | 14.696 | 0.075361 | 0.032648
3490 | 66.88 | 14.696 | 0.07536 | 16.076 | 0.032652 |  | 3490 | 16.076 | 66.88 | 14.696 | 0.07536 | 0.032652
3491 | 66.89 | 14.696 | 0.075358 | 16.079 | 0.032657 |  | 3491 | 16.079 | 66.89 | 14.696 | 0.075358 | 0.032657
3492 | 66.9 | 14.696 | 0.075357 | 16.081 | 0.032661 |  | 3492 | 16.081 | 66.9 | 14.696 | 0.075357 | 0.032661
3493 | 66.91 | 14.696 | 0.075356 | 16.084 | 0.032666 |  | 3493 | 16.084 | 66.91 | 14.696 | 0.075356 | 0.032666
3494 | 66.92 | 14.696 | 0.075354 | 16.086 | 0.03267 |  | 3494 | 16.086 | 66.92 | 14.696 | 0.075354 | 0.03267
3495 | 66.93 | 14.696 | 0.075353 | 16.089 | 0.032675 |  | 3495 | 16.089 | 66.93 | 14.696 | 0.075353 | 0.032675
3496 | 66.94 | 14.696 | 0.075351 | 16.091 | 0.03268 |  | 3496 | 16.091 | 66.94 | 14.696 | 0.075351 | 0.03268
3497 | 66.95 | 14.696 | 0.07535 | 16.093 | 0.032684 |  | 3497 | 16.093 | 66.95 | 14.696 | 0.07535 | 0.032684
3498 | 66.96 | 14.696 | 0.075348 | 16.096 | 0.032689 |  | 3498 | 16.096 | 66.96 | 14.696 | 0.075348 | 0.032689
3499 | 66.97 | 14.696 | 0.075347 | 16.098 | 0.032693 |  | 3499 | 16.098 | 66.97 | 14.696 | 0.075347 | 0.032693
3500 | 66.98 | 14.696 | 0.075345 | 16.101 | 0.032698 |  | 3500 | 16.101 | 66.98 | 14.696 | 0.075345 | 0.032698
3501 | 66.99 | 14.696 | 0.075344 | 16.103 | 0.032702 |  | 3501 | 16.103 | 66.99 | 14.696 | 0.075344 | 0.032702
3502 | 67 | 14.696 | 0.075343 | 16.105 | 0.032707 |  | 3502 | 16.105 | 67 | 14.696 | 0.075343 | 0.032707
3503 | 67.01 | 14.696 | 0.075341 | 16.108 | 0.032711 |  | 3503 | 16.108 | 67.01 | 14.696 | 0.075341 | 0.032711
3504 | 67.02 | 14.696 | 0.07534 | 16.11 | 0.032716 |  | 3504 | 16.11 | 67.02 | 14.696 | 0.07534 | 0.032716
3505 | 67.03 | 14.696 | 0.075338 | 16.113 | 0.032721 |  | 3505 | 16.113 | 67.03 | 14.696 | 0.075338 | 0.032721
3506 | 67.04 | 14.696 | 0.075337 | 16.115 | 0.032725 |  | 3506 | 16.115 | 67.04 | 14.696 | 0.075337 | 0.032725
3507 | 67.05 | 14.696 | 0.075335 | 16.117 | 0.03273 |  | 3507 | 16.117 | 67.05 | 14.696 | 0.075335 | 0.03273
3508 | 67.06 | 14.696 | 0.075334 | 16.12 | 0.032734 |  | 3508 | 16.12 | 67.06 | 14.696 | 0.075334 | 0.032734
3509 | 67.07 | 14.696 | 0.075333 | 16.122 | 0.032739 |  | 3509 | 16.122 | 67.07 | 14.696 | 0.075333 | 0.032739
3510 | 67.08 | 14.696 | 0.075331 | 16.125 | 0.032743 |  | 3510 | 16.125 | 67.08 | 14.696 | 0.075331 | 0.032743
3511 | 67.09 | 14.696 | 0.07533 | 16.127 | 0.032748 |  | 3511 | 16.127 | 67.09 | 14.696 | 0.07533 | 0.032748
3512 | 67.1 | 14.696 | 0.075328 | 16.129 | 0.032753 |  | 3512 | 16.129 | 67.1 | 14.696 | 0.075328 | 0.032753
3513 | 67.11 | 14.696 | 0.075327 | 16.132 | 0.032757 |  | 3513 | 16.132 | 67.11 | 14.696 | 0.075327 | 0.032757
3514 | 67.12 | 14.696 | 0.075325 | 16.134 | 0.032762 |  | 3514 | 16.134 | 67.12 | 14.696 | 0.075325 | 0.032762
3515 | 67.13 | 14.696 | 0.075324 | 16.137 | 0.032766 |  | 3515 | 16.137 | 67.13 | 14.696 | 0.075324 | 0.032766
3516 | 67.14 | 14.696 | 0.075323 | 16.139 | 0.032771 |  | 3516 | 16.139 | 67.14 | 14.696 | 0.075323 | 0.032771
3517 | 67.15 | 14.696 | 0.075321 | 16.141 | 0.032775 |  | 3517 | 16.141 | 67.15 | 14.696 | 0.075321 | 0.032775
3518 | 67.16 | 14.696 | 0.07532 | 16.144 | 0.03278 |  | 3518 | 16.144 | 67.16 | 14.696 | 0.07532 | 0.03278
3519 | 67.17 | 14.696 | 0.075318 | 16.146 | 0.032785 |  | 3519 | 16.146 | 67.17 | 14.696 | 0.075318 | 0.032785
3520 | 67.18 | 14.696 | 0.075317 | 16.149 | 0.032789 |  | 3520 | 16.149 | 67.18 | 14.696 | 0.075317 | 0.032789
3521 | 67.19 | 14.696 | 0.075315 | 16.151 | 0.032794 |  | 3521 | 16.151 | 67.19 | 14.696 | 0.075315 | 0.032794
3522 | 67.2 | 14.696 | 0.075314 | 16.153 | 0.032798 |  | 3522 | 16.153 | 67.2 | 14.696 | 0.075314 | 0.032798
3523 | 67.21 | 14.696 | 0.075313 | 16.156 | 0.032803 |  | 3523 | 16.156 | 67.21 | 14.696 | 0.075313 | 0.032803
3524 | 67.22 | 14.696 | 0.075311 | 16.158 | 0.032807 |  | 3524 | 16.158 | 67.22 | 14.696 | 0.075311 | 0.032807
3525 | 67.23 | 14.696 | 0.07531 | 16.161 | 0.032812 |  | 3525 | 16.161 | 67.23 | 14.696 | 0.07531 | 0.032812
3526 | 67.24 | 14.696 | 0.075308 | 16.163 | 0.032816 |  | 3526 | 16.163 | 67.24 | 14.696 | 0.075308 | 0.032816
3527 | 67.25 | 14.696 | 0.075307 | 16.165 | 0.032821 |  | 3527 | 16.165 | 67.25 | 14.696 | 0.075307 | 0.032821
3528 | 67.26 | 14.696 | 0.075305 | 16.168 | 0.032826 |  | 3528 | 16.168 | 67.26 | 14.696 | 0.075305 | 0.032826
3529 | 67.27 | 14.696 | 0.075304 | 16.17 | 0.03283 |  | 3529 | 16.17 | 67.27 | 14.696 | 0.075304 | 0.03283
3530 | 67.28 | 14.696 | 0.075302 | 16.173 | 0.032835 |  | 3530 | 16.173 | 67.28 | 14.696 | 0.075302 | 0.032835
3531 | 67.29 | 14.696 | 0.075301 | 16.175 | 0.032839 |  | 3531 | 16.175 | 67.29 | 14.696 | 0.075301 | 0.032839
3532 | 67.3 | 14.696 | 0.0753 | 16.177 | 0.032844 |  | 3532 | 16.177 | 67.3 | 14.696 | 0.0753 | 0.032844
3533 | 67.31 | 14.696 | 0.075298 | 16.18 | 0.032848 |  | 3533 | 16.18 | 67.31 | 14.696 | 0.075298 | 0.032848
3534 | 67.32 | 14.696 | 0.075297 | 16.182 | 0.032853 |  | 3534 | 16.182 | 67.32 | 14.696 | 0.075297 | 0.032853
3535 | 67.33 | 14.696 | 0.075295 | 16.185 | 0.032858 |  | 3535 | 16.185 | 67.33 | 14.696 | 0.075295 | 0.032858
3536 | 67.34 | 14.696 | 0.075294 | 16.187 | 0.032862 |  | 3536 | 16.187 | 67.34 | 14.696 | 0.075294 | 0.032862
3537 | 67.35 | 14.696 | 0.075292 | 16.19 | 0.032867 |  | 3537 | 16.19 | 67.35 | 14.696 | 0.075292 | 0.032867
3538 | 67.36 | 14.696 | 0.075291 | 16.192 | 0.032871 |  | 3538 | 16.192 | 67.36 | 14.696 | 0.075291 | 0.032871
3539 | 67.37 | 14.696 | 0.07529 | 16.194 | 0.032876 |  | 3539 | 16.194 | 67.37 | 14.696 | 0.07529 | 0.032876
3540 | 67.38 | 14.696 | 0.075288 | 16.197 | 0.03288 |  | 3540 | 16.197 | 67.38 | 14.696 | 0.075288 | 0.03288
3541 | 67.39 | 14.696 | 0.075287 | 16.199 | 0.032885 |  | 3541 | 16.199 | 67.39 | 14.696 | 0.075287 | 0.032885
3542 | 67.4 | 14.696 | 0.075285 | 16.202 | 0.032889 |  | 3542 | 16.202 | 67.4 | 14.696 | 0.075285 | 0.032889
3543 | 67.41 | 14.696 | 0.075284 | 16.204 | 0.032894 |  | 3543 | 16.204 | 67.41 | 14.696 | 0.075284 | 0.032894
3544 | 67.42 | 14.696 | 0.075282 | 16.206 | 0.032899 |  | 3544 | 16.206 | 67.42 | 14.696 | 0.075282 | 0.032899
3545 | 67.43 | 14.696 | 0.075281 | 16.209 | 0.032903 |  | 3545 | 16.209 | 67.43 | 14.696 | 0.075281 | 0.032903
3546 | 67.44 | 14.696 | 0.07528 | 16.211 | 0.032908 |  | 3546 | 16.211 | 67.44 | 14.696 | 0.07528 | 0.032908
3547 | 67.45 | 14.696 | 0.075278 | 16.214 | 0.032912 |  | 3547 | 16.214 | 67.45 | 14.696 | 0.075278 | 0.032912
3548 | 67.46 | 14.696 | 0.075277 | 16.216 | 0.032917 |  | 3548 | 16.216 | 67.46 | 14.696 | 0.075277 | 0.032917
3549 | 67.47 | 14.696 | 0.075275 | 16.218 | 0.032921 |  | 3549 | 16.218 | 67.47 | 14.696 | 0.075275 | 0.032921
3550 | 67.48 | 14.696 | 0.075274 | 16.221 | 0.032926 |  | 3550 | 16.221 | 67.48 | 14.696 | 0.075274 | 0.032926
3551 | 67.49 | 14.696 | 0.075272 | 16.223 | 0.032931 |  | 3551 | 16.223 | 67.49 | 14.696 | 0.075272 | 0.032931
3552 | 67.5 | 14.696 | 0.075271 | 16.226 | 0.032935 |  | 3552 | 16.226 | 67.5 | 14.696 | 0.075271 | 0.032935
3553 | 67.51 | 14.696 | 0.07527 | 16.228 | 0.03294 |  | 3553 | 16.228 | 67.51 | 14.696 | 0.07527 | 0.03294
3554 | 67.52 | 14.696 | 0.075268 | 16.23 | 0.032944 |  | 3554 | 16.23 | 67.52 | 14.696 | 0.075268 | 0.032944
3555 | 67.53 | 14.696 | 0.075267 | 16.233 | 0.032949 |  | 3555 | 16.233 | 67.53 | 14.696 | 0.075267 | 0.032949
3556 | 67.54 | 14.696 | 0.075265 | 16.235 | 0.032953 |  | 3556 | 16.235 | 67.54 | 14.696 | 0.075265 | 0.032953
3557 | 67.55 | 14.696 | 0.075264 | 16.238 | 0.032958 |  | 3557 | 16.238 | 67.55 | 14.696 | 0.075264 | 0.032958
3558 | 67.56 | 14.696 | 0.075262 | 16.24 | 0.032962 |  | 3558 | 16.24 | 67.56 | 14.696 | 0.075262 | 0.032962
3559 | 67.57 | 14.696 | 0.075261 | 16.242 | 0.032967 |  | 3559 | 16.242 | 67.57 | 14.696 | 0.075261 | 0.032967
3560 | 67.58 | 14.696 | 0.07526 | 16.245 | 0.032972 |  | 3560 | 16.245 | 67.58 | 14.696 | 0.07526 | 0.032972
3561 | 67.59 | 14.696 | 0.075258 | 16.247 | 0.032976 |  | 3561 | 16.247 | 67.59 | 14.696 | 0.075258 | 0.032976
3562 | 67.6 | 14.696 | 0.075257 | 16.25 | 0.032981 |  | 3562 | 16.25 | 67.6 | 14.696 | 0.075257 | 0.032981
3563 | 67.61 | 14.696 | 0.075255 | 16.252 | 0.032985 |  | 3563 | 16.252 | 67.61 | 14.696 | 0.075255 | 0.032985
3564 | 67.62 | 14.696 | 0.075254 | 16.254 | 0.03299 |  | 3564 | 16.254 | 67.62 | 14.696 | 0.075254 | 0.03299
3565 | 67.63 | 14.696 | 0.075252 | 16.257 | 0.032994 |  | 3565 | 16.257 | 67.63 | 14.696 | 0.075252 | 0.032994
3566 | 67.64 | 14.696 | 0.075251 | 16.259 | 0.032999 |  | 3566 | 16.259 | 67.64 | 14.696 | 0.075251 | 0.032999
3567 | 67.65 | 14.696 | 0.075249 | 16.262 | 0.033004 |  | 3567 | 16.262 | 67.65 | 14.696 | 0.075249 | 0.033004
3568 | 67.66 | 14.696 | 0.075248 | 16.264 | 0.033008 |  | 3568 | 16.264 | 67.66 | 14.696 | 0.075248 | 0.033008
3569 | 67.67 | 14.696 | 0.075247 | 16.266 | 0.033013 |  | 3569 | 16.266 | 67.67 | 14.696 | 0.075247 | 0.033013
3570 | 67.68 | 14.696 | 0.075245 | 16.269 | 0.033017 |  | 3570 | 16.269 | 67.68 | 14.696 | 0.075245 | 0.033017
3571 | 67.69 | 14.696 | 0.075244 | 16.271 | 0.033022 |  | 3571 | 16.271 | 67.69 | 14.696 | 0.075244 | 0.033022
3572 | 67.7 | 14.696 | 0.075242 | 16.274 | 0.033026 |  | 3572 | 16.274 | 67.7 | 14.696 | 0.075242 | 0.033026
3573 | 67.71 | 14.696 | 0.075241 | 16.276 | 0.033031 |  | 3573 | 16.276 | 67.71 | 14.696 | 0.075241 | 0.033031
3574 | 67.72 | 14.696 | 0.075239 | 16.278 | 0.033035 |  | 3574 | 16.278 | 67.72 | 14.696 | 0.075239 | 0.033035
3575 | 67.73 | 14.696 | 0.075238 | 16.281 | 0.03304 |  | 3575 | 16.281 | 67.73 | 14.696 | 0.075238 | 0.03304
3576 | 67.74 | 14.696 | 0.075237 | 16.283 | 0.033045 |  | 3576 | 16.283 | 67.74 | 14.696 | 0.075237 | 0.033045
3577 | 67.75 | 14.696 | 0.075235 | 16.286 | 0.033049 |  | 3577 | 16.286 | 67.75 | 14.696 | 0.075235 | 0.033049
3578 | 67.76 | 14.696 | 0.075234 | 16.288 | 0.033054 |  | 3578 | 16.288 | 67.76 | 14.696 | 0.075234 | 0.033054
3579 | 67.77 | 14.696 | 0.075232 | 16.291 | 0.033058 |  | 3579 | 16.291 | 67.77 | 14.696 | 0.075232 | 0.033058
3580 | 67.78 | 14.696 | 0.075231 | 16.293 | 0.033063 |  | 3580 | 16.293 | 67.78 | 14.696 | 0.075231 | 0.033063
3581 | 67.79 | 14.696 | 0.075229 | 16.295 | 0.033067 |  | 3581 | 16.295 | 67.79 | 14.696 | 0.075229 | 0.033067
3582 | 67.8 | 14.696 | 0.075228 | 16.298 | 0.033072 |  | 3582 | 16.298 | 67.8 | 14.696 | 0.075228 | 0.033072
3583 | 67.81 | 14.696 | 0.075227 | 16.3 | 0.033076 |  | 3583 | 16.3 | 67.81 | 14.696 | 0.075227 | 0.033076
3584 | 67.82 | 14.696 | 0.075225 | 16.303 | 0.033081 |  | 3584 | 16.303 | 67.82 | 14.696 | 0.075225 | 0.033081
3585 | 67.83 | 14.696 | 0.075224 | 16.305 | 0.033086 |  | 3585 | 16.305 | 67.83 | 14.696 | 0.075224 | 0.033086
3586 | 67.84 | 14.696 | 0.075222 | 16.307 | 0.03309 |  | 3586 | 16.307 | 67.84 | 14.696 | 0.075222 | 0.03309
3587 | 67.85 | 14.696 | 0.075221 | 16.31 | 0.033095 |  | 3587 | 16.31 | 67.85 | 14.696 | 0.075221 | 0.033095
3588 | 67.86 | 14.696 | 0.075219 | 16.312 | 0.033099 |  | 3588 | 16.312 | 67.86 | 14.696 | 0.075219 | 0.033099
3589 | 67.87 | 14.696 | 0.075218 | 16.315 | 0.033104 |  | 3589 | 16.315 | 67.87 | 14.696 | 0.075218 | 0.033104
3590 | 67.88 | 14.696 | 0.075217 | 16.317 | 0.033108 |  | 3590 | 16.317 | 67.88 | 14.696 | 0.075217 | 0.033108
3591 | 67.89 | 14.696 | 0.075215 | 16.319 | 0.033113 |  | 3591 | 16.319 | 67.89 | 14.696 | 0.075215 | 0.033113
3592 | 67.9 | 14.696 | 0.075214 | 16.322 | 0.033117 |  | 3592 | 16.322 | 67.9 | 14.696 | 0.075214 | 0.033117
3593 | 67.91 | 14.696 | 0.075212 | 16.324 | 0.033122 |  | 3593 | 16.324 | 67.91 | 14.696 | 0.075212 | 0.033122
3594 | 67.92 | 14.696 | 0.075211 | 16.327 | 0.033127 |  | 3594 | 16.327 | 67.92 | 14.696 | 0.075211 | 0.033127
3595 | 67.93 | 14.696 | 0.075209 | 16.329 | 0.033131 |  | 3595 | 16.329 | 67.93 | 14.696 | 0.075209 | 0.033131
3596 | 67.94 | 14.696 | 0.075208 | 16.331 | 0.033136 |  | 3596 | 16.331 | 67.94 | 14.696 | 0.075208 | 0.033136
3597 | 67.95 | 14.696 | 0.075207 | 16.334 | 0.03314 |  | 3597 | 16.334 | 67.95 | 14.696 | 0.075207 | 0.03314
3598 | 67.96 | 14.696 | 0.075205 | 16.336 | 0.033145 |  | 3598 | 16.336 | 67.96 | 14.696 | 0.075205 | 0.033145
3599 | 67.97 | 14.696 | 0.075204 | 16.339 | 0.033149 |  | 3599 | 16.339 | 67.97 | 14.696 | 0.075204 | 0.033149
3600 | 67.98 | 14.696 | 0.075202 | 16.341 | 0.033154 |  | 3600 | 16.341 | 67.98 | 14.696 | 0.075202 | 0.033154
3601 | 67.99 | 14.696 | 0.075201 | 16.343 | 0.033159 |  | 3601 | 16.343 | 67.99 | 14.696 | 0.075201 | 0.033159
3602 | 68 | 14.696 | 0.075199 | 16.346 | 0.033163 |  | 3602 | 16.346 | 68 | 14.696 | 0.075199 | 0.033163
3603 | 68.01 | 14.696 | 0.075198 | 16.348 | 0.033168 |  | 3603 | 16.348 | 68.01 | 14.696 | 0.075198 | 0.033168
3604 | 68.02 | 14.696 | 0.075197 | 16.351 | 0.033172 |  | 3604 | 16.351 | 68.02 | 14.696 | 0.075197 | 0.033172
3605 | 68.03 | 14.696 | 0.075195 | 16.353 | 0.033177 |  | 3605 | 16.353 | 68.03 | 14.696 | 0.075195 | 0.033177
3606 | 68.04 | 14.696 | 0.075194 | 16.355 | 0.033181 |  | 3606 | 16.355 | 68.04 | 14.696 | 0.075194 | 0.033181
3607 | 68.05 | 14.696 | 0.075192 | 16.358 | 0.033186 |  | 3607 | 16.358 | 68.05 | 14.696 | 0.075192 | 0.033186
3608 | 68.06 | 14.696 | 0.075191 | 16.36 | 0.03319 |  | 3608 | 16.36 | 68.06 | 14.696 | 0.075191 | 0.03319
3609 | 68.07 | 14.696 | 0.075189 | 16.363 | 0.033195 |  | 3609 | 16.363 | 68.07 | 14.696 | 0.075189 | 0.033195
3610 | 68.08 | 14.696 | 0.075188 | 16.365 | 0.0332 |  | 3610 | 16.365 | 68.08 | 14.696 | 0.075188 | 0.0332
3611 | 68.09 | 14.696 | 0.075187 | 16.367 | 0.033204 |  | 3611 | 16.367 | 68.09 | 14.696 | 0.075187 | 0.033204
3612 | 68.1 | 14.696 | 0.075185 | 16.37 | 0.033209 |  | 3612 | 16.37 | 68.1 | 14.696 | 0.075185 | 0.033209
3613 | 68.11 | 14.696 | 0.075184 | 16.372 | 0.033213 |  | 3613 | 16.372 | 68.11 | 14.696 | 0.075184 | 0.033213
3614 | 68.12 | 14.696 | 0.075182 | 16.375 | 0.033218 |  | 3614 | 16.375 | 68.12 | 14.696 | 0.075182 | 0.033218
3615 | 68.13 | 14.696 | 0.075181 | 16.377 | 0.033222 |  | 3615 | 16.377 | 68.13 | 14.696 | 0.075181 | 0.033222
3616 | 68.14 | 14.696 | 0.075179 | 16.379 | 0.033227 |  | 3616 | 16.379 | 68.14 | 14.696 | 0.075179 | 0.033227
3617 | 68.15 | 14.696 | 0.075178 | 16.382 | 0.033231 |  | 3617 | 16.382 | 68.15 | 14.696 | 0.075178 | 0.033231
3618 | 68.16 | 14.696 | 0.075177 | 16.384 | 0.033236 |  | 3618 | 16.384 | 68.16 | 14.696 | 0.075177 | 0.033236
3619 | 68.17 | 14.696 | 0.075175 | 16.387 | 0.033241 |  | 3619 | 16.387 | 68.17 | 14.696 | 0.075175 | 0.033241
3620 | 68.18 | 14.696 | 0.075174 | 16.389 | 0.033245 |  | 3620 | 16.389 | 68.18 | 14.696 | 0.075174 | 0.033245
3621 | 68.19 | 14.696 | 0.075172 | 16.391 | 0.03325 |  | 3621 | 16.391 | 68.19 | 14.696 | 0.075172 | 0.03325
3622 | 68.2 | 14.696 | 0.075171 | 16.394 | 0.033254 |  | 3622 | 16.394 | 68.2 | 14.696 | 0.075171 | 0.033254
3623 | 68.21 | 14.696 | 0.075169 | 16.396 | 0.033259 |  | 3623 | 16.396 | 68.21 | 14.696 | 0.075169 | 0.033259
3624 | 68.22 | 14.696 | 0.075168 | 16.399 | 0.033263 |  | 3624 | 16.399 | 68.22 | 14.696 | 0.075168 | 0.033263
3625 | 68.23 | 14.696 | 0.075167 | 16.401 | 0.033268 |  | 3625 | 16.401 | 68.23 | 14.696 | 0.075167 | 0.033268
3626 | 68.24 | 14.696 | 0.075165 | 16.404 | 0.033272 |  | 3626 | 16.404 | 68.24 | 14.696 | 0.075165 | 0.033272
3627 | 68.25 | 14.696 | 0.075164 | 16.406 | 0.033277 |  | 3627 | 16.406 | 68.25 | 14.696 | 0.075164 | 0.033277
3628 | 68.26 | 14.696 | 0.075162 | 16.408 | 0.033282 |  | 3628 | 16.408 | 68.26 | 14.696 | 0.075162 | 0.033282
3629 | 68.27 | 14.696 | 0.075161 | 16.411 | 0.033286 |  | 3629 | 16.411 | 68.27 | 14.696 | 0.075161 | 0.033286
3630 | 68.28 | 14.696 | 0.075159 | 16.413 | 0.033291 |  | 3630 | 16.413 | 68.28 | 14.696 | 0.075159 | 0.033291
3631 | 68.29 | 14.696 | 0.075158 | 16.416 | 0.033295 |  | 3631 | 16.416 | 68.29 | 14.696 | 0.075158 | 0.033295
3632 | 68.3 | 14.696 | 0.075157 | 16.418 | 0.0333 |  | 3632 | 16.418 | 68.3 | 14.696 | 0.075157 | 0.0333
3633 | 68.31 | 14.696 | 0.075155 | 16.42 | 0.033304 |  | 3633 | 16.42 | 68.31 | 14.696 | 0.075155 | 0.033304
3634 | 68.32 | 14.696 | 0.075154 | 16.423 | 0.033309 |  | 3634 | 16.423 | 68.32 | 14.696 | 0.075154 | 0.033309
3635 | 68.33 | 14.696 | 0.075152 | 16.425 | 0.033313 |  | 3635 | 16.425 | 68.33 | 14.696 | 0.075152 | 0.033313
3636 | 68.34 | 14.696 | 0.075151 | 16.428 | 0.033318 |  | 3636 | 16.428 | 68.34 | 14.696 | 0.075151 | 0.033318
3637 | 68.35 | 14.696 | 0.075149 | 16.43 | 0.033323 |  | 3637 | 16.43 | 68.35 | 14.696 | 0.075149 | 0.033323
3638 | 68.36 | 14.696 | 0.075148 | 16.432 | 0.033327 |  | 3638 | 16.432 | 68.36 | 14.696 | 0.075148 | 0.033327
3639 | 68.37 | 14.696 | 0.075147 | 16.435 | 0.033332 |  | 3639 | 16.435 | 68.37 | 14.696 | 0.075147 | 0.033332
3640 | 68.38 | 14.696 | 0.075145 | 16.437 | 0.033336 |  | 3640 | 16.437 | 68.38 | 14.696 | 0.075145 | 0.033336
3641 | 68.39 | 14.696 | 0.075144 | 16.44 | 0.033341 |  | 3641 | 16.44 | 68.39 | 14.696 | 0.075144 | 0.033341
3642 | 68.4 | 14.696 | 0.075142 | 16.442 | 0.033345 |  | 3642 | 16.442 | 68.4 | 14.696 | 0.075142 | 0.033345
3643 | 68.41 | 14.696 | 0.075141 | 16.444 | 0.03335 |  | 3643 | 16.444 | 68.41 | 14.696 | 0.075141 | 0.03335
3644 | 68.42 | 14.696 | 0.075139 | 16.447 | 0.033354 |  | 3644 | 16.447 | 68.42 | 14.696 | 0.075139 | 0.033354
3645 | 68.43 | 14.696 | 0.075138 | 16.449 | 0.033359 |  | 3645 | 16.449 | 68.43 | 14.696 | 0.075138 | 0.033359
3646 | 68.44 | 14.696 | 0.075137 | 16.452 | 0.033364 |  | 3646 | 16.452 | 68.44 | 14.696 | 0.075137 | 0.033364
3647 | 68.45 | 14.696 | 0.075135 | 16.454 | 0.033368 |  | 3647 | 16.454 | 68.45 | 14.696 | 0.075135 | 0.033368
3648 | 68.46 | 14.696 | 0.075134 | 16.456 | 0.033373 |  | 3648 | 16.456 | 68.46 | 14.696 | 0.075134 | 0.033373
3649 | 68.47 | 14.696 | 0.075132 | 16.459 | 0.033377 |  | 3649 | 16.459 | 68.47 | 14.696 | 0.075132 | 0.033377
3650 | 68.48 | 14.696 | 0.075131 | 16.461 | 0.033382 |  | 3650 | 16.461 | 68.48 | 14.696 | 0.075131 | 0.033382
3651 | 68.49 | 14.696 | 0.075129 | 16.464 | 0.033386 |  | 3651 | 16.464 | 68.49 | 14.696 | 0.075129 | 0.033386
3652 | 68.5 | 14.696 | 0.075128 | 16.466 | 0.033391 |  | 3652 | 16.466 | 68.5 | 14.696 | 0.075128 | 0.033391
3653 | 68.51 | 14.696 | 0.075127 | 16.468 | 0.033395 |  | 3653 | 16.468 | 68.51 | 14.696 | 0.075127 | 0.033395
3654 | 68.52 | 14.696 | 0.075125 | 16.471 | 0.0334 |  | 3654 | 16.471 | 68.52 | 14.696 | 0.075125 | 0.0334
3655 | 68.53 | 14.696 | 0.075124 | 16.473 | 0.033404 |  | 3655 | 16.473 | 68.53 | 14.696 | 0.075124 | 0.033404
3656 | 68.54 | 14.696 | 0.075122 | 16.476 | 0.033409 |  | 3656 | 16.476 | 68.54 | 14.696 | 0.075122 | 0.033409
3657 | 68.55 | 14.696 | 0.075121 | 16.478 | 0.033414 |  | 3657 | 16.478 | 68.55 | 14.696 | 0.075121 | 0.033414
3658 | 68.56 | 14.696 | 0.075119 | 16.48 | 0.033418 |  | 3658 | 16.48 | 68.56 | 14.696 | 0.075119 | 0.033418
3659 | 68.57 | 14.696 | 0.075118 | 16.483 | 0.033423 |  | 3659 | 16.483 | 68.57 | 14.696 | 0.075118 | 0.033423
3660 | 68.58 | 14.696 | 0.075117 | 16.485 | 0.033427 |  | 3660 | 16.485 | 68.58 | 14.696 | 0.075117 | 0.033427
3661 | 68.59 | 14.696 | 0.075115 | 16.488 | 0.033432 |  | 3661 | 16.488 | 68.59 | 14.696 | 0.075115 | 0.033432
3662 | 68.6 | 14.696 | 0.075114 | 16.49 | 0.033436 |  | 3662 | 16.49 | 68.6 | 14.696 | 0.075114 | 0.033436
3663 | 68.61 | 14.696 | 0.075112 | 16.492 | 0.033441 |  | 3663 | 16.492 | 68.61 | 14.696 | 0.075112 | 0.033441
3664 | 68.62 | 14.696 | 0.075111 | 16.495 | 0.033445 |  | 3664 | 16.495 | 68.62 | 14.696 | 0.075111 | 0.033445
3665 | 68.63 | 14.696 | 0.07511 | 16.497 | 0.03345 |  | 3665 | 16.497 | 68.63 | 14.696 | 0.07511 | 0.03345
3666 | 68.64 | 14.696 | 0.075108 | 16.5 | 0.033455 |  | 3666 | 16.5 | 68.64 | 14.696 | 0.075108 | 0.033455
3667 | 68.65 | 14.696 | 0.075107 | 16.502 | 0.033459 |  | 3667 | 16.502 | 68.65 | 14.696 | 0.075107 | 0.033459
3668 | 68.66 | 14.696 | 0.075105 | 16.505 | 0.033464 |  | 3668 | 16.505 | 68.66 | 14.696 | 0.075105 | 0.033464
3669 | 68.67 | 14.696 | 0.075104 | 16.507 | 0.033468 |  | 3669 | 16.507 | 68.67 | 14.696 | 0.075104 | 0.033468
3670 | 68.68 | 14.696 | 0.075102 | 16.509 | 0.033473 |  | 3670 | 16.509 | 68.68 | 14.696 | 0.075102 | 0.033473
3671 | 68.69 | 14.696 | 0.075101 | 16.512 | 0.033477 |  | 3671 | 16.512 | 68.69 | 14.696 | 0.075101 | 0.033477
3672 | 68.7 | 14.696 | 0.0751 | 16.514 | 0.033482 |  | 3672 | 16.514 | 68.7 | 14.696 | 0.0751 | 0.033482
3673 | 68.71 | 14.696 | 0.075098 | 16.517 | 0.033486 |  | 3673 | 16.517 | 68.71 | 14.696 | 0.075098 | 0.033486
3674 | 68.72 | 14.696 | 0.075097 | 16.519 | 0.033491 |  | 3674 | 16.519 | 68.72 | 14.696 | 0.075097 | 0.033491
3675 | 68.73 | 14.696 | 0.075095 | 16.521 | 0.033496 |  | 3675 | 16.521 | 68.73 | 14.696 | 0.075095 | 0.033496
3676 | 68.74 | 14.696 | 0.075094 | 16.524 | 0.0335 |  | 3676 | 16.524 | 68.74 | 14.696 | 0.075094 | 0.0335
3677 | 68.75 | 14.696 | 0.075092 | 16.526 | 0.033505 |  | 3677 | 16.526 | 68.75 | 14.696 | 0.075092 | 0.033505
3678 | 68.76 | 14.696 | 0.075091 | 16.529 | 0.033509 |  | 3678 | 16.529 | 68.76 | 14.696 | 0.075091 | 0.033509
3679 | 68.77 | 14.696 | 0.07509 | 16.531 | 0.033514 |  | 3679 | 16.531 | 68.77 | 14.696 | 0.07509 | 0.033514
3680 | 68.78 | 14.696 | 0.075088 | 16.533 | 0.033518 |  | 3680 | 16.533 | 68.78 | 14.696 | 0.075088 | 0.033518
3681 | 68.79 | 14.696 | 0.075087 | 16.536 | 0.033523 |  | 3681 | 16.536 | 68.79 | 14.696 | 0.075087 | 0.033523
3682 | 68.8 | 14.696 | 0.075085 | 16.538 | 0.033527 |  | 3682 | 16.538 | 68.8 | 14.696 | 0.075085 | 0.033527
3683 | 68.81 | 14.696 | 0.075084 | 16.541 | 0.033532 |  | 3683 | 16.541 | 68.81 | 14.696 | 0.075084 | 0.033532
3684 | 68.82 | 14.696 | 0.075082 | 16.543 | 0.033536 |  | 3684 | 16.543 | 68.82 | 14.696 | 0.075082 | 0.033536
3685 | 68.83 | 14.696 | 0.075081 | 16.545 | 0.033541 |  | 3685 | 16.545 | 68.83 | 14.696 | 0.075081 | 0.033541
3686 | 68.84 | 14.696 | 0.07508 | 16.548 | 0.033546 |  | 3686 | 16.548 | 68.84 | 14.696 | 0.07508 | 0.033546
3687 | 68.85 | 14.696 | 0.075078 | 16.55 | 0.03355 |  | 3687 | 16.55 | 68.85 | 14.696 | 0.075078 | 0.03355
3688 | 68.86 | 14.696 | 0.075077 | 16.553 | 0.033555 |  | 3688 | 16.553 | 68.86 | 14.696 | 0.075077 | 0.033555
3689 | 68.87 | 14.696 | 0.075075 | 16.555 | 0.033559 |  | 3689 | 16.555 | 68.87 | 14.696 | 0.075075 | 0.033559
3690 | 68.88 | 14.696 | 0.075074 | 16.557 | 0.033564 |  | 3690 | 16.557 | 68.88 | 14.696 | 0.075074 | 0.033564
3691 | 68.89 | 14.696 | 0.075072 | 16.56 | 0.033568 |  | 3691 | 16.56 | 68.89 | 14.696 | 0.075072 | 0.033568
3692 | 68.9 | 14.696 | 0.075071 | 16.562 | 0.033573 |  | 3692 | 16.562 | 68.9 | 14.696 | 0.075071 | 0.033573
3693 | 68.91 | 14.696 | 0.07507 | 16.565 | 0.033577 |  | 3693 | 16.565 | 68.91 | 14.696 | 0.07507 | 0.033577
3694 | 68.92 | 14.696 | 0.075068 | 16.567 | 0.033582 |  | 3694 | 16.567 | 68.92 | 14.696 | 0.075068 | 0.033582
3695 | 68.93 | 14.696 | 0.075067 | 16.569 | 0.033587 |  | 3695 | 16.569 | 68.93 | 14.696 | 0.075067 | 0.033587
3696 | 68.94 | 14.696 | 0.075065 | 16.572 | 0.033591 |  | 3696 | 16.572 | 68.94 | 14.696 | 0.075065 | 0.033591
3697 | 68.95 | 14.696 | 0.075064 | 16.574 | 0.033596 |  | 3697 | 16.574 | 68.95 | 14.696 | 0.075064 | 0.033596
3698 | 68.96 | 14.696 | 0.075062 | 16.577 | 0.0336 |  | 3698 | 16.577 | 68.96 | 14.696 | 0.075062 | 0.0336
3699 | 68.97 | 14.696 | 0.075061 | 16.579 | 0.033605 |  | 3699 | 16.579 | 68.97 | 14.696 | 0.075061 | 0.033605
3700 | 68.98 | 14.696 | 0.07506 | 16.581 | 0.033609 |  | 3700 | 16.581 | 68.98 | 14.696 | 0.07506 | 0.033609
3701 | 68.99 | 14.696 | 0.075058 | 16.584 | 0.033614 |  | 3701 | 16.584 | 68.99 | 14.696 | 0.075058 | 0.033614
3702 | 69 | 14.696 | 0.075057 | 16.586 | 0.033618 |  | 3702 | 16.586 | 69 | 14.696 | 0.075057 | 0.033618
3703 | 69.01 | 14.696 | 0.075055 | 16.589 | 0.033623 |  | 3703 | 16.589 | 69.01 | 14.696 | 0.075055 | 0.033623
3704 | 69.02 | 14.696 | 0.075054 | 16.591 | 0.033627 |  | 3704 | 16.591 | 69.02 | 14.696 | 0.075054 | 0.033627
3705 | 69.03 | 14.696 | 0.075053 | 16.594 | 0.033632 |  | 3705 | 16.594 | 69.03 | 14.696 | 0.075053 | 0.033632
3706 | 69.04 | 14.696 | 0.075051 | 16.596 | 0.033637 |  | 3706 | 16.596 | 69.04 | 14.696 | 0.075051 | 0.033637
3707 | 69.05 | 14.696 | 0.07505 | 16.598 | 0.033641 |  | 3707 | 16.598 | 69.05 | 14.696 | 0.07505 | 0.033641
3708 | 69.06 | 14.696 | 0.075048 | 16.601 | 0.033646 |  | 3708 | 16.601 | 69.06 | 14.696 | 0.075048 | 0.033646
3709 | 69.07 | 14.696 | 0.075047 | 16.603 | 0.03365 |  | 3709 | 16.603 | 69.07 | 14.696 | 0.075047 | 0.03365
3710 | 69.08 | 14.696 | 0.075045 | 16.606 | 0.033655 |  | 3710 | 16.606 | 69.08 | 14.696 | 0.075045 | 0.033655
3711 | 69.09 | 14.696 | 0.075044 | 16.608 | 0.033659 |  | 3711 | 16.608 | 69.09 | 14.696 | 0.075044 | 0.033659
3712 | 69.1 | 14.696 | 0.075043 | 16.61 | 0.033664 |  | 3712 | 16.61 | 69.1 | 14.696 | 0.075043 | 0.033664
3713 | 69.11 | 14.696 | 0.075041 | 16.613 | 0.033668 |  | 3713 | 16.613 | 69.11 | 14.696 | 0.075041 | 0.033668
3714 | 69.12 | 14.696 | 0.07504 | 16.615 | 0.033673 |  | 3714 | 16.615 | 69.12 | 14.696 | 0.07504 | 0.033673
3715 | 69.13 | 14.696 | 0.075038 | 16.618 | 0.033678 |  | 3715 | 16.618 | 69.13 | 14.696 | 0.075038 | 0.033678
3716 | 69.14 | 14.696 | 0.075037 | 16.62 | 0.033682 |  | 3716 | 16.62 | 69.14 | 14.696 | 0.075037 | 0.033682
3717 | 69.15 | 14.696 | 0.075035 | 16.622 | 0.033687 |  | 3717 | 16.622 | 69.15 | 14.696 | 0.075035 | 0.033687
3718 | 69.16 | 14.696 | 0.075034 | 16.625 | 0.033691 |  | 3718 | 16.625 | 69.16 | 14.696 | 0.075034 | 0.033691
3719 | 69.17 | 14.696 | 0.075033 | 16.627 | 0.033696 |  | 3719 | 16.627 | 69.17 | 14.696 | 0.075033 | 0.033696
3720 | 69.18 | 14.696 | 0.075031 | 16.63 | 0.0337 |  | 3720 | 16.63 | 69.18 | 14.696 | 0.075031 | 0.0337
3721 | 69.19 | 14.696 | 0.07503 | 16.632 | 0.033705 |  | 3721 | 16.632 | 69.19 | 14.696 | 0.07503 | 0.033705
3722 | 69.2 | 14.696 | 0.075028 | 16.634 | 0.033709 |  | 3722 | 16.634 | 69.2 | 14.696 | 0.075028 | 0.033709
3723 | 69.21 | 14.696 | 0.075027 | 16.637 | 0.033714 |  | 3723 | 16.637 | 69.21 | 14.696 | 0.075027 | 0.033714
3724 | 69.22 | 14.696 | 0.075025 | 16.639 | 0.033718 |  | 3724 | 16.639 | 69.22 | 14.696 | 0.075025 | 0.033718
3725 | 69.23 | 14.696 | 0.075024 | 16.642 | 0.033723 |  | 3725 | 16.642 | 69.23 | 14.696 | 0.075024 | 0.033723
3726 | 69.24 | 14.696 | 0.075023 | 16.644 | 0.033728 |  | 3726 | 16.644 | 69.24 | 14.696 | 0.075023 | 0.033728
3727 | 69.25 | 14.696 | 0.075021 | 16.646 | 0.033732 |  | 3727 | 16.646 | 69.25 | 14.696 | 0.075021 | 0.033732
3728 | 69.26 | 14.696 | 0.07502 | 16.649 | 0.033737 |  | 3728 | 16.649 | 69.26 | 14.696 | 0.07502 | 0.033737
3729 | 69.27 | 14.696 | 0.075018 | 16.651 | 0.033741 |  | 3729 | 16.651 | 69.27 | 14.696 | 0.075018 | 0.033741
3730 | 69.28 | 14.696 | 0.075017 | 16.654 | 0.033746 |  | 3730 | 16.654 | 69.28 | 14.696 | 0.075017 | 0.033746
3731 | 69.29 | 14.696 | 0.075016 | 16.656 | 0.03375 |  | 3731 | 16.656 | 69.29 | 14.696 | 0.075016 | 0.03375
3732 | 69.3 | 14.696 | 0.075014 | 16.658 | 0.033755 |  | 3732 | 16.658 | 69.3 | 14.696 | 0.075014 | 0.033755
3733 | 69.31 | 14.696 | 0.075013 | 16.661 | 0.033759 |  | 3733 | 16.661 | 69.31 | 14.696 | 0.075013 | 0.033759
3734 | 69.32 | 14.696 | 0.075011 | 16.663 | 0.033764 |  | 3734 | 16.663 | 69.32 | 14.696 | 0.075011 | 0.033764
3735 | 69.33 | 14.696 | 0.07501 | 16.666 | 0.033768 |  | 3735 | 16.666 | 69.33 | 14.696 | 0.07501 | 0.033768
3736 | 69.34 | 14.696 | 0.075008 | 16.668 | 0.033773 |  | 3736 | 16.668 | 69.34 | 14.696 | 0.075008 | 0.033773
3737 | 69.35 | 14.696 | 0.075007 | 16.67 | 0.033778 |  | 3737 | 16.67 | 69.35 | 14.696 | 0.075007 | 0.033778
3738 | 69.36 | 14.696 | 0.075006 | 16.673 | 0.033782 |  | 3738 | 16.673 | 69.36 | 14.696 | 0.075006 | 0.033782
3739 | 69.37 | 14.696 | 0.075004 | 16.675 | 0.033787 |  | 3739 | 16.675 | 69.37 | 14.696 | 0.075004 | 0.033787
3740 | 69.38 | 14.696 | 0.075003 | 16.678 | 0.033791 |  | 3740 | 16.678 | 69.38 | 14.696 | 0.075003 | 0.033791
3741 | 69.39 | 14.696 | 0.075001 | 16.68 | 0.033796 |  | 3741 | 16.68 | 69.39 | 14.696 | 0.075001 | 0.033796
3742 | 69.4 | 14.696 | 0.075 | 16.682 | 0.0338 |  | 3742 | 16.682 | 69.4 | 14.696 | 0.075 | 0.0338
3743 | 69.41 | 14.696 | 0.074998 | 16.685 | 0.033805 |  | 3743 | 16.685 | 69.41 | 14.696 | 0.074998 | 0.033805
3744 | 69.42 | 14.696 | 0.074997 | 16.687 | 0.033809 |  | 3744 | 16.687 | 69.42 | 14.696 | 0.074997 | 0.033809
3745 | 69.43 | 14.696 | 0.074996 | 16.69 | 0.033814 |  | 3745 | 16.69 | 69.43 | 14.696 | 0.074996 | 0.033814
3746 | 69.44 | 14.696 | 0.074994 | 16.692 | 0.033818 |  | 3746 | 16.692 | 69.44 | 14.696 | 0.074994 | 0.033818
3747 | 69.45 | 14.696 | 0.074993 | 16.695 | 0.033823 |  | 3747 | 16.695 | 69.45 | 14.696 | 0.074993 | 0.033823
3748 | 69.46 | 14.696 | 0.074991 | 16.697 | 0.033828 |  | 3748 | 16.697 | 69.46 | 14.696 | 0.074991 | 0.033828
3749 | 69.47 | 14.696 | 0.07499 | 16.699 | 0.033832 |  | 3749 | 16.699 | 69.47 | 14.696 | 0.07499 | 0.033832
3750 | 69.48 | 14.696 | 0.074989 | 16.702 | 0.033837 |  | 3750 | 16.702 | 69.48 | 14.696 | 0.074989 | 0.033837
3751 | 69.49 | 14.696 | 0.074987 | 16.704 | 0.033841 |  | 3751 | 16.704 | 69.49 | 14.696 | 0.074987 | 0.033841
3752 | 69.5 | 14.696 | 0.074986 | 16.707 | 0.033846 |  | 3752 | 16.707 | 69.5 | 14.696 | 0.074986 | 0.033846
3753 | 69.51 | 14.696 | 0.074984 | 16.709 | 0.03385 |  | 3753 | 16.709 | 69.51 | 14.696 | 0.074984 | 0.03385
3754 | 69.52 | 14.696 | 0.074983 | 16.711 | 0.033855 |  | 3754 | 16.711 | 69.52 | 14.696 | 0.074983 | 0.033855
3755 | 69.53 | 14.696 | 0.074981 | 16.714 | 0.033859 |  | 3755 | 16.714 | 69.53 | 14.696 | 0.074981 | 0.033859
3756 | 69.54 | 14.696 | 0.07498 | 16.716 | 0.033864 |  | 3756 | 16.716 | 69.54 | 14.696 | 0.07498 | 0.033864
3757 | 69.55 | 14.696 | 0.074979 | 16.719 | 0.033868 |  | 3757 | 16.719 | 69.55 | 14.696 | 0.074979 | 0.033868
3758 | 69.56 | 14.696 | 0.074977 | 16.721 | 0.033873 |  | 3758 | 16.721 | 69.56 | 14.696 | 0.074977 | 0.033873
3759 | 69.57 | 14.696 | 0.074976 | 16.723 | 0.033878 |  | 3759 | 16.723 | 69.57 | 14.696 | 0.074976 | 0.033878
3760 | 69.58 | 14.696 | 0.074974 | 16.726 | 0.033882 |  | 3760 | 16.726 | 69.58 | 14.696 | 0.074974 | 0.033882
3761 | 69.59 | 14.696 | 0.074973 | 16.728 | 0.033887 |  | 3761 | 16.728 | 69.59 | 14.696 | 0.074973 | 0.033887
3762 | 69.6 | 14.696 | 0.074971 | 16.731 | 0.033891 |  | 3762 | 16.731 | 69.6 | 14.696 | 0.074971 | 0.033891
3763 | 69.61 | 14.696 | 0.07497 | 16.733 | 0.033896 |  | 3763 | 16.733 | 69.61 | 14.696 | 0.07497 | 0.033896
3764 | 69.62 | 14.696 | 0.074969 | 16.735 | 0.0339 |  | 3764 | 16.735 | 69.62 | 14.696 | 0.074969 | 0.0339
3765 | 69.63 | 14.696 | 0.074967 | 16.738 | 0.033905 |  | 3765 | 16.738 | 69.63 | 14.696 | 0.074967 | 0.033905
3766 | 69.64 | 14.696 | 0.074966 | 16.74 | 0.033909 |  | 3766 | 16.74 | 69.64 | 14.696 | 0.074966 | 0.033909
3767 | 69.65 | 14.696 | 0.074964 | 16.743 | 0.033914 |  | 3767 | 16.743 | 69.65 | 14.696 | 0.074964 | 0.033914
3768 | 69.66 | 14.696 | 0.074963 | 16.745 | 0.033918 |  | 3768 | 16.745 | 69.66 | 14.696 | 0.074963 | 0.033918
3769 | 69.67 | 14.696 | 0.074962 | 16.747 | 0.033923 |  | 3769 | 16.747 | 69.67 | 14.696 | 0.074962 | 0.033923
3770 | 69.68 | 14.696 | 0.07496 | 16.75 | 0.033927 |  | 3770 | 16.75 | 69.68 | 14.696 | 0.07496 | 0.033927
3771 | 69.69 | 14.696 | 0.074959 | 16.752 | 0.033932 |  | 3771 | 16.752 | 69.69 | 14.696 | 0.074959 | 0.033932
3772 | 69.7 | 14.696 | 0.074957 | 16.755 | 0.033937 |  | 3772 | 16.755 | 69.7 | 14.696 | 0.074957 | 0.033937
3773 | 69.71 | 14.696 | 0.074956 | 16.757 | 0.033941 |  | 3773 | 16.757 | 69.71 | 14.696 | 0.074956 | 0.033941
3774 | 69.72 | 14.696 | 0.074954 | 16.759 | 0.033946 |  | 3774 | 16.759 | 69.72 | 14.696 | 0.074954 | 0.033946
3775 | 69.73 | 14.696 | 0.074953 | 16.762 | 0.03395 |  | 3775 | 16.762 | 69.73 | 14.696 | 0.074953 | 0.03395
3776 | 69.74 | 14.696 | 0.074952 | 16.764 | 0.033955 |  | 3776 | 16.764 | 69.74 | 14.696 | 0.074952 | 0.033955
3777 | 69.75 | 14.696 | 0.07495 | 16.767 | 0.033959 |  | 3777 | 16.767 | 69.75 | 14.696 | 0.07495 | 0.033959
3778 | 69.76 | 14.696 | 0.074949 | 16.769 | 0.033964 |  | 3778 | 16.769 | 69.76 | 14.696 | 0.074949 | 0.033964
3779 | 69.77 | 14.696 | 0.074947 | 16.771 | 0.033968 |  | 3779 | 16.771 | 69.77 | 14.696 | 0.074947 | 0.033968
3780 | 69.78 | 14.696 | 0.074946 | 16.774 | 0.033973 |  | 3780 | 16.774 | 69.78 | 14.696 | 0.074946 | 0.033973
3781 | 69.79 | 14.696 | 0.074944 | 16.776 | 0.033977 |  | 3781 | 16.776 | 69.79 | 14.696 | 0.074944 | 0.033977
3782 | 69.8 | 14.696 | 0.074943 | 16.779 | 0.033982 |  | 3782 | 16.779 | 69.8 | 14.696 | 0.074943 | 0.033982
3783 | 69.81 | 14.696 | 0.074942 | 16.781 | 0.033987 |  | 3783 | 16.781 | 69.81 | 14.696 | 0.074942 | 0.033987
3784 | 69.82 | 14.696 | 0.07494 | 16.783 | 0.033991 |  | 3784 | 16.783 | 69.82 | 14.696 | 0.07494 | 0.033991
3785 | 69.83 | 14.696 | 0.074939 | 16.786 | 0.033996 |  | 3785 | 16.786 | 69.83 | 14.696 | 0.074939 | 0.033996
3786 | 69.84 | 14.696 | 0.074937 | 16.788 | 0.034 |  | 3786 | 16.788 | 69.84 | 14.696 | 0.074937 | 0.034
3787 | 69.85 | 14.696 | 0.074936 | 16.791 | 0.034005 |  | 3787 | 16.791 | 69.85 | 14.696 | 0.074936 | 0.034005
3788 | 69.86 | 14.696 | 0.074935 | 16.793 | 0.034009 |  | 3788 | 16.793 | 69.86 | 14.696 | 0.074935 | 0.034009
3789 | 69.87 | 14.696 | 0.074933 | 16.796 | 0.034014 |  | 3789 | 16.796 | 69.87 | 14.696 | 0.074933 | 0.034014
3790 | 69.88 | 14.696 | 0.074932 | 16.798 | 0.034018 |  | 3790 | 16.798 | 69.88 | 14.696 | 0.074932 | 0.034018
3791 | 69.89 | 14.696 | 0.07493 | 16.8 | 0.034023 |  | 3791 | 16.8 | 69.89 | 14.696 | 0.07493 | 0.034023
3792 | 69.9 | 14.696 | 0.074929 | 16.803 | 0.034027 |  | 3792 | 16.803 | 69.9 | 14.696 | 0.074929 | 0.034027
3793 | 69.91 | 14.696 | 0.074927 | 16.805 | 0.034032 |  | 3793 | 16.805 | 69.91 | 14.696 | 0.074927 | 0.034032
3794 | 69.92 | 14.696 | 0.074926 | 16.808 | 0.034037 |  | 3794 | 16.808 | 69.92 | 14.696 | 0.074926 | 0.034037
3795 | 69.93 | 14.696 | 0.074925 | 16.81 | 0.034041 |  | 3795 | 16.81 | 69.93 | 14.696 | 0.074925 | 0.034041
3796 | 69.94 | 14.696 | 0.074923 | 16.812 | 0.034046 |  | 3796 | 16.812 | 69.94 | 14.696 | 0.074923 | 0.034046
3797 | 69.95 | 14.696 | 0.074922 | 16.815 | 0.03405 |  | 3797 | 16.815 | 69.95 | 14.696 | 0.074922 | 0.03405
3798 | 69.96 | 14.696 | 0.07492 | 16.817 | 0.034055 |  | 3798 | 16.817 | 69.96 | 14.696 | 0.07492 | 0.034055
3799 | 69.97 | 14.696 | 0.074919 | 16.82 | 0.034059 |  | 3799 | 16.82 | 69.97 | 14.696 | 0.074919 | 0.034059
3800 | 69.98 | 14.696 | 0.074918 | 16.822 | 0.034064 |  | 3800 | 16.822 | 69.98 | 14.696 | 0.074918 | 0.034064
3801 | 69.99 | 14.696 | 0.074916 | 16.824 | 0.034068 |  | 3801 | 16.824 | 69.99 | 14.696 | 0.074916 | 0.034068
3802 | 70 | 14.696 | 0.074915 | 16.827 | 0.034073 |  | 3802 | 16.827 | 70 | 14.696 | 0.074915 | 0.034073
3803 | 70.01 | 14.696 | 0.074913 | 16.829 | 0.034077 |  | 3803 | 16.829 | 70.01 | 14.696 | 0.074913 | 0.034077
3804 | 70.02 | 14.696 | 0.074912 | 16.832 | 0.034082 |  | 3804 | 16.832 | 70.02 | 14.696 | 0.074912 | 0.034082
3805 | 70.03 | 14.696 | 0.07491 | 16.834 | 0.034086 |  | 3805 | 16.834 | 70.03 | 14.696 | 0.07491 | 0.034086
3806 | 70.04 | 14.696 | 0.074909 | 16.836 | 0.034091 |  | 3806 | 16.836 | 70.04 | 14.696 | 0.074909 | 0.034091
3807 | 70.05 | 14.696 | 0.074908 | 16.839 | 0.034096 |  | 3807 | 16.839 | 70.05 | 14.696 | 0.074908 | 0.034096
3808 | 70.06 | 14.696 | 0.074906 | 16.841 | 0.0341 |  | 3808 | 16.841 | 70.06 | 14.696 | 0.074906 | 0.0341
3809 | 70.07 | 14.696 | 0.074905 | 16.844 | 0.034105 |  | 3809 | 16.844 | 70.07 | 14.696 | 0.074905 | 0.034105
3810 | 70.08 | 14.696 | 0.074903 | 16.846 | 0.034109 |  | 3810 | 16.846 | 70.08 | 14.696 | 0.074903 | 0.034109
3811 | 70.09 | 14.696 | 0.074902 | 16.848 | 0.034114 |  | 3811 | 16.848 | 70.09 | 14.696 | 0.074902 | 0.034114
3812 | 70.1 | 14.696 | 0.0749 | 16.851 | 0.034118 |  | 3812 | 16.851 | 70.1 | 14.696 | 0.0749 | 0.034118
3813 | 70.11 | 14.696 | 0.074899 | 16.853 | 0.034123 |  | 3813 | 16.853 | 70.11 | 14.696 | 0.074899 | 0.034123
3814 | 70.12 | 14.696 | 0.074898 | 16.856 | 0.034127 |  | 3814 | 16.856 | 70.12 | 14.696 | 0.074898 | 0.034127
3815 | 70.13 | 14.696 | 0.074896 | 16.858 | 0.034132 |  | 3815 | 16.858 | 70.13 | 14.696 | 0.074896 | 0.034132
3816 | 70.14 | 14.696 | 0.074895 | 16.86 | 0.034136 |  | 3816 | 16.86 | 70.14 | 14.696 | 0.074895 | 0.034136
3817 | 70.15 | 14.696 | 0.074893 | 16.863 | 0.034141 |  | 3817 | 16.863 | 70.15 | 14.696 | 0.074893 | 0.034141
3818 | 70.16 | 14.696 | 0.074892 | 16.865 | 0.034145 |  | 3818 | 16.865 | 70.16 | 14.696 | 0.074892 | 0.034145
3819 | 70.17 | 14.696 | 0.074891 | 16.868 | 0.03415 |  | 3819 | 16.868 | 70.17 | 14.696 | 0.074891 | 0.03415
3820 | 70.18 | 14.696 | 0.074889 | 16.87 | 0.034155 |  | 3820 | 16.87 | 70.18 | 14.696 | 0.074889 | 0.034155
3821 | 70.19 | 14.696 | 0.074888 | 16.872 | 0.034159 |  | 3821 | 16.872 | 70.19 | 14.696 | 0.074888 | 0.034159
3822 | 70.2 | 14.696 | 0.074886 | 16.875 | 0.034164 |  | 3822 | 16.875 | 70.2 | 14.696 | 0.074886 | 0.034164
3823 | 70.21 | 14.696 | 0.074885 | 16.877 | 0.034168 |  | 3823 | 16.877 | 70.21 | 14.696 | 0.074885 | 0.034168
3824 | 70.22 | 14.696 | 0.074883 | 16.88 | 0.034173 |  | 3824 | 16.88 | 70.22 | 14.696 | 0.074883 | 0.034173
3825 | 70.23 | 14.696 | 0.074882 | 16.882 | 0.034177 |  | 3825 | 16.882 | 70.23 | 14.696 | 0.074882 | 0.034177
3826 | 70.24 | 14.696 | 0.074881 | 16.884 | 0.034182 |  | 3826 | 16.884 | 70.24 | 14.696 | 0.074881 | 0.034182
3827 | 70.25 | 14.696 | 0.074879 | 16.887 | 0.034186 |  | 3827 | 16.887 | 70.25 | 14.696 | 0.074879 | 0.034186
3828 | 70.26 | 14.696 | 0.074878 | 16.889 | 0.034191 |  | 3828 | 16.889 | 70.26 | 14.696 | 0.074878 | 0.034191
3829 | 70.27 | 14.696 | 0.074876 | 16.892 | 0.034195 |  | 3829 | 16.892 | 70.27 | 14.696 | 0.074876 | 0.034195
3830 | 70.28 | 14.696 | 0.074875 | 16.894 | 0.0342 |  | 3830 | 16.894 | 70.28 | 14.696 | 0.074875 | 0.0342
3831 | 70.29 | 14.696 | 0.074874 | 16.897 | 0.034204 |  | 3831 | 16.897 | 70.29 | 14.696 | 0.074874 | 0.034204
3832 | 70.3 | 14.696 | 0.074872 | 16.899 | 0.034209 |  | 3832 | 16.899 | 70.3 | 14.696 | 0.074872 | 0.034209
3833 | 70.31 | 14.696 | 0.074871 | 16.901 | 0.034214 |  | 3833 | 16.901 | 70.31 | 14.696 | 0.074871 | 0.034214
3834 | 70.32 | 14.696 | 0.074869 | 16.904 | 0.034218 |  | 3834 | 16.904 | 70.32 | 14.696 | 0.074869 | 0.034218
3835 | 70.33 | 14.696 | 0.074868 | 16.906 | 0.034223 |  | 3835 | 16.906 | 70.33 | 14.696 | 0.074868 | 0.034223
3836 | 70.34 | 14.696 | 0.074866 | 16.909 | 0.034227 |  | 3836 | 16.909 | 70.34 | 14.696 | 0.074866 | 0.034227
3837 | 70.35 | 14.696 | 0.074865 | 16.911 | 0.034232 |  | 3837 | 16.911 | 70.35 | 14.696 | 0.074865 | 0.034232
3838 | 70.36 | 14.696 | 0.074864 | 16.913 | 0.034236 |  | 3838 | 16.913 | 70.36 | 14.696 | 0.074864 | 0.034236
3839 | 70.37 | 14.696 | 0.074862 | 16.916 | 0.034241 |  | 3839 | 16.916 | 70.37 | 14.696 | 0.074862 | 0.034241
3840 | 70.38 | 14.696 | 0.074861 | 16.918 | 0.034245 |  | 3840 | 16.918 | 70.38 | 14.696 | 0.074861 | 0.034245
3841 | 70.39 | 14.696 | 0.074859 | 16.921 | 0.03425 |  | 3841 | 16.921 | 70.39 | 14.696 | 0.074859 | 0.03425
3842 | 70.4 | 14.696 | 0.074858 | 16.923 | 0.034254 |  | 3842 | 16.923 | 70.4 | 14.696 | 0.074858 | 0.034254
3843 | 70.41 | 14.696 | 0.074857 | 16.925 | 0.034259 |  | 3843 | 16.925 | 70.41 | 14.696 | 0.074857 | 0.034259
3844 | 70.42 | 14.696 | 0.074855 | 16.928 | 0.034263 |  | 3844 | 16.928 | 70.42 | 14.696 | 0.074855 | 0.034263
3845 | 70.43 | 14.696 | 0.074854 | 16.93 | 0.034268 |  | 3845 | 16.93 | 70.43 | 14.696 | 0.074854 | 0.034268
3846 | 70.44 | 14.696 | 0.074852 | 16.933 | 0.034273 |  | 3846 | 16.933 | 70.44 | 14.696 | 0.074852 | 0.034273
3847 | 70.45 | 14.696 | 0.074851 | 16.935 | 0.034277 |  | 3847 | 16.935 | 70.45 | 14.696 | 0.074851 | 0.034277
3848 | 70.46 | 14.696 | 0.074849 | 16.937 | 0.034282 |  | 3848 | 16.937 | 70.46 | 14.696 | 0.074849 | 0.034282
3849 | 70.47 | 14.696 | 0.074848 | 16.94 | 0.034286 |  | 3849 | 16.94 | 70.47 | 14.696 | 0.074848 | 0.034286
3850 | 70.48 | 14.696 | 0.074847 | 16.942 | 0.034291 |  | 3850 | 16.942 | 70.48 | 14.696 | 0.074847 | 0.034291
3851 | 70.49 | 14.696 | 0.074845 | 16.945 | 0.034295 |  | 3851 | 16.945 | 70.49 | 14.696 | 0.074845 | 0.034295
3852 | 70.5 | 14.696 | 0.074844 | 16.947 | 0.0343 |  | 3852 | 16.947 | 70.5 | 14.696 | 0.074844 | 0.0343
3853 | 70.51 | 14.696 | 0.074842 | 16.949 | 0.034304 |  | 3853 | 16.949 | 70.51 | 14.696 | 0.074842 | 0.034304
3854 | 70.52 | 14.696 | 0.074841 | 16.952 | 0.034309 |  | 3854 | 16.952 | 70.52 | 14.696 | 0.074841 | 0.034309
3855 | 70.53 | 14.696 | 0.07484 | 16.954 | 0.034313 |  | 3855 | 16.954 | 70.53 | 14.696 | 0.07484 | 0.034313
3856 | 70.54 | 14.696 | 0.074838 | 16.957 | 0.034318 |  | 3856 | 16.957 | 70.54 | 14.696 | 0.074838 | 0.034318
3857 | 70.55 | 14.696 | 0.074837 | 16.959 | 0.034322 |  | 3857 | 16.959 | 70.55 | 14.696 | 0.074837 | 0.034322
3858 | 70.56 | 14.696 | 0.074835 | 16.961 | 0.034327 |  | 3858 | 16.961 | 70.56 | 14.696 | 0.074835 | 0.034327
3859 | 70.57 | 14.696 | 0.074834 | 16.964 | 0.034331 |  | 3859 | 16.964 | 70.57 | 14.696 | 0.074834 | 0.034331
3860 | 70.58 | 14.696 | 0.074833 | 16.966 | 0.034336 |  | 3860 | 16.966 | 70.58 | 14.696 | 0.074833 | 0.034336
3861 | 70.59 | 14.696 | 0.074831 | 16.969 | 0.034341 |  | 3861 | 16.969 | 70.59 | 14.696 | 0.074831 | 0.034341
3862 | 70.6 | 14.696 | 0.07483 | 16.971 | 0.034345 |  | 3862 | 16.971 | 70.6 | 14.696 | 0.07483 | 0.034345
3863 | 70.61 | 14.696 | 0.074828 | 16.973 | 0.03435 |  | 3863 | 16.973 | 70.61 | 14.696 | 0.074828 | 0.03435
3864 | 70.62 | 14.696 | 0.074827 | 16.976 | 0.034354 |  | 3864 | 16.976 | 70.62 | 14.696 | 0.074827 | 0.034354
3865 | 70.63 | 14.696 | 0.074825 | 16.978 | 0.034359 |  | 3865 | 16.978 | 70.63 | 14.696 | 0.074825 | 0.034359
3866 | 70.64 | 14.696 | 0.074824 | 16.981 | 0.034363 |  | 3866 | 16.981 | 70.64 | 14.696 | 0.074824 | 0.034363
3867 | 70.65 | 14.696 | 0.074823 | 16.983 | 0.034368 |  | 3867 | 16.983 | 70.65 | 14.696 | 0.074823 | 0.034368
3868 | 70.66 | 14.696 | 0.074821 | 16.985 | 0.034372 |  | 3868 | 16.985 | 70.66 | 14.696 | 0.074821 | 0.034372
3869 | 70.67 | 14.696 | 0.07482 | 16.988 | 0.034377 |  | 3869 | 16.988 | 70.67 | 14.696 | 0.07482 | 0.034377
3870 | 70.68 | 14.696 | 0.074818 | 16.99 | 0.034381 |  | 3870 | 16.99 | 70.68 | 14.696 | 0.074818 | 0.034381
3871 | 70.69 | 14.696 | 0.074817 | 16.993 | 0.034386 |  | 3871 | 16.993 | 70.69 | 14.696 | 0.074817 | 0.034386
3872 | 70.7 | 14.696 | 0.074816 | 16.995 | 0.03439 |  | 3872 | 16.995 | 70.7 | 14.696 | 0.074816 | 0.03439
3873 | 70.71 | 14.696 | 0.074814 | 16.998 | 0.034395 |  | 3873 | 16.998 | 70.71 | 14.696 | 0.074814 | 0.034395
3874 | 70.72 | 14.696 | 0.074813 | 17 | 0.0344 |  | 3874 | 17 | 70.72 | 14.696 | 0.074813 | 0.0344
3875 | 70.73 | 14.696 | 0.074811 | 17.002 | 0.034404 |  | 3875 | 17.002 | 70.73 | 14.696 | 0.074811 | 0.034404
3876 | 70.74 | 14.696 | 0.07481 | 17.005 | 0.034409 |  | 3876 | 17.005 | 70.74 | 14.696 | 0.07481 | 0.034409
3877 | 70.75 | 14.696 | 0.074808 | 17.007 | 0.034413 |  | 3877 | 17.007 | 70.75 | 14.696 | 0.074808 | 0.034413
3878 | 70.76 | 14.696 | 0.074807 | 17.01 | 0.034418 |  | 3878 | 17.01 | 70.76 | 14.696 | 0.074807 | 0.034418
3879 | 70.77 | 14.696 | 0.074806 | 17.012 | 0.034422 |  | 3879 | 17.012 | 70.77 | 14.696 | 0.074806 | 0.034422
3880 | 70.78 | 14.696 | 0.074804 | 17.014 | 0.034427 |  | 3880 | 17.014 | 70.78 | 14.696 | 0.074804 | 0.034427
3881 | 70.79 | 14.696 | 0.074803 | 17.017 | 0.034431 |  | 3881 | 17.017 | 70.79 | 14.696 | 0.074803 | 0.034431
3882 | 70.8 | 14.696 | 0.074801 | 17.019 | 0.034436 |  | 3882 | 17.019 | 70.8 | 14.696 | 0.074801 | 0.034436
3883 | 70.81 | 14.696 | 0.0748 | 17.022 | 0.03444 |  | 3883 | 17.022 | 70.81 | 14.696 | 0.0748 | 0.03444
3884 | 70.82 | 14.696 | 0.074799 | 17.024 | 0.034445 |  | 3884 | 17.024 | 70.82 | 14.696 | 0.074799 | 0.034445
3885 | 70.83 | 14.696 | 0.074797 | 17.026 | 0.034449 |  | 3885 | 17.026 | 70.83 | 14.696 | 0.074797 | 0.034449
3886 | 70.84 | 14.696 | 0.074796 | 17.029 | 0.034454 |  | 3886 | 17.029 | 70.84 | 14.696 | 0.074796 | 0.034454
3887 | 70.85 | 14.696 | 0.074794 | 17.031 | 0.034458 |  | 3887 | 17.031 | 70.85 | 14.696 | 0.074794 | 0.034458
3888 | 70.86 | 14.696 | 0.074793 | 17.034 | 0.034463 |  | 3888 | 17.034 | 70.86 | 14.696 | 0.074793 | 0.034463
3889 | 70.87 | 14.696 | 0.074791 | 17.036 | 0.034468 |  | 3889 | 17.036 | 70.87 | 14.696 | 0.074791 | 0.034468
3890 | 70.88 | 14.696 | 0.07479 | 17.038 | 0.034472 |  | 3890 | 17.038 | 70.88 | 14.696 | 0.07479 | 0.034472
3891 | 70.89 | 14.696 | 0.074789 | 17.041 | 0.034477 |  | 3891 | 17.041 | 70.89 | 14.696 | 0.074789 | 0.034477
3892 | 70.9 | 14.696 | 0.074787 | 17.043 | 0.034481 |  | 3892 | 17.043 | 70.9 | 14.696 | 0.074787 | 0.034481
3893 | 70.91 | 14.696 | 0.074786 | 17.046 | 0.034486 |  | 3893 | 17.046 | 70.91 | 14.696 | 0.074786 | 0.034486
3894 | 70.92 | 14.696 | 0.074784 | 17.048 | 0.03449 |  | 3894 | 17.048 | 70.92 | 14.696 | 0.074784 | 0.03449
3895 | 70.93 | 14.696 | 0.074783 | 17.05 | 0.034495 |  | 3895 | 17.05 | 70.93 | 14.696 | 0.074783 | 0.034495
3896 | 70.94 | 14.696 | 0.074782 | 17.053 | 0.034499 |  | 3896 | 17.053 | 70.94 | 14.696 | 0.074782 | 0.034499
3897 | 70.95 | 14.696 | 0.07478 | 17.055 | 0.034504 |  | 3897 | 17.055 | 70.95 | 14.696 | 0.07478 | 0.034504
3898 | 70.96 | 14.696 | 0.074779 | 17.058 | 0.034508 |  | 3898 | 17.058 | 70.96 | 14.696 | 0.074779 | 0.034508
3899 | 70.97 | 14.696 | 0.074777 | 17.06 | 0.034513 |  | 3899 | 17.06 | 70.97 | 14.696 | 0.074777 | 0.034513
3900 | 70.98 | 14.696 | 0.074776 | 17.062 | 0.034517 |  | 3900 | 17.062 | 70.98 | 14.696 | 0.074776 | 0.034517
3901 | 70.99 | 14.696 | 0.074775 | 17.065 | 0.034522 |  | 3901 | 17.065 | 70.99 | 14.696 | 0.074775 | 0.034522
3902 | 71 | 14.696 | 0.074773 | 17.067 | 0.034526 |  | 3902 | 17.067 | 71 | 14.696 | 0.074773 | 0.034526
3903 | 71.01 | 14.696 | 0.074772 | 17.07 | 0.034531 |  | 3903 | 17.07 | 71.01 | 14.696 | 0.074772 | 0.034531
3904 | 71.02 | 14.696 | 0.07477 | 17.072 | 0.034535 |  | 3904 | 17.072 | 71.02 | 14.696 | 0.07477 | 0.034535
3905 | 71.03 | 14.696 | 0.074769 | 17.074 | 0.03454 |  | 3905 | 17.074 | 71.03 | 14.696 | 0.074769 | 0.03454
3906 | 71.04 | 14.696 | 0.074767 | 17.077 | 0.034545 |  | 3906 | 17.077 | 71.04 | 14.696 | 0.074767 | 0.034545
3907 | 71.05 | 14.696 | 0.074766 | 17.079 | 0.034549 |  | 3907 | 17.079 | 71.05 | 14.696 | 0.074766 | 0.034549
3908 | 71.06 | 14.696 | 0.074765 | 17.082 | 0.034554 |  | 3908 | 17.082 | 71.06 | 14.696 | 0.074765 | 0.034554
3909 | 71.07 | 14.696 | 0.074763 | 17.084 | 0.034558 |  | 3909 | 17.084 | 71.07 | 14.696 | 0.074763 | 0.034558
3910 | 71.08 | 14.696 | 0.074762 | 17.086 | 0.034563 |  | 3910 | 17.086 | 71.08 | 14.696 | 0.074762 | 0.034563
3911 | 71.09 | 14.696 | 0.07476 | 17.089 | 0.034567 |  | 3911 | 17.089 | 71.09 | 14.696 | 0.07476 | 0.034567
3912 | 71.1 | 14.696 | 0.074759 | 17.091 | 0.034572 |  | 3912 | 17.091 | 71.1 | 14.696 | 0.074759 | 0.034572
3913 | 71.11 | 14.696 | 0.074758 | 17.094 | 0.034576 |  | 3913 | 17.094 | 71.11 | 14.696 | 0.074758 | 0.034576
3914 | 71.12 | 14.696 | 0.074756 | 17.096 | 0.034581 |  | 3914 | 17.096 | 71.12 | 14.696 | 0.074756 | 0.034581
3915 | 71.13 | 14.696 | 0.074755 | 17.099 | 0.034585 |  | 3915 | 17.099 | 71.13 | 14.696 | 0.074755 | 0.034585
3916 | 71.14 | 14.696 | 0.074753 | 17.101 | 0.03459 |  | 3916 | 17.101 | 71.14 | 14.696 | 0.074753 | 0.03459
3917 | 71.15 | 14.696 | 0.074752 | 17.103 | 0.034594 |  | 3917 | 17.103 | 71.15 | 14.696 | 0.074752 | 0.034594
3918 | 71.16 | 14.696 | 0.074751 | 17.106 | 0.034599 |  | 3918 | 17.106 | 71.16 | 14.696 | 0.074751 | 0.034599
3919 | 71.17 | 14.696 | 0.074749 | 17.108 | 0.034603 |  | 3919 | 17.108 | 71.17 | 14.696 | 0.074749 | 0.034603
3920 | 71.18 | 14.696 | 0.074748 | 17.111 | 0.034608 |  | 3920 | 17.111 | 71.18 | 14.696 | 0.074748 | 0.034608
3921 | 71.19 | 14.696 | 0.074746 | 17.113 | 0.034613 |  | 3921 | 17.113 | 71.19 | 14.696 | 0.074746 | 0.034613
3922 | 71.2 | 14.696 | 0.074745 | 17.115 | 0.034617 |  | 3922 | 17.115 | 71.2 | 14.696 | 0.074745 | 0.034617
3923 | 71.21 | 14.696 | 0.074743 | 17.118 | 0.034622 |  | 3923 | 17.118 | 71.21 | 14.696 | 0.074743 | 0.034622
3924 | 71.22 | 14.696 | 0.074742 | 17.12 | 0.034626 |  | 3924 | 17.12 | 71.22 | 14.696 | 0.074742 | 0.034626
3925 | 71.23 | 14.696 | 0.074741 | 17.123 | 0.034631 |  | 3925 | 17.123 | 71.23 | 14.696 | 0.074741 | 0.034631
3926 | 71.24 | 14.696 | 0.074739 | 17.125 | 0.034635 |  | 3926 | 17.125 | 71.24 | 14.696 | 0.074739 | 0.034635
3927 | 71.25 | 14.696 | 0.074738 | 17.127 | 0.03464 |  | 3927 | 17.127 | 71.25 | 14.696 | 0.074738 | 0.03464
3928 | 71.26 | 14.696 | 0.074736 | 17.13 | 0.034644 |  | 3928 | 17.13 | 71.26 | 14.696 | 0.074736 | 0.034644
3929 | 71.27 | 14.696 | 0.074735 | 17.132 | 0.034649 |  | 3929 | 17.132 | 71.27 | 14.696 | 0.074735 | 0.034649
3930 | 71.28 | 14.696 | 0.074734 | 17.135 | 0.034653 |  | 3930 | 17.135 | 71.28 | 14.696 | 0.074734 | 0.034653
3931 | 71.29 | 14.696 | 0.074732 | 17.137 | 0.034658 |  | 3931 | 17.137 | 71.29 | 14.696 | 0.074732 | 0.034658
3932 | 71.3 | 14.696 | 0.074731 | 17.139 | 0.034662 |  | 3932 | 17.139 | 71.3 | 14.696 | 0.074731 | 0.034662
3933 | 71.31 | 14.696 | 0.074729 | 17.142 | 0.034667 |  | 3933 | 17.142 | 71.31 | 14.696 | 0.074729 | 0.034667
3934 | 71.32 | 14.696 | 0.074728 | 17.144 | 0.034671 |  | 3934 | 17.144 | 71.32 | 14.696 | 0.074728 | 0.034671
3935 | 71.33 | 14.696 | 0.074727 | 17.147 | 0.034676 |  | 3935 | 17.147 | 71.33 | 14.696 | 0.074727 | 0.034676
3936 | 71.34 | 14.696 | 0.074725 | 17.149 | 0.03468 |  | 3936 | 17.149 | 71.34 | 14.696 | 0.074725 | 0.03468
3937 | 71.35 | 14.696 | 0.074724 | 17.151 | 0.034685 |  | 3937 | 17.151 | 71.35 | 14.696 | 0.074724 | 0.034685
3938 | 71.36 | 14.696 | 0.074722 | 17.154 | 0.03469 |  | 3938 | 17.154 | 71.36 | 14.696 | 0.074722 | 0.03469
3939 | 71.37 | 14.696 | 0.074721 | 17.156 | 0.034694 |  | 3939 | 17.156 | 71.37 | 14.696 | 0.074721 | 0.034694
3940 | 71.38 | 14.696 | 0.074719 | 17.159 | 0.034699 |  | 3940 | 17.159 | 71.38 | 14.696 | 0.074719 | 0.034699
3941 | 71.39 | 14.696 | 0.074718 | 17.161 | 0.034703 |  | 3941 | 17.161 | 71.39 | 14.696 | 0.074718 | 0.034703
3942 | 71.4 | 14.696 | 0.074717 | 17.163 | 0.034708 |  | 3942 | 17.163 | 71.4 | 14.696 | 0.074717 | 0.034708
3943 | 71.41 | 14.696 | 0.074715 | 17.166 | 0.034712 |  | 3943 | 17.166 | 71.41 | 14.696 | 0.074715 | 0.034712
3944 | 71.42 | 14.696 | 0.074714 | 17.168 | 0.034717 |  | 3944 | 17.168 | 71.42 | 14.696 | 0.074714 | 0.034717
3945 | 71.43 | 14.696 | 0.074712 | 17.171 | 0.034721 |  | 3945 | 17.171 | 71.43 | 14.696 | 0.074712 | 0.034721
3946 | 71.44 | 14.696 | 0.074711 | 17.173 | 0.034726 |  | 3946 | 17.173 | 71.44 | 14.696 | 0.074711 | 0.034726
3947 | 71.45 | 14.696 | 0.07471 | 17.175 | 0.03473 |  | 3947 | 17.175 | 71.45 | 14.696 | 0.07471 | 0.03473
3948 | 71.46 | 14.696 | 0.074708 | 17.178 | 0.034735 |  | 3948 | 17.178 | 71.46 | 14.696 | 0.074708 | 0.034735
3949 | 71.47 | 14.696 | 0.074707 | 17.18 | 0.034739 |  | 3949 | 17.18 | 71.47 | 14.696 | 0.074707 | 0.034739
3950 | 71.48 | 14.696 | 0.074705 | 17.183 | 0.034744 |  | 3950 | 17.183 | 71.48 | 14.696 | 0.074705 | 0.034744
3951 | 71.49 | 14.696 | 0.074704 | 17.185 | 0.034748 |  | 3951 | 17.185 | 71.49 | 14.696 | 0.074704 | 0.034748
3952 | 71.5 | 14.696 | 0.074703 | 17.187 | 0.034753 |  | 3952 | 17.187 | 71.5 | 14.696 | 0.074703 | 0.034753
3953 | 71.51 | 14.696 | 0.074701 | 17.19 | 0.034757 |  | 3953 | 17.19 | 71.51 | 14.696 | 0.074701 | 0.034757
3954 | 71.52 | 14.696 | 0.0747 | 17.192 | 0.034762 |  | 3954 | 17.192 | 71.52 | 14.696 | 0.0747 | 0.034762
3955 | 71.53 | 14.696 | 0.074698 | 17.195 | 0.034766 |  | 3955 | 17.195 | 71.53 | 14.696 | 0.074698 | 0.034766
3956 | 71.54 | 14.696 | 0.074697 | 17.197 | 0.034771 |  | 3956 | 17.197 | 71.54 | 14.696 | 0.074697 | 0.034771
3957 | 71.55 | 14.696 | 0.074695 | 17.2 | 0.034776 |  | 3957 | 17.2 | 71.55 | 14.696 | 0.074695 | 0.034776
3958 | 71.56 | 14.696 | 0.074694 | 17.202 | 0.03478 |  | 3958 | 17.202 | 71.56 | 14.696 | 0.074694 | 0.03478
3959 | 71.57 | 14.696 | 0.074693 | 17.204 | 0.034785 |  | 3959 | 17.204 | 71.57 | 14.696 | 0.074693 | 0.034785
3960 | 71.58 | 14.696 | 0.074691 | 17.207 | 0.034789 |  | 3960 | 17.207 | 71.58 | 14.696 | 0.074691 | 0.034789
3961 | 71.59 | 14.696 | 0.07469 | 17.209 | 0.034794 |  | 3961 | 17.209 | 71.59 | 14.696 | 0.07469 | 0.034794
3962 | 71.6 | 14.696 | 0.074688 | 17.212 | 0.034798 |  | 3962 | 17.212 | 71.6 | 14.696 | 0.074688 | 0.034798
3963 | 71.61 | 14.696 | 0.074687 | 17.214 | 0.034803 |  | 3963 | 17.214 | 71.61 | 14.696 | 0.074687 | 0.034803
3964 | 71.62 | 14.696 | 0.074686 | 17.216 | 0.034807 |  | 3964 | 17.216 | 71.62 | 14.696 | 0.074686 | 0.034807
3965 | 71.63 | 14.696 | 0.074684 | 17.219 | 0.034812 |  | 3965 | 17.219 | 71.63 | 14.696 | 0.074684 | 0.034812
3966 | 71.64 | 14.696 | 0.074683 | 17.221 | 0.034816 |  | 3966 | 17.221 | 71.64 | 14.696 | 0.074683 | 0.034816
3967 | 71.65 | 14.696 | 0.074681 | 17.224 | 0.034821 |  | 3967 | 17.224 | 71.65 | 14.696 | 0.074681 | 0.034821
3968 | 71.66 | 14.696 | 0.07468 | 17.226 | 0.034825 |  | 3968 | 17.226 | 71.66 | 14.696 | 0.07468 | 0.034825
3969 | 71.67 | 14.696 | 0.074679 | 17.228 | 0.03483 |  | 3969 | 17.228 | 71.67 | 14.696 | 0.074679 | 0.03483
3970 | 71.68 | 14.696 | 0.074677 | 17.231 | 0.034834 |  | 3970 | 17.231 | 71.68 | 14.696 | 0.074677 | 0.034834
3971 | 71.69 | 14.696 | 0.074676 | 17.233 | 0.034839 |  | 3971 | 17.233 | 71.69 | 14.696 | 0.074676 | 0.034839
3972 | 71.7 | 14.696 | 0.074674 | 17.236 | 0.034843 |  | 3972 | 17.236 | 71.7 | 14.696 | 0.074674 | 0.034843
3973 | 71.71 | 14.696 | 0.074673 | 17.238 | 0.034848 |  | 3973 | 17.238 | 71.71 | 14.696 | 0.074673 | 0.034848
3974 | 71.72 | 14.696 | 0.074672 | 17.24 | 0.034852 |  | 3974 | 17.24 | 71.72 | 14.696 | 0.074672 | 0.034852
3975 | 71.73 | 14.696 | 0.07467 | 17.243 | 0.034857 |  | 3975 | 17.243 | 71.73 | 14.696 | 0.07467 | 0.034857
3976 | 71.74 | 14.696 | 0.074669 | 17.245 | 0.034862 |  | 3976 | 17.245 | 71.74 | 14.696 | 0.074669 | 0.034862
3977 | 71.75 | 14.696 | 0.074667 | 17.248 | 0.034866 |  | 3977 | 17.248 | 71.75 | 14.696 | 0.074667 | 0.034866
3978 | 71.76 | 14.696 | 0.074666 | 17.25 | 0.034871 |  | 3978 | 17.25 | 71.76 | 14.696 | 0.074666 | 0.034871
3979 | 71.77 | 14.696 | 0.074664 | 17.252 | 0.034875 |  | 3979 | 17.252 | 71.77 | 14.696 | 0.074664 | 0.034875
3980 | 71.78 | 14.696 | 0.074663 | 17.255 | 0.03488 |  | 3980 | 17.255 | 71.78 | 14.696 | 0.074663 | 0.03488
3981 | 71.79 | 14.696 | 0.074662 | 17.257 | 0.034884 |  | 3981 | 17.257 | 71.79 | 14.696 | 0.074662 | 0.034884
3982 | 71.8 | 14.696 | 0.07466 | 17.26 | 0.034889 |  | 3982 | 17.26 | 71.8 | 14.696 | 0.07466 | 0.034889
3983 | 71.81 | 14.696 | 0.074659 | 17.262 | 0.034893 |  | 3983 | 17.262 | 71.81 | 14.696 | 0.074659 | 0.034893
3984 | 71.82 | 14.696 | 0.074657 | 17.264 | 0.034898 |  | 3984 | 17.264 | 71.82 | 14.696 | 0.074657 | 0.034898
3985 | 71.83 | 14.696 | 0.074656 | 17.267 | 0.034902 |  | 3985 | 17.267 | 71.83 | 14.696 | 0.074656 | 0.034902
3986 | 71.84 | 14.696 | 0.074655 | 17.269 | 0.034907 |  | 3986 | 17.269 | 71.84 | 14.696 | 0.074655 | 0.034907
3987 | 71.85 | 14.696 | 0.074653 | 17.272 | 0.034911 |  | 3987 | 17.272 | 71.85 | 14.696 | 0.074653 | 0.034911
3988 | 71.86 | 14.696 | 0.074652 | 17.274 | 0.034916 |  | 3988 | 17.274 | 71.86 | 14.696 | 0.074652 | 0.034916
3989 | 71.87 | 14.696 | 0.07465 | 17.276 | 0.03492 |  | 3989 | 17.276 | 71.87 | 14.696 | 0.07465 | 0.03492
3990 | 71.88 | 14.696 | 0.074649 | 17.279 | 0.034925 |  | 3990 | 17.279 | 71.88 | 14.696 | 0.074649 | 0.034925
3991 | 71.89 | 14.696 | 0.074648 | 17.281 | 0.034929 |  | 3991 | 17.281 | 71.89 | 14.696 | 0.074648 | 0.034929
3992 | 71.9 | 14.696 | 0.074646 | 17.284 | 0.034934 |  | 3992 | 17.284 | 71.9 | 14.696 | 0.074646 | 0.034934
3993 | 71.91 | 14.696 | 0.074645 | 17.286 | 0.034938 |  | 3993 | 17.286 | 71.91 | 14.696 | 0.074645 | 0.034938
3994 | 71.92 | 14.696 | 0.074643 | 17.289 | 0.034943 |  | 3994 | 17.289 | 71.92 | 14.696 | 0.074643 | 0.034943
3995 | 71.93 | 14.696 | 0.074642 | 17.291 | 0.034948 |  | 3995 | 17.291 | 71.93 | 14.696 | 0.074642 | 0.034948
3996 | 71.94 | 14.696 | 0.074641 | 17.293 | 0.034952 |  | 3996 | 17.293 | 71.94 | 14.696 | 0.074641 | 0.034952
3997 | 71.95 | 14.696 | 0.074639 | 17.296 | 0.034957 |  | 3997 | 17.296 | 71.95 | 14.696 | 0.074639 | 0.034957
3998 | 71.96 | 14.696 | 0.074638 | 17.298 | 0.034961 |  | 3998 | 17.298 | 71.96 | 14.696 | 0.074638 | 0.034961
3999 | 71.97 | 14.696 | 0.074636 | 17.301 | 0.034966 |  | 3999 | 17.301 | 71.97 | 14.696 | 0.074636 | 0.034966
4000 | 71.98 | 14.696 | 0.074635 | 17.303 | 0.03497 |  | 4000 | 17.303 | 71.98 | 14.696 | 0.074635 | 0.03497
4001 | 71.99 | 14.696 | 0.074633 | 17.305 | 0.034975 |  | 4001 | 17.305 | 71.99 | 14.696 | 0.074633 | 0.034975
4002 | 72 | 14.696 | 0.074632 | 17.308 | 0.034979 |  | 4002 | 17.308 | 72 | 14.696 | 0.074632 | 0.034979
4003 | 72.01 | 14.696 | 0.074631 | 17.31 | 0.034984 |  | 4003 | 17.31 | 72.01 | 14.696 | 0.074631 | 0.034984
4004 | 72.02 | 14.696 | 0.074629 | 17.313 | 0.034988 |  | 4004 | 17.313 | 72.02 | 14.696 | 0.074629 | 0.034988
4005 | 72.03 | 14.696 | 0.074628 | 17.315 | 0.034993 |  | 4005 | 17.315 | 72.03 | 14.696 | 0.074628 | 0.034993
4006 | 72.04 | 14.696 | 0.074626 | 17.317 | 0.034997 |  | 4006 | 17.317 | 72.04 | 14.696 | 0.074626 | 0.034997
4007 | 72.05 | 14.696 | 0.074625 | 17.32 | 0.035002 |  | 4007 | 17.32 | 72.05 | 14.696 | 0.074625 | 0.035002
4008 | 72.06 | 14.696 | 0.074624 | 17.322 | 0.035006 |  | 4008 | 17.322 | 72.06 | 14.696 | 0.074624 | 0.035006
4009 | 72.07 | 14.696 | 0.074622 | 17.325 | 0.035011 |  | 4009 | 17.325 | 72.07 | 14.696 | 0.074622 | 0.035011
4010 | 72.08 | 14.696 | 0.074621 | 17.327 | 0.035015 |  | 4010 | 17.327 | 72.08 | 14.696 | 0.074621 | 0.035015
4011 | 72.09 | 14.696 | 0.074619 | 17.329 | 0.03502 |  | 4011 | 17.329 | 72.09 | 14.696 | 0.074619 | 0.03502
4012 | 72.1 | 14.696 | 0.074618 | 17.332 | 0.035024 |  | 4012 | 17.332 | 72.1 | 14.696 | 0.074618 | 0.035024
4013 | 72.11 | 14.696 | 0.074617 | 17.334 | 0.035029 |  | 4013 | 17.334 | 72.11 | 14.696 | 0.074617 | 0.035029
4014 | 72.12 | 14.696 | 0.074615 | 17.337 | 0.035033 |  | 4014 | 17.337 | 72.12 | 14.696 | 0.074615 | 0.035033
4015 | 72.13 | 14.696 | 0.074614 | 17.339 | 0.035038 |  | 4015 | 17.339 | 72.13 | 14.696 | 0.074614 | 0.035038
4016 | 72.14 | 14.696 | 0.074612 | 17.341 | 0.035042 |  | 4016 | 17.341 | 72.14 | 14.696 | 0.074612 | 0.035042
4017 | 72.15 | 14.696 | 0.074611 | 17.344 | 0.035047 |  | 4017 | 17.344 | 72.15 | 14.696 | 0.074611 | 0.035047
4018 | 72.16 | 14.696 | 0.07461 | 17.346 | 0.035052 |  | 4018 | 17.346 | 72.16 | 14.696 | 0.07461 | 0.035052
4019 | 72.17 | 14.696 | 0.074608 | 17.349 | 0.035056 |  | 4019 | 17.349 | 72.17 | 14.696 | 0.074608 | 0.035056
4020 | 72.18 | 14.696 | 0.074607 | 17.351 | 0.035061 |  | 4020 | 17.351 | 72.18 | 14.696 | 0.074607 | 0.035061
4021 | 72.19 | 14.696 | 0.074605 | 17.353 | 0.035065 |  | 4021 | 17.353 | 72.19 | 14.696 | 0.074605 | 0.035065
4022 | 72.2 | 14.696 | 0.074604 | 17.356 | 0.03507 |  | 4022 | 17.356 | 72.2 | 14.696 | 0.074604 | 0.03507
4023 | 72.21 | 14.696 | 0.074603 | 17.358 | 0.035074 |  | 4023 | 17.358 | 72.21 | 14.696 | 0.074603 | 0.035074
4024 | 72.22 | 14.696 | 0.074601 | 17.361 | 0.035079 |  | 4024 | 17.361 | 72.22 | 14.696 | 0.074601 | 0.035079
4025 | 72.23 | 14.696 | 0.0746 | 17.363 | 0.035083 |  | 4025 | 17.363 | 72.23 | 14.696 | 0.0746 | 0.035083
4026 | 72.24 | 14.696 | 0.074598 | 17.365 | 0.035088 |  | 4026 | 17.365 | 72.24 | 14.696 | 0.074598 | 0.035088
4027 | 72.25 | 14.696 | 0.074597 | 17.368 | 0.035092 |  | 4027 | 17.368 | 72.25 | 14.696 | 0.074597 | 0.035092
4028 | 72.26 | 14.696 | 0.074595 | 17.37 | 0.035097 |  | 4028 | 17.37 | 72.26 | 14.696 | 0.074595 | 0.035097
4029 | 72.27 | 14.696 | 0.074594 | 17.373 | 0.035101 |  | 4029 | 17.373 | 72.27 | 14.696 | 0.074594 | 0.035101
4030 | 72.28 | 14.696 | 0.074593 | 17.375 | 0.035106 |  | 4030 | 17.375 | 72.28 | 14.696 | 0.074593 | 0.035106
4031 | 72.29 | 14.696 | 0.074591 | 17.377 | 0.03511 |  | 4031 | 17.377 | 72.29 | 14.696 | 0.074591 | 0.03511
4032 | 72.3 | 14.696 | 0.07459 | 17.38 | 0.035115 |  | 4032 | 17.38 | 72.3 | 14.696 | 0.07459 | 0.035115
4033 | 72.31 | 14.696 | 0.074588 | 17.382 | 0.035119 |  | 4033 | 17.382 | 72.31 | 14.696 | 0.074588 | 0.035119
4034 | 72.32 | 14.696 | 0.074587 | 17.385 | 0.035124 |  | 4034 | 17.385 | 72.32 | 14.696 | 0.074587 | 0.035124
4035 | 72.33 | 14.696 | 0.074586 | 17.387 | 0.035128 |  | 4035 | 17.387 | 72.33 | 14.696 | 0.074586 | 0.035128
4036 | 72.34 | 14.696 | 0.074584 | 17.39 | 0.035133 |  | 4036 | 17.39 | 72.34 | 14.696 | 0.074584 | 0.035133
4037 | 72.35 | 14.696 | 0.074583 | 17.392 | 0.035137 |  | 4037 | 17.392 | 72.35 | 14.696 | 0.074583 | 0.035137
4038 | 72.36 | 14.696 | 0.074581 | 17.394 | 0.035142 |  | 4038 | 17.394 | 72.36 | 14.696 | 0.074581 | 0.035142
4039 | 72.37 | 14.696 | 0.07458 | 17.397 | 0.035146 |  | 4039 | 17.397 | 72.37 | 14.696 | 0.07458 | 0.035146
4040 | 72.38 | 14.696 | 0.074579 | 17.399 | 0.035151 |  | 4040 | 17.399 | 72.38 | 14.696 | 0.074579 | 0.035151
4041 | 72.39 | 14.696 | 0.074577 | 17.402 | 0.035156 |  | 4041 | 17.402 | 72.39 | 14.696 | 0.074577 | 0.035156
4042 | 72.4 | 14.696 | 0.074576 | 17.404 | 0.03516 |  | 4042 | 17.404 | 72.4 | 14.696 | 0.074576 | 0.03516
4043 | 72.41 | 14.696 | 0.074574 | 17.406 | 0.035165 |  | 4043 | 17.406 | 72.41 | 14.696 | 0.074574 | 0.035165
4044 | 72.42 | 14.696 | 0.074573 | 17.409 | 0.035169 |  | 4044 | 17.409 | 72.42 | 14.696 | 0.074573 | 0.035169
4045 | 72.43 | 14.696 | 0.074572 | 17.411 | 0.035174 |  | 4045 | 17.411 | 72.43 | 14.696 | 0.074572 | 0.035174
4046 | 72.44 | 14.696 | 0.07457 | 17.414 | 0.035178 |  | 4046 | 17.414 | 72.44 | 14.696 | 0.07457 | 0.035178
4047 | 72.45 | 14.696 | 0.074569 | 17.416 | 0.035183 |  | 4047 | 17.416 | 72.45 | 14.696 | 0.074569 | 0.035183
4048 | 72.46 | 14.696 | 0.074567 | 17.418 | 0.035187 |  | 4048 | 17.418 | 72.46 | 14.696 | 0.074567 | 0.035187
4049 | 72.47 | 14.696 | 0.074566 | 17.421 | 0.035192 |  | 4049 | 17.421 | 72.47 | 14.696 | 0.074566 | 0.035192
4050 | 72.48 | 14.696 | 0.074565 | 17.423 | 0.035196 |  | 4050 | 17.423 | 72.48 | 14.696 | 0.074565 | 0.035196
4051 | 72.49 | 14.696 | 0.074563 | 17.426 | 0.035201 |  | 4051 | 17.426 | 72.49 | 14.696 | 0.074563 | 0.035201
4052 | 72.5 | 14.696 | 0.074562 | 17.428 | 0.035205 |  | 4052 | 17.428 | 72.5 | 14.696 | 0.074562 | 0.035205
4053 | 72.51 | 14.696 | 0.07456 | 17.43 | 0.03521 |  | 4053 | 17.43 | 72.51 | 14.696 | 0.07456 | 0.03521
4054 | 72.52 | 14.696 | 0.074559 | 17.433 | 0.035214 |  | 4054 | 17.433 | 72.52 | 14.696 | 0.074559 | 0.035214
4055 | 72.53 | 14.696 | 0.074558 | 17.435 | 0.035219 |  | 4055 | 17.435 | 72.53 | 14.696 | 0.074558 | 0.035219
4056 | 72.54 | 14.696 | 0.074556 | 17.438 | 0.035223 |  | 4056 | 17.438 | 72.54 | 14.696 | 0.074556 | 0.035223
4057 | 72.55 | 14.696 | 0.074555 | 17.44 | 0.035228 |  | 4057 | 17.44 | 72.55 | 14.696 | 0.074555 | 0.035228
4058 | 72.56 | 14.696 | 0.074553 | 17.442 | 0.035232 |  | 4058 | 17.442 | 72.56 | 14.696 | 0.074553 | 0.035232
4059 | 72.57 | 14.696 | 0.074552 | 17.445 | 0.035237 |  | 4059 | 17.445 | 72.57 | 14.696 | 0.074552 | 0.035237
4060 | 72.58 | 14.696 | 0.074551 | 17.447 | 0.035241 |  | 4060 | 17.447 | 72.58 | 14.696 | 0.074551 | 0.035241
4061 | 72.59 | 14.696 | 0.074549 | 17.45 | 0.035246 |  | 4061 | 17.45 | 72.59 | 14.696 | 0.074549 | 0.035246
4062 | 72.6 | 14.696 | 0.074548 | 17.452 | 0.03525 |  | 4062 | 17.452 | 72.6 | 14.696 | 0.074548 | 0.03525
4063 | 72.61 | 14.696 | 0.074546 | 17.454 | 0.035255 |  | 4063 | 17.454 | 72.61 | 14.696 | 0.074546 | 0.035255
4064 | 72.62 | 14.696 | 0.074545 | 17.457 | 0.035259 |  | 4064 | 17.457 | 72.62 | 14.696 | 0.074545 | 0.035259
4065 | 72.63 | 14.696 | 0.074544 | 17.459 | 0.035264 |  | 4065 | 17.459 | 72.63 | 14.696 | 0.074544 | 0.035264
4066 | 72.64 | 14.696 | 0.074542 | 17.462 | 0.035268 |  | 4066 | 17.462 | 72.64 | 14.696 | 0.074542 | 0.035268
4067 | 72.65 | 14.696 | 0.074541 | 17.464 | 0.035273 |  | 4067 | 17.464 | 72.65 | 14.696 | 0.074541 | 0.035273
4068 | 72.66 | 14.696 | 0.074539 | 17.466 | 0.035278 |  | 4068 | 17.466 | 72.66 | 14.696 | 0.074539 | 0.035278
4069 | 72.67 | 14.696 | 0.074538 | 17.469 | 0.035282 |  | 4069 | 17.469 | 72.67 | 14.696 | 0.074538 | 0.035282
4070 | 72.68 | 14.696 | 0.074536 | 17.471 | 0.035287 |  | 4070 | 17.471 | 72.68 | 14.696 | 0.074536 | 0.035287
4071 | 72.69 | 14.696 | 0.074535 | 17.474 | 0.035291 |  | 4071 | 17.474 | 72.69 | 14.696 | 0.074535 | 0.035291
4072 | 72.7 | 14.696 | 0.074534 | 17.476 | 0.035296 |  | 4072 | 17.476 | 72.7 | 14.696 | 0.074534 | 0.035296
4073 | 72.71 | 14.696 | 0.074532 | 17.478 | 0.0353 |  | 4073 | 17.478 | 72.71 | 14.696 | 0.074532 | 0.0353
4074 | 72.72 | 14.696 | 0.074531 | 17.481 | 0.035305 |  | 4074 | 17.481 | 72.72 | 14.696 | 0.074531 | 0.035305
4075 | 72.73 | 14.696 | 0.074529 | 17.483 | 0.035309 |  | 4075 | 17.483 | 72.73 | 14.696 | 0.074529 | 0.035309
4076 | 72.74 | 14.696 | 0.074528 | 17.486 | 0.035314 |  | 4076 | 17.486 | 72.74 | 14.696 | 0.074528 | 0.035314
4077 | 72.75 | 14.696 | 0.074527 | 17.488 | 0.035318 |  | 4077 | 17.488 | 72.75 | 14.696 | 0.074527 | 0.035318
4078 | 72.76 | 14.696 | 0.074525 | 17.491 | 0.035323 |  | 4078 | 17.491 | 72.76 | 14.696 | 0.074525 | 0.035323
4079 | 72.77 | 14.696 | 0.074524 | 17.493 | 0.035327 |  | 4079 | 17.493 | 72.77 | 14.696 | 0.074524 | 0.035327
4080 | 72.78 | 14.696 | 0.074522 | 17.495 | 0.035332 |  | 4080 | 17.495 | 72.78 | 14.696 | 0.074522 | 0.035332
4081 | 72.79 | 14.696 | 0.074521 | 17.498 | 0.035336 |  | 4081 | 17.498 | 72.79 | 14.696 | 0.074521 | 0.035336
4082 | 72.8 | 14.696 | 0.07452 | 17.5 | 0.035341 |  | 4082 | 17.5 | 72.8 | 14.696 | 0.07452 | 0.035341
4083 | 72.81 | 14.696 | 0.074518 | 17.503 | 0.035345 |  | 4083 | 17.503 | 72.81 | 14.696 | 0.074518 | 0.035345
4084 | 72.82 | 14.696 | 0.074517 | 17.505 | 0.03535 |  | 4084 | 17.505 | 72.82 | 14.696 | 0.074517 | 0.03535
4085 | 72.83 | 14.696 | 0.074515 | 17.507 | 0.035354 |  | 4085 | 17.507 | 72.83 | 14.696 | 0.074515 | 0.035354
4086 | 72.84 | 14.696 | 0.074514 | 17.51 | 0.035359 |  | 4086 | 17.51 | 72.84 | 14.696 | 0.074514 | 0.035359
4087 | 72.85 | 14.696 | 0.074513 | 17.512 | 0.035363 |  | 4087 | 17.512 | 72.85 | 14.696 | 0.074513 | 0.035363
4088 | 72.86 | 14.696 | 0.074511 | 17.515 | 0.035368 |  | 4088 | 17.515 | 72.86 | 14.696 | 0.074511 | 0.035368
4089 | 72.87 | 14.696 | 0.07451 | 17.517 | 0.035372 |  | 4089 | 17.517 | 72.87 | 14.696 | 0.07451 | 0.035372
4090 | 72.88 | 14.696 | 0.074508 | 17.519 | 0.035377 |  | 4090 | 17.519 | 72.88 | 14.696 | 0.074508 | 0.035377
4091 | 72.89 | 14.696 | 0.074507 | 17.522 | 0.035381 |  | 4091 | 17.522 | 72.89 | 14.696 | 0.074507 | 0.035381
4092 | 72.9 | 14.696 | 0.074506 | 17.524 | 0.035386 |  | 4092 | 17.524 | 72.9 | 14.696 | 0.074506 | 0.035386
4093 | 72.91 | 14.696 | 0.074504 | 17.527 | 0.03539 |  | 4093 | 17.527 | 72.91 | 14.696 | 0.074504 | 0.03539
4094 | 72.92 | 14.696 | 0.074503 | 17.529 | 0.035395 |  | 4094 | 17.529 | 72.92 | 14.696 | 0.074503 | 0.035395
4095 | 72.93 | 14.696 | 0.074501 | 17.531 | 0.035399 |  | 4095 | 17.531 | 72.93 | 14.696 | 0.074501 | 0.035399
4096 | 72.94 | 14.696 | 0.0745 | 17.534 | 0.035404 |  | 4096 | 17.534 | 72.94 | 14.696 | 0.0745 | 0.035404
4097 | 72.95 | 14.696 | 0.074499 | 17.536 | 0.035409 |  | 4097 | 17.536 | 72.95 | 14.696 | 0.074499 | 0.035409
4098 | 72.96 | 14.696 | 0.074497 | 17.539 | 0.035413 |  | 4098 | 17.539 | 72.96 | 14.696 | 0.074497 | 0.035413
4099 | 72.97 | 14.696 | 0.074496 | 17.541 | 0.035418 |  | 4099 | 17.541 | 72.97 | 14.696 | 0.074496 | 0.035418
4100 | 72.98 | 14.696 | 0.074494 | 17.543 | 0.035422 |  | 4100 | 17.543 | 72.98 | 14.696 | 0.074494 | 0.035422
4101 | 72.99 | 14.696 | 0.074493 | 17.546 | 0.035427 |  | 4101 | 17.546 | 72.99 | 14.696 | 0.074493 | 0.035427
4102 | 73 | 14.696 | 0.074492 | 17.548 | 0.035431 |  | 4102 | 17.548 | 73 | 14.696 | 0.074492 | 0.035431
4103 | 73.01 | 14.696 | 0.07449 | 17.551 | 0.035436 |  | 4103 | 17.551 | 73.01 | 14.696 | 0.07449 | 0.035436
4104 | 73.02 | 14.696 | 0.074489 | 17.553 | 0.03544 |  | 4104 | 17.553 | 73.02 | 14.696 | 0.074489 | 0.03544
4105 | 73.03 | 14.696 | 0.074487 | 17.555 | 0.035445 |  | 4105 | 17.555 | 73.03 | 14.696 | 0.074487 | 0.035445
4106 | 73.04 | 14.696 | 0.074486 | 17.558 | 0.035449 |  | 4106 | 17.558 | 73.04 | 14.696 | 0.074486 | 0.035449
4107 | 73.05 | 14.696 | 0.074485 | 17.56 | 0.035454 |  | 4107 | 17.56 | 73.05 | 14.696 | 0.074485 | 0.035454
4108 | 73.06 | 14.696 | 0.074483 | 17.563 | 0.035458 |  | 4108 | 17.563 | 73.06 | 14.696 | 0.074483 | 0.035458
4109 | 73.07 | 14.696 | 0.074482 | 17.565 | 0.035463 |  | 4109 | 17.565 | 73.07 | 14.696 | 0.074482 | 0.035463
4110 | 73.08 | 14.696 | 0.07448 | 17.567 | 0.035467 |  | 4110 | 17.567 | 73.08 | 14.696 | 0.07448 | 0.035467
4111 | 73.09 | 14.696 | 0.074479 | 17.57 | 0.035472 |  | 4111 | 17.57 | 73.09 | 14.696 | 0.074479 | 0.035472
4112 | 73.1 | 14.696 | 0.074478 | 17.572 | 0.035476 |  | 4112 | 17.572 | 73.1 | 14.696 | 0.074478 | 0.035476
4113 | 73.11 | 14.696 | 0.074476 | 17.575 | 0.035481 |  | 4113 | 17.575 | 73.11 | 14.696 | 0.074476 | 0.035481
4114 | 73.12 | 14.696 | 0.074475 | 17.577 | 0.035485 |  | 4114 | 17.577 | 73.12 | 14.696 | 0.074475 | 0.035485
4115 | 73.13 | 14.696 | 0.074473 | 17.579 | 0.03549 |  | 4115 | 17.579 | 73.13 | 14.696 | 0.074473 | 0.03549
4116 | 73.14 | 14.696 | 0.074472 | 17.582 | 0.035494 |  | 4116 | 17.582 | 73.14 | 14.696 | 0.074472 | 0.035494
4117 | 73.15 | 14.696 | 0.074471 | 17.584 | 0.035499 |  | 4117 | 17.584 | 73.15 | 14.696 | 0.074471 | 0.035499
4118 | 73.16 | 14.696 | 0.074469 | 17.587 | 0.035503 |  | 4118 | 17.587 | 73.16 | 14.696 | 0.074469 | 0.035503
4119 | 73.17 | 14.696 | 0.074468 | 17.589 | 0.035508 |  | 4119 | 17.589 | 73.17 | 14.696 | 0.074468 | 0.035508
4120 | 73.18 | 14.696 | 0.074466 | 17.592 | 0.035512 |  | 4120 | 17.592 | 73.18 | 14.696 | 0.074466 | 0.035512
4121 | 73.19 | 14.696 | 0.074465 | 17.594 | 0.035517 |  | 4121 | 17.594 | 73.19 | 14.696 | 0.074465 | 0.035517
4122 | 73.2 | 14.696 | 0.074464 | 17.596 | 0.035521 |  | 4122 | 17.596 | 73.2 | 14.696 | 0.074464 | 0.035521
4123 | 73.21 | 14.696 | 0.074462 | 17.599 | 0.035526 |  | 4123 | 17.599 | 73.21 | 14.696 | 0.074462 | 0.035526
4124 | 73.22 | 14.696 | 0.074461 | 17.601 | 0.03553 |  | 4124 | 17.601 | 73.22 | 14.696 | 0.074461 | 0.03553
4125 | 73.23 | 14.696 | 0.074459 | 17.604 | 0.035535 |  | 4125 | 17.604 | 73.23 | 14.696 | 0.074459 | 0.035535
4126 | 73.24 | 14.696 | 0.074458 | 17.606 | 0.035539 |  | 4126 | 17.606 | 73.24 | 14.696 | 0.074458 | 0.035539
4127 | 73.25 | 14.696 | 0.074457 | 17.608 | 0.035544 |  | 4127 | 17.608 | 73.25 | 14.696 | 0.074457 | 0.035544
4128 | 73.26 | 14.696 | 0.074455 | 17.611 | 0.035548 |  | 4128 | 17.611 | 73.26 | 14.696 | 0.074455 | 0.035548
4129 | 73.27 | 14.696 | 0.074454 | 17.613 | 0.035553 |  | 4129 | 17.613 | 73.27 | 14.696 | 0.074454 | 0.035553
4130 | 73.28 | 14.696 | 0.074452 | 17.616 | 0.035557 |  | 4130 | 17.616 | 73.28 | 14.696 | 0.074452 | 0.035557
4131 | 73.29 | 14.696 | 0.074451 | 17.618 | 0.035562 |  | 4131 | 17.618 | 73.29 | 14.696 | 0.074451 | 0.035562
4132 | 73.3 | 14.696 | 0.07445 | 17.62 | 0.035566 |  | 4132 | 17.62 | 73.3 | 14.696 | 0.07445 | 0.035566
4133 | 73.31 | 14.696 | 0.074448 | 17.623 | 0.035571 |  | 4133 | 17.623 | 73.31 | 14.696 | 0.074448 | 0.035571
4134 | 73.32 | 14.696 | 0.074447 | 17.625 | 0.035576 |  | 4134 | 17.625 | 73.32 | 14.696 | 0.074447 | 0.035576
4135 | 73.33 | 14.696 | 0.074445 | 17.628 | 0.03558 |  | 4135 | 17.628 | 73.33 | 14.696 | 0.074445 | 0.03558
4136 | 73.34 | 14.696 | 0.074444 | 17.63 | 0.035585 |  | 4136 | 17.63 | 73.34 | 14.696 | 0.074444 | 0.035585
4137 | 73.35 | 14.696 | 0.074443 | 17.632 | 0.035589 |  | 4137 | 17.632 | 73.35 | 14.696 | 0.074443 | 0.035589
4138 | 73.36 | 14.696 | 0.074441 | 17.635 | 0.035594 |  | 4138 | 17.635 | 73.36 | 14.696 | 0.074441 | 0.035594
4139 | 73.37 | 14.696 | 0.07444 | 17.637 | 0.035598 |  | 4139 | 17.637 | 73.37 | 14.696 | 0.07444 | 0.035598
4140 | 73.38 | 14.696 | 0.074438 | 17.64 | 0.035603 |  | 4140 | 17.64 | 73.38 | 14.696 | 0.074438 | 0.035603
4141 | 73.39 | 14.696 | 0.074437 | 17.642 | 0.035607 |  | 4141 | 17.642 | 73.39 | 14.696 | 0.074437 | 0.035607
4142 | 73.4 | 14.696 | 0.074436 | 17.644 | 0.035612 |  | 4142 | 17.644 | 73.4 | 14.696 | 0.074436 | 0.035612
4143 | 73.41 | 14.696 | 0.074434 | 17.647 | 0.035616 |  | 4143 | 17.647 | 73.41 | 14.696 | 0.074434 | 0.035616
4144 | 73.42 | 14.696 | 0.074433 | 17.649 | 0.035621 |  | 4144 | 17.649 | 73.42 | 14.696 | 0.074433 | 0.035621
4145 | 73.43 | 14.696 | 0.074431 | 17.652 | 0.035625 |  | 4145 | 17.652 | 73.43 | 14.696 | 0.074431 | 0.035625
4146 | 73.44 | 14.696 | 0.07443 | 17.654 | 0.03563 |  | 4146 | 17.654 | 73.44 | 14.696 | 0.07443 | 0.03563
4147 | 73.45 | 14.696 | 0.074429 | 17.656 | 0.035634 |  | 4147 | 17.656 | 73.45 | 14.696 | 0.074429 | 0.035634
4148 | 73.46 | 14.696 | 0.074427 | 17.659 | 0.035639 |  | 4148 | 17.659 | 73.46 | 14.696 | 0.074427 | 0.035639
4149 | 73.47 | 14.696 | 0.074426 | 17.661 | 0.035643 |  | 4149 | 17.661 | 73.47 | 14.696 | 0.074426 | 0.035643
4150 | 73.48 | 14.696 | 0.074424 | 17.664 | 0.035648 |  | 4150 | 17.664 | 73.48 | 14.696 | 0.074424 | 0.035648
4151 | 73.49 | 14.696 | 0.074423 | 17.666 | 0.035652 |  | 4151 | 17.666 | 73.49 | 14.696 | 0.074423 | 0.035652
4152 | 73.5 | 14.696 | 0.074422 | 17.668 | 0.035657 |  | 4152 | 17.668 | 73.5 | 14.696 | 0.074422 | 0.035657
4153 | 73.51 | 14.696 | 0.07442 | 17.671 | 0.035661 |  | 4153 | 17.671 | 73.51 | 14.696 | 0.07442 | 0.035661
4154 | 73.52 | 14.696 | 0.074419 | 17.673 | 0.035666 |  | 4154 | 17.673 | 73.52 | 14.696 | 0.074419 | 0.035666
4155 | 73.53 | 14.696 | 0.074417 | 17.676 | 0.03567 |  | 4155 | 17.676 | 73.53 | 14.696 | 0.074417 | 0.03567
4156 | 73.54 | 14.696 | 0.074416 | 17.678 | 0.035675 |  | 4156 | 17.678 | 73.54 | 14.696 | 0.074416 | 0.035675
4157 | 73.55 | 14.696 | 0.074415 | 17.681 | 0.035679 |  | 4157 | 17.681 | 73.55 | 14.696 | 0.074415 | 0.035679
4158 | 73.56 | 14.696 | 0.074413 | 17.683 | 0.035684 |  | 4158 | 17.683 | 73.56 | 14.696 | 0.074413 | 0.035684
4159 | 73.57 | 14.696 | 0.074412 | 17.685 | 0.035688 |  | 4159 | 17.685 | 73.57 | 14.696 | 0.074412 | 0.035688
4160 | 73.58 | 14.696 | 0.07441 | 17.688 | 0.035693 |  | 4160 | 17.688 | 73.58 | 14.696 | 0.07441 | 0.035693
4161 | 73.59 | 14.696 | 0.074409 | 17.69 | 0.035697 |  | 4161 | 17.69 | 73.59 | 14.696 | 0.074409 | 0.035697
4162 | 73.6 | 14.696 | 0.074408 | 17.693 | 0.035702 |  | 4162 | 17.693 | 73.6 | 14.696 | 0.074408 | 0.035702
4163 | 73.61 | 14.696 | 0.074406 | 17.695 | 0.035706 |  | 4163 | 17.695 | 73.61 | 14.696 | 0.074406 | 0.035706
4164 | 73.62 | 14.696 | 0.074405 | 17.697 | 0.035711 |  | 4164 | 17.697 | 73.62 | 14.696 | 0.074405 | 0.035711
4165 | 73.63 | 14.696 | 0.074403 | 17.7 | 0.035715 |  | 4165 | 17.7 | 73.63 | 14.696 | 0.074403 | 0.035715
4166 | 73.64 | 14.696 | 0.074402 | 17.702 | 0.03572 |  | 4166 | 17.702 | 73.64 | 14.696 | 0.074402 | 0.03572
4167 | 73.65 | 14.696 | 0.074401 | 17.705 | 0.035724 |  | 4167 | 17.705 | 73.65 | 14.696 | 0.074401 | 0.035724
4168 | 73.66 | 14.696 | 0.074399 | 17.707 | 0.035729 |  | 4168 | 17.707 | 73.66 | 14.696 | 0.074399 | 0.035729
4169 | 73.67 | 14.696 | 0.074398 | 17.709 | 0.035733 |  | 4169 | 17.709 | 73.67 | 14.696 | 0.074398 | 0.035733
4170 | 73.68 | 14.696 | 0.074396 | 17.712 | 0.035738 |  | 4170 | 17.712 | 73.68 | 14.696 | 0.074396 | 0.035738
4171 | 73.69 | 14.696 | 0.074395 | 17.714 | 0.035742 |  | 4171 | 17.714 | 73.69 | 14.696 | 0.074395 | 0.035742
4172 | 73.7 | 14.696 | 0.074394 | 17.717 | 0.035747 |  | 4172 | 17.717 | 73.7 | 14.696 | 0.074394 | 0.035747
4173 | 73.71 | 14.696 | 0.074392 | 17.719 | 0.035751 |  | 4173 | 17.719 | 73.71 | 14.696 | 0.074392 | 0.035751
4174 | 73.72 | 14.696 | 0.074391 | 17.721 | 0.035756 |  | 4174 | 17.721 | 73.72 | 14.696 | 0.074391 | 0.035756
4175 | 73.73 | 14.696 | 0.074389 | 17.724 | 0.03576 |  | 4175 | 17.724 | 73.73 | 14.696 | 0.074389 | 0.03576
4176 | 73.74 | 14.696 | 0.074388 | 17.726 | 0.035765 |  | 4176 | 17.726 | 73.74 | 14.696 | 0.074388 | 0.035765
4177 | 73.75 | 14.696 | 0.074387 | 17.729 | 0.035769 |  | 4177 | 17.729 | 73.75 | 14.696 | 0.074387 | 0.035769
4178 | 73.76 | 14.696 | 0.074385 | 17.731 | 0.035774 |  | 4178 | 17.731 | 73.76 | 14.696 | 0.074385 | 0.035774
4179 | 73.77 | 14.696 | 0.074384 | 17.733 | 0.035778 |  | 4179 | 17.733 | 73.77 | 14.696 | 0.074384 | 0.035778
4180 | 73.78 | 14.696 | 0.074382 | 17.736 | 0.035783 |  | 4180 | 17.736 | 73.78 | 14.696 | 0.074382 | 0.035783
4181 | 73.79 | 14.696 | 0.074381 | 17.738 | 0.035788 |  | 4181 | 17.738 | 73.79 | 14.696 | 0.074381 | 0.035788
4182 | 73.8 | 14.696 | 0.07438 | 17.741 | 0.035792 |  | 4182 | 17.741 | 73.8 | 14.696 | 0.07438 | 0.035792
4183 | 73.81 | 14.696 | 0.074378 | 17.743 | 0.035797 |  | 4183 | 17.743 | 73.81 | 14.696 | 0.074378 | 0.035797
4184 | 73.82 | 14.696 | 0.074377 | 17.745 | 0.035801 |  | 4184 | 17.745 | 73.82 | 14.696 | 0.074377 | 0.035801
4185 | 73.83 | 14.696 | 0.074375 | 17.748 | 0.035806 |  | 4185 | 17.748 | 73.83 | 14.696 | 0.074375 | 0.035806
4186 | 73.84 | 14.696 | 0.074374 | 17.75 | 0.03581 |  | 4186 | 17.75 | 73.84 | 14.696 | 0.074374 | 0.03581
4187 | 73.85 | 14.696 | 0.074373 | 17.753 | 0.035815 |  | 4187 | 17.753 | 73.85 | 14.696 | 0.074373 | 0.035815
4188 | 73.86 | 14.696 | 0.074371 | 17.755 | 0.035819 |  | 4188 | 17.755 | 73.86 | 14.696 | 0.074371 | 0.035819
4189 | 73.87 | 14.696 | 0.07437 | 17.757 | 0.035824 |  | 4189 | 17.757 | 73.87 | 14.696 | 0.07437 | 0.035824
4190 | 73.88 | 14.696 | 0.074368 | 17.76 | 0.035828 |  | 4190 | 17.76 | 73.88 | 14.696 | 0.074368 | 0.035828
4191 | 73.89 | 14.696 | 0.074367 | 17.762 | 0.035833 |  | 4191 | 17.762 | 73.89 | 14.696 | 0.074367 | 0.035833
4192 | 73.9 | 14.696 | 0.074366 | 17.765 | 0.035837 |  | 4192 | 17.765 | 73.9 | 14.696 | 0.074366 | 0.035837
4193 | 73.91 | 14.696 | 0.074364 | 17.767 | 0.035842 |  | 4193 | 17.767 | 73.91 | 14.696 | 0.074364 | 0.035842
4194 | 73.92 | 14.696 | 0.074363 | 17.769 | 0.035846 |  | 4194 | 17.769 | 73.92 | 14.696 | 0.074363 | 0.035846
4195 | 73.93 | 14.696 | 0.074361 | 17.772 | 0.035851 |  | 4195 | 17.772 | 73.93 | 14.696 | 0.074361 | 0.035851
4196 | 73.94 | 14.696 | 0.07436 | 17.774 | 0.035855 |  | 4196 | 17.774 | 73.94 | 14.696 | 0.07436 | 0.035855
4197 | 73.95 | 14.696 | 0.074359 | 17.777 | 0.03586 |  | 4197 | 17.777 | 73.95 | 14.696 | 0.074359 | 0.03586
4198 | 73.96 | 14.696 | 0.074357 | 17.779 | 0.035864 |  | 4198 | 17.779 | 73.96 | 14.696 | 0.074357 | 0.035864
4199 | 73.97 | 14.696 | 0.074356 | 17.782 | 0.035869 |  | 4199 | 17.782 | 73.97 | 14.696 | 0.074356 | 0.035869
4200 | 73.98 | 14.696 | 0.074354 | 17.784 | 0.035873 |  | 4200 | 17.784 | 73.98 | 14.696 | 0.074354 | 0.035873
4201 | 73.99 | 14.696 | 0.074353 | 17.786 | 0.035878 |  | 4201 | 17.786 | 73.99 | 14.696 | 0.074353 | 0.035878
4202 | 74 | 14.696 | 0.074352 | 17.789 | 0.035882 |  | 4202 | 17.789 | 74 | 14.696 | 0.074352 | 0.035882
4203 | 74.01 | 14.696 | 0.07435 | 17.791 | 0.035887 |  | 4203 | 17.791 | 74.01 | 14.696 | 0.07435 | 0.035887
4204 | 74.02 | 14.696 | 0.074349 | 17.794 | 0.035891 |  | 4204 | 17.794 | 74.02 | 14.696 | 0.074349 | 0.035891
4205 | 74.03 | 14.696 | 0.074347 | 17.796 | 0.035896 |  | 4205 | 17.796 | 74.03 | 14.696 | 0.074347 | 0.035896
4206 | 74.04 | 14.696 | 0.074346 | 17.798 | 0.0359 |  | 4206 | 17.798 | 74.04 | 14.696 | 0.074346 | 0.0359
4207 | 74.05 | 14.696 | 0.074345 | 17.801 | 0.035905 |  | 4207 | 17.801 | 74.05 | 14.696 | 0.074345 | 0.035905
4208 | 74.06 | 14.696 | 0.074343 | 17.803 | 0.035909 |  | 4208 | 17.803 | 74.06 | 14.696 | 0.074343 | 0.035909
4209 | 74.07 | 14.696 | 0.074342 | 17.806 | 0.035914 |  | 4209 | 17.806 | 74.07 | 14.696 | 0.074342 | 0.035914
4210 | 74.08 | 14.696 | 0.07434 | 17.808 | 0.035918 |  | 4210 | 17.808 | 74.08 | 14.696 | 0.07434 | 0.035918
4211 | 74.09 | 14.696 | 0.074339 | 17.81 | 0.035923 |  | 4211 | 17.81 | 74.09 | 14.696 | 0.074339 | 0.035923
4212 | 74.1 | 14.696 | 0.074338 | 17.813 | 0.035927 |  | 4212 | 17.813 | 74.1 | 14.696 | 0.074338 | 0.035927
4213 | 74.11 | 14.696 | 0.074336 | 17.815 | 0.035932 |  | 4213 | 17.815 | 74.11 | 14.696 | 0.074336 | 0.035932
4214 | 74.12 | 14.696 | 0.074335 | 17.818 | 0.035936 |  | 4214 | 17.818 | 74.12 | 14.696 | 0.074335 | 0.035936
4215 | 74.13 | 14.696 | 0.074333 | 17.82 | 0.035941 |  | 4215 | 17.82 | 74.13 | 14.696 | 0.074333 | 0.035941
4216 | 74.14 | 14.696 | 0.074332 | 17.822 | 0.035945 |  | 4216 | 17.822 | 74.14 | 14.696 | 0.074332 | 0.035945
4217 | 74.15 | 14.696 | 0.074331 | 17.825 | 0.03595 |  | 4217 | 17.825 | 74.15 | 14.696 | 0.074331 | 0.03595
4218 | 74.16 | 14.696 | 0.074329 | 17.827 | 0.035954 |  | 4218 | 17.827 | 74.16 | 14.696 | 0.074329 | 0.035954
4219 | 74.17 | 14.696 | 0.074328 | 17.83 | 0.035959 |  | 4219 | 17.83 | 74.17 | 14.696 | 0.074328 | 0.035959
4220 | 74.18 | 14.696 | 0.074326 | 17.832 | 0.035963 |  | 4220 | 17.832 | 74.18 | 14.696 | 0.074326 | 0.035963
4221 | 74.19 | 14.696 | 0.074325 | 17.834 | 0.035968 |  | 4221 | 17.834 | 74.19 | 14.696 | 0.074325 | 0.035968
4222 | 74.2 | 14.696 | 0.074324 | 17.837 | 0.035972 |  | 4222 | 17.837 | 74.2 | 14.696 | 0.074324 | 0.035972
4223 | 74.21 | 14.696 | 0.074322 | 17.839 | 0.035977 |  | 4223 | 17.839 | 74.21 | 14.696 | 0.074322 | 0.035977
4224 | 74.22 | 14.696 | 0.074321 | 17.842 | 0.035981 |  | 4224 | 17.842 | 74.22 | 14.696 | 0.074321 | 0.035981
4225 | 74.23 | 14.696 | 0.074319 | 17.844 | 0.035986 |  | 4225 | 17.844 | 74.23 | 14.696 | 0.074319 | 0.035986
4226 | 74.24 | 14.696 | 0.074318 | 17.846 | 0.03599 |  | 4226 | 17.846 | 74.24 | 14.696 | 0.074318 | 0.03599
4227 | 74.25 | 14.696 | 0.074317 | 17.849 | 0.035995 |  | 4227 | 17.849 | 74.25 | 14.696 | 0.074317 | 0.035995
4228 | 74.26 | 14.696 | 0.074315 | 17.851 | 0.035999 |  | 4228 | 17.851 | 74.26 | 14.696 | 0.074315 | 0.035999
4229 | 74.27 | 14.696 | 0.074314 | 17.854 | 0.036004 |  | 4229 | 17.854 | 74.27 | 14.696 | 0.074314 | 0.036004
4230 | 74.28 | 14.696 | 0.074313 | 17.856 | 0.036008 |  | 4230 | 17.856 | 74.28 | 14.696 | 0.074313 | 0.036008
4231 | 74.29 | 14.696 | 0.074311 | 17.858 | 0.036013 |  | 4231 | 17.858 | 74.29 | 14.696 | 0.074311 | 0.036013
4232 | 74.3 | 14.696 | 0.07431 | 17.861 | 0.036017 |  | 4232 | 17.861 | 74.3 | 14.696 | 0.07431 | 0.036017
4233 | 74.31 | 14.696 | 0.074308 | 17.863 | 0.036022 |  | 4233 | 17.863 | 74.31 | 14.696 | 0.074308 | 0.036022
4234 | 74.32 | 14.696 | 0.074307 | 17.866 | 0.036026 |  | 4234 | 17.866 | 74.32 | 14.696 | 0.074307 | 0.036026
4235 | 74.33 | 14.696 | 0.074306 | 17.868 | 0.036031 |  | 4235 | 17.868 | 74.33 | 14.696 | 0.074306 | 0.036031
4236 | 74.34 | 14.696 | 0.074304 | 17.871 | 0.036035 |  | 4236 | 17.871 | 74.34 | 14.696 | 0.074304 | 0.036035
4237 | 74.35 | 14.696 | 0.074303 | 17.873 | 0.03604 |  | 4237 | 17.873 | 74.35 | 14.696 | 0.074303 | 0.03604
4238 | 74.36 | 14.696 | 0.074301 | 17.875 | 0.036044 |  | 4238 | 17.875 | 74.36 | 14.696 | 0.074301 | 0.036044
4239 | 74.37 | 14.696 | 0.0743 | 17.878 | 0.036049 |  | 4239 | 17.878 | 74.37 | 14.696 | 0.0743 | 0.036049
4240 | 74.38 | 14.696 | 0.074299 | 17.88 | 0.036053 |  | 4240 | 17.88 | 74.38 | 14.696 | 0.074299 | 0.036053
4241 | 74.39 | 14.696 | 0.074297 | 17.883 | 0.036058 |  | 4241 | 17.883 | 74.39 | 14.696 | 0.074297 | 0.036058
4242 | 74.4 | 14.696 | 0.074296 | 17.885 | 0.036062 |  | 4242 | 17.885 | 74.4 | 14.696 | 0.074296 | 0.036062
4243 | 74.41 | 14.696 | 0.074294 | 17.887 | 0.036067 |  | 4243 | 17.887 | 74.41 | 14.696 | 0.074294 | 0.036067
4244 | 74.42 | 14.696 | 0.074293 | 17.89 | 0.036071 |  | 4244 | 17.89 | 74.42 | 14.696 | 0.074293 | 0.036071
4245 | 74.43 | 14.696 | 0.074292 | 17.892 | 0.036076 |  | 4245 | 17.892 | 74.43 | 14.696 | 0.074292 | 0.036076
4246 | 74.44 | 14.696 | 0.07429 | 17.895 | 0.03608 |  | 4246 | 17.895 | 74.44 | 14.696 | 0.07429 | 0.03608
4247 | 74.45 | 14.696 | 0.074289 | 17.897 | 0.036085 |  | 4247 | 17.897 | 74.45 | 14.696 | 0.074289 | 0.036085
4248 | 74.46 | 14.696 | 0.074287 | 17.899 | 0.036089 |  | 4248 | 17.899 | 74.46 | 14.696 | 0.074287 | 0.036089
4249 | 74.47 | 14.696 | 0.074286 | 17.902 | 0.036094 |  | 4249 | 17.902 | 74.47 | 14.696 | 0.074286 | 0.036094
4250 | 74.48 | 14.696 | 0.074285 | 17.904 | 0.036098 |  | 4250 | 17.904 | 74.48 | 14.696 | 0.074285 | 0.036098
4251 | 74.49 | 14.696 | 0.074283 | 17.907 | 0.036103 |  | 4251 | 17.907 | 74.49 | 14.696 | 0.074283 | 0.036103
4252 | 74.5 | 14.696 | 0.074282 | 17.909 | 0.036107 |  | 4252 | 17.909 | 74.5 | 14.696 | 0.074282 | 0.036107
4253 | 74.51 | 14.696 | 0.07428 | 17.911 | 0.036112 |  | 4253 | 17.911 | 74.51 | 14.696 | 0.07428 | 0.036112
4254 | 74.52 | 14.696 | 0.074279 | 17.914 | 0.036116 |  | 4254 | 17.914 | 74.52 | 14.696 | 0.074279 | 0.036116
4255 | 74.53 | 14.696 | 0.074278 | 17.916 | 0.036121 |  | 4255 | 17.916 | 74.53 | 14.696 | 0.074278 | 0.036121
4256 | 74.54 | 14.696 | 0.074276 | 17.919 | 0.036125 |  | 4256 | 17.919 | 74.54 | 14.696 | 0.074276 | 0.036125
4257 | 74.55 | 14.696 | 0.074275 | 17.921 | 0.03613 |  | 4257 | 17.921 | 74.55 | 14.696 | 0.074275 | 0.03613
4258 | 74.56 | 14.696 | 0.074273 | 17.923 | 0.036134 |  | 4258 | 17.923 | 74.56 | 14.696 | 0.074273 | 0.036134
4259 | 74.57 | 14.696 | 0.074272 | 17.926 | 0.036139 |  | 4259 | 17.926 | 74.57 | 14.696 | 0.074272 | 0.036139
4260 | 74.58 | 14.696 | 0.074271 | 17.928 | 0.036143 |  | 4260 | 17.928 | 74.58 | 14.696 | 0.074271 | 0.036143
4261 | 74.59 | 14.696 | 0.074269 | 17.931 | 0.036148 |  | 4261 | 17.931 | 74.59 | 14.696 | 0.074269 | 0.036148
4262 | 74.6 | 14.696 | 0.074268 | 17.933 | 0.036152 |  | 4262 | 17.933 | 74.6 | 14.696 | 0.074268 | 0.036152
4263 | 74.61 | 14.696 | 0.074266 | 17.935 | 0.036157 |  | 4263 | 17.935 | 74.61 | 14.696 | 0.074266 | 0.036157
4264 | 74.62 | 14.696 | 0.074265 | 17.938 | 0.036161 |  | 4264 | 17.938 | 74.62 | 14.696 | 0.074265 | 0.036161
4265 | 74.63 | 14.696 | 0.074264 | 17.94 | 0.036166 |  | 4265 | 17.94 | 74.63 | 14.696 | 0.074264 | 0.036166
4266 | 74.64 | 14.696 | 0.074262 | 17.943 | 0.03617 |  | 4266 | 17.943 | 74.64 | 14.696 | 0.074262 | 0.03617
4267 | 74.65 | 14.696 | 0.074261 | 17.945 | 0.036175 |  | 4267 | 17.945 | 74.65 | 14.696 | 0.074261 | 0.036175
4268 | 74.66 | 14.696 | 0.07426 | 17.947 | 0.036179 |  | 4268 | 17.947 | 74.66 | 14.696 | 0.07426 | 0.036179
4269 | 74.67 | 14.696 | 0.074258 | 17.95 | 0.036184 |  | 4269 | 17.95 | 74.67 | 14.696 | 0.074258 | 0.036184
4270 | 74.68 | 14.696 | 0.074257 | 17.952 | 0.036188 |  | 4270 | 17.952 | 74.68 | 14.696 | 0.074257 | 0.036188
4271 | 74.69 | 14.696 | 0.074255 | 17.955 | 0.036193 |  | 4271 | 17.955 | 74.69 | 14.696 | 0.074255 | 0.036193
4272 | 74.7 | 14.696 | 0.074254 | 17.957 | 0.036197 |  | 4272 | 17.957 | 74.7 | 14.696 | 0.074254 | 0.036197
4273 | 74.71 | 14.696 | 0.074253 | 17.959 | 0.036202 |  | 4273 | 17.959 | 74.71 | 14.696 | 0.074253 | 0.036202
4274 | 74.72 | 14.696 | 0.074251 | 17.962 | 0.036206 |  | 4274 | 17.962 | 74.72 | 14.696 | 0.074251 | 0.036206
4275 | 74.73 | 14.696 | 0.07425 | 17.964 | 0.036211 |  | 4275 | 17.964 | 74.73 | 14.696 | 0.07425 | 0.036211
4276 | 74.74 | 14.696 | 0.074248 | 17.967 | 0.036215 |  | 4276 | 17.967 | 74.74 | 14.696 | 0.074248 | 0.036215
4277 | 74.75 | 14.696 | 0.074247 | 17.969 | 0.03622 |  | 4277 | 17.969 | 74.75 | 14.696 | 0.074247 | 0.03622
4278 | 74.76 | 14.696 | 0.074246 | 17.972 | 0.036224 |  | 4278 | 17.972 | 74.76 | 14.696 | 0.074246 | 0.036224
4279 | 74.77 | 14.696 | 0.074244 | 17.974 | 0.036229 |  | 4279 | 17.974 | 74.77 | 14.696 | 0.074244 | 0.036229
4280 | 74.78 | 14.696 | 0.074243 | 17.976 | 0.036233 |  | 4280 | 17.976 | 74.78 | 14.696 | 0.074243 | 0.036233
4281 | 74.79 | 14.696 | 0.074241 | 17.979 | 0.036238 |  | 4281 | 17.979 | 74.79 | 14.696 | 0.074241 | 0.036238
4282 | 74.8 | 14.696 | 0.07424 | 17.981 | 0.036242 |  | 4282 | 17.981 | 74.8 | 14.696 | 0.07424 | 0.036242
4283 | 74.81 | 14.696 | 0.074239 | 17.984 | 0.036247 |  | 4283 | 17.984 | 74.81 | 14.696 | 0.074239 | 0.036247
4284 | 74.82 | 14.696 | 0.074237 | 17.986 | 0.036251 |  | 4284 | 17.986 | 74.82 | 14.696 | 0.074237 | 0.036251
4285 | 74.83 | 14.696 | 0.074236 | 17.988 | 0.036256 |  | 4285 | 17.988 | 74.83 | 14.696 | 0.074236 | 0.036256
4286 | 74.84 | 14.696 | 0.074234 | 17.991 | 0.03626 |  | 4286 | 17.991 | 74.84 | 14.696 | 0.074234 | 0.03626
4287 | 74.85 | 14.696 | 0.074233 | 17.993 | 0.036265 |  | 4287 | 17.993 | 74.85 | 14.696 | 0.074233 | 0.036265
4288 | 74.86 | 14.696 | 0.074232 | 17.996 | 0.036269 |  | 4288 | 17.996 | 74.86 | 14.696 | 0.074232 | 0.036269
4289 | 74.87 | 14.696 | 0.07423 | 17.998 | 0.036274 |  | 4289 | 17.998 | 74.87 | 14.696 | 0.07423 | 0.036274
4290 | 74.88 | 14.696 | 0.074229 | 18 | 0.036278 |  | 4290 | 18 | 74.88 | 14.696 | 0.074229 | 0.036278
4291 | 74.89 | 14.696 | 0.074227 | 18.003 | 0.036283 |  | 4291 | 18.003 | 74.89 | 14.696 | 0.074227 | 0.036283
4292 | 74.9 | 14.696 | 0.074226 | 18.005 | 0.036287 |  | 4292 | 18.005 | 74.9 | 14.696 | 0.074226 | 0.036287
4293 | 74.91 | 14.696 | 0.074225 | 18.008 | 0.036292 |  | 4293 | 18.008 | 74.91 | 14.696 | 0.074225 | 0.036292
4294 | 74.92 | 14.696 | 0.074223 | 18.01 | 0.036296 |  | 4294 | 18.01 | 74.92 | 14.696 | 0.074223 | 0.036296
4295 | 74.93 | 14.696 | 0.074222 | 18.012 | 0.036301 |  | 4295 | 18.012 | 74.93 | 14.696 | 0.074222 | 0.036301
4296 | 74.94 | 14.696 | 0.074221 | 18.015 | 0.036305 |  | 4296 | 18.015 | 74.94 | 14.696 | 0.074221 | 0.036305
4297 | 74.95 | 14.696 | 0.074219 | 18.017 | 0.03631 |  | 4297 | 18.017 | 74.95 | 14.696 | 0.074219 | 0.03631
4298 | 74.96 | 14.696 | 0.074218 | 18.02 | 0.036314 |  | 4298 | 18.02 | 74.96 | 14.696 | 0.074218 | 0.036314
4299 | 74.97 | 14.696 | 0.074216 | 18.022 | 0.036319 |  | 4299 | 18.022 | 74.97 | 14.696 | 0.074216 | 0.036319
4300 | 74.98 | 14.696 | 0.074215 | 18.024 | 0.036323 |  | 4300 | 18.024 | 74.98 | 14.696 | 0.074215 | 0.036323
4301 | 74.99 | 14.696 | 0.074214 | 18.027 | 0.036328 |  | 4301 | 18.027 | 74.99 | 14.696 | 0.074214 | 0.036328
4302 | 75 | 14.696 | 0.074212 | 18.029 | 0.036332 |  | 4302 | 18.029 | 75 | 14.696 | 0.074212 | 0.036332
4303 | 75.01 | 14.696 | 0.074211 | 18.032 | 0.036337 |  | 4303 | 18.032 | 75.01 | 14.696 | 0.074211 | 0.036337
4304 | 75.02 | 14.696 | 0.074209 | 18.034 | 0.036341 |  | 4304 | 18.034 | 75.02 | 14.696 | 0.074209 | 0.036341
4305 | 75.03 | 14.696 | 0.074208 | 18.036 | 0.036346 |  | 4305 | 18.036 | 75.03 | 14.696 | 0.074208 | 0.036346
4306 | 75.04 | 14.696 | 0.074207 | 18.039 | 0.03635 |  | 4306 | 18.039 | 75.04 | 14.696 | 0.074207 | 0.03635
4307 | 75.05 | 14.696 | 0.074205 | 18.041 | 0.036355 |  | 4307 | 18.041 | 75.05 | 14.696 | 0.074205 | 0.036355
4308 | 75.06 | 14.696 | 0.074204 | 18.044 | 0.036359 |  | 4308 | 18.044 | 75.06 | 14.696 | 0.074204 | 0.036359
4309 | 75.07 | 14.696 | 0.074202 | 18.046 | 0.036364 |  | 4309 | 18.046 | 75.07 | 14.696 | 0.074202 | 0.036364
4310 | 75.08 | 14.696 | 0.074201 | 18.048 | 0.036368 |  | 4310 | 18.048 | 75.08 | 14.696 | 0.074201 | 0.036368
4311 | 75.09 | 14.696 | 0.0742 | 18.051 | 0.036373 |  | 4311 | 18.051 | 75.09 | 14.696 | 0.0742 | 0.036373
4312 | 75.1 | 14.696 | 0.074198 | 18.053 | 0.036377 |  | 4312 | 18.053 | 75.1 | 14.696 | 0.074198 | 0.036377
4313 | 75.11 | 14.696 | 0.074197 | 18.056 | 0.036382 |  | 4313 | 18.056 | 75.11 | 14.696 | 0.074197 | 0.036382
4314 | 75.12 | 14.696 | 0.074195 | 18.058 | 0.036386 |  | 4314 | 18.058 | 75.12 | 14.696 | 0.074195 | 0.036386
4315 | 75.13 | 14.696 | 0.074194 | 18.06 | 0.036391 |  | 4315 | 18.06 | 75.13 | 14.696 | 0.074194 | 0.036391
4316 | 75.14 | 14.696 | 0.074193 | 18.063 | 0.036395 |  | 4316 | 18.063 | 75.14 | 14.696 | 0.074193 | 0.036395
4317 | 75.15 | 14.696 | 0.074191 | 18.065 | 0.0364 |  | 4317 | 18.065 | 75.15 | 14.696 | 0.074191 | 0.0364
4318 | 75.16 | 14.696 | 0.07419 | 18.068 | 0.036404 |  | 4318 | 18.068 | 75.16 | 14.696 | 0.07419 | 0.036404
4319 | 75.17 | 14.696 | 0.074189 | 18.07 | 0.036409 |  | 4319 | 18.07 | 75.17 | 14.696 | 0.074189 | 0.036409
4320 | 75.18 | 14.696 | 0.074187 | 18.073 | 0.036413 |  | 4320 | 18.073 | 75.18 | 14.696 | 0.074187 | 0.036413
4321 | 75.19 | 14.696 | 0.074186 | 18.075 | 0.036418 |  | 4321 | 18.075 | 75.19 | 14.696 | 0.074186 | 0.036418
4322 | 75.2 | 14.696 | 0.074184 | 18.077 | 0.036422 |  | 4322 | 18.077 | 75.2 | 14.696 | 0.074184 | 0.036422
4323 | 75.21 | 14.696 | 0.074183 | 18.08 | 0.036427 |  | 4323 | 18.08 | 75.21 | 14.696 | 0.074183 | 0.036427
4324 | 75.22 | 14.696 | 0.074182 | 18.082 | 0.036431 |  | 4324 | 18.082 | 75.22 | 14.696 | 0.074182 | 0.036431
4325 | 75.23 | 14.696 | 0.07418 | 18.085 | 0.036436 |  | 4325 | 18.085 | 75.23 | 14.696 | 0.07418 | 0.036436
4326 | 75.24 | 14.696 | 0.074179 | 18.087 | 0.03644 |  | 4326 | 18.087 | 75.24 | 14.696 | 0.074179 | 0.03644
4327 | 75.25 | 14.696 | 0.074177 | 18.089 | 0.036445 |  | 4327 | 18.089 | 75.25 | 14.696 | 0.074177 | 0.036445
4328 | 75.26 | 14.696 | 0.074176 | 18.092 | 0.036449 |  | 4328 | 18.092 | 75.26 | 14.696 | 0.074176 | 0.036449
4329 | 75.27 | 14.696 | 0.074175 | 18.094 | 0.036454 |  | 4329 | 18.094 | 75.27 | 14.696 | 0.074175 | 0.036454
4330 | 75.28 | 14.696 | 0.074173 | 18.097 | 0.036458 |  | 4330 | 18.097 | 75.28 | 14.696 | 0.074173 | 0.036458
4331 | 75.29 | 14.696 | 0.074172 | 18.099 | 0.036463 |  | 4331 | 18.099 | 75.29 | 14.696 | 0.074172 | 0.036463
4332 | 75.3 | 14.696 | 0.07417 | 18.101 | 0.036467 |  | 4332 | 18.101 | 75.3 | 14.696 | 0.07417 | 0.036467
4333 | 75.31 | 14.696 | 0.074169 | 18.104 | 0.036472 |  | 4333 | 18.104 | 75.31 | 14.696 | 0.074169 | 0.036472
4334 | 75.32 | 14.696 | 0.074168 | 18.106 | 0.036476 |  | 4334 | 18.106 | 75.32 | 14.696 | 0.074168 | 0.036476
4335 | 75.33 | 14.696 | 0.074166 | 18.109 | 0.036481 |  | 4335 | 18.109 | 75.33 | 14.696 | 0.074166 | 0.036481
4336 | 75.34 | 14.696 | 0.074165 | 18.111 | 0.036485 |  | 4336 | 18.111 | 75.34 | 14.696 | 0.074165 | 0.036485
4337 | 75.35 | 14.696 | 0.074163 | 18.113 | 0.03649 |  | 4337 | 18.113 | 75.35 | 14.696 | 0.074163 | 0.03649
4338 | 75.36 | 14.696 | 0.074162 | 18.116 | 0.036494 |  | 4338 | 18.116 | 75.36 | 14.696 | 0.074162 | 0.036494
4339 | 75.37 | 14.696 | 0.074161 | 18.118 | 0.036499 |  | 4339 | 18.118 | 75.37 | 14.696 | 0.074161 | 0.036499
4340 | 75.38 | 14.696 | 0.074159 | 18.121 | 0.036503 |  | 4340 | 18.121 | 75.38 | 14.696 | 0.074159 | 0.036503
4341 | 75.39 | 14.696 | 0.074158 | 18.123 | 0.036508 |  | 4341 | 18.123 | 75.39 | 14.696 | 0.074158 | 0.036508
4342 | 75.4 | 14.696 | 0.074157 | 18.125 | 0.036512 |  | 4342 | 18.125 | 75.4 | 14.696 | 0.074157 | 0.036512
4343 | 75.41 | 14.696 | 0.074155 | 18.128 | 0.036517 |  | 4343 | 18.128 | 75.41 | 14.696 | 0.074155 | 0.036517
4344 | 75.42 | 14.696 | 0.074154 | 18.13 | 0.036521 |  | 4344 | 18.13 | 75.42 | 14.696 | 0.074154 | 0.036521
4345 | 75.43 | 14.696 | 0.074152 | 18.133 | 0.036526 |  | 4345 | 18.133 | 75.43 | 14.696 | 0.074152 | 0.036526
4346 | 75.44 | 14.696 | 0.074151 | 18.135 | 0.03653 |  | 4346 | 18.135 | 75.44 | 14.696 | 0.074151 | 0.03653
4347 | 75.45 | 14.696 | 0.07415 | 18.137 | 0.036535 |  | 4347 | 18.137 | 75.45 | 14.696 | 0.07415 | 0.036535
4348 | 75.46 | 14.696 | 0.074148 | 18.14 | 0.036539 |  | 4348 | 18.14 | 75.46 | 14.696 | 0.074148 | 0.036539
4349 | 75.47 | 14.696 | 0.074147 | 18.142 | 0.036544 |  | 4349 | 18.142 | 75.47 | 14.696 | 0.074147 | 0.036544
4350 | 75.48 | 14.696 | 0.074145 | 18.145 | 0.036548 |  | 4350 | 18.145 | 75.48 | 14.696 | 0.074145 | 0.036548
4351 | 75.49 | 14.696 | 0.074144 | 18.147 | 0.036553 |  | 4351 | 18.147 | 75.49 | 14.696 | 0.074144 | 0.036553
4352 | 75.5 | 14.696 | 0.074143 | 18.149 | 0.036557 |  | 4352 | 18.149 | 75.5 | 14.696 | 0.074143 | 0.036557
4353 | 75.51 | 14.696 | 0.074141 | 18.152 | 0.036562 |  | 4353 | 18.152 | 75.51 | 14.696 | 0.074141 | 0.036562
4354 | 75.52 | 14.696 | 0.07414 | 18.154 | 0.036566 |  | 4354 | 18.154 | 75.52 | 14.696 | 0.07414 | 0.036566
4355 | 75.53 | 14.696 | 0.074138 | 18.157 | 0.036571 |  | 4355 | 18.157 | 75.53 | 14.696 | 0.074138 | 0.036571
4356 | 75.54 | 14.696 | 0.074137 | 18.159 | 0.036575 |  | 4356 | 18.159 | 75.54 | 14.696 | 0.074137 | 0.036575
4357 | 75.55 | 14.696 | 0.074136 | 18.162 | 0.03658 |  | 4357 | 18.162 | 75.55 | 14.696 | 0.074136 | 0.03658
4358 | 75.56 | 14.696 | 0.074134 | 18.164 | 0.036584 |  | 4358 | 18.164 | 75.56 | 14.696 | 0.074134 | 0.036584
4359 | 75.57 | 14.696 | 0.074133 | 18.166 | 0.036589 |  | 4359 | 18.166 | 75.57 | 14.696 | 0.074133 | 0.036589
4360 | 75.58 | 14.696 | 0.074132 | 18.169 | 0.036593 |  | 4360 | 18.169 | 75.58 | 14.696 | 0.074132 | 0.036593
4361 | 75.59 | 14.696 | 0.07413 | 18.171 | 0.036598 |  | 4361 | 18.171 | 75.59 | 14.696 | 0.07413 | 0.036598
4362 | 75.6 | 14.696 | 0.074129 | 18.174 | 0.036602 |  | 4362 | 18.174 | 75.6 | 14.696 | 0.074129 | 0.036602
4363 | 75.61 | 14.696 | 0.074127 | 18.176 | 0.036607 |  | 4363 | 18.176 | 75.61 | 14.696 | 0.074127 | 0.036607
4364 | 75.62 | 14.696 | 0.074126 | 18.178 | 0.036611 |  | 4364 | 18.178 | 75.62 | 14.696 | 0.074126 | 0.036611
4365 | 75.63 | 14.696 | 0.074125 | 18.181 | 0.036616 |  | 4365 | 18.181 | 75.63 | 14.696 | 0.074125 | 0.036616
4366 | 75.64 | 14.696 | 0.074123 | 18.183 | 0.03662 |  | 4366 | 18.183 | 75.64 | 14.696 | 0.074123 | 0.03662
4367 | 75.65 | 14.696 | 0.074122 | 18.186 | 0.036625 |  | 4367 | 18.186 | 75.65 | 14.696 | 0.074122 | 0.036625
4368 | 75.66 | 14.696 | 0.07412 | 18.188 | 0.036629 |  | 4368 | 18.188 | 75.66 | 14.696 | 0.07412 | 0.036629
4369 | 75.67 | 14.696 | 0.074119 | 18.19 | 0.036634 |  | 4369 | 18.19 | 75.67 | 14.696 | 0.074119 | 0.036634
4370 | 75.68 | 14.696 | 0.074118 | 18.193 | 0.036638 |  | 4370 | 18.193 | 75.68 | 14.696 | 0.074118 | 0.036638
4371 | 75.69 | 14.696 | 0.074116 | 18.195 | 0.036643 |  | 4371 | 18.195 | 75.69 | 14.696 | 0.074116 | 0.036643
4372 | 75.7 | 14.696 | 0.074115 | 18.198 | 0.036647 |  | 4372 | 18.198 | 75.7 | 14.696 | 0.074115 | 0.036647
4373 | 75.71 | 14.696 | 0.074113 | 18.2 | 0.036652 |  | 4373 | 18.2 | 75.71 | 14.696 | 0.074113 | 0.036652
4374 | 75.72 | 14.696 | 0.074112 | 18.202 | 0.036656 |  | 4374 | 18.202 | 75.72 | 14.696 | 0.074112 | 0.036656
4375 | 75.73 | 14.696 | 0.074111 | 18.205 | 0.036661 |  | 4375 | 18.205 | 75.73 | 14.696 | 0.074111 | 0.036661
4376 | 75.74 | 14.696 | 0.074109 | 18.207 | 0.036665 |  | 4376 | 18.207 | 75.74 | 14.696 | 0.074109 | 0.036665
4377 | 75.75 | 14.696 | 0.074108 | 18.21 | 0.03667 |  | 4377 | 18.21 | 75.75 | 14.696 | 0.074108 | 0.03667
4378 | 75.76 | 14.696 | 0.074107 | 18.212 | 0.036674 |  | 4378 | 18.212 | 75.76 | 14.696 | 0.074107 | 0.036674
4379 | 75.77 | 14.696 | 0.074105 | 18.214 | 0.036679 |  | 4379 | 18.214 | 75.77 | 14.696 | 0.074105 | 0.036679
4380 | 75.78 | 14.696 | 0.074104 | 18.217 | 0.036683 |  | 4380 | 18.217 | 75.78 | 14.696 | 0.074104 | 0.036683
4381 | 75.79 | 14.696 | 0.074102 | 18.219 | 0.036687 |  | 4381 | 18.219 | 75.79 | 14.696 | 0.074102 | 0.036687
4382 | 75.8 | 14.696 | 0.074101 | 18.222 | 0.036692 |  | 4382 | 18.222 | 75.8 | 14.696 | 0.074101 | 0.036692
4383 | 75.81 | 14.696 | 0.0741 | 18.224 | 0.036696 |  | 4383 | 18.224 | 75.81 | 14.696 | 0.0741 | 0.036696
4384 | 75.82 | 14.696 | 0.074098 | 18.226 | 0.036701 |  | 4384 | 18.226 | 75.82 | 14.696 | 0.074098 | 0.036701
4385 | 75.83 | 14.696 | 0.074097 | 18.229 | 0.036705 |  | 4385 | 18.229 | 75.83 | 14.696 | 0.074097 | 0.036705
4386 | 75.84 | 14.696 | 0.074095 | 18.231 | 0.03671 |  | 4386 | 18.231 | 75.84 | 14.696 | 0.074095 | 0.03671
4387 | 75.85 | 14.696 | 0.074094 | 18.234 | 0.036714 |  | 4387 | 18.234 | 75.85 | 14.696 | 0.074094 | 0.036714
4388 | 75.86 | 14.696 | 0.074093 | 18.236 | 0.036719 |  | 4388 | 18.236 | 75.86 | 14.696 | 0.074093 | 0.036719
4389 | 75.87 | 14.696 | 0.074091 | 18.238 | 0.036723 |  | 4389 | 18.238 | 75.87 | 14.696 | 0.074091 | 0.036723
4390 | 75.88 | 14.696 | 0.07409 | 18.241 | 0.036728 |  | 4390 | 18.241 | 75.88 | 14.696 | 0.07409 | 0.036728
4391 | 75.89 | 14.696 | 0.074089 | 18.243 | 0.036732 |  | 4391 | 18.243 | 75.89 | 14.696 | 0.074089 | 0.036732
4392 | 75.9 | 14.696 | 0.074087 | 18.246 | 0.036737 |  | 4392 | 18.246 | 75.9 | 14.696 | 0.074087 | 0.036737
4393 | 75.91 | 14.696 | 0.074086 | 18.248 | 0.036741 |  | 4393 | 18.248 | 75.91 | 14.696 | 0.074086 | 0.036741
4394 | 75.92 | 14.696 | 0.074084 | 18.25 | 0.036746 |  | 4394 | 18.25 | 75.92 | 14.696 | 0.074084 | 0.036746
4395 | 75.93 | 14.696 | 0.074083 | 18.253 | 0.03675 |  | 4395 | 18.253 | 75.93 | 14.696 | 0.074083 | 0.03675
4396 | 75.94 | 14.696 | 0.074082 | 18.255 | 0.036755 |  | 4396 | 18.255 | 75.94 | 14.696 | 0.074082 | 0.036755
4397 | 75.95 | 14.696 | 0.07408 | 18.258 | 0.036759 |  | 4397 | 18.258 | 75.95 | 14.696 | 0.07408 | 0.036759
4398 | 75.96 | 14.696 | 0.074079 | 18.26 | 0.036764 |  | 4398 | 18.26 | 75.96 | 14.696 | 0.074079 | 0.036764
4399 | 75.97 | 14.696 | 0.074077 | 18.263 | 0.036768 |  | 4399 | 18.263 | 75.97 | 14.696 | 0.074077 | 0.036768
4400 | 75.98 | 14.696 | 0.074076 | 18.265 | 0.036773 |  | 4400 | 18.265 | 75.98 | 14.696 | 0.074076 | 0.036773
4401 | 75.99 | 14.696 | 0.074075 | 18.267 | 0.036777 |  | 4401 | 18.267 | 75.99 | 14.696 | 0.074075 | 0.036777
4402 | 76 | 14.696 | 0.074073 | 18.27 | 0.036782 |  | 4402 | 18.27 | 76 | 14.696 | 0.074073 | 0.036782
4403 | 76.01 | 14.696 | 0.074072 | 18.272 | 0.036786 |  | 4403 | 18.272 | 76.01 | 14.696 | 0.074072 | 0.036786
4404 | 76.02 | 14.696 | 0.07407 | 18.275 | 0.036791 |  | 4404 | 18.275 | 76.02 | 14.696 | 0.07407 | 0.036791
4405 | 76.03 | 14.696 | 0.074069 | 18.277 | 0.036795 |  | 4405 | 18.277 | 76.03 | 14.696 | 0.074069 | 0.036795
4406 | 76.04 | 14.696 | 0.074068 | 18.279 | 0.0368 |  | 4406 | 18.279 | 76.04 | 14.696 | 0.074068 | 0.0368
4407 | 76.05 | 14.696 | 0.074066 | 18.282 | 0.036804 |  | 4407 | 18.282 | 76.05 | 14.696 | 0.074066 | 0.036804
4408 | 76.06 | 14.696 | 0.074065 | 18.284 | 0.036809 |  | 4408 | 18.284 | 76.06 | 14.696 | 0.074065 | 0.036809
4409 | 76.07 | 14.696 | 0.074064 | 18.287 | 0.036813 |  | 4409 | 18.287 | 76.07 | 14.696 | 0.074064 | 0.036813
4410 | 76.08 | 14.696 | 0.074062 | 18.289 | 0.036818 |  | 4410 | 18.289 | 76.08 | 14.696 | 0.074062 | 0.036818
4411 | 76.09 | 14.696 | 0.074061 | 18.291 | 0.036822 |  | 4411 | 18.291 | 76.09 | 14.696 | 0.074061 | 0.036822
4412 | 76.1 | 14.696 | 0.074059 | 18.294 | 0.036827 |  | 4412 | 18.294 | 76.1 | 14.696 | 0.074059 | 0.036827
4413 | 76.11 | 14.696 | 0.074058 | 18.296 | 0.036831 |  | 4413 | 18.296 | 76.11 | 14.696 | 0.074058 | 0.036831
4414 | 76.12 | 14.696 | 0.074057 | 18.299 | 0.036836 |  | 4414 | 18.299 | 76.12 | 14.696 | 0.074057 | 0.036836
4415 | 76.13 | 14.696 | 0.074055 | 18.301 | 0.03684 |  | 4415 | 18.301 | 76.13 | 14.696 | 0.074055 | 0.03684
4416 | 76.14 | 14.696 | 0.074054 | 18.303 | 0.036845 |  | 4416 | 18.303 | 76.14 | 14.696 | 0.074054 | 0.036845
4417 | 76.15 | 14.696 | 0.074052 | 18.306 | 0.036849 |  | 4417 | 18.306 | 76.15 | 14.696 | 0.074052 | 0.036849
4418 | 76.16 | 14.696 | 0.074051 | 18.308 | 0.036854 |  | 4418 | 18.308 | 76.16 | 14.696 | 0.074051 | 0.036854
4419 | 76.17 | 14.696 | 0.07405 | 18.311 | 0.036858 |  | 4419 | 18.311 | 76.17 | 14.696 | 0.07405 | 0.036858
4420 | 76.18 | 14.696 | 0.074048 | 18.313 | 0.036863 |  | 4420 | 18.313 | 76.18 | 14.696 | 0.074048 | 0.036863
4421 | 76.19 | 14.696 | 0.074047 | 18.315 | 0.036867 |  | 4421 | 18.315 | 76.19 | 14.696 | 0.074047 | 0.036867
4422 | 76.2 | 14.696 | 0.074046 | 18.318 | 0.036872 |  | 4422 | 18.318 | 76.2 | 14.696 | 0.074046 | 0.036872
4423 | 76.21 | 14.696 | 0.074044 | 18.32 | 0.036876 |  | 4423 | 18.32 | 76.21 | 14.696 | 0.074044 | 0.036876
4424 | 76.22 | 14.696 | 0.074043 | 18.323 | 0.036881 |  | 4424 | 18.323 | 76.22 | 14.696 | 0.074043 | 0.036881
4425 | 76.23 | 14.696 | 0.074041 | 18.325 | 0.036885 |  | 4425 | 18.325 | 76.23 | 14.696 | 0.074041 | 0.036885
4426 | 76.24 | 14.696 | 0.07404 | 18.327 | 0.03689 |  | 4426 | 18.327 | 76.24 | 14.696 | 0.07404 | 0.03689
4427 | 76.25 | 14.696 | 0.074039 | 18.33 | 0.036894 |  | 4427 | 18.33 | 76.25 | 14.696 | 0.074039 | 0.036894
4428 | 76.26 | 14.696 | 0.074037 | 18.332 | 0.036899 |  | 4428 | 18.332 | 76.26 | 14.696 | 0.074037 | 0.036899
4429 | 76.27 | 14.696 | 0.074036 | 18.335 | 0.036903 |  | 4429 | 18.335 | 76.27 | 14.696 | 0.074036 | 0.036903
4430 | 76.28 | 14.696 | 0.074034 | 18.337 | 0.036907 |  | 4430 | 18.337 | 76.28 | 14.696 | 0.074034 | 0.036907
4431 | 76.29 | 14.696 | 0.074033 | 18.339 | 0.036912 |  | 4431 | 18.339 | 76.29 | 14.696 | 0.074033 | 0.036912
4432 | 76.3 | 14.696 | 0.074032 | 18.342 | 0.036916 |  | 4432 | 18.342 | 76.3 | 14.696 | 0.074032 | 0.036916
4433 | 76.31 | 14.696 | 0.07403 | 18.344 | 0.036921 |  | 4433 | 18.344 | 76.31 | 14.696 | 0.07403 | 0.036921
4434 | 76.32 | 14.696 | 0.074029 | 18.347 | 0.036925 |  | 4434 | 18.347 | 76.32 | 14.696 | 0.074029 | 0.036925
4435 | 76.33 | 14.696 | 0.074028 | 18.349 | 0.03693 |  | 4435 | 18.349 | 76.33 | 14.696 | 0.074028 | 0.03693
4436 | 76.34 | 14.696 | 0.074026 | 18.352 | 0.036934 |  | 4436 | 18.352 | 76.34 | 14.696 | 0.074026 | 0.036934
4437 | 76.35 | 14.696 | 0.074025 | 18.354 | 0.036939 |  | 4437 | 18.354 | 76.35 | 14.696 | 0.074025 | 0.036939
4438 | 76.36 | 14.696 | 0.074023 | 18.356 | 0.036943 |  | 4438 | 18.356 | 76.36 | 14.696 | 0.074023 | 0.036943
4439 | 76.37 | 14.696 | 0.074022 | 18.359 | 0.036948 |  | 4439 | 18.359 | 76.37 | 14.696 | 0.074022 | 0.036948
4440 | 76.38 | 14.696 | 0.074021 | 18.361 | 0.036952 |  | 4440 | 18.361 | 76.38 | 14.696 | 0.074021 | 0.036952
4441 | 76.39 | 14.696 | 0.074019 | 18.364 | 0.036957 |  | 4441 | 18.364 | 76.39 | 14.696 | 0.074019 | 0.036957
4442 | 76.4 | 14.696 | 0.074018 | 18.366 | 0.036961 |  | 4442 | 18.366 | 76.4 | 14.696 | 0.074018 | 0.036961
4443 | 76.41 | 14.696 | 0.074016 | 18.368 | 0.036966 |  | 4443 | 18.368 | 76.41 | 14.696 | 0.074016 | 0.036966
4444 | 76.42 | 14.696 | 0.074015 | 18.371 | 0.03697 |  | 4444 | 18.371 | 76.42 | 14.696 | 0.074015 | 0.03697
4445 | 76.43 | 14.696 | 0.074014 | 18.373 | 0.036975 |  | 4445 | 18.373 | 76.43 | 14.696 | 0.074014 | 0.036975
4446 | 76.44 | 14.696 | 0.074012 | 18.376 | 0.036979 |  | 4446 | 18.376 | 76.44 | 14.696 | 0.074012 | 0.036979
4447 | 76.45 | 14.696 | 0.074011 | 18.378 | 0.036984 |  | 4447 | 18.378 | 76.45 | 14.696 | 0.074011 | 0.036984
4448 | 76.46 | 14.696 | 0.07401 | 18.38 | 0.036988 |  | 4448 | 18.38 | 76.46 | 14.696 | 0.07401 | 0.036988
4449 | 76.47 | 14.696 | 0.074008 | 18.383 | 0.036993 |  | 4449 | 18.383 | 76.47 | 14.696 | 0.074008 | 0.036993
4450 | 76.48 | 14.696 | 0.074007 | 18.385 | 0.036997 |  | 4450 | 18.385 | 76.48 | 14.696 | 0.074007 | 0.036997
4451 | 76.49 | 14.696 | 0.074005 | 18.388 | 0.037002 |  | 4451 | 18.388 | 76.49 | 14.696 | 0.074005 | 0.037002
4452 | 76.5 | 14.696 | 0.074004 | 18.39 | 0.037006 |  | 4452 | 18.39 | 76.5 | 14.696 | 0.074004 | 0.037006
4453 | 76.51 | 14.696 | 0.074003 | 18.392 | 0.037011 |  | 4453 | 18.392 | 76.51 | 14.696 | 0.074003 | 0.037011
4454 | 76.52 | 14.696 | 0.074001 | 18.395 | 0.037015 |  | 4454 | 18.395 | 76.52 | 14.696 | 0.074001 | 0.037015
4455 | 76.53 | 14.696 | 0.074 | 18.397 | 0.03702 |  | 4455 | 18.397 | 76.53 | 14.696 | 0.074 | 0.03702
4456 | 76.54 | 14.696 | 0.073998 | 18.4 | 0.037024 |  | 4456 | 18.4 | 76.54 | 14.696 | 0.073998 | 0.037024
4457 | 76.55 | 14.696 | 0.073997 | 18.402 | 0.037029 |  | 4457 | 18.402 | 76.55 | 14.696 | 0.073997 | 0.037029
4458 | 76.56 | 14.696 | 0.073996 | 18.404 | 0.037033 |  | 4458 | 18.404 | 76.56 | 14.696 | 0.073996 | 0.037033
4459 | 76.57 | 14.696 | 0.073994 | 18.407 | 0.037038 |  | 4459 | 18.407 | 76.57 | 14.696 | 0.073994 | 0.037038
4460 | 76.58 | 14.696 | 0.073993 | 18.409 | 0.037042 |  | 4460 | 18.409 | 76.58 | 14.696 | 0.073993 | 0.037042
4461 | 76.59 | 14.696 | 0.073992 | 18.412 | 0.037047 |  | 4461 | 18.412 | 76.59 | 14.696 | 0.073992 | 0.037047
4462 | 76.6 | 14.696 | 0.07399 | 18.414 | 0.037051 |  | 4462 | 18.414 | 76.6 | 14.696 | 0.07399 | 0.037051
4463 | 76.61 | 14.696 | 0.073989 | 18.416 | 0.037056 |  | 4463 | 18.416 | 76.61 | 14.696 | 0.073989 | 0.037056
4464 | 76.62 | 14.696 | 0.073987 | 18.419 | 0.03706 |  | 4464 | 18.419 | 76.62 | 14.696 | 0.073987 | 0.03706
4465 | 76.63 | 14.696 | 0.073986 | 18.421 | 0.037064 |  | 4465 | 18.421 | 76.63 | 14.696 | 0.073986 | 0.037064
4466 | 76.64 | 14.696 | 0.073985 | 18.424 | 0.037069 |  | 4466 | 18.424 | 76.64 | 14.696 | 0.073985 | 0.037069
4467 | 76.65 | 14.696 | 0.073983 | 18.426 | 0.037073 |  | 4467 | 18.426 | 76.65 | 14.696 | 0.073983 | 0.037073
4468 | 76.66 | 14.696 | 0.073982 | 18.428 | 0.037078 |  | 4468 | 18.428 | 76.66 | 14.696 | 0.073982 | 0.037078
4469 | 76.67 | 14.696 | 0.07398 | 18.431 | 0.037082 |  | 4469 | 18.431 | 76.67 | 14.696 | 0.07398 | 0.037082
4470 | 76.68 | 14.696 | 0.073979 | 18.433 | 0.037087 |  | 4470 | 18.433 | 76.68 | 14.696 | 0.073979 | 0.037087
4471 | 76.69 | 14.696 | 0.073978 | 18.436 | 0.037091 |  | 4471 | 18.436 | 76.69 | 14.696 | 0.073978 | 0.037091
4472 | 76.7 | 14.696 | 0.073976 | 18.438 | 0.037096 |  | 4472 | 18.438 | 76.7 | 14.696 | 0.073976 | 0.037096
4473 | 76.71 | 14.696 | 0.073975 | 18.441 | 0.0371 |  | 4473 | 18.441 | 76.71 | 14.696 | 0.073975 | 0.0371
4474 | 76.72 | 14.696 | 0.073974 | 18.443 | 0.037105 |  | 4474 | 18.443 | 76.72 | 14.696 | 0.073974 | 0.037105
4475 | 76.73 | 14.696 | 0.073972 | 18.445 | 0.037109 |  | 4475 | 18.445 | 76.73 | 14.696 | 0.073972 | 0.037109
4476 | 76.74 | 14.696 | 0.073971 | 18.448 | 0.037114 |  | 4476 | 18.448 | 76.74 | 14.696 | 0.073971 | 0.037114
4477 | 76.75 | 14.696 | 0.073969 | 18.45 | 0.037118 |  | 4477 | 18.45 | 76.75 | 14.696 | 0.073969 | 0.037118
4478 | 76.76 | 14.696 | 0.073968 | 18.453 | 0.037123 |  | 4478 | 18.453 | 76.76 | 14.696 | 0.073968 | 0.037123
4479 | 76.77 | 14.696 | 0.073967 | 18.455 | 0.037127 |  | 4479 | 18.455 | 76.77 | 14.696 | 0.073967 | 0.037127
4480 | 76.78 | 14.696 | 0.073965 | 18.457 | 0.037132 |  | 4480 | 18.457 | 76.78 | 14.696 | 0.073965 | 0.037132
4481 | 76.79 | 14.696 | 0.073964 | 18.46 | 0.037136 |  | 4481 | 18.46 | 76.79 | 14.696 | 0.073964 | 0.037136
4482 | 76.8 | 14.696 | 0.073962 | 18.462 | 0.037141 |  | 4482 | 18.462 | 76.8 | 14.696 | 0.073962 | 0.037141
4483 | 76.81 | 14.696 | 0.073961 | 18.465 | 0.037145 |  | 4483 | 18.465 | 76.81 | 14.696 | 0.073961 | 0.037145
4484 | 76.82 | 14.696 | 0.07396 | 18.467 | 0.03715 |  | 4484 | 18.467 | 76.82 | 14.696 | 0.07396 | 0.03715
4485 | 76.83 | 14.696 | 0.073958 | 18.469 | 0.037154 |  | 4485 | 18.469 | 76.83 | 14.696 | 0.073958 | 0.037154
4486 | 76.84 | 14.696 | 0.073957 | 18.472 | 0.037159 |  | 4486 | 18.472 | 76.84 | 14.696 | 0.073957 | 0.037159
4487 | 76.85 | 14.696 | 0.073956 | 18.474 | 0.037163 |  | 4487 | 18.474 | 76.85 | 14.696 | 0.073956 | 0.037163
4488 | 76.86 | 14.696 | 0.073954 | 18.477 | 0.037168 |  | 4488 | 18.477 | 76.86 | 14.696 | 0.073954 | 0.037168
4489 | 76.87 | 14.696 | 0.073953 | 18.479 | 0.037172 |  | 4489 | 18.479 | 76.87 | 14.696 | 0.073953 | 0.037172
4490 | 76.88 | 14.696 | 0.073951 | 18.481 | 0.037177 |  | 4490 | 18.481 | 76.88 | 14.696 | 0.073951 | 0.037177
4491 | 76.89 | 14.696 | 0.07395 | 18.484 | 0.037181 |  | 4491 | 18.484 | 76.89 | 14.696 | 0.07395 | 0.037181
4492 | 76.9 | 14.696 | 0.073949 | 18.486 | 0.037186 |  | 4492 | 18.486 | 76.9 | 14.696 | 0.073949 | 0.037186
4493 | 76.91 | 14.696 | 0.073947 | 18.489 | 0.03719 |  | 4493 | 18.489 | 76.91 | 14.696 | 0.073947 | 0.03719
4494 | 76.92 | 14.696 | 0.073946 | 18.491 | 0.037195 |  | 4494 | 18.491 | 76.92 | 14.696 | 0.073946 | 0.037195
4495 | 76.93 | 14.696 | 0.073945 | 18.493 | 0.037199 |  | 4495 | 18.493 | 76.93 | 14.696 | 0.073945 | 0.037199
4496 | 76.94 | 14.696 | 0.073943 | 18.496 | 0.037203 |  | 4496 | 18.496 | 76.94 | 14.696 | 0.073943 | 0.037203
4497 | 76.95 | 14.696 | 0.073942 | 18.498 | 0.037208 |  | 4497 | 18.498 | 76.95 | 14.696 | 0.073942 | 0.037208
4498 | 76.96 | 14.696 | 0.07394 | 18.501 | 0.037212 |  | 4498 | 18.501 | 76.96 | 14.696 | 0.07394 | 0.037212
4499 | 76.97 | 14.696 | 0.073939 | 18.503 | 0.037217 |  | 4499 | 18.503 | 76.97 | 14.696 | 0.073939 | 0.037217
4500 | 76.98 | 14.696 | 0.073938 | 18.505 | 0.037221 |  | 4500 | 18.505 | 76.98 | 14.696 | 0.073938 | 0.037221
4501 | 76.99 | 14.696 | 0.073936 | 18.508 | 0.037226 |  | 4501 | 18.508 | 76.99 | 14.696 | 0.073936 | 0.037226
4502 | 77 | 14.696 | 0.073935 | 18.51 | 0.03723 |  | 4502 | 18.51 | 77 | 14.696 | 0.073935 | 0.03723
4503 | 77.01 | 14.696 | 0.073933 | 18.513 | 0.037235 |  | 4503 | 18.513 | 77.01 | 14.696 | 0.073933 | 0.037235
4504 | 77.02 | 14.696 | 0.073932 | 18.515 | 0.037239 |  | 4504 | 18.515 | 77.02 | 14.696 | 0.073932 | 0.037239
4505 | 77.03 | 14.696 | 0.073931 | 18.517 | 0.037244 |  | 4505 | 18.517 | 77.03 | 14.696 | 0.073931 | 0.037244
4506 | 77.04 | 14.696 | 0.073929 | 18.52 | 0.037248 |  | 4506 | 18.52 | 77.04 | 14.696 | 0.073929 | 0.037248
4507 | 77.05 | 14.696 | 0.073928 | 18.522 | 0.037253 |  | 4507 | 18.522 | 77.05 | 14.696 | 0.073928 | 0.037253
4508 | 77.06 | 14.696 | 0.073927 | 18.525 | 0.037257 |  | 4508 | 18.525 | 77.06 | 14.696 | 0.073927 | 0.037257
4509 | 77.07 | 14.696 | 0.073925 | 18.527 | 0.037262 |  | 4509 | 18.527 | 77.07 | 14.696 | 0.073925 | 0.037262
4510 | 77.08 | 14.696 | 0.073924 | 18.529 | 0.037266 |  | 4510 | 18.529 | 77.08 | 14.696 | 0.073924 | 0.037266
4511 | 77.09 | 14.696 | 0.073922 | 18.532 | 0.037271 |  | 4511 | 18.532 | 77.09 | 14.696 | 0.073922 | 0.037271
4512 | 77.1 | 14.696 | 0.073921 | 18.534 | 0.037275 |  | 4512 | 18.534 | 77.1 | 14.696 | 0.073921 | 0.037275
4513 | 77.11 | 14.696 | 0.07392 | 18.537 | 0.03728 |  | 4513 | 18.537 | 77.11 | 14.696 | 0.07392 | 0.03728
4514 | 77.12 | 14.696 | 0.073918 | 18.539 | 0.037284 |  | 4514 | 18.539 | 77.12 | 14.696 | 0.073918 | 0.037284
4515 | 77.13 | 14.696 | 0.073917 | 18.542 | 0.037289 |  | 4515 | 18.542 | 77.13 | 14.696 | 0.073917 | 0.037289
4516 | 77.14 | 14.696 | 0.073916 | 18.544 | 0.037293 |  | 4516 | 18.544 | 77.14 | 14.696 | 0.073916 | 0.037293
4517 | 77.15 | 14.696 | 0.073914 | 18.546 | 0.037298 |  | 4517 | 18.546 | 77.15 | 14.696 | 0.073914 | 0.037298
4518 | 77.16 | 14.696 | 0.073913 | 18.549 | 0.037302 |  | 4518 | 18.549 | 77.16 | 14.696 | 0.073913 | 0.037302
4519 | 77.17 | 14.696 | 0.073911 | 18.551 | 0.037307 |  | 4519 | 18.551 | 77.17 | 14.696 | 0.073911 | 0.037307
4520 | 77.18 | 14.696 | 0.07391 | 18.554 | 0.037311 |  | 4520 | 18.554 | 77.18 | 14.696 | 0.07391 | 0.037311
4521 | 77.19 | 14.696 | 0.073909 | 18.556 | 0.037316 |  | 4521 | 18.556 | 77.19 | 14.696 | 0.073909 | 0.037316
4522 | 77.2 | 14.696 | 0.073907 | 18.558 | 0.03732 |  | 4522 | 18.558 | 77.2 | 14.696 | 0.073907 | 0.03732
4523 | 77.21 | 14.696 | 0.073906 | 18.561 | 0.037324 |  | 4523 | 18.561 | 77.21 | 14.696 | 0.073906 | 0.037324
4524 | 77.22 | 14.696 | 0.073904 | 18.563 | 0.037329 |  | 4524 | 18.563 | 77.22 | 14.696 | 0.073904 | 0.037329
4525 | 77.23 | 14.696 | 0.073903 | 18.566 | 0.037333 |  | 4525 | 18.566 | 77.23 | 14.696 | 0.073903 | 0.037333
4526 | 77.24 | 14.696 | 0.073902 | 18.568 | 0.037338 |  | 4526 | 18.568 | 77.24 | 14.696 | 0.073902 | 0.037338
4527 | 77.25 | 14.696 | 0.0739 | 18.57 | 0.037342 |  | 4527 | 18.57 | 77.25 | 14.696 | 0.0739 | 0.037342
4528 | 77.26 | 14.696 | 0.073899 | 18.573 | 0.037347 |  | 4528 | 18.573 | 77.26 | 14.696 | 0.073899 | 0.037347
4529 | 77.27 | 14.696 | 0.073898 | 18.575 | 0.037351 |  | 4529 | 18.575 | 77.27 | 14.696 | 0.073898 | 0.037351
4530 | 77.28 | 14.696 | 0.073896 | 18.578 | 0.037356 |  | 4530 | 18.578 | 77.28 | 14.696 | 0.073896 | 0.037356
4531 | 77.29 | 14.696 | 0.073895 | 18.58 | 0.03736 |  | 4531 | 18.58 | 77.29 | 14.696 | 0.073895 | 0.03736
4532 | 77.3 | 14.696 | 0.073893 | 18.582 | 0.037365 |  | 4532 | 18.582 | 77.3 | 14.696 | 0.073893 | 0.037365
4533 | 77.31 | 14.696 | 0.073892 | 18.585 | 0.037369 |  | 4533 | 18.585 | 77.31 | 14.696 | 0.073892 | 0.037369
4534 | 77.32 | 14.696 | 0.073891 | 18.587 | 0.037374 |  | 4534 | 18.587 | 77.32 | 14.696 | 0.073891 | 0.037374
4535 | 77.33 | 14.696 | 0.073889 | 18.59 | 0.037378 |  | 4535 | 18.59 | 77.33 | 14.696 | 0.073889 | 0.037378
4536 | 77.34 | 14.696 | 0.073888 | 18.592 | 0.037383 |  | 4536 | 18.592 | 77.34 | 14.696 | 0.073888 | 0.037383
4537 | 77.35 | 14.696 | 0.073887 | 18.594 | 0.037387 |  | 4537 | 18.594 | 77.35 | 14.696 | 0.073887 | 0.037387
4538 | 77.36 | 14.696 | 0.073885 | 18.597 | 0.037392 |  | 4538 | 18.597 | 77.36 | 14.696 | 0.073885 | 0.037392
4539 | 77.37 | 14.696 | 0.073884 | 18.599 | 0.037396 |  | 4539 | 18.599 | 77.37 | 14.696 | 0.073884 | 0.037396
4540 | 77.38 | 14.696 | 0.073882 | 18.602 | 0.037401 |  | 4540 | 18.602 | 77.38 | 14.696 | 0.073882 | 0.037401
4541 | 77.39 | 14.696 | 0.073881 | 18.604 | 0.037405 |  | 4541 | 18.604 | 77.39 | 14.696 | 0.073881 | 0.037405
4542 | 77.4 | 14.696 | 0.07388 | 18.606 | 0.03741 |  | 4542 | 18.606 | 77.4 | 14.696 | 0.07388 | 0.03741
4543 | 77.41 | 14.696 | 0.073878 | 18.609 | 0.037414 |  | 4543 | 18.609 | 77.41 | 14.696 | 0.073878 | 0.037414
4544 | 77.42 | 14.696 | 0.073877 | 18.611 | 0.037419 |  | 4544 | 18.611 | 77.42 | 14.696 | 0.073877 | 0.037419
4545 | 77.43 | 14.696 | 0.073875 | 18.614 | 0.037423 |  | 4545 | 18.614 | 77.43 | 14.696 | 0.073875 | 0.037423
4546 | 77.44 | 14.696 | 0.073874 | 18.616 | 0.037427 |  | 4546 | 18.616 | 77.44 | 14.696 | 0.073874 | 0.037427
4547 | 77.45 | 14.696 | 0.073873 | 18.618 | 0.037432 |  | 4547 | 18.618 | 77.45 | 14.696 | 0.073873 | 0.037432
4548 | 77.46 | 14.696 | 0.073871 | 18.621 | 0.037436 |  | 4548 | 18.621 | 77.46 | 14.696 | 0.073871 | 0.037436
4549 | 77.47 | 14.696 | 0.07387 | 18.623 | 0.037441 |  | 4549 | 18.623 | 77.47 | 14.696 | 0.07387 | 0.037441
4550 | 77.48 | 14.696 | 0.073869 | 18.626 | 0.037445 |  | 4550 | 18.626 | 77.48 | 14.696 | 0.073869 | 0.037445
4551 | 77.49 | 14.696 | 0.073867 | 18.628 | 0.03745 |  | 4551 | 18.628 | 77.49 | 14.696 | 0.073867 | 0.03745
4552 | 77.5 | 14.696 | 0.073866 | 18.631 | 0.037454 |  | 4552 | 18.631 | 77.5 | 14.696 | 0.073866 | 0.037454
4553 | 77.51 | 14.696 | 0.073864 | 18.633 | 0.037459 |  | 4553 | 18.633 | 77.51 | 14.696 | 0.073864 | 0.037459
4554 | 77.52 | 14.696 | 0.073863 | 18.635 | 0.037463 |  | 4554 | 18.635 | 77.52 | 14.696 | 0.073863 | 0.037463
4555 | 77.53 | 14.696 | 0.073862 | 18.638 | 0.037468 |  | 4555 | 18.638 | 77.53 | 14.696 | 0.073862 | 0.037468
4556 | 77.54 | 14.696 | 0.07386 | 18.64 | 0.037472 |  | 4556 | 18.64 | 77.54 | 14.696 | 0.07386 | 0.037472
4557 | 77.55 | 14.696 | 0.073859 | 18.643 | 0.037477 |  | 4557 | 18.643 | 77.55 | 14.696 | 0.073859 | 0.037477
4558 | 77.56 | 14.696 | 0.073858 | 18.645 | 0.037481 |  | 4558 | 18.645 | 77.56 | 14.696 | 0.073858 | 0.037481
4559 | 77.57 | 14.696 | 0.073856 | 18.647 | 0.037486 |  | 4559 | 18.647 | 77.57 | 14.696 | 0.073856 | 0.037486
4560 | 77.58 | 14.696 | 0.073855 | 18.65 | 0.03749 |  | 4560 | 18.65 | 77.58 | 14.696 | 0.073855 | 0.03749
4561 | 77.59 | 14.696 | 0.073853 | 18.652 | 0.037495 |  | 4561 | 18.652 | 77.59 | 14.696 | 0.073853 | 0.037495
4562 | 77.6 | 14.696 | 0.073852 | 18.655 | 0.037499 |  | 4562 | 18.655 | 77.6 | 14.696 | 0.073852 | 0.037499
4563 | 77.61 | 14.696 | 0.073851 | 18.657 | 0.037504 |  | 4563 | 18.657 | 77.61 | 14.696 | 0.073851 | 0.037504
4564 | 77.62 | 14.696 | 0.073849 | 18.659 | 0.037508 |  | 4564 | 18.659 | 77.62 | 14.696 | 0.073849 | 0.037508
4565 | 77.63 | 14.696 | 0.073848 | 18.662 | 0.037513 |  | 4565 | 18.662 | 77.63 | 14.696 | 0.073848 | 0.037513
4566 | 77.64 | 14.696 | 0.073847 | 18.664 | 0.037517 |  | 4566 | 18.664 | 77.64 | 14.696 | 0.073847 | 0.037517
4567 | 77.65 | 14.696 | 0.073845 | 18.667 | 0.037521 |  | 4567 | 18.667 | 77.65 | 14.696 | 0.073845 | 0.037521
4568 | 77.66 | 14.696 | 0.073844 | 18.669 | 0.037526 |  | 4568 | 18.669 | 77.66 | 14.696 | 0.073844 | 0.037526
4569 | 77.67 | 14.696 | 0.073842 | 18.671 | 0.03753 |  | 4569 | 18.671 | 77.67 | 14.696 | 0.073842 | 0.03753
4570 | 77.68 | 14.696 | 0.073841 | 18.674 | 0.037535 |  | 4570 | 18.674 | 77.68 | 14.696 | 0.073841 | 0.037535
4571 | 77.69 | 14.696 | 0.07384 | 18.676 | 0.037539 |  | 4571 | 18.676 | 77.69 | 14.696 | 0.07384 | 0.037539
4572 | 77.7 | 14.696 | 0.073838 | 18.679 | 0.037544 |  | 4572 | 18.679 | 77.7 | 14.696 | 0.073838 | 0.037544
4573 | 77.71 | 14.696 | 0.073837 | 18.681 | 0.037548 |  | 4573 | 18.681 | 77.71 | 14.696 | 0.073837 | 0.037548
4574 | 77.72 | 14.696 | 0.073836 | 18.683 | 0.037553 |  | 4574 | 18.683 | 77.72 | 14.696 | 0.073836 | 0.037553
4575 | 77.73 | 14.696 | 0.073834 | 18.686 | 0.037557 |  | 4575 | 18.686 | 77.73 | 14.696 | 0.073834 | 0.037557
4576 | 77.74 | 14.696 | 0.073833 | 18.688 | 0.037562 |  | 4576 | 18.688 | 77.74 | 14.696 | 0.073833 | 0.037562
4577 | 77.75 | 14.696 | 0.073831 | 18.691 | 0.037566 |  | 4577 | 18.691 | 77.75 | 14.696 | 0.073831 | 0.037566
4578 | 77.76 | 14.696 | 0.07383 | 18.693 | 0.037571 |  | 4578 | 18.693 | 77.76 | 14.696 | 0.07383 | 0.037571
4579 | 77.77 | 14.696 | 0.073829 | 18.695 | 0.037575 |  | 4579 | 18.695 | 77.77 | 14.696 | 0.073829 | 0.037575
4580 | 77.78 | 14.696 | 0.073827 | 18.698 | 0.03758 |  | 4580 | 18.698 | 77.78 | 14.696 | 0.073827 | 0.03758
4581 | 77.79 | 14.696 | 0.073826 | 18.7 | 0.037584 |  | 4581 | 18.7 | 77.79 | 14.696 | 0.073826 | 0.037584
4582 | 77.8 | 14.696 | 0.073824 | 18.703 | 0.037589 |  | 4582 | 18.703 | 77.8 | 14.696 | 0.073824 | 0.037589
4583 | 77.81 | 14.696 | 0.073823 | 18.705 | 0.037593 |  | 4583 | 18.705 | 77.81 | 14.696 | 0.073823 | 0.037593
4584 | 77.82 | 14.696 | 0.073822 | 18.707 | 0.037598 |  | 4584 | 18.707 | 77.82 | 14.696 | 0.073822 | 0.037598
4585 | 77.83 | 14.696 | 0.07382 | 18.71 | 0.037602 |  | 4585 | 18.71 | 77.83 | 14.696 | 0.07382 | 0.037602
4586 | 77.84 | 14.696 | 0.073819 | 18.712 | 0.037607 |  | 4586 | 18.712 | 77.84 | 14.696 | 0.073819 | 0.037607
4587 | 77.85 | 14.696 | 0.073818 | 18.715 | 0.037611 |  | 4587 | 18.715 | 77.85 | 14.696 | 0.073818 | 0.037611
4588 | 77.86 | 14.696 | 0.073816 | 18.717 | 0.037615 |  | 4588 | 18.717 | 77.86 | 14.696 | 0.073816 | 0.037615
4589 | 77.87 | 14.696 | 0.073815 | 18.719 | 0.03762 |  | 4589 | 18.719 | 77.87 | 14.696 | 0.073815 | 0.03762
4590 | 77.88 | 14.696 | 0.073813 | 18.722 | 0.037624 |  | 4590 | 18.722 | 77.88 | 14.696 | 0.073813 | 0.037624
4591 | 77.89 | 14.696 | 0.073812 | 18.724 | 0.037629 |  | 4591 | 18.724 | 77.89 | 14.696 | 0.073812 | 0.037629
4592 | 77.9 | 14.696 | 0.073811 | 18.727 | 0.037633 |  | 4592 | 18.727 | 77.9 | 14.696 | 0.073811 | 0.037633
4593 | 77.91 | 14.696 | 0.073809 | 18.729 | 0.037638 |  | 4593 | 18.729 | 77.91 | 14.696 | 0.073809 | 0.037638
4594 | 77.92 | 14.696 | 0.073808 | 18.732 | 0.037642 |  | 4594 | 18.732 | 77.92 | 14.696 | 0.073808 | 0.037642
4595 | 77.93 | 14.696 | 0.073807 | 18.734 | 0.037647 |  | 4595 | 18.734 | 77.93 | 14.696 | 0.073807 | 0.037647
4596 | 77.94 | 14.696 | 0.073805 | 18.736 | 0.037651 |  | 4596 | 18.736 | 77.94 | 14.696 | 0.073805 | 0.037651
4597 | 77.95 | 14.696 | 0.073804 | 18.739 | 0.037656 |  | 4597 | 18.739 | 77.95 | 14.696 | 0.073804 | 0.037656
4598 | 77.96 | 14.696 | 0.073802 | 18.741 | 0.03766 |  | 4598 | 18.741 | 77.96 | 14.696 | 0.073802 | 0.03766
4599 | 77.97 | 14.696 | 0.073801 | 18.744 | 0.037665 |  | 4599 | 18.744 | 77.97 | 14.696 | 0.073801 | 0.037665
4600 | 77.98 | 14.696 | 0.0738 | 18.746 | 0.037669 |  | 4600 | 18.746 | 77.98 | 14.696 | 0.0738 | 0.037669
4601 | 77.99 | 14.696 | 0.073798 | 18.748 | 0.037674 |  | 4601 | 18.748 | 77.99 | 14.696 | 0.073798 | 0.037674
4602 | 78 | 14.696 | 0.073797 | 18.751 | 0.037678 |  | 4602 | 18.751 | 78 | 14.696 | 0.073797 | 0.037678
4603 | 78.01 | 14.696 | 0.073796 | 18.753 | 0.037683 |  | 4603 | 18.753 | 78.01 | 14.696 | 0.073796 | 0.037683
4604 | 78.02 | 14.696 | 0.073794 | 18.756 | 0.037687 |  | 4604 | 18.756 | 78.02 | 14.696 | 0.073794 | 0.037687
4605 | 78.03 | 14.696 | 0.073793 | 18.758 | 0.037692 |  | 4605 | 18.758 | 78.03 | 14.696 | 0.073793 | 0.037692
4606 | 78.04 | 14.696 | 0.073791 | 18.76 | 0.037696 |  | 4606 | 18.76 | 78.04 | 14.696 | 0.073791 | 0.037696
4607 | 78.05 | 14.696 | 0.07379 | 18.763 | 0.0377 |  | 4607 | 18.763 | 78.05 | 14.696 | 0.07379 | 0.0377
4608 | 78.06 | 14.696 | 0.073789 | 18.765 | 0.037705 |  | 4608 | 18.765 | 78.06 | 14.696 | 0.073789 | 0.037705
4609 | 78.07 | 14.696 | 0.073787 | 18.768 | 0.037709 |  | 4609 | 18.768 | 78.07 | 14.696 | 0.073787 | 0.037709
4610 | 78.08 | 14.696 | 0.073786 | 18.77 | 0.037714 |  | 4610 | 18.77 | 78.08 | 14.696 | 0.073786 | 0.037714
4611 | 78.09 | 14.696 | 0.073785 | 18.772 | 0.037718 |  | 4611 | 18.772 | 78.09 | 14.696 | 0.073785 | 0.037718
4612 | 78.1 | 14.696 | 0.073783 | 18.775 | 0.037723 |  | 4612 | 18.775 | 78.1 | 14.696 | 0.073783 | 0.037723
4613 | 78.11 | 14.696 | 0.073782 | 18.777 | 0.037727 |  | 4613 | 18.777 | 78.11 | 14.696 | 0.073782 | 0.037727
4614 | 78.12 | 14.696 | 0.07378 | 18.78 | 0.037732 |  | 4614 | 18.78 | 78.12 | 14.696 | 0.07378 | 0.037732
4615 | 78.13 | 14.696 | 0.073779 | 18.782 | 0.037736 |  | 4615 | 18.782 | 78.13 | 14.696 | 0.073779 | 0.037736
4616 | 78.14 | 14.696 | 0.073778 | 18.784 | 0.037741 |  | 4616 | 18.784 | 78.14 | 14.696 | 0.073778 | 0.037741
4617 | 78.15 | 14.696 | 0.073776 | 18.787 | 0.037745 |  | 4617 | 18.787 | 78.15 | 14.696 | 0.073776 | 0.037745
4618 | 78.16 | 14.696 | 0.073775 | 18.789 | 0.03775 |  | 4618 | 18.789 | 78.16 | 14.696 | 0.073775 | 0.03775
4619 | 78.17 | 14.696 | 0.073774 | 18.792 | 0.037754 |  | 4619 | 18.792 | 78.17 | 14.696 | 0.073774 | 0.037754
4620 | 78.18 | 14.696 | 0.073772 | 18.794 | 0.037759 |  | 4620 | 18.794 | 78.18 | 14.696 | 0.073772 | 0.037759
4621 | 78.19 | 14.696 | 0.073771 | 18.796 | 0.037763 |  | 4621 | 18.796 | 78.19 | 14.696 | 0.073771 | 0.037763
4622 | 78.2 | 14.696 | 0.073769 | 18.799 | 0.037768 |  | 4622 | 18.799 | 78.2 | 14.696 | 0.073769 | 0.037768
4623 | 78.21 | 14.696 | 0.073768 | 18.801 | 0.037772 |  | 4623 | 18.801 | 78.21 | 14.696 | 0.073768 | 0.037772
4624 | 78.22 | 14.696 | 0.073767 | 18.804 | 0.037777 |  | 4624 | 18.804 | 78.22 | 14.696 | 0.073767 | 0.037777
4625 | 78.23 | 14.696 | 0.073765 | 18.806 | 0.037781 |  | 4625 | 18.806 | 78.23 | 14.696 | 0.073765 | 0.037781
4626 | 78.24 | 14.696 | 0.073764 | 18.808 | 0.037785 |  | 4626 | 18.808 | 78.24 | 14.696 | 0.073764 | 0.037785
4627 | 78.25 | 14.696 | 0.073763 | 18.811 | 0.03779 |  | 4627 | 18.811 | 78.25 | 14.696 | 0.073763 | 0.03779
4628 | 78.26 | 14.696 | 0.073761 | 18.813 | 0.037794 |  | 4628 | 18.813 | 78.26 | 14.696 | 0.073761 | 0.037794
4629 | 78.27 | 14.696 | 0.07376 | 18.816 | 0.037799 |  | 4629 | 18.816 | 78.27 | 14.696 | 0.07376 | 0.037799
4630 | 78.28 | 14.696 | 0.073758 | 18.818 | 0.037803 |  | 4630 | 18.818 | 78.28 | 14.696 | 0.073758 | 0.037803
4631 | 78.29 | 14.696 | 0.073757 | 18.821 | 0.037808 |  | 4631 | 18.821 | 78.29 | 14.696 | 0.073757 | 0.037808
4632 | 78.3 | 14.696 | 0.073756 | 18.823 | 0.037812 |  | 4632 | 18.823 | 78.3 | 14.696 | 0.073756 | 0.037812
4633 | 78.31 | 14.696 | 0.073754 | 18.825 | 0.037817 |  | 4633 | 18.825 | 78.31 | 14.696 | 0.073754 | 0.037817
4634 | 78.32 | 14.696 | 0.073753 | 18.828 | 0.037821 |  | 4634 | 18.828 | 78.32 | 14.696 | 0.073753 | 0.037821
4635 | 78.33 | 14.696 | 0.073752 | 18.83 | 0.037826 |  | 4635 | 18.83 | 78.33 | 14.696 | 0.073752 | 0.037826
4636 | 78.34 | 14.696 | 0.07375 | 18.833 | 0.03783 |  | 4636 | 18.833 | 78.34 | 14.696 | 0.07375 | 0.03783
4637 | 78.35 | 14.696 | 0.073749 | 18.835 | 0.037835 |  | 4637 | 18.835 | 78.35 | 14.696 | 0.073749 | 0.037835
4638 | 78.36 | 14.696 | 0.073747 | 18.837 | 0.037839 |  | 4638 | 18.837 | 78.36 | 14.696 | 0.073747 | 0.037839
4639 | 78.37 | 14.696 | 0.073746 | 18.84 | 0.037844 |  | 4639 | 18.84 | 78.37 | 14.696 | 0.073746 | 0.037844
4640 | 78.38 | 14.696 | 0.073745 | 18.842 | 0.037848 |  | 4640 | 18.842 | 78.38 | 14.696 | 0.073745 | 0.037848
4641 | 78.39 | 14.696 | 0.073743 | 18.845 | 0.037853 |  | 4641 | 18.845 | 78.39 | 14.696 | 0.073743 | 0.037853
4642 | 78.4 | 14.696 | 0.073742 | 18.847 | 0.037857 |  | 4642 | 18.847 | 78.4 | 14.696 | 0.073742 | 0.037857
4643 | 78.41 | 14.696 | 0.073741 | 18.849 | 0.037861 |  | 4643 | 18.849 | 78.41 | 14.696 | 0.073741 | 0.037861
4644 | 78.42 | 14.696 | 0.073739 | 18.852 | 0.037866 |  | 4644 | 18.852 | 78.42 | 14.696 | 0.073739 | 0.037866
4645 | 78.43 | 14.696 | 0.073738 | 18.854 | 0.03787 |  | 4645 | 18.854 | 78.43 | 14.696 | 0.073738 | 0.03787
4646 | 78.44 | 14.696 | 0.073736 | 18.857 | 0.037875 |  | 4646 | 18.857 | 78.44 | 14.696 | 0.073736 | 0.037875
4647 | 78.45 | 14.696 | 0.073735 | 18.859 | 0.037879 |  | 4647 | 18.859 | 78.45 | 14.696 | 0.073735 | 0.037879
4648 | 78.46 | 14.696 | 0.073734 | 18.861 | 0.037884 |  | 4648 | 18.861 | 78.46 | 14.696 | 0.073734 | 0.037884
4649 | 78.47 | 14.696 | 0.073732 | 18.864 | 0.037888 |  | 4649 | 18.864 | 78.47 | 14.696 | 0.073732 | 0.037888
4650 | 78.48 | 14.696 | 0.073731 | 18.866 | 0.037893 |  | 4650 | 18.866 | 78.48 | 14.696 | 0.073731 | 0.037893
4651 | 78.49 | 14.696 | 0.07373 | 18.869 | 0.037897 |  | 4651 | 18.869 | 78.49 | 14.696 | 0.07373 | 0.037897
4652 | 78.5 | 14.696 | 0.073728 | 18.871 | 0.037902 |  | 4652 | 18.871 | 78.5 | 14.696 | 0.073728 | 0.037902
4653 | 78.51 | 14.696 | 0.073727 | 18.873 | 0.037906 |  | 4653 | 18.873 | 78.51 | 14.696 | 0.073727 | 0.037906
4654 | 78.52 | 14.696 | 0.073725 | 18.876 | 0.037911 |  | 4654 | 18.876 | 78.52 | 14.696 | 0.073725 | 0.037911
4655 | 78.53 | 14.696 | 0.073724 | 18.878 | 0.037915 |  | 4655 | 18.878 | 78.53 | 14.696 | 0.073724 | 0.037915
4656 | 78.54 | 14.696 | 0.073723 | 18.881 | 0.03792 |  | 4656 | 18.881 | 78.54 | 14.696 | 0.073723 | 0.03792
4657 | 78.55 | 14.696 | 0.073721 | 18.883 | 0.037924 |  | 4657 | 18.883 | 78.55 | 14.696 | 0.073721 | 0.037924
4658 | 78.56 | 14.696 | 0.07372 | 18.885 | 0.037928 |  | 4658 | 18.885 | 78.56 | 14.696 | 0.07372 | 0.037928
4659 | 78.57 | 14.696 | 0.073719 | 18.888 | 0.037933 |  | 4659 | 18.888 | 78.57 | 14.696 | 0.073719 | 0.037933
4660 | 78.58 | 14.696 | 0.073717 | 18.89 | 0.037937 |  | 4660 | 18.89 | 78.58 | 14.696 | 0.073717 | 0.037937
4661 | 78.59 | 14.696 | 0.073716 | 18.893 | 0.037942 |  | 4661 | 18.893 | 78.59 | 14.696 | 0.073716 | 0.037942
4662 | 78.6 | 14.696 | 0.073714 | 18.895 | 0.037946 |  | 4662 | 18.895 | 78.6 | 14.696 | 0.073714 | 0.037946
4663 | 78.61 | 14.696 | 0.073713 | 18.897 | 0.037951 |  | 4663 | 18.897 | 78.61 | 14.696 | 0.073713 | 0.037951
4664 | 78.62 | 14.696 | 0.073712 | 18.9 | 0.037955 |  | 4664 | 18.9 | 78.62 | 14.696 | 0.073712 | 0.037955
4665 | 78.63 | 14.696 | 0.07371 | 18.902 | 0.03796 |  | 4665 | 18.902 | 78.63 | 14.696 | 0.07371 | 0.03796
4666 | 78.64 | 14.696 | 0.073709 | 18.905 | 0.037964 |  | 4666 | 18.905 | 78.64 | 14.696 | 0.073709 | 0.037964
4667 | 78.65 | 14.696 | 0.073708 | 18.907 | 0.037969 |  | 4667 | 18.907 | 78.65 | 14.696 | 0.073708 | 0.037969
4668 | 78.66 | 14.696 | 0.073706 | 18.91 | 0.037973 |  | 4668 | 18.91 | 78.66 | 14.696 | 0.073706 | 0.037973
4669 | 78.67 | 14.696 | 0.073705 | 18.912 | 0.037978 |  | 4669 | 18.912 | 78.67 | 14.696 | 0.073705 | 0.037978
4670 | 78.68 | 14.696 | 0.073703 | 18.914 | 0.037982 |  | 4670 | 18.914 | 78.68 | 14.696 | 0.073703 | 0.037982
4671 | 78.69 | 14.696 | 0.073702 | 18.917 | 0.037987 |  | 4671 | 18.917 | 78.69 | 14.696 | 0.073702 | 0.037987
4672 | 78.7 | 14.696 | 0.073701 | 18.919 | 0.037991 |  | 4672 | 18.919 | 78.7 | 14.696 | 0.073701 | 0.037991
4673 | 78.71 | 14.696 | 0.073699 | 18.922 | 0.037996 |  | 4673 | 18.922 | 78.71 | 14.696 | 0.073699 | 0.037996
4674 | 78.72 | 14.696 | 0.073698 | 18.924 | 0.038 |  | 4674 | 18.924 | 78.72 | 14.696 | 0.073698 | 0.038
4675 | 78.73 | 14.696 | 0.073697 | 18.926 | 0.038004 |  | 4675 | 18.926 | 78.73 | 14.696 | 0.073697 | 0.038004
4676 | 78.74 | 14.696 | 0.073695 | 18.929 | 0.038009 |  | 4676 | 18.929 | 78.74 | 14.696 | 0.073695 | 0.038009
4677 | 78.75 | 14.696 | 0.073694 | 18.931 | 0.038013 |  | 4677 | 18.931 | 78.75 | 14.696 | 0.073694 | 0.038013
4678 | 78.76 | 14.696 | 0.073693 | 18.934 | 0.038018 |  | 4678 | 18.934 | 78.76 | 14.696 | 0.073693 | 0.038018
4679 | 78.77 | 14.696 | 0.073691 | 18.936 | 0.038022 |  | 4679 | 18.936 | 78.77 | 14.696 | 0.073691 | 0.038022
4680 | 78.78 | 14.696 | 0.07369 | 18.938 | 0.038027 |  | 4680 | 18.938 | 78.78 | 14.696 | 0.07369 | 0.038027
4681 | 78.79 | 14.696 | 0.073688 | 18.941 | 0.038031 |  | 4681 | 18.941 | 78.79 | 14.696 | 0.073688 | 0.038031
4682 | 78.8 | 14.696 | 0.073687 | 18.943 | 0.038036 |  | 4682 | 18.943 | 78.8 | 14.696 | 0.073687 | 0.038036
4683 | 78.81 | 14.696 | 0.073686 | 18.946 | 0.03804 |  | 4683 | 18.946 | 78.81 | 14.696 | 0.073686 | 0.03804
4684 | 78.82 | 14.696 | 0.073684 | 18.948 | 0.038045 |  | 4684 | 18.948 | 78.82 | 14.696 | 0.073684 | 0.038045
4685 | 78.83 | 14.696 | 0.073683 | 18.95 | 0.038049 |  | 4685 | 18.95 | 78.83 | 14.696 | 0.073683 | 0.038049
4686 | 78.84 | 14.696 | 0.073682 | 18.953 | 0.038054 |  | 4686 | 18.953 | 78.84 | 14.696 | 0.073682 | 0.038054
4687 | 78.85 | 14.696 | 0.07368 | 18.955 | 0.038058 |  | 4687 | 18.955 | 78.85 | 14.696 | 0.07368 | 0.038058
4688 | 78.86 | 14.696 | 0.073679 | 18.958 | 0.038063 |  | 4688 | 18.958 | 78.86 | 14.696 | 0.073679 | 0.038063
4689 | 78.87 | 14.696 | 0.073677 | 18.96 | 0.038067 |  | 4689 | 18.96 | 78.87 | 14.696 | 0.073677 | 0.038067
4690 | 78.88 | 14.696 | 0.073676 | 18.962 | 0.038071 |  | 4690 | 18.962 | 78.88 | 14.696 | 0.073676 | 0.038071
4691 | 78.89 | 14.696 | 0.073675 | 18.965 | 0.038076 |  | 4691 | 18.965 | 78.89 | 14.696 | 0.073675 | 0.038076
4692 | 78.9 | 14.696 | 0.073673 | 18.967 | 0.03808 |  | 4692 | 18.967 | 78.9 | 14.696 | 0.073673 | 0.03808
4693 | 78.91 | 14.696 | 0.073672 | 18.97 | 0.038085 |  | 4693 | 18.97 | 78.91 | 14.696 | 0.073672 | 0.038085
4694 | 78.92 | 14.696 | 0.073671 | 18.972 | 0.038089 |  | 4694 | 18.972 | 78.92 | 14.696 | 0.073671 | 0.038089
4695 | 78.93 | 14.696 | 0.073669 | 18.974 | 0.038094 |  | 4695 | 18.974 | 78.93 | 14.696 | 0.073669 | 0.038094
4696 | 78.94 | 14.696 | 0.073668 | 18.977 | 0.038098 |  | 4696 | 18.977 | 78.94 | 14.696 | 0.073668 | 0.038098
4697 | 78.95 | 14.696 | 0.073666 | 18.979 | 0.038103 |  | 4697 | 18.979 | 78.95 | 14.696 | 0.073666 | 0.038103
4698 | 78.96 | 14.696 | 0.073665 | 18.982 | 0.038107 |  | 4698 | 18.982 | 78.96 | 14.696 | 0.073665 | 0.038107
4699 | 78.97 | 14.696 | 0.073664 | 18.984 | 0.038112 |  | 4699 | 18.984 | 78.97 | 14.696 | 0.073664 | 0.038112
4700 | 78.98 | 14.696 | 0.073662 | 18.986 | 0.038116 |  | 4700 | 18.986 | 78.98 | 14.696 | 0.073662 | 0.038116
4701 | 78.99 | 14.696 | 0.073661 | 18.989 | 0.038121 |  | 4701 | 18.989 | 78.99 | 14.696 | 0.073661 | 0.038121
4702 | 79 | 14.696 | 0.07366 | 18.991 | 0.038125 |  | 4702 | 18.991 | 79 | 14.696 | 0.07366 | 0.038125
4703 | 79.01 | 14.696 | 0.073658 | 18.994 | 0.03813 |  | 4703 | 18.994 | 79.01 | 14.696 | 0.073658 | 0.03813
4704 | 79.02 | 14.696 | 0.073657 | 18.996 | 0.038134 |  | 4704 | 18.996 | 79.02 | 14.696 | 0.073657 | 0.038134
4705 | 79.03 | 14.696 | 0.073655 | 18.999 | 0.038138 |  | 4705 | 18.999 | 79.03 | 14.696 | 0.073655 | 0.038138
4706 | 79.04 | 14.696 | 0.073654 | 19.001 | 0.038143 |  | 4706 | 19.001 | 79.04 | 14.696 | 0.073654 | 0.038143
4707 | 79.05 | 14.696 | 0.073653 | 19.003 | 0.038147 |  | 4707 | 19.003 | 79.05 | 14.696 | 0.073653 | 0.038147
4708 | 79.06 | 14.696 | 0.073651 | 19.006 | 0.038152 |  | 4708 | 19.006 | 79.06 | 14.696 | 0.073651 | 0.038152
4709 | 79.07 | 14.696 | 0.07365 | 19.008 | 0.038156 |  | 4709 | 19.008 | 79.07 | 14.696 | 0.07365 | 0.038156
4710 | 79.08 | 14.696 | 0.073649 | 19.011 | 0.038161 |  | 4710 | 19.011 | 79.08 | 14.696 | 0.073649 | 0.038161
4711 | 79.09 | 14.696 | 0.073647 | 19.013 | 0.038165 |  | 4711 | 19.013 | 79.09 | 14.696 | 0.073647 | 0.038165
4712 | 79.1 | 14.696 | 0.073646 | 19.015 | 0.03817 |  | 4712 | 19.015 | 79.1 | 14.696 | 0.073646 | 0.03817
4713 | 79.11 | 14.696 | 0.073645 | 19.018 | 0.038174 |  | 4713 | 19.018 | 79.11 | 14.696 | 0.073645 | 0.038174
4714 | 79.12 | 14.696 | 0.073643 | 19.02 | 0.038179 |  | 4714 | 19.02 | 79.12 | 14.696 | 0.073643 | 0.038179
4715 | 79.13 | 14.696 | 0.073642 | 19.023 | 0.038183 |  | 4715 | 19.023 | 79.13 | 14.696 | 0.073642 | 0.038183
4716 | 79.14 | 14.696 | 0.07364 | 19.025 | 0.038188 |  | 4716 | 19.025 | 79.14 | 14.696 | 0.07364 | 0.038188
4717 | 79.15 | 14.696 | 0.073639 | 19.027 | 0.038192 |  | 4717 | 19.027 | 79.15 | 14.696 | 0.073639 | 0.038192
4718 | 79.16 | 14.696 | 0.073638 | 19.03 | 0.038196 |  | 4718 | 19.03 | 79.16 | 14.696 | 0.073638 | 0.038196
4719 | 79.17 | 14.696 | 0.073636 | 19.032 | 0.038201 |  | 4719 | 19.032 | 79.17 | 14.696 | 0.073636 | 0.038201
4720 | 79.18 | 14.696 | 0.073635 | 19.035 | 0.038205 |  | 4720 | 19.035 | 79.18 | 14.696 | 0.073635 | 0.038205
4721 | 79.19 | 14.696 | 0.073634 | 19.037 | 0.03821 |  | 4721 | 19.037 | 79.19 | 14.696 | 0.073634 | 0.03821
4722 | 79.2 | 14.696 | 0.073632 | 19.039 | 0.038214 |  | 4722 | 19.039 | 79.2 | 14.696 | 0.073632 | 0.038214
4723 | 79.21 | 14.696 | 0.073631 | 19.042 | 0.038219 |  | 4723 | 19.042 | 79.21 | 14.696 | 0.073631 | 0.038219
4724 | 79.22 | 14.696 | 0.073629 | 19.044 | 0.038223 |  | 4724 | 19.044 | 79.22 | 14.696 | 0.073629 | 0.038223
4725 | 79.23 | 14.696 | 0.073628 | 19.047 | 0.038228 |  | 4725 | 19.047 | 79.23 | 14.696 | 0.073628 | 0.038228
4726 | 79.24 | 14.696 | 0.073627 | 19.049 | 0.038232 |  | 4726 | 19.049 | 79.24 | 14.696 | 0.073627 | 0.038232
4727 | 79.25 | 14.696 | 0.073625 | 19.051 | 0.038237 |  | 4727 | 19.051 | 79.25 | 14.696 | 0.073625 | 0.038237
4728 | 79.26 | 14.696 | 0.073624 | 19.054 | 0.038241 |  | 4728 | 19.054 | 79.26 | 14.696 | 0.073624 | 0.038241
4729 | 79.27 | 14.696 | 0.073623 | 19.056 | 0.038246 |  | 4729 | 19.056 | 79.27 | 14.696 | 0.073623 | 0.038246
4730 | 79.28 | 14.696 | 0.073621 | 19.059 | 0.03825 |  | 4730 | 19.059 | 79.28 | 14.696 | 0.073621 | 0.03825
4731 | 79.29 | 14.696 | 0.07362 | 19.061 | 0.038254 |  | 4731 | 19.061 | 79.29 | 14.696 | 0.07362 | 0.038254
4732 | 79.3 | 14.696 | 0.073618 | 19.063 | 0.038259 |  | 4732 | 19.063 | 79.3 | 14.696 | 0.073618 | 0.038259
4733 | 79.31 | 14.696 | 0.073617 | 19.066 | 0.038263 |  | 4733 | 19.066 | 79.31 | 14.696 | 0.073617 | 0.038263
4734 | 79.32 | 14.696 | 0.073616 | 19.068 | 0.038268 |  | 4734 | 19.068 | 79.32 | 14.696 | 0.073616 | 0.038268
4735 | 79.33 | 14.696 | 0.073614 | 19.071 | 0.038272 |  | 4735 | 19.071 | 79.33 | 14.696 | 0.073614 | 0.038272
4736 | 79.34 | 14.696 | 0.073613 | 19.073 | 0.038277 |  | 4736 | 19.073 | 79.34 | 14.696 | 0.073613 | 0.038277
4737 | 79.35 | 14.696 | 0.073612 | 19.075 | 0.038281 |  | 4737 | 19.075 | 79.35 | 14.696 | 0.073612 | 0.038281
4738 | 79.36 | 14.696 | 0.07361 | 19.078 | 0.038286 |  | 4738 | 19.078 | 79.36 | 14.696 | 0.07361 | 0.038286
4739 | 79.37 | 14.696 | 0.073609 | 19.08 | 0.03829 |  | 4739 | 19.08 | 79.37 | 14.696 | 0.073609 | 0.03829
4740 | 79.38 | 14.696 | 0.073608 | 19.083 | 0.038295 |  | 4740 | 19.083 | 79.38 | 14.696 | 0.073608 | 0.038295
4741 | 79.39 | 14.696 | 0.073606 | 19.085 | 0.038299 |  | 4741 | 19.085 | 79.39 | 14.696 | 0.073606 | 0.038299
4742 | 79.4 | 14.696 | 0.073605 | 19.087 | 0.038304 |  | 4742 | 19.087 | 79.4 | 14.696 | 0.073605 | 0.038304
4743 | 79.41 | 14.696 | 0.073603 | 19.09 | 0.038308 |  | 4743 | 19.09 | 79.41 | 14.696 | 0.073603 | 0.038308
4744 | 79.42 | 14.696 | 0.073602 | 19.092 | 0.038313 |  | 4744 | 19.092 | 79.42 | 14.696 | 0.073602 | 0.038313
4745 | 79.43 | 14.696 | 0.073601 | 19.095 | 0.038317 |  | 4745 | 19.095 | 79.43 | 14.696 | 0.073601 | 0.038317
4746 | 79.44 | 14.696 | 0.073599 | 19.097 | 0.038321 |  | 4746 | 19.097 | 79.44 | 14.696 | 0.073599 | 0.038321
4747 | 79.45 | 14.696 | 0.073598 | 19.1 | 0.038326 |  | 4747 | 19.1 | 79.45 | 14.696 | 0.073598 | 0.038326
4748 | 79.46 | 14.696 | 0.073597 | 19.102 | 0.03833 |  | 4748 | 19.102 | 79.46 | 14.696 | 0.073597 | 0.03833
4749 | 79.47 | 14.696 | 0.073595 | 19.104 | 0.038335 |  | 4749 | 19.104 | 79.47 | 14.696 | 0.073595 | 0.038335
4750 | 79.48 | 14.696 | 0.073594 | 19.107 | 0.038339 |  | 4750 | 19.107 | 79.48 | 14.696 | 0.073594 | 0.038339
4751 | 79.49 | 14.696 | 0.073592 | 19.109 | 0.038344 |  | 4751 | 19.109 | 79.49 | 14.696 | 0.073592 | 0.038344
4752 | 79.5 | 14.696 | 0.073591 | 19.112 | 0.038348 |  | 4752 | 19.112 | 79.5 | 14.696 | 0.073591 | 0.038348
4753 | 79.51 | 14.696 | 0.07359 | 19.114 | 0.038353 |  | 4753 | 19.114 | 79.51 | 14.696 | 0.07359 | 0.038353
4754 | 79.52 | 14.696 | 0.073588 | 19.116 | 0.038357 |  | 4754 | 19.116 | 79.52 | 14.696 | 0.073588 | 0.038357
4755 | 79.53 | 14.696 | 0.073587 | 19.119 | 0.038362 |  | 4755 | 19.119 | 79.53 | 14.696 | 0.073587 | 0.038362
4756 | 79.54 | 14.696 | 0.073586 | 19.121 | 0.038366 |  | 4756 | 19.121 | 79.54 | 14.696 | 0.073586 | 0.038366
4757 | 79.55 | 14.696 | 0.073584 | 19.124 | 0.03837 |  | 4757 | 19.124 | 79.55 | 14.696 | 0.073584 | 0.03837
4758 | 79.56 | 14.696 | 0.073583 | 19.126 | 0.038375 |  | 4758 | 19.126 | 79.56 | 14.696 | 0.073583 | 0.038375
4759 | 79.57 | 14.696 | 0.073582 | 19.128 | 0.038379 |  | 4759 | 19.128 | 79.57 | 14.696 | 0.073582 | 0.038379
4760 | 79.58 | 14.696 | 0.07358 | 19.131 | 0.038384 |  | 4760 | 19.131 | 79.58 | 14.696 | 0.07358 | 0.038384
4761 | 79.59 | 14.696 | 0.073579 | 19.133 | 0.038388 |  | 4761 | 19.133 | 79.59 | 14.696 | 0.073579 | 0.038388
4762 | 79.6 | 14.696 | 0.073577 | 19.136 | 0.038393 |  | 4762 | 19.136 | 79.6 | 14.696 | 0.073577 | 0.038393
4763 | 79.61 | 14.696 | 0.073576 | 19.138 | 0.038397 |  | 4763 | 19.138 | 79.61 | 14.696 | 0.073576 | 0.038397
4764 | 79.62 | 14.696 | 0.073575 | 19.14 | 0.038402 |  | 4764 | 19.14 | 79.62 | 14.696 | 0.073575 | 0.038402
4765 | 79.63 | 14.696 | 0.073573 | 19.143 | 0.038406 |  | 4765 | 19.143 | 79.63 | 14.696 | 0.073573 | 0.038406
4766 | 79.64 | 14.696 | 0.073572 | 19.145 | 0.038411 |  | 4766 | 19.145 | 79.64 | 14.696 | 0.073572 | 0.038411
4767 | 79.65 | 14.696 | 0.073571 | 19.148 | 0.038415 |  | 4767 | 19.148 | 79.65 | 14.696 | 0.073571 | 0.038415
4768 | 79.66 | 14.696 | 0.073569 | 19.15 | 0.03842 |  | 4768 | 19.15 | 79.66 | 14.696 | 0.073569 | 0.03842
4769 | 79.67 | 14.696 | 0.073568 | 19.152 | 0.038424 |  | 4769 | 19.152 | 79.67 | 14.696 | 0.073568 | 0.038424
4770 | 79.68 | 14.696 | 0.073566 | 19.155 | 0.038428 |  | 4770 | 19.155 | 79.68 | 14.696 | 0.073566 | 0.038428
4771 | 79.69 | 14.696 | 0.073565 | 19.157 | 0.038433 |  | 4771 | 19.157 | 79.69 | 14.696 | 0.073565 | 0.038433
4772 | 79.7 | 14.696 | 0.073564 | 19.16 | 0.038437 |  | 4772 | 19.16 | 79.7 | 14.696 | 0.073564 | 0.038437
4773 | 79.71 | 14.696 | 0.073562 | 19.162 | 0.038442 |  | 4773 | 19.162 | 79.71 | 14.696 | 0.073562 | 0.038442
4774 | 79.72 | 14.696 | 0.073561 | 19.164 | 0.038446 |  | 4774 | 19.164 | 79.72 | 14.696 | 0.073561 | 0.038446
4775 | 79.73 | 14.696 | 0.07356 | 19.167 | 0.038451 |  | 4775 | 19.167 | 79.73 | 14.696 | 0.07356 | 0.038451
4776 | 79.74 | 14.696 | 0.073558 | 19.169 | 0.038455 |  | 4776 | 19.169 | 79.74 | 14.696 | 0.073558 | 0.038455
4777 | 79.75 | 14.696 | 0.073557 | 19.172 | 0.03846 |  | 4777 | 19.172 | 79.75 | 14.696 | 0.073557 | 0.03846
4778 | 79.76 | 14.696 | 0.073556 | 19.174 | 0.038464 |  | 4778 | 19.174 | 79.76 | 14.696 | 0.073556 | 0.038464
4779 | 79.77 | 14.696 | 0.073554 | 19.176 | 0.038469 |  | 4779 | 19.176 | 79.77 | 14.696 | 0.073554 | 0.038469
4780 | 79.78 | 14.696 | 0.073553 | 19.179 | 0.038473 |  | 4780 | 19.179 | 79.78 | 14.696 | 0.073553 | 0.038473
4781 | 79.79 | 14.696 | 0.073551 | 19.181 | 0.038478 |  | 4781 | 19.181 | 79.79 | 14.696 | 0.073551 | 0.038478
4782 | 79.8 | 14.696 | 0.07355 | 19.184 | 0.038482 |  | 4782 | 19.184 | 79.8 | 14.696 | 0.07355 | 0.038482
4783 | 79.81 | 14.696 | 0.073549 | 19.186 | 0.038486 |  | 4783 | 19.186 | 79.81 | 14.696 | 0.073549 | 0.038486
4784 | 79.82 | 14.696 | 0.073547 | 19.189 | 0.038491 |  | 4784 | 19.189 | 79.82 | 14.696 | 0.073547 | 0.038491
4785 | 79.83 | 14.696 | 0.073546 | 19.191 | 0.038495 |  | 4785 | 19.191 | 79.83 | 14.696 | 0.073546 | 0.038495
4786 | 79.84 | 14.696 | 0.073545 | 19.193 | 0.0385 |  | 4786 | 19.193 | 79.84 | 14.696 | 0.073545 | 0.0385
4787 | 79.85 | 14.696 | 0.073543 | 19.196 | 0.038504 |  | 4787 | 19.196 | 79.85 | 14.696 | 0.073543 | 0.038504
4788 | 79.86 | 14.696 | 0.073542 | 19.198 | 0.038509 |  | 4788 | 19.198 | 79.86 | 14.696 | 0.073542 | 0.038509
4789 | 79.87 | 14.696 | 0.073541 | 19.201 | 0.038513 |  | 4789 | 19.201 | 79.87 | 14.696 | 0.073541 | 0.038513
4790 | 79.88 | 14.696 | 0.073539 | 19.203 | 0.038518 |  | 4790 | 19.203 | 79.88 | 14.696 | 0.073539 | 0.038518
4791 | 79.89 | 14.696 | 0.073538 | 19.205 | 0.038522 |  | 4791 | 19.205 | 79.89 | 14.696 | 0.073538 | 0.038522
4792 | 79.9 | 14.696 | 0.073536 | 19.208 | 0.038527 |  | 4792 | 19.208 | 79.9 | 14.696 | 0.073536 | 0.038527
4793 | 79.91 | 14.696 | 0.073535 | 19.21 | 0.038531 |  | 4793 | 19.21 | 79.91 | 14.696 | 0.073535 | 0.038531
4794 | 79.92 | 14.696 | 0.073534 | 19.213 | 0.038535 |  | 4794 | 19.213 | 79.92 | 14.696 | 0.073534 | 0.038535
4795 | 79.93 | 14.696 | 0.073532 | 19.215 | 0.03854 |  | 4795 | 19.215 | 79.93 | 14.696 | 0.073532 | 0.03854
4796 | 79.94 | 14.696 | 0.073531 | 19.217 | 0.038544 |  | 4796 | 19.217 | 79.94 | 14.696 | 0.073531 | 0.038544
4797 | 79.95 | 14.696 | 0.07353 | 19.22 | 0.038549 |  | 4797 | 19.22 | 79.95 | 14.696 | 0.07353 | 0.038549
4798 | 79.96 | 14.696 | 0.073528 | 19.222 | 0.038553 |  | 4798 | 19.222 | 79.96 | 14.696 | 0.073528 | 0.038553
4799 | 79.97 | 14.696 | 0.073527 | 19.225 | 0.038558 |  | 4799 | 19.225 | 79.97 | 14.696 | 0.073527 | 0.038558
4800 | 79.98 | 14.696 | 0.073525 | 19.227 | 0.038562 |  | 4800 | 19.227 | 79.98 | 14.696 | 0.073525 | 0.038562
4801 | 79.99 | 14.696 | 0.073524 | 19.229 | 0.038567 |  | 4801 | 19.229 | 79.99 | 14.696 | 0.073524 | 0.038567
4802 | 80 | 14.696 | 0.073523 | 19.232 | 0.038571 |  | 4802 | 19.232 | 80 | 14.696 | 0.073523 | 0.038571
4803 | 80.01 | 14.696 | 0.073521 | 19.234 | 0.038576 |  | 4803 | 19.234 | 80.01 | 14.696 | 0.073521 | 0.038576
4804 | 80.02 | 14.696 | 0.07352 | 19.237 | 0.03858 |  | 4804 | 19.237 | 80.02 | 14.696 | 0.07352 | 0.03858
4805 | 80.03 | 14.696 | 0.073519 | 19.239 | 0.038585 |  | 4805 | 19.239 | 80.03 | 14.696 | 0.073519 | 0.038585
4806 | 80.04 | 14.696 | 0.073517 | 19.241 | 0.038589 |  | 4806 | 19.241 | 80.04 | 14.696 | 0.073517 | 0.038589
4807 | 80.05 | 14.696 | 0.073516 | 19.244 | 0.038593 |  | 4807 | 19.244 | 80.05 | 14.696 | 0.073516 | 0.038593
4808 | 80.06 | 14.696 | 0.073515 | 19.246 | 0.038598 |  | 4808 | 19.246 | 80.06 | 14.696 | 0.073515 | 0.038598
4809 | 80.07 | 14.696 | 0.073513 | 19.249 | 0.038602 |  | 4809 | 19.249 | 80.07 | 14.696 | 0.073513 | 0.038602
4810 | 80.08 | 14.696 | 0.073512 | 19.251 | 0.038607 |  | 4810 | 19.251 | 80.08 | 14.696 | 0.073512 | 0.038607
4811 | 80.09 | 14.696 | 0.07351 | 19.253 | 0.038611 |  | 4811 | 19.253 | 80.09 | 14.696 | 0.07351 | 0.038611
4812 | 80.1 | 14.696 | 0.073509 | 19.256 | 0.038616 |  | 4812 | 19.256 | 80.1 | 14.696 | 0.073509 | 0.038616
4813 | 80.11 | 14.696 | 0.073508 | 19.258 | 0.03862 |  | 4813 | 19.258 | 80.11 | 14.696 | 0.073508 | 0.03862
4814 | 80.12 | 14.696 | 0.073506 | 19.261 | 0.038625 |  | 4814 | 19.261 | 80.12 | 14.696 | 0.073506 | 0.038625
4815 | 80.13 | 14.696 | 0.073505 | 19.263 | 0.038629 |  | 4815 | 19.263 | 80.13 | 14.696 | 0.073505 | 0.038629
4816 | 80.14 | 14.696 | 0.073504 | 19.265 | 0.038634 |  | 4816 | 19.265 | 80.14 | 14.696 | 0.073504 | 0.038634
4817 | 80.15 | 14.696 | 0.073502 | 19.268 | 0.038638 |  | 4817 | 19.268 | 80.15 | 14.696 | 0.073502 | 0.038638
4818 | 80.16 | 14.696 | 0.073501 | 19.27 | 0.038642 |  | 4818 | 19.27 | 80.16 | 14.696 | 0.073501 | 0.038642
4819 | 80.17 | 14.696 | 0.0735 | 19.273 | 0.038647 |  | 4819 | 19.273 | 80.17 | 14.696 | 0.0735 | 0.038647
4820 | 80.18 | 14.696 | 0.073498 | 19.275 | 0.038651 |  | 4820 | 19.275 | 80.18 | 14.696 | 0.073498 | 0.038651
4821 | 80.19 | 14.696 | 0.073497 | 19.278 | 0.038656 |  | 4821 | 19.278 | 80.19 | 14.696 | 0.073497 | 0.038656
4822 | 80.2 | 14.696 | 0.073495 | 19.28 | 0.03866 |  | 4822 | 19.28 | 80.2 | 14.696 | 0.073495 | 0.03866
4823 | 80.21 | 14.696 | 0.073494 | 19.282 | 0.038665 |  | 4823 | 19.282 | 80.21 | 14.696 | 0.073494 | 0.038665
4824 | 80.22 | 14.696 | 0.073493 | 19.285 | 0.038669 |  | 4824 | 19.285 | 80.22 | 14.696 | 0.073493 | 0.038669
4825 | 80.23 | 14.696 | 0.073491 | 19.287 | 0.038674 |  | 4825 | 19.287 | 80.23 | 14.696 | 0.073491 | 0.038674
4826 | 80.24 | 14.696 | 0.07349 | 19.29 | 0.038678 |  | 4826 | 19.29 | 80.24 | 14.696 | 0.07349 | 0.038678
4827 | 80.25 | 14.696 | 0.073489 | 19.292 | 0.038683 |  | 4827 | 19.292 | 80.25 | 14.696 | 0.073489 | 0.038683
4828 | 80.26 | 14.696 | 0.073487 | 19.294 | 0.038687 |  | 4828 | 19.294 | 80.26 | 14.696 | 0.073487 | 0.038687
4829 | 80.27 | 14.696 | 0.073486 | 19.297 | 0.038691 |  | 4829 | 19.297 | 80.27 | 14.696 | 0.073486 | 0.038691
4830 | 80.28 | 14.696 | 0.073485 | 19.299 | 0.038696 |  | 4830 | 19.299 | 80.28 | 14.696 | 0.073485 | 0.038696
4831 | 80.29 | 14.696 | 0.073483 | 19.302 | 0.0387 |  | 4831 | 19.302 | 80.29 | 14.696 | 0.073483 | 0.0387
4832 | 80.3 | 14.696 | 0.073482 | 19.304 | 0.038705 |  | 4832 | 19.304 | 80.3 | 14.696 | 0.073482 | 0.038705
4833 | 80.31 | 14.696 | 0.07348 | 19.306 | 0.038709 |  | 4833 | 19.306 | 80.31 | 14.696 | 0.07348 | 0.038709
4834 | 80.32 | 14.696 | 0.073479 | 19.309 | 0.038714 |  | 4834 | 19.309 | 80.32 | 14.696 | 0.073479 | 0.038714
4835 | 80.33 | 14.696 | 0.073478 | 19.311 | 0.038718 |  | 4835 | 19.311 | 80.33 | 14.696 | 0.073478 | 0.038718
4836 | 80.34 | 14.696 | 0.073476 | 19.314 | 0.038723 |  | 4836 | 19.314 | 80.34 | 14.696 | 0.073476 | 0.038723
4837 | 80.35 | 14.696 | 0.073475 | 19.316 | 0.038727 |  | 4837 | 19.316 | 80.35 | 14.696 | 0.073475 | 0.038727
4838 | 80.36 | 14.696 | 0.073474 | 19.318 | 0.038732 |  | 4838 | 19.318 | 80.36 | 14.696 | 0.073474 | 0.038732
4839 | 80.37 | 14.696 | 0.073472 | 19.321 | 0.038736 |  | 4839 | 19.321 | 80.37 | 14.696 | 0.073472 | 0.038736
4840 | 80.38 | 14.696 | 0.073471 | 19.323 | 0.03874 |  | 4840 | 19.323 | 80.38 | 14.696 | 0.073471 | 0.03874
4841 | 80.39 | 14.696 | 0.07347 | 19.326 | 0.038745 |  | 4841 | 19.326 | 80.39 | 14.696 | 0.07347 | 0.038745
4842 | 80.4 | 14.696 | 0.073468 | 19.328 | 0.038749 |  | 4842 | 19.328 | 80.4 | 14.696 | 0.073468 | 0.038749
4843 | 80.41 | 14.696 | 0.073467 | 19.33 | 0.038754 |  | 4843 | 19.33 | 80.41 | 14.696 | 0.073467 | 0.038754
4844 | 80.42 | 14.696 | 0.073465 | 19.333 | 0.038758 |  | 4844 | 19.333 | 80.42 | 14.696 | 0.073465 | 0.038758
4845 | 80.43 | 14.696 | 0.073464 | 19.335 | 0.038763 |  | 4845 | 19.335 | 80.43 | 14.696 | 0.073464 | 0.038763
4846 | 80.44 | 14.696 | 0.073463 | 19.338 | 0.038767 |  | 4846 | 19.338 | 80.44 | 14.696 | 0.073463 | 0.038767
4847 | 80.45 | 14.696 | 0.073461 | 19.34 | 0.038772 |  | 4847 | 19.34 | 80.45 | 14.696 | 0.073461 | 0.038772
4848 | 80.46 | 14.696 | 0.07346 | 19.342 | 0.038776 |  | 4848 | 19.342 | 80.46 | 14.696 | 0.07346 | 0.038776
4849 | 80.47 | 14.696 | 0.073459 | 19.345 | 0.038781 |  | 4849 | 19.345 | 80.47 | 14.696 | 0.073459 | 0.038781
4850 | 80.48 | 14.696 | 0.073457 | 19.347 | 0.038785 |  | 4850 | 19.347 | 80.48 | 14.696 | 0.073457 | 0.038785
4851 | 80.49 | 14.696 | 0.073456 | 19.35 | 0.038789 |  | 4851 | 19.35 | 80.49 | 14.696 | 0.073456 | 0.038789
4852 | 80.5 | 14.696 | 0.073455 | 19.352 | 0.038794 |  | 4852 | 19.352 | 80.5 | 14.696 | 0.073455 | 0.038794
4853 | 80.51 | 14.696 | 0.073453 | 19.354 | 0.038798 |  | 4853 | 19.354 | 80.51 | 14.696 | 0.073453 | 0.038798
4854 | 80.52 | 14.696 | 0.073452 | 19.357 | 0.038803 |  | 4854 | 19.357 | 80.52 | 14.696 | 0.073452 | 0.038803
4855 | 80.53 | 14.696 | 0.07345 | 19.359 | 0.038807 |  | 4855 | 19.359 | 80.53 | 14.696 | 0.07345 | 0.038807
4856 | 80.54 | 14.696 | 0.073449 | 19.362 | 0.038812 |  | 4856 | 19.362 | 80.54 | 14.696 | 0.073449 | 0.038812
4857 | 80.55 | 14.696 | 0.073448 | 19.364 | 0.038816 |  | 4857 | 19.364 | 80.55 | 14.696 | 0.073448 | 0.038816
4858 | 80.56 | 14.696 | 0.073446 | 19.367 | 0.038821 |  | 4858 | 19.367 | 80.56 | 14.696 | 0.073446 | 0.038821
4859 | 80.57 | 14.696 | 0.073445 | 19.369 | 0.038825 |  | 4859 | 19.369 | 80.57 | 14.696 | 0.073445 | 0.038825
4860 | 80.58 | 14.696 | 0.073444 | 19.371 | 0.03883 |  | 4860 | 19.371 | 80.58 | 14.696 | 0.073444 | 0.03883
4861 | 80.59 | 14.696 | 0.073442 | 19.374 | 0.038834 |  | 4861 | 19.374 | 80.59 | 14.696 | 0.073442 | 0.038834
4862 | 80.6 | 14.696 | 0.073441 | 19.376 | 0.038838 |  | 4862 | 19.376 | 80.6 | 14.696 | 0.073441 | 0.038838
4863 | 80.61 | 14.696 | 0.07344 | 19.379 | 0.038843 |  | 4863 | 19.379 | 80.61 | 14.696 | 0.07344 | 0.038843
4864 | 80.62 | 14.696 | 0.073438 | 19.381 | 0.038847 |  | 4864 | 19.381 | 80.62 | 14.696 | 0.073438 | 0.038847
4865 | 80.63 | 14.696 | 0.073437 | 19.383 | 0.038852 |  | 4865 | 19.383 | 80.63 | 14.696 | 0.073437 | 0.038852
4866 | 80.64 | 14.696 | 0.073435 | 19.386 | 0.038856 |  | 4866 | 19.386 | 80.64 | 14.696 | 0.073435 | 0.038856
4867 | 80.65 | 14.696 | 0.073434 | 19.388 | 0.038861 |  | 4867 | 19.388 | 80.65 | 14.696 | 0.073434 | 0.038861
4868 | 80.66 | 14.696 | 0.073433 | 19.391 | 0.038865 |  | 4868 | 19.391 | 80.66 | 14.696 | 0.073433 | 0.038865
4869 | 80.67 | 14.696 | 0.073431 | 19.393 | 0.03887 |  | 4869 | 19.393 | 80.67 | 14.696 | 0.073431 | 0.03887
4870 | 80.68 | 14.696 | 0.07343 | 19.395 | 0.038874 |  | 4870 | 19.395 | 80.68 | 14.696 | 0.07343 | 0.038874
4871 | 80.69 | 14.696 | 0.073429 | 19.398 | 0.038878 |  | 4871 | 19.398 | 80.69 | 14.696 | 0.073429 | 0.038878
4872 | 80.7 | 14.696 | 0.073427 | 19.4 | 0.038883 |  | 4872 | 19.4 | 80.7 | 14.696 | 0.073427 | 0.038883
4873 | 80.71 | 14.696 | 0.073426 | 19.403 | 0.038887 |  | 4873 | 19.403 | 80.71 | 14.696 | 0.073426 | 0.038887
4874 | 80.72 | 14.696 | 0.073425 | 19.405 | 0.038892 |  | 4874 | 19.405 | 80.72 | 14.696 | 0.073425 | 0.038892
4875 | 80.73 | 14.696 | 0.073423 | 19.407 | 0.038896 |  | 4875 | 19.407 | 80.73 | 14.696 | 0.073423 | 0.038896
4876 | 80.74 | 14.696 | 0.073422 | 19.41 | 0.038901 |  | 4876 | 19.41 | 80.74 | 14.696 | 0.073422 | 0.038901
4877 | 80.75 | 14.696 | 0.07342 | 19.412 | 0.038905 |  | 4877 | 19.412 | 80.75 | 14.696 | 0.07342 | 0.038905
4878 | 80.76 | 14.696 | 0.073419 | 19.415 | 0.03891 |  | 4878 | 19.415 | 80.76 | 14.696 | 0.073419 | 0.03891
4879 | 80.77 | 14.696 | 0.073418 | 19.417 | 0.038914 |  | 4879 | 19.417 | 80.77 | 14.696 | 0.073418 | 0.038914
4880 | 80.78 | 14.696 | 0.073416 | 19.419 | 0.038919 |  | 4880 | 19.419 | 80.78 | 14.696 | 0.073416 | 0.038919
4881 | 80.79 | 14.696 | 0.073415 | 19.422 | 0.038923 |  | 4881 | 19.422 | 80.79 | 14.696 | 0.073415 | 0.038923
4882 | 80.8 | 14.696 | 0.073414 | 19.424 | 0.038927 |  | 4882 | 19.424 | 80.8 | 14.696 | 0.073414 | 0.038927
4883 | 80.81 | 14.696 | 0.073412 | 19.427 | 0.038932 |  | 4883 | 19.427 | 80.81 | 14.696 | 0.073412 | 0.038932
4884 | 80.82 | 14.696 | 0.073411 | 19.429 | 0.038936 |  | 4884 | 19.429 | 80.82 | 14.696 | 0.073411 | 0.038936
4885 | 80.83 | 14.696 | 0.07341 | 19.431 | 0.038941 |  | 4885 | 19.431 | 80.83 | 14.696 | 0.07341 | 0.038941
4886 | 80.84 | 14.696 | 0.073408 | 19.434 | 0.038945 |  | 4886 | 19.434 | 80.84 | 14.696 | 0.073408 | 0.038945
4887 | 80.85 | 14.696 | 0.073407 | 19.436 | 0.03895 |  | 4887 | 19.436 | 80.85 | 14.696 | 0.073407 | 0.03895
4888 | 80.86 | 14.696 | 0.073405 | 19.439 | 0.038954 |  | 4888 | 19.439 | 80.86 | 14.696 | 0.073405 | 0.038954
4889 | 80.87 | 14.696 | 0.073404 | 19.441 | 0.038959 |  | 4889 | 19.441 | 80.87 | 14.696 | 0.073404 | 0.038959
4890 | 80.88 | 14.696 | 0.073403 | 19.443 | 0.038963 |  | 4890 | 19.443 | 80.88 | 14.696 | 0.073403 | 0.038963
4891 | 80.89 | 14.696 | 0.073401 | 19.446 | 0.038967 |  | 4891 | 19.446 | 80.89 | 14.696 | 0.073401 | 0.038967
4892 | 80.9 | 14.696 | 0.0734 | 19.448 | 0.038972 |  | 4892 | 19.448 | 80.9 | 14.696 | 0.0734 | 0.038972
4893 | 80.91 | 14.696 | 0.073399 | 19.451 | 0.038976 |  | 4893 | 19.451 | 80.91 | 14.696 | 0.073399 | 0.038976
4894 | 80.92 | 14.696 | 0.073397 | 19.453 | 0.038981 |  | 4894 | 19.453 | 80.92 | 14.696 | 0.073397 | 0.038981
4895 | 80.93 | 14.696 | 0.073396 | 19.456 | 0.038985 |  | 4895 | 19.456 | 80.93 | 14.696 | 0.073396 | 0.038985
4896 | 80.94 | 14.696 | 0.073395 | 19.458 | 0.03899 |  | 4896 | 19.458 | 80.94 | 14.696 | 0.073395 | 0.03899
4897 | 80.95 | 14.696 | 0.073393 | 19.46 | 0.038994 |  | 4897 | 19.46 | 80.95 | 14.696 | 0.073393 | 0.038994
4898 | 80.96 | 14.696 | 0.073392 | 19.463 | 0.038999 |  | 4898 | 19.463 | 80.96 | 14.696 | 0.073392 | 0.038999
4899 | 80.97 | 14.696 | 0.07339 | 19.465 | 0.039003 |  | 4899 | 19.465 | 80.97 | 14.696 | 0.07339 | 0.039003
4900 | 80.98 | 14.696 | 0.073389 | 19.468 | 0.039008 |  | 4900 | 19.468 | 80.98 | 14.696 | 0.073389 | 0.039008
4901 | 80.99 | 14.696 | 0.073388 | 19.47 | 0.039012 |  | 4901 | 19.47 | 80.99 | 14.696 | 0.073388 | 0.039012
4902 | 81 | 14.696 | 0.073386 | 19.472 | 0.039016 |  | 4902 | 19.472 | 81 | 14.696 | 0.073386 | 0.039016
4903 | 81.01 | 14.696 | 0.073385 | 19.475 | 0.039021 |  | 4903 | 19.475 | 81.01 | 14.696 | 0.073385 | 0.039021
4904 | 81.02 | 14.696 | 0.073384 | 19.477 | 0.039025 |  | 4904 | 19.477 | 81.02 | 14.696 | 0.073384 | 0.039025
4905 | 81.03 | 14.696 | 0.073382 | 19.48 | 0.03903 |  | 4905 | 19.48 | 81.03 | 14.696 | 0.073382 | 0.03903
4906 | 81.04 | 14.696 | 0.073381 | 19.482 | 0.039034 |  | 4906 | 19.482 | 81.04 | 14.696 | 0.073381 | 0.039034
4907 | 81.05 | 14.696 | 0.07338 | 19.484 | 0.039039 |  | 4907 | 19.484 | 81.05 | 14.696 | 0.07338 | 0.039039
4908 | 81.06 | 14.696 | 0.073378 | 19.487 | 0.039043 |  | 4908 | 19.487 | 81.06 | 14.696 | 0.073378 | 0.039043
4909 | 81.07 | 14.696 | 0.073377 | 19.489 | 0.039048 |  | 4909 | 19.489 | 81.07 | 14.696 | 0.073377 | 0.039048
4910 | 81.08 | 14.696 | 0.073376 | 19.492 | 0.039052 |  | 4910 | 19.492 | 81.08 | 14.696 | 0.073376 | 0.039052
4911 | 81.09 | 14.696 | 0.073374 | 19.494 | 0.039056 |  | 4911 | 19.494 | 81.09 | 14.696 | 0.073374 | 0.039056
4912 | 81.1 | 14.696 | 0.073373 | 19.496 | 0.039061 |  | 4912 | 19.496 | 81.1 | 14.696 | 0.073373 | 0.039061
4913 | 81.11 | 14.696 | 0.073371 | 19.499 | 0.039065 |  | 4913 | 19.499 | 81.11 | 14.696 | 0.073371 | 0.039065
4914 | 81.12 | 14.696 | 0.07337 | 19.501 | 0.03907 |  | 4914 | 19.501 | 81.12 | 14.696 | 0.07337 | 0.03907
4915 | 81.13 | 14.696 | 0.073369 | 19.504 | 0.039074 |  | 4915 | 19.504 | 81.13 | 14.696 | 0.073369 | 0.039074
4916 | 81.14 | 14.696 | 0.073367 | 19.506 | 0.039079 |  | 4916 | 19.506 | 81.14 | 14.696 | 0.073367 | 0.039079
4917 | 81.15 | 14.696 | 0.073366 | 19.508 | 0.039083 |  | 4917 | 19.508 | 81.15 | 14.696 | 0.073366 | 0.039083
4918 | 81.16 | 14.696 | 0.073365 | 19.511 | 0.039088 |  | 4918 | 19.511 | 81.16 | 14.696 | 0.073365 | 0.039088
4919 | 81.17 | 14.696 | 0.073363 | 19.513 | 0.039092 |  | 4919 | 19.513 | 81.17 | 14.696 | 0.073363 | 0.039092
4920 | 81.18 | 14.696 | 0.073362 | 19.516 | 0.039096 |  | 4920 | 19.516 | 81.18 | 14.696 | 0.073362 | 0.039096
4921 | 81.19 | 14.696 | 0.073361 | 19.518 | 0.039101 |  | 4921 | 19.518 | 81.19 | 14.696 | 0.073361 | 0.039101
4922 | 81.2 | 14.696 | 0.073359 | 19.52 | 0.039105 |  | 4922 | 19.52 | 81.2 | 14.696 | 0.073359 | 0.039105
4923 | 81.21 | 14.696 | 0.073358 | 19.523 | 0.03911 |  | 4923 | 19.523 | 81.21 | 14.696 | 0.073358 | 0.03911
4924 | 81.22 | 14.696 | 0.073356 | 19.525 | 0.039114 |  | 4924 | 19.525 | 81.22 | 14.696 | 0.073356 | 0.039114
4925 | 81.23 | 14.696 | 0.073355 | 19.528 | 0.039119 |  | 4925 | 19.528 | 81.23 | 14.696 | 0.073355 | 0.039119
4926 | 81.24 | 14.696 | 0.073354 | 19.53 | 0.039123 |  | 4926 | 19.53 | 81.24 | 14.696 | 0.073354 | 0.039123
4927 | 81.25 | 14.696 | 0.073352 | 19.532 | 0.039128 |  | 4927 | 19.532 | 81.25 | 14.696 | 0.073352 | 0.039128
4928 | 81.26 | 14.696 | 0.073351 | 19.535 | 0.039132 |  | 4928 | 19.535 | 81.26 | 14.696 | 0.073351 | 0.039132
4929 | 81.27 | 14.696 | 0.07335 | 19.537 | 0.039137 |  | 4929 | 19.537 | 81.27 | 14.696 | 0.07335 | 0.039137
4930 | 81.28 | 14.696 | 0.073348 | 19.54 | 0.039141 |  | 4930 | 19.54 | 81.28 | 14.696 | 0.073348 | 0.039141
4931 | 81.29 | 14.696 | 0.073347 | 19.542 | 0.039145 |  | 4931 | 19.542 | 81.29 | 14.696 | 0.073347 | 0.039145
4932 | 81.3 | 14.696 | 0.073346 | 19.545 | 0.03915 |  | 4932 | 19.545 | 81.3 | 14.696 | 0.073346 | 0.03915
4933 | 81.31 | 14.696 | 0.073344 | 19.547 | 0.039154 |  | 4933 | 19.547 | 81.31 | 14.696 | 0.073344 | 0.039154
4934 | 81.32 | 14.696 | 0.073343 | 19.549 | 0.039159 |  | 4934 | 19.549 | 81.32 | 14.696 | 0.073343 | 0.039159
4935 | 81.33 | 14.696 | 0.073342 | 19.552 | 0.039163 |  | 4935 | 19.552 | 81.33 | 14.696 | 0.073342 | 0.039163
4936 | 81.34 | 14.696 | 0.07334 | 19.554 | 0.039168 |  | 4936 | 19.554 | 81.34 | 14.696 | 0.07334 | 0.039168
4937 | 81.35 | 14.696 | 0.073339 | 19.557 | 0.039172 |  | 4937 | 19.557 | 81.35 | 14.696 | 0.073339 | 0.039172
4938 | 81.36 | 14.696 | 0.073337 | 19.559 | 0.039177 |  | 4938 | 19.559 | 81.36 | 14.696 | 0.073337 | 0.039177
4939 | 81.37 | 14.696 | 0.073336 | 19.561 | 0.039181 |  | 4939 | 19.561 | 81.37 | 14.696 | 0.073336 | 0.039181
4940 | 81.38 | 14.696 | 0.073335 | 19.564 | 0.039185 |  | 4940 | 19.564 | 81.38 | 14.696 | 0.073335 | 0.039185
4941 | 81.39 | 14.696 | 0.073333 | 19.566 | 0.03919 |  | 4941 | 19.566 | 81.39 | 14.696 | 0.073333 | 0.03919
4942 | 81.4 | 14.696 | 0.073332 | 19.569 | 0.039194 |  | 4942 | 19.569 | 81.4 | 14.696 | 0.073332 | 0.039194
4943 | 81.41 | 14.696 | 0.073331 | 19.571 | 0.039199 |  | 4943 | 19.571 | 81.41 | 14.696 | 0.073331 | 0.039199
4944 | 81.42 | 14.696 | 0.073329 | 19.573 | 0.039203 |  | 4944 | 19.573 | 81.42 | 14.696 | 0.073329 | 0.039203
4945 | 81.43 | 14.696 | 0.073328 | 19.576 | 0.039208 |  | 4945 | 19.576 | 81.43 | 14.696 | 0.073328 | 0.039208
4946 | 81.44 | 14.696 | 0.073327 | 19.578 | 0.039212 |  | 4946 | 19.578 | 81.44 | 14.696 | 0.073327 | 0.039212
4947 | 81.45 | 14.696 | 0.073325 | 19.581 | 0.039217 |  | 4947 | 19.581 | 81.45 | 14.696 | 0.073325 | 0.039217
4948 | 81.46 | 14.696 | 0.073324 | 19.583 | 0.039221 |  | 4948 | 19.583 | 81.46 | 14.696 | 0.073324 | 0.039221
4949 | 81.47 | 14.696 | 0.073322 | 19.585 | 0.039225 |  | 4949 | 19.585 | 81.47 | 14.696 | 0.073322 | 0.039225
4950 | 81.48 | 14.696 | 0.073321 | 19.588 | 0.03923 |  | 4950 | 19.588 | 81.48 | 14.696 | 0.073321 | 0.03923
4951 | 81.49 | 14.696 | 0.07332 | 19.59 | 0.039234 |  | 4951 | 19.59 | 81.49 | 14.696 | 0.07332 | 0.039234
4952 | 81.5 | 14.696 | 0.073318 | 19.593 | 0.039239 |  | 4952 | 19.593 | 81.5 | 14.696 | 0.073318 | 0.039239
4953 | 81.51 | 14.696 | 0.073317 | 19.595 | 0.039243 |  | 4953 | 19.595 | 81.51 | 14.696 | 0.073317 | 0.039243
4954 | 81.52 | 14.696 | 0.073316 | 19.597 | 0.039248 |  | 4954 | 19.597 | 81.52 | 14.696 | 0.073316 | 0.039248
4955 | 81.53 | 14.696 | 0.073314 | 19.6 | 0.039252 |  | 4955 | 19.6 | 81.53 | 14.696 | 0.073314 | 0.039252
4956 | 81.54 | 14.696 | 0.073313 | 19.602 | 0.039257 |  | 4956 | 19.602 | 81.54 | 14.696 | 0.073313 | 0.039257
4957 | 81.55 | 14.696 | 0.073312 | 19.605 | 0.039261 |  | 4957 | 19.605 | 81.55 | 14.696 | 0.073312 | 0.039261
4958 | 81.56 | 14.696 | 0.07331 | 19.607 | 0.039265 |  | 4958 | 19.607 | 81.56 | 14.696 | 0.07331 | 0.039265
4959 | 81.57 | 14.696 | 0.073309 | 19.609 | 0.03927 |  | 4959 | 19.609 | 81.57 | 14.696 | 0.073309 | 0.03927
4960 | 81.58 | 14.696 | 0.073308 | 19.612 | 0.039274 |  | 4960 | 19.612 | 81.58 | 14.696 | 0.073308 | 0.039274
4961 | 81.59 | 14.696 | 0.073306 | 19.614 | 0.039279 |  | 4961 | 19.614 | 81.59 | 14.696 | 0.073306 | 0.039279
4962 | 81.6 | 14.696 | 0.073305 | 19.617 | 0.039283 |  | 4962 | 19.617 | 81.6 | 14.696 | 0.073305 | 0.039283
4963 | 81.61 | 14.696 | 0.073303 | 19.619 | 0.039288 |  | 4963 | 19.619 | 81.61 | 14.696 | 0.073303 | 0.039288
4964 | 81.62 | 14.696 | 0.073302 | 19.621 | 0.039292 |  | 4964 | 19.621 | 81.62 | 14.696 | 0.073302 | 0.039292
4965 | 81.63 | 14.696 | 0.073301 | 19.624 | 0.039297 |  | 4965 | 19.624 | 81.63 | 14.696 | 0.073301 | 0.039297
4966 | 81.64 | 14.696 | 0.073299 | 19.626 | 0.039301 |  | 4966 | 19.626 | 81.64 | 14.696 | 0.073299 | 0.039301
4967 | 81.65 | 14.696 | 0.073298 | 19.629 | 0.039305 |  | 4967 | 19.629 | 81.65 | 14.696 | 0.073298 | 0.039305
4968 | 81.66 | 14.696 | 0.073297 | 19.631 | 0.03931 |  | 4968 | 19.631 | 81.66 | 14.696 | 0.073297 | 0.03931
4969 | 81.67 | 14.696 | 0.073295 | 19.633 | 0.039314 |  | 4969 | 19.633 | 81.67 | 14.696 | 0.073295 | 0.039314
4970 | 81.68 | 14.696 | 0.073294 | 19.636 | 0.039319 |  | 4970 | 19.636 | 81.68 | 14.696 | 0.073294 | 0.039319
4971 | 81.69 | 14.696 | 0.073293 | 19.638 | 0.039323 |  | 4971 | 19.638 | 81.69 | 14.696 | 0.073293 | 0.039323
4972 | 81.7 | 14.696 | 0.073291 | 19.641 | 0.039328 |  | 4972 | 19.641 | 81.7 | 14.696 | 0.073291 | 0.039328
4973 | 81.71 | 14.696 | 0.07329 | 19.643 | 0.039332 |  | 4973 | 19.643 | 81.71 | 14.696 | 0.07329 | 0.039332
4974 | 81.72 | 14.696 | 0.073289 | 19.646 | 0.039337 |  | 4974 | 19.646 | 81.72 | 14.696 | 0.073289 | 0.039337
4975 | 81.73 | 14.696 | 0.073287 | 19.648 | 0.039341 |  | 4975 | 19.648 | 81.73 | 14.696 | 0.073287 | 0.039341
4976 | 81.74 | 14.696 | 0.073286 | 19.65 | 0.039345 |  | 4976 | 19.65 | 81.74 | 14.696 | 0.073286 | 0.039345
4977 | 81.75 | 14.696 | 0.073284 | 19.653 | 0.03935 |  | 4977 | 19.653 | 81.75 | 14.696 | 0.073284 | 0.03935
4978 | 81.76 | 14.696 | 0.073283 | 19.655 | 0.039354 |  | 4978 | 19.655 | 81.76 | 14.696 | 0.073283 | 0.039354
4979 | 81.77 | 14.696 | 0.073282 | 19.658 | 0.039359 |  | 4979 | 19.658 | 81.77 | 14.696 | 0.073282 | 0.039359
4980 | 81.78 | 14.696 | 0.07328 | 19.66 | 0.039363 |  | 4980 | 19.66 | 81.78 | 14.696 | 0.07328 | 0.039363
4981 | 81.79 | 14.696 | 0.073279 | 19.662 | 0.039368 |  | 4981 | 19.662 | 81.79 | 14.696 | 0.073279 | 0.039368
4982 | 81.8 | 14.696 | 0.073278 | 19.665 | 0.039372 |  | 4982 | 19.665 | 81.8 | 14.696 | 0.073278 | 0.039372
4983 | 81.81 | 14.696 | 0.073276 | 19.667 | 0.039377 |  | 4983 | 19.667 | 81.81 | 14.696 | 0.073276 | 0.039377
4984 | 81.82 | 14.696 | 0.073275 | 19.67 | 0.039381 |  | 4984 | 19.67 | 81.82 | 14.696 | 0.073275 | 0.039381
4985 | 81.83 | 14.696 | 0.073274 | 19.672 | 0.039385 |  | 4985 | 19.672 | 81.83 | 14.696 | 0.073274 | 0.039385
4986 | 81.84 | 14.696 | 0.073272 | 19.674 | 0.03939 |  | 4986 | 19.674 | 81.84 | 14.696 | 0.073272 | 0.03939
4987 | 81.85 | 14.696 | 0.073271 | 19.677 | 0.039394 |  | 4987 | 19.677 | 81.85 | 14.696 | 0.073271 | 0.039394
4988 | 81.86 | 14.696 | 0.07327 | 19.679 | 0.039399 |  | 4988 | 19.679 | 81.86 | 14.696 | 0.07327 | 0.039399
4989 | 81.87 | 14.696 | 0.073268 | 19.682 | 0.039403 |  | 4989 | 19.682 | 81.87 | 14.696 | 0.073268 | 0.039403
4990 | 81.88 | 14.696 | 0.073267 | 19.684 | 0.039408 |  | 4990 | 19.684 | 81.88 | 14.696 | 0.073267 | 0.039408
4991 | 81.89 | 14.696 | 0.073265 | 19.686 | 0.039412 |  | 4991 | 19.686 | 81.89 | 14.696 | 0.073265 | 0.039412
4992 | 81.9 | 14.696 | 0.073264 | 19.689 | 0.039416 |  | 4992 | 19.689 | 81.9 | 14.696 | 0.073264 | 0.039416
4993 | 81.91 | 14.696 | 0.073263 | 19.691 | 0.039421 |  | 4993 | 19.691 | 81.91 | 14.696 | 0.073263 | 0.039421
4994 | 81.92 | 14.696 | 0.073261 | 19.694 | 0.039425 |  | 4994 | 19.694 | 81.92 | 14.696 | 0.073261 | 0.039425
4995 | 81.93 | 14.696 | 0.07326 | 19.696 | 0.03943 |  | 4995 | 19.696 | 81.93 | 14.696 | 0.07326 | 0.03943
4996 | 81.94 | 14.696 | 0.073259 | 19.698 | 0.039434 |  | 4996 | 19.698 | 81.94 | 14.696 | 0.073259 | 0.039434
4997 | 81.95 | 14.696 | 0.073257 | 19.701 | 0.039439 |  | 4997 | 19.701 | 81.95 | 14.696 | 0.073257 | 0.039439
4998 | 81.96 | 14.696 | 0.073256 | 19.703 | 0.039443 |  | 4998 | 19.703 | 81.96 | 14.696 | 0.073256 | 0.039443
4999 | 81.97 | 14.696 | 0.073255 | 19.706 | 0.039448 |  | 4999 | 19.706 | 81.97 | 14.696 | 0.073255 | 0.039448
5000 | 81.98 | 14.696 | 0.073253 | 19.708 | 0.039452 |  | 5000 | 19.708 | 81.98 | 14.696 | 0.073253 | 0.039452
5001 | 81.99 | 14.696 | 0.073252 | 19.71 | 0.039456 |  | 5001 | 19.71 | 81.99 | 14.696 | 0.073252 | 0.039456
5002 | 82 | 14.696 | 0.073251 | 19.713 | 0.039461 |  | 5002 | 19.713 | 82 | 14.696 | 0.073251 | 0.039461
5003 | 82.01 | 14.696 | 0.073249 | 19.715 | 0.039465 |  | 5003 | 19.715 | 82.01 | 14.696 | 0.073249 | 0.039465
5004 | 82.02 | 14.696 | 0.073248 | 19.718 | 0.03947 |  | 5004 | 19.718 | 82.02 | 14.696 | 0.073248 | 0.03947
5005 | 82.03 | 14.696 | 0.073246 | 19.72 | 0.039474 |  | 5005 | 19.72 | 82.03 | 14.696 | 0.073246 | 0.039474
5006 | 82.04 | 14.696 | 0.073245 | 19.722 | 0.039479 |  | 5006 | 19.722 | 82.04 | 14.696 | 0.073245 | 0.039479
5007 | 82.05 | 14.696 | 0.073244 | 19.725 | 0.039483 |  | 5007 | 19.725 | 82.05 | 14.696 | 0.073244 | 0.039483
5008 | 82.06 | 14.696 | 0.073242 | 19.727 | 0.039488 |  | 5008 | 19.727 | 82.06 | 14.696 | 0.073242 | 0.039488
5009 | 82.07 | 14.696 | 0.073241 | 19.73 | 0.039492 |  | 5009 | 19.73 | 82.07 | 14.696 | 0.073241 | 0.039492
5010 | 82.08 | 14.696 | 0.07324 | 19.732 | 0.039496 |  | 5010 | 19.732 | 82.08 | 14.696 | 0.07324 | 0.039496
5011 | 82.09 | 14.696 | 0.073238 | 19.735 | 0.039501 |  | 5011 | 19.735 | 82.09 | 14.696 | 0.073238 | 0.039501
5012 | 82.1 | 14.696 | 0.073237 | 19.737 | 0.039505 |  | 5012 | 19.737 | 82.1 | 14.696 | 0.073237 | 0.039505
5013 | 82.11 | 14.696 | 0.073236 | 19.739 | 0.03951 |  | 5013 | 19.739 | 82.11 | 14.696 | 0.073236 | 0.03951
5014 | 82.12 | 14.696 | 0.073234 | 19.742 | 0.039514 |  | 5014 | 19.742 | 82.12 | 14.696 | 0.073234 | 0.039514
5015 | 82.13 | 14.696 | 0.073233 | 19.744 | 0.039519 |  | 5015 | 19.744 | 82.13 | 14.696 | 0.073233 | 0.039519
5016 | 82.14 | 14.696 | 0.073232 | 19.747 | 0.039523 |  | 5016 | 19.747 | 82.14 | 14.696 | 0.073232 | 0.039523
5017 | 82.15 | 14.696 | 0.07323 | 19.749 | 0.039527 |  | 5017 | 19.749 | 82.15 | 14.696 | 0.07323 | 0.039527
5018 | 82.16 | 14.696 | 0.073229 | 19.751 | 0.039532 |  | 5018 | 19.751 | 82.16 | 14.696 | 0.073229 | 0.039532
5019 | 82.17 | 14.696 | 0.073228 | 19.754 | 0.039536 |  | 5019 | 19.754 | 82.17 | 14.696 | 0.073228 | 0.039536
5020 | 82.18 | 14.696 | 0.073226 | 19.756 | 0.039541 |  | 5020 | 19.756 | 82.18 | 14.696 | 0.073226 | 0.039541
5021 | 82.19 | 14.696 | 0.073225 | 19.759 | 0.039545 |  | 5021 | 19.759 | 82.19 | 14.696 | 0.073225 | 0.039545
5022 | 82.2 | 14.696 | 0.073223 | 19.761 | 0.03955 |  | 5022 | 19.761 | 82.2 | 14.696 | 0.073223 | 0.03955
5023 | 82.21 | 14.696 | 0.073222 | 19.763 | 0.039554 |  | 5023 | 19.763 | 82.21 | 14.696 | 0.073222 | 0.039554
5024 | 82.22 | 14.696 | 0.073221 | 19.766 | 0.039559 |  | 5024 | 19.766 | 82.22 | 14.696 | 0.073221 | 0.039559
5025 | 82.23 | 14.696 | 0.073219 | 19.768 | 0.039563 |  | 5025 | 19.768 | 82.23 | 14.696 | 0.073219 | 0.039563
5026 | 82.24 | 14.696 | 0.073218 | 19.771 | 0.039567 |  | 5026 | 19.771 | 82.24 | 14.696 | 0.073218 | 0.039567
5027 | 82.25 | 14.696 | 0.073217 | 19.773 | 0.039572 |  | 5027 | 19.773 | 82.25 | 14.696 | 0.073217 | 0.039572
5028 | 82.26 | 14.696 | 0.073215 | 19.775 | 0.039576 |  | 5028 | 19.775 | 82.26 | 14.696 | 0.073215 | 0.039576
5029 | 82.27 | 14.696 | 0.073214 | 19.778 | 0.039581 |  | 5029 | 19.778 | 82.27 | 14.696 | 0.073214 | 0.039581
5030 | 82.28 | 14.696 | 0.073213 | 19.78 | 0.039585 |  | 5030 | 19.78 | 82.28 | 14.696 | 0.073213 | 0.039585
5031 | 82.29 | 14.696 | 0.073211 | 19.783 | 0.03959 |  | 5031 | 19.783 | 82.29 | 14.696 | 0.073211 | 0.03959
5032 | 82.3 | 14.696 | 0.07321 | 19.785 | 0.039594 |  | 5032 | 19.785 | 82.3 | 14.696 | 0.07321 | 0.039594
5033 | 82.31 | 14.696 | 0.073209 | 19.787 | 0.039599 |  | 5033 | 19.787 | 82.31 | 14.696 | 0.073209 | 0.039599
5034 | 82.32 | 14.696 | 0.073207 | 19.79 | 0.039603 |  | 5034 | 19.79 | 82.32 | 14.696 | 0.073207 | 0.039603
5035 | 82.33 | 14.696 | 0.073206 | 19.792 | 0.039607 |  | 5035 | 19.792 | 82.33 | 14.696 | 0.073206 | 0.039607
5036 | 82.34 | 14.696 | 0.073204 | 19.795 | 0.039612 |  | 5036 | 19.795 | 82.34 | 14.696 | 0.073204 | 0.039612
5037 | 82.35 | 14.696 | 0.073203 | 19.797 | 0.039616 |  | 5037 | 19.797 | 82.35 | 14.696 | 0.073203 | 0.039616
5038 | 82.36 | 14.696 | 0.073202 | 19.799 | 0.039621 |  | 5038 | 19.799 | 82.36 | 14.696 | 0.073202 | 0.039621
5039 | 82.37 | 14.696 | 0.0732 | 19.802 | 0.039625 |  | 5039 | 19.802 | 82.37 | 14.696 | 0.0732 | 0.039625
5040 | 82.38 | 14.696 | 0.073199 | 19.804 | 0.03963 |  | 5040 | 19.804 | 82.38 | 14.696 | 0.073199 | 0.03963
5041 | 82.39 | 14.696 | 0.073198 | 19.807 | 0.039634 |  | 5041 | 19.807 | 82.39 | 14.696 | 0.073198 | 0.039634
5042 | 82.4 | 14.696 | 0.073196 | 19.809 | 0.039638 |  | 5042 | 19.809 | 82.4 | 14.696 | 0.073196 | 0.039638
5043 | 82.41 | 14.696 | 0.073195 | 19.811 | 0.039643 |  | 5043 | 19.811 | 82.41 | 14.696 | 0.073195 | 0.039643
5044 | 82.42 | 14.696 | 0.073194 | 19.814 | 0.039647 |  | 5044 | 19.814 | 82.42 | 14.696 | 0.073194 | 0.039647
5045 | 82.43 | 14.696 | 0.073192 | 19.816 | 0.039652 |  | 5045 | 19.816 | 82.43 | 14.696 | 0.073192 | 0.039652
5046 | 82.44 | 14.696 | 0.073191 | 19.819 | 0.039656 |  | 5046 | 19.819 | 82.44 | 14.696 | 0.073191 | 0.039656
5047 | 82.45 | 14.696 | 0.07319 | 19.821 | 0.039661 |  | 5047 | 19.821 | 82.45 | 14.696 | 0.07319 | 0.039661
5048 | 82.46 | 14.696 | 0.073188 | 19.824 | 0.039665 |  | 5048 | 19.824 | 82.46 | 14.696 | 0.073188 | 0.039665
5049 | 82.47 | 14.696 | 0.073187 | 19.826 | 0.03967 |  | 5049 | 19.826 | 82.47 | 14.696 | 0.073187 | 0.03967
5050 | 82.48 | 14.696 | 0.073186 | 19.828 | 0.039674 |  | 5050 | 19.828 | 82.48 | 14.696 | 0.073186 | 0.039674
5051 | 82.49 | 14.696 | 0.073184 | 19.831 | 0.039678 |  | 5051 | 19.831 | 82.49 | 14.696 | 0.073184 | 0.039678
5052 | 82.5 | 14.696 | 0.073183 | 19.833 | 0.039683 |  | 5052 | 19.833 | 82.5 | 14.696 | 0.073183 | 0.039683
5053 | 82.51 | 14.696 | 0.073181 | 19.836 | 0.039687 |  | 5053 | 19.836 | 82.51 | 14.696 | 0.073181 | 0.039687
5054 | 82.52 | 14.696 | 0.07318 | 19.838 | 0.039692 |  | 5054 | 19.838 | 82.52 | 14.696 | 0.07318 | 0.039692
5055 | 82.53 | 14.696 | 0.073179 | 19.84 | 0.039696 |  | 5055 | 19.84 | 82.53 | 14.696 | 0.073179 | 0.039696
5056 | 82.54 | 14.696 | 0.073177 | 19.843 | 0.039701 |  | 5056 | 19.843 | 82.54 | 14.696 | 0.073177 | 0.039701
5057 | 82.55 | 14.696 | 0.073176 | 19.845 | 0.039705 |  | 5057 | 19.845 | 82.55 | 14.696 | 0.073176 | 0.039705
5058 | 82.56 | 14.696 | 0.073175 | 19.848 | 0.039709 |  | 5058 | 19.848 | 82.56 | 14.696 | 0.073175 | 0.039709
5059 | 82.57 | 14.696 | 0.073173 | 19.85 | 0.039714 |  | 5059 | 19.85 | 82.57 | 14.696 | 0.073173 | 0.039714
5060 | 82.58 | 14.696 | 0.073172 | 19.852 | 0.039718 |  | 5060 | 19.852 | 82.58 | 14.696 | 0.073172 | 0.039718
5061 | 82.59 | 14.696 | 0.073171 | 19.855 | 0.039723 |  | 5061 | 19.855 | 82.59 | 14.696 | 0.073171 | 0.039723
5062 | 82.6 | 14.696 | 0.073169 | 19.857 | 0.039727 |  | 5062 | 19.857 | 82.6 | 14.696 | 0.073169 | 0.039727
5063 | 82.61 | 14.696 | 0.073168 | 19.86 | 0.039732 |  | 5063 | 19.86 | 82.61 | 14.696 | 0.073168 | 0.039732
5064 | 82.62 | 14.696 | 0.073167 | 19.862 | 0.039736 |  | 5064 | 19.862 | 82.62 | 14.696 | 0.073167 | 0.039736
5065 | 82.63 | 14.696 | 0.073165 | 19.864 | 0.03974 |  | 5065 | 19.864 | 82.63 | 14.696 | 0.073165 | 0.03974
5066 | 82.64 | 14.696 | 0.073164 | 19.867 | 0.039745 |  | 5066 | 19.867 | 82.64 | 14.696 | 0.073164 | 0.039745
5067 | 82.65 | 14.696 | 0.073163 | 19.869 | 0.039749 |  | 5067 | 19.869 | 82.65 | 14.696 | 0.073163 | 0.039749
5068 | 82.66 | 14.696 | 0.073161 | 19.872 | 0.039754 |  | 5068 | 19.872 | 82.66 | 14.696 | 0.073161 | 0.039754
5069 | 82.67 | 14.696 | 0.07316 | 19.874 | 0.039758 |  | 5069 | 19.874 | 82.67 | 14.696 | 0.07316 | 0.039758
5070 | 82.68 | 14.696 | 0.073158 | 19.876 | 0.039763 |  | 5070 | 19.876 | 82.68 | 14.696 | 0.073158 | 0.039763
5071 | 82.69 | 14.696 | 0.073157 | 19.879 | 0.039767 |  | 5071 | 19.879 | 82.69 | 14.696 | 0.073157 | 0.039767
5072 | 82.7 | 14.696 | 0.073156 | 19.881 | 0.039772 |  | 5072 | 19.881 | 82.7 | 14.696 | 0.073156 | 0.039772
5073 | 82.71 | 14.696 | 0.073154 | 19.884 | 0.039776 |  | 5073 | 19.884 | 82.71 | 14.696 | 0.073154 | 0.039776
5074 | 82.72 | 14.696 | 0.073153 | 19.886 | 0.03978 |  | 5074 | 19.886 | 82.72 | 14.696 | 0.073153 | 0.03978
5075 | 82.73 | 14.696 | 0.073152 | 19.888 | 0.039785 |  | 5075 | 19.888 | 82.73 | 14.696 | 0.073152 | 0.039785
5076 | 82.74 | 14.696 | 0.07315 | 19.891 | 0.039789 |  | 5076 | 19.891 | 82.74 | 14.696 | 0.07315 | 0.039789
5077 | 82.75 | 14.696 | 0.073149 | 19.893 | 0.039794 |  | 5077 | 19.893 | 82.75 | 14.696 | 0.073149 | 0.039794
5078 | 82.76 | 14.696 | 0.073148 | 19.896 | 0.039798 |  | 5078 | 19.896 | 82.76 | 14.696 | 0.073148 | 0.039798
5079 | 82.77 | 14.696 | 0.073146 | 19.898 | 0.039803 |  | 5079 | 19.898 | 82.77 | 14.696 | 0.073146 | 0.039803
5080 | 82.78 | 14.696 | 0.073145 | 19.9 | 0.039807 |  | 5080 | 19.9 | 82.78 | 14.696 | 0.073145 | 0.039807
5081 | 82.79 | 14.696 | 0.073144 | 19.903 | 0.039811 |  | 5081 | 19.903 | 82.79 | 14.696 | 0.073144 | 0.039811
5082 | 82.8 | 14.696 | 0.073142 | 19.905 | 0.039816 |  | 5082 | 19.905 | 82.8 | 14.696 | 0.073142 | 0.039816
5083 | 82.81 | 14.696 | 0.073141 | 19.908 | 0.03982 |  | 5083 | 19.908 | 82.81 | 14.696 | 0.073141 | 0.03982
5084 | 82.82 | 14.696 | 0.07314 | 19.91 | 0.039825 |  | 5084 | 19.91 | 82.82 | 14.696 | 0.07314 | 0.039825
5085 | 82.83 | 14.696 | 0.073138 | 19.913 | 0.039829 |  | 5085 | 19.913 | 82.83 | 14.696 | 0.073138 | 0.039829
5086 | 82.84 | 14.696 | 0.073137 | 19.915 | 0.039834 |  | 5086 | 19.915 | 82.84 | 14.696 | 0.073137 | 0.039834
5087 | 82.85 | 14.696 | 0.073135 | 19.917 | 0.039838 |  | 5087 | 19.917 | 82.85 | 14.696 | 0.073135 | 0.039838
5088 | 82.86 | 14.696 | 0.073134 | 19.92 | 0.039842 |  | 5088 | 19.92 | 82.86 | 14.696 | 0.073134 | 0.039842
5089 | 82.87 | 14.696 | 0.073133 | 19.922 | 0.039847 |  | 5089 | 19.922 | 82.87 | 14.696 | 0.073133 | 0.039847
5090 | 82.88 | 14.696 | 0.073131 | 19.925 | 0.039851 |  | 5090 | 19.925 | 82.88 | 14.696 | 0.073131 | 0.039851
5091 | 82.89 | 14.696 | 0.07313 | 19.927 | 0.039856 |  | 5091 | 19.927 | 82.89 | 14.696 | 0.07313 | 0.039856
5092 | 82.9 | 14.696 | 0.073129 | 19.929 | 0.03986 |  | 5092 | 19.929 | 82.9 | 14.696 | 0.073129 | 0.03986
5093 | 82.91 | 14.696 | 0.073127 | 19.932 | 0.039865 |  | 5093 | 19.932 | 82.91 | 14.696 | 0.073127 | 0.039865
5094 | 82.92 | 14.696 | 0.073126 | 19.934 | 0.039869 |  | 5094 | 19.934 | 82.92 | 14.696 | 0.073126 | 0.039869
5095 | 82.93 | 14.696 | 0.073125 | 19.937 | 0.039874 |  | 5095 | 19.937 | 82.93 | 14.696 | 0.073125 | 0.039874
5096 | 82.94 | 14.696 | 0.073123 | 19.939 | 0.039878 |  | 5096 | 19.939 | 82.94 | 14.696 | 0.073123 | 0.039878
5097 | 82.95 | 14.696 | 0.073122 | 19.941 | 0.039882 |  | 5097 | 19.941 | 82.95 | 14.696 | 0.073122 | 0.039882
5098 | 82.96 | 14.696 | 0.073121 | 19.944 | 0.039887 |  | 5098 | 19.944 | 82.96 | 14.696 | 0.073121 | 0.039887
5099 | 82.97 | 14.696 | 0.073119 | 19.946 | 0.039891 |  | 5099 | 19.946 | 82.97 | 14.696 | 0.073119 | 0.039891
5100 | 82.98 | 14.696 | 0.073118 | 19.949 | 0.039896 |  | 5100 | 19.949 | 82.98 | 14.696 | 0.073118 | 0.039896
5101 | 82.99 | 14.696 | 0.073117 | 19.951 | 0.0399 |  | 5101 | 19.951 | 82.99 | 14.696 | 0.073117 | 0.0399
5102 | 83 | 14.696 | 0.073115 | 19.953 | 0.039905 |  | 5102 | 19.953 | 83 | 14.696 | 0.073115 | 0.039905
5103 | 83.01 | 14.696 | 0.073114 | 19.956 | 0.039909 |  | 5103 | 19.956 | 83.01 | 14.696 | 0.073114 | 0.039909
5104 | 83.02 | 14.696 | 0.073113 | 19.958 | 0.039913 |  | 5104 | 19.958 | 83.02 | 14.696 | 0.073113 | 0.039913
5105 | 83.03 | 14.696 | 0.073111 | 19.961 | 0.039918 |  | 5105 | 19.961 | 83.03 | 14.696 | 0.073111 | 0.039918
5106 | 83.04 | 14.696 | 0.07311 | 19.963 | 0.039922 |  | 5106 | 19.963 | 83.04 | 14.696 | 0.07311 | 0.039922
5107 | 83.05 | 14.696 | 0.073108 | 19.965 | 0.039927 |  | 5107 | 19.965 | 83.05 | 14.696 | 0.073108 | 0.039927
5108 | 83.06 | 14.696 | 0.073107 | 19.968 | 0.039931 |  | 5108 | 19.968 | 83.06 | 14.696 | 0.073107 | 0.039931
5109 | 83.07 | 14.696 | 0.073106 | 19.97 | 0.039936 |  | 5109 | 19.97 | 83.07 | 14.696 | 0.073106 | 0.039936
5110 | 83.08 | 14.696 | 0.073104 | 19.973 | 0.03994 |  | 5110 | 19.973 | 83.08 | 14.696 | 0.073104 | 0.03994
5111 | 83.09 | 14.696 | 0.073103 | 19.975 | 0.039944 |  | 5111 | 19.975 | 83.09 | 14.696 | 0.073103 | 0.039944
5112 | 83.1 | 14.696 | 0.073102 | 19.977 | 0.039949 |  | 5112 | 19.977 | 83.1 | 14.696 | 0.073102 | 0.039949
5113 | 83.11 | 14.696 | 0.0731 | 19.98 | 0.039953 |  | 5113 | 19.98 | 83.11 | 14.696 | 0.0731 | 0.039953
5114 | 83.12 | 14.696 | 0.073099 | 19.982 | 0.039958 |  | 5114 | 19.982 | 83.12 | 14.696 | 0.073099 | 0.039958
5115 | 83.13 | 14.696 | 0.073098 | 19.985 | 0.039962 |  | 5115 | 19.985 | 83.13 | 14.696 | 0.073098 | 0.039962
5116 | 83.14 | 14.696 | 0.073096 | 19.987 | 0.039967 |  | 5116 | 19.987 | 83.14 | 14.696 | 0.073096 | 0.039967
5117 | 83.15 | 14.696 | 0.073095 | 19.989 | 0.039971 |  | 5117 | 19.989 | 83.15 | 14.696 | 0.073095 | 0.039971
5118 | 83.16 | 14.696 | 0.073094 | 19.992 | 0.039975 |  | 5118 | 19.992 | 83.16 | 14.696 | 0.073094 | 0.039975
5119 | 83.17 | 14.696 | 0.073092 | 19.994 | 0.03998 |  | 5119 | 19.994 | 83.17 | 14.696 | 0.073092 | 0.03998
5120 | 83.18 | 14.696 | 0.073091 | 19.997 | 0.039984 |  | 5120 | 19.997 | 83.18 | 14.696 | 0.073091 | 0.039984
5121 | 83.19 | 14.696 | 0.07309 | 19.999 | 0.039989 |  | 5121 | 19.999 | 83.19 | 14.696 | 0.07309 | 0.039989
5122 | 83.2 | 14.696 | 0.073088 | 20.002 | 0.039993 |  | 5122 | 20.002 | 83.2 | 14.696 | 0.073088 | 0.039993
5123 | 83.21 | 14.696 | 0.073087 | 20.004 | 0.039998 |  | 5123 | 20.004 | 83.21 | 14.696 | 0.073087 | 0.039998
5124 | 83.22 | 14.696 | 0.073086 | 20.006 | 0.040002 |  | 5124 | 20.006 | 83.22 | 14.696 | 0.073086 | 0.040002
5125 | 83.23 | 14.696 | 0.073084 | 20.009 | 0.040006 |  | 5125 | 20.009 | 83.23 | 14.696 | 0.073084 | 0.040006
5126 | 83.24 | 14.696 | 0.073083 | 20.011 | 0.040011 |  | 5126 | 20.011 | 83.24 | 14.696 | 0.073083 | 0.040011
5127 | 83.25 | 14.696 | 0.073081 | 20.014 | 0.040015 |  | 5127 | 20.014 | 83.25 | 14.696 | 0.073081 | 0.040015
5128 | 83.26 | 14.696 | 0.07308 | 20.016 | 0.04002 |  | 5128 | 20.016 | 83.26 | 14.696 | 0.07308 | 0.04002
5129 | 83.27 | 14.696 | 0.073079 | 20.018 | 0.040024 |  | 5129 | 20.018 | 83.27 | 14.696 | 0.073079 | 0.040024
5130 | 83.28 | 14.696 | 0.073077 | 20.021 | 0.040029 |  | 5130 | 20.021 | 83.28 | 14.696 | 0.073077 | 0.040029
5131 | 83.29 | 14.696 | 0.073076 | 20.023 | 0.040033 |  | 5131 | 20.023 | 83.29 | 14.696 | 0.073076 | 0.040033
5132 | 83.3 | 14.696 | 0.073075 | 20.026 | 0.040038 |  | 5132 | 20.026 | 83.3 | 14.696 | 0.073075 | 0.040038
5133 | 83.31 | 14.696 | 0.073073 | 20.028 | 0.040042 |  | 5133 | 20.028 | 83.31 | 14.696 | 0.073073 | 0.040042
5134 | 83.32 | 14.696 | 0.073072 | 20.03 | 0.040046 |  | 5134 | 20.03 | 83.32 | 14.696 | 0.073072 | 0.040046
5135 | 83.33 | 14.696 | 0.073071 | 20.033 | 0.040051 |  | 5135 | 20.033 | 83.33 | 14.696 | 0.073071 | 0.040051
5136 | 83.34 | 14.696 | 0.073069 | 20.035 | 0.040055 |  | 5136 | 20.035 | 83.34 | 14.696 | 0.073069 | 0.040055
5137 | 83.35 | 14.696 | 0.073068 | 20.038 | 0.04006 |  | 5137 | 20.038 | 83.35 | 14.696 | 0.073068 | 0.04006
5138 | 83.36 | 14.696 | 0.073067 | 20.04 | 0.040064 |  | 5138 | 20.04 | 83.36 | 14.696 | 0.073067 | 0.040064
5139 | 83.37 | 14.696 | 0.073065 | 20.042 | 0.040069 |  | 5139 | 20.042 | 83.37 | 14.696 | 0.073065 | 0.040069
5140 | 83.38 | 14.696 | 0.073064 | 20.045 | 0.040073 |  | 5140 | 20.045 | 83.38 | 14.696 | 0.073064 | 0.040073
5141 | 83.39 | 14.696 | 0.073063 | 20.047 | 0.040077 |  | 5141 | 20.047 | 83.39 | 14.696 | 0.073063 | 0.040077
5142 | 83.4 | 14.696 | 0.073061 | 20.05 | 0.040082 |  | 5142 | 20.05 | 83.4 | 14.696 | 0.073061 | 0.040082
5143 | 83.41 | 14.696 | 0.07306 | 20.052 | 0.040086 |  | 5143 | 20.052 | 83.41 | 14.696 | 0.07306 | 0.040086
5144 | 83.42 | 14.696 | 0.073059 | 20.054 | 0.040091 |  | 5144 | 20.054 | 83.42 | 14.696 | 0.073059 | 0.040091
5145 | 83.43 | 14.696 | 0.073057 | 20.057 | 0.040095 |  | 5145 | 20.057 | 83.43 | 14.696 | 0.073057 | 0.040095
5146 | 83.44 | 14.696 | 0.073056 | 20.059 | 0.0401 |  | 5146 | 20.059 | 83.44 | 14.696 | 0.073056 | 0.0401
5147 | 83.45 | 14.696 | 0.073054 | 20.062 | 0.040104 |  | 5147 | 20.062 | 83.45 | 14.696 | 0.073054 | 0.040104
5148 | 83.46 | 14.696 | 0.073053 | 20.064 | 0.040108 |  | 5148 | 20.064 | 83.46 | 14.696 | 0.073053 | 0.040108
5149 | 83.47 | 14.696 | 0.073052 | 20.066 | 0.040113 |  | 5149 | 20.066 | 83.47 | 14.696 | 0.073052 | 0.040113
5150 | 83.48 | 14.696 | 0.07305 | 20.069 | 0.040117 |  | 5150 | 20.069 | 83.48 | 14.696 | 0.07305 | 0.040117
5151 | 83.49 | 14.696 | 0.073049 | 20.071 | 0.040122 |  | 5151 | 20.071 | 83.49 | 14.696 | 0.073049 | 0.040122
5152 | 83.5 | 14.696 | 0.073048 | 20.074 | 0.040126 |  | 5152 | 20.074 | 83.5 | 14.696 | 0.073048 | 0.040126
5153 | 83.51 | 14.696 | 0.073046 | 20.076 | 0.040131 |  | 5153 | 20.076 | 83.51 | 14.696 | 0.073046 | 0.040131
5154 | 83.52 | 14.696 | 0.073045 | 20.078 | 0.040135 |  | 5154 | 20.078 | 83.52 | 14.696 | 0.073045 | 0.040135
5155 | 83.53 | 14.696 | 0.073044 | 20.081 | 0.040139 |  | 5155 | 20.081 | 83.53 | 14.696 | 0.073044 | 0.040139
5156 | 83.54 | 14.696 | 0.073042 | 20.083 | 0.040144 |  | 5156 | 20.083 | 83.54 | 14.696 | 0.073042 | 0.040144
5157 | 83.55 | 14.696 | 0.073041 | 20.086 | 0.040148 |  | 5157 | 20.086 | 83.55 | 14.696 | 0.073041 | 0.040148
5158 | 83.56 | 14.696 | 0.07304 | 20.088 | 0.040153 |  | 5158 | 20.088 | 83.56 | 14.696 | 0.07304 | 0.040153
5159 | 83.57 | 14.696 | 0.073038 | 20.091 | 0.040157 |  | 5159 | 20.091 | 83.57 | 14.696 | 0.073038 | 0.040157
5160 | 83.58 | 14.696 | 0.073037 | 20.093 | 0.040162 |  | 5160 | 20.093 | 83.58 | 14.696 | 0.073037 | 0.040162
5161 | 83.59 | 14.696 | 0.073036 | 20.095 | 0.040166 |  | 5161 | 20.095 | 83.59 | 14.696 | 0.073036 | 0.040166
5162 | 83.6 | 14.696 | 0.073034 | 20.098 | 0.04017 |  | 5162 | 20.098 | 83.6 | 14.696 | 0.073034 | 0.04017
5163 | 83.61 | 14.696 | 0.073033 | 20.1 | 0.040175 |  | 5163 | 20.1 | 83.61 | 14.696 | 0.073033 | 0.040175
5164 | 83.62 | 14.696 | 0.073032 | 20.103 | 0.040179 |  | 5164 | 20.103 | 83.62 | 14.696 | 0.073032 | 0.040179
5165 | 83.63 | 14.696 | 0.07303 | 20.105 | 0.040184 |  | 5165 | 20.105 | 83.63 | 14.696 | 0.07303 | 0.040184
5166 | 83.64 | 14.696 | 0.073029 | 20.107 | 0.040188 |  | 5166 | 20.107 | 83.64 | 14.696 | 0.073029 | 0.040188
5167 | 83.65 | 14.696 | 0.073028 | 20.11 | 0.040193 |  | 5167 | 20.11 | 83.65 | 14.696 | 0.073028 | 0.040193
5168 | 83.66 | 14.696 | 0.073026 | 20.112 | 0.040197 |  | 5168 | 20.112 | 83.66 | 14.696 | 0.073026 | 0.040197
5169 | 83.67 | 14.696 | 0.073025 | 20.115 | 0.040201 |  | 5169 | 20.115 | 83.67 | 14.696 | 0.073025 | 0.040201
5170 | 83.68 | 14.696 | 0.073023 | 20.117 | 0.040206 |  | 5170 | 20.117 | 83.68 | 14.696 | 0.073023 | 0.040206
5171 | 83.69 | 14.696 | 0.073022 | 20.119 | 0.04021 |  | 5171 | 20.119 | 83.69 | 14.696 | 0.073022 | 0.04021
5172 | 83.7 | 14.696 | 0.073021 | 20.122 | 0.040215 |  | 5172 | 20.122 | 83.7 | 14.696 | 0.073021 | 0.040215
5173 | 83.71 | 14.696 | 0.073019 | 20.124 | 0.040219 |  | 5173 | 20.124 | 83.71 | 14.696 | 0.073019 | 0.040219
5174 | 83.72 | 14.696 | 0.073018 | 20.127 | 0.040223 |  | 5174 | 20.127 | 83.72 | 14.696 | 0.073018 | 0.040223
5175 | 83.73 | 14.696 | 0.073017 | 20.129 | 0.040228 |  | 5175 | 20.129 | 83.73 | 14.696 | 0.073017 | 0.040228
5176 | 83.74 | 14.696 | 0.073015 | 20.131 | 0.040232 |  | 5176 | 20.131 | 83.74 | 14.696 | 0.073015 | 0.040232
5177 | 83.75 | 14.696 | 0.073014 | 20.134 | 0.040237 |  | 5177 | 20.134 | 83.75 | 14.696 | 0.073014 | 0.040237
5178 | 83.76 | 14.696 | 0.073013 | 20.136 | 0.040241 |  | 5178 | 20.136 | 83.76 | 14.696 | 0.073013 | 0.040241
5179 | 83.77 | 14.696 | 0.073011 | 20.139 | 0.040246 |  | 5179 | 20.139 | 83.77 | 14.696 | 0.073011 | 0.040246
5180 | 83.78 | 14.696 | 0.07301 | 20.141 | 0.04025 |  | 5180 | 20.141 | 83.78 | 14.696 | 0.07301 | 0.04025
5181 | 83.79 | 14.696 | 0.073009 | 20.143 | 0.040254 |  | 5181 | 20.143 | 83.79 | 14.696 | 0.073009 | 0.040254
5182 | 83.8 | 14.696 | 0.073007 | 20.146 | 0.040259 |  | 5182 | 20.146 | 83.8 | 14.696 | 0.073007 | 0.040259
5183 | 83.81 | 14.696 | 0.073006 | 20.148 | 0.040263 |  | 5183 | 20.148 | 83.81 | 14.696 | 0.073006 | 0.040263
5184 | 83.82 | 14.696 | 0.073005 | 20.151 | 0.040268 |  | 5184 | 20.151 | 83.82 | 14.696 | 0.073005 | 0.040268
5185 | 83.83 | 14.696 | 0.073003 | 20.153 | 0.040272 |  | 5185 | 20.153 | 83.83 | 14.696 | 0.073003 | 0.040272
5186 | 83.84 | 14.696 | 0.073002 | 20.155 | 0.040277 |  | 5186 | 20.155 | 83.84 | 14.696 | 0.073002 | 0.040277
5187 | 83.85 | 14.696 | 0.073001 | 20.158 | 0.040281 |  | 5187 | 20.158 | 83.85 | 14.696 | 0.073001 | 0.040281
5188 | 83.86 | 14.696 | 0.072999 | 20.16 | 0.040285 |  | 5188 | 20.16 | 83.86 | 14.696 | 0.072999 | 0.040285
5189 | 83.87 | 14.696 | 0.072998 | 20.163 | 0.04029 |  | 5189 | 20.163 | 83.87 | 14.696 | 0.072998 | 0.04029
5190 | 83.88 | 14.696 | 0.072997 | 20.165 | 0.040294 |  | 5190 | 20.165 | 83.88 | 14.696 | 0.072997 | 0.040294
5191 | 83.89 | 14.696 | 0.072995 | 20.168 | 0.040299 |  | 5191 | 20.168 | 83.89 | 14.696 | 0.072995 | 0.040299
5192 | 83.9 | 14.696 | 0.072994 | 20.17 | 0.040303 |  | 5192 | 20.17 | 83.9 | 14.696 | 0.072994 | 0.040303
5193 | 83.91 | 14.696 | 0.072992 | 20.172 | 0.040308 |  | 5193 | 20.172 | 83.91 | 14.696 | 0.072992 | 0.040308
5194 | 83.92 | 14.696 | 0.072991 | 20.175 | 0.040312 |  | 5194 | 20.175 | 83.92 | 14.696 | 0.072991 | 0.040312
5195 | 83.93 | 14.696 | 0.07299 | 20.177 | 0.040316 |  | 5195 | 20.177 | 83.93 | 14.696 | 0.07299 | 0.040316
5196 | 83.94 | 14.696 | 0.072988 | 20.18 | 0.040321 |  | 5196 | 20.18 | 83.94 | 14.696 | 0.072988 | 0.040321
5197 | 83.95 | 14.696 | 0.072987 | 20.182 | 0.040325 |  | 5197 | 20.182 | 83.95 | 14.696 | 0.072987 | 0.040325
5198 | 83.96 | 14.696 | 0.072986 | 20.184 | 0.04033 |  | 5198 | 20.184 | 83.96 | 14.696 | 0.072986 | 0.04033
5199 | 83.97 | 14.696 | 0.072984 | 20.187 | 0.040334 |  | 5199 | 20.187 | 83.97 | 14.696 | 0.072984 | 0.040334
5200 | 83.98 | 14.696 | 0.072983 | 20.189 | 0.040339 |  | 5200 | 20.189 | 83.98 | 14.696 | 0.072983 | 0.040339
5201 | 83.99 | 14.696 | 0.072982 | 20.192 | 0.040343 |  | 5201 | 20.192 | 83.99 | 14.696 | 0.072982 | 0.040343
5202 | 84 | 14.696 | 0.07298 | 20.194 | 0.040347 |  | 5202 | 20.194 | 84 | 14.696 | 0.07298 | 0.040347
5203 | 84.01 | 14.696 | 0.072979 | 20.196 | 0.040352 |  | 5203 | 20.196 | 84.01 | 14.696 | 0.072979 | 0.040352
5204 | 84.02 | 14.696 | 0.072978 | 20.199 | 0.040356 |  | 5204 | 20.199 | 84.02 | 14.696 | 0.072978 | 0.040356
5205 | 84.03 | 14.696 | 0.072976 | 20.201 | 0.040361 |  | 5205 | 20.201 | 84.03 | 14.696 | 0.072976 | 0.040361
5206 | 84.04 | 14.696 | 0.072975 | 20.204 | 0.040365 |  | 5206 | 20.204 | 84.04 | 14.696 | 0.072975 | 0.040365
5207 | 84.05 | 14.696 | 0.072974 | 20.206 | 0.04037 |  | 5207 | 20.206 | 84.05 | 14.696 | 0.072974 | 0.04037
5208 | 84.06 | 14.696 | 0.072972 | 20.208 | 0.040374 |  | 5208 | 20.208 | 84.06 | 14.696 | 0.072972 | 0.040374
5209 | 84.07 | 14.696 | 0.072971 | 20.211 | 0.040378 |  | 5209 | 20.211 | 84.07 | 14.696 | 0.072971 | 0.040378
5210 | 84.08 | 14.696 | 0.07297 | 20.213 | 0.040383 |  | 5210 | 20.213 | 84.08 | 14.696 | 0.07297 | 0.040383
5211 | 84.09 | 14.696 | 0.072968 | 20.216 | 0.040387 |  | 5211 | 20.216 | 84.09 | 14.696 | 0.072968 | 0.040387
5212 | 84.1 | 14.696 | 0.072967 | 20.218 | 0.040392 |  | 5212 | 20.218 | 84.1 | 14.696 | 0.072967 | 0.040392
5213 | 84.11 | 14.696 | 0.072966 | 20.22 | 0.040396 |  | 5213 | 20.22 | 84.11 | 14.696 | 0.072966 | 0.040396
5214 | 84.12 | 14.696 | 0.072964 | 20.223 | 0.040401 |  | 5214 | 20.223 | 84.12 | 14.696 | 0.072964 | 0.040401
5215 | 84.13 | 14.696 | 0.072963 | 20.225 | 0.040405 |  | 5215 | 20.225 | 84.13 | 14.696 | 0.072963 | 0.040405
5216 | 84.14 | 14.696 | 0.072962 | 20.228 | 0.040409 |  | 5216 | 20.228 | 84.14 | 14.696 | 0.072962 | 0.040409
5217 | 84.15 | 14.696 | 0.07296 | 20.23 | 0.040414 |  | 5217 | 20.23 | 84.15 | 14.696 | 0.07296 | 0.040414
5218 | 84.16 | 14.696 | 0.072959 | 20.232 | 0.040418 |  | 5218 | 20.232 | 84.16 | 14.696 | 0.072959 | 0.040418
5219 | 84.17 | 14.696 | 0.072958 | 20.235 | 0.040423 |  | 5219 | 20.235 | 84.17 | 14.696 | 0.072958 | 0.040423
5220 | 84.18 | 14.696 | 0.072956 | 20.237 | 0.040427 |  | 5220 | 20.237 | 84.18 | 14.696 | 0.072956 | 0.040427
5221 | 84.19 | 14.696 | 0.072955 | 20.24 | 0.040431 |  | 5221 | 20.24 | 84.19 | 14.696 | 0.072955 | 0.040431
5222 | 84.2 | 14.696 | 0.072953 | 20.242 | 0.040436 |  | 5222 | 20.242 | 84.2 | 14.696 | 0.072953 | 0.040436
5223 | 84.21 | 14.696 | 0.072952 | 20.244 | 0.04044 |  | 5223 | 20.244 | 84.21 | 14.696 | 0.072952 | 0.04044
5224 | 84.22 | 14.696 | 0.072951 | 20.247 | 0.040445 |  | 5224 | 20.247 | 84.22 | 14.696 | 0.072951 | 0.040445
5225 | 84.23 | 14.696 | 0.072949 | 20.249 | 0.040449 |  | 5225 | 20.249 | 84.23 | 14.696 | 0.072949 | 0.040449
5226 | 84.24 | 14.696 | 0.072948 | 20.252 | 0.040454 |  | 5226 | 20.252 | 84.24 | 14.696 | 0.072948 | 0.040454
5227 | 84.25 | 14.696 | 0.072947 | 20.254 | 0.040458 |  | 5227 | 20.254 | 84.25 | 14.696 | 0.072947 | 0.040458
5228 | 84.26 | 14.696 | 0.072945 | 20.257 | 0.040462 |  | 5228 | 20.257 | 84.26 | 14.696 | 0.072945 | 0.040462
5229 | 84.27 | 14.696 | 0.072944 | 20.259 | 0.040467 |  | 5229 | 20.259 | 84.27 | 14.696 | 0.072944 | 0.040467
5230 | 84.28 | 14.696 | 0.072943 | 20.261 | 0.040471 |  | 5230 | 20.261 | 84.28 | 14.696 | 0.072943 | 0.040471
5231 | 84.29 | 14.696 | 0.072941 | 20.264 | 0.040476 |  | 5231 | 20.264 | 84.29 | 14.696 | 0.072941 | 0.040476
5232 | 84.3 | 14.696 | 0.07294 | 20.266 | 0.04048 |  | 5232 | 20.266 | 84.3 | 14.696 | 0.07294 | 0.04048
5233 | 84.31 | 14.696 | 0.072939 | 20.269 | 0.040485 |  | 5233 | 20.269 | 84.31 | 14.696 | 0.072939 | 0.040485
5234 | 84.32 | 14.696 | 0.072937 | 20.271 | 0.040489 |  | 5234 | 20.271 | 84.32 | 14.696 | 0.072937 | 0.040489
5235 | 84.33 | 14.696 | 0.072936 | 20.273 | 0.040493 |  | 5235 | 20.273 | 84.33 | 14.696 | 0.072936 | 0.040493
5236 | 84.34 | 14.696 | 0.072935 | 20.276 | 0.040498 |  | 5236 | 20.276 | 84.34 | 14.696 | 0.072935 | 0.040498
5237 | 84.35 | 14.696 | 0.072933 | 20.278 | 0.040502 |  | 5237 | 20.278 | 84.35 | 14.696 | 0.072933 | 0.040502
5238 | 84.36 | 14.696 | 0.072932 | 20.281 | 0.040507 |  | 5238 | 20.281 | 84.36 | 14.696 | 0.072932 | 0.040507
5239 | 84.37 | 14.696 | 0.072931 | 20.283 | 0.040511 |  | 5239 | 20.283 | 84.37 | 14.696 | 0.072931 | 0.040511
5240 | 84.38 | 14.696 | 0.072929 | 20.285 | 0.040515 |  | 5240 | 20.285 | 84.38 | 14.696 | 0.072929 | 0.040515
5241 | 84.39 | 14.696 | 0.072928 | 20.288 | 0.04052 |  | 5241 | 20.288 | 84.39 | 14.696 | 0.072928 | 0.04052
5242 | 84.4 | 14.696 | 0.072927 | 20.29 | 0.040524 |  | 5242 | 20.29 | 84.4 | 14.696 | 0.072927 | 0.040524
5243 | 84.41 | 14.696 | 0.072925 | 20.293 | 0.040529 |  | 5243 | 20.293 | 84.41 | 14.696 | 0.072925 | 0.040529
5244 | 84.42 | 14.696 | 0.072924 | 20.295 | 0.040533 |  | 5244 | 20.295 | 84.42 | 14.696 | 0.072924 | 0.040533
5245 | 84.43 | 14.696 | 0.072923 | 20.297 | 0.040538 |  | 5245 | 20.297 | 84.43 | 14.696 | 0.072923 | 0.040538
5246 | 84.44 | 14.696 | 0.072921 | 20.3 | 0.040542 |  | 5246 | 20.3 | 84.44 | 14.696 | 0.072921 | 0.040542
5247 | 84.45 | 14.696 | 0.07292 | 20.302 | 0.040546 |  | 5247 | 20.302 | 84.45 | 14.696 | 0.07292 | 0.040546
5248 | 84.46 | 14.696 | 0.072919 | 20.305 | 0.040551 |  | 5248 | 20.305 | 84.46 | 14.696 | 0.072919 | 0.040551
5249 | 84.47 | 14.696 | 0.072917 | 20.307 | 0.040555 |  | 5249 | 20.307 | 84.47 | 14.696 | 0.072917 | 0.040555
5250 | 84.48 | 14.696 | 0.072916 | 20.309 | 0.04056 |  | 5250 | 20.309 | 84.48 | 14.696 | 0.072916 | 0.04056
5251 | 84.49 | 14.696 | 0.072914 | 20.312 | 0.040564 |  | 5251 | 20.312 | 84.49 | 14.696 | 0.072914 | 0.040564
5252 | 84.5 | 14.696 | 0.072913 | 20.314 | 0.040569 |  | 5252 | 20.314 | 84.5 | 14.696 | 0.072913 | 0.040569
5253 | 84.51 | 14.696 | 0.072912 | 20.317 | 0.040573 |  | 5253 | 20.317 | 84.51 | 14.696 | 0.072912 | 0.040573
5254 | 84.52 | 14.696 | 0.07291 | 20.319 | 0.040577 |  | 5254 | 20.319 | 84.52 | 14.696 | 0.07291 | 0.040577
5255 | 84.53 | 14.696 | 0.072909 | 20.321 | 0.040582 |  | 5255 | 20.321 | 84.53 | 14.696 | 0.072909 | 0.040582
5256 | 84.54 | 14.696 | 0.072908 | 20.324 | 0.040586 |  | 5256 | 20.324 | 84.54 | 14.696 | 0.072908 | 0.040586
5257 | 84.55 | 14.696 | 0.072906 | 20.326 | 0.040591 |  | 5257 | 20.326 | 84.55 | 14.696 | 0.072906 | 0.040591
5258 | 84.56 | 14.696 | 0.072905 | 20.329 | 0.040595 |  | 5258 | 20.329 | 84.56 | 14.696 | 0.072905 | 0.040595
5259 | 84.57 | 14.696 | 0.072904 | 20.331 | 0.040599 |  | 5259 | 20.331 | 84.57 | 14.696 | 0.072904 | 0.040599
5260 | 84.58 | 14.696 | 0.072902 | 20.333 | 0.040604 |  | 5260 | 20.333 | 84.58 | 14.696 | 0.072902 | 0.040604
5261 | 84.59 | 14.696 | 0.072901 | 20.336 | 0.040608 |  | 5261 | 20.336 | 84.59 | 14.696 | 0.072901 | 0.040608
5262 | 84.6 | 14.696 | 0.0729 | 20.338 | 0.040613 |  | 5262 | 20.338 | 84.6 | 14.696 | 0.0729 | 0.040613
5263 | 84.61 | 14.696 | 0.072898 | 20.341 | 0.040617 |  | 5263 | 20.341 | 84.61 | 14.696 | 0.072898 | 0.040617
5264 | 84.62 | 14.696 | 0.072897 | 20.343 | 0.040622 |  | 5264 | 20.343 | 84.62 | 14.696 | 0.072897 | 0.040622
5265 | 84.63 | 14.696 | 0.072896 | 20.346 | 0.040626 |  | 5265 | 20.346 | 84.63 | 14.696 | 0.072896 | 0.040626
5266 | 84.64 | 14.696 | 0.072894 | 20.348 | 0.04063 |  | 5266 | 20.348 | 84.64 | 14.696 | 0.072894 | 0.04063
5267 | 84.65 | 14.696 | 0.072893 | 20.35 | 0.040635 |  | 5267 | 20.35 | 84.65 | 14.696 | 0.072893 | 0.040635
5268 | 84.66 | 14.696 | 0.072892 | 20.353 | 0.040639 |  | 5268 | 20.353 | 84.66 | 14.696 | 0.072892 | 0.040639
5269 | 84.67 | 14.696 | 0.07289 | 20.355 | 0.040644 |  | 5269 | 20.355 | 84.67 | 14.696 | 0.07289 | 0.040644
5270 | 84.68 | 14.696 | 0.072889 | 20.358 | 0.040648 |  | 5270 | 20.358 | 84.68 | 14.696 | 0.072889 | 0.040648
5271 | 84.69 | 14.696 | 0.072888 | 20.36 | 0.040653 |  | 5271 | 20.36 | 84.69 | 14.696 | 0.072888 | 0.040653
5272 | 84.7 | 14.696 | 0.072886 | 20.362 | 0.040657 |  | 5272 | 20.362 | 84.7 | 14.696 | 0.072886 | 0.040657
5273 | 84.71 | 14.696 | 0.072885 | 20.365 | 0.040661 |  | 5273 | 20.365 | 84.71 | 14.696 | 0.072885 | 0.040661
5274 | 84.72 | 14.696 | 0.072884 | 20.367 | 0.040666 |  | 5274 | 20.367 | 84.72 | 14.696 | 0.072884 | 0.040666
5275 | 84.73 | 14.696 | 0.072882 | 20.37 | 0.04067 |  | 5275 | 20.37 | 84.73 | 14.696 | 0.072882 | 0.04067
5276 | 84.74 | 14.696 | 0.072881 | 20.372 | 0.040675 |  | 5276 | 20.372 | 84.74 | 14.696 | 0.072881 | 0.040675
5277 | 84.75 | 14.696 | 0.07288 | 20.374 | 0.040679 |  | 5277 | 20.374 | 84.75 | 14.696 | 0.07288 | 0.040679
5278 | 84.76 | 14.696 | 0.072878 | 20.377 | 0.040683 |  | 5278 | 20.377 | 84.76 | 14.696 | 0.072878 | 0.040683
5279 | 84.77 | 14.696 | 0.072877 | 20.379 | 0.040688 |  | 5279 | 20.379 | 84.77 | 14.696 | 0.072877 | 0.040688
5280 | 84.78 | 14.696 | 0.072876 | 20.382 | 0.040692 |  | 5280 | 20.382 | 84.78 | 14.696 | 0.072876 | 0.040692
5281 | 84.79 | 14.696 | 0.072874 | 20.384 | 0.040697 |  | 5281 | 20.384 | 84.79 | 14.696 | 0.072874 | 0.040697
5282 | 84.8 | 14.696 | 0.072873 | 20.386 | 0.040701 |  | 5282 | 20.386 | 84.8 | 14.696 | 0.072873 | 0.040701
5283 | 84.81 | 14.696 | 0.072872 | 20.389 | 0.040706 |  | 5283 | 20.389 | 84.81 | 14.696 | 0.072872 | 0.040706
5284 | 84.82 | 14.696 | 0.07287 | 20.391 | 0.04071 |  | 5284 | 20.391 | 84.82 | 14.696 | 0.07287 | 0.04071
5285 | 84.83 | 14.696 | 0.072869 | 20.394 | 0.040714 |  | 5285 | 20.394 | 84.83 | 14.696 | 0.072869 | 0.040714
5286 | 84.84 | 14.696 | 0.072868 | 20.396 | 0.040719 |  | 5286 | 20.396 | 84.84 | 14.696 | 0.072868 | 0.040719
5287 | 84.85 | 14.696 | 0.072866 | 20.398 | 0.040723 |  | 5287 | 20.398 | 84.85 | 14.696 | 0.072866 | 0.040723
5288 | 84.86 | 14.696 | 0.072865 | 20.401 | 0.040728 |  | 5288 | 20.401 | 84.86 | 14.696 | 0.072865 | 0.040728
5289 | 84.87 | 14.696 | 0.072863 | 20.403 | 0.040732 |  | 5289 | 20.403 | 84.87 | 14.696 | 0.072863 | 0.040732
5290 | 84.88 | 14.696 | 0.072862 | 20.406 | 0.040736 |  | 5290 | 20.406 | 84.88 | 14.696 | 0.072862 | 0.040736
5291 | 84.89 | 14.696 | 0.072861 | 20.408 | 0.040741 |  | 5291 | 20.408 | 84.89 | 14.696 | 0.072861 | 0.040741
5292 | 84.9 | 14.696 | 0.072859 | 20.41 | 0.040745 |  | 5292 | 20.41 | 84.9 | 14.696 | 0.072859 | 0.040745
5293 | 84.91 | 14.696 | 0.072858 | 20.413 | 0.04075 |  | 5293 | 20.413 | 84.91 | 14.696 | 0.072858 | 0.04075
5294 | 84.92 | 14.696 | 0.072857 | 20.415 | 0.040754 |  | 5294 | 20.415 | 84.92 | 14.696 | 0.072857 | 0.040754
5295 | 84.93 | 14.696 | 0.072855 | 20.418 | 0.040759 |  | 5295 | 20.418 | 84.93 | 14.696 | 0.072855 | 0.040759
5296 | 84.94 | 14.696 | 0.072854 | 20.42 | 0.040763 |  | 5296 | 20.42 | 84.94 | 14.696 | 0.072854 | 0.040763
5297 | 84.95 | 14.696 | 0.072853 | 20.422 | 0.040767 |  | 5297 | 20.422 | 84.95 | 14.696 | 0.072853 | 0.040767
5298 | 84.96 | 14.696 | 0.072851 | 20.425 | 0.040772 |  | 5298 | 20.425 | 84.96 | 14.696 | 0.072851 | 0.040772
5299 | 84.97 | 14.696 | 0.07285 | 20.427 | 0.040776 |  | 5299 | 20.427 | 84.97 | 14.696 | 0.07285 | 0.040776
5300 | 84.98 | 14.696 | 0.072849 | 20.43 | 0.040781 |  | 5300 | 20.43 | 84.98 | 14.696 | 0.072849 | 0.040781
5301 | 84.99 | 14.696 | 0.072847 | 20.432 | 0.040785 |  | 5301 | 20.432 | 84.99 | 14.696 | 0.072847 | 0.040785
5302 | 85 | 14.696 | 0.072846 | 20.435 | 0.040789 |  | 5302 | 20.435 | 85 | 14.696 | 0.072846 | 0.040789
5303 | 85.01 | 14.696 | 0.072845 | 20.437 | 0.040794 |  | 5303 | 20.437 | 85.01 | 14.696 | 0.072845 | 0.040794
5304 | 85.02 | 14.696 | 0.072843 | 20.439 | 0.040798 |  | 5304 | 20.439 | 85.02 | 14.696 | 0.072843 | 0.040798
5305 | 85.03 | 14.696 | 0.072842 | 20.442 | 0.040803 |  | 5305 | 20.442 | 85.03 | 14.696 | 0.072842 | 0.040803
5306 | 85.04 | 14.696 | 0.072841 | 20.444 | 0.040807 |  | 5306 | 20.444 | 85.04 | 14.696 | 0.072841 | 0.040807
5307 | 85.05 | 14.696 | 0.072839 | 20.447 | 0.040812 |  | 5307 | 20.447 | 85.05 | 14.696 | 0.072839 | 0.040812
5308 | 85.06 | 14.696 | 0.072838 | 20.449 | 0.040816 |  | 5308 | 20.449 | 85.06 | 14.696 | 0.072838 | 0.040816
5309 | 85.07 | 14.696 | 0.072837 | 20.451 | 0.04082 |  | 5309 | 20.451 | 85.07 | 14.696 | 0.072837 | 0.04082
5310 | 85.08 | 14.696 | 0.072835 | 20.454 | 0.040825 |  | 5310 | 20.454 | 85.08 | 14.696 | 0.072835 | 0.040825
5311 | 85.09 | 14.696 | 0.072834 | 20.456 | 0.040829 |  | 5311 | 20.456 | 85.09 | 14.696 | 0.072834 | 0.040829
5312 | 85.1 | 14.696 | 0.072833 | 20.459 | 0.040834 |  | 5312 | 20.459 | 85.1 | 14.696 | 0.072833 | 0.040834
5313 | 85.11 | 14.696 | 0.072831 | 20.461 | 0.040838 |  | 5313 | 20.461 | 85.11 | 14.696 | 0.072831 | 0.040838
5314 | 85.12 | 14.696 | 0.07283 | 20.463 | 0.040842 |  | 5314 | 20.463 | 85.12 | 14.696 | 0.07283 | 0.040842
5315 | 85.13 | 14.696 | 0.072829 | 20.466 | 0.040847 |  | 5315 | 20.466 | 85.13 | 14.696 | 0.072829 | 0.040847
5316 | 85.14 | 14.696 | 0.072827 | 20.468 | 0.040851 |  | 5316 | 20.468 | 85.14 | 14.696 | 0.072827 | 0.040851
5317 | 85.15 | 14.696 | 0.072826 | 20.471 | 0.040856 |  | 5317 | 20.471 | 85.15 | 14.696 | 0.072826 | 0.040856
5318 | 85.16 | 14.696 | 0.072825 | 20.473 | 0.04086 |  | 5318 | 20.473 | 85.16 | 14.696 | 0.072825 | 0.04086
5319 | 85.17 | 14.696 | 0.072823 | 20.475 | 0.040865 |  | 5319 | 20.475 | 85.17 | 14.696 | 0.072823 | 0.040865
5320 | 85.18 | 14.696 | 0.072822 | 20.478 | 0.040869 |  | 5320 | 20.478 | 85.18 | 14.696 | 0.072822 | 0.040869
5321 | 85.19 | 14.696 | 0.072821 | 20.48 | 0.040873 |  | 5321 | 20.48 | 85.19 | 14.696 | 0.072821 | 0.040873
5322 | 85.2 | 14.696 | 0.072819 | 20.483 | 0.040878 |  | 5322 | 20.483 | 85.2 | 14.696 | 0.072819 | 0.040878
5323 | 85.21 | 14.696 | 0.072818 | 20.485 | 0.040882 |  | 5323 | 20.485 | 85.21 | 14.696 | 0.072818 | 0.040882
5324 | 85.22 | 14.696 | 0.072817 | 20.487 | 0.040887 |  | 5324 | 20.487 | 85.22 | 14.696 | 0.072817 | 0.040887
5325 | 85.23 | 14.696 | 0.072815 | 20.49 | 0.040891 |  | 5325 | 20.49 | 85.23 | 14.696 | 0.072815 | 0.040891
5326 | 85.24 | 14.696 | 0.072814 | 20.492 | 0.040895 |  | 5326 | 20.492 | 85.24 | 14.696 | 0.072814 | 0.040895
5327 | 85.25 | 14.696 | 0.072813 | 20.495 | 0.0409 |  | 5327 | 20.495 | 85.25 | 14.696 | 0.072813 | 0.0409
5328 | 85.26 | 14.696 | 0.072811 | 20.497 | 0.040904 |  | 5328 | 20.497 | 85.26 | 14.696 | 0.072811 | 0.040904
5329 | 85.27 | 14.696 | 0.07281 | 20.499 | 0.040909 |  | 5329 | 20.499 | 85.27 | 14.696 | 0.07281 | 0.040909
5330 | 85.28 | 14.696 | 0.072809 | 20.502 | 0.040913 |  | 5330 | 20.502 | 85.28 | 14.696 | 0.072809 | 0.040913
5331 | 85.29 | 14.696 | 0.072807 | 20.504 | 0.040918 |  | 5331 | 20.504 | 85.29 | 14.696 | 0.072807 | 0.040918
5332 | 85.3 | 14.696 | 0.072806 | 20.507 | 0.040922 |  | 5332 | 20.507 | 85.3 | 14.696 | 0.072806 | 0.040922
5333 | 85.31 | 14.696 | 0.072804 | 20.509 | 0.040926 |  | 5333 | 20.509 | 85.31 | 14.696 | 0.072804 | 0.040926
5334 | 85.32 | 14.696 | 0.072803 | 20.511 | 0.040931 |  | 5334 | 20.511 | 85.32 | 14.696 | 0.072803 | 0.040931
5335 | 85.33 | 14.696 | 0.072802 | 20.514 | 0.040935 |  | 5335 | 20.514 | 85.33 | 14.696 | 0.072802 | 0.040935
5336 | 85.34 | 14.696 | 0.0728 | 20.516 | 0.04094 |  | 5336 | 20.516 | 85.34 | 14.696 | 0.0728 | 0.04094
5337 | 85.35 | 14.696 | 0.072799 | 20.519 | 0.040944 |  | 5337 | 20.519 | 85.35 | 14.696 | 0.072799 | 0.040944
5338 | 85.36 | 14.696 | 0.072798 | 20.521 | 0.040948 |  | 5338 | 20.521 | 85.36 | 14.696 | 0.072798 | 0.040948
5339 | 85.37 | 14.696 | 0.072796 | 20.524 | 0.040953 |  | 5339 | 20.524 | 85.37 | 14.696 | 0.072796 | 0.040953
5340 | 85.38 | 14.696 | 0.072795 | 20.526 | 0.040957 |  | 5340 | 20.526 | 85.38 | 14.696 | 0.072795 | 0.040957
5341 | 85.39 | 14.696 | 0.072794 | 20.528 | 0.040962 |  | 5341 | 20.528 | 85.39 | 14.696 | 0.072794 | 0.040962
5342 | 85.4 | 14.696 | 0.072792 | 20.531 | 0.040966 |  | 5342 | 20.531 | 85.4 | 14.696 | 0.072792 | 0.040966
5343 | 85.41 | 14.696 | 0.072791 | 20.533 | 0.04097 |  | 5343 | 20.533 | 85.41 | 14.696 | 0.072791 | 0.04097
5344 | 85.42 | 14.696 | 0.07279 | 20.536 | 0.040975 |  | 5344 | 20.536 | 85.42 | 14.696 | 0.07279 | 0.040975
5345 | 85.43 | 14.696 | 0.072788 | 20.538 | 0.040979 |  | 5345 | 20.538 | 85.43 | 14.696 | 0.072788 | 0.040979
5346 | 85.44 | 14.696 | 0.072787 | 20.54 | 0.040984 |  | 5346 | 20.54 | 85.44 | 14.696 | 0.072787 | 0.040984
5347 | 85.45 | 14.696 | 0.072786 | 20.543 | 0.040988 |  | 5347 | 20.543 | 85.45 | 14.696 | 0.072786 | 0.040988
5348 | 85.46 | 14.696 | 0.072784 | 20.545 | 0.040993 |  | 5348 | 20.545 | 85.46 | 14.696 | 0.072784 | 0.040993
5349 | 85.47 | 14.696 | 0.072783 | 20.548 | 0.040997 |  | 5349 | 20.548 | 85.47 | 14.696 | 0.072783 | 0.040997
5350 | 85.48 | 14.696 | 0.072782 | 20.55 | 0.041001 |  | 5350 | 20.55 | 85.48 | 14.696 | 0.072782 | 0.041001
5351 | 85.49 | 14.696 | 0.07278 | 20.552 | 0.041006 |  | 5351 | 20.552 | 85.49 | 14.696 | 0.07278 | 0.041006
5352 | 85.5 | 14.696 | 0.072779 | 20.555 | 0.04101 |  | 5352 | 20.555 | 85.5 | 14.696 | 0.072779 | 0.04101
5353 | 85.51 | 14.696 | 0.072778 | 20.557 | 0.041015 |  | 5353 | 20.557 | 85.51 | 14.696 | 0.072778 | 0.041015
5354 | 85.52 | 14.696 | 0.072776 | 20.56 | 0.041019 |  | 5354 | 20.56 | 85.52 | 14.696 | 0.072776 | 0.041019
5355 | 85.53 | 14.696 | 0.072775 | 20.562 | 0.041023 |  | 5355 | 20.562 | 85.53 | 14.696 | 0.072775 | 0.041023
5356 | 85.54 | 14.696 | 0.072774 | 20.564 | 0.041028 |  | 5356 | 20.564 | 85.54 | 14.696 | 0.072774 | 0.041028
5357 | 85.55 | 14.696 | 0.072772 | 20.567 | 0.041032 |  | 5357 | 20.567 | 85.55 | 14.696 | 0.072772 | 0.041032
5358 | 85.56 | 14.696 | 0.072771 | 20.569 | 0.041037 |  | 5358 | 20.569 | 85.56 | 14.696 | 0.072771 | 0.041037
5359 | 85.57 | 14.696 | 0.07277 | 20.572 | 0.041041 |  | 5359 | 20.572 | 85.57 | 14.696 | 0.07277 | 0.041041
5360 | 85.58 | 14.696 | 0.072768 | 20.574 | 0.041045 |  | 5360 | 20.574 | 85.58 | 14.696 | 0.072768 | 0.041045
5361 | 85.59 | 14.696 | 0.072767 | 20.576 | 0.04105 |  | 5361 | 20.576 | 85.59 | 14.696 | 0.072767 | 0.04105
5362 | 85.6 | 14.696 | 0.072766 | 20.579 | 0.041054 |  | 5362 | 20.579 | 85.6 | 14.696 | 0.072766 | 0.041054
5363 | 85.61 | 14.696 | 0.072764 | 20.581 | 0.041059 |  | 5363 | 20.581 | 85.61 | 14.696 | 0.072764 | 0.041059
5364 | 85.62 | 14.696 | 0.072763 | 20.584 | 0.041063 |  | 5364 | 20.584 | 85.62 | 14.696 | 0.072763 | 0.041063
5365 | 85.63 | 14.696 | 0.072762 | 20.586 | 0.041068 |  | 5365 | 20.586 | 85.63 | 14.696 | 0.072762 | 0.041068
5366 | 85.64 | 14.696 | 0.07276 | 20.588 | 0.041072 |  | 5366 | 20.588 | 85.64 | 14.696 | 0.07276 | 0.041072
5367 | 85.65 | 14.696 | 0.072759 | 20.591 | 0.041076 |  | 5367 | 20.591 | 85.65 | 14.696 | 0.072759 | 0.041076
5368 | 85.66 | 14.696 | 0.072758 | 20.593 | 0.041081 |  | 5368 | 20.593 | 85.66 | 14.696 | 0.072758 | 0.041081
5369 | 85.67 | 14.696 | 0.072756 | 20.596 | 0.041085 |  | 5369 | 20.596 | 85.67 | 14.696 | 0.072756 | 0.041085
5370 | 85.68 | 14.696 | 0.072755 | 20.598 | 0.04109 |  | 5370 | 20.598 | 85.68 | 14.696 | 0.072755 | 0.04109
5371 | 85.69 | 14.696 | 0.072754 | 20.6 | 0.041094 |  | 5371 | 20.6 | 85.69 | 14.696 | 0.072754 | 0.041094
5372 | 85.7 | 14.696 | 0.072752 | 20.603 | 0.041098 |  | 5372 | 20.603 | 85.7 | 14.696 | 0.072752 | 0.041098
5373 | 85.71 | 14.696 | 0.072751 | 20.605 | 0.041103 |  | 5373 | 20.605 | 85.71 | 14.696 | 0.072751 | 0.041103
5374 | 85.72 | 14.696 | 0.07275 | 20.608 | 0.041107 |  | 5374 | 20.608 | 85.72 | 14.696 | 0.07275 | 0.041107
5375 | 85.73 | 14.696 | 0.072748 | 20.61 | 0.041112 |  | 5375 | 20.61 | 85.73 | 14.696 | 0.072748 | 0.041112
5376 | 85.74 | 14.696 | 0.072747 | 20.613 | 0.041116 |  | 5376 | 20.613 | 85.74 | 14.696 | 0.072747 | 0.041116
5377 | 85.75 | 14.696 | 0.072746 | 20.615 | 0.04112 |  | 5377 | 20.615 | 85.75 | 14.696 | 0.072746 | 0.04112
5378 | 85.76 | 14.696 | 0.072744 | 20.617 | 0.041125 |  | 5378 | 20.617 | 85.76 | 14.696 | 0.072744 | 0.041125
5379 | 85.77 | 14.696 | 0.072743 | 20.62 | 0.041129 |  | 5379 | 20.62 | 85.77 | 14.696 | 0.072743 | 0.041129
5380 | 85.78 | 14.696 | 0.072742 | 20.622 | 0.041134 |  | 5380 | 20.622 | 85.78 | 14.696 | 0.072742 | 0.041134
5381 | 85.79 | 14.696 | 0.07274 | 20.625 | 0.041138 |  | 5381 | 20.625 | 85.79 | 14.696 | 0.07274 | 0.041138
5382 | 85.8 | 14.696 | 0.072739 | 20.627 | 0.041143 |  | 5382 | 20.627 | 85.8 | 14.696 | 0.072739 | 0.041143
5383 | 85.81 | 14.696 | 0.072738 | 20.629 | 0.041147 |  | 5383 | 20.629 | 85.81 | 14.696 | 0.072738 | 0.041147
5384 | 85.82 | 14.696 | 0.072736 | 20.632 | 0.041151 |  | 5384 | 20.632 | 85.82 | 14.696 | 0.072736 | 0.041151
5385 | 85.83 | 14.696 | 0.072735 | 20.634 | 0.041156 |  | 5385 | 20.634 | 85.83 | 14.696 | 0.072735 | 0.041156
5386 | 85.84 | 14.696 | 0.072734 | 20.637 | 0.04116 |  | 5386 | 20.637 | 85.84 | 14.696 | 0.072734 | 0.04116
5387 | 85.85 | 14.696 | 0.072732 | 20.639 | 0.041165 |  | 5387 | 20.639 | 85.85 | 14.696 | 0.072732 | 0.041165
5388 | 85.86 | 14.696 | 0.072731 | 20.641 | 0.041169 |  | 5388 | 20.641 | 85.86 | 14.696 | 0.072731 | 0.041169
5389 | 85.87 | 14.696 | 0.07273 | 20.644 | 0.041173 |  | 5389 | 20.644 | 85.87 | 14.696 | 0.07273 | 0.041173
5390 | 85.88 | 14.696 | 0.072728 | 20.646 | 0.041178 |  | 5390 | 20.646 | 85.88 | 14.696 | 0.072728 | 0.041178
5391 | 85.89 | 14.696 | 0.072727 | 20.649 | 0.041182 |  | 5391 | 20.649 | 85.89 | 14.696 | 0.072727 | 0.041182
5392 | 85.9 | 14.696 | 0.072726 | 20.651 | 0.041187 |  | 5392 | 20.651 | 85.9 | 14.696 | 0.072726 | 0.041187
5393 | 85.91 | 14.696 | 0.072724 | 20.653 | 0.041191 |  | 5393 | 20.653 | 85.91 | 14.696 | 0.072724 | 0.041191
5394 | 85.92 | 14.696 | 0.072723 | 20.656 | 0.041195 |  | 5394 | 20.656 | 85.92 | 14.696 | 0.072723 | 0.041195
5395 | 85.93 | 14.696 | 0.072722 | 20.658 | 0.0412 |  | 5395 | 20.658 | 85.93 | 14.696 | 0.072722 | 0.0412
5396 | 85.94 | 14.696 | 0.07272 | 20.661 | 0.041204 |  | 5396 | 20.661 | 85.94 | 14.696 | 0.07272 | 0.041204
5397 | 85.95 | 14.696 | 0.072719 | 20.663 | 0.041209 |  | 5397 | 20.663 | 85.95 | 14.696 | 0.072719 | 0.041209
5398 | 85.96 | 14.696 | 0.072718 | 20.665 | 0.041213 |  | 5398 | 20.665 | 85.96 | 14.696 | 0.072718 | 0.041213
5399 | 85.97 | 14.696 | 0.072716 | 20.668 | 0.041217 |  | 5399 | 20.668 | 85.97 | 14.696 | 0.072716 | 0.041217
5400 | 85.98 | 14.696 | 0.072715 | 20.67 | 0.041222 |  | 5400 | 20.67 | 85.98 | 14.696 | 0.072715 | 0.041222
5401 | 85.99 | 14.696 | 0.072714 | 20.673 | 0.041226 |  | 5401 | 20.673 | 85.99 | 14.696 | 0.072714 | 0.041226
5402 | 86 | 14.696 | 0.072712 | 20.675 | 0.041231 |  | 5402 | 20.675 | 86 | 14.696 | 0.072712 | 0.041231
5403 | 86.01 | 14.696 | 0.072711 | 20.677 | 0.041235 |  | 5403 | 20.677 | 86.01 | 14.696 | 0.072711 | 0.041235
5404 | 86.02 | 14.696 | 0.07271 | 20.68 | 0.04124 |  | 5404 | 20.68 | 86.02 | 14.696 | 0.07271 | 0.04124
5405 | 86.03 | 14.696 | 0.072708 | 20.682 | 0.041244 |  | 5405 | 20.682 | 86.03 | 14.696 | 0.072708 | 0.041244
5406 | 86.04 | 14.696 | 0.072707 | 20.685 | 0.041248 |  | 5406 | 20.685 | 86.04 | 14.696 | 0.072707 | 0.041248
5407 | 86.05 | 14.696 | 0.072706 | 20.687 | 0.041253 |  | 5407 | 20.687 | 86.05 | 14.696 | 0.072706 | 0.041253
5408 | 86.06 | 14.696 | 0.072704 | 20.689 | 0.041257 |  | 5408 | 20.689 | 86.06 | 14.696 | 0.072704 | 0.041257
5409 | 86.07 | 14.696 | 0.072703 | 20.692 | 0.041262 |  | 5409 | 20.692 | 86.07 | 14.696 | 0.072703 | 0.041262
5410 | 86.08 | 14.696 | 0.072702 | 20.694 | 0.041266 |  | 5410 | 20.694 | 86.08 | 14.696 | 0.072702 | 0.041266
5411 | 86.09 | 14.696 | 0.0727 | 20.697 | 0.04127 |  | 5411 | 20.697 | 86.09 | 14.696 | 0.0727 | 0.04127
5412 | 86.1 | 14.696 | 0.072699 | 20.699 | 0.041275 |  | 5412 | 20.699 | 86.1 | 14.696 | 0.072699 | 0.041275
5413 | 86.11 | 14.696 | 0.072698 | 20.702 | 0.041279 |  | 5413 | 20.702 | 86.11 | 14.696 | 0.072698 | 0.041279
5414 | 86.12 | 14.696 | 0.072696 | 20.704 | 0.041284 |  | 5414 | 20.704 | 86.12 | 14.696 | 0.072696 | 0.041284
5415 | 86.13 | 14.696 | 0.072695 | 20.706 | 0.041288 |  | 5415 | 20.706 | 86.13 | 14.696 | 0.072695 | 0.041288
5416 | 86.14 | 14.696 | 0.072694 | 20.709 | 0.041292 |  | 5416 | 20.709 | 86.14 | 14.696 | 0.072694 | 0.041292
5417 | 86.15 | 14.696 | 0.072692 | 20.711 | 0.041297 |  | 5417 | 20.711 | 86.15 | 14.696 | 0.072692 | 0.041297
5418 | 86.16 | 14.696 | 0.072691 | 20.714 | 0.041301 |  | 5418 | 20.714 | 86.16 | 14.696 | 0.072691 | 0.041301
5419 | 86.17 | 14.696 | 0.072689 | 20.716 | 0.041306 |  | 5419 | 20.716 | 86.17 | 14.696 | 0.072689 | 0.041306
5420 | 86.18 | 14.696 | 0.072688 | 20.718 | 0.04131 |  | 5420 | 20.718 | 86.18 | 14.696 | 0.072688 | 0.04131
5421 | 86.19 | 14.696 | 0.072687 | 20.721 | 0.041314 |  | 5421 | 20.721 | 86.19 | 14.696 | 0.072687 | 0.041314
5422 | 86.2 | 14.696 | 0.072685 | 20.723 | 0.041319 |  | 5422 | 20.723 | 86.2 | 14.696 | 0.072685 | 0.041319
5423 | 86.21 | 14.696 | 0.072684 | 20.726 | 0.041323 |  | 5423 | 20.726 | 86.21 | 14.696 | 0.072684 | 0.041323
5424 | 86.22 | 14.696 | 0.072683 | 20.728 | 0.041328 |  | 5424 | 20.728 | 86.22 | 14.696 | 0.072683 | 0.041328
5425 | 86.23 | 14.696 | 0.072681 | 20.73 | 0.041332 |  | 5425 | 20.73 | 86.23 | 14.696 | 0.072681 | 0.041332
5426 | 86.24 | 14.696 | 0.07268 | 20.733 | 0.041336 |  | 5426 | 20.733 | 86.24 | 14.696 | 0.07268 | 0.041336
5427 | 86.25 | 14.696 | 0.072679 | 20.735 | 0.041341 |  | 5427 | 20.735 | 86.25 | 14.696 | 0.072679 | 0.041341
5428 | 86.26 | 14.696 | 0.072677 | 20.738 | 0.041345 |  | 5428 | 20.738 | 86.26 | 14.696 | 0.072677 | 0.041345
5429 | 86.27 | 14.696 | 0.072676 | 20.74 | 0.04135 |  | 5429 | 20.74 | 86.27 | 14.696 | 0.072676 | 0.04135
5430 | 86.28 | 14.696 | 0.072675 | 20.742 | 0.041354 |  | 5430 | 20.742 | 86.28 | 14.696 | 0.072675 | 0.041354
5431 | 86.29 | 14.696 | 0.072673 | 20.745 | 0.041359 |  | 5431 | 20.745 | 86.29 | 14.696 | 0.072673 | 0.041359
5432 | 86.3 | 14.696 | 0.072672 | 20.747 | 0.041363 |  | 5432 | 20.747 | 86.3 | 14.696 | 0.072672 | 0.041363
5433 | 86.31 | 14.696 | 0.072671 | 20.75 | 0.041367 |  | 5433 | 20.75 | 86.31 | 14.696 | 0.072671 | 0.041367
5434 | 86.32 | 14.696 | 0.072669 | 20.752 | 0.041372 |  | 5434 | 20.752 | 86.32 | 14.696 | 0.072669 | 0.041372
5435 | 86.33 | 14.696 | 0.072668 | 20.754 | 0.041376 |  | 5435 | 20.754 | 86.33 | 14.696 | 0.072668 | 0.041376
5436 | 86.34 | 14.696 | 0.072667 | 20.757 | 0.041381 |  | 5436 | 20.757 | 86.34 | 14.696 | 0.072667 | 0.041381
5437 | 86.35 | 14.696 | 0.072665 | 20.759 | 0.041385 |  | 5437 | 20.759 | 86.35 | 14.696 | 0.072665 | 0.041385
5438 | 86.36 | 14.696 | 0.072664 | 20.762 | 0.041389 |  | 5438 | 20.762 | 86.36 | 14.696 | 0.072664 | 0.041389
5439 | 86.37 | 14.696 | 0.072663 | 20.764 | 0.041394 |  | 5439 | 20.764 | 86.37 | 14.696 | 0.072663 | 0.041394
5440 | 86.38 | 14.696 | 0.072661 | 20.766 | 0.041398 |  | 5440 | 20.766 | 86.38 | 14.696 | 0.072661 | 0.041398
5441 | 86.39 | 14.696 | 0.07266 | 20.769 | 0.041403 |  | 5441 | 20.769 | 86.39 | 14.696 | 0.07266 | 0.041403
5442 | 86.4 | 14.696 | 0.072659 | 20.771 | 0.041407 |  | 5442 | 20.771 | 86.4 | 14.696 | 0.072659 | 0.041407
5443 | 86.41 | 14.696 | 0.072657 | 20.774 | 0.041411 |  | 5443 | 20.774 | 86.41 | 14.696 | 0.072657 | 0.041411
5444 | 86.42 | 14.696 | 0.072656 | 20.776 | 0.041416 |  | 5444 | 20.776 | 86.42 | 14.696 | 0.072656 | 0.041416
5445 | 86.43 | 14.696 | 0.072655 | 20.779 | 0.04142 |  | 5445 | 20.779 | 86.43 | 14.696 | 0.072655 | 0.04142
5446 | 86.44 | 14.696 | 0.072653 | 20.781 | 0.041425 |  | 5446 | 20.781 | 86.44 | 14.696 | 0.072653 | 0.041425
5447 | 86.45 | 14.696 | 0.072652 | 20.783 | 0.041429 |  | 5447 | 20.783 | 86.45 | 14.696 | 0.072652 | 0.041429
5448 | 86.46 | 14.696 | 0.072651 | 20.786 | 0.041433 |  | 5448 | 20.786 | 86.46 | 14.696 | 0.072651 | 0.041433
5449 | 86.47 | 14.696 | 0.072649 | 20.788 | 0.041438 |  | 5449 | 20.788 | 86.47 | 14.696 | 0.072649 | 0.041438
5450 | 86.48 | 14.696 | 0.072648 | 20.791 | 0.041442 |  | 5450 | 20.791 | 86.48 | 14.696 | 0.072648 | 0.041442
5451 | 86.49 | 14.696 | 0.072647 | 20.793 | 0.041447 |  | 5451 | 20.793 | 86.49 | 14.696 | 0.072647 | 0.041447
5452 | 86.5 | 14.696 | 0.072645 | 20.795 | 0.041451 |  | 5452 | 20.795 | 86.5 | 14.696 | 0.072645 | 0.041451
5453 | 86.51 | 14.696 | 0.072644 | 20.798 | 0.041455 |  | 5453 | 20.798 | 86.51 | 14.696 | 0.072644 | 0.041455
5454 | 86.52 | 14.696 | 0.072643 | 20.8 | 0.04146 |  | 5454 | 20.8 | 86.52 | 14.696 | 0.072643 | 0.04146
5455 | 86.53 | 14.696 | 0.072641 | 20.803 | 0.041464 |  | 5455 | 20.803 | 86.53 | 14.696 | 0.072641 | 0.041464
5456 | 86.54 | 14.696 | 0.07264 | 20.805 | 0.041469 |  | 5456 | 20.805 | 86.54 | 14.696 | 0.07264 | 0.041469
5457 | 86.55 | 14.696 | 0.072639 | 20.807 | 0.041473 |  | 5457 | 20.807 | 86.55 | 14.696 | 0.072639 | 0.041473
5458 | 86.56 | 14.696 | 0.072637 | 20.81 | 0.041477 |  | 5458 | 20.81 | 86.56 | 14.696 | 0.072637 | 0.041477
5459 | 86.57 | 14.696 | 0.072636 | 20.812 | 0.041482 |  | 5459 | 20.812 | 86.57 | 14.696 | 0.072636 | 0.041482
5460 | 86.58 | 14.696 | 0.072635 | 20.815 | 0.041486 |  | 5460 | 20.815 | 86.58 | 14.696 | 0.072635 | 0.041486
5461 | 86.59 | 14.696 | 0.072633 | 20.817 | 0.041491 |  | 5461 | 20.817 | 86.59 | 14.696 | 0.072633 | 0.041491
5462 | 86.6 | 14.696 | 0.072632 | 20.819 | 0.041495 |  | 5462 | 20.819 | 86.6 | 14.696 | 0.072632 | 0.041495
5463 | 86.61 | 14.696 | 0.072631 | 20.822 | 0.041499 |  | 5463 | 20.822 | 86.61 | 14.696 | 0.072631 | 0.041499
5464 | 86.62 | 14.696 | 0.072629 | 20.824 | 0.041504 |  | 5464 | 20.824 | 86.62 | 14.696 | 0.072629 | 0.041504
5465 | 86.63 | 14.696 | 0.072628 | 20.827 | 0.041508 |  | 5465 | 20.827 | 86.63 | 14.696 | 0.072628 | 0.041508
5466 | 86.64 | 14.696 | 0.072627 | 20.829 | 0.041513 |  | 5466 | 20.829 | 86.64 | 14.696 | 0.072627 | 0.041513
5467 | 86.65 | 14.696 | 0.072625 | 20.831 | 0.041517 |  | 5467 | 20.831 | 86.65 | 14.696 | 0.072625 | 0.041517
5468 | 86.66 | 14.696 | 0.072624 | 20.834 | 0.041521 |  | 5468 | 20.834 | 86.66 | 14.696 | 0.072624 | 0.041521
5469 | 86.67 | 14.696 | 0.072623 | 20.836 | 0.041526 |  | 5469 | 20.836 | 86.67 | 14.696 | 0.072623 | 0.041526
5470 | 86.68 | 14.696 | 0.072621 | 20.839 | 0.04153 |  | 5470 | 20.839 | 86.68 | 14.696 | 0.072621 | 0.04153
5471 | 86.69 | 14.696 | 0.07262 | 20.841 | 0.041535 |  | 5471 | 20.841 | 86.69 | 14.696 | 0.07262 | 0.041535
5472 | 86.7 | 14.696 | 0.072619 | 20.843 | 0.041539 |  | 5472 | 20.843 | 86.7 | 14.696 | 0.072619 | 0.041539
5473 | 86.71 | 14.696 | 0.072617 | 20.846 | 0.041544 |  | 5473 | 20.846 | 86.71 | 14.696 | 0.072617 | 0.041544
5474 | 86.72 | 14.696 | 0.072616 | 20.848 | 0.041548 |  | 5474 | 20.848 | 86.72 | 14.696 | 0.072616 | 0.041548
5475 | 86.73 | 14.696 | 0.072615 | 20.851 | 0.041552 |  | 5475 | 20.851 | 86.73 | 14.696 | 0.072615 | 0.041552
5476 | 86.74 | 14.696 | 0.072613 | 20.853 | 0.041557 |  | 5476 | 20.853 | 86.74 | 14.696 | 0.072613 | 0.041557
5477 | 86.75 | 14.696 | 0.072612 | 20.855 | 0.041561 |  | 5477 | 20.855 | 86.75 | 14.696 | 0.072612 | 0.041561
5478 | 86.76 | 14.696 | 0.072611 | 20.858 | 0.041566 |  | 5478 | 20.858 | 86.76 | 14.696 | 0.072611 | 0.041566
5479 | 86.77 | 14.696 | 0.072609 | 20.86 | 0.04157 |  | 5479 | 20.86 | 86.77 | 14.696 | 0.072609 | 0.04157
5480 | 86.78 | 14.696 | 0.072608 | 20.863 | 0.041574 |  | 5480 | 20.863 | 86.78 | 14.696 | 0.072608 | 0.041574
5481 | 86.79 | 14.696 | 0.072607 | 20.865 | 0.041579 |  | 5481 | 20.865 | 86.79 | 14.696 | 0.072607 | 0.041579
5482 | 86.8 | 14.696 | 0.072605 | 20.868 | 0.041583 |  | 5482 | 20.868 | 86.8 | 14.696 | 0.072605 | 0.041583
5483 | 86.81 | 14.696 | 0.072604 | 20.87 | 0.041588 |  | 5483 | 20.87 | 86.81 | 14.696 | 0.072604 | 0.041588
5484 | 86.82 | 14.696 | 0.072603 | 20.872 | 0.041592 |  | 5484 | 20.872 | 86.82 | 14.696 | 0.072603 | 0.041592
5485 | 86.83 | 14.696 | 0.072601 | 20.875 | 0.041596 |  | 5485 | 20.875 | 86.83 | 14.696 | 0.072601 | 0.041596
5486 | 86.84 | 14.696 | 0.0726 | 20.877 | 0.041601 |  | 5486 | 20.877 | 86.84 | 14.696 | 0.0726 | 0.041601
5487 | 86.85 | 14.696 | 0.072599 | 20.88 | 0.041605 |  | 5487 | 20.88 | 86.85 | 14.696 | 0.072599 | 0.041605
5488 | 86.86 | 14.696 | 0.072597 | 20.882 | 0.04161 |  | 5488 | 20.882 | 86.86 | 14.696 | 0.072597 | 0.04161
5489 | 86.87 | 14.696 | 0.072596 | 20.884 | 0.041614 |  | 5489 | 20.884 | 86.87 | 14.696 | 0.072596 | 0.041614
5490 | 86.88 | 14.696 | 0.072595 | 20.887 | 0.041618 |  | 5490 | 20.887 | 86.88 | 14.696 | 0.072595 | 0.041618
5491 | 86.89 | 14.696 | 0.072593 | 20.889 | 0.041623 |  | 5491 | 20.889 | 86.89 | 14.696 | 0.072593 | 0.041623
5492 | 86.9 | 14.696 | 0.072592 | 20.892 | 0.041627 |  | 5492 | 20.892 | 86.9 | 14.696 | 0.072592 | 0.041627
5493 | 86.91 | 14.696 | 0.072591 | 20.894 | 0.041632 |  | 5493 | 20.894 | 86.91 | 14.696 | 0.072591 | 0.041632
5494 | 86.92 | 14.696 | 0.072589 | 20.896 | 0.041636 |  | 5494 | 20.896 | 86.92 | 14.696 | 0.072589 | 0.041636
5495 | 86.93 | 14.696 | 0.072588 | 20.899 | 0.04164 |  | 5495 | 20.899 | 86.93 | 14.696 | 0.072588 | 0.04164
5496 | 86.94 | 14.696 | 0.072587 | 20.901 | 0.041645 |  | 5496 | 20.901 | 86.94 | 14.696 | 0.072587 | 0.041645
5497 | 86.95 | 14.696 | 0.072586 | 20.904 | 0.041649 |  | 5497 | 20.904 | 86.95 | 14.696 | 0.072586 | 0.041649
5498 | 86.96 | 14.696 | 0.072584 | 20.906 | 0.041654 |  | 5498 | 20.906 | 86.96 | 14.696 | 0.072584 | 0.041654
5499 | 86.97 | 14.696 | 0.072583 | 20.908 | 0.041658 |  | 5499 | 20.908 | 86.97 | 14.696 | 0.072583 | 0.041658
5500 | 86.98 | 14.696 | 0.072582 | 20.911 | 0.041662 |  | 5500 | 20.911 | 86.98 | 14.696 | 0.072582 | 0.041662
5501 | 86.99 | 14.696 | 0.07258 | 20.913 | 0.041667 |  | 5501 | 20.913 | 86.99 | 14.696 | 0.07258 | 0.041667
5502 | 87 | 14.696 | 0.072579 | 20.916 | 0.041671 |  | 5502 | 20.916 | 87 | 14.696 | 0.072579 | 0.041671
5503 | 87.01 | 14.696 | 0.072578 | 20.918 | 0.041676 |  | 5503 | 20.918 | 87.01 | 14.696 | 0.072578 | 0.041676
5504 | 87.02 | 14.696 | 0.072576 | 20.92 | 0.04168 |  | 5504 | 20.92 | 87.02 | 14.696 | 0.072576 | 0.04168
5505 | 87.03 | 14.696 | 0.072575 | 20.923 | 0.041684 |  | 5505 | 20.923 | 87.03 | 14.696 | 0.072575 | 0.041684
5506 | 87.04 | 14.696 | 0.072574 | 20.925 | 0.041689 |  | 5506 | 20.925 | 87.04 | 14.696 | 0.072574 | 0.041689
5507 | 87.05 | 14.696 | 0.072572 | 20.928 | 0.041693 |  | 5507 | 20.928 | 87.05 | 14.696 | 0.072572 | 0.041693
5508 | 87.06 | 14.696 | 0.072571 | 20.93 | 0.041698 |  | 5508 | 20.93 | 87.06 | 14.696 | 0.072571 | 0.041698
5509 | 87.07 | 14.696 | 0.07257 | 20.932 | 0.041702 |  | 5509 | 20.932 | 87.07 | 14.696 | 0.07257 | 0.041702
5510 | 87.08 | 14.696 | 0.072568 | 20.935 | 0.041706 |  | 5510 | 20.935 | 87.08 | 14.696 | 0.072568 | 0.041706
5511 | 87.09 | 14.696 | 0.072567 | 20.937 | 0.041711 |  | 5511 | 20.937 | 87.09 | 14.696 | 0.072567 | 0.041711
5512 | 87.1 | 14.696 | 0.072566 | 20.94 | 0.041715 |  | 5512 | 20.94 | 87.1 | 14.696 | 0.072566 | 0.041715
5513 | 87.11 | 14.696 | 0.072564 | 20.942 | 0.04172 |  | 5513 | 20.942 | 87.11 | 14.696 | 0.072564 | 0.04172
5514 | 87.12 | 14.696 | 0.072563 | 20.944 | 0.041724 |  | 5514 | 20.944 | 87.12 | 14.696 | 0.072563 | 0.041724
5515 | 87.13 | 14.696 | 0.072562 | 20.947 | 0.041728 |  | 5515 | 20.947 | 87.13 | 14.696 | 0.072562 | 0.041728
5516 | 87.14 | 14.696 | 0.07256 | 20.949 | 0.041733 |  | 5516 | 20.949 | 87.14 | 14.696 | 0.07256 | 0.041733
5517 | 87.15 | 14.696 | 0.072559 | 20.952 | 0.041737 |  | 5517 | 20.952 | 87.15 | 14.696 | 0.072559 | 0.041737
5518 | 87.16 | 14.696 | 0.072558 | 20.954 | 0.041742 |  | 5518 | 20.954 | 87.16 | 14.696 | 0.072558 | 0.041742
5519 | 87.17 | 14.696 | 0.072556 | 20.957 | 0.041746 |  | 5519 | 20.957 | 87.17 | 14.696 | 0.072556 | 0.041746
5520 | 87.18 | 14.696 | 0.072555 | 20.959 | 0.04175 |  | 5520 | 20.959 | 87.18 | 14.696 | 0.072555 | 0.04175
5521 | 87.19 | 14.696 | 0.072554 | 20.961 | 0.041755 |  | 5521 | 20.961 | 87.19 | 14.696 | 0.072554 | 0.041755
5522 | 87.2 | 14.696 | 0.072552 | 20.964 | 0.041759 |  | 5522 | 20.964 | 87.2 | 14.696 | 0.072552 | 0.041759
5523 | 87.21 | 14.696 | 0.072551 | 20.966 | 0.041764 |  | 5523 | 20.966 | 87.21 | 14.696 | 0.072551 | 0.041764
5524 | 87.22 | 14.696 | 0.07255 | 20.969 | 0.041768 |  | 5524 | 20.969 | 87.22 | 14.696 | 0.07255 | 0.041768
5525 | 87.23 | 14.696 | 0.072548 | 20.971 | 0.041772 |  | 5525 | 20.971 | 87.23 | 14.696 | 0.072548 | 0.041772
5526 | 87.24 | 14.696 | 0.072547 | 20.973 | 0.041777 |  | 5526 | 20.973 | 87.24 | 14.696 | 0.072547 | 0.041777
5527 | 87.25 | 14.696 | 0.072546 | 20.976 | 0.041781 |  | 5527 | 20.976 | 87.25 | 14.696 | 0.072546 | 0.041781
5528 | 87.26 | 14.696 | 0.072544 | 20.978 | 0.041786 |  | 5528 | 20.978 | 87.26 | 14.696 | 0.072544 | 0.041786
5529 | 87.27 | 14.696 | 0.072543 | 20.981 | 0.04179 |  | 5529 | 20.981 | 87.27 | 14.696 | 0.072543 | 0.04179
5530 | 87.28 | 14.696 | 0.072542 | 20.983 | 0.041794 |  | 5530 | 20.983 | 87.28 | 14.696 | 0.072542 | 0.041794
5531 | 87.29 | 14.696 | 0.07254 | 20.985 | 0.041799 |  | 5531 | 20.985 | 87.29 | 14.696 | 0.07254 | 0.041799
5532 | 87.3 | 14.696 | 0.072539 | 20.988 | 0.041803 |  | 5532 | 20.988 | 87.3 | 14.696 | 0.072539 | 0.041803
5533 | 87.31 | 14.696 | 0.072538 | 20.99 | 0.041808 |  | 5533 | 20.99 | 87.31 | 14.696 | 0.072538 | 0.041808
5534 | 87.32 | 14.696 | 0.072536 | 20.993 | 0.041812 |  | 5534 | 20.993 | 87.32 | 14.696 | 0.072536 | 0.041812
5535 | 87.33 | 14.696 | 0.072535 | 20.995 | 0.041816 |  | 5535 | 20.995 | 87.33 | 14.696 | 0.072535 | 0.041816
5536 | 87.34 | 14.696 | 0.072534 | 20.997 | 0.041821 |  | 5536 | 20.997 | 87.34 | 14.696 | 0.072534 | 0.041821
5537 | 87.35 | 14.696 | 0.072532 | 21 | 0.041825 |  | 5537 | 21 | 87.35 | 14.696 | 0.072532 | 0.041825
5538 | 87.36 | 14.696 | 0.072531 | 21.002 | 0.04183 |  | 5538 | 21.002 | 87.36 | 14.696 | 0.072531 | 0.04183
5539 | 87.37 | 14.696 | 0.07253 | 21.005 | 0.041834 |  | 5539 | 21.005 | 87.37 | 14.696 | 0.07253 | 0.041834
5540 | 87.38 | 14.696 | 0.072528 | 21.007 | 0.041838 |  | 5540 | 21.007 | 87.38 | 14.696 | 0.072528 | 0.041838
5541 | 87.39 | 14.696 | 0.072527 | 21.009 | 0.041843 |  | 5541 | 21.009 | 87.39 | 14.696 | 0.072527 | 0.041843
5542 | 87.4 | 14.696 | 0.072526 | 21.012 | 0.041847 |  | 5542 | 21.012 | 87.4 | 14.696 | 0.072526 | 0.041847
5543 | 87.41 | 14.696 | 0.072524 | 21.014 | 0.041852 |  | 5543 | 21.014 | 87.41 | 14.696 | 0.072524 | 0.041852
5544 | 87.42 | 14.696 | 0.072523 | 21.017 | 0.041856 |  | 5544 | 21.017 | 87.42 | 14.696 | 0.072523 | 0.041856
5545 | 87.43 | 14.696 | 0.072522 | 21.019 | 0.04186 |  | 5545 | 21.019 | 87.43 | 14.696 | 0.072522 | 0.04186
5546 | 87.44 | 14.696 | 0.07252 | 21.021 | 0.041865 |  | 5546 | 21.021 | 87.44 | 14.696 | 0.07252 | 0.041865
5547 | 87.45 | 14.696 | 0.072519 | 21.024 | 0.041869 |  | 5547 | 21.024 | 87.45 | 14.696 | 0.072519 | 0.041869
5548 | 87.46 | 14.696 | 0.072518 | 21.026 | 0.041873 |  | 5548 | 21.026 | 87.46 | 14.696 | 0.072518 | 0.041873
5549 | 87.47 | 14.696 | 0.072516 | 21.029 | 0.041878 |  | 5549 | 21.029 | 87.47 | 14.696 | 0.072516 | 0.041878
5550 | 87.48 | 14.696 | 0.072515 | 21.031 | 0.041882 |  | 5550 | 21.031 | 87.48 | 14.696 | 0.072515 | 0.041882
5551 | 87.49 | 14.696 | 0.072514 | 21.034 | 0.041887 |  | 5551 | 21.034 | 87.49 | 14.696 | 0.072514 | 0.041887
5552 | 87.5 | 14.696 | 0.072512 | 21.036 | 0.041891 |  | 5552 | 21.036 | 87.5 | 14.696 | 0.072512 | 0.041891
5553 | 87.51 | 14.696 | 0.072511 | 21.038 | 0.041895 |  | 5553 | 21.038 | 87.51 | 14.696 | 0.072511 | 0.041895
5554 | 87.52 | 14.696 | 0.07251 | 21.041 | 0.0419 |  | 5554 | 21.041 | 87.52 | 14.696 | 0.07251 | 0.0419
5555 | 87.53 | 14.696 | 0.072508 | 21.043 | 0.041904 |  | 5555 | 21.043 | 87.53 | 14.696 | 0.072508 | 0.041904
5556 | 87.54 | 14.696 | 0.072507 | 21.046 | 0.041909 |  | 5556 | 21.046 | 87.54 | 14.696 | 0.072507 | 0.041909
5557 | 87.55 | 14.696 | 0.072506 | 21.048 | 0.041913 |  | 5557 | 21.048 | 87.55 | 14.696 | 0.072506 | 0.041913
5558 | 87.56 | 14.696 | 0.072504 | 21.05 | 0.041917 |  | 5558 | 21.05 | 87.56 | 14.696 | 0.072504 | 0.041917
5559 | 87.57 | 14.696 | 0.072503 | 21.053 | 0.041922 |  | 5559 | 21.053 | 87.57 | 14.696 | 0.072503 | 0.041922
5560 | 87.58 | 14.696 | 0.072502 | 21.055 | 0.041926 |  | 5560 | 21.055 | 87.58 | 14.696 | 0.072502 | 0.041926
5561 | 87.59 | 14.696 | 0.0725 | 21.058 | 0.041931 |  | 5561 | 21.058 | 87.59 | 14.696 | 0.0725 | 0.041931
5562 | 87.6 | 14.696 | 0.072499 | 21.06 | 0.041935 |  | 5562 | 21.06 | 87.6 | 14.696 | 0.072499 | 0.041935
5563 | 87.61 | 14.696 | 0.072498 | 21.062 | 0.041939 |  | 5563 | 21.062 | 87.61 | 14.696 | 0.072498 | 0.041939
5564 | 87.62 | 14.696 | 0.072496 | 21.065 | 0.041944 |  | 5564 | 21.065 | 87.62 | 14.696 | 0.072496 | 0.041944
5565 | 87.63 | 14.696 | 0.072495 | 21.067 | 0.041948 |  | 5565 | 21.067 | 87.63 | 14.696 | 0.072495 | 0.041948
5566 | 87.64 | 14.696 | 0.072494 | 21.07 | 0.041953 |  | 5566 | 21.07 | 87.64 | 14.696 | 0.072494 | 0.041953
5567 | 87.65 | 14.696 | 0.072492 | 21.072 | 0.041957 |  | 5567 | 21.072 | 87.65 | 14.696 | 0.072492 | 0.041957
5568 | 87.66 | 14.696 | 0.072491 | 21.074 | 0.041961 |  | 5568 | 21.074 | 87.66 | 14.696 | 0.072491 | 0.041961
5569 | 87.67 | 14.696 | 0.07249 | 21.077 | 0.041966 |  | 5569 | 21.077 | 87.67 | 14.696 | 0.07249 | 0.041966
5570 | 87.68 | 14.696 | 0.072488 | 21.079 | 0.04197 |  | 5570 | 21.079 | 87.68 | 14.696 | 0.072488 | 0.04197
5571 | 87.69 | 14.696 | 0.072487 | 21.082 | 0.041975 |  | 5571 | 21.082 | 87.69 | 14.696 | 0.072487 | 0.041975
5572 | 87.7 | 14.696 | 0.072486 | 21.084 | 0.041979 |  | 5572 | 21.084 | 87.7 | 14.696 | 0.072486 | 0.041979
5573 | 87.71 | 14.696 | 0.072484 | 21.086 | 0.041983 |  | 5573 | 21.086 | 87.71 | 14.696 | 0.072484 | 0.041983
5574 | 87.72 | 14.696 | 0.072483 | 21.089 | 0.041988 |  | 5574 | 21.089 | 87.72 | 14.696 | 0.072483 | 0.041988
5575 | 87.73 | 14.696 | 0.072482 | 21.091 | 0.041992 |  | 5575 | 21.091 | 87.73 | 14.696 | 0.072482 | 0.041992
5576 | 87.74 | 14.696 | 0.07248 | 21.094 | 0.041997 |  | 5576 | 21.094 | 87.74 | 14.696 | 0.07248 | 0.041997
5577 | 87.75 | 14.696 | 0.072479 | 21.096 | 0.042001 |  | 5577 | 21.096 | 87.75 | 14.696 | 0.072479 | 0.042001
5578 | 87.76 | 14.696 | 0.072478 | 21.098 | 0.042005 |  | 5578 | 21.098 | 87.76 | 14.696 | 0.072478 | 0.042005
5579 | 87.77 | 14.696 | 0.072477 | 21.101 | 0.04201 |  | 5579 | 21.101 | 87.77 | 14.696 | 0.072477 | 0.04201
5580 | 87.78 | 14.696 | 0.072475 | 21.103 | 0.042014 |  | 5580 | 21.103 | 87.78 | 14.696 | 0.072475 | 0.042014
5581 | 87.79 | 14.696 | 0.072474 | 21.106 | 0.042019 |  | 5581 | 21.106 | 87.79 | 14.696 | 0.072474 | 0.042019
5582 | 87.8 | 14.696 | 0.072473 | 21.108 | 0.042023 |  | 5582 | 21.108 | 87.8 | 14.696 | 0.072473 | 0.042023
5583 | 87.81 | 14.696 | 0.072471 | 21.11 | 0.042027 |  | 5583 | 21.11 | 87.81 | 14.696 | 0.072471 | 0.042027
5584 | 87.82 | 14.696 | 0.07247 | 21.113 | 0.042032 |  | 5584 | 21.113 | 87.82 | 14.696 | 0.07247 | 0.042032
5585 | 87.83 | 14.696 | 0.072469 | 21.115 | 0.042036 |  | 5585 | 21.115 | 87.83 | 14.696 | 0.072469 | 0.042036
5586 | 87.84 | 14.696 | 0.072467 | 21.118 | 0.042041 |  | 5586 | 21.118 | 87.84 | 14.696 | 0.072467 | 0.042041
5587 | 87.85 | 14.696 | 0.072466 | 21.12 | 0.042045 |  | 5587 | 21.12 | 87.85 | 14.696 | 0.072466 | 0.042045
5588 | 87.86 | 14.696 | 0.072465 | 21.123 | 0.042049 |  | 5588 | 21.123 | 87.86 | 14.696 | 0.072465 | 0.042049
5589 | 87.87 | 14.696 | 0.072463 | 21.125 | 0.042054 |  | 5589 | 21.125 | 87.87 | 14.696 | 0.072463 | 0.042054
5590 | 87.88 | 14.696 | 0.072462 | 21.127 | 0.042058 |  | 5590 | 21.127 | 87.88 | 14.696 | 0.072462 | 0.042058
5591 | 87.89 | 14.696 | 0.072461 | 21.13 | 0.042062 |  | 5591 | 21.13 | 87.89 | 14.696 | 0.072461 | 0.042062
5592 | 87.9 | 14.696 | 0.072459 | 21.132 | 0.042067 |  | 5592 | 21.132 | 87.9 | 14.696 | 0.072459 | 0.042067
5593 | 87.91 | 14.696 | 0.072458 | 21.135 | 0.042071 |  | 5593 | 21.135 | 87.91 | 14.696 | 0.072458 | 0.042071
5594 | 87.92 | 14.696 | 0.072457 | 21.137 | 0.042076 |  | 5594 | 21.137 | 87.92 | 14.696 | 0.072457 | 0.042076
5595 | 87.93 | 14.696 | 0.072455 | 21.139 | 0.04208 |  | 5595 | 21.139 | 87.93 | 14.696 | 0.072455 | 0.04208
5596 | 87.94 | 14.696 | 0.072454 | 21.142 | 0.042084 |  | 5596 | 21.142 | 87.94 | 14.696 | 0.072454 | 0.042084
5597 | 87.95 | 14.696 | 0.072453 | 21.144 | 0.042089 |  | 5597 | 21.144 | 87.95 | 14.696 | 0.072453 | 0.042089
5598 | 87.96 | 14.696 | 0.072451 | 21.147 | 0.042093 |  | 5598 | 21.147 | 87.96 | 14.696 | 0.072451 | 0.042093
5599 | 87.97 | 14.696 | 0.07245 | 21.149 | 0.042098 |  | 5599 | 21.149 | 87.97 | 14.696 | 0.07245 | 0.042098
5600 | 87.98 | 14.696 | 0.072449 | 21.151 | 0.042102 |  | 5600 | 21.151 | 87.98 | 14.696 | 0.072449 | 0.042102
5601 | 87.99 | 14.696 | 0.072447 | 21.154 | 0.042106 |  | 5601 | 21.154 | 87.99 | 14.696 | 0.072447 | 0.042106
5602 | 88 | 14.696 | 0.072446 | 21.156 | 0.042111 |  | 5602 | 21.156 | 88 | 14.696 | 0.072446 | 0.042111
5603 | 88.01 | 14.696 | 0.072445 | 21.159 | 0.042115 |  | 5603 | 21.159 | 88.01 | 14.696 | 0.072445 | 0.042115
5604 | 88.02 | 14.696 | 0.072443 | 21.161 | 0.04212 |  | 5604 | 21.161 | 88.02 | 14.696 | 0.072443 | 0.04212
5605 | 88.03 | 14.696 | 0.072442 | 21.163 | 0.042124 |  | 5605 | 21.163 | 88.03 | 14.696 | 0.072442 | 0.042124
5606 | 88.04 | 14.696 | 0.072441 | 21.166 | 0.042128 |  | 5606 | 21.166 | 88.04 | 14.696 | 0.072441 | 0.042128
5607 | 88.05 | 14.696 | 0.072439 | 21.168 | 0.042133 |  | 5607 | 21.168 | 88.05 | 14.696 | 0.072439 | 0.042133
5608 | 88.06 | 14.696 | 0.072438 | 21.171 | 0.042137 |  | 5608 | 21.171 | 88.06 | 14.696 | 0.072438 | 0.042137
5609 | 88.07 | 14.696 | 0.072437 | 21.173 | 0.042142 |  | 5609 | 21.173 | 88.07 | 14.696 | 0.072437 | 0.042142
5610 | 88.08 | 14.696 | 0.072435 | 21.175 | 0.042146 |  | 5610 | 21.175 | 88.08 | 14.696 | 0.072435 | 0.042146
5611 | 88.09 | 14.696 | 0.072434 | 21.178 | 0.04215 |  | 5611 | 21.178 | 88.09 | 14.696 | 0.072434 | 0.04215
5612 | 88.1 | 14.696 | 0.072433 | 21.18 | 0.042155 |  | 5612 | 21.18 | 88.1 | 14.696 | 0.072433 | 0.042155
5613 | 88.11 | 14.696 | 0.072431 | 21.183 | 0.042159 |  | 5613 | 21.183 | 88.11 | 14.696 | 0.072431 | 0.042159
5614 | 88.12 | 14.696 | 0.07243 | 21.185 | 0.042164 |  | 5614 | 21.185 | 88.12 | 14.696 | 0.07243 | 0.042164
5615 | 88.13 | 14.696 | 0.072429 | 21.187 | 0.042168 |  | 5615 | 21.187 | 88.13 | 14.696 | 0.072429 | 0.042168
5616 | 88.14 | 14.696 | 0.072427 | 21.19 | 0.042172 |  | 5616 | 21.19 | 88.14 | 14.696 | 0.072427 | 0.042172
5617 | 88.15 | 14.696 | 0.072426 | 21.192 | 0.042177 |  | 5617 | 21.192 | 88.15 | 14.696 | 0.072426 | 0.042177
5618 | 88.16 | 14.696 | 0.072425 | 21.195 | 0.042181 |  | 5618 | 21.195 | 88.16 | 14.696 | 0.072425 | 0.042181
5619 | 88.17 | 14.696 | 0.072423 | 21.197 | 0.042185 |  | 5619 | 21.197 | 88.17 | 14.696 | 0.072423 | 0.042185
5620 | 88.18 | 14.696 | 0.072422 | 21.199 | 0.04219 |  | 5620 | 21.199 | 88.18 | 14.696 | 0.072422 | 0.04219
5621 | 88.19 | 14.696 | 0.072421 | 21.202 | 0.042194 |  | 5621 | 21.202 | 88.19 | 14.696 | 0.072421 | 0.042194
5622 | 88.2 | 14.696 | 0.072419 | 21.204 | 0.042199 |  | 5622 | 21.204 | 88.2 | 14.696 | 0.072419 | 0.042199
5623 | 88.21 | 14.696 | 0.072418 | 21.207 | 0.042203 |  | 5623 | 21.207 | 88.21 | 14.696 | 0.072418 | 0.042203
5624 | 88.22 | 14.696 | 0.072417 | 21.209 | 0.042207 |  | 5624 | 21.209 | 88.22 | 14.696 | 0.072417 | 0.042207
5625 | 88.23 | 14.696 | 0.072415 | 21.212 | 0.042212 |  | 5625 | 21.212 | 88.23 | 14.696 | 0.072415 | 0.042212
5626 | 88.24 | 14.696 | 0.072414 | 21.214 | 0.042216 |  | 5626 | 21.214 | 88.24 | 14.696 | 0.072414 | 0.042216
5627 | 88.25 | 14.696 | 0.072413 | 21.216 | 0.042221 |  | 5627 | 21.216 | 88.25 | 14.696 | 0.072413 | 0.042221
5628 | 88.26 | 14.696 | 0.072412 | 21.219 | 0.042225 |  | 5628 | 21.219 | 88.26 | 14.696 | 0.072412 | 0.042225
5629 | 88.27 | 14.696 | 0.07241 | 21.221 | 0.042229 |  | 5629 | 21.221 | 88.27 | 14.696 | 0.07241 | 0.042229
5630 | 88.28 | 14.696 | 0.072409 | 21.224 | 0.042234 |  | 5630 | 21.224 | 88.28 | 14.696 | 0.072409 | 0.042234
5631 | 88.29 | 14.696 | 0.072408 | 21.226 | 0.042238 |  | 5631 | 21.226 | 88.29 | 14.696 | 0.072408 | 0.042238
5632 | 88.3 | 14.696 | 0.072406 | 21.228 | 0.042243 |  | 5632 | 21.228 | 88.3 | 14.696 | 0.072406 | 0.042243
5633 | 88.31 | 14.696 | 0.072405 | 21.231 | 0.042247 |  | 5633 | 21.231 | 88.31 | 14.696 | 0.072405 | 0.042247
5634 | 88.32 | 14.696 | 0.072404 | 21.233 | 0.042251 |  | 5634 | 21.233 | 88.32 | 14.696 | 0.072404 | 0.042251
5635 | 88.33 | 14.696 | 0.072402 | 21.236 | 0.042256 |  | 5635 | 21.236 | 88.33 | 14.696 | 0.072402 | 0.042256
5636 | 88.34 | 14.696 | 0.072401 | 21.238 | 0.04226 |  | 5636 | 21.238 | 88.34 | 14.696 | 0.072401 | 0.04226
5637 | 88.35 | 14.696 | 0.0724 | 21.24 | 0.042265 |  | 5637 | 21.24 | 88.35 | 14.696 | 0.0724 | 0.042265
5638 | 88.36 | 14.696 | 0.072398 | 21.243 | 0.042269 |  | 5638 | 21.243 | 88.36 | 14.696 | 0.072398 | 0.042269
5639 | 88.37 | 14.696 | 0.072397 | 21.245 | 0.042273 |  | 5639 | 21.245 | 88.37 | 14.696 | 0.072397 | 0.042273
5640 | 88.38 | 14.696 | 0.072396 | 21.248 | 0.042278 |  | 5640 | 21.248 | 88.38 | 14.696 | 0.072396 | 0.042278
5641 | 88.39 | 14.696 | 0.072394 | 21.25 | 0.042282 |  | 5641 | 21.25 | 88.39 | 14.696 | 0.072394 | 0.042282
5642 | 88.4 | 14.696 | 0.072393 | 21.252 | 0.042286 |  | 5642 | 21.252 | 88.4 | 14.696 | 0.072393 | 0.042286
5643 | 88.41 | 14.696 | 0.072392 | 21.255 | 0.042291 |  | 5643 | 21.255 | 88.41 | 14.696 | 0.072392 | 0.042291
5644 | 88.42 | 14.696 | 0.07239 | 21.257 | 0.042295 |  | 5644 | 21.257 | 88.42 | 14.696 | 0.07239 | 0.042295
5645 | 88.43 | 14.696 | 0.072389 | 21.26 | 0.0423 |  | 5645 | 21.26 | 88.43 | 14.696 | 0.072389 | 0.0423
5646 | 88.44 | 14.696 | 0.072388 | 21.262 | 0.042304 |  | 5646 | 21.262 | 88.44 | 14.696 | 0.072388 | 0.042304
5647 | 88.45 | 14.696 | 0.072386 | 21.264 | 0.042308 |  | 5647 | 21.264 | 88.45 | 14.696 | 0.072386 | 0.042308
5648 | 88.46 | 14.696 | 0.072385 | 21.267 | 0.042313 |  | 5648 | 21.267 | 88.46 | 14.696 | 0.072385 | 0.042313
5649 | 88.47 | 14.696 | 0.072384 | 21.269 | 0.042317 |  | 5649 | 21.269 | 88.47 | 14.696 | 0.072384 | 0.042317
5650 | 88.48 | 14.696 | 0.072382 | 21.272 | 0.042322 |  | 5650 | 21.272 | 88.48 | 14.696 | 0.072382 | 0.042322
5651 | 88.49 | 14.696 | 0.072381 | 21.274 | 0.042326 |  | 5651 | 21.274 | 88.49 | 14.696 | 0.072381 | 0.042326
5652 | 88.5 | 14.696 | 0.07238 | 21.276 | 0.04233 |  | 5652 | 21.276 | 88.5 | 14.696 | 0.07238 | 0.04233
5653 | 88.51 | 14.696 | 0.072378 | 21.279 | 0.042335 |  | 5653 | 21.279 | 88.51 | 14.696 | 0.072378 | 0.042335
5654 | 88.52 | 14.696 | 0.072377 | 21.281 | 0.042339 |  | 5654 | 21.281 | 88.52 | 14.696 | 0.072377 | 0.042339
5655 | 88.53 | 14.696 | 0.072376 | 21.284 | 0.042344 |  | 5655 | 21.284 | 88.53 | 14.696 | 0.072376 | 0.042344
5656 | 88.54 | 14.696 | 0.072374 | 21.286 | 0.042348 |  | 5656 | 21.286 | 88.54 | 14.696 | 0.072374 | 0.042348
5657 | 88.55 | 14.696 | 0.072373 | 21.289 | 0.042352 |  | 5657 | 21.289 | 88.55 | 14.696 | 0.072373 | 0.042352
5658 | 88.56 | 14.696 | 0.072372 | 21.291 | 0.042357 |  | 5658 | 21.291 | 88.56 | 14.696 | 0.072372 | 0.042357
5659 | 88.57 | 14.696 | 0.07237 | 21.293 | 0.042361 |  | 5659 | 21.293 | 88.57 | 14.696 | 0.07237 | 0.042361
5660 | 88.58 | 14.696 | 0.072369 | 21.296 | 0.042365 |  | 5660 | 21.296 | 88.58 | 14.696 | 0.072369 | 0.042365
5661 | 88.59 | 14.696 | 0.072368 | 21.298 | 0.04237 |  | 5661 | 21.298 | 88.59 | 14.696 | 0.072368 | 0.04237
5662 | 88.6 | 14.696 | 0.072367 | 21.301 | 0.042374 |  | 5662 | 21.301 | 88.6 | 14.696 | 0.072367 | 0.042374
5663 | 88.61 | 14.696 | 0.072365 | 21.303 | 0.042379 |  | 5663 | 21.303 | 88.61 | 14.696 | 0.072365 | 0.042379
5664 | 88.62 | 14.696 | 0.072364 | 21.305 | 0.042383 |  | 5664 | 21.305 | 88.62 | 14.696 | 0.072364 | 0.042383
5665 | 88.63 | 14.696 | 0.072363 | 21.308 | 0.042387 |  | 5665 | 21.308 | 88.63 | 14.696 | 0.072363 | 0.042387
5666 | 88.64 | 14.696 | 0.072361 | 21.31 | 0.042392 |  | 5666 | 21.31 | 88.64 | 14.696 | 0.072361 | 0.042392
5667 | 88.65 | 14.696 | 0.07236 | 21.313 | 0.042396 |  | 5667 | 21.313 | 88.65 | 14.696 | 0.07236 | 0.042396
5668 | 88.66 | 14.696 | 0.072359 | 21.315 | 0.042401 |  | 5668 | 21.315 | 88.66 | 14.696 | 0.072359 | 0.042401
5669 | 88.67 | 14.696 | 0.072357 | 21.317 | 0.042405 |  | 5669 | 21.317 | 88.67 | 14.696 | 0.072357 | 0.042405
5670 | 88.68 | 14.696 | 0.072356 | 21.32 | 0.042409 |  | 5670 | 21.32 | 88.68 | 14.696 | 0.072356 | 0.042409
5671 | 88.69 | 14.696 | 0.072355 | 21.322 | 0.042414 |  | 5671 | 21.322 | 88.69 | 14.696 | 0.072355 | 0.042414
5672 | 88.7 | 14.696 | 0.072353 | 21.325 | 0.042418 |  | 5672 | 21.325 | 88.7 | 14.696 | 0.072353 | 0.042418
5673 | 88.71 | 14.696 | 0.072352 | 21.327 | 0.042422 |  | 5673 | 21.327 | 88.71 | 14.696 | 0.072352 | 0.042422
5674 | 88.72 | 14.696 | 0.072351 | 21.329 | 0.042427 |  | 5674 | 21.329 | 88.72 | 14.696 | 0.072351 | 0.042427
5675 | 88.73 | 14.696 | 0.072349 | 21.332 | 0.042431 |  | 5675 | 21.332 | 88.73 | 14.696 | 0.072349 | 0.042431
5676 | 88.74 | 14.696 | 0.072348 | 21.334 | 0.042436 |  | 5676 | 21.334 | 88.74 | 14.696 | 0.072348 | 0.042436
5677 | 88.75 | 14.696 | 0.072347 | 21.337 | 0.04244 |  | 5677 | 21.337 | 88.75 | 14.696 | 0.072347 | 0.04244
5678 | 88.76 | 14.696 | 0.072345 | 21.339 | 0.042444 |  | 5678 | 21.339 | 88.76 | 14.696 | 0.072345 | 0.042444
5679 | 88.77 | 14.696 | 0.072344 | 21.341 | 0.042449 |  | 5679 | 21.341 | 88.77 | 14.696 | 0.072344 | 0.042449
5680 | 88.78 | 14.696 | 0.072343 | 21.344 | 0.042453 |  | 5680 | 21.344 | 88.78 | 14.696 | 0.072343 | 0.042453
5681 | 88.79 | 14.696 | 0.072341 | 21.346 | 0.042458 |  | 5681 | 21.346 | 88.79 | 14.696 | 0.072341 | 0.042458
5682 | 88.8 | 14.696 | 0.07234 | 21.349 | 0.042462 |  | 5682 | 21.349 | 88.8 | 14.696 | 0.07234 | 0.042462
5683 | 88.81 | 14.696 | 0.072339 | 21.351 | 0.042466 |  | 5683 | 21.351 | 88.81 | 14.696 | 0.072339 | 0.042466
5684 | 88.82 | 14.696 | 0.072337 | 21.353 | 0.042471 |  | 5684 | 21.353 | 88.82 | 14.696 | 0.072337 | 0.042471
5685 | 88.83 | 14.696 | 0.072336 | 21.356 | 0.042475 |  | 5685 | 21.356 | 88.83 | 14.696 | 0.072336 | 0.042475
5686 | 88.84 | 14.696 | 0.072335 | 21.358 | 0.04248 |  | 5686 | 21.358 | 88.84 | 14.696 | 0.072335 | 0.04248
5687 | 88.85 | 14.696 | 0.072333 | 21.361 | 0.042484 |  | 5687 | 21.361 | 88.85 | 14.696 | 0.072333 | 0.042484
5688 | 88.86 | 14.696 | 0.072332 | 21.363 | 0.042488 |  | 5688 | 21.363 | 88.86 | 14.696 | 0.072332 | 0.042488
5689 | 88.87 | 14.696 | 0.072331 | 21.365 | 0.042493 |  | 5689 | 21.365 | 88.87 | 14.696 | 0.072331 | 0.042493
5690 | 88.88 | 14.696 | 0.072329 | 21.368 | 0.042497 |  | 5690 | 21.368 | 88.88 | 14.696 | 0.072329 | 0.042497
5691 | 88.89 | 14.696 | 0.072328 | 21.37 | 0.042501 |  | 5691 | 21.37 | 88.89 | 14.696 | 0.072328 | 0.042501
5692 | 88.9 | 14.696 | 0.072327 | 21.373 | 0.042506 |  | 5692 | 21.373 | 88.9 | 14.696 | 0.072327 | 0.042506
5693 | 88.91 | 14.696 | 0.072326 | 21.375 | 0.04251 |  | 5693 | 21.375 | 88.91 | 14.696 | 0.072326 | 0.04251
5694 | 88.92 | 14.696 | 0.072324 | 21.378 | 0.042515 |  | 5694 | 21.378 | 88.92 | 14.696 | 0.072324 | 0.042515
5695 | 88.93 | 14.696 | 0.072323 | 21.38 | 0.042519 |  | 5695 | 21.38 | 88.93 | 14.696 | 0.072323 | 0.042519
5696 | 88.94 | 14.696 | 0.072322 | 21.382 | 0.042523 |  | 5696 | 21.382 | 88.94 | 14.696 | 0.072322 | 0.042523
5697 | 88.95 | 14.696 | 0.07232 | 21.385 | 0.042528 |  | 5697 | 21.385 | 88.95 | 14.696 | 0.07232 | 0.042528
5698 | 88.96 | 14.696 | 0.072319 | 21.387 | 0.042532 |  | 5698 | 21.387 | 88.96 | 14.696 | 0.072319 | 0.042532
5699 | 88.97 | 14.696 | 0.072318 | 21.39 | 0.042537 |  | 5699 | 21.39 | 88.97 | 14.696 | 0.072318 | 0.042537
5700 | 88.98 | 14.696 | 0.072316 | 21.392 | 0.042541 |  | 5700 | 21.392 | 88.98 | 14.696 | 0.072316 | 0.042541
5701 | 88.99 | 14.696 | 0.072315 | 21.394 | 0.042545 |  | 5701 | 21.394 | 88.99 | 14.696 | 0.072315 | 0.042545
5702 | 89 | 14.696 | 0.072314 | 21.397 | 0.04255 |  | 5702 | 21.397 | 89 | 14.696 | 0.072314 | 0.04255
5703 | 89.01 | 14.696 | 0.072312 | 21.399 | 0.042554 |  | 5703 | 21.399 | 89.01 | 14.696 | 0.072312 | 0.042554
5704 | 89.02 | 14.696 | 0.072311 | 21.402 | 0.042558 |  | 5704 | 21.402 | 89.02 | 14.696 | 0.072311 | 0.042558
5705 | 89.03 | 14.696 | 0.07231 | 21.404 | 0.042563 |  | 5705 | 21.404 | 89.03 | 14.696 | 0.07231 | 0.042563
5706 | 89.04 | 14.696 | 0.072308 | 21.406 | 0.042567 |  | 5706 | 21.406 | 89.04 | 14.696 | 0.072308 | 0.042567
5707 | 89.05 | 14.696 | 0.072307 | 21.409 | 0.042572 |  | 5707 | 21.409 | 89.05 | 14.696 | 0.072307 | 0.042572
5708 | 89.06 | 14.696 | 0.072306 | 21.411 | 0.042576 |  | 5708 | 21.411 | 89.06 | 14.696 | 0.072306 | 0.042576
5709 | 89.07 | 14.696 | 0.072304 | 21.414 | 0.04258 |  | 5709 | 21.414 | 89.07 | 14.696 | 0.072304 | 0.04258
5710 | 89.08 | 14.696 | 0.072303 | 21.416 | 0.042585 |  | 5710 | 21.416 | 89.08 | 14.696 | 0.072303 | 0.042585
5711 | 89.09 | 14.696 | 0.072302 | 21.418 | 0.042589 |  | 5711 | 21.418 | 89.09 | 14.696 | 0.072302 | 0.042589
5712 | 89.1 | 14.696 | 0.0723 | 21.421 | 0.042594 |  | 5712 | 21.421 | 89.1 | 14.696 | 0.0723 | 0.042594
5713 | 89.11 | 14.696 | 0.072299 | 21.423 | 0.042598 |  | 5713 | 21.423 | 89.11 | 14.696 | 0.072299 | 0.042598
5714 | 89.12 | 14.696 | 0.072298 | 21.426 | 0.042602 |  | 5714 | 21.426 | 89.12 | 14.696 | 0.072298 | 0.042602
5715 | 89.13 | 14.696 | 0.072296 | 21.428 | 0.042607 |  | 5715 | 21.428 | 89.13 | 14.696 | 0.072296 | 0.042607
5716 | 89.14 | 14.696 | 0.072295 | 21.43 | 0.042611 |  | 5716 | 21.43 | 89.14 | 14.696 | 0.072295 | 0.042611
5717 | 89.15 | 14.696 | 0.072294 | 21.433 | 0.042615 |  | 5717 | 21.433 | 89.15 | 14.696 | 0.072294 | 0.042615
5718 | 89.16 | 14.696 | 0.072292 | 21.435 | 0.04262 |  | 5718 | 21.435 | 89.16 | 14.696 | 0.072292 | 0.04262
5719 | 89.17 | 14.696 | 0.072291 | 21.438 | 0.042624 |  | 5719 | 21.438 | 89.17 | 14.696 | 0.072291 | 0.042624
5720 | 89.18 | 14.696 | 0.07229 | 21.44 | 0.042629 |  | 5720 | 21.44 | 89.18 | 14.696 | 0.07229 | 0.042629
5721 | 89.19 | 14.696 | 0.072289 | 21.442 | 0.042633 |  | 5721 | 21.442 | 89.19 | 14.696 | 0.072289 | 0.042633
5722 | 89.2 | 14.696 | 0.072287 | 21.445 | 0.042637 |  | 5722 | 21.445 | 89.2 | 14.696 | 0.072287 | 0.042637
5723 | 89.21 | 14.696 | 0.072286 | 21.447 | 0.042642 |  | 5723 | 21.447 | 89.21 | 14.696 | 0.072286 | 0.042642
5724 | 89.22 | 14.696 | 0.072285 | 21.45 | 0.042646 |  | 5724 | 21.45 | 89.22 | 14.696 | 0.072285 | 0.042646
5725 | 89.23 | 14.696 | 0.072283 | 21.452 | 0.042651 |  | 5725 | 21.452 | 89.23 | 14.696 | 0.072283 | 0.042651
5726 | 89.24 | 14.696 | 0.072282 | 21.454 | 0.042655 |  | 5726 | 21.454 | 89.24 | 14.696 | 0.072282 | 0.042655
5727 | 89.25 | 14.696 | 0.072281 | 21.457 | 0.042659 |  | 5727 | 21.457 | 89.25 | 14.696 | 0.072281 | 0.042659
5728 | 89.26 | 14.696 | 0.072279 | 21.459 | 0.042664 |  | 5728 | 21.459 | 89.26 | 14.696 | 0.072279 | 0.042664
5729 | 89.27 | 14.696 | 0.072278 | 21.462 | 0.042668 |  | 5729 | 21.462 | 89.27 | 14.696 | 0.072278 | 0.042668
5730 | 89.28 | 14.696 | 0.072277 | 21.464 | 0.042672 |  | 5730 | 21.464 | 89.28 | 14.696 | 0.072277 | 0.042672
5731 | 89.29 | 14.696 | 0.072275 | 21.467 | 0.042677 |  | 5731 | 21.467 | 89.29 | 14.696 | 0.072275 | 0.042677
5732 | 89.3 | 14.696 | 0.072274 | 21.469 | 0.042681 |  | 5732 | 21.469 | 89.3 | 14.696 | 0.072274 | 0.042681
5733 | 89.31 | 14.696 | 0.072273 | 21.471 | 0.042686 |  | 5733 | 21.471 | 89.31 | 14.696 | 0.072273 | 0.042686
5734 | 89.32 | 14.696 | 0.072271 | 21.474 | 0.04269 |  | 5734 | 21.474 | 89.32 | 14.696 | 0.072271 | 0.04269
5735 | 89.33 | 14.696 | 0.07227 | 21.476 | 0.042694 |  | 5735 | 21.476 | 89.33 | 14.696 | 0.07227 | 0.042694
5736 | 89.34 | 14.696 | 0.072269 | 21.479 | 0.042699 |  | 5736 | 21.479 | 89.34 | 14.696 | 0.072269 | 0.042699
5737 | 89.35 | 14.696 | 0.072267 | 21.481 | 0.042703 |  | 5737 | 21.481 | 89.35 | 14.696 | 0.072267 | 0.042703
5738 | 89.36 | 14.696 | 0.072266 | 21.483 | 0.042707 |  | 5738 | 21.483 | 89.36 | 14.696 | 0.072266 | 0.042707
5739 | 89.37 | 14.696 | 0.072265 | 21.486 | 0.042712 |  | 5739 | 21.486 | 89.37 | 14.696 | 0.072265 | 0.042712
5740 | 89.38 | 14.696 | 0.072263 | 21.488 | 0.042716 |  | 5740 | 21.488 | 89.38 | 14.696 | 0.072263 | 0.042716
5741 | 89.39 | 14.696 | 0.072262 | 21.491 | 0.042721 |  | 5741 | 21.491 | 89.39 | 14.696 | 0.072262 | 0.042721
5742 | 89.4 | 14.696 | 0.072261 | 21.493 | 0.042725 |  | 5742 | 21.493 | 89.4 | 14.696 | 0.072261 | 0.042725
5743 | 89.41 | 14.696 | 0.072259 | 21.495 | 0.042729 |  | 5743 | 21.495 | 89.41 | 14.696 | 0.072259 | 0.042729
5744 | 89.42 | 14.696 | 0.072258 | 21.498 | 0.042734 |  | 5744 | 21.498 | 89.42 | 14.696 | 0.072258 | 0.042734
5745 | 89.43 | 14.696 | 0.072257 | 21.5 | 0.042738 |  | 5745 | 21.5 | 89.43 | 14.696 | 0.072257 | 0.042738
5746 | 89.44 | 14.696 | 0.072256 | 21.503 | 0.042743 |  | 5746 | 21.503 | 89.44 | 14.696 | 0.072256 | 0.042743
5747 | 89.45 | 14.696 | 0.072254 | 21.505 | 0.042747 |  | 5747 | 21.505 | 89.45 | 14.696 | 0.072254 | 0.042747
5748 | 89.46 | 14.696 | 0.072253 | 21.507 | 0.042751 |  | 5748 | 21.507 | 89.46 | 14.696 | 0.072253 | 0.042751
5749 | 89.47 | 14.696 | 0.072252 | 21.51 | 0.042756 |  | 5749 | 21.51 | 89.47 | 14.696 | 0.072252 | 0.042756
5750 | 89.48 | 14.696 | 0.07225 | 21.512 | 0.04276 |  | 5750 | 21.512 | 89.48 | 14.696 | 0.07225 | 0.04276
5751 | 89.49 | 14.696 | 0.072249 | 21.515 | 0.042764 |  | 5751 | 21.515 | 89.49 | 14.696 | 0.072249 | 0.042764
5752 | 89.5 | 14.696 | 0.072248 | 21.517 | 0.042769 |  | 5752 | 21.517 | 89.5 | 14.696 | 0.072248 | 0.042769
5753 | 89.51 | 14.696 | 0.072246 | 21.519 | 0.042773 |  | 5753 | 21.519 | 89.51 | 14.696 | 0.072246 | 0.042773
5754 | 89.52 | 14.696 | 0.072245 | 21.522 | 0.042778 |  | 5754 | 21.522 | 89.52 | 14.696 | 0.072245 | 0.042778
5755 | 89.53 | 14.696 | 0.072244 | 21.524 | 0.042782 |  | 5755 | 21.524 | 89.53 | 14.696 | 0.072244 | 0.042782
5756 | 89.54 | 14.696 | 0.072242 | 21.527 | 0.042786 |  | 5756 | 21.527 | 89.54 | 14.696 | 0.072242 | 0.042786
5757 | 89.55 | 14.696 | 0.072241 | 21.529 | 0.042791 |  | 5757 | 21.529 | 89.55 | 14.696 | 0.072241 | 0.042791
5758 | 89.56 | 14.696 | 0.07224 | 21.531 | 0.042795 |  | 5758 | 21.531 | 89.56 | 14.696 | 0.07224 | 0.042795
5759 | 89.57 | 14.696 | 0.072238 | 21.534 | 0.042799 |  | 5759 | 21.534 | 89.57 | 14.696 | 0.072238 | 0.042799
5760 | 89.58 | 14.696 | 0.072237 | 21.536 | 0.042804 |  | 5760 | 21.536 | 89.58 | 14.696 | 0.072237 | 0.042804
5761 | 89.59 | 14.696 | 0.072236 | 21.539 | 0.042808 |  | 5761 | 21.539 | 89.59 | 14.696 | 0.072236 | 0.042808
5762 | 89.6 | 14.696 | 0.072234 | 21.541 | 0.042813 |  | 5762 | 21.541 | 89.6 | 14.696 | 0.072234 | 0.042813
5763 | 89.61 | 14.696 | 0.072233 | 21.544 | 0.042817 |  | 5763 | 21.544 | 89.61 | 14.696 | 0.072233 | 0.042817
5764 | 89.62 | 14.696 | 0.072232 | 21.546 | 0.042821 |  | 5764 | 21.546 | 89.62 | 14.696 | 0.072232 | 0.042821
5765 | 89.63 | 14.696 | 0.07223 | 21.548 | 0.042826 |  | 5765 | 21.548 | 89.63 | 14.696 | 0.07223 | 0.042826
5766 | 89.64 | 14.696 | 0.072229 | 21.551 | 0.04283 |  | 5766 | 21.551 | 89.64 | 14.696 | 0.072229 | 0.04283
5767 | 89.65 | 14.696 | 0.072228 | 21.553 | 0.042835 |  | 5767 | 21.553 | 89.65 | 14.696 | 0.072228 | 0.042835
5768 | 89.66 | 14.696 | 0.072227 | 21.556 | 0.042839 |  | 5768 | 21.556 | 89.66 | 14.696 | 0.072227 | 0.042839
5769 | 89.67 | 14.696 | 0.072225 | 21.558 | 0.042843 |  | 5769 | 21.558 | 89.67 | 14.696 | 0.072225 | 0.042843
5770 | 89.68 | 14.696 | 0.072224 | 21.56 | 0.042848 |  | 5770 | 21.56 | 89.68 | 14.696 | 0.072224 | 0.042848
5771 | 89.69 | 14.696 | 0.072223 | 21.563 | 0.042852 |  | 5771 | 21.563 | 89.69 | 14.696 | 0.072223 | 0.042852
5772 | 89.7 | 14.696 | 0.072221 | 21.565 | 0.042856 |  | 5772 | 21.565 | 89.7 | 14.696 | 0.072221 | 0.042856
5773 | 89.71 | 14.696 | 0.07222 | 21.568 | 0.042861 |  | 5773 | 21.568 | 89.71 | 14.696 | 0.07222 | 0.042861
5774 | 89.72 | 14.696 | 0.072219 | 21.57 | 0.042865 |  | 5774 | 21.57 | 89.72 | 14.696 | 0.072219 | 0.042865
5775 | 89.73 | 14.696 | 0.072217 | 21.572 | 0.04287 |  | 5775 | 21.572 | 89.73 | 14.696 | 0.072217 | 0.04287
5776 | 89.74 | 14.696 | 0.072216 | 21.575 | 0.042874 |  | 5776 | 21.575 | 89.74 | 14.696 | 0.072216 | 0.042874
5777 | 89.75 | 14.696 | 0.072215 | 21.577 | 0.042878 |  | 5777 | 21.577 | 89.75 | 14.696 | 0.072215 | 0.042878
5778 | 89.76 | 14.696 | 0.072213 | 21.58 | 0.042883 |  | 5778 | 21.58 | 89.76 | 14.696 | 0.072213 | 0.042883
5779 | 89.77 | 14.696 | 0.072212 | 21.582 | 0.042887 |  | 5779 | 21.582 | 89.77 | 14.696 | 0.072212 | 0.042887
5780 | 89.78 | 14.696 | 0.072211 | 21.584 | 0.042891 |  | 5780 | 21.584 | 89.78 | 14.696 | 0.072211 | 0.042891
5781 | 89.79 | 14.696 | 0.072209 | 21.587 | 0.042896 |  | 5781 | 21.587 | 89.79 | 14.696 | 0.072209 | 0.042896
5782 | 89.8 | 14.696 | 0.072208 | 21.589 | 0.0429 |  | 5782 | 21.589 | 89.8 | 14.696 | 0.072208 | 0.0429
5783 | 89.81 | 14.696 | 0.072207 | 21.592 | 0.042905 |  | 5783 | 21.592 | 89.81 | 14.696 | 0.072207 | 0.042905
5784 | 89.82 | 14.696 | 0.072205 | 21.594 | 0.042909 |  | 5784 | 21.594 | 89.82 | 14.696 | 0.072205 | 0.042909
5785 | 89.83 | 14.696 | 0.072204 | 21.596 | 0.042913 |  | 5785 | 21.596 | 89.83 | 14.696 | 0.072204 | 0.042913
5786 | 89.84 | 14.696 | 0.072203 | 21.599 | 0.042918 |  | 5786 | 21.599 | 89.84 | 14.696 | 0.072203 | 0.042918
5787 | 89.85 | 14.696 | 0.072201 | 21.601 | 0.042922 |  | 5787 | 21.601 | 89.85 | 14.696 | 0.072201 | 0.042922
5788 | 89.86 | 14.696 | 0.0722 | 21.604 | 0.042926 |  | 5788 | 21.604 | 89.86 | 14.696 | 0.0722 | 0.042926
5789 | 89.87 | 14.696 | 0.072199 | 21.606 | 0.042931 |  | 5789 | 21.606 | 89.87 | 14.696 | 0.072199 | 0.042931
5790 | 89.88 | 14.696 | 0.072198 | 21.608 | 0.042935 |  | 5790 | 21.608 | 89.88 | 14.696 | 0.072198 | 0.042935
5791 | 89.89 | 14.696 | 0.072196 | 21.611 | 0.04294 |  | 5791 | 21.611 | 89.89 | 14.696 | 0.072196 | 0.04294
5792 | 89.9 | 14.696 | 0.072195 | 21.613 | 0.042944 |  | 5792 | 21.613 | 89.9 | 14.696 | 0.072195 | 0.042944
5793 | 89.91 | 14.696 | 0.072194 | 21.616 | 0.042948 |  | 5793 | 21.616 | 89.91 | 14.696 | 0.072194 | 0.042948
5794 | 89.92 | 14.696 | 0.072192 | 21.618 | 0.042953 |  | 5794 | 21.618 | 89.92 | 14.696 | 0.072192 | 0.042953
5795 | 89.93 | 14.696 | 0.072191 | 21.62 | 0.042957 |  | 5795 | 21.62 | 89.93 | 14.696 | 0.072191 | 0.042957
5796 | 89.94 | 14.696 | 0.07219 | 21.623 | 0.042961 |  | 5796 | 21.623 | 89.94 | 14.696 | 0.07219 | 0.042961
5797 | 89.95 | 14.696 | 0.072188 | 21.625 | 0.042966 |  | 5797 | 21.625 | 89.95 | 14.696 | 0.072188 | 0.042966
5798 | 89.96 | 14.696 | 0.072187 | 21.628 | 0.04297 |  | 5798 | 21.628 | 89.96 | 14.696 | 0.072187 | 0.04297
5799 | 89.97 | 14.696 | 0.072186 | 21.63 | 0.042975 |  | 5799 | 21.63 | 89.97 | 14.696 | 0.072186 | 0.042975
5800 | 89.98 | 14.696 | 0.072184 | 21.633 | 0.042979 |  | 5800 | 21.633 | 89.98 | 14.696 | 0.072184 | 0.042979
5801 | 89.99 | 14.696 | 0.072183 | 21.635 | 0.042983 |  | 5801 | 21.635 | 89.99 | 14.696 | 0.072183 | 0.042983
5802 | 90 | 14.696 | 0.072182 | 21.637 | 0.042988 |  | 5802 | 21.637 | 90 | 14.696 | 0.072182 | 0.042988
5803 | 90.01 | 14.696 | 0.07218 | 21.64 | 0.042992 |  | 5803 | 21.64 | 90.01 | 14.696 | 0.07218 | 0.042992
5804 | 90.02 | 14.696 | 0.072179 | 21.642 | 0.042996 |  | 5804 | 21.642 | 90.02 | 14.696 | 0.072179 | 0.042996
5805 | 90.03 | 14.696 | 0.072178 | 21.645 | 0.043001 |  | 5805 | 21.645 | 90.03 | 14.696 | 0.072178 | 0.043001
5806 | 90.04 | 14.696 | 0.072176 | 21.647 | 0.043005 |  | 5806 | 21.647 | 90.04 | 14.696 | 0.072176 | 0.043005
5807 | 90.05 | 14.696 | 0.072175 | 21.649 | 0.04301 |  | 5807 | 21.649 | 90.05 | 14.696 | 0.072175 | 0.04301
5808 | 90.06 | 14.696 | 0.072174 | 21.652 | 0.043014 |  | 5808 | 21.652 | 90.06 | 14.696 | 0.072174 | 0.043014
5809 | 90.07 | 14.696 | 0.072173 | 21.654 | 0.043018 |  | 5809 | 21.654 | 90.07 | 14.696 | 0.072173 | 0.043018
5810 | 90.08 | 14.696 | 0.072171 | 21.657 | 0.043023 |  | 5810 | 21.657 | 90.08 | 14.696 | 0.072171 | 0.043023
5811 | 90.09 | 14.696 | 0.07217 | 21.659 | 0.043027 |  | 5811 | 21.659 | 90.09 | 14.696 | 0.07217 | 0.043027
5812 | 90.1 | 14.696 | 0.072169 | 21.661 | 0.043032 |  | 5812 | 21.661 | 90.1 | 14.696 | 0.072169 | 0.043032
5813 | 90.11 | 14.696 | 0.072167 | 21.664 | 0.043036 |  | 5813 | 21.664 | 90.11 | 14.696 | 0.072167 | 0.043036
5814 | 90.12 | 14.696 | 0.072166 | 21.666 | 0.04304 |  | 5814 | 21.666 | 90.12 | 14.696 | 0.072166 | 0.04304
5815 | 90.13 | 14.696 | 0.072165 | 21.669 | 0.043045 |  | 5815 | 21.669 | 90.13 | 14.696 | 0.072165 | 0.043045
5816 | 90.14 | 14.696 | 0.072163 | 21.671 | 0.043049 |  | 5816 | 21.671 | 90.14 | 14.696 | 0.072163 | 0.043049
5817 | 90.15 | 14.696 | 0.072162 | 21.673 | 0.043053 |  | 5817 | 21.673 | 90.15 | 14.696 | 0.072162 | 0.043053
5818 | 90.16 | 14.696 | 0.072161 | 21.676 | 0.043058 |  | 5818 | 21.676 | 90.16 | 14.696 | 0.072161 | 0.043058
5819 | 90.17 | 14.696 | 0.072159 | 21.678 | 0.043062 |  | 5819 | 21.678 | 90.17 | 14.696 | 0.072159 | 0.043062
5820 | 90.18 | 14.696 | 0.072158 | 21.681 | 0.043067 |  | 5820 | 21.681 | 90.18 | 14.696 | 0.072158 | 0.043067
5821 | 90.19 | 14.696 | 0.072157 | 21.683 | 0.043071 |  | 5821 | 21.683 | 90.19 | 14.696 | 0.072157 | 0.043071
5822 | 90.2 | 14.696 | 0.072155 | 21.685 | 0.043075 |  | 5822 | 21.685 | 90.2 | 14.696 | 0.072155 | 0.043075
5823 | 90.21 | 14.696 | 0.072154 | 21.688 | 0.04308 |  | 5823 | 21.688 | 90.21 | 14.696 | 0.072154 | 0.04308
5824 | 90.22 | 14.696 | 0.072153 | 21.69 | 0.043084 |  | 5824 | 21.69 | 90.22 | 14.696 | 0.072153 | 0.043084
5825 | 90.23 | 14.696 | 0.072151 | 21.693 | 0.043088 |  | 5825 | 21.693 | 90.23 | 14.696 | 0.072151 | 0.043088
5826 | 90.24 | 14.696 | 0.07215 | 21.695 | 0.043093 |  | 5826 | 21.695 | 90.24 | 14.696 | 0.07215 | 0.043093
5827 | 90.25 | 14.696 | 0.072149 | 21.697 | 0.043097 |  | 5827 | 21.697 | 90.25 | 14.696 | 0.072149 | 0.043097
5828 | 90.26 | 14.696 | 0.072148 | 21.7 | 0.043102 |  | 5828 | 21.7 | 90.26 | 14.696 | 0.072148 | 0.043102
5829 | 90.27 | 14.696 | 0.072146 | 21.702 | 0.043106 |  | 5829 | 21.702 | 90.27 | 14.696 | 0.072146 | 0.043106
5830 | 90.28 | 14.696 | 0.072145 | 21.705 | 0.04311 |  | 5830 | 21.705 | 90.28 | 14.696 | 0.072145 | 0.04311
5831 | 90.29 | 14.696 | 0.072144 | 21.707 | 0.043115 |  | 5831 | 21.707 | 90.29 | 14.696 | 0.072144 | 0.043115
5832 | 90.3 | 14.696 | 0.072142 | 21.71 | 0.043119 |  | 5832 | 21.71 | 90.3 | 14.696 | 0.072142 | 0.043119
5833 | 90.31 | 14.696 | 0.072141 | 21.712 | 0.043123 |  | 5833 | 21.712 | 90.31 | 14.696 | 0.072141 | 0.043123
5834 | 90.32 | 14.696 | 0.07214 | 21.714 | 0.043128 |  | 5834 | 21.714 | 90.32 | 14.696 | 0.07214 | 0.043128
5835 | 90.33 | 14.696 | 0.072138 | 21.717 | 0.043132 |  | 5835 | 21.717 | 90.33 | 14.696 | 0.072138 | 0.043132
5836 | 90.34 | 14.696 | 0.072137 | 21.719 | 0.043137 |  | 5836 | 21.719 | 90.34 | 14.696 | 0.072137 | 0.043137
5837 | 90.35 | 14.696 | 0.072136 | 21.722 | 0.043141 |  | 5837 | 21.722 | 90.35 | 14.696 | 0.072136 | 0.043141
5838 | 90.36 | 14.696 | 0.072134 | 21.724 | 0.043145 |  | 5838 | 21.724 | 90.36 | 14.696 | 0.072134 | 0.043145
5839 | 90.37 | 14.696 | 0.072133 | 21.726 | 0.04315 |  | 5839 | 21.726 | 90.37 | 14.696 | 0.072133 | 0.04315
5840 | 90.38 | 14.696 | 0.072132 | 21.729 | 0.043154 |  | 5840 | 21.729 | 90.38 | 14.696 | 0.072132 | 0.043154
5841 | 90.39 | 14.696 | 0.07213 | 21.731 | 0.043158 |  | 5841 | 21.731 | 90.39 | 14.696 | 0.07213 | 0.043158
5842 | 90.4 | 14.696 | 0.072129 | 21.734 | 0.043163 |  | 5842 | 21.734 | 90.4 | 14.696 | 0.072129 | 0.043163
5843 | 90.41 | 14.696 | 0.072128 | 21.736 | 0.043167 |  | 5843 | 21.736 | 90.41 | 14.696 | 0.072128 | 0.043167
5844 | 90.42 | 14.696 | 0.072126 | 21.738 | 0.043172 |  | 5844 | 21.738 | 90.42 | 14.696 | 0.072126 | 0.043172
5845 | 90.43 | 14.696 | 0.072125 | 21.741 | 0.043176 |  | 5845 | 21.741 | 90.43 | 14.696 | 0.072125 | 0.043176
5846 | 90.44 | 14.696 | 0.072124 | 21.743 | 0.04318 |  | 5846 | 21.743 | 90.44 | 14.696 | 0.072124 | 0.04318
5847 | 90.45 | 14.696 | 0.072123 | 21.746 | 0.043185 |  | 5847 | 21.746 | 90.45 | 14.696 | 0.072123 | 0.043185
5848 | 90.46 | 14.696 | 0.072121 | 21.748 | 0.043189 |  | 5848 | 21.748 | 90.46 | 14.696 | 0.072121 | 0.043189
5849 | 90.47 | 14.696 | 0.07212 | 21.75 | 0.043193 |  | 5849 | 21.75 | 90.47 | 14.696 | 0.07212 | 0.043193
5850 | 90.48 | 14.696 | 0.072119 | 21.753 | 0.043198 |  | 5850 | 21.753 | 90.48 | 14.696 | 0.072119 | 0.043198
5851 | 90.49 | 14.696 | 0.072117 | 21.755 | 0.043202 |  | 5851 | 21.755 | 90.49 | 14.696 | 0.072117 | 0.043202
5852 | 90.5 | 14.696 | 0.072116 | 21.758 | 0.043206 |  | 5852 | 21.758 | 90.5 | 14.696 | 0.072116 | 0.043206
5853 | 90.51 | 14.696 | 0.072115 | 21.76 | 0.043211 |  | 5853 | 21.76 | 90.51 | 14.696 | 0.072115 | 0.043211
5854 | 90.52 | 14.696 | 0.072113 | 21.762 | 0.043215 |  | 5854 | 21.762 | 90.52 | 14.696 | 0.072113 | 0.043215
5855 | 90.53 | 14.696 | 0.072112 | 21.765 | 0.04322 |  | 5855 | 21.765 | 90.53 | 14.696 | 0.072112 | 0.04322
5856 | 90.54 | 14.696 | 0.072111 | 21.767 | 0.043224 |  | 5856 | 21.767 | 90.54 | 14.696 | 0.072111 | 0.043224
5857 | 90.55 | 14.696 | 0.072109 | 21.77 | 0.043228 |  | 5857 | 21.77 | 90.55 | 14.696 | 0.072109 | 0.043228
5858 | 90.56 | 14.696 | 0.072108 | 21.772 | 0.043233 |  | 5858 | 21.772 | 90.56 | 14.696 | 0.072108 | 0.043233
5859 | 90.57 | 14.696 | 0.072107 | 21.774 | 0.043237 |  | 5859 | 21.774 | 90.57 | 14.696 | 0.072107 | 0.043237
5860 | 90.58 | 14.696 | 0.072105 | 21.777 | 0.043241 |  | 5860 | 21.777 | 90.58 | 14.696 | 0.072105 | 0.043241
5861 | 90.59 | 14.696 | 0.072104 | 21.779 | 0.043246 |  | 5861 | 21.779 | 90.59 | 14.696 | 0.072104 | 0.043246
5862 | 90.6 | 14.696 | 0.072103 | 21.782 | 0.04325 |  | 5862 | 21.782 | 90.6 | 14.696 | 0.072103 | 0.04325
5863 | 90.61 | 14.696 | 0.072102 | 21.784 | 0.043255 |  | 5863 | 21.784 | 90.61 | 14.696 | 0.072102 | 0.043255
5864 | 90.62 | 14.696 | 0.0721 | 21.786 | 0.043259 |  | 5864 | 21.786 | 90.62 | 14.696 | 0.0721 | 0.043259
5865 | 90.63 | 14.696 | 0.072099 | 21.789 | 0.043263 |  | 5865 | 21.789 | 90.63 | 14.696 | 0.072099 | 0.043263
5866 | 90.64 | 14.696 | 0.072098 | 21.791 | 0.043268 |  | 5866 | 21.791 | 90.64 | 14.696 | 0.072098 | 0.043268
5867 | 90.65 | 14.696 | 0.072096 | 21.794 | 0.043272 |  | 5867 | 21.794 | 90.65 | 14.696 | 0.072096 | 0.043272
5868 | 90.66 | 14.696 | 0.072095 | 21.796 | 0.043276 |  | 5868 | 21.796 | 90.66 | 14.696 | 0.072095 | 0.043276
5869 | 90.67 | 14.696 | 0.072094 | 21.799 | 0.043281 |  | 5869 | 21.799 | 90.67 | 14.696 | 0.072094 | 0.043281
5870 | 90.68 | 14.696 | 0.072092 | 21.801 | 0.043285 |  | 5870 | 21.801 | 90.68 | 14.696 | 0.072092 | 0.043285
5871 | 90.69 | 14.696 | 0.072091 | 21.803 | 0.04329 |  | 5871 | 21.803 | 90.69 | 14.696 | 0.072091 | 0.04329
5872 | 90.7 | 14.696 | 0.07209 | 21.806 | 0.043294 |  | 5872 | 21.806 | 90.7 | 14.696 | 0.07209 | 0.043294
5873 | 90.71 | 14.696 | 0.072088 | 21.808 | 0.043298 |  | 5873 | 21.808 | 90.71 | 14.696 | 0.072088 | 0.043298
5874 | 90.72 | 14.696 | 0.072087 | 21.811 | 0.043303 |  | 5874 | 21.811 | 90.72 | 14.696 | 0.072087 | 0.043303
5875 | 90.73 | 14.696 | 0.072086 | 21.813 | 0.043307 |  | 5875 | 21.813 | 90.73 | 14.696 | 0.072086 | 0.043307
5876 | 90.74 | 14.696 | 0.072084 | 21.815 | 0.043311 |  | 5876 | 21.815 | 90.74 | 14.696 | 0.072084 | 0.043311
5877 | 90.75 | 14.696 | 0.072083 | 21.818 | 0.043316 |  | 5877 | 21.818 | 90.75 | 14.696 | 0.072083 | 0.043316
5878 | 90.76 | 14.696 | 0.072082 | 21.82 | 0.04332 |  | 5878 | 21.82 | 90.76 | 14.696 | 0.072082 | 0.04332
5879 | 90.77 | 14.696 | 0.07208 | 21.823 | 0.043325 |  | 5879 | 21.823 | 90.77 | 14.696 | 0.07208 | 0.043325
5880 | 90.78 | 14.696 | 0.072079 | 21.825 | 0.043329 |  | 5880 | 21.825 | 90.78 | 14.696 | 0.072079 | 0.043329
5881 | 90.79 | 14.696 | 0.072078 | 21.827 | 0.043333 |  | 5881 | 21.827 | 90.79 | 14.696 | 0.072078 | 0.043333
5882 | 90.8 | 14.696 | 0.072077 | 21.83 | 0.043338 |  | 5882 | 21.83 | 90.8 | 14.696 | 0.072077 | 0.043338
5883 | 90.81 | 14.696 | 0.072075 | 21.832 | 0.043342 |  | 5883 | 21.832 | 90.81 | 14.696 | 0.072075 | 0.043342
5884 | 90.82 | 14.696 | 0.072074 | 21.835 | 0.043346 |  | 5884 | 21.835 | 90.82 | 14.696 | 0.072074 | 0.043346
5885 | 90.83 | 14.696 | 0.072073 | 21.837 | 0.043351 |  | 5885 | 21.837 | 90.83 | 14.696 | 0.072073 | 0.043351
5886 | 90.84 | 14.696 | 0.072071 | 21.839 | 0.043355 |  | 5886 | 21.839 | 90.84 | 14.696 | 0.072071 | 0.043355
5887 | 90.85 | 14.696 | 0.07207 | 21.842 | 0.043359 |  | 5887 | 21.842 | 90.85 | 14.696 | 0.07207 | 0.043359
5888 | 90.86 | 14.696 | 0.072069 | 21.844 | 0.043364 |  | 5888 | 21.844 | 90.86 | 14.696 | 0.072069 | 0.043364
5889 | 90.87 | 14.696 | 0.072067 | 21.847 | 0.043368 |  | 5889 | 21.847 | 90.87 | 14.696 | 0.072067 | 0.043368
5890 | 90.88 | 14.696 | 0.072066 | 21.849 | 0.043373 |  | 5890 | 21.849 | 90.88 | 14.696 | 0.072066 | 0.043373
5891 | 90.89 | 14.696 | 0.072065 | 21.851 | 0.043377 |  | 5891 | 21.851 | 90.89 | 14.696 | 0.072065 | 0.043377
5892 | 90.9 | 14.696 | 0.072063 | 21.854 | 0.043381 |  | 5892 | 21.854 | 90.9 | 14.696 | 0.072063 | 0.043381
5893 | 90.91 | 14.696 | 0.072062 | 21.856 | 0.043386 |  | 5893 | 21.856 | 90.91 | 14.696 | 0.072062 | 0.043386
5894 | 90.92 | 14.696 | 0.072061 | 21.859 | 0.04339 |  | 5894 | 21.859 | 90.92 | 14.696 | 0.072061 | 0.04339
5895 | 90.93 | 14.696 | 0.072059 | 21.861 | 0.043394 |  | 5895 | 21.861 | 90.93 | 14.696 | 0.072059 | 0.043394
5896 | 90.94 | 14.696 | 0.072058 | 21.863 | 0.043399 |  | 5896 | 21.863 | 90.94 | 14.696 | 0.072058 | 0.043399
5897 | 90.95 | 14.696 | 0.072057 | 21.866 | 0.043403 |  | 5897 | 21.866 | 90.95 | 14.696 | 0.072057 | 0.043403
5898 | 90.96 | 14.696 | 0.072056 | 21.868 | 0.043408 |  | 5898 | 21.868 | 90.96 | 14.696 | 0.072056 | 0.043408
5899 | 90.97 | 14.696 | 0.072054 | 21.871 | 0.043412 |  | 5899 | 21.871 | 90.97 | 14.696 | 0.072054 | 0.043412
5900 | 90.98 | 14.696 | 0.072053 | 21.873 | 0.043416 |  | 5900 | 21.873 | 90.98 | 14.696 | 0.072053 | 0.043416
5901 | 90.99 | 14.696 | 0.072052 | 21.876 | 0.043421 |  | 5901 | 21.876 | 90.99 | 14.696 | 0.072052 | 0.043421
5902 | 91 | 14.696 | 0.07205 | 21.878 | 0.043425 |  | 5902 | 21.878 | 91 | 14.696 | 0.07205 | 0.043425
5903 | 91.01 | 14.696 | 0.072049 | 21.88 | 0.043429 |  | 5903 | 21.88 | 91.01 | 14.696 | 0.072049 | 0.043429
5904 | 91.02 | 14.696 | 0.072048 | 21.883 | 0.043434 |  | 5904 | 21.883 | 91.02 | 14.696 | 0.072048 | 0.043434
5905 | 91.03 | 14.696 | 0.072046 | 21.885 | 0.043438 |  | 5905 | 21.885 | 91.03 | 14.696 | 0.072046 | 0.043438
5906 | 91.04 | 14.696 | 0.072045 | 21.888 | 0.043443 |  | 5906 | 21.888 | 91.04 | 14.696 | 0.072045 | 0.043443
5907 | 91.05 | 14.696 | 0.072044 | 21.89 | 0.043447 |  | 5907 | 21.89 | 91.05 | 14.696 | 0.072044 | 0.043447
5908 | 91.06 | 14.696 | 0.072042 | 21.892 | 0.043451 |  | 5908 | 21.892 | 91.06 | 14.696 | 0.072042 | 0.043451
5909 | 91.07 | 14.696 | 0.072041 | 21.895 | 0.043456 |  | 5909 | 21.895 | 91.07 | 14.696 | 0.072041 | 0.043456
5910 | 91.08 | 14.696 | 0.07204 | 21.897 | 0.04346 |  | 5910 | 21.897 | 91.08 | 14.696 | 0.07204 | 0.04346
5911 | 91.09 | 14.696 | 0.072039 | 21.9 | 0.043464 |  | 5911 | 21.9 | 91.09 | 14.696 | 0.072039 | 0.043464
5912 | 91.1 | 14.696 | 0.072037 | 21.902 | 0.043469 |  | 5912 | 21.902 | 91.1 | 14.696 | 0.072037 | 0.043469
5913 | 91.11 | 14.696 | 0.072036 | 21.904 | 0.043473 |  | 5913 | 21.904 | 91.11 | 14.696 | 0.072036 | 0.043473
5914 | 91.12 | 14.696 | 0.072035 | 21.907 | 0.043477 |  | 5914 | 21.907 | 91.12 | 14.696 | 0.072035 | 0.043477
5915 | 91.13 | 14.696 | 0.072033 | 21.909 | 0.043482 |  | 5915 | 21.909 | 91.13 | 14.696 | 0.072033 | 0.043482
5916 | 91.14 | 14.696 | 0.072032 | 21.912 | 0.043486 |  | 5916 | 21.912 | 91.14 | 14.696 | 0.072032 | 0.043486
5917 | 91.15 | 14.696 | 0.072031 | 21.914 | 0.043491 |  | 5917 | 21.914 | 91.15 | 14.696 | 0.072031 | 0.043491
5918 | 91.16 | 14.696 | 0.072029 | 21.916 | 0.043495 |  | 5918 | 21.916 | 91.16 | 14.696 | 0.072029 | 0.043495
5919 | 91.17 | 14.696 | 0.072028 | 21.919 | 0.043499 |  | 5919 | 21.919 | 91.17 | 14.696 | 0.072028 | 0.043499
5920 | 91.18 | 14.696 | 0.072027 | 21.921 | 0.043504 |  | 5920 | 21.921 | 91.18 | 14.696 | 0.072027 | 0.043504
5921 | 91.19 | 14.696 | 0.072025 | 21.924 | 0.043508 |  | 5921 | 21.924 | 91.19 | 14.696 | 0.072025 | 0.043508
5922 | 91.2 | 14.696 | 0.072024 | 21.926 | 0.043512 |  | 5922 | 21.926 | 91.2 | 14.696 | 0.072024 | 0.043512
5923 | 91.21 | 14.696 | 0.072023 | 21.928 | 0.043517 |  | 5923 | 21.928 | 91.21 | 14.696 | 0.072023 | 0.043517
5924 | 91.22 | 14.696 | 0.072021 | 21.931 | 0.043521 |  | 5924 | 21.931 | 91.22 | 14.696 | 0.072021 | 0.043521
5925 | 91.23 | 14.696 | 0.07202 | 21.933 | 0.043525 |  | 5925 | 21.933 | 91.23 | 14.696 | 0.07202 | 0.043525
5926 | 91.24 | 14.696 | 0.072019 | 21.936 | 0.04353 |  | 5926 | 21.936 | 91.24 | 14.696 | 0.072019 | 0.04353
5927 | 91.25 | 14.696 | 0.072018 | 21.938 | 0.043534 |  | 5927 | 21.938 | 91.25 | 14.696 | 0.072018 | 0.043534
5928 | 91.26 | 14.696 | 0.072016 | 21.94 | 0.043539 |  | 5928 | 21.94 | 91.26 | 14.696 | 0.072016 | 0.043539
5929 | 91.27 | 14.696 | 0.072015 | 21.943 | 0.043543 |  | 5929 | 21.943 | 91.27 | 14.696 | 0.072015 | 0.043543
5930 | 91.28 | 14.696 | 0.072014 | 21.945 | 0.043547 |  | 5930 | 21.945 | 91.28 | 14.696 | 0.072014 | 0.043547
5931 | 91.29 | 14.696 | 0.072012 | 21.948 | 0.043552 |  | 5931 | 21.948 | 91.29 | 14.696 | 0.072012 | 0.043552
5932 | 91.3 | 14.696 | 0.072011 | 21.95 | 0.043556 |  | 5932 | 21.95 | 91.3 | 14.696 | 0.072011 | 0.043556
5933 | 91.31 | 14.696 | 0.07201 | 21.952 | 0.04356 |  | 5933 | 21.952 | 91.31 | 14.696 | 0.07201 | 0.04356
5934 | 91.32 | 14.696 | 0.072008 | 21.955 | 0.043565 |  | 5934 | 21.955 | 91.32 | 14.696 | 0.072008 | 0.043565
5935 | 91.33 | 14.696 | 0.072007 | 21.957 | 0.043569 |  | 5935 | 21.957 | 91.33 | 14.696 | 0.072007 | 0.043569
5936 | 91.34 | 14.696 | 0.072006 | 21.96 | 0.043574 |  | 5936 | 21.96 | 91.34 | 14.696 | 0.072006 | 0.043574
5937 | 91.35 | 14.696 | 0.072004 | 21.962 | 0.043578 |  | 5937 | 21.962 | 91.35 | 14.696 | 0.072004 | 0.043578
5938 | 91.36 | 14.696 | 0.072003 | 21.965 | 0.043582 |  | 5938 | 21.965 | 91.36 | 14.696 | 0.072003 | 0.043582
5939 | 91.37 | 14.696 | 0.072002 | 21.967 | 0.043587 |  | 5939 | 21.967 | 91.37 | 14.696 | 0.072002 | 0.043587
5940 | 91.38 | 14.696 | 0.072001 | 21.969 | 0.043591 |  | 5940 | 21.969 | 91.38 | 14.696 | 0.072001 | 0.043591
5941 | 91.39 | 14.696 | 0.071999 | 21.972 | 0.043595 |  | 5941 | 21.972 | 91.39 | 14.696 | 0.071999 | 0.043595
5942 | 91.4 | 14.696 | 0.071998 | 21.974 | 0.0436 |  | 5942 | 21.974 | 91.4 | 14.696 | 0.071998 | 0.0436
5943 | 91.41 | 14.696 | 0.071997 | 21.977 | 0.043604 |  | 5943 | 21.977 | 91.41 | 14.696 | 0.071997 | 0.043604
5944 | 91.42 | 14.696 | 0.071995 | 21.979 | 0.043608 |  | 5944 | 21.979 | 91.42 | 14.696 | 0.071995 | 0.043608
5945 | 91.43 | 14.696 | 0.071994 | 21.981 | 0.043613 |  | 5945 | 21.981 | 91.43 | 14.696 | 0.071994 | 0.043613
5946 | 91.44 | 14.696 | 0.071993 | 21.984 | 0.043617 |  | 5946 | 21.984 | 91.44 | 14.696 | 0.071993 | 0.043617
5947 | 91.45 | 14.696 | 0.071991 | 21.986 | 0.043622 |  | 5947 | 21.986 | 91.45 | 14.696 | 0.071991 | 0.043622
5948 | 91.46 | 14.696 | 0.07199 | 21.989 | 0.043626 |  | 5948 | 21.989 | 91.46 | 14.696 | 0.07199 | 0.043626
5949 | 91.47 | 14.696 | 0.071989 | 21.991 | 0.04363 |  | 5949 | 21.991 | 91.47 | 14.696 | 0.071989 | 0.04363
5950 | 91.48 | 14.696 | 0.071987 | 21.993 | 0.043635 |  | 5950 | 21.993 | 91.48 | 14.696 | 0.071987 | 0.043635
5951 | 91.49 | 14.696 | 0.071986 | 21.996 | 0.043639 |  | 5951 | 21.996 | 91.49 | 14.696 | 0.071986 | 0.043639
5952 | 91.5 | 14.696 | 0.071985 | 21.998 | 0.043643 |  | 5952 | 21.998 | 91.5 | 14.696 | 0.071985 | 0.043643
5953 | 91.51 | 14.696 | 0.071983 | 22.001 | 0.043648 |  | 5953 | 22.001 | 91.51 | 14.696 | 0.071983 | 0.043648
5954 | 91.52 | 14.696 | 0.071982 | 22.003 | 0.043652 |  | 5954 | 22.003 | 91.52 | 14.696 | 0.071982 | 0.043652
5955 | 91.53 | 14.696 | 0.071981 | 22.005 | 0.043656 |  | 5955 | 22.005 | 91.53 | 14.696 | 0.071981 | 0.043656
5956 | 91.54 | 14.696 | 0.07198 | 22.008 | 0.043661 |  | 5956 | 22.008 | 91.54 | 14.696 | 0.07198 | 0.043661
5957 | 91.55 | 14.696 | 0.071978 | 22.01 | 0.043665 |  | 5957 | 22.01 | 91.55 | 14.696 | 0.071978 | 0.043665
5958 | 91.56 | 14.696 | 0.071977 | 22.013 | 0.04367 |  | 5958 | 22.013 | 91.56 | 14.696 | 0.071977 | 0.04367
5959 | 91.57 | 14.696 | 0.071976 | 22.015 | 0.043674 |  | 5959 | 22.015 | 91.57 | 14.696 | 0.071976 | 0.043674
5960 | 91.58 | 14.696 | 0.071974 | 22.017 | 0.043678 |  | 5960 | 22.017 | 91.58 | 14.696 | 0.071974 | 0.043678
5961 | 91.59 | 14.696 | 0.071973 | 22.02 | 0.043683 |  | 5961 | 22.02 | 91.59 | 14.696 | 0.071973 | 0.043683
5962 | 91.6 | 14.696 | 0.071972 | 22.022 | 0.043687 |  | 5962 | 22.022 | 91.6 | 14.696 | 0.071972 | 0.043687
5963 | 91.61 | 14.696 | 0.07197 | 22.025 | 0.043691 |  | 5963 | 22.025 | 91.61 | 14.696 | 0.07197 | 0.043691
5964 | 91.62 | 14.696 | 0.071969 | 22.027 | 0.043696 |  | 5964 | 22.027 | 91.62 | 14.696 | 0.071969 | 0.043696
5965 | 91.63 | 14.696 | 0.071968 | 22.029 | 0.0437 |  | 5965 | 22.029 | 91.63 | 14.696 | 0.071968 | 0.0437
5966 | 91.64 | 14.696 | 0.071966 | 22.032 | 0.043704 |  | 5966 | 22.032 | 91.64 | 14.696 | 0.071966 | 0.043704
5967 | 91.65 | 14.696 | 0.071965 | 22.034 | 0.043709 |  | 5967 | 22.034 | 91.65 | 14.696 | 0.071965 | 0.043709
5968 | 91.66 | 14.696 | 0.071964 | 22.037 | 0.043713 |  | 5968 | 22.037 | 91.66 | 14.696 | 0.071964 | 0.043713
5969 | 91.67 | 14.696 | 0.071963 | 22.039 | 0.043718 |  | 5969 | 22.039 | 91.67 | 14.696 | 0.071963 | 0.043718
5970 | 91.68 | 14.696 | 0.071961 | 22.042 | 0.043722 |  | 5970 | 22.042 | 91.68 | 14.696 | 0.071961 | 0.043722
5971 | 91.69 | 14.696 | 0.07196 | 22.044 | 0.043726 |  | 5971 | 22.044 | 91.69 | 14.696 | 0.07196 | 0.043726
5972 | 91.7 | 14.696 | 0.071959 | 22.046 | 0.043731 |  | 5972 | 22.046 | 91.7 | 14.696 | 0.071959 | 0.043731
5973 | 91.71 | 14.696 | 0.071957 | 22.049 | 0.043735 |  | 5973 | 22.049 | 91.71 | 14.696 | 0.071957 | 0.043735
5974 | 91.72 | 14.696 | 0.071956 | 22.051 | 0.043739 |  | 5974 | 22.051 | 91.72 | 14.696 | 0.071956 | 0.043739
5975 | 91.73 | 14.696 | 0.071955 | 22.054 | 0.043744 |  | 5975 | 22.054 | 91.73 | 14.696 | 0.071955 | 0.043744
5976 | 91.74 | 14.696 | 0.071953 | 22.056 | 0.043748 |  | 5976 | 22.056 | 91.74 | 14.696 | 0.071953 | 0.043748
5977 | 91.75 | 14.696 | 0.071952 | 22.058 | 0.043752 |  | 5977 | 22.058 | 91.75 | 14.696 | 0.071952 | 0.043752
5978 | 91.76 | 14.696 | 0.071951 | 22.061 | 0.043757 |  | 5978 | 22.061 | 91.76 | 14.696 | 0.071951 | 0.043757
5979 | 91.77 | 14.696 | 0.071949 | 22.063 | 0.043761 |  | 5979 | 22.063 | 91.77 | 14.696 | 0.071949 | 0.043761
5980 | 91.78 | 14.696 | 0.071948 | 22.066 | 0.043766 |  | 5980 | 22.066 | 91.78 | 14.696 | 0.071948 | 0.043766
5981 | 91.79 | 14.696 | 0.071947 | 22.068 | 0.04377 |  | 5981 | 22.068 | 91.79 | 14.696 | 0.071947 | 0.04377
5982 | 91.8 | 14.696 | 0.071946 | 22.07 | 0.043774 |  | 5982 | 22.07 | 91.8 | 14.696 | 0.071946 | 0.043774
5983 | 91.81 | 14.696 | 0.071944 | 22.073 | 0.043779 |  | 5983 | 22.073 | 91.81 | 14.696 | 0.071944 | 0.043779
5984 | 91.82 | 14.696 | 0.071943 | 22.075 | 0.043783 |  | 5984 | 22.075 | 91.82 | 14.696 | 0.071943 | 0.043783
5985 | 91.83 | 14.696 | 0.071942 | 22.078 | 0.043787 |  | 5985 | 22.078 | 91.83 | 14.696 | 0.071942 | 0.043787
5986 | 91.84 | 14.696 | 0.07194 | 22.08 | 0.043792 |  | 5986 | 22.08 | 91.84 | 14.696 | 0.07194 | 0.043792
5987 | 91.85 | 14.696 | 0.071939 | 22.082 | 0.043796 |  | 5987 | 22.082 | 91.85 | 14.696 | 0.071939 | 0.043796
5988 | 91.86 | 14.696 | 0.071938 | 22.085 | 0.0438 |  | 5988 | 22.085 | 91.86 | 14.696 | 0.071938 | 0.0438
5989 | 91.87 | 14.696 | 0.071936 | 22.087 | 0.043805 |  | 5989 | 22.087 | 91.87 | 14.696 | 0.071936 | 0.043805
5990 | 91.88 | 14.696 | 0.071935 | 22.09 | 0.043809 |  | 5990 | 22.09 | 91.88 | 14.696 | 0.071935 | 0.043809
5991 | 91.89 | 14.696 | 0.071934 | 22.092 | 0.043814 |  | 5991 | 22.092 | 91.89 | 14.696 | 0.071934 | 0.043814
5992 | 91.9 | 14.696 | 0.071932 | 22.094 | 0.043818 |  | 5992 | 22.094 | 91.9 | 14.696 | 0.071932 | 0.043818
5993 | 91.91 | 14.696 | 0.071931 | 22.097 | 0.043822 |  | 5993 | 22.097 | 91.91 | 14.696 | 0.071931 | 0.043822
5994 | 91.92 | 14.696 | 0.07193 | 22.099 | 0.043827 |  | 5994 | 22.099 | 91.92 | 14.696 | 0.07193 | 0.043827
5995 | 91.93 | 14.696 | 0.071929 | 22.102 | 0.043831 |  | 5995 | 22.102 | 91.93 | 14.696 | 0.071929 | 0.043831
5996 | 91.94 | 14.696 | 0.071927 | 22.104 | 0.043835 |  | 5996 | 22.104 | 91.94 | 14.696 | 0.071927 | 0.043835
5997 | 91.95 | 14.696 | 0.071926 | 22.106 | 0.04384 |  | 5997 | 22.106 | 91.95 | 14.696 | 0.071926 | 0.04384
5998 | 91.96 | 14.696 | 0.071925 | 22.109 | 0.043844 |  | 5998 | 22.109 | 91.96 | 14.696 | 0.071925 | 0.043844
5999 | 91.97 | 14.696 | 0.071923 | 22.111 | 0.043848 |  | 5999 | 22.111 | 91.97 | 14.696 | 0.071923 | 0.043848
6000 | 91.98 | 14.696 | 0.071922 | 22.114 | 0.043853 |  | 6000 | 22.114 | 91.98 | 14.696 | 0.071922 | 0.043853
6001 | 91.99 | 14.696 | 0.071921 | 22.116 | 0.043857 |  | 6001 | 22.116 | 91.99 | 14.696 | 0.071921 | 0.043857
6002 | 92 | 14.696 | 0.071919 | 22.119 | 0.043862 |  | 6002 | 22.119 | 92 | 14.696 | 0.071919 | 0.043862
6003 | 92.01 | 14.696 | 0.071918 | 22.121 | 0.043866 |  | 6003 | 22.121 | 92.01 | 14.696 | 0.071918 | 0.043866
6004 | 92.02 | 14.696 | 0.071917 | 22.123 | 0.04387 |  | 6004 | 22.123 | 92.02 | 14.696 | 0.071917 | 0.04387
6005 | 92.03 | 14.696 | 0.071915 | 22.126 | 0.043875 |  | 6005 | 22.126 | 92.03 | 14.696 | 0.071915 | 0.043875
6006 | 92.04 | 14.696 | 0.071914 | 22.128 | 0.043879 |  | 6006 | 22.128 | 92.04 | 14.696 | 0.071914 | 0.043879
6007 | 92.05 | 14.696 | 0.071913 | 22.131 | 0.043883 |  | 6007 | 22.131 | 92.05 | 14.696 | 0.071913 | 0.043883
6008 | 92.06 | 14.696 | 0.071912 | 22.133 | 0.043888 |  | 6008 | 22.133 | 92.06 | 14.696 | 0.071912 | 0.043888
6009 | 92.07 | 14.696 | 0.07191 | 22.135 | 0.043892 |  | 6009 | 22.135 | 92.07 | 14.696 | 0.07191 | 0.043892
6010 | 92.08 | 14.696 | 0.071909 | 22.138 | 0.043896 |  | 6010 | 22.138 | 92.08 | 14.696 | 0.071909 | 0.043896
6011 | 92.09 | 14.696 | 0.071908 | 22.14 | 0.043901 |  | 6011 | 22.14 | 92.09 | 14.696 | 0.071908 | 0.043901
6012 | 92.1 | 14.696 | 0.071906 | 22.143 | 0.043905 |  | 6012 | 22.143 | 92.1 | 14.696 | 0.071906 | 0.043905
6013 | 92.11 | 14.696 | 0.071905 | 22.145 | 0.04391 |  | 6013 | 22.145 | 92.11 | 14.696 | 0.071905 | 0.04391
6014 | 92.12 | 14.696 | 0.071904 | 22.147 | 0.043914 |  | 6014 | 22.147 | 92.12 | 14.696 | 0.071904 | 0.043914
6015 | 92.13 | 14.696 | 0.071902 | 22.15 | 0.043918 |  | 6015 | 22.15 | 92.13 | 14.696 | 0.071902 | 0.043918
6016 | 92.14 | 14.696 | 0.071901 | 22.152 | 0.043923 |  | 6016 | 22.152 | 92.14 | 14.696 | 0.071901 | 0.043923
6017 | 92.15 | 14.696 | 0.0719 | 22.155 | 0.043927 |  | 6017 | 22.155 | 92.15 | 14.696 | 0.0719 | 0.043927
6018 | 92.16 | 14.696 | 0.071898 | 22.157 | 0.043931 |  | 6018 | 22.157 | 92.16 | 14.696 | 0.071898 | 0.043931
6019 | 92.17 | 14.696 | 0.071897 | 22.159 | 0.043936 |  | 6019 | 22.159 | 92.17 | 14.696 | 0.071897 | 0.043936
6020 | 92.18 | 14.696 | 0.071896 | 22.162 | 0.04394 |  | 6020 | 22.162 | 92.18 | 14.696 | 0.071896 | 0.04394
6021 | 92.19 | 14.696 | 0.071895 | 22.164 | 0.043944 |  | 6021 | 22.164 | 92.19 | 14.696 | 0.071895 | 0.043944
6022 | 92.2 | 14.696 | 0.071893 | 22.167 | 0.043949 |  | 6022 | 22.167 | 92.2 | 14.696 | 0.071893 | 0.043949
6023 | 92.21 | 14.696 | 0.071892 | 22.169 | 0.043953 |  | 6023 | 22.169 | 92.21 | 14.696 | 0.071892 | 0.043953
6024 | 92.22 | 14.696 | 0.071891 | 22.171 | 0.043957 |  | 6024 | 22.171 | 92.22 | 14.696 | 0.071891 | 0.043957
6025 | 92.23 | 14.696 | 0.071889 | 22.174 | 0.043962 |  | 6025 | 22.174 | 92.23 | 14.696 | 0.071889 | 0.043962
6026 | 92.24 | 14.696 | 0.071888 | 22.176 | 0.043966 |  | 6026 | 22.176 | 92.24 | 14.696 | 0.071888 | 0.043966
6027 | 92.25 | 14.696 | 0.071887 | 22.179 | 0.043971 |  | 6027 | 22.179 | 92.25 | 14.696 | 0.071887 | 0.043971
6028 | 92.26 | 14.696 | 0.071885 | 22.181 | 0.043975 |  | 6028 | 22.181 | 92.26 | 14.696 | 0.071885 | 0.043975
6029 | 92.27 | 14.696 | 0.071884 | 22.183 | 0.043979 |  | 6029 | 22.183 | 92.27 | 14.696 | 0.071884 | 0.043979
6030 | 92.28 | 14.696 | 0.071883 | 22.186 | 0.043984 |  | 6030 | 22.186 | 92.28 | 14.696 | 0.071883 | 0.043984
6031 | 92.29 | 14.696 | 0.071881 | 22.188 | 0.043988 |  | 6031 | 22.188 | 92.29 | 14.696 | 0.071881 | 0.043988
6032 | 92.3 | 14.696 | 0.07188 | 22.191 | 0.043992 |  | 6032 | 22.191 | 92.3 | 14.696 | 0.07188 | 0.043992
6033 | 92.31 | 14.696 | 0.071879 | 22.193 | 0.043997 |  | 6033 | 22.193 | 92.31 | 14.696 | 0.071879 | 0.043997
6034 | 92.32 | 14.696 | 0.071878 | 22.195 | 0.044001 |  | 6034 | 22.195 | 92.32 | 14.696 | 0.071878 | 0.044001
6035 | 92.33 | 14.696 | 0.071876 | 22.198 | 0.044005 |  | 6035 | 22.198 | 92.33 | 14.696 | 0.071876 | 0.044005
6036 | 92.34 | 14.696 | 0.071875 | 22.2 | 0.04401 |  | 6036 | 22.2 | 92.34 | 14.696 | 0.071875 | 0.04401
6037 | 92.35 | 14.696 | 0.071874 | 22.203 | 0.044014 |  | 6037 | 22.203 | 92.35 | 14.696 | 0.071874 | 0.044014
6038 | 92.36 | 14.696 | 0.071872 | 22.205 | 0.044018 |  | 6038 | 22.205 | 92.36 | 14.696 | 0.071872 | 0.044018
6039 | 92.37 | 14.696 | 0.071871 | 22.208 | 0.044023 |  | 6039 | 22.208 | 92.37 | 14.696 | 0.071871 | 0.044023
6040 | 92.38 | 14.696 | 0.07187 | 22.21 | 0.044027 |  | 6040 | 22.21 | 92.38 | 14.696 | 0.07187 | 0.044027
6041 | 92.39 | 14.696 | 0.071868 | 22.212 | 0.044032 |  | 6041 | 22.212 | 92.39 | 14.696 | 0.071868 | 0.044032
6042 | 92.4 | 14.696 | 0.071867 | 22.215 | 0.044036 |  | 6042 | 22.215 | 92.4 | 14.696 | 0.071867 | 0.044036
6043 | 92.41 | 14.696 | 0.071866 | 22.217 | 0.04404 |  | 6043 | 22.217 | 92.41 | 14.696 | 0.071866 | 0.04404
6044 | 92.42 | 14.696 | 0.071865 | 22.22 | 0.044045 |  | 6044 | 22.22 | 92.42 | 14.696 | 0.071865 | 0.044045
6045 | 92.43 | 14.696 | 0.071863 | 22.222 | 0.044049 |  | 6045 | 22.222 | 92.43 | 14.696 | 0.071863 | 0.044049
6046 | 92.44 | 14.696 | 0.071862 | 22.224 | 0.044053 |  | 6046 | 22.224 | 92.44 | 14.696 | 0.071862 | 0.044053
6047 | 92.45 | 14.696 | 0.071861 | 22.227 | 0.044058 |  | 6047 | 22.227 | 92.45 | 14.696 | 0.071861 | 0.044058
6048 | 92.46 | 14.696 | 0.071859 | 22.229 | 0.044062 |  | 6048 | 22.229 | 92.46 | 14.696 | 0.071859 | 0.044062
6049 | 92.47 | 14.696 | 0.071858 | 22.232 | 0.044066 |  | 6049 | 22.232 | 92.47 | 14.696 | 0.071858 | 0.044066
6050 | 92.48 | 14.696 | 0.071857 | 22.234 | 0.044071 |  | 6050 | 22.234 | 92.48 | 14.696 | 0.071857 | 0.044071
6051 | 92.49 | 14.696 | 0.071855 | 22.236 | 0.044075 |  | 6051 | 22.236 | 92.49 | 14.696 | 0.071855 | 0.044075
6052 | 92.5 | 14.696 | 0.071854 | 22.239 | 0.044079 |  | 6052 | 22.239 | 92.5 | 14.696 | 0.071854 | 0.044079
6053 | 92.51 | 14.696 | 0.071853 | 22.241 | 0.044084 |  | 6053 | 22.241 | 92.51 | 14.696 | 0.071853 | 0.044084
6054 | 92.52 | 14.696 | 0.071851 | 22.244 | 0.044088 |  | 6054 | 22.244 | 92.52 | 14.696 | 0.071851 | 0.044088
6055 | 92.53 | 14.696 | 0.07185 | 22.246 | 0.044093 |  | 6055 | 22.246 | 92.53 | 14.696 | 0.07185 | 0.044093
6056 | 92.54 | 14.696 | 0.071849 | 22.248 | 0.044097 |  | 6056 | 22.248 | 92.54 | 14.696 | 0.071849 | 0.044097
6057 | 92.55 | 14.696 | 0.071848 | 22.251 | 0.044101 |  | 6057 | 22.251 | 92.55 | 14.696 | 0.071848 | 0.044101
6058 | 92.56 | 14.696 | 0.071846 | 22.253 | 0.044106 |  | 6058 | 22.253 | 92.56 | 14.696 | 0.071846 | 0.044106
6059 | 92.57 | 14.696 | 0.071845 | 22.256 | 0.04411 |  | 6059 | 22.256 | 92.57 | 14.696 | 0.071845 | 0.04411
6060 | 92.58 | 14.696 | 0.071844 | 22.258 | 0.044114 |  | 6060 | 22.258 | 92.58 | 14.696 | 0.071844 | 0.044114
6061 | 92.59 | 14.696 | 0.071842 | 22.26 | 0.044119 |  | 6061 | 22.26 | 92.59 | 14.696 | 0.071842 | 0.044119
6062 | 92.6 | 14.696 | 0.071841 | 22.263 | 0.044123 |  | 6062 | 22.263 | 92.6 | 14.696 | 0.071841 | 0.044123
6063 | 92.61 | 14.696 | 0.07184 | 22.265 | 0.044127 |  | 6063 | 22.265 | 92.61 | 14.696 | 0.07184 | 0.044127
6064 | 92.62 | 14.696 | 0.071838 | 22.268 | 0.044132 |  | 6064 | 22.268 | 92.62 | 14.696 | 0.071838 | 0.044132
6065 | 92.63 | 14.696 | 0.071837 | 22.27 | 0.044136 |  | 6065 | 22.27 | 92.63 | 14.696 | 0.071837 | 0.044136
6066 | 92.64 | 14.696 | 0.071836 | 22.272 | 0.04414 |  | 6066 | 22.272 | 92.64 | 14.696 | 0.071836 | 0.04414
6067 | 92.65 | 14.696 | 0.071835 | 22.275 | 0.044145 |  | 6067 | 22.275 | 92.65 | 14.696 | 0.071835 | 0.044145
6068 | 92.66 | 14.696 | 0.071833 | 22.277 | 0.044149 |  | 6068 | 22.277 | 92.66 | 14.696 | 0.071833 | 0.044149
6069 | 92.67 | 14.696 | 0.071832 | 22.28 | 0.044154 |  | 6069 | 22.28 | 92.67 | 14.696 | 0.071832 | 0.044154
6070 | 92.68 | 14.696 | 0.071831 | 22.282 | 0.044158 |  | 6070 | 22.282 | 92.68 | 14.696 | 0.071831 | 0.044158
6071 | 92.69 | 14.696 | 0.071829 | 22.285 | 0.044162 |  | 6071 | 22.285 | 92.69 | 14.696 | 0.071829 | 0.044162
6072 | 92.7 | 14.696 | 0.071828 | 22.287 | 0.044167 |  | 6072 | 22.287 | 92.7 | 14.696 | 0.071828 | 0.044167
6073 | 92.71 | 14.696 | 0.071827 | 22.289 | 0.044171 |  | 6073 | 22.289 | 92.71 | 14.696 | 0.071827 | 0.044171
6074 | 92.72 | 14.696 | 0.071825 | 22.292 | 0.044175 |  | 6074 | 22.292 | 92.72 | 14.696 | 0.071825 | 0.044175
6075 | 92.73 | 14.696 | 0.071824 | 22.294 | 0.04418 |  | 6075 | 22.294 | 92.73 | 14.696 | 0.071824 | 0.04418
6076 | 92.74 | 14.696 | 0.071823 | 22.297 | 0.044184 |  | 6076 | 22.297 | 92.74 | 14.696 | 0.071823 | 0.044184
6077 | 92.75 | 14.696 | 0.071821 | 22.299 | 0.044188 |  | 6077 | 22.299 | 92.75 | 14.696 | 0.071821 | 0.044188
6078 | 92.76 | 14.696 | 0.07182 | 22.301 | 0.044193 |  | 6078 | 22.301 | 92.76 | 14.696 | 0.07182 | 0.044193
6079 | 92.77 | 14.696 | 0.071819 | 22.304 | 0.044197 |  | 6079 | 22.304 | 92.77 | 14.696 | 0.071819 | 0.044197
6080 | 92.78 | 14.696 | 0.071818 | 22.306 | 0.044201 |  | 6080 | 22.306 | 92.78 | 14.696 | 0.071818 | 0.044201
6081 | 92.79 | 14.696 | 0.071816 | 22.309 | 0.044206 |  | 6081 | 22.309 | 92.79 | 14.696 | 0.071816 | 0.044206
6082 | 92.8 | 14.696 | 0.071815 | 22.311 | 0.04421 |  | 6082 | 22.311 | 92.8 | 14.696 | 0.071815 | 0.04421
6083 | 92.81 | 14.696 | 0.071814 | 22.313 | 0.044215 |  | 6083 | 22.313 | 92.81 | 14.696 | 0.071814 | 0.044215
6084 | 92.82 | 14.696 | 0.071812 | 22.316 | 0.044219 |  | 6084 | 22.316 | 92.82 | 14.696 | 0.071812 | 0.044219
6085 | 92.83 | 14.696 | 0.071811 | 22.318 | 0.044223 |  | 6085 | 22.318 | 92.83 | 14.696 | 0.071811 | 0.044223
6086 | 92.84 | 14.696 | 0.07181 | 22.321 | 0.044228 |  | 6086 | 22.321 | 92.84 | 14.696 | 0.07181 | 0.044228
6087 | 92.85 | 14.696 | 0.071808 | 22.323 | 0.044232 |  | 6087 | 22.323 | 92.85 | 14.696 | 0.071808 | 0.044232
6088 | 92.86 | 14.696 | 0.071807 | 22.325 | 0.044236 |  | 6088 | 22.325 | 92.86 | 14.696 | 0.071807 | 0.044236
6089 | 92.87 | 14.696 | 0.071806 | 22.328 | 0.044241 |  | 6089 | 22.328 | 92.87 | 14.696 | 0.071806 | 0.044241
6090 | 92.88 | 14.696 | 0.071805 | 22.33 | 0.044245 |  | 6090 | 22.33 | 92.88 | 14.696 | 0.071805 | 0.044245
6091 | 92.89 | 14.696 | 0.071803 | 22.333 | 0.044249 |  | 6091 | 22.333 | 92.89 | 14.696 | 0.071803 | 0.044249
6092 | 92.9 | 14.696 | 0.071802 | 22.335 | 0.044254 |  | 6092 | 22.335 | 92.9 | 14.696 | 0.071802 | 0.044254
6093 | 92.91 | 14.696 | 0.071801 | 22.337 | 0.044258 |  | 6093 | 22.337 | 92.91 | 14.696 | 0.071801 | 0.044258
6094 | 92.92 | 14.696 | 0.071799 | 22.34 | 0.044262 |  | 6094 | 22.34 | 92.92 | 14.696 | 0.071799 | 0.044262
6095 | 92.93 | 14.696 | 0.071798 | 22.342 | 0.044267 |  | 6095 | 22.342 | 92.93 | 14.696 | 0.071798 | 0.044267
6096 | 92.94 | 14.696 | 0.071797 | 22.345 | 0.044271 |  | 6096 | 22.345 | 92.94 | 14.696 | 0.071797 | 0.044271
6097 | 92.95 | 14.696 | 0.071795 | 22.347 | 0.044275 |  | 6097 | 22.347 | 92.95 | 14.696 | 0.071795 | 0.044275
6098 | 92.96 | 14.696 | 0.071794 | 22.349 | 0.04428 |  | 6098 | 22.349 | 92.96 | 14.696 | 0.071794 | 0.04428
6099 | 92.97 | 14.696 | 0.071793 | 22.352 | 0.044284 |  | 6099 | 22.352 | 92.97 | 14.696 | 0.071793 | 0.044284
6100 | 92.98 | 14.696 | 0.071792 | 22.354 | 0.044289 |  | 6100 | 22.354 | 92.98 | 14.696 | 0.071792 | 0.044289
6101 | 92.99 | 14.696 | 0.07179 | 22.357 | 0.044293 |  | 6101 | 22.357 | 92.99 | 14.696 | 0.07179 | 0.044293
6102 | 93 | 14.696 | 0.071789 | 22.359 | 0.044297 |  | 6102 | 22.359 | 93 | 14.696 | 0.071789 | 0.044297
6103 | 93.01 | 14.696 | 0.071788 | 22.362 | 0.044302 |  | 6103 | 22.362 | 93.01 | 14.696 | 0.071788 | 0.044302
6104 | 93.02 | 14.696 | 0.071786 | 22.364 | 0.044306 |  | 6104 | 22.364 | 93.02 | 14.696 | 0.071786 | 0.044306
6105 | 93.03 | 14.696 | 0.071785 | 22.366 | 0.04431 |  | 6105 | 22.366 | 93.03 | 14.696 | 0.071785 | 0.04431
6106 | 93.04 | 14.696 | 0.071784 | 22.369 | 0.044315 |  | 6106 | 22.369 | 93.04 | 14.696 | 0.071784 | 0.044315
6107 | 93.05 | 14.696 | 0.071782 | 22.371 | 0.044319 |  | 6107 | 22.371 | 93.05 | 14.696 | 0.071782 | 0.044319
6108 | 93.06 | 14.696 | 0.071781 | 22.374 | 0.044323 |  | 6108 | 22.374 | 93.06 | 14.696 | 0.071781 | 0.044323
6109 | 93.07 | 14.696 | 0.07178 | 22.376 | 0.044328 |  | 6109 | 22.376 | 93.07 | 14.696 | 0.07178 | 0.044328
6110 | 93.08 | 14.696 | 0.071779 | 22.378 | 0.044332 |  | 6110 | 22.378 | 93.08 | 14.696 | 0.071779 | 0.044332
6111 | 93.09 | 14.696 | 0.071777 | 22.381 | 0.044336 |  | 6111 | 22.381 | 93.09 | 14.696 | 0.071777 | 0.044336
6112 | 93.1 | 14.696 | 0.071776 | 22.383 | 0.044341 |  | 6112 | 22.383 | 93.1 | 14.696 | 0.071776 | 0.044341
6113 | 93.11 | 14.696 | 0.071775 | 22.386 | 0.044345 |  | 6113 | 22.386 | 93.11 | 14.696 | 0.071775 | 0.044345
6114 | 93.12 | 14.696 | 0.071773 | 22.388 | 0.044349 |  | 6114 | 22.388 | 93.12 | 14.696 | 0.071773 | 0.044349
6115 | 93.13 | 14.696 | 0.071772 | 22.39 | 0.044354 |  | 6115 | 22.39 | 93.13 | 14.696 | 0.071772 | 0.044354
6116 | 93.14 | 14.696 | 0.071771 | 22.393 | 0.044358 |  | 6116 | 22.393 | 93.14 | 14.696 | 0.071771 | 0.044358
6117 | 93.15 | 14.696 | 0.071769 | 22.395 | 0.044363 |  | 6117 | 22.395 | 93.15 | 14.696 | 0.071769 | 0.044363
6118 | 93.16 | 14.696 | 0.071768 | 22.398 | 0.044367 |  | 6118 | 22.398 | 93.16 | 14.696 | 0.071768 | 0.044367
6119 | 93.17 | 14.696 | 0.071767 | 22.4 | 0.044371 |  | 6119 | 22.4 | 93.17 | 14.696 | 0.071767 | 0.044371
6120 | 93.18 | 14.696 | 0.071765 | 22.402 | 0.044376 |  | 6120 | 22.402 | 93.18 | 14.696 | 0.071765 | 0.044376
6121 | 93.19 | 14.696 | 0.071764 | 22.405 | 0.04438 |  | 6121 | 22.405 | 93.19 | 14.696 | 0.071764 | 0.04438
6122 | 93.2 | 14.696 | 0.071763 | 22.407 | 0.044384 |  | 6122 | 22.407 | 93.2 | 14.696 | 0.071763 | 0.044384
6123 | 93.21 | 14.696 | 0.071762 | 22.41 | 0.044389 |  | 6123 | 22.41 | 93.21 | 14.696 | 0.071762 | 0.044389
6124 | 93.22 | 14.696 | 0.07176 | 22.412 | 0.044393 |  | 6124 | 22.412 | 93.22 | 14.696 | 0.07176 | 0.044393
6125 | 93.23 | 14.696 | 0.071759 | 22.414 | 0.044397 |  | 6125 | 22.414 | 93.23 | 14.696 | 0.071759 | 0.044397
6126 | 93.24 | 14.696 | 0.071758 | 22.417 | 0.044402 |  | 6126 | 22.417 | 93.24 | 14.696 | 0.071758 | 0.044402
6127 | 93.25 | 14.696 | 0.071756 | 22.419 | 0.044406 |  | 6127 | 22.419 | 93.25 | 14.696 | 0.071756 | 0.044406
6128 | 93.26 | 14.696 | 0.071755 | 22.422 | 0.04441 |  | 6128 | 22.422 | 93.26 | 14.696 | 0.071755 | 0.04441
6129 | 93.27 | 14.696 | 0.071754 | 22.424 | 0.044415 |  | 6129 | 22.424 | 93.27 | 14.696 | 0.071754 | 0.044415
6130 | 93.28 | 14.696 | 0.071752 | 22.426 | 0.044419 |  | 6130 | 22.426 | 93.28 | 14.696 | 0.071752 | 0.044419
6131 | 93.29 | 14.696 | 0.071751 | 22.429 | 0.044423 |  | 6131 | 22.429 | 93.29 | 14.696 | 0.071751 | 0.044423
6132 | 93.3 | 14.696 | 0.07175 | 22.431 | 0.044428 |  | 6132 | 22.431 | 93.3 | 14.696 | 0.07175 | 0.044428
6133 | 93.31 | 14.696 | 0.071749 | 22.434 | 0.044432 |  | 6133 | 22.434 | 93.31 | 14.696 | 0.071749 | 0.044432
6134 | 93.32 | 14.696 | 0.071747 | 22.436 | 0.044437 |  | 6134 | 22.436 | 93.32 | 14.696 | 0.071747 | 0.044437
6135 | 93.33 | 14.696 | 0.071746 | 22.438 | 0.044441 |  | 6135 | 22.438 | 93.33 | 14.696 | 0.071746 | 0.044441
6136 | 93.34 | 14.696 | 0.071745 | 22.441 | 0.044445 |  | 6136 | 22.441 | 93.34 | 14.696 | 0.071745 | 0.044445
6137 | 93.35 | 14.696 | 0.071743 | 22.443 | 0.04445 |  | 6137 | 22.443 | 93.35 | 14.696 | 0.071743 | 0.04445
6138 | 93.36 | 14.696 | 0.071742 | 22.446 | 0.044454 |  | 6138 | 22.446 | 93.36 | 14.696 | 0.071742 | 0.044454
6139 | 93.37 | 14.696 | 0.071741 | 22.448 | 0.044458 |  | 6139 | 22.448 | 93.37 | 14.696 | 0.071741 | 0.044458
6140 | 93.38 | 14.696 | 0.071739 | 22.451 | 0.044463 |  | 6140 | 22.451 | 93.38 | 14.696 | 0.071739 | 0.044463
6141 | 93.39 | 14.696 | 0.071738 | 22.453 | 0.044467 |  | 6141 | 22.453 | 93.39 | 14.696 | 0.071738 | 0.044467
6142 | 93.4 | 14.696 | 0.071737 | 22.455 | 0.044471 |  | 6142 | 22.455 | 93.4 | 14.696 | 0.071737 | 0.044471
6143 | 93.41 | 14.696 | 0.071736 | 22.458 | 0.044476 |  | 6143 | 22.458 | 93.41 | 14.696 | 0.071736 | 0.044476
6144 | 93.42 | 14.696 | 0.071734 | 22.46 | 0.04448 |  | 6144 | 22.46 | 93.42 | 14.696 | 0.071734 | 0.04448
6145 | 93.43 | 14.696 | 0.071733 | 22.463 | 0.044484 |  | 6145 | 22.463 | 93.43 | 14.696 | 0.071733 | 0.044484
6146 | 93.44 | 14.696 | 0.071732 | 22.465 | 0.044489 |  | 6146 | 22.465 | 93.44 | 14.696 | 0.071732 | 0.044489
6147 | 93.45 | 14.696 | 0.07173 | 22.467 | 0.044493 |  | 6147 | 22.467 | 93.45 | 14.696 | 0.07173 | 0.044493
6148 | 93.46 | 14.696 | 0.071729 | 22.47 | 0.044497 |  | 6148 | 22.47 | 93.46 | 14.696 | 0.071729 | 0.044497
6149 | 93.47 | 14.696 | 0.071728 | 22.472 | 0.044502 |  | 6149 | 22.472 | 93.47 | 14.696 | 0.071728 | 0.044502
6150 | 93.48 | 14.696 | 0.071726 | 22.475 | 0.044506 |  | 6150 | 22.475 | 93.48 | 14.696 | 0.071726 | 0.044506
6151 | 93.49 | 14.696 | 0.071725 | 22.477 | 0.04451 |  | 6151 | 22.477 | 93.49 | 14.696 | 0.071725 | 0.04451
6152 | 93.5 | 14.696 | 0.071724 | 22.479 | 0.044515 |  | 6152 | 22.479 | 93.5 | 14.696 | 0.071724 | 0.044515
6153 | 93.51 | 14.696 | 0.071723 | 22.482 | 0.044519 |  | 6153 | 22.482 | 93.51 | 14.696 | 0.071723 | 0.044519
6154 | 93.52 | 14.696 | 0.071721 | 22.484 | 0.044524 |  | 6154 | 22.484 | 93.52 | 14.696 | 0.071721 | 0.044524
6155 | 93.53 | 14.696 | 0.07172 | 22.487 | 0.044528 |  | 6155 | 22.487 | 93.53 | 14.696 | 0.07172 | 0.044528
6156 | 93.54 | 14.696 | 0.071719 | 22.489 | 0.044532 |  | 6156 | 22.489 | 93.54 | 14.696 | 0.071719 | 0.044532
6157 | 93.55 | 14.696 | 0.071717 | 22.491 | 0.044537 |  | 6157 | 22.491 | 93.55 | 14.696 | 0.071717 | 0.044537
6158 | 93.56 | 14.696 | 0.071716 | 22.494 | 0.044541 |  | 6158 | 22.494 | 93.56 | 14.696 | 0.071716 | 0.044541
6159 | 93.57 | 14.696 | 0.071715 | 22.496 | 0.044545 |  | 6159 | 22.496 | 93.57 | 14.696 | 0.071715 | 0.044545
6160 | 93.58 | 14.696 | 0.071713 | 22.499 | 0.04455 |  | 6160 | 22.499 | 93.58 | 14.696 | 0.071713 | 0.04455
6161 | 93.59 | 14.696 | 0.071712 | 22.501 | 0.044554 |  | 6161 | 22.501 | 93.59 | 14.696 | 0.071712 | 0.044554
6162 | 93.6 | 14.696 | 0.071711 | 22.503 | 0.044558 |  | 6162 | 22.503 | 93.6 | 14.696 | 0.071711 | 0.044558
6163 | 93.61 | 14.696 | 0.07171 | 22.506 | 0.044563 |  | 6163 | 22.506 | 93.61 | 14.696 | 0.07171 | 0.044563
6164 | 93.62 | 14.696 | 0.071708 | 22.508 | 0.044567 |  | 6164 | 22.508 | 93.62 | 14.696 | 0.071708 | 0.044567
6165 | 93.63 | 14.696 | 0.071707 | 22.511 | 0.044571 |  | 6165 | 22.511 | 93.63 | 14.696 | 0.071707 | 0.044571
6166 | 93.64 | 14.696 | 0.071706 | 22.513 | 0.044576 |  | 6166 | 22.513 | 93.64 | 14.696 | 0.071706 | 0.044576
6167 | 93.65 | 14.696 | 0.071704 | 22.515 | 0.04458 |  | 6167 | 22.515 | 93.65 | 14.696 | 0.071704 | 0.04458
6168 | 93.66 | 14.696 | 0.071703 | 22.518 | 0.044584 |  | 6168 | 22.518 | 93.66 | 14.696 | 0.071703 | 0.044584
6169 | 93.67 | 14.696 | 0.071702 | 22.52 | 0.044589 |  | 6169 | 22.52 | 93.67 | 14.696 | 0.071702 | 0.044589
6170 | 93.68 | 14.696 | 0.0717 | 22.523 | 0.044593 |  | 6170 | 22.523 | 93.68 | 14.696 | 0.0717 | 0.044593
6171 | 93.69 | 14.696 | 0.071699 | 22.525 | 0.044597 |  | 6171 | 22.525 | 93.69 | 14.696 | 0.071699 | 0.044597
6172 | 93.7 | 14.696 | 0.071698 | 22.528 | 0.044602 |  | 6172 | 22.528 | 93.7 | 14.696 | 0.071698 | 0.044602
6173 | 93.71 | 14.696 | 0.071697 | 22.53 | 0.044606 |  | 6173 | 22.53 | 93.71 | 14.696 | 0.071697 | 0.044606
6174 | 93.72 | 14.696 | 0.071695 | 22.532 | 0.04461 |  | 6174 | 22.532 | 93.72 | 14.696 | 0.071695 | 0.04461
6175 | 93.73 | 14.696 | 0.071694 | 22.535 | 0.044615 |  | 6175 | 22.535 | 93.73 | 14.696 | 0.071694 | 0.044615
6176 | 93.74 | 14.696 | 0.071693 | 22.537 | 0.044619 |  | 6176 | 22.537 | 93.74 | 14.696 | 0.071693 | 0.044619
6177 | 93.75 | 14.696 | 0.071691 | 22.54 | 0.044624 |  | 6177 | 22.54 | 93.75 | 14.696 | 0.071691 | 0.044624
6178 | 93.76 | 14.696 | 0.07169 | 22.542 | 0.044628 |  | 6178 | 22.542 | 93.76 | 14.696 | 0.07169 | 0.044628
6179 | 93.77 | 14.696 | 0.071689 | 22.544 | 0.044632 |  | 6179 | 22.544 | 93.77 | 14.696 | 0.071689 | 0.044632
6180 | 93.78 | 14.696 | 0.071688 | 22.547 | 0.044637 |  | 6180 | 22.547 | 93.78 | 14.696 | 0.071688 | 0.044637
6181 | 93.79 | 14.696 | 0.071686 | 22.549 | 0.044641 |  | 6181 | 22.549 | 93.79 | 14.696 | 0.071686 | 0.044641
6182 | 93.8 | 14.696 | 0.071685 | 22.552 | 0.044645 |  | 6182 | 22.552 | 93.8 | 14.696 | 0.071685 | 0.044645
6183 | 93.81 | 14.696 | 0.071684 | 22.554 | 0.04465 |  | 6183 | 22.554 | 93.81 | 14.696 | 0.071684 | 0.04465
6184 | 93.82 | 14.696 | 0.071682 | 22.556 | 0.044654 |  | 6184 | 22.556 | 93.82 | 14.696 | 0.071682 | 0.044654
6185 | 93.83 | 14.696 | 0.071681 | 22.559 | 0.044658 |  | 6185 | 22.559 | 93.83 | 14.696 | 0.071681 | 0.044658
6186 | 93.84 | 14.696 | 0.07168 | 22.561 | 0.044663 |  | 6186 | 22.561 | 93.84 | 14.696 | 0.07168 | 0.044663
6187 | 93.85 | 14.696 | 0.071678 | 22.564 | 0.044667 |  | 6187 | 22.564 | 93.85 | 14.696 | 0.071678 | 0.044667
6188 | 93.86 | 14.696 | 0.071677 | 22.566 | 0.044671 |  | 6188 | 22.566 | 93.86 | 14.696 | 0.071677 | 0.044671
6189 | 93.87 | 14.696 | 0.071676 | 22.568 | 0.044676 |  | 6189 | 22.568 | 93.87 | 14.696 | 0.071676 | 0.044676
6190 | 93.88 | 14.696 | 0.071675 | 22.571 | 0.04468 |  | 6190 | 22.571 | 93.88 | 14.696 | 0.071675 | 0.04468
6191 | 93.89 | 14.696 | 0.071673 | 22.573 | 0.044684 |  | 6191 | 22.573 | 93.89 | 14.696 | 0.071673 | 0.044684
6192 | 93.9 | 14.696 | 0.071672 | 22.576 | 0.044689 |  | 6192 | 22.576 | 93.9 | 14.696 | 0.071672 | 0.044689
6193 | 93.91 | 14.696 | 0.071671 | 22.578 | 0.044693 |  | 6193 | 22.578 | 93.91 | 14.696 | 0.071671 | 0.044693
6194 | 93.92 | 14.696 | 0.071669 | 22.58 | 0.044697 |  | 6194 | 22.58 | 93.92 | 14.696 | 0.071669 | 0.044697
6195 | 93.93 | 14.696 | 0.071668 | 22.583 | 0.044702 |  | 6195 | 22.583 | 93.93 | 14.696 | 0.071668 | 0.044702
6196 | 93.94 | 14.696 | 0.071667 | 22.585 | 0.044706 |  | 6196 | 22.585 | 93.94 | 14.696 | 0.071667 | 0.044706
6197 | 93.95 | 14.696 | 0.071665 | 22.588 | 0.04471 |  | 6197 | 22.588 | 93.95 | 14.696 | 0.071665 | 0.04471
6198 | 93.96 | 14.696 | 0.071664 | 22.59 | 0.044715 |  | 6198 | 22.59 | 93.96 | 14.696 | 0.071664 | 0.044715
6199 | 93.97 | 14.696 | 0.071663 | 22.592 | 0.044719 |  | 6199 | 22.592 | 93.97 | 14.696 | 0.071663 | 0.044719
6200 | 93.98 | 14.696 | 0.071662 | 22.595 | 0.044724 |  | 6200 | 22.595 | 93.98 | 14.696 | 0.071662 | 0.044724
6201 | 93.99 | 14.696 | 0.07166 | 22.597 | 0.044728 |  | 6201 | 22.597 | 93.99 | 14.696 | 0.07166 | 0.044728
6202 | 94 | 14.696 | 0.071659 | 22.6 | 0.044732 |  | 6202 | 22.6 | 94 | 14.696 | 0.071659 | 0.044732
6203 | 94.01 | 14.696 | 0.071658 | 22.602 | 0.044737 |  | 6203 | 22.602 | 94.01 | 14.696 | 0.071658 | 0.044737
6204 | 94.02 | 14.696 | 0.071656 | 22.605 | 0.044741 |  | 6204 | 22.605 | 94.02 | 14.696 | 0.071656 | 0.044741
6205 | 94.03 | 14.696 | 0.071655 | 22.607 | 0.044745 |  | 6205 | 22.607 | 94.03 | 14.696 | 0.071655 | 0.044745
6206 | 94.04 | 14.696 | 0.071654 | 22.609 | 0.04475 |  | 6206 | 22.609 | 94.04 | 14.696 | 0.071654 | 0.04475
6207 | 94.05 | 14.696 | 0.071652 | 22.612 | 0.044754 |  | 6207 | 22.612 | 94.05 | 14.696 | 0.071652 | 0.044754
6208 | 94.06 | 14.696 | 0.071651 | 22.614 | 0.044758 |  | 6208 | 22.614 | 94.06 | 14.696 | 0.071651 | 0.044758
6209 | 94.07 | 14.696 | 0.07165 | 22.617 | 0.044763 |  | 6209 | 22.617 | 94.07 | 14.696 | 0.07165 | 0.044763
6210 | 94.08 | 14.696 | 0.071649 | 22.619 | 0.044767 |  | 6210 | 22.619 | 94.08 | 14.696 | 0.071649 | 0.044767
6211 | 94.09 | 14.696 | 0.071647 | 22.621 | 0.044771 |  | 6211 | 22.621 | 94.09 | 14.696 | 0.071647 | 0.044771
6212 | 94.1 | 14.696 | 0.071646 | 22.624 | 0.044776 |  | 6212 | 22.624 | 94.1 | 14.696 | 0.071646 | 0.044776
6213 | 94.11 | 14.696 | 0.071645 | 22.626 | 0.04478 |  | 6213 | 22.626 | 94.11 | 14.696 | 0.071645 | 0.04478
6214 | 94.12 | 14.696 | 0.071643 | 22.629 | 0.044784 |  | 6214 | 22.629 | 94.12 | 14.696 | 0.071643 | 0.044784
6215 | 94.13 | 14.696 | 0.071642 | 22.631 | 0.044789 |  | 6215 | 22.631 | 94.13 | 14.696 | 0.071642 | 0.044789
6216 | 94.14 | 14.696 | 0.071641 | 22.633 | 0.044793 |  | 6216 | 22.633 | 94.14 | 14.696 | 0.071641 | 0.044793
6217 | 94.15 | 14.696 | 0.071639 | 22.636 | 0.044797 |  | 6217 | 22.636 | 94.15 | 14.696 | 0.071639 | 0.044797
6218 | 94.16 | 14.696 | 0.071638 | 22.638 | 0.044802 |  | 6218 | 22.638 | 94.16 | 14.696 | 0.071638 | 0.044802
6219 | 94.17 | 14.696 | 0.071637 | 22.641 | 0.044806 |  | 6219 | 22.641 | 94.17 | 14.696 | 0.071637 | 0.044806
6220 | 94.18 | 14.696 | 0.071636 | 22.643 | 0.04481 |  | 6220 | 22.643 | 94.18 | 14.696 | 0.071636 | 0.04481
6221 | 94.19 | 14.696 | 0.071634 | 22.645 | 0.044815 |  | 6221 | 22.645 | 94.19 | 14.696 | 0.071634 | 0.044815
6222 | 94.2 | 14.696 | 0.071633 | 22.648 | 0.044819 |  | 6222 | 22.648 | 94.2 | 14.696 | 0.071633 | 0.044819
6223 | 94.21 | 14.696 | 0.071632 | 22.65 | 0.044823 |  | 6223 | 22.65 | 94.21 | 14.696 | 0.071632 | 0.044823
6224 | 94.22 | 14.696 | 0.07163 | 22.653 | 0.044828 |  | 6224 | 22.653 | 94.22 | 14.696 | 0.07163 | 0.044828
6225 | 94.23 | 14.696 | 0.071629 | 22.655 | 0.044832 |  | 6225 | 22.655 | 94.23 | 14.696 | 0.071629 | 0.044832
6226 | 94.24 | 14.696 | 0.071628 | 22.657 | 0.044836 |  | 6226 | 22.657 | 94.24 | 14.696 | 0.071628 | 0.044836
6227 | 94.25 | 14.696 | 0.071627 | 22.66 | 0.044841 |  | 6227 | 22.66 | 94.25 | 14.696 | 0.071627 | 0.044841
6228 | 94.26 | 14.696 | 0.071625 | 22.662 | 0.044845 |  | 6228 | 22.662 | 94.26 | 14.696 | 0.071625 | 0.044845
6229 | 94.27 | 14.696 | 0.071624 | 22.665 | 0.044849 |  | 6229 | 22.665 | 94.27 | 14.696 | 0.071624 | 0.044849
6230 | 94.28 | 14.696 | 0.071623 | 22.667 | 0.044854 |  | 6230 | 22.667 | 94.28 | 14.696 | 0.071623 | 0.044854
6231 | 94.29 | 14.696 | 0.071621 | 22.669 | 0.044858 |  | 6231 | 22.669 | 94.29 | 14.696 | 0.071621 | 0.044858
6232 | 94.3 | 14.696 | 0.07162 | 22.672 | 0.044863 |  | 6232 | 22.672 | 94.3 | 14.696 | 0.07162 | 0.044863
6233 | 94.31 | 14.696 | 0.071619 | 22.674 | 0.044867 |  | 6233 | 22.674 | 94.31 | 14.696 | 0.071619 | 0.044867
6234 | 94.32 | 14.696 | 0.071617 | 22.677 | 0.044871 |  | 6234 | 22.677 | 94.32 | 14.696 | 0.071617 | 0.044871
6235 | 94.33 | 14.696 | 0.071616 | 22.679 | 0.044876 |  | 6235 | 22.679 | 94.33 | 14.696 | 0.071616 | 0.044876
6236 | 94.34 | 14.696 | 0.071615 | 22.681 | 0.04488 |  | 6236 | 22.681 | 94.34 | 14.696 | 0.071615 | 0.04488
6237 | 94.35 | 14.696 | 0.071614 | 22.684 | 0.044884 |  | 6237 | 22.684 | 94.35 | 14.696 | 0.071614 | 0.044884
6238 | 94.36 | 14.696 | 0.071612 | 22.686 | 0.044889 |  | 6238 | 22.686 | 94.36 | 14.696 | 0.071612 | 0.044889
6239 | 94.37 | 14.696 | 0.071611 | 22.689 | 0.044893 |  | 6239 | 22.689 | 94.37 | 14.696 | 0.071611 | 0.044893
6240 | 94.38 | 14.696 | 0.07161 | 22.691 | 0.044897 |  | 6240 | 22.691 | 94.38 | 14.696 | 0.07161 | 0.044897
6241 | 94.39 | 14.696 | 0.071608 | 22.694 | 0.044902 |  | 6241 | 22.694 | 94.39 | 14.696 | 0.071608 | 0.044902
6242 | 94.4 | 14.696 | 0.071607 | 22.696 | 0.044906 |  | 6242 | 22.696 | 94.4 | 14.696 | 0.071607 | 0.044906
6243 | 94.41 | 14.696 | 0.071606 | 22.698 | 0.04491 |  | 6243 | 22.698 | 94.41 | 14.696 | 0.071606 | 0.04491
6244 | 94.42 | 14.696 | 0.071604 | 22.701 | 0.044915 |  | 6244 | 22.701 | 94.42 | 14.696 | 0.071604 | 0.044915
6245 | 94.43 | 14.696 | 0.071603 | 22.703 | 0.044919 |  | 6245 | 22.703 | 94.43 | 14.696 | 0.071603 | 0.044919
6246 | 94.44 | 14.696 | 0.071602 | 22.706 | 0.044923 |  | 6246 | 22.706 | 94.44 | 14.696 | 0.071602 | 0.044923
6247 | 94.45 | 14.696 | 0.071601 | 22.708 | 0.044928 |  | 6247 | 22.708 | 94.45 | 14.696 | 0.071601 | 0.044928
6248 | 94.46 | 14.696 | 0.071599 | 22.71 | 0.044932 |  | 6248 | 22.71 | 94.46 | 14.696 | 0.071599 | 0.044932
6249 | 94.47 | 14.696 | 0.071598 | 22.713 | 0.044936 |  | 6249 | 22.713 | 94.47 | 14.696 | 0.071598 | 0.044936
6250 | 94.48 | 14.696 | 0.071597 | 22.715 | 0.044941 |  | 6250 | 22.715 | 94.48 | 14.696 | 0.071597 | 0.044941
6251 | 94.49 | 14.696 | 0.071595 | 22.718 | 0.044945 |  | 6251 | 22.718 | 94.49 | 14.696 | 0.071595 | 0.044945
6252 | 94.5 | 14.696 | 0.071594 | 22.72 | 0.044949 |  | 6252 | 22.72 | 94.5 | 14.696 | 0.071594 | 0.044949
6253 | 94.51 | 14.696 | 0.071593 | 22.722 | 0.044954 |  | 6253 | 22.722 | 94.51 | 14.696 | 0.071593 | 0.044954
6254 | 94.52 | 14.696 | 0.071592 | 22.725 | 0.044958 |  | 6254 | 22.725 | 94.52 | 14.696 | 0.071592 | 0.044958
6255 | 94.53 | 14.696 | 0.07159 | 22.727 | 0.044962 |  | 6255 | 22.727 | 94.53 | 14.696 | 0.07159 | 0.044962
6256 | 94.54 | 14.696 | 0.071589 | 22.73 | 0.044967 |  | 6256 | 22.73 | 94.54 | 14.696 | 0.071589 | 0.044967
6257 | 94.55 | 14.696 | 0.071588 | 22.732 | 0.044971 |  | 6257 | 22.732 | 94.55 | 14.696 | 0.071588 | 0.044971
6258 | 94.56 | 14.696 | 0.071586 | 22.734 | 0.044975 |  | 6258 | 22.734 | 94.56 | 14.696 | 0.071586 | 0.044975
6259 | 94.57 | 14.696 | 0.071585 | 22.737 | 0.04498 |  | 6259 | 22.737 | 94.57 | 14.696 | 0.071585 | 0.04498
6260 | 94.58 | 14.696 | 0.071584 | 22.739 | 0.044984 |  | 6260 | 22.739 | 94.58 | 14.696 | 0.071584 | 0.044984
6261 | 94.59 | 14.696 | 0.071582 | 22.742 | 0.044988 |  | 6261 | 22.742 | 94.59 | 14.696 | 0.071582 | 0.044988
6262 | 94.6 | 14.696 | 0.071581 | 22.744 | 0.044993 |  | 6262 | 22.744 | 94.6 | 14.696 | 0.071581 | 0.044993
6263 | 94.61 | 14.696 | 0.07158 | 22.746 | 0.044997 |  | 6263 | 22.746 | 94.61 | 14.696 | 0.07158 | 0.044997
6264 | 94.62 | 14.696 | 0.071579 | 22.749 | 0.045001 |  | 6264 | 22.749 | 94.62 | 14.696 | 0.071579 | 0.045001
6265 | 94.63 | 14.696 | 0.071577 | 22.751 | 0.045006 |  | 6265 | 22.751 | 94.63 | 14.696 | 0.071577 | 0.045006
6266 | 94.64 | 14.696 | 0.071576 | 22.754 | 0.04501 |  | 6266 | 22.754 | 94.64 | 14.696 | 0.071576 | 0.04501
6267 | 94.65 | 14.696 | 0.071575 | 22.756 | 0.045014 |  | 6267 | 22.756 | 94.65 | 14.696 | 0.071575 | 0.045014
6268 | 94.66 | 14.696 | 0.071573 | 22.758 | 0.045019 |  | 6268 | 22.758 | 94.66 | 14.696 | 0.071573 | 0.045019
6269 | 94.67 | 14.696 | 0.071572 | 22.761 | 0.045023 |  | 6269 | 22.761 | 94.67 | 14.696 | 0.071572 | 0.045023
6270 | 94.68 | 14.696 | 0.071571 | 22.763 | 0.045028 |  | 6270 | 22.763 | 94.68 | 14.696 | 0.071571 | 0.045028
6271 | 94.69 | 14.696 | 0.07157 | 22.766 | 0.045032 |  | 6271 | 22.766 | 94.69 | 14.696 | 0.07157 | 0.045032
6272 | 94.7 | 14.696 | 0.071568 | 22.768 | 0.045036 |  | 6272 | 22.768 | 94.7 | 14.696 | 0.071568 | 0.045036
6273 | 94.71 | 14.696 | 0.071567 | 22.771 | 0.045041 |  | 6273 | 22.771 | 94.71 | 14.696 | 0.071567 | 0.045041
6274 | 94.72 | 14.696 | 0.071566 | 22.773 | 0.045045 |  | 6274 | 22.773 | 94.72 | 14.696 | 0.071566 | 0.045045
6275 | 94.73 | 14.696 | 0.071564 | 22.775 | 0.045049 |  | 6275 | 22.775 | 94.73 | 14.696 | 0.071564 | 0.045049
6276 | 94.74 | 14.696 | 0.071563 | 22.778 | 0.045054 |  | 6276 | 22.778 | 94.74 | 14.696 | 0.071563 | 0.045054
6277 | 94.75 | 14.696 | 0.071562 | 22.78 | 0.045058 |  | 6277 | 22.78 | 94.75 | 14.696 | 0.071562 | 0.045058
6278 | 94.76 | 14.696 | 0.07156 | 22.783 | 0.045062 |  | 6278 | 22.783 | 94.76 | 14.696 | 0.07156 | 0.045062
6279 | 94.77 | 14.696 | 0.071559 | 22.785 | 0.045067 |  | 6279 | 22.785 | 94.77 | 14.696 | 0.071559 | 0.045067
6280 | 94.78 | 14.696 | 0.071558 | 22.787 | 0.045071 |  | 6280 | 22.787 | 94.78 | 14.696 | 0.071558 | 0.045071
6281 | 94.79 | 14.696 | 0.071557 | 22.79 | 0.045075 |  | 6281 | 22.79 | 94.79 | 14.696 | 0.071557 | 0.045075
6282 | 94.8 | 14.696 | 0.071555 | 22.792 | 0.04508 |  | 6282 | 22.792 | 94.8 | 14.696 | 0.071555 | 0.04508
6283 | 94.81 | 14.696 | 0.071554 | 22.795 | 0.045084 |  | 6283 | 22.795 | 94.81 | 14.696 | 0.071554 | 0.045084
6284 | 94.82 | 14.696 | 0.071553 | 22.797 | 0.045088 |  | 6284 | 22.797 | 94.82 | 14.696 | 0.071553 | 0.045088
6285 | 94.83 | 14.696 | 0.071551 | 22.799 | 0.045093 |  | 6285 | 22.799 | 94.83 | 14.696 | 0.071551 | 0.045093
6286 | 94.84 | 14.696 | 0.07155 | 22.802 | 0.045097 |  | 6286 | 22.802 | 94.84 | 14.696 | 0.07155 | 0.045097
6287 | 94.85 | 14.696 | 0.071549 | 22.804 | 0.045101 |  | 6287 | 22.804 | 94.85 | 14.696 | 0.071549 | 0.045101
6288 | 94.86 | 14.696 | 0.071548 | 22.807 | 0.045106 |  | 6288 | 22.807 | 94.86 | 14.696 | 0.071548 | 0.045106
6289 | 94.87 | 14.696 | 0.071546 | 22.809 | 0.04511 |  | 6289 | 22.809 | 94.87 | 14.696 | 0.071546 | 0.04511
6290 | 94.88 | 14.696 | 0.071545 | 22.811 | 0.045114 |  | 6290 | 22.811 | 94.88 | 14.696 | 0.071545 | 0.045114
6291 | 94.89 | 14.696 | 0.071544 | 22.814 | 0.045119 |  | 6291 | 22.814 | 94.89 | 14.696 | 0.071544 | 0.045119
6292 | 94.9 | 14.696 | 0.071542 | 22.816 | 0.045123 |  | 6292 | 22.816 | 94.9 | 14.696 | 0.071542 | 0.045123
6293 | 94.91 | 14.696 | 0.071541 | 22.819 | 0.045127 |  | 6293 | 22.819 | 94.91 | 14.696 | 0.071541 | 0.045127
6294 | 94.92 | 14.696 | 0.07154 | 22.821 | 0.045132 |  | 6294 | 22.821 | 94.92 | 14.696 | 0.07154 | 0.045132
6295 | 94.93 | 14.696 | 0.071538 | 22.823 | 0.045136 |  | 6295 | 22.823 | 94.93 | 14.696 | 0.071538 | 0.045136
6296 | 94.94 | 14.696 | 0.071537 | 22.826 | 0.04514 |  | 6296 | 22.826 | 94.94 | 14.696 | 0.071537 | 0.04514
6297 | 94.95 | 14.696 | 0.071536 | 22.828 | 0.045145 |  | 6297 | 22.828 | 94.95 | 14.696 | 0.071536 | 0.045145
6298 | 94.96 | 14.696 | 0.071535 | 22.831 | 0.045149 |  | 6298 | 22.831 | 94.96 | 14.696 | 0.071535 | 0.045149
6299 | 94.97 | 14.696 | 0.071533 | 22.833 | 0.045153 |  | 6299 | 22.833 | 94.97 | 14.696 | 0.071533 | 0.045153
6300 | 94.98 | 14.696 | 0.071532 | 22.835 | 0.045158 |  | 6300 | 22.835 | 94.98 | 14.696 | 0.071532 | 0.045158
6301 | 94.99 | 14.696 | 0.071531 | 22.838 | 0.045162 |  | 6301 | 22.838 | 94.99 | 14.696 | 0.071531 | 0.045162
6302 | 95 | 14.696 | 0.071529 | 22.84 | 0.045166 |  | 6302 | 22.84 | 95 | 14.696 | 0.071529 | 0.045166
6303 | 95.01 | 14.696 | 0.071528 | 22.843 | 0.045171 |  | 6303 | 22.843 | 95.01 | 14.696 | 0.071528 | 0.045171
6304 | 95.02 | 14.696 | 0.071527 | 22.845 | 0.045175 |  | 6304 | 22.845 | 95.02 | 14.696 | 0.071527 | 0.045175
6305 | 95.03 | 14.696 | 0.071526 | 22.848 | 0.045179 |  | 6305 | 22.848 | 95.03 | 14.696 | 0.071526 | 0.045179
6306 | 95.04 | 14.696 | 0.071524 | 22.85 | 0.045184 |  | 6306 | 22.85 | 95.04 | 14.696 | 0.071524 | 0.045184
6307 | 95.05 | 14.696 | 0.071523 | 22.852 | 0.045188 |  | 6307 | 22.852 | 95.05 | 14.696 | 0.071523 | 0.045188
6308 | 95.06 | 14.696 | 0.071522 | 22.855 | 0.045192 |  | 6308 | 22.855 | 95.06 | 14.696 | 0.071522 | 0.045192
6309 | 95.07 | 14.696 | 0.07152 | 22.857 | 0.045197 |  | 6309 | 22.857 | 95.07 | 14.696 | 0.07152 | 0.045197
6310 | 95.08 | 14.696 | 0.071519 | 22.86 | 0.045201 |  | 6310 | 22.86 | 95.08 | 14.696 | 0.071519 | 0.045201
6311 | 95.09 | 14.696 | 0.071518 | 22.862 | 0.045205 |  | 6311 | 22.862 | 95.09 | 14.696 | 0.071518 | 0.045205
6312 | 95.1 | 14.696 | 0.071517 | 22.864 | 0.04521 |  | 6312 | 22.864 | 95.1 | 14.696 | 0.071517 | 0.04521
6313 | 95.11 | 14.696 | 0.071515 | 22.867 | 0.045214 |  | 6313 | 22.867 | 95.11 | 14.696 | 0.071515 | 0.045214
6314 | 95.12 | 14.696 | 0.071514 | 22.869 | 0.045218 |  | 6314 | 22.869 | 95.12 | 14.696 | 0.071514 | 0.045218
6315 | 95.13 | 14.696 | 0.071513 | 22.872 | 0.045223 |  | 6315 | 22.872 | 95.13 | 14.696 | 0.071513 | 0.045223
6316 | 95.14 | 14.696 | 0.071511 | 22.874 | 0.045227 |  | 6316 | 22.874 | 95.14 | 14.696 | 0.071511 | 0.045227
6317 | 95.15 | 14.696 | 0.07151 | 22.876 | 0.045231 |  | 6317 | 22.876 | 95.15 | 14.696 | 0.07151 | 0.045231
6318 | 95.16 | 14.696 | 0.071509 | 22.879 | 0.045236 |  | 6318 | 22.879 | 95.16 | 14.696 | 0.071509 | 0.045236
6319 | 95.17 | 14.696 | 0.071507 | 22.881 | 0.04524 |  | 6319 | 22.881 | 95.17 | 14.696 | 0.071507 | 0.04524
6320 | 95.18 | 14.696 | 0.071506 | 22.884 | 0.045244 |  | 6320 | 22.884 | 95.18 | 14.696 | 0.071506 | 0.045244
6321 | 95.19 | 14.696 | 0.071505 | 22.886 | 0.045249 |  | 6321 | 22.886 | 95.19 | 14.696 | 0.071505 | 0.045249
6322 | 95.2 | 14.696 | 0.071504 | 22.888 | 0.045253 |  | 6322 | 22.888 | 95.2 | 14.696 | 0.071504 | 0.045253
6323 | 95.21 | 14.696 | 0.071502 | 22.891 | 0.045257 |  | 6323 | 22.891 | 95.21 | 14.696 | 0.071502 | 0.045257
6324 | 95.22 | 14.696 | 0.071501 | 22.893 | 0.045262 |  | 6324 | 22.893 | 95.22 | 14.696 | 0.071501 | 0.045262
6325 | 95.23 | 14.696 | 0.0715 | 22.896 | 0.045266 |  | 6325 | 22.896 | 95.23 | 14.696 | 0.0715 | 0.045266
6326 | 95.24 | 14.696 | 0.071498 | 22.898 | 0.04527 |  | 6326 | 22.898 | 95.24 | 14.696 | 0.071498 | 0.04527
6327 | 95.25 | 14.696 | 0.071497 | 22.9 | 0.045275 |  | 6327 | 22.9 | 95.25 | 14.696 | 0.071497 | 0.045275
6328 | 95.26 | 14.696 | 0.071496 | 22.903 | 0.045279 |  | 6328 | 22.903 | 95.26 | 14.696 | 0.071496 | 0.045279
6329 | 95.27 | 14.696 | 0.071495 | 22.905 | 0.045283 |  | 6329 | 22.905 | 95.27 | 14.696 | 0.071495 | 0.045283
6330 | 95.28 | 14.696 | 0.071493 | 22.908 | 0.045288 |  | 6330 | 22.908 | 95.28 | 14.696 | 0.071493 | 0.045288
6331 | 95.29 | 14.696 | 0.071492 | 22.91 | 0.045292 |  | 6331 | 22.91 | 95.29 | 14.696 | 0.071492 | 0.045292
6332 | 95.3 | 14.696 | 0.071491 | 22.912 | 0.045296 |  | 6332 | 22.912 | 95.3 | 14.696 | 0.071491 | 0.045296
6333 | 95.31 | 14.696 | 0.071489 | 22.915 | 0.045301 |  | 6333 | 22.915 | 95.31 | 14.696 | 0.071489 | 0.045301
6334 | 95.32 | 14.696 | 0.071488 | 22.917 | 0.045305 |  | 6334 | 22.917 | 95.32 | 14.696 | 0.071488 | 0.045305
6335 | 95.33 | 14.696 | 0.071487 | 22.92 | 0.045309 |  | 6335 | 22.92 | 95.33 | 14.696 | 0.071487 | 0.045309
6336 | 95.34 | 14.696 | 0.071486 | 22.922 | 0.045314 |  | 6336 | 22.922 | 95.34 | 14.696 | 0.071486 | 0.045314
6337 | 95.35 | 14.696 | 0.071484 | 22.925 | 0.045318 |  | 6337 | 22.925 | 95.35 | 14.696 | 0.071484 | 0.045318
6338 | 95.36 | 14.696 | 0.071483 | 22.927 | 0.045322 |  | 6338 | 22.927 | 95.36 | 14.696 | 0.071483 | 0.045322
6339 | 95.37 | 14.696 | 0.071482 | 22.929 | 0.045327 |  | 6339 | 22.929 | 95.37 | 14.696 | 0.071482 | 0.045327
6340 | 95.38 | 14.696 | 0.07148 | 22.932 | 0.045331 |  | 6340 | 22.932 | 95.38 | 14.696 | 0.07148 | 0.045331
6341 | 95.39 | 14.696 | 0.071479 | 22.934 | 0.045335 |  | 6341 | 22.934 | 95.39 | 14.696 | 0.071479 | 0.045335
6342 | 95.4 | 14.696 | 0.071478 | 22.937 | 0.04534 |  | 6342 | 22.937 | 95.4 | 14.696 | 0.071478 | 0.04534
6343 | 95.41 | 14.696 | 0.071476 | 22.939 | 0.045344 |  | 6343 | 22.939 | 95.41 | 14.696 | 0.071476 | 0.045344
6344 | 95.42 | 14.696 | 0.071475 | 22.941 | 0.045348 |  | 6344 | 22.941 | 95.42 | 14.696 | 0.071475 | 0.045348
6345 | 95.43 | 14.696 | 0.071474 | 22.944 | 0.045353 |  | 6345 | 22.944 | 95.43 | 14.696 | 0.071474 | 0.045353
6346 | 95.44 | 14.696 | 0.071473 | 22.946 | 0.045357 |  | 6346 | 22.946 | 95.44 | 14.696 | 0.071473 | 0.045357
6347 | 95.45 | 14.696 | 0.071471 | 22.949 | 0.045361 |  | 6347 | 22.949 | 95.45 | 14.696 | 0.071471 | 0.045361
6348 | 95.46 | 14.696 | 0.07147 | 22.951 | 0.045366 |  | 6348 | 22.951 | 95.46 | 14.696 | 0.07147 | 0.045366
6349 | 95.47 | 14.696 | 0.071469 | 22.953 | 0.04537 |  | 6349 | 22.953 | 95.47 | 14.696 | 0.071469 | 0.04537
6350 | 95.48 | 14.696 | 0.071467 | 22.956 | 0.045374 |  | 6350 | 22.956 | 95.48 | 14.696 | 0.071467 | 0.045374
6351 | 95.49 | 14.696 | 0.071466 | 22.958 | 0.045379 |  | 6351 | 22.958 | 95.49 | 14.696 | 0.071466 | 0.045379
6352 | 95.5 | 14.696 | 0.071465 | 22.961 | 0.045383 |  | 6352 | 22.961 | 95.5 | 14.696 | 0.071465 | 0.045383
6353 | 95.51 | 14.696 | 0.071464 | 22.963 | 0.045387 |  | 6353 | 22.963 | 95.51 | 14.696 | 0.071464 | 0.045387
6354 | 95.52 | 14.696 | 0.071462 | 22.965 | 0.045392 |  | 6354 | 22.965 | 95.52 | 14.696 | 0.071462 | 0.045392
6355 | 95.53 | 14.696 | 0.071461 | 22.968 | 0.045396 |  | 6355 | 22.968 | 95.53 | 14.696 | 0.071461 | 0.045396
6356 | 95.54 | 14.696 | 0.07146 | 22.97 | 0.0454 |  | 6356 | 22.97 | 95.54 | 14.696 | 0.07146 | 0.0454
6357 | 95.55 | 14.696 | 0.071458 | 22.973 | 0.045405 |  | 6357 | 22.973 | 95.55 | 14.696 | 0.071458 | 0.045405
6358 | 95.56 | 14.696 | 0.071457 | 22.975 | 0.045409 |  | 6358 | 22.975 | 95.56 | 14.696 | 0.071457 | 0.045409
6359 | 95.57 | 14.696 | 0.071456 | 22.977 | 0.045413 |  | 6359 | 22.977 | 95.57 | 14.696 | 0.071456 | 0.045413
6360 | 95.58 | 14.696 | 0.071455 | 22.98 | 0.045418 |  | 6360 | 22.98 | 95.58 | 14.696 | 0.071455 | 0.045418
6361 | 95.59 | 14.696 | 0.071453 | 22.982 | 0.045422 |  | 6361 | 22.982 | 95.59 | 14.696 | 0.071453 | 0.045422
6362 | 95.6 | 14.696 | 0.071452 | 22.985 | 0.045426 |  | 6362 | 22.985 | 95.6 | 14.696 | 0.071452 | 0.045426
6363 | 95.61 | 14.696 | 0.071451 | 22.987 | 0.045431 |  | 6363 | 22.987 | 95.61 | 14.696 | 0.071451 | 0.045431
6364 | 95.62 | 14.696 | 0.071449 | 22.989 | 0.045435 |  | 6364 | 22.989 | 95.62 | 14.696 | 0.071449 | 0.045435
6365 | 95.63 | 14.696 | 0.071448 | 22.992 | 0.045439 |  | 6365 | 22.992 | 95.63 | 14.696 | 0.071448 | 0.045439
6366 | 95.64 | 14.696 | 0.071447 | 22.994 | 0.045444 |  | 6366 | 22.994 | 95.64 | 14.696 | 0.071447 | 0.045444
6367 | 95.65 | 14.696 | 0.071446 | 22.997 | 0.045448 |  | 6367 | 22.997 | 95.65 | 14.696 | 0.071446 | 0.045448
6368 | 95.66 | 14.696 | 0.071444 | 22.999 | 0.045452 |  | 6368 | 22.999 | 95.66 | 14.696 | 0.071444 | 0.045452
6369 | 95.67 | 14.696 | 0.071443 | 23.002 | 0.045457 |  | 6369 | 23.002 | 95.67 | 14.696 | 0.071443 | 0.045457
6370 | 95.68 | 14.696 | 0.071442 | 23.004 | 0.045461 |  | 6370 | 23.004 | 95.68 | 14.696 | 0.071442 | 0.045461
6371 | 95.69 | 14.696 | 0.07144 | 23.006 | 0.045465 |  | 6371 | 23.006 | 95.69 | 14.696 | 0.07144 | 0.045465
6372 | 95.7 | 14.696 | 0.071439 | 23.009 | 0.04547 |  | 6372 | 23.009 | 95.7 | 14.696 | 0.071439 | 0.04547
6373 | 95.71 | 14.696 | 0.071438 | 23.011 | 0.045474 |  | 6373 | 23.011 | 95.71 | 14.696 | 0.071438 | 0.045474
6374 | 95.72 | 14.696 | 0.071436 | 23.014 | 0.045478 |  | 6374 | 23.014 | 95.72 | 14.696 | 0.071436 | 0.045478
6375 | 95.73 | 14.696 | 0.071435 | 23.016 | 0.045483 |  | 6375 | 23.016 | 95.73 | 14.696 | 0.071435 | 0.045483
6376 | 95.74 | 14.696 | 0.071434 | 23.018 | 0.045487 |  | 6376 | 23.018 | 95.74 | 14.696 | 0.071434 | 0.045487
6377 | 95.75 | 14.696 | 0.071433 | 23.021 | 0.045491 |  | 6377 | 23.021 | 95.75 | 14.696 | 0.071433 | 0.045491
6378 | 95.76 | 14.696 | 0.071431 | 23.023 | 0.045496 |  | 6378 | 23.023 | 95.76 | 14.696 | 0.071431 | 0.045496
6379 | 95.77 | 14.696 | 0.07143 | 23.026 | 0.0455 |  | 6379 | 23.026 | 95.77 | 14.696 | 0.07143 | 0.0455
6380 | 95.78 | 14.696 | 0.071429 | 23.028 | 0.045504 |  | 6380 | 23.028 | 95.78 | 14.696 | 0.071429 | 0.045504
6381 | 95.79 | 14.696 | 0.071427 | 23.03 | 0.045509 |  | 6381 | 23.03 | 95.79 | 14.696 | 0.071427 | 0.045509
6382 | 95.8 | 14.696 | 0.071426 | 23.033 | 0.045513 |  | 6382 | 23.033 | 95.8 | 14.696 | 0.071426 | 0.045513
6383 | 95.81 | 14.696 | 0.071425 | 23.035 | 0.045517 |  | 6383 | 23.035 | 95.81 | 14.696 | 0.071425 | 0.045517
6384 | 95.82 | 14.696 | 0.071424 | 23.038 | 0.045522 |  | 6384 | 23.038 | 95.82 | 14.696 | 0.071424 | 0.045522
6385 | 95.83 | 14.696 | 0.071422 | 23.04 | 0.045526 |  | 6385 | 23.04 | 95.83 | 14.696 | 0.071422 | 0.045526
6386 | 95.84 | 14.696 | 0.071421 | 23.042 | 0.04553 |  | 6386 | 23.042 | 95.84 | 14.696 | 0.071421 | 0.04553
6387 | 95.85 | 14.696 | 0.07142 | 23.045 | 0.045535 |  | 6387 | 23.045 | 95.85 | 14.696 | 0.07142 | 0.045535
6388 | 95.86 | 14.696 | 0.071418 | 23.047 | 0.045539 |  | 6388 | 23.047 | 95.86 | 14.696 | 0.071418 | 0.045539
6389 | 95.87 | 14.696 | 0.071417 | 23.05 | 0.045543 |  | 6389 | 23.05 | 95.87 | 14.696 | 0.071417 | 0.045543
6390 | 95.88 | 14.696 | 0.071416 | 23.052 | 0.045548 |  | 6390 | 23.052 | 95.88 | 14.696 | 0.071416 | 0.045548
6391 | 95.89 | 14.696 | 0.071415 | 23.054 | 0.045552 |  | 6391 | 23.054 | 95.89 | 14.696 | 0.071415 | 0.045552
6392 | 95.9 | 14.696 | 0.071413 | 23.057 | 0.045556 |  | 6392 | 23.057 | 95.9 | 14.696 | 0.071413 | 0.045556
6393 | 95.91 | 14.696 | 0.071412 | 23.059 | 0.045561 |  | 6393 | 23.059 | 95.91 | 14.696 | 0.071412 | 0.045561
6394 | 95.92 | 14.696 | 0.071411 | 23.062 | 0.045565 |  | 6394 | 23.062 | 95.92 | 14.696 | 0.071411 | 0.045565
6395 | 95.93 | 14.696 | 0.071409 | 23.064 | 0.045569 |  | 6395 | 23.064 | 95.93 | 14.696 | 0.071409 | 0.045569
6396 | 95.94 | 14.696 | 0.071408 | 23.066 | 0.045574 |  | 6396 | 23.066 | 95.94 | 14.696 | 0.071408 | 0.045574
6397 | 95.95 | 14.696 | 0.071407 | 23.069 | 0.045578 |  | 6397 | 23.069 | 95.95 | 14.696 | 0.071407 | 0.045578
6398 | 95.96 | 14.696 | 0.071406 | 23.071 | 0.045582 |  | 6398 | 23.071 | 95.96 | 14.696 | 0.071406 | 0.045582
6399 | 95.97 | 14.696 | 0.071404 | 23.074 | 0.045587 |  | 6399 | 23.074 | 95.97 | 14.696 | 0.071404 | 0.045587
6400 | 95.98 | 14.696 | 0.071403 | 23.076 | 0.045591 |  | 6400 | 23.076 | 95.98 | 14.696 | 0.071403 | 0.045591
6401 | 95.99 | 14.696 | 0.071402 | 23.079 | 0.045595 |  | 6401 | 23.079 | 95.99 | 14.696 | 0.071402 | 0.045595
6402 | 96 | 14.696 | 0.0714 | 23.081 | 0.0456 |  | 6402 | 23.081 | 96 | 14.696 | 0.0714 | 0.0456
6403 | 96.01 | 14.696 | 0.071399 | 23.083 | 0.045604 |  | 6403 | 23.083 | 96.01 | 14.696 | 0.071399 | 0.045604
6404 | 96.02 | 14.696 | 0.071398 | 23.086 | 0.045608 |  | 6404 | 23.086 | 96.02 | 14.696 | 0.071398 | 0.045608
6405 | 96.03 | 14.696 | 0.071397 | 23.088 | 0.045613 |  | 6405 | 23.088 | 96.03 | 14.696 | 0.071397 | 0.045613
6406 | 96.04 | 14.696 | 0.071395 | 23.091 | 0.045617 |  | 6406 | 23.091 | 96.04 | 14.696 | 0.071395 | 0.045617
6407 | 96.05 | 14.696 | 0.071394 | 23.093 | 0.045621 |  | 6407 | 23.093 | 96.05 | 14.696 | 0.071394 | 0.045621
6408 | 96.06 | 14.696 | 0.071393 | 23.095 | 0.045626 |  | 6408 | 23.095 | 96.06 | 14.696 | 0.071393 | 0.045626
6409 | 96.07 | 14.696 | 0.071391 | 23.098 | 0.04563 |  | 6409 | 23.098 | 96.07 | 14.696 | 0.071391 | 0.04563
6410 | 96.08 | 14.696 | 0.07139 | 23.1 | 0.045634 |  | 6410 | 23.1 | 96.08 | 14.696 | 0.07139 | 0.045634
6411 | 96.09 | 14.696 | 0.071389 | 23.103 | 0.045639 |  | 6411 | 23.103 | 96.09 | 14.696 | 0.071389 | 0.045639
6412 | 96.1 | 14.696 | 0.071388 | 23.105 | 0.045643 |  | 6412 | 23.105 | 96.1 | 14.696 | 0.071388 | 0.045643
6413 | 96.11 | 14.696 | 0.071386 | 23.107 | 0.045647 |  | 6413 | 23.107 | 96.11 | 14.696 | 0.071386 | 0.045647
6414 | 96.12 | 14.696 | 0.071385 | 23.11 | 0.045652 |  | 6414 | 23.11 | 96.12 | 14.696 | 0.071385 | 0.045652
6415 | 96.13 | 14.696 | 0.071384 | 23.112 | 0.045656 |  | 6415 | 23.112 | 96.13 | 14.696 | 0.071384 | 0.045656
6416 | 96.14 | 14.696 | 0.071382 | 23.115 | 0.04566 |  | 6416 | 23.115 | 96.14 | 14.696 | 0.071382 | 0.04566
6417 | 96.15 | 14.696 | 0.071381 | 23.117 | 0.045665 |  | 6417 | 23.117 | 96.15 | 14.696 | 0.071381 | 0.045665
6418 | 96.16 | 14.696 | 0.07138 | 23.119 | 0.045669 |  | 6418 | 23.119 | 96.16 | 14.696 | 0.07138 | 0.045669
6419 | 96.17 | 14.696 | 0.071379 | 23.122 | 0.045673 |  | 6419 | 23.122 | 96.17 | 14.696 | 0.071379 | 0.045673
6420 | 96.18 | 14.696 | 0.071377 | 23.124 | 0.045678 |  | 6420 | 23.124 | 96.18 | 14.696 | 0.071377 | 0.045678
6421 | 96.19 | 14.696 | 0.071376 | 23.127 | 0.045682 |  | 6421 | 23.127 | 96.19 | 14.696 | 0.071376 | 0.045682
6422 | 96.2 | 14.696 | 0.071375 | 23.129 | 0.045686 |  | 6422 | 23.129 | 96.2 | 14.696 | 0.071375 | 0.045686
6423 | 96.21 | 14.696 | 0.071373 | 23.131 | 0.045691 |  | 6423 | 23.131 | 96.21 | 14.696 | 0.071373 | 0.045691
6424 | 96.22 | 14.696 | 0.071372 | 23.134 | 0.045695 |  | 6424 | 23.134 | 96.22 | 14.696 | 0.071372 | 0.045695
6425 | 96.23 | 14.696 | 0.071371 | 23.136 | 0.045699 |  | 6425 | 23.136 | 96.23 | 14.696 | 0.071371 | 0.045699
6426 | 96.24 | 14.696 | 0.071369 | 23.139 | 0.045704 |  | 6426 | 23.139 | 96.24 | 14.696 | 0.071369 | 0.045704
6427 | 96.25 | 14.696 | 0.071368 | 23.141 | 0.045708 |  | 6427 | 23.141 | 96.25 | 14.696 | 0.071368 | 0.045708
6428 | 96.26 | 14.696 | 0.071367 | 23.143 | 0.045712 |  | 6428 | 23.143 | 96.26 | 14.696 | 0.071367 | 0.045712
6429 | 96.27 | 14.696 | 0.071366 | 23.146 | 0.045717 |  | 6429 | 23.146 | 96.27 | 14.696 | 0.071366 | 0.045717
6430 | 96.28 | 14.696 | 0.071364 | 23.148 | 0.045721 |  | 6430 | 23.148 | 96.28 | 14.696 | 0.071364 | 0.045721
6431 | 96.29 | 14.696 | 0.071363 | 23.151 | 0.045725 |  | 6431 | 23.151 | 96.29 | 14.696 | 0.071363 | 0.045725
6432 | 96.3 | 14.696 | 0.071362 | 23.153 | 0.04573 |  | 6432 | 23.153 | 96.3 | 14.696 | 0.071362 | 0.04573
6433 | 96.31 | 14.696 | 0.07136 | 23.155 | 0.045734 |  | 6433 | 23.155 | 96.31 | 14.696 | 0.07136 | 0.045734
6434 | 96.32 | 14.696 | 0.071359 | 23.158 | 0.045738 |  | 6434 | 23.158 | 96.32 | 14.696 | 0.071359 | 0.045738
6435 | 96.33 | 14.696 | 0.071358 | 23.16 | 0.045743 |  | 6435 | 23.16 | 96.33 | 14.696 | 0.071358 | 0.045743
6436 | 96.34 | 14.696 | 0.071357 | 23.163 | 0.045747 |  | 6436 | 23.163 | 96.34 | 14.696 | 0.071357 | 0.045747
6437 | 96.35 | 14.696 | 0.071355 | 23.165 | 0.045751 |  | 6437 | 23.165 | 96.35 | 14.696 | 0.071355 | 0.045751
6438 | 96.36 | 14.696 | 0.071354 | 23.168 | 0.045756 |  | 6438 | 23.168 | 96.36 | 14.696 | 0.071354 | 0.045756
6439 | 96.37 | 14.696 | 0.071353 | 23.17 | 0.04576 |  | 6439 | 23.17 | 96.37 | 14.696 | 0.071353 | 0.04576
6440 | 96.38 | 14.696 | 0.071351 | 23.172 | 0.045764 |  | 6440 | 23.172 | 96.38 | 14.696 | 0.071351 | 0.045764
6441 | 96.39 | 14.696 | 0.07135 | 23.175 | 0.045769 |  | 6441 | 23.175 | 96.39 | 14.696 | 0.07135 | 0.045769
6442 | 96.4 | 14.696 | 0.071349 | 23.177 | 0.045773 |  | 6442 | 23.177 | 96.4 | 14.696 | 0.071349 | 0.045773
6443 | 96.41 | 14.696 | 0.071348 | 23.18 | 0.045777 |  | 6443 | 23.18 | 96.41 | 14.696 | 0.071348 | 0.045777
6444 | 96.42 | 14.696 | 0.071346 | 23.182 | 0.045782 |  | 6444 | 23.182 | 96.42 | 14.696 | 0.071346 | 0.045782
6445 | 96.43 | 14.696 | 0.071345 | 23.184 | 0.045786 |  | 6445 | 23.184 | 96.43 | 14.696 | 0.071345 | 0.045786
6446 | 96.44 | 14.696 | 0.071344 | 23.187 | 0.04579 |  | 6446 | 23.187 | 96.44 | 14.696 | 0.071344 | 0.04579
6447 | 96.45 | 14.696 | 0.071342 | 23.189 | 0.045795 |  | 6447 | 23.189 | 96.45 | 14.696 | 0.071342 | 0.045795
6448 | 96.46 | 14.696 | 0.071341 | 23.192 | 0.045799 |  | 6448 | 23.192 | 96.46 | 14.696 | 0.071341 | 0.045799
6449 | 96.47 | 14.696 | 0.07134 | 23.194 | 0.045803 |  | 6449 | 23.194 | 96.47 | 14.696 | 0.07134 | 0.045803
6450 | 96.48 | 14.696 | 0.071339 | 23.196 | 0.045808 |  | 6450 | 23.196 | 96.48 | 14.696 | 0.071339 | 0.045808
6451 | 96.49 | 14.696 | 0.071337 | 23.199 | 0.045812 |  | 6451 | 23.199 | 96.49 | 14.696 | 0.071337 | 0.045812
6452 | 96.5 | 14.696 | 0.071336 | 23.201 | 0.045816 |  | 6452 | 23.201 | 96.5 | 14.696 | 0.071336 | 0.045816
6453 | 96.51 | 14.696 | 0.071335 | 23.204 | 0.045821 |  | 6453 | 23.204 | 96.51 | 14.696 | 0.071335 | 0.045821
6454 | 96.52 | 14.696 | 0.071333 | 23.206 | 0.045825 |  | 6454 | 23.206 | 96.52 | 14.696 | 0.071333 | 0.045825
6455 | 96.53 | 14.696 | 0.071332 | 23.208 | 0.045829 |  | 6455 | 23.208 | 96.53 | 14.696 | 0.071332 | 0.045829
6456 | 96.54 | 14.696 | 0.071331 | 23.211 | 0.045833 |  | 6456 | 23.211 | 96.54 | 14.696 | 0.071331 | 0.045833
6457 | 96.55 | 14.696 | 0.07133 | 23.213 | 0.045838 |  | 6457 | 23.213 | 96.55 | 14.696 | 0.07133 | 0.045838
6458 | 96.56 | 14.696 | 0.071328 | 23.216 | 0.045842 |  | 6458 | 23.216 | 96.56 | 14.696 | 0.071328 | 0.045842
6459 | 96.57 | 14.696 | 0.071327 | 23.218 | 0.045846 |  | 6459 | 23.218 | 96.57 | 14.696 | 0.071327 | 0.045846
6460 | 96.58 | 14.696 | 0.071326 | 23.22 | 0.045851 |  | 6460 | 23.22 | 96.58 | 14.696 | 0.071326 | 0.045851
6461 | 96.59 | 14.696 | 0.071324 | 23.223 | 0.045855 |  | 6461 | 23.223 | 96.59 | 14.696 | 0.071324 | 0.045855
6462 | 96.6 | 14.696 | 0.071323 | 23.225 | 0.045859 |  | 6462 | 23.225 | 96.6 | 14.696 | 0.071323 | 0.045859
6463 | 96.61 | 14.696 | 0.071322 | 23.228 | 0.045864 |  | 6463 | 23.228 | 96.61 | 14.696 | 0.071322 | 0.045864
6464 | 96.62 | 14.696 | 0.071321 | 23.23 | 0.045868 |  | 6464 | 23.23 | 96.62 | 14.696 | 0.071321 | 0.045868
6465 | 96.63 | 14.696 | 0.071319 | 23.232 | 0.045872 |  | 6465 | 23.232 | 96.63 | 14.696 | 0.071319 | 0.045872
6466 | 96.64 | 14.696 | 0.071318 | 23.235 | 0.045877 |  | 6466 | 23.235 | 96.64 | 14.696 | 0.071318 | 0.045877
6467 | 96.65 | 14.696 | 0.071317 | 23.237 | 0.045881 |  | 6467 | 23.237 | 96.65 | 14.696 | 0.071317 | 0.045881
6468 | 96.66 | 14.696 | 0.071315 | 23.24 | 0.045885 |  | 6468 | 23.24 | 96.66 | 14.696 | 0.071315 | 0.045885
6469 | 96.67 | 14.696 | 0.071314 | 23.242 | 0.04589 |  | 6469 | 23.242 | 96.67 | 14.696 | 0.071314 | 0.04589
6470 | 96.68 | 14.696 | 0.071313 | 23.245 | 0.045894 |  | 6470 | 23.245 | 96.68 | 14.696 | 0.071313 | 0.045894
6471 | 96.69 | 14.696 | 0.071312 | 23.247 | 0.045898 |  | 6471 | 23.247 | 96.69 | 14.696 | 0.071312 | 0.045898
6472 | 96.7 | 14.696 | 0.07131 | 23.249 | 0.045903 |  | 6472 | 23.249 | 96.7 | 14.696 | 0.07131 | 0.045903
6473 | 96.71 | 14.696 | 0.071309 | 23.252 | 0.045907 |  | 6473 | 23.252 | 96.71 | 14.696 | 0.071309 | 0.045907
6474 | 96.72 | 14.696 | 0.071308 | 23.254 | 0.045911 |  | 6474 | 23.254 | 96.72 | 14.696 | 0.071308 | 0.045911
6475 | 96.73 | 14.696 | 0.071306 | 23.257 | 0.045916 |  | 6475 | 23.257 | 96.73 | 14.696 | 0.071306 | 0.045916
6476 | 96.74 | 14.696 | 0.071305 | 23.259 | 0.04592 |  | 6476 | 23.259 | 96.74 | 14.696 | 0.071305 | 0.04592
6477 | 96.75 | 14.696 | 0.071304 | 23.261 | 0.045924 |  | 6477 | 23.261 | 96.75 | 14.696 | 0.071304 | 0.045924
6478 | 96.76 | 14.696 | 0.071303 | 23.264 | 0.045929 |  | 6478 | 23.264 | 96.76 | 14.696 | 0.071303 | 0.045929
6479 | 96.77 | 14.696 | 0.071301 | 23.266 | 0.045933 |  | 6479 | 23.266 | 96.77 | 14.696 | 0.071301 | 0.045933
6480 | 96.78 | 14.696 | 0.0713 | 23.269 | 0.045937 |  | 6480 | 23.269 | 96.78 | 14.696 | 0.0713 | 0.045937
6481 | 96.79 | 14.696 | 0.071299 | 23.271 | 0.045942 |  | 6481 | 23.271 | 96.79 | 14.696 | 0.071299 | 0.045942
6482 | 96.8 | 14.696 | 0.071297 | 23.273 | 0.045946 |  | 6482 | 23.273 | 96.8 | 14.696 | 0.071297 | 0.045946
6483 | 96.81 | 14.696 | 0.071296 | 23.276 | 0.04595 |  | 6483 | 23.276 | 96.81 | 14.696 | 0.071296 | 0.04595
6484 | 96.82 | 14.696 | 0.071295 | 23.278 | 0.045955 |  | 6484 | 23.278 | 96.82 | 14.696 | 0.071295 | 0.045955
6485 | 96.83 | 14.696 | 0.071294 | 23.281 | 0.045959 |  | 6485 | 23.281 | 96.83 | 14.696 | 0.071294 | 0.045959
6486 | 96.84 | 14.696 | 0.071292 | 23.283 | 0.045963 |  | 6486 | 23.283 | 96.84 | 14.696 | 0.071292 | 0.045963
6487 | 96.85 | 14.696 | 0.071291 | 23.285 | 0.045968 |  | 6487 | 23.285 | 96.85 | 14.696 | 0.071291 | 0.045968
6488 | 96.86 | 14.696 | 0.07129 | 23.288 | 0.045972 |  | 6488 | 23.288 | 96.86 | 14.696 | 0.07129 | 0.045972
6489 | 96.87 | 14.696 | 0.071289 | 23.29 | 0.045976 |  | 6489 | 23.29 | 96.87 | 14.696 | 0.071289 | 0.045976
6490 | 96.88 | 14.696 | 0.071287 | 23.293 | 0.045981 |  | 6490 | 23.293 | 96.88 | 14.696 | 0.071287 | 0.045981
6491 | 96.89 | 14.696 | 0.071286 | 23.295 | 0.045985 |  | 6491 | 23.295 | 96.89 | 14.696 | 0.071286 | 0.045985
6492 | 96.9 | 14.696 | 0.071285 | 23.297 | 0.045989 |  | 6492 | 23.297 | 96.9 | 14.696 | 0.071285 | 0.045989
6493 | 96.91 | 14.696 | 0.071283 | 23.3 | 0.045993 |  | 6493 | 23.3 | 96.91 | 14.696 | 0.071283 | 0.045993
6494 | 96.92 | 14.696 | 0.071282 | 23.302 | 0.045998 |  | 6494 | 23.302 | 96.92 | 14.696 | 0.071282 | 0.045998
6495 | 96.93 | 14.696 | 0.071281 | 23.305 | 0.046002 |  | 6495 | 23.305 | 96.93 | 14.696 | 0.071281 | 0.046002
6496 | 96.94 | 14.696 | 0.07128 | 23.307 | 0.046006 |  | 6496 | 23.307 | 96.94 | 14.696 | 0.07128 | 0.046006
6497 | 96.95 | 14.696 | 0.071278 | 23.309 | 0.046011 |  | 6497 | 23.309 | 96.95 | 14.696 | 0.071278 | 0.046011
6498 | 96.96 | 14.696 | 0.071277 | 23.312 | 0.046015 |  | 6498 | 23.312 | 96.96 | 14.696 | 0.071277 | 0.046015
6499 | 96.97 | 14.696 | 0.071276 | 23.314 | 0.046019 |  | 6499 | 23.314 | 96.97 | 14.696 | 0.071276 | 0.046019
6500 | 96.98 | 14.696 | 0.071274 | 23.317 | 0.046024 |  | 6500 | 23.317 | 96.98 | 14.696 | 0.071274 | 0.046024
6501 | 96.99 | 14.696 | 0.071273 | 23.319 | 0.046028 |  | 6501 | 23.319 | 96.99 | 14.696 | 0.071273 | 0.046028
6502 | 97 | 14.696 | 0.071272 | 23.322 | 0.046032 |  | 6502 | 23.322 | 97 | 14.696 | 0.071272 | 0.046032
6503 | 97.01 | 14.696 | 0.071271 | 23.324 | 0.046037 |  | 6503 | 23.324 | 97.01 | 14.696 | 0.071271 | 0.046037
6504 | 97.02 | 14.696 | 0.071269 | 23.326 | 0.046041 |  | 6504 | 23.326 | 97.02 | 14.696 | 0.071269 | 0.046041
6505 | 97.03 | 14.696 | 0.071268 | 23.329 | 0.046045 |  | 6505 | 23.329 | 97.03 | 14.696 | 0.071268 | 0.046045
6506 | 97.04 | 14.696 | 0.071267 | 23.331 | 0.04605 |  | 6506 | 23.331 | 97.04 | 14.696 | 0.071267 | 0.04605
6507 | 97.05 | 14.696 | 0.071265 | 23.334 | 0.046054 |  | 6507 | 23.334 | 97.05 | 14.696 | 0.071265 | 0.046054
6508 | 97.06 | 14.696 | 0.071264 | 23.336 | 0.046058 |  | 6508 | 23.336 | 97.06 | 14.696 | 0.071264 | 0.046058
6509 | 97.07 | 14.696 | 0.071263 | 23.338 | 0.046063 |  | 6509 | 23.338 | 97.07 | 14.696 | 0.071263 | 0.046063
6510 | 97.08 | 14.696 | 0.071262 | 23.341 | 0.046067 |  | 6510 | 23.341 | 97.08 | 14.696 | 0.071262 | 0.046067
6511 | 97.09 | 14.696 | 0.07126 | 23.343 | 0.046071 |  | 6511 | 23.343 | 97.09 | 14.696 | 0.07126 | 0.046071
6512 | 97.1 | 14.696 | 0.071259 | 23.346 | 0.046076 |  | 6512 | 23.346 | 97.1 | 14.696 | 0.071259 | 0.046076
6513 | 97.11 | 14.696 | 0.071258 | 23.348 | 0.04608 |  | 6513 | 23.348 | 97.11 | 14.696 | 0.071258 | 0.04608
6514 | 97.12 | 14.696 | 0.071256 | 23.35 | 0.046084 |  | 6514 | 23.35 | 97.12 | 14.696 | 0.071256 | 0.046084
6515 | 97.13 | 14.696 | 0.071255 | 23.353 | 0.046089 |  | 6515 | 23.353 | 97.13 | 14.696 | 0.071255 | 0.046089
6516 | 97.14 | 14.696 | 0.071254 | 23.355 | 0.046093 |  | 6516 | 23.355 | 97.14 | 14.696 | 0.071254 | 0.046093
6517 | 97.15 | 14.696 | 0.071253 | 23.358 | 0.046097 |  | 6517 | 23.358 | 97.15 | 14.696 | 0.071253 | 0.046097
6518 | 97.16 | 14.696 | 0.071251 | 23.36 | 0.046102 |  | 6518 | 23.36 | 97.16 | 14.696 | 0.071251 | 0.046102
6519 | 97.17 | 14.696 | 0.07125 | 23.362 | 0.046106 |  | 6519 | 23.362 | 97.17 | 14.696 | 0.07125 | 0.046106
6520 | 97.18 | 14.696 | 0.071249 | 23.365 | 0.04611 |  | 6520 | 23.365 | 97.18 | 14.696 | 0.071249 | 0.04611
6521 | 97.19 | 14.696 | 0.071247 | 23.367 | 0.046115 |  | 6521 | 23.367 | 97.19 | 14.696 | 0.071247 | 0.046115
6522 | 97.2 | 14.696 | 0.071246 | 23.37 | 0.046119 |  | 6522 | 23.37 | 97.2 | 14.696 | 0.071246 | 0.046119
6523 | 97.21 | 14.696 | 0.071245 | 23.372 | 0.046123 |  | 6523 | 23.372 | 97.21 | 14.696 | 0.071245 | 0.046123
6524 | 97.22 | 14.696 | 0.071244 | 23.374 | 0.046127 |  | 6524 | 23.374 | 97.22 | 14.696 | 0.071244 | 0.046127
6525 | 97.23 | 14.696 | 0.071242 | 23.377 | 0.046132 |  | 6525 | 23.377 | 97.23 | 14.696 | 0.071242 | 0.046132
6526 | 97.24 | 14.696 | 0.071241 | 23.379 | 0.046136 |  | 6526 | 23.379 | 97.24 | 14.696 | 0.071241 | 0.046136
6527 | 97.25 | 14.696 | 0.07124 | 23.382 | 0.04614 |  | 6527 | 23.382 | 97.25 | 14.696 | 0.07124 | 0.04614
6528 | 97.26 | 14.696 | 0.071238 | 23.384 | 0.046145 |  | 6528 | 23.384 | 97.26 | 14.696 | 0.071238 | 0.046145
6529 | 97.27 | 14.696 | 0.071237 | 23.386 | 0.046149 |  | 6529 | 23.386 | 97.27 | 14.696 | 0.071237 | 0.046149
6530 | 97.28 | 14.696 | 0.071236 | 23.389 | 0.046153 |  | 6530 | 23.389 | 97.28 | 14.696 | 0.071236 | 0.046153
6531 | 97.29 | 14.696 | 0.071235 | 23.391 | 0.046158 |  | 6531 | 23.391 | 97.29 | 14.696 | 0.071235 | 0.046158
6532 | 97.3 | 14.696 | 0.071233 | 23.394 | 0.046162 |  | 6532 | 23.394 | 97.3 | 14.696 | 0.071233 | 0.046162
6533 | 97.31 | 14.696 | 0.071232 | 23.396 | 0.046166 |  | 6533 | 23.396 | 97.31 | 14.696 | 0.071232 | 0.046166
6534 | 97.32 | 14.696 | 0.071231 | 23.399 | 0.046171 |  | 6534 | 23.399 | 97.32 | 14.696 | 0.071231 | 0.046171
6535 | 97.33 | 14.696 | 0.071229 | 23.401 | 0.046175 |  | 6535 | 23.401 | 97.33 | 14.696 | 0.071229 | 0.046175
6536 | 97.34 | 14.696 | 0.071228 | 23.403 | 0.046179 |  | 6536 | 23.403 | 97.34 | 14.696 | 0.071228 | 0.046179
6537 | 97.35 | 14.696 | 0.071227 | 23.406 | 0.046184 |  | 6537 | 23.406 | 97.35 | 14.696 | 0.071227 | 0.046184
6538 | 97.36 | 14.696 | 0.071226 | 23.408 | 0.046188 |  | 6538 | 23.408 | 97.36 | 14.696 | 0.071226 | 0.046188
6539 | 97.37 | 14.696 | 0.071224 | 23.411 | 0.046192 |  | 6539 | 23.411 | 97.37 | 14.696 | 0.071224 | 0.046192
6540 | 97.38 | 14.696 | 0.071223 | 23.413 | 0.046197 |  | 6540 | 23.413 | 97.38 | 14.696 | 0.071223 | 0.046197
6541 | 97.39 | 14.696 | 0.071222 | 23.415 | 0.046201 |  | 6541 | 23.415 | 97.39 | 14.696 | 0.071222 | 0.046201
6542 | 97.4 | 14.696 | 0.071221 | 23.418 | 0.046205 |  | 6542 | 23.418 | 97.4 | 14.696 | 0.071221 | 0.046205
6543 | 97.41 | 14.696 | 0.071219 | 23.42 | 0.04621 |  | 6543 | 23.42 | 97.41 | 14.696 | 0.071219 | 0.04621
6544 | 97.42 | 14.696 | 0.071218 | 23.423 | 0.046214 |  | 6544 | 23.423 | 97.42 | 14.696 | 0.071218 | 0.046214
6545 | 97.43 | 14.696 | 0.071217 | 23.425 | 0.046218 |  | 6545 | 23.425 | 97.43 | 14.696 | 0.071217 | 0.046218
6546 | 97.44 | 14.696 | 0.071215 | 23.427 | 0.046223 |  | 6546 | 23.427 | 97.44 | 14.696 | 0.071215 | 0.046223
6547 | 97.45 | 14.696 | 0.071214 | 23.43 | 0.046227 |  | 6547 | 23.43 | 97.45 | 14.696 | 0.071214 | 0.046227
6548 | 97.46 | 14.696 | 0.071213 | 23.432 | 0.046231 |  | 6548 | 23.432 | 97.46 | 14.696 | 0.071213 | 0.046231
6549 | 97.47 | 14.696 | 0.071212 | 23.435 | 0.046235 |  | 6549 | 23.435 | 97.47 | 14.696 | 0.071212 | 0.046235
6550 | 97.48 | 14.696 | 0.07121 | 23.437 | 0.04624 |  | 6550 | 23.437 | 97.48 | 14.696 | 0.07121 | 0.04624
6551 | 97.49 | 14.696 | 0.071209 | 23.439 | 0.046244 |  | 6551 | 23.439 | 97.49 | 14.696 | 0.071209 | 0.046244
6552 | 97.5 | 14.696 | 0.071208 | 23.442 | 0.046248 |  | 6552 | 23.442 | 97.5 | 14.696 | 0.071208 | 0.046248
6553 | 97.51 | 14.696 | 0.071206 | 23.444 | 0.046253 |  | 6553 | 23.444 | 97.51 | 14.696 | 0.071206 | 0.046253
6554 | 97.52 | 14.696 | 0.071205 | 23.447 | 0.046257 |  | 6554 | 23.447 | 97.52 | 14.696 | 0.071205 | 0.046257
6555 | 97.53 | 14.696 | 0.071204 | 23.449 | 0.046261 |  | 6555 | 23.449 | 97.53 | 14.696 | 0.071204 | 0.046261
6556 | 97.54 | 14.696 | 0.071203 | 23.451 | 0.046266 |  | 6556 | 23.451 | 97.54 | 14.696 | 0.071203 | 0.046266
6557 | 97.55 | 14.696 | 0.071201 | 23.454 | 0.04627 |  | 6557 | 23.454 | 97.55 | 14.696 | 0.071201 | 0.04627
6558 | 97.56 | 14.696 | 0.0712 | 23.456 | 0.046274 |  | 6558 | 23.456 | 97.56 | 14.696 | 0.0712 | 0.046274
6559 | 97.57 | 14.696 | 0.071199 | 23.459 | 0.046279 |  | 6559 | 23.459 | 97.57 | 14.696 | 0.071199 | 0.046279
6560 | 97.58 | 14.696 | 0.071197 | 23.461 | 0.046283 |  | 6560 | 23.461 | 97.58 | 14.696 | 0.071197 | 0.046283
6561 | 97.59 | 14.696 | 0.071196 | 23.463 | 0.046287 |  | 6561 | 23.463 | 97.59 | 14.696 | 0.071196 | 0.046287
6562 | 97.6 | 14.696 | 0.071195 | 23.466 | 0.046292 |  | 6562 | 23.466 | 97.6 | 14.696 | 0.071195 | 0.046292
6563 | 97.61 | 14.696 | 0.071194 | 23.468 | 0.046296 |  | 6563 | 23.468 | 97.61 | 14.696 | 0.071194 | 0.046296
6564 | 97.62 | 14.696 | 0.071192 | 23.471 | 0.0463 |  | 6564 | 23.471 | 97.62 | 14.696 | 0.071192 | 0.0463
6565 | 97.63 | 14.696 | 0.071191 | 23.473 | 0.046305 |  | 6565 | 23.473 | 97.63 | 14.696 | 0.071191 | 0.046305
6566 | 97.64 | 14.696 | 0.07119 | 23.476 | 0.046309 |  | 6566 | 23.476 | 97.64 | 14.696 | 0.07119 | 0.046309
6567 | 97.65 | 14.696 | 0.071188 | 23.478 | 0.046313 |  | 6567 | 23.478 | 97.65 | 14.696 | 0.071188 | 0.046313
6568 | 97.66 | 14.696 | 0.071187 | 23.48 | 0.046318 |  | 6568 | 23.48 | 97.66 | 14.696 | 0.071187 | 0.046318
6569 | 97.67 | 14.696 | 0.071186 | 23.483 | 0.046322 |  | 6569 | 23.483 | 97.67 | 14.696 | 0.071186 | 0.046322
6570 | 97.68 | 14.696 | 0.071185 | 23.485 | 0.046326 |  | 6570 | 23.485 | 97.68 | 14.696 | 0.071185 | 0.046326
6571 | 97.69 | 14.696 | 0.071183 | 23.488 | 0.04633 |  | 6571 | 23.488 | 97.69 | 14.696 | 0.071183 | 0.04633
6572 | 97.7 | 14.696 | 0.071182 | 23.49 | 0.046335 |  | 6572 | 23.49 | 97.7 | 14.696 | 0.071182 | 0.046335
6573 | 97.71 | 14.696 | 0.071181 | 23.492 | 0.046339 |  | 6573 | 23.492 | 97.71 | 14.696 | 0.071181 | 0.046339
6574 | 97.72 | 14.696 | 0.07118 | 23.495 | 0.046343 |  | 6574 | 23.495 | 97.72 | 14.696 | 0.07118 | 0.046343
6575 | 97.73 | 14.696 | 0.071178 | 23.497 | 0.046348 |  | 6575 | 23.497 | 97.73 | 14.696 | 0.071178 | 0.046348
6576 | 97.74 | 14.696 | 0.071177 | 23.5 | 0.046352 |  | 6576 | 23.5 | 97.74 | 14.696 | 0.071177 | 0.046352
6577 | 97.75 | 14.696 | 0.071176 | 23.502 | 0.046356 |  | 6577 | 23.502 | 97.75 | 14.696 | 0.071176 | 0.046356
6578 | 97.76 | 14.696 | 0.071174 | 23.504 | 0.046361 |  | 6578 | 23.504 | 97.76 | 14.696 | 0.071174 | 0.046361
6579 | 97.77 | 14.696 | 0.071173 | 23.507 | 0.046365 |  | 6579 | 23.507 | 97.77 | 14.696 | 0.071173 | 0.046365
6580 | 97.78 | 14.696 | 0.071172 | 23.509 | 0.046369 |  | 6580 | 23.509 | 97.78 | 14.696 | 0.071172 | 0.046369
6581 | 97.79 | 14.696 | 0.071171 | 23.512 | 0.046374 |  | 6581 | 23.512 | 97.79 | 14.696 | 0.071171 | 0.046374
6582 | 97.8 | 14.696 | 0.071169 | 23.514 | 0.046378 |  | 6582 | 23.514 | 97.8 | 14.696 | 0.071169 | 0.046378
6583 | 97.81 | 14.696 | 0.071168 | 23.516 | 0.046382 |  | 6583 | 23.516 | 97.81 | 14.696 | 0.071168 | 0.046382
6584 | 97.82 | 14.696 | 0.071167 | 23.519 | 0.046387 |  | 6584 | 23.519 | 97.82 | 14.696 | 0.071167 | 0.046387
6585 | 97.83 | 14.696 | 0.071165 | 23.521 | 0.046391 |  | 6585 | 23.521 | 97.83 | 14.696 | 0.071165 | 0.046391
6586 | 97.84 | 14.696 | 0.071164 | 23.524 | 0.046395 |  | 6586 | 23.524 | 97.84 | 14.696 | 0.071164 | 0.046395
6587 | 97.85 | 14.696 | 0.071163 | 23.526 | 0.0464 |  | 6587 | 23.526 | 97.85 | 14.696 | 0.071163 | 0.0464
6588 | 97.86 | 14.696 | 0.071162 | 23.528 | 0.046404 |  | 6588 | 23.528 | 97.86 | 14.696 | 0.071162 | 0.046404
6589 | 97.87 | 14.696 | 0.07116 | 23.531 | 0.046408 |  | 6589 | 23.531 | 97.87 | 14.696 | 0.07116 | 0.046408
6590 | 97.88 | 14.696 | 0.071159 | 23.533 | 0.046412 |  | 6590 | 23.533 | 97.88 | 14.696 | 0.071159 | 0.046412
6591 | 97.89 | 14.696 | 0.071158 | 23.536 | 0.046417 |  | 6591 | 23.536 | 97.89 | 14.696 | 0.071158 | 0.046417
6592 | 97.9 | 14.696 | 0.071156 | 23.538 | 0.046421 |  | 6592 | 23.538 | 97.9 | 14.696 | 0.071156 | 0.046421
6593 | 97.91 | 14.696 | 0.071155 | 23.54 | 0.046425 |  | 6593 | 23.54 | 97.91 | 14.696 | 0.071155 | 0.046425
6594 | 97.92 | 14.696 | 0.071154 | 23.543 | 0.04643 |  | 6594 | 23.543 | 97.92 | 14.696 | 0.071154 | 0.04643
6595 | 97.93 | 14.696 | 0.071153 | 23.545 | 0.046434 |  | 6595 | 23.545 | 97.93 | 14.696 | 0.071153 | 0.046434
6596 | 97.94 | 14.696 | 0.071151 | 23.548 | 0.046438 |  | 6596 | 23.548 | 97.94 | 14.696 | 0.071151 | 0.046438
6597 | 97.95 | 14.696 | 0.07115 | 23.55 | 0.046443 |  | 6597 | 23.55 | 97.95 | 14.696 | 0.07115 | 0.046443
6598 | 97.96 | 14.696 | 0.071149 | 23.553 | 0.046447 |  | 6598 | 23.553 | 97.96 | 14.696 | 0.071149 | 0.046447
6599 | 97.97 | 14.696 | 0.071148 | 23.555 | 0.046451 |  | 6599 | 23.555 | 97.97 | 14.696 | 0.071148 | 0.046451
6600 | 97.98 | 14.696 | 0.071146 | 23.557 | 0.046456 |  | 6600 | 23.557 | 97.98 | 14.696 | 0.071146 | 0.046456
6601 | 97.99 | 14.696 | 0.071145 | 23.56 | 0.04646 |  | 6601 | 23.56 | 97.99 | 14.696 | 0.071145 | 0.04646
6602 | 98 | 14.696 | 0.071144 | 23.562 | 0.046464 |  | 6602 | 23.562 | 98 | 14.696 | 0.071144 | 0.046464
6603 | 98.01 | 14.696 | 0.071142 | 23.565 | 0.046469 |  | 6603 | 23.565 | 98.01 | 14.696 | 0.071142 | 0.046469
6604 | 98.02 | 14.696 | 0.071141 | 23.567 | 0.046473 |  | 6604 | 23.567 | 98.02 | 14.696 | 0.071141 | 0.046473
6605 | 98.03 | 14.696 | 0.07114 | 23.569 | 0.046477 |  | 6605 | 23.569 | 98.03 | 14.696 | 0.07114 | 0.046477
6606 | 98.04 | 14.696 | 0.071139 | 23.572 | 0.046482 |  | 6606 | 23.572 | 98.04 | 14.696 | 0.071139 | 0.046482
6607 | 98.05 | 14.696 | 0.071137 | 23.574 | 0.046486 |  | 6607 | 23.574 | 98.05 | 14.696 | 0.071137 | 0.046486
6608 | 98.06 | 14.696 | 0.071136 | 23.577 | 0.04649 |  | 6608 | 23.577 | 98.06 | 14.696 | 0.071136 | 0.04649
6609 | 98.07 | 14.696 | 0.071135 | 23.579 | 0.046494 |  | 6609 | 23.579 | 98.07 | 14.696 | 0.071135 | 0.046494
6610 | 98.08 | 14.696 | 0.071133 | 23.581 | 0.046499 |  | 6610 | 23.581 | 98.08 | 14.696 | 0.071133 | 0.046499
6611 | 98.09 | 14.696 | 0.071132 | 23.584 | 0.046503 |  | 6611 | 23.584 | 98.09 | 14.696 | 0.071132 | 0.046503
6612 | 98.1 | 14.696 | 0.071131 | 23.586 | 0.046507 |  | 6612 | 23.586 | 98.1 | 14.696 | 0.071131 | 0.046507
6613 | 98.11 | 14.696 | 0.07113 | 23.589 | 0.046512 |  | 6613 | 23.589 | 98.11 | 14.696 | 0.07113 | 0.046512
6614 | 98.12 | 14.696 | 0.071128 | 23.591 | 0.046516 |  | 6614 | 23.591 | 98.12 | 14.696 | 0.071128 | 0.046516
6615 | 98.13 | 14.696 | 0.071127 | 23.593 | 0.04652 |  | 6615 | 23.593 | 98.13 | 14.696 | 0.071127 | 0.04652
6616 | 98.14 | 14.696 | 0.071126 | 23.596 | 0.046525 |  | 6616 | 23.596 | 98.14 | 14.696 | 0.071126 | 0.046525
6617 | 98.15 | 14.696 | 0.071125 | 23.598 | 0.046529 |  | 6617 | 23.598 | 98.15 | 14.696 | 0.071125 | 0.046529
6618 | 98.16 | 14.696 | 0.071123 | 23.601 | 0.046533 |  | 6618 | 23.601 | 98.16 | 14.696 | 0.071123 | 0.046533
6619 | 98.17 | 14.696 | 0.071122 | 23.603 | 0.046538 |  | 6619 | 23.603 | 98.17 | 14.696 | 0.071122 | 0.046538
6620 | 98.18 | 14.696 | 0.071121 | 23.605 | 0.046542 |  | 6620 | 23.605 | 98.18 | 14.696 | 0.071121 | 0.046542
6621 | 98.19 | 14.696 | 0.071119 | 23.608 | 0.046546 |  | 6621 | 23.608 | 98.19 | 14.696 | 0.071119 | 0.046546
6622 | 98.2 | 14.696 | 0.071118 | 23.61 | 0.046551 |  | 6622 | 23.61 | 98.2 | 14.696 | 0.071118 | 0.046551
6623 | 98.21 | 14.696 | 0.071117 | 23.613 | 0.046555 |  | 6623 | 23.613 | 98.21 | 14.696 | 0.071117 | 0.046555
6624 | 98.22 | 14.696 | 0.071116 | 23.615 | 0.046559 |  | 6624 | 23.615 | 98.22 | 14.696 | 0.071116 | 0.046559
6625 | 98.23 | 14.696 | 0.071114 | 23.617 | 0.046563 |  | 6625 | 23.617 | 98.23 | 14.696 | 0.071114 | 0.046563
6626 | 98.24 | 14.696 | 0.071113 | 23.62 | 0.046568 |  | 6626 | 23.62 | 98.24 | 14.696 | 0.071113 | 0.046568
6627 | 98.25 | 14.696 | 0.071112 | 23.622 | 0.046572 |  | 6627 | 23.622 | 98.25 | 14.696 | 0.071112 | 0.046572
6628 | 98.26 | 14.696 | 0.07111 | 23.625 | 0.046576 |  | 6628 | 23.625 | 98.26 | 14.696 | 0.07111 | 0.046576
6629 | 98.27 | 14.696 | 0.071109 | 23.627 | 0.046581 |  | 6629 | 23.627 | 98.27 | 14.696 | 0.071109 | 0.046581
6630 | 98.28 | 14.696 | 0.071108 | 23.63 | 0.046585 |  | 6630 | 23.63 | 98.28 | 14.696 | 0.071108 | 0.046585
6631 | 98.29 | 14.696 | 0.071107 | 23.632 | 0.046589 |  | 6631 | 23.632 | 98.29 | 14.696 | 0.071107 | 0.046589
6632 | 98.3 | 14.696 | 0.071105 | 23.634 | 0.046594 |  | 6632 | 23.634 | 98.3 | 14.696 | 0.071105 | 0.046594
6633 | 98.31 | 14.696 | 0.071104 | 23.637 | 0.046598 |  | 6633 | 23.637 | 98.31 | 14.696 | 0.071104 | 0.046598
6634 | 98.32 | 14.696 | 0.071103 | 23.639 | 0.046602 |  | 6634 | 23.639 | 98.32 | 14.696 | 0.071103 | 0.046602
6635 | 98.33 | 14.696 | 0.071102 | 23.642 | 0.046607 |  | 6635 | 23.642 | 98.33 | 14.696 | 0.071102 | 0.046607
6636 | 98.34 | 14.696 | 0.0711 | 23.644 | 0.046611 |  | 6636 | 23.644 | 98.34 | 14.696 | 0.0711 | 0.046611
6637 | 98.35 | 14.696 | 0.071099 | 23.646 | 0.046615 |  | 6637 | 23.646 | 98.35 | 14.696 | 0.071099 | 0.046615
6638 | 98.36 | 14.696 | 0.071098 | 23.649 | 0.04662 |  | 6638 | 23.649 | 98.36 | 14.696 | 0.071098 | 0.04662
6639 | 98.37 | 14.696 | 0.071096 | 23.651 | 0.046624 |  | 6639 | 23.651 | 98.37 | 14.696 | 0.071096 | 0.046624
6640 | 98.38 | 14.696 | 0.071095 | 23.654 | 0.046628 |  | 6640 | 23.654 | 98.38 | 14.696 | 0.071095 | 0.046628
6641 | 98.39 | 14.696 | 0.071094 | 23.656 | 0.046632 |  | 6641 | 23.656 | 98.39 | 14.696 | 0.071094 | 0.046632
6642 | 98.4 | 14.696 | 0.071093 | 23.658 | 0.046637 |  | 6642 | 23.658 | 98.4 | 14.696 | 0.071093 | 0.046637
6643 | 98.41 | 14.696 | 0.071091 | 23.661 | 0.046641 |  | 6643 | 23.661 | 98.41 | 14.696 | 0.071091 | 0.046641
6644 | 98.42 | 14.696 | 0.07109 | 23.663 | 0.046645 |  | 6644 | 23.663 | 98.42 | 14.696 | 0.07109 | 0.046645
6645 | 98.43 | 14.696 | 0.071089 | 23.666 | 0.04665 |  | 6645 | 23.666 | 98.43 | 14.696 | 0.071089 | 0.04665
6646 | 98.44 | 14.696 | 0.071087 | 23.668 | 0.046654 |  | 6646 | 23.668 | 98.44 | 14.696 | 0.071087 | 0.046654
6647 | 98.45 | 14.696 | 0.071086 | 23.67 | 0.046658 |  | 6647 | 23.67 | 98.45 | 14.696 | 0.071086 | 0.046658
6648 | 98.46 | 14.696 | 0.071085 | 23.673 | 0.046663 |  | 6648 | 23.673 | 98.46 | 14.696 | 0.071085 | 0.046663
6649 | 98.47 | 14.696 | 0.071084 | 23.675 | 0.046667 |  | 6649 | 23.675 | 98.47 | 14.696 | 0.071084 | 0.046667
6650 | 98.48 | 14.696 | 0.071082 | 23.678 | 0.046671 |  | 6650 | 23.678 | 98.48 | 14.696 | 0.071082 | 0.046671
6651 | 98.49 | 14.696 | 0.071081 | 23.68 | 0.046676 |  | 6651 | 23.68 | 98.49 | 14.696 | 0.071081 | 0.046676
6652 | 98.5 | 14.696 | 0.07108 | 23.682 | 0.04668 |  | 6652 | 23.682 | 98.5 | 14.696 | 0.07108 | 0.04668
6653 | 98.51 | 14.696 | 0.071079 | 23.685 | 0.046684 |  | 6653 | 23.685 | 98.51 | 14.696 | 0.071079 | 0.046684
6654 | 98.52 | 14.696 | 0.071077 | 23.687 | 0.046689 |  | 6654 | 23.687 | 98.52 | 14.696 | 0.071077 | 0.046689
6655 | 98.53 | 14.696 | 0.071076 | 23.69 | 0.046693 |  | 6655 | 23.69 | 98.53 | 14.696 | 0.071076 | 0.046693
6656 | 98.54 | 14.696 | 0.071075 | 23.692 | 0.046697 |  | 6656 | 23.692 | 98.54 | 14.696 | 0.071075 | 0.046697
6657 | 98.55 | 14.696 | 0.071073 | 23.694 | 0.046701 |  | 6657 | 23.694 | 98.55 | 14.696 | 0.071073 | 0.046701
6658 | 98.56 | 14.696 | 0.071072 | 23.697 | 0.046706 |  | 6658 | 23.697 | 98.56 | 14.696 | 0.071072 | 0.046706
6659 | 98.57 | 14.696 | 0.071071 | 23.699 | 0.04671 |  | 6659 | 23.699 | 98.57 | 14.696 | 0.071071 | 0.04671
6660 | 98.58 | 14.696 | 0.07107 | 23.702 | 0.046714 |  | 6660 | 23.702 | 98.58 | 14.696 | 0.07107 | 0.046714
6661 | 98.59 | 14.696 | 0.071068 | 23.704 | 0.046719 |  | 6661 | 23.704 | 98.59 | 14.696 | 0.071068 | 0.046719
6662 | 98.6 | 14.696 | 0.071067 | 23.707 | 0.046723 |  | 6662 | 23.707 | 98.6 | 14.696 | 0.071067 | 0.046723
6663 | 98.61 | 14.696 | 0.071066 | 23.709 | 0.046727 |  | 6663 | 23.709 | 98.61 | 14.696 | 0.071066 | 0.046727
6664 | 98.62 | 14.696 | 0.071065 | 23.711 | 0.046732 |  | 6664 | 23.711 | 98.62 | 14.696 | 0.071065 | 0.046732
6665 | 98.63 | 14.696 | 0.071063 | 23.714 | 0.046736 |  | 6665 | 23.714 | 98.63 | 14.696 | 0.071063 | 0.046736
6666 | 98.64 | 14.696 | 0.071062 | 23.716 | 0.04674 |  | 6666 | 23.716 | 98.64 | 14.696 | 0.071062 | 0.04674
6667 | 98.65 | 14.696 | 0.071061 | 23.719 | 0.046745 |  | 6667 | 23.719 | 98.65 | 14.696 | 0.071061 | 0.046745
6668 | 98.66 | 14.696 | 0.071059 | 23.721 | 0.046749 |  | 6668 | 23.721 | 98.66 | 14.696 | 0.071059 | 0.046749
6669 | 98.67 | 14.696 | 0.071058 | 23.723 | 0.046753 |  | 6669 | 23.723 | 98.67 | 14.696 | 0.071058 | 0.046753
6670 | 98.68 | 14.696 | 0.071057 | 23.726 | 0.046757 |  | 6670 | 23.726 | 98.68 | 14.696 | 0.071057 | 0.046757
6671 | 98.69 | 14.696 | 0.071056 | 23.728 | 0.046762 |  | 6671 | 23.728 | 98.69 | 14.696 | 0.071056 | 0.046762
6672 | 98.7 | 14.696 | 0.071054 | 23.731 | 0.046766 |  | 6672 | 23.731 | 98.7 | 14.696 | 0.071054 | 0.046766
6673 | 98.71 | 14.696 | 0.071053 | 23.733 | 0.04677 |  | 6673 | 23.733 | 98.71 | 14.696 | 0.071053 | 0.04677
6674 | 98.72 | 14.696 | 0.071052 | 23.735 | 0.046775 |  | 6674 | 23.735 | 98.72 | 14.696 | 0.071052 | 0.046775
6675 | 98.73 | 14.696 | 0.07105 | 23.738 | 0.046779 |  | 6675 | 23.738 | 98.73 | 14.696 | 0.07105 | 0.046779
6676 | 98.74 | 14.696 | 0.071049 | 23.74 | 0.046783 |  | 6676 | 23.74 | 98.74 | 14.696 | 0.071049 | 0.046783
6677 | 98.75 | 14.696 | 0.071048 | 23.743 | 0.046788 |  | 6677 | 23.743 | 98.75 | 14.696 | 0.071048 | 0.046788
6678 | 98.76 | 14.696 | 0.071047 | 23.745 | 0.046792 |  | 6678 | 23.745 | 98.76 | 14.696 | 0.071047 | 0.046792
6679 | 98.77 | 14.696 | 0.071045 | 23.747 | 0.046796 |  | 6679 | 23.747 | 98.77 | 14.696 | 0.071045 | 0.046796
6680 | 98.78 | 14.696 | 0.071044 | 23.75 | 0.046801 |  | 6680 | 23.75 | 98.78 | 14.696 | 0.071044 | 0.046801
6681 | 98.79 | 14.696 | 0.071043 | 23.752 | 0.046805 |  | 6681 | 23.752 | 98.79 | 14.696 | 0.071043 | 0.046805
6682 | 98.8 | 14.696 | 0.071042 | 23.755 | 0.046809 |  | 6682 | 23.755 | 98.8 | 14.696 | 0.071042 | 0.046809
6683 | 98.81 | 14.696 | 0.07104 | 23.757 | 0.046814 |  | 6683 | 23.757 | 98.81 | 14.696 | 0.07104 | 0.046814
6684 | 98.82 | 14.696 | 0.071039 | 23.759 | 0.046818 |  | 6684 | 23.759 | 98.82 | 14.696 | 0.071039 | 0.046818
6685 | 98.83 | 14.696 | 0.071038 | 23.762 | 0.046822 |  | 6685 | 23.762 | 98.83 | 14.696 | 0.071038 | 0.046822
6686 | 98.84 | 14.696 | 0.071036 | 23.764 | 0.046826 |  | 6686 | 23.764 | 98.84 | 14.696 | 0.071036 | 0.046826
6687 | 98.85 | 14.696 | 0.071035 | 23.767 | 0.046831 |  | 6687 | 23.767 | 98.85 | 14.696 | 0.071035 | 0.046831
6688 | 98.86 | 14.696 | 0.071034 | 23.769 | 0.046835 |  | 6688 | 23.769 | 98.86 | 14.696 | 0.071034 | 0.046835
6689 | 98.87 | 14.696 | 0.071033 | 23.771 | 0.046839 |  | 6689 | 23.771 | 98.87 | 14.696 | 0.071033 | 0.046839
6690 | 98.88 | 14.696 | 0.071031 | 23.774 | 0.046844 |  | 6690 | 23.774 | 98.88 | 14.696 | 0.071031 | 0.046844
6691 | 98.89 | 14.696 | 0.07103 | 23.776 | 0.046848 |  | 6691 | 23.776 | 98.89 | 14.696 | 0.07103 | 0.046848
6692 | 98.9 | 14.696 | 0.071029 | 23.779 | 0.046852 |  | 6692 | 23.779 | 98.9 | 14.696 | 0.071029 | 0.046852
6693 | 98.91 | 14.696 | 0.071028 | 23.781 | 0.046857 |  | 6693 | 23.781 | 98.91 | 14.696 | 0.071028 | 0.046857
6694 | 98.92 | 14.696 | 0.071026 | 23.784 | 0.046861 |  | 6694 | 23.784 | 98.92 | 14.696 | 0.071026 | 0.046861
6695 | 98.93 | 14.696 | 0.071025 | 23.786 | 0.046865 |  | 6695 | 23.786 | 98.93 | 14.696 | 0.071025 | 0.046865
6696 | 98.94 | 14.696 | 0.071024 | 23.788 | 0.04687 |  | 6696 | 23.788 | 98.94 | 14.696 | 0.071024 | 0.04687
6697 | 98.95 | 14.696 | 0.071022 | 23.791 | 0.046874 |  | 6697 | 23.791 | 98.95 | 14.696 | 0.071022 | 0.046874
6698 | 98.96 | 14.696 | 0.071021 | 23.793 | 0.046878 |  | 6698 | 23.793 | 98.96 | 14.696 | 0.071021 | 0.046878
6699 | 98.97 | 14.696 | 0.07102 | 23.796 | 0.046882 |  | 6699 | 23.796 | 98.97 | 14.696 | 0.07102 | 0.046882
6700 | 98.98 | 14.696 | 0.071019 | 23.798 | 0.046887 |  | 6700 | 23.798 | 98.98 | 14.696 | 0.071019 | 0.046887
6701 | 98.99 | 14.696 | 0.071017 | 23.8 | 0.046891 |  | 6701 | 23.8 | 98.99 | 14.696 | 0.071017 | 0.046891
6702 | 99 | 14.696 | 0.071016 | 23.803 | 0.046895 |  | 6702 | 23.803 | 99 | 14.696 | 0.071016 | 0.046895
6703 | 99.01 | 14.696 | 0.071015 | 23.805 | 0.0469 |  | 6703 | 23.805 | 99.01 | 14.696 | 0.071015 | 0.0469
6704 | 99.02 | 14.696 | 0.071014 | 23.808 | 0.046904 |  | 6704 | 23.808 | 99.02 | 14.696 | 0.071014 | 0.046904
6705 | 99.03 | 14.696 | 0.071012 | 23.81 | 0.046908 |  | 6705 | 23.81 | 99.03 | 14.696 | 0.071012 | 0.046908
6706 | 99.04 | 14.696 | 0.071011 | 23.812 | 0.046913 |  | 6706 | 23.812 | 99.04 | 14.696 | 0.071011 | 0.046913
6707 | 99.05 | 14.696 | 0.07101 | 23.815 | 0.046917 |  | 6707 | 23.815 | 99.05 | 14.696 | 0.07101 | 0.046917
6708 | 99.06 | 14.696 | 0.071008 | 23.817 | 0.046921 |  | 6708 | 23.817 | 99.06 | 14.696 | 0.071008 | 0.046921
6709 | 99.07 | 14.696 | 0.071007 | 23.82 | 0.046926 |  | 6709 | 23.82 | 99.07 | 14.696 | 0.071007 | 0.046926
6710 | 99.08 | 14.696 | 0.071006 | 23.822 | 0.04693 |  | 6710 | 23.822 | 99.08 | 14.696 | 0.071006 | 0.04693
6711 | 99.09 | 14.696 | 0.071005 | 23.824 | 0.046934 |  | 6711 | 23.824 | 99.09 | 14.696 | 0.071005 | 0.046934
6712 | 99.1 | 14.696 | 0.071003 | 23.827 | 0.046938 |  | 6712 | 23.827 | 99.1 | 14.696 | 0.071003 | 0.046938
6713 | 99.11 | 14.696 | 0.071002 | 23.829 | 0.046943 |  | 6713 | 23.829 | 99.11 | 14.696 | 0.071002 | 0.046943
6714 | 99.12 | 14.696 | 0.071001 | 23.832 | 0.046947 |  | 6714 | 23.832 | 99.12 | 14.696 | 0.071001 | 0.046947
6715 | 99.13 | 14.696 | 0.070999 | 23.834 | 0.046951 |  | 6715 | 23.834 | 99.13 | 14.696 | 0.070999 | 0.046951
6716 | 99.14 | 14.696 | 0.070998 | 23.836 | 0.046956 |  | 6716 | 23.836 | 99.14 | 14.696 | 0.070998 | 0.046956
6717 | 99.15 | 14.696 | 0.070997 | 23.839 | 0.04696 |  | 6717 | 23.839 | 99.15 | 14.696 | 0.070997 | 0.04696
6718 | 99.16 | 14.696 | 0.070996 | 23.841 | 0.046964 |  | 6718 | 23.841 | 99.16 | 14.696 | 0.070996 | 0.046964
6719 | 99.17 | 14.696 | 0.070994 | 23.844 | 0.046969 |  | 6719 | 23.844 | 99.17 | 14.696 | 0.070994 | 0.046969
6720 | 99.18 | 14.696 | 0.070993 | 23.846 | 0.046973 |  | 6720 | 23.846 | 99.18 | 14.696 | 0.070993 | 0.046973
6721 | 99.19 | 14.696 | 0.070992 | 23.848 | 0.046977 |  | 6721 | 23.848 | 99.19 | 14.696 | 0.070992 | 0.046977
6722 | 99.2 | 14.696 | 0.070991 | 23.851 | 0.046981 |  | 6722 | 23.851 | 99.2 | 14.696 | 0.070991 | 0.046981
6723 | 99.21 | 14.696 | 0.070989 | 23.853 | 0.046986 |  | 6723 | 23.853 | 99.21 | 14.696 | 0.070989 | 0.046986
6724 | 99.22 | 14.696 | 0.070988 | 23.856 | 0.04699 |  | 6724 | 23.856 | 99.22 | 14.696 | 0.070988 | 0.04699
6725 | 99.23 | 14.696 | 0.070987 | 23.858 | 0.046994 |  | 6725 | 23.858 | 99.23 | 14.696 | 0.070987 | 0.046994
6726 | 99.24 | 14.696 | 0.070985 | 23.861 | 0.046999 |  | 6726 | 23.861 | 99.24 | 14.696 | 0.070985 | 0.046999
6727 | 99.25 | 14.696 | 0.070984 | 23.863 | 0.047003 |  | 6727 | 23.863 | 99.25 | 14.696 | 0.070984 | 0.047003
6728 | 99.26 | 14.696 | 0.070983 | 23.865 | 0.047007 |  | 6728 | 23.865 | 99.26 | 14.696 | 0.070983 | 0.047007
6729 | 99.27 | 14.696 | 0.070982 | 23.868 | 0.047012 |  | 6729 | 23.868 | 99.27 | 14.696 | 0.070982 | 0.047012
6730 | 99.28 | 14.696 | 0.07098 | 23.87 | 0.047016 |  | 6730 | 23.87 | 99.28 | 14.696 | 0.07098 | 0.047016
6731 | 99.29 | 14.696 | 0.070979 | 23.873 | 0.04702 |  | 6731 | 23.873 | 99.29 | 14.696 | 0.070979 | 0.04702
6732 | 99.3 | 14.696 | 0.070978 | 23.875 | 0.047025 |  | 6732 | 23.875 | 99.3 | 14.696 | 0.070978 | 0.047025
6733 | 99.31 | 14.696 | 0.070977 | 23.877 | 0.047029 |  | 6733 | 23.877 | 99.31 | 14.696 | 0.070977 | 0.047029
6734 | 99.32 | 14.696 | 0.070975 | 23.88 | 0.047033 |  | 6734 | 23.88 | 99.32 | 14.696 | 0.070975 | 0.047033
6735 | 99.33 | 14.696 | 0.070974 | 23.882 | 0.047037 |  | 6735 | 23.882 | 99.33 | 14.696 | 0.070974 | 0.047037
6736 | 99.34 | 14.696 | 0.070973 | 23.885 | 0.047042 |  | 6736 | 23.885 | 99.34 | 14.696 | 0.070973 | 0.047042
6737 | 99.35 | 14.696 | 0.070971 | 23.887 | 0.047046 |  | 6737 | 23.887 | 99.35 | 14.696 | 0.070971 | 0.047046
6738 | 99.36 | 14.696 | 0.07097 | 23.889 | 0.04705 |  | 6738 | 23.889 | 99.36 | 14.696 | 0.07097 | 0.04705
6739 | 99.37 | 14.696 | 0.070969 | 23.892 | 0.047055 |  | 6739 | 23.892 | 99.37 | 14.696 | 0.070969 | 0.047055
6740 | 99.38 | 14.696 | 0.070968 | 23.894 | 0.047059 |  | 6740 | 23.894 | 99.38 | 14.696 | 0.070968 | 0.047059
6741 | 99.39 | 14.696 | 0.070966 | 23.897 | 0.047063 |  | 6741 | 23.897 | 99.39 | 14.696 | 0.070966 | 0.047063
6742 | 99.4 | 14.696 | 0.070965 | 23.899 | 0.047068 |  | 6742 | 23.899 | 99.4 | 14.696 | 0.070965 | 0.047068
6743 | 99.41 | 14.696 | 0.070964 | 23.901 | 0.047072 |  | 6743 | 23.901 | 99.41 | 14.696 | 0.070964 | 0.047072
6744 | 99.42 | 14.696 | 0.070963 | 23.904 | 0.047076 |  | 6744 | 23.904 | 99.42 | 14.696 | 0.070963 | 0.047076
6745 | 99.43 | 14.696 | 0.070961 | 23.906 | 0.04708 |  | 6745 | 23.906 | 99.43 | 14.696 | 0.070961 | 0.04708
6746 | 99.44 | 14.696 | 0.07096 | 23.909 | 0.047085 |  | 6746 | 23.909 | 99.44 | 14.696 | 0.07096 | 0.047085
6747 | 99.45 | 14.696 | 0.070959 | 23.911 | 0.047089 |  | 6747 | 23.911 | 99.45 | 14.696 | 0.070959 | 0.047089
6748 | 99.46 | 14.696 | 0.070957 | 23.913 | 0.047093 |  | 6748 | 23.913 | 99.46 | 14.696 | 0.070957 | 0.047093
6749 | 99.47 | 14.696 | 0.070956 | 23.916 | 0.047098 |  | 6749 | 23.916 | 99.47 | 14.696 | 0.070956 | 0.047098
6750 | 99.48 | 14.696 | 0.070955 | 23.918 | 0.047102 |  | 6750 | 23.918 | 99.48 | 14.696 | 0.070955 | 0.047102
6751 | 99.49 | 14.696 | 0.070954 | 23.921 | 0.047106 |  | 6751 | 23.921 | 99.49 | 14.696 | 0.070954 | 0.047106
6752 | 99.5 | 14.696 | 0.070952 | 23.923 | 0.047111 |  | 6752 | 23.923 | 99.5 | 14.696 | 0.070952 | 0.047111
6753 | 99.51 | 14.696 | 0.070951 | 23.925 | 0.047115 |  | 6753 | 23.925 | 99.51 | 14.696 | 0.070951 | 0.047115
6754 | 99.52 | 14.696 | 0.07095 | 23.928 | 0.047119 |  | 6754 | 23.928 | 99.52 | 14.696 | 0.07095 | 0.047119
6755 | 99.53 | 14.696 | 0.070949 | 23.93 | 0.047124 |  | 6755 | 23.93 | 99.53 | 14.696 | 0.070949 | 0.047124
6756 | 99.54 | 14.696 | 0.070947 | 23.933 | 0.047128 |  | 6756 | 23.933 | 99.54 | 14.696 | 0.070947 | 0.047128
6757 | 99.55 | 14.696 | 0.070946 | 23.935 | 0.047132 |  | 6757 | 23.935 | 99.55 | 14.696 | 0.070946 | 0.047132
6758 | 99.56 | 14.696 | 0.070945 | 23.938 | 0.047136 |  | 6758 | 23.938 | 99.56 | 14.696 | 0.070945 | 0.047136
6759 | 99.57 | 14.696 | 0.070944 | 23.94 | 0.047141 |  | 6759 | 23.94 | 99.57 | 14.696 | 0.070944 | 0.047141
6760 | 99.58 | 14.696 | 0.070942 | 23.942 | 0.047145 |  | 6760 | 23.942 | 99.58 | 14.696 | 0.070942 | 0.047145
6761 | 99.59 | 14.696 | 0.070941 | 23.945 | 0.047149 |  | 6761 | 23.945 | 99.59 | 14.696 | 0.070941 | 0.047149
6762 | 99.6 | 14.696 | 0.07094 | 23.947 | 0.047154 |  | 6762 | 23.947 | 99.6 | 14.696 | 0.07094 | 0.047154
6763 | 99.61 | 14.696 | 0.070938 | 23.95 | 0.047158 |  | 6763 | 23.95 | 99.61 | 14.696 | 0.070938 | 0.047158
6764 | 99.62 | 14.696 | 0.070937 | 23.952 | 0.047162 |  | 6764 | 23.952 | 99.62 | 14.696 | 0.070937 | 0.047162
6765 | 99.63 | 14.696 | 0.070936 | 23.954 | 0.047167 |  | 6765 | 23.954 | 99.63 | 14.696 | 0.070936 | 0.047167
6766 | 99.64 | 14.696 | 0.070935 | 23.957 | 0.047171 |  | 6766 | 23.957 | 99.64 | 14.696 | 0.070935 | 0.047171
6767 | 99.65 | 14.696 | 0.070933 | 23.959 | 0.047175 |  | 6767 | 23.959 | 99.65 | 14.696 | 0.070933 | 0.047175
6768 | 99.66 | 14.696 | 0.070932 | 23.962 | 0.047179 |  | 6768 | 23.962 | 99.66 | 14.696 | 0.070932 | 0.047179
6769 | 99.67 | 14.696 | 0.070931 | 23.964 | 0.047184 |  | 6769 | 23.964 | 99.67 | 14.696 | 0.070931 | 0.047184
6770 | 99.68 | 14.696 | 0.07093 | 23.966 | 0.047188 |  | 6770 | 23.966 | 99.68 | 14.696 | 0.07093 | 0.047188
6771 | 99.69 | 14.696 | 0.070928 | 23.969 | 0.047192 |  | 6771 | 23.969 | 99.69 | 14.696 | 0.070928 | 0.047192
6772 | 99.7 | 14.696 | 0.070927 | 23.971 | 0.047197 |  | 6772 | 23.971 | 99.7 | 14.696 | 0.070927 | 0.047197
6773 | 99.71 | 14.696 | 0.070926 | 23.974 | 0.047201 |  | 6773 | 23.974 | 99.71 | 14.696 | 0.070926 | 0.047201
6774 | 99.72 | 14.696 | 0.070924 | 23.976 | 0.047205 |  | 6774 | 23.976 | 99.72 | 14.696 | 0.070924 | 0.047205
6775 | 99.73 | 14.696 | 0.070923 | 23.978 | 0.04721 |  | 6775 | 23.978 | 99.73 | 14.696 | 0.070923 | 0.04721
6776 | 99.74 | 14.696 | 0.070922 | 23.981 | 0.047214 |  | 6776 | 23.981 | 99.74 | 14.696 | 0.070922 | 0.047214
6777 | 99.75 | 14.696 | 0.070921 | 23.983 | 0.047218 |  | 6777 | 23.983 | 99.75 | 14.696 | 0.070921 | 0.047218
6778 | 99.76 | 14.696 | 0.070919 | 23.986 | 0.047222 |  | 6778 | 23.986 | 99.76 | 14.696 | 0.070919 | 0.047222
6779 | 99.77 | 14.696 | 0.070918 | 23.988 | 0.047227 |  | 6779 | 23.988 | 99.77 | 14.696 | 0.070918 | 0.047227
6780 | 99.78 | 14.696 | 0.070917 | 23.99 | 0.047231 |  | 6780 | 23.99 | 99.78 | 14.696 | 0.070917 | 0.047231
6781 | 99.79 | 14.696 | 0.070916 | 23.993 | 0.047235 |  | 6781 | 23.993 | 99.79 | 14.696 | 0.070916 | 0.047235
6782 | 99.8 | 14.696 | 0.070914 | 23.995 | 0.04724 |  | 6782 | 23.995 | 99.8 | 14.696 | 0.070914 | 0.04724
6783 | 99.81 | 14.696 | 0.070913 | 23.998 | 0.047244 |  | 6783 | 23.998 | 99.81 | 14.696 | 0.070913 | 0.047244
6784 | 99.82 | 14.696 | 0.070912 | 24 | 0.047248 |  | 6784 | 24 | 99.82 | 14.696 | 0.070912 | 0.047248
6785 | 99.83 | 14.696 | 0.07091 | 24.002 | 0.047253 |  | 6785 | 24.002 | 99.83 | 14.696 | 0.07091 | 0.047253
6786 | 99.84 | 14.696 | 0.070909 | 24.005 | 0.047257 |  | 6786 | 24.005 | 99.84 | 14.696 | 0.070909 | 0.047257
6787 | 99.85 | 14.696 | 0.070908 | 24.007 | 0.047261 |  | 6787 | 24.007 | 99.85 | 14.696 | 0.070908 | 0.047261
6788 | 99.86 | 14.696 | 0.070907 | 24.01 | 0.047265 |  | 6788 | 24.01 | 99.86 | 14.696 | 0.070907 | 0.047265
6789 | 99.87 | 14.696 | 0.070905 | 24.012 | 0.04727 |  | 6789 | 24.012 | 99.87 | 14.696 | 0.070905 | 0.04727
6790 | 99.88 | 14.696 | 0.070904 | 24.015 | 0.047274 |  | 6790 | 24.015 | 99.88 | 14.696 | 0.070904 | 0.047274
6791 | 99.89 | 14.696 | 0.070903 | 24.017 | 0.047278 |  | 6791 | 24.017 | 99.89 | 14.696 | 0.070903 | 0.047278
6792 | 99.9 | 14.696 | 0.070902 | 24.019 | 0.047283 |  | 6792 | 24.019 | 99.9 | 14.696 | 0.070902 | 0.047283
6793 | 99.91 | 14.696 | 0.0709 | 24.022 | 0.047287 |  | 6793 | 24.022 | 99.91 | 14.696 | 0.0709 | 0.047287
6794 | 99.92 | 14.696 | 0.070899 | 24.024 | 0.047291 |  | 6794 | 24.024 | 99.92 | 14.696 | 0.070899 | 0.047291
6795 | 99.93 | 14.696 | 0.070898 | 24.027 | 0.047296 |  | 6795 | 24.027 | 99.93 | 14.696 | 0.070898 | 0.047296
6796 | 99.94 | 14.696 | 0.070896 | 24.029 | 0.0473 |  | 6796 | 24.029 | 99.94 | 14.696 | 0.070896 | 0.0473
6797 | 99.95 | 14.696 | 0.070895 | 24.031 | 0.047304 |  | 6797 | 24.031 | 99.95 | 14.696 | 0.070895 | 0.047304
6798 | 99.96 | 14.696 | 0.070894 | 24.034 | 0.047308 |  | 6798 | 24.034 | 99.96 | 14.696 | 0.070894 | 0.047308
6799 | 99.97 | 14.696 | 0.070893 | 24.036 | 0.047313 |  | 6799 | 24.036 | 99.97 | 14.696 | 0.070893 | 0.047313
6800 | 99.98 | 14.696 | 0.070891 | 24.039 | 0.047317 |  | 6800 | 24.039 | 99.98 | 14.696 | 0.070891 | 0.047317
6801 | 99.99 | 14.696 | 0.07089 | 24.041 | 0.047321 |  | 6801 | 24.041 | 99.99 | 14.696 | 0.07089 | 0.047321
6802 | 100 | 14.696 | 0.070889 | 24.043 | 0.047326 |  | 6802 | 24.043 | 100 | 14.696 | 0.070889 | 0.047326
6803 | 100.01 | 14.696 | 0.070888 | 24.046 | 0.04733 |  | 6803 | 24.046 | 100.01 | 14.696 | 0.070888 | 0.04733
6804 | 100.02 | 14.696 | 0.070886 | 24.048 | 0.047334 |  | 6804 | 24.048 | 100.02 | 14.696 | 0.070886 | 0.047334
6805 | 100.03 | 14.696 | 0.070885 | 24.051 | 0.047339 |  | 6805 | 24.051 | 100.03 | 14.696 | 0.070885 | 0.047339
6806 | 100.04 | 14.696 | 0.070884 | 24.053 | 0.047343 |  | 6806 | 24.053 | 100.04 | 14.696 | 0.070884 | 0.047343
6807 | 100.05 | 14.696 | 0.070883 | 24.055 | 0.047347 |  | 6807 | 24.055 | 100.05 | 14.696 | 0.070883 | 0.047347
6808 | 100.06 | 14.696 | 0.070881 | 24.058 | 0.047351 |  | 6808 | 24.058 | 100.06 | 14.696 | 0.070881 | 0.047351
6809 | 100.07 | 14.696 | 0.07088 | 24.06 | 0.047356 |  | 6809 | 24.06 | 100.07 | 14.696 | 0.07088 | 0.047356
6810 | 100.08 | 14.696 | 0.070879 | 24.063 | 0.04736 |  | 6810 | 24.063 | 100.08 | 14.696 | 0.070879 | 0.04736
6811 | 100.09 | 14.696 | 0.070877 | 24.065 | 0.047364 |  | 6811 | 24.065 | 100.09 | 14.696 | 0.070877 | 0.047364
6812 | 100.1 | 14.696 | 0.070876 | 24.067 | 0.047369 |  | 6812 | 24.067 | 100.1 | 14.696 | 0.070876 | 0.047369
6813 | 100.11 | 14.696 | 0.070875 | 24.07 | 0.047373 |  | 6813 | 24.07 | 100.11 | 14.696 | 0.070875 | 0.047373
6814 | 100.12 | 14.696 | 0.070874 | 24.072 | 0.047377 |  | 6814 | 24.072 | 100.12 | 14.696 | 0.070874 | 0.047377
6815 | 100.13 | 14.696 | 0.070872 | 24.075 | 0.047382 |  | 6815 | 24.075 | 100.13 | 14.696 | 0.070872 | 0.047382
6816 | 100.14 | 14.696 | 0.070871 | 24.077 | 0.047386 |  | 6816 | 24.077 | 100.14 | 14.696 | 0.070871 | 0.047386
6817 | 100.15 | 14.696 | 0.07087 | 24.079 | 0.04739 |  | 6817 | 24.079 | 100.15 | 14.696 | 0.07087 | 0.04739
6818 | 100.16 | 14.696 | 0.070869 | 24.082 | 0.047394 |  | 6818 | 24.082 | 100.16 | 14.696 | 0.070869 | 0.047394
6819 | 100.17 | 14.696 | 0.070867 | 24.084 | 0.047399 |  | 6819 | 24.084 | 100.17 | 14.696 | 0.070867 | 0.047399
6820 | 100.18 | 14.696 | 0.070866 | 24.087 | 0.047403 |  | 6820 | 24.087 | 100.18 | 14.696 | 0.070866 | 0.047403
6821 | 100.19 | 14.696 | 0.070865 | 24.089 | 0.047407 |  | 6821 | 24.089 | 100.19 | 14.696 | 0.070865 | 0.047407
6822 | 100.2 | 14.696 | 0.070863 | 24.092 | 0.047412 |  | 6822 | 24.092 | 100.2 | 14.696 | 0.070863 | 0.047412
6823 | 100.21 | 14.696 | 0.070862 | 24.094 | 0.047416 |  | 6823 | 24.094 | 100.21 | 14.696 | 0.070862 | 0.047416
6824 | 100.22 | 14.696 | 0.070861 | 24.096 | 0.04742 |  | 6824 | 24.096 | 100.22 | 14.696 | 0.070861 | 0.04742
6825 | 100.23 | 14.696 | 0.07086 | 24.099 | 0.047425 |  | 6825 | 24.099 | 100.23 | 14.696 | 0.07086 | 0.047425
6826 | 100.24 | 14.696 | 0.070858 | 24.101 | 0.047429 |  | 6826 | 24.101 | 100.24 | 14.696 | 0.070858 | 0.047429
6827 | 100.25 | 14.696 | 0.070857 | 24.104 | 0.047433 |  | 6827 | 24.104 | 100.25 | 14.696 | 0.070857 | 0.047433
6828 | 100.26 | 14.696 | 0.070856 | 24.106 | 0.047437 |  | 6828 | 24.106 | 100.26 | 14.696 | 0.070856 | 0.047437
6829 | 100.27 | 14.696 | 0.070855 | 24.108 | 0.047442 |  | 6829 | 24.108 | 100.27 | 14.696 | 0.070855 | 0.047442
6830 | 100.28 | 14.696 | 0.070853 | 24.111 | 0.047446 |  | 6830 | 24.111 | 100.28 | 14.696 | 0.070853 | 0.047446
6831 | 100.29 | 14.696 | 0.070852 | 24.113 | 0.04745 |  | 6831 | 24.113 | 100.29 | 14.696 | 0.070852 | 0.04745
6832 | 100.3 | 14.696 | 0.070851 | 24.116 | 0.047455 |  | 6832 | 24.116 | 100.3 | 14.696 | 0.070851 | 0.047455
6833 | 100.31 | 14.696 | 0.07085 | 24.118 | 0.047459 |  | 6833 | 24.118 | 100.31 | 14.696 | 0.07085 | 0.047459
6834 | 100.32 | 14.696 | 0.070848 | 24.12 | 0.047463 |  | 6834 | 24.12 | 100.32 | 14.696 | 0.070848 | 0.047463
6835 | 100.33 | 14.696 | 0.070847 | 24.123 | 0.047468 |  | 6835 | 24.123 | 100.33 | 14.696 | 0.070847 | 0.047468
6836 | 100.34 | 14.696 | 0.070846 | 24.125 | 0.047472 |  | 6836 | 24.125 | 100.34 | 14.696 | 0.070846 | 0.047472
6837 | 100.35 | 14.696 | 0.070844 | 24.128 | 0.047476 |  | 6837 | 24.128 | 100.35 | 14.696 | 0.070844 | 0.047476
6838 | 100.36 | 14.696 | 0.070843 | 24.13 | 0.04748 |  | 6838 | 24.13 | 100.36 | 14.696 | 0.070843 | 0.04748
6839 | 100.37 | 14.696 | 0.070842 | 24.132 | 0.047485 |  | 6839 | 24.132 | 100.37 | 14.696 | 0.070842 | 0.047485
6840 | 100.38 | 14.696 | 0.070841 | 24.135 | 0.047489 |  | 6840 | 24.135 | 100.38 | 14.696 | 0.070841 | 0.047489
6841 | 100.39 | 14.696 | 0.070839 | 24.137 | 0.047493 |  | 6841 | 24.137 | 100.39 | 14.696 | 0.070839 | 0.047493
6842 | 100.4 | 14.696 | 0.070838 | 24.14 | 0.047498 |  | 6842 | 24.14 | 100.4 | 14.696 | 0.070838 | 0.047498
6843 | 100.41 | 14.696 | 0.070837 | 24.142 | 0.047502 |  | 6843 | 24.142 | 100.41 | 14.696 | 0.070837 | 0.047502
6844 | 100.42 | 14.696 | 0.070836 | 24.144 | 0.047506 |  | 6844 | 24.144 | 100.42 | 14.696 | 0.070836 | 0.047506
6845 | 100.43 | 14.696 | 0.070834 | 24.147 | 0.047511 |  | 6845 | 24.147 | 100.43 | 14.696 | 0.070834 | 0.047511
6846 | 100.44 | 14.696 | 0.070833 | 24.149 | 0.047515 |  | 6846 | 24.149 | 100.44 | 14.696 | 0.070833 | 0.047515
6847 | 100.45 | 14.696 | 0.070832 | 24.152 | 0.047519 |  | 6847 | 24.152 | 100.45 | 14.696 | 0.070832 | 0.047519
6848 | 100.46 | 14.696 | 0.070831 | 24.154 | 0.047523 |  | 6848 | 24.154 | 100.46 | 14.696 | 0.070831 | 0.047523
6849 | 100.47 | 14.696 | 0.070829 | 24.157 | 0.047528 |  | 6849 | 24.157 | 100.47 | 14.696 | 0.070829 | 0.047528
6850 | 100.48 | 14.696 | 0.070828 | 24.159 | 0.047532 |  | 6850 | 24.159 | 100.48 | 14.696 | 0.070828 | 0.047532
6851 | 100.49 | 14.696 | 0.070827 | 24.161 | 0.047536 |  | 6851 | 24.161 | 100.49 | 14.696 | 0.070827 | 0.047536
6852 | 100.5 | 14.696 | 0.070825 | 24.164 | 0.047541 |  | 6852 | 24.164 | 100.5 | 14.696 | 0.070825 | 0.047541
6853 | 100.51 | 14.696 | 0.070824 | 24.166 | 0.047545 |  | 6853 | 24.166 | 100.51 | 14.696 | 0.070824 | 0.047545
6854 | 100.52 | 14.696 | 0.070823 | 24.169 | 0.047549 |  | 6854 | 24.169 | 100.52 | 14.696 | 0.070823 | 0.047549
6855 | 100.53 | 14.696 | 0.070822 | 24.171 | 0.047553 |  | 6855 | 24.171 | 100.53 | 14.696 | 0.070822 | 0.047553
6856 | 100.54 | 14.696 | 0.07082 | 24.173 | 0.047558 |  | 6856 | 24.173 | 100.54 | 14.696 | 0.07082 | 0.047558
6857 | 100.55 | 14.696 | 0.070819 | 24.176 | 0.047562 |  | 6857 | 24.176 | 100.55 | 14.696 | 0.070819 | 0.047562
6858 | 100.56 | 14.696 | 0.070818 | 24.178 | 0.047566 |  | 6858 | 24.178 | 100.56 | 14.696 | 0.070818 | 0.047566
6859 | 100.57 | 14.696 | 0.070817 | 24.181 | 0.047571 |  | 6859 | 24.181 | 100.57 | 14.696 | 0.070817 | 0.047571
6860 | 100.58 | 14.696 | 0.070815 | 24.183 | 0.047575 |  | 6860 | 24.183 | 100.58 | 14.696 | 0.070815 | 0.047575
6861 | 100.59 | 14.696 | 0.070814 | 24.185 | 0.047579 |  | 6861 | 24.185 | 100.59 | 14.696 | 0.070814 | 0.047579
6862 | 100.6 | 14.696 | 0.070813 | 24.188 | 0.047584 |  | 6862 | 24.188 | 100.6 | 14.696 | 0.070813 | 0.047584
6863 | 100.61 | 14.696 | 0.070812 | 24.19 | 0.047588 |  | 6863 | 24.19 | 100.61 | 14.696 | 0.070812 | 0.047588
6864 | 100.62 | 14.696 | 0.07081 | 24.193 | 0.047592 |  | 6864 | 24.193 | 100.62 | 14.696 | 0.07081 | 0.047592
6865 | 100.63 | 14.696 | 0.070809 | 24.195 | 0.047596 |  | 6865 | 24.195 | 100.63 | 14.696 | 0.070809 | 0.047596
6866 | 100.64 | 14.696 | 0.070808 | 24.197 | 0.047601 |  | 6866 | 24.197 | 100.64 | 14.696 | 0.070808 | 0.047601
6867 | 100.65 | 14.696 | 0.070806 | 24.2 | 0.047605 |  | 6867 | 24.2 | 100.65 | 14.696 | 0.070806 | 0.047605
6868 | 100.66 | 14.696 | 0.070805 | 24.202 | 0.047609 |  | 6868 | 24.202 | 100.66 | 14.696 | 0.070805 | 0.047609
6869 | 100.67 | 14.696 | 0.070804 | 24.205 | 0.047614 |  | 6869 | 24.205 | 100.67 | 14.696 | 0.070804 | 0.047614
6870 | 100.68 | 14.696 | 0.070803 | 24.207 | 0.047618 |  | 6870 | 24.207 | 100.68 | 14.696 | 0.070803 | 0.047618
6871 | 100.69 | 14.696 | 0.070801 | 24.209 | 0.047622 |  | 6871 | 24.209 | 100.69 | 14.696 | 0.070801 | 0.047622
6872 | 100.7 | 14.696 | 0.0708 | 24.212 | 0.047626 |  | 6872 | 24.212 | 100.7 | 14.696 | 0.0708 | 0.047626
6873 | 100.71 | 14.696 | 0.070799 | 24.214 | 0.047631 |  | 6873 | 24.214 | 100.71 | 14.696 | 0.070799 | 0.047631
6874 | 100.72 | 14.696 | 0.070798 | 24.217 | 0.047635 |  | 6874 | 24.217 | 100.72 | 14.696 | 0.070798 | 0.047635
6875 | 100.73 | 14.696 | 0.070796 | 24.219 | 0.047639 |  | 6875 | 24.219 | 100.73 | 14.696 | 0.070796 | 0.047639
6876 | 100.74 | 14.696 | 0.070795 | 24.221 | 0.047644 |  | 6876 | 24.221 | 100.74 | 14.696 | 0.070795 | 0.047644
6877 | 100.75 | 14.696 | 0.070794 | 24.224 | 0.047648 |  | 6877 | 24.224 | 100.75 | 14.696 | 0.070794 | 0.047648
6878 | 100.76 | 14.696 | 0.070793 | 24.226 | 0.047652 |  | 6878 | 24.226 | 100.76 | 14.696 | 0.070793 | 0.047652
6879 | 100.77 | 14.696 | 0.070791 | 24.229 | 0.047657 |  | 6879 | 24.229 | 100.77 | 14.696 | 0.070791 | 0.047657
6880 | 100.78 | 14.696 | 0.07079 | 24.231 | 0.047661 |  | 6880 | 24.231 | 100.78 | 14.696 | 0.07079 | 0.047661
6881 | 100.79 | 14.696 | 0.070789 | 24.234 | 0.047665 |  | 6881 | 24.234 | 100.79 | 14.696 | 0.070789 | 0.047665
6882 | 100.8 | 14.696 | 0.070787 | 24.236 | 0.047669 |  | 6882 | 24.236 | 100.8 | 14.696 | 0.070787 | 0.047669
6883 | 100.81 | 14.696 | 0.070786 | 24.238 | 0.047674 |  | 6883 | 24.238 | 100.81 | 14.696 | 0.070786 | 0.047674
6884 | 100.82 | 14.696 | 0.070785 | 24.241 | 0.047678 |  | 6884 | 24.241 | 100.82 | 14.696 | 0.070785 | 0.047678
6885 | 100.83 | 14.696 | 0.070784 | 24.243 | 0.047682 |  | 6885 | 24.243 | 100.83 | 14.696 | 0.070784 | 0.047682
6886 | 100.84 | 14.696 | 0.070782 | 24.246 | 0.047687 |  | 6886 | 24.246 | 100.84 | 14.696 | 0.070782 | 0.047687
6887 | 100.85 | 14.696 | 0.070781 | 24.248 | 0.047691 |  | 6887 | 24.248 | 100.85 | 14.696 | 0.070781 | 0.047691
6888 | 100.86 | 14.696 | 0.07078 | 24.25 | 0.047695 |  | 6888 | 24.25 | 100.86 | 14.696 | 0.07078 | 0.047695
6889 | 100.87 | 14.696 | 0.070779 | 24.253 | 0.047699 |  | 6889 | 24.253 | 100.87 | 14.696 | 0.070779 | 0.047699
6890 | 100.88 | 14.696 | 0.070777 | 24.255 | 0.047704 |  | 6890 | 24.255 | 100.88 | 14.696 | 0.070777 | 0.047704
6891 | 100.89 | 14.696 | 0.070776 | 24.258 | 0.047708 |  | 6891 | 24.258 | 100.89 | 14.696 | 0.070776 | 0.047708
6892 | 100.9 | 14.696 | 0.070775 | 24.26 | 0.047712 |  | 6892 | 24.26 | 100.9 | 14.696 | 0.070775 | 0.047712
6893 | 100.91 | 14.696 | 0.070774 | 24.262 | 0.047717 |  | 6893 | 24.262 | 100.91 | 14.696 | 0.070774 | 0.047717
6894 | 100.92 | 14.696 | 0.070772 | 24.265 | 0.047721 |  | 6894 | 24.265 | 100.92 | 14.696 | 0.070772 | 0.047721
6895 | 100.93 | 14.696 | 0.070771 | 24.267 | 0.047725 |  | 6895 | 24.267 | 100.93 | 14.696 | 0.070771 | 0.047725
6896 | 100.94 | 14.696 | 0.07077 | 24.27 | 0.04773 |  | 6896 | 24.27 | 100.94 | 14.696 | 0.07077 | 0.04773
6897 | 100.95 | 14.696 | 0.070768 | 24.272 | 0.047734 |  | 6897 | 24.272 | 100.95 | 14.696 | 0.070768 | 0.047734
6898 | 100.96 | 14.696 | 0.070767 | 24.274 | 0.047738 |  | 6898 | 24.274 | 100.96 | 14.696 | 0.070767 | 0.047738
6899 | 100.97 | 14.696 | 0.070766 | 24.277 | 0.047742 |  | 6899 | 24.277 | 100.97 | 14.696 | 0.070766 | 0.047742
6900 | 100.98 | 14.696 | 0.070765 | 24.279 | 0.047747 |  | 6900 | 24.279 | 100.98 | 14.696 | 0.070765 | 0.047747
6901 | 100.99 | 14.696 | 0.070763 | 24.282 | 0.047751 |  | 6901 | 24.282 | 100.99 | 14.696 | 0.070763 | 0.047751
6902 | 101 | 14.696 | 0.070762 | 24.284 | 0.047755 |  | 6902 | 24.284 | 101 | 14.696 | 0.070762 | 0.047755
6903 | 101.01 | 14.696 | 0.070761 | 24.286 | 0.04776 |  | 6903 | 24.286 | 101.01 | 14.696 | 0.070761 | 0.04776
6904 | 101.02 | 14.696 | 0.07076 | 24.289 | 0.047764 |  | 6904 | 24.289 | 101.02 | 14.696 | 0.07076 | 0.047764
6905 | 101.03 | 14.696 | 0.070758 | 24.291 | 0.047768 |  | 6905 | 24.291 | 101.03 | 14.696 | 0.070758 | 0.047768
6906 | 101.04 | 14.696 | 0.070757 | 24.294 | 0.047772 |  | 6906 | 24.294 | 101.04 | 14.696 | 0.070757 | 0.047772
6907 | 101.05 | 14.696 | 0.070756 | 24.296 | 0.047777 |  | 6907 | 24.296 | 101.05 | 14.696 | 0.070756 | 0.047777
6908 | 101.06 | 14.696 | 0.070755 | 24.298 | 0.047781 |  | 6908 | 24.298 | 101.06 | 14.696 | 0.070755 | 0.047781
6909 | 101.07 | 14.696 | 0.070753 | 24.301 | 0.047785 |  | 6909 | 24.301 | 101.07 | 14.696 | 0.070753 | 0.047785
6910 | 101.08 | 14.696 | 0.070752 | 24.303 | 0.04779 |  | 6910 | 24.303 | 101.08 | 14.696 | 0.070752 | 0.04779
6911 | 101.09 | 14.696 | 0.070751 | 24.306 | 0.047794 |  | 6911 | 24.306 | 101.09 | 14.696 | 0.070751 | 0.047794
6912 | 101.1 | 14.696 | 0.070749 | 24.308 | 0.047798 |  | 6912 | 24.308 | 101.1 | 14.696 | 0.070749 | 0.047798
6913 | 101.11 | 14.696 | 0.070748 | 24.311 | 0.047802 |  | 6913 | 24.311 | 101.11 | 14.696 | 0.070748 | 0.047802
6914 | 101.12 | 14.696 | 0.070747 | 24.313 | 0.047807 |  | 6914 | 24.313 | 101.12 | 14.696 | 0.070747 | 0.047807
6915 | 101.13 | 14.696 | 0.070746 | 24.315 | 0.047811 |  | 6915 | 24.315 | 101.13 | 14.696 | 0.070746 | 0.047811
6916 | 101.14 | 14.696 | 0.070744 | 24.318 | 0.047815 |  | 6916 | 24.318 | 101.14 | 14.696 | 0.070744 | 0.047815
6917 | 101.15 | 14.696 | 0.070743 | 24.32 | 0.04782 |  | 6917 | 24.32 | 101.15 | 14.696 | 0.070743 | 0.04782
6918 | 101.16 | 14.696 | 0.070742 | 24.323 | 0.047824 |  | 6918 | 24.323 | 101.16 | 14.696 | 0.070742 | 0.047824
6919 | 101.17 | 14.696 | 0.070741 | 24.325 | 0.047828 |  | 6919 | 24.325 | 101.17 | 14.696 | 0.070741 | 0.047828
6920 | 101.18 | 14.696 | 0.070739 | 24.327 | 0.047833 |  | 6920 | 24.327 | 101.18 | 14.696 | 0.070739 | 0.047833
6921 | 101.19 | 14.696 | 0.070738 | 24.33 | 0.047837 |  | 6921 | 24.33 | 101.19 | 14.696 | 0.070738 | 0.047837
6922 | 101.2 | 14.696 | 0.070737 | 24.332 | 0.047841 |  | 6922 | 24.332 | 101.2 | 14.696 | 0.070737 | 0.047841
6923 | 101.21 | 14.696 | 0.070736 | 24.335 | 0.047845 |  | 6923 | 24.335 | 101.21 | 14.696 | 0.070736 | 0.047845
6924 | 101.22 | 14.696 | 0.070734 | 24.337 | 0.04785 |  | 6924 | 24.337 | 101.22 | 14.696 | 0.070734 | 0.04785
6925 | 101.23 | 14.696 | 0.070733 | 24.339 | 0.047854 |  | 6925 | 24.339 | 101.23 | 14.696 | 0.070733 | 0.047854
6926 | 101.24 | 14.696 | 0.070732 | 24.342 | 0.047858 |  | 6926 | 24.342 | 101.24 | 14.696 | 0.070732 | 0.047858
6927 | 101.25 | 14.696 | 0.070731 | 24.344 | 0.047863 |  | 6927 | 24.344 | 101.25 | 14.696 | 0.070731 | 0.047863
6928 | 101.26 | 14.696 | 0.070729 | 24.347 | 0.047867 |  | 6928 | 24.347 | 101.26 | 14.696 | 0.070729 | 0.047867
6929 | 101.27 | 14.696 | 0.070728 | 24.349 | 0.047871 |  | 6929 | 24.349 | 101.27 | 14.696 | 0.070728 | 0.047871
6930 | 101.28 | 14.696 | 0.070727 | 24.351 | 0.047875 |  | 6930 | 24.351 | 101.28 | 14.696 | 0.070727 | 0.047875
6931 | 101.29 | 14.696 | 0.070725 | 24.354 | 0.04788 |  | 6931 | 24.354 | 101.29 | 14.696 | 0.070725 | 0.04788
6932 | 101.3 | 14.696 | 0.070724 | 24.356 | 0.047884 |  | 6932 | 24.356 | 101.3 | 14.696 | 0.070724 | 0.047884
6933 | 101.31 | 14.696 | 0.070723 | 24.359 | 0.047888 |  | 6933 | 24.359 | 101.31 | 14.696 | 0.070723 | 0.047888
6934 | 101.32 | 14.696 | 0.070722 | 24.361 | 0.047893 |  | 6934 | 24.361 | 101.32 | 14.696 | 0.070722 | 0.047893
6935 | 101.33 | 14.696 | 0.07072 | 24.363 | 0.047897 |  | 6935 | 24.363 | 101.33 | 14.696 | 0.07072 | 0.047897
6936 | 101.34 | 14.696 | 0.070719 | 24.366 | 0.047901 |  | 6936 | 24.366 | 101.34 | 14.696 | 0.070719 | 0.047901
6937 | 101.35 | 14.696 | 0.070718 | 24.368 | 0.047905 |  | 6937 | 24.368 | 101.35 | 14.696 | 0.070718 | 0.047905
6938 | 101.36 | 14.696 | 0.070717 | 24.371 | 0.04791 |  | 6938 | 24.371 | 101.36 | 14.696 | 0.070717 | 0.04791
6939 | 101.37 | 14.696 | 0.070715 | 24.373 | 0.047914 |  | 6939 | 24.373 | 101.37 | 14.696 | 0.070715 | 0.047914
6940 | 101.38 | 14.696 | 0.070714 | 24.375 | 0.047918 |  | 6940 | 24.375 | 101.38 | 14.696 | 0.070714 | 0.047918
6941 | 101.39 | 14.696 | 0.070713 | 24.378 | 0.047923 |  | 6941 | 24.378 | 101.39 | 14.696 | 0.070713 | 0.047923
6942 | 101.4 | 14.696 | 0.070712 | 24.38 | 0.047927 |  | 6942 | 24.38 | 101.4 | 14.696 | 0.070712 | 0.047927
6943 | 101.41 | 14.696 | 0.07071 | 24.383 | 0.047931 |  | 6943 | 24.383 | 101.41 | 14.696 | 0.07071 | 0.047931
6944 | 101.42 | 14.696 | 0.070709 | 24.385 | 0.047935 |  | 6944 | 24.385 | 101.42 | 14.696 | 0.070709 | 0.047935
6945 | 101.43 | 14.696 | 0.070708 | 24.388 | 0.04794 |  | 6945 | 24.388 | 101.43 | 14.696 | 0.070708 | 0.04794
6946 | 101.44 | 14.696 | 0.070707 | 24.39 | 0.047944 |  | 6946 | 24.39 | 101.44 | 14.696 | 0.070707 | 0.047944
6947 | 101.45 | 14.696 | 0.070705 | 24.392 | 0.047948 |  | 6947 | 24.392 | 101.45 | 14.696 | 0.070705 | 0.047948
6948 | 101.46 | 14.696 | 0.070704 | 24.395 | 0.047953 |  | 6948 | 24.395 | 101.46 | 14.696 | 0.070704 | 0.047953
6949 | 101.47 | 14.696 | 0.070703 | 24.397 | 0.047957 |  | 6949 | 24.397 | 101.47 | 14.696 | 0.070703 | 0.047957
6950 | 101.48 | 14.696 | 0.070701 | 24.4 | 0.047961 |  | 6950 | 24.4 | 101.48 | 14.696 | 0.070701 | 0.047961
6951 | 101.49 | 14.696 | 0.0707 | 24.402 | 0.047965 |  | 6951 | 24.402 | 101.49 | 14.696 | 0.0707 | 0.047965
6952 | 101.5 | 14.696 | 0.070699 | 24.404 | 0.04797 |  | 6952 | 24.404 | 101.5 | 14.696 | 0.070699 | 0.04797
6953 | 101.51 | 14.696 | 0.070698 | 24.407 | 0.047974 |  | 6953 | 24.407 | 101.51 | 14.696 | 0.070698 | 0.047974
6954 | 101.52 | 14.696 | 0.070696 | 24.409 | 0.047978 |  | 6954 | 24.409 | 101.52 | 14.696 | 0.070696 | 0.047978
6955 | 101.53 | 14.696 | 0.070695 | 24.412 | 0.047983 |  | 6955 | 24.412 | 101.53 | 14.696 | 0.070695 | 0.047983
6956 | 101.54 | 14.696 | 0.070694 | 24.414 | 0.047987 |  | 6956 | 24.414 | 101.54 | 14.696 | 0.070694 | 0.047987
6957 | 101.55 | 14.696 | 0.070693 | 24.416 | 0.047991 |  | 6957 | 24.416 | 101.55 | 14.696 | 0.070693 | 0.047991
6958 | 101.56 | 14.696 | 0.070691 | 24.419 | 0.047996 |  | 6958 | 24.419 | 101.56 | 14.696 | 0.070691 | 0.047996
6959 | 101.57 | 14.696 | 0.07069 | 24.421 | 0.048 |  | 6959 | 24.421 | 101.57 | 14.696 | 0.07069 | 0.048
6960 | 101.58 | 14.696 | 0.070689 | 24.424 | 0.048004 |  | 6960 | 24.424 | 101.58 | 14.696 | 0.070689 | 0.048004
6961 | 101.59 | 14.696 | 0.070688 | 24.426 | 0.048008 |  | 6961 | 24.426 | 101.59 | 14.696 | 0.070688 | 0.048008
6962 | 101.6 | 14.696 | 0.070686 | 24.428 | 0.048013 |  | 6962 | 24.428 | 101.6 | 14.696 | 0.070686 | 0.048013
6963 | 101.61 | 14.696 | 0.070685 | 24.431 | 0.048017 |  | 6963 | 24.431 | 101.61 | 14.696 | 0.070685 | 0.048017
6964 | 101.62 | 14.696 | 0.070684 | 24.433 | 0.048021 |  | 6964 | 24.433 | 101.62 | 14.696 | 0.070684 | 0.048021
6965 | 101.63 | 14.696 | 0.070683 | 24.436 | 0.048026 |  | 6965 | 24.436 | 101.63 | 14.696 | 0.070683 | 0.048026
6966 | 101.64 | 14.696 | 0.070681 | 24.438 | 0.04803 |  | 6966 | 24.438 | 101.64 | 14.696 | 0.070681 | 0.04803
6967 | 101.65 | 14.696 | 0.07068 | 24.44 | 0.048034 |  | 6967 | 24.44 | 101.65 | 14.696 | 0.07068 | 0.048034
6968 | 101.66 | 14.696 | 0.070679 | 24.443 | 0.048038 |  | 6968 | 24.443 | 101.66 | 14.696 | 0.070679 | 0.048038
6969 | 101.67 | 14.696 | 0.070677 | 24.445 | 0.048043 |  | 6969 | 24.445 | 101.67 | 14.696 | 0.070677 | 0.048043
6970 | 101.68 | 14.696 | 0.070676 | 24.448 | 0.048047 |  | 6970 | 24.448 | 101.68 | 14.696 | 0.070676 | 0.048047
6971 | 101.69 | 14.696 | 0.070675 | 24.45 | 0.048051 |  | 6971 | 24.45 | 101.69 | 14.696 | 0.070675 | 0.048051
6972 | 101.7 | 14.696 | 0.070674 | 24.452 | 0.048056 |  | 6972 | 24.452 | 101.7 | 14.696 | 0.070674 | 0.048056
6973 | 101.71 | 14.696 | 0.070672 | 24.455 | 0.04806 |  | 6973 | 24.455 | 101.71 | 14.696 | 0.070672 | 0.04806
6974 | 101.72 | 14.696 | 0.070671 | 24.457 | 0.048064 |  | 6974 | 24.457 | 101.72 | 14.696 | 0.070671 | 0.048064
6975 | 101.73 | 14.696 | 0.07067 | 24.46 | 0.048068 |  | 6975 | 24.46 | 101.73 | 14.696 | 0.07067 | 0.048068
6976 | 101.74 | 14.696 | 0.070669 | 24.462 | 0.048073 |  | 6976 | 24.462 | 101.74 | 14.696 | 0.070669 | 0.048073
6977 | 101.75 | 14.696 | 0.070667 | 24.465 | 0.048077 |  | 6977 | 24.465 | 101.75 | 14.696 | 0.070667 | 0.048077
6978 | 101.76 | 14.696 | 0.070666 | 24.467 | 0.048081 |  | 6978 | 24.467 | 101.76 | 14.696 | 0.070666 | 0.048081
6979 | 101.77 | 14.696 | 0.070665 | 24.469 | 0.048086 |  | 6979 | 24.469 | 101.77 | 14.696 | 0.070665 | 0.048086
6980 | 101.78 | 14.696 | 0.070664 | 24.472 | 0.04809 |  | 6980 | 24.472 | 101.78 | 14.696 | 0.070664 | 0.04809
6981 | 101.79 | 14.696 | 0.070662 | 24.474 | 0.048094 |  | 6981 | 24.474 | 101.79 | 14.696 | 0.070662 | 0.048094
6982 | 101.8 | 14.696 | 0.070661 | 24.477 | 0.048098 |  | 6982 | 24.477 | 101.8 | 14.696 | 0.070661 | 0.048098
6983 | 101.81 | 14.696 | 0.07066 | 24.479 | 0.048103 |  | 6983 | 24.479 | 101.81 | 14.696 | 0.07066 | 0.048103
6984 | 101.82 | 14.696 | 0.070659 | 24.481 | 0.048107 |  | 6984 | 24.481 | 101.82 | 14.696 | 0.070659 | 0.048107
6985 | 101.83 | 14.696 | 0.070657 | 24.484 | 0.048111 |  | 6985 | 24.484 | 101.83 | 14.696 | 0.070657 | 0.048111
6986 | 101.84 | 14.696 | 0.070656 | 24.486 | 0.048116 |  | 6986 | 24.486 | 101.84 | 14.696 | 0.070656 | 0.048116
6987 | 101.85 | 14.696 | 0.070655 | 24.489 | 0.04812 |  | 6987 | 24.489 | 101.85 | 14.696 | 0.070655 | 0.04812
6988 | 101.86 | 14.696 | 0.070653 | 24.491 | 0.048124 |  | 6988 | 24.491 | 101.86 | 14.696 | 0.070653 | 0.048124
6989 | 101.87 | 14.696 | 0.070652 | 24.493 | 0.048128 |  | 6989 | 24.493 | 101.87 | 14.696 | 0.070652 | 0.048128
6990 | 101.88 | 14.696 | 0.070651 | 24.496 | 0.048133 |  | 6990 | 24.496 | 101.88 | 14.696 | 0.070651 | 0.048133
6991 | 101.89 | 14.696 | 0.07065 | 24.498 | 0.048137 |  | 6991 | 24.498 | 101.89 | 14.696 | 0.07065 | 0.048137
6992 | 101.9 | 14.696 | 0.070648 | 24.501 | 0.048141 |  | 6992 | 24.501 | 101.9 | 14.696 | 0.070648 | 0.048141
6993 | 101.91 | 14.696 | 0.070647 | 24.503 | 0.048146 |  | 6993 | 24.503 | 101.91 | 14.696 | 0.070647 | 0.048146
6994 | 101.92 | 14.696 | 0.070646 | 24.505 | 0.04815 |  | 6994 | 24.505 | 101.92 | 14.696 | 0.070646 | 0.04815
6995 | 101.93 | 14.696 | 0.070645 | 24.508 | 0.048154 |  | 6995 | 24.508 | 101.93 | 14.696 | 0.070645 | 0.048154
6996 | 101.94 | 14.696 | 0.070643 | 24.51 | 0.048158 |  | 6996 | 24.51 | 101.94 | 14.696 | 0.070643 | 0.048158
6997 | 101.95 | 14.696 | 0.070642 | 24.513 | 0.048163 |  | 6997 | 24.513 | 101.95 | 14.696 | 0.070642 | 0.048163
6998 | 101.96 | 14.696 | 0.070641 | 24.515 | 0.048167 |  | 6998 | 24.515 | 101.96 | 14.696 | 0.070641 | 0.048167
6999 | 101.97 | 14.696 | 0.07064 | 24.517 | 0.048171 |  | 6999 | 24.517 | 101.97 | 14.696 | 0.07064 | 0.048171
7000 | 101.98 | 14.696 | 0.070638 | 24.52 | 0.048176 |  | 7000 | 24.52 | 101.98 | 14.696 | 0.070638 | 0.048176
7001 | 101.99 | 14.696 | 0.070637 | 24.522 | 0.04818 |  | 7001 | 24.522 | 101.99 | 14.696 | 0.070637 | 0.04818
7002 | 102 | 14.696 | 0.070636 | 24.525 | 0.048184 |  | 7002 | 24.525 | 102 | 14.696 | 0.070636 | 0.048184
7003 | 102.01 | 14.696 | 0.070635 | 24.527 | 0.048188 |  | 7003 | 24.527 | 102.01 | 14.696 | 0.070635 | 0.048188
7004 | 102.02 | 14.696 | 0.070633 | 24.529 | 0.048193 |  | 7004 | 24.529 | 102.02 | 14.696 | 0.070633 | 0.048193
7005 | 102.03 | 14.696 | 0.070632 | 24.532 | 0.048197 |  | 7005 | 24.532 | 102.03 | 14.696 | 0.070632 | 0.048197
7006 | 102.04 | 14.696 | 0.070631 | 24.534 | 0.048201 |  | 7006 | 24.534 | 102.04 | 14.696 | 0.070631 | 0.048201
7007 | 102.05 | 14.696 | 0.07063 | 24.537 | 0.048206 |  | 7007 | 24.537 | 102.05 | 14.696 | 0.07063 | 0.048206
7008 | 102.06 | 14.696 | 0.070628 | 24.539 | 0.04821 |  | 7008 | 24.539 | 102.06 | 14.696 | 0.070628 | 0.04821
7009 | 102.07 | 14.696 | 0.070627 | 24.542 | 0.048214 |  | 7009 | 24.542 | 102.07 | 14.696 | 0.070627 | 0.048214
7010 | 102.08 | 14.696 | 0.070626 | 24.544 | 0.048218 |  | 7010 | 24.544 | 102.08 | 14.696 | 0.070626 | 0.048218
7011 | 102.09 | 14.696 | 0.070625 | 24.546 | 0.048223 |  | 7011 | 24.546 | 102.09 | 14.696 | 0.070625 | 0.048223
7012 | 102.1 | 14.696 | 0.070623 | 24.549 | 0.048227 |  | 7012 | 24.549 | 102.1 | 14.696 | 0.070623 | 0.048227
7013 | 102.11 | 14.696 | 0.070622 | 24.551 | 0.048231 |  | 7013 | 24.551 | 102.11 | 14.696 | 0.070622 | 0.048231
7014 | 102.12 | 14.696 | 0.070621 | 24.554 | 0.048236 |  | 7014 | 24.554 | 102.12 | 14.696 | 0.070621 | 0.048236
7015 | 102.13 | 14.696 | 0.070619 | 24.556 | 0.04824 |  | 7015 | 24.556 | 102.13 | 14.696 | 0.070619 | 0.04824
7016 | 102.14 | 14.696 | 0.070618 | 24.558 | 0.048244 |  | 7016 | 24.558 | 102.14 | 14.696 | 0.070618 | 0.048244
7017 | 102.15 | 14.696 | 0.070617 | 24.561 | 0.048248 |  | 7017 | 24.561 | 102.15 | 14.696 | 0.070617 | 0.048248
7018 | 102.16 | 14.696 | 0.070616 | 24.563 | 0.048253 |  | 7018 | 24.563 | 102.16 | 14.696 | 0.070616 | 0.048253
7019 | 102.17 | 14.696 | 0.070614 | 24.566 | 0.048257 |  | 7019 | 24.566 | 102.17 | 14.696 | 0.070614 | 0.048257
7020 | 102.18 | 14.696 | 0.070613 | 24.568 | 0.048261 |  | 7020 | 24.568 | 102.18 | 14.696 | 0.070613 | 0.048261
7021 | 102.19 | 14.696 | 0.070612 | 24.57 | 0.048265 |  | 7021 | 24.57 | 102.19 | 14.696 | 0.070612 | 0.048265
7022 | 102.2 | 14.696 | 0.070611 | 24.573 | 0.04827 |  | 7022 | 24.573 | 102.2 | 14.696 | 0.070611 | 0.04827
7023 | 102.21 | 14.696 | 0.070609 | 24.575 | 0.048274 |  | 7023 | 24.575 | 102.21 | 14.696 | 0.070609 | 0.048274
7024 | 102.22 | 14.696 | 0.070608 | 24.578 | 0.048278 |  | 7024 | 24.578 | 102.22 | 14.696 | 0.070608 | 0.048278
7025 | 102.23 | 14.696 | 0.070607 | 24.58 | 0.048283 |  | 7025 | 24.58 | 102.23 | 14.696 | 0.070607 | 0.048283
7026 | 102.24 | 14.696 | 0.070606 | 24.582 | 0.048287 |  | 7026 | 24.582 | 102.24 | 14.696 | 0.070606 | 0.048287
7027 | 102.25 | 14.696 | 0.070604 | 24.585 | 0.048291 |  | 7027 | 24.585 | 102.25 | 14.696 | 0.070604 | 0.048291
7028 | 102.26 | 14.696 | 0.070603 | 24.587 | 0.048295 |  | 7028 | 24.587 | 102.26 | 14.696 | 0.070603 | 0.048295
7029 | 102.27 | 14.696 | 0.070602 | 24.59 | 0.0483 |  | 7029 | 24.59 | 102.27 | 14.696 | 0.070602 | 0.0483
7030 | 102.28 | 14.696 | 0.070601 | 24.592 | 0.048304 |  | 7030 | 24.592 | 102.28 | 14.696 | 0.070601 | 0.048304
7031 | 102.29 | 14.696 | 0.070599 | 24.594 | 0.048308 |  | 7031 | 24.594 | 102.29 | 14.696 | 0.070599 | 0.048308
7032 | 102.3 | 14.696 | 0.070598 | 24.597 | 0.048313 |  | 7032 | 24.597 | 102.3 | 14.696 | 0.070598 | 0.048313
7033 | 102.31 | 14.696 | 0.070597 | 24.599 | 0.048317 |  | 7033 | 24.599 | 102.31 | 14.696 | 0.070597 | 0.048317
7034 | 102.32 | 14.696 | 0.070596 | 24.602 | 0.048321 |  | 7034 | 24.602 | 102.32 | 14.696 | 0.070596 | 0.048321
7035 | 102.33 | 14.696 | 0.070594 | 24.604 | 0.048325 |  | 7035 | 24.604 | 102.33 | 14.696 | 0.070594 | 0.048325
7036 | 102.34 | 14.696 | 0.070593 | 24.607 | 0.04833 |  | 7036 | 24.607 | 102.34 | 14.696 | 0.070593 | 0.04833
7037 | 102.35 | 14.696 | 0.070592 | 24.609 | 0.048334 |  | 7037 | 24.609 | 102.35 | 14.696 | 0.070592 | 0.048334
7038 | 102.36 | 14.696 | 0.07059 | 24.611 | 0.048338 |  | 7038 | 24.611 | 102.36 | 14.696 | 0.07059 | 0.048338
7039 | 102.37 | 14.696 | 0.070589 | 24.614 | 0.048343 |  | 7039 | 24.614 | 102.37 | 14.696 | 0.070589 | 0.048343
7040 | 102.38 | 14.696 | 0.070588 | 24.616 | 0.048347 |  | 7040 | 24.616 | 102.38 | 14.696 | 0.070588 | 0.048347
7041 | 102.39 | 14.696 | 0.070587 | 24.619 | 0.048351 |  | 7041 | 24.619 | 102.39 | 14.696 | 0.070587 | 0.048351
7042 | 102.4 | 14.696 | 0.070585 | 24.621 | 0.048355 |  | 7042 | 24.621 | 102.4 | 14.696 | 0.070585 | 0.048355
7043 | 102.41 | 14.696 | 0.070584 | 24.623 | 0.04836 |  | 7043 | 24.623 | 102.41 | 14.696 | 0.070584 | 0.04836
7044 | 102.42 | 14.696 | 0.070583 | 24.626 | 0.048364 |  | 7044 | 24.626 | 102.42 | 14.696 | 0.070583 | 0.048364
7045 | 102.43 | 14.696 | 0.070582 | 24.628 | 0.048368 |  | 7045 | 24.628 | 102.43 | 14.696 | 0.070582 | 0.048368
7046 | 102.44 | 14.696 | 0.07058 | 24.631 | 0.048373 |  | 7046 | 24.631 | 102.44 | 14.696 | 0.07058 | 0.048373
7047 | 102.45 | 14.696 | 0.070579 | 24.633 | 0.048377 |  | 7047 | 24.633 | 102.45 | 14.696 | 0.070579 | 0.048377
7048 | 102.46 | 14.696 | 0.070578 | 24.635 | 0.048381 |  | 7048 | 24.635 | 102.46 | 14.696 | 0.070578 | 0.048381
7049 | 102.47 | 14.696 | 0.070577 | 24.638 | 0.048385 |  | 7049 | 24.638 | 102.47 | 14.696 | 0.070577 | 0.048385
7050 | 102.48 | 14.696 | 0.070575 | 24.64 | 0.04839 |  | 7050 | 24.64 | 102.48 | 14.696 | 0.070575 | 0.04839
7051 | 102.49 | 14.696 | 0.070574 | 24.643 | 0.048394 |  | 7051 | 24.643 | 102.49 | 14.696 | 0.070574 | 0.048394
7052 | 102.5 | 14.696 | 0.070573 | 24.645 | 0.048398 |  | 7052 | 24.645 | 102.5 | 14.696 | 0.070573 | 0.048398
7053 | 102.51 | 14.696 | 0.070572 | 24.647 | 0.048403 |  | 7053 | 24.647 | 102.51 | 14.696 | 0.070572 | 0.048403
7054 | 102.52 | 14.696 | 0.07057 | 24.65 | 0.048407 |  | 7054 | 24.65 | 102.52 | 14.696 | 0.07057 | 0.048407
7055 | 102.53 | 14.696 | 0.070569 | 24.652 | 0.048411 |  | 7055 | 24.652 | 102.53 | 14.696 | 0.070569 | 0.048411
7056 | 102.54 | 14.696 | 0.070568 | 24.655 | 0.048415 |  | 7056 | 24.655 | 102.54 | 14.696 | 0.070568 | 0.048415
7057 | 102.55 | 14.696 | 0.070567 | 24.657 | 0.04842 |  | 7057 | 24.657 | 102.55 | 14.696 | 0.070567 | 0.04842
7058 | 102.56 | 14.696 | 0.070565 | 24.659 | 0.048424 |  | 7058 | 24.659 | 102.56 | 14.696 | 0.070565 | 0.048424
7059 | 102.57 | 14.696 | 0.070564 | 24.662 | 0.048428 |  | 7059 | 24.662 | 102.57 | 14.696 | 0.070564 | 0.048428
7060 | 102.58 | 14.696 | 0.070563 | 24.664 | 0.048432 |  | 7060 | 24.664 | 102.58 | 14.696 | 0.070563 | 0.048432
7061 | 102.59 | 14.696 | 0.070562 | 24.667 | 0.048437 |  | 7061 | 24.667 | 102.59 | 14.696 | 0.070562 | 0.048437
7062 | 102.6 | 14.696 | 0.07056 | 24.669 | 0.048441 |  | 7062 | 24.669 | 102.6 | 14.696 | 0.07056 | 0.048441
7063 | 102.61 | 14.696 | 0.070559 | 24.671 | 0.048445 |  | 7063 | 24.671 | 102.61 | 14.696 | 0.070559 | 0.048445
7064 | 102.62 | 14.696 | 0.070558 | 24.674 | 0.04845 |  | 7064 | 24.674 | 102.62 | 14.696 | 0.070558 | 0.04845
7065 | 102.63 | 14.696 | 0.070557 | 24.676 | 0.048454 |  | 7065 | 24.676 | 102.63 | 14.696 | 0.070557 | 0.048454
7066 | 102.64 | 14.696 | 0.070555 | 24.679 | 0.048458 |  | 7066 | 24.679 | 102.64 | 14.696 | 0.070555 | 0.048458
7067 | 102.65 | 14.696 | 0.070554 | 24.681 | 0.048462 |  | 7067 | 24.681 | 102.65 | 14.696 | 0.070554 | 0.048462
7068 | 102.66 | 14.696 | 0.070553 | 24.684 | 0.048467 |  | 7068 | 24.684 | 102.66 | 14.696 | 0.070553 | 0.048467
7069 | 102.67 | 14.696 | 0.070551 | 24.686 | 0.048471 |  | 7069 | 24.686 | 102.67 | 14.696 | 0.070551 | 0.048471
7070 | 102.68 | 14.696 | 0.07055 | 24.688 | 0.048475 |  | 7070 | 24.688 | 102.68 | 14.696 | 0.07055 | 0.048475
7071 | 102.69 | 14.696 | 0.070549 | 24.691 | 0.04848 |  | 7071 | 24.691 | 102.69 | 14.696 | 0.070549 | 0.04848
7072 | 102.7 | 14.696 | 0.070548 | 24.693 | 0.048484 |  | 7072 | 24.693 | 102.7 | 14.696 | 0.070548 | 0.048484
7073 | 102.71 | 14.696 | 0.070546 | 24.696 | 0.048488 |  | 7073 | 24.696 | 102.71 | 14.696 | 0.070546 | 0.048488
7074 | 102.72 | 14.696 | 0.070545 | 24.698 | 0.048492 |  | 7074 | 24.698 | 102.72 | 14.696 | 0.070545 | 0.048492
7075 | 102.73 | 14.696 | 0.070544 | 24.7 | 0.048497 |  | 7075 | 24.7 | 102.73 | 14.696 | 0.070544 | 0.048497
7076 | 102.74 | 14.696 | 0.070543 | 24.703 | 0.048501 |  | 7076 | 24.703 | 102.74 | 14.696 | 0.070543 | 0.048501
7077 | 102.75 | 14.696 | 0.070541 | 24.705 | 0.048505 |  | 7077 | 24.705 | 102.75 | 14.696 | 0.070541 | 0.048505
7078 | 102.76 | 14.696 | 0.07054 | 24.708 | 0.04851 |  | 7078 | 24.708 | 102.76 | 14.696 | 0.07054 | 0.04851
7079 | 102.77 | 14.696 | 0.070539 | 24.71 | 0.048514 |  | 7079 | 24.71 | 102.77 | 14.696 | 0.070539 | 0.048514
7080 | 102.78 | 14.696 | 0.070538 | 24.712 | 0.048518 |  | 7080 | 24.712 | 102.78 | 14.696 | 0.070538 | 0.048518
7081 | 102.79 | 14.696 | 0.070536 | 24.715 | 0.048522 |  | 7081 | 24.715 | 102.79 | 14.696 | 0.070536 | 0.048522
7082 | 102.8 | 14.696 | 0.070535 | 24.717 | 0.048527 |  | 7082 | 24.717 | 102.8 | 14.696 | 0.070535 | 0.048527
7083 | 102.81 | 14.696 | 0.070534 | 24.72 | 0.048531 |  | 7083 | 24.72 | 102.81 | 14.696 | 0.070534 | 0.048531
7084 | 102.82 | 14.696 | 0.070533 | 24.722 | 0.048535 |  | 7084 | 24.722 | 102.82 | 14.696 | 0.070533 | 0.048535
7085 | 102.83 | 14.696 | 0.070531 | 24.724 | 0.048539 |  | 7085 | 24.724 | 102.83 | 14.696 | 0.070531 | 0.048539
7086 | 102.84 | 14.696 | 0.07053 | 24.727 | 0.048544 |  | 7086 | 24.727 | 102.84 | 14.696 | 0.07053 | 0.048544
7087 | 102.85 | 14.696 | 0.070529 | 24.729 | 0.048548 |  | 7087 | 24.729 | 102.85 | 14.696 | 0.070529 | 0.048548
7088 | 102.86 | 14.696 | 0.070528 | 24.732 | 0.048552 |  | 7088 | 24.732 | 102.86 | 14.696 | 0.070528 | 0.048552
7089 | 102.87 | 14.696 | 0.070526 | 24.734 | 0.048557 |  | 7089 | 24.734 | 102.87 | 14.696 | 0.070526 | 0.048557
7090 | 102.88 | 14.696 | 0.070525 | 24.736 | 0.048561 |  | 7090 | 24.736 | 102.88 | 14.696 | 0.070525 | 0.048561
7091 | 102.89 | 14.696 | 0.070524 | 24.739 | 0.048565 |  | 7091 | 24.739 | 102.89 | 14.696 | 0.070524 | 0.048565
7092 | 102.9 | 14.696 | 0.070523 | 24.741 | 0.048569 |  | 7092 | 24.741 | 102.9 | 14.696 | 0.070523 | 0.048569
7093 | 102.91 | 14.696 | 0.070521 | 24.744 | 0.048574 |  | 7093 | 24.744 | 102.91 | 14.696 | 0.070521 | 0.048574
7094 | 102.92 | 14.696 | 0.07052 | 24.746 | 0.048578 |  | 7094 | 24.746 | 102.92 | 14.696 | 0.07052 | 0.048578
7095 | 102.93 | 14.696 | 0.070519 | 24.748 | 0.048582 |  | 7095 | 24.748 | 102.93 | 14.696 | 0.070519 | 0.048582
7096 | 102.94 | 14.696 | 0.070518 | 24.751 | 0.048587 |  | 7096 | 24.751 | 102.94 | 14.696 | 0.070518 | 0.048587
7097 | 102.95 | 14.696 | 0.070516 | 24.753 | 0.048591 |  | 7097 | 24.753 | 102.95 | 14.696 | 0.070516 | 0.048591
7098 | 102.96 | 14.696 | 0.070515 | 24.756 | 0.048595 |  | 7098 | 24.756 | 102.96 | 14.696 | 0.070515 | 0.048595
7099 | 102.97 | 14.696 | 0.070514 | 24.758 | 0.048599 |  | 7099 | 24.758 | 102.97 | 14.696 | 0.070514 | 0.048599
7100 | 102.98 | 14.696 | 0.070513 | 24.761 | 0.048604 |  | 7100 | 24.761 | 102.98 | 14.696 | 0.070513 | 0.048604
7101 | 102.99 | 14.696 | 0.070511 | 24.763 | 0.048608 |  | 7101 | 24.763 | 102.99 | 14.696 | 0.070511 | 0.048608
7102 | 103 | 14.696 | 0.07051 | 24.765 | 0.048612 |  | 7102 | 24.765 | 103 | 14.696 | 0.07051 | 0.048612
7103 | 103.01 | 14.696 | 0.070509 | 24.768 | 0.048616 |  | 7103 | 24.768 | 103.01 | 14.696 | 0.070509 | 0.048616
7104 | 103.02 | 14.696 | 0.070508 | 24.77 | 0.048621 |  | 7104 | 24.77 | 103.02 | 14.696 | 0.070508 | 0.048621
7105 | 103.03 | 14.696 | 0.070506 | 24.773 | 0.048625 |  | 7105 | 24.773 | 103.03 | 14.696 | 0.070506 | 0.048625
7106 | 103.04 | 14.696 | 0.070505 | 24.775 | 0.048629 |  | 7106 | 24.775 | 103.04 | 14.696 | 0.070505 | 0.048629
7107 | 103.05 | 14.696 | 0.070504 | 24.777 | 0.048634 |  | 7107 | 24.777 | 103.05 | 14.696 | 0.070504 | 0.048634
7108 | 103.06 | 14.696 | 0.070502 | 24.78 | 0.048638 |  | 7108 | 24.78 | 103.06 | 14.696 | 0.070502 | 0.048638
7109 | 103.07 | 14.696 | 0.070501 | 24.782 | 0.048642 |  | 7109 | 24.782 | 103.07 | 14.696 | 0.070501 | 0.048642
7110 | 103.08 | 14.696 | 0.0705 | 24.785 | 0.048646 |  | 7110 | 24.785 | 103.08 | 14.696 | 0.0705 | 0.048646
7111 | 103.09 | 14.696 | 0.070499 | 24.787 | 0.048651 |  | 7111 | 24.787 | 103.09 | 14.696 | 0.070499 | 0.048651
7112 | 103.1 | 14.696 | 0.070497 | 24.789 | 0.048655 |  | 7112 | 24.789 | 103.1 | 14.696 | 0.070497 | 0.048655
7113 | 103.11 | 14.696 | 0.070496 | 24.792 | 0.048659 |  | 7113 | 24.792 | 103.11 | 14.696 | 0.070496 | 0.048659
7114 | 103.12 | 14.696 | 0.070495 | 24.794 | 0.048663 |  | 7114 | 24.794 | 103.12 | 14.696 | 0.070495 | 0.048663
7115 | 103.13 | 14.696 | 0.070494 | 24.797 | 0.048668 |  | 7115 | 24.797 | 103.13 | 14.696 | 0.070494 | 0.048668
7116 | 103.14 | 14.696 | 0.070492 | 24.799 | 0.048672 |  | 7116 | 24.799 | 103.14 | 14.696 | 0.070492 | 0.048672
7117 | 103.15 | 14.696 | 0.070491 | 24.801 | 0.048676 |  | 7117 | 24.801 | 103.15 | 14.696 | 0.070491 | 0.048676
7118 | 103.16 | 14.696 | 0.07049 | 24.804 | 0.048681 |  | 7118 | 24.804 | 103.16 | 14.696 | 0.07049 | 0.048681
7119 | 103.17 | 14.696 | 0.070489 | 24.806 | 0.048685 |  | 7119 | 24.806 | 103.17 | 14.696 | 0.070489 | 0.048685
7120 | 103.18 | 14.696 | 0.070487 | 24.809 | 0.048689 |  | 7120 | 24.809 | 103.18 | 14.696 | 0.070487 | 0.048689
7121 | 103.19 | 14.696 | 0.070486 | 24.811 | 0.048693 |  | 7121 | 24.811 | 103.19 | 14.696 | 0.070486 | 0.048693
7122 | 103.2 | 14.696 | 0.070485 | 24.813 | 0.048698 |  | 7122 | 24.813 | 103.2 | 14.696 | 0.070485 | 0.048698
7123 | 103.21 | 14.696 | 0.070484 | 24.816 | 0.048702 |  | 7123 | 24.816 | 103.21 | 14.696 | 0.070484 | 0.048702
7124 | 103.22 | 14.696 | 0.070482 | 24.818 | 0.048706 |  | 7124 | 24.818 | 103.22 | 14.696 | 0.070482 | 0.048706
7125 | 103.23 | 14.696 | 0.070481 | 24.821 | 0.048711 |  | 7125 | 24.821 | 103.23 | 14.696 | 0.070481 | 0.048711
7126 | 103.24 | 14.696 | 0.07048 | 24.823 | 0.048715 |  | 7126 | 24.823 | 103.24 | 14.696 | 0.07048 | 0.048715
7127 | 103.25 | 14.696 | 0.070479 | 24.825 | 0.048719 |  | 7127 | 24.825 | 103.25 | 14.696 | 0.070479 | 0.048719
7128 | 103.26 | 14.696 | 0.070477 | 24.828 | 0.048723 |  | 7128 | 24.828 | 103.26 | 14.696 | 0.070477 | 0.048723
7129 | 103.27 | 14.696 | 0.070476 | 24.83 | 0.048728 |  | 7129 | 24.83 | 103.27 | 14.696 | 0.070476 | 0.048728
7130 | 103.28 | 14.696 | 0.070475 | 24.833 | 0.048732 |  | 7130 | 24.833 | 103.28 | 14.696 | 0.070475 | 0.048732
7131 | 103.29 | 14.696 | 0.070474 | 24.835 | 0.048736 |  | 7131 | 24.835 | 103.29 | 14.696 | 0.070474 | 0.048736
7132 | 103.3 | 14.696 | 0.070472 | 24.838 | 0.04874 |  | 7132 | 24.838 | 103.3 | 14.696 | 0.070472 | 0.04874
7133 | 103.31 | 14.696 | 0.070471 | 24.84 | 0.048745 |  | 7133 | 24.84 | 103.31 | 14.696 | 0.070471 | 0.048745
7134 | 103.32 | 14.696 | 0.07047 | 24.842 | 0.048749 |  | 7134 | 24.842 | 103.32 | 14.696 | 0.07047 | 0.048749
7135 | 103.33 | 14.696 | 0.070469 | 24.845 | 0.048753 |  | 7135 | 24.845 | 103.33 | 14.696 | 0.070469 | 0.048753
7136 | 103.34 | 14.696 | 0.070467 | 24.847 | 0.048758 |  | 7136 | 24.847 | 103.34 | 14.696 | 0.070467 | 0.048758
7137 | 103.35 | 14.696 | 0.070466 | 24.85 | 0.048762 |  | 7137 | 24.85 | 103.35 | 14.696 | 0.070466 | 0.048762
7138 | 103.36 | 14.696 | 0.070465 | 24.852 | 0.048766 |  | 7138 | 24.852 | 103.36 | 14.696 | 0.070465 | 0.048766
7139 | 103.37 | 14.696 | 0.070464 | 24.854 | 0.04877 |  | 7139 | 24.854 | 103.37 | 14.696 | 0.070464 | 0.04877
7140 | 103.38 | 14.696 | 0.070462 | 24.857 | 0.048775 |  | 7140 | 24.857 | 103.38 | 14.696 | 0.070462 | 0.048775
7141 | 103.39 | 14.696 | 0.070461 | 24.859 | 0.048779 |  | 7141 | 24.859 | 103.39 | 14.696 | 0.070461 | 0.048779
7142 | 103.4 | 14.696 | 0.07046 | 24.862 | 0.048783 |  | 7142 | 24.862 | 103.4 | 14.696 | 0.07046 | 0.048783
7143 | 103.41 | 14.696 | 0.070459 | 24.864 | 0.048787 |  | 7143 | 24.864 | 103.41 | 14.696 | 0.070459 | 0.048787
7144 | 103.42 | 14.696 | 0.070457 | 24.866 | 0.048792 |  | 7144 | 24.866 | 103.42 | 14.696 | 0.070457 | 0.048792
7145 | 103.43 | 14.696 | 0.070456 | 24.869 | 0.048796 |  | 7145 | 24.869 | 103.43 | 14.696 | 0.070456 | 0.048796
7146 | 103.44 | 14.696 | 0.070455 | 24.871 | 0.0488 |  | 7146 | 24.871 | 103.44 | 14.696 | 0.070455 | 0.0488
7147 | 103.45 | 14.696 | 0.070454 | 24.874 | 0.048805 |  | 7147 | 24.874 | 103.45 | 14.696 | 0.070454 | 0.048805
7148 | 103.46 | 14.696 | 0.070452 | 24.876 | 0.048809 |  | 7148 | 24.876 | 103.46 | 14.696 | 0.070452 | 0.048809
7149 | 103.47 | 14.696 | 0.070451 | 24.878 | 0.048813 |  | 7149 | 24.878 | 103.47 | 14.696 | 0.070451 | 0.048813
7150 | 103.48 | 14.696 | 0.07045 | 24.881 | 0.048817 |  | 7150 | 24.881 | 103.48 | 14.696 | 0.07045 | 0.048817
7151 | 103.49 | 14.696 | 0.070449 | 24.883 | 0.048822 |  | 7151 | 24.883 | 103.49 | 14.696 | 0.070449 | 0.048822
7152 | 103.5 | 14.696 | 0.070447 | 24.886 | 0.048826 |  | 7152 | 24.886 | 103.5 | 14.696 | 0.070447 | 0.048826
7153 | 103.51 | 14.696 | 0.070446 | 24.888 | 0.04883 |  | 7153 | 24.888 | 103.51 | 14.696 | 0.070446 | 0.04883
7154 | 103.52 | 14.696 | 0.070445 | 24.89 | 0.048834 |  | 7154 | 24.89 | 103.52 | 14.696 | 0.070445 | 0.048834
7155 | 103.53 | 14.696 | 0.070444 | 24.893 | 0.048839 |  | 7155 | 24.893 | 103.53 | 14.696 | 0.070444 | 0.048839
7156 | 103.54 | 14.696 | 0.070442 | 24.895 | 0.048843 |  | 7156 | 24.895 | 103.54 | 14.696 | 0.070442 | 0.048843
7157 | 103.55 | 14.696 | 0.070441 | 24.898 | 0.048847 |  | 7157 | 24.898 | 103.55 | 14.696 | 0.070441 | 0.048847
7158 | 103.56 | 14.696 | 0.07044 | 24.9 | 0.048852 |  | 7158 | 24.9 | 103.56 | 14.696 | 0.07044 | 0.048852
7159 | 103.57 | 14.696 | 0.070438 | 24.903 | 0.048856 |  | 7159 | 24.903 | 103.57 | 14.696 | 0.070438 | 0.048856
7160 | 103.58 | 14.696 | 0.070437 | 24.905 | 0.04886 |  | 7160 | 24.905 | 103.58 | 14.696 | 0.070437 | 0.04886
7161 | 103.59 | 14.696 | 0.070436 | 24.907 | 0.048864 |  | 7161 | 24.907 | 103.59 | 14.696 | 0.070436 | 0.048864
7162 | 103.6 | 14.696 | 0.070435 | 24.91 | 0.048869 |  | 7162 | 24.91 | 103.6 | 14.696 | 0.070435 | 0.048869
7163 | 103.61 | 14.696 | 0.070433 | 24.912 | 0.048873 |  | 7163 | 24.912 | 103.61 | 14.696 | 0.070433 | 0.048873
7164 | 103.62 | 14.696 | 0.070432 | 24.915 | 0.048877 |  | 7164 | 24.915 | 103.62 | 14.696 | 0.070432 | 0.048877
7165 | 103.63 | 14.696 | 0.070431 | 24.917 | 0.048881 |  | 7165 | 24.917 | 103.63 | 14.696 | 0.070431 | 0.048881
7166 | 103.64 | 14.696 | 0.07043 | 24.919 | 0.048886 |  | 7166 | 24.919 | 103.64 | 14.696 | 0.07043 | 0.048886
7167 | 103.65 | 14.696 | 0.070428 | 24.922 | 0.04889 |  | 7167 | 24.922 | 103.65 | 14.696 | 0.070428 | 0.04889
7168 | 103.66 | 14.696 | 0.070427 | 24.924 | 0.048894 |  | 7168 | 24.924 | 103.66 | 14.696 | 0.070427 | 0.048894
7169 | 103.67 | 14.696 | 0.070426 | 24.927 | 0.048899 |  | 7169 | 24.927 | 103.67 | 14.696 | 0.070426 | 0.048899
7170 | 103.68 | 14.696 | 0.070425 | 24.929 | 0.048903 |  | 7170 | 24.929 | 103.68 | 14.696 | 0.070425 | 0.048903
7171 | 103.69 | 14.696 | 0.070423 | 24.931 | 0.048907 |  | 7171 | 24.931 | 103.69 | 14.696 | 0.070423 | 0.048907
7172 | 103.7 | 14.696 | 0.070422 | 24.934 | 0.048911 |  | 7172 | 24.934 | 103.7 | 14.696 | 0.070422 | 0.048911
7173 | 103.71 | 14.696 | 0.070421 | 24.936 | 0.048916 |  | 7173 | 24.936 | 103.71 | 14.696 | 0.070421 | 0.048916
7174 | 103.72 | 14.696 | 0.07042 | 24.939 | 0.04892 |  | 7174 | 24.939 | 103.72 | 14.696 | 0.07042 | 0.04892
7175 | 103.73 | 14.696 | 0.070418 | 24.941 | 0.048924 |  | 7175 | 24.941 | 103.73 | 14.696 | 0.070418 | 0.048924
7176 | 103.74 | 14.696 | 0.070417 | 24.943 | 0.048928 |  | 7176 | 24.943 | 103.74 | 14.696 | 0.070417 | 0.048928
7177 | 103.75 | 14.696 | 0.070416 | 24.946 | 0.048933 |  | 7177 | 24.946 | 103.75 | 14.696 | 0.070416 | 0.048933
7178 | 103.76 | 14.696 | 0.070415 | 24.948 | 0.048937 |  | 7178 | 24.948 | 103.76 | 14.696 | 0.070415 | 0.048937
7179 | 103.77 | 14.696 | 0.070413 | 24.951 | 0.048941 |  | 7179 | 24.951 | 103.77 | 14.696 | 0.070413 | 0.048941
7180 | 103.78 | 14.696 | 0.070412 | 24.953 | 0.048946 |  | 7180 | 24.953 | 103.78 | 14.696 | 0.070412 | 0.048946
7181 | 103.79 | 14.696 | 0.070411 | 24.955 | 0.04895 |  | 7181 | 24.955 | 103.79 | 14.696 | 0.070411 | 0.04895
7182 | 103.8 | 14.696 | 0.07041 | 24.958 | 0.048954 |  | 7182 | 24.958 | 103.8 | 14.696 | 0.07041 | 0.048954
7183 | 103.81 | 14.696 | 0.070408 | 24.96 | 0.048958 |  | 7183 | 24.96 | 103.81 | 14.696 | 0.070408 | 0.048958
7184 | 103.82 | 14.696 | 0.070407 | 24.963 | 0.048963 |  | 7184 | 24.963 | 103.82 | 14.696 | 0.070407 | 0.048963
7185 | 103.83 | 14.696 | 0.070406 | 24.965 | 0.048967 |  | 7185 | 24.965 | 103.83 | 14.696 | 0.070406 | 0.048967
7186 | 103.84 | 14.696 | 0.070405 | 24.967 | 0.048971 |  | 7186 | 24.967 | 103.84 | 14.696 | 0.070405 | 0.048971
7187 | 103.85 | 14.696 | 0.070403 | 24.97 | 0.048975 |  | 7187 | 24.97 | 103.85 | 14.696 | 0.070403 | 0.048975
7188 | 103.86 | 14.696 | 0.070402 | 24.972 | 0.04898 |  | 7188 | 24.972 | 103.86 | 14.696 | 0.070402 | 0.04898
7189 | 103.87 | 14.696 | 0.070401 | 24.975 | 0.048984 |  | 7189 | 24.975 | 103.87 | 14.696 | 0.070401 | 0.048984
7190 | 103.88 | 14.696 | 0.0704 | 24.977 | 0.048988 |  | 7190 | 24.977 | 103.88 | 14.696 | 0.0704 | 0.048988
7191 | 103.89 | 14.696 | 0.070398 | 24.98 | 0.048993 |  | 7191 | 24.98 | 103.89 | 14.696 | 0.070398 | 0.048993
7192 | 103.9 | 14.696 | 0.070397 | 24.982 | 0.048997 |  | 7192 | 24.982 | 103.9 | 14.696 | 0.070397 | 0.048997
7193 | 103.91 | 14.696 | 0.070396 | 24.984 | 0.049001 |  | 7193 | 24.984 | 103.91 | 14.696 | 0.070396 | 0.049001
7194 | 103.92 | 14.696 | 0.070395 | 24.987 | 0.049005 |  | 7194 | 24.987 | 103.92 | 14.696 | 0.070395 | 0.049005
7195 | 103.93 | 14.696 | 0.070393 | 24.989 | 0.04901 |  | 7195 | 24.989 | 103.93 | 14.696 | 0.070393 | 0.04901
7196 | 103.94 | 14.696 | 0.070392 | 24.992 | 0.049014 |  | 7196 | 24.992 | 103.94 | 14.696 | 0.070392 | 0.049014
7197 | 103.95 | 14.696 | 0.070391 | 24.994 | 0.049018 |  | 7197 | 24.994 | 103.95 | 14.696 | 0.070391 | 0.049018
7198 | 103.96 | 14.696 | 0.07039 | 24.996 | 0.049022 |  | 7198 | 24.996 | 103.96 | 14.696 | 0.07039 | 0.049022
7199 | 103.97 | 14.696 | 0.070388 | 24.999 | 0.049027 |  | 7199 | 24.999 | 103.97 | 14.696 | 0.070388 | 0.049027
7200 | 103.98 | 14.696 | 0.070387 | 25.001 | 0.049031 |  | 7200 | 25.001 | 103.98 | 14.696 | 0.070387 | 0.049031
7201 | 103.99 | 14.696 | 0.070386 | 25.004 | 0.049035 |  | 7201 | 25.004 | 103.99 | 14.696 | 0.070386 | 0.049035
7202 | 104 | 14.696 | 0.070385 | 25.006 | 0.049039 |  | 7202 | 25.006 | 104 | 14.696 | 0.070385 | 0.049039
7203 | 104.01 | 14.696 | 0.070383 | 25.008 | 0.049044 |  | 7203 | 25.008 | 104.01 | 14.696 | 0.070383 | 0.049044
7204 | 104.02 | 14.696 | 0.070382 | 25.011 | 0.049048 |  | 7204 | 25.011 | 104.02 | 14.696 | 0.070382 | 0.049048
7205 | 104.03 | 14.696 | 0.070381 | 25.013 | 0.049052 |  | 7205 | 25.013 | 104.03 | 14.696 | 0.070381 | 0.049052
7206 | 104.04 | 14.696 | 0.07038 | 25.016 | 0.049057 |  | 7206 | 25.016 | 104.04 | 14.696 | 0.07038 | 0.049057
7207 | 104.05 | 14.696 | 0.070378 | 25.018 | 0.049061 |  | 7207 | 25.018 | 104.05 | 14.696 | 0.070378 | 0.049061
7208 | 104.06 | 14.696 | 0.070377 | 25.02 | 0.049065 |  | 7208 | 25.02 | 104.06 | 14.696 | 0.070377 | 0.049065
7209 | 104.07 | 14.696 | 0.070376 | 25.023 | 0.049069 |  | 7209 | 25.023 | 104.07 | 14.696 | 0.070376 | 0.049069
7210 | 104.08 | 14.696 | 0.070375 | 25.025 | 0.049074 |  | 7210 | 25.025 | 104.08 | 14.696 | 0.070375 | 0.049074
7211 | 104.09 | 14.696 | 0.070373 | 25.028 | 0.049078 |  | 7211 | 25.028 | 104.09 | 14.696 | 0.070373 | 0.049078
7212 | 104.1 | 14.696 | 0.070372 | 25.03 | 0.049082 |  | 7212 | 25.03 | 104.1 | 14.696 | 0.070372 | 0.049082
7213 | 104.11 | 14.696 | 0.070371 | 25.032 | 0.049086 |  | 7213 | 25.032 | 104.11 | 14.696 | 0.070371 | 0.049086
7214 | 104.12 | 14.696 | 0.07037 | 25.035 | 0.049091 |  | 7214 | 25.035 | 104.12 | 14.696 | 0.07037 | 0.049091
7215 | 104.13 | 14.696 | 0.070368 | 25.037 | 0.049095 |  | 7215 | 25.037 | 104.13 | 14.696 | 0.070368 | 0.049095
7216 | 104.14 | 14.696 | 0.070367 | 25.04 | 0.049099 |  | 7216 | 25.04 | 104.14 | 14.696 | 0.070367 | 0.049099
7217 | 104.15 | 14.696 | 0.070366 | 25.042 | 0.049104 |  | 7217 | 25.042 | 104.15 | 14.696 | 0.070366 | 0.049104
7218 | 104.16 | 14.696 | 0.070365 | 25.044 | 0.049108 |  | 7218 | 25.044 | 104.16 | 14.696 | 0.070365 | 0.049108
7219 | 104.17 | 14.696 | 0.070363 | 25.047 | 0.049112 |  | 7219 | 25.047 | 104.17 | 14.696 | 0.070363 | 0.049112
7220 | 104.18 | 14.696 | 0.070362 | 25.049 | 0.049116 |  | 7220 | 25.049 | 104.18 | 14.696 | 0.070362 | 0.049116
7221 | 104.19 | 14.696 | 0.070361 | 25.052 | 0.049121 |  | 7221 | 25.052 | 104.19 | 14.696 | 0.070361 | 0.049121
7222 | 104.2 | 14.696 | 0.07036 | 25.054 | 0.049125 |  | 7222 | 25.054 | 104.2 | 14.696 | 0.07036 | 0.049125
7223 | 104.21 | 14.696 | 0.070358 | 25.057 | 0.049129 |  | 7223 | 25.057 | 104.21 | 14.696 | 0.070358 | 0.049129
7224 | 104.22 | 14.696 | 0.070357 | 25.059 | 0.049133 |  | 7224 | 25.059 | 104.22 | 14.696 | 0.070357 | 0.049133
7225 | 104.23 | 14.696 | 0.070356 | 25.061 | 0.049138 |  | 7225 | 25.061 | 104.23 | 14.696 | 0.070356 | 0.049138
7226 | 104.24 | 14.696 | 0.070355 | 25.064 | 0.049142 |  | 7226 | 25.064 | 104.24 | 14.696 | 0.070355 | 0.049142
7227 | 104.25 | 14.696 | 0.070353 | 25.066 | 0.049146 |  | 7227 | 25.066 | 104.25 | 14.696 | 0.070353 | 0.049146
7228 | 104.26 | 14.696 | 0.070352 | 25.069 | 0.04915 |  | 7228 | 25.069 | 104.26 | 14.696 | 0.070352 | 0.04915
7229 | 104.27 | 14.696 | 0.070351 | 25.071 | 0.049155 |  | 7229 | 25.071 | 104.27 | 14.696 | 0.070351 | 0.049155
7230 | 104.28 | 14.696 | 0.07035 | 25.073 | 0.049159 |  | 7230 | 25.073 | 104.28 | 14.696 | 0.07035 | 0.049159
7231 | 104.29 | 14.696 | 0.070348 | 25.076 | 0.049163 |  | 7231 | 25.076 | 104.29 | 14.696 | 0.070348 | 0.049163
7232 | 104.3 | 14.696 | 0.070347 | 25.078 | 0.049168 |  | 7232 | 25.078 | 104.3 | 14.696 | 0.070347 | 0.049168
7233 | 104.31 | 14.696 | 0.070346 | 25.081 | 0.049172 |  | 7233 | 25.081 | 104.31 | 14.696 | 0.070346 | 0.049172
7234 | 104.32 | 14.696 | 0.070345 | 25.083 | 0.049176 |  | 7234 | 25.083 | 104.32 | 14.696 | 0.070345 | 0.049176
7235 | 104.33 | 14.696 | 0.070343 | 25.085 | 0.04918 |  | 7235 | 25.085 | 104.33 | 14.696 | 0.070343 | 0.04918
7236 | 104.34 | 14.696 | 0.070342 | 25.088 | 0.049185 |  | 7236 | 25.088 | 104.34 | 14.696 | 0.070342 | 0.049185
7237 | 104.35 | 14.696 | 0.070341 | 25.09 | 0.049189 |  | 7237 | 25.09 | 104.35 | 14.696 | 0.070341 | 0.049189
7238 | 104.36 | 14.696 | 0.07034 | 25.093 | 0.049193 |  | 7238 | 25.093 | 104.36 | 14.696 | 0.07034 | 0.049193
7239 | 104.37 | 14.696 | 0.070338 | 25.095 | 0.049197 |  | 7239 | 25.095 | 104.37 | 14.696 | 0.070338 | 0.049197
7240 | 104.38 | 14.696 | 0.070337 | 25.097 | 0.049202 |  | 7240 | 25.097 | 104.38 | 14.696 | 0.070337 | 0.049202
7241 | 104.39 | 14.696 | 0.070336 | 25.1 | 0.049206 |  | 7241 | 25.1 | 104.39 | 14.696 | 0.070336 | 0.049206
7242 | 104.4 | 14.696 | 0.070335 | 25.102 | 0.04921 |  | 7242 | 25.102 | 104.4 | 14.696 | 0.070335 | 0.04921
7243 | 104.41 | 14.696 | 0.070333 | 25.105 | 0.049214 |  | 7243 | 25.105 | 104.41 | 14.696 | 0.070333 | 0.049214
7244 | 104.42 | 14.696 | 0.070332 | 25.107 | 0.049219 |  | 7244 | 25.107 | 104.42 | 14.696 | 0.070332 | 0.049219
7245 | 104.43 | 14.696 | 0.070331 | 25.109 | 0.049223 |  | 7245 | 25.109 | 104.43 | 14.696 | 0.070331 | 0.049223
7246 | 104.44 | 14.696 | 0.07033 | 25.112 | 0.049227 |  | 7246 | 25.112 | 104.44 | 14.696 | 0.07033 | 0.049227
7247 | 104.45 | 14.696 | 0.070328 | 25.114 | 0.049232 |  | 7247 | 25.114 | 104.45 | 14.696 | 0.070328 | 0.049232
7248 | 104.46 | 14.696 | 0.070327 | 25.117 | 0.049236 |  | 7248 | 25.117 | 104.46 | 14.696 | 0.070327 | 0.049236
7249 | 104.47 | 14.696 | 0.070326 | 25.119 | 0.04924 |  | 7249 | 25.119 | 104.47 | 14.696 | 0.070326 | 0.04924
7250 | 104.48 | 14.696 | 0.070325 | 25.122 | 0.049244 |  | 7250 | 25.122 | 104.48 | 14.696 | 0.070325 | 0.049244
7251 | 104.49 | 14.696 | 0.070323 | 25.124 | 0.049249 |  | 7251 | 25.124 | 104.49 | 14.696 | 0.070323 | 0.049249
7252 | 104.5 | 14.696 | 0.070322 | 25.126 | 0.049253 |  | 7252 | 25.126 | 104.5 | 14.696 | 0.070322 | 0.049253
7253 | 104.51 | 14.696 | 0.070321 | 25.129 | 0.049257 |  | 7253 | 25.129 | 104.51 | 14.696 | 0.070321 | 0.049257
7254 | 104.52 | 14.696 | 0.07032 | 25.131 | 0.049261 |  | 7254 | 25.131 | 104.52 | 14.696 | 0.07032 | 0.049261
7255 | 104.53 | 14.696 | 0.070318 | 25.134 | 0.049266 |  | 7255 | 25.134 | 104.53 | 14.696 | 0.070318 | 0.049266
7256 | 104.54 | 14.696 | 0.070317 | 25.136 | 0.04927 |  | 7256 | 25.136 | 104.54 | 14.696 | 0.070317 | 0.04927
7257 | 104.55 | 14.696 | 0.070316 | 25.138 | 0.049274 |  | 7257 | 25.138 | 104.55 | 14.696 | 0.070316 | 0.049274
7258 | 104.56 | 14.696 | 0.070315 | 25.141 | 0.049278 |  | 7258 | 25.141 | 104.56 | 14.696 | 0.070315 | 0.049278
7259 | 104.57 | 14.696 | 0.070313 | 25.143 | 0.049283 |  | 7259 | 25.143 | 104.57 | 14.696 | 0.070313 | 0.049283
7260 | 104.58 | 14.696 | 0.070312 | 25.146 | 0.049287 |  | 7260 | 25.146 | 104.58 | 14.696 | 0.070312 | 0.049287
7261 | 104.59 | 14.696 | 0.070311 | 25.148 | 0.049291 |  | 7261 | 25.148 | 104.59 | 14.696 | 0.070311 | 0.049291
7262 | 104.6 | 14.696 | 0.07031 | 25.15 | 0.049296 |  | 7262 | 25.15 | 104.6 | 14.696 | 0.07031 | 0.049296
7263 | 104.61 | 14.696 | 0.070308 | 25.153 | 0.0493 |  | 7263 | 25.153 | 104.61 | 14.696 | 0.070308 | 0.0493
7264 | 104.62 | 14.696 | 0.070307 | 25.155 | 0.049304 |  | 7264 | 25.155 | 104.62 | 14.696 | 0.070307 | 0.049304
7265 | 104.63 | 14.696 | 0.070306 | 25.158 | 0.049308 |  | 7265 | 25.158 | 104.63 | 14.696 | 0.070306 | 0.049308
7266 | 104.64 | 14.696 | 0.070305 | 25.16 | 0.049313 |  | 7266 | 25.16 | 104.64 | 14.696 | 0.070305 | 0.049313
7267 | 104.65 | 14.696 | 0.070303 | 25.162 | 0.049317 |  | 7267 | 25.162 | 104.65 | 14.696 | 0.070303 | 0.049317
7268 | 104.66 | 14.696 | 0.070302 | 25.165 | 0.049321 |  | 7268 | 25.165 | 104.66 | 14.696 | 0.070302 | 0.049321
7269 | 104.67 | 14.696 | 0.070301 | 25.167 | 0.049325 |  | 7269 | 25.167 | 104.67 | 14.696 | 0.070301 | 0.049325
7270 | 104.68 | 14.696 | 0.0703 | 25.17 | 0.04933 |  | 7270 | 25.17 | 104.68 | 14.696 | 0.0703 | 0.04933
7271 | 104.69 | 14.696 | 0.070298 | 25.172 | 0.049334 |  | 7271 | 25.172 | 104.69 | 14.696 | 0.070298 | 0.049334
7272 | 104.7 | 14.696 | 0.070297 | 25.174 | 0.049338 |  | 7272 | 25.174 | 104.7 | 14.696 | 0.070297 | 0.049338
7273 | 104.71 | 14.696 | 0.070296 | 25.177 | 0.049342 |  | 7273 | 25.177 | 104.71 | 14.696 | 0.070296 | 0.049342
7274 | 104.72 | 14.696 | 0.070295 | 25.179 | 0.049347 |  | 7274 | 25.179 | 104.72 | 14.696 | 0.070295 | 0.049347
7275 | 104.73 | 14.696 | 0.070293 | 25.182 | 0.049351 |  | 7275 | 25.182 | 104.73 | 14.696 | 0.070293 | 0.049351
7276 | 104.74 | 14.696 | 0.070292 | 25.184 | 0.049355 |  | 7276 | 25.184 | 104.74 | 14.696 | 0.070292 | 0.049355
7277 | 104.75 | 14.696 | 0.070291 | 25.186 | 0.04936 |  | 7277 | 25.186 | 104.75 | 14.696 | 0.070291 | 0.04936
7278 | 104.76 | 14.696 | 0.07029 | 25.189 | 0.049364 |  | 7278 | 25.189 | 104.76 | 14.696 | 0.07029 | 0.049364
7279 | 104.77 | 14.696 | 0.070288 | 25.191 | 0.049368 |  | 7279 | 25.191 | 104.77 | 14.696 | 0.070288 | 0.049368
7280 | 104.78 | 14.696 | 0.070287 | 25.194 | 0.049372 |  | 7280 | 25.194 | 104.78 | 14.696 | 0.070287 | 0.049372
7281 | 104.79 | 14.696 | 0.070286 | 25.196 | 0.049377 |  | 7281 | 25.196 | 104.79 | 14.696 | 0.070286 | 0.049377
7282 | 104.8 | 14.696 | 0.070285 | 25.199 | 0.049381 |  | 7282 | 25.199 | 104.8 | 14.696 | 0.070285 | 0.049381
7283 | 104.81 | 14.696 | 0.070283 | 25.201 | 0.049385 |  | 7283 | 25.201 | 104.81 | 14.696 | 0.070283 | 0.049385
7284 | 104.82 | 14.696 | 0.070282 | 25.203 | 0.049389 |  | 7284 | 25.203 | 104.82 | 14.696 | 0.070282 | 0.049389
7285 | 104.83 | 14.696 | 0.070281 | 25.206 | 0.049394 |  | 7285 | 25.206 | 104.83 | 14.696 | 0.070281 | 0.049394
7286 | 104.84 | 14.696 | 0.07028 | 25.208 | 0.049398 |  | 7286 | 25.208 | 104.84 | 14.696 | 0.07028 | 0.049398
7287 | 104.85 | 14.696 | 0.070278 | 25.211 | 0.049402 |  | 7287 | 25.211 | 104.85 | 14.696 | 0.070278 | 0.049402
7288 | 104.86 | 14.696 | 0.070277 | 25.213 | 0.049406 |  | 7288 | 25.213 | 104.86 | 14.696 | 0.070277 | 0.049406
7289 | 104.87 | 14.696 | 0.070276 | 25.215 | 0.049411 |  | 7289 | 25.215 | 104.87 | 14.696 | 0.070276 | 0.049411
7290 | 104.88 | 14.696 | 0.070275 | 25.218 | 0.049415 |  | 7290 | 25.218 | 104.88 | 14.696 | 0.070275 | 0.049415
7291 | 104.89 | 14.696 | 0.070273 | 25.22 | 0.049419 |  | 7291 | 25.22 | 104.89 | 14.696 | 0.070273 | 0.049419
7292 | 104.9 | 14.696 | 0.070272 | 25.223 | 0.049423 |  | 7292 | 25.223 | 104.9 | 14.696 | 0.070272 | 0.049423
7293 | 104.91 | 14.696 | 0.070271 | 25.225 | 0.049428 |  | 7293 | 25.225 | 104.91 | 14.696 | 0.070271 | 0.049428
7294 | 104.92 | 14.696 | 0.07027 | 25.227 | 0.049432 |  | 7294 | 25.227 | 104.92 | 14.696 | 0.07027 | 0.049432
7295 | 104.93 | 14.696 | 0.070268 | 25.23 | 0.049436 |  | 7295 | 25.23 | 104.93 | 14.696 | 0.070268 | 0.049436
7296 | 104.94 | 14.696 | 0.070267 | 25.232 | 0.049441 |  | 7296 | 25.232 | 104.94 | 14.696 | 0.070267 | 0.049441
7297 | 104.95 | 14.696 | 0.070266 | 25.235 | 0.049445 |  | 7297 | 25.235 | 104.95 | 14.696 | 0.070266 | 0.049445
7298 | 104.96 | 14.696 | 0.070265 | 25.237 | 0.049449 |  | 7298 | 25.237 | 104.96 | 14.696 | 0.070265 | 0.049449
7299 | 104.97 | 14.696 | 0.070263 | 25.239 | 0.049453 |  | 7299 | 25.239 | 104.97 | 14.696 | 0.070263 | 0.049453
7300 | 104.98 | 14.696 | 0.070262 | 25.242 | 0.049458 |  | 7300 | 25.242 | 104.98 | 14.696 | 0.070262 | 0.049458
7301 | 104.99 | 14.696 | 0.070261 | 25.244 | 0.049462 |  | 7301 | 25.244 | 104.99 | 14.696 | 0.070261 | 0.049462
7302 | 105 | 14.696 | 0.07026 | 25.247 | 0.049466 |  | 7302 | 25.247 | 105 | 14.696 | 0.07026 | 0.049466
7303 | 105.01 | 14.696 | 0.070258 | 25.249 | 0.04947 |  | 7303 | 25.249 | 105.01 | 14.696 | 0.070258 | 0.04947
7304 | 105.02 | 14.696 | 0.070257 | 25.251 | 0.049475 |  | 7304 | 25.251 | 105.02 | 14.696 | 0.070257 | 0.049475
7305 | 105.03 | 14.696 | 0.070256 | 25.254 | 0.049479 |  | 7305 | 25.254 | 105.03 | 14.696 | 0.070256 | 0.049479
7306 | 105.04 | 14.696 | 0.070255 | 25.256 | 0.049483 |  | 7306 | 25.256 | 105.04 | 14.696 | 0.070255 | 0.049483
7307 | 105.05 | 14.696 | 0.070253 | 25.259 | 0.049487 |  | 7307 | 25.259 | 105.05 | 14.696 | 0.070253 | 0.049487
7308 | 105.06 | 14.696 | 0.070252 | 25.261 | 0.049492 |  | 7308 | 25.261 | 105.06 | 14.696 | 0.070252 | 0.049492
7309 | 105.07 | 14.696 | 0.070251 | 25.264 | 0.049496 |  | 7309 | 25.264 | 105.07 | 14.696 | 0.070251 | 0.049496
7310 | 105.08 | 14.696 | 0.07025 | 25.266 | 0.0495 |  | 7310 | 25.266 | 105.08 | 14.696 | 0.07025 | 0.0495
7311 | 105.09 | 14.696 | 0.070248 | 25.268 | 0.049504 |  | 7311 | 25.268 | 105.09 | 14.696 | 0.070248 | 0.049504
7312 | 105.1 | 14.696 | 0.070247 | 25.271 | 0.049509 |  | 7312 | 25.271 | 105.1 | 14.696 | 0.070247 | 0.049509
7313 | 105.11 | 14.696 | 0.070246 | 25.273 | 0.049513 |  | 7313 | 25.273 | 105.11 | 14.696 | 0.070246 | 0.049513
7314 | 105.12 | 14.696 | 0.070245 | 25.276 | 0.049517 |  | 7314 | 25.276 | 105.12 | 14.696 | 0.070245 | 0.049517
7315 | 105.13 | 14.696 | 0.070243 | 25.278 | 0.049521 |  | 7315 | 25.278 | 105.13 | 14.696 | 0.070243 | 0.049521
7316 | 105.14 | 14.696 | 0.070242 | 25.28 | 0.049526 |  | 7316 | 25.28 | 105.14 | 14.696 | 0.070242 | 0.049526
7317 | 105.15 | 14.696 | 0.070241 | 25.283 | 0.04953 |  | 7317 | 25.283 | 105.15 | 14.696 | 0.070241 | 0.04953
7318 | 105.16 | 14.696 | 0.07024 | 25.285 | 0.049534 |  | 7318 | 25.285 | 105.16 | 14.696 | 0.07024 | 0.049534
7319 | 105.17 | 14.696 | 0.070238 | 25.288 | 0.049539 |  | 7319 | 25.288 | 105.17 | 14.696 | 0.070238 | 0.049539
7320 | 105.18 | 14.696 | 0.070237 | 25.29 | 0.049543 |  | 7320 | 25.29 | 105.18 | 14.696 | 0.070237 | 0.049543
7321 | 105.19 | 14.696 | 0.070236 | 25.292 | 0.049547 |  | 7321 | 25.292 | 105.19 | 14.696 | 0.070236 | 0.049547
7322 | 105.2 | 14.696 | 0.070235 | 25.295 | 0.049551 |  | 7322 | 25.295 | 105.2 | 14.696 | 0.070235 | 0.049551
7323 | 105.21 | 14.696 | 0.070234 | 25.297 | 0.049556 |  | 7323 | 25.297 | 105.21 | 14.696 | 0.070234 | 0.049556
7324 | 105.22 | 14.696 | 0.070232 | 25.3 | 0.04956 |  | 7324 | 25.3 | 105.22 | 14.696 | 0.070232 | 0.04956
7325 | 105.23 | 14.696 | 0.070231 | 25.302 | 0.049564 |  | 7325 | 25.302 | 105.23 | 14.696 | 0.070231 | 0.049564
7326 | 105.24 | 14.696 | 0.07023 | 25.304 | 0.049568 |  | 7326 | 25.304 | 105.24 | 14.696 | 0.07023 | 0.049568
7327 | 105.25 | 14.696 | 0.070229 | 25.307 | 0.049573 |  | 7327 | 25.307 | 105.25 | 14.696 | 0.070229 | 0.049573
7328 | 105.26 | 14.696 | 0.070227 | 25.309 | 0.049577 |  | 7328 | 25.309 | 105.26 | 14.696 | 0.070227 | 0.049577
7329 | 105.27 | 14.696 | 0.070226 | 25.312 | 0.049581 |  | 7329 | 25.312 | 105.27 | 14.696 | 0.070226 | 0.049581
7330 | 105.28 | 14.696 | 0.070225 | 25.314 | 0.049585 |  | 7330 | 25.314 | 105.28 | 14.696 | 0.070225 | 0.049585
7331 | 105.29 | 14.696 | 0.070224 | 25.316 | 0.04959 |  | 7331 | 25.316 | 105.29 | 14.696 | 0.070224 | 0.04959
7332 | 105.3 | 14.696 | 0.070222 | 25.319 | 0.049594 |  | 7332 | 25.319 | 105.3 | 14.696 | 0.070222 | 0.049594
7333 | 105.31 | 14.696 | 0.070221 | 25.321 | 0.049598 |  | 7333 | 25.321 | 105.31 | 14.696 | 0.070221 | 0.049598
7334 | 105.32 | 14.696 | 0.07022 | 25.324 | 0.049602 |  | 7334 | 25.324 | 105.32 | 14.696 | 0.07022 | 0.049602
7335 | 105.33 | 14.696 | 0.070219 | 25.326 | 0.049607 |  | 7335 | 25.326 | 105.33 | 14.696 | 0.070219 | 0.049607
7336 | 105.34 | 14.696 | 0.070217 | 25.328 | 0.049611 |  | 7336 | 25.328 | 105.34 | 14.696 | 0.070217 | 0.049611
7337 | 105.35 | 14.696 | 0.070216 | 25.331 | 0.049615 |  | 7337 | 25.331 | 105.35 | 14.696 | 0.070216 | 0.049615
7338 | 105.36 | 14.696 | 0.070215 | 25.333 | 0.049619 |  | 7338 | 25.333 | 105.36 | 14.696 | 0.070215 | 0.049619
7339 | 105.37 | 14.696 | 0.070214 | 25.336 | 0.049624 |  | 7339 | 25.336 | 105.37 | 14.696 | 0.070214 | 0.049624
7340 | 105.38 | 14.696 | 0.070212 | 25.338 | 0.049628 |  | 7340 | 25.338 | 105.38 | 14.696 | 0.070212 | 0.049628
7341 | 105.39 | 14.696 | 0.070211 | 25.341 | 0.049632 |  | 7341 | 25.341 | 105.39 | 14.696 | 0.070211 | 0.049632
7342 | 105.4 | 14.696 | 0.07021 | 25.343 | 0.049637 |  | 7342 | 25.343 | 105.4 | 14.696 | 0.07021 | 0.049637
7343 | 105.41 | 14.696 | 0.070209 | 25.345 | 0.049641 |  | 7343 | 25.345 | 105.41 | 14.696 | 0.070209 | 0.049641
7344 | 105.42 | 14.696 | 0.070207 | 25.348 | 0.049645 |  | 7344 | 25.348 | 105.42 | 14.696 | 0.070207 | 0.049645
7345 | 105.43 | 14.696 | 0.070206 | 25.35 | 0.049649 |  | 7345 | 25.35 | 105.43 | 14.696 | 0.070206 | 0.049649
7346 | 105.44 | 14.696 | 0.070205 | 25.353 | 0.049654 |  | 7346 | 25.353 | 105.44 | 14.696 | 0.070205 | 0.049654
7347 | 105.45 | 14.696 | 0.070204 | 25.355 | 0.049658 |  | 7347 | 25.355 | 105.45 | 14.696 | 0.070204 | 0.049658
7348 | 105.46 | 14.696 | 0.070202 | 25.357 | 0.049662 |  | 7348 | 25.357 | 105.46 | 14.696 | 0.070202 | 0.049662
7349 | 105.47 | 14.696 | 0.070201 | 25.36 | 0.049666 |  | 7349 | 25.36 | 105.47 | 14.696 | 0.070201 | 0.049666
7350 | 105.48 | 14.696 | 0.0702 | 25.362 | 0.049671 |  | 7350 | 25.362 | 105.48 | 14.696 | 0.0702 | 0.049671
7351 | 105.49 | 14.696 | 0.070199 | 25.365 | 0.049675 |  | 7351 | 25.365 | 105.49 | 14.696 | 0.070199 | 0.049675
7352 | 105.5 | 14.696 | 0.070197 | 25.367 | 0.049679 |  | 7352 | 25.367 | 105.5 | 14.696 | 0.070197 | 0.049679
7353 | 105.51 | 14.696 | 0.070196 | 25.369 | 0.049683 |  | 7353 | 25.369 | 105.51 | 14.696 | 0.070196 | 0.049683
7354 | 105.52 | 14.696 | 0.070195 | 25.372 | 0.049688 |  | 7354 | 25.372 | 105.52 | 14.696 | 0.070195 | 0.049688
7355 | 105.53 | 14.696 | 0.070194 | 25.374 | 0.049692 |  | 7355 | 25.374 | 105.53 | 14.696 | 0.070194 | 0.049692
7356 | 105.54 | 14.696 | 0.070192 | 25.377 | 0.049696 |  | 7356 | 25.377 | 105.54 | 14.696 | 0.070192 | 0.049696
7357 | 105.55 | 14.696 | 0.070191 | 25.379 | 0.0497 |  | 7357 | 25.379 | 105.55 | 14.696 | 0.070191 | 0.0497
7358 | 105.56 | 14.696 | 0.07019 | 25.381 | 0.049705 |  | 7358 | 25.381 | 105.56 | 14.696 | 0.07019 | 0.049705
7359 | 105.57 | 14.696 | 0.070189 | 25.384 | 0.049709 |  | 7359 | 25.384 | 105.57 | 14.696 | 0.070189 | 0.049709
7360 | 105.58 | 14.696 | 0.070187 | 25.386 | 0.049713 |  | 7360 | 25.386 | 105.58 | 14.696 | 0.070187 | 0.049713
7361 | 105.59 | 14.696 | 0.070186 | 25.389 | 0.049717 |  | 7361 | 25.389 | 105.59 | 14.696 | 0.070186 | 0.049717
7362 | 105.6 | 14.696 | 0.070185 | 25.391 | 0.049722 |  | 7362 | 25.391 | 105.6 | 14.696 | 0.070185 | 0.049722
7363 | 105.61 | 14.696 | 0.070184 | 25.393 | 0.049726 |  | 7363 | 25.393 | 105.61 | 14.696 | 0.070184 | 0.049726
7364 | 105.62 | 14.696 | 0.070182 | 25.396 | 0.04973 |  | 7364 | 25.396 | 105.62 | 14.696 | 0.070182 | 0.04973
7365 | 105.63 | 14.696 | 0.070181 | 25.398 | 0.049734 |  | 7365 | 25.398 | 105.63 | 14.696 | 0.070181 | 0.049734
7366 | 105.64 | 14.696 | 0.07018 | 25.401 | 0.049739 |  | 7366 | 25.401 | 105.64 | 14.696 | 0.07018 | 0.049739
7367 | 105.65 | 14.696 | 0.070179 | 25.403 | 0.049743 |  | 7367 | 25.403 | 105.65 | 14.696 | 0.070179 | 0.049743
7368 | 105.66 | 14.696 | 0.070177 | 25.405 | 0.049747 |  | 7368 | 25.405 | 105.66 | 14.696 | 0.070177 | 0.049747
7369 | 105.67 | 14.696 | 0.070176 | 25.408 | 0.049751 |  | 7369 | 25.408 | 105.67 | 14.696 | 0.070176 | 0.049751
7370 | 105.68 | 14.696 | 0.070175 | 25.41 | 0.049756 |  | 7370 | 25.41 | 105.68 | 14.696 | 0.070175 | 0.049756
7371 | 105.69 | 14.696 | 0.070174 | 25.413 | 0.04976 |  | 7371 | 25.413 | 105.69 | 14.696 | 0.070174 | 0.04976
7372 | 105.7 | 14.696 | 0.070173 | 25.415 | 0.049764 |  | 7372 | 25.415 | 105.7 | 14.696 | 0.070173 | 0.049764
7373 | 105.71 | 14.696 | 0.070171 | 25.418 | 0.049768 |  | 7373 | 25.418 | 105.71 | 14.696 | 0.070171 | 0.049768
7374 | 105.72 | 14.696 | 0.07017 | 25.42 | 0.049773 |  | 7374 | 25.42 | 105.72 | 14.696 | 0.07017 | 0.049773
7375 | 105.73 | 14.696 | 0.070169 | 25.422 | 0.049777 |  | 7375 | 25.422 | 105.73 | 14.696 | 0.070169 | 0.049777
7376 | 105.74 | 14.696 | 0.070168 | 25.425 | 0.049781 |  | 7376 | 25.425 | 105.74 | 14.696 | 0.070168 | 0.049781
7377 | 105.75 | 14.696 | 0.070166 | 25.427 | 0.049786 |  | 7377 | 25.427 | 105.75 | 14.696 | 0.070166 | 0.049786
7378 | 105.76 | 14.696 | 0.070165 | 25.43 | 0.04979 |  | 7378 | 25.43 | 105.76 | 14.696 | 0.070165 | 0.04979
7379 | 105.77 | 14.696 | 0.070164 | 25.432 | 0.049794 |  | 7379 | 25.432 | 105.77 | 14.696 | 0.070164 | 0.049794