## Cross-check
y = 0.2x3 - 26.5x2 + 1,238.0x - 16,140.8 |  | y = 0.1816x3 - 26.539x2 + 1238x - 16141 |  | y = 0.18162922x3 - 26.53867426x2 + 1,237.95410915x - 16,140.80378586
X | Y | X | Y | X | Y
40 | 3780 | 40 | 2539 | 40 | 2539.7518
45 | 4132.5 | 45 | 2375.825 | 45 | 2377.2784
50 | 4510 | 50 | 2111.5 | 50 | 2113.8685
55 | 5062.5 | 55 | 1882.225 | 55 | 1885.7441
60 | 5940 | 60 | 1824.2 | 60 | 1829.1269
65 | 7292.5 | 65 | 2073.625 | 65 | 2080.2391
70 | 9270 | 70 | 2766.7 | 70 | 2775.3024
75 | 12022.5 | 75 | 4039.625 | 75 | 4050.5389
80 | 15700 | 80 | 6028.6 | 80 | 6042.1703
85 | 20452.5 | 85 | 8869.825 | 85 | 8886.4187
90 | 26430 | 90 | 12699.5 | 90 | 12719.5059
95 | 33782.5 | 95 | 17653.825 | 95 | 17677.6539
100 | 42660 | 100 | 23869 | 100 | 23897.0845
105 | 53212.5 | 105 | 31481.225 | 105 | 31514.0198
110 | 65590 | 110 | 40626.7 | 110 | 40664.6815
115 | 79942.5 | 115 | 51441.625 | 115 | 51485.2916

## Combined
Data | Nominal Capacity, tons | Nominal full load kW | Nominal kW/ton | Evaporator Flow, gpm | Nominal Δt, °F | Date of Manufacture | [31 empty] | Chillers Running Axis |  | Scale factor = | 10 | Design Δt Line
Chiller 1 - | 1470 | 744 | 0.50612 | 2687 | 13.1299 | 2010-09-22 | [31 empty] | X | Y | Lables |  | X | Y
Chiller 2 - | 1470 | 821 | 0.5585 | 3000 | 11.76 | 2013-11-21 | [31 empty] | 43385.9583 | 0 | 0 |  | 43383.5 | 11.5435
Chiller 3 - | 1470 | 818 | 0.55646 | 3000 | 11.76 | 2015-08-27 | [31 empty] | 43385.9583 | 10 | 1 |  | 43385.95 | 11.5435
Chiller 4 - | 1470 | 821 | 0.5585 | 3000 | 11.76 | 2012-03-28 | [31 empty] | 43385.9583 | 20 | 2
Chiller 5 - | 1470 | 816 | 0.5551 | 3000 | 11.76 | 2016-02-11 | [31 empty] | 43385.9583 | 30 | 3
Chiller 6 - | 1300 | 703 | 0.54077 | 3000 | 10.4 | 2010-09-29 | [31 empty] | 43385.9583 | 40 | 4
Chiller 7 - | 1300 | 703 | 0.54077 | 3000 | 10.4 | 2010-09-29 | [31 empty] | 43385.9583 | 50 | 5
Total - | 9950 | 5426 | 0.54533 | 20687 | 11.5435 | [32 empty] | 43385.9583 | 60 | 6
Distribution Pump Rating - |  |  |  | 23700 | [33 empty] | 43385.9583 | 70 | 7
The following assumes that the tons are approximately linearly related linearly to the % RLA | [37 empty] | 43385.9583 | 80 | 8
[38 empty] | 43385.9583 | 90 | 9
[38 empty] | 43385.9583 | 100 | 10
Date and time | Hour of Day | Day of Week (Sumnday = 1) | Chiller 1 |  | Chiller 2 |  | Chiller 3 |  | Chiller 4 |  | Chiller 5 |  | Chiller 6 |  | Chiller 7 |  | Total Tons | OAT, °F | Chiller Running; 1/Green = On, 0/Red = Off
[19 empty] | Chiller 1 |  | Chiller 2 |  | Chiller 3 |  | Chiller 4 |  | Chiller 5 |  | Chiller 6 |  | Chiller 7 |  | Number of Chillers Running | Total Evaporator Flow, gpm | Calculated Plant Δt, °F | Chillers Running Scaled for 3rd Axis | Estimated Number of Chillers Required; Yellow = More than may be needed | Estimated Chillers Scaled
|  |  | % RLA | Tons | % RLA | Tons | % RLA | Tons | % RLA | Tons | % RLA | Tons | % RLA | Tons | % RLA | Tons |  |  | On/Off | Evaporator Flow, gpm | On/Off | Evaporator Flow, gpm | On/Off | Evaporator Flow, gpm | On/Off | Evaporator Flow, gpm | On/Off | Evaporator Flow, gpm | On/Off | Evaporator Flow, gpm | On/Off | Evaporator Flow, gpm
2018-10-10 16:48 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 0 | 0 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 3473.7217 | 82.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 4 | 11687 | 7.1335 | 40 | 3 | 30
2018-10-10 16:49 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 82.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:50 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 82.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:51 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 82.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:52 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 82.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:53 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:54 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:55 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:56 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:57 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:58 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 16:59 | 16 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:00 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:01 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:02 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:03 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:04 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:05 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:06 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:07 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:08 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:09 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:10 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:11 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:12 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:13 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:14 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:15 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:16 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:17 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:18 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:19 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:20 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:21 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:22 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:23 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:24 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:25 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:26 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:27 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:28 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:29 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:30 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:31 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:32 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:33 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:34 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:35 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:36 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:37 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:38 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 78.1 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:39 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:40 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:41 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:42 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:43 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:44 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:45 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:46 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:47 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:48 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:49 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:50 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:51 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:52 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:53 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:54 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:55 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:56 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:57 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:58 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 17:59 | 17 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:00 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:01 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:02 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:03 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:04 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:05 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:06 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:07 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:08 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:09 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:10 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:11 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:12 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:13 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:14 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:15 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:16 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:17 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:18 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:19 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:20 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:21 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:22 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:23 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:24 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:25 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:26 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:27 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:28 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:29 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:30 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:31 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:32 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:33 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:34 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:35 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:36 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:37 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:38 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:39 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:40 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:41 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:42 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:43 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:44 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:45 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:46 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:47 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:48 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:49 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:50 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:51 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:52 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:53 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:54 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:55 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:56 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:57 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:58 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 18:59 | 18 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:00 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:01 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:02 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:03 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:04 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:05 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:06 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:07 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:08 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:09 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:10 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:11 | 19 | 4 | 89.9849 | 1322.778 | 91.1212 | 1339.4816 | 62.4648 | 918.2326 | 0 | 0 | 0 | 0 | 55.2015 | 811.462 | 94.2781 | 1385.8881 | 4391.9543 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.1769 | 50 | 3 | 30
2018-10-10 19:12 | 19 | 4 | 90 | 1323 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 90.4418 | 1329.4945 | 4622.4679 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.5536 | 50 | 4 | 40
2018-10-10 19:13 | 19 | 4 | 90 | 1323 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4622.4679 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.5536 | 50 | 4 | 40
2018-10-10 19:14 | 19 | 4 | 90 | 1323 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4622.4679 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 7.5536 | 50 | 4 | 40
2018-10-10 19:15 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:16 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:17 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:18 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:19 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:20 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:21 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:22 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:23 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:24 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:25 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:26 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:27 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:28 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:29 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:30 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:31 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:32 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:33 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:34 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:35 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:36 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:37 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:38 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:39 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:40 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:41 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:42 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:43 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:44 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:45 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:46 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:47 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:48 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:49 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:50 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:51 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:52 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73.9 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:53 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:54 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:55 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:56 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:57 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:58 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 19:59 | 19 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:00 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:01 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:02 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:03 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:04 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:05 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:06 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:07 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:08 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:09 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:10 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:11 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:12 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:13 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:14 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:15 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:16 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:17 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:18 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:19 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:20 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:21 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:22 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:23 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:24 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:25 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:26 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:27 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:28 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:29 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:30 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:31 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:32 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:33 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:34 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:35 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:36 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:37 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:38 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:39 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:40 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:41 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:42 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:43 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:44 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:45 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:46 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:47 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:48 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:49 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:50 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:51 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:52 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:53 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:54 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:55 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:56 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:57 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:58 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 20:59 | 20 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:00 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:01 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:02 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:03 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:04 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:05 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:06 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:07 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:08 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:09 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:10 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:11 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:12 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:13 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:14 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:15 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:16 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:17 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:18 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:19 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:20 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:21 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:22 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:23 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:24 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:25 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:26 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:27 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:28 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:29 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:30 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:31 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:32 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:33 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:34 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 94.1002 | 1383.2729 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 4272.9681 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.9824 | 50 | 3 | 30
2018-10-10 21:35 | 21 | 4 | 66.2245 | 973.5002 | 76.9132 | 1130.624 | 75.0961 | 1103.9127 | 0 | 0 | 0 | 0 | 53.4402 | 785.5709 | 66.0674 | 971.1908 | 3993.6078 | 73 | 1 | 2687 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.5259 | 50 | 3 | 30
2018-10-10 21:36 | 21 | 4 | 69.3378 | 1019.2657 | 80.1684 | 1178.4755 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4219.0705 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8944 | 50 | 3 | 30
2018-10-10 21:37 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:38 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:39 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:40 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:41 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:42 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:43 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:44 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:45 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:46 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:47 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:48 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:49 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:50 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:51 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:52 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:53 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:54 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:55 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:56 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:57 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:58 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 21:59 | 21 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:00 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:01 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:02 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:03 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:04 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:05 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:06 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:07 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:08 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:09 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:10 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:11 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:12 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:13 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:14 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:15 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:16 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:17 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:18 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:19 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:20 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:21 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:22 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:23 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:24 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:25 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:26 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:27 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:28 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:29 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:30 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:31 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:32 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:33 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:34 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:35 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:36 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:37 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:38 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:39 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:40 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:41 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:42 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:43 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:44 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:45 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:46 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:47 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:48 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:49 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:50 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:51 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:52 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:53 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:54 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:55 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:56 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:57 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:58 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 22:59 | 22 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:00 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:01 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:02 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:03 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:04 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:05 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:06 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:07 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:08 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:09 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:10 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:11 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:12 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:13 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:14 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:15 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:16 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:17 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:18 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:19 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:20 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:21 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:22 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:23 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:24 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:25 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:26 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:27 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:28 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:29 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:30 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:31 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:32 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:33 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:34 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:35 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:36 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:37 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:38 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:39 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:40 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:41 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:42 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:43 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:44 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:45 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:46 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:47 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:48 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:49 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:50 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:51 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:52 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:53 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:54 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:55 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:56 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:57 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:58 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-10 23:59 | 23 | 4 | 69.3378 | 1019.2657 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 81.193 | 1193.5371 | 56.3124 | 827.7923 | 58.0327 | 853.0807 | 4202.0185 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8665 | 50 | 3 | 30
2018-10-11 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 54.2794 | 797.9072 | 58.6031 | 861.4656 | 4183.6112 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 5 | 14687 | 6.8364 | 50 | 3 | 30
2018-10-11 00:01 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:02 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:03 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:04 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:05 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:06 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:07 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:08 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:09 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:10 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:11 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:12 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:13 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:14 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:15 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:16 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:17 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:18 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:19 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:20 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:21 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:22 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:23 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:24 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:25 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:26 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:27 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:28 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:29 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:30 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:31 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:32 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:33 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:34 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:35 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:36 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:37 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:38 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:39 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:40 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:41 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:42 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:43 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:44 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:45 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:46 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:47 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:48 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:49 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:50 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:51 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:52 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:53 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:54 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:55 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:56 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:57 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:58 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 00:59 | 0 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:00 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:01 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:02 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:03 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:04 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:05 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:06 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:07 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:08 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:09 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:10 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:11 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:12 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:13 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:14 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:15 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:16 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:17 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:18 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:19 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:20 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:21 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:22 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:23 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:24 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:25 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:26 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:27 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:28 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:29 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:30 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:31 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:32 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:33 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:34 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:35 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:36 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:37 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:38 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:39 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:40 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:41 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:42 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:43 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:44 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:45 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:46 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:47 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:48 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:49 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:50 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:51 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:52 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73.9 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:53 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:54 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:55 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:56 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:57 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:58 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 01:59 | 1 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:00 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:01 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:02 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:03 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:04 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:05 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:06 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:07 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:08 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:09 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:10 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:11 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:12 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:13 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:14 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:15 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:16 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:17 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:18 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:19 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:20 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:21 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:22 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:23 | 2 | 5 | 67.4189 | 991.0578 | 79.0084 | 1161.4235 | 0 | 0 | 0 | 0 | 83.8927 | 1233.2227 | 0 | 0 | 58.6031 | 861.4656 | 3385.704 | 73 | 1 | 2687 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 4 | 11687 | 6.9528 | 40 | 3 | 30
2018-10-11 02:24 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:25 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:26 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:27 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:28 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:29 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:30 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:31 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:32 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:33 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:34 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:35 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:36 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:37 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:38 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:39 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:40 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:41 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:42 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:43 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:44 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:45 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:46 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:47 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:48 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:49 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:50 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:51 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:52 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 73 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:53 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:54 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:55 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:56 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:57 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:58 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 02:59 | 2 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:00 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:01 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:02 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:03 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:04 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:05 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:06 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:07 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:08 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:09 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:10 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:11 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:12 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:13 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:14 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:15 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:16 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:17 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:18 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:19 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:20 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:21 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:22 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:23 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:24 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:25 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:26 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:27 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:28 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:29 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:30 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:31 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:32 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:33 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:34 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:35 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:36 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:37 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:38 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:39 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:40 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:41 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:42 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:43 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:44 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:45 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:46 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:47 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:48 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:49 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:50 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:51 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:52 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 70 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:53 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:54 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:55 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:56 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:57 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:58 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 03:59 | 3 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:00 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:01 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:02 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:03 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:04 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:05 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:06 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:07 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:08 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:09 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:10 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:11 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:12 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:13 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:14 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:15 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:16 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:17 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:18 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:19 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:20 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:21 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:22 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:23 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:24 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:25 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:26 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:27 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:28 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:29 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:30 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:31 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:32 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:33 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:34 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:35 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:36 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:37 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:38 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:39 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:40 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:41 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:42 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:43 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:44 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:45 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:46 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9237 | 1071.9784 | 0 | 0 | 55.3528 | 813.6862 | 1945.448 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.3748 | 30 | 1 | 10
2018-10-11 04:47 | 4 | 5 | 59.4197 | 873.4696 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6535 | 1229.7064 | 0 | 0 | 55.3528 | 813.6862 | 2103.176 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.8105 | 30 | 2 | 20
2018-10-11 04:48 | 4 | 5 | 61.5359 | 904.5777 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 2145.2724 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.9268 | 30 | 2 | 20
2018-10-11 04:49 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 66.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:50 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 66.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:51 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 66.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:52 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 66.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:53 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:54 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:55 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:56 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:57 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:58 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 04:59 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:00 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:01 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:02 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:03 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:04 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:05 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:06 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:07 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:08 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:09 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:10 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:11 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:12 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:13 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:14 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:15 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:16 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:17 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:18 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:19 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:20 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:21 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:22 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:23 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:24 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:25 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:26 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:27 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:28 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:29 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:30 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:31 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:32 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:33 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:34 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:35 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:36 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:37 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:38 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:39 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:40 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:41 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:42 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:43 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:44 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:45 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:46 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:47 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:48 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:49 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:50 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:51 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:52 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:53 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:54 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:55 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:56 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:57 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:58 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 05:59 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:00 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:01 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:02 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:03 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:04 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:05 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:06 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:07 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:08 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:09 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:10 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:11 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:12 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:13 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:14 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:15 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:16 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:17 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:18 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:19 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:20 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:21 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:22 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:23 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:24 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:25 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:26 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:27 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:28 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:29 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:30 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:31 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:32 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:33 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:34 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:35 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:36 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:37 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:38 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:39 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:40 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:41 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:42 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:43 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:44 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:45 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:46 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:47 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:48 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:49 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:50 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:51 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:52 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:53 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:54 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:55 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:56 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:57 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:58 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 06:59 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:00 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:01 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:02 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:03 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:04 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:05 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:06 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:07 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:08 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:09 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:10 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:11 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.401 | 1240.6947 | 0 | 0 | 55.8984 | 821.7065 | 1240.6947 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9628 | 20 | 1 | 10
2018-10-11 07:12 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 64.5278 | 948.5587 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:13 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:14 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:15 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:16 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:17 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:18 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:19 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:20 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:21 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:22 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:23 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:24 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:25 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:26 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:27 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:28 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:29 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:30 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:31 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:32 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:33 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:34 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:35 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:36 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:37 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:38 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:39 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:40 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:41 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:42 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:43 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:44 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:45 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:46 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:47 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:48 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:49 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:50 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:51 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:52 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:53 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:54 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:55 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:56 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:57 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:58 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 07:59 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:00 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:01 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:02 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:03 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:04 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:05 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:06 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:07 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:08 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:09 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:10 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:11 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:12 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:13 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:14 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:15 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:16 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:17 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:18 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:19 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:20 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:21 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:22 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:23 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:24 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:25 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:26 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:27 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:28 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:29 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:30 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:31 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:32 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:33 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:34 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:35 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:36 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:37 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:38 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:39 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:40 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:41 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:42 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:43 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:44 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:45 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:46 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:47 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:48 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:49 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:50 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:51 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:52 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:53 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:54 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:55 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:56 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:57 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:58 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 08:59 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:00 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:01 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:02 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:03 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:04 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:05 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:06 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:07 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:08 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:09 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:10 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:11 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:12 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:13 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:14 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:15 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:16 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:17 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:18 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:19 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:20 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:21 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:22 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:23 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:24 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:25 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:26 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:27 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:28 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:29 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:30 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:31 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:32 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:33 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:34 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:35 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2543 | 1253.2382 | 0 | 0 | 59.1809 | 869.9592 | 1253.2382 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.013 | 20 | 1 | 10
2018-10-11 09:36 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:37 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:38 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:39 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:40 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:41 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:42 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:43 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:44 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:45 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:46 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:47 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:48 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:49 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:50 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:51 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:52 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:53 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:54 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:55 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:56 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:57 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:58 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 09:59 | 9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:00 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:01 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:02 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:03 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:04 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:05 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:06 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:07 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:08 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:09 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:10 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:11 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:12 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:13 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:14 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:15 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:16 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:17 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:18 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:19 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:20 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:21 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:22 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:23 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:24 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:25 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:26 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:27 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:28 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:29 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:30 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:31 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:32 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:33 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:34 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:35 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:36 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:37 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:38 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:39 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:40 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:41 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:42 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:43 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:44 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:45 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:46 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:47 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:48 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:49 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:50 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:51 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:52 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:53 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:54 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:55 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:56 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:57 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:58 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 10:59 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:00 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:01 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:02 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:03 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:04 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:05 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:06 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:07 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:08 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:09 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:10 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:11 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:12 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:13 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:14 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:15 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:16 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:17 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:18 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:19 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:20 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:21 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:22 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:23 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:24 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:25 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:26 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:27 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:28 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:29 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:30 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:31 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:32 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:33 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:34 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:35 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:36 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:37 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:38 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:39 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:40 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:41 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:42 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:43 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:44 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:45 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:46 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:47 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:48 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:49 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:50 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:51 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:52 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 57.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:53 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:54 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:55 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:56 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:57 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:58 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 11:59 | 11 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1137 | 1162.9714 | 0 | 0 | 56.9179 | 836.6931 | 1162.9714 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.6519 | 20 | 1 | 10
2018-10-11 12:00 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:01 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:02 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:03 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:04 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:05 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:06 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:07 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:08 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:09 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:10 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:11 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:12 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:13 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:14 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:15 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:16 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:17 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:18 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:19 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:20 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 60.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:21 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:22 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:23 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:24 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:25 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:26 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:27 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:28 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:29 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:30 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:31 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:32 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:33 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:34 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:35 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:36 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:37 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:38 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:39 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:40 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:41 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:42 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:43 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:44 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:45 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:46 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:47 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:48 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:49 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:50 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:51 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:52 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:53 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:54 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:55 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:56 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:57 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:58 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 12:59 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:00 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:01 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:02 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:03 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:04 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:05 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:06 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:07 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:08 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:09 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:10 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:11 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:12 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:13 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:14 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:15 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:16 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:17 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:18 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:19 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:20 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:21 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:22 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:23 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:24 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:25 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:26 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:27 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:28 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:29 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:30 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:31 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:32 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:33 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:34 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:35 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:36 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:37 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:38 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:39 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:40 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:41 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:42 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:43 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:44 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:45 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:46 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:47 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:48 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:49 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:50 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:51 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:52 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 64.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:53 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:54 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:55 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:56 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:57 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:58 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 13:59 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:00 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:01 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:02 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:03 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:04 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:05 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:06 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:07 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:08 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:09 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:10 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:11 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:12 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:13 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:14 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:15 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:16 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:17 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:18 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:19 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:20 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:21 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:22 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:23 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8647 | 1232.8111 | 0 | 0 | 60.5639 | 890.2893 | 1232.8111 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 4.9312 | 20 | 1 | 10
2018-10-11 14:24 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 1336.3902 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 2 | 6000 | 5.3456 | 20 | 1 | 10
2018-10-11 14:25 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:26 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:27 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:28 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:29 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:30 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:31 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:32 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:33 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:34 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:35 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:36 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:37 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:38 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:39 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:40 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:41 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:42 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:43 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:44 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:45 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:46 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:47 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:48 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:49 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:50 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:51 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:52 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:53 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:54 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:55 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:56 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:57 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:58 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 14:59 | 14 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:00 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:01 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:02 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:03 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:04 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:05 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:06 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:07 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:08 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:09 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:10 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:11 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:12 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:13 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:14 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:15 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:16 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:17 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:18 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:19 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:20 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:21 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:22 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:23 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:24 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:25 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:26 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:27 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:28 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:29 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:30 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:31 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:32 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:33 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:34 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:35 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:36 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:37 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:38 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:39 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:40 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:41 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:42 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:43 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:44 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:45 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:46 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:47 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:48 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:49 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:50 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:51 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:52 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:53 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:54 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:55 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:56 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:57 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:58 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 15:59 | 15 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:00 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:01 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:02 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:03 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:04 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:05 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:06 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:07 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:08 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:09 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:10 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:11 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:12 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:13 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:14 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:15 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:16 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:17 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:18 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:19 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:20 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:21 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:22 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:23 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:24 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:25 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:26 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:27 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:28 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:29 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:30 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:31 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:32 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:33 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:34 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:35 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:36 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:37 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:38 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:39 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:40 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:41 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:42 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:43 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:44 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:45 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:46 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:47 | 16 | 5 | 70.7447 | 1039.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9109 | 1336.3902 | 0 | 0 | 66.4328 | 976.5622 | 2376.3373 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 6.5652 | 30 | 2 | 20
2018-10-11 16:48 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:49 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:50 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:51 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:52 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66.9 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:53 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:54 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:55 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:56 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:57 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:58 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 16:59 | 16 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:00 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:01 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:02 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:03 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:04 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:05 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:06 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:07 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:08 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:09 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:10 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:11 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:12 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:13 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:14 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:15 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:16 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:17 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:18 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:19 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:20 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:21 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:22 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:23 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:24 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:25 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:26 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:27 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:28 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:29 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:30 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:31 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:32 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:33 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:34 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:35 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:36 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:37 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:38 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:39 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:40 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:41 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:42 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:43 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:44 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:45 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:46 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:47 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:48 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:49 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:50 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:51 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:52 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 66 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:53 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:54 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:55 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:56 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:57 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:58 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 17:59 | 17 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:00 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:01 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:02 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:03 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:04 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:05 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:06 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:07 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:08 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:09 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:10 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:11 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:12 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:13 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:14 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:15 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:16 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:17 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:18 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:19 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:20 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:21 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:22 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:23 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:24 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:25 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:26 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:27 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:28 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:29 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:30 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:31 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:32 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:33 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:34 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:35 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:36 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:37 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:38 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:39 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:40 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:41 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:42 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:43 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:44 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:45 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:46 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:47 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:48 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:49 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:50 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:51 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:52 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 63 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:53 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:54 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:55 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:56 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:57 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:58 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 18:59 | 18 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:00 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:01 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:02 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:03 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:04 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:05 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:06 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:07 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:08 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:09 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:10 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:11 | 19 | 5 | 64.5424 | 948.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 1124.7308 | 0 | 0 | 55.8984 | 821.7065 | 2073.5041 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.7286 | 30 | 2 | 20
2018-10-11 19:12 | 19 | 5 | 62.2416 | 914.9515 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2006.1252 | 61 | 1 | 2687 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 8687 | 5.5424 | 30 | 2 | 20
2018-10-11 19:13 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:14 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:15 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:16 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:17 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:18 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:19 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:20 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:21 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:22 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:23 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:24 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:25 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:26 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:27 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:28 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:29 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:30 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:31 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:32 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:33 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:34 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:35 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:36 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:37 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:38 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:39 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:40 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:41 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:42 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:43 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:44 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:45 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:46 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:47 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:48 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:49 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:50 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:51 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:52 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:53 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:54 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:55 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:56 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:57 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:58 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 19:59 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:00 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:01 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:02 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:03 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:04 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:05 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:06 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:07 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:08 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:09 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:10 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:11 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:12 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:13 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:14 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:15 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:16 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:17 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:18 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:19 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:20 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:21 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:22 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:23 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:24 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:25 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:26 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:27 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:28 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:29 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:30 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:31 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:32 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:33 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:34 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:35 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:36 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:37 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:38 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:39 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:40 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:41 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:42 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:43 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:44 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:45 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:46 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:47 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:48 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:49 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:50 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:51 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:52 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:53 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:54 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:55 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:56 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:57 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:58 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 20:59 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:00 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:01 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:02 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:03 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:04 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:05 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:06 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:07 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:08 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:09 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:10 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:11 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:12 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:13 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:14 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:15 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:16 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:17 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:18 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:19 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:20 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:21 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:22 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:23 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:24 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:25 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:26 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:27 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:28 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:29 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:30 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:31 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:32 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:33 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:34 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:35 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3733 | 975.6875 | 74.2295 | 1091.1736 | 0 | 0 | 52.5357 | 772.2748 | 2066.8612 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.5116 | 30 | 2 | 20
2018-10-11 21:36 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 48.8578 | 718.2097 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.654 | 30 | 2 | 20
2018-10-11 21:37 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:38 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:39 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:40 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:41 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:42 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:43 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:44 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:45 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:46 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:47 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:48 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:49 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:50 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:51 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:52 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:53 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:54 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:55 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:56 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:57 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:58 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 21:59 | 21 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:00 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:01 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:02 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:03 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:04 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:05 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:06 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:07 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:08 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:09 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:10 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:11 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:12 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:13 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:14 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:15 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:16 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:17 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:18 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:19 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:20 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:21 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:22 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:23 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:24 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:25 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:26 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:27 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:28 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:29 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:30 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:31 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:32 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:33 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:34 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:35 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:36 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:37 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:38 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:39 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:40 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:41 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:42 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:43 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:44 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:45 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:46 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:47 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:48 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:49 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:50 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:51 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:52 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 55.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:53 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:54 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:55 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:56 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:57 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:58 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 22:59 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:00 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:01 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:02 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:03 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:04 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:05 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:06 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:07 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:08 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:09 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:10 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:11 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:12 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:13 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:14 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:15 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:16 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:17 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:18 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:19 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:20 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:21 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:22 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:23 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:24 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:25 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:26 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:27 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:28 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:29 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:30 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:31 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:32 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:33 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:34 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:35 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:36 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:37 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:38 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:39 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:40 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:41 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:42 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:43 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:44 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:45 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:46 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:47 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:48 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:49 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:50 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:51 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:52 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:53 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:54 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:55 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:56 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:57 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:58 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-11 23:59 | 23 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6724 | 1097.6843 | 69.5614 | 1022.5526 | 0 | 0 | 0 | 0 | 2120.2369 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.4809 | 20 | 2 | 20
2018-10-12 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:01 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:02 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:03 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:04 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:05 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:06 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:07 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:08 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:09 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:10 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:11 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:12 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:13 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:14 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:15 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:16 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:17 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:18 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:19 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:20 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:21 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:22 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:23 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:24 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:25 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:26 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:27 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:28 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:29 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:30 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:31 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:32 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:33 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:34 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:35 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:36 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:37 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:38 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:39 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:40 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:41 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:42 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:43 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:44 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:45 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:46 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:47 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:48 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:49 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:50 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:51 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:52 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 53.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:53 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:54 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:55 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:56 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:57 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:58 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 00:59 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:00 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:01 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:02 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:03 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:04 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:05 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:06 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:07 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:08 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:09 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:10 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:11 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:12 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:13 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:14 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:15 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:16 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:17 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:18 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:19 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:20 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:21 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:22 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:23 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:24 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:25 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:26 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:27 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:28 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:29 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:30 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:31 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:32 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:33 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:34 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:35 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:36 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:37 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:38 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:39 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:40 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:41 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:42 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:43 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:44 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:45 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:46 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:47 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:48 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:49 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:50 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:51 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:52 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:53 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:54 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:55 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:56 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:57 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:58 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 01:59 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:00 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:01 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:02 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:03 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:04 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:05 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:06 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:07 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:08 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:09 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:10 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:11 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:12 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:13 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:14 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:15 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:16 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:17 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:18 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:19 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:20 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:21 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:22 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:23 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5416 | 1051.6615 | 71.0027 | 1043.7397 | 0 | 0 | 0 | 0 | 2095.4012 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 8.3816 | 20 | 2 | 20
2018-10-12 02:24 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:25 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:26 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:27 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:28 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:29 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:30 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:31 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:32 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:33 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:34 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:35 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:36 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:37 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:38 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:39 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:40 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:41 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:42 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:43 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:44 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:45 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:46 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:47 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:48 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:49 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:50 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:51 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:52 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:53 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:54 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:55 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:56 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:57 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:58 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 02:59 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:00 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:01 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:02 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:03 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:04 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:05 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:06 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:07 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:08 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:09 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:10 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:11 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:12 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:13 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:14 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:15 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:16 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:17 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:18 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:19 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:20 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:21 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:22 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:23 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:24 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:25 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:26 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:27 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:28 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:29 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:30 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:31 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:32 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:33 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:34 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:35 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:36 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:37 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:38 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:39 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:40 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:41 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:42 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:43 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:44 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:45 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:46 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:47 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:48 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:49 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:50 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:51 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:52 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:53 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:54 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:55 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:56 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:57 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:58 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 03:59 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:00 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:01 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:02 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:03 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:04 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:05 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:06 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:07 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:08 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:09 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:10 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:11 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:12 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:13 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:14 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:15 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:16 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:17 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:18 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:19 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:20 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:21 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:22 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:23 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:24 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:25 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:26 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:27 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:28 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:29 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:30 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:31 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:32 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:33 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:34 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:35 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:36 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:37 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:38 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:39 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:40 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:41 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:42 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:43 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:44 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:45 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:46 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:47 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62.9213 | 924.9431 | 68.8141 | 1011.5673 | 0 | 0 | 0 | 0 | 1936.5104 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.746 | 20 | 1 | 10
2018-10-12 04:48 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:49 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:50 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:51 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:52 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:53 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:54 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:55 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:56 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:57 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:58 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 04:59 | 4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:00 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:01 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:02 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:03 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:04 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:05 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:06 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:07 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:08 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:09 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:10 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:11 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:12 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:13 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:14 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:15 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:16 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:17 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:18 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:19 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:20 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:21 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:22 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:23 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:24 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:25 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:26 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:27 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:28 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:29 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:30 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:31 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:32 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:33 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:34 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:35 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:36 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:37 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:38 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:39 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:40 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:41 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:42 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:43 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:44 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:45 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:46 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:47 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:48 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:49 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:50 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:51 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:52 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:53 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:54 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:55 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:56 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:57 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:58 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 05:59 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:00 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:01 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:02 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:03 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:04 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:05 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:06 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:07 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:08 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:09 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:10 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:11 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:12 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:13 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:14 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:15 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:16 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:17 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:18 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:19 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:20 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:21 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:22 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:23 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:24 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:25 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:26 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:27 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:28 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:29 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:30 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:31 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:32 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:33 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:34 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:35 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:36 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:37 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:38 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:39 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:40 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:41 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:42 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:43 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:44 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:45 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:46 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:47 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:48 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:49 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:50 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:51 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:52 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:53 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:54 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:55 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:56 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:57 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:58 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 06:59 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:00 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:01 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:02 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:03 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:04 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:05 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:06 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:07 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:08 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:09 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:10 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:11 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 67.5146 | 992.4646 | 62.7692 | 922.7072 | 0 | 0 | 0 | 0 | 1915.1719 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.6607 | 20 | 1 | 10
2018-10-12 07:12 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 0 | 0 | 0 | 0 | 1962.938 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 7.8518 | 20 | 2 | 20
2018-10-12 07:13 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:14 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:15 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:16 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:17 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:18 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:19 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:20 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:21 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:22 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:23 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:24 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:25 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:26 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:27 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:28 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:29 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:30 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:31 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:32 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:33 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:34 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:35 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:36 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:37 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:38 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:39 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:40 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:41 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:42 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:43 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:44 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:45 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:46 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:47 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:48 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:49 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:50 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:51 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:52 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:53 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:54 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:55 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:56 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:57 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:58 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 07:59 | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:00 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:01 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:02 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:03 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:04 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:05 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:06 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:07 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:08 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:09 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:10 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:11 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:12 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:13 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:14 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:15 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:16 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:17 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:18 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:19 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:20 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:21 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:22 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:23 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:24 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:25 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:26 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:27 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:28 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:29 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:30 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:31 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:32 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:33 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:34 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:35 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:36 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:37 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:38 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:39 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:40 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:41 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:42 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:43 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:44 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:45 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:46 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:47 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:48 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:49 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:50 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:51 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:52 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 48.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:53 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:54 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:55 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:56 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:57 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:58 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 08:59 | 8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:00 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:01 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:02 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:03 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:04 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:05 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:06 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:07 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:08 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:09 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:10 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:11 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:12 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:13 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:14 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:15 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:16 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:17 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:18 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:19 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:20 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:21 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:22 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:23 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:24 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:25 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:26 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:27 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:28 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:29 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:30 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:31 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:32 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:33 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:34 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:35 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 66.7628 | 981.4132 | 66.7704 | 981.5249 | 47.6596 | 700.5961 | 0 | 0 | 2663.5342 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 7.1028 | 30 | 2 | 20
2018-10-12 09:36 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:37 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:38 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:39 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:40 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:41 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:42 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:43 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:44 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:45 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:46 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:47 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:48 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:49 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:50 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:51 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:52 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:53 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:54 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:55 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:56 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:57 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:58 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 09:59 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:00 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:01 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:02 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:03 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:04 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:05 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:06 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:07 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:08 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:09 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:10 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:11 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:12 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:13 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:14 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:15 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:16 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:17 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:18 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:19 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:20 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:21 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:22 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:23 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:24 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:25 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:26 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:27 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:28 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:29 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:30 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:31 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:32 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:33 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:34 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:35 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:36 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:37 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:38 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:39 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:40 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:41 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:42 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:43 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:44 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:45 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:46 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:47 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:48 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:49 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:50 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:51 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:52 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:53 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:54 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:55 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:56 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:57 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:58 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 10:59 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:00 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:01 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:02 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:03 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:04 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:05 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:06 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:07 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:08 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:09 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:10 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:11 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:12 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:13 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:14 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:15 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:16 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:17 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:18 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:19 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:20 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:21 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:22 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:23 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:24 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:25 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:26 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:27 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:28 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:29 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:30 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:31 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:32 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:33 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:34 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:35 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:36 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:37 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:38 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:39 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:40 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:41 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:42 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:43 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:44 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:45 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:46 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:47 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:48 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:49 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:50 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:51 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:52 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:53 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:54 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:55 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:56 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:57 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:58 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 11:59 | 11 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2532 | 1120.922 | 74.7479 | 1098.7941 | 57.0653 | 838.8599 | 0 | 0 | 3058.5761 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 1 | 3000 | 0 | 0 | 3 | 9000 | 8.1562 | 30 | 2 | 20
2018-10-12 12:00 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:01 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:02 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:03 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:04 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:05 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:06 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:07 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:08 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:09 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:10 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:11 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:12 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:13 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:14 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:15 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:16 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:17 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:18 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:19 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:20 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:21 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:22 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:23 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:24 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:25 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:26 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:27 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:28 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:29 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:30 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:31 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:32 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:33 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:34 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:35 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:36 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:37 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:38 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:39 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:40 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:41 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:42 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:43 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:44 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:45 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:46 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:47 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:48 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:49 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:50 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:51 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:52 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:53 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:54 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:55 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:56 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:57 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:58 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 12:59 | 12 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:00 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:01 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:02 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:03 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:04 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:05 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:06 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:07 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:08 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:09 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:10 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:11 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:12 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:13 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:14 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:15 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:16 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:17 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:18 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:19 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:20 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:21 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:22 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:23 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:24 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:25 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:26 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:27 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:28 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:29 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:30 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:31 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:32 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:33 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:34 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:35 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:36 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:37 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:38 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:39 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:40 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:41 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:42 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:43 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:44 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:45 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:46 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:47 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:48 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:49 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:50 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:51 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:52 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 62.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:53 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:54 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:55 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:56 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:57 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:58 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 13:59 | 13 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:00 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:01 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:02 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:03 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:04 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:05 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:06 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:07 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:08 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:09 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:10 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:11 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:12 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:13 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:14 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:15 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:16 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:17 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:18 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:19 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:20 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:21 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:22 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:23 | 14 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4699 | 1285.8075 | 74.7066 | 1098.187 | 0 | 0 | 0 | 0 | 2383.9945 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 2 | 6000 | 9.536 | 20 | 2 | 20
2018-10-12 14:24 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 75.0678 | 1103.4967 | 0 | 0 | 0 | 0 | 3277.1533 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 1 | 3000 | 0 | 0 | 0 | 0 | 3 | 9000 | 8.7391 | 30 | 3 | 30
2018-10-12 14:25 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:26 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:27 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:28 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:29 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:30 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:31 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:32 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:33 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:34 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:35 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:36 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:37 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:38 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:39 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:40 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:41 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:42 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:43 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:44 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:45 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:46 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:47 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:48 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:49 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:50 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:51 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:52 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:53 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:54 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:55 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:56 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:57 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:58 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 14:59 | 14 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:00 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:01 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:02 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:03 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:04 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:05 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:06 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:07 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:08 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:09 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:10 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:11 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:12 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:13 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:14 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:15 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:16 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:17 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:18 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:19 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:20 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:21 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:22 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:23 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:24 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:25 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:26 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:27 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:28 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:29 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:30 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:31 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:32 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:33 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:34 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:35 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:36 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:37 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:38 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:39 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:40 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:41 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:42 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:43 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:44 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:45 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:46 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:47 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:48 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:49 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:50 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:51 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:52 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 64.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:53 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:54 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:55 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:56 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:57 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:58 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 15:59 | 15 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:00 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:01 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:02 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:03 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:04 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:05 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:06 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:07 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:08 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:09 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:10 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:11 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:12 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:13 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:14 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:15 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:16 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:17 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:18 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:19 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:20 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:21 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:22 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:23 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:24 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:25 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:26 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:27 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:28 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:29 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:30 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:31 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:32 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:33 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:34 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:35 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:36 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:37 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:38 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:39 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:40 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:41 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:42 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:43 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:44 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:45 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:46 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:47 | 16 | 6 | 0 | 0 | 68.0312 | 1000.0586 | 0 | 0 | 79.8366 | 1173.598 | 0 | 0 | 0 | 0 | 51.6735 | 759.6004 | 2173.6567 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.7964 | 30 | 2 | 20
2018-10-12 16:48 | 16 | 6 | 0 | 0 | 63.5835 | 934.6775 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1949.2832 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.1981 | 30 | 1 | 10
2018-10-12 16:49 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:50 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:51 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:52 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 66 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:53 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:54 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:55 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:56 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:57 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:58 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 16:59 | 16 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:00 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:01 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:02 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:03 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:04 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:05 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:06 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:07 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:08 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:09 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:10 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:11 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:12 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:13 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:14 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:15 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:16 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:17 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:18 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:19 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:20 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:21 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:22 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:23 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:24 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:25 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:26 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:27 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:28 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:29 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:30 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:31 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:32 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:33 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:34 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:35 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:36 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:37 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:38 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:39 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:40 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:41 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:42 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:43 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:44 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:45 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:46 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:47 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:48 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:49 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:50 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:51 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:52 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 63 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:53 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:54 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:55 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:56 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:57 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:58 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 17:59 | 17 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:00 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:01 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:02 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:03 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:04 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:05 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:06 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:07 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:08 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:09 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:10 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:11 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:12 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:13 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:14 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:15 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:16 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:17 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:18 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:19 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:20 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:21 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:22 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:23 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:24 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:25 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:26 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:27 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:28 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:29 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:30 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:31 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:32 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:33 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:34 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:35 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:36 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:37 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:38 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:39 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:40 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:41 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:42 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:43 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:44 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:45 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:46 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:47 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:48 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:49 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:50 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:51 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:52 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 62.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:53 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:54 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:55 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:56 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:57 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:58 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 18:59 | 18 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:00 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:01 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:02 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:03 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:04 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:05 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:06 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:07 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:08 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:09 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:10 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:11 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 52.388 | 770.1036 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:12 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:13 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:14 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:15 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:16 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:17 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:18 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:19 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:20 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:21 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:22 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:23 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:24 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:25 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:26 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:27 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:28 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:29 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:30 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:31 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:32 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:33 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:34 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:35 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:36 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:37 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:38 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:39 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:40 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:41 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:42 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:43 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:44 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:45 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:46 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:47 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:48 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:49 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:50 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:51 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:52 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 60.1 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:53 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:54 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:55 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:56 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:57 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:58 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 19:59 | 19 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:00 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:01 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:02 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:03 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:04 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:05 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:06 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:07 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:08 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:09 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:10 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:11 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:12 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:13 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:14 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:15 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:16 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:17 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:18 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:19 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:20 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:21 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:22 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:23 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:24 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:25 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:26 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:27 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:28 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:29 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:30 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:31 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:32 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:33 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:34 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:35 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:36 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:37 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:38 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:39 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:40 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:41 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:42 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:43 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:44 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:45 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:46 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:47 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:48 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:49 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:50 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:51 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:52 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 55.9 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:53 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:54 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:55 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:56 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:57 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:58 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 20:59 | 20 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:00 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:01 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:02 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:03 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:04 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:05 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:06 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:07 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:08 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:09 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:10 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:11 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:12 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:13 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:14 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:15 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:16 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:17 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:18 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:19 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:20 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:21 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:22 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:23 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:24 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:25 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:26 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:27 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:28 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:29 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:30 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:31 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:32 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:33 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:34 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:35 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:36 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:37 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:38 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:39 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:40 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:41 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:42 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:43 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:44 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:45 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:46 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:47 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:48 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:49 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
2018-10-12 21:50 | 21 | 6 | 0 | 0 | 58.7032 | 862.937 | 0 | 0 | 69.0208 | 1014.6058 | 0 | 0 | 0 | 0 | 45.9715 | 675.781 | 1877.5428 | 57 | 0 | 0 | 1 | 3000 | 0 | 0 | 1 | 3000 | 0 | 0 | 0 | 0 | 1 | 3000 | 3 | 9000 | 5.0068 | 30 | 1 | 10
Formulas:
Data = [Data, row above]+(1/(24*60))

## Chiller 1 Pct RLA
Percent Average Motor Current (RLA)(Date and Time), created by Plot Digitizer, 2.6.6
Date: 10/13/18, 3:12:38 PM
1900-01-23
Date and Time | Percent Average Motor Current (RLA) | Zero Filter | Minute Value
2018-10-10 16:48 | 89.9849 | 89.9849 | 48
2018-10-10 19:12 | 90 | 90 | 12
2018-10-10 19:15 | 66.2245 | 66.2245 | 15
2018-10-10 21:36 | 69.3378 | 69.3378 | 36
2018-10-11 | 67.4189 | 67.4189 | 0
2018-10-11 02:24 | 59.4197 | 59.4197 | 24
2018-10-11 04:48 | 61.5359 | 61.5359 | 48
2018-10-11 04:49 | -1.6031 | 0 | 49
2018-10-11 14:24 | -3.1329 | 0 | 24
2018-10-11 14:25 | 70.7447 | 70.7447 | 25
2018-10-11 16:48 | 64.5424 | 64.5424 | 48
2018-10-11 19:12 | 62.2416 | 62.2416 | 12
2018-10-11 19:13 | -1.2115 | 0 | 13
2018-10-12 16:48 | -3.2693 | 0 | 48

## Chiller 2 Pct RLA
Chiller 2 Pct RLA(Date and Time), created by Plot Digitizer, 2.6.6
Date: 10/13/18, 4:13:11 PM
1900-01-14
Date and Time | Chiller 2 Pct RLA | Zero Filter | Minute Value
2018-10-10 16:48 | 91.1212 | 91.1212 | 48
2018-10-10 19:12 | 92.6568 | 92.6568 | 12
2018-10-10 19:12 | 76.9132 | 76.9132 | 12
2018-10-10 21:36 | 80.1684 | 80.1684 | 36
2018-10-10 21:37 | 79.0084 | 79.0084 | 37
2018-10-11 02:24 | 68.2291 | 68.2291 | 24
2018-10-11 02:24 | 0.26882 | 0 | 24
2018-10-12 14:24 | -1.8643 | 0 | 24
2018-10-12 14:24 | 68.0312 | 68.0312 | 24
2018-10-12 16:48 | 63.5835 | 63.5835 | 48
2018-10-12 16:49 | 58.7032 | 58.7032 | 49

## Chiller 3 Pct RLA
Chiller 3 Pct RLA(Date and Time), created by Plot Digitizer, 2.6.6
Date: 10/13/18, 3:24:48 PM
1900-01-06
Date and Time | Chiller 3 Pct RLA | Zero Filter | Minute Value
2018-10-10 16:48 | 0.51556 | 0 | 48
2018-10-10 16:49 | 62.4648 | 62.4648 | 49
2018-10-10 19:12 | 94.1002 | 94.1002 | 12
2018-10-10 21:35 | 75.0961 | 75.0961 | 35
2018-10-10 21:36 | -1.1584 | 0 | 36
2018-10-12 16:48 | -0.85166 | 0 | 48

## Chiller 4 Pct RLA
Chiller 4 Percent RLA(Date and Time), created by Plot Digitizer, 2.6.6
Date: 10/13/18, 3:32:16 PM
1900-01-30
Date and Time | Chiller 4 Percent RLA | Zero Filter | Minute Value
2018-10-10 16:48 | 0.68597 | 0 | 48
2018-10-11 19:12 | -0.55089 | 0 | 12
2018-10-11 19:13 | 66.3733 | 66.3733 | 13
2018-10-11 21:36 | 74.6724 | 74.6724 | 36
2018-10-12 | 71.5416 | 71.5416 | 0
2018-10-12 02:24 | 62.9213 | 62.9213 | 24
2018-10-12 04:48 | 67.5146 | 67.5146 | 48
2018-10-12 07:12 | 66.7628 | 66.7628 | 12
2018-10-12 09:36 | 76.2532 | 76.2532 | 36
2018-10-12 12:00 | 87.4699 | 87.4699 | 0
2018-10-12 14:24 | 79.8366 | 79.8366 | 24
2018-10-12 16:48 | 69.0208 | 69.0208 | 48

## Chiller 5 Pct RLA
Chiller 5 Pct RLA(Date and Time), created by Plot Digitizer, 2.6.6
Date: 10/13/18, 3:39:51 PM
1900-02-26
Date and Time | Chiller 5 Pct RLA | Zero Filter | Minute Value
2018-10-10 16:48 | -0.63813 | 0 | 48
2018-10-10 19:12 | -0.53512 | 0 | 12
2018-10-10 21:36 | 81.193 | 81.193 | 36
2018-10-11 | 83.8927 | 83.8927 | 0
2018-10-11 02:24 | 72.9237 | 72.9237 | 24
2018-10-11 04:47 | 83.6535 | 83.6535 | 47
2018-10-11 04:48 | 84.401 | 84.401 | 48
2018-10-11 07:12 | 85.2543 | 85.2543 | 12
2018-10-11 09:36 | 79.1137 | 79.1137 | 36
2018-10-11 12:00 | 83.8647 | 83.8647 | 0
2018-10-11 14:24 | 90.9109 | 90.9109 | 24
2018-10-11 16:48 | 76.5123 | 76.5123 | 48
2018-10-11 19:12 | 74.2295 | 74.2295 | 12
2018-10-11 21:36 | 69.5614 | 69.5614 | 36
2018-10-12 | 71.0027 | 71.0027 | 0
2018-10-12 02:24 | 68.8141 | 68.8141 | 24
2018-10-12 04:48 | 62.7692 | 62.7692 | 48
2018-10-12 07:12 | 66.7704 | 66.7704 | 12
2018-10-12 09:36 | 74.7479 | 74.7479 | 36
2018-10-12 12:00 | 74.7066 | 74.7066 | 0
2018-10-12 14:24 | 75.0678 | 75.0678 | 24
2018-10-12 14:25 | 0.26592 | 0 | 25
2018-10-12 16:48 | 1.2721 | 0 | 48

## Chiller 6 Pct RLA
Chiller 6 Pct RLA(Date and Time), created by Plot Digitizer, 2.6.6
Date: 10/13/18, 3:44:17 PM
1900-01-16
Date and Time | Chiller 6 Pct RLA | Zero Filter | Minute Value
2018-10-10 16:48 | 55.2015 | 55.2015 | 48
2018-10-10 19:12 | 53.4402 | 53.4402 | 12
2018-10-10 21:36 | 56.3124 | 56.3124 | 36
2018-10-11 | 54.2794 | 54.2794 | 0
2018-10-11 00:01 | 0.1904 | 0 | 1
2018-10-12 07:12 | 0.18879 | 0 | 12
2018-10-12 07:13 | 47.6596 | 47.6596 | 13
2018-10-12 09:36 | 57.0653 | 57.0653 | 36
2018-10-12 12:00 | 54.7935 | 54.7935 | 0
2018-10-12 12:00 | -0.45643 | 0 | 0
2018-10-12 16:48 | 0.12223 | 0 | 48

## Chiller 7 Pct RLA
Chiller 7 Pct RLA(Date and Time), created by Plot Digitizer, 2.6.6
Date: 10/13/18, 3:55:18 PM
1900-02-16
Date and Time | Chiller 7 Pct RLA | Zero Filter | Minute Value
2018-10-10 16:48 | 94.2781 | 94.2781 | 48
2018-10-10 19:12 | 90.4418 | 90.4418 | 12
2018-10-10 19:13 | 66.0674 | 66.0674 | 13
2018-10-10 21:36 | 58.0327 | 58.0327 | 36
2018-10-11 | 58.6031 | 58.6031 | 0
2018-10-11 02:24 | 55.3528 | 55.3528 | 24
2018-10-11 04:48 | 55.8984 | 55.8984 | 48
2018-10-11 07:12 | 64.5278 | 64.5278 | 12
2018-10-11 07:13 | 59.1809 | 59.1809 | 13
2018-10-11 09:36 | 56.9179 | 56.9179 | 36
2018-10-11 12:00 | 60.5639 | 60.5639 | 0
2018-10-11 14:24 | 66.4328 | 66.4328 | 24
2018-10-11 16:48 | 55.8984 | 55.8984 | 48
2018-10-11 19:12 | 52.5357 | 52.5357 | 12
2018-10-11 21:36 | 48.8578 | 48.8578 | 36
2018-10-11 21:37 | 0.14518 | 0 | 37
2018-10-12 14:24 | -0.68578 | 0 | 24
2018-10-12 14:25 | 51.6735 | 51.6735 | 25
2018-10-12 16:48 | 52.388 | 52.388 | 48
2018-10-12 19:12 | 45.9715 | 45.9715 | 12

## NOAA Weather Data
station | valid | lon | lat | tmpf | dwpf | relh | drct | sknt | p01i | alti | mslp | vsby | gust | skyc1 | skyc2 | skyc3 | skyc4 | skyl1 | skyl2 | skyl3 | skyl4 | wxcodes | metar
BNA | 2018-10-08 00:53 | -86.6892 | 36.1189 | 70 | 66.9 | 89.9 | 140 | 5 | 0 | 30.14 | 1019.8 | 5 | M | CLR | M | M | M | M | M | M | M | BR | KBNA 080553Z 14005KT 5SM BR CLR 21/19 A3014 RMK AO2 SLP198 T02110194 10239 20206 403170200 58001 $
BNA | 2018-10-08 01:53 | -86.6892 | 36.1189 | 71.1 | 68 | 89.94 | 160 | 5 | 0 | 30.14 | 1019.8 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 080653Z 16005KT 10SM CLR 22/20 A3014 RMK AO2 SLP198 T02170200 $
BNA | 2018-10-08 02:53 | -86.6892 | 36.1189 | 70 | 66.9 | 89.9 | 0 | 0 | 0 | 30.14 | 1020 | 6 | M | CLR | M | M | M | M | M | M | M | BR | KBNA 080753Z 00000KT 6SM BR CLR 21/19 A3014 RMK AO2 SLP200 T02110194 $
BNA | 2018-10-08 03:53 | -86.6892 | 36.1189 | 69.1 | 66.9 | 92.71 | 0 | 0 | 0 | 30.14 | 1020.1 | 6 | M | CLR | M | M | M | M | M | M | M | BR | KBNA 080853Z 00000KT 6SM BR CLR 21/19 A3014 RMK AO2 SLP201 T02060194 51001 $
BNA | 2018-10-08 04:53 | -86.6892 | 36.1189 | 69.1 | 66 | 89.86 | 110 | 3 | 0 | 30.14 | 1020 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 080953Z 11003KT 10SM CLR 21/19 A3014 RMK AO2 SLP200 T02060189 $
BNA | 2018-10-08 05:53 | -86.6892 | 36.1189 | 70 | 66 | 87.14 | 150 | 5 | 0 | 30.15 | 1020.4 | 7 | M | CLR | M | M | M | M | M | M | M | M | KBNA 081053Z 15005KT 7SM CLR 21/19 A3015 RMK AO2 SLP204 T02110189 $
BNA | 2018-10-08 06:53 | -86.6892 | 36.1189 | 68 | 64.9 | 89.81 | 120 | 4 | 0 | 30.16 | 1020.8 | 6 | M | FEW | M | M | M | 12000 | M | M | M | BR | KBNA 081153Z 12004KT 6SM BR FEW120 20/18 A3016 RMK AO2 SLP208 70014 T02000183 10217 20194 53006 $
BNA | 2018-10-08 07:53 | -86.6892 | 36.1189 | 72 | 66.9 | 83.99 | 130 | 4 | 0 | 30.17 | 1021.2 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 081253Z 13004KT 10SM CLR 22/19 A3017 RMK AO2 SLP212 T02220194 $
BNA | 2018-10-08 08:53 | -86.6892 | 36.1189 | 75 | 68 | 78.86 | 150 | 4 | 0 | 30.18 | 1021.2 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 081353Z 15004KT 10SM CLR 24/20 A3018 RMK AO2 SLP212 T02390200 $
BNA | 2018-10-08 09:53 | -86.6892 | 36.1189 | 80.1 | 69.1 | 69.18 | 160 | 5 | 0 | 30.18 | 1021.4 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 081453Z 16005KT 10SM CLR 27/21 A3018 RMK AO2 SLP214 T02670206 51007 $
BNA | 2018-10-08 10:53 | -86.6892 | 36.1189 | 82.9 | 69.1 | 63.16 | 150 | 8 | 0 | 30.19 | 1021.5 | 10 | M | SCT | BKN | M | M | 3200 | 9000 | M | M | M | KBNA 081553Z 15008KT 10SM SCT032 BKN090 28/21 A3019 RMK AO2 SLP215 T02830206 $
BNA | 2018-10-08 11:53 | -86.6892 | 36.1189 | 84 | 69.1 | 60.95 | 180 | 7 | 0 | 30.17 | 1021.1 | 10 | M | SCT | BKN | BKN | M | 3700 | 4500 | 8000 | M | M | KBNA 081653Z 18007KT 10SM SCT037 BKN045 BKN080 29/21 A3017 RMK AO2 SLP211 T02890206 $
BNA | 2018-10-08 12:53 | -86.6892 | 36.1189 | 86 | 69.1 | 57.16 | 180 | 8 | 0 | 30.15 | 1020.2 | 10 | M | FEW | SCT | BKN | M | 4500 | 5500 | 7500 | M | M | KBNA 081753Z 18008KT 10SM FEW045 SCT055 BKN075 30/21 A3015 RMK AO2 SLP202 T03000206 10300 20200 58012 $
BNA | 2018-10-08 13:53 | -86.6892 | 36.1189 | 84.9 | 69.1 | 59.21 | 170 | 8 | 0 | 30.13 | 1019.5 | 10 | M | FEW | SCT | BKN | M | 4500 | 8000 | 11000 | M | M | KBNA 081853Z 17008KT 10SM FEW045 SCT080 BKN110 29/21 A3013 RMK AO2 RAB18E27 SLP195 P0000 T02940206 $
BNA | 2018-10-08 14:53 | -86.6892 | 36.1189 | 87.1 | 68 | 53.15 | 160 | 6 | 0 | 30.11 | 1018.8 | 10 | M | SCT | BKN | BKN | M | 4500 | 8000 | 11000 | M | M | KBNA 081953Z 16006KT 10SM SCT045TCU BKN080 BKN110 31/20 A3011 RMK AO2 SLP188 TCU ALQDS T03060200 $
BNA | 2018-10-08 15:53 | -86.6892 | 36.1189 | 88 | 66.9 | 49.73 | 180 | 10 | 0 | 30.09 | 1018.3 | 10 | M | SCT | SCT | BKN | M | 4500 | 8500 | 12000 | M | M | KBNA 082053Z 18010KT 10SM SCT045TCU SCT085 BKN120 31/19 A3009 RMK AO2 SLP183 TCU NW-E AND OHD 60000 T03110194 56018 $
BNA | 2018-10-08 16:53 | -86.6892 | 36.1189 | 82.9 | 66.9 | 58.55 | 60 | 11 | 0.01 | 30.1 | 1018.5 | 5 | 25 | BKN | BKN | BKN | M | 4500 | 8000 | 11000 | M | RA | KBNA 082153Z 06011G25KT 5SM R02L/3000VP6000FT RA BKN045TCU BKN080 BKN110 28/19 A3010 RMK AO2 RAB50 SLP185 TCU NW-NE AND OHD P0001 T02830194 $
BNA | 2018-10-08 17:53 | -86.6892 | 36.1189 | 82 | 68 | 62.62 | 140 | 3 | 0.06 | 30.09 | 1018.1 | 10 | M | FEW | SCT | SCT | M | 4500 | 8000 | 11000 | M | M | KBNA 082253Z 14003KT 10SM FEW045 SCT080 SCT110 28/20 A3009 RMK AO2 RAE06 SLP181 CB DSNT NW P0006 T02780200 $
BNA | 2018-10-08 18:53 | -86.6892 | 36.1189 | 79 | 69.1 | 71.72 | 110 | 4 | 0 | 30.09 | 1018.2 | 10 | M | FEW | SCT | M | M | 4500 | 8000 | M | M | M | KBNA 082353Z 11004KT 10SM FEW045 SCT080 26/21 A3009 RMK AO2 SLP182 60007 T02610206 10311 20261 55002 $
BNA | 2018-10-08 19:53 | -86.6892 | 36.1189 | 78.1 | 69.1 | 73.88 | 120 | 6 | 0 | 30.09 | 1018.3 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 090053Z 12006KT 10SM CLR 26/21 A3009 RMK AO2 SLP183 T02560206 $
BNA | 2018-10-08 20:53 | -86.6892 | 36.1189 | 75.9 | 69.1 | 79.47 | 140 | 4 | 0 | 30.1 | 1018.8 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 090153Z 14004KT 10SM CLR 24/21 A3010 RMK AO2 SLP188 T02440206 $
BNA | 2018-10-08 21:53 | -86.6892 | 36.1189 | 73.9 | 68 | 81.82 | 150 | 3 | 0 | 30.11 | 1018.9 | 10 | M | FEW | M | M | M | 5000 | M | M | M | M | KBNA 090253Z 15003KT 10SM FEW050 23/20 A3011 RMK AO2 SLP189 T02330200 53007 $
BNA | 2018-10-08 22:53 | -86.6892 | 36.1189 | 73 | 66.9 | 81.2 | 140 | 4 | 0 | 30.11 | 1018.9 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 090353Z 14004KT 10SM CLR 23/19 A3011 RMK AO2 SLP189 T02280194 $
BNA | 2018-10-08 23:53 | -86.6892 | 36.1189 | 73 | 66.9 | 81.2 | 150 | 6 | 0 | 30.1 | 1018.6 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 090453Z 15006KT 10SM CLR 23/19 A3010 RMK AO2 SLP186 T02280194 $
BNA | 2018-10-09 00:53 | -86.6892 | 36.1189 | 72 | 66.9 | 83.99 | 140 | 5 | 0 | 30.1 | 1018.5 | 10 | M | FEW | M | M | M | 20000 | M | M | M | M | KBNA 090553Z 14005KT 10SM FEW200 22/19 A3010 RMK AO2 SLP185 T02220194 10261 20222 403110194 58003 $
BNA | 2018-10-09 01:53 | -86.6892 | 36.1189 | 71.1 | 66.9 | 86.59 | 0 | 0 | 0 | 30.11 | 1018.8 | 10 | M | FEW | M | M | M | 4500 | M | M | M | M | KBNA 090653Z 00000KT 10SM FEW045 22/19 A3011 RMK AO2 SLP188 T02170194 $
BNA | 2018-10-09 02:53 | -86.6892 | 36.1189 | 72 | 66 | 81.41 | 0 | 0 | 0 | 30.1 | 1018.4 | 10 | M | FEW | BKN | M | M | 9000 | 20000 | M | M | M | KBNA 090753Z 00000KT 10SM FEW090 BKN200 22/19 A3010 RMK AO2 SLP184 T02220189 $
BNA | 2018-10-09 03:53 | -86.6892 | 36.1189 | 71.1 | 66 | 83.93 | 120 | 3 | 0 | 30.1 | 1018.4 | 10 | M | FEW | BKN | M | M | 8500 | 20000 | M | M | M | KBNA 090853Z 12003KT 10SM FEW085 BKN200 22/19 A3010 RMK AO2 SLP184 T02170189 58001 $
BNA | 2018-10-09 04:53 | -86.6892 | 36.1189 | 71.1 | 66 | 83.93 | 120 | 4 | 0 | 30.1 | 1018.6 | 10 | M | SCT | BKN | M | M | 8000 | 10000 | M | M | M | KBNA 090953Z 12004KT 10SM SCT080 BKN100 22/19 A3010 RMK AO2 SLP186 T02170189 $
BNA | 2018-10-09 05:53 | -86.6892 | 36.1189 | 71.1 | 66 | 83.93 | 0 | 0 | 0 | 30.1 | 1018.7 | 10 | M | SCT | OVC | M | M | 9000 | 20000 | M | M | M | KBNA 091053Z 00000KT 10SM SCT090 OVC200 22/19 A3010 RMK AO2 SLP187 T02170189 $
BNA | 2018-10-09 06:53 | -86.6892 | 36.1189 | 71.1 | 66 | 83.93 | 110 | 4 | 0 | 30.1 | 1018.5 | 10 | M | SCT | BKN | BKN | M | 8500 | 18000 | 25000 | M | M | KBNA 091153Z 11004KT 10SM SCT085 BKN180 BKN250 22/19 A3010 RMK AO2 SLP185 70007 T02170189 10222 20211 50000 $
BNA | 2018-10-09 07:53 | -86.6892 | 36.1189 | 73 | 66 | 78.7 | 120 | 7 | 0 | 30.1 | 1018.6 | 10 | M | BKN | BKN | M | M | 20000 | 25000 | M | M | M | KBNA 091253Z 12007KT 10SM BKN200 BKN250 23/19 A3010 RMK AO2 SLP186 T02280189 $
BNA | 2018-10-09 08:53 | -86.6892 | 36.1189 | 77 | 64.9 | 66.27 | 140 | 11 | 0 | 30.11 | 1018.9 | 10 | M | FEW | SCT | SCT | M | 9000 | 20000 | 25000 | M | M | KBNA 091353Z 14011KT 10SM FEW090 SCT200 SCT250 25/18 A3011 RMK AO2 SLP189 T02500183
BNA | 2018-10-09 09:53 | -86.6892 | 36.1189 | 80.1 | 64.9 | 59.83 | 150 | 12 | 0 | 30.1 | 1018.6 | 10 | M | FEW | FEW | SCT | SCT | 3500 | 8500 | 20000 | 25000 | M | KBNA 091453Z 15012KT 10SM FEW035 FEW085 SCT200 SCT250 27/18 A3010 RMK AO2 SLP186 T02670183 50001
BNA | 2018-10-09 10:53 | -86.6892 | 36.1189 | 81 | 64 | 56.3 | 140 | 11 | 0 | 30.09 | 1018.2 | 10 | 20 | FEW | SCT | M | M | 4000 | 20000 | M | M | M | KBNA 091553Z 14011G20KT 10SM FEW040 SCT200 27/18 A3009 RMK AO2 SLP182 T02720178
BNA | 2018-10-09 11:53 | -86.6892 | 36.1189 | 82.9 | 64 | 52.93 | 130 | 11 | 0 | 30.07 | 1017.6 | 10 | 23 | BKN | M | M | M | 4100 | M | M | M | M | KBNA 091653Z 13011G23KT 10SM BKN041 28/18 A3007 RMK AO2 SLP176 T02830178
BNA | 2018-10-09 12:53 | -86.6892 | 36.1189 | 82.9 | 64 | 52.93 | 140 | 13 | 0 | 30.05 | 1017 | 10 | 19 | BKN | BKN | M | M | 4400 | 25000 | M | M | M | KBNA 091753Z 14013G19KT 10SM BKN044 BKN250 28/18 A3005 RMK AO2 SLP170 T02830178 10289 20217 58015
BNA | 2018-10-09 13:53 | -86.6892 | 36.1189 | 84 | 64 | 51.08 | 150 | 12 | 0 | 30.02 | 1016 | 10 | M | FEW | BKN | BKN | M | 4300 | 5500 | 6500 | M | M | KBNA 091853Z 15012KT 10SM FEW043 BKN055 BKN065 29/18 A3002 RMK AO2 SLP160 T02890178
BNA | 2018-10-09 14:53 | -86.6892 | 36.1189 | 82 | 64 | 54.5 | 160 | 11 | 0 | 30.03 | 1016.1 | 10 | M | FEW | BKN | M | M | 4300 | 5500 | M | M | M | KBNA 091953Z 16011KT 10SM FEW043 BKN055 28/18 A3003 RMK AO2 SLP161 T02780178
BNA | 2018-10-09 15:53 | -86.6892 | 36.1189 | 80.1 | 64 | 57.98 | 140 | 14 | 0 | 30.02 | 1015.7 | 10 | 19 | FEW | BKN | M | M | 4000 | 5000 | M | M | M | KBNA 092053Z 14014G19KT 10SM FEW040 BKN050 27/18 A3002 RMK AO2 SLP157 T02670178 56013
BNA | 2018-10-09 16:53 | -86.6892 | 36.1189 | 79 | 64 | 60.11 | 150 | 11 | 0 | 30 | 1015.2 | 10 | M | BKN | OVC | M | M | 3900 | 5000 | M | M | M | KBNA 092153Z 15011KT 10SM BKN039 OVC050 26/18 A3000 RMK AO2 SLP152 T02610178
BNA | 2018-10-09 17:53 | -86.6892 | 36.1189 | 78.1 | 64 | 61.92 | 140 | 8 | 0 | 29.99 | 1014.9 | 10 | M | BKN | BKN | M | M | 4600 | 5500 | M | M | M | KBNA 092253Z 14008KT 10SM BKN046 BKN055 26/18 A2999 RMK AO2 SLP149 T02560178
BNA | 2018-10-09 18:53 | -86.6892 | 36.1189 | 77 | 64 | 64.21 | 120 | 8 | 0 | 29.98 | 1014.4 | 10 | M | BKN | BKN | M | M | 4400 | 6000 | M | M | M | KBNA 092353Z 12008KT 10SM BKN044 BKN060 25/18 A2998 RMK AO2 SLP144 T02500178 10294 20250 57013
BNA | 2018-10-09 19:53 | -86.6892 | 36.1189 | 75.9 | 63 | 64.31 | 120 | 8 | 0 | 29.96 | 1013.9 | 10 | M | BKN | M | M | M | 6000 | M | M | M | M | KBNA 100053Z 12008KT 10SM BKN060 24/17 A2996 RMK AO2 SLP139 T02440172
BNA | 2018-10-09 20:53 | -86.6892 | 36.1189 | 73.9 | 64 | 71.21 | 140 | 5 | 0 | 29.96 | 1013.9 | 10 | M | BKN | M | M | M | 15000 | M | M | M | M | KBNA 100153Z 14005KT 10SM BKN150 23/18 A2996 RMK AO2 SLP139 T02330178
BNA | 2018-10-09 21:53 | -86.6892 | 36.1189 | 73.9 | 64 | 71.21 | 120 | 6 | 0 | 29.95 | 1013.6 | 10 | M | BKN | M | M | M | 15000 | M | M | M | M | KBNA 100253Z 12006KT 10SM BKN150 23/18 A2995 RMK AO2 SLP136 T02330178 56008
BNA | 2018-10-09 22:53 | -86.6892 | 36.1189 | 72 | 64 | 75.92 | 130 | 5 | 0 | 29.94 | 1013.2 | 10 | M | BKN | M | M | M | 15000 | M | M | M | M | KBNA 100353Z 13005KT 10SM BKN150 22/18 A2994 RMK AO2 SLP132 T02220178
BNA | 2018-10-09 23:53 | -86.6892 | 36.1189 | 72 | 63 | 73.31 | 140 | 7 | 0 | 29.93 | 1012.8 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 100453Z 14007KT 10SM CLR 22/17 A2993 RMK AO2 SLP128 T02220172
BNA | 2018-10-10 00:53 | -86.6892 | 36.1189 | 73 | 64 | 73.4 | 0 | 0 | 0 | 29.93 | 1012.7 | 10 | M | BKN | M | M | M | 13000 | M | M | M | M | KBNA 100553Z 00000KT 10SM BKN130 23/18 A2993 RMK AO2 SLP127 T02280178 10250 20222 402940211 56008
BNA | 2018-10-10 01:53 | -86.6892 | 36.1189 | 72 | 64 | 75.92 | 100 | 4 | 0 | 29.91 | 1012 | 10 | M | BKN | M | M | M | 13000 | M | M | M | M | KBNA 100653Z 10004KT 10SM BKN130 22/18 A2991 RMK AO2 SLP120 T02220178
BNA | 2018-10-10 02:53 | -86.6892 | 36.1189 | 72 | 64.9 | 78.35 | 90 | 4 | 0 | 29.9 | 1011.9 | 10 | M | FEW | BKN | M | M | 7000 | 13000 | M | M | M | KBNA 100753Z 09004KT 10SM FEW070 BKN130 22/18 A2990 RMK AO2 SLP119 T02220183
BNA | 2018-10-10 03:53 | -86.6892 | 36.1189 | 73 | 64.9 | 75.75 | 90 | 5 | 0 | 29.88 | 1011.2 | 10 | M | BKN | BKN | M | M | 4100 | 13000 | M | M | M | KBNA 100853Z 09005KT 10SM BKN041 BKN130 23/18 A2988 RMK AO2 SLP112 T02280183 56015
BNA | 2018-10-10 04:53 | -86.6892 | 36.1189 | 73 | 64.9 | 75.75 | 90 | 6 | 0 | 29.88 | 1011.1 | 10 | M | OVC | M | M | M | 3600 | M | M | M | M | KBNA 100953Z 09006KT 10SM OVC036 23/18 A2988 RMK AO2 SLP111 T02280183
BNA | 2018-10-10 05:53 | -86.6892 | 36.1189 | 73 | 66 | 78.7 | 110 | 5 | 0 | 29.87 | 1010.9 | 10 | M | BKN | OVC | M | M | 3000 | 3700 | M | M | M | KBNA 101053Z 11005KT 10SM BKN030 OVC037 23/19 A2987 RMK AO2 SLP109 T02280189
BNA | 2018-10-10 06:14 | -86.6892 | 36.1189 | 73 | 66 | 78.7 | 130 | 5 | 0 | 29.87 | M | 10 | M | BKN | OVC | M | M | 2800 | 3700 | M | M | M | KBNA 101114Z 13005KT 10SM BKN028 OVC037 23/19 A2987 RMK AO2 T02280189
BNA | 2018-10-10 06:53 | -86.6892 | 36.1189 | 73 | 66 | 78.7 | 140 | 5 | 0 | 29.86 | 1010.6 | 10 | M | BKN | BKN | OVC | M | 2700 | 3200 | 4000 | M | M | KBNA 101153Z 14005KT 10SM BKN027 BKN032 OVC040 23/19 A2986 RMK AO2 SLP106 T02280189 10233 20222 58006
BNA | 2018-10-10 07:53 | -86.6892 | 36.1189 | 73 | 66.9 | 81.2 | 130 | 3 | 0 | 29.86 | 1010.6 | 10 | M | OVC | M | M | M | 2400 | M | M | M | M | KBNA 101253Z 13003KT 10SM OVC024 23/19 A2986 RMK AO2 SLP106 T02280194
BNA | 2018-10-10 08:53 | -86.6892 | 36.1189 | 75 | 66.9 | 75.92 | 120 | 5 | 0 | 29.86 | 1010.5 | 10 | M | BKN | BKN | OVC | M | 2600 | 4000 | 14000 | M | M | KBNA 101353Z 12005KT 10SM BKN026 BKN040 OVC140 24/19 A2986 RMK AO2 SLP105 T02390194
BNA | 2018-10-10 09:53 | -86.6892 | 36.1189 | 77 | 68 | 73.78 | 150 | 7 | 0 | 29.86 | 1010.5 | 10 | M | BKN | BKN | OVC | M | 2300 | 4000 | 20000 | M | M | KBNA 101453Z 15007KT 10SM BKN023 BKN040 OVC200 25/20 A2986 RMK AO2 SLP105 T02500200 57001
BNA | 2018-10-10 10:53 | -86.6892 | 36.1189 | 80.1 | 69.1 | 69.18 | 190 | 14 | 0 | 29.86 | 1010.4 | 10 | 18 | OVC | M | M | M | 2600 | M | M | M | M | KBNA 101553Z 19014G18KT 10SM OVC026 27/21 A2986 RMK AO2 SLP104 T02670206
BNA | 2018-10-10 11:26 | -86.6892 | 36.1189 | 81 | 69.1 | 67.18 | 190 | 10 | 0 | 29.85 | M | 10 | M | SCT | BKN | OVC | M | 2500 | 3100 | 4700 | M | M | KBNA 101626Z 19010KT 10SM SCT025 BKN031 OVC047 27/21 A2985 RMK AO2 T02720206
BNA | 2018-10-10 11:53 | -86.6892 | 36.1189 | 81 | 69.1 | 67.18 | 190 | 9 | 0 | 29.84 | 1009.9 | 10 | M | FEW | SCT | OVC | M | 2700 | 3400 | 4900 | M | M | KBNA 101653Z 19009KT 10SM FEW027 SCT034 OVC049 27/21 A2984 RMK AO2 SLP099 T02720206
BNA | 2018-10-10 12:53 | -86.6892 | 36.1189 | 84 | 69.1 | 60.95 | 180 | 9 | 0 | 29.81 | 1008.8 | 10 | M | FEW | SCT | SCT | BKN | 5500 | 10000 | 20000 | 25000 | M | KBNA 101753Z 18009KT 10SM FEW055 SCT100 SCT200 BKN250 29/21 A2981 RMK AO2 SLP088 T02890206 10289 20228 58016
BNA | 2018-10-10 13:53 | -86.6892 | 36.1189 | 84 | 70 | 62.86 | 200 | 7 | 0 | 29.79 | 1007.9 | 10 | M | FEW | SCT | BKN | OVC | 6000 | 8500 | 12000 | 25000 | M | KBNA 101853Z 20007KT 10SM FEW060 SCT085 BKN120 OVC250 29/21 A2979 RMK AO2 SLP079 T02890211
BNA | 2018-10-10 14:53 | -86.6892 | 36.1189 | 82 | 69.1 | 65.03 | 250 | 6 | 0 | 29.77 | 1007.5 | 10 | M | SCT | BKN | BKN | BKN | 3100 | 4300 | 8000 | 13000 | M | KBNA 101953Z 25006KT 10SM SCT031 BKN043 BKN080 BKN130 28/21 A2977 RMK AO2 SLP075 T02780206
BNA | 2018-10-10 15:53 | -86.6892 | 36.1189 | 82.9 | 69.1 | 63.16 | 200 | 5 | 0 | 29.76 | 1007.1 | 10 | M | FEW | SCT | BKN | BKN | 3400 | 6000 | 9000 | 13000 | M | KBNA 102053Z 20005KT 10SM FEW034CB SCT060 BKN090 BKN130 BKN220 28/21 A2976 RMK AO2 SLP071 CB SE MOV NE T02830206 56018
BNA | 2018-10-10 16:53 | -86.6892 | 36.1189 | 78.1 | 70 | 76.19 | 310 | 10 | 0 | 29.77 | 1007.4 | 10 | M | FEW | BKN | BKN | BKN | 1500 | 3000 | 6000 | 13000 | #NAME? | KBNA 102153Z 31010KT 10SM -RA FEW015 BKN030 BKN060 BKN130 OVC180 26/21 A2977 RMK AO2 RAB53 SLP074 P0000 T02560211
BNA | 2018-10-10 17:39 | -86.6892 | 36.1189 | 73.9 | 71.1 | 90.97 | M | 4 | 0.17 | 29.77 | M | 2 | M | BKN | BKN | OVC | M | 3000 | 3700 | 8500 | M | #NAME? | KBNA 102239Z VRB04KT 2SM R02L/3500VP6000FT +RA BR BKN030 BKN037 OVC085 23/22 A2977 RMK AO2 P0017 T02330217
BNA | 2018-10-10 17:53 | -86.6892 | 36.1189 | 73.9 | 71.1 | 90.97 | 260 | 3 | 0.22 | 29.77 | 1007.5 | 7 | M | SCT | BKN | OVC | M | 2000 | 3200 | 8500 | M | #NAME? | KBNA 102253Z 26003KT 7SM -RA SCT020 BKN032 OVC085 23/22 A2977 RMK AO2 SLP075 P0022 T02330217
BNA | 2018-10-10 18:53 | -86.6892 | 36.1189 | 73.9 | 71.1 | 90.97 | 240 | 4 | 0.07 | 29.77 | 1007.5 | 5 | M | FEW | BKN | OVC | M | 3200 | 5000 | 9000 | M | RA BR | KBNA 102353Z 24004KT 5SM RA BR FEW032 BKN050 OVC090 23/22 A2977 RMK AO2 SLP075 P0007 60029 T02330217 10294 20233 51004
BNA | 2018-10-10 19:53 | -86.6892 | 36.1189 | 73 | 71.1 | 93.77 | 150 | 3 | 0.07 | 29.78 | 1007.7 | 10 | M | FEW | BKN | BKN | OVC | 4500 | 6500 | 10000 | 13000 | M | KBNA 110053Z 15003KT 10SM FEW045 BKN065 BKN100 OVC130 23/22 A2978 RMK AO2 RAE34 SLP077 P0007 T02280217
BNA | 2018-10-10 20:53 | -86.6892 | 36.1189 | 73 | 71.1 | 93.77 | 0 | 0 | 0 | 29.78 | 1007.7 | 10 | M | FEW | BKN | BKN | OVC | 4500 | 10000 | 17000 | 25000 | M | KBNA 110153Z 00000KT 10SM FEW045 BKN100 BKN170 OVC250 23/22 A2978 RMK AO2 SLP077 T02280217
BNA | 2018-10-10 21:53 | -86.6892 | 36.1189 | 73.9 | 70 | 87.63 | 0 | 0 | 0 | 29.79 | 1007.9 | 10 | M | FEW | BKN | OVC | M | 500 | 4300 | 6000 | M | M | KBNA 110253Z 00000KT 10SM FEW005 BKN043 OVC060 23/21 A2979 RMK AO2 SLP079 60007 T02330211 53004
BNA | 2018-10-10 22:53 | -86.6892 | 36.1189 | 73 | 71.1 | 93.77 | 170 | 3 | 0 | 29.78 | 1007.9 | 10 | M | FEW | BKN | OVC | M | 3400 | 4300 | 6000 | M | M | KBNA 110353Z 17003KT 10SM FEW034 BKN043 OVC060 23/22 A2978 RMK AO2 SLP079 T02280217
BNA | 2018-10-10 23:21 | -86.6892 | 36.1189 | 73.9 | 71.1 | 90.97 | 0 | 0 | 0 | 29.78 | M | 10 | M | SCT | BKN | OVC | M | 600 | 4600 | 6500 | M | M | KBNA 110421Z 00000KT 10SM SCT006 BKN046 OVC065 23/22 A2978 RMK AO2 T02330217
BNA | 2018-10-10 23:53 | -86.6892 | 36.1189 | 73.9 | 71.1 | 90.97 | 290 | 4 | 0 | 29.78 | 1007.6 | 10 | M | BKN | BKN | OVC | M | 4900 | 7000 | 11000 | M | M | KBNA 110453Z 29004KT 10SM BKN049 BKN070 OVC110 23/22 A2978 RMK AO2 SLP076 T02330217
BNA | 2018-10-11 00:53 | -86.6892 | 36.1189 | 73.9 | 70 | 87.63 | 320 | 8 | 0 | 29.78 | 1007.5 | 10 | M | BKN | OVC | M | M | 3100 | 4100 | M | M | M | KBNA 110553Z 32008KT 10SM BKN031 OVC041 23/21 A2978 RMK AO2 SLP075 60007 T02330211 10233 20228 402940222 57003
BNA | 2018-10-11 01:53 | -86.6892 | 36.1189 | 73 | 69.1 | 87.59 | 320 | 6 | 0 | 29.78 | 1007.6 | 10 | M | BKN | M | M | M | 6500 | M | M | M | M | KBNA 110653Z 32006KT 10SM BKN065 23/21 A2978 RMK AO2 SLP076 T02280206
BNA | 2018-10-11 02:53 | -86.6892 | 36.1189 | 70 | 66.9 | 89.9 | 340 | 10 | 0 | 29.78 | 1007.7 | 10 | M | BKN | M | M | M | 1400 | M | M | M | M | KBNA 110753Z 34010KT 10SM BKN014 21/19 A2978 RMK AO2 SLP077 T02110194
BNA | 2018-10-11 03:53 | -86.6892 | 36.1189 | 66.9 | 61 | 81.33 | 330 | 13 | 0 | 29.81 | 1008.8 | 10 | M | OVC | M | M | M | 1200 | M | M | M | M | KBNA 110853Z 33013KT 10SM OVC012 19/16 A2981 RMK AO2 SLP088 T01940161 53012
BNA | 2018-10-11 04:53 | -86.6892 | 36.1189 | 63 | 55 | 75.11 | 350 | 12 | 0 | 29.83 | 1009.6 | 10 | M | FEW | M | M | M | 1800 | M | M | M | M | KBNA 110953Z 35012KT 10SM FEW018 17/13 A2983 RMK AO2 SLP096 T01720128
BNA | 2018-10-11 05:31 | -86.6892 | 36.1189 | 62.1 | 54 | 74.75 | 330 | 10 | 0 | 29.85 | M | 10 | 18 | BKN | BKN | M | M | 2100 | 2700 | M | M | M | KBNA 111031Z 33010G18KT 10SM BKN021 BKN027 17/12 A2985 RMK AO2 T01670122
BNA | 2018-10-11 05:53 | -86.6892 | 36.1189 | 61 | 53.1 | 75.2 | 340 | 11 | 0 | 29.86 | 1010.7 | 10 | 18 | BKN | BKN | M | M | 2200 | 2700 | M | M | M | KBNA 111053Z 34011G18KT 10SM BKN022 BKN027 16/12 A2986 RMK AO2 SLP107 T01610117
BNA | 2018-10-11 06:53 | -86.6892 | 36.1189 | 59 | 52 | 77.55 | 310 | 11 | 0 | 29.89 | 1011.6 | 10 | M | OVC | M | M | M | 1600 | M | M | M | M | KBNA 111153Z 31011KT 10SM OVC016 15/11 A2989 RMK AO2 SLP116 70036 T01500111 10233 20150 53025
BNA | 2018-10-11 07:53 | -86.6892 | 36.1189 | 57.9 | 50 | 74.91 | 320 | 10 | 0 | 29.91 | 1012.4 | 10 | M | OVC | M | M | M | 1700 | M | M | M | M | KBNA 111253Z 32010KT 10SM OVC017 14/10 A2991 RMK AO2 SLP124 T01440100
BNA | 2018-10-11 08:53 | -86.6892 | 36.1189 | 57 | 46.9 | 68.9 | 330 | 11 | 0 | 29.94 | 1013.3 | 10 | M | BKN | M | M | M | 2000 | M | M | M | M | KBNA 111353Z 33011KT 10SM BKN020 14/08 A2994 RMK AO2 SLP133 T01390083
BNA | 2018-10-11 09:53 | -86.6892 | 36.1189 | 57 | 46.9 | 68.9 | 340 | 10 | 0 | 29.96 | 1013.9 | 10 | M | OVC | M | M | M | 1900 | M | M | M | M | KBNA 111453Z 34010KT 10SM OVC019 14/08 A2996 RMK AO2 SLP139 T01390083 51022
BNA | 2018-10-11 10:53 | -86.6892 | 36.1189 | 57.9 | 46.9 | 66.7 | 310 | 11 | 0 | 29.98 | 1014.7 | 10 | M | OVC | M | M | M | 2200 | M | M | M | M | KBNA 111553Z 31011KT 10SM OVC022 14/08 A2998 RMK AO2 SLP147 T01440083
BNA | 2018-10-11 11:53 | -86.6892 | 36.1189 | 60.1 | 46.9 | 61.65 | 300 | 11 | 0 | 29.99 | 1015.1 | 10 | M | BKN | M | M | M | 2300 | M | M | M | M | KBNA 111653Z 30011KT 10SM BKN023 16/08 A2999 RMK AO2 SLP151 T01560083
BNA | 2018-10-11 12:21 | -86.6892 | 36.1189 | 63 | 48 | 57.99 | 310 | 9 | 0 | 29.99 | M | 10 | M | SCT | M | M | M | 2700 | M | M | M | M | KBNA 111721Z 31009KT 10SM SCT027 17/09 A2999 RMK AO2 T01720089
BNA | 2018-10-11 12:53 | -86.6892 | 36.1189 | 64.9 | 48 | 54.26 | 290 | 9 | 0 | 29.98 | 1014.6 | 10 | M | FEW | M | M | M | 3100 | M | M | M | M | KBNA 111753Z 29009KT 10SM FEW031 18/09 A2998 RMK AO2 SLP146 T01830089 10183 20139 50008
BNA | 2018-10-11 13:53 | -86.6892 | 36.1189 | 66 | 46.9 | 50.1 | 320 | 11 | 0 | 29.96 | 1014 | 10 | M | FEW | M | M | M | 3700 | M | M | M | M | KBNA 111853Z 32011KT 10SM FEW037 19/08 A2996 RMK AO2 SLP140 T01890083
BNA | 2018-10-11 14:53 | -86.6892 | 36.1189 | 66.9 | 46.9 | 48.56 | 320 | 13 | 0 | 29.97 | 1014.2 | 10 | 18 | CLR | M | M | M | M | M | M | M | M | KBNA 111953Z 32013G18KT 10SM CLR 19/08 A2997 RMK AO2 SLP142 T01940083
BNA | 2018-10-11 15:53 | -86.6892 | 36.1189 | 66.9 | 45 | 45.19 | 340 | 9 | 0 | 29.97 | 1014.3 | 10 | 18 | CLR | M | M | M | M | M | M | M | M | KBNA 112053Z 34009G18KT 10SM CLR 19/07 A2997 RMK AO2 SLP143 T01940072 55004
BNA | 2018-10-11 16:53 | -86.6892 | 36.1189 | 66 | 45 | 46.62 | 320 | 10 | 0 | 29.97 | 1014.4 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 112153Z 32010KT 10SM CLR 19/07 A2997 RMK AO2 SLP144 T01890072
BNA | 2018-10-11 17:53 | -86.6892 | 36.1189 | 63 | 44.1 | 50.03 | 350 | 11 | 0 | 29.98 | 1014.7 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 112253Z 35011KT 10SM CLR 17/07 A2998 RMK AO2 SLP147 T01720067
BNA | 2018-10-11 18:53 | -86.6892 | 36.1189 | 61 | 44.1 | 53.69 | 320 | 7 | 0 | 29.99 | 1015.4 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 112353Z 32007KT 10SM CLR 16/07 A2999 RMK AO2 SLP154 T01610067 10206 20156 53008
BNA | 2018-10-11 19:53 | -86.6892 | 36.1189 | 59 | 45 | 59.67 | 340 | 7 | 0 | 30.02 | 1016.1 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120053Z 34007KT 10SM CLR 15/07 A3002 RMK AO2 SLP161 T01500072
BNA | 2018-10-11 20:53 | -86.6892 | 36.1189 | 57 | 44.1 | 61.95 | 350 | 9 | 0 | 30.03 | 1016.6 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120153Z 35009KT 10SM CLR 14/07 A3003 RMK AO2 SLP166 T01390067
BNA | 2018-10-11 21:53 | -86.6892 | 36.1189 | 55.9 | 43 | 61.81 | 340 | 6 | 0 | 30.05 | 1017.3 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120253Z 34006KT 10SM CLR 13/06 A3005 RMK AO2 SLP173 T01330061 51018
BNA | 2018-10-11 22:53 | -86.6892 | 36.1189 | 54 | 42.1 | 63.98 | 330 | 6 | 0 | 30.06 | 1017.7 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120353Z 33006KT 10SM CLR 12/06 A3006 RMK AO2 SLP177 T01220056
BNA | 2018-10-11 23:53 | -86.6892 | 36.1189 | 53.1 | 42.1 | 66.13 | 340 | 4 | 0 | 30.07 | 1018.2 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120453Z 34004KT 10SM CLR 12/06 A3007 RMK AO2 SLP182 T01170056
BNA | 2018-10-12 00:53 | -86.6892 | 36.1189 | 52 | 42.1 | 68.86 | 340 | 3 | 0 | 30.08 | 1018.3 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120553Z 34003KT 10SM CLR 11/06 A3008 RMK AO2 SLP183 T01110056 10161 20106 402330106 51010
BNA | 2018-10-12 01:53 | -86.6892 | 36.1189 | 50 | 41 | 71.07 | 360 | 6 | 0 | 30.08 | 1018.3 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120653Z 36006KT 10SM CLR 10/05 A3008 RMK AO2 SLP183 T01000050
BNA | 2018-10-12 02:53 | -86.6892 | 36.1189 | 48.9 | 41 | 74.05 | 360 | 6 | 0 | 30.07 | 1018.1 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120753Z 36006KT 10SM CLR 09/05 A3007 RMK AO2 SLP181 T00940050
BNA | 2018-10-12 03:53 | -86.6892 | 36.1189 | 48.9 | 41 | 74.05 | 340 | 6 | 0 | 30.08 | 1018.1 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120853Z 34006KT 10SM CLR 09/05 A3008 RMK AO2 SLP181 T00940050 57001
BNA | 2018-10-12 04:53 | -86.6892 | 36.1189 | 46.9 | 39.9 | 76.48 | 360 | 6 | 0 | 30.07 | 1018.1 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 120953Z 36006KT 10SM CLR 08/04 A3007 RMK AO2 SLP181 T00830044
BNA | 2018-10-12 05:53 | -86.6892 | 36.1189 | 46 | 39.9 | 79.13 | 350 | 4 | 0 | 30.07 | 1018 | 10 | M | CLR | M | M | M | M | M | M | M | M | KBNA 121053Z 35004KT 10SM CLR 08/04 A3007 RMK AO2 SLP180 T00780044
BNA | 2018-10-12 06:53 | -86.6892 | 36.1189 | 46 | 39 | 76.4 | 10 | 6 | 0 | 30.07 | 1018.2 | 10 | M | FEW | M | M | M | 20000 | M | M | M | M | KBNA 121153Z 01006KT 10SM FEW200 08/04 A3007 RMK AO2 SLP182 T00780039 10111 20078 55000
BNA | 2018-10-12 07:53 | -86.6892 | 36.1189 | 48.9 | 39.9 | 70.95 | 20 | 5 | 0 | 30.07 | 1017.9 | 10 | M | FEW | M | M | M | 20000 | M | M | M | M | KBNA 121253Z 02005KT 10SM FEW200 09/04 A3007 RMK AO2 SLP179 T00940044
BNA | 2018-10-12 08:53 | -86.6892 | 36.1189 | 52 | 39.9 | 63.24 | 40 | 6 | 0 | 30.07 | 1018 | 10 | M | FEW | M | M | M | 25000 | M | M | M | M | KBNA 121353Z 04006KT 10SM FEW250 11/04 A3007 RMK AO2 SLP180 T01110044
BNA | 2018-10-12 09:53 | -86.6892 | 36.1189 | 55 | 39 | 54.7 | 30 | 4 | 0 | 30.07 | 1018.1 | 10 | M | FEW | M | M | M | 25000 | M | M | M | M | KBNA 121453Z 03004KT 10SM FEW250 13/04 A3007 RMK AO2 SLP181 T01280039 55001
BNA | 2018-10-12 10:53 | -86.6892 | 36.1189 | 57 | 37.9 | 48.73 | M | 3 | 0 | 30.06 | 1017.7 | 10 | M | SCT | M | M | M | 25000 | M | M | M | M | KBNA 121553Z VRB03KT 10SM SCT250 14/03 A3006 RMK AO2 SLP177 T01390033
BNA | 2018-10-12 11:53 | -86.6892 | 36.1189 | 61 | 39 | 44.1 | 40 | 5 | 0 | 30.04 | 1016.9 | 10 | M | SCT | M | M | M | 25000 | M | M | M | M | KBNA 121653Z 04005KT 10SM SCT250 16/04 A3004 RMK AO2 SLP169 T01610039
BNA | 2018-10-12 12:53 | -86.6892 | 36.1189 | 62.1 | 37 | 39.21 | 0 | 0 | 0 | 30.01 | 1016 | 10 | M | BKN | M | M | M | 25000 | M | M | M | M | KBNA 121753Z 00000KT 10SM BKN250 17/03 A3001 RMK AO2 SLP160 T01670028 10172 20078 58020
BNA | 2018-10-12 13:53 | -86.6892 | 36.1189 | 63 | 35.1 | 35.24 | 0 | 0 | 0 | 29.99 | 1015.2 | 10 | M | FEW | BKN | M | M | 20000 | 25000 | M | M | M | KBNA 121853Z 00000KT 10SM FEW200 BKN250 17/02 A2999 RMK AO2 SLP152 T01720017
BNA | 2018-10-12 14:53 | -86.6892 | 36.1189 | 64.9 | 37 | 35.54 | M | 4 | 0 | 29.95 | 1014.1 | 10 | M | FEW | BKN | M | M | 18000 | 25000 | M | M | M | KBNA 121953Z VRB04KT 10SM FEW180 BKN250 18/03 A2995 RMK AO2 SLP141 T01830028
BNA | 2018-10-12 15:53 | -86.6892 | 36.1189 | 66 | 37.9 | 35.44 | 320 | 5 | 0 | 29.95 | 1013.9 | 10 | M | BKN | OVC | M | M | 13000 | 25000 | M | M | M | KBNA 122053Z 32005KT 10SM BKN130 OVC250 19/03 A2995 RMK AO2 SLP139 T01890033 56019
BNA | 2018-10-12 16:53 | -86.6892 | 36.1189 | 63 | 36 | 36.52 | 280 | 4 | 0 | 29.93 | 1013.4 | 10 | M | SCT | OVC | M | M | 8000 | 12000 | M | M | M | KBNA 122153Z 28004KT 10SM SCT080 OVC120 17/02 A2993 RMK AO2 SLP134 T01720022
BNA | 2018-10-12 17:53 | -86.6892 | 36.1189 | 62.1 | 39 | 42.41 | 300 | 5 | 0 | 29.93 | 1013.5 | 10 | M | BKN | OVC | M | M | 7500 | 12000 | M | M | M | KBNA 122253Z 30005KT 10SM BKN075 OVC120 17/04 A2993 RMK AO2 SLP135 T01670039
BNA | 2018-10-12 18:53 | -86.6892 | 36.1189 | 60.1 | 39 | 45.53 | 310 | 5 | 0 | 29.93 | 1013.3 | 10 | M | BKN | OVC | M | M | 8000 | 9500 | M | M | #NAME? | KBNA 122353Z 31005KT 10SM -RA BKN080 OVC095 16/04 A2993 RMK AO2 RAB35 SLP133 P0000 60000 T01560039 10194 20156 56008
BNA | 2018-10-12 19:53 | -86.6892 | 36.1189 | 55.9 | 45 | 66.72 | 280 | 4 | 0 | 29.94 | 1013.8 | 10 | M | BKN | OVC | M | M | 5500 | 8000 | M | M | M | KBNA 130053Z 28004KT 10SM BKN055 OVC080 13/07 A2994 RMK AO2 RAE47 SLP138 P0000 T01330072
BNA | 2018-10-12 20:53 | -86.6892 | 36.1189 | 57 | 46 | 66.59 | 290 | 3 | 0 | 29.94 | 1013.6 | 10 | M | OVC | M | M | M | 7500 | M | M | M | M | KBNA 130153Z 29003KT 10SM OVC075 14/08 A2994 RMK AO2 SLP136 T01390078
BNA | 2018-10-12 21:53 | -86.6892 | 36.1189 | 55.9 | 44.1 | 64.47 | M | 6 | 0 | 29.94 | 1013.8 | 10 | M | BKN | OVC | M | M | 4700 | 6000 | M | M | M | KBNA 130253Z VRB06KT 10SM BKN047 OVC060 13/07 A2994 RMK AO2 SLP138 60000 T01330067 51005
BNA | 2018-10-12 22:53 | -86.6892 | 36.1189 | 55.9 | 43 | 61.81 | M | 6 | 0 | 29.95 | 1014 | 10 | M | OVC | M | M | M | 4100 | M | M | M | M | KBNA 130353Z VRB06KT 10SM OVC041 13/06 A2995 RMK AO2 SLP140 T01330061
BNA | 2018-10-12 23:53 | -86.6892 | 36.1189 | 55 | 44.1 | 66.61 | 330 | 5 | 0 | 29.97 | 1014.4 | 10 | M | OVC | M | M | M | 3900 | M | M | M | M | KBNA 130453Z 33005KT 10SM OVC039 13/07 A2997 RMK AO2 SLP144 T01280067

## Pump Head Estimates
Evaporator Pumps
Nominal gpm = | 3000 | gpm
Rated head = | 40 | ft.w.c.
Motor hp = | 40 | hp
Estimated pump head
Item | Head, ft.w.c. |  | Linear Feet |  | Assumed Line Size, inches | Friction Rate, ft.w.c. per 100 feet of pipe |  | Multiplier |  | Comment
| Low End | High End | Low End | High End |  | Low End | High End | Low End | High End
Pipe | 1.008 | 1.328 | 63 | 83 | 12 | 1.6 | 1.6
Fittings | 0.504 | 1.328 | [5 empty] | 0.5 | 1 | Used a low multiplier because not a lot of fittings
Evaporator | 15 | 20
Subtotal | 16.512 | 22.656 | [5 empty] | 0.1 | 0.1
Safety Factor | 1.6512 | 2.2656
Total | 18.1632 | 24.9216
Estimated hp and kW (See equation to the right)
| Low End | High End
Flow rate - | 3000 | 3000 | gpm
Required head - | 18.1632 | 24.9216 | ft.w.c.
Throttled valve - | 21.8368 | 15.0784 | ft.w.c. | Assumes the valve throttles the pump to design conditions
Total head - | 40 | 40 | ft.w.c.
Pump Efficiency - | 85% | 75% | Based on engineering judgement and past expereince
bhp - | 35.6506 | 40.404
Motor % loaded - | 89.13% | 101%
Motor efficiency - | 94.1% | 94.1% | Based on the nominal nameplate efficiency of the motor
hp out of the drive system to the motor - | 37.8859 | 42.9373
Drive system full load rating - | N/A | N/A | Looking at this for the pumps with out drives on them
Drive system % loaded - | N/A | N/A
Drive system efficiency - | 100% | 100% | There is no drive
hp into the drive - | 37.8859 | 42.9373
kW into the drive - | 28.2629 | 32.0313
Assumed electric rate - | 0.1032 | 0.1032 | Source = | https://www.electricitylocal.com/states/tennessee/nashville/
Cost per hour to operate - | 2.9167 | 3.3056
Condenser Pumps | Chiller 1 |  |  | Chiller 2, 3, 4, 5 |  | Chiller 6, 7
Nominal gpm = | 3500 | gpm |  | 4500 | gpm | 3300 | gpm
Rated head = | 95 | ft.w.c. |  | 70 | ft.w.c. | 70 | ft.w.c.
Motor hp = | 100 | hp |  | 100 | hp | 75 | hp
Estimated pump head
Item | Head, ft.w.c. |  | Linear Feet |  | Assumed Line Size, inches | Friction Rate, ft.w.c. per 100 feet of pipe |  | Multiplier |  | Comment
| Low End | High End | Low End | High End |  | Low End | High End | Low End | High End
12" Pipe | 2.04 | 4.392 | 102 | 122 | 12 | 2 | 3.6 |  |  | Low end friction rate at 3300 gpm, high end at 4500 gpm
16" Pipe | 0.4836 | 0.858 | 78 | 78 | 16 | 0.62 | 1.1 |  |  | Low end friction rate at 3300 gpm, high end at 4500 gpm
Fittings | 1.02 | 4.392 | [5 empty] | 0.5 | 1 | Used a low multiplier because not a lot of fittings
Condenser | 15 | 20
Tower lift | 8 | 10 | [7 empty] | Estimated
Tower nozzels | 13.86 | 27.72 | [7 empty] | 6-12 psi estimated
Subtotal | 40.4036 | 67.362
Safety Factor | 4.0404 | 6.7362 | [5 empty] | 0.1 | 0.1
Total | 44.444 | 74.0982
Estimated hp and kW
| Low End | High End
Flow rate - | 3300 | 4500 | gpm
Required head - | 44.444 | 74.0982 | ft.w.c.
Throttled valve - | 50.556 | 0 | ft.w.c. | Assumes the valve throttles the pump to design conditions
Total head - | 95 | 74.0982 | ft.w.c.
Pump Efficiency - | 80% | 80% | Based on engineering judgement and past expereince
bhp - | 98.9583 | 105.2531
Motor % loaded - | 98.96% | 105.3%
Motor efficiency - | 95.8% | 95.8% | Based on the nominal nameplate efficiency of the motor
hp out of the drive system to the motor - | 103.2968 | 109.8676
Drive system full load rating - | 100 | 100 | hp, assumed this matches the motor
Drive system % loaded - | 100% | 100%
Drive system efficiency - | 97% | 97% | Based on Safetronics data
hp into the drive - | 106.4915 | 113.2655
kW into the drive - | 79.4427 | 84.4961
Assumed electric rate - | 0.1032 | 0.1032 | Source = | https://www.electricitylocal.com/states/tennessee/nashville/
Cost per hour to operate - | 8.1985 | 8.72

## Cooling Tower
HP range from BAC Selection Software
| Total hp |  | Cost premium
Maximum | 120 | Best first cost | Base
Middle | 60 | Good life cycle cost | 16%
Minimum | 40 | Best life cycle cost | 49%

## Distribution Pumps
Estimated hp and kW for one pump
Nominal gpm = | 7900 | gpm
Rated head = | 170 | ft.w.c.
Motor hp = | 450 | hp
Header DP Set point = | 143.22 | ft.w.c.
| Full load | 25% Plant Load
Flow rate - | 7900 | 7900 | gpm
Required head - | 170 | 143.22 | ft.w.c. | Assumes a fixed DP at the plant header
Throttled valve - | 0 | 0 | ft.w.c. | Assumes the valve throttles the pump to design conditions
Total head - | 170 | 143.22 | ft.w.c.
Pump Efficiency - | 85% | 85% | Based on engineering judgement and past expereince
bhp (output from the hydraulic drive) - | 398.9899 | 336.1373 | hp
Hydraylic drive efficiency - | 88.66% | 88.66%
Input to the hydraulic drive - | 450 | 379.1118 | hp, assumed the motor was full loaded by the pump through the drive at the pumps design bhp
Motor % loaded - | 100% | 88.66%
Motor efficiency - | 96% | 96% | Based on engineering judgement and past expereince
hp into the motor - | 468.75 | 350.143
kW into the motor - | 349.6875 | 261.2067
Assumed electric rate - | 0.1032 | 0.1032 | Source = | https://www.electricitylocal.com/states/tennessee/nashville/
Cost per hour to operate - | 36.0879 | 26.9567

## Hourly Cost
Cost to run a typical chiller for one hour, Chiller 2 basis
Rated tons |  | 1470 | tons
Rated kW |  | 821 | kW/ton
Minimum load |  | 25%
|  | 367.5 | tons
Electric rate |  | 0.1032 | per kWh
|  | Full Load |  |  |  | 25% Chiller Load, Note 6 |  |  |  | Notes
Item |  | kW | kW/ton | % of Total | Cost | kW | kW/ton | % of Total | Cost
Compressor |  | 821 | 0.5585 | 79.49% | 84.7276 | 205.25 | 0.5585 | 35.23% | 21.1819 | Note 5
Condenser pump |  | 84.4961 | 0.05748 | 8.181% | 8.72 | 84.4961 | 0.22992 | 14.5% | 8.72 | Note 2
Evaporator Pump |  | 30.1471 | 0.020508 | 2.919% | 3.1112 | 30.1471 | 0.082033 | 5.175% | 3.1112 | Note 1
Cooling tower fan |  | 44.76 | 0.030449 | 4.334% | 4.6193 | 0.69937 | 0.0019031 | 0.1201% | 0.072176 | Note 3
Distribution pump |  | 51.6624 | 0.035144 | 5.002% | 5.3316 | 261.2067 | 0.71077 | 44.84% | 26.9567 | Note 4
Compressor oil pump |  | 0.746 | 0.00050748 | 0.07223% | 0.076988 | 0.746 | 0.0020299 | 0.1281% | 0.076988
Total |  | 1032.8115 | 0.70259 | 100% | 106.5867 | 582.5452 | 1.5852 | 100% | 60.119
Notes
1 | Use average value calculated on the "Pump Head Estimates" tab.
2 | Used the highest condenser pump kW on the "Pump Head Estimates" tab.
3 | Used middle of the road fan hp
4 | At full load, this is the total distribution pump kW proportioned to the chiller based on it's share of the load. At 25% load, this is all of the distribution pump energy.
5 | This assumes a linear compressor kW/ton curve, which is probably not totally true
6 | This is one machine operating at 25% load, which would put the plant at 4% load.

## Time Values
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Decimal equivalents of time for time axis scaling
| Date Format | Number Format
Today | 2019-04-11 07:21 | 43566.3065
Date of choice | 2018-10-12 23:00 | 43385.9583
Minutes
1 | 5 | 10 | 15 | 30 | 45
0.00069444 | 0.0034722 | 0.0069444 | 0.010417 | 0.020833 | 0.03125
Hours
1 | 2 | 3 | 4 | 5 | 6
1 am | 2 am | 3 am | 4 am | 5 am | 6 am
0.041667 | 0.083333 | 0.125 | 0.16667 | 0.20833 | 0.25
7 | 8 | 9 | 10 | 11 | 12
7 am | 8 am | 9 am | 10 am | 11 am | Noon
0.29167 | 0.33333 | 0.375 | 0.41667 | 0.45833 | 0.5
13 | 14 | 15 | 16 | 17 | 18
1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm
0.54167 | 0.58333 | 0.625 | 0.66667 | 0.70833 | 0.75
19 | 20 | 21 | 22 | 23 | 24
7 pm | 8 pm | 9 pm | 10 pm | 11 pm | Midnight
0.79167 | 0.83333 | 0.875 | 0.91667 | 0.95833 | 1
This table can be used to come up with the serial number that represents date and time information in a spreadsheet. Excel treats date and time as a serial number. The most common bases are January 1, 1900 or January 2, 1904; one is the IBM type machine standard and the other is the Mac type machine standard. These dates are represented as one and are then incremented by 1 for each day there-after. In this system, 1 hour is 1/24, 1 minute is 1/(24*60), etc.
This spread sheet contains some of the more common increments that I use when scaling the time axis on graphs. When you open it, it automatically displays the current date and time in date format as well as the number format in the cells to the right of "Today". The number to the left of the decimal place represents the date and the numbers to the right of the decimal place represent the time.
Immediately below the current date, you can key in a date or time or date and time in the date format cell next to "Date of Choice" (white colored cell). The integer that represents what you keyed in will show up in the cell immediately to the right under "Number Format". For example, if you key in 3/28/03 11:00 AM in the white cell, you will get 37708.45833. The 37708 portion of the number represents the date (March 28, 2003) and the 45833 represents the time, 11:00 am, which is the 11th hour of that day. So, to use the spreadsheet to create a number that represented a certain date and time you would key it into the white cell and read the result out in the cell immediately to the left.
The remainder of the table provides values that represent incremental parts of a day or hour. I use them mostly to scale the divisions on the time axis on a graph.
For example, if I wanted a graph that ran from midnight on March 27, 2003 to midnight on March 28, 2003, with a grid line at each hour, I would select the axis I wanted by right clicking on it, then pick "Format Axis". On the "Scale" tab, I would set the minimum for 37707, which is the integer associated with March 27, 2003. I would set the maximum for 37708, which is the integer representing March 28, 2003. I would then set the major unit for .0416667, the decimal which represents 1 hour (1/24). You can pick this value up from the table in the hours section under "1". If I wanted 5 minutes, I would use .00347222, which you can pick up off the table under minutes.
Incidentally, for the major divisions to show up, you need to check the "Major Gridlines" boxes for the X and Y axis under the "Gridlines" tab associated with "Chart Options". "Chart Options" is one of the selections available on the "Chart" drop down menu.