## Instructions
Facility Dynamics Headquarters - 6760 Alexander Bell Drive, Suite 200, Columbia, MD 21046, Phone: (410) 290-0900; www.facilitydynamics.com
Facility Dynamics NW Satellite Location - 8560 North Buchanan Avenue, Portland, Oregon 97203, Phone: ; www.facilitydynamics.com
Engineering Calculation
Date: |  |  | 2019-03-07 09:16
Project Name: |  |  | Logic Diagram Example
Project Number: |  |  | 09202000
Engineer: |  |  | David Sellers
Notice: Facility Dynamics Engineering has provided this spreadsheet to support training classes and personal development. We are happy to have you use it to learn about building systems and related concepts and calculations But you are using it at your own risk and neither FDE nor I can be responsible for the results you generate with it and the decisions you make as a result. Please check your work and use your head. In addition, we consider the spreadsheet to be original work and intellectual property. In other words, we own the spreadsheet and it is copyrighted in our name. Having said that, it is important to us to strike an appropriate balance between a desire to support the industry and pass on knowledge that has been handed down to us by our mentors and people like Isaac Newton and Willis Carrier for example, while protecting our intellectual property rights. So thank you in advance for being conscious of that as you apply this spreadsheet. By opening and working with this file, you are acknowledging that you have read and understand this copyright notice and will comply with its requirements including our list of permissions. To view our permissions, please visit http://www.av8rdas.com/copyright-and-permissions.html.
Overview and General Instructions
1 | This spreadsheet contains a set of logic diagram symbols that can be used to develop control logic diagrams as a way of communicating operating sequence information to contractors, a design team, an operating team, etc. There is no industry standard for the symbols and the foundation of this symbol set is the symbol set that FDE uses for their work. The symbol set used by Eikon (Automated Logic Controls' programming language) is somewhat similar.
Traditionally, FDE produces their logic diagrams using AutoCAD and our symbol library exists in that format. But I have come to realize that when we are teaching logic diagrams and trying to have students develop their own, one of the obstacles to success is having a symbol library and drawing tool available to use. These days, students that are practicing engineers frequently have access to and familiarity with AutoCAD so for those students, simply providing our library in its AutoCAD format was a reasonable solution. But for some of the classes we are involved with, there are technical folks performing technical functions, commissioning and operations in particular, who understand and want to communicate logic but, because of their background, are not "fluent" in AutoCAD and/or do not have access to it.
Initially, we addressed the issue by having the students use a pencil and paper to simply draw their own symbols for classroom exercises. Of course, that made the process time consuming in terms of creating and duplicating symbols and after class, the students were still confronted with the need to develop a symbol library in a tool that they were comfortable using to draw electronically.
In an effort to address that challenge, in some venues, we started using free software packages like Eikon for Educators (Automated Logic Controls' programming language) or WindLGC (IDEC's programming language for their "smart relays") as a tool for interactively developing logic diagrams. Both of these tools have the added benefit of allowing you to simulate your logic and verify that the "dominos" all fall in the right order (they can't simulate building/process dynamics). But some might consider the diagrams produced to be proprietary in nature and thus, not particularly useful for construction documents. And we also found that we were spending a lot of time teaching "how to use Eikon" or "how to use WindLGC" rather than "how to develop logic diagrams".
As a result, we decided to try to create a tool that used a fairly common, readily available drawing application. Since the MS Office suite includes a substantial library of basic shapes and the objects created can be copied and pasted across all of the MS Object products, and since many people running Apple's IOS have a Windows shell available, and since the objects created in MS office can be copied and pasted as bit maps into other applications, we chose MS Office as our drawing application. Personally, I find it easiest to develop MS drawing objects in PowerPoint and since I had a slide set with many of our symbols already developed in it, I built from that starting point and developed the symbol library in PowerPoint.
Subsequently, I discovered that you could set row and column heights in terms of inches instead of points in Excel if you made the adjustment in the "Page Layout" view. That capability, along with the ability to quickly format the boarders on cells meant that it was fairly easy to make electronic "graph paper" in Excel. In turn, that lead to the development of the tool you are currently looking at.
The symbol set contains most of the common control functions used for building control systems. Generally, the symbols are identical to the FDE AutoCAD symbols. But in some cases, I have added some enhancements for teaching purposes or to accommodate some personal preferences that I have. More complex functions can usually be built by combining multiple symbols. For example, if you needed a High Selector for 7 inputs rather than 4, you could combine a number of 4 input selectors (Option 1 below). Or, you could create and define a new symbol in your symbol list that was exactly what you needed, as illustrated by Option 2.
Option 2 can be expedient if you find yourself using the same combination of logic blocks to represent a function frequently. What really matters is that if you create a new logic block, you be sure to define it in your symbol list including what each input and output represents and how it works.
2 | The spreadsheet has been set up to use the column and row features of Excel to create electronic graph paper. The grid is set for 0.30 inches square. If you wanted to adjust it and the symbols to some other dimension, you can set row with and column height to units other than points by using the "Page View" setting on the "View" tab, selecting the rows and columns you want to adjust, and entering the desired dimension and related units.
Related to the grid setting, for reasons I have yet to understand, even thought the symbols were drawn on a 0.3 inch grid and the columns and rows are set to that in the spreadsheet, sometimes, Excel "elects" to change things slight. For instance, the grid will reset to 0.29 inches or when you paste an object in, it will not be quite an even multiple of the grid size.
For the time being, the way I work around that is to use the arrow keys to position the symbol so it is on the grid after I paste it in. Usually I use one arrow key click up and one arrow key click left, which will put the top left corner of the symbol on the grid. Then I "grab" the grip (the little black square that shows up when you mouse over a symbol) on lower right corner of other symbol and push or pull it to the nearest grid intersection. While that changes the aspect ratio of the various elements slightly (for instance, squares will no longer be true squares), for a small change, it is not detectable to the eye, at least to my eye. But having things snapped to the grid makes it a lot easier to organize the drawing and interconnect the elements.
The connectors typically snap to the center of the geometric shapes, not the corners. The supporting PowerPoint that describes the symbols in detail discusses how this works if you are not familiar with this MS Office drawing object behavior. This is actually a very useful feature because if you make sure your connectors are snapped to the objects they are connecting, then you can move objects around to re-organize your drawing and will not have to re-establish the connections.
As I said, the supporting PowerPoint slides cover this in more detail. The reason I mention this here is that using the procedure I describe above to slightly resize the symbols can sometimes result in the grips for symbols that have a number of squares stacked vertically or horizontally to no longer be directly on a grid line. So when you draw the connector, it may not be perfectly straight.
How much this matters probably depends on how "anal" you are unless the connector is really long. But if it bothers you, you can either turn off the "snap to grid" setting and manually position things. Or, you can grab the grips on the individual elements and push or pull them so they are on a grid point, which is what I do. Once you have done it to a symbol, it seems to hold if you copy and paste that symbol on a specific worksheet.
3 | The illustration and text that follows describe some of the characteristics and features of the tool.
| 1 | The symbols were originally drawn in PowerPoint for a presentation about logic diagrams and are laid out on a 0.3 inch grid. The size was set by my experience in minimum font sizes for projecting in a training setting. Rather than re-draw the, I simply used them at that scale and set the grid size in the spreadsheet accordingly. On the one hand, that means you can fit less logic on a given sheet than you would be able to fit if they were smaller. But on the other hand, if you wanted to print your drawing set to 11 x 17 so it was more portable out in the field, the larger symbols and text will still be legible, at least to me.
| 2 | The sheet size is set for 24"h x 36"w. This is not a standard Excel output size but you can use the "Add Page Size" feature in Acrobat to set up a sheet of that size in Acrobat and then print to .pdf that way. In addition, this sheet size and the larger symbols generally will print satisfactorily if you scale it to fit on an 11 x 17 sheet size, which is a standard size for many printers and for Acrobat.
| 3 | The title block uses somewhat silly place holders for things like the drawing seal, the name of the project, the name of the architectural firm and engineering firm, the production team, etc. All of those items can be edited to match your project and the logo can be changed to match your logo.
| 4 | The symbols were originally drawn based on using a black background because that seems to project better in a presentation. But if you are printing the sheets out, it will use a lot of blank ink/toner and that may not be desirable. Or you simply may prefer to have a white background. To accommodate those preferences, two of the green control buttons at the bottom left side of the sheet can be used to toggle between a black background and a white background. The buttons simply run a macro that changes the color pallet from one named "FDE Primary" to "FDE Primary White" and back. The colors are simply my preferences; I like primary colors and I like using colors to help distinguish things like analog vs. digital (amber vs. blue) for instance. But, you could edit the color pallets to create background colors and line and fill colors that matched your preferences and/or company standards.
| 5 | I personally believe that if you draw things like logic diagrams and system diagrams on a grid so that things tend to line up and have an orderly arrangement, then the drawing looks more presentable and is easier to read. So, I turn on Excel's "Snap to Grid" feature when I develop the system diagram, and the spreadsheet will likely be defaulted to that when you open it. But you can always turn it off.
Related to this, I also find it handy to have a visual display of the grid available when I am drawing (basically, I like to have my electronic drawing sheet look like graph paper). But when I print, I may want to print with out the "graph paper" look, either to meet a client's preference or so that the sheet looks less "busy". So, I have two green control buttons set up to turn the grid display on and off. All the Marco does is select the entire spreadsheet and then add or remove boarders from the cells, meaning you could do it manually that way. Note that the color pallet affects the way the grid will look since the border colors come from the color pallet.
| 6 | For symbols to be effective, it is important that the people reading them fully understand what they mean. Since I originally created the symbols I use in this tool in PowerPoint for a training class and the slides included all of the details about what the various inputs, outputs, and constants meant, I decided to simply use the basic symbol description (for instance "PID Loop" or "Analog Input") in my symbol list in this tool and then provide a link that would open the appropriate PowerPoint slide to provide the details. So, if you click the symbol name, that is what should happen as long as you have downloaded the PowerPoint show in addition to the Excel tool and placed it on your hard drive.
| 7 | Related to the preceding, the links I have created are relative links. So, if you have placed the PowerPoint show file with the symbol definitions in it in the same folder as the spreadsheet tool, they should work with out any additional effort on your part. However, if you made edits to the PowerPoint file to define a symbol you have created and wanted to rename it or wanted to keep it in a different location, then that will break the links.
To address that issue, I included cells where you can enter the location and file name for the PowerPoint show file that defines the symbols. If you enter the appropriate information in those two cells, then the hyperlinks are set up to "read" that information and update accordingly. This is a new feature and I have not tested it a lot, so if you have problems with it, you may have to directly edit each of the links. But so far, in the limited testing that I have done, it seems to work.
| 8 | Each tab of the tool is set up to represent one sheet of a drawing set. Currently, the first three sheets are dedicated to the symbols list and drawing list. The drawing list has been set up so you can hyperlink to the appropriate tabs as associated with the different sheets in the drawing set. The sheets after the first sheet include a fifth, green, control button that allows you to jump back to the first sheet and then use the drawing list to jump to a different sheet. The current tool includes a blank sheet and sheets with a number of examples of the different logic diagrams that are essentially the "answers" for some of the exercises we do in some of our training classes.
If you keep the "Blank" sheet blank, you can make additional sheets by clicking on the word "Blank" on the tab, right clicking, and then selecting the "Move or Copy …" function and then selecting the location where you want the new sheet. Be sure to click the "Copy" check box that is in the dialog box, otherwise you will just move the "Blank" tab instead of copying it. Excel will automatically assign a new name to the new tab in the form of <Blank#> where # represents how many copies you have made of the tab (i.e., the first copy will be "Blank 2", the second "Blank 3", etc.). But if you double click on the tab name, you can edit it to what ever you want to name it.
| 9 | Note that the symbol list includes a lopsided "Z" shaped line in addition to a straight line for each connection type. The "Z" shape is actually a special MS Office shape. It is a single shape with three connected lines in it. Once you place it, you can drag the end points at each end of the "Z" to the start and end locations you want and drag a point in the middle of the vertical line to shift the position of it horizontally. The shape makes it much faster to connect to points that are offset from each other relative to the time it takes to do it by drawing three lines.
© 2017 Facility Dynamics Engineering - All Rights Reserved
1
2
3
4
5
6
6
7
8
9

## TC-00 Symbols
[13 empty] | Morgan, Wright, Jungermann and Kelley | Architects, Master Planners | 2700 Gumby Place ¦ Suite 1872 ¦ San Deigo, CA 92101 619.608.1887
| Input, Output, Vitrual Points, and Constants |  |  |  | Connectors and Reference Flags | [5 empty] | Drawing List
[11 empty] | Sheet Number | Description
[11 empty] | TC-00 | Symbols and Abbreviations, Drawing List
Input Point Logic Block
[11 empty] | TC-01 | Symbols and Abbreviations (continued)
[11 empty] | TC-01 | Symbols and Abbreviations (continued)
[9 empty] | Connectors (Virtual Wires) |  | TC-02 | Symbols and Abbreviations (continued)
Symbols and Abbreviations (continued)
[11 empty] | TC-01 | Blank sheet to start your own drawing
Symbols and Abbreviations (continued)
[11 empty] | TC-01 | Hi Signal Selector Example
Symbols and Abbreviations (continued)
[11 empty] | TC-01 | Bureaucratic Affairs Building HHW Hx Control Example - Basic Heat Exchanger Control
Symbols and Abbreviations (continued)
Reference Flags - Origin
Output Point Logic Block
[11 empty] | TC-01 | Bureaucratic Affairs Building HHW Hx Control Example - Enhanced features to improve performance and utility and save energy
Symbols and Abbreviations (continued)
[9 empty] | Reference Flags - From Indicated Sheet |  | TC-02 | Bureacratic Affairs Building Occupancy Control Logic Example
Hijend Hospitality Interntational
[11 empty] | TC-03 | Bureacratic Affairs Building Finned Tube Radiation Zone Control Example
San Diego Bayview Marquis Hotel and Marina
Power Return Flag
[11 empty] | TC-04 and TC-05 | Bureacratic Affairs Building Hot Water Pump Control Example
Logic Functions
|  | Virtual Point Logic Block | [10 empty] | Issued for Bid:
[11 empty] | TC-01 | University of Wisconsin DDC Class Mixed Air Section Control Exercise Solution | 2002-09-20
[7 empty] | And Logic Block |  |  | Nand (Not And) Logic Block |  |  | Drawn By:
M. Nyun 4-20-2002
Checked By:
[11 empty] | TC-01 | Two Speed Cooling Tower Fan with Bypass Valve Control Example | M. Nature 7-20-2002
[13 empty] | Rev | Date
[7 empty] | Or Logic Block |  |  | Nor (Not Or) Logic Block
[11 empty] | Supporting Information | Supporting information for the Bureaucratic Affairs Building including a HW system diagram, floor plans with FTR zones shown, and images from the building model.
[7 empty] | Exclusive Or Logic Block |  |  | Not Logic Block
Constant Logic Block
If Logic Block
Symbols and Abbreviations
TC-00
OF ##
© 2017 Faciltiy Dynamics Engineering - All Rights Reserved
|  |  | Symbol Definition File Location - |  |  | D:\FDE Tools\Logic Diagrams\Logic Diagram Tool
|  |  | Symbol Definition File Name - |  |  | Logic Diagram Symbols v5.ppsx
O
R
Ia
Ib
O
A
N
D
Ia
Ib
O
X
O
R
Ia
Ib
O
N
A
N
D
Ia
Ib
O
N
O
R
Ia
Ib
O
Isaac Newton
Main Man
Registered
State of Mass
F=ma
#1
NOT
I
O
IF
I
Condition
O
SP
“Units”
Value
Constant Function
C
Value
Constant Function
C
Typical Point Name
VP
Typical Point Name
VP
Typical Point Name
VPOA
Value
Constant Function
COA
Typical Point Name
VPOA
Typical Point Name
Address
AI
Typical Point Name
Address
DI
Typical Point Name
Address
AO
Normal
Units
Typical Point Name
Address
DO
Normal
Units
Reference
Reference
TC-##
Reference
Reference
TC-##
Power Recovery
Analog Value
Constant Function
C

## TC-01 Symbols
[11 empty] | Morgan, Wright, Jungermann and Kelley | Architects, Master Planners | 2700 Gumby Place ¦ Suite 1872 ¦ San Deigo, CA 92101 619.608.1887
Control Processes and Functions
|  |  | Piloted Switch Logic Block |  |  |  |  | Proof of Operation Logic Block
Ratio Logic Block
Set Point Optimization (Trim and Respond) Logic Block
Dead Band Piloted Switch Logic Block
High Selector Logic Block
PID (Proportional + Integral + Derivative) Loop Logic Block
[5 empty] | Ramp Up Logic Block | [5 empty] | Hijend Hospitality Interntational
Reset Logic Block
San Diego Bayview Marquis Hotel and Marina
Low Selector Logic Block
Issued for Bid:
[5 empty] | Ramp Down Logic Block | [5 empty] | 2002-09-20
|  | Floating Control Logic Block | [8 empty] | Drawn By:
M. Nyun 4-20-2002
Checked By:
M. Nature 7-20-2002
[11 empty] | Rev | Date
Calculation Logic Block
Start Ramp Logic Block
Averaging Logic Block
Stop Ramp Logic Block
Symbols and Abbreviations
TC-01
OF ##
© 2017 Faciltiy Dynamics Engineering - All Rights Reserved
|  |  |  | Symbol Definition File Location - |  |  | D:\FDE Tools\Logic Diagrams\Logic Diagram Tool
|  |  |  | Symbol Definition File Name - |  |  | Logic Diagram Symbols v5.ppsx
Isaac Newton
Main Man
Registered
State of Mass
F=ma
#1
F
L
T
SP
OOpn
I
Go
IDB
“Action/Normal”
OCls
IOn
IOff
IGOff
RT=###
RAMP UP
I
IRt
“Units”
O
O
I
TStart
RAMP DOWN
I
IRt
“Units”
O
O
I
TStop
START RAMP
I
IRt
“Units”
O
ISP
ILim
O
I
TStart
STOP RAMP
I
IRt
“Units”
O
ISP
ILim
O
I
TStop
SET POINT OPTIMIZATION
ISPDesign
“Adj. Units”
O
“Up/Dn”
Time
SPULim
SPDes
LdMax
LdMin
ISPUpLim
ISPLoLim
IAdjInrmnt
IDelay
IFdBk
IFdBkUpLim
IFdBkLoLim
“FdBk Input”
“FdBk Units”
H
I
G
H
I1
O
I2
I3
I4
L
O
W
I1
O
I2
I3
I4
A
V
E
R
A
G
E
I1
O
I2
I3
I4
CALC
I1
Equation
O
I2
I3
I4
I5
I6
I7
I8
I9
I10
P
R
O
O
F
IDly
ONml
IPrf
ICmd
OAlr
IRst
H
I
G
H
I1
O
I2
L
O
W
I1
O
I2
A
V
G
I1
O
I2
P
I
D
SP
O
I
Go
KP
KI
KD
“Units”
IGOff
“Action”
RESET - DA
IHi
ILo
SPIHi
SPILo
I
O
SPIHi
SPILo
ILo
IHi
RESET - RA
IHi
ILo
SPIHi
SPILo
I
O
SPIHi
SPILo
ILo
IHi
RATIO - DA
IHi
ILo
SPIHi
SPILo
I
SP
SPIHi
SPILo
ILo
IHi
RATIO - RA
IHi
ILo
OIHi
OILo
I
O
SPIHi
SPILo
ILo
IHi
SW
INO
INC
Pilot
O
SW
Pilot
ONO
ONC
I
SW
DB
Pilot
PHi
PLo
ONO
I
ONC
SW
DB
INO
O
INC
Pilot
PHi
PLo

## TC-02 Symbols
[8 empty] | Morgan, Wright, Jungermann and Kelley | Architects, Master Planners | 2700 Gumby Place ¦ Suite 1872 ¦ San Deigo, CA 92101 619.608.1887
| Timers, Counters, and Clocks |  |  |  | Graphics, Trends, Alarms, Messages
Display Value on System Graphic Logic Block
One Shot Relay
Counter Logic Block
Trend Parameter and Archive Data Logic Block
Interval Timer Logic Block
Alarm Based on Parameter Logic Block
Operator Message Logic Block
|  | Time Clock/Scheduler Logic Block | [5 empty] | Hijend Hospitality Interntational
San Diego Bayview Marquis Hotel and Marina
Run Time Monitor Logic Block
|  | On Delay Logic Block | [5 empty] | Issued for Bid:
2002-09-20
Drawn By:
M. Nyun 4-20-2002
[7 empty] | Hard Wired Safety | Checked By:
M. Nature 7-20-2002
[8 empty] | Rev | Date
Off Delay Logic Block
Latch On Logic Block
Latch Off Logic Block
Symbols and Abbreviations
TC-02
OF ##
© 2017 Faciltiy Dynamics Engineering - All Rights Reserved
|  |  |  | Symbol Definition File Location - |  | D:\FDE Tools\Logic Diagrams\Logic Diagram Tool
|  |  |  | Symbol Definition File Name - |  | Logic Diagram Symbols v5.ppsx
Isaac Newton
Main Man
Registered
State of Mass
F=ma
#1
TIMER
ITr
ISP
O
Unit
IMax
CLOCK
IOr
O
I
ON DELAY
I
ISP
O
Unit
OFF DELAY
I
ISP
O
Unit
LATCH ON
I
O
IRst
LATCH OFF
I
O
IRst
Graphic
Alarm
Message ###
Graphic
Alarm
Message ###
1 SHOT
ITr
ISP
O
Unit
IMax
1
2
3
I
IRst
COUNT
O
4
2
0
I
IRst
R
T
M
I
Function
SAFETY
SPMR or AR
I
Function
SAFETY
SPMR or AR

## HW Hx Cntrl Basic
#VALUE!
[10 empty] | Morgan, Wright, Jungermann and Kelley | Architects, Master Planners | 2700 Gumby Place ¦ Suite 1872 ¦ San Deigo, CA 92101 619.608.1887
Bureaucratic Affairs Building Heating Hot Water System (BA-1-HWS) Hot Water Heat Exchanger Control
+
-
State Of Anxiety
Bureaucratic Affairs Bldg. Control Upgrade
Issued for Bid:
2008-09-20
Drawn By:
M. Nyun 4-20-2008
Checked By:
M. Nature 7-20-2008
[10 empty] | Rev | Date
Notes
|  |  |  | 1 |  | Coordinate address during submittal review the the project specific hardware requirements and network architecture.
|  |  |  | 2 | 2 | Tune during the Cx process for stable operation under all operating conditions. |  |  |  | HHW Hx Control
|  |  |  | 3 | 3 | The design intent is for this to be a PI loop unless field experience indicates that the derivative function is required or desirable.
|  |  |  | 4 | 4 | Maintain the last command when the control process shuts down
TC-01
OF 04
© 2017 Faciltiy Dynamics Engineering - All Rights Reserved
|  | Symbol Definition File Location - | [5 empty] | D:\FDE Tools\Logic Diagrams
Isaac Newton
Main Man
Registered
State of Mass
F=ma
#1
P
I
D
SP
O
I
Go
KP
KI
KD
IGOff
DA
4-20 ma
STHX-1-LWT
Note 1
AI
170°F
STHX-1-LWT-SP
COA
Note 4
STHX-1-LWT-OFF
COA
Note 2
STHX-1-LWT-PG
COA
Note 2
STHX-1-LWT-IG
COA
Note 3
STHX-1-LWT-DG
COA
HWPMP-1-DPSW
Note 1
DI
HWPMP-2-DPSW
Note 1
DI
HWPMP-1-DPSW
HWPMP-2-DPSW
STMVLV-CMD
Note 1
AO
NO
4-20 ma
O
R
Ia
Ib
O

## HW Hx Cntrl Enhanced
#VALUE!
[10 empty] | Morgan, Wright, Jungermann and Kelley | Architects, Master Planners | 2700 Gumby Place ¦ Suite 1872 ¦ San Deigo, CA 92101 619.608.1887
+
-
State Of Anxiety
Bureaucratic Affairs Bldg. Control Upgrade
Issued for Bid:
2008-09-20
Drawn By:
M. Nyun 4-20-2008
Checked By:
M. Nature 7-20-2008
[10 empty] | Rev | Date
Notes
|  |  |  | 1 |  | Coordinate address during submittal review the the project specific hardware requirements and network architecture.
|  |  |  | 2 | 2 | Tune during the Cx process for stable operation under all operating conditions. |  |  |  | HHW Hx Control
|  |  |  | 3 | 3 | The design intent is for this to be a PI loop unless field experience indicates that the derivative function is required or desirable.
|  |  |  | 4 | 4 | Maintain the last command when the control process shuts down
TC-01
Bureaucratic Affairs Building Heating Hot Water System (BA-1-HWS) Hot Water Heat Exchanger Control
OF 04
© 2017 Faciltiy Dynamics Engineering - All Rights Reserved
|  | Symbol Definition File Location - | [5 empty] | D:\FDE Tools\Logic Diagrams
Alarm
Graphic
Isaac Newton
Main Man
Registered
State of Mass
F=ma
#1
P
I
D
SP
O
I
Go
KP
KI
KD
IGOff
DA
4-20 ma
STHX-1-LWT
Note 1
AI
Note 4
STHX-1-LWT-OFF
COA
Note 2
STHX-1-LWT-PG
COA
Note 2
STHX-1-LWT-IG
COA
Note 3
STHX-1-LWT-DG
COA
HWPMP-1-DPSW
Note 1
DI
HWPMP-2-DPSW
Note 1
DI
HWPMP-1-DPSW
HWPMP-2-DPSW
STMVLV-CMD
Note 1
AO
NO
4-20 ma
O
R
Ia
Ib
O
Graphic
SW
INO
INC
Pilot
O
Graphic
Graphic
Graphic
Graphic
STHX-1-EWT
Note 1
AI
BLD-OCC
TC-02
NOT
I
O
SW
INO
INC
Pilot
O
H
I
G
H
I1
O
I2
L
O
W
I1
O
I2
RESET - RA
IHi
ILo
SPIHi
SPILo
I
O
SPIHi
SPILo
ILo
IHi
Graphic
SYSTM-OAT
Note 1
AI
SYSTM-OAT
140°F
STHX-1-LWT-UNOCC-SP
COA
170°F
STHX-1-LWT-RSTIHI-SP
COA
102.5°F
STHX-1-LWT-UNOCC-SP
COA
7.4°F
STHX-1-OAT-RSTILO-SP
COA
55°F
STHX-1-OAT-RSTIHI-SP
COA
20 ma
STHX-1-CLS-SP
C