## Slide 1: Existing Building Commissioning Workshop: Series 17, April 13, 2022 Session
Introduction to Proportional + Integral + Derivative (PID) Control
David Sellers
Senior Engineer, Facility Dynamics Engineering
Presented By:

## Slide 2: A Simple Analog Control System
Sensor
Set Point and Throttling Range Adjustments
Final Control Element
Feedback Mechanism

## Slide 3: A Simple Control Requirement
The make up valve is the device to be controlled; a.k.a. the Controlled Variable or Final Control Element
Notes: Development 2

## Slide 4: A Simple Control Requirement
The tank water level is the Process Variable
Set Point
The desired level becomes the Set Point
Notes: Development 2

## Slide 5: A Simple Proportional Control System
The float is the Sensor
Set Point
The valve handle and linkage is the Actuation System
The lever arms and the pivot point are the controller
Notes: Development 2

## Slide 6: A Simple Proportional Control System
The linkage system makes the water level proportional to the amount the control valve is opened
Set Point
Notes: Development 2

## Slide 7: A Simple Proportional Control System
The ratio of the lever arms on each side of the fulcrum sets the proportional band and gain the of the control system
Set Point
Notes: Development 2

## Slide 8: A Simple Proportional Control System
As long as the demand does not exceed the capacity of the delivery system (i.e. steady state can be achieved inside the proportional band) the system will be under control
Control Point
Set Point
The proportional band is the change in the process variable that causes the controlled variable to go through its full range
Notes: Development 2

## Slide 9: A Simple Proportional Control System
Set Point
By its nature, a proportional control system will always have a difference or “error” between the set point and the control point except at one specific condition
Control Point
Error
Notes: Development 2

## Slide 10: A Simple Proportional Control System
Set Point
We could reduce the error by increasing the gain of the controller (making it more sensitive to a level change in this case) …
Control Point
Notes: Development 2

## Slide 11: A Simple Proportional Control System
Set Point
… but at some point, feedback from the process would interact with the control loop in a way that would make it unstable
Control Point
Notes: Development 2

## Slide 12: The Impact of Narrowing Throttling Range
Proportional band =400% and set point changed to 80% (black line)
Set point changed to 80%
Significant error between the control point and set point

## Slide 13: The Impact of Narrowing Throttling Range
Proportional band =400% (black line)
Proportional band =300% and set point changed to 80% (red line)
Set point changed to 80%
Error between the control point and set point is reduced

## Slide 14: The Impact of Narrowing Throttling Range
Proportional band =400% (black line)
Proportional band =300% (red line)
Proportional band =200% and set point changed to 80% (blue line)
Set point changed to 80%
Error between the control point and set point is further reduced
Signs of instability and hunting emerge

## Slide 15: The Impact of Narrowing Throttling Range
Proportional band =400% (black line)
Proportional band =300% (red line)
Proportional band =200% (blue line)
Proportional band =150% and set point changed to 80% (gray line)
Set point changed to 80%
The system begins to resonate at it’s natural frequency (hunting begins)

## Slide 16: The Impact of Narrowing Throttling Range
Proportional band =400% (black line)
Proportional band =300% (red line)
Proportional band =200% (blue line)
Proportional band =150% (gray line)
Proportional band =100% and set point changed to 80% (second black line)
Set point changed to 80%
The system becomes dynamically unstable

## Slide 17: Bottom Lines On Proportional Control
All proportional control processes will show a difference between set point and control point (a.k.a. error) under all operating conditions other than one very specific condition
The error can be reduced by narrowing down the throttling range
There is a limit to how much you can narrow the throttling range with out hunting
The limit is a function of the physics of the control system; things like lags, play in the linkage system, the nature of the process, etc.

## Slide 18: Then a Miracle Occurs
Image from http://www.sciencecartoonsplus.com/pages/gallery.php
Notes: http://www.sciencecartoonsplus.com/pages/gallery.php

## Slide 19: Proportional plus Integral plus Derivative Control (PID)
PID is the Miracle that can:
  Eliminate error
  Reduce the magnitude of a spike when a system is upset
  Reduce the settling time after an upset

## Slide 20: A Simple Proportional Control System
Set Point
By its nature, a proportional control system will always have a difference or “error” between the set point and the control point except at one specific condition
Control Point
Error
Eliminating Proportional Error;
Becomes Less Simple
Notes: Development 2

## Slide 21: A Simple Proportional Control System
Set Point
Control Point
If the system has capacity beyond the current operating requirement, and the error had persisted for a while, the operator could adjust the float to eliminate the error at the current load condition
Eliminating Proportional Error;
Becomes Less Simple
Notes: Development 2

## Slide 22: A Simple Proportional Control System
Set Point
Control Point
If the system has capacity beyond the current operating requirement, and the error had persisted for a while, the operator could adjust the float to eliminate the error at the current load condition
Eliminating Proportional Error;
Becomes Less Simple
Notes: Development 2

## Slide 23: A Simple Proportional Control System
By monitoring the error over time, the operator could adjust the float setting so that it always maintained the desired set point
Set Point =
Control Point
Eliminating Proportional Error;
Becomes Less Simple
Notes: Development 2

## Slide 24: A Simple Proportional Control System
This is what the Integral function in a Proportional plus Integral plus Derivative control loop does
Set Point =
Control Point
Eliminating Proportional Error;
Becomes Less Simple
Notes: Development 2

## Slide 25: The Impact of Adding Integral Gain
Set point changed to 80%
Proportional only response; 250% proportional band
Note error between the control point and set point

## Slide 26: The Impact of Adding Integral Gain
Set point changed to 80%
Proportional only response; 250% proportional band
Proportional + Integral response; 250% proportional band, Integral time = 2 minutes
Error eliminated!

## Slide 27: The Impact of Adding Integral Gain
Set point changed to 80%
Proportional only response; 250% proportional band
Proportional + Integral response; 250% proportional band, Integral time = 2 minutes
Proportional + Integral response; 250% proportional band, Integral time = 0.75 minutes
Signs of instability and hunting emerge

## Slide 28: A Simple Proportional Control System
Similarly, the operator could monitor the process and if he or she saw the error start to rapidly change relative to time, they could quickly push the float up or down to minimize the deviation from set point
Set Point =
Control Point
Eliminating Proportional Error;
Becomes Less Simple
Notes: Development 2

## Slide 29: A Simple Proportional Control System
Once the sudden change is over the operator could reset the float to match the current load condition and maintain the required set point
Set Point =
Control Point
Eliminating Proportional Error;
Becomes Less Simple
Notes: Development 2

## Slide 30: A Simple Proportional Control System
This is what the Derivative function in a Proportional plus Integral plus Derivative control loop does
Set Point =
Control Point
Eliminating Proportional Error;
Becomes Less Simple
Notes: Development 2

## Slide 31: The Impact of Adding Derivative Gain
Set point changed to 80%
Proportional only response; 250% proportional band
Proportional + Integral response; 250% proportional band, Integral time = 2 minutes

## Slide 32: The Impact of Adding Derivative Gain
Set point changed to 80%
Proportional + Integral + Derivative response; 250% proportional band, Integral time = 0.75 minutes, Derivative time = 0.1 minutes
Properly applied, derivative reduces the spike at upset and shortens the settling time

## Slide 33: PID; Its Been Around for a While
Image courtesy Control Engineering Magazine
Notes: Started to show up in the HVAC industry in the late 1970’s
Technology actually developed in the late 1930’s.
Ziegler-Nichols tuning techniques developed in the 1940’s.

## Slide 34: PID Good News and Bad News
Good News
Eliminate offset
  Save energy
  Improve precision
Minimize process swings at start-up
Bad News
Not well understood by the HVAC industry
  More difficult to tune and adjust
  More difficult to maintain
Algorithm used varies with the manufacturer
  Tuning solution specifics are not portable
  Auto-tuning is not a panacea
Difficult to apply correctly
Often misapplied

## Slide 35: PID; The Math Perspective

## Slide 36: Integral Gain; Minutes per Repeat or Repeats per Minute
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
Proportional only response to the upset
P only response
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 37: Integral Gain; Minutes per Repeat or Repeats per Minute
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
P only response
PI response
Integral response to the upset
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 38: Integral Gain; Minutes per Repeat or Repeats per Minute
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
P only response
PI response
Integral gain of 1 repeat per minute will increases the output by an amount equal to the P only response after one minute
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 39: Potential Problems when Adding Integral Action
Loop instability unless a commensurate reduction in proportional gain is made
Tuning and maintenance become more complex, time consuming and difficult
“Wind-up” can occur
  During HVAC system overload conditions.
  During HVAC shut down if not handled appropriately

## Slide 40: Derivative Gain is in Minutes
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
Proportional only response to the upset
P only response
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 41: Derivative Gain is in Minutes
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
P only response
PD response
Derivative response to the upset
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 42: Derivative Gain is in Minutes
Increasing Time
Minutes
Increasing Output Signal
1
2
3
Process upset occurs
P only response
PI response
A derivative gain of 1 minute will immediately increases the output by an amount equal to the Integral response after one minute
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 43: Derivative Action Is Difficult to Apply
Provides no benefit if there is not enough
Too much can cause many more problems than it is worth
Typically not necessary for HVAC applications
Use it with CAUTION!

## Slide 44: PID Controller Tuning
Roots of the process are in Optimum Settings for Automatic Controllers
    John G. Ziegler
    Nathan B. Nichols
    1940
    Ziegler-Nichols Method
Image courtesy Control Engineering Magazine

## Slide 45: The Quarter Decay Ratio; Signature of a Well Tuned PID Loop
Increasing Time
Minutes
Increasing Process Variable
1
2
3
Process upset occurs
Set Point
Process Variable
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 46: The Quarter Decay Ratio; Signature of a Well Tuned PID Loop
Increasing Time
Minutes
Increasing Process Variable
1
2
3
Process upset occurs
Set Point
Process Variable
This …
… is about 4 times as big as this
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 47: Closed Loop Tuning Method
With the system under automatic control, determine the Natural Period
  Proportional gain = ¼ to ½ of the ultimate gain producing the Natural Period
  Integral time in minutes per repeat = 1.2 times the Natural Period
  Derivative time in minutes = 1/8 of the Natural Period
Natural Period

## Slide 48: Open Loop Tuning Method
Also useful for troubleshooting
With the system under manual control, insert a step change and observe the response curve. Set the controller as follows:
  Proportional gain = 1/(RL) to 1/(2 RL)
  Integral time in minutes per repeat = 5 times the apparent dead time
  Derivative time in minutes = ½ the apparent dead time.
Point in time when the step change was initiated
Apparent dead time (Lag; L)
Slope of the response curve after a stable rate of change is established (Rate of change; R)
Some processes are self regulating and will level off. Others won’t.

## Slide 49: Learning by Doing (But With Out Blowing Something Up)

## Slide 50: Tuning Resources
Controller Tuning and Control Loop Performance by David W. St. Clair
  Judy St. Clair Straight Line Control, LLC 6326 4th Avenue South Richfield, MN 55423 USA Phone:612-869-6814 Fax: 612-869-2761 jastclair@pro-ns.net http://www.straightlinecontrol.com
Notes: To order a copy of "Reference Guide to PID Tuning" visit www.controleng.com/info and request number 367 from the August 1998 North American issue of Control Engineering.
Judy St. Clair Straight Line Control, LLC 6326 4th Avenue South Richfield, MN 55423 USA Phone:612-869-6814 Fax: 612-869-2761 jastclair@pro-ns.net http://www.straightlinecontrol.com

## Slide 51: Tuning Resources
Reference Guide to PID Tuning
  Available from the publishers of Control Engineering
  See A Field Perspective on Engineering Blog Post for Links
Notes: To order a copy of "Reference Guide to PID Tuning" visit www.controleng.com/info and request number 367 from the August 1998 North American issue of Control Engineering.
Judy St. Clair Straight Line Control, LLC 6326 4th Avenue South Richfield, MN 55423 USA Phone:612-869-6814 Fax: 612-869-2761 jastclair@pro-ns.net http://www.straightlinecontrol.com

## Slide 52: Tuning Resources
See An Overview of Proportional plus Integral plus Derivative Control and Suggestions for Its Successful Application and Implementation from the proceedings of the 2001 International Conference on Enhanced Building Operations

## Slide 53: The Quarter Decay Ratio; Signature of a Well Tuned PID Loop
Increasing Time
Minutes
Increasing Process Variable
1
2
3
Process upset occurs
Set Point
Process Variable
This spike needs to be small enough to not break something
This settling time needs to be reasonable in the context of the load served by the process
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 54: It All Depends on the Lags David W. St. Clair

## Slide 55: Lags and the Response to a Set Point Change
The controller has to react to the change
A volume of air needs to move through the line and fill the actuator
The actuator linkage has to move through any “play” that exists
The valve plug needs to move
Steam needs to flow into the heat exchanger
The thermal mass of the heat exchanger and water needs to change temperature
The warmer water needs to move to the sensor location
The mass of the sensor and well needs to change temperature
Notes: The warmer water needs to move to the sensor location

## Slide 56: Some Observations
Red to Black is the control system response with increasing gains applied to the controller until the natural period is identified

## Slide 57: Some Observations
Apparent dead time (Lag; L)
Natural period PN

## Slide 58: Some Observations
1
2
3
4
The Natural Period is about 4 times the Apparent Dead Time

## Slide 59: Some Observations
The deviation from set point upon an upset with tightly tuned control loop (gray line) is about the same as a totally un-tuned loop (red line) at a point in time equal to about half the natural period

## Slide 60: Some Observations
A tightly tuned control loop (gray line) will take about twice the natural period to re-stabilize after an upset

## Slide 61: Lags; The Bottom Line
Increasing Time
Minutes
Increasing Process Variable
1
2
3
Process upset occurs
Set Point
Process Variable
If this breaks something, or …
… if this is too long, and …
… if this is less than twice the apparent dead time …
… then you won’t be able to solve the problem with loop tuning until you get rid of some lags
Notes: H F
7.84 8.00
6.00 7.00
3.06 5.00
1.10 3.00
0.49 2.00
0.12 1.00
0.00 0.00

## Slide 62: Getting Rid of Lags; Sometimes It’s Easier than Others
Easier
Add positioning relays to valve and damper actuators
Install faster actuators (particularly applicable to electric actuators)
Reduce the thermal lag associated with wells by not using them
Use tighter linkages to minimize hysteresis
Use ramps instead of acceleration and deceleration times in VFDs
Harder
Reducing transportation times
Reducing the thermal lags associated with the size of the machinery (mass of coils, fans, duct, pipe, etc.)

## Slide 63: A Bit More About Ramps
Acceleration and Deceleration times
Apply all of the time, any time there is a change in the process
  An acceleration setting of, for example, 1hz/second will always apply regardless of if the difference between set point and control point was because of a start-up or step change in set point vs. minor variations in the control point relative to set point
  This introduces a permanent lag into the control process with the associated implications for tuning the process
Ramps
Only apply when the set point is outside some window relative to the control point
  Ramps will only apply if the difference between the set point and control point is large (outside of some predefined window)
  If the set point and control point are inside the window, then the lag associated with the ramp drops out of the picture
  As a result, the response to a minor variation in set point is much faster than the response to a step change (start up or set point change

## Slide 64: It All Depends on the Lags David W. St. Clair
An Air Handling System Example

## Slide 65
T
Fz
T
VFD
T
H
T
H
VFD
Dampers Move
Air Has to Mix
Mass of the Equipment Modifies the Real Temperature
Air Must Move to the Sensor
Sensor Reaction Time
Control Process Reaction Time
Pneumatic tubing lags
Actuator Motion
Linkage Motion

## Slide 66: It All Depends on the Lags David W. St. Clair
An more detailed air handing system example:
https://tinyurl.com/LagsAndTheBigBangTheory